## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 10 - Circuit Simulator Data Only
Test Date: | 2010-03-25
DCSim DAQ Start Time | 10:11
DCSim Time for Synchronization | 10:40
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 10:40
Fire Time | 11:27
Offset | 1:16 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 4560 | seconds
Heat Source Offset | 0:47 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2811 | seconds
Heat Source Stop Time | 12:33
Test Duration | 1:06 | hour:minutes:seconds
| 3960 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | Kerite, 9c, 12AWG, without zinc wrap |  | There are two cable TCs monitoring internal temperatures of the Kerite cable in C Position. Channels 10 and 11 are represented as "C Position - Kerite 9c wo - 3'" and "C Position - Kerite 9c wo - 5'" in the raw temperature files. | There are three TCs monitoring air temperatures along the middle of the tray in C Position. Channels 5, 6, and 7 are represented as "C Position - 3'", "C Position - Middle", and "C Position - 7'" in the raw temperature files.
MOV 2 | Kerite, 10c, 12AWG, with zinc wrap |  | Channel 2 represented as "B-Position - Kerite 10c w" in the Temperature Data File is monitoring the center of the cable sample sitting within the tray. | Channel 1 represented as "B-Position - Tray - Middle" in the Temperature Data File is monitoring the air temperature in the middle of the tray at B Position.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-1.2812 | 121.9574 | -61.0931 | 60.498 | 0.0019074 | 0 | 0.062827 | 0.063929 | -0.0010041 | -0.0022794 | -0.0017304 | 0.00018312 | -0.0015872 | -1.3935 | 0.066734 | 0.00014521 | 0.0042127 | -0.0017303 | -0.022888 | 60.2005 | -61.0016 | 60.791 | -60.8002 | -61.2167 | -61.3174 | 0.032043 | 60.26 | -61.1206 | 60.5667 | -61.0107 | -61.0886 | -61.2991 | 0.091553 | -0.29755 | 0.29297 | 0.29297 | -0.2243 | -0.1236 | -0.31586 | -0.21515 | -0.027465 | -0.23804 | 0.068664 | 0.082398 | -0.20599 | 0.004578 | -0.17853 | 0.032043 | 0.20142 | 121.7926 | 0.10986 | 121.6873 | 121.2021 | 121.3806 | 121.2936 | 121.3531 | -121.4996 | -121.6187 | 121.8842 | 121.6599 | 61.0703 | 61.1252
0.46875 | 121.8567 | -61.1664 | 60.5072 | 0.0095369 | 0 | 0.069022 | 0.069056 | 0.0026275 | -0.00078404 | -0.00044863 | 0.0032349 | 0.001617 | -1.3935 | 0.068015 | -6.8386e-05 | 0.0033581 | -2.1314e-05 | 0.036621 | 60.2463 | -61.0611 | 60.7407 | -60.878 | -61.3037 | -61.3861 | -0.009155 | 60.2554 | -61.1526 | 60.4568 | -61.1481 | -61.2167 | -61.4044 | 0.10529 | -0.26093 | 0.23346 | 0.28839 | -0.21973 | -0.13733 | -0.32501 | -0.24262 | 0.013733 | -0.25177 | -0.050354 | 0.018311 | -0.23804 | -0.050354 | -0.25177 | -0.064087 | 0.1831 | 121.8018 | 0.004578 | 121.6095 | 121.3074 | 121.4081 | 121.4127 | 121.4218 | -121.5683 | -121.6599 | 121.907 | 121.6232 | 61.203 | 61.1572
2.2188 | 121.907 | -61.0977 | 60.5301 | 0.0019074 | 0 | 0.064108 | 0.063715 | 0.0017731 | -0.00078404 | -2.1434e-05 | -0.0028687 | 0.00076264 | -1.3942 | 0.060539 | -0.0011364 | 0.0022901 | -0.0032257 | 0.050354 | 60.2325 | -60.9924 | 60.8047 | -60.7819 | -61.1893 | -61.2991 | 0.050354 | 60.2417 | -61.0977 | 60.5209 | -61.0474 | -61.1114 | -61.3312 | 0.10529 | -0.29755 | 0.27466 | 0.31586 | -0.20142 | -0.091553 | -0.3067 | -0.19684 | 0 | -0.28839 | -0.009155 | 0.050354 | -0.23346 | -0.013733 | -0.23346 | -0.013733 | 0.21057 | 121.7972 | 0.050354 | 121.6187 | 121.225 | 121.3394 | 121.3303 | 121.3394 | -121.5225 | -121.6278 | 121.9025 | 121.6187 | 61.1481 | 61.1481
3.9844 | 121.9666 | -61.0794 | 60.4935 | -0.0057221 | 0 | 0.064963 | 0.063929 | 0.00091851 | -0.0020658 | -0.0017304 | -0.0028687 | -9.1956e-05 | -1.3942 | 0.065238 | -0.0013502 | 0.0059217 | 0.0025421 | 0.032043 | 60.1913 | -61.0062 | 60.8047 | -60.7727 | -61.1938 | -61.29 | 0.09613 | 60.2234 | -61.0977 | 60.5896 | -61.0062 | -61.0382 | -61.2717 | 0.073242 | -0.30212 | 0.31128 | 0.3067 | -0.21057 | -0.11444 | -0.28381 | -0.18768 | -0.01831 | -0.27008 | 0.096131 | 0.073242 | -0.19226 | 0.041199 | -0.17395 | 0.059509 | 0.23346 | 121.8109 | 0.091552 | 121.6873 | 121.1975 | 121.3211 | 121.2708 | 121.3028 | -121.4996 | -121.5912 | 121.8842 | 121.669 | 61.1115 | 61.1755
5.6719 | 121.9666 | -61.0748 | 60.5118 | 0.0019074 | 0 | 0.064963 | 0.062433 | -0.00014949 | -0.0022794 | -0.00087583 | 0.00018312 | 0.00076264 | -1.395 | 0.062461 | -0.0011364 | 0.0052807 | -0.00087591 | 0.045776 | 60.2051 | -60.9833 | 60.8505 | -60.7315 | -61.1618 | -61.2534 | 0.10071 | 60.2417 | -61.084 | 60.5759 | -61.0016 | -61.0611 | -61.2808 | 0.091553 | -0.3067 | 0.33874 | 0.34332 | -0.17853 | -0.086975 | -0.27008 | -0.17853 | -0.009155 | -0.27008 | 0.064087 | 0.073242 | -0.20599 | 0.013733 | -0.19684 | 0.022888 | 0.25177 | 121.8338 | 0.082397 | 121.6599 | 121.1884 | 121.3257 | 121.2799 | 121.3165 | -121.4951 | -121.5958 | 121.9254 | 121.6507 | 61.1206 | 61.1755
7.3438 | 121.8338 | -61.1114 | 60.5713 | 0.0019074 | 0 | 0.064108 | 0.064783 | -0.0020721 | -0.0022794 | -0.00023503 | 0.00018312 | 0.001617 | -1.3935 | 0.066306 | -0.0022046 | 0.0037855 | -0.00066231 | -0.013733 | 60.2875 | -61.0382 | 60.7086 | -60.9009 | -61.2808 | -61.377 | -0.050354 | 60.3104 | -61.1114 | 60.4477 | -61.1252 | -61.2122 | -61.3998 | 0.073242 | -0.28381 | 0.13733 | 0.21057 | -0.2655 | -0.16937 | -0.33875 | -0.24262 | 0 | -0.26093 | -0.1236 | -0.013733 | -0.28839 | -0.10071 | -0.28839 | -0.10071 | 0.13733 | 121.7468 | -0.013733 | 121.5591 | 121.3257 | 121.4218 | 121.3989 | 121.4218 | -121.6095 | -121.6827 | 121.8201 | 121.5591 | 61.0977 | 61.0611
9.0312 | 121.8018 | -61.1664 | 60.5072 | 0.0019074 | 0 | 0.066245 | 0.066065 | -0.00079049 | -0.00057044 | -0.0023712 | -0.0028687 | 0.002258 | -1.3937 | 0.057548 | -0.00070919 | 0.0050671 | -0.00023491 | -0.059509 | 60.2097 | -61.0657 | 60.6537 | -60.9695 | -61.3998 | -61.4868 | -0.15564 | 60.2463 | -61.1801 | 60.3745 | -61.2396 | -61.3037 | -61.4594 | 0.10071 | -0.29755 | 0.14648 | 0.19684 | -0.32043 | -0.23346 | -0.42114 | -0.33417 | -0.013733 | -0.26093 | -0.13275 | -0.073242 | -0.29297 | -0.13733 | -0.27924 | -0.1236 | 0.096131 | 121.7194 | -0.059509 | 121.5546 | 121.2753 | 121.4264 | 121.376 | 121.4127 | -121.5729 | -121.6873 | 121.8201 | 121.5408 | 61.1069 | 61.0107
10.7188 | 121.9162 | -61.1343 | 60.4202 | 0.055313 | 0 | 0.06774 | 0.067774 | 0.0013459 | -0.00099764 | 0.0023286 | 0.015442 | 0.0020444 | -1.3937 | 0.07122 | -0.00049559 | 0.0046399 | -0.00087591 | 0.004578 | 60.2325 | -61.0519 | 60.7773 | -60.8047 | -61.2625 | -61.3586 | 0.041199 | 60.2051 | -61.171 | 60.5164 | -61.1023 | -61.1801 | -61.3632 | 0.082397 | -0.18768 | 0.35706 | 0.32959 | -0.22431 | -0.12817 | -0.3067 | -0.21057 | -0.036621 | -0.21515 | 0.09613 | 0.032043 | -0.22888 | -0.045777 | -0.19226 | -0.009156 | 0.24719 | 121.8292 | 0.068664 | 121.6873 | 121.2845 | 121.376 | 121.3669 | 121.3394 | -121.4722 | -121.5912 | 121.9116 | 121.6507 | 61.1389 | 61.1755
12.4531 | 121.9299 | -61.1664 | 60.4248 | -0.0057221 | 0 | 0.067526 | 0.06457 | 0.00027771 | -0.0016384 | -0.00023503 | -0.0059205 | -0.0013736 | -1.3959 | 0.065879 | 0.001427 | 0.0069897 | -2.1314e-05 | -0.027466 | 60.1685 | -61.084 | 60.7361 | -60.8688 | -61.2991 | -61.3724 | -0.004578 | 60.1685 | -61.1664 | 60.5072 | -61.1114 | -61.171 | -61.3541 | 0.082398 | -0.25635 | 0.31128 | 0.29755 | -0.20599 | -0.13275 | -0.28839 | -0.21515 | 0 | -0.25635 | 0.082397 | 0.054932 | -0.18768 | -0.004577 | -0.18768 | -0.004577 | 0.21515 | 121.8201 | 0.054932 | 121.6736 | 121.2524 | 121.3348 | 121.3348 | 121.3348 | -121.5088 | -121.5912 | 121.9025 | 121.6736 | 61.1389 | 61.1618
14.1406 | 121.9482 | -61.1206 | 60.4477 | 0.017166 | 0 | 0.069235 | 0.064142 | -0.00079049 | -0.00035684 | -0.001944 | 0.021545 | 0.0031124 | -1.3925 | 0.065879 | 0.00078621 | 0.0080579 | 0.00019229 | -0.009155 | 60.1913 | -61.0291 | 60.7452 | -60.8414 | -61.2991 | -61.3495 | 0.041199 | 60.1959 | -61.1801 | 60.5255 | -61.0977 | -61.1664 | -61.3358 | 0.091552 | -0.25635 | 0.29755 | 0.27923 | -0.22888 | -0.17853 | -0.32043 | -0.27008 | -0.05951 | -0.25177 | 0.07782 | 0.022888 | -0.21515 | -0.045777 | -0.15564 | 0.013733 | 0.18768 | 121.7743 | 0.082398 | 121.7056 | 121.2204 | 121.376 | 121.3119 | 121.3165 | -121.4767 | -121.6278 | 121.8658 | 121.6461 | 61.1114 | 61.1618
15.8125 | 121.8018 | -61.116 | 60.5576 | -0.0057221 | 0 | 0.065817 | 0.065638 | -0.0029267 | -0.0016384 | -0.003012 | 0.00018312 | 0.00097624 | -1.3918 | 0.062248 | -0.0045544 | 0.0027173 | -0.00044851 | 0.004578 | 60.2463 | -61.0062 | 60.7315 | -60.8734 | -61.2717 | -61.3632 | -0.059509 | 60.3012 | -61.1114 | 60.4431 | -61.1435 | -61.1847 | -61.3861 | 0.10986 | -0.31128 | 0.17395 | 0.24262 | -0.24719 | -0.15564 | -0.35705 | -0.2655 | 0.004578 | -0.25635 | -0.11444 | -0.027466 | -0.27008 | -0.068664 | -0.27466 | -0.073242 | 0.13275 | 121.7377 | -0.032044 | 121.5546 | 121.2524 | 121.4127 | 121.3623 | 121.4172 | -121.5637 | -121.669 | 121.8475 | 121.5591 | 61.1206 | 61.0565
17.4844 | 121.8887 | -61.1389 | 60.4797 | 0.024795 | 0 | 0.068808 | 0.064356 | -0.0029267 | -0.00035684 | 0.00083317 | 0.00018312 | 0.002258 | -1.3927 | 0.068229 | -0.00049559 | 0.0050671 | -0.0025849 | -0.032043 | 60.2371 | -61.0336 | 60.7269 | -60.8505 | -61.2717 | -61.3541 | -0.022888 | 60.2188 | -61.1435 | 60.4843 | -61.1206 | -61.171 | -61.3632 | 0.10529 | -0.24261 | 0.24719 | 0.28839 | -0.21515 | -0.13275 | -0.32043 | -0.23804 | -0.004578 | -0.26093 | 0.004578 | 0.018311 | -0.2243 | -0.032043 | -0.21973 | -0.027465 | 0.18311 | 121.7606 | 0.022889 | 121.6278 | 121.2708 | 121.3623 | 121.376 | 121.3577 | -121.5134 | -121.6232 | 121.8658 | 121.6232 | 61.1069 | 61.116
19.1719 | 121.9254 | -61.0886 | 60.5164 | -0.0057221 | 0 | 0.067313 | 0.06222 | 0.0011321 | -0.00099764 | -0.00087583 | 0.00018312 | 0.00054904 | -1.395 | 0.069938 | -0.0045544 | 0.0029309 | -0.0015167 | 0.054932 | 60.2188 | -60.9833 | 60.8185 | -60.7544 | -61.1893 | -61.2854 | 0.073242 | 60.26 | -61.084 | 60.5484 | -61.0153 | -61.0977 | -61.2991 | 0.10529 | -0.29755 | 0.30212 | 0.33417 | -0.19684 | -0.10071 | -0.30212 | -0.20599 | 0.004578 | -0.25635 | 0.032044 | 0.073242 | -0.21057 | -0.009155 | -0.21515 | -0.013733 | 0.22888 | 121.8018 | 0.068664 | 121.6324 | 121.2021 | 121.344 | 121.3074 | 121.3486 | -121.4996 | -121.6003 | 121.907 | 121.637 | 61.1435 | 61.1618
20.9219 | 121.9025 | -61.1481 | 60.4706 | 0.0095369 | 0 | 0.065176 | 0.066279 | -0.0042083 | 7.0564e-05 | 0.00083317 | 0.00018312 | 0.00033544 | -1.395 | 0.069084 | -0.00092279 | 0.0042127 | 0.00083309 | -0.027466 | 60.2005 | -61.0474 | 60.7269 | -60.8643 | -61.2762 | -61.377 | -0.032043 | 60.228 | -61.116 | 60.5026 | -61.0886 | -61.1481 | -61.3403 | 0.10071 | -0.27008 | 0.25635 | 0.28381 | -0.22888 | -0.12817 | -0.32959 | -0.22888 | 0.032043 | -0.24262 | 0.032044 | 0.059509 | -0.19226 | 0 | -0.2243 | -0.032043 | 0.1831 | 121.7743 | 0.027466 | 121.6187 | 121.2479 | 121.344 | 121.3486 | 121.376 | -121.5179 | -121.5866 | 121.875 | 121.6507 | 61.1206 | 61.116
22.6094 | 121.8842 | -61.1298 | 60.4385 | 0.047683 | 0 | 0.066885 | 0.06457 | 0.0045501 | 0.0017796 | 0.00083317 | 0.01239 | 0.0020444 | -1.3916 | 0.067802 | -0.00070919 | 0.0039991 | -0.0023713 | -0.009155 | 60.2097 | -61.0748 | 60.7636 | -60.8047 | -61.2671 | -61.3449 | 0.022888 | 60.2051 | -61.1938 | 60.4935 | -61.116 | -61.171 | -61.3724 | 0.054932 | -0.22888 | 0.32501 | 0.32501 | -0.21515 | -0.13733 | -0.27008 | -0.19226 | -0.064087 | -0.23346 | 0.054931 | 0.013733 | -0.24261 | -0.041198 | -0.17853 | 0.022889 | 0.27008 | 121.8384 | 0.07782 | 121.6873 | 121.2845 | 121.3989 | 121.3394 | 121.3348 | -121.5134 | -121.6324 | 121.8933 | 121.6232 | 61.1206 | 61.1526
24.3594 | 121.8613 | -61.0886 | 60.5392 | -0.0057221 | 0 | 0.064749 | 0.065424 | 0.0019867 | -0.00014304 | -0.0010894 | -0.0028687 | 0.00054904 | -1.392 | 0.064811 | -0.0039136 | 0.0037855 | -0.00066231 | 0.059509 | 60.2325 | -60.9924 | 60.8002 | -60.791 | -61.2076 | -61.3083 | 0.022888 | 60.2966 | -61.116 | 60.4935 | -61.0931 | -61.1572 | -61.3632 | 0.09613 | -0.3067 | 0.26093 | 0.29755 | -0.21973 | -0.11902 | -0.31586 | -0.21515 | -0.027466 | -0.24262 | -0.045777 | -0.004578 | -0.27466 | -0.068665 | -0.24719 | -0.041199 | 0.20142 | 121.7926 | 0.022888 | 121.6095 | 121.225 | 121.4127 | 121.3211 | 121.3852 | -121.5317 | -121.6553 | 121.8887 | 121.582 | 61.1481 | 61.1115
26.0312 | 121.9391 | -61.1435 | 60.4294 | 0.017166 | 0 | 0.066672 | 0.064997 | 0.0039093 | -0.00035684 | -0.004721 | 0.00018312 | 0.00033544 | -1.392 | 0.07122 | -0.00092279 | 0.0044263 | -0.0021575 | -0.027466 | 60.1776 | -61.0565 | 60.7315 | -60.8643 | -61.2946 | -61.3678 | 0 | 60.1593 | -61.1389 | 60.498 | -61.116 | -61.1801 | -61.3541 | 0.086975 | -0.25177 | 0.30212 | 0.27924 | -0.2243 | -0.15106 | -0.31128 | -0.23804 | 0.004578 | -0.27008 | 0.068665 | 0.027466 | -0.21057 | -0.036621 | -0.21515 | -0.041199 | 0.19226 | 121.788 | 0.022888 | 121.637 | 121.2341 | 121.2982 | 121.3211 | 121.3028 | -121.4859 | -121.5683 | 121.875 | 121.6415 | 61.116 | 61.1435
27.7188 | 121.9116 | -61.1252 | 60.4706 | 0.0095369 | 0 | 0.064963 | 0.063929 | -0.0010041 | -0.00078404 | -0.003012 | 0.0032349 | 0.00054904 | -1.3937 | 0.073783 | -0.0015638 | 0.0057081 | -0.00066231 | -0.041199 | 60.228 | -61.0153 | 60.7315 | -60.8551 | -61.29 | -61.3678 | -0.041199 | 60.26 | -61.1343 | 60.498 | -61.0886 | -61.1389 | -61.3449 | 0.10986 | -0.24262 | 0.26093 | 0.27008 | -0.24262 | -0.16479 | -0.35248 | -0.27466 | -0.009155 | -0.21057 | 0.027466 | 0.036621 | -0.21973 | -0.013733 | -0.21057 | -0.004578 | 0.16022 | 121.7468 | 0.045776 | 121.6324 | 121.2433 | 121.3943 | 121.3531 | 121.3852 | -121.4859 | -121.6049 | 121.8567 | 121.6232 | 61.084 | 61.084
29.4688 | 121.8475 | -61.116 | 60.5118 | 0.040054 | 0 | 0.065817 | 0.066065 | 0.0011321 | 0.00049776 | -0.00044863 | 0.018494 | 0.0046078 | -1.3903 | 0.062461 | -0.0039136 | 0.0042127 | 0.0019013 | 0.013733 | 60.3058 | -61.0657 | 60.7361 | -60.8734 | -61.2579 | -61.3449 | -0.036621 | 60.3195 | -61.1526 | 60.4568 | -61.1114 | -61.1847 | -61.3632 | 0.050354 | -0.20599 | 0.2243 | 0.24262 | -0.22888 | -0.14191 | -0.27924 | -0.19226 | -0.036621 | -0.19226 | -0.054932 | 0.004578 | -0.24719 | -0.068664 | -0.21057 | -0.032043 | 0.19226 | 121.8018 | 0.041199 | 121.6095 | 121.3715 | 121.4722 | 121.4218 | 121.4355 | -121.5775 | -121.6644 | 121.8521 | 121.5729 | 61.1298 | 61.0794
31.1562 | 121.9482 | -61.1389 | 60.3836 | 0.0019074 | 0 | 0.067954 | 0.063929 | 0.0034821 | 0.00028416 | -0.00023503 | -0.0059205 | 0.00097624 | -1.3933 | 0.075279 | 0.00014521 | 0.0052807 | -0.00023491 | -0.045776 | 60.1685 | -61.0382 | 60.7269 | -60.8643 | -61.2854 | -61.377 | -0.032043 | 60.173 | -61.1664 | 60.498 | -61.1114 | -61.171 | -61.3724 | 0.10071 | -0.21515 | 0.34332 | 0.27466 | -0.23804 | -0.14648 | -0.33875 | -0.24719 | -0.027466 | -0.21057 | 0.11444 | 0.027466 | -0.23346 | -0.032043 | -0.20599 | -0.004577 | 0.17395 | 121.7651 | 0.054932 | 121.6644 | 121.2067 | 121.3394 | 121.3074 | 121.312 | -121.4218 | -121.55 | 121.8658 | 121.637 | 61.0931 | 61.1069
32.8438 | 121.788 | -61.1664 | 60.4843 | 0.0095369 | 0 | 0.064963 | 0.065211 | -0.0039947 | 0.00049776 | 0.001474 | 0.0032349 | 0.00097624 | -1.394 | 0.056907 | -0.0015638 | 0.0044263 | 0.0033967 | -0.054932 | 60.2234 | -61.0519 | 60.6308 | -60.9833 | -61.4044 | -61.4639 | -0.15106 | 60.2554 | -61.1755 | 60.3882 | -61.2213 | -61.3037 | -61.4639 | 0.11444 | -0.26093 | 0.14648 | 0.18311 | -0.29755 | -0.23804 | -0.41199 | -0.35248 | -0.009155 | -0.22888 | -0.09613 | -0.054931 | -0.29755 | -0.13733 | -0.28839 | -0.12817 | 0.068665 | 121.6827 | -0.045776 | 121.5637 | 121.2753 | 121.431 | 121.3898 | 121.4218 | -121.5363 | -121.6599 | 121.7972 | 121.5546 | 61.1114 | 61.0153
34.5312 | 121.788 | -61.1664 | 60.4752 | -0.0057221 | 0 | 0.064963 | 0.06756 | 0.0022003 | -0.0016384 | 0.00083317 | -0.0028687 | 0.0011898 | -1.394 | 0.064597 | -0.0022046 | 0.00079467 | -0.0030121 | -0.059509 | 60.2097 | -61.0565 | 60.6354 | -60.9558 | -61.3907 | -61.4639 | -0.14191 | 60.2325 | -61.1755 | 60.3836 | -61.2259 | -61.29 | -61.4456 | 0.10986 | -0.2655 | 0.16022 | 0.21057 | -0.29755 | -0.2243 | -0.40741 | -0.33417 | -0.009155 | -0.24262 | -0.091553 | -0.059509 | -0.27924 | -0.1236 | -0.27008 | -0.11444 | 0.10071 | 121.6919 | -0.050354 | 121.5591 | 121.2662 | 121.4081 | 121.376 | 121.3989 | -121.5317 | -121.6507 | 121.8018 | 121.55 | 61.1069 | 61.0245
36.2188 | 121.7789 | -61.1114 | 60.5759 | 0.0019074 | 0 | 0.064963 | 0.066279 | -0.0010041 | -0.0050564 | -2.1434e-05 | 0.00018312 | -0.00094636 | -1.3929 | 0.06182 | -0.005409 | 0.0027173 | 0.00040589 | 0.004578 | 60.2692 | -61.0107 | 60.7269 | -60.8643 | -61.2717 | -61.3724 | -0.036621 | 60.2692 | -61.0977 | 60.434 | -61.1252 | -61.1847 | -61.3815 | 0.10071 | -0.3067 | 0.15106 | 0.24719 | -0.26093 | -0.16022 | -0.36163 | -0.26093 | 0.013733 | -0.3067 | -0.14191 | -0.013733 | -0.27008 | -0.073242 | -0.28381 | -0.086975 | 0.14648 | 121.7377 | -0.027466 | 121.5317 | 121.2799 | 121.3669 | 121.3806 | 121.3806 | -121.5866 | -121.6736 | 121.8384 | 121.5454 | 61.116 | 61.0748
37.9844 | 121.8613 | -61.1114 | 60.4889 | 0.024795 | 0 | 0.066672 | 0.066492 | 0.0036957 | -0.00078404 | 0.00040597 | 0.0032349 | 0.003967 | -1.3944 | 0.068656 | -0.0017774 | 0.0033581 | -0.00087591 | 0.041199 | 60.2692 | -61.0336 | 60.7086 | -60.8414 | -61.2579 | -61.3586 | 0.004578 | 60.2463 | -61.1435 | 60.466 | -61.1114 | -61.1984 | -61.3632 | 0.07782 | -0.21973 | 0.21973 | 0.27008 | -0.24719 | -0.14649 | -0.32501 | -0.22431 | -0.032044 | -0.24262 | -0.022889 | 0 | -0.25177 | -0.086975 | -0.21973 | -0.054931 | 0.19226 | 121.7422 | 0.032044 | 121.6095 | 121.3028 | 121.3898 | 121.3806 | 121.3577 | -121.5225 | -121.6324 | 121.8201 | 121.5775 | 61.1526 | 61.116
39.7344 | 121.9299 | -61.0886 | 60.5072 | 0.0019074 | 0 | 0.063254 | 0.062647 | -0.00057689 | -0.00014304 | -0.0023712 | -0.0059205 | -9.1956e-05 | -1.3937 | 0.065879 | -0.00028199 | 0.0037855 | 0.0014741 | 0.036621 | 60.2371 | -60.9833 | 60.8368 | -60.7178 | -61.1572 | -61.2625 | 0.07782 | 60.2371 | -61.0977 | 60.5667 | -60.9787 | -61.0565 | -61.2854 | 0.10529 | -0.27008 | 0.32959 | 0.37079 | -0.17395 | -0.068665 | -0.27924 | -0.17395 | -0.009155 | -0.27008 | 0.059509 | 0.10986 | -0.19684 | 0.032043 | -0.18768 | 0.041198 | 0.2655 | 121.8201 | 0.11902 | 121.6644 | 121.2204 | 121.3348 | 121.3257 | 121.3257 | -121.4905 | -121.6049 | 121.9254 | 121.6553 | 61.1252 | 61.1664
41.4062 | 121.843 | -61.1343 | 60.4935 | 0.017166 | 0 | 0.063467 | 0.065424 | 0.0026275 | -0.00014304 | 0.002115 | 0.0062865 | 0.001617 | -1.3925 | 0.063529 | 0.00099981 | 0.0044263 | -0.0047211 | 0.022888 | 60.2325 | -61.0748 | 60.7269 | -60.8597 | -61.29 | -61.3861 | -0.022888 | 60.2646 | -61.1435 | 60.434 | -61.1435 | -61.2259 | -61.3953 | 0.059509 | -0.26093 | 0.23346 | 0.27466 | -0.25177 | -0.15564 | -0.31128 | -0.21515 | -0.009156 | -0.22888 | -0.059509 | -0.009156 | -0.26093 | -0.091553 | -0.25177 | -0.082397 | 0.21515 | 121.8018 | 0 | 121.5775 | 121.3074 | 121.4081 | 121.3669 | 121.3989 | -121.5683 | -121.637 | 121.8613 | 121.5683 | 61.1572 | 61.1114
43.1719 | 121.9482 | -61.0474 | 60.498 | 0.0019074 | 0 | 0.062186 | 0.061793 | -0.00057689 | -0.001852 | 0.0016876 | 0.0032349 | -0.0015872 | -1.3927 | 0.065666 | -0.0011364 | 0.0054945 | -0.00023491 | 0.032043 | 60.2142 | -60.9787 | 60.8093 | -60.7315 | -61.171 | -61.2488 | 0.10071 | 60.2188 | -61.0657 | 60.5484 | -60.997 | -61.0474 | -61.2854 | 0.068664 | -0.28381 | 0.31128 | 0.31586 | -0.20142 | -0.1236 | -0.27008 | -0.19226 | -0.018311 | -0.27924 | 0.050354 | 0.050354 | -0.23804 | 0 | -0.21973 | 0.018311 | 0.24719 | 121.788 | 0.068665 | 121.6141 | 121.1929 | 121.2845 | 121.2616 | 121.2662 | -121.4767 | -121.5637 | 121.8567 | 121.5958 | 61.0794 | 61.1481
44.9375 | 121.843 | -61.1343 | 60.4889 | 0.024795 | 0 | 0.065604 | 0.066065 | -0.00079049 | 0.00028416 | -2.1434e-05 | 0.00018312 | 0.0018306 | -1.395 | 0.064597 | -0.0024182 | 0.0046399 | -2.1314e-05 | 0.032043 | 60.26 | -61.0382 | 60.7361 | -60.8505 | -61.2808 | -61.3632 | 0 | 60.26 | -61.1343 | 60.4568 | -61.116 | -61.1984 | -61.3724 | 0.09613 | -0.22888 | 0.24719 | 0.28381 | -0.22888 | -0.14648 | -0.32501 | -0.24262 | 0 | -0.22888 | -0.032044 | 0.01831 | -0.23804 | -0.064087 | -0.23804 | -0.064087 | 0.18768 | 121.7743 | 0.01831 | 121.5912 | 121.2982 | 121.3943 | 121.3943 | 121.3943 | -121.5271 | -121.6232 | 121.8704 | 121.5912 | 61.1664 | 61.1343
46.625 | 121.8109 | -61.1389 | 60.4706 | 0.0095369 | 0 | 0.064963 | 0.06457 | 0.0017731 | -0.0016384 | -0.00023503 | 0.0032349 | 0.0014034 | -1.3942 | 0.068229 | -0.00092279 | 0.0054945 | -0.0019439 | 0.009155 | 60.2509 | -61.0336 | 60.6903 | -60.8826 | -61.3174 | -61.3953 | -0.036621 | 60.2371 | -61.1572 | 60.4156 | -61.171 | -61.2442 | -61.4136 | 0.10529 | -0.21973 | 0.21973 | 0.25635 | -0.25635 | -0.17853 | -0.36163 | -0.28381 | -0.018311 | -0.23346 | -0.054932 | -0.032043 | -0.27466 | -0.10529 | -0.25635 | -0.086975 | 0.15106 | 121.7239 | -0.013732 | 121.5729 | 121.2845 | 121.3943 | 121.3898 | 121.376 | -121.5042 | -121.6278 | 121.8292 | 121.5546 | 61.1481 | 61.1023
48.3594 | 121.9254 | -61.084 | 60.5026 | 0.0019074 | 0 | 0.066458 | 0.063715 | -0.0035675 | -0.00057044 | 0.0012604 | -0.0028687 | -0.00094636 | -1.395 | 0.060111 | -0.0017774 | 0.0052807 | -0.00044851 | 0.050354 | 60.2234 | -60.9695 | 60.8322 | -60.7269 | -61.1664 | -61.2671 | 0.07782 | 60.26 | -61.0703 | 60.5484 | -60.9833 | -61.0611 | -61.2854 | 0.11444 | -0.27924 | 0.32959 | 0.35706 | -0.18311 | -0.082398 | -0.29755 | -0.19684 | 0.013733 | -0.24262 | 0.045776 | 0.10071 | -0.20142 | 0.022888 | -0.21515 | 0.009155 | 0.24261 | 121.8018 | 0.086975 | 121.6187 | 121.1929 | 121.3303 | 121.3074 | 121.344 | -121.4722 | -121.5729 | 121.9162 | 121.6324 | 61.1343 | 61.1618
50.0625 | 121.7697 | -61.1664 | 60.4843 | 0.0019074 | 0 | 0.065176 | 0.067774 | 0.0015595 | 0.00092496 | -2.1434e-05 | -0.0028687 | 0.001617 | -1.3918 | 0.065879 | -0.0022046 | 0.0057081 | 0.0029693 | -0.064087 | 60.2371 | -61.0657 | 60.6216 | -60.9787 | -61.3861 | -61.4822 | -0.17853 | 60.2142 | -61.1755 | 60.3607 | -61.2625 | -61.2808 | -61.4594 | 0.10071 | -0.24719 | 0.13733 | 0.18768 | -0.31586 | -0.21973 | -0.41656 | -0.32043 | -0.009155 | -0.27008 | -0.1236 | -0.09613 | -0.29297 | -0.11444 | -0.28381 | -0.10529 | 0.086975 | 121.6873 | -0.086975 | 121.5363 | 121.3028 | 121.3898 | 121.4035 | 121.3806 | -121.55 | -121.6599 | 121.788 | 121.5271 | 61.1023 | 60.9879
51.7969 | 121.8796 | -61.1343 | 60.4385 | 0.032425 | 0 | 0.068594 | 0.064142 | -0.0014313 | 0.00092496 | -0.00023503 | 0.01239 | 0.00097624 | -1.3935 | 0.068015 | -0.00028199 | 0.0065625 | 0.0029693 | -0.032043 | 60.228 | -61.0428 | 60.7407 | -60.8368 | -61.2488 | -61.3358 | -0.018311 | 60.2051 | -61.1572 | 60.4752 | -61.116 | -61.1618 | -61.3632 | 0.091552 | -0.21057 | 0.30212 | 0.29755 | -0.20142 | -0.11444 | -0.29297 | -0.20599 | -0.022889 | -0.23346 | 0.036621 | 0.01831 | -0.22888 | -0.027466 | -0.20599 | -0.004577 | 0.20599 | 121.7834 | 0.041199 | 121.6324 | 121.2708 | 121.3623 | 121.3623 | 121.3394 | -121.4813 | -121.5958 | 121.875 | 121.6095 | 61.1023 | 61.116
53.4688 | 121.8063 | -61.1755 | 60.4752 | 0.0019074 | 0 | 0.063895 | 0.067133 | -0.00014949 | 0.00028416 | -2.1434e-05 | 0.00018312 | 0.0024716 | -1.3942 | 0.063957 | -0.00049559 | 0.0057081 | 0.0029693 | -0.07782 | 60.2234 | -61.0931 | 60.6079 | -60.997 | -61.4044 | -61.4639 | -0.15106 | 60.2142 | -61.1801 | 60.379 | -61.2259 | -61.29 | -61.4273 | 0.082397 | -0.25177 | 0.13275 | 0.17853 | -0.28839 | -0.22888 | -0.37079 | -0.31128 | -0.004578 | -0.26093 | -0.096131 | -0.050354 | -0.25177 | -0.11444 | -0.24719 | -0.10986 | 0.096131 | 121.701 | -0.045776 | 121.5591 | 121.3165 | 121.3943 | 121.3989 | 121.3898 | -121.5683 | -121.6553 | 121.7834 | 121.5546 | 61.0977 | 61.0245
55.25 | 121.9162 | -61.1069 | 60.4752 | 0.0095369 | 0 | 0.065176 | 0.063929 | -0.0016449 | -0.00057044 | -0.00087583 | 0.0032349 | 0.00033544 | -1.3942 | 0.066093 | -0.0015638 | 0.0061353 | 0.0042511 | -0.036621 | 60.1868 | -61.0382 | 60.7178 | -60.8505 | -61.2534 | -61.3403 | -0.018311 | 60.2188 | -61.1298 | 60.4935 | -61.0611 | -61.1023 | -61.3312 | 0.068665 | -0.28839 | 0.24261 | 0.25635 | -0.23346 | -0.14648 | -0.30212 | -0.21515 | -0.022888 | -0.25635 | 0.01831 | 0.045777 | -0.2243 | 0.004578 | -0.20142 | 0.027466 | 0.18768 | 121.756 | 0.068665 | 121.6232 | 121.225 | 121.3486 | 121.2936 | 121.3257 | -121.5134 | -121.6049 | 121.8246 | 121.6003 | 61.0703 | 61.0886
57 | 121.9162 | -61.1618 | 60.4156 | 0.0019074 | 0 | 0.064749 | 0.065211 | -0.0010041 | -0.0014248 | 0.00019217 | -0.0028687 | 0.00012184 | -1.3935 | 0.064811 | 0.00078621 | 0.0057081 | 0.00019229 | -0.059509 | 60.173 | -61.0519 | 60.6766 | -60.8871 | -61.322 | -61.3861 | -0.027466 | 60.1822 | -61.171 | 60.4889 | -61.1023 | -61.1847 | -61.3449 | 0.10986 | -0.24261 | 0.26093 | 0.27466 | -0.2243 | -0.16022 | -0.33417 | -0.27008 | -0.009155 | -0.23346 | 0.073243 | 0.059509 | -0.18311 | -0.022888 | -0.17395 | -0.013733 | 0.16479 | 121.7285 | 0.068664 | 121.6599 | 121.225 | 121.3531 | 121.3348 | 121.344 | -121.4676 | -121.5866 | 121.8384 | 121.6507 | 61.1023 | 61.1343
58.6875 | 121.8887 | -61.1389 | 60.4156 | 0.0019074 | 0 | 0.065604 | 0.064783 | 6.4114e-05 | -0.0029202 | 0.00040597 | -0.0028687 | 0.001617 | -1.3922 | 0.064597 | -0.00049559 | 0.0046399 | -0.00066231 | -0.086975 | 60.2005 | -61.084 | 60.6583 | -60.9146 | -61.3632 | -61.4273 | -0.054932 | 60.1959 | -61.1572 | 60.466 | -61.1298 | -61.1893 | -61.3632 | 0.054932 | -0.21515 | 0.24262 | 0.2243 | -0.28839 | -0.2243 | -0.34332 | -0.27924 | -0.018311 | -0.21973 | 0.050354 | 0.009155 | -0.2243 | -0.050354 | -0.20599 | -0.032043 | 0.16937 | 121.7422 | 0.027466 | 121.6232 | 121.2845 | 121.3531 | 121.3394 | 121.3348 | -121.4996 | -121.5729 | 121.7972 | 121.6049 | 61.0519 | 61.084
60.4375 | 121.8292 | -61.0931 | 60.5347 | 0.0019074 | 0 | 0.067313 | 0.064142 | 0.00027771 | -0.0022794 | 0.0012604 | -0.0028687 | -0.00030556 | -1.3918 | 0.066947 | -0.0015638 | 0.0035719 | 0.0012603 | 0.041199 | 60.2097 | -60.9695 | 60.7864 | -60.7773 | -61.1893 | -61.2946 | 0.027466 | 60.2783 | -61.0748 | 60.4843 | -61.0748 | -61.1435 | -61.3358 | 0.1236 | -0.32501 | 0.25177 | 0.31586 | -0.20142 | -0.09613 | -0.32501 | -0.21973 | 0.018311 | -0.25635 | -0.050354 | 0.018311 | -0.24261 | -0.050354 | -0.26093 | -0.068665 | 0.19226 | 121.756 | 0 | 121.5591 | 121.1792 | 121.3531 | 121.3028 | 121.3715 | -121.5042 | -121.6095 | 121.8796 | 121.5775 | 61.1343 | 61.1206
62.1875 | 121.9208 | -61.0657 | 60.4706 | 0.0019074 | 0 | 0.063681 | 0.063502 | -0.0044221 | -0.00035684 | 0.00061957 | -0.0089723 | -0.00094636 | -1.394 | 0.070793 | -0.001991 | 0.0027173 | -0.0021575 | 0.004578 | 60.228 | -60.9879 | 60.7819 | -60.7636 | -61.1893 | -61.2671 | 0.073242 | 60.228 | -61.0886 | 60.5576 | -60.9741 | -61.0565 | -61.2762 | 0.07782 | -0.24262 | 0.31128 | 0.30212 | -0.20142 | -0.1236 | -0.27924 | -0.20142 | -0.022888 | -0.24262 | 0.086975 | 0.091553 | -0.21057 | 0.009155 | -0.18768 | 0.032043 | 0.2243 | 121.7697 | 0.11444 | 121.6461 | 121.2158 | 121.3165 | 121.2936 | 121.2936 | -121.4584 | -121.5591 | 121.8475 | 121.6232 | 61.0703 | 61.1389
63.875 | 121.9208 | -61.1481 | 60.3928 | 0.0095369 | 0 | 0.064749 | 0.064783 | 0.0026275 | -0.00099764 | 0.0027558 | -0.0028687 | -9.1956e-05 | -1.3946 | 0.069511 | 0.0029224 | 0.0059217 | -0.0017303 | -0.032043 | 60.1501 | -61.0565 | 60.7224 | -60.8414 | -61.29 | -61.377 | 0 | 60.1639 | -61.1572 | 60.4843 | -61.0886 | -61.1435 | -61.3312 | 0.091552 | -0.24262 | 0.32959 | 0.3067 | -0.22888 | -0.14191 | -0.32043 | -0.23346 | -0.009156 | -0.22888 | 0.091553 | 0.059509 | -0.18311 | 0.004577 | -0.17395 | 0.013733 | 0.21515 | 121.7789 | 0.068665 | 121.6415 | 121.2067 | 121.3211 | 121.2982 | 121.3119 | -121.4493 | -121.55 | 121.8704 | 121.6324 | 61.116 | 61.1481
65.5625 | 121.8979 | -61.1572 | 60.4156 | 0.0019074 | 0 | 0.06539 | 0.066065 | -0.00057689 | 7.0564e-05 | -0.00066223 | -0.0028687 | -9.1956e-05 | -1.394 | 0.065666 | -0.00028199 | 0.0065625 | -0.0030121 | -0.050354 | 60.1776 | -61.0611 | 60.7086 | -60.8643 | -61.2991 | -61.3861 | -0.018311 | 60.173 | -61.1252 | 60.4752 | -61.0886 | -61.1755 | -61.3266 | 0.096131 | -0.23804 | 0.29297 | 0.29297 | -0.22888 | -0.14191 | -0.32501 | -0.23804 | 0.032044 | -0.24261 | 0.05951 | 0.068665 | -0.16937 | -0.01831 | -0.20142 | -0.050354 | 0.19684 | 121.7697 | 0.036621 | 121.6003 | 121.2387 | 121.2982 | 121.3348 | 121.3303 | -121.4767 | -121.5408 | 121.8658 | 121.6324 | 61.1069 | 61.1389
67.2344 | 121.9254 | -61.0703 | 60.4706 | -0.0057221 | 0 | 0.066885 | 0.06222 | -0.0059173 | -0.0031338 | -0.0017304 | -0.0028687 | -0.0013736 | -1.3955 | 0.069724 | -0.0024182 | 0.0069897 | 0.0012603 | 0.004578 | 60.2417 | -61.0062 | 60.7819 | -60.7636 | -61.1801 | -61.2762 | 0.068665 | 60.2097 | -61.084 | 60.553 | -60.997 | -61.0611 | -61.2717 | 0.064086 | -0.22888 | 0.31128 | 0.3067 | -0.20599 | -0.10986 | -0.27008 | -0.17395 | -0.013733 | -0.26093 | 0.082398 | 0.073242 | -0.20142 | 0.009155 | -0.18768 | 0.022888 | 0.24262 | 121.788 | 0.086975 | 121.637 | 121.2479 | 121.2936 | 121.3119 | 121.2799 | -121.4767 | -121.5546 | 121.8521 | 121.6232 | 61.0748 | 61.1389
68.9219 | 121.9299 | -61.0703 | 60.4752 | -0.013352 | 0 | 0.063467 | 0.063715 | 0.00027771 | -0.003561 | -0.0021576 | -0.0028687 | 0.00097624 | -1.3925 | 0.068015 | -0.0022046 | 0.0042127 | -0.0017303 | 0.004578 | 60.2188 | -60.9695 | 60.7956 | -60.7361 | -61.171 | -61.2488 | 0.10071 | 60.2325 | -61.0977 | 60.5576 | -60.9787 | -61.0245 | -61.2625 | 0.10071 | -0.25635 | 0.32043 | 0.33417 | -0.17853 | -0.10071 | -0.27924 | -0.20142 | -0.027466 | -0.24262 | 0.082397 | 0.091552 | -0.19226 | 0.045776 | -0.16479 | 0.073242 | 0.23346 | 121.7651 | 0.11902 | 121.6553 | 121.1884 | 121.3303 | 121.2891 | 121.3028 | -121.4447 | -121.5729 | 121.8658 | 121.6278 | 61.0748 | 61.171
70.6719 | 121.9116 | -61.0519 | 60.4843 | -0.013352 | 0 | 0.063681 | 0.064997 | 0.0022003 | -0.0012112 | -0.001944 | -0.0028687 | 0.00054904 | -1.3944 | 0.063957 | -0.0043408 | 0.0031445 | 0.0036103 | 0.041199 | 60.2005 | -60.9833 | 60.8185 | -60.7315 | -61.1572 | -61.2625 | 0.086975 | 60.2646 | -61.084 | 60.553 | -60.9695 | -61.0428 | -61.2625 | 0.068665 | -0.28381 | 0.33417 | 0.32043 | -0.21057 | -0.10529 | -0.27924 | -0.17395 | -0.032043 | -0.21973 | 0.068665 | 0.082398 | -0.21057 | 0.009155 | -0.17853 | 0.041198 | 0.25177 | 121.8018 | 0.11444 | 121.637 | 121.1838 | 121.3486 | 121.2524 | 121.3165 | -121.4676 | -121.5683 | 121.8704 | 121.6049 | 61.0931 | 61.1389
72.3438 | 121.8292 | -61.1435 | 60.498 | 0.017166 | 0 | 0.064963 | 0.067133 | 0.0024139 | -0.0012112 | 0.003183 | 0.00018312 | 0.0018306 | -1.392 | 0.062675 | -0.0043408 | 0.0035719 | 0.00019229 | 0.009155 | 60.2554 | -61.0428 | 60.7315 | -60.8643 | -61.2854 | -61.3815 | -0.018311 | 60.2417 | -61.1343 | 60.4523 | -61.1252 | -61.2122 | -61.3678 | 0.10071 | -0.24262 | 0.23346 | 0.27924 | -0.23804 | -0.14191 | -0.33875 | -0.24261 | 0.009156 | -0.25635 | -0.045776 | 0.018311 | -0.2243 | -0.068664 | -0.23346 | -0.07782 | 0.17853 | 121.7743 | 0.009155 | 121.5866 | 121.2982 | 121.376 | 121.3989 | 121.3852 | -121.5408 | -121.6324 | 121.875 | 121.5958 | 61.1526 | 61.1252
74.0938 | 121.7834 | -61.1023 | 60.5484 | 0.0095369 | 0 | 0.06539 | 0.065424 | -0.0037811 | -0.0020658 | -0.0027984 | -0.0059205 | -0.00051916 | -1.3927 | 0.059043 | -0.0060498 | 0.0059217 | 0.0010467 | -0.018311 | 60.2554 | -60.9879 | 60.6995 | -60.8688 | -61.2579 | -61.3632 | -0.027466 | 60.3333 | -61.1389 | 60.4111 | -61.1298 | -61.1847 | -61.3632 | 0.11444 | -0.29297 | 0.15106 | 0.23346 | -0.26093 | -0.15564 | -0.37537 | -0.27008 | -0.036621 | -0.21515 | -0.13733 | -0.027466 | -0.26093 | -0.082397 | -0.2243 | -0.045776 | 0.11902 | 121.6873 | 0.009155 | 121.55 | 121.2433 | 121.4722 | 121.3577 | 121.4355 | -121.5363 | -121.6873 | 121.8018 | 121.5134 | 61.084 | 61.0748
75.7812 | 121.9299 | -61.0611 | 60.4797 | -0.0057221 | 0 | 0.064963 | 0.061579 | 0.00091851 | -0.002493 | 0.00019217 | 0.00018312 | -0.0013736 | -1.394 | 0.075065 | -0.001991 | 0.0046399 | 0.0021149 | 0 | 60.1868 | -60.9833 | 60.7681 | -60.7864 | -61.1801 | -61.2717 | 0.059509 | 60.228 | -61.116 | 60.5484 | -60.997 | -61.0565 | -61.2854 | 0.07782 | -0.29297 | 0.28839 | 0.27466 | -0.21057 | -0.11902 | -0.28839 | -0.19684 | -0.054932 | -0.25177 | 0.068665 | 0.064087 | -0.2243 | 0.004577 | -0.16937 | 0.059509 | 0.19684 | 121.7514 | 0.11902 | 121.6644 | 121.17 | 121.344 | 121.2479 | 121.2891 | -121.463 | -121.5958 | 121.8292 | 121.6095 | 61.0611 | 61.1206
77.4688 | 121.7972 | -61.0703 | 60.5576 | -0.013352 | 0 | 0.064108 | 0.064783 | -0.0012177 | -0.00035684 | 0.0016876 | -0.0059205 | 0.0026852 | -1.394 | 0.05648 | -0.0079724 | 0.0020765 | -0.0036529 | -0.004578 | 60.2737 | -61.0245 | 60.6949 | -60.8643 | -61.2671 | -61.3541 | -0.064087 | 60.2737 | -61.0931 | 60.4156 | -61.1069 | -61.1664 | -61.3541 | 0.045776 | -0.28381 | 0.13733 | 0.20599 | -0.28381 | -0.19684 | -0.32959 | -0.24262 | -0.022889 | -0.28381 | -0.14191 | -0.036622 | -0.28381 | -0.096131 | -0.26093 | -0.073242 | 0.16022 | 121.7194 | -0.013733 | 121.5088 | 121.2982 | 121.3669 | 121.344 | 121.344 | -121.582 | -121.6507 | 121.7651 | 121.4859 | 61.0657 | 61.0062
79.2344 | 121.7972 | -61.1206 | 60.5484 | 0.040054 | 0 | 0.067526 | 0.065851 | 0.0024139 | -0.00035684 | 0.0025422 | 0.015442 | 0.001617 | -1.3931 | 0.062888 | -0.0024182 | 0.0054945 | 0.00019229 | 0.009155 | 60.3287 | -61.0291 | 60.7086 | -60.8734 | -61.2625 | -61.322 | -0.045776 | 60.3104 | -61.1389 | 60.4431 | -61.1252 | -61.171 | -61.3541 | 0.091552 | -0.21973 | 0.16022 | 0.24719 | -0.20142 | -0.14191 | -0.29297 | -0.23346 | -0.018311 | -0.23804 | -0.10529 | -0.004578 | -0.23346 | -0.050354 | -0.21515 | -0.032043 | 0.15564 | 121.7377 | 0.013733 | 121.582 | 121.3577 | 121.4493 | 121.4493 | 121.431 | -121.5775 | -121.6873 | 121.8292 | 121.5637 | 61.1298 | 61.0748
80.9375 | 121.7789 | -61.1938 | 60.4614 | -0.0057221 | 0 | 0.066458 | 0.066279 | -0.00057689 | -0.00099764 | 0.00040597 | 0.0032349 | 0.0011898 | -1.395 | 0.07357 | -0.00092279 | 0.0044263 | -2.1314e-05 | -0.091553 | 60.2097 | -61.0428 | 60.5942 | -60.9741 | -61.3953 | -61.4639 | -0.14191 | 60.2188 | -61.1847 | 60.3699 | -61.2122 | -61.2762 | -61.4182 | 0.15106 | -0.25177 | 0.13275 | 0.21973 | -0.27008 | -0.20142 | -0.42114 | -0.35248 | 0.009156 | -0.24262 | -0.091553 | -0.01831 | -0.2243 | -0.082397 | -0.23346 | -0.091553 | 0.068665 | 121.637 | -0.027466 | 121.5546 | 121.2524 | 121.4035 | 121.4035 | 121.4127 | -121.5042 | -121.6461 | 121.788 | 121.5637 | 61.1023 | 61.0519
82.6875 | 121.7743 | -61.1755 | 60.4385 | 0.0095369 | 0 | 0.065176 | 0.066279 | 0.0032685 | -0.00099764 | -0.0015166 | 0.00018312 | 0.0026852 | -1.3925 | 0.061393 | -0.0022046 | 0.0046399 | 0.00061949 | -0.013733 | 60.228 | -61.0382 | 60.6674 | -60.9009 | -61.3358 | -61.4182 | -0.091553 | 60.228 | -61.1481 | 60.3928 | -61.1847 | -61.2488 | -61.4182 | 0.13733 | -0.21057 | 0.22888 | 0.27466 | -0.24262 | -0.16022 | -0.37994 | -0.29755 | 0.027466 | -0.21057 | -0.045777 | -0.009155 | -0.24262 | -0.073242 | -0.27008 | -0.10071 | 0.13733 | 121.7056 | -0.036621 | 121.5408 | 121.2662 | 121.376 | 121.4035 | 121.4035 | -121.4767 | -121.5866 | 121.843 | 121.5683 | 61.1618 | 61.084
84.3594 | 121.7926 | -61.1664 | 60.4202 | -0.0057221 | 0 | 0.063681 | 0.066706 | -0.0016449 | -0.00057044 | -0.0015166 | 0.00018312 | 0.0018306 | -1.3963 | 0.063102 | -0.00092279 | 0.0054945 | 0.0010467 | -0.09613 | 60.2142 | -61.0565 | 60.5942 | -60.9512 | -61.3815 | -61.4594 | -0.1236 | 60.2005 | -61.1847 | 60.3928 | -61.1893 | -61.2671 | -61.409 | 0.10986 | -0.20599 | 0.17395 | 0.21515 | -0.29297 | -0.21515 | -0.40283 | -0.32501 | -0.01831 | -0.21973 | -0.027466 | -0.022888 | -0.24262 | -0.10071 | -0.22431 | -0.082398 | 0.10529 | 121.6507 | -0.004578 | 121.5775 | 121.2708 | 121.3852 | 121.3806 | 121.3669 | -121.4767 | -121.6049 | 121.7606 | 121.5591 | 61.0703 | 61.0428
86.0469 | 121.8567 | -61.116 | 60.4431 | 0.017166 | 0 | 0.066031 | 0.063502 | -0.0014313 | -0.0020658 | -0.0023712 | 0.0032349 | -0.00030556 | -1.3922 | 0.07122 | -0.0011364 | 0.0046399 | 0.00040589 | -0.041199 | 60.1959 | -61.0245 | 60.6903 | -60.8459 | -61.2671 | -61.3495 | -0.041199 | 60.1822 | -61.1298 | 60.4706 | -61.0977 | -61.1526 | -61.3495 | 0.091553 | -0.24719 | 0.24719 | 0.27008 | -0.23346 | -0.15106 | -0.32501 | -0.24262 | -0.013733 | -0.26093 | 0.027466 | 0.018311 | -0.23346 | -0.036621 | -0.21973 | -0.022888 | 0.17853 | 121.7148 | 0.032044 | 121.6003 | 121.2204 | 121.312 | 121.312 | 121.2982 | -121.4676 | -121.5729 | 121.8063 | 121.5866 | 61.0748 | 61.0748
87.7344 | 121.9254 | -61.0977 | 60.4843 | 0.0019074 | 0 | 0.063895 | 0.063074 | -0.0063447 | -0.0029202 | 0.00040597 | -0.0028687 | -0.0020146 | -1.3927 | 0.06652 | -0.001991 | 0.0054945 | 0.0053193 | 0 | 60.2097 | -60.9879 | 60.7819 | -60.7681 | -61.1801 | -61.2717 | 0.073242 | 60.2188 | -61.0703 | 60.553 | -60.9879 | -61.0428 | -61.2625 | 0.10986 | -0.27466 | 0.29755 | 0.32959 | -0.17395 | -0.082398 | -0.28381 | -0.19226 | 0.027466 | -0.2655 | 0.068665 | 0.10986 | -0.16479 | 0.054931 | -0.19226 | 0.027465 | 0.21973 | 121.7697 | 0.082397 | 121.6232 | 121.1975 | 121.2891 | 121.3074 | 121.3165 | -121.4722 | -121.5546 | 121.8796 | 121.6507 | 61.0977 | 61.171
89.4688 | 121.8567 | -61.1618 | 60.4111 | -0.0057221 | 0 | 0.064963 | 0.06756 | -0.00057689 | -0.00099764 | -0.0038666 | -0.0028687 | 0.0035396 | -1.3935 | 0.064597 | 0.00057241 | 0.0065625 | -0.0034393 | -0.091553 | 60.2005 | -61.0336 | 60.6125 | -60.9467 | -61.3724 | -61.4548 | -0.091553 | 60.1913 | -61.1481 | 60.4156 | -61.1343 | -61.2076 | -61.3678 | 0.12817 | -0.21057 | 0.20142 | 0.21515 | -0.29297 | -0.21057 | -0.42114 | -0.33874 | 0.013733 | -0.21973 | 0.004577 | 0.027466 | -0.20599 | -0.045777 | -0.21973 | -0.05951 | 0.086975 | 121.6461 | 0.013733 | 121.5637 | 121.2341 | 121.3394 | 121.3623 | 121.3531 | -121.4447 | -121.5591 | 121.7743 | 121.5775 | 61.0703 | 61.0703
91.25 | 121.8246 | -61.1298 | 60.4248 | -0.0057221 | 0 | 0.065604 | 0.065851 | 0.0015595 | -0.0020658 | -0.00087583 | 0.00018312 | 0.0028988 | -1.3942 | 0.065666 | -0.00070919 | 0.0052807 | 0.00019229 | -0.086975 | 60.1959 | -61.0611 | 60.6079 | -60.9467 | -61.3632 | -61.4456 | -0.11444 | 60.1776 | -61.1755 | 60.4019 | -61.1572 | -61.2396 | -61.4044 | 0.068665 | -0.22888 | 0.1831 | 0.18311 | -0.31586 | -0.23346 | -0.38452 | -0.30212 | -0.045776 | -0.24719 | -0.022888 | -0.027466 | -0.27466 | -0.10986 | -0.22888 | -0.064087 | 0.11444 | 121.669 | 0.01831 | 121.5775 | 121.257 | 121.3531 | 121.3257 | 121.3074 | -121.4859 | -121.6003 | 121.7377 | 121.5317 | 61.0428 | 61.0153
93.0156 | 121.8018 | -61.1114 | 60.466 | 0.017166 | 0 | 0.067099 | 0.066492 | -0.00057689 | 0.0019932 | 0.00083317 | 0.0032349 | 0.0028988 | -1.3908 | 0.068443 | -0.0045544 | 0.0050671 | 0.0023285 | 0.013733 | 60.2737 | -61.0107 | 60.7086 | -60.8368 | -61.2534 | -61.3586 | -0.004578 | 60.228 | -61.1389 | 60.4614 | -61.116 | -61.1801 | -61.3541 | 0.10071 | -0.19226 | 0.24262 | 0.27466 | -0.24719 | -0.14191 | -0.3479 | -0.24262 | -0.027466 | -0.23804 | -0.004577 | -0.004578 | -0.24262 | -0.068665 | -0.21515 | -0.041199 | 0.17395 | 121.7194 | 0.022888 | 121.6003 | 121.2845 | 121.3669 | 121.3852 | 121.3394 | -121.4767 | -121.6049 | 121.8201 | 121.5729 | 61.1252 | 61.1069
94.7188 | 121.7651 | -61.1801 | 60.4568 | -0.0057221 | 0 | 0.066672 | 0.065211 | -0.0042083 | 0.0024204 | 0.0023286 | 0.00018312 | 0.00076264 | -1.3927 | 0.068229 | -6.8386e-05 | 0.0033581 | -0.0027985 | -0.086975 | 60.2371 | -61.0611 | 60.585 | -60.997 | -61.409 | -61.4914 | -0.15106 | 60.1959 | -61.1618 | 60.3561 | -61.2167 | -61.2946 | -61.409 | 0.11902 | -0.21973 | 0.12817 | 0.18311 | -0.31128 | -0.22888 | -0.4303 | -0.3479 | 0.018311 | -0.26093 | -0.10071 | -0.036621 | -0.22888 | -0.11444 | -0.24719 | -0.13275 | 0.064087 | 121.6461 | -0.054932 | 121.5179 | 121.2982 | 121.3577 | 121.4172 | 121.376 | -121.5179 | -121.6187 | 121.7651 | 121.5363 | 61.0931 | 61.0291
96.4688 | 121.8155 | -61.1526 | 60.4202 | 0.0095369 | 0 | 0.064536 | 0.065424 | -0.0010041 | -0.00099764 | 0.0016876 | -0.0028687 | 0.0024716 | -1.3942 | 0.062888 | -0.001991 | 0.0048535 | 0.0080963 | -0.10071 | 60.2234 | -61.0703 | 60.6079 | -60.9558 | -61.3678 | -61.4639 | -0.11902 | 60.2005 | -61.1435 | 60.3836 | -61.1893 | -61.2396 | -61.409 | 0.082398 | -0.19684 | 0.18768 | 0.19684 | -0.31128 | -0.21515 | -0.39368 | -0.29755 | 0.009155 | -0.21973 | -0.036621 | -0.036621 | -0.25635 | -0.086975 | -0.2655 | -0.09613 | 0.11444 | 121.6782 | -0.045776 | 121.5271 | 121.2936 | 121.344 | 121.376 | 121.3531 | -121.4905 | -121.5637 | 121.7606 | 121.5363 | 61.0519 | 61.0336
98.25 | 121.9162 | -61.116 | 60.3928 | 0.0095369 | 0 | 0.06539 | 0.066279 | 0.0017731 | 0.00028416 | -0.00023503 | -0.0028687 | -0.0015872 | -1.3944 | 0.069297 | 0.0012134 | 0.0084851 | 0.0021149 | -0.036621 | 60.1456 | -61.0565 | 60.6995 | -60.8322 | -61.2717 | -61.3632 | -0.009155 | 60.1456 | -61.1389 | 60.4797 | -61.0611 | -61.1389 | -61.3174 | 0.059509 | -0.24719 | 0.3067 | 0.28381 | -0.24719 | -0.15564 | -0.3067 | -0.21515 | -0.022888 | -0.24719 | 0.086975 | 0.054932 | -0.20142 | -0.022888 | -0.17853 | 0 | 0.22431 | 121.756 | 0.07782 | 121.6187 | 121.2021 | 121.2845 | 121.2616 | 121.2616 | -121.4493 | -121.5317 | 121.8155 | 121.5958 | 61.0794 | 61.1069
99.9844 | 121.8475 | -61.0657 | 60.5118 | -0.0057221 | 0 | 0.064749 | 0.063502 | -0.0014313 | -0.0016384 | 0.0023286 | 0.00018312 | 0.00033544 | -1.3935 | 0.071433 | -0.003059 | 0.0044263 | -0.0036529 | 0.036621 | 60.2463 | -60.9512 | 60.7819 | -60.7544 | -61.1664 | -61.2717 | 0.054932 | 60.2325 | -61.0611 | 60.5072 | -61.0153 | -61.0519 | -61.2808 | 0.11444 | -0.2655 | 0.27008 | 0.31128 | -0.20599 | -0.10071 | -0.32043 | -0.21515 | 0.004578 | -0.27924 | -0.004578 | 0.050354 | -0.21515 | 0.013733 | -0.21973 | 0.009155 | 0.19684 | 121.7331 | 0.045776 | 121.5683 | 121.1975 | 121.2936 | 121.312 | 121.2982 | -121.463 | -121.5729 | 121.8475 | 121.5729 | 61.1023 | 61.1206
101.7344 | 121.756 | -61.0748 | 60.5392 | -0.0057221 | 0 | 0.061972 | 0.064356 | -0.0014313 | -0.00014304 | 0.00061957 | -0.0028687 | 0.0011898 | -1.392 | 0.069724 | -0.003059 | 0.0052807 | -0.0021575 | -0.004578 | 60.26 | -60.9924 | 60.6949 | -60.8505 | -61.2534 | -61.3358 | -0.059509 | 60.3058 | -61.0794 | 60.434 | -61.116 | -61.1526 | -61.3449 | 0.082397 | -0.27924 | 0.15564 | 0.2243 | -0.26093 | -0.17853 | -0.34332 | -0.26093 | -0.004578 | -0.23346 | -0.10529 | -0.041199 | -0.27008 | -0.07782 | -0.2655 | -0.073242 | 0.14191 | 121.6873 | -0.036621 | 121.5134 | 121.2524 | 121.3852 | 121.3348 | 121.3806 | -121.5317 | -121.6187 | 121.7697 | 121.5088 | 61.0703 | 61.0153
103.4062 | 121.9025 | -61.1343 | 60.379 | 0.0019074 | 0 | 0.066245 | 0.064997 | 0.0026275 | -0.00014304 | -0.00087583 | -0.0028687 | -9.1956e-05 | -1.3937 | 0.062248 | 0.0035632 | 0.0067761 | -0.00023491 | -0.032043 | 60.1593 | -61.0474 | 60.7086 | -60.8368 | -61.2808 | -61.3541 | -0.004578 | 60.1456 | -61.1389 | 60.4797 | -61.084 | -61.1618 | -61.3266 | 0.086975 | -0.21973 | 0.32959 | 0.29755 | -0.21973 | -0.14648 | -0.3067 | -0.23346 | -0.004578 | -0.23346 | 0.10071 | 0.050354 | -0.19226 | -0.027466 | -0.18768 | -0.022888 | 0.21057 | 121.756 | 0.054932 | 121.6187 | 121.2067 | 121.2845 | 121.2936 | 121.2799 | -121.4264 | -121.5179 | 121.843 | 121.6141 | 61.1023 | 61.1298
105.1875 | 121.8109 | -61.1206 | 60.4614 | 0.040054 | 0 | 0.065176 | 0.06692 | 0.00091851 | -0.00014304 | 0.00019217 | 0.0093383 | 0.00012184 | -1.3925 | 0.071433 | -0.0034864 | 0.0042127 | -0.0034393 | 0.018311 | 60.2829 | -61.0382 | 60.704 | -60.8414 | -61.2534 | -61.3358 | 0.004578 | 60.2463 | -61.1481 | 60.4385 | -61.0977 | -61.171 | -61.3358 | 0.082397 | -0.17853 | 0.24261 | 0.27923 | -0.21515 | -0.13275 | -0.29755 | -0.21515 | -0.027466 | -0.21515 | -0.022888 | 0.022888 | -0.21515 | -0.050354 | -0.18768 | -0.022888 | 0.19684 | 121.7422 | 0.050354 | 121.5866 | 121.3211 | 121.3943 | 121.4035 | 121.3669 | -121.4996 | -121.6095 | 121.8246 | 121.5591 | 61.1389 | 61.1252
107.0469 | 121.8155 | -61.1298 | 60.4752 | 0.017166 | 0 | 0.064749 | 0.065211 | 0.0015595 | -0.0014248 | -0.00087583 | 0.0093383 | 0.0026852 | -1.3916 | 0.063102 | -0.0058362 | 0.0037855 | 0.00019229 | 0.018311 | 60.2325 | -61.0428 | 60.704 | -60.8276 | -61.2579 | -61.3495 | -0.004578 | 60.2325 | -61.1389 | 60.4523 | -61.084 | -61.1664 | -61.3312 | 0.086975 | -0.24262 | 0.22888 | 0.30212 | -0.21973 | -0.12817 | -0.3067 | -0.21515 | -0.009155 | -0.24262 | -0.022888 | 0.045777 | -0.20142 | -0.036621 | -0.19226 | -0.027466 | 0.21515 | 121.7468 | 0.054932 | 121.5912 | 121.2753 | 121.3715 | 121.3623 | 121.3623 | -121.5179 | -121.6141 | 121.8338 | 121.582 | 61.1481 | 61.1252
109.0156 | 121.843 | -61.0565 | 60.4889 | 0.0019074 | 0 | 0.064322 | 0.062647 | 0.0043365 | -0.00057044 | -0.00044863 | -0.0028687 | -0.00116 | -1.3952 | 0.065879 | -0.0015638 | 0.0048535 | -0.00066231 | 0.041199 | 60.2188 | -60.9741 | 60.7864 | -60.7498 | -61.171 | -61.2625 | 0.050354 | 60.2417 | -61.0428 | 60.5209 | -60.997 | -61.0565 | -61.2579 | 0.082398 | -0.27008 | 0.29755 | 0.3067 | -0.20599 | -0.11444 | -0.28839 | -0.19684 | 0.013733 | -0.24719 | 0.032043 | 0.05951 | -0.20142 | 0 | -0.21515 | -0.013733 | 0.2243 | 121.7606 | 0.045777 | 121.5637 | 121.1929 | 121.2845 | 121.2753 | 121.2982 | -121.463 | -121.5317 | 121.843 | 121.5775 | 61.0977 | 61.1069
110.7031 | 121.8887 | -61.1206 | 60.4065 | 0.047683 | 0 | 0.06774 | 0.065638 | 0.0015595 | 0.0030612 | 0.0029694 | 0.018494 | 0.0020444 | -1.392 | 0.064597 | 0.00057241 | 0.0065625 | 0.0010467 | -0.004578 | 60.1959 | -61.0657 | 60.7224 | -60.7773 | -61.2442 | -61.3312 | 0.059509 | 60.1868 | -61.1481 | 60.4706 | -61.0657 | -61.1298 | -61.3266 | 0.054931 | -0.21057 | 0.31586 | 0.34332 | -0.21057 | -0.1236 | -0.2655 | -0.17853 | -0.027466 | -0.21973 | 0.064087 | 0.054931 | -0.20599 | -0.009156 | -0.17853 | 0.01831 | 0.28839 | 121.788 | 0.082397 | 121.6187 | 121.2616 | 121.3348 | 121.3165 | 121.3074 | -121.4722 | -121.5546 | 121.843 | 121.5912 | 61.116 | 61.1801
112.4062 | 121.8567 | -61.1023 | 60.4385 | 0.040054 | 0 | 0.065817 | 0.065638 | -0.00036309 | 0.0017796 | 0.001474 | 0.01239 | 0.00033544 | -1.3933 | 0.070365 | -0.00070919 | 0.0050671 | 0.00040589 | -0.045776 | 60.1822 | -61.0245 | 60.7315 | -60.8185 | -61.2625 | -61.3403 | -0.009155 | 60.1959 | -61.1435 | 60.4568 | -61.0886 | -61.1298 | -61.3358 | 0.07782 | -0.25635 | 0.29297 | 0.28381 | -0.23804 | -0.16022 | -0.31586 | -0.23804 | -0.041199 | -0.24262 | 0.01831 | 0.013733 | -0.23346 | -0.027466 | -0.19226 | 0.013733 | 0.20599 | 121.756 | 0.054932 | 121.6003 | 121.2067 | 121.3394 | 121.2845 | 121.2982 | -121.463 | -121.582 | 121.8338 | 121.5591 | 61.0565 | 61.0931
114.1094 | 121.8796 | -61.0428 | 60.4843 | 0.0019074 | 0 | 0.061972 | 0.061793 | 0.0034821 | -0.00078404 | 0.0012604 | 0.0032349 | 0.00076264 | -1.3927 | 0.072074 | -0.0026318 | 0.0059217 | -0.00023491 | 0.041199 | 60.2005 | -60.965 | 60.7956 | -60.7178 | -61.1435 | -61.2625 | 0.068665 | 60.2509 | -61.0794 | 60.5255 | -60.9833 | -61.0611 | -61.2625 | 0.07782 | -0.28381 | 0.31128 | 0.32501 | -0.21973 | -0.10071 | -0.29755 | -0.17853 | -0.036621 | -0.23346 | 0.041199 | 0.05951 | -0.21973 | -0.01831 | -0.1831 | 0.018311 | 0.24719 | 121.7606 | 0.096131 | 121.6049 | 121.1655 | 121.3303 | 121.2433 | 121.2936 | -121.4493 | -121.5637 | 121.8384 | 121.5683 | 61.084 | 61.1115
115.7812 | 121.8796 | -61.1114 | 60.3882 | 0.047683 | 0 | 0.066458 | 0.065638 | 0.0036957 | 0.00092496 | 0.0019012 | 0.0032349 | 0.00097624 | -1.3931 | 0.064597 | 0.00099981 | 0.0044263 | -0.0025849 | -0.013733 | 60.1776 | -61.0703 | 60.7544 | -60.7819 | -61.2259 | -61.3266 | 0.041199 | 60.173 | -61.1572 | 60.4706 | -61.0794 | -61.1481 | -61.322 | 0.041199 | -0.21057 | 0.36621 | 0.32959 | -0.21515 | -0.11444 | -0.25635 | -0.15564 | -0.045777 | -0.21515 | 0.082397 | 0.032043 | -0.21057 | -0.036621 | -0.16479 | 0.009156 | 0.28839 | 121.8246 | 0.07782 | 121.6278 | 121.2479 | 121.3303 | 121.2891 | 121.2845 | -121.4584 | -121.5454 | 121.8658 | 121.582 | 61.0977 | 61.1526
117.4688 | 121.7926 | -61.1206 | 60.4294 | 0.0095369 | 0 | 0.064322 | 0.066706 | 0.00091851 | -0.0012112 | 0.0010468 | 0.00018312 | 0.0035396 | -1.3927 | 0.064811 | -0.003059 | 0.0063489 | -0.00066231 | -0.009155 | 60.2097 | -61.0474 | 60.6812 | -60.878 | -61.2946 | -61.3861 | -0.059509 | 60.2188 | -61.1206 | 60.3836 | -61.1435 | -61.2259 | -61.3907 | 0.073242 | -0.21973 | 0.25177 | 0.24261 | -0.2655 | -0.17395 | -0.33875 | -0.24719 | 0 | -0.21057 | -0.045776 | -0.022889 | -0.27008 | -0.10529 | -0.27008 | -0.10529 | 0.16937 | 121.7285 | -0.022889 | 121.5042 | 121.257 | 121.3394 | 121.3303 | 121.3394 | -121.4767 | -121.55 | 121.8018 | 121.5042 | 61.1114 | 61.0611
119.1406 | 121.788 | -61.1298 | 60.4706 | 0.017166 | 0 | 0.065604 | 0.066279 | -0.0016449 | -0.00035684 | -0.00066223 | 0.0032349 | 0.0014034 | -1.3933 | 0.05947 | -0.0022046 | 0.0022901 | 0.0021149 | 0.004578 | 60.2371 | -61.0245 | 60.7086 | -60.8551 | -61.2717 | -61.3724 | -0.013733 | 60.2371 | -61.1343 | 60.4202 | -61.116 | -61.1938 | -61.377 | 0.10529 | -0.23346 | 0.23804 | 0.27466 | -0.24261 | -0.14191 | -0.3479 | -0.24719 | -0.004577 | -0.23346 | -0.050354 | 0.013733 | -0.24719 | -0.064087 | -0.24262 | -0.05951 | 0.16937 | 121.7331 | 0.01831 | 121.5546 | 121.2616 | 121.3715 | 121.3669 | 121.3669 | -121.4951 | -121.6049 | 121.8384 | 121.55 | 61.1343 | 61.116
120.8281 | 121.7972 | -61.0977 | 60.4752 | 0.055313 | 0 | 0.067099 | 0.066706 | 0.0024139 | -0.00035684 | 0.0010468 | 0.01239 | 0.002258 | -1.3901 | 0.057548 | -0.0024182 | 0.0048535 | -0.00066231 | 0.032043 | 60.2921 | -61.0291 | 60.6903 | -60.8322 | -61.2534 | -61.3495 | -0.022888 | 60.26 | -61.1343 | 60.4385 | -61.084 | -61.1481 | -61.3266 | 0.068664 | -0.18311 | 0.21515 | 0.2655 | -0.25177 | -0.15564 | -0.32043 | -0.2243 | -0.036621 | -0.21515 | -0.036621 | 0.013733 | -0.22888 | -0.050354 | -0.19226 | -0.013733 | 0.19684 | 121.7194 | 0.050354 | 121.5729 | 121.3211 | 121.3943 | 121.3898 | 121.3577 | -121.5042 | -121.6095 | 121.788 | 121.5363 | 61.1298 | 61.0748
122.5 | 121.907 | -61.0565 | 60.4752 | -0.0057221 | 0 | 0.064749 | 0.062647 | -0.00057689 | -0.00078404 | 0.00061957 | 0.0032349 | -0.00116 | -1.3937 | 0.062675 | -0.0015638 | 0.0044263 | -0.00023491 | -0.013733 | 60.2005 | -60.9833 | 60.7636 | -60.7452 | -61.1481 | -61.2488 | 0.10071 | 60.2234 | -61.084 | 60.5484 | -60.9604 | -61.0107 | -61.235 | 0.073243 | -0.27466 | 0.28839 | 0.31128 | -0.19226 | -0.091552 | -0.2655 | -0.1648 | -0.027465 | -0.25177 | 0.073242 | 0.096131 | -0.17853 | 0.045777 | -0.15106 | 0.073242 | 0.23804 | 121.7468 | 0.1236 | 121.6324 | 121.1838 | 121.3074 | 121.257 | 121.2799 | -121.4584 | -121.5591 | 121.8201 | 121.6049 | 61.0428 | 61.1572
124.1875 | 121.7606 | -61.1618 | 60.4477 | 0.0019074 | 0 | 0.064322 | 0.066065 | 0.00070491 | -0.0012112 | -0.00087583 | -0.0059205 | 0.0014034 | -1.3944 | 0.071006 | -0.00049559 | 0.0050671 | 0.0027557 | -0.10071 | 60.2005 | -61.0382 | 60.585 | -60.9833 | -61.3953 | -61.4731 | -0.16479 | 60.2005 | -61.1435 | 60.3516 | -61.2122 | -61.2717 | -61.4182 | 0.1236 | -0.24719 | 0.13733 | 0.17853 | -0.31128 | -0.23346 | -0.43488 | -0.35706 | 0.01831 | -0.24719 | -0.096131 | -0.050354 | -0.25635 | -0.10986 | -0.27466 | -0.12817 | 0.054932 | 121.6232 | -0.068664 | 121.4951 | 121.2387 | 121.344 | 121.3623 | 121.3623 | -121.4859 | -121.5912 | 121.7468 | 121.5134 | 61.0611 | 60.997
125.8438 | 121.7743 | -61.0886 | 60.5164 | 0.0019074 | 0 | 0.065817 | 0.066279 | -0.00057689 | 7.0564e-05 | 0.0019012 | 0.015442 | 0.003967 | -1.392 | 0.056693 | -0.0062634 | 0.0050671 | 0.00040589 | 0.013733 | 60.3195 | -61.0519 | 60.6903 | -60.8551 | -61.2305 | -61.3129 | -0.059509 | 60.2875 | -61.116 | 60.4156 | -61.116 | -61.1801 | -61.3312 | 0.036621 | -0.19684 | 0.17395 | 0.23346 | -0.2243 | -0.14191 | -0.26093 | -0.17853 | -0.027466 | -0.22888 | -0.10071 | -0.027466 | -0.24261 | -0.091553 | -0.21515 | -0.064087 | 0.19684 | 121.7422 | 0 | 121.5317 | 121.3715 | 121.4035 | 121.4081 | 121.376 | -121.5683 | -121.6324 | 121.7789 | 121.5042 | 61.1023 | 61.0291
127.5312 | 121.8704 | -61.1252 | 60.4202 | 0.040054 | 0 | 0.066885 | 0.065851 | -0.0014313 | 7.0564e-05 | -0.00023503 | 0.015442 | 0.0024716 | -1.3912 | 0.062461 | -0.00049559 | 0.0059217 | 0.0021149 | -0.013733 | 60.1547 | -61.0748 | 60.7361 | -60.7773 | -61.2396 | -61.3129 | 0.041199 | 60.1456 | -61.1618 | 60.4752 | -61.0657 | -61.1252 | -61.322 | 0.050354 | -0.2655 | 0.31586 | 0.3479 | -0.18768 | -0.11444 | -0.23804 | -0.16479 | -0.036621 | -0.27466 | 0.054932 | 0.059509 | -0.19684 | 0 | -0.16022 | 0.036621 | 0.29755 | 121.8109 | 0.09613 | 121.637 | 121.2296 | 121.3074 | 121.2799 | 121.2708 | -121.4951 | -121.582 | 121.8613 | 121.6003 | 61.1114 | 61.1664
129.2812 | 121.7606 | -61.1343 | 60.4706 | -0.013352 | 0 | 0.066031 | 0.066065 | 0.00027771 | -0.0022794 | 0.00061957 | 0.0032349 | 0.00076264 | -1.3948 | 0.063743 | -0.00070919 | 0.0076307 | 0.00083309 | -0.091553 | 60.1913 | -61.0611 | 60.585 | -60.965 | -61.409 | -61.4685 | -0.15106 | 60.228 | -61.1572 | 60.3378 | -61.2167 | -61.2671 | -61.409 | 0.073242 | -0.27924 | 0.11444 | 0.16937 | -0.33417 | -0.27466 | -0.40741 | -0.3479 | -0.022889 | -0.24262 | -0.13275 | -0.082398 | -0.27466 | -0.13275 | -0.25177 | -0.10986 | 0.09613 | 121.6461 | -0.059509 | 121.4951 | 121.2524 | 121.3852 | 121.3257 | 121.3623 | -121.5317 | -121.6278 | 121.7194 | 121.4722 | 61.0428 | 60.9833
130.9531 | 121.8155 | -61.1206 | 60.4294 | -0.0057221 | 0 | 0.066031 | 0.065211 | 0.00049131 | 0.0017796 | -2.1434e-05 | -0.0028687 | -0.00030556 | -1.3922 | 0.061179 | -0.00070919 | 0.0050671 | 0.00083309 | -0.10071 | 60.2051 | -61.0611 | 60.585 | -60.9329 | -61.3815 | -61.4319 | -0.10529 | 60.1685 | -61.1618 | 60.4111 | -61.1435 | -61.2122 | -61.3678 | 0.059509 | -0.2243 | 0.15564 | 0.18768 | -0.31128 | -0.26093 | -0.37079 | -0.32044 | -0.041199 | -0.26093 | -0.01831 | -0.022889 | -0.24719 | -0.091553 | -0.20599 | -0.050354 | 0.12817 | 121.6461 | 0.01831 | 121.5729 | 121.2662 | 121.3303 | 121.3257 | 121.2891 | -121.4905 | -121.5912 | 121.7056 | 121.5317 | 61.0199 | 61.0153
132.6406 | 121.8796 | -61.0794 | 60.4614 | 0.0095369 | 0 | 0.065176 | 0.064997 | 0.0011321 | -0.0014248 | 0.0033966 | -0.0028687 | -0.00030556 | -1.3948 | 0.070152 | -0.0015638 | 0.0044263 | 0.0025421 | -0.054932 | 60.2097 | -61.0107 | 60.7132 | -60.8047 | -61.2259 | -61.2946 | 0 | 60.2005 | -61.1114 | 60.5164 | -61.0153 | -61.0703 | -61.2671 | 0.068665 | -0.25177 | 0.25177 | 0.27466 | -0.21515 | -0.14648 | -0.28381 | -0.21515 | -0.032043 | -0.26093 | 0.054931 | 0.064087 | -0.18768 | 0.009156 | -0.15564 | 0.041199 | 0.20599 | 121.7239 | 0.09613 | 121.6278 | 121.2204 | 121.3119 | 121.2891 | 121.2799 | -121.4722 | -121.5729 | 121.7926 | 121.5958 | 61.0245 | 61.0794
134.3125 | 121.7972 | -61.1069 | 60.4156 | 0.0019074 | 0 | 0.06539 | 0.06457 | -0.0016449 | -0.00014304 | 0.00083317 | 0.00018312 | 0.00054904 | -1.3933 | 0.065879 | 0.0016406 | 0.0050671 | 0.0038239 | -0.082397 | 60.2005 | -61.0474 | 60.5988 | -60.9467 | -61.3724 | -61.4227 | -0.11902 | 60.1776 | -61.1435 | 60.3699 | -61.1755 | -61.2488 | -61.377 | 0.05951 | -0.21515 | 0.18311 | 0.16022 | -0.31586 | -0.2655 | -0.37537 | -0.32501 | -0.036621 | -0.23804 | -0.045776 | -0.068664 | -0.27008 | -0.14191 | -0.23346 | -0.10529 | 0.10071 | 121.6461 | -0.032043 | 121.5134 | 121.2479 | 121.3211 | 121.3074 | 121.2845 | -121.463 | -121.5591 | 121.7056 | 121.4767 | 61.0245 | 60.9879
135.9844 | 121.7514 | -61.1298 | 60.466 | 0.0019074 | 0 | 0.064108 | 0.065851 | -0.0020721 | -0.0012112 | 0.001474 | -0.0059205 | 0.0026852 | -1.3935 | 0.066947 | -0.0032728 | 0.0044263 | 0.00061949 | -0.064087 | 60.2051 | -61.0611 | 60.6079 | -60.9375 | -61.377 | -61.441 | -0.14191 | 60.2097 | -61.1343 | 60.3516 | -61.2076 | -61.2854 | -61.4136 | 0.068665 | -0.26093 | 0.14191 | 0.19226 | -0.31128 | -0.24719 | -0.37994 | -0.31586 | -0.004577 | -0.25635 | -0.11444 | -0.07782 | -0.28381 | -0.15564 | -0.27924 | -0.15106 | 0.1236 | 121.669 | -0.073243 | 121.4859 | 121.2662 | 121.344 | 121.3348 | 121.3394 | -121.5271 | -121.6003 | 121.7377 | 121.4813 | 61.0657 | 60.9879
137.6719 | 121.8246 | -61.0794 | 60.4431 | 0.017166 | 0 | 0.063254 | 0.06222 | -0.00057689 | 0.00092496 | -2.1434e-05 | 0.0062865 | -0.002869 | -1.3931 | 0.066306 | -0.00070919 | 0.0052807 | -0.00023491 | -0.059509 | 60.1685 | -61.0062 | 60.6857 | -60.8276 | -61.2534 | -61.3358 | -0.045776 | 60.1913 | -61.1298 | 60.4294 | -61.0748 | -61.1481 | -61.3266 | 0.073242 | -0.27466 | 0.24262 | 0.25177 | -0.25635 | -0.17395 | -0.32959 | -0.24719 | -0.050354 | -0.25177 | -0.013733 | 0.004578 | -0.24719 | -0.068664 | -0.19684 | -0.01831 | 0.17853 | 121.6919 | 0.054932 | 121.5591 | 121.1746 | 121.3211 | 121.2479 | 121.2708 | -121.4493 | -121.5729 | 121.7651 | 121.5088 | 61.0199 | 61.0336
139.3438 | 121.7468 | -61.1618 | 60.4385 | 0.0019074 | 0 | 0.066031 | 0.065851 | 0.0034821 | 7.0564e-05 | 0.00083317 | -0.0059205 | 0.0028988 | -1.3933 | 0.071433 | -0.0015638 | 0.0052807 | 0.0031829 | -0.064087 | 60.1913 | -61.0565 | 60.5667 | -60.9924 | -61.4044 | -61.4685 | -0.15106 | 60.2051 | -61.1572 | 60.3561 | -61.1984 | -61.2717 | -61.3953 | 0.10528 | -0.24719 | 0.12817 | 0.16937 | -0.3067 | -0.24262 | -0.41199 | -0.3479 | 0.004577 | -0.23346 | -0.082398 | -0.036621 | -0.23346 | -0.10986 | -0.23804 | -0.11444 | 0.064087 | 121.6232 | -0.041198 | 121.5134 | 121.2479 | 121.3623 | 121.3531 | 121.3669 | -121.4951 | -121.5958 | 121.7285 | 121.5179 | 61.0977 | 61.0107
141.0156 | 121.7514 | -61.171 | 60.4523 | 0.0019074 | 0 | 0.06539 | 0.064783 | 0.0026275 | -0.00014304 | -0.0010894 | -0.0059205 | 0.00076264 | -1.3948 | 0.064811 | -0.0026318 | 0.0054945 | 0.0014741 | -0.082397 | 60.1959 | -61.0428 | 60.5621 | -60.9879 | -61.4182 | -61.4822 | -0.16937 | 60.2142 | -61.1481 | 60.3561 | -61.2122 | -61.2762 | -61.4044 | 0.12817 | -0.25635 | 0.10986 | 0.18311 | -0.31128 | -0.24719 | -0.43945 | -0.37537 | 0.022888 | -0.23804 | -0.096131 | -0.041199 | -0.23346 | -0.10529 | -0.25635 | -0.12817 | 0.054932 | 121.6049 | -0.064087 | 121.5042 | 121.2387 | 121.3623 | 121.3669 | 121.3852 | -121.4951 | -121.6003 | 121.7331 | 121.5271 | 61.0886 | 61.0016
142.6875 | 121.7606 | -61.1389 | 60.4111 | 0.0019074 | 0 | 0.066031 | 0.065638 | -0.0024995 | -0.0014248 | 0.0010468 | -0.0028687 | 0.0024716 | -1.3918 | 0.068443 | -0.0013502 | 0.0050671 | 0.0021149 | -0.09613 | 60.2188 | -61.0382 | 60.5713 | -60.9421 | -61.3815 | -61.4319 | -0.11902 | 60.2097 | -61.1435 | 60.3653 | -61.1755 | -61.2442 | -61.3953 | 0.10071 | -0.19226 | 0.16022 | 0.19684 | -0.29297 | -0.24262 | -0.39368 | -0.34332 | -0.004578 | -0.20142 | -0.045777 | -0.036621 | -0.25635 | -0.10529 | -0.25177 | -0.10071 | 0.09613 | 121.6095 | -0.032043 | 121.5088 | 121.257 | 121.3531 | 121.3577 | 121.3486 | -121.4493 | -121.5546 | 121.7102 | 121.5042 | 61.0428 | 61.0199
144.375 | 121.8979 | -61.1023 | 60.3836 | 0.0019074 | 0 | 0.06539 | 0.063929 | 6.4114e-05 | -0.00057044 | -0.00087583 | -0.0028687 | 0.0011898 | -1.3942 | 0.069938 | 0.0018542 | 0.0067761 | -0.0027985 | -0.059509 | 60.1639 | -61.0336 | 60.672 | -60.8276 | -61.2991 | -61.3724 | -0.009155 | 60.1547 | -61.1572 | 60.4752 | -61.0748 | -61.1389 | -61.3037 | 0.068665 | -0.21973 | 0.28839 | 0.27466 | -0.27008 | -0.19684 | -0.33874 | -0.2655 | -0.054932 | -0.22888 | 0.091553 | 0.027466 | -0.20142 | -0.036621 | -0.14648 | 0.018311 | 0.20599 | 121.7056 | 0.082398 | 121.6324 | 121.1975 | 121.312 | 121.2662 | 121.257 | -121.4172 | -121.5408 | 121.7743 | 121.5775 | 61.0428 | 61.0931
146.0781 | 121.756 | -61.0931 | 60.5484 | 0.0019074 | 0 | 0.064322 | 0.065211 | -0.0010041 | -0.002493 | -0.003012 | 0.00018312 | 0.00054904 | -1.3931 | 0.065879 | -0.0060498 | 0.0052807 | -0.00023491 | -0.041199 | 60.2646 | -60.9924 | 60.672 | -60.8551 | -61.2625 | -61.3541 | -0.064087 | 60.2737 | -61.0931 | 60.4111 | -61.0931 | -61.1572 | -61.3403 | 0.10071 | -0.28381 | 0.1236 | 0.23804 | -0.26093 | -0.16937 | -0.36163 | -0.27008 | 0 | -0.27466 | -0.13733 | 0 | -0.24719 | -0.064087 | -0.24719 | -0.064087 | 0.13733 | 121.6644 | 0 | 121.5042 | 121.257 | 121.3669 | 121.3577 | 121.3669 | -121.5408 | -121.6415 | 121.7651 | 121.5042 | 61.0519 | 61.0291
147.75 | 121.7697 | -61.0886 | 60.5026 | 0.0019074 | 0 | 0.067099 | 0.062647 | -0.0031403 | -0.0020658 | -0.0010894 | 0.00018312 | 0.00076264 | -1.3942 | 0.063957 | -0.0051954 | 0.0042127 | 0.0016877 | 0.041199 | 60.2417 | -60.9604 | 60.7452 | -60.7727 | -61.203 | -61.3037 | 0.009155 | 60.2509 | -61.0794 | 60.4431 | -61.0565 | -61.1206 | -61.3174 | 0.12817 | -0.26093 | 0.24261 | 0.31586 | -0.21515 | -0.11444 | -0.34332 | -0.24262 | 0.009155 | -0.25177 | -0.05951 | 0.032043 | -0.22888 | -0.032043 | -0.23804 | -0.041198 | 0.18768 | 121.7056 | 0.022888 | 121.5225 | 121.2021 | 121.3303 | 121.3303 | 121.3394 | -121.463 | -121.582 | 121.8338 | 121.5317 | 61.1298 | 61.0977
149.4219 | 121.8613 | -61.0519 | 60.4431 | 0.0019074 | 0 | 0.063467 | 0.063929 | -0.0010041 | -0.0022794 | 0.001474 | -0.0028687 | -0.00116 | -1.3927 | 0.061393 | -0.0032728 | 0.0074171 | -0.0017303 | -0.050354 | 60.173 | -61.0245 | 60.6857 | -60.8139 | -61.2396 | -61.3129 | -0.022888 | 60.2097 | -61.0931 | 60.4797 | -61.0291 | -61.084 | -61.2671 | 0.027466 | -0.27008 | 0.24262 | 0.23804 | -0.26093 | -0.18768 | -0.28839 | -0.21515 | -0.041199 | -0.23346 | 0.036621 | 0.022888 | -0.21515 | -0.032043 | -0.17395 | 0.009156 | 0.21057 | 121.7102 | 0.064087 | 121.5729 | 121.1975 | 121.3028 | 121.225 | 121.2616 | -121.4676 | -121.5363 | 121.7377 | 121.5317 | 61.0016 | 61.0291
151.0938 | 121.8887 | -61.0519 | 60.4477 | -0.0057221 | 0 | 0.064536 | 0.064356 | -0.0039947 | -0.0031338 | -0.001303 | -0.0028687 | -0.00073276 | -1.3937 | 0.067161 | -0.0015638 | 0.0037855 | 0.00040589 | 0.009155 | 60.1913 | -60.965 | 60.7727 | -60.7269 | -61.1664 | -61.2534 | 0.086975 | 60.2142 | -61.0703 | 60.5347 | -60.965 | -61.0199 | -61.2305 | 0.086975 | -0.25635 | 0.32501 | 0.32501 | -0.20142 | -0.11444 | -0.28839 | -0.20142 | -0.01831 | -0.23346 | 0.086975 | 0.086975 | -0.17853 | 0.032044 | -0.16022 | 0.050354 | 0.23804 | 121.7377 | 0.10529 | 121.6049 | 121.1563 | 121.2845 | 121.2433 | 121.2662 | -121.4127 | -121.5179 | 121.8246 | 121.5866 | 61.0611 | 61.1389
152.7969 | 121.8109 | -61.0931 | 60.4111 | 0.040054 | 0 | 0.068381 | 0.066492 | 0.0039093 | -0.00057044 | 0.0010468 | 0.0032349 | 0.00097624 | -1.3927 | 0.065238 | -0.00028199 | 0.0046399 | -0.00066231 | -0.041199 | 60.1959 | -61.0291 | 60.6995 | -60.791 | -61.2488 | -61.322 | 0.004578 | 60.1913 | -61.1252 | 60.4431 | -61.0748 | -61.1481 | -61.3495 | 0.064087 | -0.21515 | 0.28839 | 0.30212 | -0.22888 | -0.15564 | -0.29297 | -0.21973 | -0.032043 | -0.21973 | 0.032043 | 0.018311 | -0.25635 | -0.054931 | -0.2243 | -0.022888 | 0.23804 | 121.7285 | 0.050354 | 121.5683 | 121.225 | 121.3165 | 121.2891 | 121.2845 | -121.4401 | -121.5363 | 121.7926 | 121.5363 | 61.0519 | 61.0977
154.4688 | 121.8796 | -61.0977 | 60.3607 | 0.0019074 | 0 | 0.067526 | 0.064783 | 0.0041229 | 7.0564e-05 | -0.00087583 | 0.00018312 | -9.1956e-05 | -1.3948 | 0.069084 | 0.0022814 | 0.0065625 | -0.0021575 | -0.027466 | 60.1501 | -61.0153 | 60.6995 | -60.8276 | -61.2717 | -61.3449 | -0.013733 | 60.1273 | -61.1343 | 60.4706 | -61.0657 | -61.1618 | -61.3083 | 0.082397 | -0.21057 | 0.33875 | 0.27008 | -0.24719 | -0.17395 | -0.32959 | -0.25635 | -0.036621 | -0.23346 | 0.10986 | 0.032043 | -0.21057 | -0.064087 | -0.17395 | -0.027466 | 0.18768 | 121.7148 | 0.068664 | 121.6049 | 121.1655 | 121.2616 | 121.2479 | 121.225 | -121.376 | -121.4951 | 121.7972 | 121.5683 | 61.0703 | 61.084
156.1719 | 121.7834 | -61.1069 | 60.498 | 0.047683 | 0 | 0.065604 | 0.065211 | -0.00057689 | -0.00099764 | 0.0019012 | 0.021545 | 0.0063168 | -1.3937 | 0.061393 | -0.0037 | 0.0046399 | -0.0017303 | 0.018311 | 60.2829 | -61.0062 | 60.6857 | -60.8368 | -61.235 | -61.2991 | -0.041199 | 60.2783 | -61.1023 | 60.4294 | -61.0977 | -61.1481 | -61.3312 | 0.10071 | -0.21515 | 0.18768 | 0.27008 | -0.19226 | -0.12817 | -0.29297 | -0.22888 | 0.004578 | -0.21973 | -0.068665 | 0.009156 | -0.2243 | -0.041198 | -0.22888 | -0.045776 | 0.16937 | 121.6919 | 0.004578 | 121.5317 | 121.2891 | 121.3806 | 121.3898 | 121.3852 | -121.5042 | -121.6003 | 121.7926 | 121.5363 | 61.1252 | 61.0657
157.8438 | 121.7468 | -61.0703 | 60.498 | -0.0057221 | 0 | 0.066458 | 0.066492 | -0.0031403 | -0.0012112 | 0.00019217 | 0.021545 | 0.0011898 | -1.3908 | 0.063529 | -0.0032728 | 0.0042127 | -0.00087591 | -0.022888 | 60.2783 | -60.9924 | 60.6766 | -60.8414 | -61.2259 | -61.29 | -0.041199 | 60.3149 | -61.116 | 60.3882 | -61.1114 | -61.1618 | -61.3266 | 0.077819 | -0.21973 | 0.17853 | 0.22888 | -0.21973 | -0.15564 | -0.29755 | -0.23346 | -0.045777 | -0.18311 | -0.10986 | -0.041199 | -0.25635 | -0.091553 | -0.21057 | -0.045776 | 0.15106 | 121.669 | 0.004578 | 121.5042 | 121.2708 | 121.431 | 121.3486 | 121.3852 | -121.4905 | -121.6141 | 121.7468 | 121.4584 | 61.0474 | 61.0291
159.5156 | 121.7422 | -61.1526 | 60.4523 | 0.0019074 | 0 | 0.066031 | 0.064783 | -0.0010041 | 7.0564e-05 | 0.0016876 | -0.0059205 | 0.0020444 | -1.3935 | 0.056907 | -6.8386e-05 | 0.0037855 | 0.0012603 | -0.068665 | 60.1959 | -61.0245 | 60.5988 | -60.9283 | -61.3541 | -61.4273 | -0.13275 | 60.2142 | -61.1435 | 60.3378 | -61.1847 | -61.2717 | -61.3998 | 0.12817 | -0.25635 | 0.14648 | 0.2243 | -0.27466 | -0.20142 | -0.40283 | -0.32959 | 0.009155 | -0.23804 | -0.11444 | -0.032043 | -0.24719 | -0.11902 | -0.25635 | -0.12817 | 0.09613 | 121.6232 | -0.041198 | 121.4813 | 121.2204 | 121.3577 | 121.3486 | 121.3669 | -121.4767 | -121.5958 | 121.7514 | 121.4905 | 61.084 | 61.0199
161.1875 | 121.7651 | -61.116 | 60.4614 | 0.0019074 | 0 | 0.06539 | 0.066706 | 0.0011321 | -0.00099764 | 0.00019217 | 0.00018312 | 0.001617 | -1.394 | 0.065666 | 0.0016406 | 0.0061353 | -0.0021575 | -0.009155 | 60.2188 | -61.0336 | 60.6628 | -60.8459 | -61.2762 | -61.3632 | -0.041199 | 60.2371 | -61.1252 | 60.3882 | -61.1343 | -61.2076 | -61.3632 | 0.082398 | -0.24262 | 0.20142 | 0.27008 | -0.24719 | -0.16022 | -0.32959 | -0.24262 | -0.009155 | -0.2243 | -0.073242 | -0.01831 | -0.24719 | -0.091553 | -0.23804 | -0.082398 | 0.18768 | 121.6965 | -0.009155 | 121.5134 | 121.2524 | 121.3623 | 121.3348 | 121.3531 | -121.4951 | -121.5866 | 121.7789 | 121.5042 | 61.1069 | 61.0748
162.8594 | 121.7377 | -61.0886 | 60.5164 | -0.0057221 | 0 | 0.063895 | 0.064356 | -0.0022857 | -0.0027066 | 0.00061957 | 0.00018312 | 0.0018306 | -1.3922 | 0.062461 | -0.0043408 | 0.0061353 | 0.0025421 | -0.022888 | 60.2646 | -60.9787 | 60.6583 | -60.8505 | -61.2488 | -61.322 | -0.064087 | 60.26 | -61.0886 | 60.4065 | -61.084 | -61.1481 | -61.3312 | 0.10986 | -0.25177 | 0.14191 | 0.23804 | -0.23346 | -0.16022 | -0.34332 | -0.27008 | 0 | -0.25635 | -0.10986 | 0.004578 | -0.24261 | -0.059509 | -0.24261 | -0.059509 | 0.12817 | 121.637 | 0.004578 | 121.4951 | 121.2433 | 121.3486 | 121.3531 | 121.3486 | -121.4951 | -121.6049 | 121.7468 | 121.4951 | 61.0657 | 61.0245
164.5312 | 121.8338 | -61.0703 | 60.4889 | -0.0057221 | 0 | 0.067099 | 0.06222 | -0.0033539 | -0.00099764 | 0.00061957 | -0.0059205 | 0.0011898 | -1.3946 | 0.069511 | -0.0032728 | 0.0050671 | 0.0012603 | 0.032043 | 60.2051 | -60.9558 | 60.7773 | -60.7315 | -61.1618 | -61.2534 | 0.068665 | 60.2234 | -61.0611 | 60.5072 | -60.9741 | -61.0382 | -61.2579 | 0.11444 | -0.28381 | 0.28839 | 0.33874 | -0.18311 | -0.091553 | -0.29755 | -0.20599 | 0.009155 | -0.2655 | 0.01831 | 0.09613 | -0.18768 | 0.032043 | -0.19684 | 0.022888 | 0.2243 | 121.7331 | 0.086975 | 121.5683 | 121.1609 | 121.2845 | 121.2753 | 121.2936 | -121.4447 | -121.55 | 121.8475 | 121.5775 | 61.1023 | 61.1389
166.2344 | 121.8704 | -61.0977 | 60.3836 | 0.0019074 | 0 | 0.065176 | 0.063288 | 0.0024139 | 7.0564e-05 | -0.00044863 | -0.0059205 | 0.00097624 | -1.3944 | 0.067588 | 0.00057241 | 0.0065625 | -0.0032257 | -0.041199 | 60.1501 | -61.0199 | 60.672 | -60.8368 | -61.2762 | -61.3541 | -0.013733 | 60.1456 | -61.1389 | 60.4568 | -61.0565 | -61.1481 | -61.3083 | 0.07782 | -0.23346 | 0.28839 | 0.26093 | -0.25635 | -0.17853 | -0.33417 | -0.25635 | -0.041199 | -0.23804 | 0.073242 | 0.041198 | -0.21057 | -0.050354 | -0.16937 | -0.009155 | 0.1831 | 121.6919 | 0.082397 | 121.5958 | 121.17 | 121.2845 | 121.2479 | 121.2433 | -121.4035 | -121.5225 | 121.7697 | 121.5546 | 61.0565 | 61.084
167.9688 | 121.8201 | -61.0931 | 60.4385 | 0.040054 | 0 | 0.066031 | 0.065424 | 0.0028411 | -0.00057044 | -0.00087583 | 0.0093383 | -0.00094636 | -1.3912 | 0.06652 | 0.00057241 | 0.0057081 | -0.0023713 | -0.045776 | 60.173 | -61.0336 | 60.6812 | -60.8185 | -61.2534 | -61.3266 | -0.022888 | 60.1776 | -61.1526 | 60.4477 | -61.0748 | -61.1298 | -61.3266 | 0.05951 | -0.2655 | 0.24261 | 0.27466 | -0.23346 | -0.16022 | -0.29297 | -0.21973 | -0.059509 | -0.26093 | 0.009155 | 0.018311 | -0.23346 | -0.036621 | -0.17395 | 0.022888 | 0.21515 | 121.7148 | 0.07782 | 121.6003 | 121.2067 | 121.3303 | 121.2662 | 121.2708 | -121.4722 | -121.5912 | 121.7743 | 121.5408 | 61.0474 | 61.0703
169.6562 | 121.843 | -61.084 | 60.4477 | 0.0095369 | 0 | 0.06539 | 0.065211 | 0.0017731 | -0.0012112 | -0.00087583 | -0.0028687 | 0.00012184 | -1.3942 | 0.069724 | -0.0022046 | 0.0067761 | 0.0012603 | -0.041199 | 60.1822 | -60.9924 | 60.6812 | -60.8093 | -61.235 | -61.3174 | -0.013733 | 60.2005 | -61.0931 | 60.4752 | -61.0107 | -61.0931 | -61.2762 | 0.091552 | -0.2655 | 0.23346 | 0.27466 | -0.23346 | -0.15106 | -0.32501 | -0.24261 | -0.009156 | -0.24719 | 0.027466 | 0.073242 | -0.19226 | -0.009156 | -0.18311 | 0 | 0.18311 | 121.6736 | 0.082398 | 121.5683 | 121.1746 | 121.2936 | 121.2662 | 121.2845 | -121.4401 | -121.5408 | 121.7651 | 121.5591 | 61.0428 | 61.0703
171.3281 | 121.8155 | -61.0336 | 60.5026 | 0.0019074 | 0 | 0.066031 | 0.064997 | -0.0037811 | -0.0016384 | -0.00044863 | 0.00018312 | 0.0014034 | -1.3929 | 0.062461 | -0.0049818 | 0.0052807 | 0.0027557 | 0.045776 | 60.2234 | -60.9604 | 60.7727 | -60.7407 | -61.1618 | -61.2579 | 0.032043 | 60.2509 | -61.0794 | 60.4614 | -61.0199 | -61.0977 | -61.2808 | 0.073242 | -0.27924 | 0.27008 | 0.29297 | -0.22431 | -0.12817 | -0.29755 | -0.20142 | -0.045777 | -0.25177 | -0.041199 | 0.013733 | -0.24719 | -0.064087 | -0.20142 | -0.01831 | 0.21973 | 121.7331 | 0.05951 | 121.5408 | 121.1838 | 121.3303 | 121.257 | 121.2845 | -121.463 | -121.582 | 121.8063 | 121.4951 | 61.0794 | 61.0657
173 | 121.8704 | -61.0474 | 60.4431 | 0.0019074 | 0 | 0.064963 | 0.06457 | -0.0024995 | 7.0564e-05 | 0.00040597 | 0.00018312 | 0.00033544 | -1.3952 | 0.068656 | -0.0011364 | 0.0048535 | 0.0014741 | -0.013733 | 60.173 | -60.9512 | 60.7498 | -60.7681 | -61.1755 | -61.2625 | 0.045776 | 60.2325 | -61.0748 | 60.5209 | -60.9695 | -61.0291 | -61.2213 | 0.09613 | -0.27008 | 0.3067 | 0.27924 | -0.21515 | -0.12817 | -0.31128 | -0.2243 | -0.027466 | -0.21057 | 0.07782 | 0.07782 | -0.17395 | 0.01831 | -0.14648 | 0.045776 | 0.18311 | 121.7011 | 0.10529 | 121.5958 | 121.1243 | 121.3074 | 121.2204 | 121.2799 | -121.3943 | -121.5179 | 121.7972 | 121.5683 | 61.0336 | 61.0931
174.6719 | 121.8842 | -61.0336 | 60.4431 | 0.0019074 | 0 | 0.06539 | 0.063929 | -0.0050629 | -0.0029202 | -0.00066223 | -0.0028687 | 0.00033544 | -1.3965 | 0.063316 | -0.0022046 | 0.0044263 | 0.0033967 | 0 | 60.1913 | -60.9512 | 60.759 | -60.7361 | -61.171 | -61.2534 | 0.082397 | 60.1868 | -61.084 | 60.5392 | -60.9512 | -61.0245 | -61.235 | 0.082397 | -0.25177 | 0.31586 | 0.29755 | -0.21973 | -0.13733 | -0.30212 | -0.21973 | -0.050354 | -0.25635 | 0.096131 | 0.082397 | -0.20142 | 0.009155 | -0.15106 | 0.059509 | 0.21515 | 121.7102 | 0.13275 | 121.6232 | 121.1426 | 121.2708 | 121.225 | 121.2204 | -121.3943 | -121.5271 | 121.7926 | 121.5729 | 61.0336 | 61.116
176.375 | 121.7422 | -61.084 | 60.5164 | -0.0057221 | 0 | 0.063681 | 0.065851 | 0.0032685 | -0.0039884 | -0.00087583 | -0.0028687 | 0.0020444 | -1.3946 | 0.063529 | -0.0034864 | 0.0046399 | 0.0021149 | 0.022888 | 60.2325 | -60.965 | 60.6995 | -60.8093 | -61.2167 | -61.2991 | -0.022888 | 60.2646 | -61.0703 | 60.3973 | -61.084 | -61.1298 | -61.322 | 0.11902 | -0.28381 | 0.18311 | 0.27466 | -0.21515 | -0.13275 | -0.33417 | -0.25177 | 0.013733 | -0.25177 | -0.11902 | 0 | -0.23804 | -0.045777 | -0.25177 | -0.05951 | 0.15564 | 121.6644 | -0.013733 | 121.4676 | 121.1975 | 121.3348 | 121.3165 | 121.3486 | -121.4813 | -121.5866 | 121.7834 | 121.4813 | 61.1069 | 61.0611
178.1094 | 121.756 | -61.0794 | 60.4889 | 0.047683 | 0 | 0.066031 | 0.066492 | -0.0027131 | -0.001852 | -0.00044863 | 0.015442 | 0.003967 | -1.3927 | 0.05947 | -0.0039136 | 0.0072035 | -0.0015167 | 0.022888 | 60.2966 | -61.0199 | 60.6766 | -60.8505 | -61.2488 | -61.322 | -0.041199 | 60.2921 | -61.1298 | 60.4111 | -61.0886 | -61.1572 | -61.3266 | 0.05951 | -0.19226 | 0.18768 | 0.22888 | -0.24261 | -0.16937 | -0.30212 | -0.22888 | -0.050354 | -0.19684 | -0.07782 | -0.009155 | -0.24719 | -0.07782 | -0.19684 | -0.027466 | 0.16937 | 121.6965 | 0.041199 | 121.5408 | 121.3165 | 121.4218 | 121.376 | 121.3715 | -121.5088 | -121.6187 | 121.756 | 121.4905 | 61.1023 | 61.0382
179.8438 | 121.8155 | -61.0931 | 60.4431 | 0.032425 | 0 | 0.065604 | 0.064142 | -0.0027131 | -0.0014248 | 0.001474 | 0.00018312 | 0.00076264 | -1.3965 | 0.071006 | -0.0015638 | 0.0059217 | -0.00044851 | -0.050354 | 60.2097 | -61.0062 | 60.6903 | -60.8231 | -61.2534 | -61.322 | -0.036621 | 60.2005 | -61.1252 | 60.4294 | -61.0748 | -61.1389 | -61.322 | 0.086975 | -0.23346 | 0.24719 | 0.27008 | -0.22888 | -0.16022 | -0.31586 | -0.24719 | -0.032043 | -0.24262 | -0.013733 | 0.018311 | -0.22888 | -0.045776 | -0.19684 | -0.013733 | 0.18311 | 121.6965 | 0.050354 | 121.5546 | 121.2158 | 121.3257 | 121.3028 | 121.2936 | -121.4493 | -121.5683 | 121.7834 | 121.5225 | 61.0428 | 61.0565
181.5156 | 121.7422 | -61.0657 | 60.4935 | -0.0057221 | 0 | 0.062186 | 0.06756 | 0.0015595 | -0.0037746 | -0.0015166 | 0.021545 | 0.0018306 | -1.3908 | 0.065452 | -0.0043408 | 0.0033581 | -0.0019439 | 0 | 60.2737 | -61.0291 | 60.6812 | -60.8231 | -61.2259 | -61.3083 | -0.054932 | 60.3149 | -61.1206 | 60.4065 | -61.1069 | -61.1526 | -61.3174 | 0.036621 | -0.21973 | 0.18768 | 0.24262 | -0.24262 | -0.16022 | -0.27924 | -0.19684 | -0.054931 | -0.17853 | -0.086975 | -0.041199 | -0.25177 | -0.086975 | -0.19684 | -0.032044 | 0.20599 | 121.7102 | 0.013732 | 121.5271 | 121.3028 | 121.4355 | 121.3394 | 121.3806 | -121.5225 | -121.6141 | 121.7468 | 121.4722 | 61.0657 | 61.0107
183.1875 | 121.8246 | -61.0703 | 60.4431 | 0.017166 | 0 | 0.066672 | 0.066065 | 0.00027771 | 0.00049776 | -0.001303 | 0.00018312 | -0.00051916 | -1.3952 | 0.066093 | -0.0011364 | 0.0054945 | -0.0010895 | -0.041199 | 60.1868 | -61.0016 | 60.6766 | -60.8276 | -61.2488 | -61.3266 | -0.032043 | 60.2005 | -61.116 | 60.4477 | -61.0336 | -61.1114 | -61.2854 | 0.068664 | -0.25635 | 0.23346 | 0.24261 | -0.25635 | -0.17853 | -0.32501 | -0.24719 | -0.045777 | -0.24262 | 0.004578 | 0.036621 | -0.21515 | -0.041199 | -0.16937 | 0.004578 | 0.17395 | 121.6782 | 0.082398 | 121.5637 | 121.1884 | 121.3165 | 121.257 | 121.2708 | -121.4447 | -121.5591 | 121.7468 | 121.5179 | 61.0291 | 61.0382
184.8906 | 121.8613 | -61.0474 | 60.4523 | -0.0057221 | 0 | 0.063254 | 0.064356 | -0.0016449 | -0.0012112 | -2.1434e-05 | -0.0028687 | 0.00076264 | -1.3946 | 0.062675 | -0.0028454 | 0.0078443 | -0.0013031 | 0.027466 | 60.1868 | -60.9695 | 60.7773 | -60.6949 | -61.1389 | -61.2259 | 0.1236 | 60.2097 | -61.0474 | 60.5118 | -60.9421 | -61.0245 | -61.2167 | 0.07782 | -0.2655 | 0.32501 | 0.35248 | -0.17853 | -0.091553 | -0.25635 | -0.16937 | 0 | -0.24262 | 0.059509 | 0.10528 | -0.16937 | 0.022888 | -0.16937 | 0.022888 | 0.27466 | 121.7468 | 0.10528 | 121.5591 | 121.1563 | 121.257 | 121.2341 | 121.257 | -121.4218 | -121.4996 | 121.8246 | 121.5591 | 61.0748 | 61.171
186.5781 | 121.875 | -61.0611 | 60.4385 | 0.017166 | 0 | 0.066031 | 0.064356 | -0.0016449 | -0.0020658 | -0.0021576 | 0.00018312 | -0.001801 | -1.3957 | 0.064811 | -0.0022046 | 0.0048535 | 0.0019013 | 0.009155 | 60.2142 | -61.0062 | 60.7636 | -60.7452 | -61.1847 | -61.2534 | 0.068665 | 60.1913 | -61.0886 | 60.5164 | -60.9604 | -61.0336 | -61.2076 | 0.054931 | -0.22431 | 0.32501 | 0.31586 | -0.19226 | -0.1236 | -0.24719 | -0.17853 | -0.027466 | -0.24719 | 0.077819 | 0.10071 | -0.14648 | 0.027466 | -0.11902 | 0.054932 | 0.26093 | 121.7697 | 0.12817 | 121.6049 | 121.2204 | 121.2799 | 121.2753 | 121.2524 | -121.4447 | -121.5271 | 121.8246 | 121.5775 | 61.0703 | 61.1298
188.3281 | 121.8613 | -61.0474 | 60.4431 | 0.0019074 | 0 | 0.063467 | 0.064783 | 0.00091851 | -0.0012112 | -0.001303 | -0.0089723 | 0.00054904 | -1.3952 | 0.06887 | -0.0024182 | 0.0048535 | 0.00040589 | -0.032043 | 60.1685 | -60.9924 | 60.7224 | -60.7452 | -61.1893 | -61.2579 | 0.027466 | 60.2188 | -61.0657 | 60.5026 | -60.9695 | -61.0428 | -61.235 | 0.054931 | -0.27466 | 0.27924 | 0.30212 | -0.21057 | -0.14191 | -0.2655 | -0.19684 | -0.018311 | -0.2243 | 0.05951 | 0.07782 | -0.18768 | 0.004577 | -0.16937 | 0.022888 | 0.24719 | 121.7148 | 0.096131 | 121.5683 | 121.1609 | 121.2845 | 121.2158 | 121.2662 | -121.4355 | -121.5088 | 121.7697 | 121.55 | 61.0153 | 61.0748
190.0312 | 121.8155 | -61.0977 | 60.4111 | 0.040054 | 0 | 0.066458 | 0.064997 | 0.00049131 | 0.00028416 | -0.0023712 | 0.015442 | 0.0018306 | -1.392 | 0.066947 | 0.00078621 | 0.0057081 | 0.00083309 | -0.018311 | 60.1822 | -61.0382 | 60.7361 | -60.7636 | -61.2305 | -61.3174 | 0.036621 | 60.2005 | -61.1526 | 60.4477 | -61.0611 | -61.1206 | -61.3129 | 0.059509 | -0.22888 | 0.32501 | 0.33417 | -0.21973 | -0.13275 | -0.27924 | -0.19226 | -0.054932 | -0.21057 | 0.036621 | 0.036621 | -0.21515 | -0.022888 | -0.16022 | 0.032044 | 0.27466 | 121.7743 | 0.091553 | 121.6003 | 121.2204 | 121.3531 | 121.2799 | 121.2982 | -121.4493 | -121.5637 | 121.8338 | 121.5454 | 61.0794 | 61.1343
191.7344 | 121.8201 | -61.1023 | 60.3973 | 0.047683 | 0 | 0.066458 | 0.066706 | -0.00057689 | 0.00049776 | -0.00066223 | 0.015442 | 0.001617 | -1.3929 | 0.071433 | -0.00049559 | 0.0069897 | 0.00083309 | -0.022888 | 60.173 | -61.0382 | 60.7269 | -60.7681 | -61.2396 | -61.3037 | 0.036621 | 60.1547 | -61.1526 | 60.4385 | -61.0703 | -61.1343 | -61.3129 | 0.064087 | -0.2243 | 0.32959 | 0.33417 | -0.20142 | -0.13733 | -0.2655 | -0.20142 | -0.050354 | -0.24262 | 0.041199 | 0.032044 | -0.21057 | -0.032043 | -0.16022 | 0.018311 | 0.27008 | 121.7651 | 0.082398 | 121.5912 | 121.2112 | 121.3074 | 121.2753 | 121.257 | -121.4355 | -121.55 | 121.8292 | 121.5408 | 61.0794 | 61.1389
193.4531 | 121.8613 | -61.1023 | 60.379 | 0.0019074 | 0 | 0.065176 | 0.065211 | 0.0026275 | 0.00049776 | -0.0015166 | -0.0059205 | -9.1956e-05 | -1.3929 | 0.068443 | 0.00014521 | 0.0063489 | -0.0023713 | -0.064087 | 60.1547 | -61.0382 | 60.6628 | -60.8597 | -61.2946 | -61.3632 | -0.027466 | 60.1639 | -61.1664 | 60.434 | -61.0657 | -61.1298 | -61.3037 | 0.064087 | -0.2243 | 0.28381 | 0.24262 | -0.26093 | -0.19226 | -0.32501 | -0.25635 | -0.064087 | -0.21515 | 0.054932 | 0.036621 | -0.20142 | -0.027466 | -0.13733 | 0.036621 | 0.17853 | 121.701 | 0.10071 | 121.6003 | 121.1929 | 121.3303 | 121.257 | 121.2662 | -121.4172 | -121.5454 | 121.7651 | 121.5363 | 61.0382 | 61.0748
195.1562 | 121.7285 | -61.0428 | 60.5118 | 0.0095369 | 0 | 0.062399 | 0.063715 | -0.0010041 | -0.0022794 | -0.00087583 | -0.0059205 | 0.0026852 | -1.3927 | 0.052421 | -0.0069044 | 0.0046399 | 0.00083309 | -0.013733 | 60.2646 | -61.0016 | 60.672 | -60.8322 | -61.2442 | -61.3358 | -0.059509 | 60.2783 | -61.0794 | 60.3928 | -61.0703 | -61.1526 | -61.3174 | 0.041199 | -0.24719 | 0.16022 | 0.21057 | -0.29297 | -0.20142 | -0.33417 | -0.24262 | -0.036621 | -0.23346 | -0.11902 | -0.027465 | -0.27466 | -0.10986 | -0.23804 | -0.073242 | 0.16937 | 121.6736 | 0.009156 | 121.4722 | 121.2662 | 121.3577 | 121.3074 | 121.3211 | -121.5134 | -121.5912 | 121.7148 | 121.4355 | 61.0291 | 60.9833
196.8438 | 121.7789 | -61.1023 | 60.4523 | 0.024795 | 0 | 0.064536 | 0.066706 | 0.0017731 | -0.0020658 | 0.0033966 | 0.0032349 | 0.0020444 | -1.3942 | 0.065025 | -0.0028454 | 0.0054945 | -0.0015167 | 0.018311 | 60.2417 | -61.0291 | 60.6949 | -60.8139 | -61.2442 | -61.3403 | -0.013733 | 60.2325 | -61.1206 | 60.4111 | -61.0657 | -61.1481 | -61.3174 | 0.073242 | -0.21057 | 0.24261 | 0.28839 | -0.23804 | -0.14191 | -0.31128 | -0.21515 | -0.01831 | -0.21973 | -0.041199 | 0.036621 | -0.21515 | -0.045776 | -0.19684 | -0.027466 | 0.21515 | 121.7239 | 0.054931 | 121.5317 | 121.2708 | 121.3531 | 121.344 | 121.3348 | -121.4813 | -121.5729 | 121.7972 | 121.5134 | 61.1206 | 61.0886
198.5156 | 121.8292 | -61.1069 | 60.3653 | 0.0095369 | 0 | 0.067099 | 0.065424 | 0.0026275 | 7.0564e-05 | 0.00061957 | 0.00018312 | 0.00097624 | -1.3967 | 0.069511 | -0.00070919 | 0.0059217 | 0.0021149 | -0.091553 | 60.173 | -61.0199 | 60.6445 | -60.8688 | -61.3129 | -61.3815 | -0.050354 | 60.1547 | -61.1572 | 60.4294 | -61.0703 | -61.1389 | -61.2991 | 0.086976 | -0.19226 | 0.27924 | 0.23804 | -0.27466 | -0.20599 | -0.36163 | -0.29297 | -0.050354 | -0.21057 | 0.064087 | 0.036622 | -0.19226 | -0.032043 | -0.14191 | 0.018311 | 0.15106 | 121.6644 | 0.086976 | 121.5866 | 121.1929 | 121.312 | 121.2799 | 121.2616 | -121.3852 | -121.5225 | 121.7514 | 121.5363 | 61.0153 | 61.0565
200.2656 | 121.8109 | -61.0794 | 60.4156 | 0.040054 | 0 | 0.066245 | 0.066279 | -0.0014313 | 0.00049776 | -2.1434e-05 | 0.01239 | 0.0018306 | -1.3914 | 0.066734 | -0.00049559 | 0.0063489 | -0.0025849 | -0.045776 | 60.1639 | -61.0199 | 60.6857 | -60.7773 | -61.2579 | -61.3174 | -0.022888 | 60.1959 | -61.116 | 60.4294 | -61.0748 | -61.116 | -61.3083 | 0.05951 | -0.25177 | 0.27008 | 0.30212 | -0.23804 | -0.17853 | -0.29755 | -0.23804 | -0.036621 | -0.21973 | 0.013733 | 0.004578 | -0.22888 | -0.036621 | -0.19226 | 0 | 0.24261 | 121.7056 | 0.041199 | 121.5454 | 121.1838 | 121.312 | 121.2433 | 121.2753 | -121.4355 | -121.5317 | 121.7651 | 121.5088 | 61.0336 | 61.0565
201.9531 | 121.8063 | -61.0977 | 60.4248 | 0.024795 | 0 | 0.064749 | 0.066065 | -0.0016449 | -0.0014248 | -0.00044863 | 0.0062865 | 0.0014034 | -1.3931 | 0.060325 | -0.0024182 | 0.0067761 | 0.00083309 | -0.050354 | 60.1913 | -61.0245 | 60.6903 | -60.8276 | -61.2625 | -61.3266 | -0.050354 | 60.1822 | -61.0977 | 60.4248 | -61.0703 | -61.1252 | -61.29 | 0.073242 | -0.23346 | 0.2655 | 0.27008 | -0.22888 | -0.16479 | -0.30212 | -0.23804 | 0 | -0.24262 | 0 | 0.027466 | -0.19226 | -0.027466 | -0.19226 | -0.027466 | 0.19684 | 121.7148 | 0.027466 | 121.5225 | 121.2158 | 121.2799 | 121.2891 | 121.2799 | -121.4493 | -121.5225 | 121.788 | 121.5225 | 61.0474 | 61.0474
203.625 | 121.8109 | -61.1023 | 60.3973 | 0.055313 | 0 | 0.066245 | 0.066279 | -0.0010041 | 0.0019932 | -0.00023503 | 0.0093383 | 0.0026852 | -1.3961 | 0.067802 | -0.0022046 | 0.0046399 | 0.0027557 | -0.018311 | 60.1685 | -61.0519 | 60.704 | -60.7681 | -61.2488 | -61.3083 | 0.009155 | 60.1547 | -61.1526 | 60.4477 | -61.0657 | -61.1343 | -61.2991 | 0.050354 | -0.22888 | 0.3067 | 0.33417 | -0.20599 | -0.14648 | -0.25635 | -0.19684 | -0.050354 | -0.24262 | 0.050354 | 0.036621 | -0.19684 | -0.032043 | -0.14648 | 0.018311 | 0.28381 | 121.756 | 0.086975 | 121.6003 | 121.2204 | 121.3074 | 121.2708 | 121.257 | -121.4493 | -121.55 | 121.8063 | 121.55 | 61.084 | 61.1114
205.375 | 121.7697 | -61.084 | 60.4477 | 0.024795 | 0 | 0.066031 | 0.065851 | 0.0036957 | 7.0564e-05 | 0.00019217 | 0.00018312 | 0.0037532 | -1.3918 | 0.061607 | -0.0028454 | 0.0061353 | -0.0010895 | 0.013733 | 60.2463 | -61.0107 | 60.6949 | -60.8093 | -61.2534 | -61.3449 | -0.009155 | 60.2234 | -61.1206 | 60.4019 | -61.0886 | -61.1572 | -61.3129 | 0.073242 | -0.20142 | 0.24719 | 0.27466 | -0.26093 | -0.16937 | -0.33417 | -0.24262 | -0.036621 | -0.2243 | -0.045776 | -0.004578 | -0.22888 | -0.073243 | -0.19226 | -0.036622 | 0.20142 | 121.7056 | 0.032043 | 121.5225 | 121.257 | 121.344 | 121.3303 | 121.3074 | -121.4584 | -121.5683 | 121.7789 | 121.4859 | 61.0977 | 61.0748
207.0625 | 121.8521 | -61.1069 | 60.3928 | -0.0057221 | 0 | 0.066458 | 0.063715 | -0.00079049 | -0.001852 | 0.00083317 | -0.0028687 | 0.00097624 | -1.3922 | 0.06652 | 0.00014521 | 0.0061353 | 0.0016877 | -0.036621 | 60.1318 | -61.0153 | 60.6812 | -60.7864 | -61.2625 | -61.3495 | 0.027466 | 60.1501 | -61.171 | 60.4523 | -61.0428 | -61.116 | -61.29 | 0.091553 | -0.26093 | 0.28839 | 0.32044 | -0.24261 | -0.15564 | -0.33417 | -0.24719 | -0.064086 | -0.24262 | 0.05951 | 0.064087 | -0.1831 | -0.009155 | -0.11902 | 0.054931 | 0.22888 | 121.6965 | 0.12817 | 121.6232 | 121.1472 | 121.3211 | 121.2387 | 121.257 | -121.4081 | -121.5637 | 121.788 | 121.5591 | 61.0703 | 61.1343
208.7344 | 121.8246 | -61.0886 | 60.3836 | -0.0057221 | 0 | 0.066458 | 0.062861 | -0.0033539 | 0.00092496 | 0.0023286 | 0.015442 | 0.003326 | -1.3922 | 0.060966 | 0.0024952 | 0.0080579 | 0.0010467 | -0.032043 | 60.1273 | -61.0336 | 60.7315 | -60.7636 | -61.2076 | -61.3083 | 0.041199 | 60.1501 | -61.1526 | 60.4523 | -61.0291 | -61.1023 | -61.29 | 0.054932 | -0.25635 | 0.3479 | 0.32501 | -0.21973 | -0.11902 | -0.27466 | -0.17395 | -0.064087 | -0.23346 | 0.068665 | 0.059509 | -0.20142 | -0.013733 | -0.13733 | 0.050354 | 0.27008 | 121.7651 | 0.1236 | 121.6049 | 121.1609 | 121.3028 | 121.2158 | 121.2387 | -121.4172 | -121.5363 | 121.8201 | 121.5408 | 61.0565 | 61.1298
210.4219 | 121.8567 | -61.0291 | 60.4614 | 0.0019074 | 0 | 0.066031 | 0.062861 | -0.0018585 | -0.0027066 | -0.00066223 | -0.0028687 | 0.00012184 | -1.3931 | 0.065666 | -0.0051954 | 0.0042127 | -2.1314e-05 | 0.018311 | 60.2051 | -60.9329 | 60.7819 | -60.6766 | -61.1343 | -61.2213 | 0.11444 | 60.2097 | -61.0519 | 60.5072 | -60.9512 | -61.0153 | -61.2305 | 0.096131 | -0.25635 | 0.32043 | 0.35248 | -0.19226 | -0.10529 | -0.28839 | -0.20142 | -0.022888 | -0.25177 | 0.045776 | 0.07782 | -0.20142 | 0.013733 | -0.17853 | 0.036621 | 0.25635 | 121.7148 | 0.10071 | 121.5591 | 121.138 | 121.2616 | 121.2341 | 121.2387 | -121.3943 | -121.5134 | 121.8109 | 121.5363 | 61.0474 | 61.1435
212.1094 | 121.8018 | -61.0703 | 60.4202 | 0.032425 | 0 | 0.066031 | 0.065211 | -0.0018585 | -0.00078404 | -0.00087583 | 0.0032349 | -0.00030556 | -1.392 | 0.063316 | -0.0024182 | 0.0063489 | -0.0023713 | -0.054932 | 60.1913 | -60.997 | 60.6857 | -60.8185 | -61.2442 | -61.3174 | -0.036621 | 60.2051 | -61.0977 | 60.4111 | -61.0748 | -61.1252 | -61.3174 | 0.073242 | -0.22888 | 0.2655 | 0.25177 | -0.24719 | -0.17395 | -0.32044 | -0.24719 | -0.027466 | -0.21515 | -0.009155 | -0.004578 | -0.24719 | -0.054932 | -0.21973 | -0.027466 | 0.17853 | 121.6827 | 0.022888 | 121.5088 | 121.1884 | 121.3028 | 121.2616 | 121.2753 | -121.4172 | -121.5179 | 121.756 | 121.4813 | 61.0153 | 61.0336
213.9062 | 121.7651 | -61.0886 | 60.4523 | 0.0095369 | 0 | 0.066885 | 0.067133 | 0.0054047 | -0.00035684 | 0.0016876 | -0.0028687 | 0.0014034 | -1.3922 | 0.06182 | -0.0039136 | 0.0042127 | 0.0012603 | 0.018311 | 60.2234 | -60.997 | 60.6857 | -60.8368 | -61.2854 | -61.3403 | -0.009155 | 60.2325 | -61.1069 | 60.3928 | -61.084 | -61.171 | -61.3083 | 0.091553 | -0.22888 | 0.23346 | 0.25177 | -0.25177 | -0.19684 | -0.34332 | -0.28839 | -0.018311 | -0.21973 | -0.05951 | 0.004578 | -0.21973 | -0.082397 | -0.20142 | -0.064086 | 0.16022 | 121.6827 | 0.022889 | 121.4996 | 121.2204 | 121.3394 | 121.312 | 121.3211 | -121.4493 | -121.5591 | 121.7743 | 121.4813 | 61.1069 | 61.0794
215.5938 | 121.7651 | -61.084 | 60.4568 | 0.024795 | 0 | 0.06539 | 0.066279 | 0.00049131 | -0.00078404 | 0.00061957 | 0.0032349 | 0.0028988 | -1.3959 | 0.063529 | -0.0034864 | 0.0031445 | 0.0010467 | 0.009155 | 60.2234 | -60.997 | 60.6949 | -60.8002 | -61.2488 | -61.3403 | -0.013733 | 60.2417 | -61.116 | 60.3928 | -61.0886 | -61.1481 | -61.3174 | 0.086975 | -0.23346 | 0.23804 | 0.28381 | -0.25635 | -0.16479 | -0.34332 | -0.25177 | -0.032044 | -0.21515 | -0.064087 | -0.004578 | -0.23346 | -0.064087 | -0.20142 | -0.032043 | 0.19684 | 121.6919 | 0.027466 | 121.5088 | 121.2204 | 121.3577 | 121.3074 | 121.3257 | -121.4539 | -121.5729 | 121.7789 | 121.4767 | 61.0931 | 61.0703
217.3438 | 121.788 | -61.1069 | 60.4111 | 0.040054 | 0 | 0.065817 | 0.066279 | 0.0041229 | 7.0564e-05 | -0.00066223 | 0.0062865 | 0.001617 | -1.3948 | 0.063102 | -0.0024182 | 0.0057081 | 0.00019229 | -0.045776 | 60.1685 | -61.0382 | 60.6857 | -60.7636 | -61.2396 | -61.3174 | -0.004578 | 60.1913 | -61.1206 | 60.4248 | -61.0519 | -61.1252 | -61.2991 | 0.068665 | -0.24262 | 0.27466 | 0.34332 | -0.21057 | -0.13275 | -0.27924 | -0.20142 | -0.013732 | -0.21973 | 0.013733 | 0.054932 | -0.19226 | -0.01831 | -0.17853 | -0.004578 | 0.27466 | 121.7239 | 0.068664 | 121.5454 | 121.2067 | 121.3119 | 121.2753 | 121.2982 | -121.4493 | -121.5317 | 121.7926 | 121.5317 | 61.0611 | 61.1023
219.0469 | 121.7056 | -61.0565 | 60.5164 | -0.020981 | 0 | 0.064322 | 0.064142 | 0.00049131 | -0.0012112 | 0.00083317 | -0.0059205 | 0.003326 | -1.3944 | 0.062888 | -0.0039136 | 0.0029309 | 0.00040589 | -0.032043 | 60.26 | -60.9833 | 60.6445 | -60.8368 | -61.2488 | -61.3174 | -0.059509 | 60.2829 | -61.0794 | 60.3836 | -61.084 | -61.1435 | -61.3083 | 0.073243 | -0.25635 | 0.12817 | 0.21973 | -0.26093 | -0.19226 | -0.33417 | -0.2655 | -0.022888 | -0.23346 | -0.13275 | -0.027465 | -0.25177 | -0.086975 | -0.22888 | -0.064087 | 0.14648 | 121.6278 | -0.004577 | 121.463 | 121.2433 | 121.3623 | 121.3165 | 121.3394 | -121.4996 | -121.5958 | 121.7011 | 121.4401 | 61.0245 | 60.997
220.7344 | 121.8063 | -61.0703 | 60.4156 | 0.017166 | 0 | 0.064322 | 0.063502 | -0.0020721 | -0.0012112 | -0.0021576 | 0.00018312 | -0.00073276 | -1.3931 | 0.069724 | -0.0024182 | 0.0048535 | 0.0051057 | -0.041199 | 60.173 | -61.0153 | 60.6583 | -60.8093 | -61.2396 | -61.322 | -0.059509 | 60.1822 | -61.0977 | 60.4202 | -61.0428 | -61.0931 | -61.29 | 0.054931 | -0.24261 | 0.24262 | 0.26093 | -0.25177 | -0.16937 | -0.3067 | -0.2243 | -0.027466 | -0.23346 | 0.004578 | 0.027465 | -0.21973 | -0.022889 | -0.19226 | 0.004577 | 0.20599 | 121.6736 | 0.054931 | 121.5179 | 121.1884 | 121.2799 | 121.2433 | 121.2524 | -121.431 | -121.5134 | 121.7285 | 121.4905 | 61.0291 | 61.0107
222.4375 | 121.8704 | -61.0291 | 60.4706 | -0.0057221 | 0 | 0.061545 | 0.063288 | -0.0024995 | -0.0067654 | 0.00040597 | -0.012024 | -0.00073276 | -1.3944 | 0.06182 | -0.0026318 | 0.0042127 | -2.1314e-05 | 0.013733 | 60.1776 | -60.9512 | 60.7681 | -60.6812 | -61.1343 | -61.2259 | 0.10986 | 60.2097 | -61.0519 | 60.5255 | -60.9375 | -61.0016 | -61.2122 | 0.07782 | -0.29297 | 0.29755 | 0.3479 | -0.19684 | -0.10529 | -0.27466 | -0.1831 | -0.022888 | -0.26093 | 0.054932 | 0.091553 | -0.18311 | 0.027466 | -0.16022 | 0.050354 | 0.27008 | 121.7194 | 0.11444 | 121.5775 | 121.1288 | 121.2616 | 121.2067 | 121.2387 | -121.4218 | -121.5225 | 121.7972 | 121.5546 | 61.0428 | 61.1389
224.25 | 121.7422 | -61.1343 | 60.3836 | -0.0057221 | 0 | 0.065604 | 0.065638 | 0.0017731 | -0.00035684 | 0.00019217 | -0.0028687 | 0.001617 | -1.3927 | 0.062675 | -0.00070919 | 0.0044263 | 0.00061949 | -0.091553 | 60.1959 | -61.0611 | 60.5621 | -60.9146 | -61.3541 | -61.4136 | -0.11902 | 60.1822 | -61.1481 | 60.3516 | -61.1572 | -61.235 | -61.3724 | 0.073242 | -0.18768 | 0.17853 | 0.21973 | -0.27924 | -0.21973 | -0.35248 | -0.29297 | -0.013733 | -0.20142 | -0.032044 | -0.022889 | -0.23804 | -0.10071 | -0.2243 | -0.086975 | 0.14648 | 121.6232 | -0.009156 | 121.4996 | 121.257 | 121.3303 | 121.3303 | 121.3165 | -121.4447 | -121.5317 | 121.6965 | 121.4859 | 61.0428 | 61.0153
226.0156 | 121.8475 | -61.0886 | 60.379 | 0.0019074 | 0 | 0.066458 | 0.065424 | 0.0049773 | 0.00028416 | 0.0016876 | -0.0028687 | -0.00116 | -1.3933 | 0.073783 | 0.00078621 | 0.0059217 | -0.0023713 | -0.022888 | 60.1044 | -61.0245 | 60.6812 | -60.7956 | -61.2625 | -61.3449 | -0.009155 | 60.1318 | -61.1481 | 60.4431 | -61.0519 | -61.1252 | -61.2762 | 0.064087 | -0.27466 | 0.30212 | 0.29297 | -0.25635 | -0.17395 | -0.32043 | -0.23804 | -0.059509 | -0.24719 | 0.064087 | 0.036621 | -0.18768 | -0.036621 | -0.12817 | 0.022888 | 0.22888 | 121.7056 | 0.09613 | 121.5912 | 121.1288 | 121.2799 | 121.1929 | 121.2204 | -121.4035 | -121.5271 | 121.7697 | 121.5317 | 61.0657 | 61.0794
227.7969 | 121.7377 | -61.1206 | 60.4568 | 0.0019074 | 0 | 0.062613 | 0.064783 | 0.0032685 | -0.0027066 | -0.00044863 | -0.0028687 | 0.0035396 | -1.3931 | 0.056693 | -0.0045544 | 0.0059217 | -0.00087591 | -0.004578 | 60.2097 | -61.0199 | 60.6491 | -60.8505 | -61.2762 | -61.3678 | -0.045776 | 60.1913 | -61.0931 | 60.3699 | -61.1435 | -61.2167 | -61.3632 | 0.10071 | -0.24719 | 0.19226 | 0.27008 | -0.24719 | -0.15564 | -0.3479 | -0.25635 | 0.027465 | -0.2655 | -0.086975 | -0.022889 | -0.24262 | -0.096131 | -0.27008 | -0.1236 | 0.16937 | 121.669 | -0.050354 | 121.463 | 121.2296 | 121.2845 | 121.3303 | 121.3119 | -121.4767 | -121.55 | 121.7697 | 121.4905 | 61.116 | 61.0748
229.4844 | 121.7468 | -61.0794 | 60.4614 | 0.047683 | 0 | 0.064749 | 0.066492 | 0.0028411 | -0.00035684 | 0.00061957 | 0.01239 | 0.0014034 | -1.3912 | 0.055839 | -0.0028454 | 0.0050671 | -0.0015167 | 0.009155 | 60.2783 | -61.0199 | 60.6812 | -60.8231 | -61.1984 | -61.29 | -0.032043 | 60.2783 | -61.1069 | 60.4156 | -61.0474 | -61.1389 | -61.2991 | 0.05951 | -0.18311 | 0.21973 | 0.25635 | -0.21057 | -0.11902 | -0.27008 | -0.17853 | -0.027466 | -0.18311 | -0.045777 | 0.032044 | -0.21973 | -0.059509 | -0.19226 | -0.032043 | 0.19684 | 121.701 | 0.05951 | 121.5225 | 121.2982 | 121.3852 | 121.3577 | 121.3577 | -121.4813 | -121.5683 | 121.7606 | 121.4951 | 61.0886 | 61.0474
231.25 | 121.7789 | -61.0748 | 60.4111 | 0.055313 | 0 | 0.067954 | 0.064142 | 0.0030547 | 0.0011386 | 0.0025422 | 0.0093383 | 0.0011898 | -1.3944 | 0.069084 | -0.0011364 | 0.0084851 | -2.1314e-05 | -0.036621 | 60.1593 | -61.0382 | 60.6674 | -60.7819 | -61.2396 | -61.3083 | 0 | 60.1913 | -61.1343 | 60.4111 | -61.0519 | -61.1206 | -61.3037 | 0.036621 | -0.25177 | 0.25635 | 0.29297 | -0.23346 | -0.16479 | -0.27008 | -0.20142 | -0.059509 | -0.21973 | 0 | 0.022888 | -0.22888 | -0.045776 | -0.16937 | 0.013733 | 0.25635 | 121.7056 | 0.082397 | 121.5454 | 121.1975 | 121.3257 | 121.2341 | 121.2662 | -121.4493 | -121.5454 | 121.7422 | 121.4859 | 61.0382 | 61.0748
233.0156 | 121.7972 | -61.0977 | 60.3973 | 0.0019074 | 0 | 0.065817 | 0.066706 | -0.0042083 | -0.0022794 | -0.001303 | 0.00018312 | 0.00054904 | -1.394 | 0.060325 | -0.0022046 | 0.0082715 | -0.0017303 | -0.091553 | 60.2005 | -61.0474 | 60.5713 | -60.8963 | -61.3403 | -61.4136 | -0.082397 | 60.1685 | -61.1435 | 60.379 | -61.1069 | -61.1618 | -61.322 | 0.050354 | -0.19684 | 0.17395 | 0.20142 | -0.31586 | -0.24261 | -0.36621 | -0.29297 | -0.045777 | -0.22888 | -0.018311 | -0.009156 | -0.2243 | -0.064087 | -0.17853 | -0.01831 | 0.15106 | 121.6187 | 0.036621 | 121.5225 | 121.2479 | 121.312 | 121.2982 | 121.2662 | -121.4447 | -121.5408 | 121.669 | 121.4767 | 61.0062 | 61.0153
234.7031 | 121.8201 | -61.0977 | 60.3745 | 0.040054 | 0 | 0.065604 | 0.06457 | -0.00036309 | 0.0037022 | -0.0010894 | 0.0093383 | 0.00097624 | -1.3918 | 0.054984 | 0.00014521 | 0.0076307 | -0.00023491 | -0.004578 | 60.173 | -61.0291 | 60.7086 | -60.7544 | -61.2259 | -61.2946 | 0.022888 | 60.1547 | -61.1435 | 60.434 | -61.0657 | -61.1069 | -61.29 | 0.068664 | -0.20142 | 0.33417 | 0.34332 | -0.19684 | -0.12817 | -0.2655 | -0.19684 | -0.045777 | -0.21973 | 0.059509 | 0.032043 | -0.19226 | -0.009156 | -0.14648 | 0.036621 | 0.27466 | 121.7377 | 0.07782 | 121.5775 | 121.2021 | 121.2982 | 121.2708 | 121.2524 | -121.4035 | -121.5179 | 121.8063 | 121.5317 | 61.0931 | 61.1206
236.4531 | 121.7972 | -61.0291 | 60.4706 | -0.0057221 | 0 | 0.064749 | 0.062433 | -0.0018585 | -0.0027066 | -0.0010894 | -0.0059205 | 0.00012184 | -1.3965 | 0.062675 | -0.004768 | 0.0054945 | -2.1314e-05 | 0.050354 | 60.1776 | -60.9467 | 60.7727 | -60.7224 | -61.1389 | -61.235 | 0.064087 | 60.2188 | -61.0382 | 60.4752 | -60.9833 | -61.0519 | -61.2579 | 0.082398 | -0.29297 | 0.30212 | 0.3067 | -0.20599 | -0.10986 | -0.28839 | -0.19226 | -0.009155 | -0.25177 | 0.004578 | 0.045777 | -0.22888 | -0.022888 | -0.21973 | -0.013733 | 0.2243 | 121.7194 | 0.054932 | 121.5134 | 121.1243 | 121.257 | 121.2067 | 121.2479 | -121.4172 | -121.5088 | 121.8018 | 121.5042 | 61.0794 | 61.0931
238.2344 | 121.8018 | -61.0703 | 60.4202 | 0.032425 | 0 | 0.066245 | 0.063288 | -0.00036309 | -0.00035684 | 0.0016876 | 0.0032349 | 0.00054904 | -1.3927 | 0.066947 | -0.00028199 | 0.0065625 | 0.0014741 | -0.054932 | 60.1868 | -61.0153 | 60.6583 | -60.8047 | -61.2396 | -61.3083 | -0.059509 | 60.1776 | -61.0931 | 60.4202 | -61.0291 | -61.0977 | -61.2762 | 0.054931 | -0.23346 | 0.23804 | 0.2655 | -0.23804 | -0.16937 | -0.29297 | -0.2243 | -0.022889 | -0.24261 | 0 | 0.041198 | -0.20599 | -0.027466 | -0.18311 | -0.004577 | 0.21057 | 121.6736 | 0.064087 | 121.5134 | 121.2021 | 121.2708 | 121.257 | 121.2479 | -121.4355 | -121.5134 | 121.7285 | 121.4905 | 61.0153 | 61.0107
239.9844 | 121.7972 | -61.0794 | 60.4111 | 0.024795 | 0 | 0.065817 | 0.063929 | 0.00091851 | -0.00078404 | 0.0012604 | 0.0093383 | 0.0024716 | -1.3933 | 0.067375 | -0.0011364 | 0.0059217 | 0.00019229 | -0.050354 | 60.1822 | -61.0062 | 60.6583 | -60.8093 | -61.2213 | -61.322 | -0.045776 | 60.1959 | -61.1298 | 60.4156 | -61.0748 | -61.1252 | -61.29 | 0.073242 | -0.22888 | 0.24719 | 0.27008 | -0.24261 | -0.14191 | -0.31586 | -0.21515 | -0.050354 | -0.21515 | 0.004577 | 0.004578 | -0.21057 | -0.045776 | -0.16022 | 0.004578 | 0.19684 | 121.6644 | 0.054932 | 121.5454 | 121.1884 | 121.3257 | 121.2616 | 121.2753 | -121.4172 | -121.5408 | 121.7377 | 121.4951 | 61.0291 | 61.0336
241.6719 | 121.8475 | -61.0382 | 60.4477 | -0.0057221 | 0 | 0.062186 | 0.062433 | -0.0031403 | -0.00078404 | 0.002115 | -0.0028687 | -0.00073276 | -1.3946 | 0.070579 | -0.0043408 | 0.0067761 | -0.0019439 | -0.022888 | 60.1776 | -60.9879 | 60.7224 | -60.7636 | -61.171 | -61.2488 | 0.032043 | 60.2188 | -61.0703 | 60.4889 | -60.9833 | -61.0107 | -61.2259 | 0.050354 | -0.27008 | 0.27466 | 0.27466 | -0.21057 | -0.13275 | -0.26093 | -0.18311 | -0.032043 | -0.22888 | 0.041199 | 0.054932 | -0.18768 | 0.027466 | -0.15564 | 0.059509 | 0.2243 | 121.7102 | 0.086975 | 121.5591 | 121.1655 | 121.2891 | 121.2158 | 121.257 | -121.4355 | -121.5179 | 121.7606 | 121.5271 | 61.0153 | 61.0703
243.4375 | 121.7514 | -61.1206 | 60.3882 | -0.0057221 | 0 | 0.066031 | 0.064997 | 0.0024139 | -0.0014248 | -0.00044863 | -0.0028687 | 0.002258 | -1.3955 | 0.065238 | 0.0012134 | 0.0069897 | -0.0025849 | -0.091553 | 60.1822 | -61.0565 | 60.5621 | -60.9192 | -61.3586 | -61.409 | -0.12817 | 60.1456 | -61.1389 | 60.3516 | -61.1343 | -61.2076 | -61.3403 | 0.064086 | -0.20599 | 0.17395 | 0.20142 | -0.28839 | -0.23804 | -0.35248 | -0.30212 | -0.018311 | -0.24262 | -0.036622 | -0.013733 | -0.21973 | -0.086976 | -0.20142 | -0.068665 | 0.13733 | 121.6187 | 0.004578 | 121.4905 | 121.2387 | 121.2845 | 121.3028 | 121.2662 | -121.4447 | -121.5271 | 121.6827 | 121.4722 | 61.0291 | 60.9924
245.1875 | 121.788 | -61.0977 | 60.4248 | 0.017166 | 0 | 0.066672 | 0.066706 | 0.0045501 | 7.0564e-05 | 0.0010468 | 0.01239 | 0.00012184 | -1.3929 | 0.064597 | 0.00014521 | 0.0054945 | 0.0023285 | -0.045776 | 60.173 | -61.0062 | 60.672 | -60.8047 | -61.2488 | -61.2991 | -0.036621 | 60.1776 | -61.1206 | 60.4065 | -61.0474 | -61.1023 | -61.29 | 0.091552 | -0.25177 | 0.24719 | 0.29297 | -0.20142 | -0.15106 | -0.29297 | -0.24261 | -0.022888 | -0.24719 | -0.018311 | 0.050354 | -0.19226 | -0.004578 | -0.16937 | 0.01831 | 0.20142 | 121.6782 | 0.073242 | 121.5271 | 121.1792 | 121.2982 | 121.2708 | 121.2753 | -121.431 | -121.5454 | 121.7697 | 121.5042 | 61.0519 | 61.0611
246.8906 | 121.7468 | -61.0519 | 60.4797 | -0.0057221 | 0 | 0.064322 | 0.064783 | -0.0031403 | -0.003561 | -2.1434e-05 | -0.0028687 | 0.0011898 | -1.3935 | 0.056907 | -0.0060498 | 0.0042127 | -2.1314e-05 | 0.050354 | 60.173 | -60.9329 | 60.7498 | -60.7315 | -61.1526 | -61.2579 | 0.027466 | 60.2234 | -61.0428 | 60.4202 | -61.0199 | -61.0886 | -61.2534 | 0.11902 | -0.3067 | 0.27008 | 0.32043 | -0.20599 | -0.10071 | -0.32501 | -0.21973 | 0.009155 | -0.25635 | -0.059509 | 0.032044 | -0.20142 | -0.036621 | -0.21057 | -0.045776 | 0.20142 | 121.6827 | 0.022889 | 121.463 | 121.106 | 121.2662 | 121.225 | 121.2753 | -121.4127 | -121.5225 | 121.8018 | 121.4722 | 61.1023 | 61.0794
248.6406 | 121.8613 | -61.0245 | 60.466 | 0.0019074 | 0 | 0.06539 | 0.063715 | -0.0027131 | -0.001852 | -0.001303 | -0.0028687 | 0.0014034 | -1.3929 | 0.071006 | -0.001991 | 0.0046399 | -0.00066231 | 0.009155 | 60.173 | -60.965 | 60.7498 | -60.6903 | -61.1389 | -61.2259 | 0.091553 | 60.1913 | -61.0611 | 60.5118 | -60.9329 | -60.9787 | -61.1984 | 0.059509 | -0.29297 | 0.28381 | 0.33417 | -0.20142 | -0.11444 | -0.26093 | -0.17395 | -0.036621 | -0.27466 | 0.045777 | 0.091553 | -0.17395 | 0.045776 | -0.13733 | 0.082397 | 0.27466 | 121.7148 | 0.12817 | 121.5729 | 121.138 | 121.2524 | 121.1975 | 121.2158 | -121.431 | -121.5271 | 121.7743 | 121.5363 | 61.0336 | 61.116
250.3438 | 121.6965 | -61.0931 | 60.4385 | 0.0019074 | 0 | 0.067526 | 0.066279 | 0.0026275 | -0.0020658 | -0.0021576 | -0.0028687 | 0.0018306 | -1.3935 | 0.068443 | -0.0013502 | 0.0067761 | 0.00019229 | -0.059509 | 60.2097 | -61.0382 | 60.585 | -60.9055 | -61.3449 | -61.4044 | -0.13275 | 60.228 | -61.1206 | 60.3241 | -61.1664 | -61.2488 | -61.377 | 0.054932 | -0.22888 | 0.14648 | 0.18768 | -0.31128 | -0.25177 | -0.36621 | -0.3067 | -0.027465 | -0.21057 | -0.11444 | -0.073242 | -0.28381 | -0.15564 | -0.25635 | -0.12817 | 0.13275 | 121.6232 | -0.045777 | 121.4447 | 121.2479 | 121.3486 | 121.3028 | 121.3211 | -121.4767 | -121.5591 | 121.6782 | 121.4172 | 61.0336 | 60.9604
252.1094 | 121.701 | -61.0657 | 60.5072 | 0.0019074 | 0 | 0.062613 | 0.065851 | 0.0047637 | -0.004202 | -0.001303 | 0.00018312 | 0.00076264 | -1.3927 | 0.062675 | -0.0051954 | 0.0033581 | 0.00040589 | -0.022888 | 60.2234 | -60.9787 | 60.6628 | -60.8185 | -61.2534 | -61.3266 | -0.059509 | 60.2463 | -61.0657 | 60.3745 | -61.0703 | -61.1298 | -61.2946 | 0.086975 | -0.28381 | 0.15564 | 0.24719 | -0.26093 | -0.18768 | -0.3479 | -0.27466 | 0 | -0.26093 | -0.13275 | -0.004577 | -0.22888 | -0.064087 | -0.22888 | -0.064087 | 0.16022 | 121.6415 | -0.004577 | 121.4401 | 121.2021 | 121.312 | 121.2891 | 121.312 | -121.4859 | -121.5729 | 121.7285 | 121.4401 | 61.0428 | 61.0062
253.8594 | 121.7239 | -61.1114 | 60.4385 | 0.0019074 | 0 | 0.066458 | 0.064997 | 0.00091851 | -0.00527 | -0.0010894 | -0.0028687 | 0.0014034 | -1.3925 | 0.057975 | -0.0015638 | 0.0044263 | 0.00040589 | -0.004578 | 60.1959 | -61.0016 | 60.6262 | -60.8368 | -61.29 | -61.3678 | -0.068665 | 60.2051 | -61.0977 | 60.3424 | -61.1114 | -61.203 | -61.3449 | 0.10986 | -0.24262 | 0.18768 | 0.27466 | -0.25635 | -0.17853 | -0.36621 | -0.28839 | 0.013733 | -0.23346 | -0.096131 | 0 | -0.23346 | -0.091553 | -0.24719 | -0.10529 | 0.16479 | 121.6278 | -0.013733 | 121.4401 | 121.1975 | 121.3028 | 121.3074 | 121.3165 | -121.4401 | -121.5363 | 121.7377 | 121.4539 | 61.1069 | 61.0428
255.5469 | 121.7102 | -61.1389 | 60.4156 | 0.0019074 | 0 | 0.062399 | 0.064356 | -0.0024995 | -0.0022794 | 0.0010468 | 0.00018312 | 0.0031124 | -1.3952 | 0.066734 | -0.001991 | 0.0061353 | -0.00066231 | -0.09613 | 60.1593 | -61.0611 | 60.5392 | -60.9467 | -61.3541 | -61.4227 | -0.16479 | 60.1913 | -61.1526 | 60.3195 | -61.1755 | -61.2259 | -61.3678 | 0.07782 | -0.25635 | 0.1236 | 0.19226 | -0.28381 | -0.21515 | -0.36163 | -0.29297 | -0.013733 | -0.2243 | -0.09613 | -0.036621 | -0.22888 | -0.086975 | -0.21515 | -0.073242 | 0.11444 | 121.6003 | -0.022888 | 121.4722 | 121.2204 | 121.344 | 121.2982 | 121.3303 | -121.4767 | -121.5683 | 121.6782 | 121.4584 | 61.0428 | 60.9741
257.2969 | 121.7285 | -61.1343 | 60.4248 | 0.0095369 | 0 | 0.06539 | 0.064997 | -0.00014949 | -0.00099764 | -0.00044863 | -0.0089723 | 0.0028988 | -1.3918 | 0.061607 | -0.0022046 | 0.0059217 | 0.0016877 | -0.091553 | 60.1822 | -61.0428 | 60.5438 | -60.9375 | -61.3861 | -61.4365 | -0.14191 | 60.1685 | -61.1252 | 60.3241 | -61.171 | -61.2259 | -61.3541 | 0.091552 | -0.24262 | 0.11902 | 0.19684 | -0.30212 | -0.25177 | -0.39368 | -0.34332 | 0.009155 | -0.25635 | -0.10071 | -0.036621 | -0.21973 | -0.091553 | -0.22888 | -0.10071 | 0.10529 | 121.5866 | -0.045776 | 121.4493 | 121.225 | 121.2936 | 121.3165 | 121.3028 | -121.4676 | -121.55 | 121.6782 | 121.4584 | 61.0428 | 60.9924
259 | 121.756 | -61.0565 | 60.4568 | 0.047683 | 0 | 0.066031 | 0.065851 | 0.0049773 | 0.00028416 | 0.001474 | 0.015442 | 0.0026852 | -1.3929 | 0.059898 | -0.001991 | 0.0046399 | -0.0034393 | 0.018311 | 60.2783 | -60.997 | 60.6674 | -60.791 | -61.1984 | -61.3083 | -0.027466 | 60.2554 | -61.1114 | 60.3928 | -61.0657 | -61.1252 | -61.29 | 0.05951 | -0.17853 | 0.21057 | 0.2655 | -0.25177 | -0.14191 | -0.31128 | -0.20142 | -0.054931 | -0.20142 | -0.064087 | -0.009155 | -0.23346 | -0.068664 | -0.17853 | -0.013733 | 0.20599 | 121.6644 | 0.045776 | 121.5042 | 121.2753 | 121.3669 | 121.3348 | 121.312 | -121.4539 | -121.5683 | 121.7239 | 121.4493 | 61.0748 | 61.0291
260.7031 | 121.701 | -61.1252 | 60.4248 | 0.0019074 | 0 | 0.067954 | 0.06457 | 0.0028411 | -0.0014248 | -0.0023712 | -0.0028687 | 0.00054904 | -1.3972 | 0.065452 | -0.0015638 | 0.0035719 | 0.00083309 | -0.10071 | 60.2005 | -61.0382 | 60.5392 | -60.9375 | -61.3724 | -61.4227 | -0.15106 | 60.1913 | -61.1389 | 60.3149 | -61.1664 | -61.235 | -61.3678 | 0.086975 | -0.22431 | 0.11444 | 0.18768 | -0.29755 | -0.24719 | -0.38452 | -0.33417 | -0.013733 | -0.23346 | -0.10986 | -0.041199 | -0.24262 | -0.10986 | -0.22888 | -0.09613 | 0.10071 | 121.5775 | -0.027466 | 121.4539 | 121.2387 | 121.3303 | 121.3257 | 121.3165 | -121.463 | -121.5637 | 121.6644 | 121.4401 | 61.0245 | 60.9741
262.4688 | 121.7789 | -61.084 | 60.3882 | 0.040054 | 0 | 0.067526 | 0.06457 | 0.0034821 | 0.00092496 | 0.00019217 | 0.015442 | 0.00012184 | -1.3929 | 0.068443 | -0.001991 | 0.0069897 | -0.00066231 | -0.027466 | 60.1868 | -61.0153 | 60.6903 | -60.759 | -61.2122 | -61.2854 | 0.022888 | 60.1456 | -61.1298 | 60.4202 | -61.0474 | -61.0977 | -61.2854 | 0.068664 | -0.20142 | 0.30212 | 0.32501 | -0.20142 | -0.12817 | -0.27008 | -0.19684 | -0.045777 | -0.24262 | 0.032043 | 0.036621 | -0.20142 | -0.013733 | -0.15564 | 0.032044 | 0.25635 | 121.7056 | 0.082398 | 121.55 | 121.2021 | 121.2753 | 121.2708 | 121.2296 | -121.4035 | -121.5179 | 121.7743 | 121.5042 | 61.0565 | 61.1069
264.1719 | 121.7606 | -61.0931 | 60.4477 | 0.032425 | 0 | 0.066245 | 0.065424 | 0.00091851 | 0.0011386 | -0.001303 | 0.015442 | 0.0026852 | -1.3925 | 0.057334 | -0.0015638 | 0.0046399 | 0.0023285 | 0.018311 | 60.2646 | -61.0107 | 60.6674 | -60.8002 | -61.2122 | -61.3037 | -0.004578 | 60.2417 | -61.0748 | 60.4019 | -61.0565 | -61.1114 | -61.2854 | 0.082398 | -0.18311 | 0.21973 | 0.29297 | -0.21057 | -0.11902 | -0.29297 | -0.20142 | 0.018311 | -0.20599 | -0.045776 | 0.036621 | -0.19226 | -0.01831 | -0.21057 | -0.036621 | 0.21057 | 121.6782 | 0.01831 | 121.4767 | 121.2753 | 121.3165 | 121.3577 | 121.3348 | -121.4584 | -121.5225 | 121.7606 | 121.4951 | 61.1115 | 61.0886
265.875 | 121.8201 | -61.084 | 60.3561 | -0.0057221 | 0 | 0.064322 | 0.065211 | 0.0019867 | -0.00078404 | 0.00061957 | -0.0028687 | -0.00030556 | -1.3935 | 0.057334 | -0.0011364 | 0.0074171 | -0.0030121 | -0.041199 | 60.1318 | -61.0153 | 60.64 | -60.7773 | -61.2579 | -61.322 | -0.004578 | 60.1273 | -61.1114 | 60.4385 | -61.0336 | -61.1069 | -61.2671 | 0.068664 | -0.2243 | 0.28381 | 0.3067 | -0.23804 | -0.17395 | -0.3067 | -0.24262 | -0.027466 | -0.22888 | 0.082398 | 0.050354 | -0.18311 | -0.022889 | -0.15564 | 0.004577 | 0.23804 | 121.6553 | 0.07782 | 121.55 | 121.1472 | 121.2387 | 121.2158 | 121.2112 | -121.3715 | -121.4676 | 121.7239 | 121.5225 | 61.0428 | 61.0794
267.5781 | 121.7468 | -61.0794 | 60.466 | 0.040054 | 0 | 0.06539 | 0.066492 | 0.0051911 | -0.00014304 | 0.00019217 | 0.01239 | 0.0024716 | -1.3929 | 0.064811 | -0.0045544 | 0.0063489 | 0.0021149 | 0.032043 | 60.2554 | -60.997 | 60.6583 | -60.8139 | -61.2213 | -61.2991 | -0.013733 | 60.2188 | -61.1069 | 60.3973 | -61.0519 | -61.1252 | -61.2625 | 0.082398 | -0.21057 | 0.19226 | 0.2655 | -0.21973 | -0.14191 | -0.30212 | -0.2243 | -0.027466 | -0.24719 | -0.068664 | 0.027466 | -0.1831 | -0.045776 | -0.15564 | -0.01831 | 0.1831 | 121.6553 | 0.054932 | 121.5042 | 121.2524 | 121.3257 | 121.3348 | 121.2982 | -121.463 | -121.5729 | 121.7377 | 121.4767 | 61.1115 | 61.0657
269.3281 | 121.8292 | -61.0611 | 60.379 | -0.020981 | 0 | 0.06539 | 0.063074 | -0.00014949 | 0.00028416 | 0.0025422 | -0.0028687 | 0.0011898 | -1.395 | 0.07122 | -6.8386e-05 | 0.010408 | -0.0021575 | -0.059509 | 60.1685 | -61.0245 | 60.6491 | -60.8231 | -61.2625 | -61.3266 | -0.013733 | 60.1273 | -61.116 | 60.4248 | -61.0428 | -61.1069 | -61.2534 | 0.036621 | -0.21057 | 0.27008 | 0.23804 | -0.2655 | -0.20142 | -0.30212 | -0.23804 | -0.054932 | -0.25177 | 0.045777 | 0.01831 | -0.19226 | -0.045777 | -0.13733 | 0.009155 | 0.20142 | 121.6736 | 0.073242 | 121.5408 | 121.1929 | 121.2433 | 121.2296 | 121.1884 | -121.4035 | -121.4951 | 121.7102 | 121.4859 | 61.0016 | 61.0474
271.0938 | 121.8155 | -61.084 | 60.4019 | -0.0057221 | 0 | 0.069022 | 0.064356 | 0.00091851 | 0.00092496 | 0.0025422 | 0.01239 | 0.0014034 | -1.3927 | 0.067375 | -0.001991 | 0.0052807 | -0.00044851 | -0.013733 | 60.1593 | -61.0336 | 60.704 | -60.759 | -61.2076 | -61.2946 | 0.032043 | 60.1593 | -61.1481 | 60.4431 | -61.0153 | -61.0931 | -61.2579 | 0.050354 | -0.24262 | 0.30212 | 0.32501 | -0.21057 | -0.1236 | -0.26093 | -0.17395 | -0.064087 | -0.24262 | 0.041198 | 0.068664 | -0.17395 | -0.009156 | -0.10986 | 0.054931 | 0.27466 | 121.7377 | 0.13275 | 121.5912 | 121.1929 | 121.3074 | 121.2433 | 121.2433 | -121.4355 | -121.55 | 121.788 | 121.5271 | 61.0703 | 61.116
272.7969 | 121.7743 | -61.1069 | 60.4019 | -0.013352 | 0 | 0.064963 | 0.065638 | 0.00091851 | -0.0022794 | -0.001944 | -0.0028687 | 0.0014034 | -1.3967 | 0.069724 | -0.0034864 | 0.0059217 | -0.00066231 | -0.086975 | 60.1868 | -61.0519 | 60.5667 | -60.9192 | -61.3266 | -61.4182 | -0.10071 | 60.1456 | -61.116 | 60.3699 | -61.1069 | -61.171 | -61.3312 | 0.054932 | -0.21515 | 0.16479 | 0.18768 | -0.31128 | -0.21973 | -0.36621 | -0.27466 | -0.009155 | -0.25635 | -0.032044 | 0 | -0.2243 | -0.064086 | -0.21515 | -0.054931 | 0.13275 | 121.6187 | 0.009155 | 121.4859 | 121.2387 | 121.2616 | 121.2936 | 121.2524 | -121.4539 | -121.5179 | 121.6736 | 121.4767 | 61.0199 | 61.0062
274.4844 | 121.6782 | -61.116 | 60.434 | -0.0057221 | 0 | 0.066245 | 0.066492 | 0.0047637 | -0.0012112 | 0.0012604 | 0.0032349 | 0.0024716 | -1.3916 | 0.065025 | -0.003059 | 0.0078443 | -0.00087591 | -0.059509 | 60.228 | -61.0336 | 60.5621 | -60.9146 | -61.3403 | -61.4227 | -0.15106 | 60.2051 | -61.1206 | 60.3195 | -61.171 | -61.2534 | -61.3632 | 0.082398 | -0.20599 | 0.12817 | 0.20142 | -0.3067 | -0.2243 | -0.3891 | -0.3067 | -0.004577 | -0.22888 | -0.11444 | -0.054931 | -0.24719 | -0.13733 | -0.24262 | -0.13275 | 0.11902 | 121.5958 | -0.050354 | 121.4401 | 121.2616 | 121.3257 | 121.344 | 121.3211 | -121.4676 | -121.5546 | 121.6782 | 121.4355 | 61.0565 | 60.965
276.2656 | 121.8063 | -61.0199 | 60.4706 | 0.0019074 | 0 | 0.064963 | 0.062647 | -0.0012177 | -0.0014248 | -0.0010894 | 0.00018312 | -0.001801 | -1.3927 | 0.061393 | -0.0022046 | 0.0059217 | 0.0046783 | 0.027466 | 60.1639 | -60.9375 | 60.7498 | -60.7132 | -61.1252 | -61.2305 | 0.041199 | 60.2051 | -61.0245 | 60.4752 | -60.9604 | -61.0107 | -61.2167 | 0.082397 | -0.3067 | 0.27924 | 0.3067 | -0.21057 | -0.10529 | -0.29297 | -0.18768 | -0.004578 | -0.2655 | 0.004578 | 0.059509 | -0.19684 | 0.009155 | -0.19226 | 0.013733 | 0.2243 | 121.6873 | 0.064087 | 121.4996 | 121.1014 | 121.2296 | 121.1838 | 121.225 | -121.4081 | -121.4951 | 121.7697 | 121.4951 | 61.0474 | 61.0611
278.0469 | 121.7972 | -61.0703 | 60.4065 | 0.0095369 | 0 | 0.066885 | 0.062647 | -0.0020721 | -0.0016384 | 0.0010468 | 0.0032349 | -0.00051916 | -1.3942 | 0.066947 | -0.0024182 | 0.0072035 | 0.0019013 | -0.050354 | 60.173 | -61.0062 | 60.6445 | -60.8047 | -61.2305 | -61.3129 | -0.045776 | 60.1639 | -61.0977 | 60.4248 | -61.0245 | -61.084 | -61.2625 | 0.064086 | -0.23346 | 0.23804 | 0.2655 | -0.24262 | -0.16022 | -0.3067 | -0.2243 | -0.027466 | -0.24262 | 0.018311 | 0.045776 | -0.19226 | -0.013733 | -0.16479 | 0.013733 | 0.20142 | 121.6507 | 0.073242 | 121.5225 | 121.1792 | 121.2616 | 121.2433 | 121.2341 | -121.4127 | -121.5042 | 121.7148 | 121.4951 | 61.0199 | 61.0245
279.75 | 121.6873 | -61.116 | 60.4431 | 0.0095369 | 0 | 0.067099 | 0.066706 | -0.0033539 | -0.00099764 | -0.0023712 | -0.0028687 | 0.0020444 | -1.392 | 0.069084 | -6.8386e-05 | 0.0048535 | -0.0030121 | -0.082397 | 60.173 | -61.0153 | 60.5667 | -60.9329 | -61.3449 | -61.4319 | -0.16479 | 60.2005 | -61.1252 | 60.2966 | -61.1938 | -61.2579 | -61.3724 | 0.10071 | -0.27008 | 0.1236 | 0.18311 | -0.31586 | -0.22888 | -0.41656 | -0.32959 | -0.009155 | -0.24262 | -0.14648 | -0.07782 | -0.25635 | -0.14191 | -0.24719 | -0.13275 | 0.082398 | 121.582 | -0.068665 | 121.4218 | 121.1884 | 121.3257 | 121.2891 | 121.3165 | -121.4584 | -121.5683 | 121.6827 | 121.4127 | 61.0336 | 60.9512
281.5 | 121.6873 | -61.116 | 60.4202 | 0.0019074 | 0 | 0.065176 | 0.064142 | -0.0024995 | -0.0020658 | -0.001303 | -0.0028687 | 0.00097624 | -1.3942 | 0.06417 | -0.0024182 | 0.0061353 | 0.0019013 | -0.073242 | 60.1959 | -61.0062 | 60.5484 | -60.9421 | -61.3678 | -61.4227 | -0.16937 | 60.1822 | -61.1298 | 60.3149 | -61.1984 | -61.2534 | -61.3724 | 0.10986 | -0.2243 | 0.12817 | 0.17395 | -0.3067 | -0.25177 | -0.41656 | -0.36163 | -0.013733 | -0.23804 | -0.10529 | -0.082397 | -0.25635 | -0.13733 | -0.24261 | -0.1236 | 0.064087 | 121.5546 | -0.068664 | 121.4447 | 121.2021 | 121.312 | 121.312 | 121.2982 | -121.4264 | -121.55 | 121.6644 | 121.431 | 61.0428 | 60.9467
283.2812 | 121.8246 | -61.0062 | 60.4477 | -0.0057221 | 0 | 0.062613 | 0.061152 | -0.0018585 | -0.0044156 | 0.00040597 | -0.0028687 | -0.00051916 | -1.3935 | 0.067161 | -0.0028454 | 0.0046399 | 0.0010467 | 0.027466 | 60.1868 | -60.9375 | 60.7407 | -60.672 | -61.1114 | -61.2213 | 0.07782 | 60.2142 | -61.0474 | 60.4935 | -60.9375 | -61.0016 | -61.1984 | 0.068665 | -0.26093 | 0.29297 | 0.33417 | -0.21515 | -0.10528 | -0.28381 | -0.17395 | -0.041198 | -0.23346 | 0.045776 | 0.068665 | -0.19226 | 0.004578 | -0.15106 | 0.045776 | 0.2655 | 121.6782 | 0.10986 | 121.5408 | 121.1243 | 121.2616 | 121.1929 | 121.2204 | -121.3852 | -121.4951 | 121.7468 | 121.4996 | 61.0336 | 61.084
285.0469 | 121.7331 | -61.0657 | 60.5026 | 0.040054 | 0 | 0.065604 | 0.066706 | -0.00014949 | -0.00099764 | -2.1434e-05 | 0.021545 | 0.0046078 | -1.3922 | 0.061607 | -0.0039136 | 0.0044263 | -2.1314e-05 | 0.004578 | 60.2646 | -61.0062 | 60.6537 | -60.8185 | -61.2167 | -61.3037 | -0.059509 | 60.2829 | -61.1023 | 60.3928 | -61.0611 | -61.1252 | -61.2671 | 0.059509 | -0.23804 | 0.15106 | 0.24719 | -0.23804 | -0.15106 | -0.29755 | -0.21057 | -0.036621 | -0.21973 | -0.10986 | 0.004578 | -0.20142 | -0.059509 | -0.1648 | -0.022888 | 0.18768 | 121.6599 | 0.041199 | 121.4951 | 121.2708 | 121.3852 | 121.3303 | 121.3486 | -121.5088 | -121.6049 | 121.7194 | 121.4584 | 61.0703 | 61.0062
286.75 | 121.7972 | -61.0748 | 60.434 | 0.0095369 | 0 | 0.063467 | 0.06457 | -0.0029267 | 0.00071136 | 0.0012604 | 0.00018312 | -0.00030556 | -1.3944 | 0.069938 | -0.0011364 | 0.0074171 | 0.0010467 | -0.050354 | 60.1822 | -60.9695 | 60.6445 | -60.8139 | -61.2259 | -61.2946 | -0.045776 | 60.1868 | -61.0977 | 60.4248 | -61.0153 | -61.0703 | -61.2488 | 0.10529 | -0.25177 | 0.21057 | 0.26093 | -0.21973 | -0.15106 | -0.32501 | -0.25635 | -0.022888 | -0.24719 | -0.009155 | 0.059509 | -0.17395 | 0.004578 | -0.15106 | 0.027466 | 0.15564 | 121.6141 | 0.082397 | 121.5225 | 121.1517 | 121.2845 | 121.257 | 121.2616 | -121.4035 | -121.5317 | 121.7194 | 121.4996 | 61.0245 | 61.0291
288.5 | 121.7102 | -61.0977 | 60.4065 | -0.0057221 | 0 | 0.065604 | 0.066706 | 0.0011321 | 0.00071136 | -0.003653 | 0.00018312 | 0.0011898 | -1.3918 | 0.068229 | -0.0011364 | 0.0084851 | 0.00083309 | -0.11444 | 60.2005 | -61.0382 | 60.5438 | -60.9329 | -61.3495 | -61.4044 | -0.15106 | 60.1868 | -61.1435 | 60.3241 | -61.1572 | -61.2167 | -61.3358 | 0.059509 | -0.20599 | 0.13733 | 0.1648 | -0.3067 | -0.25177 | -0.36621 | -0.31128 | -0.045777 | -0.21973 | -0.082397 | -0.05951 | -0.23804 | -0.11902 | -0.19226 | -0.073242 | 0.10529 | 121.582 | -0.013733 | 121.4676 | 121.2387 | 121.3303 | 121.2982 | 121.2845 | -121.4447 | -121.55 | 121.6415 | 121.4218 | 60.9833 | 60.9467
290.2969 | 121.7468 | -61.0886 | 60.4431 | 0.017166 | 0 | 0.065176 | 0.067347 | 0.0019867 | 0.00028416 | 0.0040376 | 0.0093383 | 0.002258 | -1.3944 | 0.060966 | -0.003059 | 0.0065625 | -0.0030121 | 0 | 60.2509 | -61.0199 | 60.6628 | -60.7819 | -61.2213 | -61.2991 | -0.013733 | 60.2463 | -61.084 | 60.4065 | -61.0336 | -61.116 | -61.2717 | 0.068665 | -0.19226 | 0.21973 | 0.3067 | -0.21057 | -0.13275 | -0.27924 | -0.20142 | 0.004578 | -0.19684 | -0.036621 | 0.054932 | -0.1831 | -0.027466 | -0.18768 | -0.032044 | 0.23804 | 121.6827 | 0.050354 | 121.4905 | 121.2708 | 121.3303 | 121.3394 | 121.3348 | -121.463 | -121.5271 | 121.7514 | 121.4951 | 61.0886 | 61.0748
292.0625 | 121.8155 | -61.0977 | 60.3561 | -0.020981 | 0 | 0.066458 | 0.064356 | 0.0054047 | -0.001852 | -0.00023503 | -0.0059205 | 0.0018306 | -1.3944 | 0.05883 | -6.8386e-05 | 0.0054945 | -0.0010895 | -0.09613 | 60.1639 | -61.0016 | 60.6033 | -60.8551 | -61.2991 | -61.3586 | -0.054932 | 60.141 | -61.1206 | 60.4248 | -61.0565 | -61.116 | -61.2717 | 0.09613 | -0.19226 | 0.24719 | 0.24261 | -0.26093 | -0.20142 | -0.35706 | -0.29755 | -0.022888 | -0.21515 | 0.068665 | 0.041198 | -0.17395 | -0.018311 | -0.15106 | 0.004577 | 0.14648 | 121.6049 | 0.064086 | 121.5454 | 121.1655 | 121.2616 | 121.2616 | 121.2387 | -121.3577 | -121.4767 | 121.7011 | 121.5225 | 61.0016 | 61.0428
293.8281 | 121.7194 | -61.0931 | 60.434 | 0.0095369 | 0 | 0.063254 | 0.066492 | 0.0036957 | -0.00078404 | 0.0010468 | -0.0028687 | 0.002258 | -1.3948 | 0.067375 | -0.003059 | 0.0059217 | -2.1314e-05 | -0.086975 | 60.1776 | -61.0382 | 60.5255 | -60.9375 | -61.3541 | -61.4365 | -0.14648 | 60.2005 | -61.1481 | 60.3149 | -61.1481 | -61.2305 | -61.3586 | 0.054932 | -0.25635 | 0.091553 | 0.15564 | -0.34332 | -0.26093 | -0.39825 | -0.31586 | -0.054931 | -0.23346 | -0.11902 | -0.054931 | -0.2655 | -0.13733 | -0.21057 | -0.082398 | 0.10071 | 121.5637 | 0 | 121.463 | 121.2158 | 121.3486 | 121.2708 | 121.2936 | -121.4722 | -121.582 | 121.6187 | 121.4081 | 61.0062 | 60.9467
295.5156 | 121.7697 | -61.0931 | 60.3699 | -0.0057221 | 0 | 0.066672 | 0.065211 | -0.00014949 | 7.0564e-05 | -0.0017304 | -0.0028687 | 0.00012184 | -1.3922 | 0.060111 | -0.0011364 | 0.0054945 | -0.0013031 | -0.11902 | 60.173 | -61.0336 | 60.5667 | -60.8963 | -61.3358 | -61.409 | -0.09613 | 60.1685 | -61.1435 | 60.3699 | -61.0977 | -61.1618 | -61.3129 | 0.05951 | -0.19684 | 0.19684 | 0.19684 | -0.31586 | -0.24261 | -0.37537 | -0.30212 | -0.050354 | -0.20142 | 0 | -0.004577 | -0.21973 | -0.068664 | -0.16937 | -0.01831 | 0.13733 | 121.6003 | 0.045777 | 121.5134 | 121.2067 | 121.312 | 121.2662 | 121.2616 | -121.4035 | -121.5134 | 121.6599 | 121.463 | 60.9741 | 60.997
297.2812 | 121.8613 | -61.0245 | 60.4294 | -0.0057221 | 0 | 0.063895 | 0.062647 | -0.0016449 | -0.001852 | -0.0025848 | 0.00018312 | 0.00054904 | -1.3931 | 0.061393 | -0.0013502 | 0.0063489 | 0.0010467 | -0.009155 | 60.1822 | -60.965 | 60.7269 | -60.704 | -61.1252 | -61.2122 | 0.091553 | 60.1868 | -61.0519 | 60.4889 | -60.9192 | -60.9833 | -61.1755 | 0.059509 | -0.24719 | 0.29755 | 0.32043 | -0.18768 | -0.10071 | -0.24719 | -0.16022 | -0.027466 | -0.24261 | 0.05951 | 0.10529 | -0.15106 | 0.041199 | -0.1236 | 0.068665 | 0.26093 | 121.6919 | 0.13275 | 121.5408 | 121.1472 | 121.2387 | 121.2067 | 121.2112 | -121.3943 | -121.4813 | 121.7514 | 121.5134 | 61.0153 | 61.116
299.0469 | 121.669 | -61.116 | 60.4111 | -0.0057221 | 0 | 0.06539 | 0.064783 | 0.00070491 | 0.00028416 | -0.0034392 | -0.0028687 | 0.0026852 | -1.394 | 0.064384 | -0.0026318 | 0.0050671 | 0.0019013 | -0.068665 | 60.2005 | -61.0382 | 60.5576 | -60.9283 | -61.3495 | -61.4319 | -0.15564 | 60.1822 | -61.1206 | 60.2875 | -61.1801 | -61.2534 | -61.3724 | 0.07782 | -0.21057 | 0.14648 | 0.18768 | -0.31586 | -0.23346 | -0.39368 | -0.31128 | -0.004577 | -0.22888 | -0.1236 | -0.064087 | -0.25635 | -0.13733 | -0.25177 | -0.13275 | 0.10986 | 121.5958 | -0.05951 | 121.4081 | 121.2387 | 121.3028 | 121.3165 | 121.2982 | -121.4493 | -121.5317 | 121.6736 | 121.4035 | 61.0474 | 60.9604
300.75 | 121.8201 | -61.0153 | 60.4202 | 0.0019074 | 0 | 0.064749 | 0.062647 | 0.0019867 | 0.0011386 | -2.1434e-05 | -0.0028687 | -0.00094636 | -1.3931 | 0.071433 | -0.0017774 | 0.0063489 | -0.0036529 | 0.018311 | 60.1776 | -60.9421 | 60.7498 | -60.6628 | -61.0977 | -61.1938 | 0.082397 | 60.2097 | -61.0245 | 60.5026 | -60.9146 | -60.9787 | -61.1847 | 0.073242 | -0.24261 | 0.32959 | 0.35248 | -0.17853 | -0.082397 | -0.25177 | -0.15564 | -0.009155 | -0.21057 | 0.082398 | 0.10071 | -0.16937 | 0.036621 | -0.16022 | 0.045776 | 0.27924 | 121.6919 | 0.10986 | 121.5271 | 121.1197 | 121.2341 | 121.1929 | 121.225 | -121.3623 | -121.4447 | 121.7651 | 121.5179 | 61.0336 | 61.0977
302.4531 | 121.6919 | -61.1114 | 60.4202 | 0.0019074 | 0 | 0.064963 | 0.063288 | 0.0019867 | -0.001852 | 0.0019012 | -0.0028687 | 0.00033544 | -1.3935 | 0.065238 | -0.00092279 | 0.0052807 | -0.0013031 | -0.091553 | 60.173 | -61.0382 | 60.5484 | -60.9421 | -61.3586 | -61.4319 | -0.17853 | 60.1913 | -61.1206 | 60.3149 | -61.1572 | -61.2305 | -61.3541 | 0.073242 | -0.24719 | 0.12817 | 0.16937 | -0.32044 | -0.24719 | -0.39368 | -0.32044 | -0.009155 | -0.22888 | -0.10529 | -0.045777 | -0.24262 | -0.11902 | -0.23346 | -0.10986 | 0.09613 | 121.5866 | -0.036622 | 121.4355 | 121.2112 | 121.3119 | 121.2845 | 121.3028 | -121.4584 | -121.5408 | 121.6599 | 121.4264 | 61.0199 | 60.9329
304.1562 | 121.8109 | -61.0886 | 60.379 | 0.047683 | 0 | 0.067099 | 0.063074 | -0.0016449 | 7.0564e-05 | 0.002115 | 0.0093383 | 0.0020444 | -1.3912 | 0.065666 | 0.00014521 | 0.0093397 | -0.00044851 | -0.032043 | 60.1593 | -61.0245 | 60.6903 | -60.7452 | -61.2076 | -61.29 | 0.027466 | 60.1547 | -61.1206 | 60.4294 | -61.0291 | -61.0794 | -61.2579 | 0.064087 | -0.21973 | 0.31128 | 0.34332 | -0.20142 | -0.11902 | -0.2655 | -0.18311 | -0.032043 | -0.2243 | 0.050354 | 0.059509 | -0.16937 | 0.009155 | -0.13733 | 0.041198 | 0.27924 | 121.7148 | 0.091552 | 121.55 | 121.1838 | 121.2753 | 121.2479 | 121.2433 | -121.4035 | -121.4996 | 121.7789 | 121.5179 | 61.0565 | 61.116
305.9062 | 121.8155 | -61.0886 | 60.3561 | -0.0057221 | 0 | 0.06539 | 0.06457 | -0.00014949 | -0.0012112 | -0.001303 | 0.00018312 | 0.0014034 | -1.395 | 0.064384 | -0.00092279 | 0.0086987 | 0.0048919 | -0.041199 | 60.1501 | -60.9924 | 60.6537 | -60.791 | -61.2488 | -61.322 | -0.009155 | 60.1501 | -61.0931 | 60.4385 | -61.0382 | -61.0977 | -61.2488 | 0.09613 | -0.20599 | 0.29755 | 0.29755 | -0.23346 | -0.16022 | -0.32959 | -0.25635 | -0.004578 | -0.20599 | 0.082398 | 0.050354 | -0.16022 | -0.009155 | -0.15564 | -0.004577 | 0.20142 | 121.6461 | 0.054932 | 121.5317 | 121.1426 | 121.2433 | 121.2387 | 121.2387 | -121.3486 | -121.4493 | 121.7422 | 121.5271 | 61.0474 | 61.0794
307.6094 | 121.6873 | -61.0428 | 60.4477 | -0.0057221 | 0 | 0.064963 | 0.064142 | -0.0031403 | -0.001852 | -0.0027984 | 0.0032349 | 0.00076264 | -1.3948 | 0.059898 | -0.004768 | 0.0067761 | 0.00040589 | 0.013733 | 60.2005 | -60.9421 | 60.6674 | -60.7819 | -61.1893 | -61.2854 | -0.027466 | 60.2509 | -61.0565 | 60.3928 | -61.0428 | -61.0977 | -61.2579 | 0.10071 | -0.24719 | 0.21973 | 0.26093 | -0.24261 | -0.14648 | -0.34332 | -0.24719 | -0.013733 | -0.19684 | -0.054932 | 0 | -0.21515 | -0.054931 | -0.20142 | -0.041198 | 0.16022 | 121.6095 | 0.013733 | 121.4493 | 121.1426 | 121.3074 | 121.2433 | 121.2936 | -121.3898 | -121.5042 | 121.7102 | 121.4355 | 61.0565 | 61.0153
309.375 | 121.6827 | -61.0336 | 60.4614 | 0.0019074 | 0 | 0.063467 | 0.062433 | 0.0017731 | -0.00099764 | -0.00023503 | -0.0028687 | -0.00073276 | -1.3946 | 0.063743 | -0.0045544 | 0.0029309 | 0.0027557 | -0.004578 | 60.2188 | -60.9467 | 60.6445 | -60.7819 | -61.203 | -61.2808 | -0.041199 | 60.2646 | -61.0474 | 60.3882 | -61.0382 | -61.1114 | -61.2717 | 0.086975 | -0.24262 | 0.1831 | 0.25177 | -0.24719 | -0.16937 | -0.33417 | -0.25635 | -0.013733 | -0.19684 | -0.073242 | -0.004578 | -0.23804 | -0.07782 | -0.2243 | -0.064087 | 0.16479 | 121.5912 | 0.009155 | 121.4355 | 121.1655 | 121.3119 | 121.2524 | 121.2982 | -121.4081 | -121.5088 | 121.6782 | 121.4218 | 61.0291 | 60.9924
311.1406 | 121.8155 | -61.0748 | 60.3607 | 0.0019074 | 0 | 0.066885 | 0.064783 | -0.0012177 | -0.0020658 | -0.001303 | -0.0028687 | 0.00097624 | -1.3959 | 0.06652 | 0.0012134 | 0.0059217 | 0.0038239 | -0.041199 | 60.1227 | -60.997 | 60.6674 | -60.7864 | -61.2305 | -61.3174 | -0.013733 | 60.1273 | -61.116 | 60.4202 | -61.0245 | -61.0977 | -61.2625 | 0.07782 | -0.23804 | 0.3067 | 0.28839 | -0.24262 | -0.15564 | -0.32044 | -0.23346 | -0.041199 | -0.23346 | 0.059509 | 0.050354 | -0.18768 | -0.022888 | -0.14648 | 0.018311 | 0.21057 | 121.6644 | 0.091553 | 121.5363 | 121.1197 | 121.2433 | 121.1975 | 121.2021 | -121.3577 | -121.4767 | 121.7422 | 121.4951 | 61.0336 | 61.0611
312.9062 | 121.7926 | -61.0794 | 60.3561 | 0.0095369 | 0 | 0.069449 | 0.062647 | 6.4114e-05 | -0.002493 | 0.0025422 | 0.00018312 | 0.00012184 | -1.3944 | 0.062461 | -6.8386e-05 | 0.0067761 | -0.0038665 | -0.09613 | 60.1776 | -61.0291 | 60.6125 | -60.8551 | -61.2762 | -61.3495 | -0.036621 | 60.1181 | -61.1206 | 60.4065 | -61.0611 | -61.1252 | -61.2579 | 0.050354 | -0.17853 | 0.25635 | 0.2243 | -0.27008 | -0.19684 | -0.32043 | -0.24719 | -0.041198 | -0.23804 | 0.050354 | 0.018311 | -0.17853 | -0.045776 | -0.13733 | -0.004578 | 0.17395 | 121.6415 | 0.059509 | 121.5271 | 121.2067 | 121.2387 | 121.257 | 121.1975 | -121.3852 | -121.4767 | 121.6919 | 121.4859 | 60.9833 | 61.0428
314.5938 | 121.7743 | -61.0748 | 60.4065 | 0.032425 | 0 | 0.067099 | 0.062433 | 0.0026275 | 0.00071136 | -0.0015166 | 0.00018312 | -0.00030556 | -1.3955 | 0.056266 | -0.0028454 | 0.0057081 | 0.00019229 | -0.064087 | 60.1913 | -61.0016 | 60.6491 | -60.7864 | -61.1938 | -61.2991 | -0.059509 | 60.1776 | -61.084 | 60.4065 | -61.0474 | -61.1023 | -61.2625 | 0.073242 | -0.21515 | 0.24262 | 0.28839 | -0.2243 | -0.11902 | -0.29755 | -0.19226 | -0.009155 | -0.22888 | 0 | 0.027466 | -0.18768 | -0.027466 | -0.17853 | -0.018311 | 0.21515 | 121.6507 | 0.036621 | 121.4905 | 121.1929 | 121.2616 | 121.2662 | 121.2524 | -121.4081 | -121.4905 | 121.7239 | 121.4813 | 61.0107 | 61.0153
316.3438 | 121.8338 | -61.0016 | 60.4477 | 0.0019074 | 0 | 0.064322 | 0.062647 | -0.0033539 | -0.0014248 | 0.0019012 | -0.0028687 | -0.0013736 | -1.395 | 0.068656 | -0.003059 | 0.0052807 | -0.0070709 | 0 | 60.1639 | -60.9558 | 60.7636 | -60.6583 | -61.0977 | -61.1801 | 0.086975 | 60.1959 | -61.0245 | 60.498 | -60.9192 | -60.9787 | -61.1755 | 0.045776 | -0.28381 | 0.31586 | 0.34332 | -0.17853 | -0.09613 | -0.2243 | -0.14191 | -0.022888 | -0.25177 | 0.050354 | 0.082398 | -0.17395 | 0.022888 | -0.15106 | 0.045776 | 0.29755 | 121.7194 | 0.10529 | 121.5225 | 121.1197 | 121.2204 | 121.1655 | 121.1975 | -121.4035 | -121.4722 | 121.7651 | 121.4996 | 61.0016 | 61.0886
318.1094 | 121.8155 | -61.0336 | 60.4523 | 0.0095369 | 0 | 0.065176 | 0.063288 | 0.00070491 | -0.0012112 | -2.1434e-05 | -0.0028687 | 0.00012184 | -1.394 | 0.068015 | -0.0017774 | 0.0052807 | 0.00040589 | -0.027466 | 60.1776 | -60.9558 | 60.7132 | -60.7315 | -61.1389 | -61.235 | 0.045776 | 60.1868 | -61.0199 | 60.4889 | -60.9467 | -61.0016 | -61.1755 | 0.077819 | -0.27466 | 0.26093 | 0.30212 | -0.20142 | -0.10529 | -0.27923 | -0.18311 | 0.013733 | -0.2655 | 0.036621 | 0.086975 | -0.14191 | 0.032043 | -0.15564 | 0.01831 | 0.2243 | 121.669 | 0.073242 | 121.5088 | 121.1334 | 121.2067 | 121.2112 | 121.2204 | -121.4081 | -121.4722 | 121.7468 | 121.5225 | 61.0062 | 61.0794
319.875 | 121.7194 | -61.0657 | 60.4523 | 0.047683 | 0 | 0.064536 | 0.066492 | 6.4114e-05 | -0.0012112 | 0.0010468 | 0.0093383 | 0.0031124 | -1.3925 | 0.065666 | -0.0022046 | 0.0048535 | 0.0016877 | 0.018311 | 60.2692 | -60.9833 | 60.6628 | -60.791 | -61.2122 | -61.2991 | -0.013733 | 60.2417 | -61.0977 | 60.4019 | -61.0428 | -61.1023 | -61.2534 | 0.082398 | -0.18311 | 0.21057 | 0.27466 | -0.23346 | -0.14648 | -0.31586 | -0.22888 | -0.032043 | -0.21057 | -0.050354 | 0.022888 | -0.18768 | -0.036621 | -0.15564 | -0.004578 | 0.19226 | 121.6461 | 0.054931 | 121.4996 | 121.2524 | 121.3394 | 121.3348 | 121.3074 | -121.4355 | -121.55 | 121.7285 | 121.4676 | 61.084 | 61.0519
321.5781 | 121.7331 | -61.0291 | 60.4523 | 0.024795 | 0 | 0.066672 | 0.065851 | -0.00014949 | -0.0016384 | -0.00023503 | 0.0062865 | 0.002258 | -1.3957 | 0.062888 | -0.0039136 | 0.0046399 | 0.0010467 | 0.009155 | 60.2234 | -60.9924 | 60.6491 | -60.7864 | -61.2259 | -61.3083 | 0.009155 | 60.2417 | -61.0794 | 60.4019 | -61.0382 | -61.1069 | -61.2579 | 0.036621 | -0.22888 | 0.19684 | 0.24262 | -0.27924 | -0.19684 | -0.31586 | -0.23346 | -0.050354 | -0.21057 | -0.050354 | -0.009155 | -0.22888 | -0.07782 | -0.17853 | -0.027466 | 0.20599 | 121.6415 | 0.041199 | 121.4813 | 121.2158 | 121.3211 | 121.2524 | 121.2708 | -121.4447 | -121.5317 | 121.6782 | 121.431 | 61.0382 | 61.0382
323.3594 | 121.6736 | -61.0291 | 60.4843 | -0.0057221 | 0 | 0.063467 | 0.063074 | -0.0014313 | -0.0027066 | -2.1434e-05 | 0.0032349 | -0.0013736 | -1.3925 | 0.057121 | -0.007118 | 0.0046399 | 0.0031829 | -0.036621 | 60.2509 | -60.9467 | 60.6216 | -60.8185 | -61.2076 | -61.29 | -0.068665 | 60.2829 | -61.0703 | 60.379 | -61.0428 | -61.1252 | -61.2808 | 0.082398 | -0.23346 | 0.13733 | 0.21057 | -0.26093 | -0.17853 | -0.34332 | -0.26093 | -0.041198 | -0.20142 | -0.10529 | -0.013733 | -0.25177 | -0.09613 | -0.21057 | -0.054932 | 0.12817 | 121.5683 | 0.027465 | 121.4493 | 121.1975 | 121.3531 | 121.2799 | 121.312 | -121.431 | -121.5546 | 121.6507 | 121.4081 | 60.9924 | 60.9604
325.1406 | 121.7743 | -61.0291 | 60.4614 | 0.0019074 | 0 | 0.063681 | 0.062861 | -0.0042083 | -0.0046292 | 0.0012604 | -0.0059205 | 0.00012184 | -1.3944 | 0.062888 | -0.001991 | 0.0050671 | -0.00044851 | 0.004578 | 60.1685 | -60.9238 | 60.7498 | -60.6949 | -61.1343 | -61.2213 | 0.045776 | 60.2142 | -61.0153 | 60.4706 | -60.9421 | -60.997 | -61.1847 | 0.10529 | -0.29297 | 0.28839 | 0.33417 | -0.19226 | -0.10529 | -0.29755 | -0.21057 | 0.013733 | -0.24719 | 0.009155 | 0.086975 | -0.15564 | 0.032044 | -0.16937 | 0.018311 | 0.22888 | 121.6736 | 0.073242 | 121.4859 | 121.0922 | 121.2296 | 121.1975 | 121.2433 | -121.3852 | -121.4767 | 121.7789 | 121.4996 | 61.0336 | 61.0748
326.8438 | 121.8018 | -61.0748 | 60.3836 | 0.0095369 | 0 | 0.064749 | 0.065211 | 0.0028411 | -0.0031338 | -0.00023503 | -0.0059205 | -0.00030556 | -1.3922 | 0.059257 | 0.00057241 | 0.0065625 | 0.00019229 | -0.086975 | 60.1501 | -60.997 | 60.6125 | -60.8185 | -61.2488 | -61.3449 | -0.041199 | 60.141 | -61.1206 | 60.4248 | -61.0291 | -61.1023 | -61.2442 | 0.07782 | -0.23346 | 0.22888 | 0.25635 | -0.27008 | -0.17395 | -0.3479 | -0.25177 | -0.045776 | -0.24262 | 0.041199 | 0.045776 | -0.16937 | -0.027466 | -0.1236 | 0.01831 | 0.17853 | 121.6095 | 0.091552 | 121.5454 | 121.1472 | 121.2616 | 121.225 | 121.2158 | -121.3806 | -121.5042 | 121.6873 | 121.4996 | 60.9879 | 61.0336
328.6094 | 121.7926 | -61.0062 | 60.4568 | -0.0057221 | 0 | 0.063254 | 0.061365 | -0.0010041 | -0.00527 | -0.0025848 | 0.00018312 | 0.00033544 | -1.394 | 0.067161 | -0.0056226 | 0.0065625 | 0.0019013 | 0.013733 | 60.1959 | -60.9329 | 60.7498 | -60.6857 | -61.1298 | -61.1847 | 0.082397 | 60.2005 | -61.0153 | 60.4935 | -60.9375 | -60.9879 | -61.1938 | 0.073243 | -0.26093 | 0.29297 | 0.32044 | -0.17853 | -0.1236 | -0.25177 | -0.19684 | -0.009155 | -0.25635 | 0.036621 | 0.068665 | -0.18768 | 0.018311 | -0.17853 | 0.027466 | 0.24719 | 121.6827 | 0.07782 | 121.5088 | 121.1288 | 121.2158 | 121.2021 | 121.2067 | -121.3898 | -121.4722 | 121.756 | 121.4996 | 61.0199 | 61.0886
330.375 | 121.6919 | -61.0931 | 60.4248 | -0.0057221 | 0 | 0.067099 | 0.064783 | -0.0029267 | -0.00099764 | 0.001474 | -0.0059205 | 0.00012184 | -1.3963 | 0.062888 | -0.0011364 | 0.0065625 | -0.0027985 | -0.07782 | 60.2005 | -61.0016 | 60.585 | -60.8826 | -61.3083 | -61.3998 | -0.12817 | 60.2051 | -61.116 | 60.3241 | -61.1435 | -61.1984 | -61.3358 | 0.091553 | -0.22431 | 0.16022 | 0.21057 | -0.3067 | -0.21515 | -0.39825 | -0.3067 | -0.022888 | -0.21973 | -0.10071 | -0.050354 | -0.24261 | -0.10529 | -0.21973 | -0.082397 | 0.11902 | 121.5866 | -0.027466 | 121.4401 | 121.2021 | 121.3211 | 121.2936 | 121.2982 | -121.4264 | -121.5408 | 121.6782 | 121.4172 | 61.0153 | 60.965
332.125 | 121.701 | -61.0977 | 60.434 | 0.0019074 | 0 | 0.064963 | 0.065211 | -0.0014313 | -0.00078404 | 0.0012604 | -0.0028687 | 0.0011898 | -1.394 | 0.06417 | -0.0026318 | 0.0074171 | 0.0019013 | -0.1236 | 60.1913 | -61.0336 | 60.5209 | -60.9192 | -61.3403 | -61.3998 | -0.14648 | 60.2005 | -61.1389 | 60.3333 | -61.1389 | -61.2076 | -61.3266 | 0.064087 | -0.24262 | 0.086975 | 0.17853 | -0.30212 | -0.24261 | -0.36621 | -0.3067 | -0.041199 | -0.23346 | -0.10071 | -0.041199 | -0.22888 | -0.10986 | -0.18768 | -0.068665 | 0.11444 | 121.5546 | 0 | 121.4722 | 121.225 | 121.3394 | 121.2891 | 121.2982 | -121.4676 | -121.5729 | 121.6187 | 121.431 | 60.9741 | 60.9512
333.8281 | 121.7422 | -61.0474 | 60.4477 | 0.032425 | 0 | 0.065817 | 0.064783 | 0.0049773 | -0.0012112 | -2.1434e-05 | 0.0093383 | 0.0018306 | -1.394 | 0.061393 | -0.005409 | 0.0074171 | 0.0010467 | -0.013733 | 60.2325 | -61.0062 | 60.6628 | -60.7727 | -61.2122 | -61.29 | -0.013733 | 60.2417 | -61.0886 | 60.3882 | -61.0428 | -61.1114 | -61.2534 | 0.041198 | -0.21515 | 0.21515 | 0.27466 | -0.24262 | -0.1648 | -0.28381 | -0.20599 | -0.041199 | -0.20599 | -0.059509 | 0.004577 | -0.20599 | -0.064087 | -0.16479 | -0.022888 | 0.23346 | 121.669 | 0.045776 | 121.4767 | 121.2387 | 121.3303 | 121.2799 | 121.2891 | -121.4539 | -121.5363 | 121.7102 | 121.4355 | 61.0336 | 61.0336
335.5938 | 121.6873 | -61.0886 | 60.4111 | 0.0095369 | 0 | 0.06539 | 0.065851 | 0.0015595 | -0.00035684 | -0.00087583 | -0.0028687 | 0.0024716 | -1.3946 | 0.059043 | -0.0022046 | 0.0076307 | -0.0013031 | -0.11444 | 60.1822 | -61.0199 | 60.5347 | -60.9283 | -61.3449 | -61.409 | -0.16022 | 60.1593 | -61.1298 | 60.3149 | -61.1526 | -61.1938 | -61.3358 | 0.068665 | -0.22888 | 0.1236 | 0.16022 | -0.32043 | -0.25635 | -0.3891 | -0.32501 | -0.041199 | -0.25177 | -0.096131 | -0.064087 | -0.24719 | -0.10529 | -0.20599 | -0.064087 | 0.091552 | 121.5546 | -0.022888 | 121.4447 | 121.2021 | 121.2891 | 121.2708 | 121.2479 | -121.431 | -121.5408 | 121.6232 | 121.4035 | 60.9741 | 60.9283
337.3594 | 121.7285 | -61.0474 | 60.466 | 0.040054 | 0 | 0.067313 | 0.065211 | 0.00091851 | -0.002493 | 0.003183 | 0.018494 | 0.0028988 | -1.3933 | 0.06182 | -0.0043408 | 0.0067761 | -0.0066437 | -0.013733 | 60.2875 | -60.997 | 60.6537 | -60.8047 | -61.1984 | -61.2808 | -0.045776 | 60.2875 | -61.0748 | 60.4065 | -61.0199 | -61.0886 | -61.2488 | 0.050354 | -0.17853 | 0.18768 | 0.24261 | -0.23346 | -0.15106 | -0.28381 | -0.20142 | -0.027466 | -0.17853 | -0.059509 | 0.027466 | -0.20142 | -0.041199 | -0.17395 | -0.013733 | 0.19226 | 121.6507 | 0.054932 | 121.4813 | 121.2845 | 121.3623 | 121.3348 | 121.3348 | -121.463 | -121.5408 | 121.701 | 121.4539 | 61.0336 | 61.0016
339.0781 | 121.8246 | -61.0199 | 60.4706 | 0.0019074 | 0 | 0.065176 | 0.061152 | 0.00049131 | -0.00099764 | -0.0017304 | -0.0028687 | -0.00116 | -1.3935 | 0.066734 | -0.0017774 | 0.0057081 | 0.0014741 | -0.032043 | 60.2005 | -60.9375 | 60.7269 | -60.6903 | -61.1069 | -61.1984 | 0.082397 | 60.1593 | -61.0428 | 60.5072 | -60.8963 | -60.9604 | -61.1664 | 0.082397 | -0.27008 | 0.25635 | 0.32959 | -0.17853 | -0.086976 | -0.26093 | -0.16937 | -0.022889 | -0.31128 | 0.036621 | 0.1236 | -0.14648 | 0.059509 | -0.1236 | 0.082398 | 0.24719 | 121.6644 | 0.14648 | 121.55 | 121.138 | 121.2021 | 121.2204 | 121.1792 | -121.4081 | -121.5134 | 121.7468 | 121.5271 | 60.9879 | 61.1023
340.8438 | 121.7972 | -61.0611 | 60.3745 | 0.055313 | 0 | 0.06539 | 0.064142 | 0.0060455 | 0.0015658 | 0.0042512 | 0.01239 | 0.0020444 | -1.3957 | 0.07357 | -0.0013502 | 0.0069897 | 0.0038239 | -0.032043 | 60.1456 | -60.9924 | 60.6903 | -60.7361 | -61.1893 | -61.2625 | 0.041199 | 60.1776 | -61.1206 | 60.4523 | -61.0291 | -61.084 | -61.2442 | 0.068664 | -0.22888 | 0.31586 | 0.32501 | -0.20142 | -0.12817 | -0.27008 | -0.19684 | -0.059509 | -0.19684 | 0.07782 | 0.032043 | -0.18311 | -0.022888 | -0.1236 | 0.036621 | 0.25635 | 121.6827 | 0.091552 | 121.5729 | 121.138 | 121.2982 | 121.2067 | 121.2387 | -121.3669 | -121.4951 | 121.7514 | 121.5134 | 61.0291 | 61.1023
342.5312 | 121.7697 | -61.0519 | 60.4065 | 0.024795 | 0 | 0.066672 | 0.063715 | 0.0019867 | -0.00014304 | -0.0021576 | 0.01239 | -0.00030556 | -1.3942 | 0.069297 | -0.0015638 | 0.0076307 | 0.0012603 | -0.082397 | 60.1685 | -60.997 | 60.6628 | -60.7819 | -61.2076 | -61.2854 | -0.045776 | 60.1868 | -61.0931 | 60.4202 | -61.0336 | -61.0931 | -61.2625 | 0.054932 | -0.23804 | 0.25635 | 0.27008 | -0.23346 | -0.15564 | -0.28839 | -0.21057 | -0.041199 | -0.21973 | 0.013733 | 0.018311 | -0.21057 | -0.041199 | -0.16937 | 0 | 0.21515 | 121.6599 | 0.05951 | 121.5134 | 121.1655 | 121.2799 | 121.2204 | 121.2387 | -121.4035 | -121.4996 | 121.7148 | 121.4722 | 60.9695 | 61.0062
344.2969 | 121.7972 | -61.0474 | 60.3745 | 0.0095369 | 0 | 0.068594 | 0.067774 | 0.0049773 | -0.00078404 | 0.0023286 | 0.01239 | -0.00030556 | -1.3935 | 0.069084 | -0.00070919 | 0.0084851 | 0.0016877 | -0.064087 | 60.141 | -61.0336 | 60.6995 | -60.7361 | -61.1847 | -61.2625 | 0.041199 | 60.1685 | -61.1252 | 60.434 | -61.0107 | -61.0703 | -61.2259 | 0.013733 | -0.23346 | 0.32501 | 0.31128 | -0.21515 | -0.13733 | -0.22888 | -0.15106 | -0.07782 | -0.20599 | 0.059509 | 0.036621 | -0.17853 | -0.022888 | -0.10071 | 0.054932 | 0.29755 | 121.7331 | 0.11444 | 121.5591 | 121.1746 | 121.2936 | 121.1884 | 121.2158 | -121.4081 | -121.4996 | 121.7468 | 121.4813 | 60.9833 | 61.0886
346.0469 | 121.7606 | -61.0519 | 60.3836 | 0.070572 | 0 | 0.066672 | 0.064997 | 0.0017731 | -0.00057044 | 0.0010468 | 0.018494 | 0.0020444 | -1.3925 | 0.063102 | -0.0028454 | 0.0076307 | 0.00083309 | -0.073242 | 60.1685 | -61.0153 | 60.6949 | -60.7315 | -61.1984 | -61.2762 | 0.018311 | 60.1822 | -61.1114 | 60.4294 | -61.0336 | -61.0794 | -61.2396 | 0.036621 | -0.21515 | 0.31128 | 0.32043 | -0.2243 | -0.14648 | -0.26093 | -0.1831 | -0.059509 | -0.20142 | 0.045776 | 0.018311 | -0.18768 | -0.027466 | -0.12817 | 0.032043 | 0.28381 | 121.7102 | 0.07782 | 121.5408 | 121.1838 | 121.2936 | 121.2204 | 121.2341 | -121.3989 | -121.4951 | 121.7468 | 121.4813 | 60.9787 | 61.0703
347.7344 | 121.8292 | -61.0016 | 60.4431 | -0.0057221 | 0 | 0.064963 | 0.063074 | -0.0010041 | -0.00057044 | -0.004721 | 0.00018312 | -0.00073276 | -1.3957 | 0.063743 | -0.0043408 | 0.0082715 | -0.00044851 | -0.041199 | 60.1959 | -60.9421 | 60.7315 | -60.6857 | -61.1298 | -61.1893 | 0.082397 | 60.1868 | -61.0382 | 60.5164 | -60.9192 | -60.9604 | -61.1618 | 0.059509 | -0.24719 | 0.28839 | 0.31586 | -0.18768 | -0.12817 | -0.24719 | -0.18768 | -0.036621 | -0.25635 | 0.073242 | 0.082398 | -0.16022 | 0.041199 | -0.1236 | 0.07782 | 0.25635 | 121.6736 | 0.11902 | 121.5546 | 121.138 | 121.225 | 121.1975 | 121.1884 | -121.3852 | -121.4813 | 121.7331 | 121.5179 | 60.9604 | 61.084
349.5 | 121.7194 | -61.0657 | 60.4523 | 0.017166 | 0 | 0.063681 | 0.065851 | 0.00049131 | 0.0013522 | -0.0017304 | 0.0032349 | 0.001617 | -1.3925 | 0.062034 | -0.0049818 | 0.0052807 | -0.0030121 | -0.018311 | 60.2051 | -60.965 | 60.6674 | -60.7956 | -61.2167 | -61.2991 | -0.045776 | 60.2509 | -61.0748 | 60.379 | -61.0703 | -61.1343 | -61.2579 | 0.10071 | -0.24719 | 0.21515 | 0.27008 | -0.23346 | -0.15106 | -0.33417 | -0.25177 | -0.009155 | -0.20142 | -0.073243 | -0.004577 | -0.19226 | -0.068664 | -0.18311 | -0.059509 | 0.16937 | 121.6324 | 0.004578 | 121.4539 | 121.17 | 121.3257 | 121.2708 | 121.3165 | -121.4172 | -121.5271 | 121.7331 | 121.4447 | 61.0474 | 61.0199
351.2656 | 121.8155 | -60.9924 | 60.4614 | -0.0057221 | 0 | 0.065817 | 0.062433 | 0.00027771 | -0.002493 | -0.001944 | 0.00018312 | 0.00012184 | -1.3935 | 0.060752 | -0.0045544 | 0.0065625 | 0.00061949 | -0.018311 | 60.1959 | -60.9146 | 60.7636 | -60.6491 | -61.0794 | -61.1893 | 0.068665 | 60.2142 | -61.0291 | 60.5026 | -60.9192 | -60.9558 | -61.1755 | 0.07782 | -0.2655 | 0.30212 | 0.34332 | -0.19684 | -0.086975 | -0.27466 | -0.1648 | -0.036621 | -0.24719 | 0.041199 | 0.073243 | -0.1831 | 0.036621 | -0.14648 | 0.073242 | 0.2655 | 121.6782 | 0.10986 | 121.5317 | 121.1105 | 121.2433 | 121.1884 | 121.2067 | -121.376 | -121.4905 | 121.756 | 121.4951 | 60.9741 | 61.0611
353.0312 | 121.701 | -61.0794 | 60.4385 | 0.032425 | 0 | 0.065817 | 0.065424 | 0.00027771 | -0.001852 | 0.00019217 | 0.0032349 | 0.0020444 | -1.3942 | 0.061179 | -0.003059 | 0.0044263 | -0.0064301 | -0.022888 | 60.2142 | -60.9695 | 60.6445 | -60.7773 | -61.2122 | -61.322 | -0.027466 | 60.2142 | -61.084 | 60.3836 | -61.0611 | -61.1252 | -61.2579 | 0.10986 | -0.22431 | 0.20599 | 0.30212 | -0.24261 | -0.13275 | -0.35248 | -0.24262 | -0.004577 | -0.22431 | -0.054932 | 0.018311 | -0.17853 | -0.045776 | -0.17395 | -0.041199 | 0.19226 | 121.6141 | 0.022888 | 121.4676 | 121.1838 | 121.2982 | 121.2936 | 121.2936 | -121.4081 | -121.5225 | 121.7239 | 121.463 | 61.0565 | 61.0519
354.7344 | 121.7056 | -61.0245 | 60.4797 | 0.047683 | 0 | 0.066458 | 0.065424 | 0.00091851 | -0.0020658 | -2.1434e-05 | 0.018494 | 0.00076264 | -1.3925 | 0.060752 | -0.0037 | 0.0044263 | -0.0051483 | -0.041199 | 60.2692 | -60.9787 | 60.6537 | -60.7956 | -61.2076 | -61.2808 | -0.041199 | 60.3058 | -61.084 | 60.4065 | -61.0245 | -61.0931 | -61.2259 | 0.045776 | -0.21057 | 0.17395 | 0.22888 | -0.25635 | -0.18311 | -0.30212 | -0.22888 | -0.059509 | -0.17395 | -0.073242 | 0 | -0.20142 | -0.068665 | -0.14191 | -0.009156 | 0.18311 | 121.6324 | 0.059509 | 121.4905 | 121.2479 | 121.3898 | 121.2936 | 121.3303 | -121.4584 | -121.5637 | 121.6782 | 121.431 | 60.9833 | 60.9833
356.4844 | 121.701 | -61.0245 | 60.4889 | 0.055313 | 0 | 0.064963 | 0.065424 | -0.0031403 | -0.00014304 | 0.001474 | 0.0093383 | 0.0018306 | -1.3899 | 0.060111 | -0.0034864 | 0.0067761 | 0.00040589 | -0.018311 | 60.2966 | -60.9833 | 60.6583 | -60.7956 | -61.1893 | -61.2671 | -0.059509 | 60.2829 | -61.084 | 60.379 | -61.0428 | -61.084 | -61.2534 | 0.041199 | -0.19226 | 0.16937 | 0.22888 | -0.24262 | -0.16479 | -0.28381 | -0.20599 | -0.059509 | -0.20599 | -0.10986 | -0.018311 | -0.22888 | -0.059509 | -0.16937 | 0 | 0.18768 | 121.6415 | 0.041198 | 121.463 | 121.2799 | 121.3669 | 121.3211 | 121.3074 | -121.4722 | -121.5729 | 121.6827 | 121.4035 | 61.0062 | 60.965
358.1875 | 121.8155 | -61.0016 | 60.4523 | 0.0019074 | 0 | 0.064536 | 0.062861 | -0.0042083 | -0.0020658 | 0.00061957 | -0.0028687 | -0.0022282 | -1.3931 | 0.067375 | -0.001991 | 0.0050671 | 0.0023285 | -0.068665 | 60.2005 | -60.9375 | 60.7086 | -60.6949 | -61.1114 | -61.203 | 0.036621 | 60.1776 | -61.0519 | 60.498 | -60.9146 | -60.9604 | -61.1572 | 0.064087 | -0.25177 | 0.25635 | 0.3067 | -0.20142 | -0.10986 | -0.2655 | -0.17395 | -0.050354 | -0.27466 | 0.045776 | 0.086975 | -0.15564 | 0.041199 | -0.10529 | 0.091553 | 0.24262 | 121.6461 | 0.13733 | 121.55 | 121.138 | 121.2296 | 121.2021 | 121.1792 | -121.3898 | -121.5042 | 121.7102 | 121.4996 | 60.9329 | 61.0382
359.9531 | 121.7194 | -61.0565 | 60.4385 | 0.024795 | 0 | 0.064322 | 0.066492 | -0.0037811 | -0.00078404 | -0.001944 | 0.0032349 | 0.0041806 | -1.3927 | 0.067588 | -0.0028454 | 0.0076307 | -0.00023491 | -0.036621 | 60.228 | -60.9833 | 60.6766 | -60.7452 | -61.1938 | -61.2762 | -0.018311 | 60.228 | -61.0565 | 60.4156 | -61.0245 | -61.1069 | -61.2488 | 0.073243 | -0.21057 | 0.23804 | 0.31128 | -0.21973 | -0.13733 | -0.29297 | -0.21057 | 0 | -0.21057 | -0.022889 | 0.032044 | -0.19226 | -0.050354 | -0.19226 | -0.050354 | 0.23804 | 121.6599 | 0.032044 | 121.4722 | 121.2112 | 121.2845 | 121.2845 | 121.2845 | -121.4218 | -121.4951 | 121.7331 | 121.4722 | 61.0199 | 61.0382
361.6562 | 121.756 | -61.0519 | 60.4294 | 0.032425 | 0 | 0.065176 | 0.063715 | -0.0063447 | -0.001852 | -0.0015166 | 0.0032349 | 0.0011898 | -1.3925 | 0.06417 | -0.0032728 | 0.0076307 | 0.0027557 | -0.10529 | 60.1685 | -60.997 | 60.672 | -60.7407 | -61.1893 | -61.2534 | -0.032043 | 60.1959 | -61.0977 | 60.4294 | -61.0245 | -61.0703 | -61.2442 | 0.054932 | -0.26093 | 0.24262 | 0.31128 | -0.20142 | -0.13733 | -0.25635 | -0.19226 | -0.045776 | -0.23346 | 0 | 0.027466 | -0.19226 | -0.01831 | -0.14648 | 0.027466 | 0.25635 | 121.669 | 0.073242 | 121.5271 | 121.1655 | 121.2936 | 121.2204 | 121.2479 | -121.4264 | -121.5271 | 121.7239 | 121.4813 | 60.9467 | 61.0199
363.4219 | 121.7926 | -61.0428 | 60.3653 | -0.0057221 | 0 | 0.065176 | 0.065211 | -0.0018585 | 0.00092496 | -0.0021576 | -0.0028687 | 0.001617 | -1.3957 | 0.066306 | -0.00092279 | 0.0072035 | -0.00044851 | -0.09613 | 60.1456 | -60.9879 | 60.6583 | -60.7773 | -61.2213 | -61.2946 | -0.036621 | 60.1547 | -61.0886 | 60.4477 | -61.0107 | -61.0474 | -61.2213 | 0.054932 | -0.21973 | 0.29297 | 0.2655 | -0.25177 | -0.17853 | -0.3067 | -0.23346 | -0.045776 | -0.21057 | 0.082398 | 0.032044 | -0.17853 | -0.004577 | -0.13275 | 0.041199 | 0.21057 | 121.6461 | 0.07782 | 121.5363 | 121.1334 | 121.2433 | 121.1884 | 121.1975 | -121.3531 | -121.4539 | 121.7011 | 121.4905 | 60.9467 | 61.0062
365.125 | 121.7377 | -61.0382 | 60.466 | 0.017166 | 0 | 0.062399 | 0.066065 | 0.0019867 | -0.002493 | 0.0027558 | 0.0062865 | 0.001617 | -1.3965 | 0.062248 | -0.0022046 | 0.0042127 | 0.0012603 | -0.027466 | 60.2692 | -60.9924 | 60.6583 | -60.759 | -61.1893 | -61.2808 | -0.018311 | 60.2371 | -61.0565 | 60.4156 | -61.0199 | -61.1069 | -61.2396 | 0.045776 | -0.19684 | 0.19226 | 0.27924 | -0.24262 | -0.15106 | -0.28839 | -0.19684 | -0.018311 | -0.22888 | -0.050354 | 0.018311 | -0.20142 | -0.068665 | -0.1831 | -0.050354 | 0.23346 | 121.6507 | 0.036622 | 121.4722 | 121.2616 | 121.2936 | 121.3074 | 121.2753 | -121.4584 | -121.5225 | 121.6965 | 121.4539 | 61.0107 | 61.0199
366.9062 | 121.6644 | -61.0428 | 60.5255 | 0.0095369 | 0 | 0.064963 | 0.064783 | 0.0019867 | -0.0039884 | -0.0017304 | 0.024597 | 0.00097624 | -1.3912 | 0.066306 | -0.0062634 | 0.0033581 | 0.0014741 | -0.082397 | 60.2646 | -60.9512 | 60.6354 | -60.791 | -61.1893 | -61.2534 | -0.041199 | 60.3149 | -61.0703 | 60.3973 | -61.0336 | -61.0794 | -61.2442 | 0.091553 | -0.26093 | 0.10986 | 0.25177 | -0.21057 | -0.14648 | -0.30212 | -0.23804 | -0.027465 | -0.21057 | -0.12817 | 0.009156 | -0.20142 | -0.036621 | -0.17395 | -0.009156 | 0.16022 | 121.5866 | 0.036621 | 121.4676 | 121.2158 | 121.3852 | 121.3074 | 121.3577 | -121.4767 | -121.5958 | 121.6782 | 121.4401 | 60.9604 | 61.0016
368.6094 | 121.7468 | -61.0336 | 60.4568 | 0.032425 | 0 | 0.065817 | 0.062647 | -0.0033539 | -0.0031338 | -0.00087583 | 0.0062865 | -0.00051916 | -1.3955 | 0.067375 | -0.0011364 | 0.0067761 | -0.00044851 | -0.11444 | 60.1868 | -60.9467 | 60.6491 | -60.7636 | -61.1801 | -61.2579 | -0.059509 | 60.1868 | -61.0657 | 60.4111 | -61.0245 | -61.0794 | -61.235 | 0.086975 | -0.27008 | 0.19226 | 0.27008 | -0.22431 | -0.14648 | -0.31128 | -0.23346 | -0.032044 | -0.27008 | -0.045776 | 0.009155 | -0.20142 | -0.045777 | -0.16937 | -0.013733 | 0.1831 | 121.5958 | 0.041199 | 121.4767 | 121.1334 | 121.2524 | 121.2204 | 121.2204 | -121.4035 | -121.5225 | 121.6827 | 121.4447 | 60.9192 | 60.9741
370.3594 | 121.7468 | -61.0016 | 60.4843 | 0.0095369 | 0 | 0.063467 | 0.062433 | -0.0027131 | -0.0020658 | 0.0010468 | 0.00018312 | -0.001801 | -1.3944 | 0.065666 | -0.0032728 | 0.0065625 | -0.0010895 | -0.041199 | 60.1913 | -60.9329 | 60.7544 | -60.6857 | -61.0931 | -61.203 | 0.027466 | 60.26 | -61.0062 | 60.4614 | -60.9741 | -61.0016 | -61.1984 | 0.068665 | -0.29297 | 0.27008 | 0.31586 | -0.20142 | -0.091553 | -0.27008 | -0.16022 | -0.004578 | -0.2243 | -0.022888 | 0.027466 | -0.19684 | 0 | -0.19226 | 0.004578 | 0.24719 | 121.6873 | 0.032044 | 121.4676 | 121.1243 | 121.2662 | 121.1929 | 121.2616 | -121.4172 | -121.4905 | 121.756 | 121.463 | 60.9604 | 61.0291
372.125 | 121.7331 | -61.0519 | 60.4477 | 0.032425 | 0 | 0.066458 | 0.066706 | -0.0022857 | -0.0027066 | -0.0021576 | 0.015442 | 0.002258 | -1.3944 | 0.057975 | -0.0022046 | 0.0074171 | -0.00044851 | -0.036621 | 60.2692 | -60.9695 | 60.6628 | -60.759 | -61.1755 | -61.2854 | -0.022888 | 60.2646 | -61.0657 | 60.4065 | -61.0062 | -61.0886 | -61.2167 | 0.082398 | -0.17853 | 0.21515 | 0.29297 | -0.23346 | -0.1236 | -0.31586 | -0.20599 | -0.013733 | -0.18311 | -0.041199 | 0.045776 | -0.16479 | -0.036621 | -0.15106 | -0.022888 | 0.21057 | 121.6324 | 0.059509 | 121.4722 | 121.2387 | 121.3303 | 121.3211 | 121.3165 | -121.4172 | -121.5134 | 121.7148 | 121.4584 | 61.0153 | 61.0291
373.8906 | 121.7972 | -60.965 | 60.4568 | -0.0057221 | 0 | 0.064749 | 0.062647 | 0.0024139 | -0.0029202 | -2.1434e-05 | 0.00018312 | 0.0011898 | -1.3965 | 0.069511 | -0.0022046 | 0.0067761 | 0.0023285 | -0.036621 | 60.2142 | -60.91 | 60.7819 | -60.64 | -61.0703 | -61.171 | 0.064087 | 60.2325 | -61.0107 | 60.5209 | -60.8917 | -60.9467 | -61.1572 | 0.054932 | -0.24262 | 0.32501 | 0.32501 | -0.20599 | -0.10529 | -0.26093 | -0.16022 | -0.045776 | -0.2243 | 0.064087 | 0.073242 | -0.19226 | 0.018311 | -0.14648 | 0.064087 | 0.27008 | 121.6919 | 0.11902 | 121.5317 | 121.1243 | 121.2433 | 121.1792 | 121.1975 | -121.3669 | -121.4676 | 121.7468 | 121.4859 | 60.9283 | 61.0291
375.5781 | 121.7194 | -61.0199 | 60.4797 | 0.040054 | 0 | 0.064108 | 0.067347 | 0.0026275 | -0.0031338 | -0.0017304 | 0.01239 | 0.0037532 | -1.3935 | 0.057762 | -0.0049818 | 0.0052807 | -0.0025849 | -0.045776 | 60.2417 | -60.9558 | 60.6583 | -60.7681 | -61.1526 | -61.2671 | -0.050354 | 60.2966 | -61.0703 | 60.4156 | -61.0062 | -61.0657 | -61.2259 | 0.064086 | -0.23804 | 0.17853 | 0.25177 | -0.24719 | -0.13275 | -0.31128 | -0.19684 | -0.050354 | -0.18311 | -0.064087 | 0.013732 | -0.20599 | -0.045777 | -0.15564 | 0.004577 | 0.18768 | 121.6141 | 0.064086 | 121.4859 | 121.1975 | 121.3669 | 121.2616 | 121.3165 | -121.4355 | -121.55 | 121.6782 | 121.4355 | 60.9741 | 60.9695
377.3438 | 121.7514 | -61.0153 | 60.4797 | 0.024795 | 0 | 0.066031 | 0.063929 | 0.0026275 | -0.0012112 | -0.00044863 | 0.0062865 | 0.0037532 | -1.3931 | 0.061393 | -0.0037 | 0.0067761 | 0.0010467 | -0.054932 | 60.2234 | -60.9421 | 60.6812 | -60.7452 | -61.1801 | -61.2625 | -0.009155 | 60.228 | -61.0703 | 60.434 | -61.0062 | -61.0565 | -61.2167 | 0.073242 | -0.25635 | 0.20142 | 0.27008 | -0.24719 | -0.16479 | -0.32043 | -0.23804 | -0.054931 | -0.25177 | -0.045776 | 0.009155 | -0.20142 | -0.041199 | -0.14648 | 0.013732 | 0.19684 | 121.6232 | 0.064086 | 121.5042 | 121.1655 | 121.2982 | 121.2387 | 121.2433 | -121.4218 | -121.55 | 121.6965 | 121.4493 | 60.9604 | 61.0062
379.1094 | 121.7651 | -61.0153 | 60.4706 | 0.0019074 | 0 | 0.06539 | 0.062647 | -0.0035675 | -0.003561 | 0.0019012 | 0.00018312 | -0.0013736 | -1.3961 | 0.070579 | -0.0015638 | 0.0078443 | -0.00044851 | -0.13275 | 60.2142 | -60.9375 | 60.6628 | -60.7636 | -61.1664 | -61.2534 | -0.059509 | 60.2097 | -61.0657 | 60.4385 | -60.9604 | -61.0199 | -61.1984 | 0.07782 | -0.25635 | 0.19226 | 0.25177 | -0.23804 | -0.15106 | -0.31586 | -0.22888 | -0.050354 | -0.26093 | -0.032043 | 0.054932 | -0.1831 | -0.004577 | -0.13275 | 0.045777 | 0.17395 | 121.6003 | 0.10529 | 121.5042 | 121.1517 | 121.2753 | 121.2296 | 121.225 | -121.4081 | -121.5363 | 121.6782 | 121.4539 | 60.8826 | 60.9558
380.7969 | 121.7148 | -61.0016 | 60.5026 | -0.0057221 | 0 | 0.062399 | 0.062647 | -0.0052765 | -0.0014248 | 0.00019217 | -0.0028687 | 0.00033544 | -1.3944 | 0.067588 | -0.0043408 | 0.0074171 | -0.00087591 | -0.036621 | 60.2142 | -60.8871 | 60.7269 | -60.6857 | -61.0977 | -61.203 | 0.013733 | 60.2692 | -60.997 | 60.4385 | -60.9695 | -61.0336 | -61.1938 | 0.11444 | -0.28839 | 0.2243 | 0.31586 | -0.20142 | -0.09613 | -0.31586 | -0.21057 | 0.004578 | -0.23346 | -0.064087 | 0.032044 | -0.19226 | -0.032043 | -0.19684 | -0.036621 | 0.20142 | 121.6141 | 0.027466 | 121.4355 | 121.1014 | 121.2662 | 121.2158 | 121.2708 | -121.3898 | -121.4996 | 121.7285 | 121.4401 | 60.965 | 61.0153
382.5 | 121.6599 | -61.084 | 60.4431 | -0.0057221 | 0 | 0.06539 | 0.066065 | -0.00057689 | -0.0029202 | 0.00083317 | -0.0028687 | -0.00030556 | -1.3929 | 0.053703 | -0.001991 | 0.0057081 | -2.1314e-05 | -0.14648 | 60.2188 | -60.9741 | 60.5759 | -60.8826 | -61.3174 | -61.3953 | -0.15564 | 60.2325 | -61.0886 | 60.3195 | -61.1435 | -61.2076 | -61.322 | 0.10986 | -0.2243 | 0.13275 | 0.20142 | -0.31128 | -0.23346 | -0.42114 | -0.34332 | -0.004578 | -0.21057 | -0.1236 | -0.05951 | -0.23804 | -0.1236 | -0.23346 | -0.11902 | 0.091553 | 121.55 | -0.054932 | 121.4081 | 121.1929 | 121.3211 | 121.3028 | 121.3165 | -121.4172 | -121.5317 | 121.6599 | 121.4035 | 60.9375 | 60.9283
384.2031 | 121.8063 | -61.0428 | 60.3745 | 0.0019074 | 0 | 0.064108 | 0.061793 | 0.0011321 | -0.002493 | 0.00040597 | -0.0059205 | -0.0013736 | -1.3952 | 0.065025 | 0.00078621 | 0.0078443 | 0.0038239 | -0.1236 | 60.1593 | -60.9558 | 60.672 | -60.7452 | -61.203 | -61.29 | -0.013733 | 60.1456 | -61.084 | 60.4614 | -60.9924 | -61.0565 | -61.1984 | 0.086975 | -0.21515 | 0.29755 | 0.29755 | -0.24719 | -0.16022 | -0.33417 | -0.24719 | -0.041198 | -0.22888 | 0.086975 | 0.050354 | -0.15564 | -0.013733 | -0.11444 | 0.027465 | 0.21057 | 121.6278 | 0.091552 | 121.5454 | 121.1151 | 121.2296 | 121.2021 | 121.1884 | -121.3303 | -121.4584 | 121.7148 | 121.5042 | 60.9192 | 61.0291
385.8906 | 121.788 | -60.9558 | 60.4706 | 0.0019074 | 0 | 0.065817 | 0.060938 | -0.0020721 | -0.0020658 | -0.00087583 | -0.0028687 | -9.1956e-05 | -1.3948 | 0.065025 | -0.00092279 | 0.0065625 | 0.0016877 | -0.064087 | 60.2188 | -60.9009 | 60.7681 | -60.6354 | -61.084 | -61.1755 | 0.050354 | 60.2188 | -61.0062 | 60.5072 | -60.91 | -60.9604 | -61.1481 | 0.054932 | -0.25177 | 0.29755 | 0.32043 | -0.21973 | -0.12817 | -0.27466 | -0.1831 | -0.050354 | -0.25177 | 0.036621 | 0.045777 | -0.19226 | -0.004577 | -0.14191 | 0.045777 | 0.2655 | 121.669 | 0.096131 | 121.5134 | 121.1197 | 121.225 | 121.1746 | 121.1746 | -121.3715 | -121.4767 | 121.7239 | 121.463 | 60.8917 | 61.0062
387.5938 | 121.7468 | -61.0565 | 60.4019 | 0.0019074 | 0 | 0.064322 | 0.063502 | 0.0036957 | -0.00078404 | -0.00023503 | 0.00018312 | -0.00073276 | -1.3937 | 0.069084 | -0.00092279 | 0.0046399 | -0.0015167 | -0.17853 | 60.2097 | -61.0016 | 60.5942 | -60.8597 | -61.3083 | -61.3632 | -0.13275 | 60.1593 | -61.0748 | 60.4065 | -61.0428 | -61.116 | -61.2534 | 0.054932 | -0.19226 | 0.19226 | 0.19684 | -0.3067 | -0.25177 | -0.36163 | -0.3067 | -0.01831 | -0.24262 | 0.004577 | 0.013733 | -0.19684 | -0.059509 | -0.17853 | -0.041199 | 0.14191 | 121.5958 | 0.032043 | 121.4813 | 121.2112 | 121.2341 | 121.2662 | 121.2158 | -121.4035 | -121.4767 | 121.6507 | 121.463 | 60.878 | 60.9238
389.2969 | 121.6873 | -61.0062 | 60.4935 | 0.047683 | 0 | 0.063895 | 0.066492 | 0.00070491 | -0.00057044 | -0.001944 | 0.015442 | 0.0024716 | -1.3925 | 0.062675 | -0.0051954 | 0.0046399 | -2.1314e-05 | -0.068665 | 60.2966 | -60.9604 | 60.6583 | -60.7773 | -61.171 | -61.2488 | -0.054932 | 60.3149 | -61.0611 | 60.3973 | -61.0199 | -61.0931 | -61.2167 | 0.045777 | -0.19684 | 0.1648 | 0.22888 | -0.24261 | -0.16479 | -0.28839 | -0.21057 | -0.054931 | -0.17853 | -0.09613 | -0.013732 | -0.21057 | -0.086975 | -0.15564 | -0.032044 | 0.18311 | 121.6187 | 0.041199 | 121.4584 | 121.257 | 121.376 | 121.3028 | 121.3211 | -121.4539 | -121.5546 | 121.6644 | 121.4035 | 60.9375 | 60.9512
391.0469 | 121.6644 | -61.0565 | 60.4614 | 0.0019074 | 0 | 0.065817 | 0.065424 | 0.0022003 | -0.00035684 | -0.0010894 | 0.00018312 | 0.0011898 | -1.3925 | 0.06417 | -0.0017774 | 0.0065625 | 0.00019229 | -0.13733 | 60.2463 | -60.9787 | 60.6079 | -60.8368 | -61.2808 | -61.3403 | -0.14191 | 60.2188 | -61.0428 | 60.3516 | -61.0977 | -61.1572 | -61.2808 | 0.07782 | -0.21515 | 0.14648 | 0.21973 | -0.28381 | -0.2243 | -0.36163 | -0.30212 | 0.013733 | -0.24262 | -0.10986 | -0.041198 | -0.2243 | -0.10071 | -0.23804 | -0.11444 | 0.14191 | 121.5866 | -0.054931 | 121.3943 | 121.225 | 121.2616 | 121.3028 | 121.2753 | -121.4401 | -121.5042 | 121.6644 | 121.4081 | 60.9192 | 60.9146
392.7969 | 121.7102 | -61.0428 | 60.4523 | 0.024795 | 0 | 0.064108 | 0.064356 | -0.00036309 | -0.00099764 | 0.0029694 | 0.00018312 | 0.0020444 | -1.3976 | 0.059684 | -0.0013502 | 0.0057081 | 0.0023285 | -0.091553 | 60.2417 | -60.9558 | 60.6766 | -60.7361 | -61.1984 | -61.2717 | -0.045776 | 60.2417 | -61.0428 | 60.4156 | -61.0199 | -61.1114 | -61.2396 | 0.086975 | -0.21057 | 0.2243 | 0.3067 | -0.22888 | -0.15564 | -0.31586 | -0.24261 | 0 | -0.21057 | -0.036622 | 0.022889 | -0.19684 | -0.068664 | -0.19684 | -0.068664 | 0.21973 | 121.6324 | 0.022889 | 121.4584 | 121.1975 | 121.2845 | 121.2845 | 121.2845 | -121.4081 | -121.4951 | 121.7194 | 121.4584 | 60.9512 | 60.997
394.5 | 121.6644 | -61.1069 | 60.434 | 0.0019074 | 0 | 0.066885 | 0.066065 | -0.00014949 | -0.00035684 | 0.00061957 | 0.00018312 | 0.00097624 | -1.3942 | 0.070579 | -0.0039136 | 0.0063489 | 0.0019013 | -0.17853 | 60.2417 | -60.9787 | 60.5484 | -60.91 | -61.3129 | -61.3953 | -0.16937 | 60.2097 | -61.0886 | 60.3607 | -61.1298 | -61.1755 | -61.29 | 0.12817 | -0.19226 | 0.11444 | 0.19684 | -0.28839 | -0.20599 | -0.41656 | -0.33417 | 0.018311 | -0.2243 | -0.073242 | -0.022888 | -0.1831 | -0.068664 | -0.20142 | -0.086975 | 0.068665 | 121.5271 | -0.041199 | 121.4493 | 121.2204 | 121.2982 | 121.3486 | 121.3165 | -121.4127 | -121.5225 | 121.6553 | 121.4676 | 60.9283 | 60.9375
396.25 | 121.7972 | -61.0245 | 60.3928 | 0.055313 | 0 | 0.068808 | 0.065851 | -0.0018585 | 0.0015658 | -0.00044863 | 0.015442 | -0.00116 | -1.3925 | 0.063316 | 0.00078621 | 0.0095533 | 0.0025421 | -0.1236 | 60.1685 | -60.9787 | 60.7132 | -60.6812 | -61.1618 | -61.2259 | 0 | 60.1959 | -61.1023 | 60.4568 | -60.9741 | -61.0428 | -61.1938 | 0.045776 | -0.2243 | 0.32044 | 0.34332 | -0.20142 | -0.13733 | -0.24719 | -0.1831 | -0.07782 | -0.19684 | 0.064087 | 0.050354 | -0.16937 | -0.018311 | -0.091553 | 0.059509 | 0.29755 | 121.6919 | 0.12817 | 121.5591 | 121.1472 | 121.2982 | 121.1929 | 121.2204 | -121.3715 | -121.4951 | 121.7377 | 121.4813 | 60.9009 | 61.0245
398.0156 | 121.7056 | -60.9924 | 60.498 | 0.0019074 | 0 | 0.063681 | 0.061793 | -0.0039947 | -0.00035684 | 0.0010468 | 0.0032349 | -0.00073276 | -1.394 | 0.066306 | -0.0022046 | 0.0078443 | -0.00023491 | -0.073242 | 60.2188 | -60.8963 | 60.7407 | -60.6857 | -61.1023 | -61.1984 | 0 | 60.2646 | -61.0107 | 60.4523 | -60.9695 | -61.0016 | -61.1847 | 0.096131 | -0.27924 | 0.24262 | 0.3067 | -0.20599 | -0.10986 | -0.30212 | -0.20599 | -0.01831 | -0.23346 | -0.045776 | 0.022889 | -0.19226 | -0.009155 | -0.17395 | 0.009155 | 0.21057 | 121.637 | 0.041199 | 121.463 | 121.1151 | 121.2753 | 121.2112 | 121.257 | -121.3943 | -121.5088 | 121.7331 | 121.4447 | 60.9192 | 60.9924
399.7344 | 121.8018 | -60.965 | 60.434 | -0.0057221 | 0 | 0.063467 | 0.063502 | -0.0035675 | -0.0016384 | -0.001944 | -0.0028687 | -0.0022282 | -1.3972 | 0.060111 | -6.8386e-05 | 0.0061353 | -0.0017303 | -0.14648 | 60.2188 | -60.9329 | 60.7178 | -60.6857 | -61.1114 | -61.1847 | 0.032043 | 60.2234 | -61.0016 | 60.5118 | -60.8871 | -60.9375 | -61.1435 | 0.032044 | -0.21515 | 0.28381 | 0.27924 | -0.21973 | -0.14648 | -0.25177 | -0.17853 | -0.036621 | -0.21057 | 0.07782 | 0.07782 | -0.17853 | 0.027466 | -0.14191 | 0.064087 | 0.24719 | 121.6507 | 0.11444 | 121.5134 | 121.1517 | 121.225 | 121.1838 | 121.1884 | -121.3669 | -121.4355 | 121.6827 | 121.4767 | 60.8185 | 60.997
401.5 | 121.8018 | -60.9512 | 60.498 | 0.0019074 | 0 | 0.064108 | 0.063074 | -0.0029267 | -0.0031338 | 0.00019217 | 0.00018312 | 0.00076264 | -1.3952 | 0.067161 | -0.005409 | 0.0059217 | -0.0019439 | -0.082397 | 60.2234 | -60.8963 | 60.791 | -60.6171 | -61.0565 | -61.1206 | 0.073242 | 60.2509 | -60.9787 | 60.5392 | -60.8688 | -60.9146 | -61.1069 | 0.054932 | -0.27466 | 0.29297 | 0.33417 | -0.16937 | -0.10529 | -0.2243 | -0.16022 | -0.027466 | -0.24719 | 0.041199 | 0.082398 | -0.15564 | 0.036621 | -0.12817 | 0.064087 | 0.27924 | 121.6873 | 0.10986 | 121.5179 | 121.1197 | 121.2296 | 121.1746 | 121.2021 | -121.3943 | -121.4767 | 121.7422 | 121.4905 | 60.8688 | 61.0245
403.2031 | 121.7514 | -61.0107 | 60.4385 | 0.055313 | 0 | 0.067313 | 0.064142 | 0.0034821 | -0.00035684 | 0.0046784 | 0.015442 | 0.0014034 | -1.3946 | 0.062461 | -0.00092279 | 0.0086987 | -0.00023491 | -0.13733 | 60.2005 | -60.9375 | 60.6995 | -60.6949 | -61.1481 | -61.2259 | 0 | 60.2097 | -61.0611 | 60.4523 | -60.9695 | -61.0336 | -61.1893 | 0.073242 | -0.23804 | 0.26093 | 0.31586 | -0.21515 | -0.13733 | -0.28839 | -0.21057 | -0.050354 | -0.22888 | 0.013733 | 0.041199 | -0.17853 | -0.022888 | -0.12817 | 0.027466 | 0.24262 | 121.637 | 0.091553 | 121.5134 | 121.138 | 121.2708 | 121.2112 | 121.2204 | -121.376 | -121.4996 | 121.7102 | 121.463 | 60.8734 | 61.0107
404.9688 | 121.8018 | -61.0062 | 60.3882 | 0.0095369 | 0 | 0.065817 | 0.066065 | -0.0029267 | 0.0013522 | -0.0017304 | -0.0089723 | -0.00094636 | -1.395 | 0.062248 | 0.00057241 | 0.0080579 | 0.00061949 | -0.14191 | 60.1639 | -60.9512 | 60.6949 | -60.7361 | -61.1847 | -61.2488 | -0.022888 | 60.1593 | -61.0428 | 60.466 | -60.9695 | -61.0336 | -61.1893 | 0.054932 | -0.22431 | 0.3067 | 0.27008 | -0.24261 | -0.17853 | -0.29755 | -0.23346 | -0.036621 | -0.22888 | 0.077819 | 0.036622 | -0.1831 | -0.027465 | -0.14648 | 0.009156 | 0.21515 | 121.6461 | 0.073243 | 121.5088 | 121.1151 | 121.2021 | 121.17 | 121.1655 | -121.3394 | -121.431 | 121.7011 | 121.4722 | 60.8643 | 60.9833
406.6562 | 121.6599 | -60.9741 | 60.5347 | -0.0057221 | 0 | 0.066031 | 0.065424 | -0.0039947 | -0.0014248 | 0.00083317 | -0.0059205 | 0.00076264 | -1.3963 | 0.06417 | -0.005409 | 0.0048535 | 0.00019229 | -0.086975 | 60.26 | -60.8826 | 60.7315 | -60.6949 | -61.1023 | -61.203 | -0.032043 | 60.3058 | -60.9695 | 60.4477 | -60.9604 | -61.0153 | -61.171 | 0.091553 | -0.27466 | 0.19684 | 0.27924 | -0.22888 | -0.12817 | -0.32044 | -0.21973 | 0.004578 | -0.22888 | -0.086975 | 0.013733 | -0.19684 | -0.041199 | -0.20142 | -0.045777 | 0.18768 | 121.6141 | 0.009155 | 121.4172 | 121.1426 | 121.2753 | 121.2341 | 121.2799 | -121.4172 | -121.5042 | 121.7056 | 121.4218 | 60.8871 | 60.9421
408.4219 | 121.6553 | -60.9833 | 60.5072 | 0.0095369 | 0 | 0.064536 | 0.064783 | 0.0015595 | -0.0031338 | 0.00083317 | 0.00018312 | 0.0028988 | -1.3925 | 0.056266 | -0.0060498 | 0.0048535 | 0.0019013 | -0.15564 | 60.2875 | -60.91 | 60.6583 | -60.7452 | -61.1664 | -61.2442 | -0.045776 | 60.3607 | -61.0199 | 60.4156 | -61.0016 | -61.0611 | -61.2076 | 0.073242 | -0.21973 | 0.15106 | 0.23804 | -0.26093 | -0.18311 | -0.33417 | -0.25635 | -0.036621 | -0.14648 | -0.091553 | -0.018311 | -0.22431 | -0.07782 | -0.18768 | -0.041199 | 0.1648 | 121.5683 | 0.01831 | 121.4355 | 121.1975 | 121.3806 | 121.2708 | 121.344 | -121.4172 | -121.5271 | 121.6415 | 121.3989 | 60.8276 | 60.9375
410.125 | 121.6827 | -61.0062 | 60.5164 | 0.0095369 | 0 | 0.065176 | 0.064142 | 0.0026275 | -0.0012112 | 0.001474 | -0.0089723 | 0.00097624 | -1.3948 | 0.066093 | -0.0043408 | 0.0046399 | -0.0030121 | -0.09613 | 60.2509 | -60.878 | 60.7224 | -60.7086 | -61.1069 | -61.2122 | -0.041199 | 60.2829 | -60.9924 | 60.4294 | -60.9695 | -61.0336 | -61.1893 | 0.12817 | -0.2655 | 0.20599 | 0.29755 | -0.20599 | -0.10071 | -0.33417 | -0.22888 | 0.013733 | -0.23346 | -0.086975 | 0.036622 | -0.1831 | -0.027465 | -0.19684 | -0.041198 | 0.16937 | 121.6003 | 0.022889 | 121.4218 | 121.1288 | 121.2753 | 121.257 | 121.2891 | -121.3943 | -121.5088 | 121.7285 | 121.4355 | 60.91 | 60.965
411.875 | 121.6736 | -61.0199 | 60.4568 | 0.0019074 | 0 | 0.064536 | 0.062433 | -0.0014313 | -0.0031338 | 0.0010468 | 0.00018312 | 0.0011898 | -1.3929 | 0.057121 | -0.0015638 | 0.0054945 | -0.0010895 | -0.22888 | 60.2051 | -60.9787 | 60.5759 | -60.8688 | -61.2854 | -61.3586 | -0.17853 | 60.2463 | -61.0794 | 60.3561 | -61.0886 | -61.1481 | -61.2579 | 0.041198 | -0.25177 | 0.11902 | 0.15106 | -0.33875 | -0.2655 | -0.37994 | -0.3067 | -0.05951 | -0.21057 | -0.10071 | -0.068665 | -0.23804 | -0.12817 | -0.17853 | -0.068664 | 0.10986 | 121.5546 | -0.009155 | 121.4355 | 121.1838 | 121.3257 | 121.225 | 121.2662 | -121.4355 | -121.5363 | 121.5958 | 121.376 | 60.791 | 60.8414
413.5781 | 121.6827 | -60.9879 | 60.4843 | 0.0095369 | 0 | 0.063895 | 0.06457 | -0.0042083 | -0.0027066 | -0.001303 | -0.0059205 | 0.0024716 | -1.3916 | 0.067802 | 0.00035881 | 0.0065625 | -0.0015167 | -0.13275 | 60.26 | -60.9009 | 60.6857 | -60.7315 | -61.1755 | -61.2625 | -0.054932 | 60.2692 | -61.0153 | 60.4202 | -61.0016 | -61.0794 | -61.2167 | 0.086975 | -0.2243 | 0.20142 | 0.25635 | -0.27466 | -0.18768 | -0.36163 | -0.27466 | -0.027466 | -0.21515 | -0.064087 | -0.013733 | -0.22888 | -0.091553 | -0.20142 | -0.064087 | 0.16937 | 121.5866 | 0.013733 | 121.4355 | 121.1609 | 121.2845 | 121.2479 | 121.257 | -121.3852 | -121.4996 | 121.6736 | 121.4081 | 60.8551 | 60.9329
415.3438 | 121.6553 | -61.0611 | 60.4752 | 0.0019074 | 0 | 0.065817 | 0.064997 | -0.0024995 | -0.0031338 | -0.00044863 | 0.00018312 | 0.00097624 | -1.3948 | 0.059684 | -0.00070919 | 0.0074171 | 0.0057465 | -0.21973 | 60.2737 | -60.9467 | 60.6079 | -60.8414 | -61.2717 | -61.3449 | -0.16937 | 60.2737 | -61.0611 | 60.347 | -61.0931 | -61.1618 | -61.29 | 0.11444 | -0.20142 | 0.13275 | 0.21973 | -0.28381 | -0.21057 | -0.39825 | -0.32501 | 0 | -0.20142 | -0.12817 | -0.032044 | -0.22888 | -0.10071 | -0.22888 | -0.10071 | 0.10529 | 121.5546 | -0.032044 | 121.4081 | 121.2204 | 121.3348 | 121.3348 | 121.3348 | -121.4218 | -121.5363 | 121.669 | 121.4081 | 60.8414 | 60.8917
417.1094 | 121.6644 | -60.9787 | 60.5804 | -0.013352 | 0 | 0.064963 | 0.066492 | -0.0035675 | -0.002493 | 0.00061957 | 0.00018312 | 0.001617 | -1.3931 | 0.05947 | -0.0056226 | 0.0057081 | -0.00066231 | -0.17395 | 60.2829 | -60.8734 | 60.6674 | -60.7498 | -61.1481 | -61.2259 | -0.086975 | 60.3424 | -60.997 | 60.4294 | -60.9695 | -61.0382 | -61.1801 | 0.10529 | -0.29755 | 0.086975 | 0.22888 | -0.24719 | -0.16937 | -0.35248 | -0.27466 | -0.01831 | -0.23804 | -0.15106 | 0.009156 | -0.20142 | -0.059509 | -0.18311 | -0.041199 | 0.1236 | 121.5408 | 0.027466 | 121.4264 | 121.1563 | 121.3394 | 121.2616 | 121.3211 | -121.4539 | -121.5775 | 121.6461 | 121.4081 | 60.8047 | 60.8917
418.8594 | 121.7926 | -60.9924 | 60.3973 | 0.0095369 | 0 | 0.063254 | 0.063715 | 0.0015595 | -0.00078404 | -2.1434e-05 | 0.0032349 | 0.00012184 | -1.3914 | 0.062034 | 0.0016406 | 0.0076307 | -0.00066231 | -0.22888 | 60.1593 | -60.9467 | 60.6354 | -60.7544 | -61.1893 | -61.2762 | -0.045776 | 60.1959 | -61.0565 | 60.4797 | -60.9695 | -61.0382 | -61.1755 | 0.045777 | -0.23804 | 0.23804 | 0.23804 | -0.28381 | -0.19684 | -0.32959 | -0.24262 | -0.064087 | -0.20142 | 0.082397 | 0.022889 | -0.1831 | -0.045776 | -0.11902 | 0.018311 | 0.19226 | 121.582 | 0.086976 | 121.5363 | 121.106 | 121.2524 | 121.1517 | 121.1884 | -121.344 | -121.4539 | 121.6278 | 121.4722 | 60.7636 | 60.9467
420.5625 | 121.6644 | -60.9329 | 60.553 | 0.0095369 | 0 | 0.063895 | 0.063502 | -0.0014313 | -0.0027066 | 0.00019217 | 0.018494 | 0.001617 | -1.3935 | 0.056693 | -0.0060498 | 0.0080579 | -0.0021575 | -0.17853 | 60.347 | -60.8459 | 60.7178 | -60.6903 | -61.0931 | -61.171 | -0.064087 | 60.3607 | -60.9695 | 60.4477 | -60.965 | -61.0153 | -61.1526 | 0.086975 | -0.20599 | 0.16479 | 0.24261 | -0.23804 | -0.16022 | -0.32501 | -0.24719 | -0.036621 | -0.19226 | -0.10529 | -0.032044 | -0.21973 | -0.082398 | -0.18311 | -0.045777 | 0.15564 | 121.5637 | 0.004577 | 121.4172 | 121.1929 | 121.3303 | 121.2799 | 121.2936 | -121.3989 | -121.5225 | 121.6507 | 121.3806 | 60.7544 | 60.8688
422.3125 | 121.6965 | -60.9833 | 60.5164 | 0.040054 | 0 | 0.065604 | 0.067133 | 0.0015595 | 0.002634 | 0.002115 | 0.018494 | 0.001617 | -1.3908 | 0.060539 | -0.0043408 | 0.0054945 | -0.0021575 | -0.15106 | 60.347 | -60.9375 | 60.6857 | -60.7452 | -61.1343 | -61.2259 | -0.045776 | 60.3287 | -61.0382 | 60.4431 | -60.9558 | -61.0245 | -61.171 | 0.045776 | -0.16937 | 0.16937 | 0.23804 | -0.24262 | -0.15106 | -0.28839 | -0.19684 | -0.054932 | -0.18768 | -0.073242 | 0.027465 | -0.18768 | -0.041199 | -0.13275 | 0.013733 | 0.19226 | 121.6232 | 0.082397 | 121.4813 | 121.2845 | 121.3669 | 121.3303 | 121.3119 | -121.4539 | -121.5546 | 121.669 | 121.4264 | 60.8322 | 60.9375
424.0781 | 121.6599 | -61.0382 | 60.5026 | -0.0057221 | 0 | 0.065604 | 0.064356 | -0.00036309 | -0.00057044 | 0.0016876 | 0.0032349 | 0.0014034 | -1.3933 | 0.063102 | -0.0034864 | 0.0054945 | -2.1314e-05 | -0.18768 | 60.2417 | -60.9283 | 60.6308 | -60.791 | -61.235 | -61.3129 | -0.1236 | 60.2371 | -61.0382 | 60.3836 | -61.0519 | -61.1206 | -61.2488 | 0.10986 | -0.26093 | 0.12817 | 0.24719 | -0.27466 | -0.19684 | -0.38452 | -0.3067 | 0 | -0.2655 | -0.11902 | -0.013733 | -0.21057 | -0.082397 | -0.21057 | -0.082397 | 0.13733 | 121.5591 | -0.013733 | 121.4218 | 121.17 | 121.2753 | 121.2799 | 121.2753 | -121.431 | -121.5408 | 121.669 | 121.4218 | 60.8505 | 60.9146
425.7656 | 121.8018 | -60.997 | 60.4385 | -0.0057221 | 0 | 0.066245 | 0.063715 | 0.00070491 | -0.0027066 | -0.0027984 | -0.0059205 | 0.00033544 | -1.3925 | 0.058402 | -0.00028199 | 0.0072035 | 0.00019229 | -0.24261 | 60.2371 | -60.9512 | 60.6857 | -60.7269 | -61.1801 | -61.2488 | -0.059509 | 60.1959 | -61.0153 | 60.498 | -60.9421 | -61.0199 | -61.1481 | 0.045776 | -0.20142 | 0.24719 | 0.27008 | -0.25177 | -0.18311 | -0.29755 | -0.22888 | -0.018311 | -0.24262 | 0.059509 | 0.054931 | -0.15106 | -0.022888 | -0.13275 | -0.004577 | 0.2243 | 121.637 | 0.073242 | 121.5134 | 121.1884 | 121.2112 | 121.2341 | 121.1929 | -121.3898 | -121.4539 | 121.6827 | 121.4951 | 60.7544 | 60.9375
427.4688 | 121.8246 | -60.9512 | 60.498 | 0.0095369 | 0 | 0.06304 | 0.063288 | -0.0033539 | -0.0027066 | 0.001474 | -0.0059205 | -0.001801 | -1.3961 | 0.065452 | -0.0015638 | 0.0069897 | 0.0033967 | -0.16937 | 60.2371 | -60.8734 | 60.7864 | -60.585 | -61.0336 | -61.1298 | 0.086975 | 60.26 | -60.9604 | 60.5713 | -60.8093 | -60.8917 | -61.0794 | 0.07782 | -0.26093 | 0.28839 | 0.36621 | -0.17853 | -0.082397 | -0.25635 | -0.16022 | -0.009155 | -0.23804 | 0.073242 | 0.14191 | -0.12817 | 0.059509 | -0.11902 | 0.068664 | 0.28839 | 121.6599 | 0.15106 | 121.5317 | 121.1105 | 121.2204 | 121.1884 | 121.2112 | -121.3715 | -121.4584 | 121.7377 | 121.5225 | 60.7819 | 61.0382
429.25 | 121.7651 | -60.9787 | 60.4935 | 0.032425 | 0 | 0.065176 | 0.06457 | 0.00091851 | -0.0014248 | -0.00087583 | 0.00018312 | -0.00073276 | -1.3969 | 0.070793 | -0.0024182 | 0.0074171 | 0.0025421 | -0.22888 | 60.2463 | -60.9009 | 60.6903 | -60.7086 | -61.1389 | -61.2167 | -0.059509 | 60.2463 | -60.9924 | 60.4889 | -60.9329 | -60.9787 | -61.1526 | 0.07782 | -0.24719 | 0.19684 | 0.27008 | -0.23804 | -0.16022 | -0.31586 | -0.23804 | -0.013733 | -0.24719 | -0.004577 | 0.045777 | -0.17395 | 0 | -0.16022 | 0.013733 | 0.19226 | 121.5912 | 0.05951 | 121.4813 | 121.1472 | 121.2387 | 121.225 | 121.225 | -121.3943 | -121.4859 | 121.669 | 121.4676 | 60.7498 | 60.9192
430.9531 | 121.7102 | -60.9558 | 60.5164 | 0.040054 | 0 | 0.064749 | 0.063074 | -0.0027131 | -0.0012112 | 0.00040597 | 0.0062865 | 0.0028988 | -1.3931 | 0.057762 | -0.0037 | 0.0065625 | -0.00087591 | -0.14191 | 60.3561 | -60.8917 | 60.7361 | -60.6995 | -61.0977 | -61.1847 | -0.036621 | 60.3058 | -60.9879 | 60.4797 | -60.9604 | -61.0199 | -61.1526 | 0.064087 | -0.16022 | 0.21973 | 0.25635 | -0.22888 | -0.14191 | -0.29297 | -0.20599 | -0.032043 | -0.21057 | -0.036621 | -0.004577 | -0.19684 | -0.064086 | -0.16479 | -0.032043 | 0.19226 | 121.6278 | 0.027466 | 121.4676 | 121.2479 | 121.2936 | 121.312 | 121.2616 | -121.4081 | -121.5042 | 121.6919 | 121.4355 | 60.8139 | 60.9192
432.6562 | 121.6736 | -61.0474 | 60.4889 | -0.0057221 | 0 | 0.064749 | 0.064997 | 0.0011321 | 0.0013522 | -0.0015166 | 0.0032349 | 0.00097624 | -1.3944 | 0.061393 | -0.0015638 | 0.0076307 | -2.1314e-05 | -0.27466 | 60.2692 | -60.91 | 60.5896 | -60.8597 | -61.2717 | -61.3403 | -0.16937 | 60.26 | -61.0474 | 60.3836 | -61.0703 | -61.1343 | -61.2534 | 0.13733 | -0.21973 | 0.10071 | 0.18768 | -0.29297 | -0.2243 | -0.4303 | -0.36163 | 0 | -0.22888 | -0.10529 | -0.022888 | -0.20599 | -0.086975 | -0.20599 | -0.086975 | 0.050354 | 121.4996 | -0.022888 | 121.431 | 121.1792 | 121.3074 | 121.3165 | 121.3074 | -121.3989 | -121.5363 | 121.637 | 121.431 | 60.7727 | 60.878
434.4375 | 121.6827 | -60.9467 | 60.5896 | -0.013352 | 0 | 0.062827 | 0.066279 | -0.0014313 | 0.00049776 | -0.00087583 | 0.00018312 | 0.003326 | -1.3948 | 0.059898 | -0.0043408 | 0.0054945 | -0.0034393 | -0.18768 | 60.3104 | -60.8597 | 60.6949 | -60.6995 | -61.1298 | -61.1938 | -0.082397 | 60.3241 | -60.9695 | 60.4431 | -60.9604 | -61.0062 | -61.1847 | 0.086975 | -0.27924 | 0.10529 | 0.24719 | -0.24719 | -0.18311 | -0.33417 | -0.27008 | -0.022888 | -0.2655 | -0.14648 | -0.013733 | -0.23804 | -0.05951 | -0.21515 | -0.036622 | 0.16022 | 121.5546 | 0.009155 | 121.4127 | 121.17 | 121.2936 | 121.257 | 121.2708 | -121.4493 | -121.5591 | 121.6415 | 121.3898 | 60.759 | 60.8643
436.2031 | 121.6873 | -61.0245 | 60.498 | -0.0057221 | 0 | 0.066031 | 0.066706 | -0.0018585 | -0.0020658 | 0.002115 | 0.00018312 | 0.00054904 | -1.3927 | 0.059043 | -0.00092279 | 0.0069897 | -0.0025849 | -0.29297 | 60.228 | -60.9604 | 60.585 | -60.8459 | -61.2717 | -61.322 | -0.15564 | 60.2188 | -61.0245 | 60.3653 | -61.0748 | -61.1343 | -61.2396 | 0.064087 | -0.27008 | 0.086975 | 0.17853 | -0.29755 | -0.24719 | -0.36163 | -0.31128 | 0 | -0.27924 | -0.13275 | -0.050354 | -0.21515 | -0.10986 | -0.21515 | -0.10986 | 0.11444 | 121.5454 | -0.050354 | 121.3898 | 121.1884 | 121.2433 | 121.2524 | 121.2433 | -121.4584 | -121.5225 | 121.6095 | 121.3898 | 60.7315 | 60.8688
437.8906 | 121.8063 | -60.9421 | 60.4843 | -0.0057221 | 0 | 0.064108 | 0.061579 | 0.0026275 | -0.003561 | 0.00040597 | -0.0028687 | -0.00030556 | -1.3935 | 0.067161 | -0.0037 | 0.0089123 | -0.00087591 | -0.20142 | 60.228 | -60.8734 | 60.7727 | -60.6125 | -61.0565 | -61.1389 | 0.07782 | 60.2509 | -60.9787 | 60.5621 | -60.8505 | -60.9055 | -61.0886 | 0.068665 | -0.25635 | 0.28839 | 0.32959 | -0.19684 | -0.11444 | -0.2655 | -0.18311 | -0.036621 | -0.23346 | 0.07782 | 0.091553 | -0.14648 | 0.036621 | -0.10986 | 0.073242 | 0.26093 | 121.6461 | 0.12817 | 121.5408 | 121.1014 | 121.2296 | 121.17 | 121.1929 | -121.3577 | -121.463 | 121.7148 | 121.5042 | 60.7407 | 61.0199
439.5938 | 121.8018 | -60.9421 | 60.498 | 0.0019074 | 0 | 0.064108 | 0.06222 | -0.0039947 | 0.0011386 | -0.0021576 | 0.00018312 | -0.00073276 | -1.3931 | 0.065025 | -0.0028454 | 0.0061353 | 0.0046783 | -0.2243 | 60.2142 | -60.9009 | 60.7544 | -60.6445 | -61.0703 | -61.1526 | 0.022888 | 60.2463 | -60.9833 | 60.5255 | -60.8505 | -60.9192 | -61.0931 | 0.041199 | -0.28381 | 0.25635 | 0.29755 | -0.21057 | -0.12817 | -0.25177 | -0.16937 | -0.041198 | -0.25177 | 0.027466 | 0.091553 | -0.15106 | 0.022889 | -0.10986 | 0.064087 | 0.25635 | 121.6553 | 0.13275 | 121.5088 | 121.1151 | 121.2296 | 121.1563 | 121.1884 | -121.3989 | -121.4813 | 121.6965 | 121.4676 | 60.7178 | 60.965
441.3438 | 121.7834 | -61.0016 | 60.4385 | 0.0019074 | 0 | 0.065604 | 0.064997 | -0.0012177 | -0.00078404 | 0.00061957 | -0.0028687 | 0.0014034 | -1.3955 | 0.066093 | 0.00014521 | 0.0072035 | -0.0015167 | -0.30212 | 60.2097 | -60.9238 | 60.672 | -60.7315 | -61.1847 | -61.2534 | -0.050354 | 60.1822 | -61.0336 | 60.4843 | -60.9512 | -61.0291 | -61.1435 | 0.07782 | -0.22888 | 0.23346 | 0.27008 | -0.25177 | -0.1831 | -0.32959 | -0.26093 | -0.032043 | -0.25635 | 0.045776 | 0.050354 | -0.14191 | -0.027466 | -0.10986 | 0.004577 | 0.19226 | 121.5958 | 0.082397 | 121.5179 | 121.1334 | 121.2158 | 121.2112 | 121.1838 | -121.3623 | -121.4722 | 121.6736 | 121.4859 | 60.6995 | 60.9512
443.1094 | 121.7743 | -60.9375 | 60.5026 | 0.0095369 | 0 | 0.065817 | 0.064997 | -0.0046357 | -0.00035684 | -0.0023712 | -0.0059205 | 0.00033544 | -1.3933 | 0.064811 | -0.0017774 | 0.0093397 | 0.00019229 | -0.28839 | 60.2554 | -60.9055 | 60.7315 | -60.6812 | -61.1023 | -61.1801 | -0.018311 | 60.2783 | -60.9741 | 60.5347 | -60.8643 | -60.9146 | -61.0931 | 0.032043 | -0.24719 | 0.22888 | 0.25635 | -0.24262 | -0.16479 | -0.27466 | -0.19684 | -0.036621 | -0.22431 | 0.032043 | 0.073242 | -0.15564 | 0.022888 | -0.11902 | 0.059509 | 0.22431 | 121.637 | 0.10986 | 121.5088 | 121.1609 | 121.2524 | 121.1929 | 121.2158 | -121.4081 | -121.4767 | 121.669 | 121.4722 | 60.6491 | 60.9192
444.8125 | 121.756 | -60.9283 | 60.5072 | 0.024795 | 0 | 0.065604 | 0.063288 | -0.0020721 | -0.0016384 | 0.00040597 | 0.0032349 | 0.00076264 | -1.395 | 0.067375 | -0.0037 | 0.0067761 | 0.0016877 | -0.28839 | 60.2463 | -60.91 | 60.7224 | -60.6766 | -61.1069 | -61.171 | -0.059509 | 60.2737 | -60.9695 | 60.4843 | -60.9329 | -60.9787 | -61.1343 | 0.018311 | -0.26093 | 0.21515 | 0.25177 | -0.24261 | -0.17853 | -0.26093 | -0.19684 | -0.041198 | -0.23346 | -0.022888 | -0.004577 | -0.20599 | -0.050354 | -0.16479 | -0.009156 | 0.23346 | 121.6324 | 0.036621 | 121.4539 | 121.1563 | 121.2433 | 121.1746 | 121.2021 | -121.4172 | -121.4767 | 121.6507 | 121.4127 | 60.64 | 60.8688
446.5781 | 121.8292 | -60.9146 | 60.5072 | 0.017166 | 0 | 0.064108 | 0.063929 | -0.00057689 | -0.0027066 | 0.0010468 | 0.00018312 | -0.00030556 | -1.3955 | 0.065879 | -0.0037 | 0.0067761 | 0.0012603 | -0.21973 | 60.26 | -60.8551 | 60.8139 | -60.5759 | -61.0107 | -61.1069 | 0.086975 | 60.2783 | -60.9238 | 60.5804 | -60.8093 | -60.8597 | -61.0428 | 0.059509 | -0.24719 | 0.3067 | 0.33874 | -0.19226 | -0.09613 | -0.25177 | -0.15564 | -0.009155 | -0.22888 | 0.073242 | 0.10529 | -0.12817 | 0.054932 | -0.11902 | 0.064087 | 0.27924 | 121.669 | 0.11444 | 121.5042 | 121.1151 | 121.2021 | 121.1746 | 121.1929 | -121.3623 | -121.431 | 121.7285 | 121.4951 | 60.6949 | 61.0016
448.3438 | 121.7056 | -60.9558 | 60.5438 | 0.032425 | 0 | 0.065817 | 0.066706 | 0.0041229 | -0.0029202 | 0.0012604 | 0.015442 | 0.0028988 | -1.3948 | 0.058189 | -0.0049818 | 0.0061353 | -0.00066231 | -0.21515 | 60.3561 | -60.8871 | 60.7498 | -60.6857 | -61.0886 | -61.1664 | -0.045776 | 60.3378 | -60.9695 | 60.4706 | -60.9421 | -61.0062 | -61.1435 | 0.068665 | -0.18768 | 0.20599 | 0.27008 | -0.21057 | -0.13275 | -0.27924 | -0.20142 | -0.013732 | -0.20599 | -0.073242 | 0.013733 | -0.18768 | -0.050354 | -0.17395 | -0.036622 | 0.20142 | 121.637 | 0.027465 | 121.4401 | 121.2433 | 121.3074 | 121.312 | 121.2936 | -121.431 | -121.5134 | 121.7056 | 121.4264 | 60.7407 | 60.91
450.1094 | 121.788 | -60.8734 | 60.5804 | 0.0095369 | 0 | 0.06304 | 0.063074 | -0.0044221 | -0.001852 | -2.1434e-05 | -0.0028687 | -0.001801 | -1.3955 | 0.06417 | -0.0013502 | 0.0067761 | -0.00087591 | -0.2243 | 60.3012 | -60.8002 | 60.8551 | -60.5209 | -60.9741 | -61.0657 | 0.073242 | 60.3287 | -60.878 | 60.5896 | -60.7773 | -60.8551 | -61.0382 | 0.073242 | -0.27924 | 0.27466 | 0.35248 | -0.19226 | -0.10071 | -0.2655 | -0.17395 | -0.004578 | -0.25177 | 0.009156 | 0.09613 | -0.16479 | 0.01831 | -0.16022 | 0.022888 | 0.27924 | 121.6553 | 0.10071 | 121.4676 | 121.1014 | 121.2067 | 121.1746 | 121.2021 | -121.3806 | -121.4584 | 121.7285 | 121.463 | 60.6491 | 60.9467
451.8594 | 121.8201 | -60.8505 | 60.5988 | 0.0019074 | 0 | 0.065604 | 0.063929 | -0.0029267 | -0.0022794 | -2.1434e-05 | -0.0028687 | 0.001617 | -1.3946 | 0.062034 | -0.0039136 | 0.0076307 | 0.00061949 | -0.24261 | 60.3333 | -60.7773 | 60.8871 | -60.498 | -60.9329 | -61.0291 | 0.086975 | 60.3424 | -60.8688 | 60.6491 | -60.7498 | -60.8002 | -60.9787 | 0.073242 | -0.2655 | 0.28839 | 0.35248 | -0.17853 | -0.082397 | -0.25177 | -0.15564 | -0.01831 | -0.25635 | 0.050354 | 0.10071 | -0.12817 | 0.050354 | -0.10986 | 0.068664 | 0.27924 | 121.6644 | 0.11902 | 121.5179 | 121.1105 | 121.2112 | 121.1838 | 121.1929 | -121.376 | -121.4676 | 121.7377 | 121.4996 | 60.6079 | 60.9375
453.5625 | 121.8018 | -60.7956 | 60.6079 | 0.0019074 | 0 | 0.064322 | 0.063288 | -0.0031403 | -0.0016384 | -0.0045074 | 0.0032349 | -0.0020146 | -1.3929 | 0.076988 | -0.00092279 | 0.0076307 | 0.0010467 | -0.26093 | 60.3699 | -60.7773 | 60.878 | -60.5209 | -60.9375 | -61.0291 | 0.054932 | 60.3561 | -60.8459 | 60.6766 | -60.7361 | -60.791 | -60.965 | 0.01831 | -0.23804 | 0.27008 | 0.27466 | -0.23346 | -0.14191 | -0.25177 | -0.16022 | -0.050354 | -0.25177 | 0.068665 | 0.059509 | -0.16937 | 0.004577 | -0.11902 | 0.054931 | 0.25635 | 121.6553 | 0.10986 | 121.5225 | 121.1472 | 121.2021 | 121.1655 | 121.1517 | -121.3852 | -121.4539 | 121.6736 | 121.4722 | 60.5347 | 60.8505
455.3125 | 121.8109 | -60.7498 | 60.6949 | -0.0057221 | 0 | 0.063467 | 0.063929 | 0.0017731 | -0.001852 | -0.0038666 | -0.0028687 | -0.00094636 | -1.3957 | 0.06417 | -0.0022046 | 0.0050671 | 0.0012603 | -0.23804 | 60.4385 | -60.6995 | 60.9787 | -60.4019 | -60.8688 | -60.9467 | 0.09613 | 60.4431 | -60.7544 | 60.7544 | -60.6583 | -60.6995 | -60.878 | 0.050354 | -0.25635 | 0.28381 | 0.3479 | -0.19684 | -0.11902 | -0.24719 | -0.16937 | -0.004578 | -0.25177 | 0.05951 | 0.091553 | -0.12817 | 0.050354 | -0.1236 | 0.054932 | 0.29755 | 121.6782 | 0.096131 | 121.5088 | 121.138 | 121.1975 | 121.1884 | 121.1929 | -121.3943 | -121.4493 | 121.7285 | 121.5042 | 60.5118 | 60.8459
457.0625 | 121.7926 | -60.6583 | 60.7681 | -0.0057221 | 0 | 0.064536 | 0.06457 | 0.00049131 | -0.0033474 | -0.00066223 | 0.00018312 | -9.1956e-05 | -1.3929 | 0.067588 | -0.0024182 | 0.0069897 | 0.0010467 | -0.24261 | 60.5301 | -60.585 | 61.0794 | -60.2921 | -60.7269 | -60.8368 | 0.082397 | 60.5576 | -60.6857 | 60.8322 | -60.5667 | -60.6125 | -60.8047 | 0.073242 | -0.23804 | 0.31128 | 0.36621 | -0.17853 | -0.068665 | -0.25177 | -0.14191 | -0.027466 | -0.21057 | 0.064087 | 0.091553 | -0.14648 | 0.045776 | -0.11902 | 0.073242 | 0.29297 | 121.6644 | 0.11902 | 121.5179 | 121.1151 | 121.2433 | 121.1884 | 121.2158 | -121.3531 | -121.4539 | 121.7377 | 121.4905 | 60.4156 | 60.7407
458.75 | 121.6644 | -60.6079 | 60.8826 | 0.0019074 | 0 | 0.063467 | 0.064142 | -0.0027131 | -0.0029202 | -0.003012 | 0.018494 | 0.0031124 | -1.3914 | 0.059898 | -0.005409 | 0.0035719 | 0.00083309 | -0.29297 | 60.6308 | -60.5576 | 61.0153 | -60.4019 | -60.8093 | -60.878 | -0.050354 | 60.6857 | -60.6903 | 60.7544 | -60.6491 | -60.7086 | -60.8505 | 0.050354 | -0.25177 | 0.13275 | 0.20599 | -0.27008 | -0.20142 | -0.32044 | -0.25177 | -0.082398 | -0.19684 | -0.12817 | -0.041199 | -0.24262 | -0.10071 | -0.16022 | -0.01831 | 0.15564 | 121.5729 | 0.041199 | 121.4447 | 121.1884 | 121.376 | 121.2387 | 121.2936 | -121.4401 | -121.5729 | 121.6232 | 121.3623 | 60.3149 | 60.5576
460.5 | 121.6736 | -60.6125 | 60.8826 | 0.040054 | 0 | 0.064536 | 0.065851 | -0.00057689 | -0.0022794 | 0.00061957 | 0.01239 | 0.001617 | -1.3933 | 0.062034 | -0.0043408 | 0.0054945 | -0.00087591 | -0.2655 | 60.6995 | -60.5438 | 61.0428 | -60.3653 | -60.7819 | -60.8551 | -0.050354 | 60.7132 | -60.6628 | 60.7819 | -60.6354 | -60.6903 | -60.8368 | 0.068665 | -0.1831 | 0.16022 | 0.24719 | -0.24262 | -0.16937 | -0.31128 | -0.23804 | -0.050354 | -0.16937 | -0.10071 | -0.022888 | -0.2243 | -0.07782 | -0.17395 | -0.027466 | 0.17853 | 121.5866 | 0.027466 | 121.4447 | 121.2433 | 121.376 | 121.312 | 121.3257 | -121.4264 | -121.5454 | 121.6553 | 121.3943 | 60.347 | 60.5621
462.2656 | 121.6736 | -60.5667 | 60.9787 | -0.0057221 | 0 | 0.063895 | 0.066492 | -0.00079049 | 0.0017796 | 0.0042512 | 0.018494 | 0.003326 | -1.3933 | 0.05883 | -0.003059 | 0.0061353 | -0.0017303 | -0.3067 | 60.7681 | -60.4889 | 61.1023 | -60.3058 | -60.7361 | -60.791 | -0.059509 | 60.759 | -60.6171 | 60.8368 | -60.5621 | -60.6262 | -60.7727 | 0.077819 | -0.21057 | 0.1236 | 0.26093 | -0.22431 | -0.16937 | -0.30212 | -0.24719 | -0.050354 | -0.21973 | -0.14191 | 0.004577 | -0.20599 | -0.05951 | -0.15564 | -0.009156 | 0.18311 | 121.5912 | 0.054931 | 121.4539 | 121.257 | 121.376 | 121.3348 | 121.3257 | -121.4676 | -121.5958 | 121.669 | 121.4035 | 60.26 | 60.5072
464.0156 | 121.6644 | -60.5438 | 60.9787 | -0.013352 | 0 | 0.064963 | 0.063929 | -0.0059173 | -0.0033474 | 0.00019217 | -0.0028687 | 0.002258 | -1.3929 | 0.065238 | -0.0037 | 0.0048535 | 0.0014741 | -0.32501 | 60.7315 | -60.434 | 61.1069 | -60.3058 | -60.7178 | -60.8139 | -0.082397 | 60.7269 | -60.5621 | 60.8551 | -60.553 | -60.6033 | -60.7636 | 0.10986 | -0.24719 | 0.12817 | 0.23804 | -0.27008 | -0.17395 | -0.37994 | -0.28381 | -0.018311 | -0.25177 | -0.1236 | -0.009156 | -0.21973 | -0.05951 | -0.20142 | -0.041199 | 0.12817 | 121.5408 | 0.009155 | 121.4172 | 121.1655 | 121.2891 | 121.2753 | 121.2708 | -121.4127 | -121.5408 | 121.6507 | 121.3989 | 60.2188 | 60.4614
465.7031 | 121.6736 | -60.553 | 60.9238 | 0.0019074 | 0 | 0.066031 | 0.066279 | 0.0036957 | -0.001852 | -0.0027984 | -0.0059205 | 0.001617 | -1.395 | 0.062248 | 0.001427 | 0.0072035 | -0.00023491 | -0.40283 | 60.7407 | -60.466 | 61.0703 | -60.3607 | -60.7727 | -60.8551 | -0.16022 | 60.704 | -60.5713 | 60.8551 | -60.5713 | -60.6445 | -60.759 | 0.086976 | -0.1831 | 0.14648 | 0.19226 | -0.30212 | -0.21973 | -0.3891 | -0.3067 | -0.01831 | -0.21973 | -0.068664 | -0.01831 | -0.20599 | -0.091552 | -0.18768 | -0.073242 | 0.10529 | 121.5363 | 0 | 121.4264 | 121.2067 | 121.2753 | 121.2936 | 121.257 | -121.3898 | -121.4951 | 121.6232 | 121.4081 | 60.1501 | 60.3928
467.4531 | 121.6782 | -60.5164 | 61.0062 | -0.0057221 | 0 | 0.066245 | 0.063288 | 0.0047637 | -0.0012112 | 0.00083317 | 0.00018312 | 0.0026852 | -1.3942 | 0.069297 | -0.0015638 | 0.0084851 | -0.0021575 | -0.40283 | 60.7498 | -60.4156 | 61.084 | -60.3287 | -60.7452 | -60.8185 | -0.16937 | 60.7727 | -60.5301 | 60.8871 | -60.5438 | -60.6262 | -60.7315 | 0.10071 | -0.25635 | 0.077819 | 0.18768 | -0.30212 | -0.22888 | -0.40283 | -0.32959 | -0.013733 | -0.23346 | -0.11902 | -0.027466 | -0.21515 | -0.10986 | -0.20142 | -0.096131 | 0.086975 | 121.4996 | -0.013733 | 121.4172 | 121.1655 | 121.3028 | 121.2662 | 121.2891 | -121.4218 | -121.5363 | 121.6003 | 121.4035 | 60.1135 | 60.347
469.2031 | 121.7056 | -60.4202 | 61.084 | 0.040054 | 0 | 0.065604 | 0.06692 | -0.00014949 | -0.00078404 | -0.00087583 | 0.01239 | 0.0031124 | -1.3918 | 0.059684 | -0.0026318 | 0.0061353 | -0.0038665 | -0.32044 | 60.8826 | -60.3745 | 61.2442 | -60.173 | -60.5713 | -60.6445 | -0.050354 | 60.878 | -60.4797 | 60.9924 | -60.4065 | -60.466 | -60.6079 | 0.045776 | -0.20142 | 0.16022 | 0.24719 | -0.2243 | -0.15106 | -0.27008 | -0.19684 | -0.059509 | -0.20599 | -0.091552 | 0.013733 | -0.18768 | -0.045776 | -0.12817 | 0.013733 | 0.20142 | 121.6187 | 0.073242 | 121.4722 | 121.257 | 121.3577 | 121.3028 | 121.2982 | -121.4584 | -121.5637 | 121.6644 | 121.4127 | 60.0998 | 60.3699
470.9062 | 121.8018 | -60.4019 | 61.0382 | -0.0057221 | 0 | 0.064536 | 0.061579 | -0.0024995 | -0.001852 | 0.00083317 | -0.0028687 | 0.00012184 | -1.395 | 0.059684 | -6.8386e-05 | 0.0093397 | 0.0010467 | -0.35248 | 60.7681 | -60.3378 | 61.2854 | -60.0952 | -60.5164 | -60.5942 | 0.054932 | 60.791 | -60.434 | 61.0794 | -60.3012 | -60.3653 | -60.5392 | 0.064087 | -0.27008 | 0.24719 | 0.3067 | -0.19226 | -0.11444 | -0.25635 | -0.17853 | -0.032043 | -0.24719 | 0.041199 | 0.10071 | -0.13733 | 0.036622 | -0.10529 | 0.068665 | 0.24261 | 121.6232 | 0.13275 | 121.5134 | 121.106 | 121.225 | 121.17 | 121.1929 | -121.376 | -121.4722 | 121.6873 | 121.4813 | 60.0494 | 60.4568
472.6719 | 121.7239 | -60.6766 | 60.7544 | -0.013352 | 0 | 0.064322 | 0.068201 | 0.0024139 | -0.00099764 | -0.00023503 | -0.0028687 | 0.0026852 | -1.3961 | 0.067375 | 0.0012134 | 0.0078443 | 0.0010467 | -0.41199 | 60.5667 | -60.5988 | 60.9421 | -60.4752 | -60.9009 | -60.9833 | -0.09613 | 60.5392 | -60.7086 | 60.7727 | -60.6628 | -60.7315 | -60.8551 | 0.07782 | -0.18768 | 0.18768 | 0.20142 | -0.3067 | -0.2243 | -0.38452 | -0.30212 | -0.032043 | -0.21515 | 0.01831 | 0.013733 | -0.17853 | -0.054931 | -0.14648 | -0.022888 | 0.1236 | 121.5408 | 0.045776 | 121.4813 | 121.1655 | 121.2479 | 121.2433 | 121.2158 | -121.3531 | -121.463 | 121.6187 | 121.4493 | 60.2646 | 60.5804
474.4219 | 121.669 | -60.672 | 60.8093 | 0.0019074 | 0 | 0.065817 | 0.064997 | -0.0012177 | -0.00099764 | 0.00083317 | -0.0028687 | 0.0026852 | -1.3942 | 0.063743 | -0.001991 | 0.0076307 | 0.0029693 | -0.4303 | 60.6216 | -60.5804 | 60.9375 | -60.4843 | -60.9055 | -60.965 | -0.16479 | 60.585 | -60.6995 | 60.7315 | -60.7178 | -60.7773 | -60.8871 | 0.091553 | -0.18768 | 0.12817 | 0.18768 | -0.29297 | -0.23346 | -0.38452 | -0.32501 | -0.027466 | -0.2243 | -0.07782 | -0.045776 | -0.21515 | -0.10529 | -0.18768 | -0.07782 | 0.09613 | 121.5179 | -0.01831 | 121.431 | 121.2021 | 121.2845 | 121.2936 | 121.257 | -121.3898 | -121.5088 | 121.6095 | 121.4035 | 60.2417 | 60.5072
476.125 | 121.701 | -60.5896 | 60.8963 | 0.040054 | 0 | 0.065604 | 0.065211 | 0.0022003 | 0.0011386 | -2.1434e-05 | 0.0062865 | 0.0028988 | -1.3929 | 0.059898 | -0.0037 | 0.0061353 | -0.0019439 | -0.32501 | 60.6949 | -60.5301 | 61.0748 | -60.3424 | -60.7498 | -60.8231 | -0.032043 | 60.6583 | -60.6308 | 60.8276 | -60.5713 | -60.6445 | -60.7727 | 0.05951 | -0.20142 | 0.17853 | 0.24719 | -0.23346 | -0.16022 | -0.29297 | -0.21973 | -0.041198 | -0.23804 | -0.068664 | 0.018311 | -0.18311 | -0.054931 | -0.14191 | -0.013733 | 0.18768 | 121.6049 | 0.059509 | 121.4584 | 121.225 | 121.2891 | 121.2845 | 121.2479 | -121.4264 | -121.5271 | 121.6644 | 121.4172 | 60.2646 | 60.5576
477.8281 | 121.6461 | -60.5759 | 60.9146 | -0.0057221 | 0 | 0.062186 | 0.065424 | 0.0030547 | -0.0014248 | -0.0025848 | 0.00018312 | 0.00012184 | -1.3931 | 0.062461 | -0.0026318 | 0.0063489 | -0.0025849 | -0.43945 | 60.6995 | -60.498 | 61.0291 | -60.3745 | -60.8185 | -60.8734 | -0.17853 | 60.6857 | -60.5804 | 60.7956 | -60.6216 | -60.6949 | -60.8047 | 0.07782 | -0.21515 | 0.11444 | 0.20142 | -0.29755 | -0.24261 | -0.37537 | -0.32043 | -0.004577 | -0.22888 | -0.11902 | -0.045776 | -0.22888 | -0.11902 | -0.22431 | -0.11444 | 0.1236 | 121.5271 | -0.041199 | 121.376 | 121.1975 | 121.2662 | 121.2753 | 121.2616 | -121.4127 | -121.4951 | 121.6049 | 121.3715 | 60.1364 | 60.3973
479.5938 | 121.7514 | -60.3516 | 61.0794 | 0.024795 | 0 | 0.065176 | 0.061365 | 0.0028411 | -0.00014304 | 0.00061957 | 0.00018312 | -0.00094636 | -1.3944 | 0.084678 | -0.0022046 | 0.0091261 | -0.00087591 | -0.42572 | 60.8368 | -60.3104 | 61.2854 | -60.1089 | -60.5484 | -60.6216 | -0.073242 | 60.8231 | -60.4156 | 61.0611 | -60.3516 | -60.3882 | -60.5484 | 0.041198 | -0.24262 | 0.20599 | 0.24261 | -0.27008 | -0.19684 | -0.31128 | -0.23804 | -0.064087 | -0.25635 | -0.018311 | 0 | -0.19684 | -0.036622 | -0.13275 | 0.027465 | 0.20142 | 121.5958 | 0.064087 | 121.4767 | 121.1472 | 121.2387 | 121.1884 | 121.1746 | -121.3898 | -121.4951 | 121.637 | 121.4127 | 59.9258 | 60.2783
481.3594 | 121.7102 | -60.2966 | 61.1755 | 0.017166 | 0 | 0.063681 | 0.066065 | 0.0045501 | 0.00028416 | -0.001944 | 0.0093383 | 0.00033544 | -1.3933 | 0.063743 | -0.0043408 | 0.0061353 | -0.0032257 | -0.34332 | 60.9741 | -60.2463 | 61.377 | -60.0403 | -60.4477 | -60.5301 | -0.013733 | 60.965 | -60.3333 | 61.1252 | -60.2921 | -60.3378 | -60.4935 | 0.050354 | -0.20142 | 0.20142 | 0.25635 | -0.23346 | -0.15106 | -0.28381 | -0.20142 | -0.036621 | -0.21057 | -0.050354 | 0.004578 | -0.19684 | -0.041199 | -0.16022 | -0.004578 | 0.20599 | 121.6232 | 0.041199 | 121.4584 | 121.2204 | 121.2982 | 121.2708 | 121.2616 | -121.4218 | -121.5088 | 121.6736 | 121.4218 | 59.9533 | 60.2829
483.0625 | 121.8063 | -60.26 | 61.1572 | -0.020981 | 0 | 0.063895 | 0.063502 | 0.00027771 | -0.003561 | -0.0015166 | -0.0059205 | -0.00073276 | -1.395 | 0.067375 | -0.0022046 | 0.0044263 | -0.00044851 | -0.41199 | 60.8826 | -60.2188 | 61.4182 | -59.967 | -60.3928 | -60.466 | 0.013733 | 60.9238 | -60.2921 | 61.1984 | -60.1822 | -60.2325 | -60.4156 | 0.041199 | -0.27466 | 0.26093 | 0.29297 | -0.20599 | -0.13275 | -0.24719 | -0.17395 | -0.032043 | -0.23346 | 0.041198 | 0.07782 | -0.15564 | 0.027466 | -0.1236 | 0.059509 | 0.25177 | 121.637 | 0.10986 | 121.4905 | 121.1014 | 121.2158 | 121.1426 | 121.1838 | -121.376 | -121.4493 | 121.6782 | 121.4584 | 59.848 | 60.2737
484.8125 | 121.6507 | -60.4889 | 61.0245 | -0.013352 | 0 | 0.063895 | 0.065211 | -0.0044221 | -0.004202 | -0.00044863 | -0.0028687 | 0.0020444 | -1.3948 | 0.061393 | -0.005409 | 0.0039991 | 0.00040589 | -0.41657 | 60.759 | -60.4202 | 61.1252 | -60.2829 | -60.672 | -60.7681 | -0.07782 | 60.7819 | -60.5072 | 60.8871 | -60.5072 | -60.5667 | -60.7224 | 0.068665 | -0.2655 | 0.10071 | 0.20599 | -0.27923 | -0.1831 | -0.3479 | -0.25177 | -0.01831 | -0.24262 | -0.13733 | -0.01831 | -0.23346 | -0.077819 | -0.21515 | -0.059509 | 0.13733 | 121.5454 | 0 | 121.3943 | 121.1792 | 121.2891 | 121.2479 | 121.2708 | -121.4447 | -121.5317 | 121.6141 | 121.376 | 60.0723 | 60.4111
486.5 | 121.6599 | -60.5621 | 60.9787 | -0.0057221 | 0 | 0.064536 | 0.064356 | -0.0016449 | -0.00057044 | -0.001944 | 0.00018312 | 0.0028988 | -1.394 | 0.060539 | -0.0028454 | 0.0074171 | -0.0023713 | -0.43488 | 60.7269 | -60.4431 | 61.1069 | -60.3149 | -60.7361 | -60.8231 | -0.13275 | 60.7086 | -60.5301 | 60.8368 | -60.585 | -60.6445 | -60.7544 | 0.11902 | -0.25177 | 0.12817 | 0.24719 | -0.26093 | -0.17395 | -0.37994 | -0.29297 | 0.032044 | -0.27008 | -0.14191 | -0.022888 | -0.19226 | -0.082397 | -0.22431 | -0.11444 | 0.12817 | 121.55 | -0.054932 | 121.3669 | 121.17 | 121.2387 | 121.2891 | 121.2708 | -121.4218 | -121.5088 | 121.669 | 121.3989 | 60.1273 | 60.4294
488.25 | 121.6736 | -60.5392 | 60.9421 | -0.013352 | 0 | 0.066458 | 0.065851 | 6.4114e-05 | -0.0022794 | -0.0010894 | -0.0028687 | 0.00076264 | -1.394 | 0.060111 | -0.0013502 | 0.0065625 | -0.00087591 | -0.50354 | 60.6995 | -60.4797 | 61.0474 | -60.3699 | -60.7819 | -60.8414 | -0.16479 | 60.6949 | -60.5667 | 60.8597 | -60.5804 | -60.6491 | -60.7407 | 0.05951 | -0.24262 | 0.10528 | 0.16937 | -0.30212 | -0.24261 | -0.36163 | -0.30212 | -0.027465 | -0.24719 | -0.082398 | -0.041198 | -0.20142 | -0.10986 | -0.17395 | -0.082398 | 0.10986 | 121.5271 | -0.013733 | 121.4264 | 121.1792 | 121.2616 | 121.2387 | 121.2341 | -121.4218 | -121.5088 | 121.5866 | 121.3989 | 60.0357 | 60.3745
490.0156 | 121.7285 | -60.5026 | 60.9421 | 0.040054 | 0 | 0.064749 | 0.063929 | 0.0036957 | -0.001852 | -0.00066223 | 0.0093383 | 0.0018306 | -1.3946 | 0.075065 | -0.0011364 | 0.0063489 | -0.0019439 | -0.4715 | 60.704 | -60.434 | 61.1893 | -60.2051 | -60.6308 | -60.6995 | -0.041199 | 60.7361 | -60.5255 | 60.9558 | -60.466 | -60.5164 | -60.6766 | 0.068665 | -0.23804 | 0.24719 | 0.29755 | -0.19684 | -0.12817 | -0.2655 | -0.19684 | -0.022888 | -0.20599 | 0.013733 | 0.036622 | -0.17395 | -0.013732 | -0.15106 | 0.009156 | 0.22888 | 121.6232 | 0.05951 | 121.4813 | 121.138 | 121.2616 | 121.2067 | 121.2387 | -121.376 | -121.4676 | 121.6919 | 121.4584 | 60.0311 | 60.4614
491.7188 | 121.701 | -60.4477 | 61.0748 | 0.040054 | 0 | 0.063895 | 0.064783 | 0.0011321 | -0.00099764 | -2.1434e-05 | 0.015442 | 0.002258 | -1.3925 | 0.062248 | -0.0043408 | 0.0057081 | 0.00040589 | -0.41657 | 60.8597 | -60.4202 | 61.2076 | -60.2142 | -60.6079 | -60.6949 | -0.050354 | 60.8643 | -60.4843 | 60.9512 | -60.4568 | -60.4797 | -60.6308 | 0.027466 | -0.21515 | 0.13275 | 0.23346 | -0.24719 | -0.16022 | -0.27466 | -0.18768 | -0.036621 | -0.21057 | -0.1236 | -0.009155 | -0.1831 | -0.032043 | -0.14648 | 0.004578 | 0.20599 | 121.6278 | 0.027466 | 121.4355 | 121.2799 | 121.3486 | 121.3074 | 121.312 | -121.4951 | -121.5591 | 121.6553 | 121.3989 | 60.0311 | 60.3973
493.4688 | 121.6782 | -60.4477 | 61.0382 | 0.055313 | 0 | 0.066672 | 0.065424 | -0.0035675 | -0.001852 | 0.00061957 | 0.018494 | 0.0041806 | -1.3929 | 0.061179 | -0.004768 | 0.0050671 | 0.00083309 | -0.41657 | 60.8322 | -60.3973 | 61.1801 | -60.2188 | -60.6125 | -60.704 | -0.091553 | 60.8414 | -60.4935 | 60.9238 | -60.4797 | -60.5209 | -60.6766 | 0.050354 | -0.20599 | 0.14191 | 0.22888 | -0.25635 | -0.16479 | -0.3067 | -0.21515 | -0.045776 | -0.19684 | -0.11444 | -0.032043 | -0.22888 | -0.073242 | -0.18311 | -0.027466 | 0.17853 | 121.5775 | 0.013733 | 121.4172 | 121.2296 | 121.3348 | 121.2799 | 121.2891 | -121.4355 | -121.5317 | 121.6278 | 121.3715 | 60.0311 | 60.3561
495.25 | 121.7834 | -60.4202 | 61.0016 | -0.0057221 | 0 | 0.064536 | 0.063715 | 0.00091851 | -0.00035684 | -2.1434e-05 | -0.0028687 | -0.0015872 | -1.395 | 0.05947 | -0.00028199 | 0.0061353 | -0.00023491 | -0.49439 | 60.7452 | -60.3745 | 61.2259 | -60.173 | -60.585 | -60.6583 | -0.022888 | 60.7269 | -60.4614 | 61.0382 | -60.3653 | -60.4065 | -60.5804 | 0.045776 | -0.25635 | 0.2243 | 0.24719 | -0.23804 | -0.1648 | -0.28381 | -0.21057 | -0.041199 | -0.27466 | 0.036621 | 0.054932 | -0.16022 | 0.013733 | -0.11902 | 0.054932 | 0.20142 | 121.6003 | 0.096131 | 121.4996 | 121.1197 | 121.1884 | 121.1655 | 121.1472 | -121.376 | -121.463 | 121.6461 | 121.4584 | 59.9258 | 60.3973
497.0156 | 121.6553 | -60.4294 | 61.0474 | -0.013352 | 0 | 0.065604 | 0.063715 | -0.00014949 | -0.002493 | -0.001303 | -0.0059205 | 0.0020444 | -1.3944 | 0.064597 | -0.005409 | 0.0063489 | 0.0031829 | -0.4715 | 60.8231 | -60.3241 | 61.1938 | -60.1913 | -60.6079 | -60.6812 | -0.073242 | 60.8185 | -60.4431 | 60.9512 | -60.4477 | -60.5072 | -60.6628 | 0.10528 | -0.2243 | 0.14649 | 0.23804 | -0.25177 | -0.17853 | -0.35705 | -0.28381 | -0.013733 | -0.22888 | -0.09613 | -0.018311 | -0.23346 | -0.07782 | -0.21973 | -0.064087 | 0.13275 | 121.5179 | -0.004578 | 121.3943 | 121.1472 | 121.2616 | 121.2524 | 121.2479 | -121.3715 | -121.4905 | 121.6232 | 121.3806 | 59.9579 | 60.3561
498.7031 | 121.6599 | -60.4477 | 61.0474 | 0.0095369 | 0 | 0.065817 | 0.064356 | 0.0024139 | -0.00057044 | -0.0010894 | -0.0028687 | -0.00030556 | -1.3925 | 0.064811 | -0.0011364 | 0.0050671 | -0.0042939 | -0.53101 | 60.8231 | -60.3699 | 61.1481 | -60.2554 | -60.6903 | -60.7544 | -0.14648 | 60.8276 | -60.4706 | 60.9375 | -60.498 | -60.5392 | -60.6583 | 0.07782 | -0.2243 | 0.10071 | 0.19226 | -0.3067 | -0.24262 | -0.38452 | -0.32044 | -0.022888 | -0.21973 | -0.10986 | -0.050354 | -0.21057 | -0.091553 | -0.18768 | -0.068665 | 0.11444 | 121.5179 | -0.027466 | 121.4081 | 121.1929 | 121.2982 | 121.2708 | 121.2753 | -121.4172 | -121.5179 | 121.5958 | 121.3852 | 59.9167 | 60.3012
500.4531 | 121.7377 | -60.4065 | 61.0336 | 0.0019074 | 0 | 0.064322 | 0.064142 | 0.0019867 | -0.0016384 | -0.00044863 | 0.0032349 | 0.0024716 | -1.394 | 0.067588 | -0.00092279 | 0.0091261 | 0.0023285 | -0.56305 | 60.8322 | -60.3653 | 61.2122 | -60.2097 | -60.6445 | -60.704 | -0.11444 | 60.8185 | -60.434 | 61.0382 | -60.3973 | -60.4614 | -60.5988 | 0.041199 | -0.20142 | 0.17853 | 0.19684 | -0.29755 | -0.23804 | -0.33875 | -0.27924 | -0.027466 | -0.21515 | 0.004578 | 0.009155 | -0.19226 | -0.054932 | -0.16479 | -0.027466 | 0.15564 | 121.5775 | 0.036621 | 121.4722 | 121.1975 | 121.2524 | 121.2387 | 121.225 | -121.3989 | -121.4676 | 121.6187 | 121.4447 | 59.8434 | 60.2921
502.2188 | 121.8109 | -60.3607 | 61.0611 | -0.0057221 | 0 | 0.065176 | 0.062433 | -0.0027131 | -0.00057044 | 0.00019217 | -0.0028687 | -0.00116 | -1.3946 | 0.065879 | -0.0013502 | 0.0072035 | 0.0019013 | -0.47607 | 60.7773 | -60.3149 | 61.3449 | -60.0357 | -60.466 | -60.553 | 0.07782 | 60.8093 | -60.3653 | 61.1343 | -60.26 | -60.3195 | -60.498 | 0.045777 | -0.28381 | 0.28381 | 0.32501 | -0.19226 | -0.10529 | -0.23804 | -0.15106 | -0.004577 | -0.25177 | 0.073242 | 0.10071 | -0.13733 | 0.041199 | -0.13275 | 0.045776 | 0.27923 | 121.6599 | 0.10529 | 121.4996 | 121.0922 | 121.1746 | 121.138 | 121.17 | -121.376 | -121.4264 | 121.7056 | 121.4951 | 59.8846 | 60.4385
503.9219 | 121.7194 | -60.3928 | 61.0565 | 0.0019074 | 0 | 0.065176 | 0.063502 | -0.0014313 | -0.0012112 | -0.0025848 | -0.0059205 | 0.00012184 | -1.3935 | 0.065025 | -0.0024182 | 0.0067761 | -0.0025849 | -0.46234 | 60.8047 | -60.3149 | 61.2991 | -60.0769 | -60.4935 | -60.5942 | 0.018311 | 60.8414 | -60.3882 | 61.0153 | -60.3653 | -60.4111 | -60.5759 | 0.07782 | -0.25177 | 0.24261 | 0.31586 | -0.20142 | -0.10071 | -0.27924 | -0.17853 | 0.004577 | -0.21515 | -0.041199 | 0.027466 | -0.18311 | -0.018311 | -0.18768 | -0.022888 | 0.23804 | 121.6141 | 0.022889 | 121.4035 | 121.1197 | 121.2296 | 121.1975 | 121.2341 | -121.3715 | -121.4447 | 121.6919 | 121.4081 | 59.9304 | 60.4111
505.6875 | 121.7377 | -60.3653 | 61.0611 | 0.040054 | 0 | 0.06539 | 0.065424 | -0.0012177 | -0.00014304 | 0.0016876 | 0.0093383 | 0.0014034 | -1.3922 | 0.066306 | -0.0024182 | 0.0082715 | 0.0014741 | -0.54016 | 60.8093 | -60.3241 | 61.2808 | -60.1181 | -60.5301 | -60.6216 | -0.054932 | 60.8276 | -60.4294 | 61.0336 | -60.3745 | -60.4156 | -60.5713 | 0.041198 | -0.25177 | 0.21973 | 0.24719 | -0.25635 | -0.16479 | -0.29755 | -0.20599 | -0.064087 | -0.23346 | -0.027466 | -0.009156 | -0.20599 | -0.050354 | -0.14191 | 0.013733 | 0.20599 | 121.6049 | 0.054931 | 121.463 | 121.1334 | 121.257 | 121.1746 | 121.1929 | -121.3852 | -121.4905 | 121.6461 | 121.3989 | 59.8251 | 60.3104
507.4531 | 121.7606 | -60.3745 | 61.0519 | 0.0019074 | 0 | 0.064749 | 0.063288 | -0.0016449 | 7.0564e-05 | 0.00083317 | 0.00018312 | 0.0014034 | -1.3931 | 0.060111 | -0.0026318 | 0.0067761 | 0.0029693 | -0.48065 | 60.791 | -60.3287 | 61.3312 | -60.0723 | -60.4843 | -60.5896 | 0.032043 | 60.8139 | -60.3973 | 61.0657 | -60.3241 | -60.3653 | -60.5484 | 0.045777 | -0.26093 | 0.27924 | 0.30212 | -0.21515 | -0.10986 | -0.26093 | -0.15564 | -0.022888 | -0.23804 | 0.013733 | 0.050354 | -0.17395 | 0.009156 | -0.15106 | 0.032044 | 0.25635 | 121.6599 | 0.073242 | 121.463 | 121.1197 | 121.2112 | 121.1655 | 121.1884 | -121.3806 | -121.4493 | 121.7056 | 121.4401 | 59.8938 | 60.4065
509.1719 | 121.669 | -60.3882 | 61.0931 | 0.0019074 | 0 | 0.064108 | 0.062647 | -0.0035675 | -0.001852 | -0.001303 | -0.0059205 | 0.0014034 | -1.391 | 0.06887 | -0.005409 | 0.0052807 | -0.00023491 | -0.49896 | 60.8322 | -60.3012 | 61.2625 | -60.1364 | -60.553 | -60.6216 | -0.059509 | 60.878 | -60.3928 | 60.9833 | -60.3928 | -60.4385 | -60.6079 | 0.086976 | -0.26093 | 0.16937 | 0.25177 | -0.23346 | -0.16479 | -0.32043 | -0.25177 | -0.004577 | -0.21515 | -0.10986 | -0.004577 | -0.21973 | -0.050354 | -0.21515 | -0.045777 | 0.16479 | 121.5637 | 0 | 121.376 | 121.1334 | 121.2708 | 121.2204 | 121.2662 | -121.3943 | -121.4859 | 121.6507 | 121.3715 | 59.8892 | 60.3287
510.9375 | 121.7239 | -60.3882 | 61.0291 | 0.032425 | 0 | 0.065604 | 0.063288 | -0.0046357 | 0.00071136 | 0.0016876 | 0.0062865 | -0.00030556 | -1.3957 | 0.070152 | -0.0013502 | 0.0065625 | -0.00044851 | -0.58594 | 60.8093 | -60.3104 | 61.2717 | -60.1181 | -60.5438 | -60.64 | -0.07782 | 60.8093 | -60.4202 | 61.0336 | -60.3928 | -60.4294 | -60.5713 | 0.07782 | -0.21973 | 0.24261 | 0.27008 | -0.25177 | -0.15564 | -0.32959 | -0.23346 | -0.032043 | -0.21973 | 0.004577 | -0.004577 | -0.1831 | -0.041198 | -0.15106 | -0.009155 | 0.19226 | 121.582 | 0.027466 | 121.4539 | 121.1197 | 121.2296 | 121.1975 | 121.1975 | -121.3394 | -121.4493 | 121.6599 | 121.4218 | 59.8022 | 60.3104
512.6562 | 121.6736 | -60.3928 | 61.0794 | 0.017166 | 0 | 0.066245 | 0.06457 | 0.0056183 | -0.00078404 | -0.0015166 | 0.0032349 | 0.0028988 | -1.3931 | 0.062675 | -0.0011364 | 0.0061353 | -0.0019439 | -0.54474 | 60.8551 | -60.3104 | 61.2808 | -60.1135 | -60.5667 | -60.6537 | -0.064087 | 60.8459 | -60.4019 | 61.0107 | -60.4019 | -60.4797 | -60.6033 | 0.082397 | -0.2243 | 0.20142 | 0.27924 | -0.26093 | -0.17395 | -0.34332 | -0.25635 | -0.009156 | -0.23346 | -0.068665 | -0.009156 | -0.21057 | -0.086975 | -0.20142 | -0.077819 | 0.19684 | 121.5912 | 0 | 121.4127 | 121.1655 | 121.2479 | 121.2479 | 121.2387 | -121.3898 | -121.4813 | 121.6736 | 121.4035 | 59.848 | 60.3287
514.4219 | 121.6965 | -60.3287 | 61.1435 | 0.017166 | 0 | 0.06539 | 0.06756 | 0.0017731 | -0.0016384 | 0.00040597 | 0.0032349 | 0.00012184 | -1.3925 | 0.049857 | -0.0037 | 0.0059217 | 0.00061949 | -0.53558 | 60.9329 | -60.2463 | 61.3541 | -60.0494 | -60.4843 | -60.5667 | -0.027466 | 60.9238 | -60.3195 | 61.0977 | -60.3195 | -60.3607 | -60.5209 | 0.082397 | -0.21057 | 0.21057 | 0.27924 | -0.23804 | -0.15564 | -0.32043 | -0.23804 | 0.009155 | -0.21973 | -0.045777 | 0.009155 | -0.19226 | -0.032044 | -0.20142 | -0.041199 | 0.19684 | 121.6003 | 0 | 121.4172 | 121.1792 | 121.2433 | 121.2616 | 121.2524 | -121.3898 | -121.463 | 121.6827 | 121.4264 | 59.7931 | 60.3012
516.1406 | 121.6919 | -60.2966 | 61.2076 | -0.0057221 | 0 | 0.064749 | 0.061579 | 0.0036957 | -0.00099764 | 0.0016876 | -0.0028687 | -0.00030556 | -1.3933 | 0.066947 | -0.0056226 | 0.0069897 | -0.0013031 | -0.52643 | 60.9192 | -60.1959 | 61.4182 | -59.9762 | -60.3836 | -60.4843 | -0.013733 | 60.9421 | -60.3149 | 61.1252 | -60.2692 | -60.3241 | -60.4706 | 0.10071 | -0.28839 | 0.21057 | 0.32043 | -0.18768 | -0.086975 | -0.28839 | -0.18768 | -0.01831 | -0.2655 | -0.082398 | 0.027466 | -0.17395 | -0.027466 | -0.15564 | -0.009156 | 0.21973 | 121.6141 | 0.045776 | 121.4401 | 121.1151 | 121.257 | 121.2158 | 121.2387 | -121.4035 | -121.5225 | 121.7148 | 121.4218 | 59.7702 | 60.2829
517.8438 | 121.6232 | -60.2829 | 61.1984 | 0.0095369 | 0 | 0.064749 | 0.065851 | 0.0024139 | -0.00035684 | -0.00087583 | -0.0028687 | 0.0031124 | -1.3933 | 0.060325 | -0.0011364 | 0.0076307 | 0.0010467 | -0.55389 | 60.9512 | -60.2051 | 61.3678 | -60.0082 | -60.466 | -60.5392 | -0.059509 | 60.9467 | -60.3195 | 61.1069 | -60.3012 | -60.3699 | -60.4935 | 0.07782 | -0.24719 | 0.16937 | 0.27466 | -0.25635 | -0.1831 | -0.33417 | -0.26093 | -0.036621 | -0.25177 | -0.091552 | -0.01831 | -0.21057 | -0.086975 | -0.17395 | -0.050354 | 0.19684 | 121.5729 | 0.018311 | 121.4264 | 121.1563 | 121.2662 | 121.2341 | 121.2296 | -121.4035 | -121.5179 | 121.6507 | 121.3898 | 59.729 | 60.2234
519.6094 | 121.7148 | -60.2783 | 61.1801 | -0.0057221 | 0 | 0.066245 | 0.063715 | 6.4114e-05 | -0.0020658 | -0.0021576 | -0.0028687 | 0.0011898 | -1.3942 | 0.068229 | -0.004768 | 0.0059217 | 0.00061949 | -0.54474 | 60.9238 | -60.1959 | 61.4227 | -59.9625 | -60.3699 | -60.466 | 0.009155 | 60.9375 | -60.3012 | 61.1481 | -60.2417 | -60.2921 | -60.4523 | 0.082397 | -0.25635 | 0.24261 | 0.31586 | -0.18768 | -0.091553 | -0.27008 | -0.17395 | -0.022888 | -0.24262 | -0.032044 | 0.036621 | -0.17395 | -0.013733 | -0.15106 | 0.009155 | 0.23346 | 121.6187 | 0.059509 | 121.4493 | 121.1197 | 121.2387 | 121.2021 | 121.2158 | -121.376 | -121.4813 | 121.701 | 121.4264 | 59.7336 | 60.2875
521.375 | 121.7422 | -60.3333 | 61.0611 | 0.032425 | 0 | 0.067313 | 0.065424 | -0.0014313 | -0.0020658 | -2.1434e-05 | 0.01239 | 0.002258 | -1.3922 | 0.059684 | 0.00078621 | 0.0074171 | -0.00066231 | -0.60425 | 60.8505 | -60.2737 | 61.377 | -59.9854 | -60.4614 | -60.5301 | 0.009155 | 60.8643 | -60.3745 | 61.1298 | -60.2829 | -60.3333 | -60.4935 | 0.059509 | -0.21057 | 0.31586 | 0.3479 | -0.19684 | -0.12817 | -0.25635 | -0.18768 | -0.041199 | -0.19684 | 0.068665 | 0.050354 | -0.16022 | 0 | -0.11902 | 0.041199 | 0.28839 | 121.6507 | 0.091553 | 121.5042 | 121.1243 | 121.2387 | 121.1838 | 121.1975 | -121.3348 | -121.4355 | 121.7102 | 121.463 | 59.729 | 60.3424
523.0625 | 121.7377 | -60.26 | 61.171 | 0.062942 | 0 | 0.066031 | 0.064997 | 0.0024139 | -0.0014248 | 0.0023286 | 0.0093383 | -0.00030556 | -1.3952 | 0.06182 | 0.00035881 | 0.0086987 | -0.0036529 | -0.62256 | 60.91 | -60.2234 | 61.4182 | -59.9442 | -60.4248 | -60.4843 | -0.036621 | 60.9375 | -60.2921 | 61.1755 | -60.2463 | -60.2966 | -60.4431 | 0.036621 | -0.26093 | 0.24719 | 0.31586 | -0.2243 | -0.16479 | -0.26093 | -0.20142 | -0.032043 | -0.23346 | 0.004578 | 0.013733 | -0.1831 | -0.036621 | -0.15106 | -0.004578 | 0.27924 | 121.6415 | 0.045776 | 121.4676 | 121.1334 | 121.2296 | 121.17 | 121.1975 | -121.3943 | -121.463 | 121.6782 | 121.4355 | 59.6375 | 60.2234
524.8281 | 121.7377 | -60.1868 | 61.2671 | -0.0057221 | 0 | 0.065176 | 0.063502 | -0.0022857 | -0.0027066 | 0.0019012 | 0.00018312 | -0.00030556 | -1.395 | 0.067161 | -0.0045544 | 0.0061353 | 0.0029693 | -0.56763 | 60.9924 | -60.0998 | 61.528 | -59.8572 | -60.2921 | -60.379 | 0.027466 | 61.0199 | -60.1913 | 61.2625 | -60.1227 | -60.1639 | -60.347 | 0.086976 | -0.27466 | 0.26093 | 0.32959 | -0.19226 | -0.10529 | -0.27924 | -0.19226 | -0.004577 | -0.24719 | -0.004578 | 0.064087 | -0.16022 | 0.022889 | -0.15564 | 0.027466 | 0.24261 | 121.6278 | 0.068664 | 121.4539 | 121.0922 | 121.2112 | 121.1792 | 121.2067 | -121.3669 | -121.4584 | 121.7148 | 121.4493 | 59.6191 | 60.2142
526.5312 | 121.6644 | -60.1868 | 61.3403 | -0.013352 | 0 | 0.063681 | 0.064142 | -0.0044221 | -0.0020658 | -0.0021576 | -0.0059205 | 0.0018306 | -1.3942 | 0.062248 | -0.0024182 | 0.0044263 | -0.0023713 | -0.60883 | 61.0977 | -60.0632 | 61.496 | -59.8755 | -60.3012 | -60.379 | -0.045776 | 61.1206 | -60.141 | 61.235 | -60.1547 | -60.2051 | -60.3561 | 0.1236 | -0.24261 | 0.15564 | 0.31128 | -0.19226 | -0.11444 | -0.31586 | -0.23804 | 0.045777 | -0.21973 | -0.10529 | 0.032044 | -0.16937 | -0.01831 | -0.21515 | -0.064087 | 0.18768 | 121.5591 | -0.013733 | 121.376 | 121.1609 | 121.2616 | 121.2845 | 121.3074 | -121.4035 | -121.4813 | 121.6827 | 121.4218 | 59.5779 | 60.141
528.2812 | 121.7514 | -60.1273 | 61.2625 | 0.055313 | 0 | 0.065604 | 0.066279 | 0.0011321 | 0.0015658 | 0.0025422 | 0.015442 | 0.0031124 | -1.3927 | 0.068015 | -0.00049559 | 0.0078443 | -0.0042939 | -0.62714 | 61.0565 | -60.1227 | 61.5829 | -59.8022 | -60.2783 | -60.347 | 0 | 61.0519 | -60.2142 | 61.322 | -60.1089 | -60.1364 | -60.3195 | 0.004577 | -0.20599 | 0.32043 | 0.32501 | -0.21973 | -0.15106 | -0.2243 | -0.15564 | -0.086975 | -0.21057 | 0.059509 | 0.01831 | -0.19226 | -0.009156 | -0.10529 | 0.077819 | 0.32044 | 121.7056 | 0.10529 | 121.5363 | 121.1792 | 121.2662 | 121.1838 | 121.1792 | -121.3852 | -121.4767 | 121.7102 | 121.4493 | 59.5001 | 60.1273
529.9844 | 121.7285 | -60.0815 | 61.3541 | 0.040054 | 0 | 0.065604 | 0.064783 | 0.00027771 | 0.00049776 | -0.001303 | 0.015442 | 0.0018306 | -1.3927 | 0.062675 | -0.0013502 | 0.0069897 | -0.0023713 | -0.6546 | 61.1023 | -60.054 | 61.6013 | -59.7839 | -60.2325 | -60.3058 | -0.036621 | 61.1298 | -60.1227 | 61.3724 | -60.0723 | -60.0952 | -60.2646 | 0.027466 | -0.25177 | 0.24719 | 0.29755 | -0.2243 | -0.15106 | -0.25177 | -0.17853 | -0.041199 | -0.2243 | 0.01831 | 0.009155 | -0.1831 | -0.013733 | -0.14191 | 0.027466 | 0.27008 | 121.6553 | 0.050354 | 121.4951 | 121.1563 | 121.2524 | 121.1838 | 121.2112 | -121.4081 | -121.4767 | 121.6827 | 121.4539 | 59.4269 | 60.0449
531.75 | 121.6873 | -60.0632 | 61.4136 | 0.017166 | 0 | 0.063895 | 0.068415 | -0.0014313 | -0.0033474 | -0.0017304 | 0.0062865 | 0.0028988 | -1.395 | 0.057548 | -0.0041272 | 0.0067761 | -0.0034393 | -0.6134 | 61.1938 | -60.0082 | 61.6241 | -59.7885 | -60.2463 | -60.3149 | -0.032043 | 61.2076 | -60.0861 | 61.3403 | -60.0723 | -60.1318 | -60.2554 | 0.054931 | -0.21973 | 0.21057 | 0.27466 | -0.25177 | -0.18311 | -0.3067 | -0.23804 | -0.022889 | -0.20599 | -0.073242 | -0.009156 | -0.19226 | -0.068665 | -0.16937 | -0.045776 | 0.21973 | 121.6324 | 0.013733 | 121.4264 | 121.2021 | 121.2936 | 121.257 | 121.2708 | -121.4218 | -121.4996 | 121.6873 | 121.4035 | 59.4498 | 60.0311
533.4375 | 121.7743 | -60.0403 | 61.3632 | -0.013352 | 0 | 0.066672 | 0.06457 | 0.0017731 | -0.0014248 | -0.0017304 | -0.0059205 | -0.00073276 | -1.3952 | 0.071861 | 0.001427 | 0.0086987 | 0.0014741 | -0.68665 | 61.1435 | -59.9808 | 61.6379 | -59.761 | -60.2188 | -60.2875 | -0.036621 | 61.1481 | -60.0586 | 61.4136 | -60.0037 | -60.054 | -60.2005 | 0.059509 | -0.21973 | 0.27466 | 0.27924 | -0.24719 | -0.17853 | -0.3067 | -0.23804 | -0.018311 | -0.21515 | 0.050354 | 0.036621 | -0.16022 | -0.013733 | -0.14191 | 0.004578 | 0.21973 | 121.6187 | 0.054932 | 121.4722 | 121.1243 | 121.2067 | 121.1838 | 121.1884 | -121.344 | -121.4218 | 121.6782 | 121.4539 | 59.3536 | 60.0037
535.2031 | 121.7377 | -59.9762 | 61.441 | 0.055313 | 0 | 0.067954 | 0.066279 | 0.0039093 | 0.00049776 | -0.0021576 | 0.01239 | 0.0020444 | -1.3918 | 0.065452 | -0.00049559 | 0.0095533 | 0.00083309 | -0.67749 | 61.2396 | -59.9167 | 61.734 | -59.6329 | -60.1135 | -60.1547 | 0.004578 | 61.2305 | -60.0082 | 61.496 | -59.935 | -59.9991 | -60.1456 | 0.059509 | -0.20142 | 0.29297 | 0.34332 | -0.17853 | -0.13733 | -0.23804 | -0.19684 | -0.032044 | -0.21057 | 0.054932 | 0.041198 | -0.16937 | -0.022888 | -0.13733 | 0.009156 | 0.28381 | 121.6507 | 0.073242 | 121.5042 | 121.1563 | 121.2387 | 121.2158 | 121.2067 | -121.3577 | -121.4493 | 121.7102 | 121.4722 | 59.2987 | 59.9808
536.9062 | 121.6461 | -59.9167 | 61.5921 | 0.0019074 | 0 | 0.063254 | 0.063929 | 0.00027771 | -0.0022794 | -0.0023712 | -0.0028687 | 0.0031124 | -1.3918 | 0.057762 | -0.0051954 | 0.0063489 | 0.0016877 | -0.68207 | 61.3312 | -59.8343 | 61.702 | -59.6924 | -60.1135 | -60.1822 | -0.086975 | 61.3495 | -59.9304 | 61.441 | -59.9442 | -59.9899 | -60.1364 | 0.082397 | -0.26093 | 0.10986 | 0.2243 | -0.2655 | -0.19684 | -0.3479 | -0.27923 | -0.013733 | -0.24261 | -0.15106 | -0.027466 | -0.21973 | -0.073242 | -0.20599 | -0.059509 | 0.14191 | 121.5363 | -0.013733 | 121.3715 | 121.1655 | 121.2799 | 121.2479 | 121.2662 | -121.4264 | -121.5225 | 121.6187 | 121.3577 | 59.2346 | 59.8297
538.6094 | 121.7743 | -59.9625 | 61.4548 | 0.0019074 | 0 | 0.066031 | 0.063288 | 0.00049131 | -0.001852 | 0.0012604 | 0.021545 | 0.0024716 | -1.3912 | 0.067802 | -0.00092279 | 0.0091261 | 0.0033967 | -0.71869 | 61.2076 | -59.8892 | 61.7157 | -59.6649 | -60.1135 | -60.173 | 0.018311 | 61.2167 | -60.0403 | 61.496 | -59.903 | -59.9716 | -60.1044 | 0.073242 | -0.24719 | 0.26093 | 0.29755 | -0.21057 | -0.15106 | -0.28381 | -0.2243 | -0.07782 | -0.23804 | 0.041199 | 0.059509 | -0.14191 | -0.009156 | -0.064087 | 0.068664 | 0.2243 | 121.6049 | 0.13733 | 121.5363 | 121.0968 | 121.257 | 121.17 | 121.1792 | -121.344 | -121.4951 | 121.6782 | 121.4584 | 59.2438 | 59.9808
540.3906 | 121.7697 | -59.8572 | 61.5509 | 0.0019074 | 0 | 0.063681 | 0.064142 | -0.00079049 | -0.0016384 | -0.0010894 | -0.0028687 | 0.00033544 | -1.3948 | 0.063743 | -0.0043408 | 0.0057081 | 0.00083309 | -0.63171 | 61.3037 | -59.7885 | 61.8393 | -59.5322 | -59.967 | -60.0632 | 0.073242 | 61.3129 | -59.8755 | 61.5784 | -59.7839 | -59.8434 | -60.0128 | 0.068665 | -0.24719 | 0.28839 | 0.32501 | -0.20599 | -0.10986 | -0.27466 | -0.17853 | -0.01831 | -0.23804 | 0.027466 | 0.073242 | -0.15564 | 0.013733 | -0.13733 | 0.032043 | 0.25635 | 121.6278 | 0.091552 | 121.4539 | 121.0922 | 121.1884 | 121.1609 | 121.17 | -121.3394 | -121.4264 | 121.6965 | 121.4355 | 59.2255 | 59.9304
542.1719 | 121.669 | -59.7977 | 61.6974 | 0.047683 | 0 | 0.066245 | 0.065424 | 0.00049131 | 7.0564e-05 | -0.00087583 | 0.015442 | 0.002258 | -1.3922 | 0.062248 | -0.0028454 | 0.0050671 | -0.0045075 | -0.67291 | 61.4822 | -59.7656 | 61.8256 | -59.5825 | -59.967 | -60.0632 | -0.073242 | 61.4822 | -59.8297 | 61.5601 | -59.816 | -59.8755 | -60.0174 | 0.032043 | -0.21515 | 0.12817 | 0.21515 | -0.2655 | -0.16937 | -0.29755 | -0.20142 | -0.032044 | -0.21515 | -0.13733 | -0.018311 | -0.21973 | -0.07782 | -0.18768 | -0.045776 | 0.1831 | 121.5912 | 0.013733 | 121.3898 | 121.2479 | 121.312 | 121.2799 | 121.2799 | -121.463 | -121.5271 | 121.6232 | 121.3577 | 59.1248 | 59.7244
543.875 | 121.7697 | -59.935 | 61.5051 | -0.0057221 | 0 | 0.06539 | 0.064783 | -0.0048493 | -0.00014304 | -0.0021576 | -0.0059205 | 0.0011898 | -1.3952 | 0.056907 | -0.003059 | 0.0054945 | -0.00066231 | -0.65918 | 61.2625 | -59.8343 | 61.7981 | -59.5871 | -60.0174 | -60.1135 | 0.041199 | 61.2762 | -59.9121 | 61.5509 | -59.8297 | -59.8755 | -60.0815 | 0.10071 | -0.24262 | 0.29297 | 0.3479 | -0.17853 | -0.082397 | -0.27923 | -0.1831 | 0.022889 | -0.22888 | 0.045776 | 0.10529 | -0.14648 | 0.05951 | -0.16937 | 0.036621 | 0.24719 | 121.6324 | 0.082397 | 121.463 | 121.0968 | 121.1884 | 121.1975 | 121.2112 | -121.3394 | -121.4172 | 121.7331 | 121.4859 | 59.2758 | 59.9762
545.5781 | 121.6919 | -60.0082 | 61.4639 | 0.024795 | 0 | 0.063895 | 0.064356 | 0.0034821 | -0.00057044 | 0.0016876 | 0.0032349 | 0.0011898 | -1.3935 | 0.060111 | -0.0034864 | 0.0057081 | 0.0016877 | -0.6958 | 61.2122 | -59.967 | 61.6608 | -59.7336 | -60.1822 | -60.2463 | -0.018311 | 61.2442 | -60.0266 | 61.3953 | -59.9808 | -60.0586 | -60.1913 | 0.041199 | -0.25177 | 0.19684 | 0.27466 | -0.23804 | -0.17395 | -0.27924 | -0.21515 | -0.01831 | -0.21973 | -0.068664 | 0.027466 | -0.1831 | -0.050354 | -0.16479 | -0.032044 | 0.23346 | 121.6278 | 0.045776 | 121.4218 | 121.1792 | 121.2708 | 121.2204 | 121.2524 | -121.431 | -121.4905 | 121.669 | 121.4035 | 59.3124 | 59.9899
547.3438 | 121.7789 | -59.9579 | 61.4365 | -0.013352 | 0 | 0.066885 | 0.06457 | 0.0028411 | 0.0013522 | -0.00066223 | 0.00018312 | 0.001617 | -1.394 | 0.065025 | 0.0020678 | 0.0078443 | -0.0013031 | -0.77362 | 61.2534 | -59.8663 | 61.7203 | -59.6741 | -60.1318 | -60.1913 | -0.036621 | 61.2259 | -59.9854 | 61.5051 | -59.9075 | -59.9716 | -60.1089 | 0.091553 | -0.1831 | 0.28381 | 0.28381 | -0.23346 | -0.17395 | -0.32501 | -0.2655 | -0.027466 | -0.21057 | 0.068665 | 0.050354 | -0.15106 | -0.013733 | -0.1236 | 0.013733 | 0.19226 | 121.5866 | 0.07782 | 121.4905 | 121.1197 | 121.2112 | 121.2112 | 121.1838 | -121.3028 | -121.4218 | 121.6782 | 121.463 | 59.1843 | 59.9213
549.125 | 121.637 | -59.9625 | 61.5326 | 0.0095369 | 0 | 0.062827 | 0.066065 | 0.0034821 | -0.0012112 | -0.00066223 | 0.00018312 | 0.0020444 | -1.3955 | 0.064597 | -0.0032728 | 0.0082715 | -0.00066231 | -0.7782 | 61.3129 | -59.8618 | 61.6653 | -59.7244 | -60.1639 | -60.2371 | -0.13733 | 61.3037 | -59.9716 | 61.409 | -59.9991 | -60.0632 | -60.1868 | 0.10071 | -0.21973 | 0.13275 | 0.23804 | -0.27466 | -0.20142 | -0.37537 | -0.30212 | -0.009156 | -0.22888 | -0.1236 | -0.036621 | -0.22431 | -0.10071 | -0.21515 | -0.091552 | 0.13733 | 121.5271 | -0.027465 | 121.3806 | 121.1746 | 121.2753 | 121.2753 | 121.2662 | -121.3943 | -121.5042 | 121.6278 | 121.3715 | 59.1843 | 59.8251
550.8906 | 121.7743 | -60.0952 | 61.3083 | 0.0019074 | 0 | 0.06539 | 0.061365 | -0.0029267 | -0.0016384 | -0.0027984 | 0.0032349 | 0.00033544 | -1.394 | 0.065025 | -0.005409 | 0.0099805 | -0.00023491 | -0.74616 | 61.0474 | -60.0403 | 61.6013 | -59.7519 | -60.2005 | -60.2966 | 0.054932 | 61.0565 | -60.1135 | 61.3449 | -60.0128 | -60.0769 | -60.2463 | 0.054932 | -0.26093 | 0.29297 | 0.34332 | -0.20142 | -0.10528 | -0.25635 | -0.16022 | -0.01831 | -0.25177 | 0.036621 | 0.082398 | -0.15106 | 0.018311 | -0.13275 | 0.036621 | 0.28839 | 121.6415 | 0.10071 | 121.4584 | 121.0876 | 121.17 | 121.1426 | 121.1517 | -121.3486 | -121.4218 | 121.6965 | 121.4401 | 59.3491 | 60.1501
552.5938 | 121.7789 | -59.9854 | 61.3953 | 0.0019074 | 0 | 0.064108 | 0.062006 | -0.0018585 | -0.0039884 | -2.1434e-05 | -0.0059205 | 0.0011898 | -1.3937 | 0.07357 | -0.0024182 | 0.0076307 | 0.00040589 | -0.70038 | 61.1526 | -59.9304 | 61.702 | -59.6466 | -60.1135 | -60.2051 | 0.064087 | 61.1801 | -60.022 | 61.4365 | -59.9121 | -59.9579 | -60.1593 | 0.054932 | -0.24262 | 0.3067 | 0.33875 | -0.21973 | -0.12817 | -0.27466 | -0.18311 | -0.036621 | -0.21515 | 0.041198 | 0.073243 | -0.17395 | 0.027466 | -0.13733 | 0.064087 | 0.28381 | 121.6324 | 0.10986 | 121.4584 | 121.0831 | 121.2021 | 121.138 | 121.1655 | -121.3257 | -121.4172 | 121.6873 | 121.4218 | 59.285 | 60.0494
554.3438 | 121.756 | -60.0128 | 61.4136 | 0.0019074 | 0 | 0.064749 | 0.066492 | -0.00014949 | 0.00092496 | 0.0029694 | 0.015442 | 0.00076264 | -1.3922 | 0.059043 | -0.00049559 | 0.0063489 | 0.00061949 | -0.80566 | 61.1389 | -59.9716 | 61.702 | -59.6786 | -60.1456 | -60.2097 | 0 | 61.171 | -60.0586 | 61.441 | -59.9533 | -60.0174 | -60.1593 | 0.041198 | -0.27466 | 0.28839 | 0.33417 | -0.19684 | -0.13275 | -0.23804 | -0.17395 | -0.045777 | -0.24261 | 0.027466 | 0.059509 | -0.14648 | -0.004578 | -0.10071 | 0.041199 | 0.29297 | 121.6736 | 0.10529 | 121.4996 | 121.1105 | 121.2296 | 121.1517 | 121.1838 | -121.3852 | -121.4722 | 121.7148 | 121.4539 | 59.2072 | 60.0128
556.0625 | 121.7239 | -59.9075 | 61.5051 | 0.062942 | 0 | 0.065817 | 0.066065 | 0.0077545 | -0.00057044 | -0.00044863 | 0.01239 | 0.00054904 | -1.3914 | 0.06887 | -0.0024182 | 0.0065625 | 0.0031829 | -0.80566 | 61.2671 | -59.8755 | 61.7523 | -59.61 | -60.0952 | -60.1547 | -0.018311 | 61.2534 | -59.9716 | 61.496 | -59.9213 | -59.9579 | -60.1044 | 0.032044 | -0.23804 | 0.24719 | 0.29755 | -0.24719 | -0.18768 | -0.27924 | -0.21973 | -0.064087 | -0.25177 | -0.009155 | -0.013733 | -0.19684 | -0.050354 | -0.13275 | 0.013733 | 0.2655 | 121.6278 | 0.050354 | 121.4676 | 121.1426 | 121.225 | 121.1746 | 121.1609 | -121.3806 | -121.4767 | 121.6599 | 121.4035 | 59.1019 | 59.8892
557.8281 | 121.6415 | -59.9396 | 61.5097 | 0.0019074 | 0 | 0.064536 | 0.065851 | -0.00057689 | -0.00057044 | -0.00066223 | -0.0028687 | 0.003326 | -1.3944 | 0.064384 | -0.0017774 | 0.0074171 | -0.0019439 | -0.80109 | 61.3312 | -59.8663 | 61.702 | -59.6878 | -60.141 | -60.1959 | -0.091553 | 61.3174 | -59.9579 | 61.4319 | -59.9854 | -60.0357 | -60.1547 | 0.073242 | -0.17853 | 0.19226 | 0.25177 | -0.25635 | -0.20142 | -0.32959 | -0.27466 | -0.018311 | -0.19226 | -0.07782 | -0.045777 | -0.21515 | -0.096131 | -0.19684 | -0.07782 | 0.17853 | 121.5683 | -0.027466 | 121.3898 | 121.1975 | 121.2753 | 121.2708 | 121.257 | -121.376 | -121.4676 | 121.6415 | 121.3715 | 59.1385 | 59.848
559.5312 | 121.6782 | -59.8938 | 61.5509 | 0.032425 | 0 | 0.064749 | 0.066706 | -0.0029267 | -0.0014248 | 0.001474 | 0.015442 | 0.0020444 | -1.3944 | 0.055839 | -0.001991 | 0.0065625 | 0.00083309 | -0.7782 | 61.3678 | -59.848 | 61.7569 | -59.6466 | -60.0403 | -60.1135 | -0.073242 | 61.377 | -59.9304 | 61.5005 | -59.8938 | -59.935 | -60.0906 | 0.045777 | -0.1831 | 0.20599 | 0.24719 | -0.21973 | -0.14648 | -0.2655 | -0.19226 | -0.036621 | -0.17395 | -0.050354 | 0 | -0.19684 | -0.041199 | -0.16022 | -0.004578 | 0.20142 | 121.6049 | 0.036621 | 121.431 | 121.2158 | 121.3074 | 121.2616 | 121.2708 | -121.3989 | -121.4813 | 121.6507 | 121.3943 | 59.1156 | 59.8206
561.2969 | 121.7606 | -59.8114 | 61.5967 | 0.0019074 | 0 | 0.064322 | 0.064356 | 0.00049131 | -0.0020658 | -0.00044863 | -0.0028687 | -9.1956e-05 | -1.3948 | 0.062034 | -0.0039136 | 0.0078443 | 0.0029693 | -0.85144 | 61.3678 | -59.7565 | 61.8439 | -59.5139 | -59.9258 | -60.0082 | -0.004578 | 61.377 | -59.8297 | 61.6562 | -59.729 | -59.7702 | -59.9533 | 0.054931 | -0.22888 | 0.24719 | 0.29755 | -0.19684 | -0.11444 | -0.25177 | -0.16937 | -0.018311 | -0.21973 | 0.059509 | 0.082397 | -0.14191 | 0.041198 | -0.1236 | 0.059509 | 0.24262 | 121.6003 | 0.10071 | 121.4859 | 121.1243 | 121.2067 | 121.1792 | 121.1884 | -121.3531 | -121.4264 | 121.6553 | 121.4676 | 58.96 | 59.8068
563 | 121.6965 | -59.7931 | 61.6745 | 0.0019074 | 0 | 0.063895 | 0.062647 | -0.0020721 | -0.0029202 | -0.001303 | -0.0059205 | 0.0024716 | -1.395 | 0.063529 | -0.003059 | 0.0046399 | -0.0019439 | -0.78735 | 61.3861 | -59.7244 | 61.8896 | -59.4681 | -59.8938 | -59.9899 | 0.013733 | 61.4319 | -59.816 | 61.6104 | -59.7656 | -59.8251 | -59.9762 | 0.068665 | -0.28839 | 0.21515 | 0.32501 | -0.19684 | -0.10071 | -0.2655 | -0.16937 | -0.022888 | -0.24262 | -0.064087 | 0.027466 | -0.18311 | -0.032043 | -0.16022 | -0.009155 | 0.25635 | 121.6141 | 0.050354 | 121.4264 | 121.1105 | 121.2479 | 121.1792 | 121.225 | -121.3989 | -121.4905 | 121.6827 | 121.4035 | 59.0057 | 59.8068
564.7969 | 121.6461 | -60.1868 | 61.3358 | -0.0057221 | 0 | 0.064322 | 0.06457 | 0.0028411 | -0.0031338 | 0.00019217 | -0.0028687 | 0.001617 | -1.3948 | 0.062034 | -0.0045544 | 0.0050671 | 0.0014741 | -0.87891 | 61.0748 | -60.1227 | 61.3998 | -59.9716 | -60.3699 | -60.4614 | -0.09613 | 61.0703 | -60.1959 | 61.1664 | -60.2097 | -60.26 | -60.4111 | 0.064087 | -0.26093 | 0.064087 | 0.21515 | -0.27466 | -0.1831 | -0.33875 | -0.24719 | -0.009155 | -0.2655 | -0.16937 | -0.022888 | -0.2243 | -0.073242 | -0.21515 | -0.064087 | 0.15106 | 121.5225 | -0.013733 | 121.3623 | 121.1975 | 121.2662 | 121.2616 | 121.257 | -121.4584 | -121.5317 | 121.5866 | 121.3531 | 59.3079 | 60.0906
566.4844 | 121.7194 | -60.2188 | 61.2167 | 0.040054 | 0 | 0.067954 | 0.063929 | -0.0018585 | -0.00014304 | -0.00087583 | 0.0062865 | 0.0014034 | -1.3931 | 0.06417 | -0.003059 | 0.0086987 | 0.0031829 | -0.84228 | 60.9741 | -60.1685 | 61.4227 | -59.9396 | -60.3745 | -60.4431 | -0.004578 | 60.9833 | -60.2646 | 61.1938 | -60.2097 | -60.2371 | -60.4202 | 0.050354 | -0.24262 | 0.20599 | 0.27924 | -0.2243 | -0.15564 | -0.27466 | -0.20599 | -0.045776 | -0.23346 | -0.022888 | 0.009155 | -0.20142 | -0.018311 | -0.15564 | 0.027465 | 0.22888 | 121.5912 | 0.054931 | 121.4584 | 121.1426 | 121.2479 | 121.1929 | 121.2021 | -121.3852 | -121.4813 | 121.6415 | 121.4127 | 59.3765 | 60.2142
568.25 | 121.6415 | -60.1547 | 61.3495 | -0.0057221 | 0 | 0.064322 | 0.066065 | 0.0017731 | -0.001852 | -2.1434e-05 | -0.0059205 | 0.0018306 | -1.3935 | 0.066093 | -0.0022046 | 0.0057081 | 0.0021149 | -0.92468 | 61.1114 | -60.0632 | 61.4319 | -59.9899 | -60.4156 | -60.4797 | -0.18768 | 61.116 | -60.1501 | 61.2259 | -60.2188 | -60.2692 | -60.3653 | 0.091553 | -0.23804 | 0.082398 | 0.1648 | -0.32501 | -0.26093 | -0.41657 | -0.35248 | 0.004578 | -0.23346 | -0.1236 | -0.064087 | -0.21057 | -0.11444 | -0.21515 | -0.11902 | 0.073242 | 121.4951 | -0.068665 | 121.376 | 121.1746 | 121.2662 | 121.2662 | 121.2708 | -121.4127 | -121.4996 | 121.5866 | 121.3806 | 59.23 | 59.967
569.9375 | 121.756 | -60.1685 | 61.2396 | -0.013352 | 0 | 0.06304 | 0.063074 | 0.0028411 | -0.0022794 | 0.001474 | 0.021545 | 0.0020444 | -1.3942 | 0.066947 | 0.0024952 | 0.0072035 | -0.00023491 | -0.90637 | 60.9787 | -60.0998 | 61.5555 | -59.8297 | -60.2921 | -60.3607 | 0.009155 | 61.0565 | -60.2234 | 61.2854 | -60.1089 | -60.1639 | -60.3058 | 0.068665 | -0.26093 | 0.31586 | 0.33874 | -0.19226 | -0.1236 | -0.26093 | -0.19226 | -0.054932 | -0.1831 | 0.045776 | 0.059509 | -0.13733 | 0.004578 | -0.082397 | 0.05951 | 0.27008 | 121.6553 | 0.11444 | 121.5088 | 121.0785 | 121.2799 | 121.1472 | 121.225 | -121.3394 | -121.463 | 121.7239 | 121.4539 | 59.2621 | 60.1776
571.6406 | 121.7148 | -60.2051 | 61.2122 | 0.032425 | 0 | 0.066458 | 0.06457 | -0.0012177 | -0.00014304 | -0.00044863 | 0.0062865 | 0.0018306 | -1.3946 | 0.068015 | -0.003059 | 0.0067761 | -0.00066231 | -0.9201 | 60.9604 | -60.1456 | 61.4365 | -59.9213 | -60.3699 | -60.4385 | -0.059509 | 60.9833 | -60.2234 | 61.2259 | -60.1868 | -60.2234 | -60.3882 | 0.059509 | -0.25177 | 0.2243 | 0.28381 | -0.23346 | -0.16479 | -0.29297 | -0.2243 | -0.018311 | -0.22888 | 0.013733 | 0.01831 | -0.18311 | -0.018311 | -0.1648 | 0 | 0.2243 | 121.582 | 0.036621 | 121.4493 | 121.106 | 121.2067 | 121.1655 | 121.1884 | -121.3577 | -121.4355 | 121.6415 | 121.431 | 59.285 | 60.1456
573.3906 | 121.756 | -59.9213 | 61.4685 | -0.013352 | 0 | 0.065604 | 0.063074 | 0.0011321 | -0.00078404 | -0.0015166 | -0.0059205 | 0.00076264 | -1.3935 | 0.060966 | -0.00028199 | 0.0084851 | -0.0027985 | -0.94757 | 61.2717 | -59.8618 | 61.7249 | -59.6832 | -60.1364 | -60.1685 | -0.054932 | 61.2534 | -59.9625 | 61.5234 | -59.8892 | -59.9487 | -60.0723 | 0.05951 | -0.19684 | 0.25635 | 0.23804 | -0.24719 | -0.21515 | -0.3067 | -0.27466 | -0.041198 | -0.21515 | 0.054931 | 0.032044 | -0.15106 | -0.027465 | -0.10986 | 0.013733 | 0.17853 | 121.5866 | 0.073242 | 121.4859 | 121.1334 | 121.2158 | 121.1929 | 121.1746 | -121.3303 | -121.431 | 121.6461 | 121.4447 | 58.9737 | 59.8663
575.1719 | 121.6461 | -59.8846 | 61.5921 | 0.0019074 | 0 | 0.063467 | 0.065851 | -0.0018585 | -0.0014248 | -0.00044863 | 0.0032349 | 0.001617 | -1.394 | 0.063957 | -0.006477 | 0.0054945 | -0.00066231 | -0.92468 | 61.3632 | -59.8343 | 61.7249 | -59.6741 | -60.0769 | -60.1593 | -0.082397 | 61.4044 | -59.9396 | 61.4594 | -59.9258 | -59.9762 | -60.0998 | 0.050354 | -0.22888 | 0.13275 | 0.21057 | -0.27466 | -0.19226 | -0.32501 | -0.24261 | -0.054931 | -0.18768 | -0.13275 | -0.041198 | -0.21515 | -0.091552 | -0.16022 | -0.036621 | 0.16022 | 121.5591 | 0.013733 | 121.3989 | 121.1975 | 121.344 | 121.2479 | 121.2891 | -121.4264 | -121.5317 | 121.6095 | 121.344 | 58.96 | 59.8022
576.9375 | 121.7056 | -60.1318 | 61.2991 | 0.017166 | 0 | 0.064963 | 0.064997 | -0.0012177 | 0.00092496 | 0.00083317 | 0.0032349 | -0.00051916 | -1.3957 | 0.066306 | -0.00049559 | 0.0076307 | 0.0033967 | -0.95673 | 61.0428 | -60.0632 | 61.5097 | -59.8618 | -60.2829 | -60.3699 | -0.07782 | 61.0565 | -60.1639 | 61.2762 | -60.1089 | -60.1685 | -60.3058 | 0.068665 | -0.25635 | 0.21057 | 0.27008 | -0.23804 | -0.15106 | -0.3067 | -0.21973 | -0.032043 | -0.24261 | -0.022888 | 0.022888 | -0.17395 | -0.036621 | -0.14191 | -0.004578 | 0.20142 | 121.5729 | 0.054931 | 121.4401 | 121.106 | 121.2204 | 121.1746 | 121.1884 | -121.3623 | -121.463 | 121.6415 | 121.4081 | 59.1751 | 60.054
578.6406 | 121.7102 | -60.0815 | 61.3358 | -0.0057221 | 0 | 0.064749 | 0.062647 | 0.0022003 | -0.0020658 | -0.0010894 | -0.0028687 | 0.00076264 | -1.3942 | 0.063743 | -0.0045544 | 0.0076307 | 0.0031829 | -0.89722 | 61.0703 | -60.022 | 61.6013 | -59.7839 | -60.2051 | -60.3058 | 0.013733 | 61.0931 | -60.1089 | 61.322 | -60.0357 | -60.0815 | -60.26 | 0.059509 | -0.2655 | 0.2655 | 0.29755 | -0.2243 | -0.1236 | -0.28381 | -0.1831 | -0.027466 | -0.24261 | -0.013733 | 0.045776 | -0.17853 | 0 | -0.15106 | 0.027466 | 0.23804 | 121.6232 | 0.073242 | 121.431 | 121.0922 | 121.2021 | 121.1517 | 121.1746 | -121.3577 | -121.4447 | 121.6827 | 121.4035 | 59.1843 | 60.0952
580.3906 | 121.637 | -60.26 | 61.2167 | -0.0057221 | 0 | 0.06304 | 0.061793 | -0.0054901 | -0.003561 | 0.002115 | 0.00018312 | 0.0018306 | -1.3946 | 0.068015 | -0.0032728 | 0.0050671 | 0.0014741 | -0.92468 | 60.9604 | -60.173 | 61.377 | -59.9899 | -60.4156 | -60.5026 | -0.068665 | 60.9879 | -60.2783 | 61.1069 | -60.2783 | -60.3104 | -60.4752 | 0.086975 | -0.25635 | 0.16022 | 0.27008 | -0.24262 | -0.15564 | -0.32959 | -0.24261 | -0.01831 | -0.22888 | -0.10986 | -0.01831 | -0.21515 | -0.050354 | -0.19684 | -0.032044 | 0.18311 | 121.55 | 0 | 121.3852 | 121.1334 | 121.2662 | 121.2204 | 121.2479 | -121.3898 | -121.4951 | 121.637 | 121.3669 | 59.3353 | 60.1913
582.0781 | 121.7148 | -60.5759 | 60.8368 | 0.055313 | 0 | 0.065604 | 0.066492 | 0.00070491 | -0.00078404 | 0.00019217 | 0.015442 | -0.00051916 | -1.3929 | 0.063316 | 0.00014521 | 0.0069897 | -0.0021575 | -0.98877 | 60.6354 | -60.5255 | 61.0886 | -60.2692 | -60.7269 | -60.8047 | -0.041199 | 60.6262 | -60.6262 | 60.8551 | -60.553 | -60.585 | -60.759 | 0.050354 | -0.20142 | 0.25177 | 0.3067 | -0.22888 | -0.15106 | -0.27924 | -0.20142 | -0.050354 | -0.21057 | 0.018311 | 0.022888 | -0.1831 | -0.009155 | -0.13275 | 0.041199 | 0.25635 | 121.6141 | 0.073242 | 121.4813 | 121.1609 | 121.2524 | 121.2112 | 121.2021 | -121.3623 | -121.463 | 121.6644 | 121.431 | 59.5871 | 60.5347
583.8438 | 121.6782 | -60.6491 | 60.8139 | 0.047683 | 0 | 0.065604 | 0.066065 | -0.0010041 | -0.0014248 | -2.1434e-05 | 0.018494 | 0.0031124 | -1.392 | 0.064811 | -0.0043408 | 0.0059217 | -2.1314e-05 | -0.97046 | 60.6216 | -60.5896 | 61.0016 | -60.3928 | -60.7956 | -60.878 | -0.07782 | 60.64 | -60.6674 | 60.759 | -60.64 | -60.6949 | -60.8139 | 0.059509 | -0.19226 | 0.18768 | 0.25635 | -0.22888 | -0.14648 | -0.28839 | -0.20599 | -0.01831 | -0.17395 | -0.054932 | 0.009155 | -0.16479 | -0.045776 | -0.14648 | -0.027466 | 0.19684 | 121.5912 | 0.027465 | 121.4264 | 121.2112 | 121.3074 | 121.2708 | 121.2891 | -121.4035 | -121.4813 | 121.6507 | 121.4081 | 59.6787 | 60.5713
585.5469 | 121.7514 | -61.4319 | 59.9533 | 0.0019074 | 0 | 0.063681 | 0.063929 | -0.0010041 | -0.001852 | -0.00023503 | -0.0059205 | -9.1956e-05 | -1.3944 | 0.063529 | -0.0056226 | 0.0042127 | -2.1314e-05 | -0.98877 | 59.729 | -61.3495 | 60.2509 | -61.0748 | -61.5417 | -61.6516 | 0.022888 | 59.7244 | -61.4502 | 60.0082 | -61.3586 | -61.3953 | -61.5967 | 0.082398 | -0.2243 | 0.29755 | 0.35706 | -0.21973 | -0.10986 | -0.30212 | -0.19226 | -0.01831 | -0.22888 | 0.054932 | 0.073242 | -0.16479 | 0.036621 | -0.14648 | 0.054931 | 0.27466 | 121.6003 | 0.091552 | 121.4584 | 121.0785 | 121.1746 | 121.1609 | 121.1563 | -121.3028 | -121.4035 | 121.6827 | 121.4401 | 60.4431 | 61.4548
587.3281 | 121.7651 | -60.7773 | 60.6171 | -0.0057221 | 0 | 0.063681 | 0.065211 | 0.0047637 | -0.0016384 | -0.001944 | -0.0028687 | 0.0014034 | -1.394 | 0.059898 | 0.00014521 | 0.0084851 | 0.0014741 | -1.0483 | 60.3745 | -60.7178 | 60.8643 | -60.5118 | -60.9467 | -61.0245 | -0.045776 | 60.3836 | -60.8414 | 60.6674 | -60.7498 | -60.8093 | -60.9375 | 0.05951 | -0.24261 | 0.24719 | 0.2655 | -0.24719 | -0.16937 | -0.3067 | -0.22888 | -0.064087 | -0.23346 | 0.050354 | 0.027466 | -0.16022 | -0.032043 | -0.09613 | 0.032044 | 0.20599 | 121.582 | 0.091553 | 121.5088 | 121.0922 | 121.225 | 121.1517 | 121.1609 | -121.3348 | -121.4584 | 121.6415 | 121.4447 | 59.729 | 60.7315
589.0312 | 121.7789 | -60.4843 | 60.9009 | 0.0019074 | 0 | 0.064108 | 0.063715 | -0.0042083 | 0.00028416 | 0.00040597 | -0.0028687 | -0.00030556 | -1.3937 | 0.07357 | -0.0037 | 0.0086987 | 0.0012603 | -1.0117 | 60.7224 | -60.3745 | 61.2167 | -60.141 | -60.5713 | -60.6445 | -0.004578 | 60.7132 | -60.4889 | 60.997 | -60.379 | -60.4294 | -60.5988 | 0.10986 | -0.17853 | 0.31586 | 0.34332 | -0.16022 | -0.086975 | -0.27008 | -0.19684 | -0.004578 | -0.18768 | 0.09613 | 0.10529 | -0.11444 | 0.054932 | -0.10986 | 0.05951 | 0.23346 | 121.5912 | 0.10986 | 121.4859 | 121.0968 | 121.2021 | 121.2067 | 121.1975 | -121.2753 | -121.3898 | 121.701 | 121.4813 | 59.4727 | 60.4797
590.7969 | 121.6599 | -62.4481 | 59.0332 | -0.013352 | 0 | 0.063467 | 0.063929 | -0.0059173 | -0.003561 | -0.00066223 | 0.0032349 | 0.0028988 | -1.3942 | 0.058402 | -0.005409 | 0.0063489 | -0.0017303 | -1.0666 | 58.7585 | -62.3566 | 59.1888 | -62.1597 | -62.6083 | -62.6816 | -0.082397 | 58.8135 | -62.4527 | 58.9371 | -62.4435 | -62.4893 | -62.6495 | 0.091553 | -0.27466 | 0.15564 | 0.28839 | -0.23346 | -0.16022 | -0.32501 | -0.25177 | -0.004578 | -0.21973 | -0.09613 | 0.004578 | -0.20142 | -0.041199 | -0.19684 | -0.036621 | 0.19684 | 121.5454 | 0.009156 | 121.3898 | 121.1151 | 121.2662 | 121.2067 | 121.2616 | -121.3898 | -121.4859 | 121.637 | 121.3852 | 61.3815 | 62.3657
592.5781 | 121.7285 | -62.6266 | 58.754 | 0.040054 | 0 | 0.066885 | 0.066706 | 0.00091851 | -0.00057044 | 0.0023286 | 0.015442 | -0.0015872 | -1.3927 | 0.073356 | -0.00070919 | 0.0078443 | 0.00061949 | -1.1261 | 58.5388 | -62.5854 | 59.0515 | -62.2879 | -62.7502 | -62.8326 | -0.004578 | 58.548 | -62.6999 | 58.8135 | -62.5854 | -62.6358 | -62.8006 | 0.041199 | -0.21515 | 0.29755 | 0.33875 | -0.20599 | -0.1236 | -0.24719 | -0.1648 | -0.073242 | -0.20599 | 0.05951 | 0.041199 | -0.17395 | -0.009155 | -0.10071 | 0.064087 | 0.29755 | 121.637 | 0.11444 | 121.5134 | 121.1243 | 121.2479 | 121.1655 | 121.1746 | -121.3394 | -121.4539 | 121.6782 | 121.4401 | 61.5005 | 62.6221
594.3438 | 121.6461 | -63.4964 | 57.9483 | 0.0019074 | 0 | 0.066031 | 0.064356 | 0.0026275 | -0.0020658 | -0.0027984 | -0.0059205 | 0.001617 | -1.3942 | 0.064384 | -0.0011364 | 0.0091261 | 0.0012603 | -1.2314 | 57.7515 | -63.414 | 58.0994 | -63.2767 | -63.7344 | -63.7985 | -0.19684 | 57.7744 | -63.4964 | 57.8979 | -63.5468 | -63.588 | -63.6978 | 0.082398 | -0.19684 | 0.15106 | 0.21973 | -0.30212 | -0.23804 | -0.38452 | -0.32044 | 0 | -0.17395 | -0.050354 | -0.050354 | -0.20142 | -0.091553 | -0.20142 | -0.091553 | 0.13733 | 121.5134 | -0.050354 | 121.3943 | 121.1655 | 121.2708 | 121.2479 | 121.2708 | -121.3623 | -121.4447 | 121.5958 | 121.3943 | 62.265 | 63.2996
596.0938 | 121.7926 | -64.2883 | 57.1381 | 0.0019074 | 0 | 0.064536 | 0.063074 | -0.0022857 | -0.00078404 | -0.001944 | 0.00018312 | -0.0020146 | -1.3948 | 0.062248 | -0.0043408 | 0.0078443 | -0.0013031 | -1.1536 | 56.8863 | -64.2151 | 57.4081 | -63.9084 | -64.3616 | -64.4485 | 0.054932 | 56.8726 | -64.2883 | 57.2113 | -64.151 | -64.2059 | -64.3936 | 0.073242 | -0.25177 | 0.27008 | 0.37994 | -0.16022 | -0.073242 | -0.23346 | -0.14648 | 0 | -0.2655 | 0.073242 | 0.13733 | -0.10529 | 0.082397 | -0.10529 | 0.082397 | 0.3067 | 121.6232 | 0.13733 | 121.4996 | 121.1014 | 121.1609 | 121.1746 | 121.1609 | -121.3531 | -121.4264 | 121.6965 | 121.4996 | 63.1348 | 64.3433
597.8594 | 121.6461 | -63.0432 | 58.4427 | 0.0019074 | 0 | 0.062399 | 0.064997 | 6.4114e-05 | -0.0037746 | 0.0010468 | 0.021545 | 0.0035396 | -1.3931 | 0.058189 | -0.0056226 | 0.0035719 | -0.00066231 | -1.1902 | 58.1497 | -62.9791 | 58.5709 | -62.7823 | -63.2034 | -63.2767 | -0.07782 | 58.2367 | -63.1027 | 58.3145 | -63.0661 | -63.1073 | -63.2675 | 0.064087 | -0.29297 | 0.12817 | 0.26093 | -0.23346 | -0.16022 | -0.29755 | -0.2243 | -0.059509 | -0.20599 | -0.12817 | -0.022888 | -0.2243 | -0.064087 | -0.16479 | -0.004578 | 0.19684 | 121.55 | 0.036621 | 121.4172 | 121.1288 | 121.3394 | 121.1929 | 121.2799 | -121.4218 | -121.5454 | 121.6141 | 121.3577 | 61.853 | 62.9654
599.5625 | 121.6782 | -63.7848 | 57.6691 | 0.040054 | 0 | 0.066672 | 0.064356 | 0.0013459 | -0.002493 | 0.0012604 | 0.01239 | 0.0035396 | -1.3942 | 0.06182 | -0.0034864 | 0.0063489 | -0.0010895 | -1.1765 | 57.4677 | -63.7756 | 57.8384 | -63.5147 | -63.9359 | -64.0274 | -0.11902 | 57.4905 | -63.8672 | 57.605 | -63.7711 | -63.8214 | -63.9725 | 0.009155 | -0.20142 | 0.16937 | 0.27008 | -0.24262 | -0.15106 | -0.25177 | -0.16022 | -0.082397 | -0.17853 | -0.064087 | 0.013733 | -0.18768 | -0.036621 | -0.10529 | 0.045776 | 0.26093 | 121.6141 | 0.09613 | 121.4722 | 121.2433 | 121.3577 | 121.2524 | 121.2753 | -121.4447 | -121.5363 | 121.6232 | 121.3898 | 62.6083 | 63.6658
601.3125 | 121.7606 | -64.325 | 57.1106 | 0.0019074 | 0 | 0.065176 | 0.063288 | 0.0024139 | -0.0020658 | -0.001303 | -0.0059205 | 0.0024716 | -1.394 | 0.069724 | -0.00049559 | 0.0086987 | -0.0013031 | -1.2863 | 56.9687 | -64.1235 | 57.4173 | -63.8901 | -64.3662 | -64.476 | -0.16479 | 56.8771 | -64.2792 | 57.1472 | -64.2197 | -64.3158 | -64.4623 | 0.20142 | -0.14191 | 0.3067 | 0.43487 | -0.15106 | -0.041199 | -0.35248 | -0.24262 | 0.045776 | -0.23346 | 0.036621 | 0.10528 | -0.13733 | 0.009155 | -0.18311 | -0.036621 | 0.23346 | 121.5408 | 0.059509 | 121.4264 | 121.0922 | 121.1563 | 121.2936 | 121.2021 | -121.2341 | -121.3898 | 121.7422 | 121.4722 | 63.0386 | 64.1602
603.0781 | 121.7651 | -64.769 | 56.6437 | 0.0019074 | 0 | 0.064108 | 0.064783 | 0.00049131 | -0.0046292 | -0.00066223 | -0.0028687 | -0.00116 | -1.3925 | 0.063529 | -0.0041272 | 0.0076307 | -0.0027985 | -1.2131 | 56.4011 | -64.6774 | 56.9366 | -64.3662 | -64.8285 | -64.9338 | 0.013733 | 56.4102 | -64.7827 | 56.6895 | -64.65 | -64.7049 | -64.9063 | 0.091553 | -0.24261 | 0.29297 | 0.40283 | -0.1648 | -0.059509 | -0.25635 | -0.15106 | -0.013733 | -0.23346 | 0.045776 | 0.11902 | -0.13733 | 0.064087 | -0.1236 | 0.07782 | 0.31128 | 121.6141 | 0.13275 | 121.4722 | 121.0785 | 121.1929 | 121.17 | 121.1792 | -121.3211 | -121.4264 | 121.7056 | 121.4584 | 63.5559 | 64.7827
604.8594 | 121.6873 | -63.8351 | 57.6141 | 0.017166 | 0 | 0.064749 | 0.065638 | 0.0032685 | -0.0014248 | -0.0010894 | 0.0062865 | 0.00054904 | -1.3914 | 0.058189 | -0.0013502 | 0.0091261 | -0.0019439 | -1.2222 | 57.3853 | -63.7848 | 57.7927 | -63.5559 | -64.0137 | -64.0823 | -0.082397 | 57.3624 | -63.858 | 57.5867 | -63.7985 | -63.8443 | -64.0091 | 0.050354 | -0.22888 | 0.17853 | 0.27924 | -0.24719 | -0.17853 | -0.29755 | -0.22888 | -0.022888 | -0.25177 | -0.027466 | 0.036621 | -0.17395 | -0.009155 | -0.15106 | 0.013733 | 0.22888 | 121.5775 | 0.059509 | 121.4447 | 121.17 | 121.2204 | 121.2204 | 121.1975 | -121.3989 | -121.4722 | 121.6278 | 121.4218 | 62.6129 | 63.7527
606.5625 | 121.7239 | -65.3 | 56.0898 | 0.032425 | 0 | 0.063681 | 0.064142 | 0.00049131 | -0.00035684 | -0.00044863 | 0.0093383 | 0.00097624 | -1.3931 | 0.064597 | -0.0028454 | 0.0084851 | -0.0021575 | -1.4465 | 55.8655 | -65.2634 | 56.337 | -64.9796 | -65.4556 | -65.5289 | -0.19684 | 55.9113 | -65.3687 | 56.1218 | -65.2771 | -65.3091 | -65.4694 | 0.036621 | -0.2243 | 0.24719 | 0.32044 | -0.22888 | -0.15564 | -0.2655 | -0.19226 | -0.068664 | -0.17853 | 0.032043 | 0.022888 | -0.16937 | -0.009155 | -0.10071 | 0.059509 | 0.28381 | 121.6003 | 0.091552 | 121.4905 | 121.1288 | 121.2799 | 121.1655 | 121.2112 | -121.3531 | -121.4584 | 121.637 | 121.4218 | 63.8535 | 65.1031
608.3438 | 121.7285 | -66.9388 | 54.4785 | 0.062942 | 0 | 0.067526 | 0.065638 | 0.0019867 | 0.0013522 | -0.00044863 | 0.015442 | 0.00012184 | -1.3927 | 0.066093 | -6.8386e-05 | 0.0080579 | 0.0023285 | -1.4236 | 54.2679 | -66.8655 | 54.744 | -66.5543 | -67.0715 | -67.131 | -0.10529 | 54.245 | -67.0029 | 54.5151 | -66.8747 | -66.925 | -67.0898 | 0.073242 | -0.21057 | 0.2655 | 0.38452 | -0.19226 | -0.13275 | -0.2655 | -0.20599 | -0.064087 | -0.23346 | 0.036621 | 0.064087 | -0.15106 | 0.013733 | -0.086975 | 0.07782 | 0.31128 | 121.6095 | 0.12817 | 121.5179 | 121.1334 | 121.2479 | 121.2067 | 121.1838 | -121.344 | -121.4813 | 121.6827 | 121.4539 | 65.5151 | 66.8335
610.1094 | 121.7468 | -67.3737 | 54.0756 | -0.0057221 | 0 | 0.064749 | 0.064356 | 0.0026275 | -0.0020658 | 0.0010468 | -0.0028687 | -0.00030556 | -1.3942 | 0.065238 | -0.0032728 | 0.0063489 | -0.0010895 | -1.3779 | 53.8147 | -67.2821 | 54.3182 | -66.9846 | -67.4606 | -67.5613 | -0.082397 | 53.7735 | -67.4011 | 54.1077 | -67.2409 | -67.3141 | -67.5018 | 0.091553 | -0.26093 | 0.24261 | 0.3891 | -0.18768 | -0.086975 | -0.27924 | -0.17853 | -0.027466 | -0.30212 | 0.032043 | 0.13275 | -0.12817 | 0.059509 | -0.10071 | 0.086975 | 0.29755 | 121.6003 | 0.16022 | 121.5088 | 121.0968 | 121.1746 | 121.1884 | 121.1472 | -121.3577 | -121.4767 | 121.6919 | 121.4813 | 65.9958 | 67.2913
611.8125 | 121.7102 | -68.7469 | 52.6428 | 0.017166 | 0 | 0.06539 | 0.063929 | -0.0012177 | -0.00078404 | -0.0015166 | 0.0093383 | 0.0014034 | -1.3952 | 0.067161 | -0.0026318 | 0.0080579 | -0.0038665 | -1.5518 | 52.4139 | -68.7286 | 52.8854 | -68.4128 | -68.8889 | -68.9529 | -0.16479 | 52.4506 | -68.779 | 52.6703 | -68.7149 | -68.7469 | -68.9301 | 0.01831 | -0.22888 | 0.24262 | 0.33417 | -0.20599 | -0.14191 | -0.2243 | -0.16022 | -0.032044 | -0.19226 | 0.027466 | 0.032043 | -0.18311 | 0 | -0.15106 | 0.032044 | 0.31586 | 121.6141 | 0.064087 | 121.4493 | 121.1426 | 121.2296 | 121.1609 | 121.1975 | -121.3715 | -121.4218 | 121.6324 | 121.4172 | 67.1951 | 68.5822
613.5312 | 121.6324 | -69.6899 | 51.7319 | 0.0019074 | 0 | 0.064322 | 0.066065 | -0.00057689 | -0.002493 | 0.0019012 | -0.0028687 | 0.0024716 | -1.3942 | 0.062888 | -0.0013502 | 0.0082715 | 0.0016877 | -1.5976 | 51.535 | -69.6487 | 51.8784 | -69.4702 | -69.9463 | -70.0104 | -0.27008 | 51.5579 | -69.7449 | 51.6998 | -69.6945 | -69.7495 | -69.8959 | 0.041198 | -0.19684 | 0.14648 | 0.21973 | -0.32043 | -0.25635 | -0.36163 | -0.29755 | -0.054932 | -0.17395 | -0.032044 | -0.004578 | -0.20599 | -0.05951 | -0.15106 | -0.004578 | 0.17853 | 121.5271 | 0.050354 | 121.4447 | 121.1838 | 121.3028 | 121.225 | 121.2479 | -121.3806 | -121.4767 | 121.5683 | 121.3898 | 68.0923 | 69.4199
615.2969 | 121.6278 | -69.3878 | 52.0981 | 0.0019074 | 0 | 0.064536 | 0.065211 | 0.0028411 | -0.0022794 | -0.001303 | 0.0032349 | 0.0020444 | -1.3933 | 0.065025 | -0.00092279 | 0.0097669 | -0.0017303 | -1.6434 | 51.8463 | -69.3192 | 52.2217 | -69.0903 | -69.5847 | -69.6487 | -0.29755 | 51.8921 | -69.4153 | 52.0432 | -69.3466 | -69.4153 | -69.5572 | 0.068664 | -0.25177 | 0.1236 | 0.29755 | -0.26093 | -0.19684 | -0.32959 | -0.2655 | -0.027466 | -0.20599 | -0.054931 | 0.041198 | -0.16937 | -0.027466 | -0.14191 | 0 | 0.22888 | 121.5408 | 0.068664 | 121.4584 | 121.1655 | 121.3074 | 121.2341 | 121.2799 | -121.4172 | -121.5134 | 121.6095 | 121.431 | 67.7444 | 69.0903
617.0625 | 121.7056 | -69.6075 | 51.8097 | 0.0019074 | 0 | 0.063467 | 0.061793 | 0.00070491 | -0.0022794 | 0.00019217 | -0.0028687 | 0.0011898 | -1.3955 | 0.060539 | -0.0041272 | 0.0065625 | -0.0021575 | -1.5198 | 51.5533 | -69.516 | 52.0523 | -69.2322 | -69.7128 | -69.8044 | -0.10071 | 51.5808 | -69.6625 | 51.8326 | -69.4977 | -69.5663 | -69.7495 | 0.091553 | -0.25635 | 0.24262 | 0.37537 | -0.19684 | -0.10529 | -0.28839 | -0.19684 | -0.054932 | -0.22888 | 0.022889 | 0.10986 | -0.14191 | 0.041199 | -0.086975 | 0.096131 | 0.28381 | 121.5683 | 0.16479 | 121.4951 | 121.0693 | 121.2433 | 121.1609 | 121.1884 | -121.3257 | -121.4722 | 121.6599 | 121.4401 | 68.0878 | 69.5068
618.8438 | 121.7194 | -69.0445 | 52.3636 | 0.024795 | 0 | 0.066245 | 0.063929 | -0.0014313 | -0.0037746 | -0.001944 | 0.00018312 | 0.00012184 | -1.3931 | 0.060539 | -0.0037 | 0.0084851 | -0.00044851 | -1.593 | 52.1255 | -68.9987 | 52.5742 | -68.7149 | -69.191 | -69.2551 | -0.16937 | 52.1347 | -69.0857 | 52.4139 | -68.9438 | -68.9896 | -69.191 | 0.045777 | -0.23804 | 0.21057 | 0.32959 | -0.21057 | -0.14648 | -0.25635 | -0.19226 | -0.041198 | -0.22888 | 0.050354 | 0.10071 | -0.14648 | 0.054932 | -0.10529 | 0.09613 | 0.28381 | 121.5729 | 0.14191 | 121.4996 | 121.1243 | 121.2204 | 121.17 | 121.1792 | -121.3623 | -121.4493 | 121.6187 | 121.4584 | 67.4515 | 68.8751
620.5469 | 121.7194 | -70.1431 | 51.2741 | 0.017166 | 0 | 0.063895 | 0.065851 | 0.0036957 | 0.00028416 | 0.0012604 | 0.0062865 | 0.0018306 | -1.3931 | 0.062248 | -0.0013502 | 0.0067761 | -0.0017303 | -1.6754 | 51.0773 | -70.0745 | 51.5076 | -69.7678 | -70.253 | -70.3262 | -0.23346 | 51.0544 | -70.1981 | 51.3016 | -70.0653 | -70.1202 | -70.2805 | 0.068664 | -0.19684 | 0.23346 | 0.37537 | -0.18311 | -0.10986 | -0.25177 | -0.17853 | -0.054932 | -0.21973 | 0.027466 | 0.077819 | -0.13733 | 0.022888 | -0.082398 | 0.07782 | 0.3067 | 121.582 | 0.13275 | 121.4996 | 121.1517 | 121.2524 | 121.2204 | 121.1975 | -121.3486 | -121.4722 | 121.6507 | 121.4447 | 68.4677 | 69.9097
622.2812 | 121.6461 | -69.5389 | 51.915 | 0.0019074 | 0 | 0.066031 | 0.064142 | 6.4114e-05 | -0.0020658 | -0.00087583 | 0.00018312 | 0.0024716 | -1.3946 | 0.058189 | -0.0062634 | 0.0059217 | 0.0012603 | -1.6022 | 51.6541 | -69.4382 | 52.121 | -69.1681 | -69.6533 | -69.7403 | -0.1831 | 51.6815 | -69.5572 | 51.86 | -69.4885 | -69.5435 | -69.7311 | 0.10071 | -0.26093 | 0.20599 | 0.37079 | -0.20142 | -0.11444 | -0.30212 | -0.21515 | -0.018311 | -0.23346 | -0.054932 | 0.050354 | -0.19226 | -0.004578 | -0.17395 | 0.013733 | 0.27008 | 121.5591 | 0.068665 | 121.4172 | 121.0922 | 121.2387 | 121.1929 | 121.2204 | -121.3531 | -121.4722 | 121.6599 | 121.3989 | 67.9367 | 69.3558
624.0469 | 121.6278 | -67.9047 | 53.5629 | 0.0019074 | 0 | 0.063895 | 0.066065 | 0.0049773 | 0.00049776 | -0.0015166 | 0.00018312 | 0.0020444 | -1.3952 | 0.063957 | -0.00049559 | 0.0063489 | 0.00061949 | -1.6113 | 53.3615 | -67.8085 | 53.7003 | -67.6392 | -68.1015 | -68.1702 | -0.27008 | 53.389 | -67.9138 | 53.4988 | -67.8864 | -67.955 | -68.0969 | 0.09613 | -0.20142 | 0.13733 | 0.2655 | -0.2655 | -0.19684 | -0.36163 | -0.29297 | -0.009155 | -0.17395 | -0.064087 | 0.01831 | -0.19226 | -0.050354 | -0.18311 | -0.041199 | 0.16937 | 121.5088 | 0.027465 | 121.4127 | 121.17 | 121.3028 | 121.2662 | 121.2936 | -121.3715 | -121.4767 | 121.6049 | 121.4035 | 66.2933 | 67.6346
625.75 | 121.6415 | -75.0275 | 46.4539 | 0.0019074 | 0 | 0.064108 | 0.063074 | -0.0012177 | -0.0022794 | 0.002115 | -0.0059205 | 0.0014034 | -1.3944 | 0.061179 | -0.0037 | 0.0052807 | 0.00040589 | -1.9272 | 46.1884 | -74.968 | 46.5546 | -74.675 | -75.1602 | -75.2563 | -0.35248 | 46.2524 | -75.1236 | 46.3623 | -74.9634 | -75.0412 | -75.2151 | 0.059509 | -0.2655 | 0.10071 | 0.35248 | -0.22888 | -0.13275 | -0.28839 | -0.19226 | -0.09613 | -0.20142 | -0.091552 | 0.064087 | -0.18768 | -0.013733 | -0.091553 | 0.082397 | 0.29297 | 121.5225 | 0.16022 | 121.4859 | 121.1563 | 121.376 | 121.2158 | 121.2799 | -121.4218 | -121.5775 | 121.582 | 121.3898 | 73.1003 | 74.675
627.5312 | 121.7606 | -79.1428 | 42.1967 | -0.0057221 | 0 | 0.064749 | 0.067133 | 0.0019867 | -0.0022794 | 0.00083317 | -0.0059205 | 0.001617 | -1.3927 | 0.066947 | -0.0032728 | 0.0069897 | 0.00083309 | -0.89722 | 42.0273 | -79.1245 | 42.4347 | -78.7811 | -79.3488 | -79.4037 | 0.70953 | 42.0319 | -79.248 | 42.3111 | -79.0466 | -79.1336 | -79.3488 | 0.01831 | -0.16937 | 0.23804 | 0.36163 | -0.26093 | -0.20599 | -0.27924 | -0.2243 | -0.10529 | -0.16479 | 0.11444 | 0.09613 | -0.20599 | 0.009155 | -0.10071 | 0.11444 | 0.34332 | 121.5591 | 0.20142 | 121.5591 | 121.1517 | 121.2799 | 121.17 | 121.1746 | -121.3211 | -121.4447 | 121.5775 | 121.4539 | 78.2455 | 79.8523
629.2969 | 121.6827 | -74.4278 | 47.0306 | 0.040054 | 0 | 0.066885 | 0.062861 | 0.0032685 | 0.00092496 | 0.00019217 | 0.01239 | 0.0037532 | -1.3944 | 0.067161 | -0.0039136 | 0.0091261 | 0.00083309 | -1.8265 | 46.8613 | -74.3271 | 47.2321 | -74.025 | -74.5102 | -74.6017 | -0.31128 | 46.8704 | -74.4598 | 47.0169 | -74.3271 | -74.3912 | -74.5651 | 0.10071 | -0.16937 | 0.20142 | 0.40283 | -0.17395 | -0.082398 | -0.27466 | -0.18311 | -0.032044 | -0.16022 | -0.013733 | 0.10071 | -0.13733 | 0.036621 | -0.10529 | 0.068665 | 0.30212 | 121.5591 | 0.13275 | 121.4767 | 121.1884 | 121.3303 | 121.2891 | 121.2982 | -121.3577 | -121.4905 | 121.6599 | 121.4447 | 72.6013 | 74.1165
631.0625 | 121.6644 | -81.0287 | 40.3976 | 0.0019074 | 0 | 0.064536 | 0.066706 | 0.0030547 | -0.001852 | 0.00040597 | 0.018494 | 0.00097624 | -1.3922 | 0.059257 | -0.0039136 | 0.0067761 | 0.0040375 | -2.1927 | 40.1779 | -81.0516 | 40.5121 | -80.6717 | -81.1523 | -81.2714 | -0.49896 | 40.2328 | -81.1569 | 40.3976 | -80.9326 | -81.0013 | -81.2073 | -0.022888 | -0.21973 | 0.11444 | 0.35706 | -0.24261 | -0.1236 | -0.21973 | -0.10071 | -0.12817 | -0.16479 | 0 | 0.096131 | -0.17853 | 0.027466 | -0.050354 | 0.15564 | 0.37994 | 121.5637 | 0.2243 | 121.5546 | 121.2296 | 121.3898 | 121.2067 | 121.2616 | -121.4493 | -121.5546 | 121.5408 | 121.4264 | 78.8361 | 80.5298
632.7969 | 121.6782 | -79.3488 | 42.1005 | 0.055313 | 0 | 0.064108 | 0.067774 | 0.0022003 | -0.0012112 | 0.0027558 | 0.0093383 | 0.0031124 | -1.3933 | 0.064384 | -0.0045544 | 0.0089123 | 0.0055329 | -2.0874 | 41.9312 | -79.2664 | 42.3157 | -78.9047 | -79.4266 | -79.5181 | -0.41199 | 41.9632 | -79.39 | 42.1326 | -79.1885 | -79.2618 | -79.4495 | 0.082398 | -0.16937 | 0.21515 | 0.44403 | -0.16937 | -0.07782 | -0.25177 | -0.16022 | -0.041199 | -0.13733 | 0.032043 | 0.16022 | -0.10071 | 0.086975 | -0.059509 | 0.12817 | 0.36163 | 121.582 | 0.20142 | 121.5225 | 121.1975 | 121.3531 | 121.2799 | 121.312 | -121.3669 | -121.4905 | 121.6644 | 121.4813 | 77.2614 | 78.9368
634.5781 | 121.7789 | -86.5585 | 34.758 | 0.0019074 | 0 | 0.065176 | 0.060724 | 0.00070491 | -0.00057044 | -0.0017304 | 0.021545 | 0.0020444 | -1.3918 | 0.070579 | 0.00078621 | 0.010835 | 0.0012603 | -2.5177 | 34.5337 | -86.5082 | 35.0464 | -86.0779 | -86.6318 | -86.7371 | -0.55847 | 34.6069 | -86.705 | 34.9548 | -86.3617 | -86.4624 | -86.6867 | 0.050354 | -0.22431 | 0.28839 | 0.48065 | -0.17853 | -0.073242 | -0.22888 | -0.1236 | -0.14648 | -0.15106 | 0.19684 | 0.19684 | -0.12817 | 0.096131 | 0.01831 | 0.24262 | 0.4303 | 121.5546 | 0.34332 | 121.6599 | 121.0419 | 121.312 | 121.0922 | 121.1655 | -121.2662 | -121.463 | 121.6049 | 121.5134 | 84.0408 | 86.0001
636.3594 | 121.7285 | -87.6663 | 33.7234 | 0.0019074 | 0 | 0.063254 | 0.065638 | -0.0022857 | -0.00057044 | 0.0019012 | 0.00018312 | -0.00073276 | -1.3948 | 0.064384 | -0.0011364 | 0.0074171 | 0.00040589 | -2.5726 | 33.4442 | -87.6572 | 33.8882 | -87.2314 | -87.8128 | -87.8998 | -0.6546 | 33.5129 | -87.7441 | 33.8333 | -87.4786 | -87.5565 | -87.7899 | 0.009155 | -0.27924 | 0.16479 | 0.43488 | -0.23346 | -0.14648 | -0.24261 | -0.15564 | -0.07782 | -0.21057 | 0.10986 | 0.18768 | -0.1236 | 0.10986 | -0.045776 | 0.18768 | 0.42572 | 121.5454 | 0.2655 | 121.5775 | 121.1014 | 121.257 | 121.1105 | 121.1792 | -121.3806 | -121.4676 | 121.5546 | 121.4996 | 85.0937 | 87.0117
638.125 | 121.6141 | -81.1066 | 40.3519 | -0.0057221 | 0 | 0.066885 | 0.065638 | 0.0039093 | -0.002493 | -0.0010894 | 0.0032349 | 0.00054904 | -1.3946 | 0.061607 | -0.0039136 | 0.0076307 | -0.0034393 | -1.3275 | 40.2328 | -80.8777 | 40.6906 | -80.5161 | -81.0425 | -81.1432 | 0.31128 | 40.3427 | -80.9555 | 40.4892 | -81.0379 | -81.134 | -81.2897 | 0.22888 | -0.11902 | 0.33874 | 0.59051 | -0.036621 | 0.064087 | -0.2655 | -0.16479 | 0.15106 | -0.009156 | 0.13733 | 0.068664 | -0.18311 | -0.027466 | -0.33417 | -0.17853 | 0.36163 | 121.5683 | -0.082398 | 121.4447 | 121.1105 | 121.2982 | 121.3394 | 121.4493 | -121.2296 | -121.3074 | 121.7972 | 121.5958 | 79.7791 | 81.4178
639.8281 | 121.756 | -82.7133 | 38.6673 | -0.020981 | 0 | 0.06539 | 0.064142 | -0.0027131 | 0.0017796 | 0.0010468 | 0.018494 | 0.00054904 | -1.392 | 0.069297 | -0.0011364 | 0.0095533 | 0.00061949 | -2.3392 | 38.4293 | -82.6309 | 38.974 | -82.196 | -82.7637 | -82.8552 | -0.48523 | 38.4888 | -82.7957 | 38.8 | -82.5073 | -82.5897 | -82.814 | 0.082398 | -0.23804 | 0.3067 | 0.51727 | -0.14191 | -0.050354 | -0.22431 | -0.13275 | -0.082397 | -0.17853 | 0.13275 | 0.20599 | -0.10071 | 0.1236 | -0.018311 | 0.20599 | 0.43488 | 121.6049 | 0.28839 | 121.5958 | 121.0602 | 121.2845 | 121.1426 | 121.2021 | -121.2982 | -121.463 | 121.6873 | 121.5134 | 80.3741 | 82.2281
641.5312 | 121.6782 | -84.8282 | 37.2299 | 0.017166 | 0 | 0.065176 | 0.063074 | 0.00049131 | -0.0027066 | -0.0034392 | 0.00018312 | -9.1956e-05 | -1.3922 | 0.07357 | -0.0043408 | 0.010194 | 0.00083309 | -2.2614 | 34.4376 | -86.6592 | 34.8999 | -86.2061 | -86.7645 | -86.8561 | -0.33417 | 34.5291 | -86.7325 | 35.0098 | -86.2473 | -86.0641 | -84.9197 | -1.8311 | -2.7924 | -2.33 | -1.3779 | -2.0279 | -1.9363 | -0.19684 | -0.10529 | -1.9043 | -2.7008 | -2.2202 | -1.4191 | -0.091553 | -1.236 | 1.8127 | 0.66833 | 0.45319 | 121.5591 | 0.48523 | 121.7422 | 121.0968 | 121.2616 | 119.2657 | 119.3573 | -123.8892 | -123.9624 | 119.7281 | 119.838 | 82.5668 | 84.494
643.3125 | 121.7743 | -89.0854 | 32.2678 | -0.0057221 | 0 | 0.065604 | 0.061579 | -0.0012177 | -0.0031338 | -0.003653 | 0.00018312 | -0.0013736 | -1.3946 | 0.06182 | -0.0032728 | 0.0059217 | -2.1314e-05 | -2.6413 | 32.0435 | -89.0213 | 32.5607 | -88.5269 | -89.1174 | -89.241 | -0.70496 | 32.0801 | -89.1953 | 32.4692 | -88.8199 | -88.9389 | -89.1953 | 0.064087 | -0.2243 | 0.29297 | 0.55847 | -0.15564 | -0.032044 | -0.21973 | -0.096131 | -0.10986 | -0.18768 | 0.20142 | 0.2655 | -0.10986 | 0.14648 | 0 | 0.25635 | 0.49438 | 121.582 | 0.37537 | 121.6644 | 121.0648 | 121.2753 | 121.1288 | 121.1655 | -121.2891 | -121.463 | 121.6461 | 121.5546 | 86.4441 | 88.3804
645.0781 | 121.7651 | -89.5111 | 31.8375 | -0.0057221 | 0 | 0.062186 | 0.062647 | -0.0010041 | -0.0022794 | -2.1434e-05 | -0.0028687 | -0.0013736 | -1.394 | 0.059684 | -0.0028454 | 0.0084851 | -0.0013031 | -2.6871 | 31.5765 | -89.4745 | 32.1808 | -88.916 | -89.5294 | -89.6347 | -0.71411 | 31.6727 | -89.566 | 31.9931 | -89.2685 | -89.36 | -89.6347 | 0.036621 | -0.26093 | 0.34332 | 0.59509 | -0.1236 | -0.018311 | -0.16022 | -0.054932 | -0.054932 | -0.16479 | 0.15564 | 0.24261 | -0.1236 | 0.15106 | -0.068665 | 0.20599 | 0.55847 | 121.6553 | 0.29755 | 121.5591 | 121.051 | 121.2387 | 121.0876 | 121.1838 | -121.3119 | -121.4035 | 121.6919 | 121.5042 | 86.824 | 88.797
646.7969 | 121.6278 | -90.9256 | 30.5008 | 0.0019074 | 0 | 0.066031 | 0.065851 | -0.00057689 | -0.00014304 | -0.0017304 | -0.0028687 | 0.0031124 | -1.3946 | 0.061179 | -0.003059 | 0.0084851 | 0.00019229 | -2.8336 | 30.2765 | -90.8569 | 30.661 | -90.4633 | -91.0538 | -91.1591 | -0.97504 | 30.3543 | -90.9897 | 30.5191 | -90.802 | -90.8936 | -91.095 | 0.068664 | -0.2243 | 0.16022 | 0.46234 | -0.23346 | -0.12817 | -0.30212 | -0.19684 | -0.064087 | -0.14648 | 0.018311 | 0.1236 | -0.16937 | 0.032043 | -0.10529 | 0.09613 | 0.39368 | 121.5179 | 0.18768 | 121.5088 | 121.1334 | 121.344 | 121.2021 | 121.2799 | -121.3577 | -121.4905 | 121.5866 | 121.4447 | 88.092 | 89.9506
648.5156 | 121.7606 | -87.5702 | 33.8242 | -0.0057221 | 0 | 0.063895 | 0.062433 | -0.00057689 | -0.0033474 | -0.0032256 | 0.00018312 | -0.00094636 | -1.3959 | 0.073142 | -0.0037 | 0.0074171 | -0.0017303 | -2.623 | 33.5632 | -87.4741 | 34.1446 | -86.9751 | -87.5656 | -87.6892 | -0.71411 | 33.6411 | -87.6251 | 33.9523 | -87.3093 | -87.4146 | -87.6663 | 0.09613 | -0.26093 | 0.32043 | 0.59509 | -0.11902 | 0.004577 | -0.21515 | -0.091553 | -0.054932 | -0.18311 | 0.12817 | 0.26093 | -0.096131 | 0.15564 | -0.041199 | 0.21057 | 0.49896 | 121.6187 | 0.31586 | 121.5775 | 121.0373 | 121.2662 | 121.1334 | 121.2112 | -121.2982 | -121.4493 | 121.7148 | 121.5225 | 84.9472 | 86.8561
650.2969 | 121.7239 | -97.6044 | 23.7488 | 0.047683 | 0 | 0.065817 | 0.065211 | -0.0014313 | -0.00014304 | -0.00087583 | 0.0093383 | 0.00054904 | -1.3922 | 0.06182 | -0.0032728 | 0.0067761 | -0.00023491 | -3.2227 | 23.5565 | -97.5677 | 23.996 | -97.0459 | -97.6639 | -97.7875 | -1.2405 | 23.5977 | -97.7783 | 23.8724 | -97.3984 | -97.4991 | -97.7554 | 0.036621 | -0.19226 | 0.24719 | 0.55847 | -0.18311 | -0.059509 | -0.21973 | -0.09613 | -0.17395 | -0.15106 | 0.1236 | 0.20599 | -0.15106 | 0.10529 | 0.022888 | 0.27924 | 0.52185 | 121.5637 | 0.37994 | 121.6507 | 121.1243 | 121.376 | 121.1609 | 121.2021 | -121.3165 | -121.5271 | 121.6003 | 121.4767 | 94.3817 | 96.3638
652.0625 | 121.6599 | -90.4449 | 30.9769 | 0.0095369 | 0 | 0.065604 | 0.065851 | 0.0041229 | -0.0029202 | -0.0023712 | 0.0062865 | 0.0026852 | -1.3935 | 0.060539 | -0.0043408 | 0.0074171 | 0.00040589 | -2.8336 | 30.7755 | -90.3763 | 31.2149 | -89.8819 | -90.4816 | -90.6052 | -0.95673 | 30.8166 | -90.5136 | 31.041 | -90.239 | -90.3488 | -90.564 | 0.068664 | -0.20142 | 0.23804 | 0.56305 | -0.16022 | -0.036621 | -0.22888 | -0.10528 | -0.068665 | -0.16022 | 0.064087 | 0.20599 | -0.11902 | 0.09613 | -0.050354 | 0.16479 | 0.49439 | 121.5912 | 0.27466 | 121.5546 | 121.1517 | 121.3303 | 121.2204 | 121.2616 | -121.3531 | -121.4905 | 121.6599 | 121.4859 | 87.6114 | 89.4882
653.8281 | 121.6278 | -91.8594 | 29.5807 | -0.013352 | 0 | 0.066672 | 0.065638 | 0.00091851 | -0.001852 | -2.1434e-05 | 0.00018312 | 0.0024716 | -1.3942 | 0.059043 | -0.0017774 | 0.0082715 | 0.0019013 | -2.9755 | 29.393 | -91.7679 | 29.7043 | -91.4246 | -92.0013 | -92.1021 | -1.0849 | 29.4113 | -91.9418 | 29.599 | -91.6992 | -91.8091 | -91.9968 | 0.091553 | -0.18768 | 0.1236 | 0.43488 | -0.24262 | -0.14191 | -0.33417 | -0.23346 | -0.082397 | -0.16937 | 0.018311 | 0.16022 | -0.13733 | 0.050354 | -0.054932 | 0.13275 | 0.34332 | 121.4722 | 0.24261 | 121.5408 | 121.1609 | 121.3531 | 121.2524 | 121.2708 | -121.3486 | -121.5225 | 121.5637 | 121.4584 | 88.884 | 90.7745
655.5312 | 121.5546 | -92.926 | 28.5004 | -0.0057221 | 0 | 0.067099 | 0.065851 | -0.0016449 | -0.00527 | 0.0029694 | 0.00018312 | 0.002258 | -1.394 | 0.060325 | -0.0026318 | 0.0076307 | -0.0068573 | -3.067 | 28.244 | -92.8574 | 28.6606 | -92.4591 | -93.0771 | -93.1595 | -1.1673 | 28.3173 | -93.0267 | 28.5049 | -92.7979 | -92.894 | -93.0771 | 0.068664 | -0.25635 | 0.16022 | 0.46692 | -0.23346 | -0.15106 | -0.30212 | -0.21973 | -0.10071 | -0.18311 | 0.004578 | 0.12817 | -0.15106 | 0.032043 | -0.050354 | 0.13275 | 0.39825 | 121.5179 | 0.22888 | 121.5317 | 121.1014 | 121.344 | 121.17 | 121.2433 | -121.3577 | -121.5271 | 121.5866 | 121.431 | 89.859 | 91.7587
657.2812 | 121.6827 | -43.5699 | 77.8702 | -0.0057221 | 0 | 0.066031 | 0.063074 | 6.4114e-05 | -0.00057044 | -0.0017304 | 0.0032349 | -0.0032962 | -1.3976 | 0.063529 | 0.00035881 | 0.0093397 | -0.0017303 | -0.79193 | 77.6779 | -43.4006 | 78.1631 | -43.309 | -43.6752 | -43.7485 | 0.082397 | 77.6276 | -43.4647 | 77.8564 | -43.5471 | -43.5928 | -43.6798 | 0.16937 | -0.19226 | 0.29297 | 0.26093 | -0.17853 | -0.10529 | -0.3479 | -0.27466 | 0.10529 | -0.24262 | -0.013733 | 0.022888 | -0.10986 | -0.022888 | -0.21515 | -0.12817 | 0.091553 | 121.5637 | -0.082397 | 121.3211 | 121.0785 | 121.0922 | 121.2479 | 121.1975 | -121.2708 | -121.3348 | 121.7331 | 121.4264 | 42.778 | 43.6523
659.0469 | 121.6415 | -43.6798 | 77.7466 | 0.017166 | 0 | 0.065176 | 0.064997 | -0.0033539 | -0.0020658 | -0.00066223 | 0.0032349 | -0.00030556 | -1.3946 | 0.072288 | -0.005409 | 0.0069897 | -0.0017303 | -0.8606 | 77.4994 | -43.602 | 77.9114 | -43.5333 | -43.8858 | -43.959 | 0.013733 | 77.4948 | -43.6707 | 77.6779 | -43.7393 | -43.7485 | -43.8583 | 0.07782 | -0.24719 | 0.16479 | 0.14649 | -0.27923 | -0.20599 | -0.35706 | -0.28381 | 0.009156 | -0.25177 | -0.068665 | -0.059509 | -0.17853 | -0.068664 | -0.18768 | -0.07782 | 0.068665 | 121.5134 | -0.068665 | 121.3486 | 121.1014 | 121.1655 | 121.1792 | 121.1746 | -121.3486 | -121.4172 | 121.5912 | 121.3577 | 42.8192 | 43.6935
660.75 | 121.5729 | -43.4784 | 78.0304 | -0.0057221 | 0 | 0.063467 | 0.060724 | 6.4114e-05 | -0.0022794 | 0.00019217 | -0.0028687 | 0.00054904 | -1.3931 | 0.057762 | -0.0062634 | 0.0063489 | -0.00023491 | -0.8606 | 77.7557 | -43.3914 | 78.1128 | -43.3914 | -43.7347 | -43.7805 | -0.041199 | 77.7374 | -43.4509 | 77.8061 | -43.5699 | -43.6157 | -43.7027 | 0.086976 | -0.27466 | 0.082397 | 0.086976 | -0.30212 | -0.25635 | -0.3891 | -0.34332 | 0.027466 | -0.29297 | -0.22431 | -0.091552 | -0.2243 | -0.13733 | -0.25177 | -0.1648 | 0 | 121.5042 | -0.11902 | 121.257 | 121.1472 | 121.1884 | 121.2341 | 121.2158 | -121.4218 | -121.4813 | 121.5912 | 121.2845 | 42.6178 | 43.4372
662.5156 | 121.6644 | -41.5924 | 79.834 | 0.0019074 | 0 | 0.066031 | 0.066279 | 0.00027771 | -0.00099764 | -0.0021576 | -0.0028687 | 0.0026852 | -1.3974 | 0.059257 | -0.0024182 | 0.0086987 | 0.0023285 | -0.83313 | 79.6371 | -41.5237 | 79.9713 | -41.5237 | -41.8854 | -41.9312 | -0.009155 | 79.5776 | -41.5741 | 79.7424 | -41.6794 | -41.7114 | -41.7709 | 0.068664 | -0.19684 | 0.13733 | 0.068664 | -0.33874 | -0.29297 | -0.40741 | -0.36163 | 0.01831 | -0.25635 | -0.091552 | -0.086975 | -0.17853 | -0.11902 | -0.19684 | -0.13733 | 0 | 121.4951 | -0.10528 | 121.3165 | 121.1609 | 121.1517 | 121.2296 | 121.17 | -121.3577 | -121.4081 | 121.5637 | 121.3348 | 40.7593 | 41.5833
664.2969 | 121.7102 | -41.4276 | 79.9713 | 0.0019074 | 0 | 0.064108 | 0.064142 | -0.0020721 | -0.001852 | -0.0032256 | -0.0028687 | -9.1956e-05 | -1.3959 | 0.065238 | -0.00092279 | 0.010408 | 0.00061949 | -0.78278 | 79.7333 | -41.3544 | 80.1956 | -41.2766 | -41.6473 | -41.6885 | 0.054932 | 79.7012 | -41.4047 | 79.9667 | -41.4551 | -41.5009 | -41.5878 | 0.073242 | -0.23804 | 0.22431 | 0.15106 | -0.26093 | -0.21973 | -0.33417 | -0.29297 | 0.022888 | -0.27008 | -0.004577 | -0.027466 | -0.16022 | -0.073242 | -0.18311 | -0.09613 | 0.07782 | 121.55 | -0.050354 | 121.3715 | 121.0876 | 121.106 | 121.1609 | 121.1288 | -121.3257 | -121.376 | 121.6232 | 121.3943 | 40.6448 | 41.4825
666 | 121.7239 | -42.2699 | 79.1336 | 0.0095369 | 0 | 0.062613 | 0.063502 | -0.0014313 | -0.0027066 | -0.00023503 | -0.0028687 | -9.1956e-05 | -1.3935 | 0.061607 | -0.0013502 | 0.0093397 | 0.0019013 | -0.86517 | 78.8956 | -42.2287 | 79.3488 | -42.1417 | -42.4576 | -42.5262 | 0.054932 | 78.8864 | -42.2607 | 79.1061 | -42.2928 | -42.2974 | -42.4301 | 0.041198 | -0.23804 | 0.21515 | 0.12817 | -0.25635 | -0.18768 | -0.29755 | -0.22888 | 0.009155 | -0.24719 | -0.027466 | -0.022889 | -0.16022 | -0.027466 | -0.16937 | -0.036621 | 0.086975 | 121.5775 | -0.032044 | 121.3669 | 121.1243 | 121.1472 | 121.1655 | 121.1563 | -121.3623 | -121.3943 | 121.6187 | 121.376 | 41.4047 | 42.3248
667.7812 | 121.6599 | -37.7884 | 83.6517 | -0.013352 | 0 | 0.065604 | 0.062861 | 0.00049131 | -0.0033474 | -0.0034392 | -0.0028687 | 0.0011898 | -1.3961 | 0.056693 | -0.0045544 | 0.0078443 | 0.00061949 | -0.65918 | 83.3771 | -37.706 | 83.8715 | -37.6419 | -37.9486 | -38.0219 | 0.022888 | 83.3954 | -37.7655 | 83.5419 | -37.8571 | -37.8937 | -37.9852 | 0.082397 | -0.27466 | 0.21973 | 0.14648 | -0.23346 | -0.16022 | -0.31586 | -0.24261 | 0.022888 | -0.25635 | -0.10986 | -0.068665 | -0.19684 | -0.10529 | -0.21973 | -0.12817 | 0.064087 | 121.5775 | -0.091553 | 121.3074 | 121.0831 | 121.1609 | 121.1655 | 121.1838 | -121.3577 | -121.4172 | 121.6599 | 121.3303 | 37.1292 | 37.8113
669.4688 | 121.6919 | -44.1376 | 77.2705 | 0.024795 | 0 | 0.065176 | 0.063288 | -0.00014949 | 0.00028416 | -0.00087583 | 0.0093383 | 0.001617 | -1.3933 | 0.064597 | -0.00092279 | 0.0069897 | -0.0017303 | -0.9613 | 77.037 | -44.0735 | 77.4811 | -44.014 | -44.371 | -44.4122 | 0.004578 | 77.0233 | -44.165 | 77.2018 | -44.22 | -44.2474 | -44.3436 | 0.064087 | -0.23346 | 0.21057 | 0.1236 | -0.27466 | -0.23346 | -0.33874 | -0.29755 | -0.027466 | -0.24719 | -0.068665 | -0.082398 | -0.20599 | -0.10986 | -0.17853 | -0.082398 | 0.059509 | 121.5546 | -0.054932 | 121.3669 | 121.1105 | 121.1884 | 121.1746 | 121.1609 | -121.344 | -121.4355 | 121.6187 | 121.3394 | 43.1763 | 44.1422
671.2344 | 121.6553 | -45.4102 | 76.0437 | 0.040054 | 0 | 0.062613 | 0.065211 | -0.0024995 | -0.0029202 | -0.00087583 | 0.01239 | 0.0024716 | -1.392 | 0.061179 | -0.0062634 | 0.0054945 | 0.00061949 | -0.97504 | 75.8881 | -45.3278 | 76.2085 | -45.2728 | -45.607 | -45.6711 | -0.027466 | 75.8606 | -45.4376 | 75.9201 | -45.4971 | -45.52 | -45.6161 | 0.082397 | -0.15564 | 0.16479 | 0.13733 | -0.26093 | -0.19684 | -0.34332 | -0.27924 | -0.027466 | -0.1831 | -0.1236 | -0.086975 | -0.20599 | -0.10986 | -0.17853 | -0.082398 | 0.054932 | 121.5363 | -0.059509 | 121.3577 | 121.2158 | 121.2982 | 121.2982 | 121.2708 | -121.3715 | -121.4813 | 121.6187 | 121.3303 | 44.4351 | 45.3827
672.9375 | 121.7422 | -42.2379 | 79.1565 | 0.017166 | 0 | 0.062186 | 0.062433 | -0.0012177 | -0.001852 | -0.001303 | -0.0028687 | 0.0011898 | -1.394 | 0.064597 | -0.0028454 | 0.0072035 | 0.0014741 | -0.92468 | 78.9688 | -42.1555 | 79.4312 | -42.0685 | -42.4164 | -42.4667 | 0.009155 | 78.9368 | -42.2287 | 79.1473 | -42.2653 | -42.2745 | -42.3935 | 0.082397 | -0.18768 | 0.27466 | 0.16937 | -0.22888 | -0.17853 | -0.31128 | -0.26093 | 0.009155 | -0.21973 | -0.009155 | -0.027466 | -0.15564 | -0.036621 | -0.16479 | -0.045776 | 0.086976 | 121.5866 | -0.036621 | 121.376 | 121.1243 | 121.1655 | 121.2067 | 121.1746 | -121.312 | -121.3852 | 121.669 | 121.3852 | 41.3132 | 42.247
674.7031 | 121.7239 | -42.7368 | 78.6438 | 0.0019074 | 0 | 0.062613 | 0.064997 | -0.0027131 | -0.0016384 | -0.00066223 | 0.0032349 | 0.0020444 | -1.3955 | 0.070793 | 0.00014521 | 0.0078443 | -0.0025849 | -0.93842 | 78.4698 | -42.7139 | 78.8727 | -42.6315 | -42.9977 | -43.0527 | 0.018311 | 78.4058 | -42.7551 | 78.6209 | -42.8055 | -42.8421 | -42.9062 | 0.022888 | -0.17395 | 0.22888 | 0.10528 | -0.31586 | -0.26093 | -0.33874 | -0.28381 | -0.018311 | -0.23804 | -0.022888 | -0.068665 | -0.16937 | -0.10529 | -0.15106 | -0.086975 | 0.082397 | 121.5866 | -0.050354 | 121.376 | 121.1838 | 121.1609 | 121.2067 | 121.1426 | -121.3577 | -121.3989 | 121.6095 | 121.3577 | 41.7984 | 42.7551
676.3906 | 121.7194 | -42.3294 | 79.0787 | 0.0019074 | 0 | 0.062399 | 0.065211 | -0.00079049 | -0.0022794 | 0.00061957 | 0.00018312 | 0.0020444 | -1.394 | 0.06887 | -0.003059 | 0.0084851 | -0.0036529 | -0.9613 | 78.8589 | -42.2974 | 79.2709 | -42.2241 | -42.5812 | -42.6407 | -0.013733 | 78.7903 | -42.3523 | 79.0283 | -42.4118 | -42.4118 | -42.5217 | 0.032044 | -0.21973 | 0.19226 | 0.10529 | -0.31128 | -0.25177 | -0.34332 | -0.28381 | -0.022888 | -0.28839 | -0.050354 | -0.082397 | -0.19226 | -0.082397 | -0.16937 | -0.059509 | 0.073242 | 121.5683 | -0.059509 | 121.3806 | 121.1563 | 121.1426 | 121.1884 | 121.1197 | -121.376 | -121.431 | 121.6003 | 121.3577 | 41.3681 | 42.3157
678.1562 | 121.6461 | -42.2836 | 79.1977 | 0.040054 | 0 | 0.067526 | 0.063929 | 6.4114e-05 | -0.00078404 | -0.00023503 | 0.015442 | 0.0028988 | -1.3916 | 0.060539 | -0.0045544 | 0.0059217 | -0.0045075 | -0.91095 | 79.0283 | -42.2195 | 79.3579 | -42.1555 | -42.485 | -42.54 | -0.032043 | 79.0009 | -42.2699 | 79.0604 | -42.366 | -42.4026 | -42.4667 | 0.064087 | -0.16937 | 0.16022 | 0.12817 | -0.25635 | -0.20142 | -0.32043 | -0.2655 | 0.013733 | -0.19684 | -0.13733 | -0.082398 | -0.18311 | -0.11902 | -0.19684 | -0.13275 | 0.064086 | 121.5775 | -0.096131 | 121.3303 | 121.2479 | 121.2708 | 121.3119 | 121.2845 | -121.4172 | -121.4676 | 121.6415 | 121.344 | 41.3727 | 42.2516
679.9531 | 121.669 | -41.5466 | 79.9164 | 0.024795 | 0 | 0.063254 | 0.066492 | 0.0028411 | -0.0012112 | 0.0016876 | 0.0032349 | 0.0014034 | -1.3948 | 0.060539 | -0.0024182 | 0.0072035 | -2.1314e-05 | -0.83771 | 79.6967 | -41.5146 | 80.0858 | -41.4322 | -41.7709 | -41.835 | 0.022888 | 79.6738 | -41.5649 | 79.7882 | -41.6428 | -41.6748 | -41.7526 | 0.032044 | -0.21973 | 0.16937 | 0.11444 | -0.28839 | -0.2243 | -0.32044 | -0.25635 | -0.01831 | -0.24262 | -0.12817 | -0.09613 | -0.20599 | -0.12817 | -0.18768 | -0.10986 | 0.082397 | 121.6003 | -0.07782 | 121.3531 | 121.2112 | 121.2387 | 121.2433 | 121.2204 | -121.431 | -121.4813 | 121.6324 | 121.3348 | 40.7089 | 41.5695
681.6562 | 121.7285 | -41.4642 | 79.9576 | 0.0019074 | 0 | 0.064749 | 0.063929 | -0.0016449 | -0.0022794 | -2.1434e-05 | -0.0028687 | 0.00012184 | -1.3944 | 0.067802 | -0.0062634 | 0.0067761 | 0.0016877 | -0.85602 | 79.6967 | -41.391 | 80.2048 | -41.2766 | -41.6428 | -41.716 | 0.09613 | 79.6783 | -41.4459 | 79.8935 | -41.5192 | -41.5375 | -41.6519 | 0.073242 | -0.26093 | 0.24719 | 0.18768 | -0.25177 | -0.17853 | -0.32501 | -0.25177 | 0.01831 | -0.27924 | -0.064087 | -0.054932 | -0.18768 | -0.073243 | -0.20599 | -0.091553 | 0.11444 | 121.5958 | -0.073242 | 121.3394 | 121.0876 | 121.1243 | 121.1609 | 121.1426 | -121.3486 | -121.4035 | 121.669 | 121.3577 | 40.6082 | 41.5604
683.4219 | 121.6415 | -40.3427 | 81.1478 | 0.040054 | 0 | 0.064749 | 0.06457 | 0.0028411 | -0.0016384 | -0.0025848 | 0.015442 | 0.0041806 | -1.3948 | 0.062675 | -0.005409 | 0.0072035 | -0.00087591 | -0.82398 | 80.9738 | -40.3015 | 81.2622 | -40.2649 | -40.567 | -40.6311 | -0.027466 | 80.9097 | -40.3564 | 80.9784 | -40.4572 | -40.4755 | -40.5533 | 0.041198 | -0.17395 | 0.11444 | 0.077819 | -0.28839 | -0.22431 | -0.32959 | -0.2655 | -0.013733 | -0.23804 | -0.16937 | -0.11444 | -0.21057 | -0.13275 | -0.19684 | -0.11902 | 0.036621 | 121.5637 | -0.10071 | 121.3348 | 121.2753 | 121.2662 | 121.3165 | 121.2524 | -121.4493 | -121.5042 | 121.6049 | 121.3211 | 39.5187 | 40.3152
685.1875 | 121.756 | -47.0764 | 74.2676 | -0.0057221 | 0 | 0.063895 | 0.065638 | 0.00070491 | 0.0013522 | 0.0012604 | 0.024597 | 0.0035396 | -1.392 | 0.067588 | -0.00070919 | 0.0091261 | -0.0036529 | -1.2497 | 74.0616 | -47.0627 | 74.588 | -46.8704 | -47.2641 | -47.319 | 0.009155 | 74.057 | -47.1497 | 74.3225 | -47.1222 | -47.1725 | -47.2595 | 0.013733 | -0.20599 | 0.32044 | 0.20599 | -0.24262 | -0.18768 | -0.25635 | -0.20142 | -0.073242 | -0.21057 | 0.054932 | -0.045776 | -0.1831 | -0.09613 | -0.10986 | -0.022888 | 0.19226 | 121.6507 | 0.027466 | 121.4722 | 121.1243 | 121.2067 | 121.138 | 121.1334 | -121.3303 | -121.4172 | 121.6644 | 121.3989 | 45.8267 | 47.0856
686.9531 | 121.6278 | -46.6095 | 74.8672 | 0.0019074 | 0 | 0.066245 | 0.064997 | -0.0027131 | -0.00057044 | 0.0016876 | 0.024597 | 0.003967 | -1.3918 | 0.053489 | -0.005409 | 0.0067761 | 0.0016877 | -1.2314 | 74.6246 | -46.55 | 74.9817 | -46.4722 | -46.8155 | -46.875 | -0.054932 | 74.6567 | -46.6415 | 74.6979 | -46.7194 | -46.7468 | -46.8292 | 0.059509 | -0.24262 | 0.11444 | 0.13733 | -0.2655 | -0.20599 | -0.32501 | -0.2655 | -0.032044 | -0.21057 | -0.16937 | -0.10986 | -0.21973 | -0.13733 | -0.18768 | -0.10529 | 0.07782 | 121.5317 | -0.077819 | 121.3394 | 121.1746 | 121.2982 | 121.2341 | 121.2662 | -121.4172 | -121.5088 | 121.5912 | 121.3074 | 45.3781 | 46.5546
688.6719 | 121.6644 | -46.7056 | 74.762 | 0.040054 | 0 | 0.064536 | 0.065424 | 0.0013459 | -0.0016384 | 0.0012604 | 0.015442 | 0.0020444 | -1.3935 | 0.056053 | -0.0045544 | 0.0069897 | 0.00083309 | -1.1444 | 74.5834 | -46.6644 | 74.913 | -46.55 | -46.8658 | -46.9345 | -0.018311 | 74.5605 | -46.6965 | 74.6613 | -46.7697 | -46.8018 | -46.8933 | 0.041198 | -0.17853 | 0.15106 | 0.15564 | -0.22888 | -0.16022 | -0.27008 | -0.20142 | 0.009155 | -0.20142 | -0.10071 | -0.064087 | -0.18768 | -0.096131 | -0.19684 | -0.10529 | 0.11444 | 121.5775 | -0.073242 | 121.3577 | 121.2479 | 121.257 | 121.2891 | 121.2662 | -121.4264 | -121.4584 | 121.6187 | 121.3669 | 45.5612 | 46.6873
690.4375 | 121.6141 | -45.5795 | 75.8972 | 0.0019074 | 0 | 0.066245 | 0.064997 | 0.0047637 | -0.0027066 | -0.0017304 | 0.00018312 | 0.0037532 | -1.3931 | 0.061607 | -0.0022046 | 0.0067761 | -0.00044851 | -1.236 | 75.705 | -45.5017 | 75.9705 | -45.5338 | -45.8908 | -45.9412 | -0.16022 | 75.6683 | -45.5566 | 75.7462 | -45.7214 | -45.7535 | -45.7855 | 0.07782 | -0.19226 | 0.073242 | 0.045777 | -0.36163 | -0.31128 | -0.43945 | -0.3891 | 0.022888 | -0.22888 | -0.15106 | -0.14191 | -0.20599 | -0.17395 | -0.22888 | -0.19684 | -0.032043 | 121.4722 | -0.16479 | 121.3028 | 121.2067 | 121.225 | 121.2845 | 121.2479 | -121.3989 | -121.4539 | 121.55 | 121.3257 | 44.3436 | 45.4193
692.1875 | 121.6003 | -44.1696 | 77.3254 | 0.0019074 | 0 | 0.061758 | 0.063502 | -0.00036309 | -0.001852 | 0.00083317 | -0.0028687 | 0.0018306 | -1.3935 | 0.064811 | -0.0045544 | 0.0074171 | -2.1314e-05 | -1.0986 | 77.1057 | -44.0552 | 77.4124 | -44.0414 | -44.371 | -44.4489 | -0.059509 | 77.0645 | -44.1422 | 77.1561 | -44.2657 | -44.3069 | -44.3939 | 0.11444 | -0.21973 | 0.086976 | 0.12817 | -0.27924 | -0.20142 | -0.39368 | -0.31586 | 0.027466 | -0.26093 | -0.16937 | -0.09613 | -0.2243 | -0.13733 | -0.25177 | -0.1648 | 0.013733 | 121.4676 | -0.1236 | 121.2982 | 121.1609 | 121.2067 | 121.2753 | 121.2341 | -121.3806 | -121.4676 | 121.582 | 121.3257 | 43.071 | 44.1101
693.8906 | 121.756 | -42.9199 | 78.5019 | -0.013352 | 0 | 0.064536 | 0.062647 | -0.0037811 | -0.0029202 | -0.001303 | -0.0028687 | -0.00094636 | -1.3963 | 0.063743 | -0.0028454 | 0.0082715 | -0.0013031 | -1.0574 | 78.273 | -42.8467 | 78.7308 | -42.7322 | -43.0756 | -43.1351 | 0.059509 | 78.2318 | -42.9108 | 78.4882 | -42.9291 | -42.9565 | -43.0756 | 0.073242 | -0.22888 | 0.22888 | 0.18768 | -0.21515 | -0.15564 | -0.28839 | -0.22888 | 0.009155 | -0.27008 | -0.013733 | -0.009155 | -0.15564 | -0.036621 | -0.16479 | -0.045776 | 0.11444 | 121.5775 | -0.01831 | 121.3989 | 121.1197 | 121.1426 | 121.1929 | 121.1517 | -121.3486 | -121.4127 | 121.6507 | 121.4081 | 41.8625 | 42.9794
695.6562 | 121.6187 | -41.2354 | 80.278 | -0.0057221 | 0 | 0.064963 | 0.065211 | -0.0048493 | -0.0012112 | -0.00066223 | 0.021545 | 0.0026852 | -1.3944 | 0.060325 | -0.0056226 | 0.0057081 | 0.0023285 | -0.97504 | 80.0629 | -41.1438 | 80.3879 | -41.1118 | -41.4322 | -41.4871 | -0.032043 | 80.0629 | -41.2308 | 80.0766 | -41.3452 | -41.3727 | -41.4505 | 0.091553 | -0.21515 | 0.10986 | 0.1236 | -0.25177 | -0.19684 | -0.34332 | -0.28839 | 0.004578 | -0.21515 | -0.20142 | -0.10986 | -0.21515 | -0.13733 | -0.21973 | -0.14191 | 0.032044 | 121.5317 | -0.11444 | 121.3074 | 121.2067 | 121.2936 | 121.2982 | 121.2982 | -121.4218 | -121.5088 | 121.6232 | 121.312 | 40.2603 | 41.2033
697.4219 | 121.6873 | -38.4979 | 82.9834 | 0.024795 | 0 | 0.064963 | 0.063288 | -0.0010041 | -0.0014248 | 0.00061957 | 0.0062865 | 0.00097624 | -1.394 | 0.065452 | -0.0013502 | 0.0089123 | 0.0019013 | -0.8606 | 82.7454 | -38.4018 | 83.1573 | -38.3972 | -38.6948 | -38.7589 | 0.009155 | 82.7087 | -38.4613 | 82.8506 | -38.6032 | -38.6124 | -38.6902 | 0.096131 | -0.23804 | 0.17395 | 0.10071 | -0.26093 | -0.19684 | -0.35706 | -0.29297 | 0.036621 | -0.27466 | -0.13275 | -0.10528 | -0.19226 | -0.11444 | -0.22888 | -0.15106 | 0.004577 | 121.5591 | -0.14191 | 121.312 | 121.1472 | 121.17 | 121.2433 | 121.2067 | -121.3852 | -121.4447 | 121.6553 | 121.3486 | 37.6373 | 38.5071
699.1875 | 121.6827 | -35.5728 | 85.8948 | 0.0095369 | 0 | 0.063895 | 0.063715 | -0.0027131 | -0.0012112 | -0.001944 | 0.0032349 | 0.00033544 | -1.3942 | 0.062034 | -0.00028199 | 0.0093397 | -0.00023491 | -0.70038 | 85.6567 | -35.5042 | 86.055 | -35.495 | -35.7925 | -35.8475 | 0.045776 | 85.6155 | -35.5682 | 85.7529 | -35.6827 | -35.6918 | -35.7559 | 0.068665 | -0.23804 | 0.16022 | 0.07782 | -0.27466 | -0.21973 | -0.34332 | -0.28839 | 0.004578 | -0.27923 | -0.14191 | -0.10986 | -0.18311 | -0.11902 | -0.18768 | -0.1236 | 0.009155 | 121.5591 | -0.11444 | 121.3211 | 121.1609 | 121.1838 | 121.2296 | 121.1884 | -121.3989 | -121.463 | 121.6278 | 121.3257 | 34.8724 | 35.6186
700.9531 | 121.7056 | -33.7692 | 87.7075 | 0.032425 | 0 | 0.066245 | 0.065638 | -0.00036309 | -0.00078404 | -0.00066223 | 0.018494 | 0.0024716 | -1.3922 | 0.061607 | 0.00035881 | 0.011476 | -0.00066231 | -0.55389 | 87.4924 | -33.6777 | 87.9364 | -33.6182 | -33.934 | -33.9798 | 0.15564 | 87.4557 | -33.7509 | 87.616 | -33.8242 | -33.8699 | -33.9432 | 0.091553 | -0.21515 | 0.22888 | 0.15106 | -0.21057 | -0.16479 | -0.30212 | -0.25635 | 0.01831 | -0.25177 | -0.091553 | -0.054932 | -0.17395 | -0.10071 | -0.19226 | -0.11902 | 0.059509 | 121.6141 | -0.073242 | 121.3669 | 121.17 | 121.2067 | 121.2616 | 121.225 | -121.3852 | -121.4584 | 121.7056 | 121.3852 | 33.2153 | 33.9249
702.6562 | 121.6141 | -32.4783 | 89.0396 | 0.0095369 | 0 | 0.064322 | 0.067347 | 0.0030547 | 7.0564e-05 | -0.0015166 | -0.0028687 | 0.0026852 | -1.3948 | 0.060752 | -0.0034864 | 0.0065625 | -0.0013031 | -0.50812 | 88.8245 | -32.3776 | 89.1586 | -32.4326 | -32.7072 | -32.7805 | 0.082397 | 88.7741 | -32.4234 | 88.8199 | -32.6202 | -32.6569 | -32.7209 | 0.10071 | -0.21515 | 0.11902 | 0.045777 | -0.30212 | -0.22888 | -0.40283 | -0.32959 | 0.054932 | -0.2655 | -0.21973 | -0.14191 | -0.24261 | -0.17853 | -0.29755 | -0.23346 | -0.054931 | 121.5363 | -0.19684 | 121.2433 | 121.2021 | 121.1975 | 121.3028 | 121.2524 | -121.4172 | -121.463 | 121.637 | 121.2982 | 31.9702 | 32.5607
704.4219 | 121.7285 | -32.4005 | 89.0533 | 0.0019074 | 0 | 0.06304 | 0.063074 | -0.0029267 | -0.0046292 | -0.0021576 | -0.0028687 | -0.0015872 | -1.3946 | 0.06182 | -0.0037 | 0.0082715 | -0.0042939 | -0.55847 | 88.797 | -32.3318 | 89.2319 | -32.3273 | -32.5974 | -32.6431 | 0.13733 | 88.7741 | -32.3868 | 88.9572 | -32.46 | -32.4738 | -32.5562 | 0.068665 | -0.25635 | 0.17853 | 0.073242 | -0.24261 | -0.19684 | -0.31128 | -0.2655 | 0.013733 | -0.27924 | -0.096131 | -0.059509 | -0.15564 | -0.073242 | -0.16937 | -0.086975 | 0.004577 | 121.5637 | -0.073242 | 121.344 | 121.1288 | 121.1609 | 121.1975 | 121.1746 | -121.3852 | -121.4401 | 121.6324 | 121.3577 | 31.842 | 32.5378
706.125 | 121.6553 | -31.7322 | 89.7995 | 0.055313 | 0 | 0.065176 | 0.06692 | 0.0013459 | 0.0017796 | 0.00083317 | 0.0093383 | 0.0035396 | -1.3931 | 0.060752 | -0.0058362 | 0.0067761 | -0.0036529 | -0.46234 | 89.5889 | -31.6589 | 89.9185 | -31.6818 | -31.929 | -32.0023 | 0.082397 | 89.5294 | -31.691 | 89.5844 | -31.8375 | -31.8787 | -31.9244 | 0.073242 | -0.21057 | 0.11902 | 0.050354 | -0.27008 | -0.19684 | -0.34332 | -0.27008 | 0.041199 | -0.27008 | -0.21515 | -0.10528 | -0.19226 | -0.14648 | -0.23346 | -0.18768 | -0.022888 | 121.5775 | -0.14648 | 121.2753 | 121.2479 | 121.2204 | 121.3211 | 121.2616 | -121.4584 | -121.4905 | 121.6507 | 121.3165 | 31.2698 | 31.8146
707.8906 | 121.6782 | -30.8716 | 90.5914 | 0.032425 | 0 | 0.064963 | 0.065638 | 0.0066863 | -0.0020658 | 0.001474 | 0.01239 | 0.00033544 | -1.3959 | 0.065452 | -6.8386e-05 | 0.0084851 | 0.0044647 | -0.4715 | 90.3763 | -30.7846 | 90.7654 | -30.8029 | -31.0822 | -31.1417 | 0.11444 | 90.3259 | -30.8762 | 90.4495 | -30.9906 | -31.0089 | -31.0684 | 0.086975 | -0.21515 | 0.17395 | 0.068665 | -0.27008 | -0.21057 | -0.35706 | -0.29755 | -0.004578 | -0.2655 | -0.14191 | -0.11902 | -0.19684 | -0.13733 | -0.19226 | -0.13275 | -0.01831 | 121.55 | -0.11444 | 121.3257 | 121.1609 | 121.2021 | 121.2479 | 121.1975 | -121.376 | -121.4676 | 121.637 | 121.3211 | 30.4001 | 30.986
709.6562 | 121.637 | -28.9444 | 92.5827 | 0.0019074 | 0 | 0.064963 | 0.063288 | 0.0017731 | -0.001852 | 0.00083317 | 0.00018312 | 0.0031124 | -1.3959 | 0.066734 | -0.0049818 | 0.0063489 | -0.0015167 | -0.28839 | 92.3492 | -28.8208 | 92.7155 | -28.8528 | -29.1092 | -29.1824 | 0.16022 | 92.3172 | -28.8666 | 92.363 | -29.0634 | -29.0863 | -29.1504 | 0.1236 | -0.23346 | 0.13275 | 0.091553 | -0.23804 | -0.1648 | -0.36163 | -0.28839 | 0.07782 | -0.2655 | -0.21973 | -0.11902 | -0.20599 | -0.14191 | -0.28381 | -0.21973 | -0.032043 | 121.5363 | -0.19684 | 121.2296 | 121.17 | 121.1838 | 121.2936 | 121.2616 | -121.4035 | -121.4493 | 121.6599 | 121.3074 | 28.656 | 29.1046
711.3594 | 121.6507 | -28.0014 | 93.4982 | 0.024795 | 0 | 0.063681 | 0.066492 | -0.0022857 | -0.0014248 | 0.0027558 | 0.0062865 | 0.002258 | -1.3952 | 0.059684 | -0.0058362 | 0.0069897 | -0.00044851 | -0.2243 | 93.2968 | -27.9236 | 93.631 | -27.9373 | -28.1982 | -28.2761 | 0.21057 | 93.251 | -27.9831 | 93.3289 | -28.1204 | -28.1616 | -28.1891 | 0.07782 | -0.20142 | 0.13275 | 0.064087 | -0.27466 | -0.19684 | -0.35248 | -0.27466 | 0.018311 | -0.24719 | -0.16937 | -0.11902 | -0.18768 | -0.16022 | -0.20599 | -0.17853 | -0.013733 | 121.5546 | -0.13733 | 121.3119 | 121.2204 | 121.2341 | 121.2982 | 121.2524 | -121.4218 | -121.4813 | 121.6324 | 121.3303 | 27.7771 | 28.212
713.125 | 121.6232 | -27.1408 | 94.3726 | 0.0019074 | 0 | 0.063895 | 0.06457 | 0.00091851 | -0.00099764 | 0.00061957 | -0.0028687 | 0.0031124 | -1.3955 | 0.063529 | -0.0039136 | 0.0080579 | -0.00087591 | -0.24719 | 94.1803 | -27.0447 | 94.487 | -27.1133 | -27.3697 | -27.4292 | 0.15564 | 94.1208 | -27.063 | 94.1391 | -27.2873 | -27.3422 | -27.3697 | 0.09613 | -0.19226 | 0.11444 | 0.027466 | -0.28839 | -0.22888 | -0.38452 | -0.32501 | 0.07782 | -0.25177 | -0.23346 | -0.14648 | -0.22888 | -0.20142 | -0.3067 | -0.27924 | -0.068664 | 121.5317 | -0.2243 | 121.2021 | 121.225 | 121.1838 | 121.3211 | 121.2616 | -121.4172 | -121.4355 | 121.6278 | 121.2799 | 26.8936 | 27.2964
714.9062 | 121.6827 | -25.8591 | 95.6131 | 0.0019074 | 0 | 0.063895 | 0.063715 | 0.0043365 | -0.0044156 | 0.0012604 | 0.0032349 | 0.0024716 | -1.394 | 0.060966 | -0.0013502 | 0.0089123 | -0.0017303 | -0.21515 | 95.4163 | -25.8224 | 95.7001 | -25.9048 | -26.152 | -26.1887 | 0.17853 | 95.3476 | -25.8591 | 95.4391 | -25.9964 | -26.0422 | -26.0422 | 0.036621 | -0.19684 | 0.086975 | -0.045776 | -0.32959 | -0.29297 | -0.36621 | -0.32959 | 0 | -0.2655 | -0.17395 | -0.13733 | -0.18311 | -0.18311 | -0.18311 | -0.18311 | -0.082397 | 121.5225 | -0.13733 | 121.2982 | 121.2387 | 121.2067 | 121.2753 | 121.2067 | -121.4355 | -121.4722 | 121.5591 | 121.2982 | 25.6439 | 26.0376
716.5938 | 121.7422 | -24.646 | 96.7987 | 0.0095369 | 0 | 0.063681 | 0.061793 | 6.4114e-05 | -0.00099764 | -2.1434e-05 | 0.00018312 | 0.0020444 | -1.3931 | 0.060752 | -0.0028454 | 0.0059217 | 0.0010467 | -0.082397 | 96.5744 | -24.5636 | 97.0322 | -24.5132 | -24.7696 | -24.8383 | 0.36163 | 96.5332 | -24.6323 | 96.7072 | -24.6963 | -24.7147 | -24.7833 | 0.082397 | -0.2243 | 0.23346 | 0.13275 | -0.19226 | -0.1236 | -0.27466 | -0.20599 | 0.013733 | -0.2655 | -0.091553 | -0.050354 | -0.13733 | -0.068665 | -0.15106 | -0.082398 | 0.050354 | 121.5958 | -0.064087 | 121.3394 | 121.138 | 121.1655 | 121.2204 | 121.1792 | -121.3623 | -121.431 | 121.6782 | 121.3531 | 24.5636 | 25.0076
718.3438 | 121.669 | -25.1633 | 96.3364 | 0.0019074 | 0 | 0.065817 | 0.064142 | -0.0048493 | -0.0014248 | 0.0012604 | 0.0032349 | 0.0046078 | -1.392 | 0.065452 | -0.003059 | 0.0078443 | -0.0038665 | -0.086975 | 96.1487 | -25.1038 | 96.4737 | -25.1404 | -25.3555 | -25.4242 | 0.27924 | 96.0983 | -25.1266 | 96.1349 | -25.2869 | -25.3418 | -25.3555 | 0.059509 | -0.18768 | 0.13733 | 0.022888 | -0.26093 | -0.19226 | -0.32043 | -0.25177 | 0.036621 | -0.23804 | -0.20142 | -0.1236 | -0.19226 | -0.17853 | -0.22888 | -0.21515 | -0.036621 | 121.5775 | -0.16022 | 121.2616 | 121.2524 | 121.225 | 121.312 | 121.2616 | -121.4401 | -121.463 | 121.637 | 121.2982 | 25.0763 | 25.4425
720.0938 | 121.6049 | -24.614 | 96.936 | 0.0019074 | 0 | 0.063467 | 0.06692 | 0.0013459 | -0.0022794 | -0.00044863 | 0.015442 | 0.0024716 | -1.3918 | 0.07122 | -0.006477 | 0.0074171 | 0.0019013 | -0.07782 | 96.7438 | -24.5453 | 96.9864 | -24.5956 | -24.8016 | -24.8749 | 0.2243 | 96.7026 | -24.5865 | 96.6431 | -24.7696 | -24.7879 | -24.8108 | 0.068665 | -0.19226 | 0.050354 | 0.018311 | -0.26093 | -0.18768 | -0.32959 | -0.25635 | 0.027466 | -0.23346 | -0.29297 | -0.15564 | -0.19684 | -0.17395 | -0.2243 | -0.20142 | -0.050354 | 121.5317 | -0.1831 | 121.2296 | 121.2891 | 121.2891 | 121.3577 | 121.3165 | -121.4813 | -121.5225 | 121.6003 | 121.257 | 24.5361 | 24.8383
721.7969 | 121.701 | -24.1013 | 97.3892 | 0.017166 | 0 | 0.065176 | 0.063715 | -0.0010041 | -0.0020658 | -0.00023503 | 0.0062865 | -0.00030556 | -1.3935 | 0.065238 | -0.0013502 | 0.0078443 | 0.0029693 | -0.10071 | 97.1695 | -24.028 | 97.5266 | -24.0601 | -24.2798 | -24.3393 | 0.2655 | 97.1054 | -24.0601 | 97.2015 | -24.2111 | -24.2386 | -24.2889 | 0.073242 | -0.21973 | 0.13733 | 0.041198 | -0.23804 | -0.17853 | -0.31128 | -0.25177 | 0.041198 | -0.28381 | -0.18768 | -0.10986 | -0.18768 | -0.13733 | -0.22888 | -0.17853 | -0.032044 | 121.5546 | -0.15106 | 121.2616 | 121.1975 | 121.1655 | 121.2708 | 121.2067 | -121.4172 | -121.4493 | 121.6278 | 121.3028 | 24.0005 | 24.3668
723.5625 | 121.6827 | -29.1504 | 92.3767 | 0.040054 | 0 | 0.063467 | 0.065211 | 0.0043365 | -0.0022794 | -0.00066223 | 0.0093383 | 0.0020444 | -1.3929 | 0.054771 | -0.003059 | 0.0074171 | -0.0019439 | -0.36163 | 92.1524 | -29.0909 | 92.4774 | -29.0909 | -29.3701 | -29.4296 | 0.21515 | 92.1112 | -29.1275 | 92.1753 | -29.2831 | -29.306 | -29.3472 | 0.05951 | -0.2243 | 0.10071 | 0.05951 | -0.27923 | -0.21973 | -0.33874 | -0.27924 | 0.022889 | -0.2655 | -0.20142 | -0.13275 | -0.19684 | -0.15564 | -0.21973 | -0.17853 | 0 | 121.5683 | -0.15564 | 121.3028 | 121.2433 | 121.2387 | 121.3028 | 121.2616 | -121.4676 | -121.5042 | 121.6278 | 121.3257 | 28.7888 | 29.3655
725.25 | 121.7194 | -27.5665 | 93.8828 | -0.0057221 | 0 | 0.063895 | 0.065211 | -0.0020721 | -0.0016384 | -0.0017304 | -0.0028687 | 0.0020444 | -1.3946 | 0.05883 | -0.00028199 | 0.010408 | -0.00044851 | -0.36163 | 93.6905 | -27.4979 | 94.0384 | -27.5482 | -27.8137 | -27.8641 | 0.19226 | 93.6127 | -27.5391 | 93.7683 | -27.6672 | -27.7084 | -27.7267 | 0.068664 | -0.19226 | 0.15564 | 0.01831 | -0.29755 | -0.24719 | -0.36621 | -0.31586 | 0.027466 | -0.27008 | -0.11444 | -0.10071 | -0.16022 | -0.14191 | -0.18768 | -0.16937 | -0.050354 | 121.5363 | -0.12817 | 121.3074 | 121.1884 | 121.1517 | 121.257 | 121.1792 | -121.3806 | -121.4218 | 121.6049 | 121.3348 | 27.2049 | 27.7588
727 | 121.6278 | -28.9124 | 92.6147 | -0.013352 | 0 | 0.064108 | 0.066065 | -0.0020721 | -0.00057044 | -0.0010894 | 0.00018312 | 0.0041806 | -1.3935 | 0.067161 | -0.003059 | 0.0069897 | -0.0042939 | -0.4715 | 92.4408 | -28.8208 | 92.6605 | -28.9536 | -29.2007 | -29.2419 | 0.064087 | 92.3492 | -28.8757 | 92.363 | -29.1046 | -29.1275 | -29.1367 | 0.091553 | -0.17395 | 0.045776 | -0.041198 | -0.32959 | -0.28839 | -0.42114 | -0.37994 | 0.036622 | -0.2655 | -0.25177 | -0.19226 | -0.2243 | -0.21515 | -0.26093 | -0.25177 | -0.13275 | 121.4813 | -0.22888 | 121.2387 | 121.2616 | 121.225 | 121.3531 | 121.2616 | -121.4355 | -121.4905 | 121.5729 | 121.2753 | 28.4409 | 28.9764
728.7656 | 121.6873 | -24.0692 | 97.4304 | -0.0057221 | 0 | 0.062613 | 0.061579 | -0.0059173 | -0.0048428 | -0.001303 | 0.00018312 | 0.00076264 | -1.394 | 0.068229 | -0.0039136 | 0.0059217 | 0.00083309 | -0.10986 | 97.1512 | -23.9777 | 97.5815 | -24.0005 | -24.2157 | -24.2981 | 0.27008 | 97.1283 | -24.0326 | 97.2427 | -24.1516 | -24.1608 | -24.2249 | 0.091553 | -0.27924 | 0.15106 | 0.068665 | -0.22888 | -0.14648 | -0.32043 | -0.23804 | 0.036621 | -0.30212 | -0.18768 | -0.082397 | -0.15564 | -0.091553 | -0.19226 | -0.12817 | -0.022888 | 121.5591 | -0.11902 | 121.2753 | 121.1288 | 121.1609 | 121.2204 | 121.1975 | -121.4081 | -121.463 | 121.6507 | 121.312 | 23.9594 | 24.3393
730.4688 | 121.7377 | -18.837 | 102.6627 | 0.0019074 | 0 | 0.065817 | 0.063074 | -0.0035675 | -0.0039884 | -0.00087583 | -0.0028687 | 0.00097624 | -1.394 | 0.065025 | -6.8386e-05 | 0.0097669 | 0.0021149 | 0.31128 | 102.4429 | -18.7088 | 102.8503 | -18.7408 | -18.9377 | -18.9972 | 0.48065 | 102.3743 | -18.7592 | 102.5436 | -18.8553 | -18.9102 | -18.8965 | 0.12817 | -0.21973 | 0.18768 | 0.09613 | -0.16022 | -0.10071 | -0.28839 | -0.22888 | 0.07782 | -0.28839 | -0.11902 | -0.018311 | -0.059509 | -0.073242 | -0.13733 | -0.15106 | -0.032044 | 121.5591 | -0.096131 | 121.3028 | 121.1517 | 121.1334 | 121.2799 | 121.2112 | -121.3715 | -121.4218 | 121.6873 | 121.3806 | 19.1483 | 19.3176
732.25 | 121.6827 | -17.0975 | 104.4205 | 0.0019074 | 0 | 0.064322 | 0.061793 | -0.0050629 | -0.00057044 | -0.003012 | -0.0028687 | 0.0018306 | -1.3959 | 0.057548 | -0.0058362 | 0.0074171 | -0.0017303 | 0.43488 | 104.1824 | -16.983 | 104.599 | -16.983 | -17.157 | -17.244 | 0.52185 | 104.1321 | -17.0288 | 104.2282 | -17.0929 | -17.1341 | -17.1707 | 0.11444 | -0.23804 | 0.17853 | 0.11444 | -0.14648 | -0.059509 | -0.26093 | -0.17395 | 0.068664 | -0.28839 | -0.19226 | 0.004577 | -0.073242 | -0.036621 | -0.14191 | -0.10529 | 0 | 121.582 | -0.064087 | 121.257 | 121.1655 | 121.1609 | 121.2799 | 121.2296 | -121.4035 | -121.4493 | 121.6965 | 121.3257 | 17.5323 | 17.6193
733.9531 | 121.6553 | -17.9626 | 103.5919 | 0.0095369 | 0 | 0.06539 | 0.066492 | 0.0019867 | 0.0011386 | 0.00061957 | 0.0062865 | 0.0018306 | -1.3959 | 0.059684 | -0.0039136 | 0.0076307 | -0.0019439 | 0.3891 | 103.3676 | -17.8619 | 103.6789 | -17.9214 | -18.0817 | -18.1686 | 0.46234 | 103.3081 | -17.9123 | 103.3218 | -18.0634 | -18.1091 | -18.1046 | 0.10071 | -0.2243 | 0.086975 | 0.041198 | -0.20599 | -0.11902 | -0.3067 | -0.21973 | 0.050354 | -0.28381 | -0.27008 | -0.10071 | -0.14191 | -0.14649 | -0.19226 | -0.19684 | -0.05951 | 121.5408 | -0.15106 | 121.2341 | 121.2296 | 121.2204 | 121.3303 | 121.2708 | -121.4539 | -121.5042 | 121.6415 | 121.2845 | 18.3517 | 18.425
735.7188 | 121.7102 | -24.7787 | 96.698 | 0.0019074 | 0 | 0.063681 | 0.064783 | -0.0010041 | 0.00071136 | -0.0027984 | 0.0062865 | -0.00073276 | -1.3976 | 0.06652 | -0.001991 | 0.0084851 | 0.0019013 | -0.21515 | 96.4737 | -24.7192 | 96.8079 | -24.7742 | -24.9939 | -25.058 | 0.25177 | 96.405 | -24.7604 | 96.5012 | -24.9115 | -24.9481 | -24.9802 | 0.05951 | -0.2243 | 0.10986 | 0.004578 | -0.27923 | -0.21515 | -0.33874 | -0.27466 | 0.018311 | -0.29297 | -0.19684 | -0.13275 | -0.20142 | -0.16937 | -0.21973 | -0.18768 | -0.054932 | 121.5271 | -0.15106 | 121.2616 | 121.1929 | 121.1655 | 121.2524 | 121.1838 | -121.4172 | -121.4584 | 121.5866 | 121.2799 | 24.5636 | 25.0305
737.4062 | 121.6507 | -23.2727 | 98.259 | 0.047683 | 0 | 0.063895 | 0.063929 | 0.0024139 | -0.0014248 | 0.00019217 | 0.01239 | 0.0031124 | -1.3935 | 0.062675 | -0.0043408 | 0.0057081 | -0.0042939 | 0.009155 | 98.0438 | -23.2315 | 98.3185 | -23.2727 | -23.4604 | -23.5428 | 0.30212 | 98.0118 | -23.2635 | 97.9843 | -23.4192 | -23.4467 | -23.4604 | 0.041199 | -0.21515 | 0.059509 | 0 | -0.27008 | -0.18768 | -0.31128 | -0.22888 | 0.009155 | -0.24719 | -0.27466 | -0.14648 | -0.18768 | -0.17395 | -0.19684 | -0.18311 | -0.041199 | 121.55 | -0.15564 | 121.2479 | 121.2753 | 121.2753 | 121.3165 | 121.2845 | -121.4905 | -121.5225 | 121.5912 | 121.257 | 23.2819 | 23.5748
739.1719 | 121.701 | -18.7042 | 102.7954 | 0.040054 | 0 | 0.065604 | 0.066492 | 0.0013459 | -0.00035684 | 0.0016876 | 0.0093383 | 0.0028988 | -1.3925 | 0.069084 | -0.0026318 | 0.0089123 | -0.00023491 | 0.26093 | 102.5848 | -18.631 | 102.951 | -18.6081 | -18.8141 | -18.8782 | 0.45319 | 102.5116 | -18.6539 | 102.6031 | -18.782 | -18.8187 | -18.8278 | 0.073243 | -0.21057 | 0.15564 | 0.096131 | -0.17395 | -0.10986 | -0.24719 | -0.18311 | 0.050354 | -0.28381 | -0.19226 | -0.077819 | -0.1236 | -0.11444 | -0.17395 | -0.16479 | 0.022888 | 121.582 | -0.12817 | 121.257 | 121.2158 | 121.1655 | 121.2891 | 121.2158 | -121.4264 | -121.4493 | 121.6553 | 121.3074 | 18.9651 | 19.1574
740.9375 | 121.7331 | -17.6147 | 103.8712 | -0.0057221 | 0 | 0.064322 | 0.066706 | 0.0011321 | -0.001852 | -0.001944 | -0.0028687 | 0.00097624 | -1.3935 | 0.066093 | -0.0045544 | 0.0076307 | -0.00023491 | 0.32044 | 103.624 | -17.5323 | 103.9948 | -17.5919 | -17.7475 | -17.8116 | 0.44403 | 103.5782 | -17.569 | 103.6835 | -17.6514 | -17.6743 | -17.7155 | 0.082397 | -0.24719 | 0.1236 | 0.022888 | -0.19684 | -0.13275 | -0.27923 | -0.21515 | 0.045776 | -0.29297 | -0.18768 | -0.036621 | -0.10071 | -0.059509 | -0.14648 | -0.10528 | -0.059509 | 121.5271 | -0.082397 | 121.2524 | 121.1563 | 121.1472 | 121.2387 | 121.1929 | -121.4035 | -121.4401 | 121.6095 | 121.2982 | 17.9352 | 18.0588
742.6406 | 121.7514 | -16.2506 | 105.2399 | -0.0057221 | 0 | 0.06539 | 0.064356 | 0.0041229 | -0.0014248 | -0.0017304 | 0.00018312 | 0.0014034 | -1.3957 | 0.063102 | -0.00049559 | 0.010621 | 0.00040589 | 0.48981 | 105.0293 | -16.1636 | 105.4184 | -16.1682 | -16.3513 | -16.42 | 0.55389 | 104.9561 | -16.2003 | 105.1071 | -16.2506 | -16.3101 | -16.3101 | 0.086975 | -0.21057 | 0.17853 | 0.082397 | -0.16937 | -0.10071 | -0.25635 | -0.18768 | 0.050354 | -0.28381 | -0.13275 | 0 | -0.05951 | -0.05951 | -0.10986 | -0.10986 | -0.004578 | 121.582 | -0.050354 | 121.3074 | 121.1929 | 121.1563 | 121.2799 | 121.2067 | -121.4035 | -121.4401 | 121.669 | 121.3577 | 16.7404 | 16.8045
744.4062 | 121.6736 | -16.5894 | 104.9469 | -0.0057221 | 0 | 0.063681 | 0.062647 | -0.0016449 | -0.0022794 | -0.0040802 | -0.0028687 | 0.0020444 | -1.3944 | 0.060752 | -0.0039136 | 0.0065625 | 0.0029693 | 0.48523 | 104.6814 | -16.4795 | 105.0842 | -16.4932 | -16.6443 | -16.7267 | 0.52643 | 104.6768 | -16.5207 | 104.6951 | -16.6397 | -16.6718 | -16.6763 | 0.10986 | -0.2655 | 0.13733 | 0.09613 | -0.13733 | -0.054932 | -0.24719 | -0.16479 | 0.068664 | -0.27008 | -0.25177 | -0.050354 | -0.086976 | -0.082398 | -0.15564 | -0.15106 | -0.013733 | 121.5637 | -0.11902 | 121.2158 | 121.1609 | 121.1975 | 121.2708 | 121.2662 | -121.4264 | -121.4676 | 121.6736 | 121.2845 | 17.0746 | 17.1158
746.1562 | 121.6736 | -14.7354 | 106.7825 | 0.0019074 | 0 | 0.064108 | 0.063715 | -0.00079049 | -0.0050564 | 0.0027558 | 0.00018312 | -0.00094636 | -1.3933 | 0.062888 | -0.006477 | 0.0057081 | 0.00019229 | 0.8194 | 106.5674 | -14.621 | 106.9473 | -14.6301 | -14.7629 | -14.8636 | 0.82855 | 106.5079 | -14.6576 | 106.5491 | -14.7491 | -14.8041 | -14.8132 | 0.11444 | -0.21515 | 0.16479 | 0.10529 | -0.12817 | -0.027465 | -0.24261 | -0.14191 | 0.07782 | -0.27466 | -0.23346 | -0.013733 | -0.077819 | -0.068664 | -0.15564 | -0.14648 | -0.009155 | 121.5683 | -0.091553 | 121.2067 | 121.1884 | 121.1655 | 121.3028 | 121.2433 | -121.4035 | -121.4401 | 121.6827 | 121.2845 | 15.5548 | 15.564
747.8594 | 121.6461 | -13.3759 | 108.2291 | 0.040054 | 0 | 0.066031 | 0.062433 | -0.0012177 | -0.0033474 | 0.0012604 | 0.021545 | 0.0037532 | -1.3944 | 0.068229 | -0.004768 | 0.0059217 | -0.0017303 | 0.6958 | 108.0185 | -13.2889 | 108.2703 | -13.3209 | -13.4171 | -13.504 | 0.59509 | 107.9453 | -13.3301 | 107.9224 | -13.4125 | -13.4537 | -13.4354 | 0.086975 | -0.21057 | 0.041199 | 0.054931 | -0.12817 | -0.041199 | -0.21515 | -0.12817 | 0.045776 | -0.28381 | -0.3067 | -0.036622 | -0.05951 | -0.07782 | -0.10529 | -0.1236 | -0.032044 | 121.5591 | -0.082398 | 121.2524 | 121.3074 | 121.2753 | 121.3943 | 121.3211 | -121.5179 | -121.5591 | 121.6461 | 121.2982 | 14.0717 | 13.9709
749.625 | 121.7331 | -12.204 | 109.2865 | 0.0019074 | 0 | 0.06539 | 0.063502 | 0.0017731 | -0.00078404 | 0.00019217 | 0.018494 | 0.00097624 | -1.3933 | 0.05883 | 0.00035881 | 0.0080579 | 0.0012603 | 0.76446 | 109.0805 | -12.1078 | 109.5062 | -12.0438 | -12.2086 | -12.291 | 0.73242 | 109.0393 | -12.1902 | 109.108 | -12.1857 | -12.2269 | -12.2131 | 0.09613 | -0.20599 | 0.21973 | 0.16022 | -0.086976 | -0.004578 | -0.18311 | -0.10071 | 0.013732 | -0.24719 | -0.17853 | 0.01831 | -0.009156 | -0.022889 | -0.022888 | -0.036621 | 0.064087 | 121.6141 | 0.004578 | 121.2982 | 121.1884 | 121.2296 | 121.2845 | 121.2433 | -121.3943 | -121.4767 | 121.7102 | 121.312 | 12.9684 | 12.9364
751.3906 | 121.6461 | -10.1578 | 111.4426 | 0.040054 | 0 | 0.064963 | 0.065851 | 0.00070491 | -0.00099764 | -0.00087583 | 0.018494 | 0.0028988 | -1.3925 | 0.059257 | -0.0041272 | 0.0059217 | -0.0053619 | 0.95215 | 111.2228 | -10.0616 | 111.5021 | -10.025 | -10.1349 | -10.199 | 0.75073 | 111.1633 | -10.0891 | 111.145 | -10.1028 | -10.1624 | -10.1303 | 0.09613 | -0.21973 | 0.059509 | 0.13275 | -0.041199 | 0.022888 | -0.13733 | -0.073242 | 0.068665 | -0.27924 | -0.29755 | 0.054932 | 0.027466 | -0.004578 | -0.041199 | -0.073243 | 0.036622 | 121.5637 | -0.013733 | 121.2341 | 121.2845 | 121.2524 | 121.3806 | 121.3211 | -121.5042 | -121.5317 | 121.6599 | 121.3028 | 11.1099 | 10.9085
753.1562 | 121.7056 | -10.3821 | 111.1267 | 0.047683 | 0 | 0.065817 | 0.064997 | 0.0073273 | 7.0564e-05 | -0.00066223 | 0.01239 | -9.1956e-05 | -1.3925 | 0.06182 | -0.00070919 | 0.0097669 | 0.0021149 | 0.92926 | 110.9299 | -10.2814 | 111.3235 | -10.1852 | -10.3409 | -10.3958 | 0.79193 | 110.8841 | -10.3409 | 110.9619 | -10.3134 | -10.3683 | -10.3546 | 0.10071 | -0.19684 | 0.19684 | 0.19684 | -0.013733 | 0.041199 | -0.11444 | -0.059509 | 0.041199 | -0.24262 | -0.1648 | 0.068664 | 0.027466 | 0.013733 | -0.013733 | -0.027466 | 0.09613 | 121.6049 | 0.027465 | 121.3028 | 121.2112 | 121.225 | 121.312 | 121.2662 | -121.4081 | -121.4676 | 121.7056 | 121.344 | 11.3113 | 11.174
754.8906 | 121.5912 | -10.0937 | 111.4929 | -0.0057221 | 0 | 0.06539 | 0.065638 | 0.0011321 | -0.0031338 | -0.00087583 | -0.0028687 | 0.0028988 | -1.3948 | 0.064384 | -0.0032728 | 0.0078443 | -0.0023713 | 0.92926 | 111.3098 | -9.9747 | 111.4883 | -10.08 | -10.1944 | -10.231 | 0.63629 | 111.2091 | -10.0388 | 111.1313 | -10.1349 | -10.1807 | -10.1257 | 0.11902 | -0.18311 | -0.004578 | 0.013733 | -0.13733 | -0.10071 | -0.25635 | -0.21973 | 0.054932 | -0.28381 | -0.36163 | -0.041199 | -0.032043 | -0.086975 | -0.086975 | -0.14191 | -0.10529 | 121.463 | -0.096131 | 121.17 | 121.2845 | 121.2479 | 121.4035 | 121.3028 | -121.4676 | -121.5317 | 121.582 | 121.225 | 11.0229 | 10.73
756.6562 | 121.7377 | -9.3384 | 112.1933 | -0.0057221 | 0 | 0.06539 | 0.063074 | 0.0017731 | -0.0031338 | -0.0038666 | -0.0059205 | -0.0013736 | -1.3952 | 0.066947 | -0.0037 | 0.0099805 | 0.0010467 | 1.0025 | 111.9415 | -9.2514 | 112.3215 | -9.169 | -9.3018 | -9.3658 | 0.86975 | 111.8958 | -9.3109 | 111.9965 | -9.2285 | -9.2834 | -9.288 | 0.086975 | -0.25177 | 0.12817 | 0.16937 | -0.027466 | 0.036621 | -0.11444 | -0.050354 | 0.027466 | -0.29755 | -0.19684 | 0.10986 | 0.050354 | 0.054932 | 0.022888 | 0.027466 | 0.082398 | 121.5729 | 0.082397 | 121.3074 | 121.1929 | 121.2067 | 121.2799 | 121.2341 | -121.4447 | -121.5042 | 121.6599 | 121.3348 | 10.3409 | 10.2081
758.4219 | 121.6599 | -8.4778 | 113.0905 | 0.024795 | 0 | 0.066885 | 0.062861 | 0.0039093 | -0.0022794 | 0.001474 | 0.01239 | 0.0031124 | -1.3944 | 0.070365 | -0.0039136 | 0.0069897 | -0.0049347 | 1.1261 | 112.9349 | -8.4 | 113.1775 | -8.3267 | -8.432 | -8.5144 | 0.84686 | 112.825 | -8.4274 | 112.825 | -8.4183 | -8.4686 | -8.4274 | 0.07782 | -0.15564 | 0.086975 | 0.15106 | -0.036621 | 0.045776 | -0.11444 | -0.032044 | 0.050354 | -0.2655 | -0.2655 | 0.059509 | 0.050354 | 0.009155 | 0 | -0.041199 | 0.073242 | 121.5775 | 0.009155 | 121.2524 | 121.3348 | 121.2524 | 121.4127 | 121.3028 | -121.4905 | -121.5179 | 121.6553 | 121.3028 | 9.6039 | 9.3246
760.125 | 121.7239 | -8.107 | 113.4064 | 0.0019074 | 0 | 0.062827 | 0.065638 | -0.00036309 | -0.00014304 | 0.00019217 | -0.0028687 | 0.0026852 | -1.3957 | 0.067161 | -0.00028199 | 0.010621 | 0.0016877 | 1.1307 | 113.1821 | -8.0154 | 113.5529 | -7.9239 | -8.0841 | -8.139 | 0.89264 | 113.1226 | -8.0566 | 113.2324 | -8.0109 | -8.0521 | -8.0292 | 0.091553 | -0.2243 | 0.14648 | 0.18311 | -0.032043 | 0.022889 | -0.1236 | -0.068664 | 0.050354 | -0.28381 | -0.17395 | 0.096131 | 0.07782 | 0.054932 | 0.027466 | 0.004578 | 0.091553 | 121.5683 | 0.045777 | 121.2891 | 121.1975 | 121.1792 | 121.2891 | 121.2296 | -121.4218 | -121.463 | 121.6599 | 121.3394 | 9.2377 | 8.9996
761.8906 | 121.6827 | -7.8964 | 113.6993 | 0.0019074 | 0 | 0.064108 | 0.064356 | -0.00036309 | -0.002493 | -0.00087583 | 0.00018312 | 0.0018306 | -1.3982 | 0.068015 | -0.0045544 | 0.0065625 | 0.0014741 | 1.1627 | 113.4247 | -7.782 | 113.7955 | -7.6813 | -7.7957 | -7.869 | 0.90179 | 113.3789 | -7.8369 | 113.4155 | -7.8049 | -7.8323 | -7.8323 | 0.11444 | -0.27466 | 0.09613 | 0.21515 | 0.027465 | 0.10071 | -0.086976 | -0.013733 | 0.059509 | -0.32044 | -0.28381 | 0.091552 | 0.064087 | 0.064087 | 0.004578 | 0.004578 | 0.10071 | 121.5775 | 0.032043 | 121.2524 | 121.2067 | 121.2158 | 121.3211 | 121.2753 | -121.4813 | -121.5363 | 121.6919 | 121.3119 | 9.0591 | 8.7982
763.6406 | 121.6049 | -7.6492 | 113.9465 | 0.0019074 | 0 | 0.064322 | 0.064783 | -0.0031403 | -0.00099764 | 0.00083317 | -0.0089723 | 0.003326 | -1.3929 | 0.065666 | -0.0011364 | 0.0089123 | -0.0023713 | 1.1719 | 113.7588 | -7.5348 | 113.9923 | -7.5027 | -7.6492 | -7.6996 | 0.81482 | 113.6948 | -7.5668 | 113.6169 | -7.6263 | -7.6904 | -7.608 | 0.11444 | -0.18768 | 0.045777 | 0.14648 | -0.050354 | 0 | -0.16479 | -0.11444 | 0.082398 | -0.25177 | -0.32959 | 0.022888 | 0.041199 | -0.041199 | -0.041199 | -0.1236 | 0.032043 | 121.5271 | -0.05951 | 121.1838 | 121.2936 | 121.2616 | 121.4081 | 121.344 | -121.4813 | -121.5134 | 121.6415 | 121.2662 | 8.8211 | 8.4641
765.3906 | 121.6095 | -7.2372 | 114.386 | 0.0019074 | 0 | 0.064108 | 0.064783 | 0.0028411 | -0.0033474 | 0.00083317 | 0.00018312 | 0.0011898 | -1.3925 | 0.057762 | -0.0039136 | 0.0078443 | 0.00061949 | 1.2222 | 114.1525 | -7.1228 | 114.3951 | -7.0999 | -7.2189 | -7.283 | 0.8606 | 114.0839 | -7.1686 | 114.0289 | -7.2006 | -7.2601 | -7.1915 | 0.11444 | -0.23346 | 0.009156 | 0.13733 | -0.045776 | 0.018311 | -0.16022 | -0.09613 | 0.068665 | -0.30212 | -0.35706 | 0.036621 | 0.045777 | -0.022888 | -0.022888 | -0.091553 | 0.022888 | 121.5179 | -0.032044 | 121.1975 | 121.2753 | 121.2524 | 121.3898 | 121.3211 | -121.5088 | -121.5546 | 121.6324 | 121.2662 | 8.4595 | 8.0978
767.0938 | 121.7056 | -7.0129 | 114.5416 | 0.047683 | 0 | 0.067313 | 0.064142 | -0.00014949 | -0.0012112 | 0.0025422 | 0.015442 | 0.0026852 | -1.3929 | 0.063316 | -6.8386e-05 | 0.0078443 | 0.0019013 | 1.2085 | 114.3494 | -6.9397 | 114.6698 | -6.7749 | -6.9168 | -6.9763 | 0.95673 | 114.2487 | -6.9855 | 114.3082 | -6.9031 | -6.9397 | -6.9351 | 0.073242 | -0.19226 | 0.12817 | 0.23804 | 0.036621 | 0.09613 | -0.036621 | 0.022888 | 0.027465 | -0.29297 | -0.23346 | 0.10986 | 0.077819 | 0.073242 | 0.050354 | 0.045777 | 0.16479 | 121.6095 | 0.082398 | 121.2936 | 121.2891 | 121.2341 | 121.3623 | 121.2616 | -121.4813 | -121.5271 | 121.6827 | 121.3211 | 8.2214 | 7.9697
768.875 | 121.6324 | -6.4133 | 115.2054 | 0.0095369 | 0 | 0.064963 | 0.065211 | 0.0015595 | -0.002493 | 0.0010468 | 0.00018312 | 0.0026852 | -1.3952 | 0.063529 | -0.0026318 | 0.0080579 | 0.0031829 | 1.2268 | 115.0085 | -6.3034 | 115.1916 | -6.3034 | -6.4178 | -6.4545 | 0.85144 | 114.9353 | -6.3446 | 114.8666 | -6.3675 | -6.3995 | -6.34 | 0.10986 | -0.19684 | -0.013733 | 0.10986 | -0.041199 | -0.004578 | -0.15106 | -0.11444 | 0.068665 | -0.27008 | -0.33875 | 0.045776 | 0.073242 | 0.013733 | 0.004577 | -0.054932 | 0 | 121.4951 | -0.022889 | 121.2112 | 121.312 | 121.2799 | 121.4218 | 121.3486 | -121.5088 | -121.55 | 121.6049 | 121.2799 | 7.6401 | 7.2647
770.6406 | 121.701 | -6.0928 | 115.4617 | 0.0019074 | 0 | 0.064536 | 0.066065 | -0.0012177 | -0.001852 | -0.0015166 | 0.00018312 | -9.1956e-05 | -1.3952 | 0.070579 | 0.0016406 | 0.0072035 | -0.00044851 | 1.2726 | 115.3015 | -5.983 | 115.5396 | -5.928 | -6.0654 | -6.1066 | 0.96588 | 115.1962 | -6.0242 | 115.2512 | -5.9738 | -6.0333 | -5.9601 | 0.10986 | -0.16022 | 0.07782 | 0.16479 | -0.013733 | 0.027465 | -0.1236 | -0.082398 | 0.068664 | -0.2655 | -0.21057 | 0.11902 | 0.13275 | 0.059509 | 0.064087 | -0.009155 | 0.054931 | 121.5225 | 0.050354 | 121.2753 | 121.2845 | 121.2204 | 121.3943 | 121.2891 | -121.4447 | -121.4859 | 121.6324 | 121.344 | 7.3654 | 7.0587
772.3906 | 121.6049 | -5.8914 | 115.7089 | -0.0057221 | 0 | 0.063895 | 0.068629 | 0.0011321 | -0.00057044 | 0.00040597 | -0.0028687 | 0.0024716 | -1.395 | 0.067802 | -0.0026318 | 0.0097669 | -0.0010895 | 1.3504 | 115.5258 | -5.7678 | 115.7455 | -5.7358 | -5.8548 | -5.9189 | 0.94757 | 115.4526 | -5.8136 | 115.361 | -5.8456 | -5.896 | -5.8182 | 0.1236 | -0.1831 | 0.036621 | 0.15564 | -0.027466 | 0.036621 | -0.15106 | -0.086975 | 0.077819 | -0.25635 | -0.3479 | 0.045776 | 0.073242 | -0.004578 | -0.004577 | -0.082397 | 0.032043 | 121.5134 | -0.032043 | 121.1746 | 121.2936 | 121.2662 | 121.4172 | 121.344 | -121.4767 | -121.5225 | 121.637 | 121.2524 | 7.2418 | 6.839
774.0938 | 121.6324 | -5.6076 | 116.011 | 0.040054 | 0 | 0.064963 | 0.06457 | 0.00027771 | -0.0014248 | 0.0010468 | 0.018494 | 0.003967 | -1.3942 | 0.067161 | -0.0060498 | 0.0072035 | -0.0019439 | 1.3779 | 115.8508 | -5.4977 | 116.0339 | -5.4428 | -5.5161 | -5.5801 | 0.95215 | 115.7639 | -5.5435 | 115.6815 | -5.5344 | -5.5756 | -5.5069 | 0.10986 | -0.16022 | 0.022889 | 0.1648 | 0.027466 | 0.091553 | -0.082397 | -0.01831 | 0.064087 | -0.24719 | -0.32959 | 0.073242 | 0.10071 | 0.032043 | 0.036621 | -0.032044 | 0.054932 | 121.5317 | 0.009155 | 121.225 | 121.3486 | 121.3074 | 121.4584 | 121.3715 | -121.5088 | -121.5546 | 121.6415 | 121.2891 | 6.9855 | 6.5598
775.8438 | 121.669 | -5.4016 | 116.1758 | 0.024795 | 0 | 0.063895 | 0.064997 | 6.4114e-05 | -0.00014304 | -0.0015166 | 0.0062865 | 0.0035396 | -1.3942 | 0.059684 | -0.0026318 | 0.0078443 | -0.0017303 | 1.4603 | 115.9698 | -5.3284 | 116.2262 | -5.2048 | -5.3421 | -5.397 | 1.0437 | 115.9149 | -5.3696 | 115.8875 | -5.3055 | -5.3558 | -5.3009 | 0.073242 | -0.20599 | 0.050354 | 0.19684 | 0.004577 | 0.059509 | -0.068665 | -0.013733 | 0.032043 | -0.26093 | -0.28839 | 0.09613 | 0.10071 | 0.045776 | 0.068665 | 0.013733 | 0.1236 | 121.5546 | 0.064087 | 121.257 | 121.2982 | 121.2845 | 121.3715 | 121.3165 | -121.5042 | -121.5454 | 121.6278 | 121.2891 | 6.8619 | 6.4453
777.5312 | 121.6507 | -5.2551 | 116.3361 | 0.040054 | 0 | 0.064322 | 0.066706 | 0.0015595 | -0.0016384 | -0.00023503 | 0.018494 | 0.0018306 | -1.3952 | 0.06417 | -0.0058362 | 0.0072035 | -0.00023491 | 1.4557 | 116.1621 | -5.1773 | 116.3956 | -5.0858 | -5.1636 | -5.2368 | 1.0208 | 116.0843 | -5.2139 | 116.0431 | -5.1682 | -5.2139 | -5.1498 | 0.07782 | -0.17395 | 0.059509 | 0.16937 | 0.018311 | 0.091553 | -0.059509 | 0.013733 | 0.041199 | -0.25177 | -0.29297 | 0.086975 | 0.10529 | 0.041199 | 0.064087 | 0 | 0.091553 | 121.5729 | 0.045776 | 121.257 | 121.3394 | 121.2982 | 121.4172 | 121.3394 | -121.5134 | -121.55 | 121.6507 | 121.2982 | 6.7108 | 6.2759
779.2969 | 121.5912 | -5.0262 | 116.5787 | -0.0057221 | 0 | 0.065604 | 0.065424 | 0.00091851 | -0.0029202 | 0.0016876 | -0.0059205 | 0.0018306 | -1.3929 | 0.057334 | -0.0024182 | 0.0078443 | 0.00019229 | 1.4053 | 116.4047 | -4.9301 | 116.5558 | -4.953 | -5.0491 | -5.0812 | 0.90179 | 116.3086 | -4.9576 | 116.1987 | -4.9896 | -5.0491 | -4.9484 | 0.09613 | -0.17395 | -0.022888 | 0.073242 | -0.054932 | -0.022888 | -0.15106 | -0.11902 | 0.068664 | -0.27008 | -0.37994 | 0.036621 | 0.07782 | -0.022888 | 0.009156 | -0.091552 | -0.022888 | 121.4859 | -0.032043 | 121.1563 | 121.3348 | 121.2662 | 121.431 | 121.3348 | -121.5088 | -121.5363 | 121.582 | 121.225 | 6.4316 | 5.928
781.0625 | 121.6827 | -4.7836 | 116.7664 | 0.047683 | 0 | 0.06539 | 0.063288 | -0.0044221 | -0.0016384 | 0.0016876 | 0.015442 | 0.00054904 | -1.3937 | 0.065238 | -0.0011364 | 0.0086987 | -0.0010895 | 1.4557 | 116.5741 | -4.6875 | 116.8671 | -4.5685 | -4.7012 | -4.7379 | 1.0712 | 116.4734 | -4.747 | 116.5146 | -4.6875 | -4.7104 | -4.6738 | 0.09613 | -0.19226 | 0.10071 | 0.21515 | 0.045776 | 0.082397 | -0.050354 | -0.013733 | 0.036621 | -0.29297 | -0.25177 | 0.09613 | 0.10986 | 0.073242 | 0.073242 | 0.036621 | 0.11902 | 121.5546 | 0.059509 | 121.2616 | 121.2616 | 121.2204 | 121.3577 | 121.257 | -121.4539 | -121.5134 | 121.6507 | 121.2982 | 6.2393 | 5.8548
782.8281 | 121.6553 | -4.541 | 117.0776 | 0.0019074 | 0 | 0.062613 | 0.062433 | 0.00091851 | -0.0033474 | -0.001303 | -0.0059205 | 0.0020444 | -1.3959 | 0.065666 | -0.0069044 | 0.0074171 | -0.0017303 | 1.5381 | 116.835 | -4.4128 | 117.1555 | -4.3076 | -4.3762 | -4.4724 | 1.0941 | 116.7755 | -4.4724 | 116.7435 | -4.4312 | -4.4724 | -4.4403 | 0.12817 | -0.24262 | 0.07782 | 0.23346 | 0.068665 | 0.16479 | -0.059509 | 0.036621 | 0.068665 | -0.30212 | -0.33417 | 0.10986 | 0.10071 | 0.068665 | 0.032043 | 0 | 0.10529 | 121.5683 | 0.041199 | 121.2158 | 121.2479 | 121.2479 | 121.376 | 121.3165 | -121.4905 | -121.55 | 121.6965 | 121.2845 | 6.0791 | 5.6351
784.6094 | 121.6782 | -4.5776 | 116.9907 | 0.032425 | 0 | 0.063467 | 0.064356 | -0.00057689 | -0.0044156 | -0.00044863 | 0.0093383 | -0.00073276 | -1.3952 | 0.069938 | -0.0039136 | 0.0067761 | -0.0019439 | 1.4648 | 116.7572 | -4.4769 | 117.0502 | -4.3991 | -4.4907 | -4.5456 | 1.0437 | 116.6931 | -4.5319 | 116.7114 | -4.4861 | -4.5273 | -4.4678 | 0.10071 | -0.23346 | 0.059509 | 0.17853 | 0.032044 | 0.086975 | -0.068664 | -0.013733 | 0.045777 | -0.29755 | -0.27924 | 0.091553 | 0.10986 | 0.050354 | 0.064087 | 0.004577 | 0.07782 | 121.5271 | 0.045776 | 121.2433 | 121.2341 | 121.225 | 121.3348 | 121.2708 | -121.4676 | -121.5225 | 121.6278 | 121.2891 | 6.0425 | 5.6213
786.3125 | 121.7377 | -4.303 | 117.2607 | 0.0019074 | 0 | 0.063254 | 0.062433 | -0.0022857 | -0.0014248 | -2.1434e-05 | 0.00018312 | 0.00097624 | -1.3969 | 0.064384 | -0.0037 | 0.0072035 | -0.00066231 | 1.5701 | 117.0593 | -4.1656 | 117.4026 | -4.0054 | -4.1565 | -4.2023 | 1.1765 | 116.9724 | -4.2297 | 117.041 | -4.1199 | -4.1656 | -4.1428 | 0.13733 | -0.20142 | 0.14191 | 0.29755 | 0.10071 | 0.14648 | -0.036622 | 0.009155 | 0.073243 | -0.28839 | -0.21973 | 0.18311 | 0.16022 | 0.13733 | 0.086975 | 0.064087 | 0.16022 | 121.5683 | 0.10986 | 121.2708 | 121.225 | 121.2021 | 121.3623 | 121.2753 | -121.4264 | -121.4905 | 121.7056 | 121.344 | 5.8731 | 5.4794
788.0781 | 121.6003 | -4.0924 | 117.5629 | -0.0057221 | 0 | 0.06304 | 0.065424 | 0.00070491 | -0.0033474 | 0.00040597 | -0.0059205 | 0.0028988 | -1.3959 | 0.059257 | -0.00070919 | 0.0069897 | -0.0017303 | 1.5335 | 117.3523 | -3.9688 | 117.5079 | -3.9871 | -4.0878 | -4.1199 | 0.99792 | 117.2745 | -4.0009 | 117.1555 | -4.0329 | -4.0833 | -3.9917 | 0.1236 | -0.21057 | -0.054931 | 0.10528 | -0.027466 | 0.004577 | -0.15106 | -0.11902 | 0.091553 | -0.28839 | -0.40741 | 0.059509 | 0.10071 | 0.009155 | 0.009155 | -0.082398 | -0.018311 | 121.4767 | -0.032044 | 121.1563 | 121.3211 | 121.2753 | 121.4447 | 121.3669 | -121.5317 | -121.5637 | 121.6003 | 121.2479 | 5.6259 | 5.0903
789.7812 | 121.6736 | -3.7811 | 117.778 | 0.047683 | 0 | 0.064322 | 0.061579 | 0.0026275 | -0.0016384 | -2.1434e-05 | 0.0062865 | 0.0014034 | -1.3933 | 0.069938 | -0.00092279 | 0.0086987 | 0.0036103 | 1.5839 | 117.6041 | -3.6942 | 117.8787 | -3.5522 | -3.6896 | -3.7216 | 1.1261 | 117.485 | -3.7445 | 117.5034 | -3.6987 | -3.7262 | -3.6667 | 0.086975 | -0.17395 | 0.10071 | 0.22888 | 0.059509 | 0.091553 | -0.027466 | 0.004578 | 0.036621 | -0.29297 | -0.27466 | 0.082398 | 0.11444 | 0.054932 | 0.07782 | 0.018311 | 0.14191 | 121.5729 | 0.045777 | 121.2479 | 121.2982 | 121.2296 | 121.3852 | 121.2662 | -121.4722 | -121.5225 | 121.6599 | 121.2845 | 5.365 | 4.9072
791.4844 | 121.5958 | -3.5019 | 118.1213 | 0.0019074 | 0 | 0.064749 | 0.066279 | -0.00036309 | -0.0014248 | -0.00044863 | 0.00018312 | 0.0028988 | -1.3942 | 0.061179 | -0.0024182 | 0.0084851 | 0.0010467 | 1.593 | 117.9428 | -3.3829 | 118.0801 | -3.3875 | -3.4836 | -3.5156 | 1.0529 | 117.8329 | -3.4332 | 117.778 | -3.4561 | -3.5019 | -3.3875 | 0.11902 | -0.17853 | -0.041199 | 0.11444 | -0.013733 | 0.01831 | -0.13275 | -0.10071 | 0.068664 | -0.28839 | -0.34332 | 0.045776 | 0.11444 | 0 | 0.045777 | -0.068664 | -0.004577 | 121.463 | -0.022888 | 121.2112 | 121.3257 | 121.2662 | 121.4447 | 121.3348 | -121.5042 | -121.5546 | 121.582 | 121.2799 | 5.0949 | 4.5547
793.25 | 121.6049 | -3.3646 | 118.2404 | 0.0019074 | 0 | 0.061331 | 0.062006 | -0.0027131 | -0.00078404 | 0.0012604 | -0.0028687 | 0.0018306 | -1.3957 | 0.059684 | -0.0062634 | 0.0061353 | -0.0038665 | 1.6159 | 118.0481 | -3.2501 | 118.2404 | -3.2135 | -3.3005 | -3.3508 | 1.0941 | 118.0023 | -3.3005 | 117.8787 | -3.2959 | -3.3371 | -3.2684 | 0.11444 | -0.19226 | 0 | 0.15106 | 0.013733 | 0.064087 | -0.10071 | -0.050354 | 0.064087 | -0.23804 | -0.36163 | 0.068665 | 0.09613 | 0.027466 | 0.032043 | -0.036621 | 0.036621 | 121.4905 | 0.004578 | 121.1792 | 121.2982 | 121.3028 | 121.4127 | 121.3669 | -121.4905 | -121.5408 | 121.6049 | 121.2433 | 4.9805 | 4.4586
795.0156 | 121.701 | -3.1586 | 118.4418 | 0.017166 | 0 | 0.063467 | 0.064142 | 0.0024139 | -0.00099764 | -0.0017304 | -0.0028687 | -9.1956e-05 | -1.3961 | 0.063529 | -0.0041272 | 0.0089123 | 0.0031829 | 1.6525 | 118.2175 | -3.035 | 118.4921 | -2.9526 | -3.0441 | -3.1036 | 1.1627 | 118.1213 | -3.1082 | 118.1717 | -3.0075 | -3.0258 | -3.0029 | 0.1236 | -0.2243 | 0.050354 | 0.20599 | 0.054931 | 0.11444 | -0.068665 | -0.009155 | 0.050354 | -0.32043 | -0.27008 | 0.15106 | 0.15564 | 0.13275 | 0.10528 | 0.082397 | 0.082397 | 121.5271 | 0.10071 | 121.2799 | 121.2524 | 121.2296 | 121.376 | 121.2799 | -121.4767 | -121.55 | 121.6507 | 121.3303 | 4.8111 | 4.3213
796.7812 | 121.6415 | -3.0808 | 118.5196 | 0.0019074 | 0 | 0.062613 | 0.063929 | -0.0012177 | -0.0046292 | -0.0027984 | -0.0028687 | 0.0018306 | -1.3963 | 0.060966 | -0.0049818 | 0.0059217 | 0.0014741 | 1.7395 | 118.2907 | -2.9526 | 118.6295 | -2.8244 | -2.9297 | -2.9755 | 1.2085 | 118.2175 | -3.0121 | 118.2404 | -2.9343 | -2.98 | -2.9388 | 0.12817 | -0.22888 | 0.10986 | 0.25635 | 0.10529 | 0.15106 | -0.022888 | 0.022889 | 0.068665 | -0.30212 | -0.27924 | 0.14649 | 0.14191 | 0.10071 | 0.073242 | 0.032043 | 0.12817 | 121.582 | 0.07782 | 121.2524 | 121.2433 | 121.2296 | 121.3715 | 121.2982 | -121.4722 | -121.5317 | 121.7102 | 121.3211 | 4.8203 | 4.2892
798.5312 | 121.7239 | -2.9984 | 118.5654 | -0.0057221 | 0 | 0.064322 | 0.064356 | 0.00070491 | -0.002493 | 0.00019217 | -0.0028687 | 0.00097624 | -1.3952 | 0.067375 | -0.0034864 | 0.0074171 | -0.0019439 | 1.7624 | 118.3685 | -2.8473 | 118.7347 | -2.7145 | -2.829 | -2.8885 | 1.2451 | 118.2953 | -2.916 | 118.3594 | -2.8152 | -2.8427 | -2.8244 | 0.15106 | -0.19684 | 0.16937 | 0.28381 | 0.10986 | 0.16937 | -0.041199 | 0.018311 | 0.082397 | -0.27008 | -0.20599 | 0.18311 | 0.17395 | 0.15564 | 0.091553 | 0.073243 | 0.13275 | 121.582 | 0.10071 | 121.2753 | 121.2158 | 121.2112 | 121.3669 | 121.2936 | -121.4127 | -121.4813 | 121.7331 | 121.3577 | 4.7607 | 4.2435
800.2969 | 121.6141 | -2.9572 | 118.6661 | -0.0057221 | 0 | 0.06304 | 0.06457 | 0.0017731 | -0.0014248 | -0.001303 | 0.00018312 | 0.0020444 | -1.3952 | 0.072502 | -0.004768 | 0.0063489 | 0.0036103 | 1.767 | 118.4372 | -2.8152 | 118.7119 | -2.742 | -2.8473 | -2.8931 | 1.149 | 118.4006 | -2.8656 | 118.3136 | -2.8564 | -2.8976 | -2.8519 | 0.14191 | -0.22888 | 0.045776 | 0.21515 | 0.064087 | 0.10986 | -0.077819 | -0.032043 | 0.091552 | -0.2655 | -0.35248 | 0.10071 | 0.10528 | 0.059509 | 0.013733 | -0.032043 | 0.073243 | 121.5271 | 0.009156 | 121.1792 | 121.2524 | 121.2662 | 121.3943 | 121.3577 | -121.4813 | -121.5317 | 121.669 | 121.2708 | 4.7241 | 4.1061
802 | 121.7331 | -2.7878 | 118.7531 | 0.0019074 | 0 | 0.061972 | 0.06222 | -0.0042083 | -0.003561 | -0.0010894 | -0.0028687 | 0.0018306 | -1.3967 | 0.062888 | -0.0028454 | 0.0084851 | -0.0013031 | 1.7944 | 118.5287 | -2.6688 | 118.9087 | -2.5177 | -2.6321 | -2.6962 | 1.2817 | 118.4692 | -2.7328 | 118.5516 | -2.6001 | -2.6367 | -2.6184 | 0.11902 | -0.2243 | 0.15564 | 0.27008 | 0.091553 | 0.15564 | -0.027466 | 0.036621 | 0.054932 | -0.28381 | -0.20142 | 0.18768 | 0.16937 | 0.15106 | 0.11444 | 0.09613 | 0.15106 | 121.5775 | 0.13275 | 121.2845 | 121.1975 | 121.2021 | 121.3165 | 121.257 | -121.4218 | -121.4859 | 121.6965 | 121.3394 | 4.5822 | 4.0695
803.7656 | 121.5866 | -2.7466 | 118.8858 | 0.0019074 | 0 | 0.064963 | 0.06692 | -0.0029267 | -0.0012112 | -0.0017304 | -0.0059205 | 0.0026852 | -1.395 | 0.059257 | -0.0026318 | 0.0074171 | -0.00023491 | 1.7715 | 118.7164 | -2.5955 | 118.895 | -2.5955 | -2.7054 | -2.7374 | 1.0941 | 118.6386 | -2.6459 | 118.5425 | -2.6825 | -2.7374 | -2.6184 | 0.15106 | -0.16937 | 0.009155 | 0.15106 | 0.009155 | 0.041199 | -0.14191 | -0.10986 | 0.10071 | -0.24719 | -0.34332 | 0.064087 | 0.12817 | 0.009155 | 0.027466 | -0.091553 | 0 | 121.4905 | -0.036621 | 121.1884 | 121.312 | 121.2845 | 121.463 | 121.3852 | -121.4813 | -121.5317 | 121.6415 | 121.2891 | 4.5181 | 3.8406
805.5469 | 121.6919 | -2.623 | 118.895 | 0.0095369 | 0 | 0.063467 | 0.06457 | 0.00070491 | -0.0012112 | -0.0038666 | -0.0028687 | 0.0011898 | -1.3961 | 0.05947 | -0.00028199 | 0.0099805 | -0.00087591 | 1.7578 | 118.7714 | -2.5269 | 118.9865 | -2.4445 | -2.5864 | -2.6184 | 1.2039 | 118.6615 | -2.5543 | 118.6935 | -2.504 | -2.5452 | -2.4536 | 0.096131 | -0.1236 | 0.091553 | 0.17853 | 0.004578 | 0.036621 | -0.091553 | -0.05951 | 0.068665 | -0.23346 | -0.20142 | 0.11902 | 0.16937 | 0.07782 | 0.10071 | 0.009155 | 0.082397 | 121.5134 | 0.050354 | 121.2479 | 121.2982 | 121.2158 | 121.3943 | 121.2845 | -121.4218 | -121.4493 | 121.6095 | 121.3165 | 4.3808 | 3.8269
807.3125 | 121.7239 | -2.5772 | 118.9774 | 0.0019074 | 0 | 0.062827 | 0.063929 | 0.00049131 | -0.00078404 | 0.00019217 | 0.00018312 | 0.00097624 | -1.3961 | 0.070152 | -0.00049559 | 0.0099805 | -0.0049347 | 1.7807 | 118.7805 | -2.4994 | 119.0735 | -2.3849 | -2.504 | -2.5406 | 1.2405 | 118.6935 | -2.5177 | 118.7668 | -2.4353 | -2.4811 | -2.4033 | 0.077819 | -0.19684 | 0.09613 | 0.19226 | 0.036621 | 0.073242 | -0.041198 | -0.004577 | 0.059509 | -0.28381 | -0.21057 | 0.14191 | 0.17395 | 0.09613 | 0.11444 | 0.036621 | 0.11444 | 121.5729 | 0.082397 | 121.2845 | 121.2799 | 121.2112 | 121.3577 | 121.2708 | -121.4767 | -121.4951 | 121.6507 | 121.344 | 4.3579 | 3.8177
809.0156 | 121.5912 | -2.4811 | 119.1147 | 0.0019074 | 0 | 0.064536 | 0.065638 | 0.0024139 | -0.0016384 | -0.00023503 | -0.0028687 | 0.0041806 | -1.3946 | 0.059043 | -0.0051954 | 0.0089123 | -0.0010895 | 1.7899 | 118.9545 | -2.3804 | 119.0826 | -2.4078 | -2.5085 | -2.5314 | 1.1215 | 118.8492 | -2.4445 | 118.7393 | -2.449 | -2.504 | -2.3941 | 0.10071 | -0.16022 | -0.032043 | 0.073242 | -0.050354 | -0.027466 | -0.15106 | -0.12817 | 0.036621 | -0.2655 | -0.37537 | 0.032043 | 0.086975 | -0.022888 | 0.050354 | -0.059509 | -0.027466 | 121.463 | -0.004578 | 121.1838 | 121.3348 | 121.2936 | 121.4355 | 121.3303 | -121.4951 | -121.5591 | 121.5637 | 121.2204 | 4.2709 | 3.6026
810.7812 | 121.6095 | -2.4033 | 119.2154 | -0.0057221 | 0 | 0.063681 | 0.066706 | -0.0012177 | -0.00035684 | -0.001303 | -0.0059205 | 0.0028988 | -1.3925 | 0.063316 | -0.0022046 | 0.011049 | 0.0014741 | 1.8082 | 119.0689 | -2.2842 | 119.1696 | -2.298 | -2.3941 | -2.4124 | 1.149 | 118.9316 | -2.3621 | 118.8583 | -2.3666 | -2.4078 | -2.298 | 0.11902 | -0.14648 | -0.045776 | 0.10528 | -0.009156 | 0.009155 | -0.12817 | -0.10986 | 0.041198 | -0.28381 | -0.35706 | 0.036621 | 0.10528 | -0.004578 | 0.064087 | -0.045776 | -0.013733 | 121.4539 | -0.004577 | 121.2204 | 121.3531 | 121.2936 | 121.4722 | 121.3348 | -121.4996 | -121.5775 | 121.5729 | 121.2616 | 4.2114 | 3.5522
812.5469 | 121.6187 | -2.2202 | 119.4168 | -0.0057221 | 0 | 0.063681 | 0.06457 | -0.00079049 | -0.0016384 | -0.0021576 | 0.00018312 | 0.0024716 | -1.3935 | 0.072715 | -0.0043408 | 0.0091261 | 0.0010467 | 1.8951 | 119.2017 | -2.0737 | 119.458 | -1.9867 | -2.0874 | -2.1515 | 1.2497 | 119.133 | -2.124 | 119.0552 | -2.1057 | -2.1469 | -2.0966 | 0.14648 | -0.21515 | 0.041199 | 0.23346 | 0.068665 | 0.13275 | -0.07782 | -0.013733 | 0.096131 | -0.28381 | -0.36163 | 0.11444 | 0.1236 | 0.073242 | 0.027465 | -0.022889 | 0.086975 | 121.5317 | 0.01831 | 121.1792 | 121.2753 | 121.257 | 121.4218 | 121.3531 | -121.4905 | -121.5408 | 121.6782 | 121.2753 | 4.1153 | 3.4698
814.3125 | 121.5912 | -2.1744 | 119.4305 | 0.0019074 | 0 | 0.063681 | 0.064783 | -0.00036309 | -0.0037746 | 0.001474 | -0.0028687 | 0.0026852 | -1.3935 | 0.062888 | -0.0041272 | 0.0080579 | -0.0013031 | 1.886 | 119.2566 | -2.0508 | 119.426 | -2.0187 | -2.1469 | -2.1835 | 1.2268 | 119.1559 | -2.1103 | 119.101 | -2.1423 | -2.179 | -2.0782 | 0.1236 | -0.17395 | -0.004578 | 0.15564 | -0.009156 | 0.027465 | -0.13275 | -0.096131 | 0.064086 | -0.27466 | -0.32959 | 0.032043 | 0.09613 | -0.004578 | 0.032044 | -0.068664 | 0.032043 | 121.4767 | -0.032043 | 121.2112 | 121.3074 | 121.2662 | 121.431 | 121.3303 | -121.4813 | -121.5408 | 121.6003 | 121.2753 | 4.0604 | 3.4012
816.0156 | 121.7239 | -2.1149 | 119.4626 | 0.017166 | 0 | 0.063895 | 0.060724 | -0.00036309 | -0.0020658 | -0.00087583 | -0.0028687 | 0.00012184 | -1.3937 | 0.068015 | -0.00092279 | 0.0080579 | 0.00040589 | 1.8448 | 119.2337 | -1.9821 | 119.5084 | -1.9089 | -2.005 | -2.0462 | 1.2909 | 119.1605 | -2.0554 | 119.2337 | -1.9547 | -1.9684 | -1.9363 | 0.13275 | -0.22888 | 0.045777 | 0.20599 | 0.068664 | 0.10986 | -0.064087 | -0.022888 | 0.059509 | -0.30212 | -0.22888 | 0.16022 | 0.17853 | 0.14648 | 0.11902 | 0.086975 | 0.073242 | 121.4905 | 0.10071 | 121.2891 | 121.2158 | 121.2158 | 121.3486 | 121.2753 | -121.4447 | -121.5179 | 121.6232 | 121.3486 | 3.9597 | 3.4058
817.7812 | 121.6187 | -2.1881 | 119.4031 | 0.017166 | 0 | 0.063895 | 0.066065 | -0.0014313 | -0.0039884 | -0.0017304 | 0.0032349 | 0.0043942 | -1.394 | 0.060539 | -0.0049818 | 0.0080579 | 0.0010467 | 1.9409 | 119.2245 | -2.0737 | 119.4443 | -1.9592 | -2.0782 | -2.1286 | 1.3412 | 119.1147 | -2.1149 | 119.1147 | -2.0645 | -2.1103 | -2.0279 | 0.11444 | -0.17853 | 0.041199 | 0.22888 | 0.059509 | 0.10986 | -0.054932 | -0.004578 | 0.073242 | -0.28839 | -0.28839 | 0.1236 | 0.16022 | 0.077819 | 0.086975 | 0.004577 | 0.11444 | 121.5179 | 0.050354 | 121.2296 | 121.2982 | 121.2296 | 121.4127 | 121.3028 | -121.4767 | -121.5179 | 121.6324 | 121.3028 | 4.129 | 3.5294
819.5 | 121.6324 | -2.2018 | 119.2291 | -0.013352 | 0 | 0.064108 | 0.061793 | 0.0024139 | -0.0031338 | -0.00023503 | 0.00018312 | -0.00030556 | -1.3942 | 0.060539 | -0.0022046 | 0.0082715 | -0.00087591 | 1.918 | 119.0231 | -2.0874 | 119.3619 | -1.9318 | -2.0416 | -2.0966 | 1.3962 | 118.9453 | -2.1423 | 119.0231 | -2.005 | -2.0645 | -2.0233 | 0.11444 | -0.20599 | 0.13275 | 0.27008 | 0.10529 | 0.16022 | -0.009156 | 0.045776 | 0.059509 | -0.28381 | -0.20599 | 0.19684 | 0.17853 | 0.13733 | 0.11902 | 0.07782 | 0.15564 | 121.4493 | 0.13733 | 121.1655 | 121.1105 | 121.0876 | 121.225 | 121.1472 | -121.3165 | -121.3715 | 121.5637 | 121.225 | 4.1199 | 3.598
821.25 | 121.5225 | -2.2751 | 119.0918 | 0.017166 | 0 | 0.063254 | 0.06222 | -0.0014313 | -0.0016384 | -0.00087583 | 0.0032349 | -0.00094636 | -1.3942 | 0.058189 | -0.00092279 | 0.0078443 | 0.0016877 | 1.8539 | 118.9224 | -2.1698 | 119.1879 | -2.092 | -2.1835 | -2.2339 | 1.2589 | 118.8446 | -2.2293 | 118.8675 | -2.1835 | -2.1973 | -2.1332 | 0.10528 | -0.16937 | 0.09613 | 0.1831 | 0.041198 | 0.091552 | -0.064087 | -0.013733 | 0.045776 | -0.24719 | -0.2243 | 0.091552 | 0.14191 | 0.077819 | 0.09613 | 0.032043 | 0.07782 | 121.3577 | 0.045776 | 121.0968 | 121.0922 | 121.0739 | 121.1975 | 121.1197 | -121.2616 | -121.3211 | 121.463 | 121.1426 | 4.129 | 3.5339
823.0156 | 121.3394 | -1.9226 | 119.3436 | 0.055313 | 0 | 0.065604 | 0.068415 | 0.0017731 | -0.001852 | -0.00044863 | 0.0093383 | 0.0035396 | -1.395 | 0.064811 | -0.0037 | 0.0078443 | -0.0032257 | 1.9958 | 119.2245 | -1.8448 | 119.3939 | -1.7441 | -1.8356 | -1.8723 | 1.3458 | 119.101 | -1.8768 | 119.0918 | -1.8036 | -1.8402 | -1.7761 | 0.077819 | -0.11902 | 0.050354 | 0.17853 | 0.050354 | 0.086975 | -0.027465 | 0.009156 | 0.045776 | -0.24261 | -0.25177 | 0.11902 | 0.14648 | 0.082397 | 0.10071 | 0.036621 | 0.10071 | 121.2387 | 0.073242 | 120.9686 | 121.0693 | 120.9778 | 121.1472 | 121.0236 | -121.1884 | -121.2204 | 121.3165 | 121.0144 | 3.9185 | 3.2684
824.7812 | 121.5546 | -1.7487 | 119.5908 | 0.0095369 | 0 | 0.061758 | 0.062861 | -0.0027131 | -0.001852 | -0.001303 | -0.0059205 | -0.00073276 | -1.395 | 0.066093 | -0.0026318 | 0.0095533 | -0.00023491 | 2.0142 | 119.3893 | -1.6525 | 119.7601 | -1.4832 | -1.6113 | -1.6617 | 1.4282 | 119.339 | -1.6937 | 119.4305 | -1.5701 | -1.6113 | -1.5976 | 0.09613 | -0.20142 | 0.16937 | 0.2655 | 0.086975 | 0.13733 | -0.009155 | 0.041199 | 0.054931 | -0.25177 | -0.16022 | 0.17853 | 0.15106 | 0.13733 | 0.096131 | 0.082398 | 0.16937 | 121.4127 | 0.1236 | 121.1243 | 121.0419 | 121.0327 | 121.138 | 121.0876 | -121.2433 | -121.2845 | 121.5088 | 121.1792 | 3.7628 | 3.1769
826.5312 | 121.6049 | -1.767 | 119.6457 | 0.0019074 | 0 | 0.064108 | 0.064356 | 0.00027771 | -0.003561 | -0.00044863 | 0.00018312 | 0.0014034 | -1.3959 | 0.062034 | 0.00057241 | 0.0091261 | 0.00061949 | 2.0096 | 119.4626 | -1.6663 | 119.783 | -1.5472 | -1.6434 | -1.7075 | 1.3916 | 119.3802 | -1.7166 | 119.4717 | -1.6067 | -1.6388 | -1.5839 | 0.10071 | -0.18311 | 0.13733 | 0.21973 | 0.05951 | 0.1236 | -0.041198 | 0.022888 | 0.050354 | -0.2655 | -0.17395 | 0.16022 | 0.18311 | 0.12817 | 0.13275 | 0.07782 | 0.11902 | 121.4493 | 0.10986 | 121.1884 | 121.1288 | 121.0968 | 121.2296 | 121.1472 | -121.312 | -121.3623 | 121.55 | 121.2387 | 3.7766 | 3.1586
828.2969 | 121.6232 | -1.7853 | 119.6686 | -0.0057221 | 0 | 0.063895 | 0.062433 | -0.0016449 | -0.00035684 | -0.00066223 | 0.00018312 | -0.001801 | -1.394 | 0.063957 | -0.004768 | 0.0097669 | -0.0032257 | 2.0142 | 119.4946 | -1.6479 | 119.8151 | -1.4969 | -1.6159 | -1.6891 | 1.4603 | 119.4031 | -1.712 | 119.4672 | -1.593 | -1.6205 | -1.5976 | 0.13733 | -0.17395 | 0.14648 | 0.28839 | 0.09613 | 0.16937 | -0.041199 | 0.032043 | 0.073242 | -0.2655 | -0.20142 | 0.19226 | 0.18768 | 0.1648 | 0.11444 | 0.091553 | 0.15106 | 121.463 | 0.11902 | 121.1792 | 121.1426 | 121.1151 | 121.2799 | 121.1884 | -121.3165 | -121.3806 | 121.6003 | 121.2524 | 3.7994 | 3.2455
830.0156 | 121.5912 | -1.799 | 119.7006 | 0.017166 | 0 | 0.064108 | 0.063502 | -0.0031403 | -0.00035684 | -0.003653 | 0.0093383 | 0.00097624 | -1.3955 | 0.063743 | -0.0013502 | 0.0097669 | -0.0030121 | 1.9638 | 119.5084 | -1.7029 | 119.7647 | -1.5793 | -1.6754 | -1.7212 | 1.3412 | 119.4397 | -1.7258 | 119.4534 | -1.6708 | -1.6983 | -1.6434 | 0.09613 | -0.19226 | 0.064086 | 0.21973 | 0.07782 | 0.1236 | -0.01831 | 0.027466 | 0.073242 | -0.26093 | -0.24719 | 0.12817 | 0.15564 | 0.10071 | 0.082397 | 0.027466 | 0.1236 | 121.4676 | 0.054932 | 121.1792 | 121.2112 | 121.1655 | 121.3074 | 121.2387 | -121.4035 | -121.4264 | 121.5637 | 121.2524 | 3.7628 | 3.1403
831.7969 | 121.5729 | -1.8402 | 119.6594 | 0.017166 | 0 | 0.061758 | 0.062647 | 0.00027771 | -0.00078404 | -0.0010894 | 0.0032349 | 0.0054622 | -1.3946 | 0.060752 | -0.0037 | 0.0084851 | -0.0010895 | 2.0737 | 119.5312 | -1.7349 | 119.7418 | -1.6342 | -1.7441 | -1.7899 | 1.4008 | 119.4214 | -1.7807 | 119.4031 | -1.7349 | -1.7807 | -1.7029 | 0.10529 | -0.12817 | 0.082397 | 0.20599 | 0.050354 | 0.09613 | -0.054932 | -0.009156 | 0.059509 | -0.23804 | -0.25635 | 0.10529 | 0.13733 | 0.059509 | 0.07782 | 0 | 0.10071 | 121.4767 | 0.045777 | 121.1838 | 121.2662 | 121.2021 | 121.3715 | 121.2616 | -121.3943 | -121.4401 | 121.582 | 121.2433 | 3.9139 | 3.241
833.5 | 121.5958 | -1.8539 | 119.6777 | -0.0057221 | 0 | 0.065176 | 0.064356 | -0.0024995 | -0.0029202 | -0.00066223 | -0.0028687 | 0.0011898 | -1.394 | 0.062248 | -0.00049559 | 0.011476 | 0.00083309 | 1.9775 | 119.5312 | -1.7212 | 119.7006 | -1.68 | -1.8173 | -1.8173 | 1.2955 | 119.4489 | -1.7624 | 119.4534 | -1.7212 | -1.7761 | -1.68 | 0.13275 | -0.14648 | 0.022889 | 0.17395 | 0.036621 | 0.036621 | -0.096131 | -0.096131 | 0.091553 | -0.22888 | -0.2243 | 0.13275 | 0.17395 | 0.07782 | 0.082397 | -0.013733 | 0.041198 | 121.4218 | 0.041199 | 121.2158 | 121.2524 | 121.2112 | 121.3852 | 121.3028 | -121.3989 | -121.4401 | 121.5546 | 121.3074 | 3.8315 | 3.1494
835.2656 | 121.6324 | -1.8265 | 119.7189 | 0.0019074 | 0 | 0.065176 | 0.061579 | -0.00014949 | -0.0031338 | 0.00019217 | 0.00018312 | 0.002258 | -1.3948 | 0.066734 | -0.0011364 | 0.0095533 | 0.00061949 | 1.9913 | 119.5541 | -1.712 | 119.7464 | -1.6571 | -1.7624 | -1.799 | 1.3229 | 119.4305 | -1.7532 | 119.4855 | -1.6891 | -1.7212 | -1.6434 | 0.11444 | -0.1648 | 0.027466 | 0.16937 | 0.027466 | 0.064087 | -0.086975 | -0.050354 | 0.073242 | -0.28839 | -0.23346 | 0.13733 | 0.1831 | 0.10529 | 0.10986 | 0.032044 | 0.054932 | 121.4584 | 0.064087 | 121.2387 | 121.2662 | 121.1838 | 121.3806 | 121.257 | -121.431 | -121.4722 | 121.5729 | 121.312 | 3.8177 | 3.1494
837.0312 | 121.582 | -1.7899 | 119.8242 | 0.047683 | 0 | 0.064108 | 0.066492 | 0.0013459 | -0.00014304 | 0.00019217 | 0.01239 | 0.0035396 | -1.3899 | 0.065452 | -0.004768 | 0.0076307 | -0.0027985 | 2.0691 | 119.664 | -1.7029 | 119.8242 | -1.5839 | -1.6617 | -1.7349 | 1.3412 | 119.5679 | -1.7395 | 119.4855 | -1.6708 | -1.7166 | -1.6205 | 0.086975 | -0.16022 | 0 | 0.20599 | 0.054932 | 0.12817 | -0.032043 | 0.041199 | 0.050354 | -0.25635 | -0.33875 | 0.11902 | 0.16937 | 0.073242 | 0.11902 | 0.022888 | 0.11902 | 121.5271 | 0.068665 | 121.225 | 121.3669 | 121.3074 | 121.4539 | 121.3577 | -121.5271 | -121.5637 | 121.6141 | 121.2753 | 3.8589 | 3.1311
838.7969 | 121.55 | -1.7349 | 119.8608 | 0.0019074 | 0 | 0.062613 | 0.066492 | -0.0022857 | -0.00035684 | -0.00087583 | 0.0032349 | 0.0020444 | -1.3946 | 0.060752 | -0.0037 | 0.0065625 | 0.0012603 | 2.0599 | 119.6915 | -1.6296 | 119.8242 | -1.5701 | -1.6891 | -1.7166 | 1.3229 | 119.5679 | -1.6846 | 119.5038 | -1.6708 | -1.7258 | -1.6205 | 0.10528 | -0.16937 | -0.036621 | 0.16479 | 0.01831 | 0.045776 | -0.086975 | -0.059509 | 0.050354 | -0.29297 | -0.35706 | 0.064087 | 0.11444 | 0.009155 | 0.064087 | -0.041199 | 0.05951 | 121.4539 | 0.013733 | 121.1884 | 121.3211 | 121.2524 | 121.4264 | 121.3028 | -121.4905 | -121.5454 | 121.5591 | 121.2387 | 3.7949 | 3.0579
840.5625 | 121.7102 | -1.6891 | 119.8151 | -0.0057221 | 0 | 0.063467 | 0.062433 | -0.0016449 | -0.0020658 | -2.1434e-05 | 0.0032349 | 0.00033544 | -1.3959 | 0.065025 | -0.0043408 | 0.0082715 | 0.0014741 | 2.0737 | 119.6503 | -1.561 | 119.957 | -1.4191 | -1.5198 | -1.5656 | 1.474 | 119.5358 | -1.6205 | 119.6548 | -1.4786 | -1.506 | -1.4923 | 0.12817 | -0.16479 | 0.14191 | 0.27008 | 0.1236 | 0.16937 | -0.004578 | 0.041199 | 0.068665 | -0.27923 | -0.16022 | 0.21057 | 0.19684 | 0.18311 | 0.12817 | 0.11444 | 0.14191 | 121.5179 | 0.14191 | 121.2753 | 121.2112 | 121.1563 | 121.3394 | 121.225 | -121.376 | -121.4355 | 121.6461 | 121.344 | 3.7628 | 3.1631
842.3281 | 121.6782 | -1.6067 | 119.9066 | 0.0095369 | 0 | 0.063895 | 0.064142 | 0.0017731 | -0.00057044 | 0.00040597 | -0.0059205 | 0.0014034 | -1.3948 | 0.065238 | -0.001991 | 0.0093397 | 0.0012603 | 2.0599 | 119.7556 | -1.5152 | 119.989 | -1.4191 | -1.5335 | -1.5747 | 1.3962 | 119.6411 | -1.5472 | 119.7235 | -1.4694 | -1.5106 | -1.4191 | 0.091552 | -0.15106 | 0.082398 | 0.18768 | 0.032043 | 0.073242 | -0.059509 | -0.01831 | 0.059509 | -0.2655 | -0.1831 | 0.13733 | 0.18768 | 0.09613 | 0.12817 | 0.036621 | 0.096131 | 121.5042 | 0.07782 | 121.2708 | 121.2708 | 121.1884 | 121.3623 | 121.2479 | -121.4218 | -121.4539 | 121.5958 | 121.3303 | 3.6667 | 3.0029
844.0938 | 121.6232 | -1.6251 | 119.9707 | 0.047683 | 0 | 0.062613 | 0.065638 | 0.0017731 | -0.0016384 | -0.0027984 | 0.015442 | 0.0028988 | -1.3916 | 0.064597 | -0.003059 | 0.0072035 | -0.0060027 | 2.1423 | 119.8334 | -1.5335 | 120.0165 | -1.4328 | -1.5106 | -1.5656 | 1.4099 | 119.7052 | -1.5656 | 119.6869 | -1.4923 | -1.5335 | -1.4694 | 0.091553 | -0.13733 | 0.045776 | 0.19226 | 0.059509 | 0.11444 | -0.032044 | 0.022888 | 0.059509 | -0.2655 | -0.28381 | 0.13275 | 0.15564 | 0.091553 | 0.096131 | 0.032044 | 0.10071 | 121.55 | 0.073242 | 121.2524 | 121.3669 | 121.2708 | 121.4584 | 121.3303 | -121.5042 | -121.5363 | 121.6415 | 121.312 | 3.7674 | 3.035
845.8125 | 121.6965 | -1.5427 | 119.9799 | 0.0019074 | 0 | 0.064108 | 0.065424 | -0.0029267 | -0.0012112 | 0.00040597 | 0.00018312 | 0.0020444 | -1.3961 | 0.062248 | -0.00092279 | 0.0095533 | -0.00087591 | 2.0966 | 119.8242 | -1.4465 | 120.076 | -1.3367 | -1.4465 | -1.4923 | 1.442 | 119.7052 | -1.4786 | 119.7922 | -1.3916 | -1.4145 | -1.3641 | 0.096131 | -0.15564 | 0.096131 | 0.20599 | 0.050354 | 0.096131 | -0.045777 | 0 | 0.064087 | -0.27466 | -0.18768 | 0.15106 | 0.17853 | 0.12817 | 0.11444 | 0.064087 | 0.10986 | 121.5225 | 0.086975 | 121.2708 | 121.2708 | 121.1838 | 121.3669 | 121.2479 | -121.4264 | -121.4584 | 121.6187 | 121.3348 | 3.6392 | 2.9846
847.5781 | 121.5683 | -1.5747 | 120.0577 | -0.0057221 | 0 | 0.064749 | 0.061793 | 0.00070491 | -0.0020658 | -2.1434e-05 | 0.00018312 | 0.0026852 | -1.3948 | 0.060752 | -0.0060498 | 0.0072035 | -0.00066231 | 2.0874 | 119.8288 | -1.442 | 120.0073 | -1.4053 | -1.4969 | -1.5289 | 1.355 | 119.751 | -1.506 | 119.7006 | -1.4877 | -1.5289 | -1.442 | 0.13275 | -0.22888 | -0.050354 | 0.16937 | 0.045776 | 0.07782 | -0.086975 | -0.054931 | 0.068665 | -0.3067 | -0.35706 | 0.086975 | 0.13275 | 0.045776 | 0.064086 | -0.022889 | 0.036622 | 121.4493 | 0.01831 | 121.2067 | 121.2708 | 121.257 | 121.4035 | 121.3257 | -121.4996 | -121.5637 | 121.582 | 121.2753 | 3.6621 | 2.9297
849.3438 | 121.5546 | -1.4236 | 120.2179 | 0.0095369 | 0 | 0.065176 | 0.064356 | 6.4114e-05 | -0.0048428 | -0.00066223 | 0.00018312 | 0.0020444 | -1.3944 | 0.067375 | -0.0037 | 0.0063489 | -0.0027985 | 2.1286 | 120.0302 | -1.2909 | 120.163 | -1.2909 | -1.387 | -1.4328 | 1.3412 | 119.9249 | -1.3458 | 119.8471 | -1.3779 | -1.4145 | -1.2955 | 0.13275 | -0.18768 | -0.054932 | 0.13275 | -0.009155 | 0.036621 | -0.14191 | -0.09613 | 0.07782 | -0.29297 | -0.37079 | 0.045776 | 0.12817 | 0.009155 | 0.050354 | -0.068665 | 0 | 121.4539 | -0.032044 | 121.1929 | 121.3211 | 121.2708 | 121.4539 | 121.3486 | -121.5088 | -121.5637 | 121.5866 | 121.2708 | 3.5522 | 2.7649
851.0469 | 121.701 | -1.2863 | 120.2545 | 0.0095369 | 0 | 0.06304 | 0.06457 | -0.00036309 | -0.0020658 | -0.00023503 | 0.00018312 | 0.0011898 | -1.395 | 0.06417 | -0.0017774 | 0.0091261 | 0.00040589 | 2.1378 | 120.0943 | -1.1902 | 120.3003 | -1.1169 | -1.2268 | -1.2589 | 1.4511 | 119.989 | -1.2131 | 120.0623 | -1.1581 | -1.181 | -1.1078 | 0.09613 | -0.16022 | 0.045776 | 0.16937 | 0.027466 | 0.059509 | -0.068664 | -0.036621 | 0.073242 | -0.2655 | -0.19226 | 0.12817 | 0.17853 | 0.10529 | 0.10529 | 0.032044 | 0.073243 | 121.4905 | 0.054932 | 121.2753 | 121.2845 | 121.2021 | 121.3806 | 121.2753 | -121.4447 | -121.4676 | 121.5866 | 121.3486 | 3.4241 | 2.7374
852.8125 | 121.6599 | -1.2726 | 120.3049 | 0.0019074 | 0 | 0.063895 | 0.060724 | -0.0027131 | -0.0016384 | -0.001944 | -0.0028687 | 0.0011898 | -1.3959 | 0.06417 | -0.0045544 | 0.0074171 | 0.00019229 | 2.2156 | 120.0714 | -1.1444 | 120.401 | -1.0162 | -1.1169 | -1.1627 | 1.4648 | 120.0348 | -1.2039 | 120.0302 | -1.1261 | -1.1581 | -1.1307 | 0.12817 | -0.23346 | 0.09613 | 0.25635 | 0.10986 | 0.15564 | -0.018311 | 0.027466 | 0.068665 | -0.27008 | -0.27466 | 0.14648 | 0.14191 | 0.11444 | 0.073242 | 0.045776 | 0.12817 | 121.5454 | 0.077819 | 121.2341 | 121.2158 | 121.2387 | 121.344 | 121.3074 | -121.4493 | -121.5088 | 121.6736 | 121.3028 | 3.4882 | 2.7374
854.5781 | 121.6553 | -1.2589 | 120.3278 | 0.0019074 | 0 | 0.062613 | 0.062647 | -0.0033539 | -0.00527 | -0.0021576 | 0.00018312 | 0.0020444 | -1.395 | 0.067802 | -0.004768 | 0.0072035 | -0.0017303 | 2.2385 | 120.0989 | -1.1215 | 120.4239 | -0.98419 | -1.0895 | -1.1444 | 1.4923 | 120.0485 | -1.1719 | 120.0714 | -1.1124 | -1.1536 | -1.0941 | 0.13733 | -0.22888 | 0.09613 | 0.27466 | 0.11444 | 0.16937 | -0.022888 | 0.032043 | 0.086975 | -0.27924 | -0.25635 | 0.14648 | 0.1648 | 0.10529 | 0.07782 | 0.018311 | 0.13733 | 121.5454 | 0.059509 | 121.2433 | 121.2204 | 121.2204 | 121.3577 | 121.3074 | -121.4493 | -121.4996 | 121.6827 | 121.3303 | 3.4973 | 2.7512
856.2656 | 121.6278 | -1.2543 | 120.3598 | -0.013352 | 0 | 0.063681 | 0.064356 | -0.00057689 | -0.0016384 | -0.00044863 | -0.0028687 | 0.00097624 | -1.3942 | 0.066947 | -0.0045544 | 0.0061353 | -0.0025849 | 2.243 | 120.1218 | -1.0986 | 120.433 | -0.99792 | -1.0757 | -1.1444 | 1.4648 | 120.076 | -1.1627 | 120.0668 | -1.1261 | -1.1307 | -1.0895 | 0.15564 | -0.23804 | 0.073242 | 0.25635 | 0.10986 | 0.17853 | -0.045776 | 0.022888 | 0.091552 | -0.28381 | -0.29297 | 0.12817 | 0.16479 | 0.1236 | 0.073242 | 0.032044 | 0.10071 | 121.5317 | 0.036621 | 121.2296 | 121.2204 | 121.2387 | 121.376 | 121.3303 | -121.4584 | -121.5225 | 121.6873 | 121.3211 | 3.4973 | 2.7191
858.0312 | 121.6507 | -1.2268 | 120.369 | 0.024795 | 0 | 0.064749 | 0.066279 | 0.0017731 | 0.00049776 | -0.00044863 | 0.0032349 | 0.0035396 | -1.3935 | 0.065238 | -0.0037 | 0.0076307 | -0.0030121 | 2.2705 | 120.2225 | -1.1215 | 120.4056 | -1.0162 | -1.1307 | -1.1765 | 1.4877 | 120.1035 | -1.1673 | 120.108 | -1.1078 | -1.1353 | -1.0666 | 0.10529 | -0.14649 | 0.036621 | 0.21057 | 0.050354 | 0.096131 | -0.054932 | -0.009155 | 0.05951 | -0.2655 | -0.26093 | 0.11902 | 0.16022 | 0.091553 | 0.10071 | 0.032043 | 0.10529 | 121.5271 | 0.059509 | 121.2753 | 121.344 | 121.2708 | 121.4493 | 121.3303 | -121.4905 | -121.5363 | 121.6324 | 121.3348 | 3.4973 | 2.7145
859.7969 | 121.7056 | -1.1856 | 120.3506 | 0.0019074 | 0 | 0.062399 | 0.063502 | -0.0042083 | -0.0048428 | 0.00019217 | 0.00018312 | -0.00030556 | -1.3969 | 0.064597 | -0.0039136 | 0.0097669 | -0.0017303 | 2.243 | 120.1538 | -1.0712 | 120.488 | -0.90637 | -1.0254 | -1.0895 | 1.5244 | 120.108 | -1.1169 | 120.1767 | -0.99335 | -1.0345 | -0.99792 | 0.11444 | -0.19684 | 0.13733 | 0.27924 | 0.09613 | 0.16022 | -0.018311 | 0.045776 | 0.068665 | -0.24262 | -0.17395 | 0.19226 | 0.18768 | 0.15106 | 0.11902 | 0.082397 | 0.1648 | 121.5591 | 0.1236 | 121.2936 | 121.225 | 121.225 | 121.3394 | 121.2936 | -121.4218 | -121.4676 | 121.6736 | 121.3623 | 3.4287 | 2.71
861.5469 | 121.6919 | -1.1536 | 120.4102 | 0.0019074 | 0 | 0.063467 | 0.060724 | -0.0012177 | -0.00014304 | -0.001303 | -0.0059205 | 0.001617 | -1.3967 | 0.065452 | -0.0051954 | 0.0084851 | -0.0045075 | 2.2842 | 120.195 | -1.03 | 120.5338 | -0.87891 | -0.99792 | -1.0529 | 1.5289 | 120.1263 | -1.0986 | 120.1996 | -0.98419 | -1.0117 | -0.97504 | 0.1236 | -0.21515 | 0.1236 | 0.27466 | 0.10071 | 0.15564 | -0.022888 | 0.032043 | 0.054931 | -0.28381 | -0.21057 | 0.16937 | 0.17853 | 0.14191 | 0.1236 | 0.086975 | 0.15106 | 121.5637 | 0.11444 | 121.2982 | 121.225 | 121.225 | 121.3486 | 121.2799 | -121.4401 | -121.5088 | 121.6873 | 121.3531 | 3.4378 | 2.6825
863.2969 | 121.5912 | -1.181 | 120.4514 | 0.047683 | 0 | 0.063467 | 0.06692 | 0.0064727 | -0.001852 | 0.0025422 | 0.01239 | 0.003967 | -1.3922 | 0.063529 | -0.005409 | 0.0080579 | 0.00061949 | 2.2842 | 120.2591 | -1.0941 | 120.4376 | -1.0117 | -1.0666 | -1.1169 | 1.4191 | 120.2133 | -1.1261 | 120.1172 | -1.0803 | -1.1169 | -1.0391 | 0.086975 | -0.19226 | -0.013733 | 0.16937 | 0.064087 | 0.11444 | -0.022888 | 0.027466 | 0.054931 | -0.23804 | -0.33417 | 0.10071 | 0.14191 | 0.064087 | 0.086975 | 0.009156 | 0.082397 | 121.5317 | 0.045777 | 121.2433 | 121.3531 | 121.3394 | 121.4401 | 121.3943 | -121.5454 | -121.5775 | 121.6187 | 121.2982 | 3.4653 | 2.6001
865.0156 | 121.6278 | -1.1581 | 120.4651 | 0.047683 | 0 | 0.065817 | 0.065638 | 0.0026275 | -0.0039884 | 0.0025422 | 0.0093383 | 0.0011898 | -1.3946 | 0.062461 | -0.0037 | 0.0078443 | -0.00087591 | 2.3209 | 120.3094 | -1.0757 | 120.4697 | -0.97504 | -1.0391 | -1.1032 | 1.4786 | 120.2133 | -1.1124 | 120.1767 | -1.0208 | -1.0712 | -0.98877 | 0.082397 | -0.15564 | 0.004578 | 0.1831 | 0.054932 | 0.11902 | -0.027465 | 0.036621 | 0.045776 | -0.25177 | -0.28839 | 0.13733 | 0.16937 | 0.086975 | 0.1236 | 0.041199 | 0.10071 | 121.5454 | 0.091553 | 121.2891 | 121.3852 | 121.3257 | 121.4676 | 121.3715 | -121.5408 | -121.5775 | 121.6278 | 121.3348 | 3.479 | 2.6367
866.7812 | 121.5775 | -1.1673 | 120.4788 | 0.0019074 | 0 | 0.064322 | 0.064783 | 0.0030547 | -0.00099764 | -0.0010894 | -0.0028687 | 0.001617 | -1.3955 | 0.060325 | -6.8386e-05 | 0.0095533 | -0.0040801 | 2.2156 | 120.3369 | -1.0391 | 120.4102 | -1.0345 | -1.1353 | -1.1581 | 1.3824 | 120.195 | -1.0803 | 120.1492 | -1.1124 | -1.149 | -1.0345 | 0.12817 | -0.14191 | -0.068665 | 0.13275 | 0.009155 | 0.032043 | -0.11902 | -0.09613 | 0.086975 | -0.28381 | -0.32959 | 0.054931 | 0.13275 | 0.01831 | 0.045776 | -0.068665 | 0.004578 | 121.4493 | -0.032044 | 121.2296 | 121.376 | 121.2753 | 121.5042 | 121.3623 | -121.5179 | -121.5591 | 121.5775 | 121.3165 | 3.3829 | 2.5497
868.5469 | 121.6873 | -1.0666 | 120.5109 | 0.0095369 | 0 | 0.064536 | 0.063288 | 0.0032685 | -0.001852 | -0.0032256 | 0.00018312 | 0.00054904 | -1.3963 | 0.068443 | -0.0015638 | 0.0095533 | 0.0014741 | 2.2476 | 120.3415 | -0.95673 | 120.5566 | -0.8606 | -0.9613 | -1.0025 | 1.474 | 120.2454 | -0.99792 | 120.282 | -0.91553 | -0.93842 | -0.89722 | 0.10986 | -0.16937 | 0.045777 | 0.20599 | 0.064087 | 0.10528 | -0.045776 | -0.004578 | 0.068664 | -0.2655 | -0.22888 | 0.15106 | 0.16937 | 0.12817 | 0.10071 | 0.059509 | 0.09613 | 121.5134 | 0.082398 | 121.2799 | 121.2982 | 121.2433 | 121.4081 | 121.3119 | -121.4676 | -121.5088 | 121.6232 | 121.3486 | 3.3142 | 2.5406
870.2969 | 121.6003 | -1.0529 | 120.5612 | -0.0057221 | 0 | 0.063681 | 0.064142 | -0.0024995 | -0.001852 | -0.00044863 | -0.0028687 | 0.00054904 | -1.3946 | 0.060752 | -0.005409 | 0.0089123 | -0.00066231 | 2.2751 | 120.3644 | -0.93384 | 120.5566 | -0.87891 | -0.97046 | -1.0162 | 1.4511 | 120.3003 | -0.98419 | 120.2271 | -0.9613 | -0.99792 | -0.94299 | 0.11902 | -0.19684 | -0.004577 | 0.17395 | 0.036621 | 0.082397 | -0.082397 | -0.036621 | 0.068664 | -0.26093 | -0.33417 | 0.091552 | 0.10986 | 0.054931 | 0.041199 | -0.013733 | 0.054932 | 121.4905 | 0.022888 | 121.2112 | 121.2982 | 121.2845 | 121.4172 | 121.3531 | -121.4951 | -121.5454 | 121.6095 | 121.2799 | 3.3279 | 2.504
872 | 121.6141 | -1.0712 | 120.5795 | 0.047683 | 0 | 0.064536 | 0.065424 | -0.0022857 | -0.0014248 | 0.0016876 | 0.015442 | 0.003326 | -1.3927 | 0.061393 | -0.0037 | 0.0086987 | 0.0012603 | 2.3071 | 120.4193 | -0.96588 | 120.5521 | -0.87433 | -0.97504 | -0.99792 | 1.4786 | 120.3278 | -1.0208 | 120.2362 | -0.97046 | -0.99335 | -0.92926 | 0.10529 | -0.16022 | -0.027466 | 0.19684 | 0.073242 | 0.09613 | -0.032044 | -0.009156 | 0.050354 | -0.25177 | -0.34332 | 0.10071 | 0.14191 | 0.07782 | 0.091553 | 0.027466 | 0.091552 | 121.5179 | 0.050354 | 121.257 | 121.3852 | 121.3486 | 121.4905 | 121.3989 | -121.5454 | -121.6003 | 121.6232 | 121.3074 | 3.3783 | 2.5497
873.7656 | 121.7056 | -0.96588 | 120.6024 | 0.0019074 | 0 | 0.063467 | 0.063502 | 0.0032685 | -0.0027066 | -0.001944 | -0.0059205 | 0.00097624 | -1.3955 | 0.070152 | -0.00049559 | 0.0078443 | -0.00087591 | 2.2614 | 120.4376 | -0.8606 | 120.6573 | -0.79193 | -0.91095 | -0.93842 | 1.5106 | 120.3415 | -0.91095 | 120.401 | -0.82855 | -0.87891 | -0.7782 | 0.10528 | -0.16479 | 0.054932 | 0.17395 | 0.027465 | 0.054931 | -0.07782 | -0.050354 | 0.054931 | -0.26093 | -0.20142 | 0.13733 | 0.18768 | 0.086975 | 0.13275 | 0.032044 | 0.068665 | 121.5179 | 0.082398 | 121.312 | 121.2982 | 121.2524 | 121.4035 | 121.3074 | -121.463 | -121.5134 | 121.6232 | 121.3669 | 3.2272 | 2.4765
875.4844 | 121.6461 | -0.94299 | 120.6757 | 0.017166 | 0 | 0.06304 | 0.065424 | 0.0013459 | -0.0012112 | -0.00066223 | 0.0032349 | 0.0046078 | -1.3946 | 0.055198 | -0.0028454 | 0.0084851 | -0.00023491 | 2.3712 | 120.4697 | -0.85602 | 120.7077 | -0.737 | -0.85144 | -0.89264 | 1.5564 | 120.3781 | -0.90179 | 120.4056 | -0.82855 | -0.8606 | -0.79651 | 0.086975 | -0.20599 | 0.032044 | 0.20599 | 0.050354 | 0.091553 | -0.036621 | 0.004578 | 0.041199 | -0.29755 | -0.27008 | 0.11444 | 0.14648 | 0.082397 | 0.10528 | 0.041198 | 0.11902 | 121.5637 | 0.073242 | 121.3074 | 121.3257 | 121.2799 | 121.4127 | 121.3211 | -121.5317 | -121.5775 | 121.6507 | 121.3486 | 3.3142 | 2.4994
877.25 | 121.669 | -0.91095 | 120.6757 | 0.017166 | 0 | 0.065604 | 0.062647 | 0.0013459 | -0.0029202 | -0.0021576 | 0.0032349 | -0.00030556 | -1.3935 | 0.06652 | -0.0022046 | 0.0097669 | -0.0013031 | 2.3117 | 120.5109 | -0.78735 | 120.726 | -0.71411 | -0.79193 | -0.85144 | 1.4969 | 120.3964 | -0.84686 | 120.4193 | -0.79193 | -0.81024 | -0.74616 | 0.1236 | -0.16479 | 0.050354 | 0.19684 | 0.05951 | 0.11902 | -0.064086 | -0.004577 | 0.064087 | -0.27924 | -0.25635 | 0.11902 | 0.1648 | 0.10071 | 0.10071 | 0.036621 | 0.073243 | 121.5134 | 0.054932 | 121.2662 | 121.2982 | 121.2433 | 121.4218 | 121.3074 | -121.463 | -121.5225 | 121.637 | 121.3303 | 3.2227 | 2.4078
879.0312 | 121.6003 | -0.89722 | 120.7031 | 0.0095369 | 0 | 0.061118 | 0.066065 | -0.00014949 | -0.0012112 | 0.0012604 | 0.01239 | 0.0026852 | -1.395 | 0.065452 | -0.0069044 | 0.010408 | 0.0029693 | 2.3254 | 120.5521 | -0.81482 | 120.7077 | -0.71869 | -0.79651 | -0.82855 | 1.4923 | 120.5017 | -0.86517 | 120.3827 | -0.83313 | -0.85602 | -0.76904 | 0.082398 | -0.15106 | 0.004578 | 0.17853 | 0.068665 | 0.10071 | -0.013733 | 0.01831 | 0.032044 | -0.20142 | -0.32044 | 0.064087 | 0.12817 | 0.041199 | 0.09613 | 0.009155 | 0.09613 | 121.5225 | 0.032043 | 121.2479 | 121.3669 | 121.3669 | 121.4493 | 121.3989 | -121.5179 | -121.5683 | 121.6049 | 121.2799 | 3.2227 | 2.3895
880.8125 | 121.6324 | -0.89722 | 120.7214 | 0.078201 | 0 | 0.064963 | 0.065424 | 0.0015595 | -0.00099764 | 0.00040597 | 0.015442 | 0.0052486 | -1.3925 | 0.056053 | -0.0041272 | 0.0078443 | 0.0027557 | 2.3804 | 120.575 | -0.81482 | 120.7306 | -0.72784 | -0.79193 | -0.83771 | 1.5015 | 120.5017 | -0.86517 | 120.4193 | -0.7782 | -0.83313 | -0.75989 | 0.082398 | -0.14648 | 0.009155 | 0.16937 | 0.059509 | 0.10529 | -0.022889 | 0.022888 | 0.032044 | -0.21973 | -0.30212 | 0.11902 | 0.13733 | 0.064087 | 0.10528 | 0.032043 | 0.086975 | 121.5454 | 0.086975 | 121.2845 | 121.3898 | 121.3669 | 121.4722 | 121.3989 | -121.5363 | -121.5866 | 121.6278 | 121.3165 | 3.2776 | 2.3987
882.5156 | 121.7239 | -0.82398 | 120.694 | -0.013352 | 0 | 0.065817 | 0.063929 | -0.0018585 | -0.0016384 | 0.00040597 | 0.00018312 | 0.0011898 | -1.3959 | 0.067588 | 0.001427 | 0.010194 | -0.00087591 | 2.3849 | 120.5338 | -0.72327 | 120.8176 | -0.6134 | -0.74616 | -0.7782 | 1.6022 | 120.433 | -0.80109 | 120.5429 | -0.70038 | -0.73242 | -0.6546 | 0.10071 | -0.16022 | 0.1236 | 0.21057 | 0.045777 | 0.07782 | -0.054931 | -0.022888 | 0.022889 | -0.26093 | -0.15106 | 0.1236 | 0.16937 | 0.091553 | 0.14648 | 0.068664 | 0.10986 | 121.5408 | 0.10071 | 121.344 | 121.257 | 121.2341 | 121.3577 | 121.257 | -121.4172 | -121.4951 | 121.6415 | 121.3669 | 3.2089 | 2.4261
884.2812 | 121.6141 | -0.87433 | 120.726 | 0.0019074 | 0 | 0.063467 | 0.066279 | -0.00014949 | -0.0012112 | -0.00044863 | -0.0089723 | 0.0026852 | -1.3961 | 0.060539 | -0.0028454 | 0.010408 | -0.0013031 | 2.33 | 120.5795 | -0.77362 | 120.7077 | -0.75989 | -0.85602 | -0.88348 | 1.4648 | 120.4971 | -0.80566 | 120.4193 | -0.81024 | -0.84686 | -0.75073 | 0.10071 | -0.14648 | -0.01831 | 0.11444 | -0.009155 | 0.018311 | -0.10986 | -0.082397 | 0.068665 | -0.22888 | -0.3067 | 0.064087 | 0.1236 | 0.027466 | 0.054932 | -0.041199 | 0.013733 | 121.4813 | -0.004578 | 121.225 | 121.3531 | 121.3028 | 121.4539 | 121.3715 | -121.4996 | -121.5317 | 121.582 | 121.2936 | 3.2043 | 2.3392
886.0469 | 121.6736 | -0.84228 | 120.7443 | 0.0095369 | 0 | 0.06069 | 0.063074 | 0.0017731 | 7.0564e-05 | -2.1434e-05 | -0.0028687 | 0.00012184 | -1.3957 | 0.063957 | -0.0037 | 0.0074171 | -0.0030121 | 2.417 | 120.52 | -0.70953 | 120.845 | -0.58136 | -0.68207 | -0.73242 | 1.593 | 120.4468 | -0.75989 | 120.5154 | -0.67749 | -0.70496 | -0.67291 | 0.13275 | -0.2243 | 0.10071 | 0.26092 | 0.10986 | 0.16022 | -0.022888 | 0.027466 | 0.082397 | -0.29755 | -0.22888 | 0.16479 | 0.16937 | 0.13733 | 0.086975 | 0.054932 | 0.12817 | 121.5546 | 0.082398 | 121.2753 | 121.2296 | 121.2067 | 121.3623 | 121.2891 | -121.4539 | -121.5042 | 121.6873 | 121.3577 | 3.2593 | 2.4353
887.75 | 121.6827 | -0.81482 | 120.7352 | 0.055313 | 0 | 0.064749 | 0.064356 | 0.00049131 | -0.00035684 | 0.00083317 | 0.018494 | 0.00097624 | -1.3946 | 0.06652 | -6.8386e-05 | 0.011689 | -0.0015167 | 2.3987 | 120.5887 | -0.71869 | 120.8725 | -0.53101 | -0.67291 | -0.72327 | 1.6388 | 120.5154 | -0.75531 | 120.5521 | -0.66376 | -0.6958 | -0.64545 | 0.09613 | -0.14648 | 0.13733 | 0.28381 | 0.091552 | 0.14191 | -0.004578 | 0.045776 | 0.059509 | -0.21973 | -0.1831 | 0.15106 | 0.16937 | 0.11902 | 0.10986 | 0.059509 | 0.18768 | 121.5912 | 0.091553 | 121.3074 | 121.3074 | 121.2708 | 121.4035 | 121.3303 | -121.4539 | -121.4905 | 121.6873 | 121.3669 | 3.2135 | 2.4536
889.5 | 121.6278 | -0.80566 | 120.8221 | 0.017166 | 0 | 0.063467 | 0.066065 | 0.0049773 | -0.0037746 | -0.003012 | 0.0032349 | 0.005035 | -1.3944 | 0.071647 | -0.0037 | 0.0091261 | -0.0017303 | 2.4307 | 120.6253 | -0.6958 | 120.8267 | -0.6134 | -0.71411 | -0.77362 | 1.593 | 120.5475 | -0.74616 | 120.4971 | -0.71411 | -0.75989 | -0.68665 | 0.10986 | -0.19684 | 0.004577 | 0.19226 | 0.032043 | 0.091553 | -0.07782 | -0.01831 | 0.059509 | -0.27466 | -0.32501 | 0.091553 | 0.11902 | 0.045776 | 0.059509 | -0.013733 | 0.082398 | 121.5225 | 0.032044 | 121.2433 | 121.3211 | 121.2936 | 121.431 | 121.3531 | -121.5179 | -121.5683 | 121.6324 | 121.3028 | 3.2364 | 2.3987
891.2812 | 121.582 | -0.82398 | 120.8176 | -0.0057221 | 0 | 0.063681 | 0.063288 | 0.0041229 | -0.0027066 | 0.00019217 | 0.00018312 | 0.0018306 | -1.3957 | 0.063529 | -0.0032728 | 0.011262 | 0.00083309 | 2.3758 | 120.6573 | -0.70038 | 120.7535 | -0.71869 | -0.81482 | -0.81482 | 1.4694 | 120.5383 | -0.73242 | 120.4834 | -0.76904 | -0.81024 | -0.69122 | 0.1236 | -0.16022 | -0.064087 | 0.10529 | 0.009156 | 0.009156 | -0.11444 | -0.11444 | 0.091553 | -0.27924 | -0.33417 | 0.054932 | 0.13275 | 0.013733 | 0.041199 | -0.07782 | -0.018311 | 121.4539 | -0.036621 | 121.2158 | 121.3577 | 121.2708 | 121.4813 | 121.3623 | -121.5179 | -121.55 | 121.5775 | 121.3074 | 3.1998 | 2.2934
893.0469 | 121.7239 | -0.76446 | 120.8038 | 0.0019074 | 0 | 0.064749 | 0.064142 | 0.0022003 | 0.00071136 | 0.002115 | -0.0028687 | -0.00030556 | -1.3957 | 0.069084 | -0.0045544 | 0.011262 | 0.0033967 | 2.3712 | 120.6116 | -0.6546 | 120.8633 | -0.55389 | -0.6546 | -0.68207 | 1.5656 | 120.5429 | -0.70496 | 120.6024 | -0.59967 | -0.63629 | -0.58594 | 0.10986 | -0.19226 | 0.059509 | 0.21057 | 0.082397 | 0.10986 | -0.027466 | 0 | 0.059509 | -0.26093 | -0.20142 | 0.16479 | 0.17853 | 0.12817 | 0.11902 | 0.068664 | 0.10071 | 121.5179 | 0.10529 | 121.3074 | 121.2662 | 121.2479 | 121.376 | 121.3074 | -121.4584 | -121.5088 | 121.6278 | 121.3669 | 3.1357 | 2.33
894.7656 | 121.7422 | -0.75531 | 120.8176 | 0.0019074 | 0 | 0.063254 | 0.062433 | 0.00027771 | -0.0031338 | -2.1434e-05 | -0.0028687 | -0.00051916 | -1.3946 | 0.062675 | -0.0015638 | 0.0089123 | 0.0014741 | 2.4307 | 120.6345 | -0.60425 | 120.9412 | -0.48065 | -0.58136 | -0.63629 | 1.6846 | 120.5521 | -0.67749 | 120.6573 | -0.54016 | -0.57678 | -0.56763 | 0.15106 | -0.18311 | 0.1236 | 0.27466 | 0.11902 | 0.17395 | -0.032044 | 0.022888 | 0.07782 | -0.2655 | -0.16022 | 0.21515 | 0.18768 | 0.17853 | 0.10986 | 0.10071 | 0.1236 | 121.5454 | 0.13733 | 121.3348 | 121.2387 | 121.2296 | 121.3898 | 121.3074 | -121.4218 | -121.4951 | 121.6965 | 121.4127 | 3.186 | 2.4399
896.5156 | 121.7377 | -0.73242 | 120.8359 | 0.0019074 | 0 | 0.063254 | 0.062647 | -0.0014313 | -0.0027066 | -0.0010894 | 0.00018312 | -0.001801 | -1.3976 | 0.061179 | -0.0051954 | 0.0093397 | -0.00023491 | 2.4628 | 120.639 | -0.60425 | 120.9686 | -0.45319 | -0.56305 | -0.62714 | 1.6754 | 120.5566 | -0.65918 | 120.6619 | -0.53101 | -0.56763 | -0.53558 | 0.12817 | -0.19684 | 0.13275 | 0.27924 | 0.10529 | 0.16937 | -0.022888 | 0.041199 | 0.073242 | -0.27923 | -0.17395 | 0.20142 | 0.19684 | 0.1648 | 0.1236 | 0.091553 | 0.15106 | 121.5729 | 0.12817 | 121.3211 | 121.2433 | 121.2158 | 121.3715 | 121.2891 | -121.4401 | -121.4951 | 121.701 | 121.3943 | 3.1952 | 2.4078
898.2812 | 121.7148 | -0.71411 | 120.8359 | 0.0019074 | 0 | 0.064108 | 0.063502 | -0.0027131 | -0.00014304 | 0.001474 | -0.0028687 | -9.1956e-05 | -1.398 | 0.068015 | 0.00078621 | 0.010408 | -0.0017303 | 2.4582 | 120.6482 | -0.63171 | 120.932 | -0.51727 | -0.62256 | -0.69122 | 1.6571 | 120.5292 | -0.67749 | 120.6436 | -0.5722 | -0.63171 | -0.54932 | 0.082397 | -0.18768 | 0.096131 | 0.19684 | 0.022888 | 0.091552 | -0.059509 | 0.009155 | 0.036621 | -0.3067 | -0.19226 | 0.14191 | 0.1648 | 0.082397 | 0.12817 | 0.045776 | 0.11444 | 121.5637 | 0.10529 | 121.3211 | 121.2799 | 121.2067 | 121.3623 | 121.2433 | -121.4676 | -121.5134 | 121.6461 | 121.3577 | 3.1723 | 2.3712
899.9844 | 121.6415 | -0.7782 | 120.8221 | 0.017166 | 0 | 0.063895 | 0.068201 | -0.0014313 | -0.0037746 | -0.0017304 | 0.0062865 | 0.0041806 | -1.3944 | 0.061607 | -0.0045544 | 0.0067761 | -0.0010895 | 2.5085 | 120.6848 | -0.6546 | 120.9 | -0.56305 | -0.64545 | -0.6958 | 1.6205 | 120.6024 | -0.70496 | 120.5795 | -0.63171 | -0.68665 | -0.60425 | 0.1236 | -0.13733 | 0.077819 | 0.21515 | 0.082397 | 0.13275 | -0.041199 | 0.009155 | 0.073242 | -0.21973 | -0.24262 | 0.14648 | 0.17395 | 0.091552 | 0.10071 | 0.01831 | 0.091553 | 121.5546 | 0.073242 | 121.2845 | 121.3394 | 121.3074 | 121.463 | 121.3806 | -121.4767 | -121.5271 | 121.6782 | 121.3577 | 3.2867 | 2.3987
901.7656 | 121.6599 | -0.74158 | 120.8405 | 0.0019074 | 0 | 0.064749 | 0.063288 | -0.0039947 | -0.004202 | -0.0015166 | -0.0059205 | 0.0020444 | -1.3946 | 0.066947 | -0.004768 | 0.0072035 | -0.0032257 | 2.4948 | 120.6436 | -0.58594 | 120.9457 | -0.48065 | -0.5722 | -0.63171 | 1.6479 | 120.5887 | -0.65918 | 120.6116 | -0.59052 | -0.62714 | -0.58594 | 0.15564 | -0.19684 | 0.10529 | 0.26093 | 0.10986 | 0.16937 | -0.045777 | 0.013732 | 0.082397 | -0.25177 | -0.22888 | 0.15106 | 0.15564 | 0.11444 | 0.073243 | 0.032044 | 0.10529 | 121.5317 | 0.068665 | 121.2708 | 121.2296 | 121.2479 | 121.3852 | 121.3303 | -121.4264 | -121.4996 | 121.6873 | 121.3531 | 3.2364 | 2.3895
903.5156 | 121.6919 | -0.73242 | 120.8405 | 0.0095369 | 0 | 0.065176 | 0.063715 | -0.0010041 | -0.0022794 | -0.0025848 | 0.00018312 | 0.00033544 | -1.3952 | 0.065025 | -0.0022046 | 0.0082715 | 0.0021149 | 2.449 | 120.6848 | -0.59967 | 120.9183 | -0.54474 | -0.62714 | -0.66376 | 1.5976 | 120.5612 | -0.67291 | 120.6253 | -0.59052 | -0.60883 | -0.55847 | 0.13275 | -0.15564 | 0.07782 | 0.18768 | 0.068665 | 0.10529 | -0.064087 | -0.027466 | 0.059509 | -0.27924 | -0.21515 | 0.14191 | 0.17395 | 0.1236 | 0.11444 | 0.064087 | 0.054931 | 121.5179 | 0.082398 | 121.2982 | 121.2845 | 121.2341 | 121.4172 | 121.2936 | -121.4401 | -121.5134 | 121.6507 | 121.3577 | 3.1815 | 2.33
905.2188 | 121.6049 | -0.74158 | 120.8771 | -0.0057221 | 0 | 0.064108 | 0.065851 | -0.0042083 | -0.0016384 | -0.00066223 | -0.0059205 | 0.0018306 | -1.3963 | 0.05947 | -0.0022046 | 0.0059217 | -0.0019439 | 2.5131 | 120.694 | -0.64545 | 120.8908 | -0.54932 | -0.67291 | -0.70038 | 1.6205 | 120.6207 | -0.67749 | 120.575 | -0.64087 | -0.71411 | -0.59967 | 0.09613 | -0.18311 | 0.013733 | 0.19226 | 0.041199 | 0.068664 | -0.054931 | -0.027466 | 0.064087 | -0.25635 | -0.30212 | 0.10071 | 0.14191 | 0.027466 | 0.07782 | -0.036621 | 0.096131 | 121.5363 | 0.036621 | 121.2524 | 121.3394 | 121.2982 | 121.4355 | 121.3623 | -121.5225 | -121.5546 | 121.6324 | 121.3165 | 3.2547 | 2.3621
906.9844 | 121.5958 | -0.75989 | 120.8862 | 0.0095369 | 0 | 0.064963 | 0.06692 | 0.0022003 | -0.002493 | -0.0023712 | 0.00018312 | 0.0041806 | -1.395 | 0.058402 | -0.0028454 | 0.0089123 | 0.0027557 | 2.4445 | 120.7397 | -0.61798 | 120.8176 | -0.62714 | -0.72327 | -0.75531 | 1.5335 | 120.6253 | -0.68207 | 120.5521 | -0.70038 | -0.72784 | -0.62714 | 0.14191 | -0.14648 | -0.068664 | 0.13275 | 0.004578 | 0.036621 | -0.13733 | -0.10529 | 0.07782 | -0.26093 | -0.33417 | 0.05951 | 0.13275 | 0.032044 | 0.054932 | -0.045776 | -0.009155 | 121.4355 | -0.01831 | 121.2341 | 121.3577 | 121.3074 | 121.4996 | 121.3852 | -121.5042 | -121.5683 | 121.5775 | 121.312 | 3.2043 | 2.2934
908.7656 | 121.6965 | -0.70953 | 120.8313 | -0.013352 | 0 | 0.062399 | 0.062861 | 0.00070491 | -0.0022794 | -0.00044863 | -0.0059205 | 0.00033544 | -1.3963 | 0.063102 | -0.0049818 | 0.0059217 | 0.0040375 | 2.5131 | 120.6848 | -0.59967 | 120.9915 | -0.44403 | -0.55847 | -0.60425 | 1.68 | 120.5933 | -0.63629 | 120.6711 | -0.52185 | -0.55847 | -0.53101 | 0.10986 | -0.14648 | 0.16022 | 0.2655 | 0.10529 | 0.15106 | -0.004578 | 0.041198 | 0.073242 | -0.23804 | -0.16022 | 0.18768 | 0.17853 | 0.15106 | 0.10529 | 0.07782 | 0.15564 | 121.5912 | 0.11444 | 121.3074 | 121.2845 | 121.2296 | 121.3943 | 121.3028 | -121.431 | -121.4676 | 121.7011 | 121.3806 | 3.2227 | 2.3895
910.4844 | 121.7102 | -0.70953 | 120.8817 | -0.0057221 | 0 | 0.06304 | 0.064356 | 0.0022003 | -0.0012112 | -0.00087583 | -0.0028687 | 0.00054904 | -1.3974 | 0.060966 | 0.00057241 | 0.0089123 | -2.1314e-05 | 2.4536 | 120.7169 | -0.60883 | 120.9091 | -0.53101 | -0.6546 | -0.67749 | 1.6296 | 120.5933 | -0.64545 | 120.6528 | -0.55847 | -0.59509 | -0.52643 | 0.10071 | -0.16479 | 0.027466 | 0.17853 | 0.032044 | 0.054932 | -0.068664 | -0.045776 | 0.064087 | -0.28839 | -0.22888 | 0.15106 | 0.18311 | 0.11444 | 0.11902 | 0.050354 | 0.07782 | 121.5179 | 0.086975 | 121.2982 | 121.3257 | 121.2387 | 121.4264 | 121.3028 | -121.4905 | -121.5271 | 121.6187 | 121.3623 | 3.1631 | 2.3392
912.2344 | 121.7377 | -0.70038 | 120.845 | -0.0057221 | 0 | 0.064322 | 0.062006 | 0.00091851 | -0.0048428 | -0.0017304 | -0.0028687 | 0.0014034 | -1.3972 | 0.066947 | -0.0011364 | 0.0082715 | 0.00040589 | 2.5543 | 120.6802 | -0.56763 | 121.0144 | -0.42572 | -0.52185 | -0.59052 | 1.7075 | 120.5933 | -0.6134 | 120.6757 | -0.50812 | -0.54474 | -0.5127 | 0.13275 | -0.16479 | 0.16937 | 0.27466 | 0.10986 | 0.17853 | -0.022888 | 0.045776 | 0.086975 | -0.25177 | -0.16937 | 0.19226 | 0.18768 | 0.15564 | 0.10071 | 0.068664 | 0.14191 | 121.582 | 0.10529 | 121.2891 | 121.2479 | 121.2067 | 121.3806 | 121.2936 | -121.4127 | -121.4584 | 121.7148 | 121.376 | 3.2547 | 2.4078
914 | 121.7377 | -0.69122 | 120.8588 | -0.0057221 | 0 | 0.062399 | 0.061793 | -0.0031403 | -0.0037746 | -0.00087583 | -0.0028687 | 0.00012184 | -1.3955 | 0.060752 | -0.0043408 | 0.011476 | 0.0014741 | 2.5497 | 120.6848 | -0.56305 | 121.0327 | -0.41657 | -0.53558 | -0.5722 | 1.6937 | 120.6207 | -0.63629 | 120.6802 | -0.50354 | -0.52185 | -0.49896 | 0.12817 | -0.17395 | 0.17395 | 0.27466 | 0.11902 | 0.15564 | -0.009156 | 0.027466 | 0.054931 | -0.23804 | -0.17853 | 0.18768 | 0.19226 | 0.16937 | 0.13733 | 0.11444 | 0.14648 | 121.5958 | 0.13275 | 121.3165 | 121.2479 | 121.257 | 121.376 | 121.312 | -121.4218 | -121.4951 | 121.7239 | 121.3715 | 3.241 | 2.3849
915.7031 | 121.7239 | -0.69122 | 120.8771 | -0.0057221 | 0 | 0.06304 | 0.060724 | -0.0027131 | -0.0048428 | 0.00019217 | 0.00018312 | -0.00116 | -1.3952 | 0.063102 | -0.0058362 | 0.0086987 | 0.0016877 | 2.5452 | 120.6894 | -0.56305 | 121.0144 | -0.39825 | -0.5127 | -0.56305 | 1.7303 | 120.6116 | -0.60425 | 120.6757 | -0.50812 | -0.55389 | -0.5127 | 0.12817 | -0.18768 | 0.13733 | 0.29297 | 0.12817 | 0.17853 | 0 | 0.050354 | 0.086975 | -0.2655 | -0.20142 | 0.18311 | 0.17853 | 0.13733 | 0.091553 | 0.050354 | 0.1648 | 121.5775 | 0.09613 | 121.2799 | 121.2524 | 121.2158 | 121.3806 | 121.3028 | -121.4401 | -121.4813 | 121.7056 | 121.3669 | 3.2364 | 2.4216
917.4531 | 121.5912 | -0.70953 | 120.9229 | -0.0057221 | 0 | 0.064749 | 0.065638 | 0.0011321 | -0.0022794 | -0.0015166 | 0.00018312 | 0.005035 | -1.3952 | 0.055839 | -0.0024182 | 0.0076307 | -0.0025849 | 2.4948 | 120.7672 | -0.58594 | 120.8588 | -0.58594 | -0.66834 | -0.70038 | 1.5244 | 120.7031 | -0.63629 | 120.5933 | -0.65002 | -0.70496 | -0.59509 | 0.1236 | -0.15564 | -0.064087 | 0.1236 | 0.009156 | 0.041199 | -0.11444 | -0.082398 | 0.073242 | -0.21973 | -0.32959 | 0.05951 | 0.11444 | 0.004578 | 0.041199 | -0.068664 | 0 | 121.4447 | -0.013732 | 121.2296 | 121.3531 | 121.3394 | 121.4767 | 121.4127 | -121.5088 | -121.5591 | 121.5683 | 121.3028 | 3.2043 | 2.2339
919.2188 | 121.7422 | -0.68207 | 120.845 | -0.0057221 | 0 | 0.062613 | 0.062647 | -0.0042083 | -0.0012112 | -0.0034392 | 0.0032349 | -0.00051916 | -1.3965 | 0.06652 | -0.0024182 | 0.0069897 | 0.00061949 | 2.5543 | 120.7031 | -0.55389 | 121.0007 | -0.41199 | -0.51727 | -0.56305 | 1.7487 | 120.6345 | -0.61798 | 120.7169 | -0.48065 | -0.50812 | -0.48523 | 0.12817 | -0.14191 | 0.15564 | 0.27008 | 0.11902 | 0.1648 | -0.009155 | 0.036621 | 0.064087 | -0.21057 | -0.12817 | 0.20142 | 0.19684 | 0.17395 | 0.13275 | 0.10986 | 0.14191 | 121.5546 | 0.13733 | 121.3348 | 121.257 | 121.2524 | 121.3852 | 121.3165 | -121.3989 | -121.463 | 121.6827 | 121.3989 | 3.2364 | 2.4307
920.9375 | 121.6461 | -0.68665 | 120.9274 | 0.024795 | 0 | 0.064322 | 0.067988 | 6.4114e-05 | 7.0564e-05 | 0.001474 | 0.0062865 | 0.003326 | -1.3965 | 0.063743 | -0.0037 | 0.0084851 | -0.0010895 | 2.623 | 120.7718 | -0.58594 | 120.9686 | -0.47607 | -0.58136 | -0.62714 | 1.6937 | 120.6894 | -0.64087 | 120.6573 | -0.56305 | -0.59967 | -0.52643 | 0.10071 | -0.15564 | 0.041199 | 0.21057 | 0.05951 | 0.10529 | -0.041199 | 0.004577 | 0.045777 | -0.23804 | -0.27008 | 0.1236 | 0.16022 | 0.086976 | 0.11444 | 0.041199 | 0.10986 | 121.5546 | 0.07782 | 121.2982 | 121.3577 | 121.3303 | 121.4584 | 121.376 | -121.5134 | -121.5683 | 121.6553 | 121.344 | 3.3096 | 2.3804
922.7031 | 121.5912 | -0.6958 | 120.9732 | 0.0019074 | 0 | 0.063681 | 0.064142 | 0.0045501 | -0.0020658 | -0.00087583 | 0.00018312 | 0.002258 | -1.3937 | 0.067588 | -0.003059 | 0.0065625 | 0.00019229 | 2.5681 | 120.8084 | -0.55847 | 120.9229 | -0.55389 | -0.65002 | -0.68207 | 1.5564 | 120.6802 | -0.62256 | 120.6024 | -0.63629 | -0.67749 | -0.56763 | 0.13733 | -0.16479 | -0.050354 | 0.14191 | 0.013733 | 0.045777 | -0.1236 | -0.091552 | 0.073242 | -0.29297 | -0.37079 | 0.059509 | 0.12817 | 0.018311 | 0.054932 | -0.054931 | 0.004578 | 121.4813 | -0.013733 | 121.225 | 121.3669 | 121.3028 | 121.5042 | 121.376 | -121.5317 | -121.5958 | 121.6187 | 121.2982 | 3.2639 | 2.2522
924.3906 | 121.5912 | -0.68665 | 120.9641 | -0.0057221 | 0 | 0.063254 | 0.064997 | -0.0048493 | -0.0031338 | 0.00083317 | -0.0059205 | 0.00097624 | -1.3942 | 0.05947 | -0.0062634 | 0.0072035 | -0.0036529 | 2.5452 | 120.7581 | -0.56305 | 120.9045 | -0.53101 | -0.59052 | -0.65002 | 1.5518 | 120.7169 | -0.61798 | 120.6116 | -0.58594 | -0.63171 | -0.55389 | 0.1236 | -0.20599 | -0.059509 | 0.15564 | 0.036622 | 0.096131 | -0.086975 | -0.027466 | 0.068665 | -0.24719 | -0.35248 | 0.10071 | 0.13275 | 0.054932 | 0.064087 | -0.013733 | 0.032043 | 121.4676 | 0.032044 | 121.2296 | 121.3211 | 121.3348 | 121.4447 | 121.4035 | -121.5271 | -121.582 | 121.5912 | 121.2982 | 3.2318 | 2.2385
926.1562 | 121.7377 | -0.61798 | 120.9366 | -0.0057221 | 0 | 0.061758 | 0.062433 | 6.4114e-05 | -0.00057044 | -0.001303 | 0.0032349 | 0.00054904 | -1.3957 | 0.068015 | -0.0011364 | 0.010835 | -0.0019439 | 2.5726 | 120.7581 | -0.50812 | 121.0419 | -0.40741 | -0.49439 | -0.54932 | 1.68 | 120.6665 | -0.57678 | 120.7489 | -0.45319 | -0.48065 | -0.45319 | 0.10986 | -0.17853 | 0.10529 | 0.21057 | 0.068665 | 0.1236 | -0.041198 | 0.013733 | 0.041199 | -0.27008 | -0.18768 | 0.1648 | 0.1648 | 0.13733 | 0.1236 | 0.09613 | 0.10071 | 121.55 | 0.1236 | 121.3257 | 121.2662 | 121.2433 | 121.376 | 121.2845 | -121.4447 | -121.5134 | 121.6599 | 121.3669 | 3.1906 | 2.298
927.9062 | 121.5958 | -0.66376 | 120.9732 | 0.062942 | 0 | 0.063681 | 0.066279 | -0.00036309 | -0.0014248 | -0.0015166 | 0.018494 | 0.0046078 | -1.3955 | 0.053275 | -0.004768 | 0.0057081 | 0.0016877 | 2.5955 | 120.845 | -0.5722 | 120.9595 | -0.49896 | -0.58136 | -0.61798 | 1.593 | 120.7535 | -0.6134 | 120.6253 | -0.59509 | -0.61798 | -0.53558 | 0.091552 | -0.12817 | -0.013733 | 0.1648 | 0.045776 | 0.082397 | -0.045776 | -0.009155 | 0.050354 | -0.21973 | -0.3479 | 0.068664 | 0.12817 | 0.045776 | 0.07782 | -0.004578 | 0.073243 | 121.5317 | 0.01831 | 121.2387 | 121.4172 | 121.3669 | 121.5088 | 121.4172 | -121.5454 | -121.5866 | 121.6232 | 121.2891 | 3.2593 | 2.2568
929.6094 | 121.5912 | -0.66376 | 120.9641 | 0.0019074 | 0 | 0.064108 | 0.064783 | 0.0013459 | -0.0039884 | 0.00061957 | -0.0059205 | 0.003967 | -1.3944 | 0.05883 | -0.00028199 | 0.0078443 | -0.00087591 | 2.6001 | 120.7901 | -0.54932 | 120.9366 | -0.50354 | -0.63171 | -0.67291 | 1.5656 | 120.7169 | -0.59509 | 120.6299 | -0.60425 | -0.6546 | -0.54474 | 0.11444 | -0.17395 | -0.027466 | 0.16022 | -0.009156 | 0.032043 | -0.1236 | -0.082398 | 0.068664 | -0.24719 | -0.33417 | 0.059509 | 0.11902 | 0.009155 | 0.050354 | -0.059509 | 0.045776 | 121.4859 | -0.009155 | 121.225 | 121.3394 | 121.312 | 121.4539 | 121.3806 | -121.5134 | -121.5591 | 121.6003 | 121.2936 | 3.2639 | 2.2293
931.375 | 121.6644 | -0.65918 | 120.9641 | 0.0019074 | 0 | 0.066458 | 0.064997 | 0.0017731 | -0.0014248 | -0.0025848 | -0.0059205 | 0.0031124 | -1.3942 | 0.060325 | -0.0011364 | 0.0093397 | -0.0027985 | 2.5772 | 120.8267 | -0.52185 | 120.9274 | -0.50354 | -0.62714 | -0.65002 | 1.5747 | 120.7123 | -0.59509 | 120.6848 | -0.56763 | -0.60883 | -0.50812 | 0.13733 | -0.13733 | -0.036621 | 0.15564 | 0.009156 | 0.032044 | -0.12817 | -0.10529 | 0.064087 | -0.25177 | -0.27924 | 0.091553 | 0.15106 | 0.050354 | 0.086975 | -0.013733 | 0.018311 | 121.4493 | 0.027466 | 121.2799 | 121.3486 | 121.3074 | 121.4859 | 121.3715 | -121.4859 | -121.5591 | 121.5866 | 121.344 | 3.2364 | 2.2339
933.0938 | 121.6919 | -0.63171 | 120.9595 | 0.040054 | 0 | 0.064963 | 0.064356 | 0.0034821 | -0.00099764 | 0.00019217 | 0.018494 | 0.00097624 | -1.3933 | 0.068443 | -0.00049559 | 0.010621 | -0.0015167 | 2.623 | 120.7626 | -0.50812 | 121.051 | -0.3479 | -0.47607 | -0.51727 | 1.7029 | 120.7214 | -0.59052 | 120.7214 | -0.4715 | -0.51727 | -0.4715 | 0.1236 | -0.19684 | 0.091552 | 0.28381 | 0.11444 | 0.15564 | -0.009155 | 0.032044 | 0.041199 | -0.23804 | -0.23804 | 0.16022 | 0.16022 | 0.11444 | 0.11902 | 0.073242 | 0.16022 | 121.5591 | 0.11902 | 121.312 | 121.2708 | 121.312 | 121.3943 | 121.3531 | -121.4676 | -121.55 | 121.6827 | 121.3531 | 3.2547 | 2.3346
934.8594 | 121.6415 | -0.64545 | 120.9732 | 0.024795 | 0 | 0.064963 | 0.065211 | 0.0011321 | -0.0029202 | 0.00061957 | 0.0062865 | 0.0026852 | -1.3952 | 0.05947 | -0.0045544 | 0.0076307 | 0.00061949 | 2.6733 | 120.7993 | -0.54016 | 121.0236 | -0.41657 | -0.53558 | -0.5722 | 1.6983 | 120.7352 | -0.5722 | 120.7077 | -0.49896 | -0.5722 | -0.48065 | 0.10529 | -0.17395 | 0.050354 | 0.22888 | 0.073242 | 0.10986 | -0.032044 | 0.004578 | 0.073242 | -0.23804 | -0.2655 | 0.14648 | 0.16479 | 0.073242 | 0.091553 | 0 | 0.1236 | 121.5637 | 0.073243 | 121.2799 | 121.3394 | 121.3074 | 121.4447 | 121.3806 | -121.5134 | -121.5454 | 121.669 | 121.3531 | 3.3188 | 2.3438
936.625 | 121.6782 | -0.60883 | 120.9732 | 0.017166 | 0 | 0.062613 | 0.063715 | 0.0019867 | -0.0020658 | 0.00040597 | 0.0032349 | 0.0020444 | -1.3959 | 0.065025 | -0.0043408 | 0.0084851 | -0.0010895 | 2.6047 | 120.7947 | -0.50354 | 121.0098 | -0.43488 | -0.52643 | -0.55847 | 1.6296 | 120.726 | -0.5722 | 120.7031 | -0.51727 | -0.53101 | -0.4715 | 0.10529 | -0.17853 | 0.036621 | 0.17395 | 0.050354 | 0.082398 | -0.054932 | -0.022888 | 0.036621 | -0.24719 | -0.27008 | 0.091553 | 0.13733 | 0.07782 | 0.10071 | 0.041199 | 0.068665 | 121.5134 | 0.054932 | 121.2753 | 121.2982 | 121.2982 | 121.4035 | 121.3348 | -121.4767 | -121.5454 | 121.6187 | 121.312 | 3.2135 | 2.2385
938.3906 | 121.6736 | -0.60425 | 121.0007 | 0.0019074 | 0 | 0.064749 | 0.062647 | 0.0024139 | -0.0027066 | -0.00066223 | -0.0028687 | 0.00012184 | -1.3957 | 0.059043 | -0.0045544 | 0.0099805 | -0.0027985 | 2.71 | 120.7672 | -0.46234 | 121.0648 | -0.36621 | -0.43945 | -0.50354 | 1.7212 | 120.726 | -0.54016 | 120.7306 | -0.46234 | -0.49896 | -0.4715 | 0.14191 | -0.23346 | 0.064087 | 0.23804 | 0.10071 | 0.1648 | -0.041199 | 0.022888 | 0.064087 | -0.27466 | -0.27008 | 0.14191 | 0.13275 | 0.10529 | 0.068664 | 0.041199 | 0.09613 | 121.5271 | 0.07782 | 121.2708 | 121.2296 | 121.2662 | 121.3715 | 121.3303 | -121.463 | -121.5408 | 121.669 | 121.3348 | 3.3142 | 2.3254
940.1094 | 121.6095 | -0.63629 | 121.0007 | -0.0057221 | 0 | 0.064108 | 0.065638 | -0.00057689 | -0.00078404 | 0.0012604 | -0.0028687 | 0.0037532 | -1.3937 | 0.057975 | -0.0024182 | 0.0074171 | 0.0019013 | 2.6276 | 120.8496 | -0.49439 | 120.9274 | -0.52185 | -0.61798 | -0.63171 | 1.5976 | 120.7397 | -0.55847 | 120.6665 | -0.5722 | -0.6134 | -0.49896 | 0.14191 | -0.15106 | -0.073242 | 0.11444 | 0.004578 | 0.018311 | -0.13733 | -0.1236 | 0.07782 | -0.26093 | -0.33417 | 0.064087 | 0.13733 | 0.022889 | 0.05951 | -0.054931 | -0.027466 | 121.4218 | -0.013733 | 121.225 | 121.344 | 121.2982 | 121.4859 | 121.376 | -121.4951 | -121.5591 | 121.5637 | 121.3028 | 3.2639 | 2.2339
941.8906 | 121.6644 | -0.59967 | 120.9686 | 0.017166 | 0 | 0.063467 | 0.062647 | 0.0026275 | -0.00035684 | -2.1434e-05 | 0.0062865 | 0.00033544 | -1.3955 | 0.060111 | -0.0017774 | 0.0069897 | -0.00044851 | 2.6184 | 120.8176 | -0.48065 | 121.0373 | -0.40741 | -0.5127 | -0.53558 | 1.6342 | 120.7306 | -0.5722 | 120.7352 | -0.49896 | -0.52185 | -0.44403 | 0.11902 | -0.15106 | 0.068664 | 0.19226 | 0.064087 | 0.086975 | -0.054931 | -0.032043 | 0.027465 | -0.23804 | -0.23346 | 0.10071 | 0.15564 | 0.077819 | 0.12817 | 0.050354 | 0.073242 | 121.5179 | 0.073243 | 121.3074 | 121.2982 | 121.3028 | 121.4172 | 121.3303 | -121.4493 | -121.5408 | 121.637 | 121.3348 | 3.2181 | 2.2339
943.6562 | 121.6278 | -0.62256 | 121.0007 | 0.032425 | 0 | 0.063681 | 0.065424 | -0.0020721 | -0.002493 | -0.0025848 | 0.01239 | 0.0046078 | -1.3931 | 0.059898 | -0.0060498 | 0.0076307 | -0.0027985 | 2.7054 | 120.9274 | -0.5127 | 121.0098 | -0.44861 | -0.50354 | -0.54474 | 1.6708 | 120.7855 | -0.57678 | 120.7123 | -0.5127 | -0.53558 | -0.4715 | 0.10986 | -0.073242 | 0.009156 | 0.17395 | 0.07782 | 0.11902 | -0.032044 | 0.009155 | 0.045777 | -0.21515 | -0.28839 | 0.10986 | 0.15106 | 0.086976 | 0.10529 | 0.041199 | 0.064087 | 121.5225 | 0.064087 | 121.2891 | 121.4401 | 121.3623 | 121.55 | 121.4081 | -121.5134 | -121.5775 | 121.6324 | 121.3348 | 3.3279 | 2.2934
945.3594 | 121.6919 | -0.59052 | 120.9732 | 0.040054 | 0 | 0.064322 | 0.065211 | 0.0013459 | -0.0022794 | -0.00087583 | 0.0093383 | 0.0014034 | -1.395 | 0.068443 | -0.001991 | 0.0093397 | 0.0016877 | 2.6642 | 120.8359 | -0.4715 | 121.0785 | -0.33875 | -0.45319 | -0.49896 | 1.68 | 120.7397 | -0.54016 | 120.7535 | -0.4715 | -0.50354 | -0.43488 | 0.11902 | -0.13733 | 0.10528 | 0.25177 | 0.091553 | 0.13733 | -0.027465 | 0.018311 | 0.050354 | -0.23346 | -0.21973 | 0.11902 | 0.15564 | 0.086975 | 0.10529 | 0.036621 | 0.13275 | 121.55 | 0.068664 | 121.2936 | 121.3074 | 121.2799 | 121.4264 | 121.3303 | -121.4447 | -121.5134 | 121.669 | 121.344 | 3.2547 | 2.2705
947.1406 | 121.6782 | -0.57678 | 121.0327 | 0.040054 | 0 | 0.063895 | 0.06222 | -0.00014949 | -0.00099764 | -0.0017304 | 0.0062865 | 0.0026852 | -1.3952 | 0.06417 | -0.0024182 | 0.0097669 | 0.0038239 | 2.6367 | 120.8496 | -0.46692 | 121.0785 | -0.37537 | -0.45319 | -0.51727 | 1.6708 | 120.7901 | -0.51727 | 120.7626 | -0.46234 | -0.48065 | -0.42572 | 0.10986 | -0.18311 | 0.045776 | 0.20142 | 0.059509 | 0.1236 | -0.050354 | 0.013733 | 0.059509 | -0.24262 | -0.27008 | 0.11444 | 0.15106 | 0.09613 | 0.091553 | 0.036621 | 0.091553 | 121.5454 | 0.054932 | 121.2799 | 121.3165 | 121.3074 | 121.4264 | 121.3669 | -121.4996 | -121.55 | 121.6553 | 121.3394 | 3.2135 | 2.2476
948.8438 | 121.5775 | -0.59967 | 121.0373 | -0.0057221 | 0 | 0.06539 | 0.065424 | 0.0024139 | -0.00099764 | -0.00066223 | -0.0028687 | 0.0020444 | -1.3955 | 0.060966 | -0.0043408 | 0.0076307 | -0.0015167 | 2.6871 | 120.8542 | -0.48065 | 120.9961 | -0.48523 | -0.56763 | -0.60425 | 1.6113 | 120.8038 | -0.5127 | 120.694 | -0.54474 | -0.59967 | -0.48065 | 0.11902 | -0.1831 | -0.041198 | 0.11444 | -0.004578 | 0.032043 | -0.1236 | -0.086975 | 0.086975 | -0.23346 | -0.34332 | 0.054931 | 0.11902 | 0 | 0.032043 | -0.086975 | -0.004577 | 121.4767 | -0.032044 | 121.2067 | 121.3348 | 121.3165 | 121.4539 | 121.4035 | -121.5179 | -121.55 | 121.5958 | 121.2936 | 3.2867 | 2.211
950.5938 | 121.7239 | -0.55847 | 120.9961 | 0.0095369 | 0 | 0.063895 | 0.06692 | 0.0060455 | -0.0012112 | -0.0010894 | 0.018494 | 0.0024716 | -1.3935 | 0.063957 | -0.0015638 | 0.0093397 | -0.00087591 | 2.7237 | 120.8588 | -0.45319 | 121.17 | -0.27466 | -0.40283 | -0.43945 | 1.799 | 120.7809 | -0.51727 | 120.8313 | -0.39368 | -0.43945 | -0.37994 | 0.10529 | -0.13733 | 0.17395 | 0.28381 | 0.11902 | 0.15564 | 0.013733 | 0.050354 | 0.041199 | -0.21515 | -0.16479 | 0.16479 | 0.17853 | 0.11902 | 0.13733 | 0.07782 | 0.17853 | 121.6232 | 0.1236 | 121.3486 | 121.312 | 121.2982 | 121.4172 | 121.3394 | -121.4493 | -121.5134 | 121.7285 | 121.3898 | 3.2822 | 2.3575
952.3594 | 121.6095 | -0.58136 | 121.0556 | 0.0019074 | 0 | 0.064749 | 0.065424 | 0.0011321 | -0.0048428 | -2.1434e-05 | 0.00018312 | 0.002258 | -1.3946 | 0.06417 | -0.0032728 | 0.010408 | -0.0017303 | 2.7374 | 120.8725 | -0.44861 | 121.0281 | -0.41657 | -0.52185 | -0.57678 | 1.6571 | 120.8313 | -0.49896 | 120.7169 | -0.52185 | -0.55847 | -0.45319 | 0.13275 | -0.18311 | -0.027466 | 0.16479 | 0.004578 | 0.059509 | -0.12817 | -0.073243 | 0.082398 | -0.2243 | -0.33875 | 0.059509 | 0.12817 | 0.022888 | 0.045776 | -0.05951 | 0.032043 | 121.4767 | -0.022889 | 121.2158 | 121.3211 | 121.3303 | 121.4539 | 121.4127 | -121.5042 | -121.5546 | 121.6095 | 121.2982 | 3.3188 | 2.2385
954.0625 | 121.6415 | -0.56305 | 121.051 | -0.0057221 | 0 | 0.060904 | 0.064783 | 0.0017731 | -0.0020658 | -0.0015166 | -0.0028687 | 0.0014034 | -1.3957 | 0.054771 | -0.0058362 | 0.0082715 | -0.0015167 | 2.7649 | 120.8679 | -0.42572 | 121.1105 | -0.32959 | -0.42114 | -0.4715 | 1.7075 | 120.7901 | -0.47607 | 120.7443 | -0.44403 | -0.4715 | -0.42572 | 0.13733 | -0.1831 | 0.05951 | 0.23346 | 0.091552 | 0.14191 | -0.045777 | 0.004577 | 0.086975 | -0.26093 | -0.3067 | 0.11902 | 0.13733 | 0.091552 | 0.050354 | 0.004577 | 0.09613 | 121.5363 | 0.032043 | 121.2204 | 121.2936 | 121.2662 | 121.431 | 121.3531 | -121.4767 | -121.5271 | 121.6736 | 121.3074 | 3.3279 | 2.2705
955.8438 | 121.7194 | -0.53101 | 121.0373 | -0.0057221 | 0 | 0.061118 | 0.061365 | -0.0010041 | -0.0029202 | -2.1434e-05 | -0.0059205 | 0.00012184 | -1.395 | 0.063957 | -0.0039136 | 0.0084851 | -0.00044851 | 2.7969 | 120.8542 | -0.39368 | 121.1563 | -0.27008 | -0.37994 | -0.42114 | 1.7807 | 120.7809 | -0.44861 | 120.8496 | -0.33875 | -0.37537 | -0.3479 | 0.13733 | -0.1831 | 0.11902 | 0.26092 | 0.10986 | 0.15106 | -0.027466 | 0.013733 | 0.082398 | -0.25635 | -0.18768 | 0.19226 | 0.18311 | 0.15564 | 0.10071 | 0.073242 | 0.1236 | 121.55 | 0.10986 | 121.2982 | 121.2479 | 121.2296 | 121.3852 | 121.312 | -121.431 | -121.4859 | 121.6873 | 121.3806 | 3.3279 | 2.3117
957.6094 | 121.6873 | -0.52185 | 121.051 | 0.0019074 | 0 | 0.061545 | 0.061579 | 6.4114e-05 | -0.002493 | -0.00066223 | 0.00018312 | 0.0020444 | -1.3978 | 0.06652 | -0.006477 | 0.0067761 | 0.0014741 | 2.8015 | 120.8405 | -0.38452 | 121.17 | -0.27924 | -0.37079 | -0.43488 | 1.7624 | 120.7718 | -0.46692 | 120.8221 | -0.36163 | -0.39825 | -0.36163 | 0.13733 | -0.21057 | 0.11902 | 0.24261 | 0.086976 | 0.15106 | -0.050354 | 0.013732 | 0.054932 | -0.27923 | -0.22888 | 0.16022 | 0.16022 | 0.1236 | 0.10529 | 0.068665 | 0.10529 | 121.5546 | 0.10529 | 121.2891 | 121.225 | 121.2387 | 121.3623 | 121.2936 | -121.4355 | -121.5179 | 121.6919 | 121.344 | 3.3234 | 2.2842
959.375 | 121.6827 | -0.53558 | 121.0464 | 0.017166 | 0 | 0.066672 | 0.063502 | -0.0014313 | -0.0031338 | -0.001303 | 0.0032349 | -9.1956e-05 | -1.3946 | 0.058616 | -0.0024182 | 0.0084851 | -0.0030121 | 2.7328 | 120.8908 | -0.42114 | 121.1105 | -0.32501 | -0.43488 | -0.46234 | 1.6891 | 120.7901 | -0.47607 | 120.8084 | -0.3891 | -0.4303 | -0.37079 | 0.11444 | -0.15564 | 0.064087 | 0.21057 | 0.073242 | 0.10071 | -0.041198 | -0.013732 | 0.059509 | -0.25635 | -0.23804 | 0.14648 | 0.16479 | 0.10529 | 0.10529 | 0.045776 | 0.096131 | 121.5317 | 0.086975 | 121.2845 | 121.312 | 121.2662 | 121.4264 | 121.3257 | -121.4676 | -121.5225 | 121.6461 | 121.344 | 3.2684 | 2.2247
961.0938 | 121.6782 | -0.52643 | 121.0602 | -0.0057221 | 0 | 0.063681 | 0.063502 | 0.0026275 | -0.0048428 | -0.00087583 | 0.00018312 | -0.00051916 | -1.395 | 0.061607 | -0.001991 | 0.0082715 | -0.00044851 | 2.8381 | 120.8542 | -0.39368 | 121.1609 | -0.26093 | -0.37537 | -0.41657 | 1.7944 | 120.8084 | -0.45319 | 120.8267 | -0.35706 | -0.41199 | -0.37079 | 0.13275 | -0.20599 | 0.10071 | 0.2655 | 0.10986 | 0.15106 | -0.022888 | 0.018311 | 0.073242 | -0.25177 | -0.23346 | 0.16937 | 0.15564 | 0.11444 | 0.082397 | 0.041199 | 0.13275 | 121.5546 | 0.09613 | 121.2799 | 121.2479 | 121.2616 | 121.3806 | 121.3348 | -121.4539 | -121.5134 | 121.6873 | 121.3531 | 3.3646 | 2.3209
962.875 | 121.6736 | -0.5127 | 121.0419 | 0.032425 | 0 | 0.064536 | 0.063288 | -0.0050629 | -0.00078404 | -0.00066223 | 0.0062865 | 0.0026852 | -1.394 | 0.063316 | -0.0011364 | 0.0099805 | 0.0019013 | 2.7512 | 120.8817 | -0.41199 | 121.1426 | -0.31128 | -0.41657 | -0.43945 | 1.7487 | 120.8313 | -0.48523 | 120.813 | -0.39368 | -0.43488 | -0.37079 | 0.10071 | -0.16022 | 0.10071 | 0.20142 | 0.073242 | 0.09613 | -0.027466 | -0.004578 | 0.027466 | -0.21057 | -0.22888 | 0.11902 | 0.14191 | 0.07782 | 0.11444 | 0.050354 | 0.10071 | 121.5546 | 0.091552 | 121.2982 | 121.2936 | 121.3165 | 121.3943 | 121.344 | -121.4539 | -121.5271 | 121.6553 | 121.3257 | 3.2639 | 2.2614
964.5781 | 121.6736 | -0.52185 | 121.0831 | 0.047683 | 0 | 0.063681 | 0.067774 | 0.0022003 | -0.002493 | 0.00019217 | 0.0093383 | 0.0014034 | -1.3946 | 0.068015 | -0.0013502 | 0.0086987 | -0.00044851 | 2.8152 | 120.9137 | -0.41199 | 121.1655 | -0.22888 | -0.37994 | -0.39825 | 1.7853 | 120.8359 | -0.45776 | 120.8496 | -0.37079 | -0.42572 | -0.35248 | 0.10986 | -0.16937 | 0.082397 | 0.29297 | 0.1236 | 0.14191 | 0.013733 | 0.032043 | 0.064087 | -0.24719 | -0.23346 | 0.15106 | 0.16937 | 0.096131 | 0.10529 | 0.032044 | 0.1831 | 121.5775 | 0.086975 | 121.3074 | 121.3257 | 121.2936 | 121.4355 | 121.3577 | -121.4951 | -121.5408 | 121.6873 | 121.3715 | 3.3371 | 2.3071
966.3438 | 121.7148 | -0.50812 | 121.0693 | 0.0019074 | 0 | 0.061758 | 0.062006 | 0.00049131 | -0.002493 | 0.0027558 | -0.0028687 | 0.001617 | -1.3944 | 0.065879 | -0.0041272 | 0.010408 | -0.00087591 | 2.8336 | 120.8817 | -0.37994 | 121.2158 | -0.23346 | -0.33875 | -0.39368 | 1.8356 | 120.8313 | -0.4303 | 120.8817 | -0.32501 | -0.35248 | -0.32044 | 0.12817 | -0.18768 | 0.14648 | 0.27466 | 0.11444 | 0.16937 | -0.013733 | 0.041199 | 0.07782 | -0.23804 | -0.18768 | 0.18311 | 0.18768 | 0.15564 | 0.10986 | 0.07782 | 0.14649 | 121.5958 | 0.10529 | 121.312 | 121.2616 | 121.2616 | 121.3898 | 121.3394 | -121.4493 | -121.4996 | 121.7239 | 121.3898 | 3.3417 | 2.3438
968.0469 | 121.7377 | -0.49896 | 121.0785 | -0.0057221 | 0 | 0.062399 | 0.063502 | -0.0018585 | -0.003561 | -0.0021576 | 0.0032349 | 0.0020444 | -1.3963 | 0.057121 | -0.0026318 | 0.0086987 | -0.00087591 | 2.7832 | 120.8679 | -0.38452 | 121.1563 | -0.29297 | -0.37537 | -0.40283 | 1.7944 | 120.8313 | -0.4303 | 120.8725 | -0.32959 | -0.35706 | -0.3067 | 0.11444 | -0.21057 | 0.07782 | 0.20599 | 0.09613 | 0.1236 | -0.018311 | 0.009155 | 0.068664 | -0.24719 | -0.20599 | 0.16937 | 0.19226 | 0.14191 | 0.1236 | 0.073242 | 0.091552 | 121.5408 | 0.10071 | 121.3028 | 121.2524 | 121.2616 | 121.3669 | 121.3303 | -121.463 | -121.5088 | 121.6553 | 121.3715 | 3.2822 | 2.2934
969.8125 | 121.6873 | -0.5127 | 121.0922 | 0.040054 | 0 | 0.064322 | 0.065424 | 6.4114e-05 | 0.00028416 | -0.00023503 | 0.01239 | 0.0028988 | -1.3933 | 0.066947 | -0.001991 | 0.0067761 | -2.1314e-05 | 2.8198 | 120.8954 | -0.39825 | 121.1792 | -0.24261 | -0.3891 | -0.40741 | 1.799 | 120.8359 | -0.44403 | 120.8542 | -0.36621 | -0.40283 | -0.34332 | 0.11444 | -0.19684 | 0.086975 | 0.27008 | 0.10529 | 0.1236 | -0.009156 | 0.009155 | 0.068664 | -0.25635 | -0.23804 | 0.14648 | 0.16937 | 0.10986 | 0.10071 | 0.041199 | 0.15564 | 121.5775 | 0.07782 | 121.2982 | 121.2936 | 121.2799 | 121.4081 | 121.3486 | -121.4905 | -121.5363 | 121.6919 | 121.3669 | 3.3325 | 2.3117
971.5 | 121.6873 | -0.52185 | 121.0693 | 0.0019074 | 0 | 0.064322 | 0.06756 | -0.00014949 | -0.0033474 | 0.001474 | -0.0059205 | 0.00054904 | -1.3942 | 0.062461 | -0.00028199 | 0.0091261 | -0.0042939 | 2.7832 | 120.9229 | -0.38452 | 121.0968 | -0.3479 | -0.4715 | -0.49439 | 1.7395 | 120.8679 | -0.43945 | 120.8542 | -0.37537 | -0.4303 | -0.33417 | 0.13733 | -0.14648 | 0.027466 | 0.17395 | 0.027466 | 0.050354 | -0.10986 | -0.086976 | 0.082398 | -0.20142 | -0.21515 | 0.14648 | 0.18768 | 0.091553 | 0.10529 | 0.009155 | 0.036621 | 121.4813 | 0.064087 | 121.2936 | 121.3074 | 121.3074 | 121.4447 | 121.3898 | -121.4539 | -121.5088 | 121.6187 | 121.376 | 3.3051 | 2.2614
973.2656 | 121.7102 | -0.48981 | 121.0693 | -0.0057221 | 0 | 0.063467 | 0.064142 | -0.00036309 | -0.00078404 | 0.001474 | 0.00018312 | 0.0026852 | -1.3952 | 0.065238 | -0.0017774 | 0.010621 | -0.00087591 | 2.8107 | 120.9137 | -0.3891 | 121.1609 | -0.29755 | -0.40283 | -0.43945 | 1.8082 | 120.8542 | -0.4303 | 120.8954 | -0.33417 | -0.37994 | -0.29297 | 0.10071 | -0.15564 | 0.091553 | 0.19226 | 0.050354 | 0.086975 | -0.050354 | -0.013733 | 0.059509 | -0.21515 | -0.17395 | 0.15564 | 0.19684 | 0.10986 | 0.13733 | 0.050354 | 0.091553 | 121.55 | 0.096131 | 121.3257 | 121.3028 | 121.2845 | 121.4035 | 121.344 | -121.4584 | -121.4996 | 121.6507 | 121.3852 | 3.3005 | 2.298
975.0469 | 121.6324 | -0.52185 | 121.0876 | -0.013352 | 0 | 0.065176 | 0.064997 | -0.00036309 | -0.0012112 | -0.00087583 | -0.0059205 | 0.0014034 | -1.3972 | 0.063102 | -0.0017774 | 0.0086987 | -0.0015167 | 2.8061 | 120.9732 | -0.39368 | 121.0968 | -0.37994 | -0.48523 | -0.49896 | 1.6891 | 120.8725 | -0.44403 | 120.8313 | -0.4303 | -0.48981 | -0.35706 | 0.12817 | -0.11444 | 0.009156 | 0.14191 | 0.022889 | 0.036622 | -0.10529 | -0.091552 | 0.07782 | -0.21515 | -0.25635 | 0.091553 | 0.16479 | 0.032044 | 0.086975 | -0.045776 | 0.013733 | 121.4905 | 0.013733 | 121.2753 | 121.3669 | 121.3165 | 121.4951 | 121.3943 | -121.4813 | -121.5317 | 121.6187 | 121.3531 | 3.3279 | 2.211
976.7656 | 121.7377 | -0.4715 | 121.0785 | 0.0019074 | 0 | 0.063681 | 0.062433 | -0.0016449 | -0.0031338 | 0.0010468 | 0.00018312 | 0.0020444 | -1.3952 | 0.070579 | -0.0043408 | 0.0082715 | 0.0027557 | 2.8564 | 120.9137 | -0.3479 | 121.1929 | -0.23804 | -0.32044 | -0.37537 | 1.7944 | 120.8359 | -0.41199 | 120.9091 | -0.27924 | -0.32501 | -0.27466 | 0.1236 | -0.16479 | 0.11444 | 0.23346 | 0.096131 | 0.15106 | -0.027466 | 0.027465 | 0.05951 | -0.24262 | -0.16937 | 0.19226 | 0.19684 | 0.14648 | 0.13733 | 0.086975 | 0.10986 | 121.5408 | 0.13275 | 121.3211 | 121.2616 | 121.2479 | 121.3852 | 121.3074 | -121.4264 | -121.4905 | 121.6644 | 121.3806 | 3.3279 | 2.2659
978.5156 | 121.6095 | -0.49896 | 121.1426 | 0.0019074 | 0 | 0.062827 | 0.066279 | -0.00057689 | -0.0046292 | -0.00023503 | -0.0028687 | 0.002258 | -1.3955 | 0.059043 | -0.006477 | 0.010408 | 0.00061949 | 2.8885 | 120.9549 | -0.35706 | 121.138 | -0.31586 | -0.39368 | -0.44403 | 1.7441 | 120.8862 | -0.42572 | 120.7809 | -0.40283 | -0.44403 | -0.38452 | 0.14191 | -0.18768 | -0.004578 | 0.18311 | 0.054931 | 0.10529 | -0.086975 | -0.036621 | 0.073242 | -0.25635 | -0.36163 | 0.09613 | 0.11444 | 0.054931 | 0.041199 | -0.018311 | 0.041199 | 121.4951 | 0.022888 | 121.2067 | 121.312 | 121.3119 | 121.4539 | 121.3852 | -121.4996 | -121.5683 | 121.637 | 121.2799 | 3.3875 | 2.243
980.2969 | 121.6873 | -0.48981 | 121.0968 | 0.017166 | 0 | 0.065604 | 0.065851 | 0.00027771 | -0.0016384 | 0.00040597 | 0.00018312 | 0.0011898 | -1.3952 | 0.066947 | -0.003059 | 0.0093397 | -2.1314e-05 | 2.8519 | 120.9641 | -0.35706 | 121.1609 | -0.2655 | -0.36163 | -0.39368 | 1.7578 | 120.8496 | -0.40741 | 120.8908 | -0.32044 | -0.35248 | -0.3067 | 0.13275 | -0.13275 | 0.064087 | 0.2243 | 0.09613 | 0.12817 | -0.036621 | -0.004577 | 0.082397 | -0.24719 | -0.20599 | 0.16937 | 0.18311 | 0.13733 | 0.10071 | 0.054932 | 0.091553 | 121.5179 | 0.086975 | 121.2982 | 121.3211 | 121.257 | 121.4539 | 121.3394 | -121.4539 | -121.5042 | 121.6507 | 121.3806 | 3.3417 | 2.2476
982 | 121.7102 | -0.48065 | 121.0831 | 0.0019074 | 0 | 0.063895 | 0.060938 | 0.0015595 | -0.0027066 | 0.00019217 | -0.0028687 | 0.00076264 | -1.3959 | 0.068015 | -0.0026318 | 0.0074171 | 0.0023285 | 2.8885 | 120.9045 | -0.36621 | 121.1792 | -0.23346 | -0.33875 | -0.37537 | 1.8036 | 120.8679 | -0.41199 | 120.9183 | -0.27466 | -0.31586 | -0.27924 | 0.11444 | -0.17853 | 0.09613 | 0.24719 | 0.10529 | 0.14191 | -0.009155 | 0.027466 | 0.068665 | -0.21515 | -0.16479 | 0.20599 | 0.20142 | 0.1648 | 0.13275 | 0.09613 | 0.13275 | 121.5454 | 0.13733 | 121.3303 | 121.2708 | 121.2799 | 121.3852 | 121.3486 | -121.4493 | -121.4951 | 121.6599 | 121.3989 | 3.3691 | 2.2842
983.7656 | 121.6095 | -0.50354 | 121.1288 | 0.0019074 | 0 | 0.065604 | 0.06457 | -0.0027131 | -0.001852 | -0.00023503 | -0.0028687 | 0.0048214 | -1.3948 | 0.066947 | -0.0037 | 0.0093397 | 0.0016877 | 2.8885 | 120.9686 | -0.37537 | 121.0922 | -0.37537 | -0.48523 | -0.49896 | 1.7075 | 120.9 | -0.42114 | 120.813 | -0.4303 | -0.47607 | -0.37994 | 0.12817 | -0.16022 | -0.036621 | 0.12817 | 0.004578 | 0.018311 | -0.1236 | -0.10986 | 0.082397 | -0.22888 | -0.31586 | 0.073242 | 0.1236 | 0.027466 | 0.041199 | -0.054931 | 0 | 121.4676 | -0.009155 | 121.2341 | 121.344 | 121.3211 | 121.4722 | 121.4035 | -121.5042 | -121.55 | 121.5958 | 121.3165 | 3.392 | 2.211
985.4688 | 121.7422 | -0.46234 | 121.1105 | -0.0057221 | 0 | 0.063681 | 0.063929 | -0.0074127 | -0.003561 | -0.0017304 | -0.0028687 | -9.1956e-05 | -1.3946 | 0.067375 | -0.0037 | 0.0074171 | -0.00066231 | 2.916 | 120.9274 | -0.35248 | 121.1929 | -0.24719 | -0.33875 | -0.35706 | 1.8082 | 120.8679 | -0.41199 | 120.9183 | -0.28381 | -0.32501 | -0.27466 | 0.10986 | -0.18311 | 0.082397 | 0.21515 | 0.10529 | 0.1236 | -0.004578 | 0.013733 | 0.050354 | -0.24262 | -0.19226 | 0.17853 | 0.18768 | 0.13733 | 0.13733 | 0.086975 | 0.10529 | 121.5454 | 0.12817 | 121.3303 | 121.2799 | 121.2799 | 121.3898 | 121.3303 | -121.463 | -121.5225 | 121.6553 | 121.3806 | 3.3783 | 2.2705
987.25 | 121.7148 | -0.45319 | 121.1105 | -0.013352 | 0 | 0.063254 | 0.063502 | 0.00049131 | -0.0020658 | -0.0015166 | -0.0028687 | 0.00097624 | -1.3963 | 0.066093 | -0.0028454 | 0.0086987 | 0.0025421 | 2.9617 | 120.9045 | -0.33875 | 121.2524 | -0.19226 | -0.29297 | -0.34332 | 1.886 | 120.8771 | -0.3891 | 120.9045 | -0.27924 | -0.31586 | -0.28839 | 0.11444 | -0.20599 | 0.14191 | 0.26092 | 0.10986 | 0.16022 | -0.004578 | 0.045776 | 0.064087 | -0.23346 | -0.20599 | 0.17395 | 0.16479 | 0.13733 | 0.10071 | 0.073242 | 0.14648 | 121.5912 | 0.10986 | 121.2936 | 121.2433 | 121.2662 | 121.3577 | 121.3303 | -121.4493 | -121.4996 | 121.7056 | 121.3577 | 3.4149 | 2.3392
989.0156 | 121.7422 | -0.46234 | 121.0922 | -0.0057221 | 0 | 0.06069 | 0.063288 | -0.0054901 | -0.0027066 | -0.0038666 | -0.0028687 | 0.002258 | -1.3952 | 0.066093 | -0.0045544 | 0.0074171 | -0.00087591 | 2.9526 | 120.9137 | -0.32501 | 121.2341 | -0.20599 | -0.30212 | -0.33875 | 1.8768 | 120.8725 | -0.38452 | 120.9412 | -0.25177 | -0.29297 | -0.26093 | 0.13733 | -0.17853 | 0.14191 | 0.25635 | 0.1236 | 0.16022 | -0.013733 | 0.022888 | 0.07782 | -0.21973 | -0.15106 | 0.21057 | 0.20142 | 0.16937 | 0.1236 | 0.091552 | 0.11902 | 121.5591 | 0.13275 | 121.3257 | 121.2387 | 121.257 | 121.376 | 121.3348 | -121.4172 | -121.4767 | 121.6965 | 121.4035 | 3.4149 | 2.3392
990.7969 | 121.7148 | -0.44861 | 121.1472 | 0.0019074 | 0 | 0.065176 | 0.063715 | 0.0013459 | 0.00049776 | -0.00023503 | -0.0059205 | 0.002258 | -1.395 | 0.066093 | -0.00070919 | 0.010408 | -0.0036529 | 2.9709 | 120.9549 | -0.33417 | 121.2067 | -0.21515 | -0.3479 | -0.37994 | 1.8585 | 120.8908 | -0.3891 | 120.9457 | -0.28381 | -0.33417 | -0.24719 | 0.11444 | -0.19226 | 0.059509 | 0.23346 | 0.068664 | 0.10071 | -0.045777 | -0.013733 | 0.059509 | -0.25635 | -0.20142 | 0.1648 | 0.20142 | 0.11444 | 0.14191 | 0.054932 | 0.11902 | 121.5408 | 0.10529 | 121.3348 | 121.2891 | 121.2799 | 121.4035 | 121.3394 | -121.4813 | -121.5363 | 121.6553 | 121.3943 | 3.4195 | 2.3071
992.5 | 121.669 | -0.44403 | 121.1334 | 0.017166 | 0 | 0.065176 | 0.063074 | 0.0032685 | -0.0027066 | -0.001303 | 0.00018312 | 0.00076264 | -1.3955 | 0.063316 | -0.0026318 | 0.010194 | -0.00023491 | 2.9114 | 120.9549 | -0.36163 | 121.2021 | -0.24261 | -0.35706 | -0.37994 | 1.7761 | 120.9229 | -0.39368 | 120.8817 | -0.32501 | -0.37994 | -0.31128 | 0.082398 | -0.17853 | 0.068664 | 0.20142 | 0.064087 | 0.086975 | -0.018311 | 0.004577 | 0.050354 | -0.21057 | -0.25177 | 0.11902 | 0.13275 | 0.064087 | 0.082398 | 0.013733 | 0.11902 | 121.5637 | 0.068665 | 121.2753 | 121.3165 | 121.3165 | 121.3989 | 121.3669 | -121.4951 | -121.5271 | 121.6461 | 121.3257 | 3.3554 | 2.2202
994.2656 | 121.6003 | -0.47607 | 121.1655 | 0.017166 | 0 | 0.063467 | 0.065851 | 0.0011321 | -0.0029202 | -0.0023712 | -0.0028687 | 0.0035396 | -1.3963 | 0.063743 | -0.0034864 | 0.0082715 | -2.1314e-05 | 2.9617 | 120.9869 | -0.33875 | 121.1426 | -0.32501 | -0.44403 | -0.47607 | 1.7624 | 120.9274 | -0.40283 | 120.8405 | -0.42114 | -0.46692 | -0.35248 | 0.13733 | -0.17853 | -0.022888 | 0.15106 | 0 | 0.032043 | -0.13733 | -0.10529 | 0.073242 | -0.23804 | -0.32501 | 0.054931 | 0.1236 | 0.009155 | 0.050354 | -0.064087 | 0.013733 | 121.4813 | -0.018311 | 121.2433 | 121.3257 | 121.3303 | 121.463 | 121.4035 | -121.5042 | -121.5683 | 121.6187 | 121.3165 | 3.4378 | 2.2385
996.0469 | 121.6232 | -0.48523 | 121.1517 | -0.0057221 | 0 | 0.064536 | 0.06457 | -0.0012177 | -0.0020658 | -0.0017304 | 0.00018312 | 0.0037532 | -1.3948 | 0.05883 | -0.0022046 | 0.0076307 | 0.0019013 | 2.9205 | 121.0236 | -0.35248 | 121.106 | -0.35248 | -0.45776 | -0.46234 | 1.7349 | 120.9457 | -0.41657 | 120.845 | -0.40741 | -0.44403 | -0.34332 | 0.13275 | -0.12817 | -0.045776 | 0.13275 | 0.022888 | 0.027465 | -0.10986 | -0.10529 | 0.068664 | -0.20599 | -0.3067 | 0.077819 | 0.14191 | 0.041198 | 0.073242 | -0.027466 | 0 | 121.4584 | 0.009155 | 121.2616 | 121.376 | 121.3623 | 121.5088 | 121.431 | -121.5042 | -121.5683 | 121.5912 | 121.3303 | 3.4058 | 2.2202
997.8281 | 121.637 | -0.46234 | 121.1609 | 0.0019074 | 0 | 0.065604 | 0.06692 | 0.0024139 | -0.0014248 | 0.0010468 | 0.0032349 | 0.0026852 | -1.394 | 0.063102 | -0.00049559 | 0.0086987 | 0.0019013 | 2.916 | 121.0144 | -0.36621 | 121.1426 | -0.33875 | -0.4303 | -0.44861 | 1.7532 | 120.9183 | -0.40741 | 120.8817 | -0.37537 | -0.42114 | -0.32501 | 0.09613 | -0.14648 | -0.018311 | 0.1236 | 0.013733 | 0.032043 | -0.082397 | -0.064087 | 0.054931 | -0.24262 | -0.27924 | 0.086975 | 0.13733 | 0.041198 | 0.082398 | -0.013733 | 0.027466 | 121.5088 | 0.032044 | 121.2891 | 121.3806 | 121.3257 | 121.4767 | 121.3806 | -121.5271 | -121.5683 | 121.6049 | 121.344 | 3.3783 | 2.2156
999.5312 | 121.6644 | -0.43945 | 121.1472 | 0.017166 | 0 | 0.063467 | 0.062861 | 0.0013459 | -0.0029202 | -0.00044863 | 0.0032349 | 0.00033544 | -1.3942 | 0.068656 | -0.0024182 | 0.0097669 | -0.00044851 | 2.948 | 120.9457 | -0.33417 | 121.1884 | -0.24719 | -0.33417 | -0.3891 | 1.799 | 120.8817 | -0.39825 | 120.9 | -0.32044 | -0.3479 | -0.27924 | 0.10529 | -0.20142 | 0.041198 | 0.19226 | 0.050354 | 0.10529 | -0.054932 | 0 | 0.041199 | -0.2655 | -0.24719 | 0.11902 | 0.16022 | 0.091553 | 0.11902 | 0.050354 | 0.086975 | 121.5225 | 0.077819 | 121.2982 | 121.2799 | 121.2799 | 121.3852 | 121.3211 | -121.4813 | -121.5454 | 121.6278 | 121.3394 | 3.3875 | 2.2385
1001.2969 | 121.7377 | -0.41657 | 121.1426 | -0.0057221 | 0 | 0.061758 | 0.062006 | -0.0044221 | -0.0020658 | -2.1434e-05 | -0.0028687 | 0.00097624 | -1.3925 | 0.068015 | -0.0039136 | 0.0076307 | 0.0010467 | 2.9663 | 120.9732 | -0.32501 | 121.225 | -0.19226 | -0.30212 | -0.3479 | 1.8677 | 120.8771 | -0.36621 | 120.9412 | -0.24719 | -0.28381 | -0.23346 | 0.091553 | -0.16937 | 0.082398 | 0.2243 | 0.068665 | 0.11444 | -0.022888 | 0.022888 | 0.050354 | -0.2655 | -0.20142 | 0.16937 | 0.18311 | 0.13275 | 0.13275 | 0.082398 | 0.13275 | 121.55 | 0.11902 | 121.3074 | 121.2982 | 121.2433 | 121.3898 | 121.2936 | -121.4676 | -121.5088 | 121.6415 | 121.3577 | 3.3829 | 2.2842
1003.0781 | 121.6782 | -0.4303 | 121.1563 | 0.0019074 | 0 | 0.063895 | 0.066065 | -0.0012177 | -0.002493 | -0.001303 | -0.0028687 | 0.0026852 | -1.395 | 0.067161 | -0.0022046 | 0.0091261 | 0.00040589 | 2.9617 | 120.9915 | -0.32501 | 121.1472 | -0.29755 | -0.42572 | -0.4303 | 1.7899 | 120.9091 | -0.39368 | 120.9045 | -0.32959 | -0.37537 | -0.29755 | 0.10529 | -0.16479 | -0.009155 | 0.13275 | 0 | 0.004578 | -0.10529 | -0.10071 | 0.036621 | -0.24719 | -0.25177 | 0.10071 | 0.13275 | 0.054932 | 0.096131 | 0.018311 | 0.027466 | 121.4722 | 0.064087 | 121.2982 | 121.3165 | 121.3028 | 121.4218 | 121.3394 | -121.4813 | -121.55 | 121.5775 | 121.3348 | 3.392 | 2.2202
1004.7812 | 121.7102 | -0.4303 | 121.1426 | -0.0057221 | 0 | 0.06539 | 0.062433 | 6.4114e-05 | -0.0020658 | -0.0010894 | 0.00018312 | 0.0020444 | -1.395 | 0.063316 | -0.003059 | 0.0086987 | -0.0042939 | 3.0167 | 121.0281 | -0.30212 | 121.2204 | -0.21973 | -0.32959 | -0.36163 | 1.8585 | 120.9091 | -0.3479 | 120.9641 | -0.2655 | -0.30212 | -0.2243 | 0.12817 | -0.11444 | 0.07782 | 0.21057 | 0.068665 | 0.10071 | -0.059509 | -0.027466 | 0.082398 | -0.23346 | -0.17853 | 0.1648 | 0.20599 | 0.12817 | 0.1236 | 0.045776 | 0.082397 | 121.5225 | 0.082397 | 121.3119 | 121.3303 | 121.257 | 121.4584 | 121.3394 | -121.4447 | -121.4905 | 121.6507 | 121.3943 | 3.447 | 2.2888
1006.5469 | 121.6599 | -0.46234 | 121.1609 | 0.017166 | 0 | 0.062613 | 0.065638 | 0.0013459 | -0.00014304 | 0.0023286 | 0.0062865 | 0.0035396 | -1.394 | 0.062248 | -0.0062634 | 0.0082715 | 0.0012603 | 3.0808 | 120.9732 | -0.35706 | 121.2112 | -0.24261 | -0.33417 | -0.40283 | 1.8951 | 120.9595 | -0.40283 | 120.9183 | -0.32044 | -0.38452 | -0.28839 | 0.10529 | -0.18768 | 0.050354 | 0.21973 | 0.059509 | 0.12817 | -0.045776 | 0.022889 | 0.059509 | -0.20142 | -0.24262 | 0.14191 | 0.17395 | 0.07782 | 0.11444 | 0.018311 | 0.11444 | 121.5683 | 0.082397 | 121.3211 | 121.3303 | 121.3623 | 121.4355 | 121.4218 | -121.5179 | -121.5637 | 121.6736 | 121.3806 | 3.5431 | 2.3575
1008.3125 | 121.6049 | -0.46692 | 121.1929 | 0.0019074 | 0 | 0.063895 | 0.063288 | -0.0033539 | -0.0029202 | -0.00023503 | 0.00018312 | 0.0020444 | -1.3959 | 0.056053 | -0.0090406 | 0.0076307 | -0.0034393 | 3.0258 | 120.9915 | -0.32501 | 121.138 | -0.31128 | -0.39825 | -0.42572 | 1.8127 | 120.932 | -0.39825 | 120.8267 | -0.3891 | -0.41657 | -0.35248 | 0.14191 | -0.20142 | -0.054932 | 0.15564 | 0.041199 | 0.068665 | -0.10071 | -0.073242 | 0.068665 | -0.26093 | -0.36621 | 0.07782 | 0.11444 | 0.050354 | 0.045776 | -0.018311 | 0.013733 | 121.463 | 0.009155 | 121.225 | 121.3165 | 121.3303 | 121.4584 | 121.3989 | -121.5179 | -121.5912 | 121.6049 | 121.2936 | 3.4927 | 2.2797
1010.0781 | 121.6553 | -0.45776 | 121.1746 | 0.0095369 | 0 | 0.064749 | 0.063074 | 0.0028411 | -0.0029202 | 0.00061957 | 0.0032349 | 0.0018306 | -1.3937 | 0.067588 | -0.003059 | 0.011049 | -2.1314e-05 | 3.0167 | 121.0373 | -0.33417 | 121.138 | -0.31128 | -0.4303 | -0.43488 | 1.8173 | 120.9366 | -0.37079 | 120.9137 | -0.33417 | -0.38452 | -0.27924 | 0.1236 | -0.13733 | -0.036622 | 0.14649 | 0.022889 | 0.027466 | -0.10071 | -0.096131 | 0.086975 | -0.23804 | -0.26093 | 0.1236 | 0.17853 | 0.073243 | 0.091553 | -0.013732 | 0.022888 | 121.4722 | 0.036622 | 121.2845 | 121.3715 | 121.3074 | 121.4951 | 121.3943 | -121.5088 | -121.5454 | 121.5958 | 121.3715 | 3.4744 | 2.2751
1011.7969 | 121.6782 | -0.41657 | 121.138 | 0.040054 | 0 | 0.064322 | 0.062861 | -0.00036309 | 7.0564e-05 | 0.0019012 | 0.015442 | 0.0014034 | -1.394 | 0.071647 | -0.0028454 | 0.0091261 | 0.00083309 | 3.0579 | 120.9778 | -0.32044 | 121.257 | -0.15106 | -0.29297 | -0.32501 | 1.8951 | 120.9412 | -0.36163 | 120.9366 | -0.29755 | -0.32501 | -0.28381 | 0.09613 | -0.16022 | 0.11902 | 0.2655 | 0.091553 | 0.1236 | -0.004577 | 0.027466 | 0.054932 | -0.19684 | -0.20142 | 0.11902 | 0.13275 | 0.091553 | 0.07782 | 0.036621 | 0.16937 | 121.5775 | 0.064087 | 121.2982 | 121.2982 | 121.3028 | 121.3943 | 121.3577 | -121.4584 | -121.4996 | 121.6736 | 121.3531 | 3.4744 | 2.3117
1013.4844 | 121.6827 | -0.41657 | 121.1792 | 0.040054 | 0 | 0.064108 | 0.063715 | 0.0011321 | -0.00078404 | -0.00087583 | 0.01239 | 0.0020444 | -1.3955 | 0.065879 | -0.00070919 | 0.0093397 | 0.00083309 | 3.0716 | 121.0281 | -0.3067 | 121.2341 | -0.19226 | -0.3067 | -0.33875 | 1.8677 | 120.9045 | -0.37537 | 120.9229 | -0.30212 | -0.32959 | -0.27466 | 0.10986 | -0.15106 | 0.054932 | 0.2243 | 0.07782 | 0.10986 | -0.032043 | 0 | 0.041199 | -0.27466 | -0.25635 | 0.11444 | 0.14191 | 0.086975 | 0.10071 | 0.045776 | 0.11444 | 121.5408 | 0.073242 | 121.2982 | 121.3348 | 121.2799 | 121.4447 | 121.3211 | -121.4859 | -121.5546 | 121.6507 | 121.3394 | 3.4882 | 2.2842
1015.25 | 121.6324 | -0.45319 | 121.1975 | -0.013352 | 0 | 0.064322 | 0.066065 | 0.0022003 | -0.0020658 | -0.0025848 | 0.00018312 | 0.0028988 | -1.394 | 0.060539 | 0.00035881 | 0.011903 | 0.0016877 | 3.067 | 121.0281 | -0.33417 | 121.138 | -0.32044 | -0.41657 | -0.43945 | 1.8082 | 120.9412 | -0.39368 | 120.8679 | -0.36621 | -0.41199 | -0.29755 | 0.11902 | -0.16937 | -0.05951 | 0.13275 | 0.013733 | 0.036621 | -0.10529 | -0.082398 | 0.059509 | -0.25635 | -0.32959 | 0.086975 | 0.15564 | 0.041199 | 0.096131 | -0.01831 | 0.013732 | 121.4722 | 0.027466 | 121.2616 | 121.3623 | 121.3348 | 121.4813 | 121.3943 | -121.5317 | -121.5912 | 121.5912 | 121.3211 | 3.5202 | 2.2614
1016.9688 | 121.7422 | -0.42114 | 121.1517 | -0.0057221 | 0 | 0.063681 | 0.064997 | -0.0042083 | -0.0044156 | -0.00023503 | 0.0032349 | -9.1956e-05 | -1.394 | 0.066093 | -0.0039136 | 0.0080579 | -0.0017303 | 3.1357 | 120.9778 | -0.28839 | 121.2799 | -0.11444 | -0.23346 | -0.27924 | 1.9684 | 120.8862 | -0.35248 | 120.9824 | -0.21515 | -0.26093 | -0.21973 | 0.13275 | -0.17395 | 0.12817 | 0.3067 | 0.14191 | 0.18768 | 0.009155 | 0.054932 | 0.068665 | -0.2655 | -0.16937 | 0.20599 | 0.20142 | 0.16022 | 0.13275 | 0.091553 | 0.17395 | 121.5683 | 0.13733 | 121.3348 | 121.2662 | 121.2387 | 121.3989 | 121.3074 | -121.4401 | -121.5042 | 121.701 | 121.4035 | 3.5568 | 2.3895
1018.6719 | 121.6873 | -0.41199 | 121.1746 | 0.024795 | 0 | 0.063895 | 0.06457 | 0.0039093 | -0.0033474 | -0.001944 | 0.0062865 | 0.00097624 | -1.3929 | 0.067588 | -0.0024182 | 0.0091261 | -0.0010895 | 3.0762 | 121.0144 | -0.28839 | 121.2204 | -0.23804 | -0.32044 | -0.36163 | 1.8539 | 120.932 | -0.36163 | 120.9091 | -0.28381 | -0.32044 | -0.2655 | 0.1236 | -0.16022 | 0.045776 | 0.17395 | 0.050354 | 0.091552 | -0.073242 | -0.032044 | 0.050354 | -0.24262 | -0.2655 | 0.12817 | 0.14648 | 0.091552 | 0.09613 | 0.041198 | 0.050354 | 121.5088 | 0.07782 | 121.2708 | 121.3028 | 121.2936 | 121.4264 | 121.344 | -121.463 | -121.5363 | 121.6324 | 121.3211 | 3.4882 | 2.2659
1020.4219 | 121.6415 | -0.4303 | 121.1975 | 0.024795 | 0 | 0.062399 | 0.064356 | 0.0034821 | -0.00057044 | 0.0010468 | 0.0062865 | 0.0043942 | -1.3942 | 0.058616 | -0.004768 | 0.0074171 | 0.0021149 | 3.1769 | 121.0373 | -0.33875 | 121.2204 | -0.23346 | -0.33875 | -0.38452 | 1.8997 | 120.9778 | -0.37994 | 120.9274 | -0.31128 | -0.34332 | -0.27924 | 0.091553 | -0.16022 | 0.022888 | 0.19684 | 0.045777 | 0.091553 | -0.045776 | 0 | 0.050354 | -0.21973 | -0.27008 | 0.11902 | 0.15106 | 0.086975 | 0.10071 | 0.036621 | 0.10529 | 121.5591 | 0.068665 | 121.3074 | 121.376 | 121.3577 | 121.4676 | 121.4081 | -121.5363 | -121.5775 | 121.6507 | 121.3577 | 3.6072 | 2.33
1022.2188 | 121.6553 | -0.43488 | 121.2158 | 0.024795 | 0 | 0.06304 | 0.06457 | 0.0034821 | -0.0033474 | 0.0010468 | 0.0032349 | 0.00076264 | -1.3933 | 0.057121 | -0.001991 | 0.0082715 | -0.0036529 | 3.1998 | 121.0602 | -0.32959 | 121.2204 | -0.2243 | -0.33417 | -0.36621 | 1.9363 | 120.9503 | -0.36163 | 120.932 | -0.30212 | -0.35248 | -0.27924 | 0.10529 | -0.15564 | 0.004578 | 0.21057 | 0.068664 | 0.10071 | -0.036621 | -0.004577 | 0.073242 | -0.2655 | -0.28381 | 0.13275 | 0.15564 | 0.082397 | 0.082397 | 0.009155 | 0.10529 | 121.55 | 0.059509 | 121.2936 | 121.3898 | 121.3119 | 121.4951 | 121.3852 | -121.5454 | -121.5775 | 121.6553 | 121.3669 | 3.6346 | 2.3712
1023.9219 | 121.7422 | -0.38452 | 121.1655 | -0.0057221 | 0 | 0.062613 | 0.064142 | -0.00079049 | -0.002493 | -2.1434e-05 | 0.00018312 | 0.00076264 | -1.3948 | 0.066734 | -0.004768 | 0.0080579 | 0.0014741 | 3.1723 | 120.9503 | -0.25177 | 121.312 | -0.13275 | -0.25177 | -0.28839 | 1.973 | 120.9137 | -0.34332 | 120.9915 | -0.19226 | -0.24261 | -0.20599 | 0.13275 | -0.21515 | 0.14648 | 0.25177 | 0.09613 | 0.13275 | -0.036621 | 0 | 0.041198 | -0.25177 | -0.17395 | 0.19226 | 0.17853 | 0.14191 | 0.13733 | 0.10071 | 0.11902 | 121.5637 | 0.15106 | 121.3348 | 121.2021 | 121.257 | 121.3348 | 121.2982 | -121.4172 | -121.5088 | 121.6965 | 121.376 | 3.5568 | 2.3575
1025.625 | 121.7239 | -0.38452 | 121.1884 | 0.055313 | 0 | 0.066672 | 0.066492 | -0.0029267 | -0.0014248 | 0.0042512 | 0.01239 | 0.0028988 | -1.3963 | 0.077842 | -0.00092279 | 0.0093397 | 0.0027557 | 3.1998 | 121.0373 | -0.30212 | 121.3303 | -0.1236 | -0.26093 | -0.28839 | 1.9821 | 120.9457 | -0.3479 | 120.9869 | -0.23804 | -0.27924 | -0.21515 | 0.082397 | -0.15106 | 0.14191 | 0.26093 | 0.09613 | 0.1236 | 0.013733 | 0.041199 | 0.036621 | -0.24261 | -0.20142 | 0.14648 | 0.16937 | 0.10529 | 0.13275 | 0.068664 | 0.17853 | 121.6324 | 0.10986 | 121.3348 | 121.3394 | 121.2936 | 121.4218 | 121.3303 | -121.4905 | -121.5363 | 121.7148 | 121.3715 | 3.5843 | 2.3666
1027.3906 | 121.6965 | -0.41657 | 121.1975 | -0.0057221 | 0 | 0.063467 | 0.066065 | -0.00014949 | -0.002493 | 0.00083317 | 0.0032349 | -0.00030556 | -1.394 | 0.066306 | -0.0043408 | 0.011476 | -0.0027985 | 3.1265 | 121.0327 | -0.29297 | 121.1884 | -0.24719 | -0.3479 | -0.38452 | 1.8768 | 120.9686 | -0.33417 | 120.9641 | -0.27924 | -0.3067 | -0.2243 | 0.1236 | -0.16479 | -0.009156 | 0.16937 | 0.032044 | 0.068665 | -0.091552 | -0.054931 | 0.082398 | -0.22888 | -0.23346 | 0.13733 | 0.19226 | 0.10986 | 0.10986 | 0.027465 | 0.045777 | 121.4813 | 0.054931 | 121.2982 | 121.3257 | 121.3028 | 121.4493 | 121.3852 | -121.4905 | -121.5317 | 121.6049 | 121.3806 | 3.5431 | 2.2934
1029.1719 | 121.6553 | -0.42572 | 121.225 | 0.0095369 | 0 | 0.065176 | 0.065211 | 0.0026275 | -0.002493 | 0.0010468 | 0.0062865 | 0.0043942 | -1.3952 | 0.060111 | -0.0056226 | 0.010835 | -0.0019439 | 3.2547 | 121.0693 | -0.32044 | 121.2524 | -0.20599 | -0.31586 | -0.3479 | 1.9409 | 120.9915 | -0.35248 | 120.9366 | -0.28381 | -0.33417 | -0.26093 | 0.10528 | -0.15564 | 0.027465 | 0.21973 | 0.07782 | 0.10986 | -0.027465 | 0.004578 | 0.073242 | -0.23346 | -0.28839 | 0.14191 | 0.16479 | 0.091553 | 0.091553 | 0.018311 | 0.11444 | 121.5729 | 0.068665 | 121.2891 | 121.3898 | 121.344 | 121.4951 | 121.4172 | -121.5454 | -121.5775 | 121.6782 | 121.3623 | 3.6804 | 2.3666
1030.8906 | 121.6599 | -0.4303 | 121.225 | 0.0095369 | 0 | 0.064322 | 0.064356 | 0.00070491 | 0.0015658 | 0.00083317 | 0.0062865 | 0.003967 | -1.3952 | 0.057121 | -0.0034864 | 0.0082715 | 0.00019229 | 3.2455 | 121.0831 | -0.29755 | 121.2341 | -0.19226 | -0.31586 | -0.34332 | 1.9455 | 120.9915 | -0.35248 | 120.9503 | -0.27008 | -0.31586 | -0.25177 | 0.13275 | -0.14191 | 0.009155 | 0.23804 | 0.086975 | 0.11444 | -0.045777 | -0.018311 | 0.07782 | -0.23346 | -0.27466 | 0.16022 | 0.17853 | 0.11444 | 0.10071 | 0.036621 | 0.10528 | 121.5317 | 0.082397 | 121.3028 | 121.3806 | 121.344 | 121.5134 | 121.4218 | -121.5225 | -121.5775 | 121.6644 | 121.3806 | 3.6758 | 2.3758
1032.6094 | 121.7194 | -0.38452 | 121.17 | -0.0057221 | 0 | 0.061545 | 0.061152 | 0.00027771 | -0.0029202 | 0.0012604 | 0.00018312 | 0.00012184 | -1.3959 | 0.06652 | -0.0034864 | 0.0095533 | -0.0021575 | 3.2272 | 120.9915 | -0.24261 | 121.312 | -0.068665 | -0.20142 | -0.25635 | 1.9592 | 120.9412 | -0.32501 | 121.0144 | -0.19226 | -0.21973 | -0.18768 | 0.14191 | -0.17853 | 0.14191 | 0.31586 | 0.12817 | 0.1831 | -0.013733 | 0.041199 | 0.059509 | -0.22888 | -0.15564 | 0.19226 | 0.19684 | 0.16479 | 0.13733 | 0.10529 | 0.17395 | 121.5546 | 0.13275 | 121.3394 | 121.2341 | 121.2662 | 121.376 | 121.3257 | -121.4127 | -121.4951 | 121.6965 | 121.3989 | 3.6118 | 2.3438
1034.3594 | 121.7194 | -0.37994 | 121.1655 | -0.0057221 | 0 | 0.063254 | 0.062006 | 0.0069001 | -0.0020658 | 0.00019217 | 0.024597 | 0.0020444 | -1.3946 | 0.063529 | 0.0012134 | 0.0099805 | 0.00019229 | 3.2272 | 121.0419 | -0.23346 | 121.3303 | -0.10071 | -0.23804 | -0.26093 | 1.973 | 120.9824 | -0.3479 | 121.0144 | -0.20142 | -0.25177 | -0.17395 | 0.14649 | -0.1236 | 0.16479 | 0.27924 | 0.11902 | 0.14191 | -0.027466 | -0.004578 | 0.032044 | -0.1831 | -0.15106 | 0.17853 | 0.20599 | 0.12817 | 0.17395 | 0.09613 | 0.13275 | 121.5637 | 0.14648 | 121.3623 | 121.2753 | 121.3303 | 121.4218 | 121.3623 | -121.3989 | -121.5134 | 121.7102 | 121.3943 | 3.6072 | 2.3529
1036.0625 | 121.6415 | -0.41657 | 121.2067 | 0.017166 | 0 | 0.064108 | 0.066065 | -0.0031403 | -0.0022794 | 0.002115 | 0.00018312 | 0.0028988 | -1.3948 | 0.056266 | -0.0034864 | 0.0089123 | -0.00087591 | 3.273 | 121.0876 | -0.28839 | 121.2479 | -0.19226 | -0.32044 | -0.3479 | 1.9043 | 121.0007 | -0.32501 | 120.9412 | -0.29297 | -0.35248 | -0.25177 | 0.12817 | -0.11902 | 0.041199 | 0.2243 | 0.068665 | 0.09613 | -0.059509 | -0.032044 | 0.091553 | -0.20599 | -0.2655 | 0.1236 | 0.1648 | 0.064087 | 0.073242 | -0.027466 | 0.09613 | 121.5363 | 0.032043 | 121.2662 | 121.376 | 121.3257 | 121.5042 | 121.4172 | -121.4951 | -121.5317 | 121.6644 | 121.3577 | 3.6896 | 2.3209
1037.8281 | 121.6187 | -0.39825 | 121.2112 | 0.0095369 | 0 | 0.063681 | 0.064997 | 0.0017731 | -0.0022794 | 0.00040597 | -0.0028687 | 0.0020444 | -1.3935 | 0.058402 | -0.006477 | 0.0082715 | -0.00066231 | 3.273 | 121.0831 | -0.27466 | 121.2433 | -0.20142 | -0.31128 | -0.33875 | 1.886 | 121.0144 | -0.32044 | 120.9412 | -0.28381 | -0.36163 | -0.26093 | 0.1236 | -0.12817 | 0.032043 | 0.19684 | 0.059509 | 0.086975 | -0.064087 | -0.036621 | 0.077819 | -0.19684 | -0.27008 | 0.11444 | 0.13733 | 0.036621 | 0.05951 | -0.041198 | 0.073242 | 121.5179 | 0.036622 | 121.2616 | 121.3577 | 121.3348 | 121.4813 | 121.4127 | -121.4859 | -121.5317 | 121.6415 | 121.3394 | 3.6713 | 2.2842
1039.5156 | 121.582 | -0.41199 | 121.257 | -0.0057221 | 0 | 0.064749 | 0.064997 | 0.0013459 | -0.0020658 | -0.00044863 | -0.0028687 | 0.00054904 | -1.3944 | 0.060752 | -0.0045544 | 0.011476 | 0.0012603 | 3.1998 | 121.0693 | -0.2655 | 121.17 | -0.3067 | -0.38452 | -0.41657 | 1.7715 | 121.0007 | -0.32959 | 120.8908 | -0.34332 | -0.38452 | -0.27466 | 0.14648 | -0.18768 | -0.086975 | 0.10529 | -0.004578 | 0.027466 | -0.15106 | -0.11902 | 0.082397 | -0.25635 | -0.36621 | 0.068664 | 0.13733 | 0.027466 | 0.054932 | -0.054931 | -0.041199 | 121.4355 | -0.013733 | 121.2204 | 121.3348 | 121.3303 | 121.4813 | 121.4127 | -121.5225 | -121.5866 | 121.582 | 121.3028 | 3.6118 | 2.1835
1041.2656 | 121.6827 | -0.35706 | 121.2204 | 0.040054 | 0 | 0.066672 | 0.064783 | -0.0012177 | -0.0014248 | -0.00087583 | 0.01239 | 0.0020444 | -1.3942 | 0.063529 | -0.0041272 | 0.0097669 | -0.00023491 | 3.2867 | 121.0831 | -0.25177 | 121.3074 | -0.082397 | -0.21515 | -0.25177 | 1.9547 | 120.9915 | -0.31586 | 121.0052 | -0.21515 | -0.25635 | -0.21057 | 0.10529 | -0.13733 | 0.086975 | 0.27466 | 0.10529 | 0.14191 | 0 | 0.036621 | 0.041199 | -0.22888 | -0.21515 | 0.14191 | 0.14648 | 0.10071 | 0.10529 | 0.059509 | 0.16937 | 121.5591 | 0.10071 | 121.3211 | 121.3348 | 121.3074 | 121.4401 | 121.3486 | -121.4722 | -121.5363 | 121.6644 | 121.3623 | 3.6438 | 2.3117
1042.9844 | 121.6141 | -0.3891 | 121.2616 | 0.0019074 | 0 | 0.065176 | 0.064997 | 0.0039093 | 0.00028416 | -0.00044863 | -0.0059205 | 0.0031124 | -1.3952 | 0.060111 | -0.0037 | 0.0089123 | 0.0042511 | 3.3005 | 121.1151 | -0.27466 | 121.1884 | -0.27008 | -0.37537 | -0.40283 | 1.8127 | 121.0144 | -0.32501 | 120.9229 | -0.32959 | -0.37537 | -0.26093 | 0.11444 | -0.14648 | -0.073243 | 0.11902 | -0.013733 | 0.013733 | -0.12817 | -0.10071 | 0.064087 | -0.24719 | -0.33874 | 0.059509 | 0.12817 | 0.013733 | 0.064087 | -0.050354 | 0.004577 | 121.463 | -0.004578 | 121.2479 | 121.3898 | 121.3394 | 121.5042 | 121.4035 | -121.5363 | -121.5866 | 121.5775 | 121.312 | 3.6896 | 2.2018
1044.7344 | 121.7194 | -0.34332 | 121.2296 | -0.0057221 | 0 | 0.064322 | 0.063715 | 0.0030547 | -0.0033474 | -0.0017304 | -0.0028687 | 0.001617 | -1.3935 | 0.072502 | -0.0011364 | 0.010621 | -0.0027985 | 3.2867 | 121.0693 | -0.25177 | 121.2616 | -0.16937 | -0.28381 | -0.3067 | 1.9592 | 120.9824 | -0.29755 | 121.0327 | -0.20142 | -0.23346 | -0.15564 | 0.091553 | -0.16022 | 0.032044 | 0.17395 | 0.036621 | 0.05951 | -0.054932 | -0.032043 | 0.045777 | -0.24719 | -0.19684 | 0.14191 | 0.18768 | 0.10986 | 0.14191 | 0.064087 | 0.082397 | 121.5134 | 0.09613 | 121.3303 | 121.3211 | 121.2799 | 121.4127 | 121.3257 | -121.4813 | -121.5271 | 121.6049 | 121.376 | 3.6301 | 2.3026
1046.4844 | 121.7331 | -0.33417 | 121.2341 | -0.0057221 | 0 | 0.064536 | 0.063288 | 0.0030547 | -0.0014248 | 0.0012604 | 0.00018312 | -0.0015872 | -1.3976 | 0.059043 | -0.0013502 | 0.0093397 | -0.0021575 | 3.3554 | 121.0876 | -0.22888 | 121.3211 | -0.10986 | -0.23804 | -0.27466 | 1.9684 | 120.9503 | -0.27924 | 121.0419 | -0.16937 | -0.2243 | -0.13733 | 0.10528 | -0.14648 | 0.086975 | 0.2243 | 0.059509 | 0.09613 | -0.045776 | -0.009155 | 0.054931 | -0.28381 | -0.19226 | 0.16479 | 0.19684 | 0.10986 | 0.14191 | 0.054932 | 0.11902 | 121.55 | 0.10986 | 121.3211 | 121.3165 | 121.2296 | 121.4218 | 121.2845 | -121.463 | -121.5134 | 121.6553 | 121.376 | 3.6896 | 2.3026
1048.25 | 121.6827 | -0.35248 | 121.2158 | 0.017166 | 0 | 0.064322 | 0.064356 | 0.0011321 | -0.00035684 | -0.001303 | 0.0093383 | 0.00012184 | -1.3925 | 0.067161 | -0.0051954 | 0.010408 | 0.0021149 | 3.3096 | 121.0876 | -0.24261 | 121.2708 | -0.14191 | -0.26093 | -0.28381 | 1.8997 | 120.9824 | -0.29755 | 120.9824 | -0.22888 | -0.27924 | -0.20599 | 0.10986 | -0.12817 | 0.054932 | 0.21057 | 0.068665 | 0.091553 | -0.041198 | -0.01831 | 0.054932 | -0.23346 | -0.23346 | 0.1236 | 0.14648 | 0.073242 | 0.091552 | 0.01831 | 0.10071 | 121.5134 | 0.068664 | 121.2799 | 121.3303 | 121.2799 | 121.4401 | 121.3348 | -121.4584 | -121.5134 | 121.6232 | 121.3348 | 3.6621 | 2.2522
1050.0156 | 121.637 | -0.3891 | 121.2524 | 0.0095369 | 0 | 0.065604 | 0.065638 | -0.0016449 | -0.0027066 | -2.1434e-05 | -0.0028687 | 0.002258 | -1.3937 | 0.064811 | -0.0060498 | 0.0099805 | 0.00083309 | 3.3966 | 121.1105 | -0.2655 | 121.2753 | -0.1831 | -0.28381 | -0.31586 | 1.9501 | 121.0419 | -0.31128 | 120.9686 | -0.2655 | -0.32501 | -0.23804 | 0.1236 | -0.14191 | 0.022889 | 0.20599 | 0.073242 | 0.10529 | -0.050354 | -0.01831 | 0.07782 | -0.21057 | -0.28381 | 0.1236 | 0.15106 | 0.064087 | 0.073242 | -0.013733 | 0.082398 | 121.5408 | 0.045776 | 121.2799 | 121.376 | 121.3531 | 121.4996 | 121.431 | -121.5179 | -121.5637 | 121.6644 | 121.3577 | 3.7857 | 2.3392
1051.7656 | 121.7422 | -0.34332 | 121.2341 | 0.0019074 | 0 | 0.062186 | 0.063929 | 0.0045501 | -0.002493 | -0.003012 | -0.0028687 | 0.0028988 | -1.3937 | 0.064597 | -0.003059 | 0.0091261 | -0.0027985 | 3.3325 | 121.1105 | -0.25635 | 121.2662 | -0.16937 | -0.28839 | -0.3067 | 1.9272 | 120.9961 | -0.27466 | 121.0327 | -0.19226 | -0.23804 | -0.14648 | 0.086975 | -0.1236 | 0.032043 | 0.17395 | 0.036621 | 0.054932 | -0.050354 | -0.032043 | 0.068665 | -0.23804 | -0.20142 | 0.15106 | 0.19684 | 0.10529 | 0.12817 | 0.036621 | 0.086975 | 121.5225 | 0.082397 | 121.3074 | 121.3669 | 121.2708 | 121.4539 | 121.3394 | -121.4905 | -121.5088 | 121.6095 | 121.376 | 3.6758 | 2.2705
1053.4531 | 121.6736 | -0.36163 | 121.2387 | 0.0019074 | 0 | 0.061545 | 0.061365 | -0.0035675 | -0.0031338 | -0.0042938 | 0.00018312 | 0.0020444 | -1.3933 | 0.06182 | -0.0056226 | 0.010621 | 0.0012603 | 3.4012 | 121.051 | -0.2243 | 121.3257 | -0.091553 | -0.20142 | -0.26093 | 1.9867 | 120.9824 | -0.28381 | 120.9915 | -0.20599 | -0.25177 | -0.19226 | 0.13733 | -0.18768 | 0.086976 | 0.27008 | 0.10071 | 0.16022 | -0.036621 | 0.022888 | 0.07782 | -0.25635 | -0.24719 | 0.15564 | 0.16937 | 0.10986 | 0.091552 | 0.032043 | 0.13275 | 121.55 | 0.077819 | 121.2753 | 121.2753 | 121.2662 | 121.4127 | 121.344 | -121.463 | -121.5225 | 121.6873 | 121.3531 | 3.7628 | 2.3483
1055.2344 | 121.6507 | -0.37079 | 121.2662 | 0.032425 | 0 | 0.066458 | 0.064356 | 0.0026275 | -0.0016384 | 0.00083317 | 0.0093383 | 0.0026852 | -1.3957 | 0.05947 | -0.001991 | 0.0080579 | 0.0021149 | 3.4515 | 121.138 | -0.2655 | 121.2845 | -0.16479 | -0.25177 | -0.29297 | 1.9821 | 121.0464 | -0.32959 | 120.9778 | -0.23804 | -0.28381 | -0.21057 | 0.10529 | -0.12817 | 0.018311 | 0.20599 | 0.07782 | 0.11902 | -0.027466 | 0.013733 | 0.041199 | -0.21973 | -0.28839 | 0.13275 | 0.16022 | 0.086976 | 0.11902 | 0.045777 | 0.10071 | 121.55 | 0.091553 | 121.3074 | 121.4035 | 121.376 | 121.5088 | 121.4172 | -121.5317 | -121.5958 | 121.6553 | 121.3486 | 3.8223 | 2.3529
1057.0156 | 121.6095 | -0.39368 | 121.2753 | 0.062942 | 0 | 0.063467 | 0.068842 | 0.0032685 | -0.001852 | 0.0027558 | 0.01239 | 0.0026852 | -1.3931 | 0.066093 | -0.0062634 | 0.0072035 | 0.0076691 | 3.4103 | 121.1563 | -0.28839 | 121.2433 | -0.20599 | -0.28839 | -0.31586 | 1.9318 | 121.0693 | -0.31586 | 120.9274 | -0.28381 | -0.32959 | -0.23804 | 0.10529 | -0.11902 | -0.032044 | 0.18768 | 0.07782 | 0.10529 | -0.027466 | 0 | 0.07782 | -0.20599 | -0.3479 | 0.10986 | 0.15564 | 0.064087 | 0.07782 | -0.013733 | 0.082397 | 121.5317 | 0.032044 | 121.2433 | 121.4447 | 121.3852 | 121.55 | 121.463 | -121.5637 | -121.5912 | 121.637 | 121.3211 | 3.804 | 2.3254
1058.7969 | 121.6553 | -0.37079 | 121.2799 | 0.032425 | 0 | 0.064108 | 0.064997 | -0.0018585 | -0.001852 | 0.00040597 | 0.0093383 | 0.0020444 | -1.3933 | 0.059898 | -0.0037 | 0.0084851 | 0.00040589 | 3.4561 | 121.1243 | -0.27924 | 121.2845 | -0.17853 | -0.25635 | -0.3067 | 1.973 | 121.0602 | -0.31586 | 120.9824 | -0.24261 | -0.28839 | -0.20599 | 0.091553 | -0.15564 | 0.004578 | 0.19226 | 0.064087 | 0.11444 | -0.027466 | 0.022888 | 0.054932 | -0.21973 | -0.29755 | 0.12817 | 0.16479 | 0.082398 | 0.10986 | 0.027466 | 0.10071 | 121.5637 | 0.073242 | 121.2982 | 121.4035 | 121.376 | 121.4951 | 121.431 | -121.5591 | -121.5958 | 121.6553 | 121.3531 | 3.8269 | 2.3438
1060.4844 | 121.6095 | -0.38452 | 121.2891 | 0.0019074 | 0 | 0.062399 | 0.061365 | -0.0024995 | -0.003561 | -2.1434e-05 | 0.00018312 | 0.0014034 | -1.3937 | 0.059898 | -0.0069044 | 0.0063489 | -0.0010895 | 3.3966 | 121.1197 | -0.24261 | 121.2158 | -0.2243 | -0.3067 | -0.35248 | 1.8951 | 121.0327 | -0.30212 | 120.9183 | -0.28381 | -0.32044 | -0.25635 | 0.14191 | -0.16937 | -0.073242 | 0.16022 | 0.032043 | 0.077819 | -0.10986 | -0.064087 | 0.082397 | -0.25635 | -0.37079 | 0.10071 | 0.12817 | 0.064086 | 0.045776 | -0.018311 | 0.018311 | 121.4584 | 0.018311 | 121.2204 | 121.3623 | 121.3348 | 121.5042 | 121.4172 | -121.5317 | -121.5912 | 121.6003 | 121.3028 | 3.7811 | 2.2797
1062.2812 | 121.7697 | -0.34332 | 121.2433 | 0.0019074 | 0 | 0.064108 | 0.062861 | -0.0042083 | -0.0031338 | 0.00083317 | -0.0028687 | -0.00094636 | -1.395 | 0.062461 | -0.001991 | 0.010621 | 0.0012603 | 3.4515 | 121.0556 | -0.21973 | 121.344 | -0.059509 | -0.16022 | -0.20599 | 2.0782 | 121.0052 | -0.28381 | 121.0876 | -0.1236 | -0.17395 | -0.15106 | 0.1236 | -0.18768 | 0.10071 | 0.28381 | 0.13733 | 0.18311 | 0.013733 | 0.05951 | 0.05951 | -0.23804 | -0.15564 | 0.21973 | 0.19226 | 0.16937 | 0.13275 | 0.10986 | 0.16022 | 121.5637 | 0.16022 | 121.3715 | 121.2753 | 121.2891 | 121.3989 | 121.3486 | -121.463 | -121.5271 | 121.6873 | 121.431 | 3.7949 | 2.4216
1064.0625 | 121.6919 | -0.33875 | 121.2616 | 0.040054 | 0 | 0.065817 | 0.065424 | 0.0017731 | -0.0016384 | -0.0010894 | 0.01239 | 0.001617 | -1.3937 | 0.065238 | -0.00070919 | 0.011476 | 0.0033967 | 3.4653 | 121.1105 | -0.22888 | 121.3348 | -0.07782 | -0.21515 | -0.22888 | 2.0004 | 121.0236 | -0.28839 | 121.0144 | -0.20142 | -0.24719 | -0.1831 | 0.10986 | -0.15106 | 0.073242 | 0.26093 | 0.10986 | 0.1236 | 0 | 0.013733 | 0.050354 | -0.23804 | -0.24719 | 0.13733 | 0.15564 | 0.091553 | 0.10529 | 0.041199 | 0.15106 | 121.5637 | 0.086975 | 121.3028 | 121.3394 | 121.312 | 121.4493 | 121.3623 | -121.4905 | -121.55 | 121.6736 | 121.3531 | 3.804 | 2.3392
1065.8438 | 121.6095 | -0.39368 | 121.3028 | -0.0057221 | 0 | 0.065176 | 0.066279 | 0.0011321 | -0.001852 | -2.1434e-05 | 0.01239 | 0.0028988 | -1.3927 | 0.06182 | -0.0056226 | 0.0091261 | 0.0025421 | 3.4653 | 121.138 | -0.29755 | 121.2616 | -0.19684 | -0.27008 | -0.3067 | 1.9501 | 121.1105 | -0.33875 | 120.9457 | -0.28839 | -0.32501 | -0.24261 | 0.096131 | -0.16479 | -0.041198 | 0.19684 | 0.086975 | 0.1236 | -0.009156 | 0.027465 | 0.054932 | -0.19226 | -0.35706 | 0.10529 | 0.15106 | 0.068665 | 0.09613 | 0.013733 | 0.10071 | 121.5591 | 0.050354 | 121.2845 | 121.4355 | 121.4493 | 121.5317 | 121.5042 | -121.6003 | -121.6415 | 121.6553 | 121.3394 | 3.8589 | 2.3438
1067.5312 | 121.6141 | -0.37994 | 121.2936 | -0.0057221 | 0 | 0.061118 | 0.065638 | 0.00049131 | -0.0037746 | -0.0015166 | -0.0059205 | 0.0020444 | -1.3955 | 0.057975 | -0.006477 | 0.0084851 | 0.0014741 | 3.4607 | 121.1243 | -0.22888 | 121.2387 | -0.19226 | -0.27008 | -0.32044 | 1.9455 | 121.0556 | -0.3067 | 120.9457 | -0.27466 | -0.31128 | -0.25177 | 0.15106 | -0.16937 | -0.054932 | 0.18768 | 0.059509 | 0.10986 | -0.091553 | -0.041199 | 0.073242 | -0.23804 | -0.3479 | 0.10529 | 0.12817 | 0.068665 | 0.054932 | -0.004577 | 0.036621 | 121.4676 | 0.032044 | 121.2524 | 121.3531 | 121.3623 | 121.5042 | 121.4355 | -121.5225 | -121.6003 | 121.6187 | 121.3257 | 3.8406 | 2.3254
1069.2969 | 121.7468 | -0.3067 | 121.2479 | 0.0019074 | 0 | 0.066245 | 0.062647 | 0.00070491 | -0.0016384 | 0.00040597 | -0.0059205 | 0.0018306 | -1.3935 | 0.063957 | 0.0016406 | 0.010621 | -0.0013031 | 3.4882 | 121.0922 | -0.20599 | 121.344 | -0.073242 | -0.20599 | -0.24261 | 2.1011 | 121.0419 | -0.29297 | 121.0876 | -0.15106 | -0.19226 | -0.12817 | 0.10071 | -0.15564 | 0.09613 | 0.23346 | 0.064087 | 0.10071 | -0.036621 | 0 | 0.013733 | -0.20599 | -0.16022 | 0.15564 | 0.17853 | 0.11444 | 0.16479 | 0.10071 | 0.13275 | 121.55 | 0.14191 | 121.3806 | 121.2982 | 121.3348 | 121.3989 | 121.3486 | -121.4539 | -121.5408 | 121.6507 | 121.3943 | 3.7949 | 2.4078
1071.0781 | 121.7606 | -0.33417 | 121.257 | -0.0057221 | 0 | 0.063254 | 0.063074 | -0.0010041 | -0.0020658 | -0.00087583 | -0.0028687 | 0.00012184 | -1.3948 | 0.057762 | -0.0049818 | 0.010408 | -0.0038665 | 3.4698 | 121.0785 | -0.21973 | 121.344 | -0.054932 | -0.16479 | -0.20142 | 2.0828 | 121.0098 | -0.25635 | 121.0831 | -0.12817 | -0.15106 | -0.11902 | 0.11444 | -0.17853 | 0.086975 | 0.27924 | 0.13275 | 0.16937 | 0.018311 | 0.054932 | 0.077819 | -0.24719 | -0.17395 | 0.20599 | 0.21515 | 0.1831 | 0.13733 | 0.10529 | 0.16479 | 121.5637 | 0.12817 | 121.3394 | 121.2982 | 121.2662 | 121.4127 | 121.344 | -121.4767 | -121.5134 | 121.6782 | 121.4172 | 3.804 | 2.417
1072.7969 | 121.7514 | -0.31586 | 121.2524 | 0.0095369 | 0 | 0.062399 | 0.062647 | -0.0024995 | -0.0044156 | -0.0017304 | -0.0059205 | 0.00033544 | -1.3959 | 0.06887 | -0.0041272 | 0.0078443 | -0.0034393 | 3.5019 | 121.0648 | -0.19684 | 121.3577 | -0.032043 | -0.15564 | -0.20599 | 2.1057 | 121.0098 | -0.24719 | 121.0739 | -0.13275 | -0.16937 | -0.12817 | 0.11902 | -0.18768 | 0.10529 | 0.28381 | 0.10986 | 0.16022 | -0.009156 | 0.041198 | 0.068665 | -0.24261 | -0.17853 | 0.18311 | 0.18768 | 0.14648 | 0.11902 | 0.077819 | 0.1648 | 121.5546 | 0.11444 | 121.3211 | 121.2616 | 121.257 | 121.3806 | 121.3257 | -121.4493 | -121.4996 | 121.6736 | 121.3898 | 3.8177 | 2.4216
1074.5 | 121.6461 | -0.35706 | 121.2662 | -0.0057221 | 0 | 0.063681 | 0.063929 | -0.0052765 | -0.0020658 | 0.0010468 | -0.0028687 | -9.1956e-05 | -1.3959 | 0.060966 | -0.0041272 | 0.0086987 | 0.0025421 | 3.5248 | 121.0968 | -0.20142 | 121.3211 | -0.11902 | -0.20599 | -0.26093 | 2.0142 | 121.0419 | -0.25635 | 120.9686 | -0.22888 | -0.27008 | -0.21973 | 0.15564 | -0.16937 | 0.054932 | 0.23804 | 0.096131 | 0.15106 | -0.059509 | -0.004578 | 0.10071 | -0.2243 | -0.29755 | 0.12817 | 0.13733 | 0.086975 | 0.036621 | -0.013733 | 0.082397 | 121.5225 | 0.027466 | 121.225 | 121.2982 | 121.2982 | 121.4539 | 121.3989 | -121.4676 | -121.5225 | 121.6782 | 121.3257 | 3.8818 | 2.3712
1076.2812 | 121.7148 | -0.33417 | 121.2616 | -0.013352 | 0 | 0.060904 | 0.064783 | -0.0016449 | -0.0014248 | 0.00083317 | 0.00018312 | 0.002258 | -1.3967 | 0.063102 | -0.0015638 | 0.0082715 | 0.0019013 | 3.4653 | 121.1334 | -0.23346 | 121.2845 | -0.18768 | -0.28381 | -0.30212 | 1.9638 | 121.0464 | -0.2655 | 121.0464 | -0.19226 | -0.23804 | -0.16022 | 0.10071 | -0.12817 | 0.022888 | 0.14648 | 0.032043 | 0.050354 | -0.068665 | -0.050354 | 0.068664 | -0.21515 | -0.21515 | 0.14191 | 0.17395 | 0.09613 | 0.10529 | 0.027466 | 0.045776 | 121.5179 | 0.073242 | 121.312 | 121.3669 | 121.312 | 121.4676 | 121.3806 | -121.4951 | -121.5271 | 121.6187 | 121.3806 | 3.7994 | 2.298
1078.0469 | 121.7285 | -0.31128 | 121.2479 | 0.0095369 | 0 | 0.062827 | 0.063715 | -0.00014949 | -0.0039884 | -0.0027984 | 0.00018312 | 0.00076264 | -1.3963 | 0.061179 | -0.0013502 | 0.0080579 | -0.0025849 | 3.5019 | 121.1288 | -0.21057 | 121.312 | -0.1236 | -0.2243 | -0.25635 | 2.037 | 121.0327 | -0.25635 | 121.0785 | -0.16022 | -0.21515 | -0.13275 | 0.10071 | -0.11902 | 0.064087 | 0.18768 | 0.054931 | 0.086975 | -0.045777 | -0.013733 | 0.054931 | -0.21515 | -0.16937 | 0.15106 | 0.17853 | 0.09613 | 0.1236 | 0.041199 | 0.086975 | 121.5225 | 0.096131 | 121.3348 | 121.3394 | 121.2891 | 121.4401 | 121.344 | -121.4584 | -121.5042 | 121.6232 | 121.3898 | 3.8132 | 2.3483
1079.8281 | 121.6919 | -0.32501 | 121.2708 | 0.0095369 | 0 | 0.064322 | 0.063929 | -0.0029267 | -0.0022794 | -0.00044863 | 0.0093383 | 0.0024716 | -1.395 | 0.068656 | -0.0058362 | 0.011262 | 0.0023285 | 3.5019 | 121.1288 | -0.21973 | 121.312 | -0.13275 | -0.2243 | -0.27008 | 1.9547 | 121.0327 | -0.2655 | 121.0052 | -0.21515 | -0.24719 | -0.1831 | 0.10529 | -0.14191 | 0.041199 | 0.19226 | 0.054931 | 0.10071 | -0.050354 | -0.004577 | 0.059509 | -0.23804 | -0.2655 | 0.10986 | 0.14191 | 0.07782 | 0.082398 | 0.018311 | 0.086976 | 121.5317 | 0.050354 | 121.2708 | 121.3486 | 121.2982 | 121.4539 | 121.3577 | -121.4905 | -121.5363 | 121.637 | 121.3303 | 3.8269 | 2.2797
1081.5156 | 121.7239 | -0.32044 | 121.2616 | 0.017166 | 0 | 0.063895 | 0.061365 | -0.0022857 | 0.00028416 | -0.00066223 | -0.0028687 | 0.00097624 | -1.3937 | 0.06417 | -0.0037 | 0.0086987 | -0.0030121 | 3.5019 | 121.1243 | -0.21057 | 121.3165 | -0.11444 | -0.22888 | -0.26093 | 1.9821 | 121.0327 | -0.25635 | 121.0373 | -0.16937 | -0.21057 | -0.15564 | 0.10986 | -0.13733 | 0.054931 | 0.20599 | 0.05951 | 0.091553 | -0.050354 | -0.018311 | 0.064087 | -0.22888 | -0.22431 | 0.15106 | 0.1648 | 0.10986 | 0.10071 | 0.045777 | 0.09613 | 121.5271 | 0.086975 | 121.2936 | 121.3348 | 121.2891 | 121.4447 | 121.3531 | -121.4722 | -121.5179 | 121.637 | 121.3577 | 3.8223 | 2.3026
1083.2969 | 121.6324 | -0.36621 | 121.2936 | 0.047683 | 0 | 0.064749 | 0.065851 | -0.00079049 | -0.0029202 | 0.0016876 | 0.018494 | 0.0035396 | -1.3944 | 0.05947 | -0.0037 | 0.0082715 | 0.00019229 | 3.5614 | 121.17 | -0.27924 | 121.2845 | -0.17853 | -0.26093 | -0.29297 | 1.9501 | 121.1014 | -0.31128 | 120.9686 | -0.25635 | -0.3067 | -0.21515 | 0.086975 | -0.1236 | -0.009155 | 0.18768 | 0.073242 | 0.10529 | -0.013733 | 0.018311 | 0.054932 | -0.19226 | -0.32501 | 0.10986 | 0.15106 | 0.059509 | 0.09613 | 0.004577 | 0.10071 | 121.5637 | 0.054931 | 121.2799 | 121.4493 | 121.4127 | 121.5363 | 121.4676 | -121.5729 | -121.6049 | 121.6507 | 121.3348 | 3.9276 | 2.3163
1085.0781 | 121.6965 | -0.31586 | 121.2799 | 0.017166 | 0 | 0.061545 | 0.064356 | 6.4114e-05 | -0.0016384 | 0.00040597 | 0.0032349 | 0.0020444 | -1.3963 | 0.060752 | -0.0049818 | 0.0084851 | -0.0036529 | 3.5202 | 121.106 | -0.19684 | 121.312 | -0.12817 | -0.23346 | -0.27008 | 1.9684 | 121.051 | -0.27008 | 121.0144 | -0.20599 | -0.23804 | -0.16937 | 0.11902 | -0.17395 | 0.032044 | 0.18768 | 0.045776 | 0.082398 | -0.073243 | -0.036621 | 0.045776 | -0.22888 | -0.2655 | 0.10986 | 0.14648 | 0.07782 | 0.10071 | 0.032044 | 0.068664 | 121.5088 | 0.064087 | 121.2845 | 121.3028 | 121.3211 | 121.4218 | 121.3669 | -121.4767 | -121.55 | 121.6278 | 121.3303 | 3.8361 | 2.2842
1086.8594 | 121.7285 | -0.31128 | 121.2799 | -0.0057221 | 0 | 0.063895 | 0.063929 | -0.0010041 | -0.0039884 | -0.0017304 | -0.0028687 | 0.00076264 | -1.3955 | 0.063102 | -0.0049818 | 0.0097669 | 0.0025421 | 3.6026 | 121.0922 | -0.19684 | 121.4035 | -0.041199 | -0.13275 | -0.19226 | 2.1011 | 121.0281 | -0.25177 | 121.0922 | -0.11444 | -0.16937 | -0.12817 | 0.11444 | -0.18768 | 0.1236 | 0.27008 | 0.11902 | 0.17853 | 0.004577 | 0.064087 | 0.059509 | -0.25177 | -0.18768 | 0.19684 | 0.1831 | 0.14191 | 0.1236 | 0.082397 | 0.15564 | 121.6003 | 0.13733 | 121.344 | 121.2891 | 121.2799 | 121.4035 | 121.3394 | -121.4767 | -121.5317 | 121.7148 | 121.4035 | 3.9139 | 2.4124
1088.5625 | 121.7285 | -0.30212 | 121.2799 | 0.0095369 | 0 | 0.066885 | 0.066279 | -0.00036309 | 0.0028476 | 0.003183 | 0.015442 | 0.0024716 | -1.3965 | 0.068656 | -0.0011364 | 0.0093397 | -0.00044851 | 3.6209 | 121.1655 | -0.21057 | 121.4081 | -0.013733 | -0.16937 | -0.20142 | 2.1011 | 121.051 | -0.27008 | 121.0922 | -0.13275 | -0.17853 | -0.1236 | 0.091553 | -0.11444 | 0.12817 | 0.28839 | 0.10071 | 0.13275 | 0.009155 | 0.041198 | 0.032043 | -0.22888 | -0.18768 | 0.16937 | 0.17853 | 0.1236 | 0.14649 | 0.091553 | 0.19684 | 121.6187 | 0.13733 | 121.3623 | 121.376 | 121.3211 | 121.4676 | 121.3531 | -121.4905 | -121.55 | 121.7102 | 121.3943 | 3.923 | 2.4033
1090.3438 | 121.7148 | -0.31128 | 121.2845 | 0.0019074 | 0 | 0.066245 | 0.063074 | -0.0010041 | -0.0022794 | -0.00044863 | 0.00018312 | -0.00094636 | -1.3961 | 0.060539 | -0.0043408 | 0.0099805 | -0.00087591 | 3.6255 | 121.0922 | -0.1831 | 121.3898 | -0.059509 | -0.16937 | -0.21057 | 2.0691 | 121.0236 | -0.23804 | 121.0831 | -0.1236 | -0.17853 | -0.14648 | 0.12817 | -0.19226 | 0.10529 | 0.25177 | 0.10071 | 0.14191 | -0.027466 | 0.013732 | 0.073242 | -0.26093 | -0.20142 | 0.18768 | 0.16479 | 0.13275 | 0.091553 | 0.059509 | 0.1236 | 121.5729 | 0.11444 | 121.3211 | 121.2753 | 121.2616 | 121.4035 | 121.3348 | -121.4676 | -121.5225 | 121.701 | 121.3943 | 3.9368 | 2.3804
1092.0469 | 121.7377 | -0.32044 | 121.2708 | 0.0019074 | 0 | 0.06304 | 0.063929 | -0.00057689 | -0.002493 | -0.00087583 | -0.0059205 | 0.00054904 | -1.3955 | 0.066947 | -0.0037 | 0.011476 | -0.0013031 | 3.5934 | 121.1197 | -0.1831 | 121.3303 | -0.09613 | -0.19684 | -0.21057 | 2.0554 | 121.0327 | -0.25635 | 121.0785 | -0.13275 | -0.16937 | -0.1236 | 0.13733 | -0.15106 | 0.059509 | 0.22431 | 0.10986 | 0.1236 | -0.027466 | -0.013733 | 0.064087 | -0.23804 | -0.19226 | 0.18768 | 0.19684 | 0.15106 | 0.13275 | 0.086975 | 0.086975 | 121.5134 | 0.1236 | 121.3348 | 121.3028 | 121.2891 | 121.4401 | 121.3531 | -121.4539 | -121.5271 | 121.6507 | 121.3989 | 3.9139 | 2.3758
1093.8281 | 121.7331 | -0.28381 | 121.2524 | 0.0019074 | 0 | 0.06304 | 0.064142 | -0.0010041 | -0.0031338 | -0.0021576 | 0.00018312 | 0.00012184 | -1.3963 | 0.066947 | -0.0028454 | 0.0093397 | -0.0023713 | 3.6438 | 121.0876 | -0.16937 | 121.4081 | -0.018311 | -0.14648 | -0.20142 | 2.1149 | 121.0464 | -0.23346 | 121.0876 | -0.10986 | -0.14648 | -0.1236 | 0.11444 | -0.16479 | 0.15564 | 0.2655 | 0.082397 | 0.13733 | -0.032043 | 0.022889 | 0.050354 | -0.20599 | -0.16479 | 0.17395 | 0.16022 | 0.13733 | 0.10986 | 0.086975 | 0.15106 | 121.5775 | 0.1236 | 121.3211 | 121.257 | 121.2799 | 121.3715 | 121.3303 | -121.4218 | -121.4859 | 121.6919 | 121.3715 | 3.9276 | 2.3987
1095.5938 | 121.6049 | -0.34332 | 121.3303 | -0.0057221 | 0 | 0.062827 | 0.063502 | -0.0093353 | -0.0029202 | 0.0023286 | 0.01239 | 0.0037532 | -1.392 | 0.06887 | -0.0073316 | 0.0074171 | -0.0019439 | 3.6026 | 121.1609 | -0.21973 | 121.2936 | -0.15106 | -0.2655 | -0.27008 | 1.9958 | 121.1288 | -0.32501 | 120.9595 | -0.27008 | -0.3067 | -0.21515 | 0.1236 | -0.16937 | -0.036621 | 0.19226 | 0.073242 | 0.07782 | -0.050354 | -0.045776 | 0.018311 | -0.20142 | -0.37079 | 0.073242 | 0.12817 | 0.036621 | 0.10986 | 0.01831 | 0.068665 | 121.5134 | 0.054931 | 121.2845 | 121.3806 | 121.4539 | 121.5042 | 121.4722 | -121.55 | -121.6553 | 121.637 | 121.3028 | 3.9459 | 2.3392
1097.3125 | 121.7377 | -0.29297 | 121.2799 | 0.0095369 | 0 | 0.06774 | 0.066065 | -0.0018585 | -0.0027066 | -0.0021576 | -0.0028687 | 0.00097624 | -1.3993 | 0.066947 | -0.00028199 | 0.010194 | -0.0013031 | 3.6575 | 121.1288 | -0.17853 | 121.3715 | -0.054932 | -0.19226 | -0.23346 | 2.0828 | 121.0281 | -0.23346 | 121.1105 | -0.11902 | -0.16937 | -0.091553 | 0.11444 | -0.15106 | 0.091553 | 0.23804 | 0.05951 | 0.10071 | -0.054931 | -0.013733 | 0.05951 | -0.25177 | -0.16937 | 0.17395 | 0.20142 | 0.1236 | 0.14191 | 0.064086 | 0.1236 | 121.55 | 0.11444 | 121.344 | 121.3074 | 121.2616 | 121.4218 | 121.3211 | -121.4584 | -121.5134 | 121.6644 | 121.4035 | 3.9505 | 2.3758
1099.0938 | 121.6003 | -0.33875 | 121.3074 | -0.0057221 | 0 | 0.063467 | 0.064783 | 0.00027771 | -0.002493 | 0.00040597 | -0.0028687 | 0.003326 | -1.3965 | 0.058189 | -0.0032728 | 0.0086987 | -0.0023713 | 3.6484 | 121.138 | -0.21973 | 121.2845 | -0.1831 | -0.31128 | -0.32501 | 1.9821 | 121.0739 | -0.27466 | 120.9641 | -0.2655 | -0.33417 | -0.21515 | 0.11902 | -0.16937 | -0.022888 | 0.15564 | 0.013733 | 0.027466 | -0.10529 | -0.091552 | 0.064087 | -0.23346 | -0.34332 | 0.073242 | 0.1236 | 0.004578 | 0.059509 | -0.059509 | 0.036622 | 121.5042 | 0.009155 | 121.2387 | 121.3577 | 121.3486 | 121.4767 | 121.4127 | -121.5271 | -121.582 | 121.6232 | 121.3028 | 3.9871 | 2.3209
1100.8594 | 121.7285 | -0.31128 | 121.2982 | 0.0095369 | 0 | 0.062399 | 0.063074 | -0.0012177 | -0.004202 | 0.002115 | 0.0032349 | 0.00054904 | -1.395 | 0.06887 | -0.0028454 | 0.0089123 | 0.00061949 | 3.6346 | 121.1151 | -0.20142 | 121.3303 | -0.09613 | -0.18768 | -0.24719 | 2.0187 | 121.0373 | -0.24719 | 121.0739 | -0.13733 | -0.16937 | -0.1236 | 0.10986 | -0.18311 | 0.032043 | 0.21515 | 0.064087 | 0.1236 | -0.045776 | 0.013733 | 0.064087 | -0.26093 | -0.2243 | 0.17395 | 0.18768 | 0.14191 | 0.1236 | 0.077819 | 0.10529 | 121.5317 | 0.10986 | 121.3211 | 121.3165 | 121.2845 | 121.4264 | 121.3486 | -121.4996 | -121.5454 | 121.6415 | 121.3852 | 3.9459 | 2.33
1102.5781 | 121.6873 | -0.31586 | 121.312 | 0.017166 | 0 | 0.063681 | 0.062861 | -0.00014949 | -0.003561 | -2.1434e-05 | 0.0062865 | 0.0035396 | -1.3955 | 0.065879 | -0.0024182 | 0.0093397 | 0.00061949 | 3.6438 | 121.1288 | -0.20599 | 121.3165 | -0.091553 | -0.21515 | -0.23804 | 2.0142 | 121.0648 | -0.2655 | 121.0373 | -0.20142 | -0.2243 | -0.16479 | 0.10986 | -0.18311 | 0.004577 | 0.2243 | 0.07782 | 0.10071 | -0.032043 | -0.009155 | 0.050354 | -0.24719 | -0.27466 | 0.11444 | 0.15106 | 0.091553 | 0.10071 | 0.041199 | 0.11444 | 121.5225 | 0.064087 | 121.3028 | 121.3348 | 121.3303 | 121.4447 | 121.3806 | -121.5179 | -121.5775 | 121.6324 | 121.3531 | 3.9597 | 2.33
1104.3594 | 121.7239 | -0.28381 | 121.2799 | 0.055313 | 0 | 0.064322 | 0.063929 | 0.0013459 | 0.00092496 | 0.0019012 | 0.015442 | 0.0028988 | -1.3948 | 0.065025 | -0.0017774 | 0.0097669 | 0.00040589 | 3.7262 | 121.138 | -0.2243 | 121.4127 | -0.013733 | -0.14648 | -0.17395 | 2.1423 | 121.0693 | -0.25177 | 121.0831 | -0.12817 | -0.16937 | -0.12817 | 0.059509 | -0.14191 | 0.13275 | 0.27008 | 0.10986 | 0.13733 | 0.050354 | 0.07782 | 0.032043 | -0.21057 | -0.19684 | 0.15564 | 0.15564 | 0.11444 | 0.1236 | 0.082397 | 0.21057 | 121.637 | 0.1236 | 121.3348 | 121.3623 | 121.3211 | 121.4218 | 121.3531 | -121.5042 | -121.5317 | 121.6965 | 121.3669 | 4.01 | 2.4261
1106.125 | 121.6141 | -0.32959 | 121.3074 | -0.0057221 | 0 | 0.06304 | 0.066706 | -0.0024995 | -0.001852 | -0.001303 | 0.00018312 | 0.003326 | -1.3946 | 0.061607 | -0.0015638 | 0.0097669 | -0.00023491 | 3.6667 | 121.17 | -0.2243 | 121.2616 | -0.2243 | -0.3067 | -0.32959 | 1.9821 | 121.1151 | -0.27008 | 120.9824 | -0.26093 | -0.31128 | -0.21057 | 0.10529 | -0.13733 | -0.045776 | 0.10529 | 0 | 0.022888 | -0.10529 | -0.082398 | 0.059509 | -0.19226 | -0.32501 | 0.068665 | 0.11902 | 0.018311 | 0.05951 | -0.041198 | 0 | 121.4859 | 0.009156 | 121.2524 | 121.3943 | 121.3852 | 121.4996 | 121.4447 | -121.5317 | -121.5775 | 121.5912 | 121.312 | 3.9963 | 2.3117
1107.8281 | 121.6003 | -0.33875 | 121.2982 | -0.0057221 | 0 | 0.065817 | 0.063288 | 0.00027771 | 0.00071136 | -0.0023712 | -0.0028687 | 0.0014034 | -1.395 | 0.059257 | -0.0028454 | 0.0099805 | -0.0051483 | 3.6392 | 121.2021 | -0.21057 | 121.2524 | -0.22888 | -0.32959 | -0.35706 | 1.9821 | 121.1014 | -0.26093 | 120.9961 | -0.28839 | -0.31586 | -0.20142 | 0.12817 | -0.096131 | -0.045777 | 0.10986 | -0.018311 | 0.009155 | -0.14648 | -0.11902 | 0.07782 | -0.19684 | -0.30212 | 0.050354 | 0.13733 | 0.022888 | 0.059509 | -0.054932 | -0.018311 | 121.463 | -0.027466 | 121.257 | 121.4127 | 121.3623 | 121.5408 | 121.4401 | -121.5088 | -121.5591 | 121.5912 | 121.3348 | 3.978 | 2.3209
1109.5781 | 121.6507 | -0.32501 | 121.2753 | -0.0057221 | 0 | 0.064108 | 0.066065 | 0.0011321 | -0.0039884 | -0.0017304 | -0.0028687 | 0.0014034 | -1.3944 | 0.055412 | -6.8386e-05 | 0.0084851 | -0.0038665 | 3.6667 | 121.1609 | -0.20599 | 121.2708 | -0.1831 | -0.3067 | -0.31128 | 2.0233 | 121.0831 | -0.25177 | 121.019 | -0.2243 | -0.27008 | -0.16937 | 0.11902 | -0.11444 | -0.004578 | 0.14191 | 0.013733 | 0.01831 | -0.10528 | -0.10071 | 0.073242 | -0.19226 | -0.25635 | 0.10071 | 0.15564 | 0.054931 | 0.082397 | -0.018311 | 0.022889 | 121.4767 | 0.027466 | 121.2708 | 121.3669 | 121.3348 | 121.4859 | 121.4081 | -121.4813 | -121.5271 | 121.5958 | 121.344 | 3.9917 | 2.3483
1111.3594 | 121.6919 | -0.32044 | 121.2845 | 0.024795 | 0 | 0.06539 | 0.063074 | 0.00049131 | -0.0039884 | -0.00044863 | 0.0062865 | 0.00033544 | -1.3963 | 0.068443 | -0.0037 | 0.0086987 | 0.0010467 | 3.6896 | 121.1517 | -0.17395 | 121.3577 | -0.082397 | -0.20142 | -0.2243 | 2.0645 | 121.0602 | -0.2655 | 121.0373 | -0.18768 | -0.21973 | -0.16022 | 0.14649 | -0.13275 | 0.073242 | 0.23804 | 0.096131 | 0.11902 | -0.050354 | -0.027466 | 0.054932 | -0.2243 | -0.24719 | 0.13275 | 0.16022 | 0.10071 | 0.10529 | 0.045776 | 0.091553 | 121.5317 | 0.07782 | 121.3028 | 121.3257 | 121.3257 | 121.4722 | 121.3806 | -121.4584 | -121.55 | 121.6782 | 121.3577 | 4.01 | 2.3849
1113.0781 | 121.7102 | -0.3067 | 121.2982 | 0.0019074 | 0 | 0.062827 | 0.064356 | -0.0014313 | -0.0014248 | 0.00019217 | -0.0028687 | 0.002258 | -1.3972 | 0.063102 | -0.0051954 | 0.0089123 | -0.0019439 | 3.7582 | 121.1105 | -0.17395 | 121.376 | -0.041199 | -0.13733 | -0.18768 | 2.1423 | 121.0419 | -0.22888 | 121.0602 | -0.14191 | -0.16479 | -0.11902 | 0.13275 | -0.18768 | 0.07782 | 0.2655 | 0.11902 | 0.16937 | -0.013733 | 0.036621 | 0.07782 | -0.25635 | -0.23804 | 0.16479 | 0.18768 | 0.14191 | 0.10986 | 0.064087 | 0.13275 | 121.55 | 0.086975 | 121.2891 | 121.2845 | 121.2708 | 121.4172 | 121.3486 | -121.4722 | -121.5271 | 121.6827 | 121.3669 | 4.0649 | 2.449
1114.8594 | 121.6461 | -0.31586 | 121.3165 | 0.024795 | 0 | 0.062613 | 0.066706 | -0.0031403 | 0.00049776 | 0.0027558 | 0.0093383 | 0.003967 | -1.3957 | 0.063957 | -0.006477 | 0.0074171 | 0.0021149 | 3.7857 | 121.1563 | -0.21973 | 121.3394 | -0.10986 | -0.21515 | -0.25635 | 2.1149 | 121.1197 | -0.27924 | 121.0327 | -0.19684 | -0.23804 | -0.16022 | 0.09613 | -0.16022 | 0.022889 | 0.20599 | 0.059509 | 0.10071 | -0.036621 | 0.004578 | 0.036621 | -0.19684 | -0.28381 | 0.11902 | 0.15564 | 0.07782 | 0.11902 | 0.041199 | 0.10986 | 121.5591 | 0.082398 | 121.312 | 121.376 | 121.3989 | 121.4722 | 121.4355 | -121.5363 | -121.5958 | 121.6553 | 121.3486 | 4.1016 | 2.4307
1116.5469 | 121.5866 | -0.34332 | 121.3531 | 0.0095369 | 0 | 0.062613 | 0.063929 | 6.4114e-05 | -0.001852 | 0.00083317 | -0.0059205 | 0.0028988 | -1.3955 | 0.062034 | -0.0032728 | 0.0080579 | -0.0027985 | 3.7308 | 121.1838 | -0.20142 | 121.2662 | -0.1831 | -0.29297 | -0.31586 | 1.9958 | 121.0831 | -0.25635 | 120.9915 | -0.27466 | -0.32044 | -0.21973 | 0.14191 | -0.16937 | -0.086975 | 0.16022 | 0.027466 | 0.050354 | -0.11444 | -0.091553 | 0.086975 | -0.27008 | -0.36163 | 0.068665 | 0.1236 | 0.022888 | 0.036621 | -0.064087 | 0.018311 | 121.4676 | -0.01831 | 121.2479 | 121.3852 | 121.3394 | 121.5271 | 121.4264 | -121.5546 | -121.6095 | 121.6095 | 121.3348 | 4.0741 | 2.3392
1118.3125 | 121.701 | -0.31586 | 121.312 | 0.017166 | 0 | 0.06539 | 0.062006 | -0.0012177 | -0.0016384 | -0.001303 | 0.0062865 | 0.0020444 | -1.394 | 0.061607 | -0.00092279 | 0.012117 | -0.0034393 | 3.7399 | 121.1746 | -0.19684 | 121.344 | -0.073242 | -0.18768 | -0.21515 | 2.0691 | 121.0556 | -0.25635 | 121.0419 | -0.17853 | -0.21973 | -0.14648 | 0.11902 | -0.13733 | 0.032043 | 0.24261 | 0.10071 | 0.12817 | -0.018311 | 0.009155 | 0.059509 | -0.25635 | -0.27008 | 0.13733 | 0.16937 | 0.09613 | 0.10986 | 0.036621 | 0.1236 | 121.5408 | 0.07782 | 121.2982 | 121.3715 | 121.312 | 121.4905 | 121.3715 | -121.5088 | -121.5683 | 121.6599 | 121.3577 | 4.0558 | 2.3849
1120.0938 | 121.7377 | -0.27466 | 121.3028 | -0.013352 | 0 | 0.061758 | 0.063715 | -0.0027131 | -0.0012112 | -0.00023503 | -0.0028687 | 0.0020444 | -1.3963 | 0.064384 | -6.8386e-05 | 0.010408 | -0.0038665 | 3.8086 | 121.138 | -0.16937 | 121.3806 | -0.050354 | -0.1831 | -0.21057 | 2.1423 | 121.0464 | -0.23346 | 121.1014 | -0.12817 | -0.16937 | -0.082397 | 0.10529 | -0.16479 | 0.07782 | 0.2243 | 0.064087 | 0.091553 | -0.041198 | -0.013732 | 0.041199 | -0.25635 | -0.20142 | 0.14648 | 0.19226 | 0.10529 | 0.15106 | 0.064086 | 0.11902 | 121.55 | 0.10528 | 121.3348 | 121.3074 | 121.2799 | 121.4127 | 121.3211 | -121.4722 | -121.5363 | 121.6553 | 121.376 | 4.0833 | 2.417
1121.7969 | 121.6095 | -0.3479 | 121.3165 | -0.0057221 | 0 | 0.063895 | 0.065211 | -0.0027131 | -0.004202 | -0.00023503 | 0.015442 | 0.0020444 | -1.3946 | 0.06652 | -0.0066906 | 0.0078443 | 0.0021149 | 3.7674 | 121.1838 | -0.20142 | 121.257 | -0.16937 | -0.24261 | -0.28381 | 2.0645 | 121.138 | -0.29755 | 120.9732 | -0.24261 | -0.28381 | -0.20599 | 0.14648 | -0.13275 | -0.059509 | 0.17853 | 0.064087 | 0.10528 | -0.082397 | -0.041199 | 0.050354 | -0.17853 | -0.34332 | 0.10528 | 0.14191 | 0.064087 | 0.091552 | 0.013733 | 0.032043 | 121.4584 | 0.054931 | 121.2708 | 121.3852 | 121.4355 | 121.5317 | 121.4859 | -121.5179 | -121.6141 | 121.6049 | 121.3211 | 4.1153 | 2.4124
1123.5625 | 121.6141 | -0.32044 | 121.3531 | -0.0057221 | 0 | 0.063467 | 0.067347 | -0.0016449 | -0.002493 | -0.0049346 | 0.00018312 | 0.003967 | -1.3933 | 0.059257 | -0.0015638 | 0.0078443 | 0.0025421 | 3.7765 | 121.1929 | -0.20599 | 121.2616 | -0.19226 | -0.29755 | -0.32044 | 2.005 | 121.1105 | -0.25177 | 120.9915 | -0.25635 | -0.29755 | -0.1831 | 0.11444 | -0.16022 | -0.091552 | 0.12817 | 0 | 0.022889 | -0.11444 | -0.091552 | 0.068665 | -0.24261 | -0.36163 | 0.064087 | 0.13733 | 0.022889 | 0.068665 | -0.045776 | 0.013733 | 121.4676 | -0.004578 | 121.2433 | 121.3989 | 121.3623 | 121.5134 | 121.431 | -121.5591 | -121.6049 | 121.582 | 121.312 | 4.097 | 2.3254
1125.3438 | 121.7056 | -0.29297 | 121.3028 | 0.055313 | 0 | 0.066245 | 0.062433 | 0.0041229 | 0.00092496 | -0.0010894 | 0.015442 | 0.0028988 | -1.3933 | 0.063957 | -0.0032728 | 0.0091261 | 0.0016877 | 3.8452 | 121.17 | -0.1831 | 121.4081 | -0.013733 | -0.15564 | -0.1831 | 2.1561 | 121.0831 | -0.24719 | 121.0831 | -0.14648 | -0.17853 | -0.11902 | 0.10986 | -0.13275 | 0.10529 | 0.27924 | 0.10986 | 0.13733 | 0 | 0.027465 | 0.045777 | -0.21973 | -0.21973 | 0.14648 | 0.17395 | 0.11444 | 0.12817 | 0.068664 | 0.16937 | 121.5912 | 0.10071 | 121.3303 | 121.3531 | 121.3303 | 121.463 | 121.376 | -121.4859 | -121.55 | 121.701 | 121.376 | 4.1382 | 2.449
1127.0469 | 121.6873 | -0.29297 | 121.3028 | 0.017166 | 0 | 0.063895 | 0.064783 | 0.00049131 | -0.00099764 | -0.00044863 | 0.0032349 | 0.0018306 | -1.395 | 0.059898 | -0.0043408 | 0.010621 | 0.0025421 | 3.8132 | 121.1838 | -0.18768 | 121.3531 | -0.09613 | -0.19684 | -0.2243 | 2.0782 | 121.0739 | -0.23346 | 121.0739 | -0.16022 | -0.1831 | -0.13275 | 0.10529 | -0.11902 | 0.050354 | 0.19684 | 0.068665 | 0.096131 | -0.036621 | -0.009155 | 0.05951 | -0.22888 | -0.22888 | 0.13275 | 0.16022 | 0.10986 | 0.10071 | 0.050354 | 0.091553 | 121.5408 | 0.073242 | 121.3074 | 121.3715 | 121.3074 | 121.4767 | 121.3669 | -121.4905 | -121.5363 | 121.6461 | 121.3669 | 4.1061 | 2.3712
1128.8281 | 121.7239 | -0.28381 | 121.3165 | 0.0095369 | 0 | 0.062827 | 0.064356 | -0.0018585 | -0.0037746 | -0.0021576 | -0.0028687 | 0.0020444 | -1.3937 | 0.068015 | -0.0043408 | 0.011049 | 0.0012603 | 3.8177 | 121.1472 | -0.17395 | 121.344 | -0.07782 | -0.16937 | -0.21973 | 2.0966 | 121.0785 | -0.2243 | 121.0785 | -0.13733 | -0.16937 | -0.11444 | 0.10986 | -0.16937 | 0.027466 | 0.20599 | 0.064086 | 0.11444 | -0.045777 | 0.004577 | 0.059509 | -0.23804 | -0.23804 | 0.14648 | 0.16937 | 0.11444 | 0.10986 | 0.054931 | 0.09613 | 121.5179 | 0.086975 | 121.3028 | 121.3211 | 121.3028 | 121.431 | 121.3623 | -121.4905 | -121.5408 | 121.6278 | 121.3623 | 4.1016 | 2.3804
1130.5938 | 121.6324 | -0.31586 | 121.3394 | -0.0057221 | 0 | 0.062399 | 0.06692 | 0.0039093 | -0.0012112 | 0.002115 | -0.0028687 | 0.0037532 | -1.3933 | 0.063102 | -0.0017774 | 0.0095533 | -0.0015167 | 3.8177 | 121.1929 | -0.21515 | 121.2753 | -0.17853 | -0.27924 | -0.31128 | 2.0233 | 121.1151 | -0.23804 | 121.0281 | -0.22888 | -0.27924 | -0.17395 | 0.10071 | -0.14648 | -0.064087 | 0.13733 | 0.004578 | 0.036621 | -0.09613 | -0.064087 | 0.07782 | -0.22431 | -0.31128 | 0.086975 | 0.14191 | 0.036621 | 0.064087 | -0.041199 | 0.036621 | 121.4905 | 0.009155 | 121.2662 | 121.4081 | 121.3531 | 121.5088 | 121.431 | -121.5546 | -121.5775 | 121.5912 | 121.344 | 4.1336 | 2.3392
1132.375 | 121.6324 | -0.34332 | 121.3303 | -0.0057221 | 0 | 0.063895 | 0.065638 | 0.00049131 | 7.0564e-05 | 0.00061957 | -0.0028687 | 0.005035 | -1.394 | 0.060325 | -0.0032728 | 0.0082715 | -0.00066231 | 3.8269 | 121.2158 | -0.1831 | 121.2753 | -0.17853 | -0.28381 | -0.3067 | 2.0004 | 121.106 | -0.26093 | 121.0144 | -0.23804 | -0.28381 | -0.16937 | 0.16022 | -0.11444 | -0.054931 | 0.16479 | 0.036621 | 0.05951 | -0.1236 | -0.10071 | 0.082398 | -0.2243 | -0.31586 | 0.10529 | 0.17395 | 0.05951 | 0.091552 | -0.022888 | 0.004577 | 121.4584 | 0.022888 | 121.2753 | 121.3989 | 121.3669 | 121.5591 | 121.4493 | -121.5134 | -121.5912 | 121.6187 | 121.3577 | 4.1702 | 2.3438
1134.0781 | 121.7102 | -0.27924 | 121.2936 | 0.0019074 | 0 | 0.064108 | 0.066065 | 6.4114e-05 | -0.0014248 | -0.0021576 | -0.0059205 | 0.002258 | -1.3959 | 0.062461 | -0.00092279 | 0.011049 | -0.0010895 | 3.8498 | 121.1975 | -0.17853 | 121.3303 | -0.10071 | -0.21973 | -0.24719 | 2.0966 | 121.0693 | -0.23346 | 121.106 | -0.14648 | -0.16937 | -0.09613 | 0.10071 | -0.09613 | 0.036621 | 0.17853 | 0.032044 | 0.059509 | -0.068664 | -0.041199 | 0.045777 | -0.2243 | -0.18768 | 0.13275 | 0.18311 | 0.10986 | 0.13733 | 0.064086 | 0.07782 | 121.5088 | 0.086975 | 121.3394 | 121.376 | 121.3028 | 121.4767 | 121.3486 | -121.4722 | -121.5271 | 121.6095 | 121.3852 | 4.129 | 2.3758
1135.8438 | 121.6187 | -0.33417 | 121.3348 | -0.013352 | 0 | 0.063467 | 0.064997 | 6.4114e-05 | -0.00035684 | -0.00066223 | -0.0028687 | 0.002258 | -1.3935 | 0.053062 | -0.0028454 | 0.0091261 | 0.0012603 | 3.8589 | 121.2387 | -0.19684 | 121.2753 | -0.18768 | -0.29755 | -0.3067 | 2.0325 | 121.1197 | -0.24719 | 121.0007 | -0.26093 | -0.28381 | -0.18768 | 0.13733 | -0.096131 | -0.059509 | 0.14648 | 0.027465 | 0.036621 | -0.10986 | -0.10071 | 0.086975 | -0.21515 | -0.33417 | 0.073242 | 0.14648 | 0.050354 | 0.059509 | -0.036621 | 0.009155 | 121.4722 | -0.013733 | 121.2479 | 121.4355 | 121.3669 | 121.5729 | 121.4539 | -121.5317 | -121.582 | 121.6095 | 121.3348 | 4.1931 | 2.3666
1137.6094 | 121.7422 | -0.27924 | 121.3165 | 0.0019074 | 0 | 0.064108 | 0.06222 | 0.0032685 | -0.002493 | 0.001474 | -0.0059205 | 0.0014034 | -1.3963 | 0.066093 | -0.006477 | 0.0093397 | 0.0025421 | 3.8956 | 121.1609 | -0.15564 | 121.3531 | -0.064087 | -0.16022 | -0.19684 | 2.1103 | 121.0831 | -0.21515 | 121.1105 | -0.09613 | -0.14191 | -0.091553 | 0.1236 | -0.15564 | 0.036621 | 0.21515 | 0.082398 | 0.11902 | -0.041198 | -0.004577 | 0.064087 | -0.23346 | -0.20599 | 0.18311 | 0.18768 | 0.13733 | 0.1236 | 0.073242 | 0.091553 | 121.5088 | 0.11902 | 121.3257 | 121.3165 | 121.2982 | 121.4401 | 121.3623 | -121.4722 | -121.5317 | 121.6324 | 121.3898 | 4.1748 | 2.3895
1139.3906 | 121.6873 | -0.29297 | 121.3348 | 0.017166 | 0 | 0.063681 | 0.062647 | 0.0011321 | 7.0564e-05 | 0.0010468 | 0.00018312 | 0.00076264 | -1.3952 | 0.064384 | -0.0056226 | 0.0093397 | -0.0015167 | 3.8956 | 121.1884 | -0.17395 | 121.3577 | -0.073242 | -0.18768 | -0.20599 | 2.092 | 121.0785 | -0.23346 | 121.051 | -0.15106 | -0.19684 | -0.13733 | 0.11902 | -0.14648 | 0.022888 | 0.21973 | 0.086975 | 0.10529 | -0.032044 | -0.013733 | 0.05951 | -0.25635 | -0.28381 | 0.14191 | 0.15564 | 0.096131 | 0.09613 | 0.036621 | 0.10071 | 121.5317 | 0.082397 | 121.2845 | 121.3623 | 121.3119 | 121.4813 | 121.3715 | -121.5088 | -121.5683 | 121.6507 | 121.344 | 4.1885 | 2.3849
1141.1719 | 121.7377 | -0.2655 | 121.3165 | 0.047683 | 0 | 0.065176 | 0.066492 | -0.00014949 | 0.00049776 | 0.001474 | 0.018494 | 0.0041806 | -1.3946 | 0.064384 | -0.001991 | 0.011903 | -0.0010895 | 3.9917 | 121.1884 | -0.19226 | 121.4401 | 0.027466 | -0.11444 | -0.15564 | 2.2156 | 121.1014 | -0.23346 | 121.1288 | -0.11444 | -0.14648 | -0.086975 | 0.073242 | -0.12817 | 0.1236 | 0.29297 | 0.10986 | 0.15106 | 0.036621 | 0.07782 | 0.032044 | -0.21515 | -0.18768 | 0.15106 | 0.17853 | 0.11902 | 0.14648 | 0.086975 | 0.21973 | 121.6324 | 0.11902 | 121.3623 | 121.3806 | 121.3348 | 121.4539 | 121.3669 | -121.5088 | -121.55 | 121.7056 | 121.3943 | 4.2572 | 2.4811
1142.9531 | 121.6507 | -0.31128 | 121.3577 | 0.024795 | 0 | 0.064963 | 0.065638 | -0.0027131 | -0.00014304 | 0.001474 | 0.0062865 | 0.0031124 | -1.3944 | 0.059257 | -0.004768 | 0.0086987 | -0.0036529 | 3.978 | 121.2067 | -0.17853 | 121.3623 | -0.082397 | -0.1831 | -0.21973 | 2.1469 | 121.1243 | -0.25177 | 121.0693 | -0.15106 | -0.2243 | -0.13733 | 0.13275 | -0.15106 | 0.004578 | 0.22888 | 0.091552 | 0.12817 | -0.041199 | -0.004577 | 0.059509 | -0.23346 | -0.28839 | 0.16022 | 0.17395 | 0.086975 | 0.11444 | 0.027466 | 0.096131 | 121.5408 | 0.10071 | 121.3211 | 121.3852 | 121.376 | 121.5179 | 121.4355 | -121.5363 | -121.6095 | 121.6736 | 121.3806 | 4.2892 | 2.4582
1144.6562 | 121.6644 | -0.30212 | 121.3394 | 0.032425 | 0 | 0.066245 | 0.065851 | 0.0026275 | -0.0031338 | 0.002115 | 0.0062865 | 0.0052486 | -1.3931 | 0.055625 | -0.0051954 | 0.0082715 | 0.0010467 | 4.01 | 121.2341 | -0.21057 | 121.3531 | -0.091553 | -0.18768 | -0.2243 | 2.179 | 121.1334 | -0.23346 | 121.0602 | -0.17853 | -0.23804 | -0.14648 | 0.091553 | -0.10529 | 0.013732 | 0.21057 | 0.07782 | 0.11444 | -0.013733 | 0.022888 | 0.068665 | -0.20599 | -0.27924 | 0.1236 | 0.15564 | 0.064087 | 0.086975 | -0.004578 | 0.11902 | 121.5637 | 0.054931 | 121.2936 | 121.4447 | 121.3669 | 121.5363 | 121.4355 | -121.55 | -121.5729 | 121.6553 | 121.3623 | 4.3121 | 2.4811
1146.4219 | 121.7148 | -0.29755 | 121.3165 | 0.017166 | 0 | 0.063895 | 0.060511 | 0.0028411 | -0.00099764 | -0.001303 | 0.0032349 | -0.00051916 | -1.3942 | 0.062248 | -0.0022046 | 0.0097669 | -0.0010895 | 3.9322 | 121.1746 | -0.16479 | 121.344 | -0.073242 | -0.1831 | -0.21057 | 2.1286 | 121.0831 | -0.21515 | 121.0876 | -0.13733 | -0.16479 | -0.10529 | 0.13275 | -0.14191 | 0.027466 | 0.2243 | 0.086975 | 0.11444 | -0.045776 | -0.01831 | 0.082397 | -0.23346 | -0.22888 | 0.16022 | 0.19226 | 0.13275 | 0.10986 | 0.050354 | 0.091553 | 121.5088 | 0.07782 | 121.3028 | 121.3394 | 121.2982 | 121.4722 | 121.3806 | -121.4813 | -121.5317 | 121.6415 | 121.3852 | 4.2297 | 2.4261
1148.2031 | 121.6049 | -0.31128 | 121.3303 | -0.0057221 | 0 | 0.062827 | 0.063929 | -0.0027131 | -0.0014248 | -0.0010894 | -0.0059205 | 0.0031124 | -1.3946 | 0.062034 | -0.006477 | 0.0076307 | 0.00040589 | 3.9734 | 121.1929 | -0.17853 | 121.2891 | -0.13733 | -0.23804 | -0.26093 | 2.0782 | 121.1288 | -0.22888 | 121.0007 | -0.2243 | -0.2655 | -0.20599 | 0.13275 | -0.13733 | -0.041199 | 0.17395 | 0.050354 | 0.073242 | -0.082397 | -0.059509 | 0.082397 | -0.20142 | -0.32959 | 0.086975 | 0.10528 | 0.045776 | 0.022888 | -0.036621 | 0.041199 | 121.4676 | 0.004578 | 121.2296 | 121.3715 | 121.3577 | 121.5042 | 121.4401 | -121.5088 | -121.5591 | 121.6003 | 121.3119 | 4.2847 | 2.3895
1149.9688 | 121.7422 | -0.27008 | 121.344 | -0.0057221 | 0 | 0.062613 | 0.063502 | -0.0020721 | -0.0046292 | -0.00023503 | -0.0028687 | 0.00097624 | -1.3929 | 0.069084 | -0.0028454 | 0.0099805 | -0.00023491 | 3.9963 | 121.1655 | -0.15564 | 121.3943 | -0.032043 | -0.11444 | -0.17395 | 2.1606 | 121.0968 | -0.21973 | 121.1243 | -0.073242 | -0.11444 | -0.07782 | 0.11444 | -0.17853 | 0.050354 | 0.23804 | 0.096131 | 0.15564 | -0.01831 | 0.041199 | 0.050354 | -0.24719 | -0.21973 | 0.19684 | 0.19226 | 0.15564 | 0.14191 | 0.10529 | 0.1236 | 121.55 | 0.14649 | 121.344 | 121.3211 | 121.3165 | 121.4355 | 121.3669 | -121.4996 | -121.5637 | 121.6644 | 121.3943 | 4.2664 | 2.4307
1151.6719 | 121.6919 | -0.27466 | 121.3348 | -0.013352 | 0 | 0.06304 | 0.065851 | -0.00079049 | -0.0016384 | -0.00066223 | 0.00018312 | 0.0026852 | -1.3967 | 0.057975 | -6.8386e-05 | 0.0080579 | -0.0010895 | 3.9917 | 121.2479 | -0.17853 | 121.3211 | -0.1236 | -0.23804 | -0.26093 | 2.1194 | 121.106 | -0.21973 | 121.0876 | -0.15106 | -0.18768 | -0.09613 | 0.09613 | -0.086975 | -0.013733 | 0.15106 | 0.013733 | 0.036621 | -0.082397 | -0.059509 | 0.054931 | -0.22888 | -0.24719 | 0.1236 | 0.17853 | 0.086975 | 0.1236 | 0.032044 | 0.054932 | 121.4996 | 0.068665 | 121.3074 | 121.4264 | 121.3257 | 121.5225 | 121.3806 | -121.5134 | -121.5546 | 121.5958 | 121.3623 | 4.2664 | 2.3941
1153.4375 | 121.6919 | -0.25177 | 121.3028 | 0.040054 | 0 | 0.064322 | 0.06457 | -0.0012177 | -0.00099764 | 0.0029694 | 0.01239 | 0.002258 | -1.3942 | 0.064384 | -0.0045544 | 0.0099805 | 0.0019013 | 4.0512 | 121.1975 | -0.16479 | 121.4035 | 0.009155 | -0.12817 | -0.15564 | 2.1698 | 121.1151 | -0.24261 | 121.0968 | -0.13733 | -0.15564 | -0.11902 | 0.086975 | -0.10529 | 0.10071 | 0.26093 | 0.09613 | 0.1236 | 0.009155 | 0.036621 | 0.009155 | -0.18768 | -0.20599 | 0.11444 | 0.13275 | 0.09613 | 0.1236 | 0.086975 | 0.17395 | 121.5683 | 0.10529 | 121.3394 | 121.3623 | 121.3577 | 121.4493 | 121.3669 | -121.4676 | -121.5454 | 121.6553 | 121.3486 | 4.303 | 2.4216
1155.1719 | 121.756 | -0.27008 | 121.3211 | -0.013352 | 0 | 0.062613 | 0.065638 | -0.00079049 | -0.0020658 | -0.0017304 | 0.00018312 | 0.001617 | -1.3948 | 0.066947 | -0.0034864 | 0.0095533 | 0.0012603 | 4.0741 | 121.1426 | -0.14648 | 121.4127 | 0.013733 | -0.10986 | -0.14191 | 2.2247 | 121.0968 | -0.1831 | 121.1426 | -0.059509 | -0.09613 | -0.059509 | 0.1236 | -0.17853 | 0.091553 | 0.28381 | 0.12817 | 0.16022 | 0.004577 | 0.036621 | 0.086976 | -0.2243 | -0.17853 | 0.21057 | 0.21057 | 0.17395 | 0.1236 | 0.086975 | 0.16022 | 121.5591 | 0.1236 | 121.3257 | 121.2891 | 121.2799 | 121.4127 | 121.3669 | -121.4676 | -121.5042 | 121.6827 | 121.4127 | 4.3442 | 2.4948
1156.9531 | 121.6919 | -0.27008 | 121.3348 | 0.0095369 | 0 | 0.064749 | 0.06222 | 0.0030547 | -0.0029202 | -0.00023503 | 0.0032349 | -0.00030556 | -1.3937 | 0.066947 | -0.0026318 | 0.012758 | 0.0016877 | 4.0466 | 121.1655 | -0.17853 | 121.3623 | -0.068665 | -0.17395 | -0.20142 | 2.124 | 121.1105 | -0.23346 | 121.0739 | -0.13733 | -0.1831 | -0.1236 | 0.091553 | -0.16937 | 0.027466 | 0.20142 | 0.068665 | 0.096131 | -0.022888 | 0.004578 | 0.036622 | -0.2243 | -0.26093 | 0.13275 | 0.14649 | 0.086976 | 0.10986 | 0.050354 | 0.10986 | 121.5408 | 0.09613 | 121.3074 | 121.344 | 121.344 | 121.4355 | 121.3806 | -121.5134 | -121.5683 | 121.6324 | 121.344 | 4.3167 | 2.3941
1158.7188 | 121.7331 | -0.23346 | 121.312 | -0.0057221 | 0 | 0.064749 | 0.064783 | 6.4114e-05 | -0.001852 | -2.1434e-05 | -0.0028687 | 0.001617 | -1.3957 | 0.064597 | -0.00092279 | 0.011049 | 0.0021149 | 4.1153 | 121.17 | -0.13733 | 121.4127 | -0.013733 | -0.13733 | -0.17395 | 2.2202 | 121.0785 | -0.18768 | 121.138 | -0.086975 | -0.14648 | -0.050354 | 0.09613 | -0.14191 | 0.10071 | 0.21973 | 0.059509 | 0.09613 | -0.036621 | 0 | 0.045776 | -0.23346 | -0.17395 | 0.14648 | 0.1831 | 0.086975 | 0.13733 | 0.041199 | 0.1236 | 121.55 | 0.10071 | 121.3257 | 121.3074 | 121.2662 | 121.4035 | 121.3119 | -121.4493 | -121.4996 | 121.6461 | 121.3715 | 4.3488 | 2.4536
1160.4219 | 121.7239 | -0.25177 | 121.3165 | -0.013352 | 0 | 0.06304 | 0.063502 | -0.0012177 | -0.0033474 | -0.0015166 | -0.0028687 | -9.1956e-05 | -1.3937 | 0.059898 | -0.0075452 | 0.0097669 | 0.0012603 | 4.1428 | 121.1884 | -0.11902 | 121.4264 | 0.009155 | -0.09613 | -0.16022 | 2.211 | 121.1105 | -0.18768 | 121.1197 | -0.086975 | -0.13733 | -0.082397 | 0.13275 | -0.12817 | 0.10986 | 0.26093 | 0.091553 | 0.15564 | -0.041198 | 0.022889 | 0.064087 | -0.20599 | -0.19684 | 0.16479 | 0.16937 | 0.11444 | 0.10529 | 0.050354 | 0.12817 | 121.5454 | 0.10071 | 121.3074 | 121.3074 | 121.2982 | 121.4401 | 121.3623 | -121.4355 | -121.5042 | 121.6782 | 121.3715 | 4.3945 | 2.4628
1162.2031 | 121.7422 | -0.26093 | 121.344 | -0.0057221 | 0 | 0.060904 | 0.062006 | 0.00027771 | -0.0029202 | -0.00087583 | -0.0028687 | 0.00097624 | -1.3952 | 0.065452 | -0.0037 | 0.0084851 | 0.0016877 | 4.129 | 121.1517 | -0.14648 | 121.4401 | 0.018311 | -0.10071 | -0.15106 | 2.2339 | 121.1014 | -0.19226 | 121.1288 | -0.059509 | -0.086975 | -0.068665 | 0.11444 | -0.19226 | 0.096131 | 0.27924 | 0.10986 | 0.16022 | -0.004578 | 0.045776 | 0.068664 | -0.24262 | -0.21515 | 0.20142 | 0.19226 | 0.17395 | 0.1236 | 0.10529 | 0.16479 | 121.5866 | 0.13275 | 121.3211 | 121.2982 | 121.2936 | 121.4127 | 121.3623 | -121.4905 | -121.5363 | 121.701 | 121.3898 | 4.39 | 2.4948
1163.9688 | 121.6049 | -0.30212 | 121.3806 | 0.0019074 | 0 | 0.063254 | 0.065638 | 6.4114e-05 | -0.0048428 | -0.003653 | -0.0028687 | 0.0024716 | -1.395 | 0.058616 | -0.0051954 | 0.0084851 | 0.0021149 | 4.1016 | 121.225 | -0.16022 | 121.2982 | -0.13733 | -0.2243 | -0.2655 | 2.1011 | 121.1609 | -0.21515 | 121.0007 | -0.21057 | -0.26093 | -0.1831 | 0.14191 | -0.15564 | -0.082397 | 0.16479 | 0.036621 | 0.07782 | -0.10529 | -0.064087 | 0.086975 | -0.21973 | -0.37994 | 0.091553 | 0.11902 | 0.041199 | 0.032044 | -0.045776 | 0.022888 | 121.4584 | 0.004578 | 121.2158 | 121.3852 | 121.376 | 121.5271 | 121.463 | -121.5408 | -121.5958 | 121.6003 | 121.3028 | 4.4037 | 2.4033
1165.7344 | 121.7239 | -0.25635 | 121.3211 | 0.055313 | 0 | 0.065817 | 0.065424 | 0.0022003 | -0.00035684 | 0.0010468 | 0.018494 | -0.00030556 | -1.3946 | 0.063102 | 0.0018542 | 0.010835 | -0.0019439 | 4.1931 | 121.2296 | -0.16937 | 121.4584 | 0.032043 | -0.10529 | -0.14191 | 2.2659 | 121.1151 | -0.21057 | 121.1426 | -0.09613 | -0.15106 | -0.068665 | 0.086975 | -0.091553 | 0.13733 | 0.28839 | 0.11444 | 0.15106 | 0.027466 | 0.064087 | 0.045777 | -0.20599 | -0.17853 | 0.16022 | 0.18768 | 0.10529 | 0.14191 | 0.059509 | 0.20142 | 121.6278 | 0.11444 | 121.3531 | 121.3989 | 121.3257 | 121.4859 | 121.3715 | -121.4905 | -121.5317 | 121.7148 | 121.3989 | 4.4495 | 2.5223
1167.4844 | 121.637 | -0.28381 | 121.3715 | -0.0057221 | 0 | 0.06539 | 0.064783 | 0.0017731 | -0.0044156 | -0.0017304 | -0.0059205 | 0.00097624 | -1.3942 | 0.059257 | -0.0045544 | 0.0084851 | 0.00061949 | 4.097 | 121.2296 | -0.16937 | 121.2982 | -0.14648 | -0.25177 | -0.28381 | 2.1149 | 121.1472 | -0.22888 | 121.0419 | -0.2243 | -0.27008 | -0.15564 | 0.11444 | -0.14191 | -0.073242 | 0.13733 | 0 | 0.032043 | -0.11444 | -0.082397 | 0.054931 | -0.2243 | -0.32959 | 0.059509 | 0.12817 | 0.013732 | 0.073242 | -0.041199 | 0.022889 | 121.4676 | 0.004578 | 121.2708 | 121.3989 | 121.376 | 121.5134 | 121.431 | -121.5408 | -121.6003 | 121.582 | 121.3257 | 4.3808 | 2.3987
1169.1875 | 121.6232 | -0.30212 | 121.3669 | 0.0019074 | 0 | 0.063254 | 0.065638 | 0.0017731 | -0.00078404 | -0.0023712 | -0.0028687 | 0.0026852 | -1.394 | 0.062461 | -0.0022046 | 0.0097669 | 0.0031829 | 4.1153 | 121.2524 | -0.17395 | 121.2845 | -0.16479 | -0.2655 | -0.28839 | 2.092 | 121.1426 | -0.21973 | 121.0327 | -0.24261 | -0.27466 | -0.16937 | 0.12817 | -0.11444 | -0.082397 | 0.13733 | 0.013733 | 0.036621 | -0.11444 | -0.091553 | 0.082397 | -0.2243 | -0.33417 | 0.059509 | 0.13275 | 0.027466 | 0.050354 | -0.054931 | 0.009155 | 121.4584 | -0.022888 | 121.2524 | 121.4264 | 121.3623 | 121.5546 | 121.4447 | -121.5408 | -121.5866 | 121.5866 | 121.3348 | 4.4174 | 2.3941
1170.9531 | 121.701 | -0.2655 | 121.3577 | 0.0019074 | 0 | 0.063681 | 0.063502 | 0.00049131 | -0.0029202 | -2.1434e-05 | -0.0059205 | 0.0011898 | -1.3937 | 0.068656 | -0.0058362 | 0.0086987 | -0.0017303 | 4.2068 | 121.1517 | -0.11444 | 121.4218 | 0 | -0.10529 | -0.15106 | 2.2385 | 121.1105 | -0.20142 | 121.0922 | -0.10529 | -0.14191 | -0.10071 | 0.15106 | -0.20599 | 0.064087 | 0.2655 | 0.11444 | 0.16022 | -0.036621 | 0.009155 | 0.064087 | -0.24719 | -0.2655 | 0.16022 | 0.16479 | 0.1236 | 0.10071 | 0.059509 | 0.11444 | 121.5363 | 0.09613 | 121.2936 | 121.2662 | 121.312 | 121.4172 | 121.376 | -121.4722 | -121.5591 | 121.6873 | 121.3577 | 4.4724 | 2.504
1172.7188 | 121.7285 | -0.25177 | 121.3257 | -0.0057221 | 0 | 0.064108 | 0.064783 | 0.0034821 | -0.0046292 | 0.0016876 | -0.0059205 | -0.0022282 | -1.3942 | 0.057975 | 0.00014521 | 0.0078443 | -0.0042939 | 4.216 | 121.1929 | -0.11902 | 121.4218 | -0.004578 | -0.13733 | -0.17853 | 2.2568 | 121.1426 | -0.21973 | 121.1746 | -0.086975 | -0.11902 | -0.064087 | 0.13275 | -0.13275 | 0.09613 | 0.24719 | 0.073242 | 0.11444 | -0.059509 | -0.01831 | 0.032043 | -0.18311 | -0.15106 | 0.16479 | 0.18768 | 0.13275 | 0.15564 | 0.10071 | 0.11444 | 121.5408 | 0.13275 | 121.3943 | 121.312 | 121.3623 | 121.4447 | 121.3943 | -121.4447 | -121.5454 | 121.6736 | 121.4264 | 4.4678 | 2.5085
1174.4688 | 121.756 | -0.25635 | 121.3394 | -0.0057221 | 0 | 0.06304 | 0.060938 | 0.00091851 | -0.001852 | -0.0017304 | 0.00018312 | 0.00012184 | -1.3942 | 0.060752 | -0.0051954 | 0.0093397 | -2.1314e-05 | 4.2206 | 121.1655 | -0.12817 | 121.4584 | 0.054932 | -0.082397 | -0.11902 | 2.3117 | 121.1014 | -0.16937 | 121.1563 | -0.059509 | -0.10071 | -0.068665 | 0.12817 | -0.17395 | 0.11902 | 0.31128 | 0.13733 | 0.17395 | 0.009155 | 0.045777 | 0.086975 | -0.23804 | -0.18311 | 0.19684 | 0.18768 | 0.15564 | 0.10071 | 0.068665 | 0.18311 | 121.5866 | 0.10986 | 121.3257 | 121.2936 | 121.2708 | 121.4218 | 121.3577 | -121.4676 | -121.5088 | 121.7148 | 121.4127 | 4.4769 | 2.5681
1176.1719 | 121.6415 | -0.29755 | 121.3623 | -0.0057221 | 0 | 0.06069 | 0.063715 | 0.0015595 | -0.0037746 | -0.001944 | 0.00018312 | 0.0014034 | -1.3959 | 0.062248 | -0.0058362 | 0.0091261 | 0.00083309 | 4.2343 | 121.1563 | -0.14191 | 121.376 | -0.041199 | -0.15106 | -0.18768 | 2.179 | 121.1243 | -0.21057 | 121.0648 | -0.16479 | -0.19684 | -0.16022 | 0.15564 | -0.20599 | 0.013733 | 0.25635 | 0.10986 | 0.14648 | -0.045776 | -0.009155 | 0.086975 | -0.23804 | -0.29755 | 0.13275 | 0.13733 | 0.10071 | 0.050354 | 0.013733 | 0.10071 | 121.5179 | 0.045776 | 121.2753 | 121.2982 | 121.3348 | 121.4539 | 121.4218 | -121.5042 | -121.5729 | 121.6736 | 121.3623 | 4.5319 | 2.4765
1177.9375 | 121.6461 | -0.28839 | 121.3531 | 0.024795 | 0 | 0.063254 | 0.065638 | 6.4114e-05 | -0.002493 | -0.0010894 | 0.00018312 | 0.0020444 | -1.3931 | 0.056907 | -0.0043408 | 0.010835 | -2.1314e-05 | 4.2618 | 121.2296 | -0.16479 | 121.3852 | -0.064087 | -0.17853 | -0.20599 | 2.2293 | 121.1288 | -0.20142 | 121.0648 | -0.15564 | -0.21973 | -0.12817 | 0.1236 | -0.1236 | 0.032044 | 0.2243 | 0.082397 | 0.10986 | -0.041199 | -0.013733 | 0.086975 | -0.2243 | -0.28839 | 0.13275 | 0.16022 | 0.068664 | 0.073242 | -0.018311 | 0.10071 | 121.55 | 0.045776 | 121.2662 | 121.3943 | 121.3303 | 121.5179 | 121.4172 | -121.5179 | -121.5546 | 121.6736 | 121.3531 | 4.5502 | 2.5177
1179.7188 | 121.6461 | -0.28839 | 121.3577 | -0.013352 | 0 | 0.063895 | 0.063288 | -0.00057689 | -0.0029202 | -2.1434e-05 | -0.0059205 | 0.00054904 | -1.3944 | 0.062461 | -0.0034864 | 0.0099805 | 0.00040589 | 4.2755 | 121.1975 | -0.11902 | 121.4081 | -0.027466 | -0.12817 | -0.1831 | 2.2247 | 121.1243 | -0.19684 | 121.0464 | -0.16022 | -0.19226 | -0.13275 | 0.16937 | -0.16022 | 0.050354 | 0.26093 | 0.10529 | 0.16022 | -0.064086 | -0.009155 | 0.091553 | -0.23346 | -0.31128 | 0.12817 | 0.15564 | 0.09613 | 0.064087 | 0.004577 | 0.091553 | 121.5271 | 0.036621 | 121.2433 | 121.3165 | 121.3211 | 121.4859 | 121.4127 | -121.4767 | -121.5546 | 121.6965 | 121.3348 | 4.5639 | 2.5131
1181.4062 | 121.6782 | -0.29755 | 121.3486 | 0.024795 | 0 | 0.063681 | 0.066706 | 0.0032685 | -0.0039884 | -0.00023503 | 0.0062865 | 0.0035396 | -1.3922 | 0.060539 | -0.0041272 | 0.0082715 | -0.0019439 | 4.2801 | 121.2433 | -0.17395 | 121.3623 | -0.059509 | -0.16937 | -0.20142 | 2.211 | 121.1334 | -0.22888 | 121.0785 | -0.13733 | -0.18768 | -0.11444 | 0.1236 | -0.10529 | 0.013733 | 0.23804 | 0.09613 | 0.12817 | -0.027466 | 0.004577 | 0.068664 | -0.21515 | -0.27008 | 0.16022 | 0.1831 | 0.10986 | 0.11444 | 0.041199 | 0.11444 | 121.5363 | 0.091553 | 121.3074 | 121.4172 | 121.3623 | 121.5408 | 121.431 | -121.5225 | -121.5775 | 121.6599 | 121.376 | 4.5776 | 2.5085
1183.1875 | 121.6507 | -0.27466 | 121.3989 | -0.013352 | 0 | 0.06304 | 0.06222 | -0.00014949 | -0.0056972 | 0.0012604 | 0.00018312 | 0.0026852 | -1.3961 | 0.058189 | -0.0051954 | 0.0086987 | -0.00044851 | 4.2801 | 121.1792 | -0.12817 | 121.3989 | -0.032043 | -0.1236 | -0.17853 | 2.1973 | 121.1197 | -0.20599 | 121.0602 | -0.16479 | -0.19226 | -0.13733 | 0.14648 | -0.21973 | 0 | 0.24262 | 0.09613 | 0.15106 | -0.050354 | 0.004578 | 0.068664 | -0.27924 | -0.33875 | 0.10986 | 0.13733 | 0.082397 | 0.068665 | 0.013733 | 0.096131 | 121.5271 | 0.041199 | 121.2662 | 121.3074 | 121.3257 | 121.4539 | 121.3943 | -121.5271 | -121.6049 | 121.6736 | 121.3348 | 4.5547 | 2.4719
1184.9531 | 121.5912 | -0.28381 | 121.4035 | 0.0019074 | 0 | 0.064108 | 0.065638 | -0.00014949 | -0.0020658 | -0.00087583 | 0.00018312 | 0.0031124 | -1.394 | 0.057334 | -0.0043408 | 0.010835 | -0.0013031 | 4.2206 | 121.2341 | -0.15564 | 121.2982 | -0.15106 | -0.27008 | -0.30212 | 2.0966 | 121.1746 | -0.21057 | 121.019 | -0.26093 | -0.2655 | -0.16937 | 0.12817 | -0.16937 | -0.10528 | 0.13275 | -0.018311 | 0.013732 | -0.14648 | -0.11444 | 0.073242 | -0.22888 | -0.38452 | 0.022888 | 0.11444 | 0.01831 | 0.041198 | -0.054932 | 0.004578 | 121.4539 | -0.050354 | 121.2296 | 121.3898 | 121.3852 | 121.5179 | 121.4584 | -121.5591 | -121.6141 | 121.582 | 121.3028 | 4.5044 | 2.3804
1186.6562 | 121.7377 | -0.2655 | 121.344 | -0.0057221 | 0 | 0.062399 | 0.06222 | -0.00079049 | -0.0031338 | -0.00087583 | -0.0059205 | 0.00033544 | -1.3948 | 0.063743 | -0.0028454 | 0.011049 | -0.0027985 | 4.2297 | 121.1929 | -0.14648 | 121.3898 | -0.018311 | -0.1236 | -0.16937 | 2.2247 | 121.1243 | -0.19226 | 121.1472 | -0.07782 | -0.10529 | -0.064087 | 0.11902 | -0.15106 | 0.045777 | 0.24719 | 0.09613 | 0.14191 | -0.022889 | 0.022888 | 0.073242 | -0.21973 | -0.19684 | 0.18768 | 0.20142 | 0.16022 | 0.12817 | 0.086975 | 0.12817 | 121.5363 | 0.11444 | 121.3394 | 121.3394 | 121.3165 | 121.4584 | 121.3898 | -121.4905 | -121.5363 | 121.6553 | 121.4127 | 4.4952 | 2.4902
1188.4219 | 121.7468 | -0.25635 | 121.3577 | -0.0057221 | 0 | 0.06304 | 0.061365 | -0.0012177 | -0.0020658 | -0.0015166 | -0.0028687 | 0.00012184 | -1.3955 | 0.067375 | -0.0022046 | 0.0097669 | -0.00044851 | 4.248 | 121.1792 | -0.13275 | 121.3989 | -0.018311 | -0.14191 | -0.14648 | 2.243 | 121.0968 | -0.18768 | 121.1472 | -0.082397 | -0.10986 | -0.054932 | 0.1236 | -0.17853 | 0.041199 | 0.23804 | 0.10986 | 0.11444 | -0.013733 | -0.009156 | 0.068665 | -0.26093 | -0.21057 | 0.17395 | 0.20142 | 0.14649 | 0.13275 | 0.07782 | 0.11444 | 121.5317 | 0.10529 | 121.3348 | 121.3119 | 121.2845 | 121.4355 | 121.3531 | -121.4905 | -121.5454 | 121.6553 | 121.4035 | 4.5044 | 2.4994
1190.125 | 121.6827 | -0.2655 | 121.3806 | -0.0057221 | 0 | 0.062827 | 0.06457 | -0.0037811 | -0.0014248 | -0.001303 | -0.0028687 | 0.0020444 | -1.3957 | 0.064597 | -0.0049818 | 0.0082715 | 0.00083309 | 4.3259 | 121.1975 | -0.13275 | 121.4172 | -0.004578 | -0.11444 | -0.15564 | 2.2522 | 121.1197 | -0.19684 | 121.1014 | -0.10986 | -0.16022 | -0.11902 | 0.13275 | -0.18311 | 0.036621 | 0.26092 | 0.10986 | 0.15106 | -0.022889 | 0.01831 | 0.068665 | -0.26093 | -0.27924 | 0.15564 | 0.14648 | 0.10529 | 0.077819 | 0.036621 | 0.12817 | 121.55 | 0.086975 | 121.2982 | 121.3303 | 121.3165 | 121.463 | 121.3852 | -121.5134 | -121.5775 | 121.6827 | 121.3669 | 4.5914 | 2.5177
1191.8906 | 121.6187 | -0.29297 | 121.3852 | -0.0057221 | 0 | 0.061758 | 0.068415 | 0.0047637 | -0.0014248 | -0.0040802 | 0.00018312 | 0.0031124 | -1.394 | 0.062675 | -0.0013502 | 0.0097669 | -0.0015167 | 4.2892 | 121.257 | -0.14191 | 121.3211 | -0.14648 | -0.24719 | -0.27008 | 2.1423 | 121.1517 | -0.19226 | 121.0419 | -0.21973 | -0.27466 | -0.16479 | 0.15106 | -0.12817 | -0.064087 | 0.14648 | 0.022888 | 0.045777 | -0.12817 | -0.10528 | 0.10071 | -0.23346 | -0.34332 | 0.073242 | 0.12817 | 0.018311 | 0.027466 | -0.082397 | -0.004577 | 121.463 | -0.027466 | 121.2341 | 121.3989 | 121.344 | 121.55 | 121.4447 | -121.5271 | -121.5775 | 121.6141 | 121.3348 | 4.5822 | 2.4353
1193.6562 | 121.6278 | -0.27924 | 121.3531 | -0.013352 | 0 | 0.06304 | 0.062647 | -0.00057689 | -0.00099764 | -2.1434e-05 | -0.0028687 | 0.001617 | -1.394 | 0.064597 | -0.0049818 | 0.010835 | 0.0042511 | 4.2892 | 121.2112 | -0.16022 | 121.3211 | -0.10071 | -0.20142 | -0.24261 | 2.1423 | 121.1609 | -0.21973 | 121.0236 | -0.18768 | -0.23346 | -0.16479 | 0.11902 | -0.14191 | -0.032043 | 0.17853 | 0.036621 | 0.07782 | -0.082398 | -0.041199 | 0.059509 | -0.19226 | -0.32959 | 0.091553 | 0.11444 | 0.045777 | 0.054932 | -0.013732 | 0.059509 | 121.4813 | 0.032044 | 121.2433 | 121.3715 | 121.3806 | 121.4905 | 121.4401 | -121.5134 | -121.5729 | 121.6003 | 121.3028 | 4.5685 | 2.4216
1195.3594 | 121.6461 | -0.27466 | 121.3669 | 0.017166 | 0 | 0.061972 | 0.063715 | 6.4114e-05 | -0.00099764 | -0.003012 | 0.00018312 | 0.003967 | -1.3957 | 0.066093 | -0.0024182 | 0.010621 | -0.0015167 | 4.3533 | 121.2296 | -0.16022 | 121.3806 | -0.050354 | -0.16022 | -0.2243 | 2.2202 | 121.1609 | -0.20599 | 121.0968 | -0.16479 | -0.21973 | -0.13275 | 0.11444 | -0.13733 | 0.013733 | 0.2243 | 0.050354 | 0.11444 | -0.064087 | 0 | 0.068664 | -0.20599 | -0.27008 | 0.10986 | 0.14191 | 0.054931 | 0.073243 | -0.013733 | 0.10986 | 121.5408 | 0.041199 | 121.3028 | 121.3898 | 121.3669 | 121.5042 | 121.4355 | -121.5271 | -121.5729 | 121.6553 | 121.3715 | 4.628 | 2.4948
1197.125 | 121.7194 | -0.24719 | 121.3348 | 0.070572 | 0 | 0.07009 | 0.065424 | 0.0030547 | -0.0016384 | 0.00083317 | 0.015442 | 0.0028988 | -1.3912 | 0.062675 | -0.00049559 | 0.011049 | -0.00087591 | 4.3304 | 121.2296 | -0.14648 | 121.4401 | 0.050354 | -0.11444 | -0.13275 | 2.2751 | 121.1288 | -0.19684 | 121.1426 | -0.10529 | -0.14648 | -0.082397 | 0.10071 | -0.10529 | 0.10529 | 0.29755 | 0.11444 | 0.13275 | 0.013733 | 0.032043 | 0.050354 | -0.20599 | -0.19226 | 0.14191 | 0.16479 | 0.10071 | 0.11444 | 0.050354 | 0.19684 | 121.5866 | 0.091552 | 121.3394 | 121.376 | 121.3257 | 121.4767 | 121.376 | -121.4813 | -121.5317 | 121.6873 | 121.3898 | 4.5776 | 2.5223
1198.8438 | 121.7285 | -0.23346 | 121.3394 | 0.0019074 | 0 | 0.06304 | 0.060724 | 0.00091851 | -0.0031338 | -0.0015166 | -0.0089723 | 0.00033544 | -1.3955 | 0.060966 | -0.0043408 | 0.010408 | -0.0015167 | 4.3671 | 121.17 | -0.11902 | 121.4722 | 0.045776 | -0.07782 | -0.1236 | 2.2842 | 121.1151 | -0.17395 | 121.1517 | -0.041199 | -0.07782 | -0.050354 | 0.11444 | -0.16937 | 0.13275 | 0.27924 | 0.10986 | 0.15564 | -0.004577 | 0.041199 | 0.059509 | -0.22431 | -0.18768 | 0.19226 | 0.1831 | 0.15564 | 0.1236 | 0.09613 | 0.16479 | 121.5912 | 0.13275 | 121.3257 | 121.2891 | 121.2891 | 121.4035 | 121.3486 | -121.4584 | -121.5134 | 121.7056 | 121.3852 | 4.6005 | 2.5177
1200.5625 | 121.7239 | -0.2243 | 121.3348 | 0.047683 | 0 | 0.066245 | 0.064356 | 0.0011321 | -0.00057044 | -0.00044863 | 0.018494 | 0.0031124 | -1.3937 | 0.067161 | -0.0011364 | 0.010194 | -0.0021575 | 4.3579 | 121.225 | -0.14191 | 121.463 | 0.045776 | -0.086975 | -0.12817 | 2.2659 | 121.1334 | -0.19684 | 121.1655 | -0.086975 | -0.1236 | -0.059509 | 0.082397 | -0.10986 | 0.12817 | 0.27008 | 0.09613 | 0.13733 | 0.013733 | 0.054932 | 0.027466 | -0.20142 | -0.16937 | 0.13733 | 0.16479 | 0.10071 | 0.13733 | 0.073242 | 0.18768 | 121.6049 | 0.10986 | 121.3623 | 121.3669 | 121.3303 | 121.4493 | 121.3577 | -121.4767 | -121.5317 | 121.6873 | 121.3898 | 4.5822 | 2.4902
1202.3281 | 121.7239 | -0.25177 | 121.376 | 0.0095369 | 0 | 0.063467 | 0.063288 | -0.00014949 | 0.00071136 | -2.1434e-05 | 0.00018312 | 0.002258 | -1.3959 | 0.062675 | -0.0034864 | 0.011049 | -0.00023491 | 4.3121 | 121.2067 | -0.14191 | 121.3943 | -0.054932 | -0.14648 | -0.18768 | 2.1835 | 121.1334 | -0.19684 | 121.1151 | -0.11902 | -0.16022 | -0.091553 | 0.10986 | -0.16937 | 0.01831 | 0.19684 | 0.064087 | 0.10529 | -0.045776 | -0.004577 | 0.054932 | -0.24262 | -0.26093 | 0.13275 | 0.16022 | 0.091553 | 0.10529 | 0.036621 | 0.086975 | 121.5363 | 0.077819 | 121.3119 | 121.3486 | 121.3303 | 121.4584 | 121.3852 | -121.5179 | -121.5729 | 121.6461 | 121.3669 | 4.5639 | 2.4353
1204.0938 | 121.6919 | -0.23804 | 121.3623 | 0.017166 | 0 | 0.066031 | 0.064997 | 0.0013459 | -0.001852 | -0.00087583 | 0.015442 | 0.0028988 | -1.3929 | 0.063957 | -0.0015638 | 0.011689 | 0.0042511 | 4.3488 | 121.2067 | -0.14648 | 121.4355 | 0.036621 | -0.11444 | -0.13733 | 2.2568 | 121.1609 | -0.19226 | 121.1243 | -0.11444 | -0.13275 | -0.091553 | 0.091553 | -0.15564 | 0.073242 | 0.27466 | 0.10071 | 0.1236 | 0.009155 | 0.032043 | 0.045776 | -0.20142 | -0.23804 | 0.1236 | 0.14648 | 0.10529 | 0.10071 | 0.05951 | 0.18311 | 121.582 | 0.07782 | 121.3165 | 121.3531 | 121.3531 | 121.4447 | 121.3989 | -121.5088 | -121.5546 | 121.6736 | 121.3623 | 4.5868 | 2.4948
1205.7969 | 121.6049 | -0.27924 | 121.3852 | 0.0019074 | 0 | 0.064322 | 0.066706 | 0.0062591 | -0.00099764 | -0.003653 | 0.00018312 | 0.003326 | -1.394 | 0.055625 | -0.001991 | 0.0086987 | -0.0027985 | 4.335 | 121.257 | -0.14648 | 121.3303 | -0.14191 | -0.25635 | -0.28839 | 2.1011 | 121.1884 | -0.19226 | 121.0236 | -0.25177 | -0.27466 | -0.16022 | 0.13275 | -0.12817 | -0.054932 | 0.13733 | -0.009155 | 0.022888 | -0.14191 | -0.10986 | 0.086975 | -0.19684 | -0.36163 | 0.027466 | 0.11902 | 0.004578 | 0.032044 | -0.082397 | 0.004577 | 121.4767 | -0.059509 | 121.2158 | 121.4035 | 121.3806 | 121.5363 | 121.4676 | -121.5317 | -121.5775 | 121.6095 | 121.3028 | 4.6143 | 2.3804
1207.5469 | 121.669 | -0.27008 | 121.3989 | 0.047683 | 0 | 0.065817 | 0.064997 | -0.0012177 | -0.0050564 | 0.0010468 | 0.01239 | 0.0037532 | -1.3946 | 0.063743 | -0.005409 | 0.010835 | -0.0023713 | 4.3945 | 121.2616 | -0.17395 | 121.3898 | -0.068665 | -0.16479 | -0.20599 | 2.2202 | 121.1884 | -0.21973 | 121.0876 | -0.15564 | -0.19226 | -0.10986 | 0.096131 | -0.13733 | -0.009155 | 0.20142 | 0.064087 | 0.10529 | -0.032044 | 0.009155 | 0.050354 | -0.21057 | -0.31128 | 0.11444 | 0.16022 | 0.07782 | 0.10986 | 0.027466 | 0.10528 | 121.5637 | 0.064087 | 121.3074 | 121.4355 | 121.4081 | 121.5317 | 121.4584 | -121.5729 | -121.6187 | 121.6599 | 121.3577 | 4.6646 | 2.4902
1209.3281 | 121.7789 | -0.2243 | 121.3486 | 0.0019074 | 0 | 0.061118 | 0.060511 | -0.0031403 | -0.003561 | -0.00023503 | -0.0059205 | 0.0026852 | -1.3944 | 0.072074 | -0.0049818 | 0.0097669 | -0.00023491 | 4.3671 | 121.1609 | -0.11902 | 121.4539 | 0.041199 | -0.07782 | -0.11444 | 2.2614 | 121.1243 | -0.18768 | 121.17 | -0.018311 | -0.054932 | -0.027466 | 0.10529 | -0.18768 | 0.10528 | 0.2655 | 0.10986 | 0.14648 | 0.004578 | 0.041199 | 0.036621 | -0.2243 | -0.17853 | 0.20599 | 0.19684 | 0.16937 | 0.16022 | 0.13275 | 0.16022 | 121.5729 | 0.16937 | 121.3577 | 121.2799 | 121.312 | 121.3852 | 121.3486 | -121.4676 | -121.5363 | 121.6782 | 121.3943 | 4.5914 | 2.4857
1211.0312 | 121.6782 | -0.24719 | 121.3715 | 0.017166 | 0 | 0.064536 | 0.064142 | -0.00014949 | -0.0029202 | 0.001474 | 0.0093383 | 0.0014034 | -1.3952 | 0.067588 | -0.0026318 | 0.010835 | 0.0010467 | 4.3213 | 121.2204 | -0.14191 | 121.3989 | -0.036621 | -0.13733 | -0.1831 | 2.1698 | 121.1472 | -0.19684 | 121.1151 | -0.13275 | -0.16937 | -0.09613 | 0.10528 | -0.15106 | 0.027466 | 0.21057 | 0.064087 | 0.10986 | -0.041198 | 0.004578 | 0.050354 | -0.2243 | -0.25635 | 0.11444 | 0.15106 | 0.077819 | 0.10071 | 0.027465 | 0.10529 | 121.5408 | 0.064087 | 121.3119 | 121.3623 | 121.344 | 121.4676 | 121.3943 | -121.5134 | -121.5683 | 121.6461 | 121.3623 | 4.5685 | 2.417
1212.7969 | 121.7285 | -0.2243 | 121.344 | -0.0057221 | 0 | 0.064322 | 0.062861 | 0.0015595 | -0.0031338 | -0.001944 | -0.0028687 | 0.00097624 | -1.3959 | 0.063102 | -0.0028454 | 0.0091261 | -0.00044851 | 4.3808 | 121.1884 | -0.1236 | 121.4584 | 0.045776 | -0.064087 | -0.11444 | 2.3071 | 121.138 | -0.16937 | 121.1609 | -0.041199 | -0.086975 | -0.041199 | 0.10071 | -0.15564 | 0.11444 | 0.27008 | 0.10986 | 0.16022 | 0.009155 | 0.059509 | 0.054931 | -0.20599 | -0.1831 | 0.18311 | 0.18311 | 0.13733 | 0.12817 | 0.082398 | 0.16937 | 121.582 | 0.12817 | 121.3303 | 121.312 | 121.3074 | 121.4127 | 121.3623 | -121.4676 | -121.5134 | 121.6827 | 121.3852 | 4.6051 | 2.5314
1214.5 | 121.7422 | -0.21973 | 121.3623 | 0.0019074 | 0 | 0.062613 | 0.064142 | 0.0028411 | -0.00035684 | -0.0021576 | -0.0059205 | 0.00033544 | -1.3969 | 0.063529 | -0.0011364 | 0.011903 | -0.0034393 | 4.3945 | 121.2341 | -0.10529 | 121.4355 | 0.004578 | -0.11902 | -0.16479 | 2.2705 | 121.1243 | -0.16022 | 121.1746 | -0.059509 | -0.11902 | -0.036621 | 0.11444 | -0.12817 | 0.073242 | 0.22431 | 0.054932 | 0.10071 | -0.059509 | -0.013733 | 0.05951 | -0.23804 | -0.18768 | 0.16022 | 0.18311 | 0.10071 | 0.1236 | 0.041198 | 0.10986 | 121.5408 | 0.10071 | 121.3348 | 121.3394 | 121.2845 | 121.4539 | 121.344 | -121.4676 | -121.5225 | 121.6553 | 121.3943 | 4.6143 | 2.4902
1216.2656 | 121.6736 | -0.27924 | 121.3669 | -0.013352 | 0 | 0.062613 | 0.063929 | -0.0024995 | -0.0031338 | -0.0025848 | -0.0059205 | 0.00076264 | -1.3974 | 0.065238 | -0.0051954 | 0.0082715 | -0.0032257 | 4.4083 | 121.1746 | -0.1236 | 121.4172 | -0.018311 | -0.11444 | -0.16937 | 2.243 | 121.1472 | -0.18768 | 121.0922 | -0.13275 | -0.15564 | -0.10529 | 0.15564 | -0.19226 | 0.050354 | 0.26092 | 0.10986 | 0.16479 | -0.045777 | 0.009155 | 0.091553 | -0.21973 | -0.27466 | 0.14648 | 0.17395 | 0.1236 | 0.082397 | 0.032043 | 0.10528 | 121.5408 | 0.054932 | 121.2799 | 121.2982 | 121.3348 | 121.4539 | 121.4264 | -121.4905 | -121.5546 | 121.6965 | 121.3715 | 4.6875 | 2.5223
1217.9688 | 121.7056 | -0.26093 | 121.3623 | 0.017166 | 0 | 0.062613 | 0.061793 | 0.0045501 | -0.0044156 | 0.001474 | 0.0062865 | 0.00076264 | -1.3948 | 0.054984 | -0.00070919 | 0.0099805 | 0.0012603 | 4.3533 | 121.225 | -0.13733 | 121.3898 | -0.022888 | -0.14648 | -0.19226 | 2.1927 | 121.1609 | -0.19684 | 121.106 | -0.13733 | -0.14648 | -0.091553 | 0.1236 | -0.13733 | 0.027466 | 0.23804 | 0.068664 | 0.11444 | -0.054932 | -0.009155 | 0.064087 | -0.20142 | -0.25635 | 0.1236 | 0.16937 | 0.11444 | 0.10529 | 0.050354 | 0.11444 | 121.5271 | 0.059509 | 121.3028 | 121.3623 | 121.3577 | 121.4859 | 121.4218 | -121.4996 | -121.5591 | 121.6507 | 121.3669 | 4.6143 | 2.4536
1219.7344 | 121.7056 | -0.2655 | 121.3623 | 0.017166 | 0 | 0.064322 | 0.063929 | -0.0027131 | -0.001852 | 0.0019012 | 0.0093383 | 0.002258 | -1.3967 | 0.061179 | -0.0024182 | 0.011262 | -0.0010895 | 4.3762 | 121.2708 | -0.1236 | 121.4127 | -0.018311 | -0.13275 | -0.16479 | 2.211 | 121.1655 | -0.19684 | 121.1197 | -0.1236 | -0.16479 | -0.09613 | 0.14191 | -0.091553 | 0.050354 | 0.24719 | 0.10071 | 0.13275 | -0.041199 | -0.009155 | 0.068665 | -0.19684 | -0.24262 | 0.14191 | 0.16937 | 0.10071 | 0.10071 | 0.032043 | 0.10528 | 121.5363 | 0.073242 | 121.3165 | 121.3943 | 121.3623 | 121.5363 | 121.431 | -121.4859 | -121.5591 | 121.6782 | 121.3852 | 4.6417 | 2.4765
1221.4844 | 121.701 | -0.25635 | 121.3394 | 0.032425 | 0 | 0.064108 | 0.065211 | -0.0014313 | 0.00049776 | -0.001303 | 0.0093383 | 0.0026852 | -1.3937 | 0.069724 | -0.004768 | 0.0093397 | -2.1314e-05 | 4.3671 | 121.2296 | -0.13275 | 121.4081 | -0.022888 | -0.14191 | -0.16937 | 2.2293 | 121.1517 | -0.20599 | 121.1151 | -0.11444 | -0.16022 | -0.10071 | 0.1236 | -0.10986 | 0.068664 | 0.23346 | 0.086975 | 0.11444 | -0.036622 | -0.009156 | 0.050354 | -0.18768 | -0.22431 | 0.14191 | 0.15564 | 0.096131 | 0.10529 | 0.045777 | 0.10986 | 121.5408 | 0.091553 | 121.3211 | 121.3623 | 121.3577 | 121.4859 | 121.4081 | -121.4722 | -121.5454 | 121.6644 | 121.3715 | 4.6234 | 2.4857
1223.1875 | 121.6827 | -0.24719 | 121.3623 | -0.0057221 | 0 | 0.064108 | 0.06457 | -0.0024995 | -0.0031338 | -0.001303 | -0.0028687 | 0.0028988 | -1.3946 | 0.066306 | -0.001991 | 0.0097669 | 0.0016877 | 4.3716 | 121.2524 | -0.16022 | 121.3394 | -0.11444 | -0.24719 | -0.23346 | 2.1378 | 121.1655 | -0.1831 | 121.1105 | -0.15106 | -0.19226 | -0.10986 | 0.086975 | -0.10986 | -0.022888 | 0.13275 | 0.013733 | 0 | -0.073242 | -0.086975 | 0.064087 | -0.19684 | -0.25177 | 0.09613 | 0.13733 | 0.054931 | 0.073242 | -0.009156 | 0.045776 | 121.4996 | 0.032043 | 121.2936 | 121.4127 | 121.3486 | 121.4996 | 121.4127 | -121.5225 | -121.5454 | 121.5866 | 121.3577 | 4.6188 | 2.3849
1224.9688 | 121.6736 | -0.25177 | 121.3531 | 0.024795 | 0 | 0.064536 | 0.063502 | 0.00070491 | 7.0564e-05 | -0.0010894 | 0.0032349 | 0.00097624 | -1.3946 | 0.066734 | -0.0043408 | 0.0093397 | 0.00083309 | 4.3716 | 121.2341 | -0.14191 | 121.3898 | -0.050354 | -0.15106 | -0.17395 | 2.1973 | 121.1655 | -0.18768 | 121.1014 | -0.12817 | -0.16479 | -0.11444 | 0.10986 | -0.11902 | 0.036622 | 0.20142 | 0.07782 | 0.10071 | -0.032043 | -0.009155 | 0.064087 | -0.18768 | -0.25177 | 0.1236 | 0.13733 | 0.086975 | 0.073242 | 0.022888 | 0.091553 | 121.5317 | 0.059509 | 121.2891 | 121.376 | 121.3531 | 121.4859 | 121.4172 | -121.4951 | -121.5408 | 121.6415 | 121.3531 | 4.6234 | 2.449
1226.7188 | 121.7606 | -0.24719 | 121.3303 | -0.0057221 | 0 | 0.063895 | 0.062433 | -0.0010041 | -0.003561 | 0.0010468 | -0.0028687 | -0.00030556 | -1.3952 | 0.065238 | -0.0043408 | 0.0080579 | 0.0012603 | 4.4495 | 121.1884 | -0.11902 | 121.4676 | 0.054932 | -0.068665 | -0.13733 | 2.3117 | 121.1472 | -0.16022 | 121.1792 | -0.032043 | -0.091553 | -0.045776 | 0.12817 | -0.14191 | 0.13733 | 0.30212 | 0.10986 | 0.17853 | -0.01831 | 0.050354 | 0.086975 | -0.1831 | -0.15106 | 0.21515 | 0.20142 | 0.15564 | 0.11444 | 0.068664 | 0.17395 | 121.5866 | 0.12817 | 121.3394 | 121.3074 | 121.3074 | 121.4355 | 121.3943 | -121.4493 | -121.4905 | 121.7148 | 121.4264 | 4.6967 | 2.5589
1228.4688 | 121.701 | -0.24719 | 121.3623 | 0.0019074 | 0 | 0.063681 | 0.06222 | -0.00014949 | -0.001852 | -0.0015166 | -0.0059205 | 0.00097624 | -1.3957 | 0.064384 | -0.0032728 | 0.0080579 | -0.00087591 | 4.4769 | 121.1838 | -0.091553 | 121.4493 | 0.009155 | -0.09613 | -0.14648 | 2.2614 | 121.138 | -0.18768 | 121.1243 | -0.073242 | -0.12817 | -0.086975 | 0.15564 | -0.17853 | 0.086975 | 0.25635 | 0.10071 | 0.15106 | -0.054931 | -0.004577 | 0.059509 | -0.22431 | -0.23804 | 0.17395 | 0.16022 | 0.11902 | 0.10071 | 0.059509 | 0.10071 | 121.5408 | 0.11444 | 121.312 | 121.2753 | 121.3257 | 121.431 | 121.3852 | -121.4539 | -121.55 | 121.6965 | 121.3715 | 4.7241 | 2.5085
1230.25 | 121.6965 | -0.2243 | 121.3394 | 0.032425 | 0 | 0.064108 | 0.065211 | -0.0016449 | -0.0012112 | -0.001944 | 0.015442 | 0.0020444 | -1.3952 | 0.064811 | -0.0013502 | 0.0084851 | 0.00061949 | 4.4724 | 121.2204 | -0.14648 | 121.463 | 0.054932 | -0.09613 | -0.14191 | 2.2842 | 121.1746 | -0.19226 | 121.138 | -0.10529 | -0.1236 | -0.054932 | 0.07782 | -0.11902 | 0.1236 | 0.27924 | 0.082397 | 0.12817 | 0.004577 | 0.050354 | 0.032043 | -0.16479 | -0.20142 | 0.11902 | 0.16937 | 0.10071 | 0.13733 | 0.068665 | 0.20142 | 121.6095 | 0.086975 | 121.3303 | 121.3669 | 121.3669 | 121.4447 | 121.3989 | -121.4859 | -121.5317 | 121.6873 | 121.3623 | 4.6967 | 2.5085
1232 | 121.6049 | -0.28839 | 121.3898 | 0.0019074 | 0 | 0.062186 | 0.064142 | -0.0035675 | -0.0022794 | -0.001303 | -0.0028687 | 0.0035396 | -1.394 | 0.062248 | -0.0045544 | 0.0099805 | -0.00023491 | 4.4449 | 121.2524 | -0.14648 | 121.3303 | -0.14191 | -0.24261 | -0.28381 | 2.1378 | 121.2067 | -0.20142 | 121.0281 | -0.21973 | -0.27924 | -0.15564 | 0.14191 | -0.13733 | -0.05951 | 0.14648 | 0.004578 | 0.045776 | -0.13733 | -0.096131 | 0.086975 | -0.18311 | -0.36163 | 0.068664 | 0.13275 | 0.009155 | 0.045776 | -0.07782 | 0.004577 | 121.4767 | -0.018311 | 121.2296 | 121.3989 | 121.4081 | 121.5408 | 121.4951 | -121.5363 | -121.5912 | 121.6187 | 121.3165 | 4.7333 | 2.4261
1233.7031 | 121.7743 | -0.24261 | 121.3303 | 0.0019074 | 0 | 0.064108 | 0.062647 | -0.00036309 | -0.0029202 | 0.00040597 | 0.00018312 | 0.0018306 | -1.3972 | 0.063743 | -0.0051954 | 0.010835 | -0.0013031 | 4.4586 | 121.2112 | -0.11444 | 121.4493 | 0.045776 | -0.059509 | -0.10071 | 2.3346 | 121.1334 | -0.16479 | 121.1975 | -0.045776 | -0.073242 | -0.050354 | 0.12817 | -0.11902 | 0.11902 | 0.28839 | 0.14191 | 0.18311 | 0.013733 | 0.054932 | 0.07782 | -0.19684 | -0.13275 | 0.19684 | 0.19226 | 0.16937 | 0.11444 | 0.091553 | 0.16022 | 121.5637 | 0.11902 | 121.3623 | 121.3257 | 121.2982 | 121.4539 | 121.376 | -121.4447 | -121.4951 | 121.6919 | 121.4401 | 4.7012 | 2.5772
1235.4688 | 121.7606 | -0.22888 | 121.3531 | -0.0057221 | 0 | 0.064108 | 0.061793 | -0.0024995 | -0.001852 | 0.00083317 | -0.0028687 | 0.00076264 | -1.394 | 0.06182 | -0.0034864 | 0.0089123 | -0.0013031 | 4.4907 | 121.1792 | -0.10529 | 121.4539 | 0.068665 | -0.064087 | -0.091553 | 2.3666 | 121.106 | -0.16479 | 121.2067 | -0.032043 | -0.073242 | -0.045776 | 0.1236 | -0.17395 | 0.10071 | 0.29755 | 0.13733 | 0.16479 | 0.013733 | 0.041199 | 0.064087 | -0.24719 | -0.14648 | 0.19684 | 0.18311 | 0.15564 | 0.11902 | 0.091553 | 0.17395 | 121.5591 | 0.13275 | 121.3715 | 121.2845 | 121.2708 | 121.4081 | 121.3348 | -121.4584 | -121.5179 | 121.6827 | 121.4355 | 4.7195 | 2.5955
1237.1719 | 121.6095 | -0.27008 | 121.4172 | -0.013352 | 0 | 0.063467 | 0.063288 | -0.0012177 | -0.0039884 | -0.00023503 | -0.0028687 | 0.001617 | -1.394 | 0.056693 | -0.0056226 | 0.0074171 | -0.00087591 | 4.4403 | 121.2158 | -0.15106 | 121.3257 | -0.09613 | -0.19226 | -0.23804 | 2.2018 | 121.1838 | -0.21057 | 121.0419 | -0.19226 | -0.21973 | -0.16479 | 0.11902 | -0.20142 | -0.091552 | 0.17395 | 0.032044 | 0.07782 | -0.086975 | -0.041199 | 0.05951 | -0.23346 | -0.37537 | 0.07782 | 0.10529 | 0.050354 | 0.045776 | -0.009156 | 0.054932 | 121.4767 | 0.01831 | 121.2524 | 121.3669 | 121.3943 | 121.4859 | 121.4539 | -121.5683 | -121.6278 | 121.5958 | 121.312 | 4.7104 | 2.4719
1238.9375 | 121.701 | -0.24261 | 121.3623 | 0.047683 | 0 | 0.066458 | 0.064142 | 0.0019867 | 0.00071136 | 0.0027558 | 0.0062865 | 0.0035396 | -1.3942 | 0.059898 | -0.0017774 | 0.010835 | 0.00083309 | 4.4952 | 121.2387 | -0.13733 | 121.431 | 0.027466 | -0.10071 | -0.14191 | 2.2659 | 121.1472 | -0.19226 | 121.1334 | -0.10986 | -0.14648 | -0.086975 | 0.10529 | -0.1236 | 0.068664 | 0.27008 | 0.10071 | 0.14191 | -0.004578 | 0.036621 | 0.050354 | -0.21515 | -0.22888 | 0.13275 | 0.15564 | 0.096131 | 0.10529 | 0.045777 | 0.16479 | 121.5683 | 0.082398 | 121.3257 | 121.376 | 121.3394 | 121.4813 | 121.3898 | -121.4996 | -121.5546 | 121.6736 | 121.376 | 4.7379 | 2.5085
1240.7188 | 121.5958 | -0.28839 | 121.3943 | 0.0019074 | 0 | 0.065176 | 0.066065 | 0.0013459 | -0.0031338 | -0.0021576 | -0.0089723 | 0.0031124 | -1.3944 | 0.062034 | -0.0026318 | 0.010194 | -0.0038665 | 4.4907 | 121.2708 | -0.1236 | 121.3165 | -0.12817 | -0.24261 | -0.2655 | 2.179 | 121.1746 | -0.19684 | 121.0464 | -0.21057 | -0.27008 | -0.16479 | 0.1648 | -0.1236 | -0.07782 | 0.16022 | 0.022888 | 0.045776 | -0.14191 | -0.11902 | 0.091553 | -0.21973 | -0.3479 | 0.07782 | 0.1236 | 0.01831 | 0.032043 | -0.073243 | -0.004578 | 121.4401 | -0.013733 | 121.2433 | 121.3943 | 121.3715 | 121.5591 | 121.463 | -121.5179 | -121.5912 | 121.6049 | 121.3348 | 4.7791 | 2.4673
1242.4375 | 121.7239 | -0.25177 | 121.3531 | 0.024795 | 0 | 0.061758 | 0.063715 | 0.00070491 | -0.0016384 | -0.00066223 | -0.0028687 | 0.0011898 | -1.3942 | 0.061179 | -0.001991 | 0.011049 | 0.0021149 | 4.454 | 121.2067 | -0.13275 | 121.3898 | -0.018311 | -0.13733 | -0.16937 | 2.2385 | 121.1609 | -0.19226 | 121.138 | -0.09613 | -0.11902 | -0.059509 | 0.11902 | -0.14648 | 0.036622 | 0.23346 | 0.082397 | 0.11444 | -0.036622 | -0.004578 | 0.059509 | -0.19226 | -0.21515 | 0.15564 | 0.19226 | 0.13275 | 0.13275 | 0.073242 | 0.11444 | 121.5225 | 0.096131 | 121.3303 | 121.3394 | 121.3531 | 121.4584 | 121.4127 | -121.4859 | -121.5454 | 121.6415 | 121.3898 | 4.7058 | 2.4902
1244.2031 | 121.6507 | -0.27008 | 121.3943 | 0.0095369 | 0 | 0.064536 | 0.066706 | 0.0034821 | -0.0033474 | -0.0027984 | 0.00018312 | 0.005676 | -1.3937 | 0.06417 | -0.0028454 | 0.0097669 | -0.00087591 | 4.5685 | 121.257 | -0.16022 | 121.3852 | -0.032043 | -0.16022 | -0.20142 | 2.2568 | 121.1838 | -0.19684 | 121.0876 | -0.14648 | -0.19226 | -0.10986 | 0.10986 | -0.13733 | -0.009155 | 0.23804 | 0.068665 | 0.10986 | -0.041199 | 0 | 0.073243 | -0.21057 | -0.3067 | 0.1236 | 0.16022 | 0.07782 | 0.086975 | 0.004577 | 0.12817 | 121.5454 | 0.050354 | 121.2845 | 121.4172 | 121.3806 | 121.5271 | 121.4539 | -121.5546 | -121.5912 | 121.6553 | 121.3577 | 4.8386 | 2.5269
1245.9688 | 121.5912 | -0.25635 | 121.4081 | 0.0019074 | 0 | 0.064536 | 0.065211 | 0.0022003 | -0.0037746 | 0.00040597 | 0.00018312 | 0.0024716 | -1.3959 | 0.057762 | -0.0026318 | 0.0099805 | -0.00066231 | 4.4815 | 121.2479 | -0.13275 | 121.3211 | -0.14191 | -0.24719 | -0.28381 | 2.1286 | 121.1746 | -0.19684 | 121.0373 | -0.21057 | -0.27466 | -0.16022 | 0.1236 | -0.16022 | -0.086975 | 0.11444 | -0.027465 | 0.009156 | -0.15106 | -0.11444 | 0.05951 | -0.23346 | -0.37079 | 0.045777 | 0.096131 | -0.01831 | 0.036621 | -0.07782 | -0.009156 | 121.4539 | -0.013733 | 121.2341 | 121.3806 | 121.3715 | 121.5042 | 121.431 | -121.5408 | -121.6049 | 121.5775 | 121.2936 | 4.7379 | 2.3849
1247.7188 | 121.6232 | -0.2655 | 121.4035 | 0.0019074 | 0 | 0.062186 | 0.063288 | 0.0022003 | -0.0014248 | -0.0021576 | -0.0059205 | 0.003326 | -1.3944 | 0.060966 | -0.0011364 | 0.010194 | -0.0042939 | 4.5181 | 121.2708 | -0.13275 | 121.3486 | -0.059509 | -0.20599 | -0.22888 | 2.211 | 121.1792 | -0.17395 | 121.0739 | -0.17853 | -0.24719 | -0.13733 | 0.13275 | -0.13275 | -0.054931 | 0.20599 | 0.036621 | 0.059509 | -0.096131 | -0.073243 | 0.091553 | -0.2243 | -0.32959 | 0.086975 | 0.12817 | 0.018311 | 0.036621 | -0.073242 | 0.073242 | 121.4813 | -0.004578 | 121.2479 | 121.4035 | 121.3531 | 121.5363 | 121.4447 | -121.5363 | -121.5775 | 121.6141 | 121.3394 | 4.7836 | 2.4765
1249.4219 | 121.7697 | -0.22888 | 121.3531 | -0.013352 | 0 | 0.062186 | 0.06457 | -0.0016449 | -0.0031338 | 0.0016876 | 0.00018312 | 0.0024716 | -1.3957 | 0.063316 | -0.0026318 | 0.011049 | -0.00023491 | 4.541 | 121.1929 | -0.10529 | 121.4355 | 0.041199 | -0.073242 | -0.10529 | 2.3438 | 121.138 | -0.16479 | 121.1929 | -0.027466 | -0.059509 | -0.027466 | 0.1236 | -0.16022 | 0.082398 | 0.27008 | 0.1236 | 0.15564 | 0 | 0.032044 | 0.064087 | -0.21515 | -0.16022 | 0.20142 | 0.20142 | 0.16937 | 0.13733 | 0.10529 | 0.14649 | 121.5408 | 0.13733 | 121.3577 | 121.2982 | 121.3028 | 121.4218 | 121.3669 | -121.4584 | -121.5179 | 121.6644 | 121.4218 | 4.7699 | 2.5726
1251.2031 | 121.6736 | -0.2655 | 121.4081 | 0.047683 | 0 | 0.063681 | 0.065638 | -0.0022857 | -0.00035684 | 0.00061957 | 0.0093383 | 0.0063168 | -1.3937 | 0.062461 | -0.0024182 | 0.0086987 | -0.00023491 | 4.5914 | 121.2891 | -0.19684 | 121.3852 | -0.068665 | -0.15106 | -0.19226 | 2.2842 | 121.17 | -0.20142 | 121.0968 | -0.12817 | -0.16937 | -0.10071 | 0.068665 | -0.11902 | -0.022888 | 0.19684 | 0.073242 | 0.11444 | 0.004577 | 0.045776 | 0.064087 | -0.23804 | -0.31128 | 0.13733 | 0.16479 | 0.09613 | 0.10071 | 0.032043 | 0.12817 | 121.582 | 0.073242 | 121.2982 | 121.4859 | 121.3715 | 121.5546 | 121.4355 | -121.6049 | -121.6095 | 121.6507 | 121.3623 | 4.8569 | 2.5497
1252.9688 | 121.7285 | -0.23346 | 121.3806 | 0.0095369 | 0 | 0.066458 | 0.065638 | 0.0022003 | -0.0029202 | -0.001303 | 0.0032349 | 0.00076264 | -1.3965 | 0.063743 | -0.001991 | 0.011689 | -0.00023491 | 4.4907 | 121.2799 | -0.12817 | 121.3577 | -0.068665 | -0.1831 | -0.21973 | 2.2247 | 121.1655 | -0.16937 | 121.1517 | -0.10071 | -0.13733 | -0.059509 | 0.10528 | -0.10071 | -0.022888 | 0.16479 | 0.013732 | 0.050354 | -0.091553 | -0.054931 | 0.064086 | -0.21515 | -0.22888 | 0.13275 | 0.17395 | 0.09613 | 0.10986 | 0.032044 | 0.059509 | 121.4859 | 0.068665 | 121.3211 | 121.4081 | 121.3348 | 121.5134 | 121.3989 | -121.5088 | -121.55 | 121.5912 | 121.3852 | 4.7241 | 2.4582
1254.75 | 121.5912 | -0.27466 | 121.4172 | -0.0057221 | 0 | 0.06304 | 0.062647 | 0.00049131 | -0.003561 | 0.0010468 | 0.00018312 | 0.0041806 | -1.3948 | 0.057334 | -0.0028454 | 0.010408 | -0.0042939 | 4.5364 | 121.2753 | -0.14648 | 121.3257 | -0.13733 | -0.2655 | -0.27466 | 2.1332 | 121.1838 | -0.20599 | 121.0327 | -0.22888 | -0.27924 | -0.15564 | 0.12817 | -0.14191 | -0.091552 | 0.13733 | 0 | 0.009155 | -0.12817 | -0.11902 | 0.068664 | -0.23346 | -0.38452 | 0.045776 | 0.11902 | -0.004578 | 0.050354 | -0.073242 | 0.009155 | 121.4722 | -0.022888 | 121.2387 | 121.4218 | 121.3898 | 121.55 | 121.4584 | -121.5637 | -121.6232 | 121.6003 | 121.3074 | 4.8111 | 2.4078
1256.5156 | 121.7194 | -0.25177 | 121.376 | 0.0095369 | 0 | 0.064322 | 0.063502 | -0.0018585 | -0.0037746 | -0.001944 | 0.0093383 | -0.0015872 | -1.3927 | 0.066306 | -0.0034864 | 0.0097669 | 0.0014741 | 4.5364 | 121.2433 | -0.13275 | 121.3989 | -0.036621 | -0.13733 | -0.1831 | 2.2247 | 121.1655 | -0.17395 | 121.1243 | -0.11902 | -0.15564 | -0.07782 | 0.11902 | -0.13275 | 0.022888 | 0.21515 | 0.068665 | 0.11444 | -0.050354 | -0.004578 | 0.07782 | -0.21057 | -0.25177 | 0.13275 | 0.17395 | 0.09613 | 0.09613 | 0.01831 | 0.09613 | 121.5317 | 0.054931 | 121.2982 | 121.376 | 121.3394 | 121.4951 | 121.4172 | -121.5088 | -121.55 | 121.6507 | 121.376 | 4.7882 | 2.4765
1258.2188 | 121.6919 | -0.25177 | 121.376 | -0.0057221 | 0 | 0.064536 | 0.064997 | 0.0022003 | -0.00014304 | 0.0012604 | -0.0028687 | 0.0026852 | -1.395 | 0.067588 | -0.001991 | 0.010621 | -0.00087591 | 4.5181 | 121.2708 | -0.13733 | 121.3577 | -0.09613 | -0.2243 | -0.23804 | 2.2385 | 121.1609 | -0.19226 | 121.1334 | -0.11444 | -0.16479 | -0.068665 | 0.11444 | -0.10529 | -0.018311 | 0.15564 | 0.013733 | 0.027466 | -0.10071 | -0.086975 | 0.059509 | -0.21515 | -0.24262 | 0.13733 | 0.1831 | 0.086975 | 0.1236 | 0.027466 | 0.041199 | 121.4951 | 0.07782 | 121.3257 | 121.4081 | 121.3531 | 121.5225 | 121.4127 | -121.5134 | -121.5683 | 121.6095 | 121.3852 | 4.7699 | 2.4902
1259.9844 | 121.6644 | -0.25177 | 121.4081 | 0.024795 | 0 | 0.064536 | 0.065638 | 0.0041229 | -0.0022794 | 0.0012604 | 0.0093383 | 0.00097624 | -1.3948 | 0.061393 | -0.0062634 | 0.010194 | 0.0012603 | 4.6326 | 121.2616 | -0.17853 | 121.3989 | -0.045776 | -0.13733 | -0.17853 | 2.3071 | 121.1655 | -0.19684 | 121.106 | -0.11902 | -0.1831 | -0.086975 | 0.073242 | -0.14648 | -0.009155 | 0.20599 | 0.073242 | 0.11444 | 0 | 0.041199 | 0.054932 | -0.24262 | -0.30212 | 0.13275 | 0.16479 | 0.068665 | 0.10986 | 0.013733 | 0.13275 | 121.5775 | 0.077819 | 121.3028 | 121.4401 | 121.3623 | 121.5134 | 121.4172 | -121.5866 | -121.6049 | 121.6507 | 121.3577 | 4.8843 | 2.5589
1261.6719 | 121.7056 | -0.23804 | 121.3806 | 0.032425 | 0 | 0.065817 | 0.063929 | -0.0037811 | -0.00014304 | 0.0012604 | 0.018494 | 0.0020444 | -1.3937 | 0.06887 | -0.0026318 | 0.011476 | -0.00066231 | 4.6097 | 121.2479 | -0.12817 | 121.4401 | 0.050354 | -0.086975 | -0.11444 | 2.3209 | 121.1609 | -0.19684 | 121.1334 | -0.10071 | -0.11444 | -0.073242 | 0.10986 | -0.13275 | 0.05951 | 0.28839 | 0.1236 | 0.15106 | 0.013733 | 0.041199 | 0.041199 | -0.21973 | -0.24719 | 0.13733 | 0.16479 | 0.1236 | 0.1236 | 0.082397 | 0.17853 | 121.5683 | 0.09613 | 121.3303 | 121.376 | 121.3577 | 121.4859 | 121.3989 | -121.5088 | -121.5775 | 121.6782 | 121.3715 | 4.8477 | 2.5589
1263.4375 | 121.6965 | -0.22888 | 121.3898 | 0.047683 | 0 | 0.064749 | 0.064783 | 0.0041229 | -0.0033474 | -0.00044863 | 0.0062865 | 0.0035396 | -1.3922 | 0.063316 | -0.0049818 | 0.010194 | 0.00019229 | 4.6143 | 121.2662 | -0.14648 | 121.4401 | 0.036621 | -0.09613 | -0.15106 | 2.3117 | 121.1609 | -0.20142 | 121.1288 | -0.10986 | -0.13733 | -0.07782 | 0.082398 | -0.1236 | 0.050354 | 0.2655 | 0.07782 | 0.13275 | -0.004578 | 0.050354 | 0.027466 | -0.22888 | -0.26093 | 0.11902 | 0.15106 | 0.091553 | 0.1236 | 0.064087 | 0.18311 | 121.5866 | 0.091553 | 121.3303 | 121.4127 | 121.3623 | 121.4951 | 121.3898 | -121.5363 | -121.5912 | 121.669 | 121.3577 | 4.8431 | 2.5406
1265.2188 | 121.6415 | -0.27008 | 121.4035 | 0.0095369 | 0 | 0.061118 | 0.065638 | 0.0026275 | -0.0022794 | -0.001303 | -0.0059205 | 0.0014034 | -1.3944 | 0.058616 | -0.0039136 | 0.010408 | 0.00019229 | 4.6555 | 121.257 | -0.13275 | 121.376 | -0.068665 | -0.18768 | -0.2243 | 2.2842 | 121.1884 | -0.17395 | 121.0785 | -0.16937 | -0.21057 | -0.11902 | 0.13733 | -0.14648 | -0.027465 | 0.20142 | 0.045777 | 0.082398 | -0.091553 | -0.054932 | 0.096131 | -0.21515 | -0.32501 | 0.10071 | 0.15106 | 0.05951 | 0.054931 | -0.036621 | 0.064086 | 121.5088 | 0.004577 | 121.2524 | 121.3898 | 121.3623 | 121.5271 | 121.4584 | -121.5363 | -121.5775 | 121.6461 | 121.3486 | 4.9255 | 2.5543
1266.9844 | 121.7377 | -0.23804 | 121.3898 | -0.0057221 | 0 | 0.061972 | 0.065851 | 0.0011321 | -0.0027066 | -0.001303 | -0.0028687 | 0.0024716 | -1.394 | 0.057975 | -0.00070919 | 0.011903 | -0.0025849 | 4.5731 | 121.2524 | -0.14648 | 121.3669 | -0.059509 | -0.19684 | -0.21515 | 2.2797 | 121.1609 | -0.16479 | 121.1655 | -0.10071 | -0.12817 | -0.050354 | 0.091553 | -0.13733 | -0.022889 | 0.17853 | 0.022888 | 0.041199 | -0.068665 | -0.050354 | 0.073242 | -0.22888 | -0.22431 | 0.13733 | 0.18768 | 0.10986 | 0.11444 | 0.036621 | 0.086975 | 121.5134 | 0.064087 | 121.3303 | 121.3989 | 121.3257 | 121.4905 | 121.3989 | -121.5363 | -121.5546 | 121.6049 | 121.4035 | 4.8111 | 2.5177
1268.6875 | 121.7514 | -0.24719 | 121.3486 | -0.013352 | 0 | 0.06304 | 0.061579 | -0.0057037 | -0.0031338 | 0.00040597 | -0.0028687 | 0.00033544 | -1.3976 | 0.063957 | -0.0056226 | 0.0099805 | 0.0023285 | 4.6692 | 121.2296 | -0.09613 | 121.463 | 0.041199 | -0.064087 | -0.11902 | 2.3712 | 121.1517 | -0.16479 | 121.1746 | -0.045776 | -0.073242 | -0.050354 | 0.15106 | -0.11902 | 0.11444 | 0.28839 | 0.12817 | 0.1831 | -0.022889 | 0.032043 | 0.082397 | -0.19684 | -0.17395 | 0.20142 | 0.19684 | 0.17395 | 0.11444 | 0.091553 | 0.13733 | 121.5591 | 0.11902 | 121.3394 | 121.3257 | 121.3165 | 121.4767 | 121.3989 | -121.4447 | -121.5134 | 121.7102 | 121.4218 | 4.9164 | 2.6184
1270.4688 | 121.7285 | -0.22888 | 121.3577 | 0.062942 | 0 | 0.064749 | 0.06457 | 0.0049773 | -0.00014304 | -0.00066223 | 0.018494 | -0.00051916 | -1.3925 | 0.068229 | -0.0013502 | 0.0099805 | -0.00044851 | 4.6738 | 121.2296 | -0.12817 | 121.4813 | 0.068665 | -0.07782 | -0.11902 | 2.3666 | 121.1655 | -0.19684 | 121.1838 | -0.054932 | -0.11444 | -0.045776 | 0.10071 | -0.12817 | 0.1236 | 0.29755 | 0.10986 | 0.15106 | 0.009155 | 0.050354 | 0.032044 | -0.19226 | -0.17395 | 0.17395 | 0.18311 | 0.11444 | 0.15106 | 0.082397 | 0.19684 | 121.6095 | 0.14191 | 121.3806 | 121.3577 | 121.3623 | 121.4584 | 121.3943 | -121.4859 | -121.5546 | 121.7102 | 121.4127 | 4.9026 | 2.5955
1272.1719 | 121.7239 | -0.23804 | 121.376 | -0.0057221 | 0 | 0.064963 | 0.063502 | 0.0017731 | -0.0044156 | -0.001303 | -0.0028687 | 0.0028988 | -1.3933 | 0.063102 | -0.0028454 | 0.0091261 | -0.0015167 | 4.6051 | 121.2708 | -0.14191 | 121.3715 | -0.082397 | -0.20142 | -0.20599 | 2.2842 | 121.1563 | -0.17853 | 121.1609 | -0.11444 | -0.14191 | -0.059509 | 0.09613 | -0.10529 | -0.004578 | 0.15564 | 0.032043 | 0.036621 | -0.064087 | -0.059509 | 0.059509 | -0.21973 | -0.21515 | 0.1236 | 0.17853 | 0.09613 | 0.11902 | 0.036621 | 0.05951 | 121.5134 | 0.064087 | 121.3394 | 121.4127 | 121.3348 | 121.5088 | 121.3943 | -121.5179 | -121.5546 | 121.6095 | 121.3989 | 4.8431 | 2.5223
1273.9375 | 121.6553 | -0.27466 | 121.3989 | 0.047683 | 0 | 0.063895 | 0.064356 | -0.0014313 | -0.00035684 | 0.0025422 | 0.01239 | 0.0043942 | -1.3933 | 0.065025 | -0.0045544 | 0.0089123 | 0.0019013 | 4.6738 | 121.3303 | -0.16937 | 121.3394 | -0.10071 | -0.15564 | -0.21057 | 2.2522 | 121.2296 | -0.2243 | 121.0739 | -0.16479 | -0.21515 | -0.14191 | 0.10529 | -0.068665 | -0.059509 | 0.17395 | 0.064087 | 0.11902 | -0.041198 | 0.013733 | 0.050354 | -0.16937 | -0.32501 | 0.10986 | 0.13275 | 0.059509 | 0.082397 | 0.009155 | 0.068665 | 121.5088 | 0.059509 | 121.2982 | 121.4996 | 121.4539 | 121.6049 | 121.5042 | -121.5683 | -121.6232 | 121.6141 | 121.3486 | 4.9484 | 2.5269
1275.7031 | 121.6873 | -0.2243 | 121.344 | 0.017166 | 0 | 0.066458 | 0.063074 | -0.0010041 | -0.00099764 | 0.0019012 | 0.0093383 | 0.0014034 | -1.3948 | 0.065666 | -0.0028454 | 0.012117 | -0.0019439 | 4.6051 | 121.2479 | -0.13275 | 121.4035 | -0.045776 | -0.1236 | -0.16937 | 2.2751 | 121.1334 | -0.1831 | 121.1197 | -0.10529 | -0.15106 | -0.10071 | 0.091553 | -0.09613 | 0.059509 | 0.17853 | 0.054931 | 0.10071 | -0.036622 | 0.009155 | 0.041199 | -0.21057 | -0.2243 | 0.11902 | 0.1236 | 0.073242 | 0.082397 | 0.032043 | 0.086975 | 121.5363 | 0.077819 | 121.3028 | 121.3806 | 121.3165 | 121.4722 | 121.3577 | -121.4767 | -121.5271 | 121.6278 | 121.344 | 4.8294 | 2.4994
1277.4062 | 121.7194 | -0.21057 | 121.3577 | 0.062942 | 0 | 0.065604 | 0.067133 | -0.00036309 | -0.00014304 | -2.1434e-05 | 0.018494 | 0.003326 | -1.3952 | 0.06652 | -6.8386e-05 | 0.0082715 | -0.00066231 | 4.6829 | 121.2708 | -0.12817 | 121.4859 | 0.064087 | -0.07782 | -0.10986 | 2.4033 | 121.1929 | -0.19226 | 121.1792 | -0.059509 | -0.10986 | -0.050354 | 0.082397 | -0.086975 | 0.12817 | 0.27466 | 0.10071 | 0.13275 | 0.018311 | 0.050354 | 0.01831 | -0.16479 | -0.17853 | 0.15106 | 0.16022 | 0.10071 | 0.14191 | 0.082398 | 0.19226 | 121.6141 | 0.13275 | 121.3715 | 121.3989 | 121.3852 | 121.4813 | 121.4035 | -121.4859 | -121.55 | 121.6965 | 121.3898 | 4.8935 | 2.6138
1279.1719 | 121.6049 | -0.27008 | 121.3989 | -0.0057221 | 0 | 0.064749 | 0.064783 | -0.00036309 | -0.0031338 | -0.00066223 | 0.00018312 | 0.0014034 | -1.3957 | 0.063102 | -0.0037 | 0.0099805 | 0.0038239 | 4.5959 | 121.2891 | -0.14648 | 121.312 | -0.15564 | -0.25635 | -0.28381 | 2.211 | 121.1975 | -0.19226 | 121.0648 | -0.20599 | -0.25177 | -0.14648 | 0.1236 | -0.10986 | -0.086975 | 0.11444 | -0.013732 | 0.013733 | -0.13733 | -0.10986 | 0.07782 | -0.20142 | -0.33417 | 0.064087 | 0.1236 | 0.018311 | 0.045777 | -0.059509 | -0.009156 | 121.4584 | -0.013733 | 121.257 | 121.4355 | 121.3898 | 121.5591 | 121.4676 | -121.5454 | -121.5912 | 121.582 | 121.3348 | 4.866 | 2.4811
1280.875 | 121.6644 | -0.27466 | 121.3715 | -0.0057221 | 0 | 0.063467 | 0.066279 | -0.00079049 | -0.003561 | -0.0034392 | 0.00018312 | 0.0031124 | -1.3972 | 0.062888 | -0.0015638 | 0.010408 | -0.0013031 | 4.6051 | 121.2845 | -0.13733 | 121.3303 | -0.10986 | -0.24261 | -0.23804 | 2.2156 | 121.1929 | -0.19226 | 121.1014 | -0.16479 | -0.22888 | -0.10986 | 0.13733 | -0.086975 | -0.041199 | 0.1648 | 0.036621 | 0.032043 | -0.10071 | -0.10529 | 0.082397 | -0.17853 | -0.27008 | 0.10986 | 0.1648 | 0.045776 | 0.082398 | -0.036621 | 0.027466 | 121.4676 | 0.027466 | 121.2936 | 121.4218 | 121.3852 | 121.5591 | 121.4676 | -121.5088 | -121.5637 | 121.6049 | 121.376 | 4.8798 | 2.4902
1282.6406 | 121.7514 | -0.21973 | 121.3669 | 0.0019074 | 0 | 0.062827 | 0.061793 | 0.0030547 | -0.0044156 | -0.00087583 | -0.0059205 | 0.00097624 | -1.3965 | 0.063529 | -0.0043408 | 0.010194 | 0.0012603 | 4.6234 | 121.2433 | -0.11444 | 121.4081 | -0.018311 | -0.10071 | -0.14191 | 2.3254 | 121.1655 | -0.17853 | 121.17 | -0.054932 | -0.086975 | -0.036621 | 0.10529 | -0.1236 | 0.041199 | 0.20142 | 0.07782 | 0.11902 | -0.027466 | 0.013733 | 0.041199 | -0.20142 | -0.19684 | 0.16479 | 0.18311 | 0.13275 | 0.14191 | 0.091553 | 0.09613 | 121.5225 | 0.1236 | 121.3486 | 121.3577 | 121.344 | 121.463 | 121.3852 | -121.4813 | -121.5454 | 121.6278 | 121.3898 | 4.8431 | 2.5452
1284.3906 | 121.7834 | -0.24261 | 121.3715 | -0.0057221 | 0 | 0.062186 | 0.062861 | 0.0036957 | -0.004202 | -0.0025848 | -0.0028687 | -0.00073276 | -1.395 | 0.071006 | -0.0043408 | 0.0089123 | 0.0029693 | 4.6829 | 121.225 | -0.12817 | 121.4676 | 0.059509 | -0.045776 | -0.091553 | 2.4261 | 121.1472 | -0.15564 | 121.1929 | -0.027466 | -0.064087 | -0.036621 | 0.11444 | -0.14648 | 0.09613 | 0.30212 | 0.15106 | 0.19684 | 0.036621 | 0.082398 | 0.086975 | -0.2243 | -0.17853 | 0.21515 | 0.20599 | 0.17853 | 0.11902 | 0.091553 | 0.18768 | 121.5958 | 0.12817 | 121.3486 | 121.3531 | 121.3028 | 121.4676 | 121.3898 | -121.4996 | -121.5271 | 121.7102 | 121.4355 | 4.9255 | 2.6688
1286.0938 | 121.6232 | -0.25635 | 121.4218 | 0.0019074 | 0 | 0.063254 | 0.06692 | 0.0039093 | -0.0039884 | -0.00066223 | 0.00018312 | 0.0026852 | -1.3963 | 0.064597 | -0.003059 | 0.0074171 | 0.0033967 | 4.6692 | 121.2387 | -0.1236 | 121.3348 | -0.1236 | -0.2243 | -0.27466 | 2.211 | 121.1929 | -0.19226 | 121.0602 | -0.21515 | -0.2655 | -0.15106 | 0.13275 | -0.18311 | -0.086975 | 0.13275 | -0.01831 | 0.032044 | -0.15106 | -0.10071 | 0.064087 | -0.22888 | -0.36163 | 0.041199 | 0.10529 | -0.009155 | 0.041199 | -0.073242 | 0 | 121.4584 | -0.022888 | 121.2524 | 121.3623 | 121.3852 | 121.4951 | 121.4493 | -121.5454 | -121.6141 | 121.5912 | 121.3165 | 4.9255 | 2.4673
1287.8594 | 121.7422 | -0.21057 | 121.376 | 0.0019074 | 0 | 0.065604 | 0.061152 | -0.0018585 | -0.003561 | -0.0021576 | 0.00018312 | 0.0018306 | -1.3959 | 0.070365 | -0.004768 | 0.011262 | -0.0019439 | 4.7516 | 121.2158 | -0.10986 | 121.4539 | 0.041199 | -0.073242 | -0.11444 | 2.3804 | 121.1334 | -0.15564 | 121.1655 | -0.041199 | -0.091553 | -0.041199 | 0.10071 | -0.16022 | 0.077819 | 0.25177 | 0.09613 | 0.13733 | -0.004578 | 0.036621 | 0.054931 | -0.24262 | -0.21057 | 0.16937 | 0.16937 | 0.11902 | 0.11444 | 0.064087 | 0.15106 | 121.5637 | 0.11444 | 121.3211 | 121.3257 | 121.2891 | 121.4264 | 121.344 | -121.4859 | -121.5317 | 121.6644 | 121.376 | 4.9622 | 2.5909
1289.6094 | 121.6324 | -0.27008 | 121.4127 | -0.013352 | 0 | 0.063254 | 0.061365 | 0.0028411 | -0.0027066 | -0.00023503 | -0.0028687 | 0.001617 | -1.3948 | 0.060539 | -0.0079724 | 0.0080579 | -0.0010895 | 4.7241 | 121.2296 | -0.10529 | 121.3852 | -0.036621 | -0.12817 | -0.17853 | 2.3071 | 121.1838 | -0.1831 | 121.0785 | -0.14191 | -0.20142 | -0.14191 | 0.1648 | -0.18311 | -0.027466 | 0.23346 | 0.091553 | 0.14191 | -0.073242 | -0.022888 | 0.086976 | -0.22888 | -0.33417 | 0.12817 | 0.12817 | 0.068665 | 0.041198 | -0.018311 | 0.068665 | 121.4905 | 0.041198 | 121.2616 | 121.3348 | 121.3669 | 121.4996 | 121.4539 | -121.5179 | -121.5958 | 121.6553 | 121.3486 | 4.9942 | 2.5772
1291.3125 | 121.7377 | -0.23804 | 121.3852 | 0.040054 | 0 | 0.065604 | 0.064783 | 0.00049131 | -0.00057044 | 0.001474 | 0.01239 | 0.0043942 | -1.3933 | 0.069724 | -0.00092279 | 0.0093397 | -0.0030121 | 4.7516 | 121.2433 | -0.1236 | 121.4951 | 0.059509 | -0.082397 | -0.11902 | 2.3804 | 121.17 | -0.17395 | 121.1792 | -0.073242 | -0.10986 | -0.041199 | 0.11444 | -0.14191 | 0.10986 | 0.29755 | 0.11902 | 0.15564 | 0.004577 | 0.041199 | 0.064087 | -0.21515 | -0.20599 | 0.16479 | 0.19684 | 0.12817 | 0.13275 | 0.064087 | 0.1831 | 121.6187 | 0.10071 | 121.3531 | 121.3669 | 121.344 | 121.4813 | 121.4081 | -121.5088 | -121.5591 | 121.7331 | 121.4172 | 4.9896 | 2.6184
1293.0781 | 121.6644 | -0.25635 | 121.4127 | 0.032425 | 0 | 0.065176 | 0.066706 | 0.0034821 | -0.0022794 | 0.0010468 | 0.0062865 | 0.0041806 | -1.395 | 0.060111 | -0.005409 | 0.0086987 | 0.0014741 | 4.7882 | 121.3257 | -0.17395 | 121.3898 | -0.07782 | -0.13733 | -0.18768 | 2.298 | 121.2341 | -0.20599 | 121.0968 | -0.14191 | -0.19226 | -0.09613 | 0.082398 | -0.086975 | -0.022888 | 0.17853 | 0.068665 | 0.11902 | -0.013733 | 0.036621 | 0.050354 | -0.17853 | -0.31586 | 0.11444 | 0.16022 | 0.064087 | 0.10986 | 0.013733 | 0.09613 | 121.5637 | 0.064087 | 121.3028 | 121.4996 | 121.4401 | 121.582 | 121.4905 | -121.5866 | -121.6187 | 121.6461 | 121.3531 | 5.0446 | 2.5543
1294.8281 | 121.6644 | -0.2655 | 121.4035 | 0.017166 | 0 | 0.063681 | 0.063502 | -0.00079049 | -0.0022794 | 0.00061957 | 0.0032349 | 0.0043942 | -1.394 | 0.057762 | -0.0041272 | 0.0089123 | 0.00061949 | 4.8111 | 121.2433 | -0.13733 | 121.3989 | -0.022888 | -0.14191 | -0.18768 | 2.3254 | 121.1975 | -0.19684 | 121.138 | -0.10529 | -0.17395 | -0.09613 | 0.12817 | -0.16022 | -0.004577 | 0.24261 | 0.07782 | 0.1236 | -0.050354 | -0.004578 | 0.068665 | -0.20599 | -0.2655 | 0.16022 | 0.16937 | 0.091553 | 0.10071 | 0.022888 | 0.11444 | 121.5363 | 0.091552 | 121.3348 | 121.3806 | 121.3943 | 121.5088 | 121.463 | -121.5408 | -121.6003 | 121.6644 | 121.4035 | 5.0766 | 2.5909
1296.5938 | 121.6919 | -0.23346 | 121.3989 | 0.0095369 | 0 | 0.062827 | 0.064783 | 0.0011321 | -0.0029202 | -0.00044863 | 0.0032349 | 0.00012184 | -1.3942 | 0.060966 | -0.0017774 | 0.0091261 | -0.0045075 | 4.747 | 121.2204 | -0.11444 | 121.3852 | -0.027466 | -0.12817 | -0.16479 | 2.2568 | 121.17 | -0.17853 | 121.1243 | -0.10071 | -0.14648 | -0.073242 | 0.11902 | -0.17853 | -0.013733 | 0.20599 | 0.068664 | 0.10528 | -0.050354 | -0.013733 | 0.054931 | -0.22888 | -0.27466 | 0.13275 | 0.16022 | 0.086975 | 0.10529 | 0.032044 | 0.086975 | 121.4996 | 0.07782 | 121.3028 | 121.3348 | 121.3486 | 121.4539 | 121.4035 | -121.5134 | -121.5775 | 121.6187 | 121.3577 | 4.9805 | 2.4902
1298.375 | 121.6278 | -0.2655 | 121.3943 | 0.0019074 | 0 | 0.06539 | 0.06457 | 0.0022003 | -0.0020658 | 0.00061957 | -0.0059205 | 0.003967 | -1.3944 | 0.059684 | -0.0032728 | 0.0080579 | -0.00044851 | 4.8157 | 121.2799 | -0.13733 | 121.3669 | -0.086975 | -0.20599 | -0.22888 | 2.298 | 121.17 | -0.17395 | 121.0785 | -0.17395 | -0.22888 | -0.14191 | 0.12817 | -0.11444 | -0.027466 | 0.17853 | 0.036621 | 0.059509 | -0.091553 | -0.068665 | 0.091553 | -0.2243 | -0.31586 | 0.091553 | 0.1236 | 0.036621 | 0.032043 | -0.054932 | 0.050354 | 121.5042 | 0 | 121.2524 | 121.4172 | 121.344 | 121.5454 | 121.4355 | -121.5317 | -121.5683 | 121.6324 | 121.344 | 5.0812 | 2.5635
1300.0781 | 121.7377 | -0.23804 | 121.3806 | -0.0057221 | 0 | 0.063681 | 0.064142 | 0.00070491 | -0.002493 | -0.001303 | 0.00018312 | 0.0035396 | -1.3946 | 0.071647 | -0.0024182 | 0.010408 | 0.00040589 | 4.7699 | 121.2799 | -0.12817 | 121.376 | -0.041199 | -0.17853 | -0.20142 | 2.3117 | 121.1609 | -0.17853 | 121.1609 | -0.091553 | -0.1236 | -0.045776 | 0.10986 | -0.10071 | -0.004577 | 0.19684 | 0.036621 | 0.059509 | -0.073242 | -0.050354 | 0.059509 | -0.21973 | -0.21973 | 0.14648 | 0.19226 | 0.11444 | 0.13275 | 0.054932 | 0.086975 | 121.5042 | 0.086975 | 121.3394 | 121.4081 | 121.3394 | 121.5179 | 121.3989 | -121.5088 | -121.5591 | 121.6141 | 121.3989 | 5.0079 | 2.5497
1301.8438 | 121.637 | -0.27008 | 121.3989 | 0.0095369 | 0 | 0.066031 | 0.063929 | 0.0022003 | 7.0564e-05 | -0.00044863 | 0.0032349 | 0.0026852 | -1.3957 | 0.063102 | -0.0060498 | 0.0091261 | 0.00083309 | 4.8294 | 121.2891 | -0.12817 | 121.3806 | -0.054932 | -0.15106 | -0.18768 | 2.2797 | 121.1975 | -0.17395 | 121.106 | -0.14648 | -0.21057 | -0.1236 | 0.14191 | -0.10986 | -0.018311 | 0.21515 | 0.082398 | 0.11902 | -0.059509 | -0.022888 | 0.096131 | -0.20142 | -0.29297 | 0.1236 | 0.14649 | 0.05951 | 0.050354 | -0.036621 | 0.073242 | 121.5088 | 0.027466 | 121.2799 | 121.4172 | 121.3715 | 121.5591 | 121.4676 | -121.5271 | -121.5729 | 121.6507 | 121.376 | 5.0995 | 2.5497
1303.6094 | 121.6232 | -0.25635 | 121.4172 | 0.0019074 | 0 | 0.063254 | 0.063929 | -0.0037811 | -0.004202 | -0.0025848 | -0.0028687 | 0.0024716 | -1.3933 | 0.062461 | -0.0062634 | 0.010194 | -0.00044851 | 4.7928 | 121.2753 | -0.13733 | 121.3303 | -0.09613 | -0.1831 | -0.23346 | 2.2751 | 121.2433 | -0.23346 | 121.0648 | -0.17853 | -0.21515 | -0.13733 | 0.11902 | -0.14191 | -0.086975 | 0.16022 | 0.022889 | 0.073243 | -0.09613 | -0.045776 | 0.022889 | -0.17395 | -0.35248 | 0.07782 | 0.11902 | 0.041199 | 0.09613 | 0.01831 | 0.041199 | 121.4676 | 0.054931 | 121.2982 | 121.4127 | 121.4767 | 121.5317 | 121.4996 | -121.5546 | -121.6507 | 121.5866 | 121.3211 | 5.0491 | 2.5314
1305.3125 | 121.7834 | -0.23346 | 121.3669 | -0.0057221 | 0 | 0.061331 | 0.063502 | -0.00079049 | -0.0037746 | -0.0021576 | -0.0028687 | 0.0014034 | -1.3955 | 0.063743 | -0.0034864 | 0.010408 | 0.0012603 | 4.8203 | 121.1929 | -0.10071 | 121.4493 | 0.064087 | -0.050354 | -0.10071 | 2.4216 | 121.17 | -0.14648 | 121.2112 | -0.027466 | -0.032043 | -0.018311 | 0.13275 | -0.17395 | 0.082398 | 0.29755 | 0.13275 | 0.1831 | 0 | 0.050354 | 0.086975 | -0.19684 | -0.15564 | 0.20599 | 0.21515 | 0.20142 | 0.12817 | 0.11444 | 0.1648 | 121.55 | 0.11902 | 121.3577 | 121.2936 | 121.3165 | 121.4264 | 121.4035 | -121.4676 | -121.5134 | 121.6827 | 121.4447 | 5.0537 | 2.655
1307.0781 | 121.7377 | -0.21515 | 121.3806 | 0.0019074 | 0 | 0.065604 | 0.064356 | -0.0014313 | -0.0016384 | 0.0012604 | 0.0032349 | 0.00097624 | -1.3948 | 0.062675 | -0.0015638 | 0.010835 | -2.1314e-05 | 4.8111 | 121.257 | -0.10071 | 121.4035 | -0.009155 | -0.12817 | -0.16937 | 2.3529 | 121.1792 | -0.14191 | 121.2021 | -0.068665 | -0.11444 | -0.022888 | 0.11444 | -0.1236 | 0.022888 | 0.20599 | 0.045776 | 0.086975 | -0.068665 | -0.027466 | 0.073242 | -0.20142 | -0.17853 | 0.14648 | 0.19226 | 0.10071 | 0.11902 | 0.027466 | 0.091553 | 121.5042 | 0.073242 | 121.344 | 121.3577 | 121.3211 | 121.4722 | 121.3943 | -121.4813 | -121.5225 | 121.6187 | 121.4172 | 5.0262 | 2.5681
1308.8438 | 121.756 | -0.22888 | 121.3669 | 0.017166 | 0 | 0.062399 | 0.061579 | -0.00057689 | -0.0016384 | -0.0034392 | -0.0028687 | 0.00076264 | -1.395 | 0.063529 | -0.0039136 | 0.0086987 | -0.0042939 | 4.8706 | 121.2662 | -0.091553 | 121.4447 | 0.059509 | -0.059509 | -0.10986 | 2.4261 | 121.1563 | -0.16937 | 121.1975 | -0.022888 | -0.054932 | -0.027466 | 0.13733 | -0.10071 | 0.07782 | 0.28839 | 0.11902 | 0.16937 | -0.01831 | 0.032044 | 0.059509 | -0.21057 | -0.16937 | 0.20599 | 0.20142 | 0.17395 | 0.14191 | 0.11444 | 0.15106 | 121.5363 | 0.14649 | 121.3669 | 121.3577 | 121.3257 | 121.4951 | 121.3852 | -121.4584 | -121.5363 | 121.6736 | 121.4264 | 5.0995 | 2.655
1310.6094 | 121.6232 | -0.25177 | 121.4218 | -0.0057221 | 0 | 0.064749 | 0.065424 | 0.0064727 | -0.0027066 | 0.00083317 | -0.0028687 | 0.0037532 | -1.3955 | 0.05883 | -0.0028454 | 0.0095533 | -0.0042939 | 4.8157 | 121.2936 | -0.13275 | 121.2982 | -0.13275 | -0.22888 | -0.25635 | 2.2293 | 121.2067 | -0.18768 | 121.0739 | -0.20599 | -0.25635 | -0.1236 | 0.11902 | -0.12817 | -0.1236 | 0.11902 | -0.004578 | 0.022888 | -0.1236 | -0.096131 | 0.064087 | -0.21515 | -0.3479 | 0.045776 | 0.12817 | -0.004578 | 0.064087 | -0.068665 | 0 | 121.431 | -0.018311 | 121.2616 | 121.4264 | 121.3943 | 121.5454 | 121.4584 | -121.5546 | -121.6095 | 121.55 | 121.3257 | 5.0674 | 2.4811
1312.375 | 121.6324 | -0.2655 | 121.4127 | 0.0019074 | 0 | 0.06304 | 0.066065 | -0.0033539 | -0.0014248 | -0.0023712 | 0.00018312 | 0.0026852 | -1.3942 | 0.06182 | -0.004768 | 0.0091261 | 0.0019013 | 4.8111 | 121.2982 | -0.13275 | 121.3211 | -0.11902 | -0.24261 | -0.2655 | 2.2659 | 121.225 | -0.19226 | 121.0831 | -0.17853 | -0.23804 | -0.13275 | 0.13275 | -0.11444 | -0.091553 | 0.14648 | 0 | 0.022888 | -0.13275 | -0.10986 | 0.073242 | -0.18768 | -0.32959 | 0.086975 | 0.13275 | 0.027466 | 0.05951 | -0.045776 | 0.013732 | 121.4539 | 0.013733 | 121.2753 | 121.431 | 121.4172 | 121.5637 | 121.4905 | -121.5454 | -121.6049 | 121.5866 | 121.3486 | 5.0766 | 2.5314
1314.1406 | 121.669 | -0.25177 | 121.3989 | 0.024795 | 0 | 0.06304 | 0.062647 | 0.0026275 | 0.00028416 | -0.00066223 | 0.0062865 | 0.003326 | -1.3946 | 0.063529 | -0.0039136 | 0.0084851 | -0.0047211 | 4.9164 | 121.2891 | -0.15564 | 121.3989 | -0.018311 | -0.13275 | -0.17395 | 2.3666 | 121.2158 | -0.19684 | 121.1197 | -0.12817 | -0.15564 | -0.082397 | 0.09613 | -0.10986 | 0 | 0.23346 | 0.07782 | 0.11902 | -0.01831 | 0.022889 | 0.054932 | -0.18311 | -0.27924 | 0.1236 | 0.16937 | 0.09613 | 0.11444 | 0.041198 | 0.13733 | 121.5546 | 0.068664 | 121.3165 | 121.4447 | 121.4127 | 121.5408 | 121.4676 | -121.5546 | -121.5958 | 121.6507 | 121.3715 | 5.1682 | 2.6184
1315.8438 | 121.6507 | -0.26093 | 121.4355 | -0.013352 | 0 | 0.063895 | 0.062647 | -0.0035675 | -0.0033474 | -0.003653 | -0.0059205 | 0.00076264 | -1.3933 | 0.066306 | -0.0069044 | 0.0084851 | -0.0013031 | 4.9164 | 121.257 | -0.09613 | 121.4218 | -0.009155 | -0.082397 | -0.16937 | 2.3712 | 121.1838 | -0.17395 | 121.0922 | -0.12817 | -0.16022 | -0.11902 | 0.1648 | -0.17853 | -0.013733 | 0.25177 | 0.091552 | 0.17853 | -0.073243 | 0.013733 | 0.086975 | -0.25177 | -0.34332 | 0.13275 | 0.14191 | 0.10071 | 0.054931 | 0.013733 | 0.086975 | 121.5179 | 0.045776 | 121.2662 | 121.3531 | 121.3577 | 121.5179 | 121.4447 | -121.5317 | -121.6095 | 121.6827 | 121.3531 | 5.1773 | 2.6321
1317.6094 | 121.6415 | -0.25177 | 121.431 | 0.0095369 | 0 | 0.062613 | 0.065424 | -0.0016449 | -0.0029202 | -0.0010894 | -0.0028687 | 0.0018306 | -1.3948 | 0.059684 | -0.0015638 | 0.010408 | -2.1314e-05 | 4.8706 | 121.2845 | -0.14648 | 121.3165 | -0.11444 | -0.22888 | -0.24719 | 2.2751 | 121.2158 | -0.1831 | 121.0785 | -0.17395 | -0.2243 | -0.12817 | 0.10529 | -0.14648 | -0.11444 | 0.13733 | 0.004578 | 0.022888 | -0.10071 | -0.082398 | 0.068665 | -0.21515 | -0.35248 | 0.07782 | 0.1236 | 0.027466 | 0.054931 | -0.041199 | 0.032043 | 121.463 | 0.009155 | 121.2616 | 121.431 | 121.3989 | 121.5363 | 121.4676 | -121.5775 | -121.6141 | 121.5683 | 121.3303 | 5.1224 | 2.5269
1319.375 | 121.6324 | -0.26093 | 121.4355 | -0.013352 | 0 | 0.061972 | 0.06457 | -0.00036309 | -0.0014248 | -0.00066223 | 0.018494 | 0.0035396 | -1.3933 | 0.060966 | -0.0045544 | 0.0082715 | -0.0051483 | 4.9164 | 121.2982 | -0.19684 | 121.3577 | -0.064087 | -0.15106 | -0.20599 | 2.33 | 121.2524 | -0.2243 | 121.0602 | -0.17853 | -0.20142 | -0.13733 | 0.064087 | -0.13733 | -0.07782 | 0.19684 | 0.054931 | 0.10986 | -0.009156 | 0.045776 | 0.036621 | -0.18311 | -0.37537 | 0.082397 | 0.1236 | 0.059509 | 0.086975 | 0.022888 | 0.13275 | 121.5546 | 0.045776 | 121.2845 | 121.4951 | 121.4767 | 121.5591 | 121.5134 | -121.6324 | -121.6599 | 121.6187 | 121.3211 | 5.1773 | 2.5909
1321.0781 | 121.7377 | -0.22888 | 121.4035 | -0.0057221 | 0 | 0.062399 | 0.059656 | -0.0031403 | -0.0022794 | 0.00040597 | -0.0089723 | 0.0028988 | -1.3944 | 0.063743 | -0.0058362 | 0.0078443 | -0.0019439 | 4.9713 | 121.1929 | -0.091553 | 121.463 | 0.064087 | -0.054932 | -0.11444 | 2.4033 | 121.1609 | -0.14648 | 121.1838 | -0.041199 | -0.064087 | -0.041199 | 0.13733 | -0.21057 | 0.05951 | 0.29297 | 0.11444 | 0.17395 | -0.022888 | 0.036621 | 0.082398 | -0.24261 | -0.21973 | 0.18768 | 0.18768 | 0.16479 | 0.10529 | 0.082397 | 0.15564 | 121.5546 | 0.10529 | 121.3303 | 121.2845 | 121.3074 | 121.4218 | 121.3898 | -121.4951 | -121.55 | 121.6919 | 121.4127 | 5.2002 | 2.6321
1322.8438 | 121.7102 | -0.23804 | 121.3989 | -0.0057221 | 0 | 0.064749 | 0.061579 | 0.0017731 | -0.0048428 | -0.0023712 | -0.0028687 | -0.00094636 | -1.3948 | 0.058189 | -0.004768 | 0.010835 | -0.00023491 | 4.9759 | 121.2112 | -0.091553 | 121.4584 | 0.041199 | -0.059509 | -0.12817 | 2.4124 | 121.1334 | -0.15106 | 121.1563 | -0.050354 | -0.09613 | -0.054932 | 0.14648 | -0.18768 | 0.059509 | 0.27924 | 0.10986 | 0.17853 | -0.036621 | 0.032044 | 0.086975 | -0.2655 | -0.24262 | 0.18768 | 0.1831 | 0.14191 | 0.09613 | 0.054932 | 0.13275 | 121.55 | 0.10071 | 121.3074 | 121.3028 | 121.2845 | 121.4493 | 121.3715 | -121.4905 | -121.55 | 121.6965 | 121.3943 | 5.2139 | 2.6505
1324.6094 | 121.6187 | -0.25635 | 121.4035 | -0.0057221 | 0 | 0.064963 | 0.065424 | 0.0015595 | -0.00078404 | -0.00023503 | -0.0028687 | 0.003967 | -1.3967 | 0.064384 | 0.00014521 | 0.011049 | -0.0027985 | 4.921 | 121.2845 | -0.13275 | 121.312 | -0.15106 | -0.23804 | -0.27466 | 2.2659 | 121.2067 | -0.17853 | 121.0876 | -0.20599 | -0.24261 | -0.12817 | 0.1236 | -0.11902 | -0.091552 | 0.10529 | -0.01831 | 0.018311 | -0.14191 | -0.10529 | 0.07782 | -0.19684 | -0.31586 | 0.050354 | 0.12817 | 0.013733 | 0.050354 | -0.064087 | -0.018311 | 121.4447 | -0.027466 | 121.2662 | 121.4172 | 121.3852 | 121.5408 | 121.463 | -121.5363 | -121.582 | 121.5683 | 121.344 | 5.1773 | 2.5223
1326.3125 | 121.6095 | -0.2655 | 121.4127 | -0.0057221 | 0 | 0.066031 | 0.066279 | -0.0035675 | -0.0020658 | 0.00040597 | -0.0028687 | 0.001617 | -1.394 | 0.057762 | -0.003059 | 0.0095533 | 0.0046783 | 4.9255 | 121.3257 | -0.13275 | 121.3257 | -0.13733 | -0.23804 | -0.27924 | 2.2568 | 121.2158 | -0.17853 | 121.0648 | -0.1831 | -0.23804 | -0.12817 | 0.13275 | -0.086975 | -0.086975 | 0.12817 | -0.013733 | 0.027466 | -0.14648 | -0.10529 | 0.086975 | -0.19684 | -0.3479 | 0.082398 | 0.13733 | 0.027466 | 0.050354 | -0.059509 | -0.004578 | 121.4584 | -0.004577 | 121.2433 | 121.4584 | 121.3943 | 121.5912 | 121.4813 | -121.5454 | -121.5912 | 121.5912 | 121.3303 | 5.191 | 2.5223
1328.0625 | 121.7056 | -0.23346 | 121.3852 | 0.047683 | 0 | 0.065176 | 0.06457 | -0.0052765 | -0.00078404 | 0.0027558 | 0.0032349 | 0.0018306 | -1.3901 | 0.073783 | -0.0032728 | 0.011476 | -0.0045075 | 4.9622 | 121.2891 | -0.11902 | 121.4172 | 0.032043 | -0.10071 | -0.13275 | 2.3621 | 121.17 | -0.17853 | 121.1334 | -0.10529 | -0.14191 | -0.068665 | 0.11444 | -0.096131 | 0.032043 | 0.2655 | 0.10071 | 0.13275 | -0.013732 | 0.018311 | 0.054931 | -0.21515 | -0.25177 | 0.12817 | 0.16479 | 0.091552 | 0.10986 | 0.036621 | 0.15106 | 121.5363 | 0.073242 | 121.312 | 121.4081 | 121.3486 | 121.5225 | 121.4035 | -121.5042 | -121.5637 | 121.6507 | 121.3669 | 5.1956 | 2.5955
1329.7656 | 121.6141 | -0.27924 | 121.4447 | 0.0019074 | 0 | 0.064322 | 0.067133 | -0.0035675 | -0.0029202 | -0.00023503 | 0.00018312 | 0.0041806 | -1.3948 | 0.057121 | -0.0017774 | 0.011049 | 0.0014741 | 4.9164 | 121.2982 | -0.14191 | 121.3211 | -0.13275 | -0.22888 | -0.24261 | 2.2247 | 121.2158 | -0.19226 | 121.0831 | -0.18768 | -0.23346 | -0.10529 | 0.13733 | -0.14648 | -0.1236 | 0.14648 | 0.036621 | 0.050354 | -0.10071 | -0.086975 | 0.086975 | -0.22888 | -0.36163 | 0.091553 | 0.17395 | 0.045777 | 0.086975 | -0.041198 | 0.009156 | 121.463 | 0.004578 | 121.2753 | 121.4401 | 121.4081 | 121.5775 | 121.4951 | -121.5866 | -121.637 | 121.6003 | 121.3623 | 5.1956 | 2.504
1331.5469 | 121.7514 | -0.22888 | 121.3715 | 0.0019074 | 0 | 0.064322 | 0.066706 | -0.00014949 | -0.00078404 | -0.00087583 | 0.018494 | 0.0031124 | -1.3925 | 0.06887 | -0.00028199 | 0.012544 | -0.0038665 | 5.0308 | 121.2753 | -0.10986 | 121.4813 | 0.073242 | -0.059509 | -0.10529 | 2.4261 | 121.1884 | -0.17853 | 121.2112 | -0.054932 | -0.091553 | -0.027466 | 0.11902 | -0.09613 | 0.10986 | 0.30212 | 0.1236 | 0.16937 | 0.004577 | 0.050354 | 0.050354 | -0.18311 | -0.16022 | 0.17395 | 0.20142 | 0.13733 | 0.15106 | 0.086975 | 0.18311 | 121.5912 | 0.1236 | 121.3898 | 121.3852 | 121.3669 | 121.5042 | 121.4172 | -121.4813 | -121.55 | 121.7102 | 121.4401 | 5.2597 | 2.655
1333.25 | 121.7697 | -0.20599 | 121.3806 | 0.0019074 | 0 | 0.063681 | 0.060511 | 0.0051911 | -0.0020658 | -0.001303 | -0.0028687 | 0.001617 | -1.3942 | 0.062034 | -0.0041272 | 0.011903 | 0.0010467 | 5.0354 | 121.225 | -0.10071 | 121.4905 | 0.073242 | -0.050354 | -0.10529 | 2.417 | 121.1563 | -0.15106 | 121.2021 | -0.013733 | -0.041199 | -0.032043 | 0.10529 | -0.15564 | 0.10986 | 0.27924 | 0.10071 | 0.15564 | -0.004578 | 0.050354 | 0.054932 | -0.2243 | -0.17853 | 0.19226 | 0.17395 | 0.1648 | 0.11902 | 0.10986 | 0.17395 | 121.5912 | 0.13733 | 121.3531 | 121.3257 | 121.3074 | 121.431 | 121.3623 | -121.4813 | -121.5317 | 121.6965 | 121.4081 | 5.2414 | 2.623
1335.0156 | 121.7148 | -0.24261 | 121.4035 | 0.017166 | 0 | 0.06304 | 0.061579 | -0.0029267 | 0.00028416 | -0.0010894 | 0.0032349 | 0.00054904 | -1.3967 | 0.072929 | -0.0017774 | 0.0099805 | 0.00083309 | 4.9942 | 121.2708 | -0.11902 | 121.4172 | -0.004578 | -0.11444 | -0.16022 | 2.33 | 121.1929 | -0.16022 | 121.1334 | -0.10529 | -0.14648 | -0.073242 | 0.1236 | -0.13275 | 0.013733 | 0.23804 | 0.082398 | 0.12817 | -0.041198 | 0.004578 | 0.082398 | -0.21057 | -0.27008 | 0.13733 | 0.16937 | 0.096131 | 0.086975 | 0.013733 | 0.11444 | 121.5363 | 0.054931 | 121.2936 | 121.3898 | 121.3531 | 121.5134 | 121.4355 | -121.5225 | -121.5637 | 121.6599 | 121.376 | 5.2368 | 2.5726
1336.9531 | 121.5958 | -0.27008 | 121.4355 | 0.017166 | 0 | 0.065604 | 0.065638 | -0.00014949 | -0.001852 | -0.0023712 | -0.0028687 | 0.0037532 | -1.3942 | 0.058402 | -0.0056226 | 0.010194 | -0.0051483 | 4.9942 | 121.2891 | -0.1236 | 121.3303 | -0.1236 | -0.2243 | -0.26093 | 2.2293 | 121.225 | -0.19684 | 121.0648 | -0.19684 | -0.23346 | -0.13733 | 0.14649 | -0.14648 | -0.10529 | 0.14649 | 0.009156 | 0.045777 | -0.13733 | -0.10071 | 0.073243 | -0.21057 | -0.37079 | 0.073243 | 0.13275 | 0.036622 | 0.059509 | -0.036621 | 0 | 121.4539 | 0 | 121.2616 | 121.4127 | 121.4218 | 121.5591 | 121.4951 | -121.5591 | -121.6324 | 121.6003 | 121.3348 | 5.2643 | 2.4994
1338.7188 | 121.7651 | -0.21057 | 121.3943 | -0.0057221 | 0 | 0.062186 | 0.06222 | 0.00027771 | -0.0039884 | -0.00066223 | -0.0059205 | 0.001617 | -1.3933 | 0.065025 | -0.0032728 | 0.0099805 | 0.0014741 | 5.0674 | 121.2158 | -0.10071 | 121.4951 | 0.07782 | -0.036621 | -0.11444 | 2.4307 | 121.1609 | -0.16937 | 121.2021 | -0.018311 | -0.054932 | -0.032043 | 0.10986 | -0.17853 | 0.10071 | 0.28839 | 0.09613 | 0.17395 | -0.013733 | 0.064087 | 0.041198 | -0.23346 | -0.19226 | 0.19226 | 0.17853 | 0.15564 | 0.13733 | 0.11444 | 0.17853 | 121.5958 | 0.15106 | 121.3715 | 121.3165 | 121.3303 | 121.4264 | 121.3715 | -121.4951 | -121.5637 | 121.7056 | 121.4127 | 5.278 | 2.6413
1340.4844 | 121.7651 | -0.22888 | 121.3577 | 0.0019074 | 0 | 0.063254 | 0.062647 | -0.0020721 | -0.0037746 | 0.00083317 | -0.0028687 | 0.00097624 | -1.3944 | 0.064384 | -0.0037 | 0.010408 | -0.0032257 | 5.0674 | 121.225 | -0.082397 | 121.463 | 0.064087 | -0.045776 | -0.09613 | 2.4124 | 121.1929 | -0.14648 | 121.2204 | -0.013733 | -0.036621 | -0.013733 | 0.14649 | -0.13275 | 0.10529 | 0.29297 | 0.13275 | 0.18311 | -0.013733 | 0.036621 | 0.082398 | -0.16479 | -0.13733 | 0.21515 | 0.21515 | 0.19226 | 0.13275 | 0.10986 | 0.14648 | 121.5454 | 0.13275 | 121.3669 | 121.3074 | 121.3394 | 121.4539 | 121.4218 | -121.4401 | -121.5042 | 121.6919 | 121.4493 | 5.2963 | 2.6413
1342.2031 | 121.6873 | -0.23804 | 121.4264 | 0.0019074 | 0 | 0.064108 | 0.064142 | 0.0030547 | -0.0012112 | 0.0016876 | 0.00018312 | 0.0037532 | -1.3944 | 0.066947 | -0.003059 | 0.0074171 | 0.00019229 | 5.0034 | 121.2891 | -0.13275 | 121.3486 | -0.086975 | -0.20142 | -0.24261 | 2.2705 | 121.2067 | -0.17395 | 121.1243 | -0.13275 | -0.17853 | -0.086975 | 0.10529 | -0.13733 | -0.07782 | 0.15106 | -0.004578 | 0.036621 | -0.10986 | -0.068665 | 0.064087 | -0.21973 | -0.30212 | 0.10529 | 0.15106 | 0.059509 | 0.086975 | -0.004578 | 0.045776 | 121.4813 | 0.041199 | 121.2982 | 121.4218 | 121.3806 | 121.5271 | 121.4447 | -121.5591 | -121.6003 | 121.5866 | 121.3623 | 5.2414 | 2.5085
1343.9688 | 121.7148 | -0.2243 | 121.4081 | 0.024795 | 0 | 0.063681 | 0.064356 | 0.0030547 | -0.0037746 | -0.00023503 | 0.0093383 | 0.0011898 | -1.3957 | 0.072074 | -0.0024182 | 0.010194 | 0.00083309 | 5.04 | 121.2433 | -0.11444 | 121.4172 | -0.013733 | -0.11444 | -0.15564 | 2.3163 | 121.1746 | -0.18768 | 121.138 | -0.1236 | -0.15106 | -0.073242 | 0.10986 | -0.16479 | 0.009155 | 0.21057 | 0.068664 | 0.10986 | -0.041199 | 0 | 0.036621 | -0.23346 | -0.27008 | 0.10071 | 0.15106 | 0.073242 | 0.11444 | 0.036621 | 0.10071 | 121.5317 | 0.064087 | 121.3257 | 121.3577 | 121.3623 | 121.4676 | 121.3989 | -121.5225 | -121.5958 | 121.6415 | 121.3623 | 5.2643 | 2.5406
1345.6719 | 121.6278 | -0.27466 | 121.4447 | -0.0057221 | 0 | 0.064963 | 0.063715 | -0.0010041 | 0.00028416 | -0.0015166 | -0.0059205 | 0.0031124 | -1.3965 | 0.057975 | -0.0034864 | 0.0097669 | 0.00019229 | 5.0491 | 121.3074 | -0.11902 | 121.3348 | -0.14191 | -0.24261 | -0.26093 | 2.2339 | 121.2112 | -0.18768 | 121.051 | -0.20142 | -0.24261 | -0.12817 | 0.15564 | -0.13733 | -0.10986 | 0.13275 | 0.013733 | 0.032043 | -0.14191 | -0.1236 | 0.086975 | -0.23346 | -0.39368 | 0.073242 | 0.14648 | 0.032043 | 0.059509 | -0.054932 | -0.022888 | 121.4539 | -0.013733 | 121.2387 | 121.4264 | 121.3989 | 121.582 | 121.4859 | -121.5637 | -121.6324 | 121.6095 | 121.3257 | 5.3238 | 2.5085
1347.4375 | 121.637 | -0.28381 | 121.4493 | -0.0057221 | 0 | 0.063467 | 0.066706 | 0.0019867 | -0.0037746 | 0.0019012 | 0.018494 | 0.002258 | -1.3963 | 0.063102 | -0.004768 | 0.0093397 | -0.0034393 | 5.072 | 121.3165 | -0.1831 | 121.3806 | -0.050354 | -0.13733 | -0.19226 | 2.3071 | 121.2433 | -0.23346 | 121.0693 | -0.17395 | -0.20142 | -0.13275 | 0.10071 | -0.13275 | -0.068665 | 0.23346 | 0.091552 | 0.14648 | -0.009156 | 0.045776 | 0.050354 | -0.20599 | -0.37994 | 0.10986 | 0.15106 | 0.082397 | 0.10071 | 0.032043 | 0.13275 | 121.5637 | 0.059509 | 121.3028 | 121.4996 | 121.4767 | 121.6003 | 121.5271 | -121.6324 | -121.6827 | 121.6644 | 121.3531 | 5.3558 | 2.5909
1349.1406 | 121.7697 | -0.21515 | 121.3989 | -0.0057221 | 0 | 0.061331 | 0.062647 | -0.0010041 | -0.002493 | -0.00044863 | -0.0089723 | 0.0020444 | -1.3952 | 0.07357 | -0.005409 | 0.0095533 | -0.0027985 | 5.1132 | 121.225 | -0.10071 | 121.4767 | 0.09613 | -0.027466 | -0.091553 | 2.4399 | 121.1746 | -0.16022 | 121.1929 | -0.018311 | -0.050354 | -0.018311 | 0.11444 | -0.17395 | 0.07782 | 0.31128 | 0.1236 | 0.18768 | 0.009155 | 0.073242 | 0.054932 | -0.2243 | -0.20599 | 0.19684 | 0.19684 | 0.16479 | 0.14191 | 0.10986 | 0.19684 | 121.5775 | 0.14191 | 121.3531 | 121.3257 | 121.3348 | 121.4401 | 121.3898 | -121.4996 | -121.5591 | 121.6919 | 121.4081 | 5.3284 | 2.655
1350.9062 | 121.7468 | -0.21515 | 121.4035 | 0.055313 | 0 | 0.067099 | 0.06692 | -0.00014949 | -0.00078404 | -0.00087583 | 0.018494 | 0.0028988 | -1.3952 | 0.06887 | -0.00028199 | 0.010408 | -0.0027985 | 5.1407 | 121.2662 | -0.11902 | 121.4905 | 0.082397 | -0.059509 | -0.11444 | 2.449 | 121.1884 | -0.17395 | 121.1975 | -0.050354 | -0.082397 | -0.036621 | 0.09613 | -0.13733 | 0.086976 | 0.29755 | 0.10071 | 0.15564 | 0.004578 | 0.05951 | 0.041199 | -0.21515 | -0.20599 | 0.16479 | 0.17853 | 0.13275 | 0.13733 | 0.091553 | 0.20142 | 121.6095 | 0.1236 | 121.3715 | 121.3852 | 121.3623 | 121.4813 | 121.4035 | -121.5225 | -121.5775 | 121.7056 | 121.4127 | 5.3558 | 2.6642
1352.6719 | 121.7468 | -0.20599 | 121.3852 | 0.0019074 | 0 | 0.062827 | 0.062006 | 0.00070491 | -0.0020658 | 0.0010468 | 0.024597 | 0.0048214 | -1.392 | 0.06652 | -0.0024182 | 0.011476 | 0.00083309 | 5.1086 | 121.2524 | -0.082397 | 121.4722 | 0.041199 | -0.10071 | -0.12817 | 2.449 | 121.1884 | -0.16479 | 121.2067 | -0.041199 | -0.082397 | -0.022888 | 0.1236 | -0.13275 | 0.086975 | 0.24719 | 0.07782 | 0.10529 | -0.045777 | -0.018311 | 0.041199 | -0.19684 | -0.17853 | 0.1648 | 0.18311 | 0.1236 | 0.14191 | 0.082398 | 0.1236 | 121.5546 | 0.1236 | 121.3715 | 121.3348 | 121.3531 | 121.4584 | 121.3943 | -121.4676 | -121.55 | 121.6782 | 121.4127 | 5.3146 | 2.655
1354.375 | 121.6461 | -0.27466 | 121.4172 | -0.0057221 | 0 | 0.065817 | 0.064997 | -0.00057689 | -0.0050564 | -0.00044863 | -0.0028687 | 0.0035396 | -1.3918 | 0.060539 | -0.0043408 | 0.010621 | -0.0015167 | 5.0812 | 121.2982 | -0.13275 | 121.3348 | -0.1236 | -0.2243 | -0.24261 | 2.2751 | 121.225 | -0.1831 | 121.0922 | -0.21057 | -0.23346 | -0.1236 | 0.14191 | -0.11902 | -0.082397 | 0.15106 | 0.032043 | 0.050354 | -0.10986 | -0.091553 | 0.091553 | -0.19226 | -0.32501 | 0.064087 | 0.15106 | 0.041199 | 0.059509 | -0.050354 | 0.009155 | 121.4676 | -0.027466 | 121.2753 | 121.431 | 121.4081 | 121.5729 | 121.4996 | -121.55 | -121.6003 | 121.6095 | 121.3669 | 5.3558 | 2.5497
1356.1406 | 121.6232 | -0.2655 | 121.4447 | -0.020981 | 0 | 0.062827 | 0.065424 | 0.0026275 | -0.0022794 | 0.00019217 | 0.015442 | 0.0024716 | -1.394 | 0.061393 | -0.0069044 | 0.0084851 | 0.0010467 | 5.0995 | 121.2845 | -0.17395 | 121.376 | -0.054932 | -0.14191 | -0.1831 | 2.3392 | 121.2662 | -0.20142 | 121.0556 | -0.17853 | -0.20599 | -0.13275 | 0.091553 | -0.16022 | -0.068664 | 0.21057 | 0.082398 | 0.1236 | -0.009155 | 0.032043 | 0.064087 | -0.17853 | -0.3891 | 0.086975 | 0.13275 | 0.059509 | 0.068665 | -0.004578 | 0.11902 | 121.55 | 0.022888 | 121.257 | 121.4584 | 121.4676 | 121.55 | 121.5317 | -121.6187 | -121.6461 | 121.6415 | 121.3211 | 5.365 | 2.6047
1357.8438 | 121.7789 | -0.2243 | 121.3943 | -0.013352 | 0 | 0.062399 | 0.062006 | -0.0018585 | -0.0037746 | -0.003012 | -0.0028687 | 0.00012184 | -1.394 | 0.063743 | -0.0056226 | 0.0099805 | 0.0019013 | 5.1453 | 121.2204 | -0.082397 | 121.4584 | 0.073242 | -0.054932 | -0.10071 | 2.4445 | 121.1655 | -0.15106 | 121.2204 | 0 | -0.036621 | -0.009155 | 0.14191 | -0.17395 | 0.064087 | 0.29755 | 0.1236 | 0.16937 | -0.018311 | 0.027465 | 0.073242 | -0.22888 | -0.17395 | 0.2243 | 0.21515 | 0.18768 | 0.14191 | 0.11444 | 0.15564 | 121.5408 | 0.15106 | 121.3715 | 121.3028 | 121.3165 | 121.4447 | 121.3898 | -121.4767 | -121.5454 | 121.6827 | 121.4447 | 5.3696 | 2.6688
1359.5469 | 121.6599 | -0.24261 | 121.4172 | 0.0095369 | 0 | 0.065817 | 0.065638 | 0.00049131 | -0.0031338 | -0.0017304 | 0.00018312 | 0.003326 | -1.3948 | 0.062675 | -0.0032728 | 0.010835 | -0.00044851 | 5.191 | 121.2708 | -0.10071 | 121.4218 | -0.013733 | -0.13733 | -0.20142 | 2.3483 | 121.225 | -0.17395 | 121.1014 | -0.13733 | -0.18768 | -0.11444 | 0.14191 | -0.14648 | 0.004578 | 0.22888 | 0.041199 | 0.10529 | -0.10071 | -0.036621 | 0.068665 | -0.19226 | -0.31586 | 0.10529 | 0.12817 | 0.054932 | 0.059509 | -0.013733 | 0.086975 | 121.5225 | 0.036621 | 121.2753 | 121.3715 | 121.3989 | 121.5134 | 121.4676 | -121.5179 | -121.5912 | 121.6644 | 121.344 | 5.4337 | 2.5909
1361.3125 | 121.6965 | -0.25177 | 121.4081 | 0.0019074 | 0 | 0.064108 | 0.065211 | -0.00057689 | -0.0014248 | -0.0010894 | 0.00018312 | 0.001617 | -1.395 | 0.061607 | -0.0043408 | 0.010408 | -0.0042939 | 5.1086 | 121.312 | -0.11444 | 121.3531 | -0.086975 | -0.20599 | -0.2243 | 2.3209 | 121.1975 | -0.16022 | 121.1472 | -0.12817 | -0.16479 | -0.073242 | 0.13733 | -0.09613 | -0.054932 | 0.16479 | 0.027466 | 0.045776 | -0.10986 | -0.091553 | 0.091553 | -0.21057 | -0.26093 | 0.1236 | 0.17853 | 0.086975 | 0.086975 | -0.004578 | 0.027466 | 121.4676 | 0.032043 | 121.3074 | 121.4264 | 121.3577 | 121.5637 | 121.4493 | -121.5225 | -121.5683 | 121.6049 | 121.3989 | 5.3604 | 2.5726
1363.0938 | 121.6461 | -0.2655 | 121.4355 | -0.0057221 | 0 | 0.064536 | 0.063502 | 0.0026275 | -0.0031338 | 0.0027558 | 0.018494 | 0.0031124 | -1.3948 | 0.060966 | -0.0060498 | 0.0099805 | 0.0012603 | 5.1315 | 121.3074 | -0.19226 | 121.3715 | -0.059509 | -0.13275 | -0.1831 | 2.33 | 121.2524 | -0.21057 | 121.0693 | -0.16479 | -0.20142 | -0.11902 | 0.073242 | -0.12817 | -0.064087 | 0.20599 | 0.082398 | 0.13275 | 0.009156 | 0.05951 | 0.054932 | -0.18311 | -0.36621 | 0.10071 | 0.14648 | 0.064087 | 0.091552 | 0.009155 | 0.13275 | 121.5637 | 0.045776 | 121.2799 | 121.4996 | 121.463 | 121.5729 | 121.5179 | -121.6278 | -121.6461 | 121.637 | 121.3348 | 5.397 | 2.5955
1364.8594 | 121.6187 | -0.25635 | 121.431 | -0.0057221 | 0 | 0.064108 | 0.063715 | 0.0030547 | -0.0027066 | 0.0019012 | 0.00018312 | 0.0037532 | -1.3948 | 0.059043 | -0.0022046 | 0.0091261 | 0.0012603 | 5.1544 | 121.2845 | -0.13275 | 121.3394 | -0.10071 | -0.19226 | -0.23804 | 2.2797 | 121.2433 | -0.1831 | 121.0785 | -0.18768 | -0.24261 | -0.16022 | 0.1236 | -0.14648 | -0.091552 | 0.15564 | 0.018311 | 0.064087 | -0.10529 | -0.05951 | 0.073243 | -0.18768 | -0.35248 | 0.068665 | 0.096131 | 0.013733 | 0.022888 | -0.05951 | 0.032043 | 121.4722 | -0.004578 | 121.2616 | 121.4172 | 121.4264 | 121.5408 | 121.4996 | -121.5637 | -121.6141 | 121.5958 | 121.3348 | 5.4108 | 2.536
1366.5781 | 121.6873 | -0.23804 | 121.4081 | 0.0019074 | 0 | 0.063895 | 0.062647 | 6.4114e-05 | -0.0037746 | 0.002115 | -0.0028687 | 0.0020444 | -1.3948 | 0.064597 | -0.0043408 | 0.012758 | 0.0010467 | 5.2139 | 121.2204 | -0.09613 | 121.431 | 0.032043 | -0.073242 | -0.1236 | 2.3895 | 121.2021 | -0.16022 | 121.1334 | -0.091553 | -0.14648 | -0.068665 | 0.14191 | -0.18768 | 0.022888 | 0.27008 | 0.11444 | 0.16479 | -0.027466 | 0.022888 | 0.07782 | -0.20599 | -0.27466 | 0.14648 | 0.16937 | 0.091553 | 0.091552 | 0.013733 | 0.12817 | 121.5271 | 0.068664 | 121.2936 | 121.3165 | 121.3623 | 121.4584 | 121.4401 | -121.5042 | -121.5683 | 121.669 | 121.3715 | 5.452 | 2.6276
1368.3438 | 121.7422 | -0.20599 | 121.3898 | 0.0019074 | 0 | 0.065604 | 0.063502 | 0.0066863 | -0.0027066 | 0.001474 | 0.00018312 | 0.0018306 | -1.3961 | 0.06887 | 0.00057241 | 0.011049 | -2.1314e-05 | 5.2094 | 121.2524 | -0.082397 | 121.4722 | 0.054932 | -0.10529 | -0.11902 | 2.4307 | 121.1746 | -0.15106 | 121.2067 | -0.036621 | -0.068665 | -0.022888 | 0.1236 | -0.13733 | 0.082397 | 0.26093 | 0.086975 | 0.10071 | -0.036622 | -0.022889 | 0.054932 | -0.21515 | -0.18311 | 0.16937 | 0.18311 | 0.13733 | 0.12817 | 0.082397 | 0.13733 | 121.5546 | 0.11444 | 121.3577 | 121.3348 | 121.3257 | 121.4584 | 121.3806 | -121.4722 | -121.5408 | 121.6782 | 121.4127 | 5.4153 | 2.6367
1370.1094 | 121.6736 | -0.24261 | 121.4401 | 0.032425 | 0 | 0.061972 | 0.066706 | 0.0045501 | -0.0033474 | -0.0010894 | 0.015442 | 0.0035396 | -1.3948 | 0.063102 | -0.0034864 | 0.0099805 | -0.0010895 | 5.1636 | 121.2982 | -0.16479 | 121.3989 | -0.045776 | -0.10986 | -0.18768 | 2.3666 | 121.2296 | -0.20599 | 121.1197 | -0.13733 | -0.16479 | -0.091553 | 0.07782 | -0.14191 | -0.041199 | 0.19684 | 0.054932 | 0.13275 | -0.022888 | 0.054932 | 0.036621 | -0.21057 | -0.32043 | 0.10529 | 0.15106 | 0.07782 | 0.11444 | 0.041199 | 0.11902 | 121.5637 | 0.068665 | 121.3257 | 121.463 | 121.4355 | 121.5408 | 121.4722 | -121.6049 | -121.6461 | 121.6415 | 121.3623 | 5.4062 | 2.6093
1371.875 | 121.7148 | -0.23804 | 121.3989 | 0.024795 | 0 | 0.066672 | 0.065424 | 0.00091851 | -0.001852 | -0.00023503 | 0.0032349 | 0.00012184 | -1.394 | 0.069084 | -0.0026318 | 0.0097669 | 0.00061949 | 5.1315 | 121.2845 | -0.10986 | 121.4035 | -0.013733 | -0.1236 | -0.14191 | 2.3392 | 121.1746 | -0.16937 | 121.1426 | -0.09613 | -0.12817 | -0.068665 | 0.12817 | -0.11444 | 0.004577 | 0.2243 | 0.09613 | 0.11444 | -0.032044 | -0.013733 | 0.068664 | -0.2243 | -0.25635 | 0.14191 | 0.16937 | 0.10986 | 0.10071 | 0.041199 | 0.09613 | 121.5134 | 0.073243 | 121.312 | 121.3943 | 121.344 | 121.5225 | 121.4127 | -121.5088 | -121.5683 | 121.6415 | 121.3806 | 5.3696 | 2.5772
1373.5781 | 121.7514 | -0.21515 | 121.3989 | -0.0057221 | 0 | 0.061545 | 0.061365 | -0.0027131 | -0.0020658 | -0.0021576 | -0.0059205 | 0.00097624 | -1.3974 | 0.06652 | -0.0039136 | 0.011049 | -0.0013031 | 5.2231 | 121.2341 | -0.073242 | 121.4996 | 0.073242 | -0.027466 | -0.10071 | 2.4948 | 121.1792 | -0.13733 | 121.2067 | -0.009155 | -0.050354 | -0.018311 | 0.14191 | -0.16479 | 0.10071 | 0.28839 | 0.11444 | 0.18768 | -0.027466 | 0.045776 | 0.07782 | -0.21973 | -0.19226 | 0.20599 | 0.19684 | 0.16479 | 0.11902 | 0.086975 | 0.14648 | 121.5729 | 0.12817 | 121.344 | 121.3074 | 121.3165 | 121.4493 | 121.3943 | -121.4722 | -121.5363 | 121.7148 | 121.4218 | 5.4382 | 2.71
1375.2812 | 121.6873 | -0.24719 | 121.4264 | 0.0095369 | 0 | 0.062613 | 0.065851 | 0.0060455 | -0.003561 | -0.0015166 | 0.00018312 | 0.0018306 | -1.3937 | 0.059043 | -0.0026318 | 0.010408 | 0.0012603 | 5.1315 | 121.2936 | -0.13275 | 121.3623 | -0.082397 | -0.20599 | -0.21973 | 2.3438 | 121.1975 | -0.17853 | 121.1426 | -0.11902 | -0.16022 | -0.068665 | 0.11444 | -0.13275 | -0.064087 | 0.16479 | 0.027465 | 0.041198 | -0.086976 | -0.073243 | 0.068664 | -0.22888 | -0.28381 | 0.12817 | 0.17853 | 0.086975 | 0.10986 | 0.018311 | 0.050354 | 121.4951 | 0.059509 | 121.3211 | 121.4264 | 121.376 | 121.5408 | 121.4447 | -121.5591 | -121.6049 | 121.6095 | 121.3898 | 5.3787 | 2.5909
1377 | 121.7056 | -0.20142 | 121.431 | 0.055313 | 0 | 0.064963 | 0.066706 | 0.0049773 | -0.0022794 | 0.0012604 | 0.01239 | 0.002258 | -1.3937 | 0.067375 | -0.0032728 | 0.010621 | -0.00023491 | 5.2002 | 121.2479 | -0.10529 | 121.4584 | 0.068665 | -0.054932 | -0.11902 | 2.4445 | 121.2112 | -0.16937 | 121.1746 | -0.086975 | -0.10986 | -0.045776 | 0.09613 | -0.1831 | 0.027466 | 0.27008 | 0.082397 | 0.14648 | -0.013733 | 0.050354 | 0.032043 | -0.21973 | -0.25635 | 0.11444 | 0.15564 | 0.091553 | 0.1236 | 0.05951 | 0.17395 | 121.5637 | 0.082398 | 121.344 | 121.3532 | 121.3806 | 121.4493 | 121.4127 | -121.5363 | -121.6003 | 121.6599 | 121.376 | 5.4016 | 2.6459
1378.7656 | 121.7239 | -0.2243 | 121.4218 | -0.013352 | 0 | 0.062399 | 0.065424 | -0.0054901 | -0.0039884 | -0.0023712 | 0.00018312 | 0.00097624 | -1.3946 | 0.059684 | -0.0011364 | 0.0093397 | -2.1314e-05 | 5.1453 | 121.2982 | -0.10986 | 121.3669 | -0.059509 | -0.1831 | -0.21057 | 2.3575 | 121.2204 | -0.16937 | 121.1517 | -0.091553 | -0.14191 | -0.059509 | 0.11444 | -0.1236 | -0.054932 | 0.16479 | 0.013733 | 0.041199 | -0.10071 | -0.073242 | 0.054931 | -0.20142 | -0.27008 | 0.13275 | 0.16479 | 0.082397 | 0.10986 | 0.027466 | 0.050354 | 121.4767 | 0.07782 | 121.3211 | 121.4081 | 121.3898 | 121.5225 | 121.4447 | -121.5317 | -121.5912 | 121.5912 | 121.376 | 5.3696 | 2.5818
1380.4688 | 121.6095 | -0.25635 | 121.4539 | 0.0019074 | 0 | 0.063467 | 0.065638 | 0.0043365 | -0.0033474 | -0.0023712 | 0.00018312 | 0.0035396 | -1.3946 | 0.065238 | -0.0034864 | 0.01233 | -0.00087591 | 5.1682 | 121.2799 | -0.1236 | 121.3348 | -0.11444 | -0.21973 | -0.24719 | 2.2659 | 121.2662 | -0.17395 | 121.0739 | -0.21057 | -0.23804 | -0.13275 | 0.13275 | -0.17395 | -0.11902 | 0.14191 | 0.009156 | 0.036621 | -0.1236 | -0.096131 | 0.082398 | -0.18768 | -0.37994 | 0.045777 | 0.1236 | 0.018311 | 0.041199 | -0.064087 | 0.009155 | 121.4584 | -0.036621 | 121.2479 | 121.4035 | 121.4401 | 121.5363 | 121.5225 | -121.5775 | -121.6278 | 121.5912 | 121.3303 | 5.4245 | 2.5223
1382.2344 | 121.6324 | -0.24719 | 121.4081 | 0.0019074 | 0 | 0.064108 | 0.06457 | 0.0045501 | -0.00057044 | -0.00087583 | 0.00018312 | 0.0018306 | -1.3946 | 0.055625 | -0.0013502 | 0.0097669 | -0.0057891 | 5.2139 | 121.2891 | -0.10986 | 121.3806 | -0.045776 | -0.18768 | -0.21973 | 2.3575 | 121.2112 | -0.15106 | 121.1197 | -0.16022 | -0.23346 | -0.1236 | 0.13733 | -0.11902 | -0.027466 | 0.20142 | 0.027465 | 0.059509 | -0.10986 | -0.07782 | 0.09613 | -0.19684 | -0.28839 | 0.086975 | 0.1236 | 0.013733 | 0.027466 | -0.082397 | 0.064087 | 121.4905 | -0.009155 | 121.2708 | 121.3989 | 121.3623 | 121.5363 | 121.4584 | -121.5179 | -121.5591 | 121.6278 | 121.3669 | 5.4611 | 2.6047
1383.9844 | 121.637 | -0.2655 | 121.4401 | 0.0019074 | 0 | 0.062399 | 0.065211 | -0.0018585 | -0.0033474 | -0.0010894 | -0.0059205 | 0.0035396 | -1.3927 | 0.06417 | -0.003059 | 0.010408 | 0.0023285 | 5.159 | 121.3074 | -0.13275 | 121.3348 | -0.10071 | -0.21973 | -0.23346 | 2.2888 | 121.2296 | -0.17853 | 121.1105 | -0.16937 | -0.21973 | -0.11444 | 0.13275 | -0.13275 | -0.10529 | 0.16479 | 0.032044 | 0.045776 | -0.10071 | -0.086976 | 0.086975 | -0.21057 | -0.32959 | 0.09613 | 0.15106 | 0.045776 | 0.064087 | -0.041199 | 0.032043 | 121.4676 | 0.009155 | 121.2891 | 121.4401 | 121.4081 | 121.5729 | 121.4951 | -121.5729 | -121.6187 | 121.6003 | 121.376 | 5.4245 | 2.5543
1385.75 | 121.6644 | -0.25635 | 121.4401 | -0.0057221 | 0 | 0.064108 | 0.063502 | -0.00057689 | -0.004202 | -0.0027984 | 0.00018312 | 0.0020444 | -1.3946 | 0.063529 | -0.0013502 | 0.0086987 | 0.0021149 | 5.1636 | 121.2936 | -0.10986 | 121.3394 | -0.10071 | -0.21515 | -0.23804 | 2.3163 | 121.2433 | -0.16479 | 121.1105 | -0.16479 | -0.21057 | -0.10986 | 0.14649 | -0.14648 | -0.10071 | 0.15564 | 0.018311 | 0.041199 | -0.12817 | -0.10529 | 0.091553 | -0.19684 | -0.32959 | 0.091553 | 0.14649 | 0.045777 | 0.054932 | -0.045776 | 0.009155 | 121.4493 | 0 | 121.2753 | 121.4035 | 121.4081 | 121.55 | 121.4996 | -121.55 | -121.6049 | 121.5958 | 121.3669 | 5.4199 | 2.5726
1387.5156 | 121.7651 | -0.19684 | 121.3852 | 0.0019074 | 0 | 0.064536 | 0.063074 | 0.00091851 | 7.0564e-05 | -0.003012 | 0.015442 | 0.002258 | -1.394 | 0.069938 | -0.0024182 | 0.012544 | -0.0030121 | 5.246 | 121.225 | -0.064087 | 121.5088 | 0.10071 | -0.041199 | -0.07782 | 2.4536 | 121.2067 | -0.16479 | 121.2158 | -0.041199 | -0.082397 | -0.009155 | 0.13275 | -0.16022 | 0.1236 | 0.29755 | 0.11902 | 0.15564 | -0.013733 | 0.022888 | 0.032043 | -0.17853 | -0.16937 | 0.15564 | 0.18768 | 0.11444 | 0.15564 | 0.082398 | 0.1648 | 121.5729 | 0.1236 | 121.3806 | 121.2891 | 121.3715 | 121.4218 | 121.4035 | -121.4493 | -121.55 | 121.7056 | 121.4127 | 5.4428 | 2.6505
1389.2812 | 121.6644 | -0.22888 | 121.4447 | 0.0095369 | 0 | 0.063895 | 0.064356 | 6.4114e-05 | -0.0031338 | 0.0010468 | 0.0032349 | 0.0058896 | -1.3933 | 0.061179 | -0.0049818 | 0.0099805 | -0.0010895 | 5.2643 | 121.2662 | -0.12817 | 121.431 | -0.004578 | -0.10529 | -0.16479 | 2.4307 | 121.2158 | -0.17395 | 121.1334 | -0.10986 | -0.16479 | -0.07782 | 0.10071 | -0.17853 | -0.013733 | 0.2243 | 0.064087 | 0.1236 | -0.036621 | 0.022888 | 0.054932 | -0.22888 | -0.31128 | 0.11902 | 0.15106 | 0.064087 | 0.09613 | 0.009155 | 0.1236 | 121.5591 | 0.064087 | 121.3074 | 121.3943 | 121.3898 | 121.4951 | 121.4447 | -121.5729 | -121.6187 | 121.6599 | 121.3623 | 5.4932 | 2.6596
1391.0625 | 121.701 | -0.23346 | 121.4172 | -0.0057221 | 0 | 0.064108 | 0.064142 | 0.0030547 | -0.0027066 | -0.0023712 | -0.0028687 | 0.0026852 | -1.3935 | 0.062248 | -0.0058362 | 0.011476 | -0.0021575 | 5.1727 | 121.3028 | -0.10986 | 121.3623 | -0.064087 | -0.16937 | -0.20142 | 2.3712 | 121.2021 | -0.15564 | 121.17 | -0.10071 | -0.13733 | -0.068665 | 0.1236 | -0.11444 | -0.054931 | 0.16937 | 0.032043 | 0.064086 | -0.091553 | -0.05951 | 0.077819 | -0.21515 | -0.24719 | 0.13275 | 0.16479 | 0.09613 | 0.086975 | 0.018311 | 0.045776 | 121.4722 | 0.054932 | 121.3257 | 121.4127 | 121.3577 | 121.5363 | 121.4355 | -121.5271 | -121.5729 | 121.5958 | 121.4035 | 5.4062 | 2.6047
1392.8438 | 121.6324 | -0.24261 | 121.431 | 0.0019074 | 0 | 0.063254 | 0.063929 | 0.0030547 | -0.00099764 | 0.00040597 | -0.0059205 | 0.003326 | -1.3952 | 0.063102 | -0.0060498 | 0.010194 | -0.0010895 | 5.2597 | 121.2891 | -0.11444 | 121.3806 | -0.027466 | -0.14191 | -0.20142 | 2.3987 | 121.2433 | -0.16479 | 121.1151 | -0.14648 | -0.20599 | -0.10071 | 0.12817 | -0.14191 | -0.050354 | 0.21515 | 0.041199 | 0.10071 | -0.086975 | -0.027466 | 0.07782 | -0.18768 | -0.31586 | 0.096131 | 0.14191 | 0.036621 | 0.064087 | -0.041199 | 0.086975 | 121.4951 | 0.018311 | 121.2799 | 121.4035 | 121.4081 | 121.5317 | 121.4859 | -121.5454 | -121.5958 | 121.6232 | 121.3577 | 5.5023 | 2.6413
1394.5469 | 121.6415 | -0.2655 | 121.4539 | 0.055313 | 0 | 0.064536 | 0.066279 | 0.0032685 | -0.0020658 | 0.00083317 | 0.01239 | 0.0035396 | -1.3944 | 0.063316 | -0.0058362 | 0.0095533 | 0.0044647 | 5.2505 | 121.3257 | -0.16022 | 121.3806 | -0.054932 | -0.13733 | -0.18768 | 2.3804 | 121.2753 | -0.21515 | 121.0876 | -0.15564 | -0.18768 | -0.10529 | 0.10529 | -0.12817 | -0.073242 | 0.21057 | 0.07782 | 0.12817 | -0.027466 | 0.022888 | 0.050354 | -0.17853 | -0.36621 | 0.10986 | 0.16022 | 0.07782 | 0.10986 | 0.027466 | 0.10528 | 121.5408 | 0.059509 | 121.3028 | 121.4859 | 121.4905 | 121.5912 | 121.5408 | -121.6141 | -121.669 | 121.6461 | 121.3531 | 5.5161 | 2.6459
1396.3125 | 121.7606 | -0.19684 | 121.3989 | -0.013352 | 0 | 0.06539 | 0.062647 | -0.00036309 | -0.004202 | -0.001944 | -0.0059205 | -0.0015872 | -1.3967 | 0.062675 | -0.004768 | 0.010408 | -0.0047211 | 5.2551 | 121.2387 | -0.091553 | 121.4722 | 0.091553 | -0.018311 | -0.09613 | 2.4994 | 121.17 | -0.14191 | 121.2067 | -0.018311 | -0.050354 | -0.022888 | 0.10529 | -0.16022 | 0.073242 | 0.28839 | 0.10071 | 0.17853 | -0.004577 | 0.073242 | 0.054931 | -0.22888 | -0.19226 | 0.17853 | 0.17395 | 0.14648 | 0.11902 | 0.091553 | 0.18311 | 121.5637 | 0.1236 | 121.3486 | 121.3303 | 121.312 | 121.4355 | 121.3669 | -121.4905 | -121.5408 | 121.669 | 121.4035 | 5.452 | 2.6962
1398.0781 | 121.6965 | -0.23804 | 121.431 | 0.024795 | 0 | 0.063254 | 0.065211 | -0.0016449 | -0.002493 | -2.1434e-05 | 0.0062865 | 0.0011898 | -1.394 | 0.063743 | -0.0026318 | 0.0093397 | -2.1314e-05 | 5.2643 | 121.3028 | -0.14191 | 121.4218 | -0.013733 | -0.11902 | -0.16022 | 2.4536 | 121.2341 | -0.16479 | 121.1563 | -0.09613 | -0.15564 | -0.064087 | 0.09613 | -0.12817 | -0.009155 | 0.2243 | 0.07782 | 0.11902 | -0.01831 | 0.022888 | 0.073242 | -0.19684 | -0.27466 | 0.14191 | 0.17395 | 0.082397 | 0.10071 | 0.009155 | 0.12817 | 121.5637 | 0.068665 | 121.3211 | 121.4447 | 121.3989 | 121.5408 | 121.4722 | -121.5729 | -121.5958 | 121.6599 | 121.3943 | 5.5023 | 2.6916
1399.8438 | 121.7422 | -0.20142 | 121.4035 | 0.055313 | 0 | 0.067099 | 0.063715 | -0.00057689 | -0.0016384 | 0.0016876 | 0.01239 | 0.0035396 | -1.3946 | 0.059257 | -0.0032728 | 0.0095533 | -0.0032257 | 5.2689 | 121.2662 | -0.11444 | 121.4905 | 0.091553 | -0.050354 | -0.07782 | 2.4902 | 121.2021 | -0.17395 | 121.2112 | -0.036621 | -0.09613 | -0.027466 | 0.086975 | -0.13733 | 0.086976 | 0.29297 | 0.1236 | 0.15106 | 0.036621 | 0.064087 | 0.027466 | -0.20142 | -0.19226 | 0.1648 | 0.17395 | 0.10529 | 0.14648 | 0.07782 | 0.20599 | 121.6049 | 0.13733 | 121.3852 | 121.3806 | 121.376 | 121.4676 | 121.4035 | -121.5179 | -121.5775 | 121.6919 | 121.4127 | 5.4703 | 2.6917
1401.5469 | 121.6736 | -0.24261 | 121.4127 | 0.017166 | 0 | 0.062827 | 0.065851 | 0.00049131 | -0.0022794 | 0.0019012 | 0.00018312 | 0.0026852 | -1.3935 | 0.061179 | -0.0043408 | 0.0086987 | 0.00061949 | 5.3009 | 121.2891 | -0.12817 | 121.4172 | 0.004578 | -0.11444 | -0.15564 | 2.449 | 121.225 | -0.17395 | 121.1243 | -0.12817 | -0.16022 | -0.073242 | 0.11444 | -0.1236 | 0.004577 | 0.24719 | 0.086975 | 0.12817 | -0.027466 | 0.013733 | 0.068665 | -0.18768 | -0.28839 | 0.11444 | 0.16937 | 0.082398 | 0.10071 | 0.013733 | 0.13275 | 121.5454 | 0.045776 | 121.2982 | 121.4172 | 121.3989 | 121.5317 | 121.4676 | -121.5408 | -121.5866 | 121.6599 | 121.3669 | 5.5435 | 2.6917
1403.3125 | 121.6324 | -0.25177 | 121.4127 | -0.0057221 | 0 | 0.062613 | 0.063288 | 0.0017731 | -0.0020658 | -0.00044863 | -0.0059205 | 0.00076264 | -1.3931 | 0.059898 | -0.0043408 | 0.0093397 | -0.0015167 | 5.2597 | 121.2753 | -0.10986 | 121.3486 | -0.068665 | -0.15564 | -0.20142 | 2.3758 | 121.2296 | -0.16479 | 121.0693 | -0.16022 | -0.19226 | -0.14191 | 0.14191 | -0.13733 | -0.064087 | 0.1831 | 0.050354 | 0.09613 | -0.091553 | -0.045777 | 0.086975 | -0.18311 | -0.34332 | 0.091553 | 0.10986 | 0.059509 | 0.022888 | -0.027466 | 0.041198 | 121.4584 | 0.004578 | 121.2341 | 121.3852 | 121.3943 | 121.5271 | 121.4813 | -121.5225 | -121.5775 | 121.6003 | 121.3211 | 5.5115 | 2.6276
1405.0156 | 121.6873 | -0.24261 | 121.4584 | 0.047683 | 0 | 0.063681 | 0.064997 | -0.0016449 | -0.00078404 | 0.00019217 | 0.018494 | 0.0020444 | -1.3946 | 0.061393 | -0.0037 | 0.0095533 | -0.00044851 | 5.3238 | 121.312 | -0.15564 | 121.4035 | -0.036621 | -0.10529 | -0.17395 | 2.4216 | 121.2433 | -0.18768 | 121.1243 | -0.1236 | -0.17395 | -0.086975 | 0.086975 | -0.14648 | -0.054932 | 0.20599 | 0.068665 | 0.13733 | -0.01831 | 0.050354 | 0.054932 | -0.21515 | -0.33417 | 0.11902 | 0.15564 | 0.068665 | 0.10071 | 0.013733 | 0.11902 | 121.5591 | 0.064087 | 121.312 | 121.4676 | 121.431 | 121.5546 | 121.4859 | -121.6141 | -121.6461 | 121.6461 | 121.3669 | 5.5664 | 2.6642
1406.7812 | 121.6232 | -0.2655 | 121.4539 | -0.013352 | 0 | 0.062186 | 0.062861 | 0.0032685 | -0.003561 | -0.0017304 | 0.00018312 | 0.0011898 | -1.394 | 0.063957 | -0.0034864 | 0.0086987 | -0.00066231 | 5.3009 | 121.3028 | -0.12817 | 121.3348 | -0.11444 | -0.20599 | -0.24719 | 2.3117 | 121.2479 | -0.18768 | 121.0785 | -0.21057 | -0.24719 | -0.14648 | 0.13733 | -0.15106 | -0.11902 | 0.15106 | 0.018311 | 0.059509 | -0.11902 | -0.07782 | 0.07782 | -0.20599 | -0.37537 | 0.054932 | 0.11902 | 0.018311 | 0.041199 | -0.059509 | 0.013733 | 121.463 | -0.022888 | 121.2662 | 121.431 | 121.4355 | 121.5683 | 121.5134 | -121.582 | -121.6415 | 121.6003 | 121.344 | 5.5664 | 2.5772
1408.5469 | 121.7148 | -0.21973 | 121.4127 | 0.024795 | 0 | 0.063254 | 0.063502 | -0.0014313 | -0.0016384 | -0.0023712 | 0.0062865 | -0.0015872 | -1.3935 | 0.067375 | -0.00092279 | 0.01233 | 0.00040589 | 5.3192 | 121.2891 | -0.10071 | 121.4218 | 0 | -0.10986 | -0.12817 | 2.4033 | 121.2021 | -0.17395 | 121.1517 | -0.10986 | -0.13733 | -0.054932 | 0.11902 | -0.1236 | 0.009155 | 0.21973 | 0.091553 | 0.10986 | -0.027466 | -0.009155 | 0.045777 | -0.21057 | -0.26093 | 0.10986 | 0.16479 | 0.082398 | 0.11902 | 0.036621 | 0.10071 | 121.5225 | 0.064087 | 121.3257 | 121.3898 | 121.376 | 121.5088 | 121.4218 | -121.5134 | -121.5866 | 121.6415 | 121.3715 | 5.5389 | 2.623
1410.2656 | 121.7651 | -0.21973 | 121.4218 | 0.0095369 | 0 | 0.063467 | 0.060938 | -0.0029267 | -0.0037746 | -2.1434e-05 | -0.0089723 | 0.001617 | -1.3931 | 0.070152 | -0.0041272 | 0.010194 | 0.00040589 | 5.3741 | 121.225 | -0.082397 | 121.4996 | 0.10529 | -0.022888 | -0.09613 | 2.5314 | 121.2021 | -0.14648 | 121.2067 | 0.004578 | -0.045776 | -0.027466 | 0.13733 | -0.19684 | 0.07782 | 0.32501 | 0.1236 | 0.19684 | -0.013733 | 0.059509 | 0.073243 | -0.21973 | -0.21515 | 0.22431 | 0.19226 | 0.17395 | 0.11902 | 0.10071 | 0.18768 | 121.582 | 0.15106 | 121.3531 | 121.3074 | 121.3486 | 121.4447 | 121.4218 | -121.5042 | -121.5683 | 121.7194 | 121.4264 | 5.5939 | 2.7512
1412.0312 | 121.7697 | -0.19684 | 121.3852 | -0.013352 | 0 | 0.064108 | 0.065211 | -0.0010041 | 0.00071136 | 0.0012604 | -0.0059205 | 0.0014034 | -1.3955 | 0.06652 | -6.8386e-05 | 0.011689 | -0.0038665 | 5.365 | 121.2662 | -0.086975 | 121.4767 | 0.050354 | -0.09613 | -0.13275 | 2.4948 | 121.1838 | -0.14191 | 121.225 | -0.041199 | -0.091553 | -0.004578 | 0.10986 | -0.11902 | 0.091553 | 0.24719 | 0.064087 | 0.10071 | -0.045776 | -0.009155 | 0.054931 | -0.20142 | -0.16022 | 0.15564 | 0.19226 | 0.10529 | 0.13733 | 0.050354 | 0.13733 | 121.5637 | 0.10071 | 121.3669 | 121.3531 | 121.3257 | 121.463 | 121.3806 | -121.4722 | -121.5271 | 121.6736 | 121.4218 | 5.5618 | 2.6917
1413.7344 | 121.6736 | -0.26093 | 121.4081 | 0.08583 | 0 | 0.06539 | 0.065851 | -0.0039947 | -0.0039884 | 0.0010468 | 0.018494 | 0.0037532 | -1.3935 | 0.061179 | -0.0056226 | 0.0074171 | 0.0019013 | 5.4062 | 121.3257 | -0.15106 | 121.3852 | -0.059509 | -0.13275 | -0.17395 | 2.417 | 121.257 | -0.20599 | 121.1243 | -0.11902 | -0.16937 | -0.086975 | 0.10986 | -0.082397 | -0.022888 | 0.20142 | 0.086975 | 0.12817 | -0.022888 | 0.018311 | 0.054931 | -0.15106 | -0.28381 | 0.14191 | 0.17395 | 0.091552 | 0.11902 | 0.036621 | 0.091553 | 121.5363 | 0.086975 | 121.3303 | 121.4767 | 121.463 | 121.5866 | 121.5179 | -121.5591 | -121.6141 | 121.6461 | 121.3852 | 5.6671 | 2.6779
1415.5 | 121.7697 | -0.20142 | 121.376 | -0.0057221 | 0 | 0.062399 | 0.062433 | -0.0044221 | -0.0046292 | -0.001944 | -0.0028687 | 0.00012184 | -1.3965 | 0.06182 | -0.004768 | 0.0097669 | 0.0010467 | 5.4016 | 121.2433 | -0.07782 | 121.4676 | 0.09613 | -0.032043 | -0.07782 | 2.5589 | 121.1746 | -0.14191 | 121.2341 | -0.013733 | -0.054932 | -0.018311 | 0.1236 | -0.13275 | 0.091552 | 0.29755 | 0.1236 | 0.16937 | 0 | 0.045777 | 0.059509 | -0.20142 | -0.14191 | 0.18768 | 0.18311 | 0.14648 | 0.1236 | 0.086975 | 0.17395 | 121.5454 | 0.12817 | 121.376 | 121.3211 | 121.3165 | 121.4447 | 121.376 | -121.4539 | -121.5179 | 121.669 | 121.4355 | 5.603 | 2.7603
1417.2188 | 121.7514 | -0.21515 | 121.4035 | 0.0019074 | 0 | 0.063895 | 0.067347 | 0.0015595 | -0.0012112 | 0.0019012 | 0.018494 | 0.002258 | -1.3948 | 0.062461 | -0.0011364 | 0.012758 | 0.00040589 | 5.4474 | 121.2616 | -0.07782 | 121.5088 | 0.091553 | -0.050354 | -0.07782 | 2.5269 | 121.2021 | -0.17853 | 121.225 | -0.032043 | -0.073242 | -0.009155 | 0.13733 | -0.14191 | 0.10529 | 0.3067 | 0.13733 | 0.16479 | 0 | 0.027466 | 0.036621 | -0.20142 | -0.17853 | 0.18311 | 0.20599 | 0.14191 | 0.16937 | 0.10529 | 0.16937 | 121.5866 | 0.14648 | 121.4035 | 121.3394 | 121.3806 | 121.4767 | 121.4172 | -121.4813 | -121.582 | 121.7239 | 121.4401 | 5.6625 | 2.742
1418.9844 | 121.7285 | -0.21973 | 121.4355 | 0.0019074 | 0 | 0.062186 | 0.062861 | 0.0039093 | -0.0020658 | -0.00087583 | -0.0059205 | 0.0035396 | -1.394 | 0.065238 | -0.0011364 | 0.010408 | -0.00044851 | 5.3741 | 121.3028 | -0.10986 | 121.376 | -0.054932 | -0.16937 | -0.20599 | 2.4124 | 121.2112 | -0.16479 | 121.1792 | -0.10529 | -0.11902 | -0.059509 | 0.10986 | -0.13275 | -0.059509 | 0.16479 | 0.013733 | 0.050354 | -0.096131 | -0.05951 | 0.054932 | -0.2243 | -0.25635 | 0.11444 | 0.16022 | 0.10071 | 0.10529 | 0.045776 | 0.054931 | 121.4859 | 0.059509 | 121.344 | 121.4127 | 121.376 | 121.5225 | 121.431 | -121.5454 | -121.6003 | 121.5958 | 121.3989 | 5.5939 | 2.6321
1420.6875 | 121.6553 | -0.24719 | 121.4172 | 0.0095369 | 0 | 0.064963 | 0.066706 | -0.00036309 | -0.0022794 | -0.00087583 | 0.0032349 | 0.0014034 | -1.3948 | 0.062888 | -0.0032728 | 0.010835 | 0.00019229 | 5.4611 | 121.2845 | -0.1236 | 121.4081 | -0.009155 | -0.13733 | -0.17853 | 2.449 | 121.2387 | -0.15564 | 121.1334 | -0.13275 | -0.16937 | -0.09613 | 0.1236 | -0.13275 | -0.009155 | 0.23804 | 0.068664 | 0.10986 | -0.054932 | -0.013733 | 0.091552 | -0.17853 | -0.28381 | 0.11444 | 0.15106 | 0.077819 | 0.05951 | -0.013733 | 0.11444 | 121.5317 | 0.022889 | 121.2891 | 121.4081 | 121.3943 | 121.5317 | 121.4859 | -121.5408 | -121.5729 | 121.6553 | 121.3806 | 5.7083 | 2.6962
1422.7344 | 121.7926 | -0.19684 | 121.3852 | 0.0095369 | 0 | 0.064536 | 0.063288 | -0.0016449 | -0.0031338 | -0.0017304 | -0.0059205 | -0.0022282 | -1.3976 | 0.068443 | -0.00070919 | 0.0086987 | 0.00083309 | 5.4703 | 121.2708 | -0.09613 | 121.4722 | 0.09613 | -0.027466 | -0.07782 | 2.5269 | 121.1746 | -0.12817 | 121.2341 | 0 | -0.036621 | 0 | 0.10071 | -0.11444 | 0.086975 | 0.29297 | 0.11902 | 0.16937 | 0.01831 | 0.068664 | 0.068664 | -0.21057 | -0.15106 | 0.19684 | 0.19684 | 0.16022 | 0.12817 | 0.091553 | 0.19226 | 121.5683 | 0.12817 | 121.3623 | 121.3669 | 121.3028 | 121.4676 | 121.3715 | -121.4813 | -121.5134 | 121.669 | 121.431 | 5.6671 | 2.7237
1426.4531 | 121.6736 | -0.23804 | 121.431 | 0.017166 | 0 | 0.064108 | 0.063715 | -0.0022857 | -0.0014248 | 0.003183 | 0.015442 | 0.0041806 | -1.3959 | 0.062888 | -0.0060498 | 0.0082715 | -0.0040801 | 5.5435 | 121.3348 | -0.14648 | 121.4218 | -0.027466 | -0.10529 | -0.16022 | 2.4948 | 121.2341 | -0.16937 | 121.138 | -0.10986 | -0.14191 | -0.073242 | 0.091553 | -0.09613 | -0.009155 | 0.21057 | 0.07782 | 0.13275 | -0.013733 | 0.041198 | 0.068664 | -0.19684 | -0.29297 | 0.12817 | 0.16479 | 0.09613 | 0.096131 | 0.027466 | 0.11902 | 121.5683 | 0.05951 | 121.3074 | 121.4813 | 121.4035 | 121.5729 | 121.4722 | -121.5775 | -121.6003 | 121.6599 | 121.376 | 5.7816 | 2.7328
1430.0938 | 121.7194 | -0.21515 | 121.3989 | 0.040054 | 0 | 0.066031 | 0.062861 | -0.0029267 | -0.0012112 | 0.00083317 | 0.015442 | 0.00097624 | -1.3942 | 0.060539 | -0.0037 | 0.011262 | -0.00066231 | 5.5939 | 121.3028 | -0.10071 | 121.4905 | 0.086975 | -0.064087 | -0.10071 | 2.5131 | 121.1838 | -0.17395 | 121.1929 | -0.054932 | -0.10071 | -0.027466 | 0.11444 | -0.096131 | 0.091553 | 0.30212 | 0.11444 | 0.15106 | 0 | 0.036621 | 0.041199 | -0.21515 | -0.20599 | 0.16022 | 0.18768 | 0.11444 | 0.14648 | 0.073242 | 0.18768 | 121.5912 | 0.11902 | 121.3669 | 121.4035 | 121.3577 | 121.5179 | 121.3989 | -121.4996 | -121.5729 | 121.7056 | 121.4081 | 5.809 | 2.7283
1435.9375 | 121.7697 | -0.21515 | 121.4081 | 0.0019074 | 0 | 0.061118 | 0.063502 | -0.0024995 | -0.004202 | -0.0017304 | -0.0059205 | 0.00076264 | -1.3987 | 0.067588 | -0.0043408 | 0.011903 | -0.0015167 | 5.6625 | 121.2524 | -0.068665 | 121.4951 | 0.10986 | -0.027466 | -0.073242 | 2.5497 | 121.1792 | -0.16937 | 121.2433 | -0.004578 | -0.041199 | 0.004578 | 0.14648 | -0.15564 | 0.086975 | 0.32501 | 0.14191 | 0.18768 | -0.004577 | 0.041199 | 0.045776 | -0.22888 | -0.16479 | 0.21057 | 0.21973 | 0.17395 | 0.17395 | 0.12817 | 0.17853 | 121.5637 | 0.16479 | 121.4127 | 121.3211 | 121.3486 | 121.4676 | 121.3943 | -121.4767 | -121.5775 | 121.7102 | 121.4584 | 5.8777 | 2.7649
1437.7031 | 121.6736 | -0.23346 | 121.4355 | 0.040054 | 0 | 0.064108 | 0.06457 | 0.0026275 | -0.0031338 | -0.00023503 | 0.015442 | 0.0041806 | -1.3955 | 0.062034 | -0.0034864 | 0.0095533 | 0.0016877 | 5.6808 | 121.3257 | -0.15106 | 121.4035 | -0.027466 | -0.13275 | -0.16479 | 2.4673 | 121.2616 | -0.19226 | 121.1243 | -0.11902 | -0.17395 | -0.091553 | 0.082397 | -0.10986 | -0.032044 | 0.20599 | 0.068664 | 0.10071 | -0.013733 | 0.018311 | 0.041198 | -0.17395 | -0.31128 | 0.11444 | 0.14191 | 0.059509 | 0.10071 | 0.018311 | 0.1236 | 121.5546 | 0.073242 | 121.3165 | 121.4767 | 121.4539 | 121.5591 | 121.4951 | -121.5866 | -121.6278 | 121.637 | 121.3577 | 5.9143 | 2.7008
1439.4688 | 121.6644 | -0.24719 | 121.4355 | 0.0019074 | 0 | 0.059622 | 0.065638 | -0.0057037 | -0.0048428 | -0.0015166 | 0.024597 | 0.0043942 | -1.3933 | 0.059898 | -0.0066906 | 0.0084851 | 0.0012603 | 5.6305 | 121.2753 | -0.13275 | 121.3852 | -0.045776 | -0.12817 | -0.17853 | 2.4261 | 121.2753 | -0.21057 | 121.0876 | -0.15106 | -0.20142 | -0.1236 | 0.11444 | -0.16022 | -0.050354 | 0.20142 | 0.068664 | 0.11902 | -0.045777 | 0.004577 | 0.036621 | -0.16022 | -0.3479 | 0.09613 | 0.1236 | 0.045776 | 0.086975 | 0.009155 | 0.086975 | 121.5179 | 0.059509 | 121.2982 | 121.4081 | 121.4859 | 121.5225 | 121.5225 | -121.5683 | -121.6461 | 121.6324 | 121.3348 | 5.8777 | 2.6733
1441.1719 | 121.637 | -0.25177 | 121.4722 | -0.0057221 | 0 | 0.064108 | 0.063288 | -0.00014949 | -0.002493 | -0.0025848 | -0.0028687 | 0.0020444 | -1.3957 | 0.062461 | -0.0066906 | 0.0091261 | -0.0047211 | 5.6625 | 121.2845 | -0.11444 | 121.3531 | -0.064087 | -0.15564 | -0.20142 | 2.417 | 121.2433 | -0.17853 | 121.0739 | -0.16022 | -0.18768 | -0.12817 | 0.13733 | -0.18768 | -0.11902 | 0.18768 | 0.050354 | 0.09613 | -0.086975 | -0.041199 | 0.073242 | -0.22888 | -0.39825 | 0.091553 | 0.1236 | 0.064087 | 0.050354 | -0.009155 | 0.050354 | 121.4676 | 0.018311 | 121.2524 | 121.3989 | 121.4218 | 121.5363 | 121.4951 | -121.5866 | -121.6507 | 121.6049 | 121.3257 | 5.9143 | 2.6688
1442.9375 | 121.7651 | -0.2243 | 121.4218 | 0.0019074 | 0 | 0.062827 | 0.063502 | -0.0020721 | -0.0027066 | -0.0025848 | 0.00018312 | 0.00054904 | -1.3959 | 0.063102 | -0.001991 | 0.010621 | -0.0021575 | 5.6625 | 121.2524 | -0.086975 | 121.4401 | 0.027466 | -0.068665 | -0.10529 | 2.4948 | 121.1975 | -0.14191 | 121.2021 | -0.032043 | -0.068665 | -0.022888 | 0.13733 | -0.16937 | 0.018311 | 0.25177 | 0.11902 | 0.15564 | -0.018311 | 0.01831 | 0.082397 | -0.2243 | -0.21973 | 0.19226 | 0.20142 | 0.15564 | 0.11902 | 0.073242 | 0.11444 | 121.5271 | 0.10986 | 121.344 | 121.3394 | 121.3394 | 121.4767 | 121.4218 | -121.5088 | -121.5637 | 121.6644 | 121.4264 | 5.8868 | 2.7191
1444.6562 | 121.7514 | -0.20142 | 121.4127 | 0.0019074 | 0 | 0.064963 | 0.06457 | -0.00079049 | -0.001852 | 0.00019217 | -0.0059205 | 0.0011898 | -1.394 | 0.060325 | -0.00070919 | 0.011262 | -0.0019439 | 5.6992 | 121.257 | -0.086975 | 121.463 | 0.022888 | -0.082397 | -0.13275 | 2.536 | 121.1884 | -0.15564 | 121.2387 | -0.059509 | -0.086975 | 0.009155 | 0.11444 | -0.15564 | 0.050354 | 0.2243 | 0.068665 | 0.11902 | -0.045776 | 0.004578 | 0.045776 | -0.22431 | -0.17395 | 0.14191 | 0.21057 | 0.11444 | 0.16479 | 0.068665 | 0.10986 | 121.55 | 0.096131 | 121.3943 | 121.344 | 121.344 | 121.4584 | 121.3898 | -121.4996 | -121.5683 | 121.6644 | 121.4401 | 5.9006 | 2.7374
1446.4062 | 121.7285 | -0.21515 | 121.431 | 0.055313 | 0 | 0.066031 | 0.065851 | 0.0032685 | -0.002493 | 0.00061957 | 0.01239 | 0.00054904 | -1.3933 | 0.062461 | -0.0022046 | 0.010408 | 0.0014741 | 5.7129 | 121.2982 | -0.10071 | 121.4584 | 0.064087 | -0.073242 | -0.11902 | 2.4948 | 121.2067 | -0.14191 | 121.1655 | -0.068665 | -0.11444 | -0.059509 | 0.11444 | -0.13275 | 0.027466 | 0.27924 | 0.09613 | 0.14191 | -0.018311 | 0.027466 | 0.073242 | -0.2243 | -0.2655 | 0.14648 | 0.15564 | 0.10071 | 0.082398 | 0.027466 | 0.1648 | 121.5591 | 0.073242 | 121.3074 | 121.3989 | 121.3486 | 121.5134 | 121.4218 | -121.5317 | -121.5729 | 121.6736 | 121.3806 | 5.928 | 2.71
1448.1719 | 121.7697 | -0.18768 | 121.4035 | -0.0057221 | 0 | 0.064749 | 0.06222 | -0.0016449 | -0.00099764 | 0.00083317 | 0.021545 | 0.0041806 | -1.3927 | 0.062248 | -0.0015638 | 0.010621 | -0.0038665 | 5.7312 | 121.2799 | -0.073242 | 121.4676 | 0.073242 | -0.082397 | -0.086975 | 2.5635 | 121.2158 | -0.16937 | 121.2158 | -0.009155 | -0.07782 | -0.009155 | 0.11444 | -0.1236 | 0.064087 | 0.26092 | 0.10071 | 0.10529 | -0.013733 | -0.009155 | 0.01831 | -0.18768 | -0.18768 | 0.17853 | 0.17853 | 0.10986 | 0.16022 | 0.091553 | 0.14648 | 121.5408 | 0.16022 | 121.3852 | 121.3531 | 121.3852 | 121.4676 | 121.4035 | -121.4767 | -121.5729 | 121.6553 | 121.4035 | 5.9189 | 2.7512
1449.875 | 121.7697 | -0.20142 | 121.4493 | -0.0057221 | 0 | 0.062186 | 0.062647 | 0.00027771 | -0.0044156 | -0.0017304 | 0.0032349 | -9.1956e-05 | -1.3957 | 0.062888 | -0.0051954 | 0.010194 | -0.0010895 | 5.7495 | 121.2433 | -0.10529 | 121.4584 | 0.059509 | -0.064087 | -0.10529 | 2.536 | 121.2067 | -0.15564 | 121.2021 | -0.013733 | -0.050354 | -0.004578 | 0.09613 | -0.20599 | 0.009155 | 0.26093 | 0.09613 | 0.13733 | 0 | 0.041199 | 0.045776 | -0.24262 | -0.24719 | 0.18768 | 0.19684 | 0.15106 | 0.15106 | 0.10529 | 0.16479 | 121.5637 | 0.14191 | 121.3577 | 121.3486 | 121.3623 | 121.4447 | 121.4081 | -121.5546 | -121.6049 | 121.6599 | 121.4035 | 5.9509 | 2.7374
1451.5781 | 121.7148 | -0.2243 | 121.3943 | 0.040054 | 0 | 0.065817 | 0.064356 | 0.0011321 | -0.0020658 | 0.0016876 | 0.018494 | 0.0020444 | -1.394 | 0.070579 | -0.0028454 | 0.011689 | 0.0012603 | 5.8182 | 121.2799 | -0.10986 | 121.4676 | 0.082397 | -0.054932 | -0.086975 | 2.5314 | 121.2204 | -0.17395 | 121.17 | -0.07782 | -0.10071 | -0.059509 | 0.11444 | -0.11444 | 0.073242 | 0.3067 | 0.13733 | 0.16937 | 0.022888 | 0.054931 | 0.050354 | -0.17395 | -0.2243 | 0.14648 | 0.16479 | 0.1236 | 0.11444 | 0.073242 | 0.19226 | 121.5775 | 0.09613 | 121.344 | 121.3898 | 121.3943 | 121.5042 | 121.4447 | -121.5042 | -121.5683 | 121.6919 | 121.3943 | 6.0425 | 2.7557
1453.3281 | 121.6507 | -0.26093 | 121.4401 | 0.0095369 | 0 | 0.063895 | 0.06692 | 0.0039093 | -0.004202 | -0.00044863 | -0.0028687 | 0.003967 | -1.3957 | 0.06182 | -0.003059 | 0.011049 | -0.0010895 | 5.7541 | 121.3165 | -0.1236 | 121.3486 | -0.09613 | -0.20599 | -0.21515 | 2.3987 | 121.2479 | -0.16937 | 121.1105 | -0.16479 | -0.20142 | -0.10529 | 0.13733 | -0.1236 | -0.091553 | 0.1648 | 0.045776 | 0.054931 | -0.091553 | -0.082398 | 0.091552 | -0.19226 | -0.32959 | 0.09613 | 0.15564 | 0.059509 | 0.064087 | -0.032043 | 0.027466 | 121.4722 | 0.004578 | 121.2799 | 121.4401 | 121.4172 | 121.5775 | 121.5088 | -121.5637 | -121.6095 | 121.6095 | 121.3715 | 6.015 | 2.6596
1455.0469 | 121.7926 | -0.19226 | 121.3989 | -0.0057221 | 0 | 0.061331 | 0.063715 | 0.0066863 | -0.0037746 | -0.0023712 | -0.0059205 | 0.0028988 | -1.3963 | 0.072074 | -0.0034864 | 0.0078443 | 0.0016877 | 5.8182 | 121.2479 | -0.086975 | 121.4859 | 0.091553 | -0.018311 | -0.068665 | 2.5635 | 121.2067 | -0.15564 | 121.225 | 0 | -0.027466 | -0.004578 | 0.10529 | -0.15106 | 0.086975 | 0.28381 | 0.1236 | 0.17395 | 0.01831 | 0.068664 | 0.036621 | -0.19226 | -0.17395 | 0.19226 | 0.18768 | 0.16479 | 0.15106 | 0.12817 | 0.17853 | 121.5729 | 0.15564 | 121.3806 | 121.3348 | 121.3623 | 121.4401 | 121.3989 | -121.4859 | -121.5546 | 121.6782 | 121.4172 | 6.0104 | 2.7557
1456.8125 | 121.6415 | -0.27008 | 121.431 | -0.0057221 | 0 | 0.062399 | 0.066279 | -0.0033539 | -0.00078404 | -2.1434e-05 | 0.0032349 | 0.0037532 | -1.3952 | 0.062888 | -0.0032728 | 0.010408 | 0.0029693 | 5.8273 | 121.312 | -0.12817 | 121.3348 | -0.09613 | -0.21515 | -0.23804 | 2.3804 | 121.2341 | -0.19684 | 121.0922 | -0.18768 | -0.23804 | -0.11444 | 0.14191 | -0.11902 | -0.09613 | 0.17395 | 0.032044 | 0.054932 | -0.10986 | -0.086975 | 0.073243 | -0.19684 | -0.33875 | 0.082398 | 0.15564 | 0.032044 | 0.082397 | -0.041199 | 0.032044 | 121.463 | 0.009155 | 121.2891 | 121.4401 | 121.431 | 121.582 | 121.5042 | -121.5591 | -121.6278 | 121.6049 | 121.3623 | 6.0974 | 2.6505
1458.5781 | 121.756 | -0.19684 | 121.4081 | 0.0019074 | 0 | 0.06304 | 0.060511 | 0.0032685 | -0.0016384 | -0.0025848 | -0.0059205 | 0.0018306 | -1.3946 | 0.061607 | -0.0060498 | 0.010194 | 0.00061949 | 5.9143 | 121.2433 | -0.10071 | 121.4951 | 0.091553 | -0.045776 | -0.10071 | 2.5772 | 121.2204 | -0.14648 | 121.2021 | -0.018311 | -0.059509 | -0.032043 | 0.09613 | -0.16479 | 0.086975 | 0.28839 | 0.09613 | 0.15106 | 0 | 0.054932 | 0.050354 | -0.18768 | -0.20599 | 0.17853 | 0.1648 | 0.13733 | 0.11444 | 0.086975 | 0.19226 | 121.5958 | 0.12817 | 121.3486 | 121.344 | 121.3669 | 121.4401 | 121.4172 | -121.5088 | -121.5546 | 121.6919 | 121.3989 | 6.1111 | 2.774
1460.2656 | 121.6324 | -0.24261 | 121.4493 | 0.0019074 | 0 | 0.063467 | 0.064356 | 0.0069001 | -0.0029202 | -2.1434e-05 | 0.0032349 | 0.001617 | -1.3944 | 0.065452 | -0.0041272 | 0.0099805 | 0.0012603 | 5.9052 | 121.2891 | -0.10986 | 121.3852 | -0.045776 | -0.17853 | -0.21973 | 2.4811 | 121.2524 | -0.16937 | 121.1105 | -0.15564 | -0.21973 | -0.11902 | 0.13275 | -0.16022 | -0.064087 | 0.19684 | 0.022888 | 0.064087 | -0.10986 | -0.068665 | 0.073242 | -0.19684 | -0.33875 | 0.086975 | 0.1236 | 0.022888 | 0.050354 | -0.050354 | 0.064087 | 121.4951 | 0.013733 | 121.2799 | 121.3989 | 121.4218 | 121.5317 | 121.4951 | -121.5591 | -121.6187 | 121.6278 | 121.3531 | 6.1478 | 2.7237
1462.0312 | 121.7834 | -0.20142 | 121.4081 | 0.0019074 | 0 | 0.061972 | 0.061793 | -0.0014313 | -0.0033474 | -0.00044863 | -0.0059205 | 0.00097624 | -1.395 | 0.065452 | -0.005409 | 0.0099805 | -0.00023491 | 5.8868 | 121.2799 | -0.082397 | 121.4676 | 0.07782 | -0.041199 | -0.09613 | 2.5864 | 121.1975 | -0.16022 | 121.225 | 0 | -0.041199 | -0.013733 | 0.11902 | -0.12817 | 0.059509 | 0.27924 | 0.10529 | 0.16022 | -0.013733 | 0.041198 | 0.041199 | -0.21057 | -0.1831 | 0.20142 | 0.18768 | 0.16022 | 0.14648 | 0.11902 | 0.16022 | 121.55 | 0.16022 | 121.3852 | 121.3623 | 121.3577 | 121.4813 | 121.3989 | -121.4905 | -121.5683 | 121.669 | 121.4264 | 6.0883 | 2.7878
1463.7344 | 121.701 | -0.21973 | 121.4081 | 0.024795 | 0 | 0.063467 | 0.064142 | -0.0016449 | -0.00099764 | 0.00083317 | 0.00018312 | 0.00097624 | -1.3946 | 0.068443 | -0.0037 | 0.0095533 | 0.0038239 | 5.8685 | 121.257 | -0.091553 | 121.4355 | 0.013733 | -0.10986 | -0.14648 | 2.4628 | 121.2112 | -0.16937 | 121.1655 | -0.10529 | -0.13733 | -0.073242 | 0.12817 | -0.15106 | 0.027466 | 0.23346 | 0.073243 | 0.10986 | -0.054931 | -0.01831 | 0.050354 | -0.19684 | -0.24262 | 0.11444 | 0.14649 | 0.082398 | 0.096131 | 0.032044 | 0.10529 | 121.5271 | 0.064087 | 121.3348 | 121.3486 | 121.3806 | 121.4767 | 121.431 | -121.4996 | -121.5775 | 121.6553 | 121.3852 | 6.0883 | 2.6825
1465.5 | 121.6782 | -0.25177 | 121.4493 | 0.024795 | 0 | 0.062827 | 0.066065 | 0.0066863 | 7.0564e-05 | -0.003012 | 0.015442 | 0.0043942 | -1.3957 | 0.062888 | -0.0049818 | 0.010621 | -0.0027985 | 5.9418 | 121.3028 | -0.14648 | 121.3943 | -0.036621 | -0.11902 | -0.19226 | 2.4673 | 121.2845 | -0.21515 | 121.1014 | -0.12817 | -0.17395 | -0.10071 | 0.10529 | -0.14648 | -0.054932 | 0.21515 | 0.059509 | 0.13275 | -0.045777 | 0.027465 | 0.036621 | -0.16479 | -0.3479 | 0.1236 | 0.15106 | 0.07782 | 0.11444 | 0.041199 | 0.10986 | 121.5408 | 0.086975 | 121.3165 | 121.4493 | 121.4996 | 121.5546 | 121.5363 | -121.5958 | -121.6644 | 121.6461 | 121.3531 | 6.1935 | 2.7191
1467.2812 | 121.6278 | -0.25635 | 121.4584 | 0.0095369 | 0 | 0.062827 | 0.061793 | -0.0044221 | -0.0027066 | -0.00066223 | 0.00018312 | 0.001617 | -1.3942 | 0.062675 | -0.0056226 | 0.0086987 | 0.0025421 | 5.9097 | 121.3028 | -0.12817 | 121.3531 | -0.068665 | -0.16479 | -0.19226 | 2.4307 | 121.2296 | -0.1831 | 121.0739 | -0.16479 | -0.19226 | -0.12817 | 0.12817 | -0.15564 | -0.10529 | 0.18768 | 0.064087 | 0.091553 | -0.064087 | -0.036621 | 0.073243 | -0.22888 | -0.38452 | 0.091553 | 0.12817 | 0.064087 | 0.054931 | -0.009156 | 0.059509 | 121.4813 | 0.01831 | 121.257 | 121.431 | 121.4127 | 121.5591 | 121.4859 | -121.5866 | -121.6415 | 121.6095 | 121.3303 | 6.1661 | 2.6871
1468.9844 | 121.7239 | -0.2243 | 121.4172 | 0.017166 | 0 | 0.063681 | 0.06457 | 0.00091851 | -0.00078404 | 0.00019217 | 0.0032349 | 0.0024716 | -1.3952 | 0.065879 | -0.0037 | 0.0082715 | -0.0025849 | 5.9189 | 121.2524 | -0.10529 | 121.4081 | 0.004578 | -0.10986 | -0.15106 | 2.4673 | 121.2112 | -0.14648 | 121.1655 | -0.073242 | -0.10529 | -0.050354 | 0.11902 | -0.16479 | -0.009155 | 0.22888 | 0.073242 | 0.11444 | -0.045776 | -0.004577 | 0.07782 | -0.20599 | -0.25177 | 0.15106 | 0.17395 | 0.11902 | 0.09613 | 0.041198 | 0.10986 | 121.5134 | 0.073242 | 121.3119 | 121.3577 | 121.3577 | 121.4767 | 121.4355 | -121.5225 | -121.5637 | 121.6324 | 121.3898 | 6.1432 | 2.6917
1470.7656 | 121.6324 | -0.24719 | 121.463 | -0.0057221 | 0 | 0.063467 | 0.064356 | 0.00070491 | -0.0046292 | -2.1434e-05 | 0.018494 | 0.0061032 | -1.3935 | 0.061393 | -0.0066906 | 0.0078443 | 0.00019229 | 5.9418 | 121.2891 | -0.15106 | 121.3486 | -0.059509 | -0.14191 | -0.16937 | 2.4673 | 121.2616 | -0.19684 | 121.0831 | -0.15106 | -0.19684 | -0.1236 | 0.09613 | -0.17395 | -0.11444 | 0.18768 | 0.077819 | 0.10528 | -0.018311 | 0.009155 | 0.050354 | -0.20142 | -0.37994 | 0.09613 | 0.1236 | 0.050354 | 0.073242 | 0 | 0.091553 | 121.4996 | 0.045776 | 121.2799 | 121.4401 | 121.4584 | 121.5363 | 121.5088 | -121.6141 | -121.6599 | 121.5958 | 121.3303 | 6.189 | 2.7145
1472.4531 | 121.7697 | -0.1831 | 121.4127 | 0.0019074 | 0 | 0.063895 | 0.066065 | 0.0022003 | 0.00028416 | 0.00040597 | 0.021545 | 0.0026852 | -1.3929 | 0.063743 | -0.001991 | 0.012971 | 0.0023285 | 5.9463 | 121.2524 | -0.059509 | 121.4996 | 0.11902 | -0.041199 | -0.082397 | 2.5772 | 121.2158 | -0.15564 | 121.2204 | -0.027466 | -0.07782 | -0.018311 | 0.1236 | -0.16022 | 0.086975 | 0.30212 | 0.10071 | 0.14191 | -0.022888 | 0.01831 | 0.027465 | -0.19684 | -0.19226 | 0.15564 | 0.16479 | 0.10528 | 0.13733 | 0.07782 | 0.17853 | 121.5591 | 0.12817 | 121.376 | 121.312 | 121.3715 | 121.4355 | 121.3989 | -121.4722 | -121.5683 | 121.6827 | 121.4035 | 6.1295 | 2.7603
1474.2344 | 121.756 | -0.21973 | 121.4127 | -0.013352 | 0 | 0.062613 | 0.061793 | -0.00079049 | -0.0020658 | -2.1434e-05 | -0.0028687 | 0.00033544 | -1.3961 | 0.062461 | -0.0058362 | 0.0093397 | -0.0015167 | 5.928 | 121.257 | -0.073242 | 121.4859 | 0.07782 | -0.036621 | -0.086975 | 2.5452 | 121.1975 | -0.13275 | 121.2112 | -0.004578 | -0.045776 | -0.018311 | 0.14649 | -0.15564 | 0.073242 | 0.29755 | 0.13275 | 0.18311 | -0.013733 | 0.036621 | 0.086976 | -0.21515 | -0.20142 | 0.21515 | 0.20142 | 0.17395 | 0.11444 | 0.086975 | 0.15106 | 121.5591 | 0.12817 | 121.344 | 121.3303 | 121.3303 | 121.4767 | 121.4172 | -121.4859 | -121.5454 | 121.7056 | 121.431 | 6.1478 | 2.7649
1476 | 121.756 | -0.19226 | 121.4081 | 0.0019074 | 0 | 0.061331 | 0.06457 | 0.0043365 | -0.002493 | -0.00044863 | -0.0028687 | 0.0024716 | -1.3957 | 0.062888 | -0.00049559 | 0.010194 | -0.0019439 | 5.8731 | 121.2708 | -0.10071 | 121.4172 | -0.004578 | -0.13733 | -0.16022 | 2.4811 | 121.2158 | -0.15564 | 121.2112 | -0.036621 | -0.10529 | -0.027466 | 0.091553 | -0.13733 | 0.009155 | 0.18768 | 0.032044 | 0.054932 | -0.059509 | -0.036621 | 0.036621 | -0.19226 | -0.19684 | 0.15564 | 0.16479 | 0.086975 | 0.12817 | 0.050354 | 0.09613 | 121.5179 | 0.11902 | 121.3669 | 121.3715 | 121.3715 | 121.463 | 121.4081 | -121.5088 | -121.5637 | 121.6095 | 121.4035 | 6.0654 | 2.6733
1477.7031 | 121.7789 | -0.19226 | 121.4127 | -0.0057221 | 0 | 0.061545 | 0.065211 | 0.0026275 | -0.00057044 | -0.0032256 | -0.0059205 | -0.00030556 | -1.3965 | 0.065238 | -0.0024182 | 0.012544 | -0.00044851 | 5.9326 | 121.2708 | -0.068665 | 121.463 | 0.054932 | -0.086975 | -0.1236 | 2.536 | 121.1929 | -0.13275 | 121.2387 | -0.027466 | -0.07782 | -0.009155 | 0.1236 | -0.14191 | 0.050354 | 0.24719 | 0.068665 | 0.10529 | -0.054931 | -0.01831 | 0.05951 | -0.21973 | -0.17395 | 0.16479 | 0.18311 | 0.11444 | 0.1236 | 0.054931 | 0.1236 | 121.5317 | 0.10529 | 121.3715 | 121.3394 | 121.3257 | 121.463 | 121.3852 | -121.4813 | -121.5454 | 121.6553 | 121.431 | 6.1249 | 2.7283
1479.4688 | 121.7606 | -0.18768 | 121.4035 | 0.0019074 | 0 | 0.061545 | 0.062006 | -0.0029267 | -0.00099764 | -0.0010894 | 0.00018312 | -9.1956e-05 | -1.3952 | 0.062888 | -0.0017774 | 0.01233 | -0.00044851 | 6.1295 | 121.2799 | -0.064087 | 121.4951 | 0.082397 | -0.091553 | -0.1236 | 2.5452 | 121.2021 | -0.14648 | 121.2341 | -0.027466 | -0.082397 | 0 | 0.1236 | -0.1236 | 0.091553 | 0.27008 | 0.064087 | 0.09613 | -0.059509 | -0.027466 | 0.041199 | -0.20142 | -0.16937 | 0.16022 | 0.18768 | 0.10529 | 0.14648 | 0.064087 | 0.14648 | 121.5591 | 0.11902 | 121.3806 | 121.344 | 121.3486 | 121.4676 | 121.3898 | -121.4676 | -121.55 | 121.6827 | 121.4218 | 6.3171 | 2.7328
1481.1719 | 121.6873 | -0.20142 | 121.4172 | 0.0019074 | 0 | 0.065176 | 0.066706 | 0.0024139 | -0.0029202 | -0.00066223 | -0.0059205 | 0.00097624 | -1.3955 | 0.065025 | -0.0024182 | 0.010621 | -2.1314e-05 | 6.0654 | 121.3165 | -0.11902 | 121.3715 | -0.050354 | -0.17395 | -0.20142 | 2.4399 | 121.2158 | -0.17853 | 121.17 | -0.10529 | -0.13733 | -0.064087 | 0.082397 | -0.10071 | -0.045776 | 0.15106 | 0 | 0.027466 | -0.082397 | -0.054931 | 0.022888 | -0.20142 | -0.24719 | 0.09613 | 0.13733 | 0.064087 | 0.11444 | 0.041199 | 0.068665 | 121.4905 | 0.073242 | 121.3486 | 121.4355 | 121.3943 | 121.5179 | 121.4172 | -121.5363 | -121.5958 | 121.5729 | 121.3715 | 6.2668 | 2.6413
1482.9375 | 121.7194 | -0.21057 | 121.4355 | -0.0057221 | 0 | 0.062613 | 0.062861 | -0.0010041 | -0.0020658 | -0.00066223 | 0.00018312 | 0.0014034 | -1.3944 | 0.063316 | -0.006477 | 0.0093397 | -0.0015167 | 6.189 | 121.2433 | -0.07782 | 121.4813 | 0.07782 | -0.054932 | -0.10986 | 2.5314 | 121.2158 | -0.15564 | 121.1884 | -0.045776 | -0.091553 | -0.036621 | 0.13275 | -0.19226 | 0.045776 | 0.28839 | 0.10071 | 0.15564 | -0.032043 | 0.022888 | 0.054931 | -0.21973 | -0.24719 | 0.1648 | 0.17395 | 0.11902 | 0.11902 | 0.064087 | 0.15564 | 121.5591 | 0.10986 | 121.344 | 121.3211 | 121.3715 | 121.4539 | 121.4264 | -121.5134 | -121.5912 | 121.6919 | 121.3989 | 6.3995 | 2.742
1484.6719 | 121.6827 | -0.23804 | 121.463 | -0.013352 | 0 | 0.063467 | 0.062006 | -0.0027131 | -0.0048428 | 0.00040597 | -0.0028687 | 0.0020444 | -1.3959 | 0.06652 | -0.0051954 | 0.0099805 | -0.0042939 | 6.1981 | 121.2479 | -0.10071 | 121.4539 | 0.045776 | -0.07782 | -0.1236 | 2.5131 | 121.2204 | -0.14191 | 121.138 | -0.10529 | -0.13275 | -0.082397 | 0.13733 | -0.21515 | -0.009156 | 0.28381 | 0.11444 | 0.16022 | -0.022888 | 0.022888 | 0.09613 | -0.24262 | -0.32501 | 0.13275 | 0.15564 | 0.10529 | 0.05951 | 0.009156 | 0.14648 | 121.5546 | 0.036621 | 121.2799 | 121.3486 | 121.3623 | 121.4859 | 121.4584 | -121.5637 | -121.6049 | 121.6919 | 121.376 | 6.4362 | 2.7512
1486.4375 | 121.6232 | -0.25635 | 121.463 | -0.0057221 | 0 | 0.062186 | 0.065424 | -0.0020721 | -0.0020658 | -0.001303 | 0.00018312 | 0.003967 | -1.3948 | 0.059257 | -0.003059 | 0.0097669 | -0.0021575 | 6.1707 | 121.2753 | -0.10529 | 121.3577 | -0.07782 | -0.19226 | -0.21515 | 2.3987 | 121.2616 | -0.16479 | 121.0968 | -0.17395 | -0.24261 | -0.13275 | 0.15106 | -0.18768 | -0.10529 | 0.17853 | 0.041199 | 0.064087 | -0.10986 | -0.086975 | 0.091553 | -0.20142 | -0.36621 | 0.082398 | 0.1236 | 0.013733 | 0.032044 | -0.07782 | 0.027466 | 121.463 | -0.009155 | 121.2616 | 121.3806 | 121.4264 | 121.5317 | 121.5179 | -121.5683 | -121.6278 | 121.6141 | 121.3531 | 6.427 | 2.655
1488.1406 | 121.6461 | -0.23804 | 121.4584 | 0.040054 | 0 | 0.063895 | 0.06457 | 0.0019867 | -0.0039884 | -0.0034392 | 0.015442 | 0.0048214 | -1.3937 | 0.061179 | -0.0069044 | 0.0086987 | -0.0055755 | 6.2302 | 121.3257 | -0.17853 | 121.3898 | -0.036621 | -0.14191 | -0.1831 | 2.4628 | 121.2753 | -0.19226 | 121.1014 | -0.15564 | -0.19226 | -0.10529 | 0.059509 | -0.13275 | -0.068664 | 0.20142 | 0.054932 | 0.09613 | -0.004577 | 0.036621 | 0.045776 | -0.1831 | -0.35706 | 0.082397 | 0.13275 | 0.045776 | 0.086975 | 0 | 0.14191 | 121.5683 | 0.036621 | 121.2936 | 121.5042 | 121.4676 | 121.5637 | 121.5134 | -121.637 | -121.6507 | 121.6278 | 121.3394 | 6.4682 | 2.7008
1489.9062 | 121.7285 | -0.20599 | 121.4081 | 0.0019074 | 0 | 0.064749 | 0.063074 | -0.0018585 | -0.0016384 | -0.0040802 | 0.0062865 | 0.00054904 | -1.3935 | 0.063957 | -0.003059 | 0.010194 | 0.0010467 | 6.2164 | 121.3074 | -0.10986 | 121.4264 | 0.013733 | -0.10529 | -0.14191 | 2.4857 | 121.1975 | -0.15106 | 121.1655 | -0.068665 | -0.10071 | -0.050354 | 0.096131 | -0.10071 | 0.018311 | 0.21973 | 0.064087 | 0.10071 | -0.032044 | 0.004577 | 0.054932 | -0.21057 | -0.24262 | 0.13733 | 0.15564 | 0.10529 | 0.10071 | 0.050354 | 0.1236 | 121.5363 | 0.082397 | 121.3165 | 121.4172 | 121.3486 | 121.5134 | 121.4035 | -121.5179 | -121.5591 | 121.6324 | 121.3715 | 6.4224 | 2.6917
1491.6094 | 121.7651 | -0.20599 | 121.4447 | -0.0057221 | 0 | 0.061331 | 0.062647 | -0.0022857 | -0.00527 | 0.0016876 | -0.0089723 | 0.00054904 | -1.3957 | 0.057121 | -0.0041272 | 0.0091261 | -0.00066231 | 6.3309 | 121.2204 | -0.068665 | 121.4951 | 0.12817 | -0.027466 | -0.045776 | 2.6138 | 121.1975 | -0.14191 | 121.2341 | 0.004578 | -0.036621 | -0.013733 | 0.13733 | -0.2243 | 0.050354 | 0.33417 | 0.16022 | 0.17853 | 0.022889 | 0.041199 | 0.064087 | -0.24719 | -0.21057 | 0.21057 | 0.19226 | 0.16937 | 0.12817 | 0.10529 | 0.19684 | 121.5637 | 0.14649 | 121.376 | 121.2891 | 121.3394 | 121.4264 | 121.4035 | -121.5134 | -121.5866 | 121.7011 | 121.4401 | 6.5369 | 2.8198
1493.375 | 121.756 | -0.19226 | 121.4081 | 0.0019074 | 0 | 0.062613 | 0.062861 | -0.0018585 | -0.0039884 | -0.00087583 | -0.0028687 | 0.0014034 | -1.3969 | 0.062888 | -0.0011364 | 0.011262 | -0.0030121 | 6.3721 | 121.2616 | -0.073242 | 121.4539 | 0.054932 | -0.086975 | -0.1236 | 2.5406 | 121.1975 | -0.13275 | 121.2296 | -0.036621 | -0.086975 | 0.004578 | 0.11902 | -0.14648 | 0.045776 | 0.24719 | 0.068665 | 0.10529 | -0.050354 | -0.013733 | 0.05951 | -0.21057 | -0.17853 | 0.15564 | 0.19684 | 0.10529 | 0.13733 | 0.045776 | 0.12817 | 121.5271 | 0.09613 | 121.3623 | 121.3348 | 121.3303 | 121.4539 | 121.3898 | -121.4813 | -121.5408 | 121.6461 | 121.4218 | 6.5643 | 2.7328
1495.0781 | 121.6782 | -0.24261 | 121.4218 | 0.0095369 | 0 | 0.064963 | 0.064356 | 0.00027771 | 0.00071136 | 0.002115 | 0.0093383 | 0.0054622 | -1.3931 | 0.05883 | -0.0041272 | 0.0095533 | -0.0023713 | 6.427 | 121.3028 | -0.11444 | 121.4264 | 0.022888 | -0.10986 | -0.16479 | 2.5497 | 121.2387 | -0.17853 | 121.1517 | -0.09613 | -0.15106 | -0.073242 | 0.12817 | -0.11902 | 0.004578 | 0.2655 | 0.07782 | 0.13275 | -0.050354 | 0.004578 | 0.064087 | -0.18311 | -0.27008 | 0.14649 | 0.16937 | 0.091553 | 0.10529 | 0.027466 | 0.13733 | 121.5408 | 0.082398 | 121.3303 | 121.4172 | 121.4172 | 121.5454 | 121.4813 | -121.5363 | -121.6003 | 121.669 | 121.3943 | 6.6696 | 2.7924
1496.8438 | 121.6782 | -0.24261 | 121.463 | 0.032425 | 0 | 0.063895 | 0.064997 | 0.00027771 | -0.0027066 | 0.0010468 | 0.01239 | 0.0048214 | -1.3955 | 0.059257 | -0.0045544 | 0.0099805 | -0.00044851 | 6.4453 | 121.3394 | -0.14191 | 121.4035 | -0.027466 | -0.11902 | -0.16022 | 2.4994 | 121.2799 | -0.18768 | 121.1288 | -0.10529 | -0.16479 | -0.082397 | 0.10071 | -0.1236 | -0.05951 | 0.21515 | 0.082398 | 0.1236 | -0.01831 | 0.022888 | 0.054932 | -0.18311 | -0.33417 | 0.13733 | 0.16022 | 0.07782 | 0.10529 | 0.022888 | 0.11444 | 121.5454 | 0.082397 | 121.3165 | 121.4813 | 121.4676 | 121.582 | 121.5225 | -121.6049 | -121.6507 | 121.6461 | 121.3715 | 6.6879 | 2.742
1498.5469 | 121.7056 | -0.2243 | 121.4539 | 0.017166 | 0 | 0.065176 | 0.065424 | -0.00036309 | -0.0020658 | 0.00083317 | 0.0062865 | 0.0026852 | -1.3952 | 0.060539 | -0.004768 | 0.010194 | -0.0045075 | 6.4774 | 121.3028 | -0.11902 | 121.4172 | 0.013733 | -0.10529 | -0.14648 | 2.5406 | 121.2204 | -0.17853 | 121.1609 | -0.091553 | -0.14191 | -0.059509 | 0.10529 | -0.15106 | -0.036621 | 0.23804 | 0.07782 | 0.11902 | -0.027465 | 0.013733 | 0.045776 | -0.23346 | -0.29297 | 0.13275 | 0.16479 | 0.082397 | 0.11902 | 0.036621 | 0.13275 | 121.5363 | 0.086975 | 121.3394 | 121.4218 | 121.3989 | 121.5271 | 121.4447 | -121.5729 | -121.6324 | 121.6415 | 121.3852 | 6.7017 | 2.7649
1500.3125 | 121.669 | -0.23346 | 121.4447 | 0.017166 | 0 | 0.063254 | 0.06457 | 0.0036957 | -0.0039884 | -0.0021576 | 0.0093383 | 0.0041806 | -1.3952 | 0.057334 | -0.0051954 | 0.011689 | -0.00044851 | 6.4865 | 121.2936 | -0.10986 | 121.4081 | -0.004578 | -0.11444 | -0.15564 | 2.5497 | 121.2616 | -0.16937 | 121.1563 | -0.09613 | -0.14191 | -0.064087 | 0.1236 | -0.15106 | -0.036621 | 0.22888 | 0.077819 | 0.11902 | -0.045777 | -0.004578 | 0.064086 | -0.18311 | -0.28839 | 0.13733 | 0.16937 | 0.091552 | 0.10529 | 0.027466 | 0.10529 | 121.5179 | 0.073243 | 121.3257 | 121.4035 | 121.431 | 121.5271 | 121.4951 | -121.5546 | -121.6141 | 121.6415 | 121.3898 | 6.72 | 2.7832
1502.0781 | 121.6919 | -0.23804 | 121.431 | 0.0019074 | 0 | 0.062399 | 0.06457 | 0.00027771 | -0.0033474 | -0.0027984 | 0.00018312 | 0.0026852 | -1.392 | 0.059043 | -0.0015638 | 0.011689 | -0.0021575 | 6.427 | 121.3348 | -0.13275 | 121.3623 | -0.068665 | -0.18768 | -0.21515 | 2.4445 | 121.257 | -0.1831 | 121.1334 | -0.13275 | -0.17395 | -0.086975 | 0.10529 | -0.09613 | -0.068664 | 0.16937 | 0.022888 | 0.050354 | -0.082398 | -0.054932 | 0.054932 | -0.17395 | -0.29755 | 0.10529 | 0.15106 | 0.064087 | 0.09613 | 0.009155 | 0.064086 | 121.4951 | 0.050354 | 121.3165 | 121.4676 | 121.4401 | 121.5729 | 121.4951 | -121.5637 | -121.6141 | 121.6003 | 121.3715 | 6.665 | 2.6825
1503.7812 | 121.7239 | -0.21057 | 121.4127 | 0.017166 | 0 | 0.062827 | 0.06222 | -0.0016449 | -0.0029202 | -0.00066223 | 0.00018312 | -0.00051916 | -1.3969 | 0.067161 | -0.0039136 | 0.0097669 | 0.0014741 | 6.4499 | 121.2799 | -0.11444 | 121.4127 | 0.004578 | -0.10986 | -0.14191 | 2.5085 | 121.2067 | -0.16022 | 121.17 | -0.07782 | -0.10529 | -0.041199 | 0.09613 | -0.13275 | 0 | 0.21515 | 0.068664 | 0.10071 | -0.027466 | 0.004578 | 0.050354 | -0.20599 | -0.24262 | 0.13275 | 0.16937 | 0.10529 | 0.11902 | 0.054931 | 0.11902 | 121.5271 | 0.082397 | 121.3303 | 121.3943 | 121.3669 | 121.4905 | 121.4172 | -121.5271 | -121.5729 | 121.6232 | 121.3806 | 6.6605 | 2.7191
1505.5625 | 121.756 | -0.20142 | 121.4172 | 0.0019074 | 0 | 0.062399 | 0.065851 | -0.0022857 | -0.001852 | -0.003012 | -0.0059205 | 0.0018306 | -1.3967 | 0.066734 | -0.0024182 | 0.013185 | -0.0019439 | 6.4911 | 121.3074 | -0.086975 | 121.4081 | -0.009155 | -0.14191 | -0.16479 | 2.5177 | 121.2158 | -0.13275 | 121.2021 | -0.045776 | -0.086975 | -0.027466 | 0.11444 | -0.10986 | -0.009155 | 0.19226 | 0.036621 | 0.059509 | -0.07782 | -0.054932 | 0.068665 | -0.20142 | -0.21515 | 0.15564 | 0.17395 | 0.11444 | 0.10529 | 0.045776 | 0.07782 | 121.4951 | 0.086975 | 121.3348 | 121.3943 | 121.3486 | 121.5088 | 121.4172 | -121.5042 | -121.55 | 121.6095 | 121.4035 | 6.6925 | 2.7191
1507.3281 | 121.6599 | -0.25177 | 121.4539 | 0.062942 | 0 | 0.062399 | 0.065638 | -0.00014949 | -0.004202 | 0.00083317 | 0.015442 | 0.003326 | -1.3944 | 0.056053 | -0.007118 | 0.0097669 | 0.0012603 | 6.5552 | 121.3669 | -0.14191 | 121.3806 | -0.032043 | -0.12817 | -0.17853 | 2.4811 | 121.2708 | -0.19684 | 121.106 | -0.14191 | -0.17853 | -0.10986 | 0.10986 | -0.086975 | -0.073242 | 0.21973 | 0.073242 | 0.1236 | -0.036621 | 0.013733 | 0.054932 | -0.1831 | -0.3479 | 0.10986 | 0.14191 | 0.073242 | 0.086975 | 0.01831 | 0.10986 | 121.5225 | 0.054931 | 121.3028 | 121.5088 | 121.4676 | 121.6187 | 121.5225 | -121.5958 | -121.6507 | 121.6324 | 121.3577 | 6.8069 | 2.7328
1509.0156 | 121.7651 | -0.20142 | 121.431 | 0.0019074 | 0 | 0.06304 | 0.062861 | -0.0037811 | -0.0063382 | 0.00061957 | 0.018494 | 0.003326 | -1.3955 | 0.064384 | 0.00078621 | 0.013398 | -0.0047211 | 6.5781 | 121.2708 | -0.068665 | 121.4859 | 0.082397 | -0.064087 | -0.068665 | 2.6321 | 121.2479 | -0.16479 | 121.2433 | -0.013733 | -0.068665 | -0.004578 | 0.13275 | -0.16022 | 0.054932 | 0.28381 | 0.13275 | 0.13733 | 0 | 0.004578 | 0.036621 | -0.1831 | -0.18768 | 0.18768 | 0.19684 | 0.13275 | 0.16022 | 0.09613 | 0.15106 | 121.5546 | 0.15106 | 121.4081 | 121.3394 | 121.4127 | 121.4722 | 121.4493 | -121.4996 | -121.5958 | 121.6873 | 121.4447 | 6.7795 | 2.8336
1510.7969 | 121.7239 | -0.23346 | 121.4493 | 0.0095369 | 0 | 0.062827 | 0.062647 | 0.0015595 | -0.0014248 | 0.001474 | 0.00018312 | 0.002258 | -1.3967 | 0.059684 | -0.0034864 | 0.010835 | 0.0031829 | 6.5826 | 121.2799 | -0.11444 | 121.4264 | 0.032043 | -0.11444 | -0.12817 | 2.5177 | 121.2296 | -0.15564 | 121.1746 | -0.086975 | -0.11444 | -0.059509 | 0.11902 | -0.16937 | -0.022888 | 0.2655 | 0.10528 | 0.11902 | -0.013733 | 0 | 0.077819 | -0.21973 | -0.27466 | 0.14648 | 0.17395 | 0.11902 | 0.096131 | 0.041199 | 0.14648 | 121.5408 | 0.068665 | 121.3303 | 121.3943 | 121.3852 | 121.5134 | 121.463 | -121.5637 | -121.6049 | 121.6599 | 121.4081 | 6.8161 | 2.7512
1512.5 | 121.6599 | -0.22888 | 121.4539 | -0.0057221 | 0 | 0.064536 | 0.06692 | 0.00049131 | -0.002493 | -0.00044863 | -0.0028687 | 0.0037532 | -1.3965 | 0.066306 | -6.8386e-05 | 0.010621 | 0.0031829 | 6.6055 | 121.3211 | -0.1236 | 121.3577 | -0.07782 | -0.20142 | -0.21057 | 2.4445 | 121.2524 | -0.14648 | 121.1334 | -0.14191 | -0.19684 | -0.10071 | 0.10529 | -0.13275 | -0.09613 | 0.15106 | 0.018311 | 0.027466 | -0.086975 | -0.07782 | 0.082398 | -0.20142 | -0.32043 | 0.086975 | 0.12817 | 0.032044 | 0.045776 | -0.050354 | 0.045776 | 121.4813 | 0.004577 | 121.2799 | 121.4447 | 121.3989 | 121.55 | 121.4813 | -121.5775 | -121.6003 | 121.5866 | 121.3623 | 6.8344 | 2.6733
1514.2656 | 121.6461 | -0.23804 | 121.4539 | -0.013352 | 0 | 0.062186 | 0.065851 | -0.0033539 | -0.0044156 | -2.1434e-05 | 0.00018312 | 0.0020444 | -1.394 | 0.061393 | -0.0034864 | 0.011049 | 0.00083309 | 6.633 | 121.3257 | -0.10986 | 121.344 | -0.073242 | -0.20142 | -0.2243 | 2.4445 | 121.2753 | -0.16022 | 121.106 | -0.17395 | -0.21057 | -0.11444 | 0.12817 | -0.12817 | -0.10986 | 0.16479 | 0.013733 | 0.036621 | -0.11444 | -0.091553 | 0.07782 | -0.17853 | -0.3479 | 0.064087 | 0.1236 | 0.027466 | 0.045776 | -0.050354 | 0.036621 | 121.4539 | -0.013733 | 121.2662 | 121.4355 | 121.4355 | 121.5637 | 121.5134 | -121.5637 | -121.6141 | 121.582 | 121.344 | 6.871 | 2.6825
1516.0156 | 121.637 | -0.23804 | 121.463 | 0.0019074 | 0 | 0.062399 | 0.064356 | 0.0013459 | 7.0564e-05 | -0.0021576 | -0.0059205 | 0.0035396 | -1.3965 | 0.060111 | -0.001991 | 0.0099805 | -0.00087591 | 6.7017 | 121.344 | -0.10986 | 121.3577 | -0.059509 | -0.20142 | -0.2243 | 2.4124 | 121.2387 | -0.15106 | 121.0922 | -0.1831 | -0.23346 | -0.11444 | 0.12817 | -0.11902 | -0.10529 | 0.17853 | 0.013733 | 0.036621 | -0.11444 | -0.091553 | 0.086975 | -0.22431 | -0.37079 | 0.054932 | 0.1236 | 0.004578 | 0.036621 | -0.082397 | 0.050354 | 121.4676 | -0.032043 | 121.2433 | 121.4539 | 121.3898 | 121.582 | 121.4767 | -121.5729 | -121.6141 | 121.5958 | 121.3303 | 6.9397 | 2.6505
1517.7188 | 121.7697 | -0.18768 | 121.4035 | 0.0019074 | 0 | 0.064108 | 0.065211 | 0.0017731 | -0.00099764 | -0.001944 | -0.0028687 | 0.001617 | -1.3942 | 0.058189 | -0.0017774 | 0.012544 | -2.1314e-05 | 6.7337 | 121.3074 | -0.086975 | 121.4264 | 0.032043 | -0.10529 | -0.14648 | 2.5269 | 121.2479 | -0.13733 | 121.2158 | -0.036621 | -0.082397 | 0.004578 | 0.10071 | -0.09613 | 0.022889 | 0.21973 | 0.041199 | 0.082397 | -0.059509 | -0.018311 | 0.050354 | -0.15564 | -0.18768 | 0.15106 | 0.19226 | 0.10529 | 0.14191 | 0.054932 | 0.11902 | 121.5134 | 0.10071 | 121.3531 | 121.3943 | 121.3852 | 121.4951 | 121.4355 | -121.4905 | -121.5408 | 121.6141 | 121.4035 | 6.9214 | 2.7145
1519.4844 | 121.6278 | -0.25635 | 121.463 | -0.013352 | 0 | 0.063467 | 0.066065 | 0.0019867 | -0.0016384 | -0.001303 | -0.0028687 | 0.001617 | -1.3937 | 0.060539 | -0.0034864 | 0.010835 | 0.00061949 | 6.7657 | 121.3074 | -0.10986 | 121.3623 | -0.086975 | -0.21057 | -0.23346 | 2.4216 | 121.2616 | -0.16022 | 121.106 | -0.19226 | -0.22888 | -0.1236 | 0.14649 | -0.15564 | -0.10071 | 0.16937 | 0.022889 | 0.045777 | -0.1236 | -0.10071 | 0.096131 | -0.20142 | -0.35706 | 0.064087 | 0.13275 | 0.027466 | 0.036621 | -0.068665 | 0.022888 | 121.4722 | -0.032044 | 121.2662 | 121.4172 | 121.4218 | 121.5637 | 121.5179 | -121.5729 | -121.6232 | 121.6187 | 121.3623 | 7.0221 | 2.6779
1521.25 | 121.7789 | -0.18768 | 121.4218 | 0.0019074 | 0 | 0.065176 | 0.063288 | 0.0071137 | -0.0022794 | -0.0025848 | -0.0059205 | 0.0020444 | -1.3959 | 0.061393 | -0.0013502 | 0.011049 | -0.0030121 | 6.7978 | 121.2982 | -0.064087 | 121.4722 | 0.073242 | -0.068665 | -0.10986 | 2.5681 | 121.2067 | -0.13733 | 121.2387 | -0.022888 | -0.068665 | 0 | 0.1236 | -0.1236 | 0.050354 | 0.26092 | 0.07782 | 0.11902 | -0.045776 | -0.004578 | 0.050354 | -0.21515 | -0.18311 | 0.16479 | 0.18768 | 0.11902 | 0.13733 | 0.068664 | 0.13733 | 121.5363 | 0.11444 | 121.376 | 121.3623 | 121.344 | 121.4859 | 121.3943 | -121.4859 | -121.5591 | 121.6599 | 121.4264 | 6.9855 | 2.7557
1522.9531 | 121.6461 | -0.22888 | 121.4493 | -0.0057221 | 0 | 0.062186 | 0.062647 | -0.0010041 | -0.0029202 | -2.1434e-05 | 0.0032349 | 0.0028988 | -1.3955 | 0.063316 | -0.0079724 | 0.0089123 | -2.1314e-05 | 6.8298 | 121.2936 | -0.086975 | 121.4035 | -0.009155 | -0.10071 | -0.16937 | 2.504 | 121.2616 | -0.16022 | 121.106 | -0.1236 | -0.16022 | -0.11444 | 0.14191 | -0.15564 | -0.045777 | 0.21973 | 0.059509 | 0.12817 | -0.082398 | -0.013733 | 0.068665 | -0.18768 | -0.34332 | 0.10529 | 0.11444 | 0.068665 | 0.045776 | 0 | 0.07782 | 121.4905 | 0.036621 | 121.2662 | 121.3806 | 121.4218 | 121.5225 | 121.4905 | -121.5363 | -121.6095 | 121.6324 | 121.3348 | 7.0587 | 2.7328
1524.7344 | 121.6461 | -0.24261 | 121.4813 | -0.0057221 | 0 | 0.063254 | 0.062861 | 0.0032685 | -0.001852 | -0.0017304 | 0.00018312 | 0.001617 | -1.3933 | 0.062034 | -0.0026318 | 0.011689 | 0.00061949 | 6.8161 | 121.312 | -0.10071 | 121.3394 | -0.10071 | -0.19684 | -0.21057 | 2.4445 | 121.2616 | -0.16479 | 121.106 | -0.17853 | -0.21057 | -0.10986 | 0.14191 | -0.16937 | -0.14191 | 0.14191 | 0.032044 | 0.045777 | -0.10986 | -0.09613 | 0.07782 | -0.21973 | -0.37537 | 0.064087 | 0.13275 | 0.032044 | 0.054932 | -0.045776 | 0 | 121.4401 | -0.013733 | 121.2708 | 121.4127 | 121.4264 | 121.5546 | 121.5042 | -121.582 | -121.6461 | 121.582 | 121.3486 | 7.0587 | 2.6871
1526.4844 | 121.669 | -0.22888 | 121.4584 | 0.0019074 | 0 | 0.064749 | 0.063288 | -0.0029267 | -0.0029202 | 0.00061957 | 0.00018312 | 0.00054904 | -1.3944 | 0.063102 | -0.0024182 | 0.0076307 | 0.0010467 | 6.8207 | 121.3394 | -0.10071 | 121.344 | -0.064087 | -0.20599 | -0.21973 | 2.4582 | 121.257 | -0.16479 | 121.1472 | -0.14191 | -0.20142 | -0.09613 | 0.12817 | -0.11902 | -0.11444 | 0.16479 | 0.009155 | 0.022888 | -0.11902 | -0.10529 | 0.064087 | -0.20142 | -0.31128 | 0.086975 | 0.13275 | 0.027466 | 0.068665 | -0.036621 | 0.036621 | 121.4447 | 0.022888 | 121.312 | 121.4401 | 121.4218 | 121.5683 | 121.4859 | -121.5591 | -121.6232 | 121.5729 | 121.376 | 7.0496 | 2.6871
1528.1875 | 121.7194 | -0.21515 | 121.4218 | 0.032425 | 0 | 0.063467 | 0.064356 | -0.0022857 | -0.0014248 | -0.001944 | 0.0032349 | 0.0011898 | -1.3955 | 0.060752 | -0.001991 | 0.011903 | -0.00044851 | 6.8893 | 121.2982 | -0.10071 | 121.4218 | 0.022888 | -0.086975 | -0.13733 | 2.5085 | 121.2387 | -0.14648 | 121.1792 | -0.091553 | -0.10986 | -0.059509 | 0.11444 | -0.1236 | 0 | 0.23804 | 0.07782 | 0.12817 | -0.036621 | 0.013733 | 0.068665 | -0.18311 | -0.24262 | 0.1236 | 0.15564 | 0.10529 | 0.086975 | 0.036621 | 0.1236 | 121.5225 | 0.054931 | 121.3257 | 121.3989 | 121.3852 | 121.5134 | 121.4539 | -121.5225 | -121.5683 | 121.637 | 121.3943 | 7.1045 | 2.7237
1529.9531 | 121.6599 | -0.25635 | 121.4584 | -0.0057221 | 0 | 0.063467 | 0.06457 | 0.0019867 | -0.0029202 | 0.00019217 | -0.0028687 | 0.0028988 | -1.3946 | 0.065025 | -0.0056226 | 0.0091261 | -0.0047211 | 6.9443 | 121.2799 | -0.10071 | 121.431 | 0.027466 | -0.09613 | -0.14648 | 2.5177 | 121.2158 | -0.15106 | 121.1197 | -0.1236 | -0.15106 | -0.10986 | 0.15564 | -0.17853 | -0.027466 | 0.28381 | 0.10986 | 0.16022 | -0.045776 | 0.004578 | 0.10529 | -0.24262 | -0.33874 | 0.13275 | 0.14649 | 0.10529 | 0.041199 | 0 | 0.12817 | 121.5317 | 0.027466 | 121.2708 | 121.3806 | 121.3669 | 121.5363 | 121.4722 | -121.5591 | -121.6095 | 121.6873 | 121.376 | 7.2006 | 2.774
1531.7188 | 121.7606 | -0.17853 | 121.4172 | 0.062942 | 0 | 0.065817 | 0.064997 | 0.00070491 | -0.00035684 | 0.002115 | 0.015442 | 0.00076264 | -1.3942 | 0.062461 | -0.00092279 | 0.011903 | -2.1314e-05 | 6.9763 | 121.2936 | -0.10529 | 121.4951 | 0.11902 | -0.036621 | -0.073242 | 2.623 | 121.1975 | -0.16022 | 121.2387 | -0.041199 | -0.059509 | -0.022888 | 0.073242 | -0.1236 | 0.07782 | 0.29755 | 0.10529 | 0.14191 | 0.032044 | 0.068665 | 0.018311 | -0.21973 | -0.17853 | 0.13733 | 0.15564 | 0.11902 | 0.13733 | 0.10071 | 0.22431 | 121.6003 | 0.11902 | 121.3989 | 121.3989 | 121.3577 | 121.4722 | 121.376 | -121.5225 | -121.5775 | 121.6736 | 121.4172 | 7.1548 | 2.8015
1533.4688 | 121.7926 | -0.19226 | 121.4035 | 0.0019074 | 0 | 0.060904 | 0.063074 | -0.0033539 | -0.004202 | -0.0010894 | 0.00018312 | 0.00054904 | -1.3965 | 0.074638 | -0.0056226 | 0.010621 | 0.0012603 | 6.9626 | 121.2662 | -0.082397 | 121.4767 | 0.10071 | -0.036621 | -0.07782 | 2.6367 | 121.2158 | -0.13733 | 121.2524 | 0.022888 | -0.027466 | 0.004578 | 0.10986 | -0.13733 | 0.073243 | 0.29297 | 0.11444 | 0.15564 | 0.004577 | 0.045776 | 0.054932 | -0.18768 | -0.15106 | 0.21515 | 0.19684 | 0.16479 | 0.14191 | 0.10986 | 0.18311 | 121.5591 | 0.16022 | 121.3898 | 121.3486 | 121.3531 | 121.4584 | 121.4081 | -121.4859 | -121.5408 | 121.669 | 121.4447 | 7.1548 | 2.829
1535.25 | 121.7056 | -0.19684 | 121.4447 | -0.0057221 | 0 | 0.061758 | 0.065638 | -0.0035675 | -0.001852 | -0.0015166 | -0.0089723 | 0.0028988 | -1.395 | 0.065025 | -0.0026318 | 0.010408 | -0.0013031 | 6.9351 | 121.3211 | -0.10986 | 121.3715 | -0.050354 | -0.1831 | -0.20599 | 2.4765 | 121.2433 | -0.15106 | 121.1609 | -0.11902 | -0.17395 | -0.059509 | 0.086975 | -0.1236 | -0.073242 | 0.14648 | -0.009156 | 0.013733 | -0.096131 | -0.073242 | 0.045776 | -0.20142 | -0.28381 | 0.077819 | 0.13733 | 0.022888 | 0.091553 | -0.022888 | 0.059509 | 121.4813 | 0.032043 | 121.312 | 121.431 | 121.3943 | 121.5179 | 121.4401 | -121.5546 | -121.5958 | 121.5683 | 121.3577 | 7.132 | 2.6733
1536.9375 | 121.6324 | -0.25177 | 121.4539 | 0.0095369 | 0 | 0.061331 | 0.063074 | 0.0028411 | -0.0022794 | -0.0023712 | -0.0028687 | 0.0037532 | -1.394 | 0.060111 | -0.0086132 | 0.0095533 | -0.00087591 | 6.9763 | 121.3074 | -0.10986 | 121.344 | -0.050354 | -0.15106 | -0.1831 | 2.4857 | 121.225 | -0.16022 | 121.106 | -0.13275 | -0.19684 | -0.1236 | 0.14191 | -0.14648 | -0.10986 | 0.20142 | 0.068665 | 0.10071 | -0.073242 | -0.041199 | 0.091553 | -0.22888 | -0.3479 | 0.11902 | 0.12817 | 0.054932 | 0.036621 | -0.036621 | 0.059509 | 121.4539 | 0.027466 | 121.2662 | 121.4172 | 121.3852 | 121.5591 | 121.4767 | -121.5637 | -121.6141 | 121.5958 | 121.3577 | 7.2281 | 2.7374
1538.7031 | 121.7789 | -0.19226 | 121.4172 | -0.013352 | 0 | 0.06304 | 0.061793 | -0.0054901 | -0.0033474 | -0.00023503 | -0.0059205 | -0.00116 | -1.3946 | 0.063316 | -0.004768 | 0.0082715 | -0.00044851 | 7.0724 | 121.2662 | -0.086975 | 121.4905 | 0.1236 | -0.009155 | -0.068665 | 2.6184 | 121.2204 | -0.1236 | 121.2158 | -0.013733 | -0.045776 | -0.009155 | 0.10529 | -0.15106 | 0.073243 | 0.31586 | 0.1236 | 0.18311 | 0.01831 | 0.07782 | 0.068665 | -0.19684 | -0.20142 | 0.17853 | 0.18311 | 0.14648 | 0.11444 | 0.07782 | 0.21057 | 121.5775 | 0.10986 | 121.3394 | 121.3531 | 121.344 | 121.4584 | 121.4127 | -121.5042 | -121.5408 | 121.6827 | 121.4081 | 7.2647 | 2.8107
1540.4688 | 121.6324 | -0.25635 | 121.4584 | -0.0057221 | 0 | 0.060477 | 0.063929 | -0.0035675 | -0.0039884 | -0.003012 | 0.00018312 | 0.0024716 | -1.3952 | 0.059043 | -0.0060498 | 0.0093397 | -0.00044851 | 7.0312 | 121.3165 | -0.10071 | 121.3623 | -0.041199 | -0.15564 | -0.19226 | 2.5085 | 121.2524 | -0.20599 | 121.0922 | -0.15564 | -0.1831 | -0.1236 | 0.15564 | -0.14191 | -0.09613 | 0.21515 | 0.064087 | 0.10071 | -0.091553 | -0.054932 | 0.050354 | -0.20599 | -0.36621 | 0.10071 | 0.13275 | 0.073243 | 0.082398 | 0.022889 | 0.059509 | 121.463 | 0.050354 | 121.2982 | 121.4172 | 121.4584 | 121.5729 | 121.5088 | -121.5591 | -121.6644 | 121.6187 | 121.3486 | 7.2876 | 2.7649
1542.1875 | 121.756 | -0.17853 | 121.431 | -0.0057221 | 0 | 0.063681 | 0.067133 | -0.0037811 | -0.0027066 | -0.0038666 | 0.00018312 | 0.00097624 | -1.3969 | 0.062461 | -0.00028199 | 0.010194 | -0.0027985 | 7.0679 | 121.2982 | -0.073242 | 121.4493 | 0.041199 | -0.091553 | -0.1236 | 2.6093 | 121.225 | -0.1236 | 121.2341 | -0.027466 | -0.086975 | 0.009155 | 0.10529 | -0.13275 | 0.018311 | 0.21973 | 0.054932 | 0.086975 | -0.050354 | -0.018311 | 0.054932 | -0.20599 | -0.19684 | 0.15106 | 0.18768 | 0.091553 | 0.13275 | 0.036621 | 0.11444 | 121.5225 | 0.09613 | 121.3577 | 121.3715 | 121.3486 | 121.4767 | 121.4035 | -121.5042 | -121.5546 | 121.6278 | 121.4127 | 7.2464 | 2.7878
1543.9375 | 121.6415 | -0.22888 | 121.4401 | 0.0019074 | 0 | 0.063254 | 0.06457 | -0.0012177 | -0.0029202 | -0.0021576 | 0.00018312 | 0.0011898 | -1.395 | 0.058402 | -0.0034864 | 0.012117 | 0.00083309 | 7.1365 | 121.2982 | -0.10529 | 121.3989 | 0.004578 | -0.13733 | -0.1831 | 2.5589 | 121.2662 | -0.16022 | 121.1334 | -0.13275 | -0.17853 | -0.10071 | 0.1236 | -0.14191 | -0.041199 | 0.23346 | 0.045777 | 0.091553 | -0.077819 | -0.032043 | 0.068665 | -0.17395 | -0.3067 | 0.096131 | 0.12817 | 0.050354 | 0.059509 | -0.018311 | 0.10986 | 121.5042 | 0.027466 | 121.2936 | 121.4035 | 121.4264 | 121.5271 | 121.4951 | -121.5454 | -121.6003 | 121.6278 | 121.3623 | 7.3654 | 2.7878
1545.6562 | 121.7148 | -0.21973 | 121.4218 | 0.024795 | 0 | 0.063895 | 0.064142 | 0.00070491 | -0.0022794 | -2.1434e-05 | 0.0062865 | -0.00073276 | -1.3972 | 0.070152 | -0.00028199 | 0.011262 | -0.0032257 | 7.1228 | 121.3028 | -0.10529 | 121.4355 | 0.054932 | -0.082397 | -0.10986 | 2.5543 | 121.2479 | -0.16022 | 121.2067 | -0.059509 | -0.10529 | -0.059509 | 0.11444 | -0.11902 | 0.013733 | 0.27466 | 0.10986 | 0.13733 | -0.004577 | 0.022889 | 0.05951 | -0.17395 | -0.21515 | 0.16022 | 0.16022 | 0.11444 | 0.10071 | 0.054931 | 0.16022 | 121.5408 | 0.10071 | 121.3669 | 121.4081 | 121.4081 | 121.5225 | 121.4676 | -121.5271 | -121.582 | 121.6553 | 121.4264 | 7.3425 | 2.774
1547.4219 | 121.7468 | -0.17853 | 121.431 | 0.047683 | 0 | 0.064322 | 0.065211 | 0.0054047 | -0.0014248 | 0.0019012 | 0.015442 | 0.0035396 | -1.3955 | 0.061393 | -0.0026318 | 0.011903 | -0.00066231 | 7.2144 | 121.2891 | -0.091553 | 121.5271 | 0.1236 | -0.041199 | -0.068665 | 2.6459 | 121.2433 | -0.15564 | 121.2433 | -0.022888 | -0.091553 | -0.018311 | 0.086975 | -0.14191 | 0.096131 | 0.30212 | 0.10986 | 0.13733 | 0.022888 | 0.050354 | 0.022888 | -0.18768 | -0.18768 | 0.15564 | 0.16022 | 0.086975 | 0.13733 | 0.064087 | 0.21515 | 121.6187 | 0.13275 | 121.3989 | 121.3806 | 121.3989 | 121.4676 | 121.4218 | -121.5225 | -121.5866 | 121.7056 | 121.4218 | 7.3929 | 2.8244
1549.125 | 121.7834 | -0.19226 | 121.4264 | 0.0019074 | 0 | 0.065604 | 0.064783 | 0.0015595 | -0.00099764 | -0.00023503 | 0.018494 | 0.0041806 | -1.3916 | 0.06417 | -0.00049559 | 0.013612 | 0.0021149 | 7.1869 | 121.2845 | -0.073242 | 121.4859 | 0.09613 | -0.050354 | -0.073242 | 2.6505 | 121.2479 | -0.14648 | 121.2753 | -0.009155 | -0.054932 | 0 | 0.11902 | -0.14191 | 0.059509 | 0.28839 | 0.11902 | 0.14191 | 0 | 0.022888 | 0.045777 | -0.17853 | -0.15106 | 0.18311 | 0.19226 | 0.13733 | 0.14648 | 0.091552 | 0.16937 | 121.5591 | 0.13733 | 121.4218 | 121.3577 | 121.3943 | 121.4767 | 121.4401 | -121.4996 | -121.5729 | 121.6782 | 121.4676 | 7.3792 | 2.8427
1550.8906 | 121.6873 | -0.20599 | 121.4676 | 0.040054 | 0 | 0.064963 | 0.064783 | 0.0017731 | -0.0022794 | -0.001303 | 0.0062865 | 0.0035396 | -1.3942 | 0.058616 | -0.0049818 | 0.010408 | -0.0017303 | 7.2235 | 121.344 | -0.13733 | 121.431 | 0.022888 | -0.11444 | -0.15106 | 2.5909 | 121.2753 | -0.16479 | 121.1929 | -0.091553 | -0.14191 | -0.064087 | 0.068665 | -0.1236 | -0.036621 | 0.22888 | 0.054932 | 0.091553 | -0.013733 | 0.022888 | 0.041199 | -0.19226 | -0.27466 | 0.11444 | 0.14191 | 0.064087 | 0.10071 | 0.022888 | 0.16022 | 121.5683 | 0.073242 | 121.3577 | 121.4813 | 121.4401 | 121.55 | 121.4813 | -121.6049 | -121.6324 | 121.637 | 121.3989 | 7.4295 | 2.7969
1552.5938 | 121.7834 | -0.19226 | 121.4447 | -0.0057221 | 0 | 0.061545 | 0.062861 | -0.0010041 | -0.0037746 | -0.0051482 | -0.0028687 | 0.00012184 | -1.3961 | 0.071647 | -0.004768 | 0.012117 | 0.00083309 | 7.2418 | 121.257 | -0.064087 | 121.5088 | 0.13733 | -0.027466 | -0.059509 | 2.6779 | 121.1975 | -0.13733 | 121.2891 | 0 | -0.022888 | -0.009155 | 0.12817 | -0.18768 | 0.064087 | 0.32959 | 0.13275 | 0.16479 | 0.004578 | 0.036621 | 0.054932 | -0.24719 | -0.15564 | 0.19226 | 0.18311 | 0.16937 | 0.12817 | 0.11444 | 0.20142 | 121.5729 | 0.13733 | 121.4264 | 121.3211 | 121.3348 | 121.4493 | 121.3898 | -121.5088 | -121.582 | 121.701 | 121.4813 | 7.4341 | 2.8702
1554.3594 | 121.7697 | -0.1831 | 121.431 | 0.0019074 | 0 | 0.065176 | 0.063929 | 0.0013459 | -0.0022794 | -2.1434e-05 | -0.0028687 | 0.0014034 | -1.3957 | 0.064597 | 0.00014521 | 0.010621 | -0.0030121 | 7.2418 | 121.2982 | -0.073242 | 121.4722 | 0.091553 | -0.068665 | -0.10986 | 2.6367 | 121.2433 | -0.12817 | 121.3074 | -0.041199 | -0.068665 | 0.022888 | 0.10986 | -0.13275 | 0.041199 | 0.27466 | 0.073242 | 0.11444 | -0.036621 | 0.004577 | 0.054931 | -0.18768 | -0.1236 | 0.14191 | 0.20599 | 0.11444 | 0.15106 | 0.059509 | 0.16479 | 121.5454 | 0.086975 | 121.4355 | 121.3715 | 121.3715 | 121.4813 | 121.4264 | -121.5042 | -121.5591 | 121.6553 | 121.4905 | 7.4249 | 2.8198
1556.125 | 121.6507 | -0.24719 | 121.4676 | -0.0057221 | 0 | 0.063254 | 0.066065 | 0.0024139 | -0.002493 | 0.0010468 | -0.0059205 | 0.0020444 | -1.3952 | 0.067588 | -0.0034864 | 0.011689 | -0.0019439 | 7.2098 | 121.3348 | -0.11444 | 121.3394 | -0.07782 | -0.20142 | -0.23346 | 2.4857 | 121.2799 | -0.17853 | 121.1655 | -0.17395 | -0.21515 | -0.10071 | 0.13275 | -0.13275 | -0.12817 | 0.16937 | 0.013733 | 0.045776 | -0.11902 | -0.086975 | 0.068664 | -0.18768 | -0.30212 | 0.073242 | 0.14648 | 0.032043 | 0.07782 | -0.036621 | 0.036621 | 121.4539 | 0.004578 | 121.344 | 121.4493 | 121.4584 | 121.582 | 121.5271 | -121.582 | -121.6461 | 121.5866 | 121.4127 | 7.457 | 2.7328
1557.875 | 121.6507 | -0.24261 | 121.463 | -0.0057221 | 0 | 0.064108 | 0.064356 | 0.0066863 | -0.0020658 | -0.00087583 | 0.00018312 | 0.0026852 | -1.3961 | 0.062675 | -0.0037 | 0.010194 | 0.0029693 | 7.2052 | 121.3257 | -0.10986 | 121.3531 | -0.064087 | -0.20599 | -0.21973 | 2.4857 | 121.2296 | -0.15564 | 121.1609 | -0.16479 | -0.21515 | -0.086975 | 0.13275 | -0.13733 | -0.10986 | 0.17853 | 0.022888 | 0.036621 | -0.10986 | -0.096131 | 0.086975 | -0.23346 | -0.30212 | 0.07782 | 0.15564 | 0.027466 | 0.068665 | -0.059509 | 0.045776 | 121.463 | -0.009155 | 121.3165 | 121.4355 | 121.3852 | 121.5683 | 121.4722 | -121.5729 | -121.6187 | 121.5958 | 121.4035 | 7.4478 | 2.7283
1559.5781 | 121.7606 | -0.17395 | 121.4264 | 0.062942 | 0 | 0.065604 | 0.064142 | 0.00027771 | -0.00014304 | 0.0023286 | 0.018494 | 0.0035396 | -1.3942 | 0.066734 | -0.0011364 | 0.01233 | 0.0016877 | 7.3334 | 121.3211 | -0.086975 | 121.5134 | 0.14191 | -0.027466 | -0.073242 | 2.6642 | 121.2112 | -0.15564 | 121.2799 | -0.027466 | -0.07782 | -0.009155 | 0.086975 | -0.10529 | 0.086975 | 0.31586 | 0.10071 | 0.14648 | 0.013733 | 0.059509 | 0.01831 | -0.21515 | -0.14649 | 0.14648 | 0.16479 | 0.09613 | 0.14649 | 0.07782 | 0.22888 | 121.6003 | 0.12817 | 121.4355 | 121.4081 | 121.3669 | 121.4951 | 121.3852 | -121.5134 | -121.582 | 121.6873 | 121.4539 | 7.5073 | 2.8381
1561.3438 | 121.7056 | -0.21515 | 121.4493 | 0.024795 | 0 | 0.06539 | 0.066279 | -0.0020721 | -0.004202 | 0.00083317 | 0.00018312 | 0.003326 | -1.3959 | 0.062675 | -0.0051954 | 0.0099805 | 0.00040589 | 7.3471 | 121.3303 | -0.12817 | 121.4355 | 0.054932 | -0.09613 | -0.13733 | 2.623 | 121.2479 | -0.15106 | 121.225 | -0.082397 | -0.12817 | -0.064087 | 0.086975 | -0.11902 | -0.013733 | 0.27008 | 0.07782 | 0.11902 | -0.009155 | 0.032044 | 0.064087 | -0.20142 | -0.2243 | 0.13275 | 0.15106 | 0.086975 | 0.086975 | 0.022888 | 0.18311 | 121.5637 | 0.068665 | 121.376 | 121.4584 | 121.3989 | 121.5454 | 121.463 | -121.5775 | -121.6003 | 121.6507 | 121.4401 | 7.5623 | 2.8381
1563.1094 | 121.7285 | -0.21057 | 121.4172 | -0.0057221 | 0 | 0.063895 | 0.061365 | -0.0057037 | -0.002493 | -0.00087583 | -0.0028687 | 0.001617 | -1.3957 | 0.062675 | -0.0045544 | 0.012544 | -0.0015167 | 7.3517 | 121.2845 | -0.064087 | 121.4813 | 0.082397 | -0.045776 | -0.082397 | 2.623 | 121.225 | -0.13275 | 121.2296 | -0.022888 | -0.068665 | -0.022888 | 0.14648 | -0.13275 | 0.064087 | 0.29297 | 0.12817 | 0.1648 | -0.01831 | 0.018311 | 0.07782 | -0.19226 | -0.18768 | 0.18768 | 0.18768 | 0.14191 | 0.10986 | 0.064086 | 0.14648 | 121.5454 | 0.10986 | 121.3623 | 121.3486 | 121.3577 | 121.4951 | 121.4355 | -121.4813 | -121.55 | 121.6919 | 121.4401 | 7.5623 | 2.8336
1564.8906 | 121.6827 | -0.2243 | 121.4584 | 0.024795 | 0 | 0.063895 | 0.065424 | -0.0027131 | -0.00099764 | -0.0017304 | 0.01239 | 0.0031124 | -1.394 | 0.06182 | -0.0056226 | 0.0089123 | -0.0062165 | 7.338 | 121.3348 | -0.13733 | 121.4172 | 0.009155 | -0.10986 | -0.15564 | 2.5589 | 121.2662 | -0.17853 | 121.1884 | -0.091553 | -0.13275 | -0.064087 | 0.086975 | -0.1236 | -0.041199 | 0.23346 | 0.068664 | 0.11444 | -0.018311 | 0.027466 | 0.045776 | -0.19226 | -0.27008 | 0.13275 | 0.16022 | 0.091553 | 0.11444 | 0.045777 | 0.14648 | 121.5546 | 0.086975 | 121.3669 | 121.4722 | 121.4447 | 121.5591 | 121.4905 | -121.5958 | -121.637 | 121.6415 | 121.4127 | 7.5623 | 2.7832
1566.6562 | 121.6553 | -0.24719 | 121.463 | -0.0057221 | 0 | 0.062613 | 0.064356 | 0.0017731 | -0.0027066 | -2.1434e-05 | -0.0028687 | 0.0024716 | -1.3942 | 0.059257 | -0.0028454 | 0.011689 | -0.00087591 | 7.2968 | 121.2936 | -0.10986 | 121.3486 | -0.064087 | -0.19226 | -0.21515 | 2.4857 | 121.2479 | -0.15564 | 121.1563 | -0.16022 | -0.20599 | -0.10071 | 0.13733 | -0.16937 | -0.11444 | 0.1831 | 0.032043 | 0.054931 | -0.10529 | -0.082398 | 0.091552 | -0.21515 | -0.3067 | 0.086975 | 0.14648 | 0.041198 | 0.054932 | -0.050354 | 0.045776 | 121.4584 | -0.004577 | 121.312 | 121.4035 | 121.4035 | 121.5408 | 121.4951 | -121.5729 | -121.6187 | 121.5958 | 121.4035 | 7.5439 | 2.7328
1568.3594 | 121.7743 | -0.1831 | 121.3989 | 0.062942 | 0 | 0.065604 | 0.065638 | -0.00014949 | -0.00014304 | -0.003012 | 0.01239 | 0.002258 | -1.3952 | 0.070579 | -0.0017774 | 0.013826 | 0.00040589 | 7.4203 | 121.3165 | -0.086975 | 121.5225 | 0.13275 | -0.036621 | -0.07782 | 2.6596 | 121.2616 | -0.15106 | 121.2479 | -0.022888 | -0.064087 | -0.004578 | 0.09613 | -0.082398 | 0.1236 | 0.31586 | 0.10528 | 0.14648 | 0.009155 | 0.050354 | 0.032043 | -0.13733 | -0.15106 | 0.16022 | 0.17853 | 0.11902 | 0.14648 | 0.086975 | 0.21973 | 121.6095 | 0.12817 | 121.3989 | 121.4035 | 121.4127 | 121.4996 | 121.4447 | -121.4859 | -121.55 | 121.7056 | 121.431 | 7.6035 | 2.8427
1570.1406 | 121.6782 | -0.23804 | 121.4401 | 0.0019074 | 0 | 0.06539 | 0.064997 | 0.0013459 | -0.0044156 | 0.0010468 | -0.0028687 | 0.0024716 | -1.3957 | 0.06182 | -0.0022046 | 0.012117 | -2.1314e-05 | 7.3151 | 121.3211 | -0.10529 | 121.3715 | -0.050354 | -0.17395 | -0.20599 | 2.504 | 121.2662 | -0.16022 | 121.1929 | -0.12817 | -0.16937 | -0.064087 | 0.13275 | -0.11902 | -0.068665 | 0.18768 | 0.032043 | 0.064087 | -0.10071 | -0.068664 | 0.07782 | -0.17395 | -0.24719 | 0.10986 | 0.17395 | 0.068664 | 0.09613 | -0.009156 | 0.054932 | 121.4767 | 0.032043 | 121.3531 | 121.4264 | 121.4264 | 121.5591 | 121.5042 | -121.5454 | -121.6003 | 121.6095 | 121.431 | 7.5531 | 2.742
1571.9062 | 121.7789 | -0.19684 | 121.4355 | 0.0019074 | 0 | 0.061545 | 0.060938 | -0.0016449 | -0.001852 | -0.0010894 | -0.0028687 | 0.00033544 | -1.3957 | 0.066306 | -0.0049818 | 0.010621 | -0.0017303 | 7.4112 | 121.2479 | -0.07782 | 121.5134 | 0.13733 | 0.004578 | -0.073242 | 2.6871 | 121.2204 | -0.11902 | 121.2524 | 0.004578 | -0.036621 | -0.009155 | 0.11902 | -0.18768 | 0.07782 | 0.33417 | 0.1236 | 0.20142 | 0.004578 | 0.082398 | 0.077819 | -0.21515 | -0.18311 | 0.20142 | 0.18768 | 0.16022 | 0.10986 | 0.082398 | 0.21515 | 121.5912 | 0.1236 | 121.3715 | 121.3257 | 121.3394 | 121.4447 | 121.4172 | -121.5134 | -121.5546 | 121.7102 | 121.4493 | 7.608 | 2.8839
1573.6094 | 121.7194 | -0.21057 | 121.463 | 0.032425 | 0 | 0.062827 | 0.063715 | 0.00070491 | -0.00078404 | -0.0015166 | 0.00018312 | 0.002258 | -1.3963 | 0.059898 | -0.004768 | 0.011262 | 0.0031829 | 7.3517 | 121.2936 | -0.09613 | 121.4447 | 0.050354 | -0.091553 | -0.11902 | 2.5635 | 121.2387 | -0.14648 | 121.1884 | -0.082397 | -0.11902 | -0.059509 | 0.11444 | -0.16937 | -0.018311 | 0.26093 | 0.091552 | 0.11902 | -0.022889 | 0.004577 | 0.064087 | -0.22431 | -0.27466 | 0.12817 | 0.15106 | 0.091552 | 0.086975 | 0.027465 | 0.14648 | 121.5408 | 0.064087 | 121.3348 | 121.3898 | 121.3852 | 121.5042 | 121.4493 | -121.5591 | -121.6095 | 121.6553 | 121.3989 | 7.5623 | 2.774
1575.3906 | 121.7468 | -0.17853 | 121.4447 | -0.0057221 | 0 | 0.062186 | 0.061365 | 0.0028411 | -0.004202 | 0.00061957 | -0.0028687 | 0.0024716 | -1.3944 | 0.067588 | -0.007118 | 0.011476 | -2.1314e-05 | 7.4387 | 121.2387 | -0.073242 | 121.4905 | 0.1236 | -0.032043 | -0.091553 | 2.6779 | 121.2204 | -0.15106 | 121.2341 | -0.009155 | -0.064087 | -0.013733 | 0.10529 | -0.20599 | 0.045777 | 0.30212 | 0.086975 | 0.14648 | -0.018311 | 0.041199 | 0.027466 | -0.2243 | -0.21057 | 0.16937 | 0.16479 | 0.11444 | 0.13733 | 0.086975 | 0.19684 | 121.5637 | 0.14191 | 121.3852 | 121.3119 | 121.3715 | 121.4172 | 121.3989 | -121.5179 | -121.5958 | 121.669 | 121.4127 | 7.6172 | 2.8564
1577.0938 | 121.7239 | -0.20142 | 121.4722 | 0.017166 | 0 | 0.06304 | 0.061793 | 0.0032685 | -0.0016384 | 0.00040597 | 0.0032349 | 0.00097624 | -1.3957 | 0.06652 | -0.0013502 | 0.011262 | -0.0021575 | 7.4066 | 121.3074 | -0.10071 | 121.4493 | 0.064087 | -0.082397 | -0.10529 | 2.6093 | 121.2433 | -0.15106 | 121.2021 | -0.073242 | -0.10986 | -0.041199 | 0.10071 | -0.16479 | -0.022888 | 0.2655 | 0.09613 | 0.11902 | -0.004578 | 0.018311 | 0.050354 | -0.22888 | -0.27008 | 0.12817 | 0.16022 | 0.091553 | 0.10986 | 0.041199 | 0.1648 | 121.55 | 0.07782 | 121.3531 | 121.4081 | 121.3943 | 121.5088 | 121.4447 | -121.5729 | -121.6232 | 121.6507 | 121.4035 | 7.608 | 2.8107
1578.8594 | 121.7239 | -0.21973 | 121.4722 | 0.017166 | 0 | 0.062613 | 0.064142 | 0.00091851 | -0.0016384 | 0.00061957 | 0.0062865 | 0.00097624 | -1.3944 | 0.065238 | -0.0045544 | 0.0099805 | -0.0017303 | 7.4203 | 121.2982 | -0.09613 | 121.4401 | 0.059509 | -0.073242 | -0.10529 | 2.5818 | 121.2296 | -0.15106 | 121.1975 | -0.07782 | -0.11902 | -0.054932 | 0.1236 | -0.17395 | -0.032043 | 0.27924 | 0.11444 | 0.14649 | -0.009156 | 0.022888 | 0.068665 | -0.24262 | -0.27466 | 0.14191 | 0.16479 | 0.10071 | 0.09613 | 0.032043 | 0.15564 | 121.5363 | 0.073242 | 121.3486 | 121.3943 | 121.3806 | 121.5179 | 121.4493 | -121.5683 | -121.6232 | 121.6599 | 121.4172 | 7.6401 | 2.8015
1580.5781 | 121.7834 | -0.1831 | 121.4355 | -0.0057221 | 0 | 0.063895 | 0.066065 | 0.0034821 | -0.0012112 | 0.0019012 | 0.018494 | 0.003967 | -1.3935 | 0.067375 | -0.0026318 | 0.012117 | -0.0030121 | 7.489 | 121.2662 | -0.059509 | 121.5454 | 0.14191 | -0.027466 | -0.068665 | 2.7008 | 121.2662 | -0.14648 | 121.2753 | -0.018311 | -0.050354 | -0.013733 | 0.1236 | -0.16937 | 0.10986 | 0.32501 | 0.11444 | 0.15564 | -0.009156 | 0.032043 | 0.036621 | -0.16937 | -0.16022 | 0.16479 | 0.16937 | 0.13275 | 0.13275 | 0.09613 | 0.20142 | 121.6049 | 0.12817 | 121.4218 | 121.3257 | 121.4127 | 121.4493 | 121.4493 | -121.4951 | -121.582 | 121.7285 | 121.4584 | 7.6721 | 2.8839
1582.3438 | 121.7514 | -0.19226 | 121.4447 | 0.017166 | 0 | 0.061118 | 0.063715 | -0.0024995 | -0.0037746 | -0.00044863 | 0.00018312 | 0.0011898 | -1.3952 | 0.066734 | -0.0037 | 0.011049 | 0.0014741 | 7.4478 | 121.2799 | -0.086975 | 121.4447 | 0.041199 | -0.091553 | -0.1236 | 2.5909 | 121.2524 | -0.12817 | 121.2021 | -0.054932 | -0.091553 | -0.027466 | 0.10529 | -0.1648 | 0 | 0.23346 | 0.068665 | 0.10071 | -0.036621 | -0.004578 | 0.064087 | -0.19226 | -0.24262 | 0.13733 | 0.16479 | 0.10071 | 0.10071 | 0.036621 | 0.12817 | 121.5317 | 0.073242 | 121.3303 | 121.3669 | 121.3806 | 121.4722 | 121.4447 | -121.5317 | -121.5729 | 121.637 | 121.3943 | 7.6401 | 2.7832
1584.0938 | 121.7926 | -0.20142 | 121.4401 | 0.0019074 | 0 | 0.062186 | 0.061152 | -0.0061311 | -0.00014304 | -0.0017304 | -0.0028687 | 0.0011898 | -1.3963 | 0.070365 | -0.0041272 | 0.011476 | 0.0014741 | 7.5302 | 121.2982 | -0.068665 | 121.4951 | 0.10986 | -0.032043 | -0.068665 | 2.6962 | 121.225 | -0.12817 | 121.2524 | 0.013733 | -0.018311 | 0.004578 | 0.13275 | -0.14191 | 0.054931 | 0.31128 | 0.13275 | 0.16937 | 0 | 0.036622 | 0.073242 | -0.21515 | -0.18768 | 0.21515 | 0.20599 | 0.18311 | 0.13275 | 0.10986 | 0.17853 | 121.5637 | 0.14191 | 121.3806 | 121.3669 | 121.3531 | 121.4996 | 121.4264 | -121.5088 | -121.5683 | 121.6965 | 121.4539 | 7.7316 | 2.8976
1585.875 | 121.7194 | -0.20599 | 121.4264 | 0.032425 | 0 | 0.064322 | 0.063715 | 0.00070491 | -0.0022794 | -0.0010894 | 0.0032349 | 0.00097624 | -1.3948 | 0.065238 | -0.0028454 | 0.010835 | -0.0019439 | 7.4982 | 121.2936 | -0.09613 | 121.4584 | 0.059509 | -0.082397 | -0.11444 | 2.5726 | 121.2387 | -0.16479 | 121.2021 | -0.082397 | -0.1236 | -0.059509 | 0.10986 | -0.13275 | 0.032043 | 0.2655 | 0.091553 | 0.1236 | -0.018311 | 0.013733 | 0.041199 | -0.18768 | -0.22431 | 0.1236 | 0.14649 | 0.082398 | 0.10529 | 0.041199 | 0.15564 | 121.5546 | 0.082398 | 121.3669 | 121.3898 | 121.4035 | 121.4996 | 121.4447 | -121.5225 | -121.5912 | 121.6644 | 121.4081 | 7.7042 | 2.7786
1587.5781 | 121.6507 | -0.24719 | 121.4905 | 0.0019074 | 0 | 0.065176 | 0.067133 | 0.0015595 | -0.0044156 | -2.1434e-05 | -0.0028687 | 0.0031124 | -1.3927 | 0.065879 | -0.0026318 | 0.010835 | -0.0017303 | 7.5073 | 121.344 | -0.10529 | 121.3577 | -0.082397 | -0.21057 | -0.23346 | 2.504 | 121.2753 | -0.17853 | 121.1197 | -0.1831 | -0.2243 | -0.11444 | 0.14191 | -0.14648 | -0.13275 | 0.16479 | 0.013733 | 0.036621 | -0.12817 | -0.10529 | 0.068664 | -0.21515 | -0.37079 | 0.064087 | 0.13275 | 0.022888 | 0.064087 | -0.045776 | 0.022889 | 121.463 | -0.004577 | 121.2982 | 121.4493 | 121.4539 | 121.5912 | 121.5225 | -121.5958 | -121.669 | 121.6049 | 121.3669 | 7.7545 | 2.7512
1589.3438 | 121.6644 | -0.23804 | 121.4813 | 0.047683 | 0 | 0.063254 | 0.064997 | 0.0036957 | -0.0039884 | -2.1434e-05 | 0.01239 | 0.0018306 | -1.3957 | 0.055839 | -0.0069044 | 0.010621 | -0.0034393 | 7.5943 | 121.3348 | -0.14191 | 121.3943 | -0.004578 | -0.11902 | -0.16022 | 2.5589 | 121.2982 | -0.20142 | 121.1334 | -0.14191 | -0.16937 | -0.082397 | 0.09613 | -0.14648 | -0.086975 | 0.23346 | 0.07782 | 0.11902 | -0.01831 | 0.022888 | 0.036621 | -0.1831 | -0.3479 | 0.09613 | 0.15564 | 0.068664 | 0.11902 | 0.032043 | 0.13733 | 121.5363 | 0.059509 | 121.3348 | 121.4767 | 121.4996 | 121.5729 | 121.5363 | -121.6232 | -121.6827 | 121.6324 | 121.3715 | 7.8323 | 2.7969
1591.1094 | 121.637 | -0.22888 | 121.463 | 0.0095369 | 0 | 0.061972 | 0.065211 | -0.00014949 | -0.0027066 | 0.0016876 | 0.024597 | 0.001617 | -1.3948 | 0.058616 | -0.0077588 | 0.0089123 | -0.0032257 | 7.5577 | 121.312 | -0.11902 | 121.3989 | 0.018311 | -0.07782 | -0.16022 | 2.5681 | 121.312 | -0.19684 | 121.1197 | -0.15106 | -0.19684 | -0.10986 | 0.10986 | -0.15106 | -0.064087 | 0.24719 | 0.068665 | 0.15106 | -0.041198 | 0.041199 | 0.032044 | -0.15106 | -0.34332 | 0.07782 | 0.11902 | 0.032044 | 0.086975 | 0 | 0.13733 | 121.5179 | 0.045776 | 121.3165 | 121.431 | 121.5088 | 121.5408 | 121.5408 | -121.582 | -121.6599 | 121.6278 | 121.3486 | 7.7866 | 2.7969
1592.875 | 121.6507 | -0.23804 | 121.4722 | 0.0019074 | 0 | 0.06304 | 0.062647 | -0.0018585 | -0.00099764 | -0.0015166 | 0.00018312 | 0.003326 | -1.394 | 0.055839 | -0.0045544 | 0.0078443 | -0.0062165 | 7.5897 | 121.3074 | -0.10986 | 121.3715 | -0.013733 | -0.14648 | -0.17853 | 2.5269 | 121.2341 | -0.1831 | 121.106 | -0.13733 | -0.17853 | -0.12817 | 0.12817 | -0.16479 | -0.10071 | 0.2243 | 0.059509 | 0.091553 | -0.068665 | -0.036621 | 0.054932 | -0.23804 | -0.36621 | 0.10071 | 0.10986 | 0.059509 | 0.054931 | 0.004577 | 0.09613 | 121.4813 | 0.045776 | 121.2891 | 121.4172 | 121.4172 | 121.5454 | 121.4722 | -121.582 | -121.6553 | 121.6095 | 121.344 | 7.8278 | 2.7649
1594.6406 | 121.6507 | -0.24719 | 121.4767 | -0.0057221 | 0 | 0.062827 | 0.062647 | -0.0031403 | -0.003561 | 0.00040597 | 0.018494 | 0.0037532 | -1.3961 | 0.060111 | -0.0066906 | 0.0089123 | -0.0010895 | 7.608 | 121.3211 | -0.10529 | 121.3943 | 0.009155 | -0.09613 | -0.14648 | 2.5955 | 121.3028 | -0.21515 | 121.1197 | -0.13275 | -0.18768 | -0.091553 | 0.14191 | -0.15564 | -0.082398 | 0.25635 | 0.10071 | 0.15106 | -0.041198 | 0.009156 | 0.032043 | -0.17395 | -0.35706 | 0.11444 | 0.15564 | 0.059509 | 0.1236 | 0.027466 | 0.11444 | 121.4996 | 0.082398 | 121.3348 | 121.4264 | 121.5179 | 121.5683 | 121.55 | -121.582 | -121.6919 | 121.6415 | 121.3669 | 7.8552 | 2.8427
1596.4062 | 121.637 | -0.23346 | 121.5134 | 0.0019074 | 0 | 0.063467 | 0.065424 | 0.0028411 | -0.0037746 | 0.00019217 | 0.00018312 | 0.0031124 | -1.3967 | 0.058616 | -0.0032728 | 0.0093397 | -2.1314e-05 | 7.6447 | 121.3257 | -0.10529 | 121.376 | -0.013733 | -0.1831 | -0.21057 | 2.536 | 121.2662 | -0.15106 | 121.1197 | -0.17395 | -0.21515 | -0.1236 | 0.12817 | -0.18768 | -0.13733 | 0.21973 | 0.022888 | 0.050354 | -0.10529 | -0.077819 | 0.082397 | -0.24719 | -0.39368 | 0.059509 | 0.10986 | 0.01831 | 0.027466 | -0.064087 | 0.091553 | 121.4813 | -0.022888 | 121.2708 | 121.431 | 121.4172 | 121.5591 | 121.4996 | -121.6187 | -121.6644 | 121.6095 | 121.3531 | 7.8781 | 2.7695
1598.1094 | 121.669 | -0.23346 | 121.4905 | 0.055313 | 0 | 0.064108 | 0.06457 | 0.00091851 | -0.002493 | -0.00087583 | 0.018494 | 0.003326 | -1.3929 | 0.063743 | -0.0049818 | 0.010194 | -0.0025849 | 7.6813 | 121.3394 | -0.14648 | 121.3852 | 0.018311 | -0.11444 | -0.15106 | 2.5772 | 121.2936 | -0.19684 | 121.1288 | -0.13275 | -0.17395 | -0.091553 | 0.086975 | -0.15106 | -0.10529 | 0.25177 | 0.082397 | 0.11902 | -0.004578 | 0.032043 | 0.036621 | -0.19684 | -0.36163 | 0.10071 | 0.14191 | 0.059509 | 0.10529 | 0.022888 | 0.16479 | 121.5317 | 0.064087 | 121.3257 | 121.4859 | 121.4905 | 121.5729 | 121.5271 | -121.637 | -121.6873 | 121.6187 | 121.3623 | 7.9147 | 2.8107
1599.875 | 121.669 | -0.24719 | 121.4767 | 0.047683 | 0 | 0.061972 | 0.065638 | 0.0028411 | -0.0029202 | -0.00023503 | 0.018494 | 0.003326 | -1.3955 | 0.050926 | -0.0037 | 0.0089123 | -0.0013031 | 7.7179 | 121.3531 | -0.14191 | 121.3943 | 0.009155 | -0.1236 | -0.16479 | 2.5818 | 121.2753 | -0.18768 | 121.1334 | -0.11444 | -0.16937 | -0.09613 | 0.10528 | -0.1236 | -0.082398 | 0.25635 | 0.082397 | 0.1236 | -0.022888 | 0.018311 | 0.059509 | -0.20142 | -0.34332 | 0.13275 | 0.15106 | 0.077819 | 0.091553 | 0.01831 | 0.15106 | 121.5363 | 0.073242 | 121.3211 | 121.4951 | 121.463 | 121.6003 | 121.5225 | -121.6187 | -121.6644 | 121.6415 | 121.3806 | 7.9651 | 2.829
1601.6406 | 121.7285 | -0.21057 | 121.431 | 0.024795 | 0 | 0.064536 | 0.064783 | 0.0030547 | -0.0012112 | -0.0021576 | 0.01239 | 0.0031124 | -1.3955 | 0.062888 | -6.8386e-05 | 0.010408 | 0.00061949 | 7.6996 | 121.312 | -0.091553 | 121.4493 | 0.082397 | -0.068665 | -0.10529 | 2.5955 | 121.2479 | -0.15106 | 121.2067 | -0.064087 | -0.091553 | -0.050354 | 0.11902 | -0.11902 | 0.018311 | 0.29297 | 0.10529 | 0.14191 | -0.013733 | 0.022888 | 0.059509 | -0.1831 | -0.2243 | 0.14648 | 0.16022 | 0.11902 | 0.10071 | 0.059509 | 0.17395 | 121.5408 | 0.086975 | 121.3577 | 121.4035 | 121.3989 | 121.5225 | 121.4584 | -121.5225 | -121.582 | 121.6599 | 121.4172 | 7.9102 | 2.8061
1603.3594 | 121.669 | -0.23346 | 121.4584 | -0.0057221 | 0 | 0.062613 | 0.067133 | -0.0022857 | -0.0012112 | -0.001303 | -0.0028687 | 0.0046078 | -1.3959 | 0.054771 | -0.0011364 | 0.010621 | -0.0021575 | 7.695 | 121.312 | -0.09613 | 121.3715 | -0.041199 | -0.17853 | -0.20599 | 2.5269 | 121.2524 | -0.15106 | 121.1472 | -0.14191 | -0.17853 | -0.086975 | 0.13733 | -0.14648 | -0.086975 | 0.19226 | 0.027465 | 0.054931 | -0.10986 | -0.082398 | 0.082397 | -0.20599 | -0.31128 | 0.091552 | 0.14648 | 0.054931 | 0.064087 | -0.027466 | 0.054931 | 121.4676 | 0.009155 | 121.2982 | 121.4081 | 121.4035 | 121.5454 | 121.4859 | -121.5546 | -121.6095 | 121.6049 | 121.3806 | 7.9285 | 2.7603
1605.125 | 121.7285 | -0.21057 | 121.4447 | 0.024795 | 0 | 0.063681 | 0.062433 | 0.0028411 | -0.001852 | 0.0023286 | 0.0093383 | 0.00097624 | -1.3952 | 0.06182 | -0.0013502 | 0.011262 | -0.00023491 | 7.7316 | 121.312 | -0.082397 | 121.4539 | 0.086975 | -0.086975 | -0.10071 | 2.6184 | 121.2296 | -0.14648 | 121.2021 | -0.068665 | -0.091553 | -0.045776 | 0.12817 | -0.13275 | 0.009155 | 0.29755 | 0.10986 | 0.1236 | -0.018311 | -0.004578 | 0.064087 | -0.21515 | -0.24262 | 0.14191 | 0.1648 | 0.11902 | 0.10071 | 0.054931 | 0.16937 | 121.5363 | 0.077819 | 121.3486 | 121.3943 | 121.376 | 121.5225 | 121.4401 | -121.5271 | -121.5912 | 121.6644 | 121.4127 | 7.9422 | 2.829
1606.9062 | 121.7651 | -0.18768 | 121.4264 | 0.0019074 | 0 | 0.064963 | 0.063074 | -0.00036309 | -0.0012112 | -0.0015166 | -0.0028687 | 0.0018306 | -1.395 | 0.065452 | -0.001991 | 0.011262 | -0.0023713 | 7.8094 | 121.2982 | -0.07782 | 121.4767 | 0.11444 | -0.064087 | -0.10529 | 2.6733 | 121.225 | -0.13275 | 121.2753 | -0.018311 | -0.054932 | 0.018311 | 0.10986 | -0.12817 | 0.050354 | 0.30212 | 0.082397 | 0.1236 | -0.027466 | 0.013733 | 0.054932 | -0.20142 | -0.15106 | 0.16937 | 0.20599 | 0.13275 | 0.15106 | 0.077819 | 0.19226 | 121.5546 | 0.11444 | 121.4081 | 121.376 | 121.3577 | 121.4859 | 121.4127 | -121.5042 | -121.5591 | 121.6644 | 121.463 | 7.9971 | 2.861
1608.6719 | 121.6965 | -0.2243 | 121.4813 | 0.047683 | 0 | 0.065817 | 0.064783 | -0.00014949 | -0.003561 | 0.0027558 | 0.018494 | 0.005035 | -1.3937 | 0.062461 | -0.0051954 | 0.0093397 | -0.0032257 | 7.8094 | 121.3303 | -0.14648 | 121.4172 | 0.027466 | -0.091553 | -0.1236 | 2.6001 | 121.3165 | -0.1831 | 121.17 | -0.10071 | -0.14648 | -0.064087 | 0.07782 | -0.15106 | -0.064087 | 0.25177 | 0.10071 | 0.13275 | 0.022888 | 0.054931 | 0.041199 | -0.16479 | -0.31128 | 0.1236 | 0.16022 | 0.07782 | 0.11902 | 0.036621 | 0.17395 | 121.5637 | 0.082397 | 121.3531 | 121.4767 | 121.4996 | 121.5546 | 121.5408 | -121.6278 | -121.6644 | 121.6415 | 121.3943 | 8.0338 | 2.8244
1610.4375 | 121.6873 | -0.21057 | 121.4676 | -0.0057221 | 0 | 0.061758 | 0.063929 | -0.0016449 | -0.0029202 | 0.00040597 | -0.0028687 | 0.0028988 | -1.3984 | 0.054984 | -0.0043408 | 0.011689 | -0.00044851 | 7.8232 | 121.2845 | -0.073242 | 121.463 | 0.07782 | -0.054932 | -0.1236 | 2.6642 | 121.2479 | -0.15564 | 121.1563 | -0.091553 | -0.1236 | -0.07782 | 0.13733 | -0.1831 | -0.004577 | 0.28839 | 0.086975 | 0.15564 | -0.050354 | 0.01831 | 0.054931 | -0.21973 | -0.31128 | 0.11902 | 0.13275 | 0.086975 | 0.07782 | 0.032044 | 0.15106 | 121.5363 | 0.064087 | 121.312 | 121.3577 | 121.4035 | 121.4951 | 121.4584 | -121.5408 | -121.6232 | 121.6736 | 121.3669 | 8.0338 | 2.8748
1612.2188 | 121.7422 | -0.21973 | 121.4539 | 0.0095369 | 0 | 0.063895 | 0.063502 | -0.0027131 | -0.0029202 | -0.0015166 | 0.0093383 | 0.0018306 | -1.3937 | 0.069297 | -0.0037 | 0.011049 | -0.00087591 | 7.8186 | 121.2799 | -0.07782 | 121.4447 | 0.068665 | -0.082397 | -0.12817 | 2.6138 | 121.2433 | -0.15564 | 121.2112 | -0.064087 | -0.09613 | -0.041199 | 0.14191 | -0.17395 | -0.009155 | 0.28839 | 0.091553 | 0.13733 | -0.050354 | -0.004577 | 0.064087 | -0.21057 | -0.24261 | 0.15564 | 0.17853 | 0.1236 | 0.11444 | 0.05951 | 0.14649 | 121.5225 | 0.091553 | 121.3669 | 121.3577 | 121.3989 | 121.4996 | 121.463 | -121.5317 | -121.6095 | 121.6644 | 121.431 | 8.0383 | 2.8336
1613.9844 | 121.6919 | -0.21057 | 121.4722 | 0.032425 | 0 | 0.063254 | 0.067774 | -0.00079049 | -0.0014248 | 0.0010468 | 0.0093383 | 0.0037532 | -1.3967 | 0.062461 | -0.0039136 | 0.010621 | 0.0023285 | 7.8964 | 121.3257 | -0.1236 | 121.4355 | 0.054932 | -0.086975 | -0.14191 | 2.6779 | 121.2845 | -0.17395 | 121.2112 | -0.073242 | -0.14191 | -0.054932 | 0.086975 | -0.14648 | -0.036621 | 0.2655 | 0.068664 | 0.1236 | -0.018311 | 0.036621 | 0.036621 | -0.18768 | -0.26093 | 0.13733 | 0.15564 | 0.068664 | 0.11902 | 0.032043 | 0.17853 | 121.5591 | 0.10071 | 121.3852 | 121.4493 | 121.4584 | 121.5363 | 121.4951 | -121.5958 | -121.6461 | 121.6461 | 121.4218 | 8.107 | 2.8885
1615.7031 | 121.6507 | -0.23346 | 121.4676 | 0.0019074 | 0 | 0.065176 | 0.066065 | 0.0013459 | -0.002493 | -0.0032256 | 0.00018312 | 0.0028988 | -1.3957 | 0.066734 | -0.003059 | 0.010408 | -0.00023491 | 7.8552 | 121.3531 | -0.082397 | 121.3486 | -0.054932 | -0.18768 | -0.20142 | 2.5681 | 121.2799 | -0.16937 | 121.1746 | -0.16937 | -0.21057 | -0.09613 | 0.15106 | -0.11444 | -0.11902 | 0.17853 | 0.032043 | 0.045776 | -0.11902 | -0.10529 | 0.064086 | -0.18768 | -0.29297 | 0.064086 | 0.13733 | 0.022888 | 0.073243 | -0.041198 | 0.027465 | 121.431 | 0 | 121.344 | 121.4355 | 121.4493 | 121.5866 | 121.5134 | -121.55 | -121.637 | 121.582 | 121.4081 | 8.0887 | 2.8015
1617.4688 | 121.7377 | -0.1831 | 121.4493 | 0.032425 | 0 | 0.064108 | 0.06222 | 0.00027771 | -0.00078404 | 0.0012604 | 0.01239 | 0.001617 | -1.3957 | 0.062034 | -0.0043408 | 0.013612 | 0.0019013 | 7.8964 | 121.3211 | -0.086975 | 121.4676 | 0.091553 | -0.073242 | -0.086975 | 2.655 | 121.2479 | -0.14648 | 121.2341 | -0.068665 | -0.09613 | -0.032043 | 0.09613 | -0.12817 | 0.01831 | 0.27466 | 0.09613 | 0.10986 | 0 | 0.013733 | 0.036621 | -0.20142 | -0.21515 | 0.11444 | 0.15106 | 0.086975 | 0.11444 | 0.050354 | 0.17853 | 121.5546 | 0.077819 | 121.3806 | 121.4081 | 121.3943 | 121.5042 | 121.431 | -121.5363 | -121.5958 | 121.6507 | 121.4172 | 8.0795 | 2.8381
1619.1719 | 121.7834 | -0.17853 | 121.4447 | -0.0057221 | 0 | 0.063254 | 0.062647 | -0.0024995 | -0.0029202 | -0.00087583 | 0.00018312 | 0.00012184 | -1.3957 | 0.064597 | -0.0056226 | 0.011049 | 0.0019013 | 7.9468 | 121.3074 | -0.064087 | 121.5042 | 0.16937 | -0.004578 | -0.045776 | 2.7695 | 121.2112 | -0.1236 | 121.3257 | 0.027466 | -0.022888 | 0.009155 | 0.11444 | -0.13733 | 0.059509 | 0.3479 | 0.13275 | 0.17395 | 0.018311 | 0.059509 | 0.054932 | -0.23346 | -0.11902 | 0.20599 | 0.18768 | 0.15564 | 0.13275 | 0.10071 | 0.23346 | 121.5683 | 0.15106 | 121.4493 | 121.3715 | 121.3348 | 121.4859 | 121.3898 | -121.5088 | -121.5683 | 121.6827 | 121.5042 | 8.1253 | 2.948
1620.9375 | 121.7697 | -0.17395 | 121.4584 | -0.0057221 | 0 | 0.062399 | 0.062433 | -0.0046357 | -0.0016384 | -0.0040802 | -0.0028687 | 0.0035396 | -1.394 | 0.060111 | -0.0049818 | 0.0099805 | -0.00023491 | 7.988 | 121.2616 | -0.082397 | 121.5317 | 0.16022 | -0.013733 | -0.068665 | 2.7283 | 121.2296 | -0.1236 | 121.3074 | 0.022888 | -0.009155 | 0 | 0.091553 | -0.19684 | 0.073242 | 0.33417 | 0.10528 | 0.16022 | 0.013732 | 0.068664 | 0.050354 | -0.22888 | -0.15106 | 0.19684 | 0.17395 | 0.16479 | 0.1236 | 0.11444 | 0.24261 | 121.6141 | 0.14648 | 121.431 | 121.344 | 121.3531 | 121.4355 | 121.4035 | -121.5408 | -121.582 | 121.7056 | 121.4813 | 8.1619 | 2.9022
1622.7031 | 121.7148 | -0.20599 | 121.4447 | 0.0019074 | 0 | 0.061758 | 0.064356 | 0.00049131 | -0.0027066 | -0.0040802 | 0.0062865 | 0.002258 | -1.3946 | 0.064384 | -0.003059 | 0.011049 | -0.00087591 | 7.9193 | 121.3165 | -0.086975 | 121.4493 | 0.059509 | -0.073242 | -0.11902 | 2.6459 | 121.2479 | -0.13733 | 121.2433 | -0.064087 | -0.10986 | -0.045776 | 0.11902 | -0.12817 | 0.004578 | 0.2655 | 0.086975 | 0.13275 | -0.032044 | 0.013733 | 0.068665 | -0.19684 | -0.20142 | 0.14191 | 0.16022 | 0.096131 | 0.091553 | 0.027466 | 0.14648 | 121.5363 | 0.073242 | 121.3806 | 121.4035 | 121.3852 | 121.5225 | 121.4539 | -121.5317 | -121.582 | 121.6553 | 121.4493 | 8.1253 | 2.8519
1624.4844 | 121.6919 | -0.21973 | 121.4584 | 0.017166 | 0 | 0.064108 | 0.063929 | 0.00049131 | -0.00078404 | -0.00087583 | 0.00018312 | 0.0046078 | -1.394 | 0.063957 | -0.0066906 | 0.0086987 | -0.0015167 | 7.9788 | 121.3348 | -0.11444 | 121.463 | 0.086975 | -0.082397 | -0.14648 | 2.6871 | 121.2936 | -0.14648 | 121.2433 | -0.082397 | -0.14191 | -0.050354 | 0.10529 | -0.1236 | 0.004578 | 0.3067 | 0.073243 | 0.13733 | -0.032043 | 0.032044 | 0.073243 | -0.16479 | -0.21515 | 0.13733 | 0.16937 | 0.07782 | 0.09613 | 0.004577 | 0.20142 | 121.5775 | 0.064087 | 121.3898 | 121.4493 | 121.4401 | 121.5546 | 121.5134 | -121.5729 | -121.6049 | 121.6827 | 121.463 | 8.1985 | 2.9068
1626.2656 | 121.7331 | -0.18768 | 121.463 | 0.047683 | 0 | 0.065604 | 0.063502 | 0.0017731 | -0.00078404 | -0.00087583 | 0.024597 | 0.00076264 | -1.3944 | 0.071433 | -0.0011364 | 0.0091261 | -2.1314e-05 | 8.02 | 121.3074 | -0.09613 | 121.5408 | 0.16022 | -0.027466 | -0.064087 | 2.71 | 121.2708 | -0.15106 | 121.3165 | -0.045776 | -0.09613 | -0.013733 | 0.091553 | -0.15564 | 0.07782 | 0.3479 | 0.1236 | 0.16022 | 0.032043 | 0.068664 | 0.036621 | -0.19226 | -0.14648 | 0.14191 | 0.17395 | 0.091553 | 0.13733 | 0.054932 | 0.25635 | 121.637 | 0.10529 | 121.4676 | 121.4035 | 121.4218 | 121.4951 | 121.4584 | -121.5591 | -121.6141 | 121.7285 | 121.5042 | 8.2077 | 2.8976
1627.9531 | 121.7056 | -0.22888 | 121.4722 | 0.040054 | 0 | 0.065176 | 0.064997 | -0.00057689 | -0.0012112 | 0.0025422 | 0.0093383 | 0.0043942 | -1.3959 | 0.056907 | -0.004768 | 0.010408 | -0.00066231 | 8.0658 | 121.344 | -0.13275 | 121.431 | 0.045776 | -0.086975 | -0.15106 | 2.6688 | 121.3211 | -0.17395 | 121.2387 | -0.10071 | -0.14191 | -0.059509 | 0.096131 | -0.12817 | -0.041199 | 0.27466 | 0.07782 | 0.14191 | -0.018311 | 0.045776 | 0.054932 | -0.15106 | -0.23346 | 0.12817 | 0.16937 | 0.086975 | 0.11444 | 0.032043 | 0.17853 | 121.5637 | 0.073242 | 121.4127 | 121.4767 | 121.4951 | 121.5729 | 121.55 | -121.6049 | -121.6461 | 121.6599 | 121.4676 | 8.2947 | 2.8976
1629.7344 | 121.7834 | -0.18768 | 121.431 | 0.0019074 | 0 | 0.063681 | 0.063502 | 0.00091851 | -0.0033474 | -0.0010894 | -0.0028687 | 0.001617 | -1.3967 | 0.065025 | -0.0041272 | 0.010835 | -0.0034393 | 8.0429 | 121.2753 | -0.059509 | 121.5042 | 0.1831 | 0 | -0.068665 | 2.7328 | 121.2158 | -0.13275 | 121.3211 | 0.013733 | -0.027466 | 0.009155 | 0.12817 | -0.15564 | 0.073242 | 0.37079 | 0.11902 | 0.18768 | -0.009156 | 0.059509 | 0.054932 | -0.21515 | -0.10986 | 0.20142 | 0.19684 | 0.16022 | 0.14191 | 0.10529 | 0.24261 | 121.5637 | 0.14648 | 121.4539 | 121.3348 | 121.3486 | 121.463 | 121.4035 | -121.4905 | -121.5637 | 121.6919 | 121.5088 | 8.2306 | 2.9205
1631.4375 | 121.7056 | -0.23346 | 121.4676 | 0.024795 | 0 | 0.064536 | 0.064783 | 0.0028411 | -0.001852 | -0.0010894 | 0.0093383 | 0.0043942 | -1.3952 | 0.063957 | -0.0037 | 0.011262 | -2.1314e-05 | 8.0933 | 121.3486 | -0.12817 | 121.4493 | 0.07782 | -0.07782 | -0.12817 | 2.6917 | 121.2891 | -0.15106 | 121.2524 | -0.068665 | -0.1236 | -0.059509 | 0.10528 | -0.11902 | -0.01831 | 0.31128 | 0.10528 | 0.15564 | 0 | 0.050354 | 0.082397 | -0.17853 | -0.21515 | 0.16479 | 0.17395 | 0.10986 | 0.091553 | 0.027466 | 0.20599 | 121.5775 | 0.082397 | 121.4035 | 121.4767 | 121.4401 | 121.582 | 121.5225 | -121.5958 | -121.6187 | 121.6827 | 121.4859 | 8.3267 | 2.9251
1633.2031 | 121.6461 | -0.21057 | 121.4813 | -0.020981 | 0 | 0.060904 | 0.063074 | -0.0033539 | -0.0014248 | -0.0023712 | -0.0089723 | 0.0014034 | -1.3955 | 0.05648 | -0.0056226 | 0.0080579 | -0.0017303 | 8.0933 | 121.3074 | -0.10529 | 121.3898 | 0.022888 | -0.14191 | -0.16937 | 2.5864 | 121.2479 | -0.15564 | 121.1838 | -0.12817 | -0.17853 | -0.11444 | 0.10529 | -0.17395 | -0.091552 | 0.23346 | 0.041198 | 0.068664 | -0.064087 | -0.036621 | 0.054931 | -0.23346 | -0.29755 | 0.082397 | 0.09613 | 0.032043 | 0.041199 | -0.022888 | 0.12817 | 121.4951 | 0.027466 | 121.3394 | 121.4127 | 121.4035 | 121.5179 | 121.4584 | -121.5866 | -121.637 | 121.6003 | 121.3943 | 8.3038 | 2.7969
1634.9844 | 121.6782 | -0.23346 | 121.4722 | 0.024795 | 0 | 0.063895 | 0.06692 | -0.0024995 | -0.003561 | -0.0027984 | 0.01239 | 0.0026852 | -1.3959 | 0.071006 | -0.0051954 | 0.010621 | -0.0017303 | 8.139 | 121.3943 | -0.13733 | 121.4081 | 0.022888 | -0.10986 | -0.14648 | 2.6184 | 121.3211 | -0.19684 | 121.2158 | -0.10986 | -0.16479 | -0.073242 | 0.09613 | -0.07782 | -0.064087 | 0.25635 | 0.086975 | 0.1236 | -0.009155 | 0.027466 | 0.036621 | -0.15106 | -0.25635 | 0.1236 | 0.16022 | 0.068664 | 0.1236 | 0.032043 | 0.16022 | 121.5454 | 0.086975 | 121.4127 | 121.5317 | 121.5179 | 121.6278 | 121.5546 | -121.6095 | -121.669 | 121.6415 | 121.4493 | 8.3725 | 2.8519
1636.7031 | 121.6461 | -0.24261 | 121.463 | -0.013352 | 0 | 0.062827 | 0.063929 | -0.0052765 | -0.0044156 | -0.00087583 | 0.021545 | 0.0041806 | -1.3946 | 0.055625 | -0.0049818 | 0.0091261 | -0.00087591 | 8.0795 | 121.3531 | -0.11444 | 121.4172 | 0.041199 | -0.10071 | -0.14191 | 2.6093 | 121.3257 | -0.19226 | 121.1884 | -0.1236 | -0.17853 | -0.09613 | 0.12817 | -0.10986 | -0.045777 | 0.28381 | 0.10071 | 0.14191 | -0.027466 | 0.013733 | 0.050354 | -0.13733 | -0.27466 | 0.11902 | 0.14649 | 0.064087 | 0.096131 | 0.013733 | 0.15564 | 121.5317 | 0.068665 | 121.3806 | 121.4676 | 121.5179 | 121.5958 | 121.5683 | -121.5775 | -121.6553 | 121.6599 | 121.431 | 8.3221 | 2.8519
1638.4688 | 121.756 | -0.20599 | 121.4676 | 0.0019074 | 0 | 0.064108 | 0.066706 | 0.0039093 | -0.0022794 | -0.0015166 | -0.0028687 | 0.00097624 | -1.3965 | 0.059257 | -0.0011364 | 0.0097669 | -0.0021575 | 8.0521 | 121.3348 | -0.082397 | 121.4081 | 0.059509 | -0.11902 | -0.15106 | 2.6367 | 121.2341 | -0.14191 | 121.2891 | -0.032043 | -0.07782 | 0 | 0.1236 | -0.13275 | -0.059509 | 0.2655 | 0.054932 | 0.086975 | -0.068665 | -0.036622 | 0.064087 | -0.23346 | -0.17853 | 0.17395 | 0.20599 | 0.12817 | 0.14191 | 0.064087 | 0.14191 | 121.4905 | 0.10986 | 121.431 | 121.4172 | 121.376 | 121.5408 | 121.4401 | -121.55 | -121.6095 | 121.6141 | 121.4951 | 8.2581 | 2.8427
1640.1719 | 121.7148 | -0.20599 | 121.4539 | -0.0057221 | 0 | 0.061972 | 0.06457 | -0.00057689 | -0.0022794 | 0.0012604 | -0.0028687 | 0.0020444 | -1.3972 | 0.065666 | -0.00092279 | 0.011689 | 0.0010467 | 8.0566 | 121.3211 | -0.086975 | 121.3898 | 0.022888 | -0.15564 | -0.17853 | 2.5955 | 121.2387 | -0.15106 | 121.2662 | -0.073242 | -0.11444 | -0.022888 | 0.11902 | -0.13275 | -0.064086 | 0.22888 | 0.027466 | 0.050354 | -0.091553 | -0.068665 | 0.054932 | -0.21515 | -0.18768 | 0.13275 | 0.18311 | 0.091553 | 0.12817 | 0.036621 | 0.10986 | 121.4767 | 0.07782 | 121.4172 | 121.4081 | 121.3898 | 121.5271 | 121.4447 | -121.5408 | -121.6049 | 121.5958 | 121.4722 | 8.2626 | 2.8015
1641.9375 | 121.7743 | -0.19226 | 121.4401 | 0.0019074 | 0 | 0.062827 | 0.061152 | -0.0037811 | -0.0022794 | -0.0010894 | -0.0028687 | -0.00051916 | -1.3972 | 0.062034 | -0.0045544 | 0.010194 | 0.00083309 | 8.1482 | 121.2662 | -0.064087 | 121.5225 | 0.19684 | -0.009155 | -0.050354 | 2.7374 | 121.2433 | -0.1236 | 121.2982 | 0.022888 | -0.027466 | -0.009155 | 0.12817 | -0.17395 | 0.082397 | 0.3891 | 0.14191 | 0.18311 | 0.013733 | 0.054932 | 0.068665 | -0.19684 | -0.14191 | 0.21515 | 0.18311 | 0.16479 | 0.11444 | 0.09613 | 0.26093 | 121.5866 | 0.14648 | 121.4218 | 121.3303 | 121.3669 | 121.4584 | 121.4355 | -121.5042 | -121.5637 | 121.7148 | 121.4905 | 8.3405 | 2.9297
1643.7031 | 121.6965 | -0.21515 | 121.4722 | 0.024795 | 0 | 0.064963 | 0.064997 | 0.00049131 | -0.003561 | 0.0023286 | 0.0093383 | 0.0041806 | -1.3931 | 0.067375 | -0.0041272 | 0.011049 | -0.00044851 | 8.1894 | 121.3577 | -0.12817 | 121.4493 | 0.07782 | -0.082397 | -0.13733 | 2.6779 | 121.2845 | -0.13733 | 121.2433 | -0.07782 | -0.11444 | -0.045776 | 0.086975 | -0.11444 | -0.022888 | 0.29297 | 0.07782 | 0.13275 | -0.009155 | 0.045777 | 0.07782 | -0.18768 | -0.22888 | 0.13733 | 0.16937 | 0.10071 | 0.091553 | 0.022888 | 0.20599 | 121.5775 | 0.059509 | 121.3806 | 121.4859 | 121.4218 | 121.5729 | 121.4996 | -121.6003 | -121.6095 | 121.6644 | 121.4584 | 8.4045 | 2.8931
1645.4688 | 121.7743 | -0.19226 | 121.4264 | -0.0057221 | 0 | 0.06304 | 0.062861 | -0.0018585 | -0.003561 | -0.0027984 | -0.0028687 | 0.00097624 | -1.3957 | 0.060966 | -0.003059 | 0.011476 | -0.00023491 | 8.1757 | 121.2708 | -0.059509 | 121.4905 | 0.16479 | 0 | -0.059509 | 2.7557 | 121.2341 | -0.11902 | 121.3028 | 0.009155 | -0.018311 | -0.009155 | 0.13275 | -0.15564 | 0.064087 | 0.35706 | 0.13275 | 0.19226 | 0 | 0.059509 | 0.073242 | -0.19226 | -0.1236 | 0.20142 | 0.18311 | 0.17395 | 0.10986 | 0.10071 | 0.2243 | 121.55 | 0.12817 | 121.4218 | 121.3303 | 121.3531 | 121.463 | 121.4264 | -121.4859 | -121.5454 | 121.6827 | 121.4951 | 8.3679 | 2.948
1647.1875 | 121.6644 | -0.23804 | 121.4951 | 0.055313 | 0 | 0.064108 | 0.06457 | -0.0010041 | -0.0027066 | -0.00023503 | 0.015442 | 0.0026852 | -1.3927 | 0.059898 | -0.006477 | 0.011262 | -0.0013031 | 8.1619 | 121.3348 | -0.15564 | 121.3898 | 0.027466 | -0.11444 | -0.14191 | 2.6367 | 121.3348 | -0.1831 | 121.1929 | -0.12817 | -0.14648 | -0.073242 | 0.082397 | -0.16022 | -0.10529 | 0.2655 | 0.09613 | 0.1236 | 0.013733 | 0.041199 | 0.054932 | -0.16022 | -0.30212 | 0.10986 | 0.16479 | 0.091553 | 0.10986 | 0.036621 | 0.18311 | 121.5454 | 0.054931 | 121.376 | 121.4905 | 121.5179 | 121.5729 | 121.5729 | -121.6507 | -121.6782 | 121.6278 | 121.431 | 8.4 | 2.8748
1648.9531 | 121.6827 | -0.20142 | 121.463 | 0.0095369 | 0 | 0.064108 | 0.066279 | 0.00049131 | -0.0037746 | -0.0010894 | -0.0028687 | 0.0024716 | -1.3946 | 0.061179 | -0.0056226 | 0.0093397 | -0.00087591 | 8.194 | 121.3486 | -0.086975 | 121.4539 | 0.10529 | -0.082397 | -0.1236 | 2.6917 | 121.2891 | -0.15564 | 121.225 | -0.086975 | -0.13733 | -0.054932 | 0.11444 | -0.11444 | -0.009156 | 0.3067 | 0.07782 | 0.11902 | -0.036621 | 0.004578 | 0.045776 | -0.17395 | -0.23804 | 0.11444 | 0.14648 | 0.064087 | 0.10071 | 0.018311 | 0.19226 | 121.5408 | 0.068665 | 121.3806 | 121.4355 | 121.4447 | 121.55 | 121.4905 | -121.55 | -121.6187 | 121.6553 | 121.4264 | 8.3954 | 2.8931
1650.7188 | 121.7789 | -0.19684 | 121.4401 | 0.0019074 | 0 | 0.065176 | 0.061793 | -0.00036309 | -0.0039884 | -0.00044863 | -0.0059205 | -0.00094636 | -1.395 | 0.065879 | -0.0022046 | 0.010621 | -0.0025849 | 8.1482 | 121.3074 | -0.086975 | 121.4584 | 0.10529 | -0.054932 | -0.082397 | 2.6779 | 121.1975 | -0.1236 | 121.2708 | -0.018311 | -0.050354 | 0 | 0.10986 | -0.13275 | 0.01831 | 0.30212 | 0.11444 | 0.14191 | 0.004578 | 0.032043 | 0.073242 | -0.24262 | -0.16937 | 0.17853 | 0.19684 | 0.14648 | 0.1236 | 0.073242 | 0.19226 | 121.5454 | 0.10528 | 121.3943 | 121.3943 | 121.3211 | 121.5042 | 121.3943 | -121.5271 | -121.5637 | 121.6553 | 121.4676 | 8.345 | 2.8748
1652.4688 | 121.6599 | -0.21973 | 121.4722 | 0.0019074 | 0 | 0.063681 | 0.064356 | -0.0012177 | -0.001852 | 0.00019217 | 0.0032349 | 0.0037532 | -1.3967 | 0.061393 | -0.0017774 | 0.0099805 | -0.0017303 | 8.2352 | 121.3303 | -0.10071 | 121.4081 | 0.054932 | -0.12817 | -0.16479 | 2.6596 | 121.2982 | -0.14191 | 121.2067 | -0.10529 | -0.16479 | -0.086975 | 0.11902 | -0.14191 | -0.064087 | 0.27466 | 0.054932 | 0.091553 | -0.064087 | -0.027466 | 0.07782 | -0.17395 | -0.2655 | 0.11444 | 0.13275 | 0.054932 | 0.054932 | -0.022888 | 0.15564 | 121.5088 | 0.036621 | 121.3486 | 121.431 | 121.4401 | 121.55 | 121.5179 | -121.5729 | -121.6141 | 121.6278 | 121.4264 | 8.4549 | 2.8793
1654.25 | 121.6736 | -0.21515 | 121.4493 | 0.0019074 | 0 | 0.063254 | 0.066065 | -0.0012177 | -0.0029202 | -0.0015166 | 0.00018312 | 0.0024716 | -1.3961 | 0.060111 | -0.0043408 | 0.011049 | -0.0017303 | 8.2901 | 121.3394 | -0.09613 | 121.4218 | 0.068665 | -0.11902 | -0.15106 | 2.655 | 121.2845 | -0.15564 | 121.1975 | -0.10071 | -0.15106 | -0.073242 | 0.11902 | -0.10986 | -0.027466 | 0.28381 | 0.064087 | 0.09613 | -0.054932 | -0.022889 | 0.059509 | -0.16479 | -0.25177 | 0.11444 | 0.14191 | 0.064087 | 0.082398 | 0.004578 | 0.16479 | 121.5179 | 0.054932 | 121.3531 | 121.4355 | 121.4401 | 121.5546 | 121.4996 | -121.5454 | -121.6049 | 121.637 | 121.4127 | 8.5052 | 2.8702
1655.9531 | 121.7377 | -0.21515 | 121.4584 | 0.040054 | 0 | 0.066031 | 0.063929 | 0.00027771 | -0.00078404 | 0.0023286 | 0.01239 | 0.002258 | -1.3961 | 0.068443 | -0.003059 | 0.011689 | -0.00087591 | 8.2993 | 121.3348 | -0.10529 | 121.4722 | 0.16937 | -0.068665 | -0.086975 | 2.71 | 121.2662 | -0.16022 | 121.2433 | -0.054932 | -0.082397 | -0.027466 | 0.10986 | -0.1236 | 0.013733 | 0.38452 | 0.12817 | 0.14648 | 0.018311 | 0.036621 | 0.054932 | -0.19226 | -0.21515 | 0.16022 | 0.18768 | 0.13275 | 0.13275 | 0.07782 | 0.27466 | 121.5775 | 0.10528 | 121.4035 | 121.4401 | 121.4264 | 121.55 | 121.4813 | -121.5637 | -121.6187 | 121.6873 | 121.4584 | 8.5144 | 2.9251
1657.6719 | 121.669 | -0.2243 | 121.4859 | -0.0057221 | 0 | 0.064108 | 0.063715 | 0.00091851 | -0.0048428 | -0.0010894 | -0.0028687 | 0.0037532 | -1.3937 | 0.059257 | -0.0051954 | 0.0099805 | 0.0027557 | 8.2626 | 121.3303 | -0.10529 | 121.4218 | 0.068665 | -0.13275 | -0.16022 | 2.6596 | 121.2891 | -0.15564 | 121.1609 | -0.11444 | -0.16937 | -0.07782 | 0.11902 | -0.15564 | -0.064087 | 0.29297 | 0.064087 | 0.091553 | -0.054931 | -0.027465 | 0.068664 | -0.19684 | -0.32501 | 0.10986 | 0.14648 | 0.054931 | 0.07782 | -0.013733 | 0.17395 | 121.5271 | 0.041199 | 121.3165 | 121.4355 | 121.4447 | 121.5546 | 121.5134 | -121.5912 | -121.6415 | 121.6461 | 121.3852 | 8.4869 | 2.8839
1659.4375 | 121.7148 | -0.23346 | 121.4722 | -0.0057221 | 0 | 0.062613 | 0.063288 | -0.0037811 | -0.00057044 | -0.0025848 | 0.00018312 | 0.0020444 | -1.395 | 0.064597 | -0.0017774 | 0.011262 | 0.0010467 | 8.1711 | 121.3394 | -0.09613 | 121.3852 | 0.022888 | -0.17395 | -0.18768 | 2.6184 | 121.2845 | -0.15564 | 121.1838 | -0.11444 | -0.15106 | -0.07782 | 0.13733 | -0.13275 | -0.086975 | 0.25635 | 0.045776 | 0.059509 | -0.091553 | -0.07782 | 0.077819 | -0.18768 | -0.28839 | 0.11902 | 0.15564 | 0.082397 | 0.07782 | 0.004578 | 0.11902 | 121.4813 | 0.041199 | 121.3394 | 121.4355 | 121.4401 | 121.5729 | 121.5179 | -121.5683 | -121.6278 | 121.6187 | 121.4172 | 8.4045 | 2.8519
1661.1406 | 121.7377 | -0.21515 | 121.4584 | 0.0095369 | 0 | 0.062827 | 0.064356 | -0.0039947 | -0.00057044 | 0.00061957 | 0.0032349 | 0.0024716 | -1.3935 | 0.063529 | -0.0045544 | 0.010621 | 0.0031829 | 8.1985 | 121.3257 | -0.086975 | 121.4493 | 0.086975 | -0.068665 | -0.10529 | 2.6505 | 121.257 | -0.14191 | 121.2112 | -0.068665 | -0.09613 | -0.041199 | 0.12817 | -0.13275 | -0.009155 | 0.30212 | 0.10986 | 0.14648 | -0.018311 | 0.01831 | 0.073242 | -0.20142 | -0.24719 | 0.14648 | 0.17395 | 0.11902 | 0.10071 | 0.045777 | 0.17395 | 121.5363 | 0.073242 | 121.3531 | 121.4127 | 121.3989 | 121.5408 | 121.4722 | -121.5454 | -121.6003 | 121.6644 | 121.4264 | 8.4137 | 2.8656
1662.9062 | 121.7697 | -0.17395 | 121.4355 | 0.047683 | 0 | 0.066245 | 0.06457 | 0.00091851 | -0.00057044 | -0.0010894 | 0.01239 | 0.00076264 | -1.3967 | 0.063102 | -0.0015638 | 0.012758 | 0.00061949 | 8.2718 | 121.3074 | -0.10071 | 121.5179 | 0.19684 | -0.045776 | -0.059509 | 2.8107 | 121.257 | -0.15564 | 121.2662 | -0.032043 | -0.054932 | 0.004578 | 0.073242 | -0.12817 | 0.082397 | 0.37079 | 0.11444 | 0.12817 | 0.041199 | 0.054932 | 0.01831 | -0.17853 | -0.16937 | 0.14191 | 0.17853 | 0.11902 | 0.16022 | 0.10071 | 0.29755 | 121.6187 | 0.1236 | 121.4218 | 121.4081 | 121.4127 | 121.4813 | 121.431 | -121.5363 | -121.5912 | 121.6919 | 121.4401 | 8.4457 | 2.9846
1664.6719 | 121.7651 | -0.1831 | 121.4401 | 0.040054 | 0.29672 | 0.065817 | 0.064997 | 0.0022003 | -0.0012112 | 0.0016876 | 0.015442 | 0.0028988 | -1.3927 | 0.062675 | -0.001991 | 0.011476 | -0.0032257 | 8.2672 | 121.3394 | -0.10071 | 121.5134 | 0.18768 | -0.032043 | -0.059509 | 2.7878 | 121.2753 | -0.14191 | 121.2433 | -0.032043 | -0.068665 | -0.013733 | 0.082397 | -0.10071 | 0.073242 | 0.37079 | 0.1236 | 0.15106 | 0.041199 | 0.068665 | 0.041198 | -0.16479 | -0.19684 | 0.15106 | 0.16937 | 0.11444 | 0.12817 | 0.073242 | 0.28839 | 121.6141 | 0.10986 | 121.3852 | 121.4401 | 121.4172 | 121.5225 | 121.4584 | -121.5408 | -121.582 | 121.6965 | 121.4264 | 8.4503 | 2.9709
1666.4375 | 121.7697 | -0.17853 | 121.4493 | 0.040054 | 0 | 0.067526 | 0.063715 | 0.0024139 | 0.00092496 | 0.002115 | 0.0093383 | 0.003326 | -1.3948 | 0.065025 | -0.0011364 | 0.010835 | -0.0021575 | 8.2443 | 121.312 | -0.09613 | 121.5134 | 0.17853 | -0.022888 | -0.036621 | 2.8015 | 121.257 | -0.15564 | 121.2433 | -0.022888 | -0.064087 | -0.009155 | 0.082398 | -0.13733 | 0.064087 | 0.35706 | 0.14191 | 0.15564 | 0.059509 | 0.073242 | 0.022888 | -0.19226 | -0.20599 | 0.15564 | 0.16937 | 0.11444 | 0.14649 | 0.091553 | 0.27466 | 121.6095 | 0.13275 | 121.3989 | 121.4081 | 121.4127 | 121.4905 | 121.4355 | -121.5454 | -121.6049 | 121.6919 | 121.4218 | 8.4229 | 2.98
1668.1406 | 121.8063 | -0.19226 | 121.4355 | -0.0057221 | 0 | 0.063895 | 0.062861 | 0.0011321 | -0.002493 | -0.00023503 | 0.00018312 | 0.00097624 | -1.3952 | 0.063529 | -0.0045544 | 0.011476 | -0.0017303 | 8.1757 | 121.3028 | -0.086975 | 121.4859 | 0.16022 | -0.018311 | -0.054932 | 2.7969 | 121.2799 | -0.12817 | 121.2616 | 0.009155 | -0.013733 | 0.018311 | 0.10529 | -0.13275 | 0.050354 | 0.35248 | 0.13733 | 0.17395 | 0.032043 | 0.068664 | 0.064087 | -0.15564 | -0.17395 | 0.20142 | 0.21057 | 0.17853 | 0.14649 | 0.11444 | 0.24719 | 121.5729 | 0.13733 | 121.3898 | 121.3898 | 121.4081 | 121.4951 | 121.4722 | -121.5225 | -121.5637 | 121.6782 | 121.4539 | 8.3679 | 2.9892
1669.9219 | 121.7056 | -0.20142 | 121.4539 | 0.0019074 | 1.048 | 0.064108 | 0.065211 | -0.0022857 | -0.0029202 | -0.0015166 | 0.00018312 | 0.0048214 | -1.3959 | 0.065879 | -0.0037 | 0.010621 | -2.1314e-05 | 8.075 | 121.3257 | -0.10986 | 121.3943 | 0.036621 | -0.15564 | -0.1831 | 2.6596 | 121.2524 | -0.13733 | 121.1975 | -0.10071 | -0.13275 | -0.041199 | 0.091553 | -0.12817 | -0.059509 | 0.23804 | 0.018311 | 0.045776 | -0.073242 | -0.045777 | 0.064087 | -0.20142 | -0.25635 | 0.10071 | 0.16022 | 0.068665 | 0.09613 | 0.004578 | 0.14648 | 121.5042 | 0.036621 | 121.3348 | 121.4355 | 121.3898 | 121.5271 | 121.4539 | -121.5637 | -121.5912 | 121.5958 | 121.3989 | 8.2764 | 2.861
1671.625 | 121.7102 | -0.22888 | 121.4401 | 0.047683 | 1.2365 | 0.063467 | 0.06692 | -0.00057689 | -0.0037746 | -0.00087583 | 0.01239 | 0.005035 | -1.3942 | 0.059257 | -0.0077588 | 0.011262 | -0.0023713 | 8.1619 | 121.344 | -0.13275 | 121.431 | 0.054932 | -0.086975 | -0.13275 | 2.6962 | 121.312 | -0.19684 | 121.1609 | -0.10071 | -0.16479 | -0.054932 | 0.096131 | -0.096131 | -0.009156 | 0.28381 | 0.096131 | 0.14191 | 0 | 0.045776 | 0.032044 | -0.12817 | -0.27924 | 0.12817 | 0.17395 | 0.064087 | 0.14191 | 0.032043 | 0.18768 | 121.5637 | 0.09613 | 121.3577 | 121.4767 | 121.5088 | 121.5729 | 121.5408 | -121.5729 | -121.637 | 121.6599 | 121.3898 | 8.3908 | 2.9251
1673.3906 | 121.701 | -0.21515 | 121.4676 | 0.047683 | 0.10489 | 0.064108 | 0.067347 | -0.0020721 | -0.0031338 | 0.00019217 | 0.0093383 | 0.0037532 | -1.3922 | 0.057548 | -0.0037 | 0.0093397 | -0.0034393 | 8.2123 | 121.4035 | -0.13275 | 121.4081 | 0.068665 | -0.091553 | -0.12817 | 2.7237 | 121.2891 | -0.15564 | 121.1884 | -0.09613 | -0.12817 | -0.059509 | 0.082398 | -0.064087 | -0.059509 | 0.28381 | 0.086975 | 0.1236 | 0.004577 | 0.041198 | 0.059509 | -0.17853 | -0.27924 | 0.11902 | 0.15564 | 0.086975 | 0.096131 | 0.027466 | 0.20142 | 121.5408 | 0.05951 | 121.344 | 121.5363 | 121.4447 | 121.6187 | 121.5042 | -121.6003 | -121.6232 | 121.6232 | 121.4035 | 8.4274 | 2.9388
1675.0938 | 121.6599 | -0.24261 | 121.4722 | -0.0057221 | 0 | 0.062186 | 0.063929 | 0.0032685 | -0.0031338 | -0.0025848 | 0.00018312 | 0.0020444 | -1.3961 | 0.053703 | -0.0075452 | 0.0093397 | 0.0021149 | 8.139 | 121.344 | -0.09613 | 121.3852 | 0.022888 | -0.13733 | -0.16937 | 2.6779 | 121.2799 | -0.16479 | 121.1288 | -0.12817 | -0.16479 | -0.10529 | 0.14649 | -0.12817 | -0.086975 | 0.2655 | 0.073242 | 0.10529 | -0.073243 | -0.041199 | 0.07782 | -0.19226 | -0.34332 | 0.11444 | 0.13733 | 0.07782 | 0.059509 | 0 | 0.11902 | 121.4813 | 0.036621 | 121.2936 | 121.4401 | 121.4447 | 121.5866 | 121.5225 | -121.5683 | -121.637 | 121.6278 | 121.3715 | 8.3817 | 2.9205
1676.875 | 121.7148 | -0.2243 | 121.4539 | 0.032425 | 0.054047 | 0.062827 | 0.065424 | -0.00057689 | 0.00049776 | 0.00019217 | 0.0062865 | 0.0035396 | -1.3942 | 0.065666 | -0.0034864 | 0.0099805 | -0.0015167 | 8.2626 | 121.344 | -0.1236 | 121.4493 | 0.09613 | -0.086975 | -0.13733 | 2.7557 | 121.2753 | -0.15106 | 121.1929 | -0.068665 | -0.1236 | -0.041199 | 0.10071 | -0.10986 | -0.004577 | 0.32043 | 0.086975 | 0.13733 | -0.013733 | 0.036621 | 0.073242 | -0.17853 | -0.26093 | 0.15564 | 0.18311 | 0.10071 | 0.10986 | 0.027466 | 0.21973 | 121.5729 | 0.082397 | 121.344 | 121.4676 | 121.4264 | 121.5683 | 121.4996 | -121.5775 | -121.6049 | 121.6736 | 121.4172 | 8.4869 | 2.98
1678.6406 | 121.7377 | -0.21515 | 121.4218 | 0.0095369 | 0.50543 | 0.064536 | 0.063288 | -0.0024995 | -0.0037746 | 0.0010468 | 0.0062865 | 0.0014034 | -1.3946 | 0.068015 | -0.0032728 | 0.010194 | 0.0036103 | 8.1711 | 121.3211 | -0.082397 | 121.4355 | 0.11444 | -0.073242 | -0.1236 | 2.7237 | 121.2387 | -0.14648 | 121.2021 | -0.082397 | -0.10071 | -0.050354 | 0.13275 | -0.10071 | 0.013733 | 0.32959 | 0.091553 | 0.14191 | -0.041199 | 0.009155 | 0.068665 | -0.18311 | -0.21973 | 0.13275 | 0.16479 | 0.11444 | 0.09613 | 0.045776 | 0.19684 | 121.5179 | 0.064087 | 121.3486 | 121.4035 | 121.3852 | 121.5363 | 121.4539 | -121.5042 | -121.5683 | 121.6507 | 121.4172 | 8.3862 | 2.9388
1680.4062 | 121.7102 | -0.23346 | 121.4493 | 0.017166 | 0.39798 | 0.063681 | 0.063715 | -0.0029267 | -0.001852 | -0.0015166 | -0.0028687 | 0.002258 | -1.3972 | 0.063102 | -0.0015638 | 0.013612 | 0.0010467 | 8.1299 | 121.3623 | -0.10071 | 121.376 | 0.027466 | -0.17395 | -0.17395 | 2.6871 | 121.2616 | -0.14648 | 121.1838 | -0.11902 | -0.16022 | -0.059509 | 0.13275 | -0.086975 | -0.073242 | 0.26093 | 0.059509 | 0.059509 | -0.073242 | -0.073242 | 0.086975 | -0.18768 | -0.2655 | 0.11444 | 0.17395 | 0.073242 | 0.086975 | -0.013733 | 0.12817 | 121.4767 | 0.027465 | 121.3303 | 121.463 | 121.4081 | 121.5958 | 121.4951 | -121.55 | -121.5958 | 121.6095 | 121.4172 | 8.3633 | 2.9205
1682.125 | 121.7789 | -0.20142 | 121.4539 | 0.0019074 | 0.58554 | 0.062399 | 0.061365 | -0.0033539 | -0.003561 | -0.001303 | -0.0059205 | 0.00097624 | -1.3957 | 0.060966 | -0.0037 | 0.011476 | -0.0053619 | 8.1848 | 121.2891 | -0.064087 | 121.5179 | 0.21973 | 0.004578 | -0.041199 | 2.8702 | 121.2296 | -0.13275 | 121.2845 | 0.018311 | -0.022888 | -0.004578 | 0.13733 | -0.16479 | 0.064087 | 0.42114 | 0.16022 | 0.20599 | 0.022888 | 0.068665 | 0.068665 | -0.2243 | -0.16937 | 0.21973 | 0.19684 | 0.17853 | 0.12817 | 0.10986 | 0.28381 | 121.582 | 0.15106 | 121.4172 | 121.3531 | 121.3623 | 121.4905 | 121.431 | -121.5179 | -121.5866 | 121.7194 | 121.4859 | 8.3862 | 3.0716
1683.8906 | 121.7194 | -0.21515 | 121.4355 | -0.013352 | 1.0504 | 0.066458 | 0.064997 | 0.0034821 | -0.0027066 | -0.0010894 | -0.0059205 | 0.00097624 | -1.394 | 0.062888 | -0.0028454 | 0.012544 | -0.0025849 | 8.0429 | 121.3623 | -0.10071 | 121.3943 | 0.032043 | -0.16479 | -0.1831 | 2.7054 | 121.2799 | -0.14648 | 121.2067 | -0.086975 | -0.11902 | -0.036621 | 0.11444 | -0.073242 | -0.041199 | 0.24719 | 0.032044 | 0.050354 | -0.082397 | -0.064087 | 0.068665 | -0.15564 | -0.22888 | 0.12817 | 0.17853 | 0.09613 | 0.10986 | 0.027465 | 0.13275 | 121.4951 | 0.059509 | 121.3531 | 121.463 | 121.4264 | 121.5775 | 121.4951 | -121.5363 | -121.582 | 121.6095 | 121.4218 | 8.2581 | 2.9205
1685.6562 | 121.6736 | -0.23346 | 121.4905 | -0.0057221 | 2.145 | 0.062186 | 0.062861 | -0.0029267 | -0.0031338 | 0.0010468 | -0.0028687 | 0.00097624 | -1.3976 | 0.060752 | -0.004768 | 0.0099805 | 0.0012603 | 8.0658 | 121.2936 | -0.082397 | 121.4493 | 0.11902 | -0.073242 | -0.11444 | 2.7466 | 121.2753 | -0.15564 | 121.1563 | -0.091553 | -0.14648 | -0.091553 | 0.15106 | -0.19684 | -0.041199 | 0.35248 | 0.11902 | 0.16022 | -0.032044 | 0.009155 | 0.077819 | -0.21515 | -0.33417 | 0.14191 | 0.14191 | 0.086975 | 0.064087 | 0.009156 | 0.20142 | 121.5317 | 0.064087 | 121.312 | 121.376 | 121.431 | 121.5271 | 121.5088 | -121.5729 | -121.6461 | 121.6827 | 121.3898 | 8.2993 | 2.98
1687.4219 | 121.6278 | -0.21515 | 121.4767 | 0.0019074 | 1.8419 | 0.063467 | 0.066065 | -0.0044221 | -0.0033474 | -0.00066223 | -0.0028687 | 0.0020444 | -1.3935 | 0.062248 | -0.0026318 | 0.010835 | -0.00087591 | 7.988 | 121.3623 | -0.10529 | 121.3623 | -0.009155 | -0.20142 | -0.19684 | 2.6505 | 121.2936 | -0.14191 | 121.138 | -0.15564 | -0.20599 | -0.09613 | 0.10986 | -0.11444 | -0.11444 | 0.20599 | 0.018311 | 0.013733 | -0.091552 | -0.09613 | 0.073242 | -0.18311 | -0.33875 | 0.059509 | 0.11902 | 0.009155 | 0.045777 | -0.064087 | 0.096131 | 121.4676 | -0.013733 | 121.2799 | 121.4676 | 121.4355 | 121.5775 | 121.5088 | -121.582 | -121.6187 | 121.5775 | 121.3531 | 8.2031 | 2.8656
1689.125 | 121.7148 | -0.23346 | 121.4447 | 0.0095369 | 2.2394 | 0.062827 | 0.062861 | 0.0032685 | -0.00099764 | -2.1434e-05 | 0.0062865 | 0.00097624 | -1.3969 | 0.058616 | -0.0028454 | 0.0095533 | 0.0016877 | 8.02 | 121.3623 | -0.11444 | 121.4493 | 0.11902 | -0.10071 | -0.13733 | 2.8198 | 121.2799 | -0.17395 | 121.1884 | -0.07782 | -0.11902 | -0.050354 | 0.11902 | -0.082397 | 0.004578 | 0.35248 | 0.09613 | 0.13275 | -0.022888 | 0.013733 | 0.059509 | -0.1648 | -0.25635 | 0.15564 | 0.1831 | 0.11444 | 0.1236 | 0.054931 | 0.23346 | 121.5637 | 0.09613 | 121.3623 | 121.4767 | 121.4539 | 121.5958 | 121.5134 | -121.5591 | -121.6187 | 121.6827 | 121.4218 | 8.2535 | 3.0533
1690.9062 | 121.669 | -0.22888 | 121.4813 | -0.0057221 | 1.8831 | 0.063467 | 0.062433 | -0.0014313 | -0.0054836 | -0.00087583 | 0.021545 | 0.003967 | -1.392 | 0.061179 | -0.007118 | 0.010835 | 0.00040589 | 7.9514 | 121.3394 | -0.11902 | 121.3669 | 0.032043 | -0.13733 | -0.13275 | 2.742 | 121.3303 | -0.21057 | 121.1197 | -0.12817 | -0.17853 | -0.091553 | 0.10986 | -0.14191 | -0.11444 | 0.26093 | 0.096131 | 0.091553 | -0.013732 | -0.01831 | 0.018311 | -0.15106 | -0.36163 | 0.10071 | 0.13733 | 0.050354 | 0.11902 | 0.032043 | 0.15106 | 121.4859 | 0.082397 | 121.3303 | 121.4584 | 121.5408 | 121.5683 | 121.5591 | -121.6003 | -121.6919 | 121.5958 | 121.3486 | 8.1802 | 2.9709
1692.6875 | 121.637 | -0.23804 | 121.4859 | -0.0057221 | 1.7799 | 0.064322 | 0.066706 | 0.0028411 | -0.0056972 | -2.1434e-05 | 0.00018312 | 0.0035396 | -1.3967 | 0.056693 | -0.0039136 | 0.010194 | -0.0032257 | 7.9834 | 121.3486 | -0.09613 | 121.3669 | 0.036621 | -0.16022 | -0.19684 | 2.7054 | 121.2753 | -0.15564 | 121.138 | -0.16479 | -0.20142 | -0.10986 | 0.14191 | -0.13733 | -0.11902 | 0.27466 | 0.041199 | 0.07782 | -0.10071 | -0.064087 | 0.082397 | -0.21057 | -0.3479 | 0.073242 | 0.12817 | 0.036621 | 0.045777 | -0.045776 | 0.13275 | 121.463 | -0.009155 | 121.2936 | 121.4447 | 121.431 | 121.5866 | 121.5134 | -121.582 | -121.6415 | 121.6049 | 121.376 | 8.2214 | 2.9434
1694.3906 | 121.6827 | -0.24261 | 121.4905 | 0.032425 | 1.1689 | 0.064963 | 0.065211 | 0.0049773 | -0.0014248 | 0.00040597 | 0.015442 | 0.0028988 | -1.3918 | 0.053916 | -0.0034864 | 0.010408 | 0.0010467 | 8.0063 | 121.3577 | -0.13275 | 121.3852 | 0.073242 | -0.10986 | -0.12817 | 2.7374 | 121.3303 | -0.19684 | 121.17 | -0.10529 | -0.16022 | -0.073242 | 0.10986 | -0.13275 | -0.10529 | 0.31586 | 0.11444 | 0.13275 | 0.004577 | 0.022888 | 0.045777 | -0.16022 | -0.32043 | 0.13733 | 0.16937 | 0.082398 | 0.1236 | 0.036621 | 0.20599 | 121.5179 | 0.091552 | 121.3669 | 121.4905 | 121.5271 | 121.6003 | 121.5729 | -121.6232 | -121.6873 | 121.6278 | 121.4127 | 8.2489 | 2.98
1696.1562 | 121.7239 | -0.20599 | 121.4447 | 0.032425 | 2.1751 | 0.066458 | 0.06222 | 0.00049131 | 0.00049776 | -0.00066223 | 0.015442 | 0.0014034 | -1.3955 | 0.066947 | -0.0026318 | 0.013612 | 0.0023285 | 8.0383 | 121.344 | -0.086975 | 121.4905 | 0.19684 | -0.041199 | -0.07782 | 2.829 | 121.2479 | -0.14648 | 121.2341 | -0.041199 | -0.082397 | -0.041199 | 0.11902 | -0.10071 | 0.045777 | 0.40283 | 0.12817 | 0.1648 | 0.009155 | 0.045776 | 0.05951 | -0.19684 | -0.21057 | 0.1648 | 0.1648 | 0.1236 | 0.10529 | 0.064087 | 0.28381 | 121.5775 | 0.10529 | 121.3806 | 121.431 | 121.3943 | 121.55 | 121.4539 | -121.5317 | -121.5912 | 121.6965 | 121.4401 | 8.2443 | 3.035
1697.8594 | 121.7102 | -0.19226 | 121.4859 | -0.013352 | 1.8604 | 0.066885 | 0.066706 | -0.00079049 | -0.0031338 | -0.00044863 | -0.0028687 | 0.0018306 | -1.3952 | 0.062675 | -0.0028454 | 0.0097669 | -0.0015167 | 7.9697 | 121.3486 | -0.09613 | 121.3852 | 0.041199 | -0.16022 | -0.16022 | 2.742 | 121.2662 | -0.14648 | 121.2067 | -0.086975 | -0.14191 | -0.041199 | 0.096131 | -0.13733 | -0.10071 | 0.23346 | 0.032044 | 0.032044 | -0.064087 | -0.064087 | 0.045777 | -0.21973 | -0.27924 | 0.10529 | 0.15106 | 0.050354 | 0.10529 | 0.004577 | 0.13733 | 121.4813 | 0.059509 | 121.3531 | 121.4447 | 121.4127 | 121.5408 | 121.4584 | -121.582 | -121.6324 | 121.5775 | 121.3989 | 8.1619 | 2.9343
1699.625 | 121.7194 | -0.22888 | 121.4767 | 0.032425 | 1.3768 | 0.066245 | 0.065424 | 0.0024139 | -0.00057044 | 0.00040597 | 0.0093383 | 0.002258 | -1.3946 | 0.063316 | -0.0056226 | 0.010408 | -0.0051483 | 8.0383 | 121.3486 | -0.1236 | 121.4218 | 0.11444 | -0.082397 | -0.12817 | 2.8152 | 121.3074 | -0.16937 | 121.1975 | -0.091553 | -0.13275 | -0.041199 | 0.10529 | -0.12817 | -0.054932 | 0.34332 | 0.10071 | 0.14649 | -0.004578 | 0.041199 | 0.059509 | -0.16937 | -0.27924 | 0.13733 | 0.18768 | 0.096131 | 0.12817 | 0.036622 | 0.23804 | 121.5454 | 0.07782 | 121.3669 | 121.4722 | 121.4767 | 121.5775 | 121.5363 | -121.6003 | -121.6461 | 121.6507 | 121.4264 | 8.2672 | 3.0441
1701.3281 | 121.7377 | -0.21057 | 121.4447 | 0.032425 | 2.475 | 0.064963 | 0.063715 | 0.0017731 | -0.0022794 | -0.0010894 | 0.0032349 | -9.1956e-05 | -1.3961 | 0.067161 | -0.0026318 | 0.011476 | 0.0029693 | 7.9651 | 121.3257 | -0.10071 | 121.431 | 0.1236 | -0.059509 | -0.086975 | 2.7649 | 121.2753 | -0.14648 | 121.2021 | -0.073242 | -0.10529 | -0.036621 | 0.10986 | -0.11902 | -0.013733 | 0.33417 | 0.1236 | 0.15106 | 0.013733 | 0.041199 | 0.064087 | -0.16937 | -0.24262 | 0.13733 | 0.17395 | 0.10529 | 0.10986 | 0.041198 | 0.2243 | 121.5317 | 0.073242 | 121.3486 | 121.4264 | 121.4218 | 121.5363 | 121.4859 | -121.5454 | -121.5912 | 121.6415 | 121.4127 | 8.1757 | 2.9755
1703.1094 | 121.6736 | -0.23804 | 121.463 | -0.0057221 | 2.2616 | 0.064108 | 0.061152 | 0.0015595 | -0.002493 | -0.00044863 | -0.0028687 | 0.0024716 | -1.3972 | 0.061607 | -0.0060498 | 0.012117 | 0.0016877 | 8.0292 | 121.3211 | -0.10071 | 121.4264 | 0.10529 | -0.09613 | -0.11902 | 2.7649 | 121.2845 | -0.15106 | 121.1426 | -0.10529 | -0.15564 | -0.09613 | 0.13733 | -0.14191 | -0.036621 | 0.34332 | 0.11902 | 0.14191 | -0.018311 | 0.004578 | 0.086975 | -0.17853 | -0.32044 | 0.13275 | 0.14191 | 0.082397 | 0.054932 | -0.004578 | 0.20599 | 121.5271 | 0.045776 | 121.2936 | 121.4218 | 121.4355 | 121.5591 | 121.5225 | -121.5637 | -121.6141 | 121.6644 | 121.3806 | 8.2672 | 3.0029
1704.8125 | 121.6644 | -0.21973 | 121.4905 | -0.013352 | 1.797 | 0.062399 | 0.066279 | 0.00049131 | -0.0022794 | 0.00083317 | 0.0032349 | 0.0024716 | -1.3937 | 0.058189 | -0.0013502 | 0.011903 | 0.00083309 | 7.9605 | 121.3531 | -0.10529 | 121.3577 | 0.022888 | -0.19226 | -0.20142 | 2.6917 | 121.2799 | -0.16479 | 121.1517 | -0.15106 | -0.20599 | -0.091553 | 0.11444 | -0.13733 | -0.13275 | 0.24261 | 0.018311 | 0.027466 | -0.09613 | -0.086975 | 0.054932 | -0.21057 | -0.33875 | 0.068665 | 0.12817 | 0.013733 | 0.073242 | -0.041199 | 0.12817 | 121.463 | 0.013733 | 121.3165 | 121.4584 | 121.4447 | 121.5729 | 121.4996 | -121.5958 | -121.6553 | 121.5775 | 121.3715 | 8.1802 | 2.9114
1706.5781 | 121.6827 | -0.23346 | 121.4905 | 0.0095369 | 2.6861 | 0.065176 | 0.062433 | -0.00057689 | -0.00057044 | -0.0015166 | -0.0059205 | 0.00054904 | -1.3944 | 0.065666 | -0.005409 | 0.011689 | -0.0021575 | 8.0429 | 121.312 | -0.082397 | 121.4401 | 0.14648 | -0.050354 | -0.10529 | 2.8061 | 121.2662 | -0.13275 | 121.17 | -0.09613 | -0.1236 | -0.086975 | 0.15106 | -0.17853 | -0.050354 | 0.37994 | 0.12817 | 0.1831 | -0.022889 | 0.032043 | 0.10071 | -0.2243 | -0.32043 | 0.13733 | 0.14648 | 0.10986 | 0.045776 | 0.009155 | 0.22888 | 121.5225 | 0.036621 | 121.3028 | 121.3943 | 121.3989 | 121.5454 | 121.4996 | -121.5729 | -121.6232 | 121.6736 | 121.4035 | 8.2764 | 3.0395
1708.3438 | 121.7789 | -0.17853 | 121.4493 | -0.0057221 | 1.784 | 0.066672 | 0.064997 | 0.0036957 | 7.0564e-05 | 0.00061957 | 0.018494 | -9.1956e-05 | -1.3937 | 0.05883 | -0.0011364 | 0.012758 | 0.0025421 | 8.075 | 121.3211 | -0.11444 | 121.5363 | 0.21515 | -0.018311 | -0.050354 | 2.8976 | 121.2708 | -0.15106 | 121.2616 | -0.013733 | -0.054932 | 0.013733 | 0.064087 | -0.12817 | 0.086975 | 0.39368 | 0.12817 | 0.16022 | 0.064087 | 0.09613 | 0.027466 | -0.17853 | -0.18768 | 0.16479 | 0.19226 | 0.1236 | 0.16479 | 0.09613 | 0.32959 | 121.6507 | 0.13733 | 121.4127 | 121.4355 | 121.4218 | 121.4996 | 121.4493 | -121.5637 | -121.6003 | 121.7148 | 121.4401 | 8.2535 | 3.0762
1710.0469 | 121.6827 | -0.22888 | 121.4767 | 0.024795 | 1.8224 | 0.065176 | 0.064783 | 0.0043365 | -0.00057044 | -0.001944 | 0.0062865 | 0.00097624 | -1.3955 | 0.068656 | -0.0039136 | 0.012544 | -0.0027985 | 8.0109 | 121.3348 | -0.10986 | 121.4264 | 0.11444 | -0.11444 | -0.12817 | 2.8107 | 121.2982 | -0.16022 | 121.1746 | -0.09613 | -0.15564 | -0.059509 | 0.11902 | -0.14191 | -0.050354 | 0.34332 | 0.10071 | 0.11444 | -0.018311 | -0.004578 | 0.068665 | -0.17853 | -0.30212 | 0.13275 | 0.16937 | 0.073242 | 0.10071 | 0.004577 | 0.2243 | 121.5363 | 0.064087 | 121.3348 | 121.4447 | 121.4584 | 121.5637 | 121.5271 | -121.5866 | -121.637 | 121.6553 | 121.4035 | 8.2397 | 3.0396
1711.8125 | 121.6599 | -0.23346 | 121.463 | -0.0057221 | 1.396 | 0.064963 | 0.066065 | 0.0011321 | -0.0033474 | 0.0027558 | -0.0028687 | 0.002258 | -1.3955 | 0.056907 | -0.003059 | 0.011049 | -0.0032257 | 7.9926 | 121.3623 | -0.10071 | 121.3715 | 0.050354 | -0.17395 | -0.19226 | 2.7283 | 121.3028 | -0.16022 | 121.1243 | -0.16022 | -0.20599 | -0.09613 | 0.13275 | -0.10071 | -0.091553 | 0.28381 | 0.041198 | 0.059509 | -0.091553 | -0.073242 | 0.073242 | -0.16022 | -0.33875 | 0.073242 | 0.13733 | 0.027465 | 0.064087 | -0.045777 | 0.15106 | 121.4722 | 0 | 121.2845 | 121.463 | 121.463 | 121.5958 | 121.5363 | -121.5637 | -121.6232 | 121.6049 | 121.3577 | 8.226 | 2.9617
1713.5938 | 121.7239 | -0.21057 | 121.4584 | -0.013352 | 1.4283 | 0.06304 | 0.063288 | -0.00036309 | -0.003561 | -0.0017304 | 0.0032349 | 0.0020444 | -1.395 | 0.065879 | 0.00057241 | 0.012117 | -0.0010895 | 7.9788 | 121.3531 | -0.10529 | 121.3943 | 0.068665 | -0.15564 | -0.17853 | 2.7786 | 121.257 | -0.15106 | 121.1975 | -0.086975 | -0.13275 | -0.041199 | 0.10529 | -0.10529 | -0.064087 | 0.27924 | 0.032043 | 0.054931 | -0.073242 | -0.050354 | 0.059509 | -0.20142 | -0.26093 | 0.1236 | 0.16937 | 0.07782 | 0.10986 | 0.018311 | 0.17395 | 121.4996 | 0.064087 | 121.3486 | 121.4584 | 121.4081 | 121.5637 | 121.4676 | -121.5637 | -121.6095 | 121.6049 | 121.4081 | 8.1894 | 2.9892
1715.2969 | 121.701 | -0.2243 | 121.463 | -0.0057221 | 1.6062 | 0.06304 | 0.065211 | 0.0024139 | -0.00078404 | -0.0038666 | -0.0059205 | 0.0028988 | -1.395 | 0.063743 | -0.003059 | 0.012758 | -0.0013031 | 7.9742 | 121.3577 | -0.11902 | 121.376 | 0.054932 | -0.17395 | -0.17853 | 2.742 | 121.2708 | -0.15564 | 121.1838 | -0.11444 | -0.14648 | -0.064087 | 0.10529 | -0.10529 | -0.086975 | 0.27924 | 0.045776 | 0.050354 | -0.059509 | -0.054931 | 0.068664 | -0.19226 | -0.27924 | 0.10986 | 0.16022 | 0.07782 | 0.091553 | 0.009156 | 0.17395 | 121.4951 | 0.041199 | 121.3394 | 121.4767 | 121.4264 | 121.582 | 121.4951 | -121.582 | -121.6187 | 121.6003 | 121.4081 | 8.1985 | 2.9663
1717.0625 | 121.6965 | -0.22888 | 121.4767 | 0.047683 | 2.035 | 0.064749 | 0.065424 | -0.0014313 | -0.0037746 | -0.001303 | 0.0093383 | 0.001617 | -1.3935 | 0.068443 | -0.0066906 | 0.011049 | -0.0030121 | 8.0887 | 121.376 | -0.13733 | 121.4355 | 0.091553 | -0.10071 | -0.11444 | 2.829 | 121.312 | -0.18768 | 121.1838 | -0.07782 | -0.1236 | -0.064087 | 0.091553 | -0.10071 | -0.041199 | 0.32044 | 0.11444 | 0.12817 | 0.022888 | 0.036621 | 0.041199 | -0.1648 | -0.29297 | 0.15106 | 0.16479 | 0.10529 | 0.1236 | 0.064087 | 0.22888 | 121.5729 | 0.10986 | 121.3715 | 121.5134 | 121.4996 | 121.6049 | 121.5408 | -121.6141 | -121.6644 | 121.6644 | 121.4127 | 8.3176 | 3.0579
1718.7656 | 121.701 | -0.22888 | 121.463 | 0.0095369 | 2.0709 | 0.062186 | 0.061793 | -0.00079049 | -0.0048428 | 0.001474 | 0.00018312 | 0.0011898 | -1.398 | 0.063957 | -0.0060498 | 0.0097669 | -0.0047211 | 8.107 | 121.2891 | -0.068665 | 121.4584 | 0.16479 | -0.050354 | -0.091553 | 2.829 | 121.2479 | -0.15106 | 121.1563 | -0.091553 | -0.11444 | -0.068665 | 0.16022 | -0.17395 | -0.004578 | 0.39368 | 0.13733 | 0.17853 | -0.022888 | 0.018311 | 0.07782 | -0.21515 | -0.3067 | 0.13733 | 0.16022 | 0.11444 | 0.082397 | 0.036621 | 0.23346 | 121.5271 | 0.059509 | 121.3074 | 121.3577 | 121.3989 | 121.5179 | 121.4767 | -121.5317 | -121.6141 | 121.6873 | 121.3852 | 8.3359 | 3.0579
1720.5469 | 121.6599 | -0.24261 | 121.5042 | 0.0095369 | 5.0844 | 0.061972 | 0.063715 | 0.0013459 | -0.003561 | -0.001944 | -0.0059205 | 0.003326 | -1.3946 | 0.064811 | -0.0058362 | 0.0097669 | -0.0019439 | 8.0521 | 121.344 | -0.11902 | 121.3715 | 0.059509 | -0.13275 | -0.16937 | 2.7374 | 121.2845 | -0.1831 | 121.1151 | -0.13275 | -0.16479 | -0.086975 | 0.1236 | -0.16022 | -0.13275 | 0.30212 | 0.073242 | 0.10986 | -0.050354 | -0.013732 | 0.05951 | -0.21973 | -0.3891 | 0.10986 | 0.15564 | 0.07782 | 0.09613 | 0.01831 | 0.17853 | 121.4905 | 0.050354 | 121.2982 | 121.463 | 121.4676 | 121.5866 | 121.5271 | -121.6232 | -121.6873 | 121.6141 | 121.3577 | 8.2947 | 2.98
1722.3281 | 121.7468 | -0.21973 | 121.4767 | 0.024795 | 1.3454 | 0.066245 | 0.062006 | -0.0035675 | -0.0012112 | -0.0017304 | 0.0032349 | 0.0011898 | -1.3942 | 0.066093 | -0.0028454 | 0.011476 | -0.0025849 | 8.139 | 121.3074 | -0.091553 | 121.431 | 0.13275 | -0.091553 | -0.11444 | 2.7878 | 121.2433 | -0.15106 | 121.2158 | -0.064087 | -0.10071 | -0.041199 | 0.12817 | -0.16937 | -0.045777 | 0.35248 | 0.10529 | 0.12817 | -0.022888 | 0 | 0.068665 | -0.23346 | -0.26093 | 0.15564 | 0.17853 | 0.11902 | 0.10986 | 0.050354 | 0.2243 | 121.5225 | 0.086975 | 121.3669 | 121.3989 | 121.3943 | 121.5271 | 121.463 | -121.5683 | -121.6278 | 121.6507 | 121.4355 | 8.3588 | 3.0075
1724.0938 | 121.669 | -0.26093 | 121.4767 | 0.0095369 | 1.5847 | 0.060904 | 0.063929 | 0.00027771 | -0.006979 | -0.001303 | -0.0059205 | 0.0031124 | -1.3948 | 0.060539 | -0.005409 | 0.0093397 | -0.00023491 | 8.1436 | 121.3165 | -0.11444 | 121.3806 | 0.073242 | -0.13275 | -0.16479 | 2.7786 | 121.2753 | -0.16937 | 121.1151 | -0.13275 | -0.16937 | -0.10986 | 0.14648 | -0.16022 | -0.096131 | 0.33417 | 0.09613 | 0.12817 | -0.050354 | -0.01831 | 0.091552 | -0.20142 | -0.36163 | 0.12817 | 0.15106 | 0.091552 | 0.05951 | 0 | 0.18768 | 121.4951 | 0.036622 | 121.2845 | 121.431 | 121.4447 | 121.5775 | 121.5363 | -121.5912 | -121.6461 | 121.6415 | 121.376 | 8.4045 | 3.0395
1725.7969 | 121.8201 | -0.19684 | 121.4539 | 0.0019074 | 1.3307 | 0.062186 | 0.063715 | -0.00036309 | -0.0044156 | -0.00066223 | -0.0028687 | 0.0020444 | -1.3959 | 0.063316 | -0.0041272 | 0.0095533 | -0.0040801 | 8.2169 | 121.2799 | -0.073242 | 121.4996 | 0.24261 | 0.018311 | -0.041199 | 2.948 | 121.2387 | -0.12817 | 121.2799 | 0.013733 | -0.009155 | -0.013733 | 0.1236 | -0.17395 | 0.045777 | 0.43945 | 0.15564 | 0.21515 | 0.032043 | 0.091553 | 0.068664 | -0.21515 | -0.17395 | 0.21057 | 0.18311 | 0.18768 | 0.11444 | 0.11902 | 0.31586 | 121.5729 | 0.14191 | 121.4081 | 121.3531 | 121.3669 | 121.4767 | 121.4355 | -121.5271 | -121.582 | 121.6965 | 121.4767 | 8.4137 | 3.1448
1727.5781 | 121.7606 | -0.18768 | 121.4539 | 0.024795 | 1.3759 | 0.06539 | 0.064997 | 0.0017731 | -0.0016384 | 0.0025422 | 0.01239 | 0.0031124 | -1.3952 | 0.069724 | -0.0015638 | 0.010621 | 0.0012603 | 8.2443 | 121.2936 | -0.09613 | 121.4859 | 0.21973 | -0.041199 | -0.054932 | 2.8885 | 121.2708 | -0.16022 | 121.225 | -0.050354 | -0.09613 | -0.027466 | 0.091553 | -0.16022 | 0.032044 | 0.40741 | 0.13275 | 0.14648 | 0.041198 | 0.054931 | 0.027466 | -0.1831 | -0.22888 | 0.13733 | 0.16022 | 0.091553 | 0.13275 | 0.064087 | 0.31586 | 121.582 | 0.10986 | 121.3852 | 121.3898 | 121.431 | 121.4813 | 121.4584 | -121.55 | -121.6141 | 121.6736 | 121.4127 | 8.432 | 3.0762
1729.3594 | 121.7422 | -0.21515 | 121.4767 | -0.0057221 | 2.2409 | 0.063467 | 0.063502 | 0.00070491 | -0.0037746 | -0.00066223 | -0.0059205 | -0.00030556 | -1.3969 | 0.064811 | -0.0056226 | 0.010835 | -0.00066231 | 8.3176 | 121.2753 | -0.082397 | 121.4951 | 0.19684 | -0.018311 | -0.073242 | 2.916 | 121.2616 | -0.15106 | 121.2158 | -0.032043 | -0.064087 | -0.027466 | 0.13275 | -0.20142 | 0.01831 | 0.41199 | 0.14191 | 0.19684 | 0.009155 | 0.064086 | 0.064087 | -0.21515 | -0.26093 | 0.18311 | 0.18768 | 0.15106 | 0.1236 | 0.086975 | 0.27924 | 121.5775 | 0.11902 | 121.3669 | 121.3577 | 121.4127 | 121.4905 | 121.4767 | -121.5591 | -121.6278 | 121.7102 | 121.431 | 8.5327 | 3.1311
1731.0469 | 121.7789 | -0.19226 | 121.4493 | 0.0019074 | 2.741 | 0.06304 | 0.06457 | -0.0044221 | -0.0037746 | -0.0015166 | 0.00018312 | -0.00051916 | -1.3931 | 0.058189 | -0.0015638 | 0.0089123 | -0.00066231 | 8.2672 | 121.3028 | -0.10071 | 121.4722 | 0.16479 | -0.059509 | -0.091553 | 2.9114 | 121.2341 | -0.14191 | 121.2616 | -0.018311 | -0.054932 | 0 | 0.091553 | -0.14648 | 0.022888 | 0.35706 | 0.10071 | 0.13275 | 0.009155 | 0.041199 | 0.050354 | -0.21515 | -0.18768 | 0.17395 | 0.19226 | 0.13733 | 0.14191 | 0.086975 | 0.2655 | 121.5729 | 0.1236 | 121.4035 | 121.4035 | 121.376 | 121.4951 | 121.4264 | -121.55 | -121.5912 | 121.6644 | 121.4539 | 8.4595 | 3.1036
1732.8281 | 121.7422 | -0.21515 | 121.4676 | 0.047683 | 3.0982 | 0.066458 | 0.066279 | -0.00057689 | -0.003561 | 0.0010468 | 0.0062865 | 0.002258 | -1.3952 | 0.066093 | -0.0062634 | 0.011903 | 0.0029693 | 8.2993 | 121.3028 | -0.10529 | 121.4539 | 0.16022 | -0.073242 | -0.091553 | 2.8702 | 121.2799 | -0.16937 | 121.2067 | -0.073242 | -0.091553 | -0.041199 | 0.10986 | -0.16479 | -0.013733 | 0.37537 | 0.1236 | 0.14191 | 0.013733 | 0.032044 | 0.045776 | -0.18768 | -0.26093 | 0.14191 | 0.17395 | 0.1236 | 0.12817 | 0.07782 | 0.2655 | 121.5591 | 0.096131 | 121.376 | 121.4081 | 121.4493 | 121.5179 | 121.4951 | -121.5729 | -121.637 | 121.669 | 121.4218 | 8.5144 | 3.0853
1734.5312 | 121.7697 | -0.19684 | 121.4447 | 0.0019074 | 2.6927 | 0.067954 | 0.06457 | -0.0024995 | -0.0037746 | -0.0038666 | -0.0028687 | 0.00012184 | -1.3965 | 0.061179 | -0.003059 | 0.011689 | -0.00087591 | 8.3771 | 121.2845 | -0.064087 | 121.4996 | 0.2243 | -0.027466 | -0.054932 | 2.9617 | 121.2433 | -0.13275 | 121.2387 | 0.009155 | -0.032043 | -0.009155 | 0.13275 | -0.16022 | 0.054932 | 0.42114 | 0.14191 | 0.16937 | 0.009155 | 0.036621 | 0.064087 | -0.20142 | -0.20599 | 0.20599 | 0.18768 | 0.1648 | 0.1236 | 0.10071 | 0.28839 | 121.5637 | 0.14191 | 121.3715 | 121.3486 | 121.376 | 121.4813 | 121.4401 | -121.5088 | -121.5775 | 121.6965 | 121.4355 | 8.5739 | 3.1586
1736.2969 | 121.6553 | -0.24261 | 121.463 | 0.0019074 | 3.0104 | 0.064322 | 0.066065 | 0.0030547 | -0.003561 | -0.001303 | 0.00018312 | 0.003967 | -1.3944 | 0.058402 | -0.0026318 | 0.010194 | -0.0010895 | 8.313 | 121.312 | -0.11444 | 121.3852 | 0.082397 | -0.16937 | -0.17395 | 2.8015 | 121.2891 | -0.16022 | 121.1334 | -0.16479 | -0.19684 | -0.11444 | 0.12817 | -0.15106 | -0.07782 | 0.32501 | 0.068665 | 0.073242 | -0.059509 | -0.054932 | 0.082398 | -0.17395 | -0.32959 | 0.07782 | 0.12817 | 0.045777 | 0.045776 | -0.036621 | 0.19684 | 121.4996 | -0.004578 | 121.2936 | 121.4264 | 121.4493 | 121.5546 | 121.5317 | -121.5775 | -121.6232 | 121.6278 | 121.376 | 8.5556 | 3.0441
1738 | 121.6919 | -0.24261 | 121.4584 | -0.0057221 | 2.9749 | 0.064322 | 0.063929 | -0.00057689 | -0.0020658 | -2.1434e-05 | 0.00018312 | -0.00073276 | -1.3946 | 0.057975 | -0.0034864 | 0.011903 | -0.00023491 | 8.3084 | 121.3531 | -0.11444 | 121.3623 | 0.054932 | -0.18768 | -0.18768 | 2.8015 | 121.2799 | -0.16937 | 121.1472 | -0.14648 | -0.18768 | -0.09613 | 0.12817 | -0.10529 | -0.09613 | 0.29755 | 0.054932 | 0.054932 | -0.073242 | -0.073242 | 0.073242 | -0.17853 | -0.31128 | 0.096131 | 0.14649 | 0.054932 | 0.073243 | -0.01831 | 0.16937 | 121.4767 | 0.022889 | 121.3165 | 121.4676 | 121.4493 | 121.5958 | 121.5225 | -121.5729 | -121.6278 | 121.6049 | 121.3898 | 8.551 | 3.0441
1739.7656 | 121.7148 | -0.22888 | 121.4813 | 0.0019074 | 3.1507 | 0.06069 | 0.063288 | 0.00049131 | -0.0037746 | -0.00044863 | -0.0059205 | 0.00076264 | -1.3965 | 0.063316 | -0.007118 | 0.010194 | -0.0025849 | 8.4183 | 121.2799 | -0.07782 | 121.4539 | 0.1831 | -0.059509 | -0.086975 | 2.8976 | 121.2708 | -0.15106 | 121.1746 | -0.086975 | -0.1236 | -0.07782 | 0.15106 | -0.20142 | -0.027466 | 0.41199 | 0.14191 | 0.16937 | -0.009155 | 0.018311 | 0.07782 | -0.21057 | -0.3067 | 0.14191 | 0.15106 | 0.10529 | 0.073242 | 0.027466 | 0.26092 | 121.5317 | 0.064087 | 121.3257 | 121.3577 | 121.4218 | 121.5088 | 121.4996 | -121.5591 | -121.6324 | 121.6827 | 121.4035 | 8.6472 | 3.1265
1741.4688 | 121.756 | -0.21057 | 121.463 | 0.040054 | 3.0546 | 0.065604 | 0.06457 | -0.0037811 | -0.00099764 | 0.0012604 | 0.0093383 | 0.0037532 | -1.3957 | 0.063743 | -0.0028454 | 0.010408 | 0.0021149 | 8.432 | 121.3074 | -0.10529 | 121.4539 | 0.20142 | -0.050354 | -0.09613 | 2.8931 | 121.2753 | -0.16022 | 121.2158 | -0.073242 | -0.10529 | -0.050354 | 0.10529 | -0.15564 | -0.009156 | 0.41199 | 0.11444 | 0.16022 | 0.009156 | 0.054932 | 0.050354 | -0.18768 | -0.24719 | 0.13733 | 0.16022 | 0.10529 | 0.10986 | 0.054931 | 0.3067 | 121.5591 | 0.086975 | 121.376 | 121.4127 | 121.4355 | 121.5179 | 121.4859 | -121.5683 | -121.6232 | 121.6644 | 121.4264 | 8.6426 | 3.1036
1743.2344 | 121.7102 | -0.22888 | 121.4951 | 0.040054 | 3.0702 | 0.064536 | 0.066706 | 0.00049131 | -0.0014248 | 0.003183 | 0.0093383 | 0.0035396 | -1.3952 | 0.059898 | -0.004768 | 0.010194 | -0.0015167 | 8.5052 | 121.3486 | -0.15564 | 121.4127 | 0.10986 | -0.086975 | -0.13275 | 2.8656 | 121.3028 | -0.1831 | 121.17 | -0.09613 | -0.13733 | -0.068665 | 0.073242 | -0.14648 | -0.082397 | 0.33875 | 0.096131 | 0.14191 | 0.022889 | 0.068665 | 0.045777 | -0.19226 | -0.32501 | 0.13275 | 0.16022 | 0.091553 | 0.11444 | 0.045776 | 0.2655 | 121.5683 | 0.086975 | 121.3531 | 121.5042 | 121.4859 | 121.5775 | 121.5317 | -121.6507 | -121.6782 | 121.6415 | 121.3989 | 8.7341 | 3.0945
1745.0156 | 121.7194 | -0.2243 | 121.4539 | 0.0019074 | 3.4195 | 0.066031 | 0.06457 | 0.0015595 | -0.0033474 | -0.00044863 | 0.00018312 | 0.0028988 | -1.3965 | 0.062034 | -0.00070919 | 0.012117 | 0.0016877 | 8.4686 | 121.344 | -0.09613 | 121.3669 | 0.086975 | -0.1831 | -0.1831 | 2.8427 | 121.2799 | -0.16479 | 121.1838 | -0.10529 | -0.15564 | -0.059509 | 0.12817 | -0.10986 | -0.086975 | 0.31128 | 0.041199 | 0.041199 | -0.086975 | -0.086975 | 0.059509 | -0.17395 | -0.27008 | 0.11902 | 0.16479 | 0.068664 | 0.10529 | 0.009155 | 0.1831 | 121.463 | 0.059509 | 121.3486 | 121.4401 | 121.4447 | 121.5683 | 121.5042 | -121.55 | -121.6187 | 121.5912 | 121.4081 | 8.6929 | 3.067
1746.7969 | 121.7834 | -0.19226 | 121.4355 | -0.0057221 | 3.4366 | 0.066458 | 0.063074 | 0.0024139 | -0.0016384 | -0.00044863 | 0.00018312 | 0.0020444 | -1.3967 | 0.06182 | -0.0037 | 0.012758 | -0.0013031 | 8.5602 | 121.3028 | -0.086975 | 121.4859 | 0.20599 | -0.064087 | -0.073242 | 2.9709 | 121.2021 | -0.16479 | 121.2662 | -0.013733 | -0.054932 | -0.004578 | 0.10529 | -0.13275 | 0.050354 | 0.39826 | 0.11902 | 0.12817 | 0.013733 | 0.022888 | 0.027466 | -0.23346 | -0.16937 | 0.17853 | 0.18768 | 0.13733 | 0.16022 | 0.10986 | 0.29297 | 121.5729 | 0.15106 | 121.431 | 121.3898 | 121.3669 | 121.4951 | 121.3943 | -121.5225 | -121.6003 | 121.6782 | 121.4584 | 8.7524 | 3.1631
1748.5 | 121.6599 | -0.24719 | 121.4447 | -0.013352 | 3.3278 | 0.064108 | 0.062647 | -0.0018585 | -0.0037746 | -0.0032256 | -0.0028687 | 0.0028988 | -1.3965 | 0.063957 | -0.0037 | 0.011049 | -2.1314e-05 | 8.4961 | 121.3348 | -0.11444 | 121.3943 | 0.086975 | -0.16022 | -0.16937 | 2.8473 | 121.257 | -0.17853 | 121.1609 | -0.15106 | -0.20142 | -0.11444 | 0.13275 | -0.10986 | -0.050354 | 0.33417 | 0.077819 | 0.086975 | -0.054932 | -0.045776 | 0.068664 | -0.18768 | -0.28381 | 0.09613 | 0.13275 | 0.045776 | 0.064087 | -0.022888 | 0.20142 | 121.5088 | 0.027466 | 121.3394 | 121.4493 | 121.4355 | 121.582 | 121.5042 | -121.5591 | -121.6232 | 121.6415 | 121.4081 | 8.7433 | 3.0945
1750.25 | 121.7422 | -0.23346 | 121.4447 | 0.0095369 | 3.1759 | 0.064963 | 0.063715 | -0.0012177 | -0.00078404 | 0.00019217 | 0.0032349 | -0.00094636 | -1.3959 | 0.066734 | -0.0041272 | 0.011689 | 0.0016877 | 8.5419 | 121.3028 | -0.09613 | 121.4401 | 0.16479 | -0.073242 | -0.10071 | 2.8793 | 121.2524 | -0.17853 | 121.1838 | -0.073242 | -0.11444 | -0.064087 | 0.13733 | -0.14191 | -0.004577 | 0.39825 | 0.13275 | 0.16022 | -0.004578 | 0.022888 | 0.054931 | -0.19226 | -0.26093 | 0.16022 | 0.16937 | 0.11902 | 0.11444 | 0.064087 | 0.26092 | 121.5363 | 0.10529 | 121.3623 | 121.3989 | 121.431 | 121.5363 | 121.4859 | -121.5408 | -121.6232 | 121.6736 | 121.4172 | 8.7753 | 3.1128
1752.0312 | 121.7972 | -0.17853 | 121.431 | -0.020981 | 3.1888 | 0.063254 | 0.060938 | -0.0044221 | -0.0054836 | -0.0010894 | 0.0062865 | 0.0014034 | -1.3957 | 0.065025 | -0.0058362 | 0.011476 | -0.0019439 | 8.5922 | 121.2524 | -0.09613 | 121.5179 | 0.2655 | -0.004578 | -0.045776 | 3.0029 | 121.2296 | -0.13275 | 121.2387 | 0.013733 | -0.032043 | -0.013733 | 0.082398 | -0.17853 | 0.086975 | 0.44403 | 0.13275 | 0.17395 | 0.050354 | 0.091552 | 0.045777 | -0.20142 | -0.19226 | 0.19226 | 0.16479 | 0.14648 | 0.11902 | 0.10071 | 0.36163 | 121.6141 | 0.14648 | 121.3715 | 121.3486 | 121.3623 | 121.431 | 121.4081 | -121.5271 | -121.5637 | 121.6965 | 121.4172 | 8.7708 | 3.1815
1753.75 | 121.6461 | -0.23804 | 121.4951 | -0.0057221 | 3.9016 | 0.064749 | 0.065424 | 0.00091851 | -0.003561 | -0.00044863 | 0.018494 | 0.0024716 | -1.3903 | 0.059684 | -0.0083996 | 0.010621 | -0.0013031 | 8.5327 | 121.3531 | -0.16022 | 121.3943 | 0.10529 | -0.12817 | -0.13275 | 2.8839 | 121.2936 | -0.19684 | 121.1197 | -0.14191 | -0.1831 | -0.10529 | 0.07782 | -0.14191 | -0.10071 | 0.34332 | 0.10529 | 0.10986 | 0.027466 | 0.032043 | 0.041199 | -0.20142 | -0.37537 | 0.09613 | 0.13275 | 0.054932 | 0.091552 | 0.013733 | 0.2655 | 121.5546 | 0.054931 | 121.3165 | 121.5134 | 121.4905 | 121.5912 | 121.5317 | -121.6553 | -121.6919 | 121.6324 | 121.3577 | 8.7708 | 3.1219
1755.5156 | 121.7606 | -0.21057 | 121.4355 | 0.055313 | 5.6497 | 0.064108 | 0.066279 | 0.0017731 | -0.0020658 | -0.001944 | 0.021545 | 0.0018306 | -1.395 | 0.060966 | -0.0011364 | 0.011689 | 0.00019229 | 8.6014 | 121.3074 | -0.10986 | 121.4951 | 0.25635 | -0.050354 | -0.041199 | 2.9709 | 121.2387 | -0.16479 | 121.2158 | -0.064087 | -0.10071 | -0.032043 | 0.10071 | -0.12817 | 0.059509 | 0.46692 | 0.16937 | 0.16022 | 0.068664 | 0.059509 | 0.045776 | -0.19684 | -0.21973 | 0.14648 | 0.17853 | 0.10986 | 0.13275 | 0.064087 | 0.36621 | 121.6049 | 0.10071 | 121.3806 | 121.4172 | 121.4035 | 121.5179 | 121.4493 | -121.5454 | -121.6003 | 121.7056 | 121.4264 | 8.8119 | 3.1815
1757.2969 | 121.7422 | -0.2243 | 121.431 | 0.017166 | 5.4335 | 0.063681 | 0.065211 | -0.0016449 | -0.0029202 | -0.0015166 | 0.0032349 | 0.0020444 | -1.3946 | 0.068656 | -0.0037 | 0.011903 | 0.0025421 | 8.5876 | 121.312 | -0.1236 | 121.4127 | 0.17395 | -0.10071 | -0.11444 | 2.8702 | 121.2524 | -0.17853 | 121.1884 | -0.086975 | -0.10071 | -0.054932 | 0.10071 | -0.11902 | -0.01831 | 0.39825 | 0.10986 | 0.1236 | 0.009155 | 0.022888 | 0.045776 | -0.17853 | -0.24262 | 0.13733 | 0.16937 | 0.1236 | 0.1236 | 0.07782 | 0.29755 | 121.5363 | 0.091553 | 121.3669 | 121.4355 | 121.431 | 121.5363 | 121.4767 | -121.5546 | -121.6095 | 121.637 | 121.4127 | 8.8119 | 3.0945
1759 | 121.7422 | -0.21057 | 121.4584 | 0.024795 | 5.47 | 0.065176 | 0.062861 | 6.4114e-05 | -0.00078404 | -0.0021576 | 0.0093383 | 0.0020444 | -1.3931 | 0.063316 | -0.0028454 | 0.010621 | -0.0027985 | 8.6655 | 121.3074 | -0.10529 | 121.4401 | 0.18768 | -0.09613 | -0.10529 | 2.8976 | 121.2479 | -0.17395 | 121.1884 | -0.068665 | -0.11902 | -0.059509 | 0.10529 | -0.15106 | -0.01831 | 0.39825 | 0.10529 | 0.11444 | 0 | 0.009156 | 0.036621 | -0.21057 | -0.27008 | 0.14191 | 0.15106 | 0.091552 | 0.11444 | 0.054931 | 0.29297 | 121.5454 | 0.10528 | 121.3623 | 121.4127 | 121.4218 | 121.5179 | 121.4584 | -121.5637 | -121.6324 | 121.6507 | 121.3989 | 8.876 | 3.1082
1760.7656 | 121.6553 | -0.27466 | 121.4813 | -0.0057221 | 5.215 | 0.063895 | 0.063715 | -0.00014949 | -0.0033474 | 0.00040597 | 0.024597 | 0.003326 | -1.3944 | 0.050498 | -0.007118 | 0.011049 | -0.00023491 | 8.5922 | 121.3257 | -0.12817 | 121.3898 | 0.10529 | -0.10986 | -0.13733 | 2.8885 | 121.2936 | -0.21973 | 121.1197 | -0.16479 | -0.1831 | -0.10986 | 0.14648 | -0.15564 | -0.091552 | 0.37994 | 0.13733 | 0.1648 | -0.009155 | 0.018311 | 0.054931 | -0.18768 | -0.36163 | 0.10986 | 0.1648 | 0.091553 | 0.10986 | 0.036622 | 0.23346 | 121.5179 | 0.054932 | 121.3394 | 121.4539 | 121.5134 | 121.6003 | 121.5683 | -121.6095 | -121.7011 | 121.6644 | 121.3943 | 8.8669 | 3.1631
1762.5312 | 121.7422 | -0.2243 | 121.4447 | 0.024795 | 5.1767 | 0.067313 | 0.063502 | -0.00036309 | -0.0031338 | -0.0017304 | 0.0093383 | 0.0031124 | -1.3959 | 0.070579 | -0.0032728 | 0.010835 | -0.00023491 | 8.638 | 121.3028 | -0.1236 | 121.4355 | 0.19684 | -0.086975 | -0.086975 | 2.9251 | 121.2616 | -0.16022 | 121.1975 | -0.07782 | -0.10986 | -0.064087 | 0.10071 | -0.14191 | -0.009155 | 0.42114 | 0.13733 | 0.13733 | 0.036621 | 0.036621 | 0.064087 | -0.18311 | -0.24719 | 0.14648 | 0.16022 | 0.11444 | 0.09613 | 0.050354 | 0.32043 | 121.5591 | 0.082397 | 121.3577 | 121.4264 | 121.4218 | 121.5271 | 121.4859 | -121.5683 | -121.6049 | 121.6599 | 121.4218 | 8.8623 | 3.1494
1764.2969 | 121.7789 | -0.19684 | 121.4355 | 0.055313 | 5.2205 | 0.06539 | 0.065211 | 0.00027771 | 7.0564e-05 | -2.1434e-05 | 0.0093383 | 0.0026852 | -1.395 | 0.063316 | -0.0022046 | 0.010408 | -0.0019439 | 8.757 | 121.3211 | -0.11902 | 121.5271 | 0.27466 | -0.032043 | -0.041199 | 3.0258 | 121.2479 | -0.17395 | 121.257 | -0.032043 | -0.068665 | -0.027466 | 0.077819 | -0.11444 | 0.091553 | 0.4715 | 0.15564 | 0.1648 | 0.07782 | 0.086976 | 0.022888 | -0.18768 | -0.17853 | 0.1648 | 0.16937 | 0.12817 | 0.14648 | 0.10528 | 0.39368 | 121.6461 | 0.14191 | 121.431 | 121.4401 | 121.4218 | 121.5179 | 121.4447 | -121.5546 | -121.6095 | 121.7239 | 121.4539 | 8.9539 | 3.2227
1766.0625 | 121.6553 | -0.27008 | 121.463 | -0.013352 | 5.5057 | 0.062613 | 0.062006 | -0.00079049 | -0.0020658 | -0.0025848 | -0.0059205 | 0.0043942 | -1.3957 | 0.056053 | -0.008827 | 0.011262 | -0.0021575 | 8.638 | 121.2799 | -0.11902 | 121.376 | 0.09613 | -0.14191 | -0.16022 | 2.8564 | 121.2936 | -0.17853 | 121.1105 | -0.15106 | -0.18768 | -0.12817 | 0.15106 | -0.18311 | -0.086975 | 0.36621 | 0.10986 | 0.12817 | -0.041198 | -0.022888 | 0.091553 | -0.16937 | -0.35248 | 0.11902 | 0.14191 | 0.082398 | 0.050354 | -0.009155 | 0.21515 | 121.4951 | 0.027466 | 121.2891 | 121.3989 | 121.4722 | 121.55 | 121.5637 | -121.582 | -121.6415 | 121.6461 | 121.3806 | 8.9081 | 3.1265
1767.7812 | 121.7834 | -0.21973 | 121.4218 | 0.0019074 | 5.3568 | 0.064108 | 0.063715 | -0.00057689 | -0.0056972 | -0.00087583 | 0.0032349 | 0.0018306 | -1.3955 | 0.06417 | -0.001991 | 0.013185 | -0.0013031 | 8.6472 | 121.3257 | -0.10071 | 121.4493 | 0.20599 | -0.082397 | -0.10529 | 2.9709 | 121.2387 | -0.16479 | 121.2616 | -0.027466 | -0.07782 | -0.013733 | 0.11902 | -0.09613 | 0.027466 | 0.42572 | 0.11444 | 0.13733 | -0.004578 | 0.018311 | 0.054932 | -0.18311 | -0.16022 | 0.19226 | 0.20599 | 0.14191 | 0.15106 | 0.086975 | 0.3067 | 121.55 | 0.13733 | 121.4264 | 121.4264 | 121.4035 | 121.5454 | 121.4584 | -121.5225 | -121.5866 | 121.669 | 121.4813 | 8.8669 | 3.1906
1769.5312 | 121.7972 | -0.20142 | 121.4172 | 0.0019074 | 5.2686 | 0.063681 | 0.063074 | 0.0011321 | -0.0016384 | -0.0032256 | 0.00018312 | 0.00033544 | -1.3987 | 0.059898 | -0.0013502 | 0.011262 | -0.0042939 | 8.6929 | 121.3165 | -0.09613 | 121.4813 | 0.24261 | -0.036621 | -0.059509 | 3.0258 | 121.2112 | -0.15106 | 121.2616 | 0.004578 | -0.018311 | -0.004578 | 0.10529 | -0.10071 | 0.064087 | 0.44403 | 0.14191 | 0.1648 | 0.036621 | 0.059509 | 0.050354 | -0.20599 | -0.15564 | 0.20599 | 0.19684 | 0.18311 | 0.14648 | 0.13275 | 0.33874 | 121.5775 | 0.15564 | 121.4127 | 121.4127 | 121.3623 | 121.5179 | 121.4127 | -121.5134 | -121.5683 | 121.6827 | 121.463 | 8.8943 | 3.2272
1771.3125 | 121.7148 | -0.23346 | 121.4355 | -0.013352 | 5.3577 | 0.064322 | 0.064142 | 0.0024139 | -0.0027066 | -0.00087583 | -0.0059205 | 0.002258 | -1.395 | 0.058616 | -0.0024182 | 0.011903 | -0.0019439 | 8.6197 | 121.3303 | -0.14648 | 121.3715 | 0.10529 | -0.17395 | -0.17395 | 2.9022 | 121.2708 | -0.17853 | 121.1884 | -0.10986 | -0.15106 | -0.07782 | 0.086975 | -0.10529 | -0.064087 | 0.33875 | 0.059509 | 0.059509 | -0.027466 | -0.027466 | 0.054931 | -0.16479 | -0.24719 | 0.1236 | 0.15564 | 0.082397 | 0.10071 | 0.027466 | 0.25177 | 121.5179 | 0.068665 | 121.3669 | 121.4767 | 121.4493 | 121.5637 | 121.5042 | -121.582 | -121.6141 | 121.6049 | 121.4218 | 8.8531 | 3.1357
1773.0938 | 121.7697 | -0.20599 | 121.4401 | -0.0057221 | 5.0682 | 0.063895 | 0.064142 | -0.0033539 | -0.0037746 | 0.00061957 | -0.0028687 | -0.00030556 | -1.3944 | 0.062034 | -0.008186 | 0.010621 | -0.0021575 | 8.7112 | 121.257 | -0.10071 | 121.4905 | 0.25635 | -0.032043 | -0.059509 | 3.0167 | 121.2891 | -0.15564 | 121.2158 | -0.041199 | -0.050354 | -0.032043 | 0.10529 | -0.18311 | 0.050354 | 0.46234 | 0.14649 | 0.17395 | 0.041199 | 0.068665 | 0.050354 | -0.15106 | -0.22431 | 0.1648 | 0.17395 | 0.15564 | 0.1236 | 0.10529 | 0.35706 | 121.5912 | 0.11444 | 121.3715 | 121.3577 | 121.4447 | 121.463 | 121.4951 | -121.5408 | -121.5958 | 121.6965 | 121.4218 | 8.9172 | 3.2227
1774.875 | 121.7056 | -0.24261 | 121.4676 | 0.0095369 | 4.7781 | 0.064536 | 0.064142 | 0.0019867 | -0.0046292 | -0.00044863 | 0.00018312 | 0.0071712 | -1.3944 | 0.065025 | -0.0043408 | 0.011903 | -0.0042939 | 8.6884 | 121.3074 | -0.14191 | 121.4172 | 0.18768 | -0.11444 | -0.13733 | 2.98 | 121.2708 | -0.17395 | 121.17 | -0.11444 | -0.16022 | -0.09613 | 0.10071 | -0.16022 | -0.050354 | 0.4303 | 0.10529 | 0.12817 | 0.004578 | 0.027466 | 0.068665 | -0.19684 | -0.29755 | 0.12817 | 0.14649 | 0.082398 | 0.07782 | 0.013733 | 0.32959 | 121.5591 | 0.059509 | 121.344 | 121.4493 | 121.4447 | 121.55 | 121.5134 | -121.6095 | -121.6415 | 121.6599 | 121.4127 | 8.931 | 3.2227
1776.5625 | 121.6599 | -0.27008 | 121.4859 | -0.013352 | 3.917 | 0.064536 | 0.06692 | 0.0013459 | -0.0020658 | 0.0019012 | 0.021545 | 0.003326 | -1.3925 | 0.060111 | -0.0077588 | 0.0082715 | 0.00061949 | 8.6655 | 121.3669 | -0.18768 | 121.376 | 0.14648 | -0.11902 | -0.13733 | 2.9434 | 121.2891 | -0.21973 | 121.1334 | -0.13733 | -0.18768 | -0.11902 | 0.082398 | -0.11902 | -0.10986 | 0.41657 | 0.13275 | 0.15106 | 0.050354 | 0.068664 | 0.050354 | -0.19684 | -0.35248 | 0.13275 | 0.15106 | 0.082398 | 0.10071 | 0.032044 | 0.33417 | 121.5637 | 0.082398 | 121.3531 | 121.5546 | 121.5088 | 121.637 | 121.5591 | -121.6736 | -121.7056 | 121.6461 | 121.4035 | 8.9355 | 3.2135
1778.3438 | 121.6553 | -0.26093 | 121.4996 | 0.0019074 | 4.0708 | 0.061758 | 0.064356 | -0.0031403 | -0.005911 | 0.0027558 | 0.027649 | 0.0031124 | -1.3965 | 0.060539 | -0.0075452 | 0.0099805 | -0.0036529 | 8.6243 | 121.3257 | -0.14648 | 121.3394 | 0.14191 | -0.10986 | -0.15106 | 2.948 | 121.2982 | -0.21057 | 121.1105 | -0.15564 | -0.17853 | -0.1236 | 0.11444 | -0.17395 | -0.16022 | 0.40283 | 0.10986 | 0.15106 | -0.004578 | 0.036621 | 0.050354 | -0.20142 | -0.3891 | 0.10529 | 0.13733 | 0.082397 | 0.086975 | 0.032043 | 0.28839 | 121.4859 | 0.054931 | 121.3211 | 121.4722 | 121.5088 | 121.5866 | 121.5591 | -121.6461 | -121.7102 | 121.6003 | 121.3715 | 8.8852 | 3.2089
1780.0625 | 121.6827 | -0.2655 | 121.4676 | 0.0095369 | 4.3489 | 0.066245 | 0.064997 | 0.0026275 | -0.0020658 | -0.0010894 | -0.0028687 | 0.003967 | -1.3948 | 0.063102 | -0.0028454 | 0.010194 | -0.0025849 | 8.7296 | 121.3074 | -0.11444 | 121.4127 | 0.16022 | -0.1236 | -0.15106 | 2.9755 | 121.2616 | -0.16479 | 121.1609 | -0.13733 | -0.17395 | -0.086975 | 0.15106 | -0.16022 | -0.054931 | 0.42572 | 0.11444 | 0.14191 | -0.036621 | -0.009155 | 0.10071 | -0.20599 | -0.3067 | 0.12817 | 0.17853 | 0.091553 | 0.07782 | -0.009155 | 0.27466 | 121.5271 | 0.027466 | 121.3257 | 121.4218 | 121.4264 | 121.5729 | 121.5271 | -121.582 | -121.6324 | 121.6782 | 121.4264 | 8.9951 | 3.241
1781.8438 | 121.756 | -0.2243 | 121.4447 | 0.0019074 | 4.2131 | 0.063681 | 0.065424 | 0.0022003 | -0.0020658 | -0.001944 | 0.00018312 | 0.00097624 | -1.394 | 0.059257 | -0.00070919 | 0.01233 | -0.00066231 | 8.6426 | 121.3257 | -0.12817 | 121.3898 | 0.16022 | -0.13733 | -0.15106 | 2.9663 | 121.2341 | -0.17395 | 121.2204 | -0.064087 | -0.10071 | -0.027466 | 0.09613 | -0.11902 | -0.054931 | 0.38452 | 0.073242 | 0.086975 | -0.022888 | -0.009155 | 0.050354 | -0.21057 | -0.2243 | 0.16022 | 0.19684 | 0.1236 | 0.14648 | 0.073242 | 0.28839 | 121.5179 | 0.10986 | 121.3943 | 121.4539 | 121.4081 | 121.55 | 121.4584 | -121.5729 | -121.6187 | 121.6141 | 121.4447 | 8.8669 | 3.1906
1783.6094 | 121.7651 | -0.2243 | 121.431 | 0.017166 | 4.1629 | 0.065817 | 0.064783 | 0.0024139 | -0.0027066 | -0.0017304 | 0.00018312 | 0.00076264 | -1.3969 | 0.064384 | -0.0024182 | 0.010835 | 0.0021149 | 8.7296 | 121.3028 | -0.11902 | 121.431 | 0.20599 | -0.09613 | -0.09613 | 2.9572 | 121.2067 | -0.17395 | 121.1884 | -0.059509 | -0.073242 | -0.059509 | 0.10529 | -0.12817 | 0 | 0.4303 | 0.12817 | 0.12817 | 0.022889 | 0.022889 | 0.050354 | -0.2243 | -0.24262 | 0.16479 | 0.16479 | 0.15106 | 0.11444 | 0.10071 | 0.32501 | 121.55 | 0.11444 | 121.3623 | 121.4218 | 121.3806 | 121.5271 | 121.431 | -121.55 | -121.6049 | 121.6553 | 121.4127 | 8.9539 | 3.1815
1785.375 | 121.7102 | -0.22888 | 121.4355 | 0.024795 | 4.1996 | 0.063467 | 0.067133 | 0.00091851 | -0.0031338 | 0.0012604 | -0.0028687 | 0.002258 | -1.3974 | 0.063957 | -0.0039136 | 0.010194 | -0.00044851 | 8.7891 | 121.3303 | -0.13733 | 121.4264 | 0.19684 | -0.091553 | -0.11902 | 3.0121 | 121.257 | -0.18768 | 121.1746 | -0.10071 | -0.14191 | -0.07782 | 0.091553 | -0.10529 | -0.009155 | 0.42572 | 0.10986 | 0.13733 | 0.01831 | 0.045776 | 0.041199 | -0.17853 | -0.26093 | 0.12817 | 0.15106 | 0.086975 | 0.10986 | 0.045776 | 0.33417 | 121.5637 | 0.086975 | 121.3623 | 121.4676 | 121.4447 | 121.5591 | 121.4859 | -121.5729 | -121.6232 | 121.6553 | 121.4035 | 9.0179 | 3.241
1787.0781 | 121.6507 | -0.27008 | 121.4539 | -0.013352 | 4.6516 | 0.066672 | 0.06692 | -0.0031403 | -0.0037746 | -0.00023503 | -0.0028687 | 0.003967 | -1.3959 | 0.058402 | -0.0037 | 0.01233 | -2.1314e-05 | 8.7753 | 121.3531 | -0.13733 | 121.3531 | 0.10529 | -0.19226 | -0.19226 | 2.8885 | 121.257 | -0.18768 | 121.138 | -0.17395 | -0.21973 | -0.12817 | 0.13275 | -0.10071 | -0.10071 | 0.37537 | 0.07782 | 0.07782 | -0.054932 | -0.054932 | 0.082398 | -0.19684 | -0.31586 | 0.096131 | 0.14191 | 0.050354 | 0.059509 | -0.032044 | 0.24262 | 121.4905 | 0.013733 | 121.3257 | 121.4905 | 121.4447 | 121.6232 | 121.5271 | -121.5912 | -121.6415 | 121.6232 | 121.4081 | 9.0454 | 3.1586
1788.8594 | 121.7239 | -0.21515 | 121.4447 | 0.0095369 | 4.5015 | 0.064963 | 0.062647 | 0.0024139 | -0.0012112 | 0.0012604 | 0.00018312 | 0.00033544 | -1.3952 | 0.062034 | -0.0060498 | 0.010835 | -0.00087591 | 8.7891 | 121.3074 | -0.10071 | 121.4218 | 0.21515 | -0.086975 | -0.10986 | 2.9846 | 121.2387 | -0.17853 | 121.1884 | -0.07782 | -0.1236 | -0.059509 | 0.11444 | -0.13733 | -0.022888 | 0.4303 | 0.10529 | 0.12817 | -0.009155 | 0.013733 | 0.036621 | -0.20599 | -0.25635 | 0.13733 | 0.15564 | 0.091553 | 0.11902 | 0.054932 | 0.31586 | 121.5225 | 0.10071 | 121.3669 | 121.4081 | 121.4172 | 121.5225 | 121.4539 | -121.5454 | -121.6232 | 121.637 | 121.4035 | 9.0042 | 3.1998
1790.625 | 121.788 | -0.20142 | 121.4401 | 0.0019074 | 4.5243 | 0.064322 | 0.062006 | -0.0031403 | -0.00099764 | 0.001474 | -0.0028687 | 0.0037532 | -1.3922 | 0.062888 | -0.0026318 | 0.013398 | -0.00087591 | 8.8989 | 121.3028 | -0.091553 | 121.4722 | 0.25177 | -0.068665 | -0.068665 | 3.0991 | 121.2433 | -0.18768 | 121.257 | -0.013733 | -0.041199 | -0.027466 | 0.10986 | -0.13733 | 0.032043 | 0.45319 | 0.13275 | 0.13275 | 0.022888 | 0.022888 | 0.013733 | -0.19684 | -0.18311 | 0.18768 | 0.17395 | 0.16022 | 0.16022 | 0.14648 | 0.34332 | 121.5637 | 0.17395 | 121.4447 | 121.3943 | 121.431 | 121.5042 | 121.4447 | -121.5317 | -121.6278 | 121.6736 | 121.4584 | 9.1003 | 3.3005
1792.3906 | 121.7606 | -0.21973 | 121.4401 | 0.017166 | 4.7706 | 0.063895 | 0.062647 | 0.0011321 | -0.0037746 | 0.00040597 | 0.00018312 | -9.1956e-05 | -1.3944 | 0.061179 | -0.004768 | 0.012117 | 0.0012603 | 8.8715 | 121.2753 | -0.11902 | 121.4081 | 0.21057 | -0.091553 | -0.09613 | 2.9938 | 121.2479 | -0.16479 | 121.2067 | -0.059509 | -0.073242 | -0.045776 | 0.10071 | -0.16479 | -0.032044 | 0.4303 | 0.1236 | 0.12817 | 0.022889 | 0.027466 | 0.054932 | -0.19226 | -0.23346 | 0.16022 | 0.17395 | 0.14649 | 0.11902 | 0.091553 | 0.32959 | 121.5271 | 0.10529 | 121.3715 | 121.3943 | 121.4127 | 121.4951 | 121.4676 | -121.5591 | -121.6049 | 121.6278 | 121.4264 | 9.0912 | 3.2135
1794.0938 | 121.6873 | -0.24261 | 121.4493 | 0.024795 | 4.6978 | 0.063895 | 0.06692 | 0.0032685 | -0.00057044 | -2.1434e-05 | 0.00018312 | 0.0026852 | -1.3965 | 0.058616 | -0.005409 | 0.0097669 | -0.0030121 | 8.931 | 121.2799 | -0.17395 | 121.4035 | 0.19684 | -0.11902 | -0.14191 | 3.0212 | 121.2616 | -0.19226 | 121.1563 | -0.1236 | -0.15106 | -0.086975 | 0.068665 | -0.16937 | -0.045777 | 0.43945 | 0.10071 | 0.1236 | 0.032043 | 0.054931 | 0.050354 | -0.18768 | -0.29297 | 0.11902 | 0.15564 | 0.091553 | 0.10529 | 0.041199 | 0.37079 | 121.5775 | 0.068665 | 121.3486 | 121.4539 | 121.4539 | 121.5225 | 121.5042 | -121.6232 | -121.6415 | 121.6461 | 121.3989 | 9.1736 | 3.2639
1795.875 | 121.7651 | -0.23346 | 121.4035 | -0.0057221 | 4.7649 | 0.063254 | 0.063074 | 0.0017731 | -0.0029202 | -0.00087583 | 0.00018312 | -0.00051916 | -1.3952 | 0.062248 | -0.005409 | 0.0093397 | -0.0027985 | 8.8943 | 121.2341 | -0.10071 | 121.4722 | 0.26093 | -0.045776 | -0.059509 | 3.0808 | 121.2067 | -0.17853 | 121.2204 | -0.032043 | -0.073242 | -0.032043 | 0.13275 | -0.16937 | 0.068665 | 0.49438 | 0.17395 | 0.18768 | 0.041199 | 0.054932 | 0.054931 | -0.19684 | -0.1831 | 0.20142 | 0.20142 | 0.16022 | 0.14648 | 0.10529 | 0.36163 | 121.5729 | 0.14648 | 121.3989 | 121.3348 | 121.3852 | 121.4676 | 121.4401 | -121.5042 | -121.582 | 121.7056 | 121.4539 | 9.1278 | 3.3142
1797.6562 | 121.6919 | -0.24261 | 121.4401 | 0.024795 | 4.7068 | 0.065176 | 0.067774 | 0.0019867 | -0.0020658 | -0.0038666 | 0.00018312 | 0.003967 | -1.3946 | 0.061393 | -0.0045544 | 0.010408 | -0.0042939 | 8.8898 | 121.2982 | -0.14191 | 121.4081 | 0.19226 | -0.11444 | -0.13275 | 3.0121 | 121.257 | -0.1831 | 121.1563 | -0.10986 | -0.16937 | -0.10071 | 0.10071 | -0.14191 | -0.032044 | 0.43488 | 0.10986 | 0.12817 | 0.009156 | 0.027466 | 0.05951 | -0.18311 | -0.28381 | 0.13275 | 0.14191 | 0.073242 | 0.082397 | 0.013732 | 0.33417 | 121.55 | 0.073242 | 121.3394 | 121.4401 | 121.4401 | 121.5408 | 121.4996 | -121.582 | -121.6232 | 121.6507 | 121.3989 | 9.1324 | 3.2547
1799.3594 | 121.6827 | -0.26093 | 121.4401 | 0.0019074 | 4.984 | 0.064963 | 0.063929 | -0.0010041 | -0.0033474 | 0.001474 | 0.00018312 | 0.0048214 | -1.3952 | 0.058616 | -0.0022046 | 0.011049 | 0.0027557 | 8.8943 | 121.2799 | -0.12817 | 121.3943 | 0.16937 | -0.14191 | -0.14191 | 2.9938 | 121.2662 | -0.19684 | 121.1517 | -0.13733 | -0.1831 | -0.10529 | 0.13275 | -0.16022 | -0.045777 | 0.4303 | 0.11902 | 0.11902 | -0.013733 | -0.013733 | 0.064087 | -0.17395 | -0.28839 | 0.1236 | 0.15564 | 0.07782 | 0.091552 | 0.013733 | 0.29755 | 121.5225 | 0.059509 | 121.3486 | 121.4081 | 121.463 | 121.5408 | 121.5271 | -121.5683 | -121.637 | 121.6553 | 121.4127 | 9.1553 | 3.2547
1801.125 | 121.7422 | -0.23804 | 121.4264 | 0.032425 | 4.915 | 0.064322 | 0.064356 | -0.00036309 | 0.00028416 | 0.001474 | 0.00018312 | -0.00030556 | -1.3963 | 0.072074 | -0.0058362 | 0.012758 | -0.0021575 | 8.8852 | 121.2936 | -0.11902 | 121.4127 | 0.2243 | -0.091553 | -0.10986 | 3.0075 | 121.2341 | -0.1831 | 121.1792 | -0.086975 | -0.11902 | -0.07782 | 0.11902 | -0.13275 | -0.013733 | 0.46234 | 0.12817 | 0.14648 | 0.009156 | 0.027466 | 0.054932 | -0.19226 | -0.24719 | 0.15106 | 0.16022 | 0.11902 | 0.10528 | 0.064086 | 0.34332 | 121.5317 | 0.09613 | 121.3623 | 121.4127 | 121.4172 | 121.5317 | 121.4722 | -121.5454 | -121.6095 | 121.6507 | 121.4172 | 9.1232 | 3.2455
1802.8906 | 121.7926 | -0.21973 | 121.4081 | 0.062942 | 4.8315 | 0.064108 | 0.064142 | 0.0041229 | -0.00057044 | 0.0012604 | 0.015442 | 0.002258 | -1.3942 | 0.070152 | -0.00070919 | 0.012544 | 0.0036103 | 9.0134 | 121.3257 | -0.13275 | 121.4859 | 0.28381 | -0.036621 | -0.041199 | 3.1036 | 121.2433 | -0.19226 | 121.2341 | -0.045776 | -0.064087 | -0.022888 | 0.086976 | -0.082397 | 0.07782 | 0.50354 | 0.17853 | 0.18311 | 0.091552 | 0.09613 | 0.027466 | -0.16479 | -0.17395 | 0.17395 | 0.19684 | 0.15564 | 0.16937 | 0.12817 | 0.41656 | 121.6187 | 0.14648 | 121.4264 | 121.4584 | 121.4355 | 121.5454 | 121.463 | -121.5408 | -121.6003 | 121.7056 | 121.4539 | 9.2331 | 3.3234
1804.6562 | 121.7514 | -0.24261 | 121.4127 | -0.0057221 | 4.8629 | 0.064108 | 0.064783 | -0.0020721 | -0.002493 | -0.0023712 | 0.00018312 | 0.002258 | -1.3948 | 0.05947 | -0.0022046 | 0.011476 | 0.0042511 | 8.9264 | 121.2799 | -0.14191 | 121.3806 | 0.16022 | -0.16022 | -0.16937 | 2.9938 | 121.2479 | -0.1831 | 121.2021 | -0.07782 | -0.11444 | -0.045776 | 0.10071 | -0.13275 | -0.032044 | 0.40283 | 0.073242 | 0.082398 | -0.027466 | -0.01831 | 0.05951 | -0.16479 | -0.21057 | 0.16479 | 0.19684 | 0.12817 | 0.13733 | 0.068664 | 0.30212 | 121.5225 | 0.10528 | 121.3852 | 121.4218 | 121.431 | 121.5225 | 121.4905 | -121.5546 | -121.5958 | 121.6232 | 121.4447 | 9.169 | 3.2364
1806.3594 | 121.7972 | -0.2243 | 121.3852 | 0.055313 | 4.9268 | 0.067954 | 0.065851 | -0.0031403 | -0.0031338 | 0.002115 | 0.018494 | 0.0041806 | -1.3955 | 0.065879 | -0.0026318 | 0.013612 | -0.00044851 | 9.0408 | 121.2982 | -0.12817 | 121.4905 | 0.30212 | -0.041199 | -0.045776 | 3.0945 | 121.2387 | -0.21515 | 121.2204 | -0.045776 | -0.073242 | -0.027466 | 0.09613 | -0.086975 | 0.10529 | 0.52643 | 0.17853 | 0.18311 | 0.082398 | 0.086975 | 0.009155 | -0.14648 | -0.16479 | 0.17853 | 0.19684 | 0.15106 | 0.18768 | 0.14191 | 0.4303 | 121.6187 | 0.16937 | 121.4355 | 121.4264 | 121.4539 | 121.5225 | 121.463 | -121.5134 | -121.6003 | 121.7148 | 121.4447 | 9.2651 | 3.3188
1808.1094 | 121.7239 | -0.23346 | 121.4355 | 0.032425 | 4.9093 | 0.065176 | 0.063715 | 0.0017731 | -0.0016384 | -0.001303 | 0.0093383 | 0.0028988 | -1.3944 | 0.063102 | -0.0041272 | 0.012544 | 0.0023285 | 9.0179 | 121.2799 | -0.1236 | 121.4081 | 0.21973 | -0.086975 | -0.10071 | 3.0121 | 121.2387 | -0.18768 | 121.1746 | -0.09613 | -0.11902 | -0.082397 | 0.10986 | -0.15564 | -0.027466 | 0.45319 | 0.13275 | 0.14648 | 0.022888 | 0.036621 | 0.045776 | -0.19684 | -0.26093 | 0.13733 | 0.15106 | 0.11444 | 0.10529 | 0.068664 | 0.34332 | 121.5317 | 0.091553 | 121.3623 | 121.4035 | 121.4264 | 121.5134 | 121.4722 | -121.5591 | -121.6232 | 121.6415 | 121.4081 | 9.2514 | 3.2455
1809.8906 | 121.7239 | -0.25635 | 121.4539 | 0.0095369 | 4.9851 | 0.064536 | 0.066279 | -0.0014313 | -0.0016384 | -0.00087583 | 0.0062865 | 0.0043942 | -1.3944 | 0.059257 | -0.006477 | 0.010408 | -0.0015167 | 9.05 | 121.3486 | -0.15106 | 121.4172 | 0.21973 | -0.09613 | -0.12817 | 3.0579 | 121.2753 | -0.20142 | 121.1746 | -0.086975 | -0.14191 | -0.082397 | 0.10529 | -0.10528 | -0.036621 | 0.47608 | 0.12817 | 0.16022 | 0.022888 | 0.054932 | 0.054932 | -0.17853 | -0.27923 | 0.16937 | 0.17395 | 0.11444 | 0.11902 | 0.059509 | 0.37079 | 121.5683 | 0.11444 | 121.376 | 121.4996 | 121.4767 | 121.6049 | 121.5317 | -121.6049 | -121.6553 | 121.6736 | 121.431 | 9.3063 | 3.3142
1811.5938 | 121.7926 | -0.22888 | 121.4401 | 0.0019074 | 5.0142 | 0.063895 | 0.063074 | 6.4114e-05 | -0.0037746 | 0.001474 | -0.0059205 | 0.0018306 | -1.3959 | 0.061393 | -0.0043408 | 0.010408 | 0.00061949 | 9.1827 | 121.2479 | -0.1236 | 121.4722 | 0.3067 | -0.027466 | -0.054932 | 3.1128 | 121.2158 | -0.16937 | 121.2158 | -0.018311 | -0.045776 | -0.032043 | 0.10529 | -0.19226 | 0.032043 | 0.53558 | 0.17395 | 0.20142 | 0.068664 | 0.09613 | 0.059509 | -0.22431 | -0.22431 | 0.21057 | 0.19684 | 0.18311 | 0.13733 | 0.1236 | 0.4303 | 121.5958 | 0.15106 | 121.3852 | 121.3715 | 121.3852 | 121.4767 | 121.4447 | -121.5637 | -121.6095 | 121.701 | 121.4447 | 9.4116 | 3.3417
1813.3594 | 121.7834 | -0.21973 | 121.3989 | -0.0057221 | 4.9236 | 0.06539 | 0.06222 | 0.0049773 | -0.00014304 | -0.001303 | 0.00018312 | 0.0031124 | -1.3948 | 0.065452 | -0.0017774 | 0.012758 | 0.00083309 | 9.2102 | 121.2662 | -0.10986 | 121.4584 | 0.28381 | -0.082397 | -0.082397 | 3.1219 | 121.2479 | -0.19226 | 121.2524 | -0.036621 | -0.064087 | -0.018311 | 0.10986 | -0.13275 | 0.059509 | 0.50354 | 0.13733 | 0.13733 | 0.027466 | 0.027466 | 0.027466 | -0.15106 | -0.14648 | 0.18311 | 0.20142 | 0.15564 | 0.17395 | 0.12817 | 0.39368 | 121.5683 | 0.15564 | 121.4447 | 121.376 | 121.4401 | 121.4859 | 121.4676 | -121.5088 | -121.5912 | 121.6782 | 121.4722 | 9.4299 | 3.3417
1815.125 | 121.7651 | -0.23346 | 121.4172 | 0.0019074 | 5.1466 | 0.06539 | 0.065211 | -0.00036309 | -0.0029202 | -0.00023503 | -0.0089723 | 0.002258 | -1.3963 | 0.063102 | -0.0066906 | 0.011476 | -0.0042939 | 9.3018 | 121.2616 | -0.11444 | 121.4722 | 0.3067 | -0.036621 | -0.050354 | 3.0945 | 121.225 | -0.16022 | 121.2067 | -0.036621 | -0.068665 | -0.045776 | 0.11902 | -0.15564 | 0.054932 | 0.54016 | 0.1831 | 0.19684 | 0.064087 | 0.07782 | 0.073242 | -0.19226 | -0.21057 | 0.19684 | 0.18768 | 0.16479 | 0.11444 | 0.091552 | 0.42114 | 121.5866 | 0.1236 | 121.3669 | 121.376 | 121.3852 | 121.4951 | 121.4584 | -121.5317 | -121.5775 | 121.7056 | 121.4401 | 9.5352 | 3.3279
1816.8906 | 121.7606 | -0.2243 | 121.4401 | 0.0095369 | 5.1562 | 0.063895 | 0.063288 | -0.0029267 | -0.0037746 | -0.0010894 | 0.0032349 | 0.0011898 | -1.3972 | 0.06652 | -0.0032728 | 0.010621 | -0.0010895 | 9.2743 | 121.2616 | -0.11902 | 121.4081 | 0.24261 | -0.082397 | -0.10986 | 3.0029 | 121.2112 | -0.17853 | 121.1884 | -0.073242 | -0.091553 | -0.054932 | 0.10529 | -0.17853 | -0.032044 | 0.46692 | 0.11444 | 0.14191 | 0.009156 | 0.036622 | 0.045776 | -0.22888 | -0.25177 | 0.15106 | 0.16937 | 0.13275 | 0.1236 | 0.086975 | 0.36163 | 121.5271 | 0.10529 | 121.3669 | 121.3806 | 121.3898 | 121.4859 | 121.4355 | -121.5591 | -121.6187 | 121.6324 | 121.4127 | 9.4986 | 3.2272
1818.5938 | 121.7834 | -0.22888 | 121.4218 | -0.0057221 | 5.1889 | 0.062186 | 0.063288 | 6.4114e-05 | -0.0033474 | -0.0040802 | -0.0089723 | 0.00076264 | -1.3965 | 0.066306 | -0.0073316 | 0.011262 | -0.0023713 | 9.3018 | 121.2479 | -0.10986 | 121.4767 | 0.28839 | -0.041199 | -0.054932 | 3.0991 | 121.2204 | -0.16937 | 121.2067 | -0.036621 | -0.054932 | -0.036621 | 0.11902 | -0.17395 | 0.054932 | 0.51727 | 0.17395 | 0.18768 | 0.054931 | 0.068664 | 0.059509 | -0.20142 | -0.21515 | 0.19226 | 0.19226 | 0.17395 | 0.13275 | 0.11444 | 0.39825 | 121.5866 | 0.13275 | 121.376 | 121.3577 | 121.3898 | 121.4767 | 121.4493 | -121.5317 | -121.5912 | 121.7056 | 121.4355 | 9.5306 | 3.3279
1820.3594 | 121.7377 | -0.25177 | 121.431 | 0.0095369 | 5.2852 | 0.065176 | 0.065211 | -0.00014949 | -0.0039884 | -0.00044863 | 0.00018312 | 0.0014034 | -1.3972 | 0.06652 | -0.0041272 | 0.010408 | -2.1314e-05 | 9.2514 | 121.2845 | -0.13275 | 121.3989 | 0.24261 | -0.10986 | -0.10529 | 3.0167 | 121.2204 | -0.18768 | 121.1792 | -0.10071 | -0.09613 | -0.073242 | 0.11902 | -0.14648 | -0.032043 | 0.49438 | 0.14648 | 0.14191 | 0.027465 | 0.022888 | 0.064087 | -0.21057 | -0.25177 | 0.15106 | 0.17853 | 0.15564 | 0.11444 | 0.091553 | 0.37537 | 121.5317 | 0.086975 | 121.3669 | 121.4172 | 121.4081 | 121.5363 | 121.4722 | -121.5637 | -121.6187 | 121.6507 | 121.431 | 9.5032 | 3.2684
1822.0625 | 121.7285 | -0.25635 | 121.4493 | 0.032425 | 5.212 | 0.064536 | 0.065638 | -0.0024995 | -0.002493 | -0.0015166 | 0.0062865 | 0.002258 | -1.3989 | 0.061179 | -0.0045544 | 0.010408 | -0.0017303 | 9.2285 | 121.3303 | -0.14191 | 121.4035 | 0.22888 | -0.1236 | -0.1236 | 3.0487 | 121.2708 | -0.19226 | 121.1655 | -0.11444 | -0.12817 | -0.091553 | 0.11444 | -0.11902 | -0.045777 | 0.48523 | 0.13275 | 0.13275 | 0.018311 | 0.018311 | 0.064087 | -0.17853 | -0.28381 | 0.14191 | 0.1648 | 0.12817 | 0.10071 | 0.064087 | 0.37079 | 121.5454 | 0.07782 | 121.3577 | 121.4722 | 121.463 | 121.5866 | 121.5271 | -121.5912 | -121.6415 | 121.6599 | 121.4218 | 9.4849 | 3.3051
1823.8438 | 121.7972 | -0.23346 | 121.3989 | 0.0019074 | 5.2192 | 0.065176 | 0.063502 | -0.0037811 | -0.0037746 | -0.0023712 | 0.00018312 | 0.0018306 | -1.395 | 0.060966 | -0.0043408 | 0.011262 | -0.0010895 | 9.1782 | 121.3028 | -0.10071 | 121.4401 | 0.30212 | -0.054932 | -0.045776 | 3.0853 | 121.2204 | -0.16937 | 121.2341 | -0.018311 | -0.050354 | -0.032043 | 0.13275 | -0.096131 | 0.041199 | 0.53558 | 0.18768 | 0.17853 | 0.054932 | 0.045776 | 0.064086 | -0.17853 | -0.16479 | 0.21515 | 0.20142 | 0.1831 | 0.13733 | 0.11902 | 0.40283 | 121.5408 | 0.15106 | 121.4035 | 121.4035 | 121.3898 | 121.5363 | 121.4539 | -121.4996 | -121.5683 | 121.6736 | 121.4676 | 9.4116 | 3.3188
1825.5469 | 121.7697 | -0.22888 | 121.4264 | -0.0057221 | 5.3837 | 0.064963 | 0.064142 | 0.0024139 | -0.0020658 | -0.0053618 | -0.0059205 | -0.00073276 | -1.3959 | 0.069724 | -0.0051954 | 0.012544 | 0.0027557 | 9.1873 | 121.2753 | -0.10529 | 121.4813 | 0.32501 | -0.027466 | -0.059509 | 3.1265 | 121.2296 | -0.16937 | 121.2341 | -0.022888 | -0.050354 | -0.036621 | 0.1236 | -0.15106 | 0.054931 | 0.55389 | 0.16937 | 0.20142 | 0.045777 | 0.07782 | 0.059509 | -0.19684 | -0.19226 | 0.20599 | 0.19226 | 0.17853 | 0.13275 | 0.11902 | 0.4303 | 121.5866 | 0.14649 | 121.4035 | 121.3806 | 121.3989 | 121.5042 | 121.4584 | -121.5317 | -121.5958 | 121.7102 | 121.463 | 9.4162 | 3.3554
1827.3125 | 121.6919 | -0.26093 | 121.4401 | -0.0057221 | 4.9984 | 0.06304 | 0.062647 | -0.00036309 | -0.0050564 | 0.00061957 | -0.0089723 | 0.0024716 | -1.3961 | 0.06182 | -0.0062634 | 0.011049 | -0.0021575 | 9.2011 | 121.2616 | -0.10529 | 121.4218 | 0.27466 | -0.050354 | -0.086975 | 3.0579 | 121.257 | -0.1831 | 121.1517 | -0.10986 | -0.13275 | -0.09613 | 0.15564 | -0.17853 | -0.018311 | 0.53558 | 0.17395 | 0.21057 | 0.018311 | 0.054932 | 0.07782 | -0.18311 | -0.28839 | 0.15106 | 0.1648 | 0.12817 | 0.086975 | 0.050354 | 0.37994 | 121.5271 | 0.073242 | 121.3348 | 121.3669 | 121.4401 | 121.5225 | 121.5179 | -121.5454 | -121.6232 | 121.6827 | 121.4127 | 9.462 | 3.3188
1829.0938 | 121.7468 | -0.23346 | 121.4264 | 0.040054 | 4.9456 | 0.064322 | 0.064783 | -0.0057037 | -0.00099764 | 0.00040597 | 0.021545 | 0.0024716 | -1.3935 | 0.063316 | -0.0032728 | 0.0097669 | -0.0019439 | 9.2422 | 121.2708 | -0.14648 | 121.4493 | 0.34332 | -0.054932 | -0.064087 | 3.1128 | 121.2204 | -0.20142 | 121.1884 | -0.073242 | -0.10986 | -0.059509 | 0.086975 | -0.15564 | 0.022888 | 0.57678 | 0.16937 | 0.17853 | 0.082397 | 0.091552 | 0.032043 | -0.20599 | -0.23804 | 0.16022 | 0.17395 | 0.1236 | 0.14191 | 0.091553 | 0.48981 | 121.5958 | 0.12817 | 121.3898 | 121.4172 | 121.4218 | 121.5042 | 121.4539 | -121.5729 | -121.6278 | 121.6827 | 121.4218 | 9.4757 | 3.3463
1830.8594 | 121.8063 | -0.23346 | 121.3898 | -0.013352 | 4.7986 | 0.06304 | 0.063288 | -0.0042083 | -0.0046292 | -0.0025848 | -0.0028687 | -0.00094636 | -1.3961 | 0.059257 | -0.0032728 | 0.012971 | -0.00023491 | 9.1827 | 121.257 | -0.11902 | 121.4493 | 0.32501 | -0.036621 | -0.054932 | 3.1265 | 121.2067 | -0.17395 | 121.2341 | 0.004578 | -0.027466 | -0.018311 | 0.11444 | -0.13275 | 0.059509 | 0.55847 | 0.17853 | 0.19684 | 0.064087 | 0.082398 | 0.059509 | -0.18311 | -0.15564 | 0.23804 | 0.21515 | 0.20599 | 0.15564 | 0.14648 | 0.44403 | 121.5683 | 0.17853 | 121.4081 | 121.376 | 121.3806 | 121.4905 | 121.4401 | -121.5088 | -121.5637 | 121.6827 | 121.4676 | 9.4162 | 3.36
1832.5625 | 121.6782 | -0.27924 | 121.4447 | -0.013352 | 4.7335 | 0.062827 | 0.06457 | -0.0031403 | -0.00078404 | -0.00023503 | -0.0059205 | 0.0020444 | -1.3952 | 0.065879 | -0.0043408 | 0.010621 | 0.00061949 | 9.2148 | 121.2524 | -0.13275 | 121.4035 | 0.27008 | -0.073242 | -0.1236 | 3.0304 | 121.2387 | -0.19226 | 121.1105 | -0.11902 | -0.16022 | -0.13275 | 0.14648 | -0.19226 | -0.041199 | 0.54932 | 0.15564 | 0.20599 | 0.009155 | 0.059509 | 0.086975 | -0.20599 | -0.33417 | 0.16022 | 0.14648 | 0.11902 | 0.05951 | 0.032044 | 0.40283 | 121.5363 | 0.073242 | 121.3028 | 121.3852 | 121.431 | 121.5317 | 121.5179 | -121.5775 | -121.637 | 121.6827 | 121.3898 | 9.494 | 3.3096
1834.3281 | 121.8018 | -0.23346 | 121.4081 | 0.0019074 | 4.8125 | 0.063681 | 0.063929 | -0.00036309 | -0.0031338 | -0.0040802 | -0.0059205 | 0.00054904 | -1.3948 | 0.059898 | -0.0049818 | 0.010194 | -0.0013031 | 9.2102 | 121.2387 | -0.10986 | 121.4767 | 0.36163 | -0.027466 | -0.036621 | 3.1448 | 121.2021 | -0.17853 | 121.2204 | -0.009155 | -0.032043 | -0.032043 | 0.1236 | -0.16937 | 0.068665 | 0.59509 | 0.19684 | 0.20599 | 0.073242 | 0.082397 | 0.054931 | -0.20599 | -0.18768 | 0.2243 | 0.20142 | 0.20142 | 0.14648 | 0.14648 | 0.4715 | 121.5866 | 0.16937 | 121.3989 | 121.3486 | 121.3806 | 121.4722 | 121.4355 | -121.5179 | -121.5866 | 121.7102 | 121.4539 | 9.4437 | 3.3783
1836.0938 | 121.7056 | -0.26093 | 121.4264 | 0.024795 | 4.8674 | 0.065176 | 0.065851 | 0.0041229 | -0.003561 | -0.001944 | 0.01239 | 0.0018306 | -1.394 | 0.05947 | -0.0032728 | 0.012544 | -0.0010895 | 9.2422 | 121.3257 | -0.15106 | 121.3989 | 0.24719 | -0.10986 | -0.1236 | 3.0808 | 121.2524 | -0.21057 | 121.1563 | -0.10986 | -0.14191 | -0.082397 | 0.10986 | -0.10071 | -0.027466 | 0.50812 | 0.13733 | 0.15106 | 0.027466 | 0.041199 | 0.050354 | -0.17395 | -0.27008 | 0.15106 | 0.17853 | 0.11902 | 0.12817 | 0.068664 | 0.39825 | 121.55 | 0.10071 | 121.3669 | 121.4767 | 121.463 | 121.5866 | 121.5134 | -121.5775 | -121.637 | 121.6599 | 121.4172 | 9.5032 | 3.3417
1837.8125 | 121.7056 | -0.27008 | 121.4264 | 0.024795 | 4.8845 | 0.066458 | 0.064142 | -0.00079049 | -0.0037746 | 0.00019217 | 0.0062865 | 0.003967 | -1.3965 | 0.060752 | -0.0045544 | 0.012117 | -0.0030121 | 9.2468 | 121.3211 | -0.15564 | 121.3989 | 0.25177 | -0.11444 | -0.10986 | 3.0716 | 121.257 | -0.21973 | 121.1609 | -0.10986 | -0.15106 | -0.091553 | 0.11444 | -0.10529 | -0.027466 | 0.52185 | 0.16022 | 0.15564 | 0.045777 | 0.041199 | 0.050354 | -0.16937 | -0.2655 | 0.16022 | 0.17853 | 0.11902 | 0.12817 | 0.068665 | 0.40741 | 121.5546 | 0.10986 | 121.3806 | 121.4767 | 121.4767 | 121.5912 | 121.5271 | -121.582 | -121.6461 | 121.669 | 121.431 | 9.5169 | 3.3417
1839.5312 | 121.788 | -0.23346 | 121.3943 | 0.062942 | 4.7879 | 0.066458 | 0.064997 | 0.00091851 | -0.0037746 | 0.002115 | 0.015442 | 0.0018306 | -1.3944 | 0.06652 | -0.001991 | 0.011903 | -0.00023491 | 9.2697 | 121.2982 | -0.14191 | 121.4813 | 0.37537 | -0.036621 | -0.059509 | 3.1357 | 121.2433 | -0.20599 | 121.2296 | -0.027466 | -0.086975 | -0.036621 | 0.091552 | -0.09613 | 0.086975 | 0.60882 | 0.17395 | 0.19684 | 0.082398 | 0.10529 | 0.027465 | -0.15106 | -0.16479 | 0.20599 | 0.19684 | 0.14648 | 0.16937 | 0.11902 | 0.51727 | 121.6232 | 0.17853 | 121.4355 | 121.4401 | 121.4493 | 121.5317 | 121.4767 | -121.5363 | -121.6003 | 121.7148 | 121.463 | 9.5032 | 3.3691
1841.2969 | 121.701 | -0.30212 | 121.4081 | 0.032425 | 4.9351 | 0.064108 | 0.066492 | 0.0011321 | -0.0044156 | 0.0025422 | 0.015442 | 0.0035396 | -1.3912 | 0.055412 | -0.0066906 | 0.0097669 | -0.0010895 | 9.2926 | 121.3394 | -0.19684 | 121.3623 | 0.2243 | -0.14191 | -0.14191 | 3.0212 | 121.2891 | -0.22888 | 121.1243 | -0.15106 | -0.16022 | -0.1236 | 0.10529 | -0.068664 | -0.045776 | 0.52643 | 0.16022 | 0.16022 | 0.054931 | 0.054931 | 0.073242 | -0.11902 | -0.28381 | 0.15106 | 0.17853 | 0.14191 | 0.10529 | 0.068665 | 0.42114 | 121.5591 | 0.07782 | 121.3531 | 121.5363 | 121.5179 | 121.6415 | 121.5912 | -121.6049 | -121.637 | 121.6644 | 121.4264 | 9.5947 | 3.3234
1843.0625 | 121.7468 | -0.23804 | 121.3989 | -0.0057221 | 4.814 | 0.061972 | 0.06457 | 0.00049131 | -0.0014248 | -0.00087583 | -0.0028687 | 0.0020444 | -1.3955 | 0.063743 | -0.0069044 | 0.010621 | 0.0016877 | 9.2926 | 121.2662 | -0.11902 | 121.4447 | 0.35248 | -0.045776 | -0.064087 | 3.1219 | 121.2021 | -0.17853 | 121.1929 | -0.036621 | -0.07782 | -0.064087 | 0.11902 | -0.13275 | 0.045776 | 0.59052 | 0.17395 | 0.19226 | 0.054932 | 0.073243 | 0.059509 | -0.19684 | -0.20599 | 0.20142 | 0.17395 | 0.16022 | 0.11444 | 0.10071 | 0.4715 | 121.5637 | 0.14191 | 121.3715 | 121.3852 | 121.3806 | 121.5042 | 121.4401 | -121.5179 | -121.5775 | 121.6827 | 121.431 | 9.5306 | 3.36
1844.8438 | 121.7834 | -0.25177 | 121.4218 | -0.013352 | 4.9323 | 0.063254 | 0.063502 | -0.00057689 | -0.00099764 | -2.1434e-05 | -0.0028687 | 0.00076264 | -1.3965 | 0.060325 | -0.0041272 | 0.0099805 | 0.00019229 | 9.2972 | 121.2433 | -0.11444 | 121.4676 | 0.37537 | -0.036621 | -0.041199 | 3.154 | 121.2158 | -0.18768 | 121.2112 | -0.018311 | -0.045776 | -0.045776 | 0.13733 | -0.17853 | 0.045776 | 0.62714 | 0.21057 | 0.21515 | 0.073242 | 0.07782 | 0.064087 | -0.20599 | -0.21057 | 0.23346 | 0.20599 | 0.20599 | 0.14191 | 0.14191 | 0.48981 | 121.582 | 0.16937 | 121.3989 | 121.3577 | 121.4035 | 121.4951 | 121.4676 | -121.5363 | -121.6095 | 121.7194 | 121.463 | 9.549 | 3.4058
1846.5469 | 121.7926 | -0.24719 | 121.4127 | -0.0057221 | 4.7467 | 0.063681 | 0.064142 | 0.0026275 | -0.004202 | -0.003653 | -0.0028687 | 0.00012184 | -1.3961 | 0.067375 | -0.0051954 | 0.010194 | 0.0012603 | 9.2743 | 121.2341 | -0.12817 | 121.4859 | 0.37079 | -0.032043 | -0.041199 | 3.1494 | 121.1838 | -0.17395 | 121.2158 | -0.004578 | -0.036621 | -0.032043 | 0.11902 | -0.17853 | 0.073242 | 0.61798 | 0.20599 | 0.21515 | 0.086975 | 0.096131 | 0.073242 | -0.22888 | -0.19684 | 0.24261 | 0.21515 | 0.21057 | 0.14191 | 0.13733 | 0.49896 | 121.6141 | 0.16937 | 121.3898 | 121.3623 | 121.3577 | 121.4813 | 121.431 | -121.5408 | -121.5866 | 121.7331 | 121.463 | 9.5215 | 3.3966
1848.3125 | 121.6461 | -0.28381 | 121.4218 | -0.013352 | 4.9618 | 0.065604 | 0.065211 | -0.0014313 | -0.0029202 | -0.00044863 | 0.00018312 | 0.003967 | -1.3965 | 0.063529 | -0.00070919 | 0.012117 | -0.00023491 | 9.2285 | 121.2936 | -0.16937 | 121.3165 | 0.16022 | -0.21057 | -0.21515 | 2.9251 | 121.2662 | -0.20599 | 121.0922 | -0.19226 | -0.21973 | -0.12817 | 0.11444 | -0.12817 | -0.10529 | 0.44403 | 0.068664 | 0.073242 | -0.045776 | -0.041198 | 0.077819 | -0.15564 | -0.32959 | 0.091552 | 0.15564 | 0.064086 | 0.07782 | -0.013733 | 0.32959 | 121.4859 | 0.013733 | 121.2982 | 121.463 | 121.4722 | 121.5775 | 121.55 | -121.5912 | -121.6278 | 121.6003 | 121.376 | 9.5123 | 3.2089
1850.0469 | 121.6415 | -0.29755 | 121.4264 | 0.0019074 | 5.0725 | 0.06539 | 0.066706 | 6.4114e-05 | -0.0039884 | -0.0025848 | -0.0059205 | 0.002258 | -1.3922 | 0.058616 | -0.0032728 | 0.011903 | 0.00083309 | 9.2468 | 121.3303 | -0.15564 | 121.2936 | 0.19226 | -0.21057 | -0.19226 | 2.9343 | 121.2616 | -0.20142 | 121.106 | -0.1831 | -0.22888 | -0.14191 | 0.14191 | -0.096131 | -0.13275 | 0.48981 | 0.10528 | 0.086975 | -0.036621 | -0.054931 | 0.09613 | -0.1648 | -0.32044 | 0.11444 | 0.15564 | 0.068664 | 0.059509 | -0.027466 | 0.3479 | 121.4493 | 0.018311 | 121.3074 | 121.4859 | 121.463 | 121.6278 | 121.5591 | -121.582 | -121.6278 | 121.5912 | 121.4035 | 9.5444 | 3.2318
1851.8281 | 121.7056 | -0.28381 | 121.4539 | 0.040054 | 5.0827 | 0.06539 | 0.068415 | 0.0039093 | -0.0020658 | -0.0040802 | 0.01239 | 0.0031124 | -1.394 | 0.057975 | -0.005409 | 0.010194 | 0.00061949 | 9.2743 | 121.344 | -0.19226 | 121.3531 | 0.25177 | -0.13275 | -0.14191 | 3.0258 | 121.2753 | -0.24719 | 121.1105 | -0.14648 | -0.16937 | -0.14191 | 0.091552 | -0.10986 | -0.10071 | 0.53558 | 0.14191 | 0.15106 | 0.050354 | 0.05951 | 0.036621 | -0.17853 | -0.34332 | 0.13733 | 0.14191 | 0.11444 | 0.10528 | 0.077819 | 0.44403 | 121.5454 | 0.10071 | 121.3577 | 121.5363 | 121.5225 | 121.6278 | 121.5591 | -121.6461 | -121.701 | 121.637 | 121.3943 | 9.5581 | 3.3096
1853.5938 | 121.7697 | -0.24719 | 121.4172 | 0.017166 | 5.0197 | 0.06304 | 0.065638 | -0.0031403 | -0.002493 | -0.0027984 | 0.00018312 | -0.00051916 | -1.3965 | 0.064811 | -0.0041272 | 0.013398 | 0.0014741 | 9.2239 | 121.3165 | -0.14191 | 121.3715 | 0.3067 | -0.086975 | -0.10986 | 3.0624 | 121.1975 | -0.20599 | 121.1884 | -0.064087 | -0.086975 | -0.050354 | 0.10528 | -0.10071 | -0.045776 | 0.55389 | 0.13733 | 0.16022 | 0.032044 | 0.054932 | 0.041198 | -0.21973 | -0.22888 | 0.1831 | 0.19684 | 0.16022 | 0.15564 | 0.11902 | 0.44861 | 121.5134 | 0.14191 | 121.3943 | 121.4584 | 121.4035 | 121.5637 | 121.4447 | -121.5591 | -121.6232 | 121.6187 | 121.4355 | 9.4711 | 3.3096
1855.375 | 121.701 | -0.28381 | 121.4035 | -0.0057221 | 5.0488 | 0.061758 | 0.063074 | -0.0031403 | -0.0044156 | -0.00087583 | -0.0059205 | 0.00054904 | -1.3965 | 0.058402 | -0.005409 | 0.0091261 | -0.0034393 | 9.2514 | 121.2524 | -0.1236 | 121.4172 | 0.3479 | -0.068665 | -0.07782 | 3.0945 | 121.2204 | -0.19226 | 121.1517 | -0.10529 | -0.13275 | -0.10529 | 0.16022 | -0.15106 | 0.013733 | 0.63171 | 0.20599 | 0.21515 | 0.045776 | 0.054931 | 0.091552 | -0.1831 | -0.25177 | 0.17853 | 0.17853 | 0.15106 | 0.086975 | 0.05951 | 0.4715 | 121.5408 | 0.086975 | 121.344 | 121.376 | 121.4127 | 121.5363 | 121.5042 | -121.5271 | -121.5958 | 121.701 | 121.4355 | 9.5352 | 3.3783
1857.0938 | 121.6599 | -0.3067 | 121.431 | -0.013352 | 5.0039 | 0.064322 | 0.064997 | 0.0030547 | -0.0054836 | -0.00066223 | 0.0032349 | 0.0037532 | -1.394 | 0.057121 | -0.0066906 | 0.0097669 | -0.00087591 | 9.1553 | 121.3074 | -0.16022 | 121.312 | 0.23346 | -0.16022 | -0.16937 | 2.98 | 121.2341 | -0.2243 | 121.0876 | -0.17395 | -0.18768 | -0.15106 | 0.14648 | -0.1236 | -0.11902 | 0.54016 | 0.13733 | 0.14648 | -0.009156 | 0 | 0.082398 | -0.19684 | -0.34332 | 0.13275 | 0.15564 | 0.11902 | 0.073242 | 0.036621 | 0.39368 | 121.4722 | 0.050354 | 121.312 | 121.4676 | 121.4584 | 121.6141 | 121.5408 | -121.5912 | -121.6553 | 121.6187 | 121.3943 | 9.462 | 3.2867
1858.875 | 121.756 | -0.22888 | 121.3852 | 0.047683 | 5.0834 | 0.065604 | 0.066706 | -0.0018585 | -0.00078404 | 0.00019217 | 0.0032349 | 0.002258 | -1.3967 | 0.068443 | -0.00092279 | 0.012544 | -0.0013031 | 9.2239 | 121.2845 | -0.14648 | 121.4127 | 0.3891 | -0.068665 | -0.068665 | 3.0991 | 121.2067 | -0.21057 | 121.1792 | -0.09613 | -0.11444 | -0.068665 | 0.082398 | -0.10071 | 0.027466 | 0.61798 | 0.16022 | 0.16022 | 0.077819 | 0.077819 | 0.018311 | -0.17853 | -0.20599 | 0.13275 | 0.16022 | 0.11444 | 0.14191 | 0.09613 | 0.53558 | 121.5591 | 0.11444 | 121.3898 | 121.431 | 121.4172 | 121.5134 | 121.4355 | -121.5317 | -121.5958 | 121.6415 | 121.4081 | 9.4528 | 3.3279
1860.5781 | 121.7606 | -0.25635 | 121.4401 | -0.0057221 | 4.9697 | 0.065817 | 0.065424 | -0.0014313 | -0.0056972 | 0.00061957 | -0.0028687 | 0.002258 | -1.3969 | 0.063743 | -0.0077588 | 0.012544 | -2.1314e-05 | 9.2194 | 121.2479 | -0.12817 | 121.4401 | 0.38452 | -0.036621 | -0.073242 | 3.1311 | 121.225 | -0.17853 | 121.1746 | -0.07782 | -0.073242 | -0.054932 | 0.12817 | -0.19226 | 0 | 0.64087 | 0.18311 | 0.21973 | 0.054932 | 0.091553 | 0.07782 | -0.21515 | -0.2655 | 0.17853 | 0.20142 | 0.18311 | 0.1236 | 0.10529 | 0.5127 | 121.5683 | 0.10071 | 121.3531 | 121.376 | 121.4035 | 121.5042 | 121.4813 | -121.5683 | -121.6187 | 121.6965 | 121.431 | 9.4757 | 3.3875
1862.3438 | 121.6599 | -0.28839 | 121.4584 | 0.0095369 | 5.0069 | 0.065176 | 0.066492 | 6.4114e-05 | -0.0037746 | 0.00083317 | -0.0059205 | 0.0026852 | -1.3944 | 0.062034 | -0.003059 | 0.010408 | -0.00023491 | 9.1507 | 121.312 | -0.15564 | 121.3257 | 0.24261 | -0.19684 | -0.19226 | 2.9755 | 121.2433 | -0.21057 | 121.0831 | -0.19684 | -0.2243 | -0.14648 | 0.13275 | -0.14648 | -0.13275 | 0.53101 | 0.09613 | 0.091553 | -0.036621 | -0.041198 | 0.07782 | -0.21515 | -0.37537 | 0.091553 | 0.14191 | 0.064087 | 0.064087 | -0.013733 | 0.39826 | 121.4813 | 0.013733 | 121.2936 | 121.4676 | 121.4539 | 121.6003 | 121.5317 | -121.6141 | -121.669 | 121.6141 | 121.3715 | 9.4391 | 3.2639
1864.125 | 121.7926 | -0.22888 | 121.4127 | -0.0057221 | 4.8734 | 0.06539 | 0.063929 | 0.00070491 | -0.0044156 | -0.0032256 | -0.0059205 | 0.0024716 | -1.3959 | 0.059257 | 0.00035881 | 0.011903 | -0.0042939 | 9.1782 | 121.2799 | -0.14191 | 121.4035 | 0.35706 | -0.09613 | -0.082397 | 3.1082 | 121.225 | -0.1831 | 121.2341 | -0.054932 | -0.068665 | -0.013733 | 0.086975 | -0.13275 | -0.009156 | 0.58594 | 0.14649 | 0.13275 | 0.05951 | 0.045777 | 0.045777 | -0.18768 | -0.17853 | 0.17395 | 0.21515 | 0.16022 | 0.16937 | 0.11444 | 0.49896 | 121.5454 | 0.12817 | 121.4172 | 121.4218 | 121.4081 | 121.5088 | 121.4539 | -121.5546 | -121.5958 | 121.6324 | 121.463 | 9.407 | 3.3371
1865.8281 | 121.6736 | -0.3067 | 121.4035 | -0.0057221 | 4.9347 | 0.064749 | 0.068415 | 0.0028411 | -0.0033474 | 0.00061957 | 0.00018312 | 0.002258 | -1.3942 | 0.063102 | -0.003059 | 0.010835 | -0.0017303 | 9.1736 | 121.312 | -0.16479 | 121.3074 | 0.25635 | -0.20599 | -0.18768 | 2.9755 | 121.2204 | -0.21515 | 121.1151 | -0.19226 | -0.21515 | -0.13275 | 0.14191 | -0.091552 | -0.09613 | 0.56305 | 0.11902 | 0.10071 | -0.022888 | -0.041199 | 0.091553 | -0.1831 | -0.28839 | 0.11444 | 0.17395 | 0.091553 | 0.082398 | 0 | 0.42114 | 121.4722 | 0.022888 | 121.3303 | 121.4767 | 121.4355 | 121.6187 | 121.5271 | -121.5683 | -121.6187 | 121.6141 | 121.4218 | 9.4803 | 3.2822
1867.5938 | 121.8018 | -0.25177 | 121.3715 | -0.020981 | 4.9311 | 0.064963 | 0.064142 | -0.00036309 | -0.0046292 | -2.1434e-05 | -0.0028687 | 0.00012184 | -1.3948 | 0.062461 | -0.0041272 | 0.011903 | -0.0019439 | 9.2468 | 121.2479 | -0.14648 | 121.4676 | 0.43488 | -0.041199 | -0.050354 | 3.1631 | 121.1975 | -0.20599 | 121.1975 | -0.018311 | -0.036621 | -0.050354 | 0.10529 | -0.1236 | 0.09613 | 0.68664 | 0.20142 | 0.21057 | 0.09613 | 0.10529 | 0.045776 | -0.17395 | -0.17395 | 0.23346 | 0.20142 | 0.21515 | 0.15564 | 0.16937 | 0.58136 | 121.6141 | 0.18768 | 121.4035 | 121.3943 | 121.4035 | 121.4996 | 121.4493 | -121.5179 | -121.5775 | 121.7194 | 121.4493 | 9.4986 | 3.4149
1869.3594 | 121.7194 | -0.29755 | 121.4355 | 0.024795 | 5.0945 | 0.066885 | 0.067988 | 0.0026275 | -0.0029202 | 0.00019217 | 0.0062865 | 0.0048214 | -1.3974 | 0.059898 | -0.0032728 | 0.012758 | -0.0013031 | 9.2789 | 121.3074 | -0.20142 | 121.3852 | 0.34332 | -0.1236 | -0.13275 | 3.0808 | 121.2524 | -0.2243 | 121.1472 | -0.11902 | -0.13275 | -0.10529 | 0.09613 | -0.12817 | -0.050354 | 0.64087 | 0.16479 | 0.17395 | 0.068665 | 0.07782 | 0.073242 | -0.18311 | -0.28839 | 0.17853 | 0.19226 | 0.16479 | 0.11902 | 0.091553 | 0.54474 | 121.5866 | 0.10529 | 121.3715 | 121.5088 | 121.4767 | 121.6049 | 121.55 | -121.637 | -121.6599 | 121.6827 | 121.4447 | 9.5764 | 3.3783
1871.1406 | 121.7056 | -0.28839 | 121.4355 | 0.040054 | 5.0071 | 0.063681 | 0.064997 | -0.0044221 | -0.0020658 | 0.002115 | 0.0093383 | 0.0054622 | -1.3933 | 0.062675 | -0.0060498 | 0.012117 | -0.0017303 | 9.2331 | 121.3303 | -0.19684 | 121.3623 | 0.31586 | -0.11902 | -0.14191 | 3.0533 | 121.225 | -0.2243 | 121.1334 | -0.13275 | -0.14191 | -0.10071 | 0.091553 | -0.10529 | -0.073242 | 0.60425 | 0.14648 | 0.16937 | 0.054931 | 0.077819 | 0.064087 | -0.21057 | -0.30212 | 0.15564 | 0.18768 | 0.14648 | 0.1236 | 0.082397 | 0.5127 | 121.5591 | 0.091553 | 121.3577 | 121.5271 | 121.4493 | 121.6187 | 121.5134 | -121.6324 | -121.6599 | 121.6507 | 121.4218 | 9.5215 | 3.3417
1872.9062 | 121.7468 | -0.2655 | 121.3943 | 0.017166 | 5.1421 | 0.063895 | 0.063288 | 0.0024139 | -0.002493 | 0.002115 | 0.00018312 | 0.002258 | -1.3935 | 0.060966 | -0.0022046 | 0.012117 | -2.1314e-05 | 9.2011 | 121.2616 | -0.15564 | 121.3806 | 0.35706 | -0.10986 | -0.10071 | 3.0487 | 121.1838 | -0.22888 | 121.1472 | -0.10071 | -0.1236 | -0.10986 | 0.10986 | -0.13275 | -0.013733 | 0.62256 | 0.16479 | 0.15564 | 0.054932 | 0.045777 | 0.036621 | -0.21057 | -0.24719 | 0.16479 | 0.15564 | 0.14191 | 0.11902 | 0.10529 | 0.5127 | 121.5363 | 0.12817 | 121.376 | 121.4172 | 121.4127 | 121.5271 | 121.4493 | -121.55 | -121.6232 | 121.6461 | 121.4127 | 9.4666 | 3.3142
1874.625 | 121.8613 | -0.29755 | 121.4035 | 0.0095369 | 5.1214 | 0.063681 | 0.064142 | 0.0028411 | -0.0020658 | -2.1434e-05 | -0.0089723 | 0.0037532 | -1.3952 | 0.057548 | -0.0028454 | 0.010621 | 0.0012603 | 9.2194 | 121.3211 | -0.17395 | 121.3806 | 0.33417 | -0.12817 | -0.1236 | 3.0808 | 121.2204 | -0.2243 | 121.1243 | -0.14648 | -0.16479 | -0.12817 | 0.1236 | -0.082397 | -0.022888 | 0.63171 | 0.17395 | 0.16937 | 0.050354 | 0.045776 | 0.073242 | -0.1831 | -0.27923 | 0.15106 | 0.16937 | 0.13275 | 0.09613 | 0.059509 | 0.50812 | 121.5546 | 0.07782 | 121.3486 | 121.4951 | 121.4447 | 121.6187 | 121.5179 | -121.5775 | -121.6278 | 121.6782 | 121.4218 | 9.5169 | 3.3783
1876.3906 | 121.788 | -0.27466 | 121.3943 | 0.0095369 | 5.0319 | 0.062827 | 0.065851 | -0.0024995 | -0.0016384 | -0.001303 | 0.00018312 | -0.00030556 | -1.3963 | 0.064384 | -0.004768 | 0.011689 | -0.0017303 | 9.1782 | 121.2341 | -0.15564 | 121.376 | 0.36621 | -0.10071 | -0.091553 | 3.0899 | 121.1655 | -0.23346 | 121.1746 | -0.073242 | -0.068665 | -0.054932 | 0.11902 | -0.16022 | -0.01831 | 0.64087 | 0.18311 | 0.17395 | 0.064087 | 0.054932 | 0.041199 | -0.22888 | -0.21973 | 0.20142 | 0.21973 | 0.20599 | 0.17853 | 0.16479 | 0.52185 | 121.5317 | 0.16022 | 121.4081 | 121.3898 | 121.3989 | 121.5088 | 121.4401 | -121.55 | -121.6278 | 121.6507 | 121.4493 | 9.4528 | 3.3646
1878.1719 | 121.6782 | -0.28839 | 121.3852 | -0.020981 | 4.9454 | 0.064536 | 0.063288 | -0.0027131 | -0.0044156 | -0.0023712 | -0.0059205 | 0.00076264 | -1.3961 | 0.055198 | -0.0051954 | 0.011476 | 0.00061949 | 9.1873 | 121.2479 | -0.16937 | 121.3486 | 0.34332 | -0.13275 | -0.13733 | 3.035 | 121.2112 | -0.23804 | 121.0876 | -0.16937 | -0.17853 | -0.16479 | 0.11902 | -0.13733 | -0.036621 | 0.63171 | 0.15106 | 0.15564 | 0.032044 | 0.036622 | 0.050354 | -0.17395 | -0.29755 | 0.11902 | 0.1236 | 0.10986 | 0.073242 | 0.059509 | 0.5127 | 121.5179 | 0.068664 | 121.3257 | 121.4172 | 121.4493 | 121.5363 | 121.4996 | -121.5546 | -121.6232 | 121.637 | 121.376 | 9.4757 | 3.3234
1879.8906 | 121.6553 | -0.28381 | 121.4218 | -0.013352 | 5.1233 | 0.064749 | 0.068629 | -0.0016449 | -0.0022794 | 0.00040597 | -0.0028687 | 0.0043942 | -1.3925 | 0.062248 | -0.004768 | 0.013826 | -0.00044851 | 9.2468 | 121.2891 | -0.16479 | 121.3165 | 0.3067 | -0.19226 | -0.1831 | 3.0075 | 121.2112 | -0.23804 | 121.0968 | -0.18768 | -0.21515 | -0.16479 | 0.11902 | -0.13275 | -0.10529 | 0.59051 | 0.10071 | 0.091552 | -0.01831 | -0.027466 | 0.045776 | -0.21057 | -0.32501 | 0.09613 | 0.11902 | 0.068664 | 0.073242 | 0.022888 | 0.4715 | 121.4813 | 0.050354 | 121.3348 | 121.4539 | 121.4493 | 121.5729 | 121.4951 | -121.5866 | -121.6599 | 121.6003 | 121.3806 | 9.5306 | 3.2913
1881.6719 | 121.7056 | -0.31128 | 121.4172 | -0.0057221 | 5.1122 | 0.064963 | 0.063715 | 0.0013459 | -0.002493 | -0.00087583 | 0.00018312 | 0.00076264 | -1.3969 | 0.062248 | -0.0075452 | 0.010408 | -0.00087591 | 9.3155 | 121.225 | -0.16479 | 121.3806 | 0.38452 | -0.086975 | -0.10986 | 3.0533 | 121.2112 | -0.21515 | 121.0922 | -0.13733 | -0.14648 | -0.11902 | 0.14648 | -0.19226 | -0.036621 | 0.6958 | 0.20142 | 0.2243 | 0.054932 | 0.07782 | 0.09613 | -0.20599 | -0.32501 | 0.17395 | 0.19226 | 0.16479 | 0.09613 | 0.068665 | 0.54932 | 121.5454 | 0.07782 | 121.3074 | 121.3898 | 121.4264 | 121.5363 | 121.5225 | -121.582 | -121.6324 | 121.6919 | 121.4035 | 9.6268 | 3.3646
1883.375 | 121.7148 | -0.27924 | 121.3806 | 0.017166 | 5.2139 | 0.064108 | 0.067347 | -0.0016449 | -0.0014248 | 0.00040597 | 0.00018312 | 0.0026852 | -1.3955 | 0.062888 | -0.0022046 | 0.011049 | -0.0027985 | 9.3155 | 121.2982 | -0.20142 | 121.3577 | 0.37079 | -0.13733 | -0.13733 | 3.0899 | 121.225 | -0.2243 | 121.1243 | -0.1236 | -0.14648 | -0.10529 | 0.07782 | -0.082397 | -0.022888 | 0.65002 | 0.14191 | 0.14191 | 0.064087 | 0.064087 | 0.054932 | -0.15564 | -0.25635 | 0.15564 | 0.17395 | 0.13275 | 0.11902 | 0.07782 | 0.5722 | 121.5591 | 0.10071 | 121.3486 | 121.4996 | 121.4493 | 121.5775 | 121.5042 | -121.582 | -121.6049 | 121.637 | 121.4035 | 9.5947 | 3.3691
1885.1719 | 121.7789 | -0.25635 | 121.3852 | -0.013352 | 5.0962 | 0.065176 | 0.064356 | -0.0010041 | -0.0033474 | -0.0025848 | -0.0059205 | 0.0020444 | -1.3946 | 0.052421 | 0.00078621 | 0.011476 | -0.0047211 | 9.2789 | 121.2891 | -0.1831 | 121.3348 | 0.33875 | -0.16479 | -0.15106 | 3.0487 | 121.1975 | -0.22888 | 121.1746 | -0.091553 | -0.11902 | -0.064087 | 0.073243 | -0.096131 | -0.050354 | 0.59509 | 0.10529 | 0.091553 | 0.032043 | 0.01831 | 0.027466 | -0.18768 | -0.21057 | 0.1648 | 0.19226 | 0.13733 | 0.16479 | 0.10986 | 0.52185 | 121.5179 | 0.13733 | 121.4035 | 121.4722 | 121.4264 | 121.5454 | 121.4539 | -121.5683 | -121.6141 | 121.5912 | 121.431 | 9.5352 | 3.3051
1886.9375 | 121.7926 | -0.25635 | 121.3577 | 0.0095369 | 5.0654 | 0.066245 | 0.065851 | 0.0022003 | -0.0012112 | 0.0029694 | -0.0028687 | 0.0011898 | -1.3937 | 0.067802 | -0.0022046 | 0.013185 | 0.00061949 | 9.3567 | 121.2662 | -0.14648 | 121.4127 | 0.44861 | -0.09613 | -0.082397 | 3.1815 | 121.1975 | -0.25177 | 121.2067 | -0.054932 | -0.073242 | -0.045776 | 0.10986 | -0.091553 | 0.054932 | 0.70496 | 0.17395 | 0.16022 | 0.064087 | 0.050354 | 0.004578 | -0.16022 | -0.15106 | 0.20142 | 0.21057 | 0.18311 | 0.20599 | 0.17853 | 0.59509 | 121.5591 | 0.19684 | 121.4584 | 121.4127 | 121.4493 | 121.5225 | 121.4539 | -121.5042 | -121.6095 | 121.669 | 121.463 | 9.613 | 3.4378
1888.6406 | 121.7743 | -0.27466 | 121.3669 | 0.0095369 | 5.1906 | 0.064322 | 0.063502 | -0.0027131 | -0.004202 | -0.00087583 | -0.0028687 | 0.0026852 | -1.3957 | 0.065238 | -0.0043408 | 0.01233 | -0.0027985 | 9.3018 | 121.2708 | -0.16022 | 121.3623 | 0.3891 | -0.091553 | -0.10071 | 3.0899 | 121.1609 | -0.2243 | 121.1746 | -0.068665 | -0.07782 | -0.059509 | 0.11444 | -0.09613 | -0.004577 | 0.66376 | 0.17395 | 0.18311 | 0.059509 | 0.068664 | 0.050354 | -0.20599 | -0.19226 | 0.20599 | 0.21515 | 0.19684 | 0.16479 | 0.14648 | 0.54932 | 121.5225 | 0.15564 | 121.3989 | 121.431 | 121.3852 | 121.5454 | 121.4355 | -121.5271 | -121.5912 | 121.637 | 121.4493 | 9.5764 | 3.3646
1890.4062 | 121.6873 | -0.31586 | 121.376 | 0.0095369 | 5.1082 | 0.065176 | 0.066706 | 6.4114e-05 | -0.00014304 | 0.00083317 | 0.00018312 | 0.0054622 | -1.3946 | 0.062675 | -0.0062634 | 0.012117 | -0.0025849 | 9.1644 | 121.2845 | -0.18768 | 121.3303 | 0.36163 | -0.16479 | -0.17395 | 3.0487 | 121.2204 | -0.24261 | 121.106 | -0.16937 | -0.18768 | -0.14191 | 0.12817 | -0.091553 | -0.045777 | 0.67749 | 0.14191 | 0.15106 | 0.013733 | 0.022888 | 0.073242 | -0.15564 | -0.27008 | 0.14648 | 0.17395 | 0.12817 | 0.10071 | 0.054932 | 0.54932 | 121.5179 | 0.073242 | 121.3486 | 121.4722 | 121.463 | 121.6003 | 121.5363 | -121.5637 | -121.6187 | 121.6461 | 121.4218 | 9.4803 | 3.3646
1892.1875 | 121.7331 | -0.29755 | 121.3669 | -0.013352 | 5.1643 | 0.067099 | 0.066492 | 0.0011321 | -0.0012112 | -0.00087583 | -0.0028687 | 0.0024716 | -1.3922 | 0.068015 | -0.0028454 | 0.011689 | 0.0025421 | 9.0591 | 121.2891 | -0.17853 | 121.2936 | 0.32959 | -0.20142 | -0.18768 | 3.0167 | 121.1884 | -0.25177 | 121.1288 | -0.13733 | -0.16479 | -0.11444 | 0.11902 | -0.07782 | -0.073242 | 0.62714 | 0.10986 | 0.09613 | -0.009155 | -0.022888 | 0.045776 | -0.17853 | -0.23804 | 0.16022 | 0.1831 | 0.13275 | 0.13733 | 0.086975 | 0.50812 | 121.4722 | 0.11444 | 121.3806 | 121.4676 | 121.4401 | 121.5866 | 121.4859 | -121.5454 | -121.6187 | 121.5912 | 121.4264 | 9.3567 | 3.3142
1893.9531 | 121.7926 | -0.28839 | 121.3577 | 0.0095369 | 5.1927 | 0.062186 | 0.063502 | 0.00049131 | -0.0029202 | 0.00019217 | -0.0028687 | -0.0013736 | -1.3969 | 0.063743 | -0.0058362 | 0.011903 | 0.00083309 | 9.1095 | 121.2112 | -0.15106 | 121.3943 | 0.48065 | -0.050354 | -0.050354 | 3.1494 | 121.17 | -0.21057 | 121.1746 | -0.050354 | -0.054932 | -0.07782 | 0.13733 | -0.14648 | 0.036621 | 0.76904 | 0.23804 | 0.23804 | 0.10071 | 0.10071 | 0.07782 | -0.18768 | -0.1831 | 0.23804 | 0.21057 | 0.23346 | 0.13275 | 0.15564 | 0.63171 | 121.5454 | 0.16022 | 121.3852 | 121.3623 | 121.3806 | 121.4996 | 121.4584 | -121.5088 | -121.5683 | 121.6827 | 121.463 | 9.3979 | 3.4378
1895.6719 | 121.669 | -0.32959 | 121.4127 | 0.047683 | 5.2498 | 0.066245 | 0.06692 | 0.0011321 | -0.00078404 | -0.00023503 | 0.015442 | 0.0024716 | -1.3952 | 0.057975 | -0.0075452 | 0.011476 | -0.00023491 | 9.1141 | 121.2982 | -0.24719 | 121.3165 | 0.33417 | -0.15106 | -0.14648 | 3.0029 | 121.2296 | -0.28839 | 121.0602 | -0.19226 | -0.1831 | -0.16022 | 0.082398 | -0.11444 | -0.096131 | 0.66376 | 0.18311 | 0.17853 | 0.10071 | 0.09613 | 0.041199 | -0.18311 | -0.35248 | 0.13733 | 0.16937 | 0.14649 | 0.12817 | 0.10529 | 0.58136 | 121.5637 | 0.09613 | 121.3486 | 121.5454 | 121.5179 | 121.6278 | 121.5591 | -121.6599 | -121.7011 | 121.6461 | 121.3898 | 9.4437 | 3.3325
1897.4375 | 121.6782 | -0.33417 | 121.4035 | -0.020981 | 5.2355 | 0.065176 | 0.066492 | 0.00049131 | -0.0037746 | -0.001303 | 0.00018312 | 0.003967 | -1.3967 | 0.065879 | -0.0039136 | 0.010835 | 0.0051057 | 9.0317 | 121.2799 | -0.20599 | 121.2433 | 0.28839 | -0.21973 | -0.21057 | 2.9343 | 121.2021 | -0.2655 | 121.0648 | -0.21973 | -0.23346 | -0.1831 | 0.12817 | -0.1236 | -0.16022 | 0.62256 | 0.1236 | 0.11444 | -0.004577 | -0.013733 | 0.068664 | -0.20142 | -0.33875 | 0.11444 | 0.15106 | 0.10071 | 0.082398 | 0.032044 | 0.49439 | 121.4493 | 0.045776 | 121.3303 | 121.4859 | 121.4676 | 121.6141 | 121.5363 | -121.6095 | -121.669 | 121.5775 | 121.3989 | 9.3658 | 3.2684
1899.1406 | 121.7514 | -0.28381 | 121.3577 | 0.017166 | 5.181 | 0.063254 | 0.065638 | -0.0031403 | -0.0029202 | -0.00066223 | 0.0093383 | 0.0011898 | -1.3963 | 0.066947 | -0.0058362 | 0.01233 | 0.0012603 | 9.1187 | 121.2524 | -0.20142 | 121.3348 | 0.41199 | -0.12817 | -0.10986 | 3.0212 | 121.1792 | -0.24261 | 121.1243 | -0.13733 | -0.12817 | -0.11444 | 0.082397 | -0.10529 | -0.022888 | 0.6958 | 0.17395 | 0.15564 | 0.091553 | 0.073242 | 0.041198 | -0.17853 | -0.23346 | 0.14648 | 0.16937 | 0.15564 | 0.12817 | 0.11444 | 0.6134 | 121.5363 | 0.10529 | 121.3669 | 121.4539 | 121.4218 | 121.5363 | 121.463 | -121.5591 | -121.6003 | 121.6187 | 121.4081 | 9.4025 | 3.3051
1900.9219 | 121.7651 | -0.29755 | 121.3852 | -0.0057221 | 5.1667 | 0.061758 | 0.064997 | -0.0046357 | -0.0029202 | 0.0033966 | -0.0059205 | 0.0018306 | -1.3965 | 0.066947 | -0.0051954 | 0.0099805 | -0.0015167 | 9.1507 | 121.1884 | -0.15564 | 121.3806 | 0.47607 | -0.073242 | -0.07782 | 3.0945 | 121.1563 | -0.23804 | 121.1288 | -0.10071 | -0.086975 | -0.10986 | 0.14191 | -0.19684 | -0.004578 | 0.77362 | 0.21973 | 0.2243 | 0.07782 | 0.082398 | 0.059509 | -0.22888 | -0.25635 | 0.19684 | 0.18768 | 0.21057 | 0.12817 | 0.15106 | 0.63171 | 121.5363 | 0.13733 | 121.3669 | 121.344 | 121.3943 | 121.4859 | 121.4539 | -121.5408 | -121.6232 | 121.6782 | 121.4264 | 9.4482 | 3.392
1902.6875 | 121.756 | -0.27466 | 121.376 | 0.032425 | 5.4098 | 0.066885 | 0.065638 | 0.0013459 | -0.00099764 | 0.0023286 | 0.01239 | 0.0035396 | -1.3937 | 0.064384 | -0.0013502 | 0.011903 | 0.00061949 | 9.1873 | 121.2479 | -0.20142 | 121.3669 | 0.46692 | -0.10986 | -0.082397 | 3.0899 | 121.1838 | -0.24719 | 121.1288 | -0.11444 | -0.1236 | -0.11902 | 0.073242 | -0.12817 | -0.009156 | 0.74158 | 0.19226 | 0.1648 | 0.11902 | 0.091553 | 0.027466 | -0.19226 | -0.24719 | 0.16022 | 0.15564 | 0.15106 | 0.12817 | 0.1236 | 0.66834 | 121.5683 | 0.13275 | 121.376 | 121.4493 | 121.431 | 121.5225 | 121.4584 | -121.5775 | -121.6232 | 121.6415 | 121.4035 | 9.462 | 3.3646
1904.4688 | 121.8063 | -0.29297 | 121.3531 | 0.0019074 | 5.3307 | 0.064108 | 0.062861 | -0.0024995 | -0.0020658 | -0.0023712 | -0.0028687 | 0.003326 | -1.3959 | 0.060752 | -0.005409 | 0.012117 | -0.0025849 | 9.2651 | 121.2021 | -0.1831 | 121.4127 | 0.53558 | -0.068665 | -0.068665 | 3.1357 | 121.1517 | -0.23346 | 121.1746 | -0.041199 | -0.050354 | -0.073242 | 0.10986 | -0.15106 | 0.05951 | 0.82855 | 0.2243 | 0.2243 | 0.11444 | 0.11444 | 0.05951 | -0.20142 | -0.17853 | 0.25177 | 0.21973 | 0.24261 | 0.16022 | 0.1831 | 0.71869 | 121.5958 | 0.19226 | 121.4081 | 121.3852 | 121.3852 | 121.4951 | 121.4447 | -121.5363 | -121.5866 | 121.7056 | 121.4676 | 9.5581 | 3.4286
1906.1875 | 121.669 | -0.32959 | 121.376 | 0.0019074 | 5.4882 | 0.06304 | 0.062861 | -0.00079049 | -0.00078404 | 0.0016876 | 0.015442 | 0.0048214 | -1.395 | 0.056053 | -0.0058362 | 0.010621 | -0.0038665 | 9.2056 | 121.2341 | -0.21973 | 121.3028 | 0.39825 | -0.15564 | -0.15106 | 3.0075 | 121.2341 | -0.29297 | 121.0464 | -0.19684 | -0.21057 | -0.16022 | 0.10986 | -0.14191 | -0.073243 | 0.72784 | 0.17853 | 0.17395 | 0.068665 | 0.064087 | 0.036621 | -0.14191 | -0.32959 | 0.13275 | 0.16937 | 0.11902 | 0.13275 | 0.082398 | 0.61798 | 121.5225 | 0.096131 | 121.3394 | 121.4539 | 121.5271 | 121.5637 | 121.5637 | -121.5958 | -121.669 | 121.6324 | 121.376 | 9.5352 | 3.3371
1907.9688 | 121.7972 | -0.28381 | 121.3623 | -0.0057221 | 5.4987 | 0.063467 | 0.061793 | -0.0022857 | -0.00527 | 0.00019217 | -0.0028687 | -0.00051916 | -1.3965 | 0.064597 | -0.0043408 | 0.012117 | -0.00044851 | 9.3063 | 121.1929 | -0.18768 | 121.3943 | 0.53101 | -0.041199 | -0.045776 | 3.154 | 121.1517 | -0.2243 | 121.1884 | -0.045776 | -0.054932 | -0.086975 | 0.09613 | -0.16937 | 0.032043 | 0.81482 | 0.23804 | 0.24261 | 0.14191 | 0.14648 | 0.059509 | -0.21057 | -0.17395 | 0.23804 | 0.19684 | 0.22888 | 0.13733 | 0.16937 | 0.71869 | 121.582 | 0.17853 | 121.4127 | 121.3806 | 121.376 | 121.4767 | 121.4355 | -121.55 | -121.5866 | 121.6782 | 121.4722 | 9.5901 | 3.4378
1909.75 | 121.7468 | -0.30212 | 121.3715 | -0.0057221 | 5.5448 | 0.066245 | 0.06222 | -0.0022857 | -0.002493 | -0.0010894 | -0.0059205 | 0.0024716 | -1.3972 | 0.059043 | -0.0037 | 0.011476 | -0.00087591 | 9.288 | 121.1792 | -0.17853 | 121.3715 | 0.48065 | -0.082397 | -0.10071 | 3.0808 | 121.1792 | -0.24261 | 121.1105 | -0.11902 | -0.10529 | -0.10986 | 0.1236 | -0.19226 | 0 | 0.78278 | 0.20142 | 0.21973 | 0.07782 | 0.096131 | 0.059509 | -0.19226 | -0.26093 | 0.18311 | 0.19226 | 0.19684 | 0.13275 | 0.13733 | 0.65918 | 121.55 | 0.1236 | 121.3531 | 121.3577 | 121.4218 | 121.4813 | 121.4813 | -121.55 | -121.6141 | 121.6736 | 121.4127 | 9.5901 | 3.3829
1911.4531 | 121.8201 | -0.29755 | 121.3577 | 0.0019074 | 5.4354 | 0.06304 | 0.065424 | 0.0011321 | -0.00057044 | 0.00083317 | 0.00018312 | 0.0024716 | -1.3959 | 0.066093 | -0.0032728 | 0.011476 | -0.00023491 | 9.2834 | 121.2067 | -0.16937 | 121.3898 | 0.5127 | -0.07782 | -0.054932 | 3.1311 | 121.1426 | -0.22888 | 121.1792 | -0.054932 | -0.050354 | -0.086975 | 0.12817 | -0.15106 | 0.032044 | 0.81024 | 0.24261 | 0.21973 | 0.11444 | 0.091553 | 0.068664 | -0.21515 | -0.17853 | 0.24261 | 0.21057 | 0.24719 | 0.14191 | 0.17853 | 0.68207 | 121.5591 | 0.17395 | 121.4081 | 121.376 | 121.3715 | 121.5042 | 121.4401 | -121.5271 | -121.5866 | 121.6873 | 121.4767 | 9.581 | 3.4287
1913.2188 | 121.6919 | -0.32501 | 121.3623 | 0.0019074 | 5.5091 | 0.064963 | 0.065851 | 0.0011321 | -0.001852 | 0.00061957 | 0.00018312 | 0.0041806 | -1.3946 | 0.053703 | -0.0024182 | 0.011262 | 0.0012603 | 9.2194 | 121.2708 | -0.20599 | 121.2662 | 0.35248 | -0.2243 | -0.19684 | 2.9526 | 121.2021 | -0.27466 | 121.0602 | -0.2243 | -0.21515 | -0.17853 | 0.11902 | -0.091553 | -0.096131 | 0.67749 | 0.12817 | 0.10071 | 0.009156 | -0.01831 | 0.050354 | -0.16022 | -0.30212 | 0.10071 | 0.14648 | 0.10986 | 0.09613 | 0.059509 | 0.55847 | 121.4722 | 0.050354 | 121.3348 | 121.4767 | 121.4767 | 121.5958 | 121.5271 | -121.5683 | -121.637 | 121.5912 | 121.3852 | 9.5444 | 3.2776
1915 | 121.6415 | -0.34332 | 121.3623 | 0.0019074 | 5.6153 | 0.066031 | 0.067988 | 0.0047637 | -0.0031338 | 0.0019012 | 0.00018312 | 0.0046078 | -1.3955 | 0.060325 | -0.0034864 | 0.011262 | -0.00044851 | 9.2743 | 121.2524 | -0.2243 | 121.2616 | 0.3479 | -0.24719 | -0.2243 | 2.9205 | 121.1838 | -0.28381 | 121.0464 | -0.24719 | -0.25635 | -0.19684 | 0.11902 | -0.10986 | -0.10071 | 0.69122 | 0.11902 | 0.096131 | 0 | -0.022888 | 0.05951 | -0.17853 | -0.31586 | 0.096131 | 0.14648 | 0.086975 | 0.086975 | 0.027465 | 0.5722 | 121.4859 | 0.036621 | 121.3303 | 121.4767 | 121.4676 | 121.5958 | 121.5271 | -121.5866 | -121.6461 | 121.6049 | 121.3898 | 9.6176 | 3.2639
1916.7031 | 121.788 | -0.30212 | 121.3394 | 0.024795 | 5.9438 | 0.068167 | 0.067133 | 0.0019867 | 0.0017796 | -0.00044863 | 0.015442 | 0.0028988 | -1.394 | 0.064384 | -0.0026318 | 0.010835 | -0.0025849 | 9.3704 | 121.2616 | -0.21515 | 121.4172 | 0.55389 | -0.086975 | -0.059509 | 3.1265 | 121.1884 | -0.27008 | 121.17 | -0.082397 | -0.09613 | -0.086975 | 0.086975 | -0.07782 | 0.077819 | 0.85602 | 0.24261 | 0.21515 | 0.15564 | 0.12817 | 0.032043 | -0.15106 | -0.16937 | 0.21973 | 0.21515 | 0.20599 | 0.18311 | 0.17395 | 0.76904 | 121.6324 | 0.18768 | 121.4401 | 121.4767 | 121.4584 | 121.5637 | 121.4905 | -121.5546 | -121.6095 | 121.7194 | 121.4722 | 9.6725 | 3.4287
1918.4531 | 121.8109 | -0.31586 | 121.3303 | -0.0057221 | 5.8753 | 0.066458 | 0.062006 | 0.0026275 | -0.002493 | -0.0023712 | -0.0059205 | 0.00076264 | -1.3963 | 0.06182 | -0.0049818 | 0.012758 | 0.0027557 | 9.3155 | 121.1884 | -0.18768 | 121.3623 | 0.5127 | -0.086975 | -0.09613 | 3.1036 | 121.1151 | -0.26093 | 121.1517 | -0.068665 | -0.059509 | -0.086975 | 0.12817 | -0.14191 | 0.032044 | 0.82855 | 0.21973 | 0.22888 | 0.091553 | 0.10071 | 0.054932 | -0.21515 | -0.17853 | 0.24719 | 0.22888 | 0.25635 | 0.17395 | 0.20142 | 0.70038 | 121.55 | 0.19226 | 121.4127 | 121.376 | 121.376 | 121.5042 | 121.431 | -121.5179 | -121.5912 | 121.6782 | 121.4676 | 9.6313 | 3.4195
1920.25 | 121.7056 | -0.33875 | 121.3669 | 0.040054 | 5.959 | 0.067099 | 0.067347 | 0.0026275 | -0.0016384 | 0.00061957 | 0.018494 | 0.0043942 | -1.3933 | 0.063316 | -0.007118 | 0.011476 | -0.0034393 | 9.3201 | 121.2708 | -0.23804 | 121.3028 | 0.42572 | -0.15106 | -0.15564 | 2.9846 | 121.2204 | -0.30212 | 121.051 | -0.19684 | -0.17853 | -0.16479 | 0.10071 | -0.09613 | -0.064087 | 0.76446 | 0.18311 | 0.18768 | 0.082397 | 0.086975 | 0.036621 | -0.14648 | -0.31586 | 0.14191 | 0.17395 | 0.16022 | 0.13733 | 0.1236 | 0.66376 | 121.5408 | 0.10529 | 121.3531 | 121.5088 | 121.5225 | 121.6095 | 121.5591 | -121.6049 | -121.669 | 121.6415 | 121.3898 | 9.6588 | 3.3234
1922.0312 | 121.7606 | -0.31586 | 121.3577 | 0.0019074 | 5.8902 | 0.06304 | 0.06222 | -0.00014949 | -0.0027066 | -0.0010894 | -0.0089723 | 0.0014034 | -1.3957 | 0.058402 | -0.0060498 | 0.010408 | -0.00023491 | 9.3521 | 121.17 | -0.18768 | 121.3669 | 0.53101 | -0.07782 | -0.09613 | 3.067 | 121.138 | -0.25177 | 121.138 | -0.09613 | -0.082397 | -0.10986 | 0.12817 | -0.18768 | 0.009155 | 0.84686 | 0.21973 | 0.23804 | 0.091553 | 0.10986 | 0.064087 | -0.21973 | -0.21973 | 0.21973 | 0.20599 | 0.23346 | 0.14191 | 0.16937 | 0.71869 | 121.5546 | 0.15564 | 121.3898 | 121.3577 | 121.3898 | 121.4859 | 121.4539 | -121.5454 | -121.6095 | 121.6827 | 121.4539 | 9.668 | 3.3829
1923.8125 | 121.7377 | -0.31586 | 121.3623 | 0.032425 | 5.9325 | 0.064963 | 0.066706 | -0.00014949 | -0.0029202 | -0.00023503 | 0.0032349 | 0.002258 | -1.3959 | 0.056693 | -0.005409 | 0.010408 | -0.0025849 | 9.2926 | 121.2204 | -0.21515 | 121.3486 | 0.48523 | -0.1236 | -0.11902 | 3.0029 | 121.1426 | -0.27008 | 121.1151 | -0.14648 | -0.13275 | -0.11444 | 0.10071 | -0.14191 | -0.013733 | 0.80109 | 0.19684 | 0.19226 | 0.09613 | 0.091553 | 0.045776 | -0.21973 | -0.24719 | 0.16937 | 0.20142 | 0.18311 | 0.15564 | 0.13733 | 0.70038 | 121.5637 | 0.1236 | 121.3852 | 121.4355 | 121.4127 | 121.5363 | 121.4584 | -121.5775 | -121.6324 | 121.6644 | 121.431 | 9.6085 | 3.3188
1925.5312 | 121.6507 | -0.35248 | 121.3989 | -0.013352 | 5.9537 | 0.063467 | 0.066492 | -0.00014949 | -0.0056972 | 0.0040376 | -0.0059205 | 0.005035 | -1.3948 | 0.060111 | -0.0034864 | 0.011689 | -0.0017303 | 9.2926 | 121.2524 | -0.20599 | 121.2891 | 0.41657 | -0.21057 | -0.20599 | 2.9434 | 121.1929 | -0.28381 | 121.051 | -0.21057 | -0.21973 | -0.18768 | 0.14648 | -0.14648 | -0.10986 | 0.76904 | 0.14648 | 0.14191 | 0 | -0.004577 | 0.068665 | -0.20599 | -0.3479 | 0.14191 | 0.1648 | 0.13275 | 0.09613 | 0.064086 | 0.62256 | 121.4951 | 0.073242 | 121.3348 | 121.4584 | 121.4767 | 121.6049 | 121.5454 | -121.6049 | -121.6827 | 121.6415 | 121.4035 | 9.6451 | 3.2959
1927.2812 | 121.7697 | -0.30212 | 121.3257 | -0.013352 | 5.9528 | 0.066458 | 0.066065 | -0.0016449 | -0.0044156 | -0.00044863 | -0.0028687 | 0.00076264 | -1.3959 | 0.061393 | -0.0017774 | 0.014039 | -0.00087591 | 9.288 | 121.2433 | -0.20599 | 121.3211 | 0.48981 | -0.14191 | -0.1236 | 3.0258 | 121.1288 | -0.26093 | 121.1426 | -0.091553 | -0.10071 | -0.073242 | 0.09613 | -0.082398 | -0.004578 | 0.79193 | 0.17853 | 0.16022 | 0.082398 | 0.064087 | 0.041199 | -0.19684 | -0.18311 | 0.21057 | 0.22888 | 0.20142 | 0.18768 | 0.16022 | 0.6958 | 121.5271 | 0.16937 | 121.4035 | 121.4493 | 121.3898 | 121.5454 | 121.431 | -121.5317 | -121.5866 | 121.6232 | 121.4447 | 9.5901 | 3.3279
1929.0469 | 121.6736 | -0.3479 | 121.3852 | -0.0057221 | 6.1395 | 0.062827 | 0.066065 | -0.0035675 | -0.0046292 | -0.00023503 | 0.018494 | 0.0054622 | -1.3931 | 0.064597 | -0.0075452 | 0.011049 | -0.00023491 | 9.2606 | 121.2479 | -0.2243 | 121.2845 | 0.46692 | -0.15564 | -0.12817 | 2.9526 | 121.2296 | -0.30212 | 121.0373 | -0.20599 | -0.19684 | -0.18768 | 0.1236 | -0.13733 | -0.10071 | 0.81482 | 0.21973 | 0.19226 | 0.09613 | 0.068664 | 0.045776 | -0.15564 | -0.3479 | 0.14191 | 0.16022 | 0.15106 | 0.11444 | 0.10529 | 0.69122 | 121.5088 | 0.09613 | 121.3394 | 121.4722 | 121.5317 | 121.5958 | 121.5775 | -121.6095 | -121.6873 | 121.6324 | 121.3852 | 9.6085 | 3.3005
1930.7656 | 121.6782 | -0.34332 | 121.3989 | 0.040054 | 6.0716 | 0.065604 | 0.067347 | 0.0015595 | -0.0033474 | -0.0042938 | 0.021545 | 0.0041806 | -1.3946 | 0.060325 | -0.006477 | 0.010194 | -0.0023713 | 9.3246 | 121.2708 | -0.24719 | 121.2799 | 0.45776 | -0.16022 | -0.16022 | 2.9388 | 121.2158 | -0.3067 | 121.0556 | -0.19226 | -0.1831 | -0.15106 | 0.096131 | -0.12817 | -0.11902 | 0.80109 | 0.18311 | 0.18311 | 0.086975 | 0.086975 | 0.036621 | -0.18311 | -0.34332 | 0.15106 | 0.19226 | 0.16022 | 0.15564 | 0.1236 | 0.70496 | 121.5271 | 0.11444 | 121.3623 | 121.5179 | 121.5225 | 121.6141 | 121.5591 | -121.6461 | -121.7056 | 121.6232 | 121.3989 | 9.668 | 3.2822
1932.5312 | 121.7789 | -0.29755 | 121.3577 | 0.062942 | 6.0451 | 0.067526 | 0.065424 | 0.00027771 | 7.0564e-05 | 0.0023286 | 0.015442 | 0.003326 | -1.3937 | 0.063957 | -0.001991 | 0.011689 | -0.00044851 | 9.3658 | 121.2158 | -0.20599 | 121.4127 | 0.59509 | -0.059509 | -0.041199 | 3.0945 | 121.1655 | -0.27008 | 121.1517 | -0.068665 | -0.068665 | -0.091553 | 0.091552 | -0.14191 | 0.054932 | 0.89264 | 0.25635 | 0.23804 | 0.1648 | 0.14649 | 0.027465 | -0.19226 | -0.20599 | 0.22888 | 0.20599 | 0.22888 | 0.17853 | 0.20142 | 0.80109 | 121.6187 | 0.20142 | 121.4218 | 121.4218 | 121.4355 | 121.5134 | 121.463 | -121.5637 | -121.6278 | 121.7102 | 121.4493 | 9.6634 | 3.392
1934.2969 | 121.7606 | -0.31586 | 121.3211 | 0.0019074 | 6.0637 | 0.065604 | 0.066279 | -0.00014949 | -0.00078404 | 0.00040597 | 0.00018312 | 0.001617 | -1.3957 | 0.065025 | -0.003059 | 0.010835 | -0.0023713 | 9.2789 | 121.1975 | -0.21057 | 121.3165 | 0.53101 | -0.12817 | -0.10529 | 2.9709 | 121.17 | -0.2655 | 121.1243 | -0.11444 | -0.09613 | -0.11444 | 0.10529 | -0.1236 | -0.004578 | 0.84686 | 0.21057 | 0.18768 | 0.10529 | 0.082397 | 0.050354 | -0.15106 | -0.19684 | 0.20142 | 0.20142 | 0.21973 | 0.15106 | 0.16937 | 0.74158 | 121.5271 | 0.15106 | 121.3898 | 121.4081 | 121.4355 | 121.5134 | 121.4859 | -121.5317 | -121.5866 | 121.6324 | 121.4401 | 9.5947 | 3.2867
1936 | 121.7926 | -0.32959 | 121.3531 | -0.0057221 | 6.0475 | 0.064536 | 0.063502 | 0.0017731 | -0.0022794 | 0.00061957 | -0.0028687 | 0.00054904 | -1.3957 | 0.059684 | -0.0043408 | 0.010621 | 0.0014741 | 9.2972 | 121.1884 | -0.17853 | 121.4127 | 0.61798 | -0.050354 | -0.054932 | 3.0716 | 121.1334 | -0.24261 | 121.1426 | -0.059509 | -0.022888 | -0.07782 | 0.15106 | -0.16479 | 0.05951 | 0.94757 | 0.27466 | 0.27924 | 0.1236 | 0.12817 | 0.086975 | -0.21973 | -0.21057 | 0.27008 | 0.25177 | 0.3067 | 0.16479 | 0.21973 | 0.79651 | 121.5912 | 0.18311 | 121.3852 | 121.3669 | 121.376 | 121.5179 | 121.463 | -121.5317 | -121.5958 | 121.7422 | 121.4722 | 9.6268 | 3.4012
1937.7656 | 121.7697 | -0.29755 | 121.3577 | 0.0019074 | 6.0583 | 0.064963 | 0.064997 | -0.00057689 | -0.004202 | -0.0015166 | 0.00018312 | 0.00097624 | -1.3955 | 0.068229 | -0.0039136 | 0.011262 | 0.0010467 | 9.2514 | 121.2341 | -0.18768 | 121.3348 | 0.56305 | -0.091553 | -0.09613 | 3.0075 | 121.1609 | -0.24261 | 121.1426 | -0.07782 | -0.050354 | -0.091553 | 0.10986 | -0.1236 | -0.022888 | 0.86059 | 0.20142 | 0.20599 | 0.091553 | 0.09613 | 0.054931 | -0.19684 | -0.21515 | 0.21973 | 0.20599 | 0.24719 | 0.15106 | 0.19226 | 0.75073 | 121.5225 | 0.16479 | 121.3852 | 121.4218 | 121.4035 | 121.5317 | 121.4584 | -121.5454 | -121.6003 | 121.6324 | 121.4401 | 9.549 | 3.3051
1939.4688 | 121.6553 | -0.34332 | 121.3989 | 0.0095369 | 6.0707 | 0.063681 | 0.067347 | 0.0026275 | -0.0031338 | 0.0010468 | -0.0028687 | 0.0054622 | -1.3957 | 0.056266 | -0.0037 | 0.012758 | 0.0021149 | 9.2102 | 121.2662 | -0.2243 | 121.257 | 0.46692 | -0.21973 | -0.20599 | 2.8656 | 121.1975 | -0.25635 | 121.0419 | -0.22888 | -0.21515 | -0.18768 | 0.11902 | -0.13275 | -0.14191 | 0.81024 | 0.13733 | 0.1236 | 0.01831 | 0.004577 | 0.086975 | -0.20142 | -0.35706 | 0.11444 | 0.15564 | 0.12817 | 0.068665 | 0.041199 | 0.69122 | 121.4813 | 0.027466 | 121.2982 | 121.4905 | 121.4539 | 121.6095 | 121.5408 | -121.6232 | -121.6553 | 121.6003 | 121.3852 | 9.5535 | 3.2089
1941.25 | 121.6873 | -0.32959 | 121.3852 | 0.024795 | 6.0695 | 0.065604 | 0.069056 | 0.0026275 | -0.0020658 | 0.0016876 | 0.00018312 | 0.0052486 | -1.3933 | 0.062675 | -0.0039136 | 0.011903 | 0.0010467 | 9.2194 | 121.2616 | -0.22888 | 121.3394 | 0.55389 | -0.15106 | -0.13733 | 2.9663 | 121.1838 | -0.27008 | 121.0876 | -0.16479 | -0.13733 | -0.14648 | 0.10071 | -0.1236 | -0.045776 | 0.88348 | 0.19226 | 0.17853 | 0.091553 | 0.07782 | 0.059509 | -0.20142 | -0.29755 | 0.16479 | 0.18311 | 0.19226 | 0.1236 | 0.13275 | 0.78278 | 121.5683 | 0.10529 | 121.3577 | 121.4905 | 121.4539 | 121.5912 | 121.5134 | -121.6141 | -121.6553 | 121.669 | 121.4172 | 9.5489 | 3.2959
1942.9688 | 121.7102 | -0.33417 | 121.3577 | 0.055313 | 5.9013 | 0.067099 | 0.066492 | 0.00027771 | -0.0022794 | 0.00061957 | 0.015442 | 0.0026852 | -1.3937 | 0.05883 | -0.0056226 | 0.011476 | 0.0023285 | 9.1782 | 121.2708 | -0.24261 | 121.3211 | 0.53558 | -0.14191 | -0.1236 | 2.9526 | 121.1975 | -0.28381 | 121.0785 | -0.13733 | -0.13275 | -0.14191 | 0.091552 | -0.086975 | -0.036621 | 0.86975 | 0.21057 | 0.19226 | 0.11902 | 0.10071 | 0.050354 | -0.16022 | -0.27924 | 0.19684 | 0.19226 | 0.20142 | 0.14191 | 0.15106 | 0.7782 | 121.5637 | 0.14648 | 121.3623 | 121.5134 | 121.4813 | 121.6049 | 121.5317 | -121.6003 | -121.6415 | 121.6553 | 121.4127 | 9.5123 | 3.2867
1944.6719 | 121.7239 | -0.33417 | 121.3806 | 0.040054 | 6.0094 | 0.064963 | 0.065424 | 0.0039093 | -0.0020658 | 0.002115 | 0.01239 | 0.002258 | -1.3942 | 0.060539 | -0.0051954 | 0.010194 | -0.0015167 | 9.1461 | 121.2708 | -0.25635 | 121.3074 | 0.52643 | -0.1236 | -0.1236 | 2.9526 | 121.2158 | -0.28381 | 121.0968 | -0.13275 | -0.13733 | -0.13733 | 0.077819 | -0.10986 | -0.073242 | 0.86059 | 0.21057 | 0.21057 | 0.13275 | 0.13275 | 0.050354 | -0.1648 | -0.28381 | 0.20142 | 0.19684 | 0.19684 | 0.14648 | 0.14648 | 0.78278 | 121.5637 | 0.15106 | 121.3806 | 121.5271 | 121.4996 | 121.6049 | 121.55 | -121.637 | -121.6644 | 121.6415 | 121.431 | 9.4803 | 3.2867
1946.4375 | 121.7697 | -0.29755 | 121.3303 | 0.055313 | 6.0188 | 0.06774 | 0.065424 | 0.0043365 | -0.0012112 | 0.003183 | 0.015442 | 0.0026852 | -1.394 | 0.063957 | -0.0026318 | 0.01233 | -0.00066231 | 9.1553 | 121.2433 | -0.20142 | 121.4035 | 0.66834 | -0.059509 | -0.022888 | 3.0533 | 121.1563 | -0.27466 | 121.1563 | -0.082397 | -0.045776 | -0.082397 | 0.09613 | -0.086975 | 0.073242 | 0.96588 | 0.27466 | 0.23804 | 0.17853 | 0.14191 | 0.022888 | -0.17395 | -0.17395 | 0.21515 | 0.21515 | 0.25177 | 0.19226 | 0.22888 | 0.86975 | 121.6049 | 0.19226 | 121.431 | 121.4447 | 121.431 | 121.5408 | 121.4539 | -121.5317 | -121.6049 | 121.701 | 121.4539 | 9.4528 | 3.3508
1948.2188 | 121.7194 | -0.32044 | 121.3715 | 0.017166 | 6.0989 | 0.067954 | 0.067133 | 0.0041229 | -0.0033474 | 0.0036102 | 0.0093383 | 0.0037532 | -1.3972 | 0.053916 | -0.0045544 | 0.010194 | 0.00019229 | 9.0775 | 121.2524 | -0.20599 | 121.3074 | 0.58594 | -0.1236 | -0.10986 | 2.9755 | 121.1838 | -0.27924 | 121.106 | -0.13275 | -0.11902 | -0.1236 | 0.11444 | -0.11902 | -0.064087 | 0.90637 | 0.21057 | 0.19684 | 0.096131 | 0.082398 | 0.041199 | -0.18768 | -0.2655 | 0.18768 | 0.19684 | 0.20142 | 0.15564 | 0.16022 | 0.79193 | 121.5134 | 0.14648 | 121.3852 | 121.4584 | 121.463 | 121.5729 | 121.5042 | -121.5775 | -121.6507 | 121.6278 | 121.4264 | 9.3979 | 3.2959
1949.9219 | 121.7148 | -0.33417 | 121.344 | 0.0019074 | 6.0863 | 0.064749 | 0.065851 | -0.00014949 | -0.0048428 | -0.001303 | -0.0059205 | 0.0035396 | -1.3937 | 0.066093 | -0.003059 | 0.010835 | 0.00019229 | 8.9951 | 121.2433 | -0.21515 | 121.2433 | 0.53101 | -0.21057 | -0.16479 | 2.8976 | 121.17 | -0.2655 | 121.1014 | -0.15564 | -0.13733 | -0.11902 | 0.11902 | -0.10071 | -0.10071 | 0.86517 | 0.16937 | 0.1236 | 0.050354 | 0.004578 | 0.068664 | -0.17395 | -0.24262 | 0.17853 | 0.21515 | 0.19684 | 0.14648 | 0.12817 | 0.74616 | 121.4584 | 0.10986 | 121.3669 | 121.4584 | 121.4355 | 121.5775 | 121.5042 | -121.5591 | -121.6095 | 121.5775 | 121.4355 | 9.3292 | 3.2318
1951.6406 | 121.788 | -0.32501 | 121.3303 | 0.0019074 | 6.0118 | 0.064749 | 0.066065 | -0.00036309 | -0.004202 | 0.00061957 | -0.0059205 | 0.00076264 | -1.3961 | 0.069084 | -0.0049818 | 0.010621 | 0.0014741 | 9.0179 | 121.1975 | -0.21973 | 121.312 | 0.60883 | -0.10529 | -0.086975 | 2.948 | 121.138 | -0.25177 | 121.1243 | -0.082397 | -0.045776 | -0.082397 | 0.10529 | -0.13275 | -0.01831 | 0.93384 | 0.23804 | 0.21973 | 0.13275 | 0.11444 | 0.073242 | -0.19226 | -0.20599 | 0.24262 | 0.24262 | 0.27924 | 0.16937 | 0.20599 | 0.82855 | 121.5317 | 0.16937 | 121.376 | 121.4172 | 121.3898 | 121.5225 | 121.463 | -121.55 | -121.582 | 121.637 | 121.4493 | 9.343 | 3.273
1953.4062 | 121.8018 | -0.32501 | 121.344 | 0.0095369 | 6.1034 | 0.064322 | 0.061579 | 6.4114e-05 | -0.0037746 | -0.0015166 | -0.0028687 | 0.00097624 | -1.3965 | 0.064597 | -0.0049818 | 0.011262 | 0.0021149 | 8.9996 | 121.2021 | -0.20142 | 121.376 | 0.6958 | -0.032043 | -0.009155 | 3.0487 | 121.1243 | -0.25177 | 121.1884 | -0.045776 | -0.018311 | -0.086975 | 0.1236 | -0.14191 | 0.032044 | 1.0208 | 0.31586 | 0.29297 | 0.19226 | 0.16937 | 0.073242 | -0.21973 | -0.15564 | 0.27924 | 0.23804 | 0.3067 | 0.16479 | 0.23346 | 0.89722 | 121.5775 | 0.20599 | 121.4401 | 121.4035 | 121.376 | 121.5271 | 121.4493 | -121.5454 | -121.5958 | 121.701 | 121.5134 | 9.3246 | 3.3737
1955.1875 | 121.7743 | -0.30212 | 121.344 | 0.055313 | 6.1006 | 0.067954 | 0.066706 | 0.0022003 | -0.001852 | 0.00083317 | 0.015442 | 0.0035396 | -1.3916 | 0.066947 | -0.0011364 | 0.014253 | -0.00087591 | 8.9722 | 121.2067 | -0.23346 | 121.3943 | 0.70038 | -0.059509 | -0.045776 | 3.0121 | 121.1472 | -0.29755 | 121.1609 | -0.091553 | -0.064087 | -0.086975 | 0.068665 | -0.13733 | 0.050354 | 1.0025 | 0.25635 | 0.24261 | 0.18768 | 0.17395 | 0.004578 | -0.19684 | -0.1831 | 0.21057 | 0.21515 | 0.23804 | 0.21057 | 0.23346 | 0.93384 | 121.6278 | 0.20599 | 121.4584 | 121.4401 | 121.4447 | 121.5088 | 121.4493 | -121.5775 | -121.6415 | 121.6965 | 121.463 | 9.2743 | 3.3142
1956.9062 | 121.8018 | -0.31128 | 121.3348 | -0.013352 | 6.0987 | 0.06304 | 0.064783 | -0.0014313 | -0.0027066 | 0.00040597 | 0.0032349 | 0.0011898 | -1.3957 | 0.05883 | -0.0039136 | 0.011903 | -0.0051483 | 8.9127 | 121.1609 | -0.19684 | 121.3852 | 0.70496 | -0.045776 | -0.050354 | 2.9892 | 121.1472 | -0.25635 | 121.1472 | -0.068665 | -0.013733 | -0.068665 | 0.11444 | -0.17395 | 0.050354 | 1.0162 | 0.26092 | 0.2655 | 0.14648 | 0.15106 | 0.054931 | -0.18768 | -0.18768 | 0.24261 | 0.24261 | 0.29755 | 0.18768 | 0.24262 | 0.90179 | 121.582 | 0.18768 | 121.4035 | 121.3577 | 121.4035 | 121.4722 | 121.4584 | -121.5317 | -121.5912 | 121.6965 | 121.4584 | 9.2239 | 3.3005
1958.6875 | 121.6873 | -0.35248 | 121.3486 | 0.047683 | 5.786 | 0.064108 | 0.068415 | 0.0022003 | -0.0022794 | 0.00040597 | 0.021545 | 0.003326 | -1.3946 | 0.061179 | -0.0066906 | 0.012544 | -0.00044851 | 8.8394 | 121.2387 | -0.28381 | 121.2708 | 0.55847 | -0.16022 | -0.13733 | 2.8336 | 121.225 | -0.33417 | 121.0281 | -0.20599 | -0.15564 | -0.17853 | 0.068665 | -0.10986 | -0.07782 | 0.91095 | 0.21515 | 0.19226 | 0.14648 | 0.1236 | 0.018311 | -0.1236 | -0.32044 | 0.14648 | 0.17395 | 0.19684 | 0.15564 | 0.17853 | 0.84228 | 121.5546 | 0.12817 | 121.3623 | 121.5225 | 121.5591 | 121.5912 | 121.5775 | -121.6324 | -121.6827 | 121.6232 | 121.3806 | 9.1919 | 3.186
1960.4531 | 121.7377 | -0.33875 | 121.3211 | 0.024795 | 6.0844 | 0.062186 | 0.065638 | -0.0012177 | -0.0014248 | 0.00061957 | 0.0093383 | 0.0018306 | -1.3946 | 0.07122 | -0.0034864 | 0.011262 | 0.00061949 | 8.7799 | 121.1975 | -0.21515 | 121.3165 | 0.61798 | -0.12817 | -0.09613 | 2.8885 | 121.1517 | -0.27466 | 121.106 | -0.14191 | -0.10071 | -0.11902 | 0.1236 | -0.1236 | -0.004578 | 0.95673 | 0.24262 | 0.21057 | 0.11902 | 0.086975 | 0.064087 | -0.16937 | -0.21515 | 0.19684 | 0.21973 | 0.23804 | 0.15564 | 0.17395 | 0.83313 | 121.5317 | 0.13275 | 121.3806 | 121.4127 | 121.4264 | 121.5363 | 121.4905 | -121.5363 | -121.5958 | 121.6553 | 121.4447 | 9.1187 | 3.2272
1962.25 | 121.6782 | -0.35706 | 121.3623 | -0.0057221 | 6.0088 | 0.064536 | 0.066492 | 0.00027771 | -0.0054836 | 0.0016876 | -0.0059205 | 0.0043942 | -1.3969 | 0.060111 | -0.0058362 | 0.0097669 | 0.0021149 | 8.7799 | 121.1746 | -0.20142 | 121.312 | 0.65002 | -0.10071 | -0.10986 | 2.8885 | 121.1517 | -0.29755 | 121.051 | -0.19226 | -0.14191 | -0.16479 | 0.15564 | -0.18768 | -0.050354 | 1.0071 | 0.24719 | 0.25635 | 0.091553 | 0.10071 | 0.05951 | -0.21057 | -0.31128 | 0.16479 | 0.19226 | 0.21515 | 0.13275 | 0.15564 | 0.85144 | 121.5134 | 0.10528 | 121.3486 | 121.376 | 121.4493 | 121.5317 | 121.5088 | -121.5637 | -121.6599 | 121.669 | 121.4081 | 9.137 | 3.2455
1964.0156 | 121.7468 | -0.33875 | 121.3303 | 0.024795 | 6.0058 | 0.065604 | 0.065424 | -0.00057689 | -0.0037746 | -0.0010894 | 0.0093383 | 0.00097624 | -1.3935 | 0.065452 | -0.0039136 | 0.011049 | 0.00061949 | 8.7112 | 121.1884 | -0.21057 | 121.3074 | 0.64087 | -0.1236 | -0.086975 | 2.9022 | 121.1517 | -0.28839 | 121.0831 | -0.15564 | -0.10529 | -0.12817 | 0.12817 | -0.14191 | -0.022888 | 0.97961 | 0.25177 | 0.21515 | 0.1236 | 0.086975 | 0.050354 | -0.17853 | -0.24719 | 0.18311 | 0.21057 | 0.23346 | 0.16022 | 0.18311 | 0.85144 | 121.5179 | 0.13275 | 121.3715 | 121.3989 | 121.4401 | 121.5271 | 121.4905 | -121.5408 | -121.6187 | 121.6461 | 121.4218 | 9.05 | 3.241
1965.7188 | 121.6507 | -0.37079 | 121.3623 | -0.0057221 | 6.0703 | 0.065604 | 0.065638 | 0.0019867 | -0.0020658 | 0.0016876 | -0.0059205 | 0.002258 | -1.3942 | 0.067161 | -0.0024182 | 0.010835 | -0.0034393 | 8.5876 | 121.2204 | -0.25177 | 121.2158 | 0.50812 | -0.24719 | -0.2243 | 2.7649 | 121.1929 | -0.31586 | 120.9961 | -0.24261 | -0.19684 | -0.1831 | 0.11902 | -0.14191 | -0.14649 | 0.87891 | 0.14648 | 0.1236 | 0.027466 | 0.004578 | 0.054932 | -0.16937 | -0.36621 | 0.12817 | 0.18768 | 0.17395 | 0.13275 | 0.11902 | 0.75989 | 121.4676 | 0.073242 | 121.312 | 121.4722 | 121.5088 | 121.5912 | 121.5637 | -121.6141 | -121.6782 | 121.5866 | 121.3669 | 8.9584 | 3.1357
1967.4844 | 121.6919 | -0.38452 | 121.344 | 0.0019074 | 5.9913 | 0.066245 | 0.069697 | -0.0046357 | -0.0031338 | 0.002115 | 0.00018312 | 0.0026852 | -1.3948 | 0.063102 | -0.003059 | 0.013185 | 0.0010467 | 8.519 | 121.2021 | -0.24719 | 121.2204 | 0.54016 | -0.23346 | -0.1831 | 2.774 | 121.1472 | -0.30212 | 121.0373 | -0.23804 | -0.19684 | -0.19226 | 0.13733 | -0.14191 | -0.1236 | 0.92468 | 0.20142 | 0.15106 | 0.064087 | 0.013733 | 0.082397 | -0.19684 | -0.3067 | 0.14648 | 0.19226 | 0.18768 | 0.10986 | 0.10529 | 0.78735 | 121.4676 | 0.064087 | 121.3394 | 121.4493 | 121.4493 | 121.5866 | 121.5317 | -121.5912 | -121.6461 | 121.6049 | 121.4218 | 8.9035 | 3.1586
1969.2812 | 121.7606 | -0.33417 | 121.2936 | 0.017166 | 6.1143 | 0.066672 | 0.063288 | -0.0014313 | -0.0033474 | -0.0015166 | 0.00018312 | 0.0024716 | -1.3952 | 0.061179 | -0.0043408 | 0.01233 | 0.00083309 | 8.4732 | 121.1975 | -0.22888 | 121.2845 | 0.64087 | -0.13733 | -0.11444 | 2.8519 | 121.138 | -0.27924 | 121.0968 | -0.13275 | -0.09613 | -0.1236 | 0.10528 | -0.09613 | -0.009155 | 0.97504 | 0.21973 | 0.19684 | 0.11444 | 0.091553 | 0.054931 | -0.15564 | -0.19684 | 0.20142 | 0.21057 | 0.23804 | 0.15564 | 0.18311 | 0.86975 | 121.5134 | 0.14648 | 121.376 | 121.4264 | 121.4172 | 121.5317 | 121.4722 | -121.5225 | -121.5729 | 121.6187 | 121.431 | 8.8074 | 3.186
1971.0625 | 121.701 | -0.35706 | 121.3715 | 0.0095369 | 6.1408 | 0.065817 | 0.067774 | 0.00091851 | -0.0027066 | 0.001474 | 0.0032349 | 0.0031124 | -1.3935 | 0.057548 | -0.0060498 | 0.010835 | -0.0032257 | 8.4366 | 121.2067 | -0.24719 | 121.2982 | 0.65002 | -0.14648 | -0.1236 | 2.8702 | 121.1472 | -0.30212 | 121.0556 | -0.1831 | -0.15106 | -0.16479 | 0.10986 | -0.16479 | -0.073242 | 1.0071 | 0.23346 | 0.21057 | 0.1236 | 0.10071 | 0.054932 | -0.2243 | -0.31586 | 0.17395 | 0.19226 | 0.20599 | 0.13733 | 0.15106 | 0.89722 | 121.5454 | 0.11902 | 121.3577 | 121.4539 | 121.4493 | 121.5637 | 121.5042 | -121.6187 | -121.6736 | 121.6553 | 121.4127 | 8.7936 | 3.2272
1972.7812 | 121.6873 | -0.35248 | 121.344 | 0.0095369 | 6.1513 | 0.06539 | 0.067133 | -0.0031403 | -0.0022794 | 0.002115 | -0.0028687 | 0.002258 | -1.3963 | 0.063316 | -0.0026318 | 0.011262 | 0.0029693 | 8.3817 | 121.2479 | -0.24719 | 121.2845 | 0.64545 | -0.16479 | -0.13275 | 2.861 | 121.1563 | -0.28381 | 121.051 | -0.18768 | -0.15564 | -0.16479 | 0.10529 | -0.09613 | -0.059509 | 0.99792 | 0.21973 | 0.18768 | 0.11444 | 0.082397 | 0.068665 | -0.18768 | -0.29297 | 0.1648 | 0.18768 | 0.19684 | 0.11902 | 0.12817 | 0.89264 | 121.5317 | 0.09613 | 121.3348 | 121.4951 | 121.4401 | 121.6003 | 121.5088 | -121.5912 | -121.6278 | 121.637 | 121.4035 | 8.7341 | 3.2135
1974.5469 | 121.6827 | -0.36163 | 121.3394 | 0.055313 | 6.1442 | 0.065176 | 0.06756 | -0.0020721 | -0.0029202 | 0.00083317 | 0.018494 | 0.0048214 | -1.3927 | 0.063529 | -0.0083996 | 0.011049 | -0.0042939 | 8.2901 | 121.2845 | -0.28381 | 121.257 | 0.6134 | -0.15106 | -0.14191 | 2.7969 | 121.1517 | -0.33417 | 121.019 | -0.18768 | -0.15106 | -0.16937 | 0.07782 | -0.054932 | -0.082398 | 0.97504 | 0.21973 | 0.21057 | 0.14191 | 0.13275 | 0.027466 | -0.18768 | -0.32044 | 0.17395 | 0.19226 | 0.21057 | 0.16479 | 0.1831 | 0.89722 | 121.5408 | 0.14648 | 121.3531 | 121.5683 | 121.4859 | 121.6461 | 121.5134 | -121.6232 | -121.6736 | 121.6187 | 121.3806 | 8.6517 | 3.1586
1976.3281 | 121.7285 | -0.33875 | 121.3211 | -0.0057221 | 6.2038 | 0.062186 | 0.064783 | -0.00014949 | -0.00099764 | 0.00019217 | 0.00018312 | 0.001617 | -1.3952 | 0.058402 | -0.0062634 | 0.0099805 | 0.0012603 | 8.2581 | 121.1609 | -0.2243 | 121.3257 | 0.72784 | -0.059509 | -0.045776 | 2.8839 | 121.1334 | -0.27466 | 121.0831 | -0.11444 | -0.082397 | -0.13275 | 0.11444 | -0.16022 | 0.004578 | 1.0666 | 0.29297 | 0.27924 | 0.17853 | 0.16479 | 0.064087 | -0.18768 | -0.23804 | 0.2243 | 0.20599 | 0.25635 | 0.14191 | 0.19226 | 0.95215 | 121.55 | 0.16022 | 121.3577 | 121.3852 | 121.4081 | 121.4996 | 121.4722 | -121.5454 | -121.5958 | 121.6644 | 121.4218 | 8.5968 | 3.2227
1978.0938 | 121.6919 | -0.37994 | 121.3623 | 0.047683 | 6.1143 | 0.062827 | 0.06692 | -0.00014949 | -0.0027066 | 0.00040597 | 0.018494 | 0.0024716 | -1.394 | 0.05883 | -0.0043408 | 0.012117 | 0.00061949 | 8.1482 | 121.2616 | -0.27924 | 121.2433 | 0.62256 | -0.14191 | -0.12817 | 2.7786 | 121.1746 | -0.32959 | 121.0327 | -0.19226 | -0.13733 | -0.16479 | 0.10071 | -0.10071 | -0.11902 | 1.0025 | 0.25177 | 0.23804 | 0.15106 | 0.13733 | 0.050354 | -0.18768 | -0.32959 | 0.18768 | 0.21515 | 0.24261 | 0.16479 | 0.19226 | 0.90179 | 121.5225 | 0.13733 | 121.3623 | 121.5408 | 121.5042 | 121.6415 | 121.5546 | -121.6415 | -121.6919 | 121.6232 | 121.4127 | 8.5281 | 3.1586
1979.8125 | 121.6919 | -0.36621 | 121.3486 | 0.017166 | 6.1442 | 0.06539 | 0.067347 | -0.00014949 | -0.001852 | 0.00061957 | 0.00018312 | 0.005676 | -1.395 | 0.067161 | -0.0039136 | 0.0084851 | -0.0036529 | 8.139 | 121.2387 | -0.22888 | 121.2891 | 0.6958 | -0.11902 | -0.10529 | 2.8336 | 121.17 | -0.30212 | 121.0693 | -0.16022 | -0.10986 | -0.14648 | 0.13733 | -0.10986 | -0.05951 | 1.062 | 0.26093 | 0.24719 | 0.1236 | 0.10986 | 0.064087 | -0.17853 | -0.27924 | 0.20599 | 0.21973 | 0.25635 | 0.15564 | 0.19226 | 0.92468 | 121.5179 | 0.14191 | 121.3715 | 121.4676 | 121.4722 | 121.6049 | 121.5363 | -121.5775 | -121.6507 | 121.6553 | 121.4355 | 8.5052 | 3.1998
1981.5312 | 121.7148 | -0.34332 | 121.3531 | 0.0019074 | 6.1534 | 0.064536 | 0.067347 | 0.00049131 | -0.0027066 | 0.0012604 | -0.0028687 | 0.0026852 | -1.3972 | 0.060752 | -0.0032728 | 0.013612 | -0.00023491 | 8.0292 | 121.2662 | -0.25177 | 121.2067 | 0.62714 | -0.20142 | -0.14648 | 2.7786 | 121.1609 | -0.28381 | 121.0693 | -0.16022 | -0.1236 | -0.13275 | 0.091553 | -0.086975 | -0.14648 | 0.97046 | 0.19684 | 0.14191 | 0.10529 | 0.050354 | 0.05951 | -0.19226 | -0.28381 | 0.18311 | 0.21057 | 0.21973 | 0.15106 | 0.16022 | 0.87891 | 121.4584 | 0.1236 | 121.3531 | 121.5179 | 121.4447 | 121.6095 | 121.5042 | -121.6049 | -121.637 | 121.55 | 121.4127 | 8.3725 | 3.1219
1983.2969 | 121.7194 | -0.35706 | 121.3394 | 0.040054 | 5.9755 | 0.06539 | 0.066706 | 0.0019867 | -0.001852 | 0.0033966 | 0.0062865 | 0.005035 | -1.3937 | 0.058189 | -0.0024182 | 0.011689 | -0.0021575 | 8.0338 | 121.2158 | -0.27008 | 121.3028 | 0.71869 | -0.12817 | -0.086975 | 2.8107 | 121.1746 | -0.29755 | 121.0648 | -0.15564 | -0.091553 | -0.13275 | 0.086975 | -0.1236 | -0.036622 | 1.0757 | 0.27008 | 0.22888 | 0.18311 | 0.14191 | 0.05951 | -0.16479 | -0.27466 | 0.20142 | 0.2243 | 0.2655 | 0.16479 | 0.20599 | 0.98877 | 121.5729 | 0.14191 | 121.3623 | 121.4859 | 121.4722 | 121.5729 | 121.5317 | -121.6095 | -121.637 | 121.6599 | 121.4218 | 8.3908 | 3.1677
1985.0625 | 121.8018 | -0.32044 | 121.2982 | -0.013352 | 5.9483 | 0.062827 | 0.064997 | -0.0016449 | -0.001852 | -0.00087583 | -0.0028687 | 0.0018306 | -1.3959 | 0.063529 | -0.0043408 | 0.013185 | -0.0015167 | 7.9605 | 121.17 | -0.20142 | 121.3531 | 0.82398 | -0.036621 | 0 | 2.9205 | 121.0968 | -0.2655 | 121.1563 | -0.050354 | 0.004578 | -0.082397 | 0.11902 | -0.12817 | 0.054931 | 1.1444 | 0.32044 | 0.28381 | 0.20142 | 0.1648 | 0.054932 | -0.20142 | -0.14191 | 0.27008 | 0.23804 | 0.32501 | 0.18311 | 0.27008 | 1.0254 | 121.5546 | 0.21515 | 121.4218 | 121.3715 | 121.3623 | 121.4905 | 121.4172 | -121.4996 | -121.5637 | 121.6736 | 121.4767 | 8.2809 | 3.241
1986.8438 | 121.8109 | -0.32044 | 121.3074 | -0.0057221 | 6.0255 | 0.063254 | 0.063288 | -0.0012177 | -0.0046292 | -0.0017304 | 0.00018312 | 0.0026852 | -1.395 | 0.071006 | -0.0058362 | 0.014466 | 0.00061949 | 7.8781 | 121.1609 | -0.22888 | 121.3577 | 0.83313 | -0.032043 | -0.004578 | 2.916 | 121.1014 | -0.27466 | 121.1655 | -0.054932 | 0.004578 | -0.082397 | 0.091553 | -0.14648 | 0.050354 | 1.1536 | 0.31586 | 0.28839 | 0.2243 | 0.19684 | 0.045777 | -0.20599 | -0.14191 | 0.2655 | 0.23804 | 0.32501 | 0.19226 | 0.27924 | 1.062 | 121.5866 | 0.21973 | 121.4401 | 121.3898 | 121.376 | 121.4813 | 121.4218 | -121.5363 | -121.582 | 121.6782 | 121.4859 | 8.1985 | 3.2364
1988.5312 | 121.6736 | -0.39368 | 121.312 | 0.0019074 | 6.1002 | 0.06539 | 0.067774 | -0.0012177 | -0.0033474 | 0.0012604 | -0.0028687 | 0.0048214 | -1.3957 | 0.067161 | -0.0022046 | 0.010621 | -0.0030121 | 7.7362 | 121.2021 | -0.25635 | 121.2158 | 0.63171 | -0.21973 | -0.15106 | 2.6962 | 121.1472 | -0.30212 | 121.0236 | -0.2243 | -0.16022 | -0.17853 | 0.13733 | -0.10986 | -0.096131 | 1.0254 | 0.24261 | 0.17395 | 0.10529 | 0.036621 | 0.091553 | -0.16479 | -0.28839 | 0.16937 | 0.21515 | 0.23346 | 0.1236 | 0.14191 | 0.88806 | 121.4722 | 0.07782 | 121.3257 | 121.4584 | 121.4493 | 121.5958 | 121.5408 | -121.5683 | -121.6141 | 121.6095 | 121.4172 | 8.1299 | 3.0899
1990.3125 | 121.6827 | -0.36163 | 121.344 | 0.040054 | 6.0504 | 0.065176 | 0.068842 | 0.0028411 | -0.002493 | 0.00019217 | 0.018494 | 0.0046078 | -1.3927 | 0.062248 | -0.006477 | 0.013185 | -0.0025849 | 7.6767 | 121.257 | -0.27924 | 121.2204 | 0.67291 | -0.13275 | -0.10986 | 2.7466 | 121.1884 | -0.34332 | 121.0144 | -0.1831 | -0.13733 | -0.17395 | 0.082397 | -0.086975 | -0.1236 | 1.0345 | 0.25177 | 0.22888 | 0.16937 | 0.14648 | 0.01831 | -0.15564 | -0.32959 | 0.17853 | 0.18768 | 0.2243 | 0.16937 | 0.20599 | 0.95215 | 121.4996 | 0.16022 | 121.3577 | 121.5363 | 121.5317 | 121.6187 | 121.55 | -121.6232 | -121.6873 | 121.582 | 121.376 | 8.0383 | 3.1082
1992.0312 | 121.7468 | -0.33875 | 121.3257 | 0.040054 | 6.071 | 0.068167 | 0.068201 | -0.0044221 | -0.0014248 | 0.0010468 | 0.0093383 | 0.0020444 | -1.3955 | 0.062675 | -0.0034864 | 0.011476 | 0.0010467 | 7.6309 | 121.2067 | -0.23346 | 121.3165 | 0.79193 | -0.082397 | -0.050354 | 2.8015 | 121.1243 | -0.30212 | 121.0876 | -0.12817 | -0.068665 | -0.10986 | 0.10529 | -0.11902 | -0.009156 | 1.1307 | 0.28839 | 0.25635 | 0.1831 | 0.15106 | 0.036621 | -0.20142 | -0.23804 | 0.21057 | 0.22888 | 0.27008 | 0.19226 | 0.23346 | 1.0254 | 121.55 | 0.17395 | 121.3898 | 121.4401 | 121.4264 | 121.5454 | 121.463 | -121.5591 | -121.6278 | 121.6553 | 121.4264 | 7.9697 | 3.1403
1993.8125 | 121.669 | -0.36621 | 121.3348 | 0.0019074 | 6.0934 | 0.068167 | 0.067988 | 6.4114e-05 | -0.00099764 | -0.0025848 | 0.00018312 | 0.0043942 | -1.395 | 0.060752 | -0.0017774 | 0.011262 | -2.1314e-05 | 7.4982 | 121.2387 | -0.23804 | 121.1884 | 0.61798 | -0.23804 | -0.16022 | 2.6733 | 121.1655 | -0.28839 | 121.0144 | -0.23346 | -0.16479 | -0.16937 | 0.12817 | -0.096131 | -0.14648 | 0.98419 | 0.20599 | 0.12817 | 0.07782 | 0 | 0.07782 | -0.16937 | -0.32044 | 0.13275 | 0.19684 | 0.20142 | 0.11902 | 0.1236 | 0.85602 | 121.4264 | 0.054932 | 121.3028 | 121.4767 | 121.4539 | 121.6049 | 121.5317 | -121.5729 | -121.6232 | 121.5546 | 121.3806 | 7.8644 | 3.0396
1995.5156 | 121.7194 | -0.3479 | 121.3074 | 0.032425 | 6.087 | 0.065604 | 0.069697 | 0.0011321 | -0.00099764 | 0.003183 | 0.00018312 | 0.0048214 | -1.3955 | 0.054557 | -0.0049818 | 0.010621 | -2.1314e-05 | 7.4387 | 121.2204 | -0.25635 | 121.2753 | 0.75073 | -0.11444 | -0.07782 | 2.8015 | 121.1929 | -0.30212 | 121.0785 | -0.11902 | -0.086975 | -0.12817 | 0.091552 | -0.086975 | -0.032043 | 1.0986 | 0.27008 | 0.23346 | 0.17853 | 0.14191 | 0.045776 | -0.11444 | -0.22888 | 0.22888 | 0.21973 | 0.26092 | 0.17395 | 0.21515 | 1.0071 | 121.5317 | 0.18311 | 121.3806 | 121.4767 | 121.4951 | 121.5683 | 121.5408 | -121.5637 | -121.6095 | 121.6232 | 121.4264 | 7.7866 | 3.1494
1997.2812 | 121.7743 | -0.33417 | 121.3028 | -0.013352 | 6.0853 | 0.064536 | 0.064997 | -0.0010041 | -0.004202 | 0.0010468 | -0.0059205 | 0.00012184 | -1.3957 | 0.063316 | -0.0051954 | 0.01233 | -0.00044851 | 7.3746 | 121.17 | -0.21973 | 121.344 | 0.85602 | -0.027466 | 0.004578 | 2.8656 | 121.1426 | -0.2655 | 121.1426 | -0.036621 | 0.018311 | -0.073242 | 0.11444 | -0.13275 | 0.041199 | 1.1902 | 0.33875 | 0.3067 | 0.22431 | 0.19226 | 0.068664 | -0.16022 | -0.16022 | 0.29755 | 0.26092 | 0.35248 | 0.19226 | 0.28381 | 1.0757 | 121.5637 | 0.22888 | 121.4081 | 121.3898 | 121.4081 | 121.5042 | 121.4767 | -121.5225 | -121.5683 | 121.6782 | 121.4767 | 7.7087 | 3.1998
1999.0625 | 121.7468 | -0.33417 | 121.2936 | 0.040054 | 6.1218 | 0.06539 | 0.066279 | 0.0015595 | -0.00014304 | 0.0010468 | 0.018494 | 0.0046078 | -1.3933 | 0.062461 | -0.003059 | 0.012971 | 0.0016877 | 7.3242 | 121.2158 | -0.25635 | 121.3486 | 0.86517 | -0.032043 | 0.004578 | 2.8427 | 121.1472 | -0.30212 | 121.1105 | -0.10071 | -0.018311 | -0.082397 | 0.077819 | -0.07782 | 0.054932 | 1.1993 | 0.33875 | 0.30212 | 0.26093 | 0.22431 | 0.032043 | -0.14648 | -0.1831 | 0.23346 | 0.25177 | 0.31586 | 0.21973 | 0.28381 | 1.1215 | 121.6049 | 0.20142 | 121.4127 | 121.4722 | 121.4493 | 121.55 | 121.4813 | -121.55 | -121.5958 | 121.6827 | 121.4447 | 7.6584 | 3.1769
2000.8438 | 121.756 | -0.33875 | 121.3531 | -0.0057221 | 6.0921 | 0.063681 | 0.068201 | -0.0020721 | -0.0020658 | -2.1434e-05 | -0.0059205 | 0.00097624 | -1.3955 | 0.063316 | -0.005409 | 0.011049 | 0.00083309 | 7.2556 | 121.1609 | -0.21973 | 121.3394 | 0.82398 | -0.045776 | -0.004578 | 2.8107 | 121.1105 | -0.25635 | 121.1014 | -0.091553 | -0.013733 | -0.10071 | 0.11902 | -0.19226 | -0.013732 | 1.1627 | 0.33417 | 0.29297 | 0.21515 | 0.17395 | 0.082397 | -0.24261 | -0.25177 | 0.24719 | 0.23804 | 0.32501 | 0.15564 | 0.24262 | 1.0437 | 121.5591 | 0.1648 | 121.3577 | 121.3806 | 121.3669 | 121.4996 | 121.4493 | -121.5729 | -121.6095 | 121.6782 | 121.4401 | 7.5943 | 3.1494
2002.6094 | 121.7789 | -0.35248 | 121.3257 | 0.0019074 | 6.0592 | 0.065817 | 0.067347 | -0.0022857 | -0.00057044 | -0.0021576 | -0.0059205 | 0.00033544 | -1.3933 | 0.066947 | -0.0056226 | 0.012971 | -0.0015167 | 7.1365 | 121.2112 | -0.23804 | 121.2936 | 0.78735 | -0.082397 | -0.013733 | 2.7557 | 121.138 | -0.2655 | 121.106 | -0.07782 | 0.004578 | -0.073242 | 0.11444 | -0.11444 | -0.032044 | 1.1398 | 0.33875 | 0.27008 | 0.2243 | 0.15564 | 0.086975 | -0.18768 | -0.21973 | 0.27466 | 0.27924 | 0.35706 | 0.19226 | 0.27008 | 1.0254 | 121.5317 | 0.18768 | 121.3715 | 121.4493 | 121.4035 | 121.5637 | 121.4905 | -121.5637 | -121.5912 | 121.6461 | 121.4584 | 7.489 | 3.1082
2004.375 | 121.6644 | -0.36621 | 121.3303 | 0.0019074 | 6.1248 | 0.065604 | 0.069056 | -0.00014949 | -0.002493 | 0.00019217 | -0.0028687 | 0.0035396 | -1.3937 | 0.065025 | -0.003059 | 0.011903 | 0.0019013 | 7.0038 | 121.2479 | -0.21973 | 121.1929 | 0.67291 | -0.21057 | -0.13275 | 2.6276 | 121.1609 | -0.30212 | 121.019 | -0.2243 | -0.15106 | -0.17395 | 0.14648 | -0.082397 | -0.13733 | 1.0391 | 0.23346 | 0.15564 | 0.086976 | 0.009156 | 0.064087 | -0.16937 | -0.31128 | 0.14191 | 0.19226 | 0.21515 | 0.12817 | 0.15106 | 0.89264 | 121.4127 | 0.07782 | 121.3211 | 121.4676 | 121.463 | 121.6141 | 121.5271 | -121.55 | -121.6324 | 121.5591 | 121.3852 | 7.37 | 2.9938
2006.1719 | 121.6644 | -0.37994 | 121.3394 | -0.0057221 | 6.1346 | 0.062827 | 0.06756 | -0.0039947 | -0.004202 | 0.0010468 | 0.00018312 | 0.001617 | -1.3959 | 0.05947 | -0.0069044 | 0.011476 | -0.0021575 | 6.9534 | 121.1746 | -0.22888 | 121.2296 | 0.74616 | -0.12817 | -0.064087 | 2.6733 | 121.1472 | -0.31128 | 121.0052 | -0.16937 | -0.09613 | -0.16022 | 0.15106 | -0.16479 | -0.10986 | 1.1261 | 0.31586 | 0.25177 | 0.16479 | 0.10071 | 0.068665 | -0.19226 | -0.33417 | 0.21057 | 0.21973 | 0.28381 | 0.15106 | 0.21515 | 0.97504 | 121.4584 | 0.14191 | 121.3165 | 121.4035 | 121.4584 | 121.5546 | 121.5271 | -121.5683 | -121.6507 | 121.6095 | 121.3852 | 7.3334 | 3.0533
2007.8906 | 121.7789 | -0.33875 | 121.3211 | -0.0057221 | 6.1367 | 0.065817 | 0.066706 | 6.4114e-05 | -0.002493 | 0.00083317 | -0.0089723 | 0.0024716 | -1.3972 | 0.059043 | -0.0017774 | 0.01233 | 0.0012603 | 6.8619 | 121.2204 | -0.25635 | 121.2891 | 0.79193 | -0.12817 | -0.041199 | 2.7374 | 121.1472 | -0.27008 | 121.1197 | -0.086975 | -0.009155 | -0.054932 | 0.082397 | -0.10071 | -0.032044 | 1.1307 | 0.29755 | 0.21057 | 0.21515 | 0.12817 | 0.068664 | -0.17395 | -0.20142 | 0.25177 | 0.28381 | 0.32959 | 0.21515 | 0.26093 | 1.0483 | 121.5454 | 0.18311 | 121.3898 | 121.4767 | 121.4172 | 121.5591 | 121.4859 | -121.5775 | -121.5912 | 121.6278 | 121.4584 | 7.2006 | 3.0762
2009.6562 | 121.7651 | -0.34332 | 121.312 | -0.0057221 | 6.1058 | 0.063681 | 0.065424 | -0.0010041 | -0.0014248 | 0.00083317 | -0.0028687 | 0.0018306 | -1.3955 | 0.064597 | -0.005409 | 0.01233 | -2.1314e-05 | 6.8436 | 121.1655 | -0.22888 | 121.3577 | 0.89264 | -0.013733 | 0.027466 | 2.7969 | 121.1105 | -0.26093 | 121.1243 | -0.050354 | 0.045776 | -0.07782 | 0.11444 | -0.14648 | 0.045776 | 1.236 | 0.37079 | 0.32959 | 0.25635 | 0.21515 | 0.082398 | -0.20142 | -0.18768 | 0.29297 | 0.2655 | 0.3891 | 0.18311 | 0.3067 | 1.1215 | 121.5866 | 0.21057 | 121.3852 | 121.3943 | 121.3715 | 121.5088 | 121.4539 | -121.5408 | -121.5729 | 121.701 | 121.4676 | 7.1869 | 3.1403
2011.4219 | 121.6644 | -0.38452 | 121.3257 | -0.0057221 | 6.2111 | 0.063467 | 0.068201 | 0.0034821 | -0.0012112 | -0.0010894 | 0.015442 | 0.0054622 | -1.394 | 0.060111 | -0.0051954 | 0.010408 | -0.0017303 | 6.72 | 121.2708 | -0.31128 | 121.2341 | 0.75073 | -0.11444 | -0.073242 | 2.6596 | 121.2067 | -0.34332 | 120.9915 | -0.19226 | -0.11444 | -0.15106 | 0.073242 | -0.054932 | -0.091553 | 1.1353 | 0.31128 | 0.27008 | 0.23804 | 0.19684 | 0.041198 | -0.11902 | -0.33417 | 0.19226 | 0.23346 | 0.27008 | 0.19226 | 0.22888 | 1.062 | 121.5454 | 0.15106 | 121.3348 | 121.582 | 121.55 | 121.6553 | 121.5912 | -121.637 | -121.669 | 121.6187 | 121.376 | 7.1045 | 3.0441
2013.2188 | 121.7422 | -0.35248 | 121.2891 | 0.024795 | 6.1508 | 0.065817 | 0.067133 | 0.00049131 | -0.0014248 | 0.0010468 | 0.0032349 | 0.0024716 | -1.3944 | 0.066734 | -0.0024182 | 0.013398 | 0.00061949 | 6.6833 | 121.1838 | -0.23346 | 121.2845 | 0.81024 | -0.073242 | -0.022888 | 2.7054 | 121.1151 | -0.3067 | 121.0876 | -0.12817 | -0.036621 | -0.11902 | 0.11902 | -0.10528 | -0.004577 | 1.1627 | 0.32959 | 0.27924 | 0.21057 | 0.16022 | 0.045776 | -0.17395 | -0.20142 | 0.2243 | 0.23346 | 0.31586 | 0.18768 | 0.27008 | 1.0437 | 121.5179 | 0.17853 | 121.3943 | 121.4172 | 121.4218 | 121.5363 | 121.4676 | -121.5225 | -121.5958 | 121.637 | 121.4401 | 7.0358 | 3.0579
2014.9219 | 121.7331 | -0.32959 | 121.3165 | 0.0019074 | 6.26 | 0.064536 | 0.06756 | 0.0028411 | 0.00028416 | 0.0019012 | 0.00018312 | 0.0018306 | -1.3987 | 0.063102 | -0.0043408 | 0.012117 | 0.0031829 | 6.6101 | 121.1792 | -0.23346 | 121.2662 | 0.80566 | -0.09613 | -0.018311 | 2.6871 | 121.1334 | -0.28839 | 121.0876 | -0.10071 | -0.013733 | -0.10071 | 0.096131 | -0.13733 | -0.050354 | 1.1353 | 0.31128 | 0.23346 | 0.21515 | 0.13733 | 0.041199 | -0.18311 | -0.22888 | 0.22888 | 0.22888 | 0.31586 | 0.18768 | 0.27466 | 1.0391 | 121.4996 | 0.18768 | 121.376 | 121.4127 | 121.4218 | 121.5088 | 121.463 | -121.55 | -121.6049 | 121.5958 | 121.4172 | 6.9397 | 3.0167
2016.6875 | 121.788 | -0.32501 | 121.2891 | -0.013352 | 6.2218 | 0.064963 | 0.067774 | -0.0065583 | -0.0027066 | 0.003183 | -0.0059205 | 0.0026852 | -1.3963 | 0.06887 | -0.004768 | 0.011903 | 0.0016877 | 6.5643 | 121.1746 | -0.20599 | 121.3165 | 0.86975 | -0.027466 | 0.045776 | 2.7603 | 121.1105 | -0.29297 | 121.1197 | -0.027466 | 0.068665 | -0.045776 | 0.11902 | -0.11444 | 0.027466 | 1.1948 | 0.37079 | 0.29755 | 0.25177 | 0.17853 | 0.032043 | -0.17853 | -0.16937 | 0.29755 | 0.27924 | 0.39368 | 0.24719 | 0.36163 | 1.0757 | 121.5225 | 0.2655 | 121.4127 | 121.3806 | 121.4035 | 121.4996 | 121.4355 | -121.4951 | -121.582 | 121.6415 | 121.4447 | 6.8893 | 3.0853
2018.4531 | 121.6553 | -0.37537 | 121.3074 | -0.0057221 | 6.2671 | 0.064322 | 0.06692 | 0.0039093 | -0.0014248 | 0.0019012 | -0.0059205 | 0.003967 | -1.395 | 0.062461 | -0.0051954 | 0.012117 | -0.0013031 | 6.4087 | 121.2112 | -0.26093 | 121.1929 | 0.71869 | -0.17853 | -0.07782 | 2.6001 | 121.138 | -0.29297 | 121.0281 | -0.19684 | -0.11444 | -0.15564 | 0.11444 | -0.09613 | -0.11444 | 1.0941 | 0.29755 | 0.19684 | 0.18311 | 0.082397 | 0.082397 | -0.16937 | -0.27924 | 0.17853 | 0.21973 | 0.26092 | 0.13733 | 0.17853 | 0.97961 | 121.4539 | 0.096131 | 121.3211 | 121.4722 | 121.431 | 121.5866 | 121.5134 | -121.5683 | -121.6003 | 121.5683 | 121.4035 | 6.7841 | 2.9755
2020.2344 | 121.6324 | -0.37994 | 121.3074 | 0.0019074 | 6.4375 | 0.066458 | 0.069483 | 0.00091851 | -0.0012112 | 0.00040597 | -0.0059205 | 0.0048214 | -1.3944 | 0.063957 | -0.0028454 | 0.010835 | 0.0014741 | 6.3583 | 121.2204 | -0.25177 | 121.2112 | 0.72784 | -0.17853 | -0.064087 | 2.5543 | 121.1655 | -0.31586 | 120.9824 | -0.2243 | -0.14648 | -0.16479 | 0.12817 | -0.086975 | -0.09613 | 1.1078 | 0.31586 | 0.20142 | 0.18768 | 0.073242 | 0.064087 | -0.14191 | -0.32501 | 0.15564 | 0.21515 | 0.23346 | 0.15106 | 0.16937 | 0.97961 | 121.463 | 0.091553 | 121.2982 | 121.4722 | 121.4813 | 121.6003 | 121.5454 | -121.5591 | -121.6232 | 121.5912 | 121.3623 | 6.7383 | 2.9343
2021.9375 | 121.7194 | -0.33875 | 121.3303 | 0.032425 | 6.2912 | 0.066458 | 0.067774 | -0.0031403 | -0.00035684 | -0.00087583 | 0.0062865 | 0.00097624 | -1.3965 | 0.06887 | -0.0017774 | 0.012758 | -0.00044851 | 6.3309 | 121.1929 | -0.23804 | 121.2891 | 0.83313 | -0.064087 | 0.041199 | 2.6688 | 121.1517 | -0.28839 | 121.0831 | -0.10529 | -0.009155 | -0.11444 | 0.10071 | -0.13733 | -0.041199 | 1.1719 | 0.37994 | 0.27466 | 0.27924 | 0.17395 | 0.050354 | -0.17853 | -0.24719 | 0.23346 | 0.2243 | 0.32959 | 0.17395 | 0.27924 | 1.0712 | 121.5271 | 0.18311 | 121.3715 | 121.431 | 121.4401 | 121.5317 | 121.4905 | -121.5683 | -121.6187 | 121.6278 | 121.4218 | 6.6696 | 3.0075
2023.7188 | 121.7743 | -0.32501 | 121.3303 | -0.0057221 | 6.276 | 0.064963 | 0.065424 | -0.0022857 | -0.004202 | -0.001944 | 0.00018312 | 0.0028988 | -1.3969 | 0.067802 | -0.0051954 | 0.010408 | 0.00040589 | 6.3126 | 121.138 | -0.21057 | 121.3623 | 0.9613 | 0.018311 | 0.10071 | 2.7695 | 121.1243 | -0.2655 | 121.1243 | -0.018311 | 0.07782 | -0.059509 | 0.11444 | -0.19226 | 0.032044 | 1.2863 | 0.42572 | 0.34332 | 0.31128 | 0.22888 | 0.059509 | -0.20599 | -0.20599 | 0.3067 | 0.2655 | 0.40283 | 0.20599 | 0.34332 | 1.1719 | 121.5729 | 0.24719 | 121.3898 | 121.3486 | 121.3898 | 121.463 | 121.4493 | -121.5408 | -121.5958 | 121.6873 | 121.4493 | 6.6376 | 3.0945
2025.4844 | 121.788 | -0.32501 | 121.2845 | 0.0095369 | 6.3115 | 0.06539 | 0.068629 | 0.00027771 | -0.0031338 | 0.0012604 | -0.0059205 | 0.003967 | -1.3955 | 0.068015 | -0.0041272 | 0.011903 | 0.00083309 | 6.1935 | 121.1472 | -0.21057 | 121.344 | 0.92926 | 0.009155 | 0.10529 | 2.7512 | 121.106 | -0.25635 | 121.1197 | -0.032043 | 0.064087 | -0.050354 | 0.11444 | -0.13733 | 0.059509 | 1.2543 | 0.4303 | 0.33417 | 0.31586 | 0.21973 | 0.068664 | -0.17853 | -0.16479 | 0.29297 | 0.27466 | 0.3891 | 0.20599 | 0.32044 | 1.1398 | 121.5546 | 0.22431 | 121.376 | 121.3577 | 121.3623 | 121.4722 | 121.431 | -121.4951 | -121.5408 | 121.669 | 121.4447 | 6.5186 | 3.0762
2027.2812 | 121.7331 | -0.34332 | 121.3074 | -0.0057221 | 6.2769 | 0.062613 | 0.065851 | -0.0027131 | -0.0029202 | 0.003183 | -0.0028687 | 0.0052486 | -1.3946 | 0.069938 | -0.001991 | 0.012758 | 0.0014741 | 6.0699 | 121.2204 | -0.24261 | 121.2341 | 0.79651 | -0.13733 | -0.013733 | 2.623 | 121.1334 | -0.32044 | 121.0831 | -0.11444 | -0.013733 | -0.086975 | 0.10071 | -0.086975 | -0.073242 | 1.1398 | 0.32959 | 0.20599 | 0.22888 | 0.10529 | 0.022888 | -0.17395 | -0.2243 | 0.22888 | 0.25635 | 0.32959 | 0.23346 | 0.3067 | 1.0391 | 121.4767 | 0.20599 | 121.4035 | 121.463 | 121.4539 | 121.5637 | 121.4767 | -121.55 | -121.6278 | 121.5775 | 121.4264 | 6.4133 | 2.9663
2028.9844 | 121.7789 | -0.3479 | 121.2799 | 0.0095369 | 6.2619 | 0.065176 | 0.066706 | -0.0029267 | -0.0012112 | 0.0023286 | -0.0028687 | 0.0026852 | -1.3942 | 0.065238 | -0.0058362 | 0.012544 | -0.0030121 | 6.0333 | 121.1655 | -0.23346 | 121.2753 | 0.82855 | -0.041199 | 0.07782 | 2.6642 | 121.1151 | -0.30212 | 121.0739 | -0.068665 | 0.032043 | -0.073242 | 0.11444 | -0.11444 | -0.004577 | 1.1765 | 0.42572 | 0.3067 | 0.31128 | 0.19226 | 0.045776 | -0.16479 | -0.20599 | 0.27924 | 0.27466 | 0.37994 | 0.22888 | 0.33417 | 1.062 | 121.5088 | 0.23346 | 121.376 | 121.3989 | 121.4172 | 121.5134 | 121.463 | -121.5134 | -121.582 | 121.6232 | 121.4218 | 6.3812 | 3.0121
2030.7656 | 121.6415 | -0.40283 | 121.3257 | -0.0057221 | 6.2553 | 0.063895 | 0.068415 | -0.0035675 | -0.00527 | 0.0029694 | 0.027649 | 0.0073848 | -1.3933 | 0.061179 | -0.0066906 | 0.011476 | -0.0013031 | 5.9143 | 121.1563 | -0.27924 | 121.2112 | 0.75989 | -0.13275 | -0.009155 | 2.5909 | 121.2112 | -0.36621 | 120.9641 | -0.17853 | -0.07782 | -0.17395 | 0.1236 | -0.16937 | -0.11444 | 1.1627 | 0.39368 | 0.27008 | 0.27008 | 0.14648 | 0.036621 | -0.11444 | -0.36163 | 0.2243 | 0.22888 | 0.32501 | 0.19226 | 0.28839 | 1.0391 | 121.4905 | 0.18768 | 121.3303 | 121.4355 | 121.5775 | 121.5591 | 121.6141 | -121.6049 | -121.6919 | 121.6141 | 121.3669 | 6.3171 | 2.9938
2032.4844 | 121.7651 | -0.33875 | 121.2753 | 0.0019074 | 6.2639 | 0.064749 | 0.066492 | -0.0020721 | -0.0044156 | 0.0042512 | -0.0028687 | 0.002258 | -1.3974 | 0.063957 | -0.0073316 | 0.011903 | -0.0015167 | 5.9189 | 121.1517 | -0.23346 | 121.3348 | 0.92468 | 0.009155 | 0.1236 | 2.7145 | 121.0968 | -0.29755 | 121.106 | -0.032043 | 0.073242 | -0.073242 | 0.10529 | -0.1236 | 0.059509 | 1.2634 | 0.46234 | 0.3479 | 0.35706 | 0.24261 | 0.041199 | -0.17853 | -0.16937 | 0.3067 | 0.2655 | 0.41199 | 0.2243 | 0.37079 | 1.1581 | 121.5683 | 0.2655 | 121.4035 | 121.3852 | 121.3943 | 121.4905 | 121.4355 | -121.5088 | -121.5729 | 121.6736 | 121.4447 | 6.2576 | 3.0533
2034.2656 | 121.6965 | -0.39825 | 121.3165 | 0.040054 | 6.388 | 0.066458 | 0.07226 | -0.0020721 | -0.001852 | 0.0033966 | 0.01239 | 0.0058896 | -1.3959 | 0.053062 | -0.0049818 | 0.010835 | -0.00023491 | 5.8411 | 121.2067 | -0.31128 | 121.2158 | 0.76904 | -0.086975 | 0.041199 | 2.5635 | 121.1563 | -0.38452 | 120.9961 | -0.16937 | -0.064087 | -0.15106 | 0.086975 | -0.10986 | -0.10071 | 1.1673 | 0.43945 | 0.31128 | 0.35248 | 0.2243 | 0.013733 | -0.16022 | -0.32043 | 0.22888 | 0.24719 | 0.33417 | 0.23346 | 0.32043 | 1.0803 | 121.5271 | 0.21515 | 121.3806 | 121.5179 | 121.5408 | 121.6049 | 121.5546 | -121.6278 | -121.701 | 121.6141 | 121.3943 | 6.2393 | 2.9617
2036.0469 | 121.6324 | -0.43488 | 121.312 | -0.0057221 | 6.401 | 0.066672 | 0.072687 | 0.0032685 | -0.00078404 | 0.0029694 | 0.00018312 | 0.0035396 | -1.3927 | 0.061393 | -0.0032728 | 0.012758 | 0.0025421 | 5.6992 | 121.1792 | -0.28839 | 121.1929 | 0.75073 | -0.17853 | -0.027466 | 2.4994 | 121.1334 | -0.33417 | 120.9686 | -0.2243 | -0.11902 | -0.19226 | 0.14648 | -0.13275 | -0.11902 | 1.1856 | 0.40741 | 0.25635 | 0.26093 | 0.10986 | 0.10071 | -0.17853 | -0.34332 | 0.21057 | 0.24261 | 0.31586 | 0.14191 | 0.21515 | 1.0391 | 121.4813 | 0.10986 | 121.3028 | 121.4676 | 121.4676 | 121.6141 | 121.5683 | -121.6003 | -121.6461 | 121.6278 | 121.4035 | 6.134 | 2.9343
2037.8281 | 121.7148 | -0.41199 | 121.2433 | 0.0019074 | 6.3517 | 0.06304 | 0.067133 | -0.0016449 | -0.001852 | -0.0025848 | -0.0028687 | 0.0018306 | -1.3952 | 0.071647 | -0.0073316 | 0.012971 | 0.0010467 | 5.6534 | 121.1151 | -0.27008 | 121.2479 | 0.86517 | -0.045776 | 0.09613 | 2.6276 | 121.0739 | -0.35248 | 121.0007 | -0.12817 | -0.009155 | -0.15106 | 0.14191 | -0.12817 | 0.004578 | 1.2772 | 0.50812 | 0.36621 | 0.36621 | 0.22431 | 0.059509 | -0.16937 | -0.24262 | 0.28381 | 0.26092 | 0.40283 | 0.20142 | 0.34332 | 1.1353 | 121.5179 | 0.2243 | 121.3531 | 121.3852 | 121.4264 | 121.5271 | 121.4859 | -121.5134 | -121.5958 | 121.6599 | 121.4127 | 6.0654 | 3.0395
2039.5312 | 121.7285 | -0.3891 | 121.2753 | 0.017166 | 6.3728 | 0.065817 | 0.06756 | 0.0049773 | -0.0016384 | 0.0027558 | 0.0032349 | 0.0020444 | -1.3959 | 0.066093 | -0.0037 | 0.012544 | -0.0025849 | 5.5618 | 121.17 | -0.24261 | 121.2708 | 0.83771 | -0.07782 | 0.10986 | 2.5864 | 121.0739 | -0.32501 | 121.0236 | -0.1236 | -0.004578 | -0.11902 | 0.14648 | -0.10529 | -0.004578 | 1.2268 | 0.49896 | 0.31128 | 0.35248 | 0.16479 | 0.064087 | -0.20142 | -0.25177 | 0.2655 | 0.27008 | 0.38452 | 0.20599 | 0.32043 | 1.0803 | 121.5134 | 0.20142 | 121.3486 | 121.4127 | 121.3989 | 121.5591 | 121.463 | -121.5179 | -121.6003 | 121.6599 | 121.4127 | 5.9509 | 2.9755
2041.2969 | 121.7331 | -0.31128 | 121.3028 | 0.024795 | 6.3745 | 0.066458 | 0.070765 | -0.0010041 | -0.00014304 | 0.00019217 | 0.01239 | 0.0026852 | -1.3965 | 0.065025 | -0.0024182 | 0.013398 | 0.00083309 | 5.5481 | 121.1975 | -0.23346 | 121.2982 | 0.89264 | -0.022888 | 0.16937 | 2.6093 | 121.1243 | -0.28381 | 121.0831 | -0.07782 | 0.041199 | -0.073242 | 0.07782 | -0.10529 | -0.004577 | 1.2039 | 0.48065 | 0.28839 | 0.40283 | 0.21057 | 0.027466 | -0.17853 | -0.21973 | 0.23346 | 0.23804 | 0.35248 | 0.21057 | 0.32501 | 1.1261 | 121.5317 | 0.20599 | 121.3669 | 121.431 | 121.4081 | 121.5088 | 121.4355 | -121.5363 | -121.5866 | 121.6095 | 121.3943 | 5.8594 | 2.9205
2043.0938 | 121.6507 | -0.37537 | 121.3577 | 0.047683 | 6.3743 | 0.066031 | 0.070551 | -0.00036309 | -0.003561 | 0.0027558 | 0.0093383 | 0.0054622 | -1.3952 | 0.062034 | -0.0062634 | 0.011476 | -0.0010895 | 5.452 | 121.2204 | -0.30212 | 121.2341 | 0.82855 | -0.068665 | 0.10071 | 2.5314 | 121.1746 | -0.33417 | 121.0007 | -0.16479 | -0.022888 | -0.13275 | 0.073242 | -0.13733 | -0.1236 | 1.2039 | 0.47607 | 0.3067 | 0.40283 | 0.23346 | 0.041199 | -0.1831 | -0.35706 | 0.21057 | 0.24261 | 0.35248 | 0.20142 | 0.31128 | 1.1307 | 121.5363 | 0.16937 | 121.3348 | 121.5225 | 121.5088 | 121.5958 | 121.55 | -121.6599 | -121.6919 | 121.6095 | 121.376 | 5.8273 | 2.9068
2044.8594 | 121.6553 | -0.37537 | 121.3348 | 0.0019074 | 6.3427 | 0.066458 | 0.069697 | -0.00014949 | -0.0050564 | -0.00087583 | 0.0032349 | 0.0041806 | -1.3957 | 0.057975 | -0.005409 | 0.01233 | -0.0013031 | 5.4016 | 121.1929 | -0.25177 | 121.2662 | 0.82855 | -0.11444 | 0.091553 | 2.5497 | 121.1334 | -0.31128 | 121.0281 | -0.16022 | -0.032043 | -0.13733 | 0.1236 | -0.14191 | -0.068665 | 1.2039 | 0.46692 | 0.26092 | 0.34332 | 0.13733 | 0.064087 | -0.20142 | -0.3067 | 0.21515 | 0.23804 | 0.34332 | 0.17395 | 0.27924 | 1.0803 | 121.5179 | 0.15106 | 121.3394 | 121.4447 | 121.4447 | 121.5683 | 121.5088 | -121.5866 | -121.6461 | 121.6415 | 121.4035 | 5.777 | 2.9251
2046.625 | 121.756 | -0.32501 | 121.3074 | 0.070572 | 6.2965 | 0.067954 | 0.070124 | 0.0017731 | 7.0564e-05 | 0.0033966 | 0.015442 | 0.0054622 | -1.3933 | 0.066306 | -0.0017774 | 0.012971 | 0.0027557 | 5.3558 | 121.2112 | -0.24719 | 121.3303 | 0.97961 | 0.013733 | 0.21057 | 2.6871 | 121.1243 | -0.3067 | 121.0968 | -0.050354 | 0.082397 | -0.050354 | 0.07782 | -0.09613 | 0.022888 | 1.3046 | 0.53558 | 0.33875 | 0.45776 | 0.26093 | 0.01831 | -0.1831 | -0.21057 | 0.27466 | 0.27466 | 0.40741 | 0.25635 | 0.3891 | 1.2268 | 121.5775 | 0.25635 | 121.4035 | 121.4584 | 121.431 | 121.5363 | 121.4493 | -121.5546 | -121.6141 | 121.6553 | 121.4218 | 5.6808 | 3.0121
2048.3438 | 121.6507 | -0.38452 | 121.3074 | -0.0057221 | 6.366 | 0.064963 | 0.066706 | 0.00027771 | -0.0020658 | 0.0055328 | -0.0028687 | 0.0031124 | -1.3937 | 0.060752 | -0.0069044 | 0.010408 | 0.0010467 | 5.2414 | 121.1563 | -0.21973 | 121.2524 | 0.87891 | -0.032043 | 0.15564 | 2.5452 | 121.1609 | -0.3067 | 121.0098 | -0.13733 | 0.004578 | -0.14648 | 0.16479 | -0.15106 | -0.054932 | 1.2634 | 0.54016 | 0.35248 | 0.37537 | 0.18768 | 0.077819 | -0.14648 | -0.29755 | 0.24719 | 0.23804 | 0.3891 | 0.16022 | 0.31128 | 1.0986 | 121.4722 | 0.16937 | 121.3165 | 121.376 | 121.4676 | 121.5408 | 121.5454 | -121.5271 | -121.6141 | 121.637 | 121.3943 | 5.6259 | 2.9297
2050.125 | 121.669 | -0.37994 | 121.312 | 0.0019074 | 6.3886 | 0.06539 | 0.070124 | 0.0045501 | -0.001852 | 0.0040376 | 0.00018312 | 0.0043942 | -1.3935 | 0.05648 | -0.004768 | 0.01233 | 0.0019013 | 5.2277 | 121.2021 | -0.27008 | 121.2479 | 0.87891 | -0.064087 | 0.13733 | 2.5543 | 121.1197 | -0.31586 | 121.0144 | -0.11444 | 0.009155 | -0.10529 | 0.10986 | -0.10986 | -0.064087 | 1.2589 | 0.51727 | 0.31586 | 0.40741 | 0.20599 | 0.064087 | -0.19226 | -0.29755 | 0.2655 | 0.27466 | 0.3891 | 0.21057 | 0.32501 | 1.149 | 121.5179 | 0.20142 | 121.3303 | 121.4722 | 121.4355 | 121.582 | 121.4996 | -121.582 | -121.6278 | 121.6278 | 121.3943 | 5.6076 | 2.9343
2051.9062 | 121.7468 | -0.37079 | 121.2982 | 0.0019074 | 6.4271 | 0.066885 | 0.071833 | 0.00070491 | -0.0020658 | 0.0012604 | -0.0059205 | 0.0035396 | -1.3944 | 0.061393 | -0.00028199 | 0.014039 | 0.0027557 | 5.1453 | 121.1838 | -0.27008 | 121.2158 | 0.84228 | -0.10529 | 0.13275 | 2.5497 | 121.0968 | -0.32044 | 121.0648 | -0.10529 | 0.050354 | -0.064087 | 0.10071 | -0.11444 | -0.082398 | 1.2131 | 0.50354 | 0.2655 | 0.40283 | 0.1648 | 0.050354 | -0.20142 | -0.23346 | 0.2655 | 0.3067 | 0.42114 | 0.25635 | 0.37079 | 1.1124 | 121.4859 | 0.21515 | 121.3852 | 121.4539 | 121.4172 | 121.5546 | 121.4676 | -121.5683 | -121.6187 | 121.5866 | 121.4355 | 5.5161 | 2.9205
2053.6875 | 121.701 | -0.40283 | 121.2479 | 0.0019074 | 6.4215 | 0.06539 | 0.070124 | -0.0012177 | -0.00014304 | 0.0036102 | -0.0028687 | 0.002258 | -1.3952 | 0.071861 | -0.0015638 | 0.012758 | -0.00087591 | 5.0491 | 121.1792 | -0.27924 | 121.1746 | 0.81482 | -0.13275 | 0.09613 | 2.4902 | 121.0831 | -0.32501 | 121.0144 | -0.15106 | -0.009155 | -0.1236 | 0.1236 | -0.068665 | -0.073242 | 1.2177 | 0.49896 | 0.27008 | 0.37537 | 0.14648 | 0.07782 | -0.1648 | -0.23346 | 0.25177 | 0.27924 | 0.39368 | 0.20142 | 0.31586 | 1.0941 | 121.4539 | 0.17395 | 121.3394 | 121.4584 | 121.4081 | 121.582 | 121.4859 | -121.5271 | -121.5729 | 121.5775 | 121.4172 | 5.452 | 2.8931
2055.4531 | 121.756 | -0.37537 | 121.2753 | -0.020981 | 6.5151 | 0.063254 | 0.068415 | 0.0034821 | -0.0033474 | 0.0016876 | 0.00018312 | -0.00030556 | -1.3959 | 0.062675 | -0.0058362 | 0.011262 | 0.0014741 | 5.0674 | 121.1197 | -0.24719 | 121.2799 | 0.94757 | 0.009155 | 0.23346 | 2.5955 | 121.0556 | -0.32044 | 121.0602 | -0.045776 | 0.10071 | -0.064087 | 0.12817 | -0.15564 | 0.004577 | 1.3229 | 0.60882 | 0.38452 | 0.48065 | 0.25635 | 0.054931 | -0.21973 | -0.21515 | 0.32959 | 0.31128 | 0.47607 | 0.25635 | 0.42114 | 1.1948 | 121.5271 | 0.27466 | 121.3806 | 121.3669 | 121.376 | 121.4951 | 121.431 | -121.5225 | -121.5958 | 121.6553 | 121.4355 | 5.4428 | 2.9709
2057.1719 | 121.7651 | -0.37994 | 121.2204 | 0.0019074 | 6.5255 | 0.065817 | 0.070978 | 0.0017731 | 0.00028416 | 0.0012604 | 0.0032349 | 0.0024716 | -1.3944 | 0.064597 | -0.0024182 | 0.012117 | 0.0010467 | 5.0537 | 121.1151 | -0.26093 | 121.2753 | 0.92926 | -0.032043 | 0.21515 | 2.5955 | 121.0464 | -0.29297 | 121.0922 | -0.068665 | 0.091553 | -0.054932 | 0.11902 | -0.10529 | 0.054932 | 1.3092 | 0.59509 | 0.3479 | 0.47607 | 0.22888 | 0.086975 | -0.17395 | -0.12817 | 0.31128 | 0.32501 | 0.4715 | 0.23804 | 0.38452 | 1.1902 | 121.5363 | 0.2243 | 121.3852 | 121.376 | 121.3394 | 121.4951 | 121.4264 | -121.4813 | -121.5134 | 121.6553 | 121.4722 | 5.4337 | 2.9755
2058.9375 | 121.6278 | -0.44861 | 121.2845 | -0.013352 | 6.5112 | 0.066458 | 0.068415 | 0.0056183 | -0.001852 | 0.0016876 | 0.00018312 | 0.0061032 | -1.3967 | 0.065666 | -0.007118 | 0.014039 | 0.0016877 | 4.9118 | 121.138 | -0.31128 | 121.1517 | 0.81024 | -0.15564 | 0.10529 | 2.4353 | 121.0785 | -0.35706 | 120.9274 | -0.22888 | -0.064087 | -0.1831 | 0.13733 | -0.14648 | -0.13275 | 1.2589 | 0.55389 | 0.29297 | 0.41656 | 0.15564 | 0.091552 | -0.20599 | -0.35706 | 0.21973 | 0.2655 | 0.38452 | 0.17395 | 0.29297 | 1.1215 | 121.463 | 0.12817 | 121.2845 | 121.4493 | 121.4355 | 121.5866 | 121.5271 | -121.5958 | -121.6415 | 121.6003 | 121.376 | 5.3604 | 2.8839
2060.6406 | 121.6736 | -0.4715 | 121.2479 | 0.0019074 | 6.5166 | 0.065604 | 0.072046 | -0.00057689 | -0.0027066 | 0.0038238 | -0.0059205 | 0.0018306 | -1.3948 | 0.068443 | -0.0041272 | 0.012544 | 0.00061949 | 4.8111 | 121.0922 | -0.34332 | 121.1014 | 0.76446 | -0.19226 | 0.07782 | 2.4124 | 121.0602 | -0.39825 | 120.9229 | -0.21973 | -0.073242 | -0.19684 | 0.12817 | -0.15564 | -0.14649 | 1.236 | 0.54932 | 0.27924 | 0.42114 | 0.15106 | 0.073243 | -0.18768 | -0.32501 | 0.25177 | 0.27466 | 0.39826 | 0.20142 | 0.32501 | 1.1078 | 121.4447 | 0.17853 | 121.3211 | 121.4355 | 121.4584 | 121.5637 | 121.5317 | -121.5912 | -121.6461 | 121.5729 | 121.3943 | 5.2826 | 2.8839
2062.4062 | 121.6324 | -0.4715 | 121.2296 | -0.0057221 | 6.5292 | 0.064536 | 0.069697 | 0.00091851 | -0.0020658 | 0.0044648 | -0.0089723 | 0.0026852 | -1.395 | 0.063316 | -0.0043408 | 0.012971 | -0.0015167 | 4.747 | 121.1288 | -0.3479 | 121.0739 | 0.75531 | -0.19226 | 0.068665 | 2.3849 | 121.0556 | -0.39825 | 120.9 | -0.25635 | -0.09613 | -0.20142 | 0.1236 | -0.10071 | -0.15564 | 1.2268 | 0.54016 | 0.27924 | 0.41656 | 0.15564 | 0.073243 | -0.17395 | -0.32959 | 0.21515 | 0.27008 | 0.37537 | 0.19684 | 0.30212 | 1.1032 | 121.4218 | 0.14191 | 121.2982 | 121.4767 | 121.4539 | 121.6003 | 121.5271 | -121.5775 | -121.6278 | 121.5454 | 121.3715 | 5.2185 | 2.8564
2064.125 | 121.7697 | -0.42572 | 121.1838 | -0.0057221 | 6.5247 | 0.066245 | 0.070338 | -0.0044221 | -0.0022794 | 0.0061738 | 0.024597 | 0.0046078 | -1.3944 | 0.070152 | -0.0017774 | 0.01233 | -0.00044851 | 4.8065 | 121.0922 | -0.28839 | 121.2708 | 0.97961 | -0.022888 | 0.26093 | 2.5909 | 121.0464 | -0.39368 | 121.0373 | -0.10529 | 0.068665 | -0.09613 | 0.13733 | -0.091553 | 0.086975 | 1.4053 | 0.68664 | 0.40283 | 0.54932 | 0.2655 | 0.032043 | -0.13733 | -0.14649 | 0.32043 | 0.32959 | 0.49438 | 0.29755 | 0.46234 | 1.268 | 121.5591 | 0.28839 | 121.431 | 121.3806 | 121.4401 | 121.5179 | 121.4722 | -121.4722 | -121.5775 | 121.6965 | 121.463 | 5.2322 | 3.0167
2065.9062 | 121.7468 | -0.4303 | 121.1975 | 0.0019074 | 6.5273 | 0.063895 | 0.070978 | -0.0037811 | -0.002493 | 0.003183 | -0.0028687 | 0.00033544 | -1.3965 | 0.067375 | -0.0034864 | 0.012758 | 0.0038239 | 4.7104 | 121.1014 | -0.3067 | 121.1792 | 0.89264 | -0.068665 | 0.21973 | 2.4719 | 121.0098 | -0.37537 | 120.9915 | -0.11902 | 0.07782 | -0.11444 | 0.1236 | -0.096131 | -0.018311 | 1.3229 | 0.65003 | 0.36163 | 0.52643 | 0.23804 | 0.054932 | -0.18768 | -0.20599 | 0.31128 | 0.31586 | 0.50812 | 0.26092 | 0.45319 | 1.1993 | 121.4859 | 0.25635 | 121.3669 | 121.4081 | 121.3852 | 121.5317 | 121.4401 | -121.5042 | -121.5729 | 121.6095 | 121.4218 | 5.1407 | 2.9022
2067.6875 | 121.6599 | -0.4303 | 121.2112 | 0.0095369 | 6.5403 | 0.064536 | 0.07226 | -0.0018585 | -0.0014248 | 0.0025422 | 0.0062865 | 0.0065304 | -1.3931 | 0.052635 | -0.005409 | 0.010621 | 0.00040589 | 4.6921 | 121.1151 | -0.33875 | 121.1792 | 0.87433 | -0.10071 | 0.18768 | 2.4673 | 121.0327 | -0.3891 | 120.9366 | -0.18768 | -0.036621 | -0.16479 | 0.091553 | -0.096131 | -0.032044 | 1.3046 | 0.61798 | 0.32959 | 0.52643 | 0.23804 | 0.041199 | -0.17853 | -0.27466 | 0.24262 | 0.2655 | 0.39368 | 0.2243 | 0.35248 | 1.2131 | 121.5179 | 0.20142 | 121.3257 | 121.4539 | 121.4218 | 121.5454 | 121.463 | -121.55 | -121.6003 | 121.6095 | 121.3669 | 5.1224 | 2.8976
2069.4531 | 121.7468 | -0.4303 | 121.1792 | -0.0057221 | 6.5625 | 0.06539 | 0.068842 | -0.00036309 | 0.00028416 | 0.00040597 | -0.0089723 | 0.0018306 | -1.3976 | 0.057334 | -0.0056226 | 0.012758 | 0.0012603 | 4.6051 | 121.0876 | -0.31128 | 121.17 | 0.9201 | -0.041199 | 0.23346 | 2.4948 | 121.0236 | -0.38452 | 121.0098 | -0.10071 | 0.10071 | -0.10986 | 0.11902 | -0.091553 | -0.009155 | 1.3504 | 0.66376 | 0.3891 | 0.54474 | 0.27008 | 0.045777 | -0.15564 | -0.16937 | 0.32959 | 0.32044 | 0.53101 | 0.27466 | 0.48523 | 1.2314 | 121.4813 | 0.28381 | 121.3943 | 121.3989 | 121.4081 | 121.5179 | 121.4539 | -121.4905 | -121.5637 | 121.6003 | 121.4401 | 5.0354 | 2.9251
2071.2344 | 121.7697 | -0.43488 | 121.1746 | -0.0057221 | 6.5048 | 0.063895 | 0.067133 | -0.0020721 | -0.0029202 | -0.00023503 | -0.0059205 | 0.0026852 | -1.3963 | 0.060752 | -0.0051954 | 0.012117 | -0.00087591 | 4.5547 | 121.0556 | -0.31586 | 121.1975 | 0.95215 | -0.041199 | 0.27466 | 2.5085 | 121.0236 | -0.36163 | 120.9961 | -0.073242 | 0.10071 | -0.091553 | 0.11902 | -0.11902 | 0.022888 | 1.387 | 0.70953 | 0.39368 | 0.59052 | 0.27466 | 0.073242 | -0.15106 | -0.17853 | 0.36163 | 0.34332 | 0.53558 | 0.27008 | 0.46234 | 1.268 | 121.5134 | 0.28839 | 121.3577 | 121.3715 | 121.3852 | 121.4905 | 121.4584 | -121.4905 | -121.5363 | 121.6324 | 121.431 | 4.9896 | 2.9434
2072.9375 | 121.6827 | -0.46692 | 121.2021 | 0.017166 | 6.4796 | 0.066458 | 0.06991 | 0.0019867 | -0.00035684 | 0.0019012 | 0.0062865 | 0.0052486 | -1.3952 | 0.057548 | -0.0045544 | 0.010194 | -0.0025849 | 4.5319 | 121.0876 | -0.37079 | 121.1655 | 0.90637 | -0.086975 | 0.22888 | 2.4719 | 121.0327 | -0.39825 | 120.9503 | -0.15564 | 0.009155 | -0.13733 | 0.09613 | -0.11444 | -0.036621 | 1.3733 | 0.6958 | 0.37994 | 0.59967 | 0.28381 | 0.068665 | -0.16937 | -0.25177 | 0.31128 | 0.32959 | 0.47607 | 0.26092 | 0.40741 | 1.2772 | 121.5363 | 0.24261 | 121.3486 | 121.4584 | 121.431 | 121.5546 | 121.4996 | -121.5729 | -121.6003 | 121.6324 | 121.4172 | 4.9988 | 2.9388
2074.7188 | 121.6324 | -0.46692 | 121.2296 | 0.0019074 | 6.5302 | 0.067313 | 0.072046 | 0.0013459 | 0.00071136 | 0.0044648 | -0.0028687 | 0.0073848 | -1.3948 | 0.065666 | -0.0045544 | 0.012117 | 0.0010467 | 4.4449 | 121.0922 | -0.33875 | 121.0968 | 0.83313 | -0.16479 | 0.17395 | 2.3849 | 121.0281 | -0.40283 | 120.8771 | -0.23804 | -0.064087 | -0.21515 | 0.12817 | -0.13733 | -0.13275 | 1.3 | 0.64087 | 0.30212 | 0.5127 | 0.17395 | 0.064087 | -0.20142 | -0.35248 | 0.22888 | 0.25177 | 0.40283 | 0.18768 | 0.33875 | 1.1719 | 121.4355 | 0.1648 | 121.2799 | 121.431 | 121.431 | 121.5591 | 121.4951 | -121.5683 | -121.6324 | 121.5637 | 121.344 | 4.9118 | 2.8519
2076.4844 | 121.7972 | -0.43488 | 121.1929 | -0.020981 | 6.5146 | 0.064108 | 0.070338 | -0.0014313 | -0.001852 | 0.0044648 | -0.0059205 | 0.00076264 | -1.3955 | 0.068015 | -0.004768 | 0.011476 | 0.0025421 | 4.4449 | 121.0373 | -0.31586 | 121.2021 | 0.98877 | 0 | 0.33417 | 2.5497 | 120.9824 | -0.38452 | 121.0144 | -0.059509 | 0.14191 | -0.086975 | 0.11902 | -0.15564 | 0.009155 | 1.4236 | 0.76904 | 0.43488 | 0.65002 | 0.31586 | 0.050354 | -0.21057 | -0.17853 | 0.37537 | 0.3479 | 0.57678 | 0.29755 | 0.52643 | 1.3046 | 121.5179 | 0.32501 | 121.3989 | 121.3531 | 121.3669 | 121.4722 | 121.4172 | -121.5088 | -121.5775 | 121.637 | 121.4493 | 4.8798 | 2.9846
2078.2812 | 121.6782 | -0.4715 | 121.2296 | 0.055313 | 6.5426 | 0.066458 | 0.071833 | -0.0020721 | -0.0029202 | 0.0053192 | 0.018494 | 0.0046078 | -1.3933 | 0.064597 | -0.004768 | 0.011049 | -0.0010895 | 4.3762 | 121.1014 | -0.38452 | 121.1288 | 0.85602 | -0.091553 | 0.24261 | 2.4124 | 121.0464 | -0.44403 | 120.9045 | -0.19226 | -0.004578 | -0.17853 | 0.086976 | -0.12817 | -0.10071 | 1.3275 | 0.71411 | 0.37994 | 0.62714 | 0.29297 | 0.027466 | -0.1831 | -0.32501 | 0.27924 | 0.29297 | 0.46692 | 0.2655 | 0.43945 | 1.2405 | 121.5134 | 0.25177 | 121.3486 | 121.4859 | 121.4905 | 121.5729 | 121.5179 | -121.6141 | -121.6736 | 121.6003 | 121.376 | 4.8477 | 2.8839
2079.9844 | 121.7148 | -0.43488 | 121.2021 | -0.013352 | 6.501 | 0.066245 | 0.068629 | 0.0019867 | -0.0016384 | 0.0027558 | -0.0028687 | 0.0020444 | -1.3961 | 0.066093 | -0.0045544 | 0.012544 | 0.0025421 | 4.3533 | 121.0419 | -0.30212 | 121.2158 | 0.98877 | 0.004578 | 0.37537 | 2.5269 | 121.0007 | -0.36621 | 120.9732 | -0.082397 | 0.10986 | -0.11444 | 0.13275 | -0.16022 | 0.013733 | 1.4236 | 0.81024 | 0.43945 | 0.67749 | 0.3067 | 0.068664 | -0.20142 | -0.22888 | 0.35248 | 0.32043 | 0.54474 | 0.25177 | 0.47607 | 1.2909 | 121.5179 | 0.28381 | 121.3394 | 121.344 | 121.3669 | 121.4767 | 121.4355 | -121.5042 | -121.5683 | 121.6507 | 121.4081 | 4.7882 | 2.9617
2081.7656 | 121.6919 | -0.45776 | 121.2158 | 0.047683 | 6.4268 | 0.06539 | 0.073542 | -0.00079049 | -0.0020658 | 0.003183 | 0.0093383 | 0.005676 | -1.3942 | 0.060325 | -0.005409 | 0.010835 | 0.00019229 | 4.3167 | 121.1151 | -0.37079 | 121.17 | 0.84686 | -0.068665 | 0.31128 | 2.4857 | 121.0281 | -0.39825 | 120.9183 | -0.16479 | 0.050354 | -0.15106 | 0.086975 | -0.10071 | -0.045776 | 1.3046 | 0.76904 | 0.3891 | 0.68207 | 0.30212 | 0.05951 | -0.18768 | -0.29755 | 0.29297 | 0.3067 | 0.50812 | 0.24719 | 0.44861 | 1.2177 | 121.5408 | 0.23346 | 121.3165 | 121.4859 | 121.4264 | 121.5729 | 121.4859 | -121.5866 | -121.6141 | 121.6278 | 121.376 | 4.7745 | 2.9434
2083.5469 | 121.7239 | -0.43488 | 121.1746 | 0.0019074 | 6.4516 | 0.063681 | 0.06991 | 0.0013459 | -0.0037746 | 0.0051056 | -0.0028687 | 0.0037532 | -1.3972 | 0.065666 | -0.0024182 | 0.012117 | 0.00061949 | 4.2343 | 121.0602 | -0.34332 | 121.1197 | 0.84228 | -0.10071 | 0.28381 | 2.4719 | 120.9915 | -0.39368 | 120.9732 | -0.12817 | 0.073242 | -0.10986 | 0.091552 | -0.11444 | -0.054932 | 1.2772 | 0.71869 | 0.33417 | 0.62714 | 0.24261 | 0.041198 | -0.18311 | -0.20142 | 0.3067 | 0.32501 | 0.50812 | 0.28381 | 0.46692 | 1.1856 | 121.463 | 0.2655 | 121.3669 | 121.4035 | 121.3852 | 121.4951 | 121.4264 | -121.5179 | -121.5683 | 121.5546 | 121.4081 | 4.6692 | 2.9068
2085.25 | 121.6553 | -0.46234 | 121.1792 | -0.0057221 | 6.438 | 0.062399 | 0.070551 | -0.00014949 | -0.0014248 | 0.0046784 | 0.0032349 | 0.0035396 | -1.3944 | 0.072715 | -0.0013502 | 0.011689 | 0.0025421 | 4.2206 | 121.106 | -0.34332 | 121.0648 | 0.79651 | -0.15106 | 0.27008 | 2.4124 | 121.0464 | -0.41657 | 120.9137 | -0.21973 | 0.022888 | -0.17395 | 0.11902 | -0.073242 | -0.11444 | 1.2589 | 0.73242 | 0.31128 | 0.6134 | 0.19226 | 0.045776 | -0.13275 | -0.2655 | 0.24261 | 0.28839 | 0.48523 | 0.24262 | 0.43945 | 1.1398 | 121.4081 | 0.19684 | 121.3303 | 121.4493 | 121.463 | 121.5683 | 121.5088 | -121.5225 | -121.5958 | 121.5271 | 121.376 | 4.6829 | 2.8748
2087.0312 | 121.7422 | -0.4303 | 121.1517 | 0.055313 | 6.485 | 0.06774 | 0.071619 | 0.00027771 | 0.0022068 | 0.0061738 | 0.01239 | 0.005035 | -1.3931 | 0.064384 | -0.0039136 | 0.01233 | 0.0014741 | 4.3488 | 121.0922 | -0.34332 | 121.225 | 0.97961 | 0.013733 | 0.40741 | 2.6047 | 120.9961 | -0.42114 | 120.9824 | -0.091553 | 0.13733 | -0.086975 | 0.086975 | -0.059509 | 0.073243 | 1.4099 | 0.83771 | 0.44403 | 0.75073 | 0.35706 | 0.009155 | -0.15564 | -0.16937 | 0.33875 | 0.34332 | 0.56763 | 0.33417 | 0.55847 | 1.3229 | 121.5683 | 0.32959 | 121.4035 | 121.4355 | 121.4172 | 121.5225 | 121.4264 | -121.4951 | -121.5729 | 121.6553 | 121.4127 | 4.7791 | 3.035
2088.7969 | 121.7422 | -0.43488 | 121.17 | -0.0057221 | 6.4775 | 0.060904 | 0.067774 | -0.0018585 | -0.004202 | 0.0029694 | -0.0089723 | 0.002258 | -1.3925 | 0.063102 | -0.0034864 | 0.013612 | 0.0040375 | 4.2847 | 121.0144 | -0.34332 | 121.1929 | 0.96588 | 0.009155 | 0.4303 | 2.5818 | 120.9641 | -0.39825 | 120.9778 | -0.059509 | 0.16022 | -0.10986 | 0.091552 | -0.15564 | 0.022888 | 1.4008 | 0.86517 | 0.44403 | 0.77362 | 0.35248 | 0.036621 | -0.20599 | -0.19226 | 0.37537 | 0.32501 | 0.59509 | 0.28839 | 0.55847 | 1.3092 | 121.5363 | 0.33875 | 121.376 | 121.3577 | 121.3623 | 121.4493 | 121.3989 | -121.5134 | -121.5683 | 121.6278 | 121.4127 | 4.7195 | 3.0167
2090.5 | 121.756 | -0.45776 | 121.1884 | 0.0095369 | 6.532 | 0.066031 | 0.071192 | 0.0013459 | -0.00057044 | 0.0027558 | 0.00018312 | 0.0041806 | -1.3972 | 0.06417 | -0.001991 | 0.014039 | 0.0023285 | 4.2389 | 121.0556 | -0.33875 | 121.1472 | 0.88806 | -0.07782 | 0.37079 | 2.5131 | 120.9824 | -0.3891 | 120.9457 | -0.1236 | 0.13733 | -0.091553 | 0.11902 | -0.13275 | -0.041198 | 1.3458 | 0.82855 | 0.37994 | 0.70953 | 0.26093 | 0.068665 | -0.20599 | -0.24261 | 0.33417 | 0.36621 | 0.59509 | 0.29755 | 0.52643 | 1.2268 | 121.4859 | 0.2655 | 121.3348 | 121.3943 | 121.3715 | 121.5134 | 121.4401 | -121.5271 | -121.5775 | 121.6049 | 121.4035 | 4.6967 | 2.9709
2092.2812 | 121.7606 | -0.42572 | 121.17 | -0.0057221 | 6.4657 | 0.064108 | 0.072046 | -0.0031403 | -0.0014248 | -2.1434e-05 | -0.0028687 | 0.0028988 | -1.3974 | 0.060752 | -0.0069044 | 0.012117 | 0.0014741 | 4.3121 | 121.0373 | -0.31128 | 121.2158 | 1.0208 | 0.041199 | 0.46692 | 2.6093 | 120.9732 | -0.36163 | 120.9869 | -0.032043 | 0.20599 | -0.086975 | 0.11444 | -0.13275 | 0.045776 | 1.4465 | 0.89264 | 0.46692 | 0.7782 | 0.35248 | 0.064087 | -0.19684 | -0.18311 | 0.39368 | 0.33874 | 0.63171 | 0.27466 | 0.56763 | 1.3321 | 121.5271 | 0.32959 | 121.3486 | 121.3486 | 121.3348 | 121.463 | 121.3989 | -121.4813 | -121.5317 | 121.6415 | 121.4127 | 4.7379 | 3.035
2094.0625 | 121.6415 | -0.46234 | 121.1929 | 0.024795 | 6.4888 | 0.064963 | 0.073115 | 0.0028411 | 0.00028416 | 0.0044648 | 0.00018312 | 0.0054622 | -1.3922 | 0.05648 | -0.0069044 | 0.013612 | -0.0013031 | 4.2664 | 121.0785 | -0.33875 | 121.138 | 0.91095 | -0.073242 | 0.37537 | 2.5131 | 121.0236 | -0.40283 | 120.9091 | -0.16022 | 0.064087 | -0.14648 | 0.1236 | -0.11444 | -0.054932 | 1.3733 | 0.83771 | 0.3891 | 0.71411 | 0.2655 | 0.059509 | -0.16937 | -0.28381 | 0.30212 | 0.31586 | 0.52643 | 0.25635 | 0.46692 | 1.2497 | 121.4767 | 0.24262 | 121.312 | 121.4172 | 121.4264 | 121.5408 | 121.4859 | -121.5317 | -121.5958 | 121.6003 | 121.3715 | 4.7287 | 2.9755
2095.8438 | 121.7056 | -0.45319 | 121.1563 | 0.024795 | 6.4651 | 0.066031 | 0.073755 | 0.0024139 | 0.0015658 | 0.0042512 | 0.01239 | 0.0043942 | -1.3946 | 0.069084 | -0.0039136 | 0.013612 | -0.0027985 | 4.2572 | 121.0464 | -0.33417 | 121.1929 | 1.0071 | -0.009155 | 0.4715 | 2.6184 | 121.019 | -0.42114 | 120.9549 | -0.12817 | 0.16479 | -0.10986 | 0.11902 | -0.10986 | 0.036621 | 1.4603 | 0.92468 | 0.44403 | 0.80566 | 0.32501 | 0.032043 | -0.13733 | -0.20142 | 0.32501 | 0.34332 | 0.61798 | 0.31128 | 0.58594 | 1.3412 | 121.5271 | 0.29297 | 121.376 | 121.3806 | 121.4401 | 121.4996 | 121.4722 | -121.4905 | -121.5775 | 121.6461 | 121.4081 | 4.7104 | 3.0716
2097.5469 | 121.6324 | -0.50354 | 121.2021 | -0.020981 | 6.4546 | 0.066245 | 0.07461 | 0.00049131 | -0.00099764 | 0.0040376 | 0.00018312 | 0.0037532 | -1.3967 | 0.06417 | -0.0092542 | 0.010621 | -0.0013031 | 4.1565 | 121.0693 | -0.37079 | 121.0785 | 0.88348 | -0.10529 | 0.37994 | 2.4536 | 121.0007 | -0.42114 | 120.8542 | -0.19684 | 0.068665 | -0.19684 | 0.13275 | -0.13275 | -0.1236 | 1.387 | 0.88348 | 0.39825 | 0.75073 | 0.2655 | 0.082397 | -0.20142 | -0.3479 | 0.3067 | 0.3067 | 0.5722 | 0.2243 | 0.48981 | 1.2543 | 121.4493 | 0.2243 | 121.2753 | 121.4401 | 121.4218 | 121.5729 | 121.5042 | -121.5729 | -121.6232 | 121.582 | 121.3577 | 4.66 | 2.9572
2099.3281 | 121.6141 | -0.50812 | 121.1929 | -0.020981 | 6.4589 | 0.062186 | 0.072474 | 0.0017731 | -0.002493 | 0.0038238 | -0.0059205 | 0.0048214 | -1.3974 | 0.069511 | -0.0073316 | 0.011476 | -0.00044851 | 4.1382 | 121.0373 | -0.37079 | 121.0556 | 0.87433 | -0.07782 | 0.3891 | 2.4445 | 121.0098 | -0.44861 | 120.8313 | -0.21057 | 0.068665 | -0.21057 | 0.13733 | -0.15564 | -0.13733 | 1.3824 | 0.89722 | 0.4303 | 0.75989 | 0.29297 | 0.05951 | -0.1831 | -0.36163 | 0.29755 | 0.29755 | 0.57678 | 0.23804 | 0.51727 | 1.2451 | 121.4264 | 0.23804 | 121.2799 | 121.4081 | 121.4584 | 121.5454 | 121.5179 | -121.5637 | -121.6415 | 121.5637 | 121.3394 | 4.6463 | 2.9526
2101.1094 | 121.6461 | -0.48523 | 121.1929 | 0.0019074 | 6.4657 | 0.065176 | 0.075464 | -0.0014313 | -0.00014304 | 0.0027558 | 0.00018312 | 0.0052486 | -1.394 | 0.056693 | -0.0034864 | 0.010835 | -0.0030121 | 4.1336 | 121.0373 | -0.37537 | 121.1151 | 0.94299 | -0.064087 | 0.41657 | 2.5177 | 121.0007 | -0.42114 | 120.8862 | -0.19226 | 0.091553 | -0.16937 | 0.10986 | -0.15564 | -0.07782 | 1.4282 | 0.90179 | 0.42114 | 0.79193 | 0.31128 | 0.064086 | -0.19226 | -0.3067 | 0.29297 | 0.31586 | 0.57678 | 0.25177 | 0.5127 | 1.3184 | 121.4905 | 0.22888 | 121.3074 | 121.4127 | 121.4218 | 121.5225 | 121.4859 | -121.5683 | -121.6141 | 121.6003 | 121.3715 | 4.6188 | 3.0029
2102.8906 | 121.6003 | -0.53558 | 121.1792 | 0.0019074 | 6.4523 | 0.063681 | 0.073115 | 0.0039093 | -0.0012112 | 0.0016876 | -0.0028687 | 0.005676 | -1.3929 | 0.05883 | -0.0041272 | 0.011476 | 0.0014741 | 4.0512 | 121.051 | -0.38452 | 121.0464 | 0.87891 | -0.13275 | 0.36163 | 2.4216 | 120.9869 | -0.43488 | 120.8405 | -0.25177 | 0.032043 | -0.18768 | 0.15106 | -0.12817 | -0.13275 | 1.4145 | 0.89722 | 0.40283 | 0.74615 | 0.25177 | 0.10071 | -0.19226 | -0.33875 | 0.28381 | 0.3479 | 0.56763 | 0.24719 | 0.46692 | 1.2634 | 121.431 | 0.18311 | 121.2753 | 121.4355 | 121.4218 | 121.5866 | 121.5225 | -121.5637 | -121.6141 | 121.582 | 121.376 | 4.5868 | 2.9572
2104.5938 | 121.637 | -0.50354 | 121.1563 | -0.0057221 | 6.4873 | 0.065176 | 0.073328 | 0.00091851 | -0.00014304 | 0.0070282 | 0.021545 | 0.005676 | -1.3963 | 0.06887 | -0.0060498 | 0.010835 | -2.1314e-05 | 4.0604 | 121.0922 | -0.43945 | 121.0464 | 0.91553 | -0.073242 | 0.42572 | 2.4673 | 121.0327 | -0.48065 | 120.8267 | -0.21973 | 0.082397 | -0.17853 | 0.064087 | -0.064087 | -0.10986 | 1.4191 | 0.92926 | 0.4303 | 0.86517 | 0.36621 | 0.022888 | -0.1236 | -0.32959 | 0.28381 | 0.32501 | 0.58594 | 0.30212 | 0.56305 | 1.355 | 121.4859 | 0.26093 | 121.3074 | 121.5317 | 121.5134 | 121.5958 | 121.5363 | -121.5958 | -121.637 | 121.55 | 121.3303 | 4.5639 | 2.9709
2106.3125 | 121.7194 | -0.48065 | 121.1563 | -0.020981 | 6.4666 | 0.064749 | 0.072687 | -0.00036309 | -0.00078404 | 0.0055328 | 0.00018312 | 0.003326 | -1.3967 | 0.063102 | -0.00092279 | 0.013185 | -0.0030121 | 4.0466 | 121.0373 | -0.37994 | 121.0464 | 0.90637 | -0.09613 | 0.41199 | 2.4994 | 120.9366 | -0.43488 | 120.9183 | -0.14648 | 0.16022 | -0.11444 | 0.10071 | -0.11902 | -0.10986 | 1.387 | 0.89264 | 0.38452 | 0.79193 | 0.28381 | 0.045777 | -0.21973 | -0.23804 | 0.33417 | 0.36621 | 0.64087 | 0.32043 | 0.59509 | 1.2863 | 121.4264 | 0.28839 | 121.3531 | 121.4172 | 121.3715 | 121.5179 | 121.4172 | -121.5363 | -121.5912 | 121.5271 | 121.3989 | 4.5273 | 2.98
2108.0938 | 121.6644 | -0.46692 | 121.2158 | 0.040054 | 6.4706 | 0.067099 | 0.073969 | -0.00036309 | 0.00028416 | 0.0051056 | 0.0062865 | 0.0073848 | -1.3959 | 0.059257 | -0.007118 | 0.01233 | -0.0021575 | 3.9368 | 121.0739 | -0.3891 | 121.106 | 0.97046 | -0.022888 | 0.48065 | 2.5269 | 121.0144 | -0.43945 | 120.9091 | -0.12817 | 0.16479 | -0.12817 | 0.07782 | -0.14191 | -0.10986 | 1.4374 | 0.94757 | 0.44403 | 0.86975 | 0.36621 | 0.027466 | -0.20142 | -0.3067 | 0.33874 | 0.33874 | 0.63171 | 0.31128 | 0.60425 | 1.3596 | 121.4951 | 0.31128 | 121.3486 | 121.463 | 121.4539 | 121.5408 | 121.4813 | -121.6049 | -121.6553 | 121.5729 | 121.376 | 4.4037 | 2.9938
2109.875 | 121.7514 | -0.4715 | 121.138 | -0.0057221 | 6.473 | 0.064963 | 0.071406 | -0.00036309 | -0.003561 | 0.0038238 | -0.0059205 | 0.0046078 | -1.3952 | 0.070152 | -0.0060498 | 0.011689 | 0.0036103 | 3.891 | 120.9869 | -0.3479 | 121.1288 | 1.0345 | 0.050354 | 0.56305 | 2.6138 | 120.9137 | -0.39825 | 120.9641 | -0.041199 | 0.27008 | -0.091553 | 0.1236 | -0.15106 | -0.009155 | 1.506 | 1.0345 | 0.52185 | 0.91095 | 0.39825 | 0.073243 | -0.2243 | -0.17395 | 0.4303 | 0.37994 | 0.74158 | 0.3067 | 0.66834 | 1.3824 | 121.4767 | 0.35706 | 121.3623 | 121.3348 | 121.3119 | 121.4584 | 121.3852 | -121.4859 | -121.5363 | 121.6003 | 121.4355 | 4.3625 | 3.0853
2111.5781 | 121.7377 | -0.49439 | 121.1243 | 0.024795 | 6.5016 | 0.064749 | 0.073328 | -0.0029267 | -0.00035684 | 0.0046784 | -0.0028687 | 0.0041806 | -1.3955 | 0.070579 | -0.005409 | 0.013826 | 0.0025421 | 3.8315 | 120.9732 | -0.36163 | 121.0785 | 0.96588 | -0.018311 | 0.49896 | 2.5452 | 120.9457 | -0.4303 | 120.9137 | -0.13275 | 0.22888 | -0.11444 | 0.13275 | -0.15106 | -0.045777 | 1.4603 | 0.99335 | 0.47607 | 0.86059 | 0.34332 | 0.064087 | -0.17853 | -0.21057 | 0.36163 | 0.37994 | 0.72327 | 0.31586 | 0.65918 | 1.3275 | 121.4401 | 0.29755 | 121.344 | 121.3348 | 121.376 | 121.4676 | 121.4401 | -121.4859 | -121.5546 | 121.5729 | 121.4081 | 4.3259 | 3.0396
2113.3594 | 121.701 | -0.49439 | 121.1334 | 0.0019074 | 6.4512 | 0.06539 | 0.071406 | 0.0015595 | 7.0564e-05 | 0.0046784 | 0.0032349 | 0.0031124 | -1.3931 | 0.075492 | -0.0049818 | 0.01233 | -0.0013031 | 3.8132 | 121.0007 | -0.40283 | 121.0968 | 0.98419 | -0.022888 | 0.50812 | 2.5314 | 120.9503 | -0.43945 | 120.8817 | -0.14648 | 0.19684 | -0.13275 | 0.091553 | -0.13275 | -0.036621 | 1.4786 | 1.0025 | 0.4715 | 0.91095 | 0.37994 | 0.054932 | -0.18311 | -0.25177 | 0.3479 | 0.36163 | 0.69122 | 0.3067 | 0.63629 | 1.387 | 121.4996 | 0.29297 | 121.3211 | 121.4035 | 121.3898 | 121.4951 | 121.4447 | -121.5363 | -121.5729 | 121.5912 | 121.376 | 4.3076 | 3.0258
2115.125 | 121.7468 | -0.48065 | 121.1014 | -0.013352 | 6.4514 | 0.067099 | 0.073115 | -0.00014949 | -0.00014304 | 0.0023286 | 0.027649 | 0.0058896 | -1.394 | 0.062248 | -0.0045544 | 0.016175 | 0.0021149 | 3.8223 | 121.0007 | -0.37994 | 121.1243 | 1.0849 | 0.018311 | 0.56763 | 2.6596 | 120.9229 | -0.48065 | 120.9457 | -0.091553 | 0.22888 | -0.09613 | 0.10071 | -0.10071 | 0.022889 | 1.5656 | 1.0483 | 0.49896 | 0.94757 | 0.39826 | 0 | -0.17853 | -0.15564 | 0.3891 | 0.38452 | 0.70953 | 0.38452 | 0.70953 | 1.4648 | 121.5042 | 0.3891 | 121.4264 | 121.3806 | 121.4035 | 121.4813 | 121.4035 | -121.4813 | -121.582 | 121.6049 | 121.4264 | 4.303 | 3.1403
2116.8906 | 121.6141 | -0.53101 | 121.1197 | -0.0057221 | 6.4877 | 0.067313 | 0.074824 | 0.0015595 | -0.0012112 | 0.0046784 | 0.00018312 | 0.0048214 | -1.3961 | 0.054984 | -0.001991 | 0.01233 | -0.0034393 | 3.6896 | 121.0281 | -0.41199 | 120.9869 | 0.87433 | -0.16479 | 0.40741 | 2.4536 | 120.9549 | -0.46234 | 120.8084 | -0.24719 | 0.091553 | -0.20142 | 0.11902 | -0.091553 | -0.13275 | 1.4053 | 0.93842 | 0.36621 | 0.8194 | 0.24719 | 0.068665 | -0.1648 | -0.31128 | 0.28381 | 0.32959 | 0.62256 | 0.26092 | 0.55389 | 1.2863 | 121.3989 | 0.21515 | 121.2708 | 121.4401 | 121.4172 | 121.5591 | 121.4859 | -121.5317 | -121.582 | 121.5179 | 121.3394 | 4.2206 | 2.9846
2118.6562 | 121.701 | -0.53101 | 121.0922 | -0.0057221 | 6.505 | 0.064322 | 0.07226 | 0.0022003 | -0.0031338 | 0.0051056 | 0.00018312 | 0.0048214 | -1.3963 | 0.058616 | -0.006477 | 0.013185 | 0.0014741 | 3.6804 | 120.9229 | -0.39825 | 121.1014 | 1.0345 | -0.004578 | 0.52643 | 2.5818 | 120.8954 | -0.46692 | 120.8588 | -0.12817 | 0.23346 | -0.13733 | 0.13275 | -0.16937 | 0.009155 | 1.5656 | 1.0574 | 0.52643 | 0.92468 | 0.39368 | 0.064087 | -0.19684 | -0.23346 | 0.40283 | 0.39368 | 0.76446 | 0.32959 | 0.70038 | 1.4328 | 121.4996 | 0.33874 | 121.3257 | 121.3211 | 121.3623 | 121.4539 | 121.4264 | -121.4905 | -121.5591 | 121.6324 | 121.3898 | 4.2114 | 3.1128
2120.4219 | 121.6919 | -0.54474 | 121.0739 | -0.013352 | 6.5501 | 0.06304 | 0.074183 | -0.00079049 | -0.00099764 | 0.0029694 | -0.0028687 | 0.0061032 | -1.3965 | 0.063529 | -0.00070919 | 0.01233 | 0.0019013 | 3.6209 | 120.9732 | -0.43488 | 120.9915 | 0.92468 | -0.1236 | 0.45319 | 2.5177 | 120.9183 | -0.48065 | 120.8542 | -0.16937 | 0.19226 | -0.14648 | 0.10986 | -0.10071 | -0.082398 | 1.4694 | 0.99792 | 0.42114 | 0.88806 | 0.31128 | 0.064087 | -0.15564 | -0.21973 | 0.37537 | 0.39825 | 0.737 | 0.33417 | 0.67291 | 1.3596 | 121.4264 | 0.31128 | 121.3348 | 121.4081 | 121.3989 | 121.5179 | 121.463 | -121.5088 | -121.5546 | 121.5363 | 121.3989 | 4.1657 | 3.0624
2122.125 | 121.6827 | -0.50812 | 121.0922 | -0.013352 | 6.5317 | 0.066031 | 0.073328 | -0.0020721 | -0.00057044 | 0.004892 | -0.0028687 | 0.0041806 | -1.3935 | 0.069938 | -0.0024182 | 0.012758 | -0.0017303 | 3.6255 | 121.0052 | -0.43488 | 121.0236 | 0.93384 | -0.10071 | 0.48065 | 2.5314 | 120.9229 | -0.45319 | 120.8725 | -0.16479 | 0.19684 | -0.13275 | 0.073243 | -0.086975 | -0.068664 | 1.442 | 0.98877 | 0.40741 | 0.91553 | 0.33417 | 0.054932 | -0.16937 | -0.21973 | 0.34332 | 0.37537 | 0.70496 | 0.32043 | 0.65002 | 1.3687 | 121.4584 | 0.28839 | 121.3257 | 121.4401 | 121.376 | 121.5134 | 121.431 | -121.5271 | -121.5454 | 121.5317 | 121.3806 | 4.1336 | 3.0396
2123.8906 | 121.7331 | -0.4715 | 121.0968 | 0.0019074 | 6.5411 | 0.064749 | 0.07461 | -0.0012177 | 0.00092496 | 0.0055328 | -0.0059205 | 0.0058896 | -1.3959 | 0.068229 | 0.00014521 | 0.014039 | 0.0040375 | 3.685 | 120.9641 | -0.37994 | 121.106 | 1.0666 | -0.009155 | 0.58594 | 2.6459 | 120.9091 | -0.4303 | 120.9412 | -0.09613 | 0.29755 | -0.082397 | 0.091553 | -0.13275 | 0.009155 | 1.5381 | 1.0574 | 0.46234 | 0.96588 | 0.37079 | 0.041199 | -0.18768 | -0.15564 | 0.37537 | 0.3891 | 0.76904 | 0.3479 | 0.72784 | 1.4465 | 121.4859 | 0.33417 | 121.3715 | 121.344 | 121.3394 | 121.4355 | 121.3806 | -121.4767 | -121.5271 | 121.5775 | 121.4127 | 4.1565 | 3.1174
2125.6562 | 121.6324 | -0.50812 | 121.1243 | 0.0019074 | 6.549 | 0.064536 | 0.073328 | 0.0039093 | -0.0012112 | 0.0072418 | -0.0028687 | 0.003967 | -1.3967 | 0.065238 | -0.0039136 | 0.013612 | 0.0027557 | 3.5889 | 121.0373 | -0.39825 | 120.9915 | 0.95215 | -0.10071 | 0.48523 | 2.5085 | 120.9366 | -0.45776 | 120.8588 | -0.1831 | 0.20142 | -0.14191 | 0.10986 | -0.086976 | -0.13275 | 1.4603 | 0.99335 | 0.40741 | 0.88348 | 0.29755 | 0.050354 | -0.18768 | -0.2655 | 0.32501 | 0.36621 | 0.70953 | 0.31586 | 0.65918 | 1.3504 | 121.3898 | 0.27466 | 121.3165 | 121.4355 | 121.3943 | 121.5454 | 121.4447 | -121.5225 | -121.582 | 121.4996 | 121.3669 | 4.097 | 3.0167
2127.3594 | 121.7377 | -0.48981 | 121.0968 | -0.0057221 | 6.5012 | 0.067954 | 0.073969 | 0.0028411 | 0.00049776 | 0.0063874 | 0.024597 | 0.0061032 | -1.3925 | 0.076988 | -0.0032728 | 0.015962 | 0.0046783 | 3.6667 | 120.9961 | -0.35706 | 121.1655 | 1.1536 | 0.064087 | 0.65002 | 2.7008 | 120.9641 | -0.44403 | 120.9366 | -0.059509 | 0.31128 | -0.059509 | 0.13275 | -0.10071 | 0.068664 | 1.6434 | 1.1398 | 0.55389 | 1.0071 | 0.42114 | 0.045776 | -0.13275 | -0.16022 | 0.4303 | 0.4303 | 0.80109 | 0.38452 | 0.75531 | 1.5106 | 121.5225 | 0.38452 | 121.3806 | 121.3531 | 121.4081 | 121.4859 | 121.4539 | -121.4539 | -121.5408 | 121.6553 | 121.4264 | 4.1565 | 3.1906
2129.1406 | 121.637 | -0.48065 | 121.1609 | 0.017166 | 6.5114 | 0.065176 | 0.07461 | 0.0024139 | -0.0014248 | 0.0080964 | 0.00018312 | 0.0052486 | -1.3969 | 0.062675 | -0.006477 | 0.013398 | -0.0027985 | 3.6438 | 121.051 | -0.38452 | 121.0968 | 1.0757 | 0.009155 | 0.59052 | 2.5864 | 120.9824 | -0.41657 | 120.8542 | -0.12817 | 0.2655 | -0.10529 | 0.096131 | -0.10986 | -0.064087 | 1.5564 | 1.0712 | 0.48981 | 0.97504 | 0.39368 | 0.064087 | -0.17853 | -0.3067 | 0.35248 | 0.37537 | 0.74616 | 0.31128 | 0.68207 | 1.4603 | 121.4813 | 0.28839 | 121.2708 | 121.4355 | 121.3989 | 121.5317 | 121.463 | -121.5454 | -121.5775 | 121.5775 | 121.3348 | 4.1245 | 3.067
2130.9219 | 121.6827 | -0.46234 | 121.106 | 0.0095369 | 6.5089 | 0.066245 | 0.072901 | 0.00027771 | 0.00049776 | 0.0068146 | 0.0093383 | 0.002258 | -1.3942 | 0.059898 | -0.0045544 | 0.013398 | 0.0051057 | 3.6118 | 121.019 | -0.35706 | 121.0876 | 1.1078 | 0.041199 | 0.6134 | 2.5864 | 120.9366 | -0.42572 | 120.8817 | -0.10071 | 0.31128 | -0.07782 | 0.10529 | -0.086975 | -0.018311 | 1.5701 | 1.0757 | 0.50354 | 0.97046 | 0.39825 | 0.036621 | -0.16937 | -0.2243 | 0.36163 | 0.38452 | 0.77362 | 0.3479 | 0.737 | 1.4648 | 121.4447 | 0.32501 | 121.3074 | 121.376 | 121.3623 | 121.4813 | 121.3989 | -121.463 | -121.5317 | 121.55 | 121.344 | 4.0741 | 3.0487
2132.7031 | 121.7148 | -0.45319 | 121.0922 | 0.062942 | 6.5505 | 0.068167 | 0.075678 | -0.00036309 | 0.0017796 | 0.0072418 | 0.015442 | 0.0061032 | -1.3933 | 0.068229 | -0.0032728 | 0.013398 | -0.00066231 | 3.6804 | 121.0419 | -0.36621 | 121.1792 | 1.2039 | 0.10071 | 0.69122 | 2.7145 | 120.9549 | -0.43945 | 120.9503 | -0.045776 | 0.37994 | -0.045776 | 0.086975 | -0.050354 | 0.086975 | 1.6571 | 1.1444 | 0.55389 | 1.0574 | 0.46692 | 0.013733 | -0.13733 | -0.14191 | 0.40741 | 0.40741 | 0.83313 | 0.39368 | 0.8194 | 1.5701 | 121.5454 | 0.39368 | 121.3898 | 121.4081 | 121.3943 | 121.4951 | 121.4081 | -121.4584 | -121.5317 | 121.6324 | 121.4035 | 4.1336 | 3.1677
2134.4219 | 121.6965 | -0.46692 | 121.106 | 0.0095369 | 6.523 | 0.066672 | 0.073755 | 0.00049131 | -0.00035684 | 0.0055328 | 0.0032349 | 0.0037532 | -1.3976 | 0.070365 | -0.0056226 | 0.01233 | 0.0016877 | 3.5706 | 121.0327 | -0.36621 | 121.0785 | 1.0986 | 0.041199 | 0.63171 | 2.5955 | 120.932 | -0.41199 | 120.8862 | -0.073242 | 0.35248 | -0.073242 | 0.10071 | -0.073242 | -0.027466 | 1.5656 | 1.0986 | 0.50812 | 0.99792 | 0.40741 | 0.054932 | -0.17395 | -0.21973 | 0.39368 | 0.39368 | 0.8194 | 0.33874 | 0.76446 | 1.4648 | 121.4447 | 0.33874 | 121.2982 | 121.3989 | 121.344 | 121.4996 | 121.3989 | -121.4722 | -121.5179 | 121.5454 | 121.3531 | 4.0375 | 3.0624
2136.2031 | 121.756 | -0.45319 | 121.1472 | 0.0019074 | 6.5403 | 0.063467 | 0.073115 | 6.4114e-05 | -0.0016384 | 0.0061738 | -0.0028687 | 0.0035396 | -1.395 | 0.069724 | -0.0037 | 0.01233 | 0.0014741 | 3.6163 | 120.9686 | -0.33417 | 121.1563 | 1.2039 | 0.13275 | 0.737 | 2.7374 | 120.9183 | -0.37537 | 120.9595 | -0.004578 | 0.44403 | -0.022888 | 0.11902 | -0.17853 | 0.009155 | 1.6571 | 1.1902 | 0.58594 | 1.0712 | 0.46692 | 0.07782 | -0.22888 | -0.18768 | 0.44861 | 0.4303 | 0.89722 | 0.35248 | 0.8194 | 1.5381 | 121.4905 | 0.37079 | 121.3348 | 121.3028 | 121.2936 | 121.4218 | 121.3715 | -121.4813 | -121.5225 | 121.6095 | 121.4127 | 4.0695 | 3.1906
2138 | 121.5866 | -0.48523 | 121.17 | -0.013352 | 6.567 | 0.066245 | 0.074183 | 0.0077545 | -0.00014304 | 0.0063874 | -0.0028687 | 0.0048214 | -1.3955 | 0.061393 | -0.0060498 | 0.010194 | 0.00040589 | 3.5294 | 121.0602 | -0.40283 | 121.0236 | 1.0254 | -0.036621 | 0.59052 | 2.5314 | 120.9869 | -0.44861 | 120.8221 | -0.16937 | 0.25177 | -0.13275 | 0.082397 | -0.10986 | -0.14648 | 1.5106 | 1.0757 | 0.44861 | 0.99335 | 0.36621 | 0.036621 | -0.18311 | -0.3479 | 0.31586 | 0.35248 | 0.737 | 0.31586 | 0.70038 | 1.4282 | 121.4264 | 0.27924 | 121.2708 | 121.463 | 121.4355 | 121.5454 | 121.4722 | -121.5729 | -121.6187 | 121.5088 | 121.3074 | 4.0146 | 3.0167
2139.7656 | 121.5729 | -0.50354 | 121.1334 | 0.0019074 | 6.5792 | 0.066885 | 0.076319 | -0.00014949 | -0.00014304 | 0.0068146 | 0.00018312 | 0.0063168 | -1.3961 | 0.062461 | -0.004768 | 0.011689 | -0.0010895 | 3.4882 | 121.0327 | -0.3891 | 120.9961 | 0.98419 | -0.054932 | 0.56763 | 2.5085 | 120.9595 | -0.44861 | 120.7947 | -0.16937 | 0.27924 | -0.1236 | 0.11444 | -0.10071 | -0.13733 | 1.4877 | 1.0712 | 0.44861 | 0.95673 | 0.33417 | 0.054932 | -0.17395 | -0.33874 | 0.33417 | 0.37994 | 0.78278 | 0.32501 | 0.72784 | 1.3733 | 121.3852 | 0.27924 | 121.2433 | 121.4218 | 121.4081 | 121.5363 | 121.463 | -121.5225 | -121.582 | 121.4996 | 121.2982 | 3.9917 | 3.0121
2141.4688 | 121.582 | -0.54016 | 121.1426 | -0.0057221 | 6.5969 | 0.065176 | 0.076319 | 0.0015595 | -0.00099764 | 0.010019 | -0.0028687 | 0.0058896 | -1.3948 | 0.060111 | -0.0032728 | 0.012971 | 0.0031829 | 3.4378 | 121.0144 | -0.39368 | 120.9869 | 0.97504 | -0.082397 | 0.56305 | 2.4948 | 120.9595 | -0.45776 | 120.7855 | -0.19226 | 0.27008 | -0.13733 | 0.14648 | -0.12817 | -0.15564 | 1.5152 | 1.1032 | 0.45776 | 0.95673 | 0.31128 | 0.082397 | -0.1831 | -0.35706 | 0.3479 | 0.40283 | 0.81024 | 0.32044 | 0.72785 | 1.3687 | 121.3806 | 0.2655 | 121.2433 | 121.4081 | 121.4172 | 121.5546 | 121.4996 | -121.5363 | -121.6003 | 121.5271 | 121.3257 | 3.978 | 3.035
2143.25 | 121.5912 | -0.52185 | 121.106 | -0.0057221 | 6.5875 | 0.063895 | 0.075037 | -0.00014949 | -0.001852 | 0.0074554 | -0.0059205 | 0.0052486 | -1.3931 | 0.059898 | -0.0062634 | 0.012544 | 0.0036103 | 3.4058 | 121.0052 | -0.40741 | 120.9778 | 1.0254 | -0.022888 | 0.60883 | 2.5314 | 120.9778 | -0.50354 | 120.7626 | -0.17395 | 0.29297 | -0.14648 | 0.11444 | -0.10071 | -0.12817 | 1.5472 | 1.1307 | 0.49896 | 1.0162 | 0.38452 | 0.018311 | -0.12817 | -0.34332 | 0.3479 | 0.37537 | 0.81482 | 0.35706 | 0.79651 | 1.4328 | 121.3852 | 0.32959 | 121.2662 | 121.4127 | 121.4813 | 121.5271 | 121.4996 | -121.5134 | -121.6095 | 121.4996 | 121.2845 | 3.9276 | 3.0533
2145.0156 | 121.669 | -0.48065 | 121.1426 | 0.017166 | 6.5663 | 0.065176 | 0.075892 | 0.00027771 | 0.00071136 | 0.0076692 | 0.01239 | 0.003326 | -1.3961 | 0.068656 | -0.0034864 | 0.010621 | -0.00044851 | 3.4836 | 121.0007 | -0.37079 | 121.0922 | 1.1444 | 0.054932 | 0.72784 | 2.6459 | 120.9595 | -0.44861 | 120.8725 | -0.07782 | 0.41657 | -0.07782 | 0.10986 | -0.14191 | -0.050354 | 1.6251 | 1.2085 | 0.53558 | 1.0986 | 0.42572 | 0.032044 | -0.1831 | -0.27008 | 0.40283 | 0.40283 | 0.89722 | 0.37079 | 0.86517 | 1.5152 | 121.463 | 0.37079 | 121.3211 | 121.3715 | 121.4081 | 121.4813 | 121.4401 | -121.5134 | -121.5912 | 121.5729 | 121.3531 | 3.9642 | 3.1265
2146.7969 | 121.582 | -0.48523 | 121.1426 | 0.0095369 | 6.5721 | 0.064749 | 0.074824 | 0.0015595 | -0.00014304 | 0.0046784 | -0.0028687 | 0.0052486 | -1.3952 | 0.068656 | -0.0051954 | 0.01233 | 0.0027557 | 3.4561 | 121.0373 | -0.39368 | 121.0373 | 1.0529 | -0.018311 | 0.6546 | 2.6001 | 120.9686 | -0.43488 | 120.8084 | -0.14648 | 0.33875 | -0.10529 | 0.091552 | -0.10529 | -0.10529 | 1.5381 | 1.1398 | 0.46692 | 1.0483 | 0.37537 | 0.050354 | -0.17395 | -0.33417 | 0.33875 | 0.37994 | 0.82397 | 0.32959 | 0.77362 | 1.4465 | 121.431 | 0.28839 | 121.2433 | 121.431 | 121.4035 | 121.5225 | 121.4539 | -121.5363 | -121.5775 | 121.5225 | 121.2936 | 3.9413 | 3.0853
2148.5625 | 121.637 | -0.48065 | 121.1151 | 0.0019074 | 6.5546 | 0.067099 | 0.075892 | 0.0015595 | 7.0564e-05 | 0.0055328 | 0.0093383 | 0.0063168 | -1.3937 | 0.060539 | -0.0039136 | 0.0097669 | -0.0010895 | 3.4653 | 121.019 | -0.37994 | 121.0648 | 1.1215 | 0.064087 | 0.72327 | 2.6733 | 120.9824 | -0.41657 | 120.8542 | -0.059509 | 0.43945 | -0.059509 | 0.10071 | -0.09613 | -0.050354 | 1.6022 | 1.2039 | 0.54474 | 1.1032 | 0.44403 | 0.064087 | -0.13275 | -0.26093 | 0.42114 | 0.42114 | 0.9201 | 0.35706 | 0.85602 | 1.5015 | 121.4447 | 0.35706 | 121.2708 | 121.3989 | 121.3989 | 121.4996 | 121.463 | -121.4951 | -121.5317 | 121.5454 | 121.3348 | 3.9459 | 3.154
2150.3281 | 121.5958 | -0.51727 | 121.1426 | -0.013352 | 6.5796 | 0.06539 | 0.075678 | -0.0046357 | -0.0020658 | 0.0074554 | 0.0032349 | 0.005676 | -1.3948 | 0.063102 | -0.003059 | 0.010621 | 0.0025421 | 3.4287 | 120.9778 | -0.38452 | 121.0098 | 1.0803 | 0.036621 | 0.70038 | 2.6093 | 120.9457 | -0.4715 | 120.7947 | -0.11902 | 0.40283 | -0.11902 | 0.13275 | -0.16479 | -0.13275 | 1.5976 | 1.2177 | 0.55389 | 1.0849 | 0.42114 | 0.045776 | -0.19684 | -0.3479 | 0.39825 | 0.39825 | 0.9201 | 0.35248 | 0.87433 | 1.4648 | 121.3943 | 0.35248 | 121.2662 | 121.3623 | 121.4172 | 121.4951 | 121.463 | -121.5271 | -121.6141 | 121.5271 | 121.312 | 3.9459 | 3.1265
2152.0938 | 121.6095 | -0.49896 | 121.1243 | -0.013352 | 6.5593 | 0.064322 | 0.075464 | -0.0014313 | 7.0564e-05 | 0.0080964 | -0.0059205 | 0.0048214 | -1.3946 | 0.066306 | -0.0051954 | 0.012117 | 0.00083309 | 3.447 | 120.9549 | -0.37079 | 121.0739 | 1.1398 | 0.10071 | 0.74158 | 2.655 | 120.9366 | -0.43945 | 120.8221 | -0.086975 | 0.43488 | -0.091553 | 0.12817 | -0.16937 | -0.050354 | 1.6388 | 1.2405 | 0.59967 | 1.1124 | 0.4715 | 0.059509 | -0.18768 | -0.30212 | 0.41199 | 0.40741 | 0.93384 | 0.3479 | 0.87433 | 1.5106 | 121.4447 | 0.35248 | 121.2616 | 121.3257 | 121.376 | 121.4539 | 121.4355 | -121.4951 | -121.5637 | 121.5729 | 121.3211 | 3.9459 | 3.154
2153.7969 | 121.582 | -0.52643 | 121.106 | -0.0057221 | 6.5922 | 0.066672 | 0.077173 | 0.00070491 | -0.0020658 | 0.0055328 | -0.0028687 | 0.0058896 | -1.3957 | 0.066734 | -0.0015638 | 0.011262 | 0.00083309 | 3.3966 | 121.0052 | -0.3891 | 120.9641 | 1.0025 | -0.045776 | 0.6546 | 2.5635 | 120.9457 | -0.45776 | 120.7718 | -0.16022 | 0.37079 | -0.10986 | 0.13733 | -0.10071 | -0.14191 | 1.5289 | 1.181 | 0.48065 | 1.0437 | 0.34332 | 0.068664 | -0.16022 | -0.33417 | 0.36621 | 0.41657 | 0.89722 | 0.3479 | 0.82855 | 1.3916 | 121.3531 | 0.29755 | 121.2296 | 121.3943 | 121.4035 | 121.5317 | 121.4722 | -121.4951 | -121.5637 | 121.4905 | 121.2982 | 3.923 | 3.0899
2155.5625 | 121.6278 | -0.53101 | 121.1014 | 0.032425 | 6.5973 | 0.06539 | 0.076319 | 0.00091851 | -0.0016384 | 0.011514 | 0.018494 | 0.0073848 | -1.3937 | 0.062034 | -0.0043408 | 0.012117 | 0.0029693 | 3.4287 | 121.0327 | -0.4303 | 121.0098 | 1.0757 | 0.050354 | 0.74158 | 2.623 | 120.9686 | -0.49439 | 120.8084 | -0.086975 | 0.44861 | -0.068665 | 0.10071 | -0.068664 | -0.091552 | 1.6068 | 1.2726 | 0.58136 | 1.1719 | 0.48065 | 0.036621 | -0.13275 | -0.29297 | 0.44403 | 0.46234 | 0.97961 | 0.42572 | 0.94299 | 1.506 | 121.4401 | 0.40741 | 121.3028 | 121.463 | 121.463 | 121.5637 | 121.4996 | -121.5317 | -121.5958 | 121.5408 | 121.3394 | 3.9597 | 3.154
2157.2656 | 121.5958 | -0.48065 | 121.138 | -0.0057221 | 6.5958 | 0.064108 | 0.078242 | 0.0051911 | -0.00057044 | 0.0059602 | -0.0059205 | 0.0065304 | -1.3961 | 0.055839 | -0.0024182 | 0.013612 | -0.00066231 | 3.392 | 121.0464 | -0.38452 | 120.9869 | 1.0208 | -0.013733 | 0.72327 | 2.5909 | 120.9549 | -0.4303 | 120.8176 | -0.13275 | 0.42114 | -0.059509 | 0.096131 | -0.091552 | -0.15106 | 1.5015 | 1.2039 | 0.46692 | 1.1078 | 0.37079 | 0.050354 | -0.18311 | -0.32043 | 0.3479 | 0.42114 | 0.9018 | 0.37079 | 0.85144 | 1.4053 | 121.3715 | 0.29755 | 121.2479 | 121.431 | 121.3852 | 121.5271 | 121.4355 | -121.5225 | -121.5683 | 121.4676 | 121.2982 | 3.8727 | 3.0716
2159.0469 | 121.6049 | -0.4715 | 121.138 | -0.013352 | 6.5866 | 0.064108 | 0.073328 | -0.0016449 | 0.00028416 | 0.0057464 | 0.00018312 | 0.005035 | -1.3961 | 0.065452 | -0.007118 | 0.012544 | 0.0055329 | 3.4515 | 120.9961 | -0.32501 | 121.106 | 1.1719 | 0.13275 | 0.85144 | 2.7008 | 120.9549 | -0.39825 | 120.8405 | -0.036621 | 0.53101 | -0.036621 | 0.14648 | -0.14191 | -0.032043 | 1.6434 | 1.3229 | 0.60425 | 1.1765 | 0.45776 | 0.073243 | -0.18311 | -0.29755 | 0.43488 | 0.43488 | 1.0025 | 0.36163 | 0.92926 | 1.4969 | 121.431 | 0.36163 | 121.2387 | 121.3211 | 121.3531 | 121.4676 | 121.4264 | -121.463 | -121.5363 | 121.5775 | 121.312 | 3.923 | 3.1723
2160.8281 | 121.6965 | -0.4303 | 121.1151 | -0.0057221 | 6.6031 | 0.063467 | 0.073328 | -0.0020721 | 0.00049776 | 0.0029694 | -0.0059205 | 0.0031124 | -1.3959 | 0.064384 | -0.0045544 | 0.013185 | 0.0031829 | 3.4607 | 121.0052 | -0.33417 | 121.1288 | 1.2634 | 0.20599 | 0.90637 | 2.8152 | 120.9412 | -0.37537 | 120.9457 | 0.073242 | 0.65918 | 0.054932 | 0.096131 | -0.10986 | 0.013733 | 1.6937 | 1.3367 | 0.63629 | 1.2405 | 0.54016 | 0.054932 | -0.17395 | -0.16937 | 0.50354 | 0.48523 | 1.0895 | 0.4303 | 1.0345 | 1.5976 | 121.463 | 0.44861 | 121.3211 | 121.3394 | 121.3165 | 121.4355 | 121.3715 | -121.4493 | -121.4905 | 121.5591 | 121.376 | 3.891 | 3.2455
2162.5938 | 121.7148 | -0.4303 | 121.1243 | -0.013352 | 6.6403 | 0.066031 | 0.077173 | 0.0011321 | 0.0011386 | 0.0057464 | 0.00018312 | 0.0065304 | -1.3955 | 0.065452 | -0.00049559 | 0.014039 | 0.0025421 | 3.392 | 121.0464 | -0.3479 | 121.0785 | 1.181 | 0.11444 | 0.8606 | 2.774 | 120.9457 | -0.37537 | 120.9412 | 0.050354 | 0.63629 | 0.068665 | 0.082398 | -0.07782 | -0.045777 | 1.6113 | 1.2909 | 0.54474 | 1.2085 | 0.46234 | 0.054932 | -0.17853 | -0.18311 | 0.48065 | 0.49896 | 1.0666 | 0.44403 | 1.0117 | 1.5289 | 121.4264 | 0.42572 | 121.3165 | 121.3943 | 121.3211 | 121.4767 | 121.376 | -121.4722 | -121.4996 | 121.5088 | 121.3715 | 3.8223 | 3.2043
2164.3906 | 121.6187 | -0.49896 | 121.1334 | 0.024795 | 6.6294 | 0.065604 | 0.077387 | 0.0024139 | 0.00028416 | 0.0078828 | 0.0093383 | 0.0069576 | -1.3927 | 0.060325 | -0.0034864 | 0.011903 | -2.1314e-05 | 3.4241 | 121.0373 | -0.38452 | 121.0739 | 1.1902 | 0.14191 | 0.87433 | 2.742 | 120.9961 | -0.41657 | 120.8679 | -0.013733 | 0.57678 | 0.009155 | 0.11444 | -0.096131 | -0.059509 | 1.6891 | 1.3733 | 0.64087 | 1.2589 | 0.52643 | 0.082397 | -0.13733 | -0.2655 | 0.48523 | 0.50812 | 1.0757 | 0.42572 | 0.99335 | 1.5747 | 121.4584 | 0.40283 | 121.2845 | 121.4218 | 121.4127 | 121.5363 | 121.4951 | -121.5179 | -121.55 | 121.5729 | 121.3669 | 3.923 | 3.241
2166.1719 | 121.6827 | -0.42572 | 121.1609 | -0.0057221 | 6.6311 | 0.065604 | 0.078455 | 0.0024139 | 0.0017796 | 0.0068146 | -0.0028687 | 0.0048214 | -1.3967 | 0.067161 | -0.0011364 | 0.013612 | 0.00061949 | 3.3737 | 121.0373 | -0.32501 | 121.0693 | 1.1673 | 0.10986 | 0.88348 | 2.7649 | 120.9778 | -0.39368 | 120.9366 | 0.050354 | 0.6546 | 0.086975 | 0.10071 | -0.1236 | -0.091553 | 1.593 | 1.3092 | 0.53558 | 1.2085 | 0.43488 | 0.032043 | -0.18311 | -0.22431 | 0.47607 | 0.5127 | 1.0803 | 0.48065 | 1.0483 | 1.4923 | 121.3943 | 0.44403 | 121.3303 | 121.3623 | 121.3715 | 121.463 | 121.4035 | -121.4859 | -121.5546 | 121.4951 | 121.3623 | 3.7994 | 3.1906
2167.9375 | 121.6873 | -0.43488 | 121.106 | -0.013352 | 6.6407 | 0.06539 | 0.077387 | -0.00057689 | 0.0019932 | 0.0061738 | 0.00018312 | 0.0052486 | -1.3948 | 0.068015 | -0.0013502 | 0.014894 | 0.0012603 | 3.3829 | 121.0281 | -0.35248 | 121.0419 | 1.1948 | 0.10986 | 0.8606 | 2.7786 | 120.9274 | -0.40283 | 120.9137 | 0.036621 | 0.66834 | 0.064087 | 0.082397 | -0.07782 | -0.064087 | 1.6296 | 1.2955 | 0.54474 | 1.2131 | 0.46234 | 0.032043 | -0.17853 | -0.19226 | 0.4715 | 0.49896 | 1.1032 | 0.46692 | 1.0712 | 1.5472 | 121.3943 | 0.43945 | 121.3165 | 121.3806 | 121.3303 | 121.463 | 121.3623 | -121.4584 | -121.5088 | 121.4767 | 121.3486 | 3.8177 | 3.2135
2169.7031 | 121.5912 | -0.50812 | 121.17 | 0.055313 | 6.6232 | 0.064536 | 0.07931 | -0.00079049 | -0.00057044 | 0.0085236 | 0.018494 | 0.0063168 | -1.3931 | 0.066093 | -0.006477 | 0.011689 | 0.0023285 | 3.3875 | 121.0144 | -0.40741 | 121.0098 | 1.1581 | 0.10071 | 0.86975 | 2.71 | 121.0052 | -0.45776 | 120.7993 | -0.050354 | 0.58136 | -0.013733 | 0.10071 | -0.15564 | -0.16022 | 1.6663 | 1.3779 | 0.60883 | 1.2772 | 0.50812 | 0.050354 | -0.16479 | -0.37079 | 0.45776 | 0.49438 | 1.0895 | 0.44403 | 1.0391 | 1.5656 | 121.4172 | 0.40741 | 121.257 | 121.4218 | 121.463 | 121.5225 | 121.5134 | -121.5775 | -121.6278 | 121.5179 | 121.3074 | 3.8956 | 3.2181
2171.4219 | 121.6599 | -0.44861 | 121.0739 | 0.062942 | 6.6161 | 0.066672 | 0.078455 | 0.0017731 | 0.0041294 | 0.009378 | 0.021545 | 0.005676 | -1.3963 | 0.071647 | -0.0017774 | 0.014466 | -0.0023713 | 3.4332 | 120.9961 | -0.36163 | 121.1151 | 1.3046 | 0.1831 | 0.94299 | 2.8702 | 120.9229 | -0.4303 | 120.8771 | 0.032043 | 0.68207 | 0.050354 | 0.086975 | -0.07782 | 0.041198 | 1.7532 | 1.3916 | 0.63171 | 1.3046 | 0.54474 | 0.01831 | -0.15106 | -0.19684 | 0.48065 | 0.49896 | 1.1307 | 0.48065 | 1.1124 | 1.6663 | 121.4767 | 0.46234 | 121.3074 | 121.3577 | 121.3531 | 121.4447 | 121.3715 | -121.4355 | -121.5042 | 121.5637 | 121.3257 | 3.8818 | 3.3188
2173.1875 | 121.7148 | -0.45319 | 121.0739 | -0.013352 | 6.617 | 0.064108 | 0.075037 | 0.0013459 | -0.00014304 | 0.0078828 | -0.0028687 | 0.0054622 | -1.3931 | 0.070152 | -0.006477 | 0.011689 | 0.0031829 | 3.4012 | 120.9137 | -0.33417 | 121.1288 | 1.3 | 0.2243 | 0.97046 | 2.8748 | 120.9 | -0.41199 | 120.9 | 0.09613 | 0.75073 | 0.064087 | 0.11902 | -0.16022 | 0.054931 | 1.7532 | 1.4236 | 0.67749 | 1.3046 | 0.55847 | 0.041199 | -0.17395 | -0.17395 | 0.54932 | 0.51727 | 1.2039 | 0.47607 | 1.1627 | 1.6342 | 121.463 | 0.50812 | 121.3119 | 121.2479 | 121.3119 | 121.3669 | 121.3531 | -121.4081 | -121.4859 | 121.582 | 121.3531 | 3.8544 | 3.3279
2174.9688 | 121.6827 | -0.45319 | 121.0831 | -0.013352 | 6.6567 | 0.064536 | 0.075678 | -0.0016449 | 0.00028416 | 0.0098054 | -0.0059205 | 0.005676 | -1.3965 | 0.05883 | -0.008186 | 0.011903 | 0.0031829 | 3.3875 | 120.9091 | -0.3479 | 121.106 | 1.3046 | 0.21057 | 0.96588 | 2.861 | 120.8862 | -0.39825 | 120.8954 | 0.068665 | 0.75073 | 0.07782 | 0.10529 | -0.17395 | 0.022888 | 1.7578 | 1.4191 | 0.66376 | 1.3138 | 0.55847 | 0.054932 | -0.19684 | -0.18768 | 0.52185 | 0.53101 | 1.2039 | 0.47607 | 1.149 | 1.6525 | 121.4539 | 0.46692 | 121.2936 | 121.257 | 121.2845 | 121.3623 | 121.3394 | -121.431 | -121.4813 | 121.5591 | 121.3486 | 3.8406 | 3.3142
2176.6719 | 121.6827 | -0.48065 | 121.0831 | 0.0019074 | 6.6294 | 0.063254 | 0.076105 | -0.0020721 | -0.001852 | 0.011942 | -0.0059205 | 0.0043942 | -1.3969 | 0.069084 | -0.0043408 | 0.01233 | 0.0038239 | 3.3417 | 120.9503 | -0.38452 | 121.0373 | 1.2039 | 0.14648 | 0.92926 | 2.7924 | 120.8725 | -0.43945 | 120.8679 | 0.036621 | 0.737 | 0.050354 | 0.096131 | -0.13275 | -0.045777 | 1.6846 | 1.4099 | 0.62714 | 1.3138 | 0.531 | 0.041199 | -0.21057 | -0.21515 | 0.51727 | 0.53101 | 1.2177 | 0.48981 | 1.1765 | 1.5884 | 121.4218 | 0.47607 | 121.3074 | 121.3348 | 121.312 | 121.431 | 121.3531 | -121.4676 | -121.5225 | 121.5179 | 121.3486 | 3.8223 | 3.273
2178.4531 | 121.5958 | -0.52643 | 121.0785 | 0.024795 | 6.618 | 0.063895 | 0.07696 | 0.0034821 | 7.0564e-05 | 0.0091644 | 0.0062865 | 0.005676 | -1.395 | 0.06417 | -0.0058362 | 0.012544 | 0.0019013 | 3.3646 | 120.9869 | -0.40741 | 121.0419 | 1.1993 | 0.13275 | 0.90179 | 2.8015 | 120.9595 | -0.46692 | 120.8176 | -0.022888 | 0.68207 | -0.004578 | 0.11902 | -0.091553 | -0.036621 | 1.7258 | 1.4282 | 0.65918 | 1.3092 | 0.54016 | 0.059509 | -0.11902 | -0.26093 | 0.50354 | 0.52185 | 1.2085 | 0.46234 | 1.149 | 1.6068 | 121.4493 | 0.44403 | 121.2845 | 121.3943 | 121.4264 | 121.5134 | 121.4859 | -121.4859 | -121.5454 | 121.5683 | 121.344 | 3.891 | 3.3279
2180.2344 | 121.6599 | -0.50354 | 121.0556 | 0.032425 | 6.6178 | 0.066885 | 0.078669 | 0.0075409 | -0.00014304 | 0.0070282 | 0.0062865 | 0.0054622 | -1.3935 | 0.065025 | -0.003059 | 0.011476 | 0.0016877 | 3.3325 | 120.9549 | -0.40741 | 121.0373 | 1.2726 | 0.16022 | 0.94299 | 2.8336 | 120.9045 | -0.46234 | 120.8405 | 0 | 0.72327 | 0.022888 | 0.09613 | -0.10071 | -0.018311 | 1.7761 | 1.4465 | 0.66376 | 1.3504 | 0.56763 | 0.041199 | -0.15106 | -0.21515 | 0.50354 | 0.52643 | 1.2268 | 0.48523 | 1.1856 | 1.68 | 121.4447 | 0.46234 | 121.3028 | 121.3623 | 121.3669 | 121.4584 | 121.4081 | -121.463 | -121.5179 | 121.5408 | 121.344 | 3.8361 | 3.3371
2182 | 121.669 | -0.50812 | 121.051 | 0.062942 | 6.6236 | 0.068808 | 0.078455 | 0.0071137 | 0.0017796 | 0.009378 | 0.01239 | 0.0065304 | -1.3976 | 0.069511 | -0.0017774 | 0.014253 | 0.00061949 | 3.3417 | 120.9366 | -0.40741 | 121.0876 | 1.3 | 0.17853 | 0.96588 | 2.8976 | 120.8908 | -0.46692 | 120.845 | 0.041199 | 0.77362 | 0.050354 | 0.10071 | -0.11444 | 0.036621 | 1.8082 | 1.474 | 0.68665 | 1.3733 | 0.58594 | 0.041199 | -0.16022 | -0.20599 | 0.54932 | 0.55847 | 1.2817 | 0.51727 | 1.2405 | 1.7075 | 121.4951 | 0.50812 | 121.312 | 121.344 | 121.3577 | 121.4447 | 121.3989 | -121.4584 | -121.5179 | 121.5958 | 121.3531 | 3.8498 | 3.4058
2183.7188 | 121.6827 | -0.50812 | 121.019 | 0.0019074 | 6.6176 | 0.064536 | 0.075892 | -0.0033539 | -0.0012112 | 0.0089508 | -0.0028687 | 0.0052486 | -1.3972 | 0.068015 | -0.005409 | 0.012971 | 0.0038239 | 3.3096 | 120.8954 | -0.39368 | 121.0602 | 1.2909 | 0.1831 | 0.97961 | 2.861 | 120.8679 | -0.45319 | 120.8313 | 0.068665 | 0.80566 | 0.045776 | 0.11444 | -0.1236 | 0.041199 | 1.799 | 1.4877 | 0.69122 | 1.3733 | 0.57678 | 0.054932 | -0.15106 | -0.18768 | 0.57678 | 0.55389 | 1.3138 | 0.49896 | 1.2589 | 1.6846 | 121.4539 | 0.52185 | 121.2845 | 121.2891 | 121.3211 | 121.4035 | 121.376 | -121.4127 | -121.4722 | 121.5683 | 121.3394 | 3.8177 | 3.3691
2185.4844 | 121.6782 | -0.50354 | 121.0007 | -0.013352 | 6.5836 | 0.064322 | 0.077387 | 0.0024139 | -0.00014304 | 0.0076692 | 0.00018312 | 0.0063168 | -1.3961 | 0.067375 | -0.0013502 | 0.015107 | 0.00061949 | 3.2318 | 120.9091 | -0.41199 | 121.0052 | 1.2314 | 0.10986 | 0.94757 | 2.8564 | 120.8588 | -0.45776 | 120.845 | 0.041199 | 0.80109 | 0.068665 | 0.091553 | -0.091552 | 0.004578 | 1.7349 | 1.4511 | 0.6134 | 1.3596 | 0.52185 | 0.045776 | -0.14191 | -0.15564 | 0.54474 | 0.5722 | 1.3046 | 0.52643 | 1.2589 | 1.6434 | 121.4172 | 0.49896 | 121.3028 | 121.3211 | 121.3165 | 121.4127 | 121.3623 | -121.4127 | -121.4584 | 121.5088 | 121.3486 | 3.7354 | 3.36
2187.2656 | 121.6553 | -0.51727 | 121.0236 | 0.0095369 | 6.6052 | 0.065176 | 0.077387 | 0.0019867 | -0.0014248 | 0.011942 | 0.0032349 | 0.0052486 | -1.395 | 0.062888 | -0.0043408 | 0.014253 | 0.0031829 | 3.2318 | 120.9137 | -0.41199 | 120.9778 | 1.2039 | 0.13275 | 0.94299 | 2.8015 | 120.8542 | -0.47607 | 120.7901 | -0.009155 | 0.7782 | 0.018311 | 0.10529 | -0.10986 | -0.045777 | 1.7212 | 1.4603 | 0.65002 | 1.355 | 0.54474 | 0.041199 | -0.16937 | -0.23346 | 0.50812 | 0.53558 | 1.2955 | 0.49439 | 1.2543 | 1.6159 | 121.3898 | 0.46692 | 121.2662 | 121.3257 | 121.3303 | 121.431 | 121.3715 | -121.4355 | -121.4996 | 121.4951 | 121.3074 | 3.7491 | 3.3188
2189.0469 | 121.637 | -0.52643 | 121.0373 | -0.013352 | 6.642 | 0.064536 | 0.079737 | 0.00091851 | 0.0019932 | 0.0091644 | -0.0028687 | 0.0065304 | -1.3929 | 0.060325 | -0.0028454 | 0.013612 | 0.0033967 | 3.1906 | 120.9503 | -0.43488 | 120.9457 | 1.1719 | 0.068665 | 0.90637 | 2.8244 | 120.8771 | -0.44861 | 120.8038 | 0.004578 | 0.77362 | 0.032043 | 0.091553 | -0.086975 | -0.091552 | 1.6983 | 1.4328 | 0.59509 | 1.3412 | 0.50354 | 0.07782 | -0.16022 | -0.23346 | 0.53101 | 0.55847 | 1.3 | 0.48065 | 1.2222 | 1.6067 | 121.3806 | 0.45319 | 121.2524 | 121.3852 | 121.3257 | 121.4767 | 121.4035 | -121.4722 | -121.4859 | 121.4722 | 121.3303 | 3.717 | 3.3508
2190.8125 | 121.5408 | -0.56763 | 121.0419 | -0.0057221 | 6.6163 | 0.064536 | 0.076319 | 0.0022003 | 0.0030612 | 0.0087372 | -0.0028687 | 0.008453 | -1.3944 | 0.063957 | -0.0079724 | 0.013185 | -0.00023491 | 3.1357 | 120.8954 | -0.43945 | 120.8954 | 1.1353 | 0.041199 | 0.87433 | 2.742 | 120.8908 | -0.49439 | 120.6985 | -0.10529 | 0.69122 | -0.050354 | 0.12817 | -0.14648 | -0.14648 | 1.7029 | 1.442 | 0.60883 | 1.3138 | 0.48065 | 0.073242 | -0.15106 | -0.34332 | 0.46234 | 0.51727 | 1.2589 | 0.44403 | 1.1856 | 1.5747 | 121.3348 | 0.3891 | 121.1929 | 121.3348 | 121.3852 | 121.463 | 121.4584 | -121.4813 | -121.5363 | 121.463 | 121.2662 | 3.7033 | 3.3096
2192.5156 | 121.6003 | -0.56305 | 121.0464 | 0.040054 | 6.6294 | 0.066245 | 0.077814 | 0.00070491 | 0.0015658 | 0.0089508 | 0.0093383 | 0.006744 | -1.3925 | 0.05947 | -0.0079724 | 0.012971 | 0.0016877 | 3.2318 | 120.9595 | -0.46692 | 120.9641 | 1.181 | 0.10529 | 0.95673 | 2.8427 | 120.8725 | -0.48523 | 120.7489 | -0.018311 | 0.81024 | 0.004578 | 0.09613 | -0.086975 | -0.082398 | 1.7441 | 1.5198 | 0.66834 | 1.4236 | 0.5722 | 0.07782 | -0.17395 | -0.29755 | 0.54474 | 0.56763 | 1.3733 | 0.48981 | 1.2955 | 1.6479 | 121.431 | 0.46692 | 121.2341 | 121.4264 | 121.3577 | 121.5225 | 121.4355 | -121.5134 | -121.5317 | 121.5271 | 121.312 | 3.7949 | 3.4058
2194.2969 | 121.6644 | -0.52185 | 121.0464 | 0.0019074 | 6.6219 | 0.064322 | 0.076105 | -0.0016449 | 0.0022068 | 0.0053192 | -0.0028687 | 0.0043942 | -1.3912 | 0.069724 | -0.0017774 | 0.013612 | 0.0053193 | 3.2364 | 120.8817 | -0.41199 | 120.9915 | 1.2634 | 0.17395 | 1.0025 | 2.8976 | 120.8267 | -0.4715 | 120.8221 | 0.082397 | 0.93842 | 0.091553 | 0.10986 | -0.16479 | -0.054932 | 1.7853 | 1.5244 | 0.6958 | 1.4145 | 0.58594 | 0.050354 | -0.21973 | -0.2243 | 0.60425 | 0.6134 | 1.4603 | 0.56305 | 1.4099 | 1.6754 | 121.4035 | 0.55389 | 121.2936 | 121.2936 | 121.2982 | 121.4035 | 121.3486 | -121.4584 | -121.5179 | 121.5134 | 121.344 | 3.7582 | 3.4195
2196.0625 | 121.669 | -0.48981 | 120.9824 | -0.013352 | 6.6618 | 0.066672 | 0.080591 | 0.0026275 | 0.0015658 | 0.01066 | 0.024597 | 0.0073848 | -1.394 | 0.072929 | -0.0024182 | 0.013612 | -0.00023491 | 3.2684 | 120.9274 | -0.39368 | 121.0831 | 1.3641 | 0.20599 | 1.0757 | 2.9892 | 120.8496 | -0.48981 | 120.845 | 0.09613 | 0.93842 | 0.10071 | 0.09613 | -0.054932 | 0.10071 | 1.8539 | 1.5656 | 0.6958 | 1.4694 | 0.59967 | 0 | -0.13275 | -0.13733 | 0.58594 | 0.59052 | 1.4282 | 0.59052 | 1.4282 | 1.7578 | 121.4767 | 0.58594 | 121.3348 | 121.3211 | 121.3394 | 121.4172 | 121.3394 | -121.376 | -121.4722 | 121.5729 | 121.3348 | 3.7582 | 3.479
2197.8281 | 121.6507 | -0.53558 | 120.9778 | 0.0019074 | 6.6766 | 0.064749 | 0.079523 | 0.00049131 | 0.00092496 | 0.010446 | -0.0059205 | 0.005035 | -1.3961 | 0.065025 | -0.0049818 | 0.012758 | 0.0021149 | 3.2089 | 120.8954 | -0.39368 | 120.9732 | 1.2726 | 0.16479 | 1.0117 | 2.9114 | 120.8084 | -0.45776 | 120.7947 | 0.09613 | 0.96588 | 0.091553 | 0.14191 | -0.082397 | -0.004577 | 1.8082 | 1.5472 | 0.70038 | 1.4053 | 0.55847 | 0.077819 | -0.16937 | -0.1831 | 0.63171 | 0.62714 | 1.5015 | 0.54932 | 1.4236 | 1.6663 | 121.3669 | 0.55389 | 121.2524 | 121.2891 | 121.2662 | 121.431 | 121.344 | -121.3715 | -121.4355 | 121.5088 | 121.3303 | 3.7445 | 3.447
2199.5469 | 121.6553 | -0.51727 | 120.9915 | -0.0057221 | 6.6864 | 0.067099 | 0.079737 | 0.00049131 | -0.0012112 | 0.010873 | -0.0028687 | 0.0075986 | -1.3969 | 0.063957 | -0.0039136 | 0.011476 | 0.0036103 | 3.2043 | 120.9045 | -0.42114 | 120.9778 | 1.2772 | 0.13275 | 1.0025 | 2.9388 | 120.8221 | -0.4715 | 120.813 | 0.07782 | 0.97046 | 0.10529 | 0.09613 | -0.086975 | -0.013733 | 1.7944 | 1.5198 | 0.65002 | 1.4236 | 0.55389 | 0.045776 | -0.16937 | -0.17853 | 0.59509 | 0.62256 | 1.4877 | 0.57678 | 1.442 | 1.6983 | 121.3989 | 0.54932 | 121.2845 | 121.3257 | 121.2936 | 121.4218 | 121.3394 | -121.4127 | -121.463 | 121.4951 | 121.3303 | 3.7216 | 3.4561
2201.3125 | 121.5454 | -0.58136 | 121.0419 | -0.0057221 | 6.6913 | 0.064536 | 0.07931 | 0.0011321 | 0.00049776 | 0.00831 | -0.0028687 | 0.0063168 | -1.3912 | 0.05947 | -0.0083996 | 0.01233 | 0.0040375 | 3.2135 | 120.8771 | -0.42114 | 120.9412 | 1.2497 | 0.14191 | 0.99335 | 2.8656 | 120.8542 | -0.48981 | 120.6894 | -0.032043 | 0.90179 | -0.004578 | 0.16022 | -0.16479 | -0.10071 | 1.8311 | 1.5747 | 0.72327 | 1.4145 | 0.56305 | 0.091553 | -0.18768 | -0.35248 | 0.54932 | 0.57678 | 1.4832 | 0.48523 | 1.3916 | 1.6708 | 121.3623 | 0.45776 | 121.1792 | 121.2982 | 121.344 | 121.4584 | 121.4355 | -121.463 | -121.5317 | 121.5225 | 121.2708 | 3.7949 | 3.447
2203.0938 | 121.5134 | -0.55847 | 121.0236 | 0.0019074 | 6.7043 | 0.066458 | 0.080591 | 0.0017731 | -0.00057044 | 0.010446 | -0.0089723 | 0.0080258 | -1.3922 | 0.063957 | -0.003059 | 0.013185 | 0.00083309 | 3.1723 | 120.9229 | -0.43488 | 120.9 | 1.1993 | 0.059509 | 0.94757 | 2.8152 | 120.8542 | -0.49896 | 120.6757 | -0.054932 | 0.86975 | 0 | 0.1236 | -0.10071 | -0.1236 | 1.7578 | 1.506 | 0.61798 | 1.3824 | 0.49438 | 0.05951 | -0.16937 | -0.3479 | 0.50354 | 0.55847 | 1.4282 | 0.49896 | 1.3687 | 1.6342 | 121.3348 | 0.44403 | 121.1746 | 121.3577 | 121.3531 | 121.4813 | 121.4127 | -121.4584 | -121.5225 | 121.4584 | 121.2341 | 3.7308 | 3.3737
2204.875 | 121.669 | -0.52643 | 120.9824 | -0.013352 | 6.727 | 0.067954 | 0.07931 | 0.00091851 | 7.0564e-05 | 0.010446 | 0.00018312 | 0.0048214 | -1.3929 | 0.070793 | -0.0011364 | 0.01468 | -0.0013031 | 3.2227 | 120.8725 | -0.40283 | 120.9961 | 1.3412 | 0.1831 | 1.0666 | 3.0029 | 120.8084 | -0.50354 | 120.8038 | 0.12817 | 1.0574 | 0.1236 | 0.1236 | -0.10986 | 0.013733 | 1.8677 | 1.593 | 0.70953 | 1.4694 | 0.58594 | 0.022888 | -0.17395 | -0.17853 | 0.6546 | 0.65002 | 1.5839 | 0.62714 | 1.561 | 1.7441 | 121.3989 | 0.63171 | 121.3074 | 121.2753 | 121.312 | 121.3989 | 121.3348 | -121.3852 | -121.4859 | 121.5225 | 121.3303 | 3.7491 | 3.5294
2206.5781 | 121.637 | -0.53558 | 120.9595 | 0.047683 | 6.7236 | 0.067099 | 0.081019 | -0.00014949 | 0.0022068 | 0.010446 | 0.01239 | 0.006744 | -1.3931 | 0.073142 | -0.003059 | 0.013398 | 0.0040375 | 3.2318 | 120.8817 | -0.45319 | 121.019 | 1.387 | 0.19684 | 1.1215 | 3.0441 | 120.7993 | -0.51727 | 120.7718 | 0.091553 | 1.0483 | 0.10529 | 0.082397 | -0.07782 | 0.059509 | 1.9226 | 1.6571 | 0.73242 | 1.5747 | 0.65002 | 0.01831 | -0.16022 | -0.18768 | 0.62714 | 0.64087 | 1.5839 | 0.62256 | 1.5656 | 1.8402 | 121.4722 | 0.60883 | 121.2891 | 121.3348 | 121.3165 | 121.4172 | 121.3348 | -121.4127 | -121.4767 | 121.5546 | 121.3074 | 3.7674 | 3.5797
2208.3594 | 121.5683 | -0.58136 | 121.019 | 0.040054 | 6.7116 | 0.06539 | 0.078669 | -0.0042083 | 0.00028416 | 0.013223 | 0.015442 | 0.0093074 | -1.3929 | 0.064811 | -0.0069044 | 0.011476 | 0.0042511 | 3.1357 | 120.9045 | -0.48523 | 120.9 | 1.2497 | 0.13275 | 1.0254 | 2.8931 | 120.8542 | -0.52185 | 120.6802 | 0 | 0.99335 | 0.036621 | 0.096131 | -0.11444 | -0.11902 | 1.8311 | 1.6068 | 0.71411 | 1.5106 | 0.61798 | 0.059509 | -0.16479 | -0.33874 | 0.58136 | 0.61798 | 1.5747 | 0.55847 | 1.5152 | 1.7349 | 121.3852 | 0.52185 | 121.2021 | 121.3898 | 121.376 | 121.4859 | 121.4355 | -121.5042 | -121.5408 | 121.4813 | 121.2616 | 3.717 | 3.4744
2210.0625 | 121.6141 | -0.53558 | 120.9732 | 0.032425 | 6.6915 | 0.066885 | 0.076533 | 0.00049131 | 0.00071136 | 0.012155 | 0.0093383 | 0.0071712 | -1.3963 | 0.065666 | -0.0039136 | 0.012971 | 0.0038239 | 3.1723 | 120.8771 | -0.43945 | 120.9641 | 1.3687 | 0.16937 | 1.1032 | 3.0075 | 120.8038 | -0.5127 | 120.7352 | 0.064087 | 1.0895 | 0.082397 | 0.09613 | -0.096131 | -0.009156 | 1.9043 | 1.6388 | 0.70496 | 1.5427 | 0.60883 | 0.022888 | -0.16937 | -0.23804 | 0.59967 | 0.61798 | 1.6251 | 0.59509 | 1.6022 | 1.8082 | 121.4035 | 0.57678 | 121.2479 | 121.3165 | 121.3165 | 121.4127 | 121.3394 | -121.4127 | -121.4859 | 121.4996 | 121.2708 | 3.7079 | 3.5431
2211.8281 | 121.6507 | -0.50354 | 120.9869 | -0.0057221 | 6.7197 | 0.066031 | 0.078455 | 0.0043365 | 7.0564e-05 | 0.0095918 | 0.0032349 | 0.0048214 | -1.3946 | 0.069724 | -0.0069044 | 0.016389 | 0.0010467 | 3.2043 | 120.8679 | -0.40741 | 121.0464 | 1.4557 | 0.26093 | 1.1627 | 3.0991 | 120.7993 | -0.45319 | 120.7947 | 0.16937 | 1.2177 | 0.16022 | 0.09613 | -0.11902 | 0.05951 | 1.9592 | 1.6663 | 0.76446 | 1.5701 | 0.66834 | 0.050354 | -0.18768 | -0.19226 | 0.67291 | 0.66376 | 1.7212 | 0.6134 | 1.6708 | 1.8631 | 121.4539 | 0.62256 | 121.2479 | 121.2753 | 121.2524 | 121.3715 | 121.3028 | -121.3943 | -121.4401 | 121.55 | 121.2982 | 3.7079 | 3.6026
2213.5938 | 121.5225 | -0.5722 | 121.0098 | -0.0057221 | 6.7535 | 0.066672 | 0.082728 | 0.00049131 | 0.0019932 | 0.011301 | -0.0028687 | 0.0071712 | -1.3955 | 0.064384 | -0.005409 | 0.012758 | 0.0019013 | 3.0945 | 120.9274 | -0.45776 | 120.8588 | 1.2177 | 0.064087 | 0.99335 | 2.8885 | 120.8725 | -0.48981 | 120.6482 | -0.009155 | 1.0529 | 0.068665 | 0.11444 | -0.082398 | -0.15106 | 1.7899 | 1.5656 | 0.63629 | 1.4511 | 0.52185 | 0.082398 | -0.13733 | -0.36163 | 0.56305 | 0.64087 | 1.6251 | 0.55847 | 1.5427 | 1.6754 | 121.3165 | 0.48065 | 121.138 | 121.3852 | 121.3623 | 121.4996 | 121.4447 | -121.4676 | -121.4996 | 121.431 | 121.2204 | 3.6667 | 3.4607
2215.3594 | 121.6461 | -0.51727 | 120.9686 | -0.013352 | 6.7533 | 0.066031 | 0.082941 | -0.0016449 | 0.0039158 | 0.012155 | 0.024597 | 0.0080258 | -1.3935 | 0.062888 | -0.0017774 | 0.013612 | 0.0025421 | 3.1723 | 120.9 | -0.44861 | 121.0373 | 1.4374 | 0.24261 | 1.181 | 3.1357 | 120.8084 | -0.5127 | 120.7947 | 0.14191 | 1.2314 | 0.16479 | 0.068665 | -0.068665 | 0.068664 | 1.9547 | 1.6983 | 0.75989 | 1.6296 | 0.69122 | 0.004578 | -0.16022 | -0.17395 | 0.65918 | 0.68207 | 1.7487 | 0.67749 | 1.7441 | 1.886 | 121.4859 | 0.6546 | 121.3074 | 121.3486 | 121.3211 | 121.4172 | 121.3257 | -121.4172 | -121.4813 | 121.5546 | 121.312 | 3.6896 | 3.653
2217.0781 | 121.5729 | -0.55847 | 121.0144 | -0.0057221 | 6.759 | 0.064322 | 0.079096 | 0.00070491 | 0.00071136 | 0.011087 | 0.00018312 | 0.006744 | -1.3942 | 0.073783 | -0.0075452 | 0.012758 | 0.0051057 | 3.1494 | 120.8405 | -0.42114 | 120.9549 | 1.3779 | 0.23804 | 1.149 | 3.0304 | 120.8267 | -0.48523 | 120.7031 | 0.09613 | 1.2085 | 0.10071 | 0.13733 | -0.17395 | -0.059509 | 1.9363 | 1.7075 | 0.79651 | 1.5701 | 0.65918 | 0.073243 | -0.18768 | -0.31128 | 0.6546 | 0.65918 | 1.767 | 0.58594 | 1.6937 | 1.799 | 121.376 | 0.58136 | 121.1884 | 121.2616 | 121.312 | 121.3989 | 121.3852 | -121.4355 | -121.4996 | 121.5134 | 121.2616 | 3.7079 | 3.5889
2218.8594 | 121.637 | -0.52643 | 120.9686 | -0.013352 | 6.7635 | 0.063895 | 0.080805 | 0.0011321 | 0.00071136 | 0.011514 | -0.0089723 | 0.0061032 | -1.3957 | 0.070793 | -0.005409 | 0.012971 | 0.0016877 | 3.1311 | 120.8496 | -0.40741 | 120.9869 | 1.4236 | 0.23804 | 1.1765 | 3.1219 | 120.7764 | -0.49439 | 120.7764 | 0.16937 | 1.3138 | 0.16479 | 0.11902 | -0.11902 | 0.01831 | 1.9501 | 1.7029 | 0.76446 | 1.5839 | 0.64545 | 0.032043 | -0.19226 | -0.19226 | 0.6958 | 0.69122 | 1.8402 | 0.65918 | 1.8082 | 1.8311 | 121.3943 | 0.66376 | 121.2708 | 121.257 | 121.2708 | 121.376 | 121.3028 | -121.376 | -121.463 | 121.5134 | 121.3028 | 3.6575 | 3.6484
2220.5625 | 121.5683 | -0.56305 | 121.0052 | 0.024795 | 6.7622 | 0.06539 | 0.080591 | 0.00049131 | 0.0017796 | 0.010446 | 0.0093383 | 0.0099484 | -1.3933 | 0.061179 | -0.0045544 | 0.011903 | 0.0040375 | 3.1128 | 120.8679 | -0.4715 | 120.9183 | 1.3229 | 0.16937 | 1.1215 | 3.0716 | 120.8633 | -0.52643 | 120.7123 | 0.09613 | 1.2543 | 0.1236 | 0.091552 | -0.13733 | -0.086975 | 1.886 | 1.6846 | 0.73242 | 1.593 | 0.64087 | 0.036621 | -0.14191 | -0.29297 | 0.65918 | 0.68665 | 1.8173 | 0.65002 | 1.7807 | 1.7944 | 121.3898 | 0.62256 | 121.2387 | 121.3394 | 121.3898 | 121.431 | 121.4264 | -121.4767 | -121.5317 | 121.4813 | 121.2753 | 3.6758 | 3.6346
2222.3281 | 121.6003 | -0.55389 | 120.9549 | 0.024795 | 6.7552 | 0.066672 | 0.079951 | 0.00027771 | 0.0013522 | 0.010233 | 0.00018312 | 0.0063168 | -1.3965 | 0.067588 | -0.0037 | 0.014466 | 0.00040589 | 3.067 | 120.8588 | -0.44861 | 120.9183 | 1.3458 | 0.18768 | 1.1398 | 3.0624 | 120.7855 | -0.51727 | 120.7306 | 0.1236 | 1.3321 | 0.15564 | 0.10529 | -0.09613 | -0.036621 | 1.8997 | 1.6937 | 0.74158 | 1.5884 | 0.63629 | 0.036621 | -0.16937 | -0.2243 | 0.67749 | 0.70953 | 1.886 | 0.67291 | 1.8494 | 1.7944 | 121.3669 | 0.64087 | 121.2479 | 121.3074 | 121.3028 | 121.4127 | 121.3394 | -121.4035 | -121.4722 | 121.4722 | 121.2845 | 3.6209 | 3.6163
2224.0938 | 121.5042 | -0.58594 | 121.0236 | -0.013352 | 6.7417 | 0.064963 | 0.080591 | 0.00027771 | 0.00049776 | 0.0068146 | -0.0059205 | 0.0073848 | -1.3948 | 0.06887 | -0.006477 | 0.011049 | 0.0038239 | 3.0441 | 120.8679 | -0.44861 | 120.8496 | 1.2863 | 0.14191 | 1.1124 | 3.0075 | 120.7993 | -0.50812 | 120.6436 | 0.068665 | 1.3046 | 0.082397 | 0.13733 | -0.15564 | -0.17395 | 1.8723 | 1.6983 | 0.72784 | 1.561 | 0.59052 | 0.077819 | -0.22431 | -0.37994 | 0.6546 | 0.66833 | 1.8906 | 0.59051 | 1.8127 | 1.7349 | 121.2982 | 0.57678 | 121.1517 | 121.3165 | 121.3074 | 121.4539 | 121.3852 | -121.4722 | -121.5317 | 121.4355 | 121.2296 | 3.6301 | 3.5934
2225.8594 | 121.6049 | -0.54932 | 120.9595 | 0.017166 | 6.7323 | 0.064108 | 0.082087 | -0.0024995 | 0.00049776 | 0.010233 | 0.0093383 | 0.0082394 | -1.3937 | 0.072715 | -0.0032728 | 0.014466 | 0.0053193 | 3.0762 | 120.8542 | -0.43945 | 120.9045 | 1.3367 | 0.19684 | 1.2039 | 3.0853 | 120.7855 | -0.50812 | 120.6985 | 0.12817 | 1.3916 | 0.16479 | 0.10986 | -0.10529 | -0.054932 | 1.886 | 1.7532 | 0.74615 | 1.6434 | 0.63629 | 0.041198 | -0.17395 | -0.26093 | 0.67749 | 0.71411 | 1.9409 | 0.67291 | 1.8997 | 1.7761 | 121.344 | 0.63629 | 121.2067 | 121.2936 | 121.2936 | 121.4035 | 121.3348 | -121.3989 | -121.4676 | 121.4539 | 121.2479 | 3.6255 | 3.6346
2227.625 | 121.5042 | -0.58594 | 120.9595 | -0.0057221 | 6.7682 | 0.064536 | 0.080164 | 0.00049131 | 0.0011386 | 0.0078828 | 0.021545 | 0.01123 | -1.3944 | 0.06887 | -0.0069044 | 0.012544 | 0.0023285 | 3.0396 | 120.8679 | -0.45319 | 120.8725 | 1.3184 | 0.17395 | 1.1581 | 3.067 | 120.8588 | -0.55389 | 120.6253 | 0.064087 | 1.3504 | 0.11444 | 0.13275 | -0.091553 | -0.086975 | 1.9043 | 1.7441 | 0.75989 | 1.6113 | 0.62714 | 0.032043 | -0.10071 | -0.33417 | 0.65002 | 0.70038 | 1.9363 | 0.66834 | 1.9043 | 1.7715 | 121.3257 | 0.61798 | 121.1792 | 121.3211 | 121.4127 | 121.4539 | 121.4447 | -121.4127 | -121.5134 | 121.4584 | 121.2112 | 3.6255 | 3.653
2229.4062 | 121.582 | -0.55847 | 120.9686 | 0.0019074 | 6.7804 | 0.067313 | 0.08166 | 0.0024139 | 0.002634 | 0.010873 | -0.0028687 | 0.0069576 | -1.3955 | 0.069724 | -0.00049559 | 0.01468 | 0.0023285 | 3.0487 | 120.8954 | -0.45319 | 120.8725 | 1.2909 | 0.13733 | 1.1536 | 3.1265 | 120.7855 | -0.50354 | 120.7031 | 0.13733 | 1.4465 | 0.18768 | 0.10529 | -0.073242 | -0.09613 | 1.8494 | 1.712 | 0.6958 | 1.6067 | 0.59052 | 0.054932 | -0.18311 | -0.2655 | 0.6958 | 0.74615 | 2.005 | 0.69122 | 1.9501 | 1.7441 | 121.3257 | 0.64087 | 121.2067 | 121.3486 | 121.2891 | 121.4539 | 121.344 | -121.4218 | -121.4722 | 121.431 | 121.2616 | 3.6072 | 3.685
2231.1094 | 121.6507 | -0.54932 | 120.932 | 0.0019074 | 6.7881 | 0.06539 | 0.080164 | -0.00014949 | -0.0016384 | 0.01066 | -0.0028687 | 0.0080258 | -1.3974 | 0.072288 | -0.003059 | 0.014253 | 0.0057465 | 3.0487 | 120.8038 | -0.44403 | 120.9137 | 1.3824 | 0.2243 | 1.2222 | 3.1677 | 120.7855 | -0.5127 | 120.7352 | 0.19226 | 1.5564 | 0.2243 | 0.10529 | -0.12817 | -0.018311 | 1.9318 | 1.7715 | 0.77362 | 1.6663 | 0.66834 | 0.036621 | -0.14648 | -0.19684 | 0.74158 | 0.77362 | 2.1057 | 0.737 | 2.0691 | 1.8265 | 121.3577 | 0.70496 | 121.2479 | 121.2479 | 121.2982 | 121.3531 | 121.3348 | -121.376 | -121.4447 | 121.463 | 121.2845 | 3.598 | 3.717
2232.875 | 121.5958 | -0.55847 | 120.9412 | 0.017166 | 6.7981 | 0.065817 | 0.079523 | -0.0035675 | 0.0017796 | 0.01066 | 0.0062865 | 0.0086666 | -1.3948 | 0.07357 | -0.0034864 | 0.015535 | 0.0029693 | 3.0487 | 120.8588 | -0.4715 | 120.9274 | 1.3779 | 0.20599 | 1.236 | 3.1769 | 120.7718 | -0.52643 | 120.7077 | 0.16022 | 1.5381 | 0.20142 | 0.086975 | -0.082397 | -0.013733 | 1.9363 | 1.7944 | 0.76447 | 1.7075 | 0.67749 | 0.032044 | -0.16937 | -0.23346 | 0.71869 | 0.75989 | 2.0966 | 0.72784 | 2.0645 | 1.8494 | 121.3989 | 0.68664 | 121.2341 | 121.3303 | 121.2982 | 121.4172 | 121.3303 | -121.4127 | -121.4676 | 121.4859 | 121.2662 | 3.6072 | 3.7354
2234.5781 | 121.637 | -0.56763 | 120.9137 | 0.0019074 | 6.8071 | 0.065176 | 0.079096 | 6.4114e-05 | 0.0013522 | 0.012796 | -0.0028687 | 0.0061032 | -1.3989 | 0.069084 | -0.0051954 | 0.015107 | 0.00083309 | 3.0579 | 120.7855 | -0.43488 | 120.9549 | 1.474 | 0.27466 | 1.2863 | 3.2639 | 120.7672 | -0.49439 | 120.7352 | 0.23346 | 1.6663 | 0.26093 | 0.13275 | -0.12817 | 0.041199 | 2.0416 | 1.8539 | 0.84228 | 1.7212 | 0.70953 | 0.073242 | -0.14648 | -0.17853 | 0.80109 | 0.82855 | 2.2339 | 0.75531 | 2.1606 | 1.9089 | 121.3898 | 0.72784 | 121.2296 | 121.2204 | 121.2616 | 121.3531 | 121.3348 | -121.3486 | -121.4081 | 121.5225 | 121.3028 | 3.6255 | 3.8315
2236.3438 | 121.5042 | -0.58594 | 120.9503 | -0.0057221 | 6.7975 | 0.066031 | 0.085505 | -0.0046357 | 0.0011386 | 0.0095918 | -0.0028687 | 0.010803 | -1.3952 | 0.077415 | -0.0041272 | 0.013612 | 0.0010467 | 3.0121 | 120.8771 | -0.46234 | 120.8588 | 1.3367 | 0.13733 | 1.181 | 3.1769 | 120.7764 | -0.54474 | 120.639 | 0.10071 | 1.5564 | 0.17853 | 0.1236 | -0.073242 | -0.091552 | 1.9226 | 1.767 | 0.72327 | 1.6434 | 0.59967 | 0.041198 | -0.17395 | -0.31128 | 0.68665 | 0.76447 | 2.1423 | 0.72327 | 2.1011 | 1.799 | 121.3211 | 0.64545 | 121.1838 | 121.3394 | 121.3211 | 121.463 | 121.3623 | -121.4127 | -121.4951 | 121.4447 | 121.225 | 3.598 | 3.7628
2238.125 | 121.5546 | -0.59052 | 120.9457 | 0.017166 | 6.8103 | 0.064749 | 0.083582 | -0.00079049 | 0.0015658 | 0.011514 | 0.0062865 | 0.011657 | -1.3957 | 0.066734 | -0.0058362 | 0.012544 | 0.0023285 | 3.0167 | 120.8405 | -0.49439 | 120.8862 | 1.3779 | 0.1831 | 1.2405 | 3.2272 | 120.7993 | -0.54474 | 120.6711 | 0.16479 | 1.6617 | 0.21973 | 0.09613 | -0.10529 | -0.05951 | 1.9684 | 1.8311 | 0.77362 | 1.7349 | 0.67749 | 0.045776 | -0.14648 | -0.27466 | 0.75531 | 0.81024 | 2.2522 | 0.76447 | 2.2064 | 1.8723 | 121.3806 | 0.70953 | 121.2158 | 121.3348 | 121.344 | 121.431 | 121.3898 | -121.4401 | -121.4905 | 121.4767 | 121.2616 | 3.6072 | 3.8177
2239.9062 | 121.6278 | -0.5722 | 120.9137 | -0.0057221 | 6.8018 | 0.064749 | 0.080164 | -0.0033539 | -0.0016384 | 0.013223 | 0.00018312 | 0.0095212 | -1.3963 | 0.066947 | -0.004768 | 0.014253 | 0.0059601 | 3.0167 | 120.7764 | -0.44861 | 120.9457 | 1.4603 | 0.27466 | 1.2909 | 3.3051 | 120.7306 | -0.49896 | 120.7123 | 0.24719 | 1.7761 | 0.28381 | 0.1236 | -0.13733 | 0.032044 | 2.0325 | 1.8631 | 0.84686 | 1.7395 | 0.72327 | 0.073243 | -0.1831 | -0.20142 | 0.8194 | 0.85602 | 2.3483 | 0.78277 | 2.2751 | 1.9089 | 121.3943 | 0.74615 | 121.2112 | 121.225 | 121.2296 | 121.3486 | 121.3028 | -121.3623 | -121.4127 | 121.5179 | 121.2845 | 3.5889 | 3.8773
2241.6719 | 121.6232 | -0.57678 | 120.8954 | 0.070572 | 6.8003 | 0.069663 | 0.0823 | 0.0024139 | 0.002634 | 0.013223 | 0.015442 | 0.010589 | -1.395 | 0.075279 | -0.0028454 | 0.015748 | 0.0014741 | 3.035 | 120.8359 | -0.4715 | 120.9503 | 1.4786 | 0.25635 | 1.3092 | 3.3646 | 120.7489 | -0.52643 | 120.7214 | 0.25635 | 1.799 | 0.28839 | 0.10529 | -0.05951 | 0.054931 | 2.0554 | 1.886 | 0.83313 | 1.7807 | 0.72785 | 0.050354 | -0.14648 | -0.17395 | 0.83313 | 0.86517 | 2.3758 | 0.81482 | 2.3254 | 1.9501 | 121.4218 | 0.78278 | 121.2479 | 121.3074 | 121.2753 | 121.4127 | 121.3257 | -121.3669 | -121.4218 | 121.5271 | 121.2982 | 3.6118 | 3.9413
2243.4375 | 121.6278 | -0.55847 | 120.9 | -0.0057221 | 6.8069 | 0.065817 | 0.082514 | 0.00049131 | -0.00014304 | 0.011514 | 0.030701 | 0.0095212 | -1.3933 | 0.078269 | -0.00092279 | 0.014894 | 0.0055329 | 3.0258 | 120.813 | -0.44861 | 120.9366 | 1.442 | 0.23804 | 1.3184 | 3.4058 | 120.7718 | -0.54932 | 120.7443 | 0.27008 | 1.8906 | 0.32044 | 0.10986 | -0.086975 | 0.036621 | 2.0004 | 1.8768 | 0.79651 | 1.767 | 0.68664 | 0.009156 | -0.12817 | -0.15564 | 0.82855 | 0.87891 | 2.449 | 0.86975 | 2.4399 | 1.8906 | 121.3852 | 0.8194 | 121.2936 | 121.2616 | 121.3211 | 121.3715 | 121.3303 | -121.3486 | -121.4493 | 121.4951 | 121.3028 | 3.5843 | 3.9642
2245.1562 | 121.5134 | -0.61798 | 120.9686 | -0.020981 | 6.8058 | 0.064322 | 0.081019 | -0.0022857 | 0.00071136 | 0.0098054 | -0.0059205 | 0.0075986 | -1.3959 | 0.072288 | -0.008186 | 0.012544 | 0.0066009 | 2.9709 | 120.7718 | -0.45776 | 120.8405 | 1.3641 | 0.21057 | 1.2451 | 3.2455 | 120.7764 | -0.54474 | 120.607 | 0.16479 | 1.8127 | 0.21515 | 0.16022 | -0.19684 | -0.12817 | 1.9821 | 1.8631 | 0.82855 | 1.7029 | 0.66834 | 0.073242 | -0.19226 | -0.36163 | 0.78278 | 0.83313 | 2.4307 | 0.75989 | 2.3575 | 1.8219 | 121.2982 | 0.70953 | 121.1517 | 121.2296 | 121.3211 | 121.3898 | 121.3943 | -121.4264 | -121.5134 | 121.4584 | 121.225 | 3.5889 | 3.8635
2246.9219 | 121.5729 | -0.59052 | 120.9366 | -0.0057221 | 6.8163 | 0.064749 | 0.080805 | -0.0071991 | 0.00049776 | 0.01301 | 0.00018312 | 0.0099484 | -1.3967 | 0.065452 | -0.0073316 | 0.012117 | 0.0057465 | 2.9617 | 120.7626 | -0.47607 | 120.9 | 1.442 | 0.2655 | 1.3229 | 3.3371 | 120.7581 | -0.54016 | 120.6482 | 0.24719 | 1.9318 | 0.29297 | 0.11444 | -0.17395 | -0.036621 | 2.0325 | 1.9135 | 0.85602 | 1.799 | 0.74158 | 0.050354 | -0.17853 | -0.28839 | 0.83771 | 0.88348 | 2.5223 | 0.83313 | 2.4719 | 1.918 | 121.376 | 0.78735 | 121.1884 | 121.2387 | 121.2982 | 121.3531 | 121.3486 | -121.4127 | -121.4767 | 121.4905 | 121.2387 | 3.5522 | 3.9276
2248.625 | 121.5042 | -0.61798 | 120.9412 | -0.0057221 | 6.824 | 0.064536 | 0.081019 | 0.0015595 | -0.00057044 | 0.012155 | 0.00018312 | 0.0078122 | -1.3933 | 0.068229 | -0.0062634 | 0.013398 | 0.0063873 | 2.8839 | 120.7901 | -0.48981 | 120.7993 | 1.3321 | 0.16479 | 1.2497 | 3.2776 | 120.7626 | -0.56305 | 120.5933 | 0.16022 | 1.9043 | 0.24719 | 0.12817 | -0.15106 | -0.14191 | 1.9501 | 1.8677 | 0.78278 | 1.7395 | 0.6546 | 0.054932 | -0.17853 | -0.3479 | 0.7782 | 0.86517 | 2.5223 | 0.81024 | 2.4673 | 1.8219 | 121.2891 | 0.72327 | 121.1563 | 121.2799 | 121.3257 | 121.4081 | 121.3806 | -121.431 | -121.5042 | 121.4172 | 121.2112 | 3.5019 | 3.8956
2250.4062 | 121.5271 | -0.61798 | 120.9366 | 0.040054 | 6.8297 | 0.064322 | 0.083582 | -0.00036309 | 0.00071136 | 0.01301 | 0.0093383 | 0.011871 | -1.3927 | 0.069511 | -0.0041272 | 0.014253 | 0.0036103 | 2.8976 | 120.8267 | -0.52185 | 120.8038 | 1.3138 | 0.17853 | 1.2772 | 3.3325 | 120.7855 | -0.59967 | 120.6024 | 0.19684 | 1.9775 | 0.27466 | 0.09613 | -0.10986 | -0.13275 | 1.9318 | 1.8951 | 0.79651 | 1.799 | 0.70038 | 0.018311 | -0.15106 | -0.33417 | 0.81482 | 0.89264 | 2.5955 | 0.87433 | 2.5772 | 1.8356 | 121.3257 | 0.79651 | 121.2021 | 121.3486 | 121.3852 | 121.4447 | 121.4035 | -121.4584 | -121.5363 | 121.4218 | 121.2204 | 3.5156 | 3.9505
2252.125 | 121.4905 | -0.63171 | 120.9366 | 0.0019074 | 6.8041 | 0.065176 | 0.087427 | 0.0013459 | 0.0015658 | 0.011514 | -0.0059205 | 0.011444 | -1.3961 | 0.062675 | 0.001427 | 0.013185 | 0.0040375 | 2.8656 | 120.8359 | -0.50812 | 120.7535 | 1.2817 | 0.1236 | 1.2497 | 3.3051 | 120.7764 | -0.54474 | 120.5841 | 0.16022 | 1.9913 | 0.27466 | 0.1236 | -0.10071 | -0.1831 | 1.9135 | 1.8814 | 0.75531 | 1.7578 | 0.63171 | 0.086975 | -0.16022 | -0.35248 | 0.79193 | 0.90637 | 2.623 | 0.8194 | 2.536 | 1.7899 | 121.2616 | 0.70496 | 121.1288 | 121.344 | 121.3211 | 121.4676 | 121.4081 | -121.4447 | -121.4813 | 121.3852 | 121.2158 | 3.4973 | 3.9368
2253.9062 | 121.5408 | -0.6134 | 120.8771 | 0.032425 | 6.8131 | 0.06539 | 0.085291 | 0.0028411 | 0.0015658 | 0.011942 | 0.0093383 | 0.01123 | -1.3937 | 0.065666 | -0.004768 | 0.013398 | 0.0066009 | 2.9022 | 120.8313 | -0.53101 | 120.8405 | 1.3916 | 0.21515 | 1.3275 | 3.4241 | 120.7672 | -0.58136 | 120.6345 | 0.27008 | 2.1286 | 0.34332 | 0.082397 | -0.045776 | -0.036621 | 2.005 | 1.9409 | 0.82855 | 1.8585 | 0.74616 | 0.032043 | -0.10986 | -0.24262 | 0.88348 | 0.95673 | 2.742 | 0.92468 | 2.71 | 1.9226 | 121.3715 | 0.85144 | 121.2158 | 121.3623 | 121.3486 | 121.4447 | 121.3806 | -121.4081 | -121.4584 | 121.4539 | 121.2479 | 3.5156 | 4.0375
2255.625 | 121.4859 | -0.62714 | 120.9183 | -0.0057221 | 6.8107 | 0.06539 | 0.083369 | -0.0010041 | 0.0017796 | 0.012582 | -0.0028687 | 0.010589 | -1.395 | 0.072715 | -0.0026318 | 0.013398 | 0.0038239 | 2.8244 | 120.8313 | -0.52185 | 120.7535 | 1.2909 | 0.09613 | 1.236 | 3.3417 | 120.7535 | -0.56305 | 120.5841 | 0.19226 | 2.1149 | 0.31586 | 0.10529 | -0.086975 | -0.16479 | 1.918 | 1.8631 | 0.72327 | 1.7578 | 0.61798 | 0.064087 | -0.16479 | -0.33417 | 0.8194 | 0.94299 | 2.742 | 0.87891 | 2.6779 | 1.8127 | 121.2753 | 0.75531 | 121.1472 | 121.3531 | 121.3165 | 121.4584 | 121.3806 | -121.4401 | -121.4813 | 121.3806 | 121.2112 | 3.4515 | 3.9688
2257.3906 | 121.4996 | -0.63629 | 120.9091 | -0.020981 | 6.8039 | 0.067313 | 0.083369 | -0.0014313 | 0.0015658 | 0.013651 | 0.021545 | 0.012939 | -1.3935 | 0.069938 | -0.0066906 | 0.01233 | 0.0057465 | 2.861 | 120.8176 | -0.55847 | 120.8084 | 1.3779 | 0.20142 | 1.3321 | 3.4287 | 120.7901 | -0.61798 | 120.5612 | 0.2243 | 2.2202 | 0.32501 | 0.07782 | -0.091553 | -0.10071 | 2.0142 | 1.9684 | 0.83771 | 1.8906 | 0.75989 | 0.018311 | -0.11902 | -0.3479 | 0.8606 | 0.9613 | 2.8564 | 0.94299 | 2.8381 | 1.9363 | 121.3669 | 0.84228 | 121.1792 | 121.376 | 121.4081 | 121.4539 | 121.4264 | -121.4676 | -121.5271 | 121.4447 | 121.1975 | 3.4973 | 4.0649
2259.1094 | 121.5271 | -0.63171 | 120.8862 | -0.013352 | 6.7983 | 0.065176 | 0.083582 | -0.0024995 | 0.0028476 | 0.012582 | -0.0059205 | 0.0099484 | -1.3959 | 0.071861 | -0.00070919 | 0.014253 | 0.0048919 | 2.829 | 120.7855 | -0.5127 | 120.7397 | 1.3412 | 0.13275 | 1.2634 | 3.4424 | 120.7306 | -0.55847 | 120.5933 | 0.26093 | 2.2888 | 0.37537 | 0.11902 | -0.10071 | -0.14648 | 1.973 | 1.8951 | 0.76446 | 1.7761 | 0.64545 | 0.073242 | -0.15564 | -0.29297 | 0.89264 | 1.0071 | 2.9205 | 0.93384 | 2.8473 | 1.8539 | 121.2524 | 0.8194 | 121.1517 | 121.2982 | 121.2891 | 121.4172 | 121.3623 | -121.3989 | -121.4447 | 121.3715 | 121.225 | 3.4607 | 4.0741
2260.8906 | 121.4951 | -0.65918 | 120.8725 | -0.0057221 | 6.8 | 0.061331 | 0.082514 | -0.0027131 | -0.00035684 | 0.013651 | -0.0028687 | 0.011016 | -1.395 | 0.07357 | -0.0066906 | 0.014253 | 0.0042511 | 2.8793 | 120.7397 | -0.50354 | 120.8084 | 1.4282 | 0.21515 | 1.3412 | 3.4927 | 120.7077 | -0.5722 | 120.5521 | 0.28839 | 2.3758 | 0.35248 | 0.15564 | -0.13275 | -0.064087 | 2.0874 | 2.0004 | 0.87433 | 1.8448 | 0.71869 | 0.086975 | -0.16479 | -0.32043 | 0.94757 | 1.0117 | 3.035 | 0.92468 | 2.948 | 1.9318 | 121.312 | 0.8606 | 121.1243 | 121.2433 | 121.2799 | 121.3989 | 121.3669 | -121.376 | -121.4447 | 121.4676 | 121.2112 | 3.5385 | 4.1519
2262.6562 | 121.5454 | -0.62714 | 120.8954 | 0.040054 | 6.8041 | 0.065176 | 0.084009 | -0.00079049 | 0.0030612 | 0.01066 | 0.01239 | 0.011016 | -1.3944 | 0.069297 | -0.0056226 | 0.013826 | 0.0063873 | 2.8839 | 120.7764 | -0.54016 | 120.7901 | 1.3916 | 0.21057 | 1.3504 | 3.5568 | 120.7123 | -0.59052 | 120.5978 | 0.31586 | 2.4445 | 0.41199 | 0.086975 | -0.11902 | -0.10529 | 2.0187 | 1.9775 | 0.83771 | 1.8906 | 0.75073 | 0.036621 | -0.18311 | -0.29755 | 0.94299 | 1.0391 | 3.0716 | 1.0025 | 3.035 | 1.9318 | 121.3303 | 0.90637 | 121.1884 | 121.3165 | 121.3028 | 121.4035 | 121.3394 | -121.4355 | -121.4859 | 121.4172 | 121.225 | 3.511 | 4.184
2264.4219 | 121.5775 | -0.63171 | 120.8359 | 0.0019074 | 6.8127 | 0.066245 | 0.083369 | -0.0027131 | 0.0022068 | 0.012369 | 0.00018312 | 0.01123 | -1.3944 | 0.072074 | -0.0043408 | 0.015321 | 0.0070283 | 2.8473 | 120.7489 | -0.52643 | 120.7809 | 1.4053 | 0.2243 | 1.3824 | 3.566 | 120.6802 | -0.57678 | 120.6253 | 0.37994 | 2.5864 | 0.45319 | 0.10529 | -0.086975 | -0.054931 | 2.037 | 2.0142 | 0.85602 | 1.9089 | 0.75073 | 0.054932 | -0.15564 | -0.21057 | 1.0117 | 1.0849 | 3.2181 | 1.03 | 3.1631 | 1.9318 | 121.3074 | 0.95673 | 121.2021 | 121.2753 | 121.257 | 121.3806 | 121.312 | -121.3623 | -121.4127 | 121.4127 | 121.257 | 3.479 | 4.1977
2266.2031 | 121.4905 | -0.68207 | 120.8725 | 0.070572 | 6.8137 | 0.064749 | 0.083582 | 0.00027771 | 0.0019932 | 0.013651 | 0.018494 | 0.014434 | -1.3935 | 0.068656 | -0.0073316 | 0.013612 | 0.0085235 | 2.829 | 120.7993 | -0.58136 | 120.7352 | 1.3824 | 0.19226 | 1.3504 | 3.5568 | 120.7306 | -0.63171 | 120.5109 | 0.28381 | 2.5635 | 0.39368 | 0.10071 | -0.073243 | -0.13733 | 2.0645 | 2.0325 | 0.87433 | 1.9318 | 0.77362 | 0.050354 | -0.14191 | -0.36163 | 0.96588 | 1.0757 | 3.2455 | 1.0254 | 3.1952 | 1.9638 | 121.3165 | 0.91553 | 121.1426 | 121.3806 | 121.3623 | 121.4813 | 121.4127 | -121.4539 | -121.5042 | 121.4172 | 121.1929 | 3.511 | 4.2389
2267.9062 | 121.5271 | -0.6546 | 120.8496 | 0.024795 | 6.812 | 0.064749 | 0.085718 | 0.0030547 | 0.0013522 | 0.012369 | 0.01239 | 0.014221 | -1.3952 | 0.067802 | -0.0051954 | 0.01468 | 0.0042511 | 2.8656 | 120.7672 | -0.5722 | 120.7993 | 1.4145 | 0.20142 | 1.3824 | 3.653 | 120.7077 | -0.6134 | 120.5795 | 0.36163 | 2.6733 | 0.45319 | 0.082397 | -0.082397 | -0.050354 | 2.0691 | 2.037 | 0.85602 | 1.9547 | 0.77362 | 0.041199 | -0.14191 | -0.27008 | 1.0162 | 1.1078 | 3.3279 | 1.0666 | 3.2867 | 1.9867 | 121.3715 | 0.97504 | 121.1929 | 121.3394 | 121.3211 | 121.4218 | 121.3623 | -121.4218 | -121.463 | 121.4539 | 121.2341 | 3.5202 | 4.3076
2269.6875 | 121.4767 | -0.67291 | 120.9045 | -0.013352 | 6.8109 | 0.065176 | 0.083582 | 6.4114e-05 | 0.00028416 | 0.011301 | -0.0028687 | 0.010803 | -1.3961 | 0.063743 | -0.0075452 | 0.013612 | 0.00061949 | 2.7786 | 120.7581 | -0.55847 | 120.7077 | 1.3641 | 0.15564 | 1.3229 | 3.5889 | 120.7031 | -0.59967 | 120.5063 | 0.31586 | 2.7191 | 0.43488 | 0.11444 | -0.14648 | -0.19684 | 2.037 | 1.9958 | 0.82855 | 1.8814 | 0.71411 | 0.073243 | -0.20142 | -0.39825 | 0.98877 | 1.1078 | 3.392 | 1.0345 | 3.3188 | 1.9226 | 121.2662 | 0.91553 | 121.106 | 121.3165 | 121.3028 | 121.431 | 121.376 | -121.463 | -121.5042 | 121.3806 | 121.1792 | 3.4515 | 4.2618
2271.4531 | 121.5637 | -0.67749 | 120.8359 | 0.024795 | 6.8124 | 0.064963 | 0.085505 | -0.0016449 | 0.0017796 | 0.015146 | 0.0062865 | 0.01123 | -1.3933 | 0.081901 | -0.0034864 | 0.015107 | 0.0089509 | 2.8427 | 120.7306 | -0.52185 | 120.7901 | 1.4511 | 0.2243 | 1.4145 | 3.6987 | 120.639 | -0.59967 | 120.575 | 0.39825 | 2.861 | 0.5127 | 0.15564 | -0.10528 | -0.045776 | 2.1286 | 2.092 | 0.90179 | 1.9363 | 0.74615 | 0.07782 | -0.19684 | -0.26093 | 1.0757 | 1.1902 | 3.5385 | 1.1124 | 3.4607 | 1.973 | 121.312 | 0.99792 | 121.1746 | 121.2524 | 121.2387 | 121.4081 | 121.3165 | -121.3577 | -121.4355 | 121.4676 | 121.2524 | 3.5202 | 4.3762
2273.1562 | 121.6049 | -0.63629 | 120.7993 | 0.0019074 | 6.7986 | 0.066458 | 0.084864 | -0.0042083 | 0.0013522 | 0.013223 | -0.0028687 | 0.010589 | -1.3946 | 0.070152 | -0.0045544 | 0.016816 | 0.0066009 | 2.8198 | 120.6985 | -0.54016 | 120.7947 | 1.4877 | 0.27008 | 1.4328 | 3.7949 | 120.6482 | -0.58136 | 120.6207 | 0.48065 | 3.0075 | 0.58594 | 0.096131 | -0.10071 | -0.004577 | 2.124 | 2.0691 | 0.90637 | 1.973 | 0.81024 | 0.054932 | -0.15106 | -0.17853 | 1.1169 | 1.2222 | 3.6438 | 1.1673 | 3.5889 | 2.0279 | 121.3348 | 1.062 | 121.2021 | 121.2387 | 121.2296 | 121.3348 | 121.2845 | -121.3394 | -121.3806 | 121.431 | 121.257 | 3.4561 | 4.4312
2274.9219 | 121.6187 | -0.65002 | 120.7993 | -0.013352 | 6.7853 | 0.063895 | 0.084009 | 0.00049131 | 0.00028416 | 0.0098054 | -0.0028687 | 0.0097348 | -1.3948 | 0.070152 | -0.0062634 | 0.01703 | 0.0059601 | 2.8564 | 120.6619 | -0.53101 | 120.8588 | 1.5472 | 0.28381 | 1.474 | 3.8818 | 120.6299 | -0.58594 | 120.6253 | 0.52643 | 3.0945 | 0.59509 | 0.11902 | -0.13733 | 0.05951 | 2.1973 | 2.124 | 0.93384 | 2.005 | 0.81482 | 0.064087 | -0.16937 | -0.17395 | 1.1765 | 1.2451 | 3.7445 | 1.181 | 3.6804 | 2.0782 | 121.3898 | 1.1124 | 121.2112 | 121.1929 | 121.2158 | 121.3119 | 121.2799 | -121.3303 | -121.3852 | 121.5088 | 121.2753 | 3.5065 | 4.5319
2276.6875 | 121.4676 | -0.69122 | 120.8176 | 0.0095369 | 6.7979 | 0.067313 | 0.086573 | -0.00014949 | 0.0011386 | 0.011301 | 0.00018312 | 0.01358 | -1.3929 | 0.075706 | 0.00014521 | 0.016603 | 0.0068145 | 2.774 | 120.7581 | -0.5722 | 120.6848 | 1.3641 | 0.10529 | 1.3367 | 3.7079 | 120.6711 | -0.61798 | 120.4971 | 0.39368 | 3.0167 | 0.51727 | 0.11902 | -0.059509 | -0.13275 | 2.0554 | 2.0279 | 0.79651 | 1.9089 | 0.67749 | 0.073242 | -0.14648 | -0.32044 | 1.0849 | 1.2085 | 3.7079 | 1.1353 | 3.6346 | 1.9363 | 121.257 | 1.0117 | 121.1151 | 121.3303 | 121.2891 | 121.4493 | 121.3623 | -121.3898 | -121.4355 | 121.376 | 121.1884 | 3.4653 | 4.3991
2278.4688 | 121.5134 | -0.68207 | 120.8542 | 0.055313 | 6.8039 | 0.064963 | 0.08465 | 0.0060455 | -0.00035684 | 0.013437 | 0.015442 | 0.014434 | -1.3916 | 0.06887 | -0.007118 | 0.013398 | 0.0089509 | 2.8198 | 120.7352 | -0.59052 | 120.7443 | 1.442 | 0.20599 | 1.4099 | 3.8223 | 120.7306 | -0.65002 | 120.5246 | 0.44861 | 3.154 | 0.5722 | 0.091553 | -0.11902 | -0.10986 | 2.124 | 2.092 | 0.88806 | 2.0004 | 0.79651 | 0.032044 | -0.1236 | -0.32959 | 1.1307 | 1.2543 | 3.8361 | 1.2222 | 3.804 | 2.0325 | 121.3348 | 1.0986 | 121.1746 | 121.3257 | 121.3806 | 121.4172 | 121.4127 | -121.4447 | -121.5042 | 121.4264 | 121.2067 | 3.5019 | 4.5044
2280.25 | 121.5912 | -0.62714 | 120.813 | -0.0057221 | 6.8154 | 0.064108 | 0.0823 | -0.0016449 | 0.0017796 | 0.013437 | -0.0059205 | 0.010162 | -1.3987 | 0.071006 | -0.005409 | 0.015962 | 0.0072419 | 2.7969 | 120.6894 | -0.53101 | 120.8038 | 1.506 | 0.27924 | 1.4832 | 3.9322 | 120.6436 | -0.59052 | 120.6253 | 0.57678 | 3.3966 | 0.67749 | 0.09613 | -0.1236 | -0.009155 | 2.1332 | 2.1103 | 0.90637 | 2.0142 | 0.81024 | 0.036621 | -0.16937 | -0.18768 | 1.2039 | 1.3046 | 4.0237 | 1.268 | 3.9871 | 2.037 | 121.3348 | 1.1673 | 121.2158 | 121.2204 | 121.2341 | 121.3165 | 121.2708 | -121.344 | -121.4035 | 121.431 | 121.2524 | 3.4241 | 4.5593
2281.9531 | 121.4584 | -0.67749 | 120.8633 | -0.0057221 | 6.8276 | 0.064963 | 0.083796 | 0.0047637 | 0.0019932 | 0.013651 | 0.00018312 | 0.014434 | -1.3957 | 0.070579 | -0.003059 | 0.016175 | 0.0066009 | 2.774 | 120.7535 | -0.5722 | 120.694 | 1.3779 | 0.12817 | 1.355 | 3.8315 | 120.6757 | -0.61798 | 120.4971 | 0.4303 | 3.2822 | 0.58594 | 0.10529 | -0.10986 | -0.16937 | 2.0554 | 2.0325 | 0.80566 | 1.9272 | 0.70038 | 0.059509 | -0.18768 | -0.36621 | 1.1078 | 1.2634 | 3.9597 | 1.2039 | 3.9001 | 1.9501 | 121.2662 | 1.0483 | 121.1151 | 121.3257 | 121.2936 | 121.431 | 121.3531 | -121.4355 | -121.4813 | 121.3715 | 121.1746 | 3.4515 | 4.509
2283.7344 | 121.463 | -0.69122 | 120.8588 | 0.070572 | 6.8201 | 0.066885 | 0.087214 | -0.0027131 | 0.0019932 | 0.014078 | 0.018494 | 0.014862 | -1.3929 | 0.074851 | -0.005409 | 0.014253 | 0.0089509 | 2.7924 | 120.7626 | -0.62256 | 120.7169 | 1.4374 | 0.19684 | 1.4374 | 3.9276 | 120.7031 | -0.67291 | 120.4834 | 0.48523 | 3.4287 | 0.62256 | 0.068664 | -0.096131 | -0.14191 | 2.1286 | 2.1286 | 0.88806 | 2.0599 | 0.8194 | 0.01831 | -0.15564 | -0.37537 | 1.1765 | 1.3138 | 4.1199 | 1.2955 | 4.1016 | 2.0599 | 121.3394 | 1.1581 | 121.1563 | 121.3852 | 121.376 | 121.4539 | 121.3943 | -121.4813 | -121.5317 | 121.4081 | 121.1746 | 3.4836 | 4.6188
2285.5156 | 121.4401 | -0.68207 | 120.8267 | -0.013352 | 6.8289 | 0.065604 | 0.08465 | 0.0013459 | 0.0013522 | 0.013651 | -0.0028687 | 0.013366 | -1.3955 | 0.063957 | -0.0043408 | 0.01468 | 0.011941 | 2.7374 | 120.7123 | -0.54474 | 120.6802 | 1.387 | 0.13275 | 1.3733 | 3.8956 | 120.6665 | -0.63629 | 120.5017 | 0.47607 | 3.4882 | 0.63171 | 0.13733 | -0.11444 | -0.14648 | 2.0691 | 2.0554 | 0.81482 | 1.918 | 0.67749 | 0.045776 | -0.16022 | -0.32501 | 1.1581 | 1.3138 | 4.1702 | 1.268 | 4.1245 | 1.9318 | 121.225 | 1.1124 | 121.138 | 121.257 | 121.3028 | 121.3943 | 121.3486 | -121.3715 | -121.463 | 121.3623 | 121.1838 | 3.4195 | 4.5776
2287.2969 | 121.5912 | -0.63629 | 120.7581 | -0.013352 | 6.8323 | 0.064108 | 0.082514 | -0.0035675 | 0.0019932 | 0.013223 | -0.0059205 | 0.011657 | -1.3955 | 0.077628 | -0.004768 | 0.015748 | 0.0072419 | 2.8336 | 120.6711 | -0.52185 | 120.8221 | 1.6205 | 0.32044 | 1.5427 | 4.1473 | 120.607 | -0.58594 | 120.6024 | 0.68665 | 3.7903 | 0.7782 | 0.11444 | -0.086975 | 0.064087 | 2.2568 | 2.179 | 0.95673 | 2.0645 | 0.84229 | 0.050355 | -0.15106 | -0.15564 | 1.3229 | 1.4145 | 4.4266 | 1.3641 | 4.3762 | 2.1423 | 121.344 | 1.2726 | 121.1884 | 121.1929 | 121.1929 | 121.3074 | 121.2433 | -121.2799 | -121.344 | 121.4584 | 121.2387 | 3.4698 | 4.7836
2289.0781 | 121.4813 | -0.68665 | 120.8313 | -0.0057221 | 6.8379 | 0.065604 | 0.085932 | -0.00057689 | 0.0024204 | 0.012369 | -0.0028687 | 0.014007 | -1.394 | 0.07656 | -0.0034864 | 0.01703 | 0.0085235 | 2.7649 | 120.7306 | -0.5722 | 120.6665 | 1.4374 | 0.15106 | 1.3962 | 4.0512 | 120.6436 | -0.62256 | 120.4971 | 0.5722 | 3.7354 | 0.73242 | 0.11444 | -0.10071 | -0.16479 | 2.124 | 2.0828 | 0.83771 | 1.9684 | 0.72327 | 0.064087 | -0.18768 | -0.33417 | 1.2589 | 1.4191 | 4.422 | 1.355 | 4.3579 | 2.0096 | 121.2387 | 1.1948 | 121.1197 | 121.3028 | 121.2662 | 121.4172 | 121.3303 | -121.4035 | -121.4539 | 121.3531 | 121.1838 | 3.4515 | 4.7379
2290.7969 | 121.5637 | -0.6546 | 120.7947 | -0.0057221 | 6.8391 | 0.064108 | 0.082728 | -0.00014949 | -0.00035684 | 0.011301 | -0.0028687 | 0.011016 | -1.3935 | 0.069297 | -0.0077588 | 0.017671 | 0.010019 | 2.8015 | 120.6436 | -0.54016 | 120.7993 | 1.5793 | 0.31128 | 1.5198 | 4.216 | 120.5933 | -0.58594 | 120.5795 | 0.71869 | 3.9825 | 0.83313 | 0.11444 | -0.15106 | 0.004577 | 2.2339 | 2.1744 | 0.96588 | 2.0599 | 0.85144 | 0.068665 | -0.20142 | -0.21515 | 1.3733 | 1.4877 | 4.6371 | 1.4191 | 4.5685 | 2.1194 | 121.3394 | 1.3046 | 121.1655 | 121.1838 | 121.1792 | 121.2982 | 121.2479 | -121.3348 | -121.3806 | 121.4539 | 121.2341 | 3.4561 | 4.8706
2292.5781 | 121.5454 | -0.67291 | 120.7764 | 0.017166 | 6.8398 | 0.066245 | 0.085718 | -0.0029267 | 0.0049838 | 0.015787 | 0.0062865 | 0.015075 | -1.3922 | 0.082969 | -0.0034864 | 0.018312 | 0.0089509 | 2.7649 | 120.6848 | -0.5722 | 120.7306 | 1.5335 | 0.25177 | 1.474 | 4.1977 | 120.6024 | -0.63629 | 120.5338 | 0.68207 | 4.0146 | 0.8194 | 0.10071 | -0.091553 | -0.045776 | 2.2064 | 2.1469 | 0.92468 | 2.0462 | 0.82397 | 0.036621 | -0.17395 | -0.24261 | 1.355 | 1.4923 | 4.6875 | 1.4557 | 4.6509 | 2.1057 | 121.3028 | 1.3184 | 121.17 | 121.257 | 121.2387 | 121.3577 | 121.2753 | -121.3486 | -121.4127 | 121.4035 | 121.2067 | 3.4378 | 4.8706
2294.3594 | 121.6049 | -0.6546 | 120.7901 | -0.0057221 | 6.8308 | 0.064963 | 0.082728 | -0.00057689 | 0.00092496 | 0.012582 | -0.0089723 | 0.013794 | -1.395 | 0.077201 | -0.0060498 | 0.016389 | 0.0072419 | 2.774 | 120.6345 | -0.55389 | 120.7764 | 1.5747 | 0.31128 | 1.561 | 4.335 | 120.6024 | -0.59052 | 120.5795 | 0.80109 | 4.2297 | 0.9201 | 0.10071 | -0.15564 | -0.013733 | 2.2293 | 2.2156 | 0.96588 | 2.1149 | 0.86517 | 0.064087 | -0.18768 | -0.21057 | 1.4557 | 1.5747 | 4.8843 | 1.5106 | 4.8203 | 2.1286 | 121.3303 | 1.3916 | 121.17 | 121.1884 | 121.1929 | 121.2891 | 121.257 | -121.344 | -121.3806 | 121.431 | 121.2341 | 3.4287 | 4.9896
2296.1562 | 121.5729 | -0.66376 | 120.7489 | 0.062942 | 6.8351 | 0.068167 | 0.088923 | 0.0022003 | 0.0045566 | 0.015787 | 0.018494 | 0.016998 | -1.3944 | 0.075065 | -0.0022046 | 0.018739 | 0.0089509 | 2.8198 | 120.6619 | -0.59509 | 120.813 | 1.6159 | 0.31128 | 1.5472 | 4.4403 | 120.5978 | -0.65918 | 120.5841 | 0.80566 | 4.303 | 0.93842 | 0.068664 | -0.086975 | 0.064087 | 2.2797 | 2.211 | 0.97504 | 2.1423 | 0.90637 | 0.004577 | -0.15106 | -0.16479 | 1.4694 | 1.6022 | 4.9667 | 1.5976 | 4.9622 | 2.211 | 121.4081 | 1.4648 | 121.2433 | 121.257 | 121.257 | 121.3257 | 121.2616 | -121.344 | -121.4081 | 121.4767 | 121.2479 | 3.4836 | 5.1041
2297.9375 | 121.4447 | -0.70953 | 120.7855 | -0.0057221 | 6.8351 | 0.066245 | 0.086359 | 0.00070491 | 0.0034884 | 0.011087 | -0.0028687 | 0.016143 | -1.3914 | 0.081046 | -0.0043408 | 0.016603 | 0.0091645 | 2.6962 | 120.6757 | -0.57678 | 120.6573 | 1.4328 | 0.14648 | 1.4236 | 4.3076 | 120.6345 | -0.65002 | 120.4468 | 0.69122 | 4.2801 | 0.84686 | 0.13275 | -0.10986 | -0.12817 | 2.1423 | 2.1332 | 0.85602 | 2.0004 | 0.72327 | 0.05951 | -0.15106 | -0.33875 | 1.4008 | 1.5564 | 4.9896 | 1.4969 | 4.9301 | 2.0096 | 121.2341 | 1.3412 | 121.0968 | 121.2524 | 121.2845 | 121.3852 | 121.344 | -121.3623 | -121.4355 | 121.3669 | 121.1563 | 3.4058 | 5.0171
2299.6406 | 121.4767 | -0.71869 | 120.7855 | 0.0095369 | 6.8334 | 0.066031 | 0.087214 | 0.0013459 | 0.002634 | 0.013651 | 0.00018312 | 0.017425 | -1.3927 | 0.079337 | -0.0058362 | 0.016603 | 0.0093781 | 2.7008 | 120.6894 | -0.59509 | 120.6894 | 1.4969 | 0.19684 | 1.4511 | 4.4357 | 120.6207 | -0.63629 | 120.4834 | 0.78278 | 4.4449 | 0.92468 | 0.1236 | -0.09613 | -0.09613 | 2.2156 | 2.1698 | 0.91553 | 2.0462 | 0.79193 | 0.082397 | -0.16479 | -0.30212 | 1.5015 | 1.6434 | 5.1636 | 1.561 | 5.0812 | 2.092 | 121.2845 | 1.4191 | 121.1197 | 121.2845 | 121.257 | 121.4081 | 121.3394 | -121.3806 | -121.4218 | 121.4081 | 121.2021 | 3.4195 | 5.1544
2301.3438 | 121.55 | -0.6546 | 120.7443 | 0.040054 | 6.8417 | 0.067099 | 0.084223 | -0.0014313 | 0.0041294 | 0.011942 | 0.024597 | 0.015289 | -1.3918 | 0.076347 | -0.0034864 | 0.016816 | 0.010019 | 2.742 | 120.7031 | -0.58136 | 120.7947 | 1.6342 | 0.29755 | 1.561 | 4.5822 | 120.5978 | -0.65918 | 120.5383 | 0.87891 | 4.6417 | 1.0254 | 0.073242 | -0.041199 | 0.050354 | 2.2888 | 2.2156 | 0.95215 | 2.1423 | 0.87891 | -0.004578 | -0.14649 | -0.20599 | 1.5335 | 1.68 | 5.2963 | 1.6846 | 5.3009 | 2.2156 | 121.376 | 1.5381 | 121.1975 | 121.2845 | 121.257 | 121.3577 | 121.2524 | -121.3257 | -121.4035 | 121.4493 | 121.1929 | 3.3966 | 5.2368
2303.125 | 121.5729 | -0.66376 | 120.7901 | -0.013352 | 6.8404 | 0.066245 | 0.083796 | -0.0012177 | 0.0022068 | 0.011087 | 0.00018312 | 0.014007 | -1.394 | 0.08596 | -0.0045544 | 0.014894 | 0.0091645 | 2.6413 | 120.6619 | -0.56305 | 120.7077 | 1.5427 | 0.2655 | 1.5335 | 4.6097 | 120.5704 | -0.62714 | 120.5338 | 0.94299 | 4.8111 | 1.0757 | 0.10071 | -0.12817 | -0.082397 | 2.2064 | 2.1973 | 0.92926 | 2.0966 | 0.82855 | 0.036621 | -0.21973 | -0.25635 | 1.6067 | 1.7395 | 5.4749 | 1.7029 | 5.4382 | 2.1057 | 121.2708 | 1.5701 | 121.1609 | 121.225 | 121.1975 | 121.3257 | 121.2341 | -121.3531 | -121.4172 | 121.3715 | 121.1975 | 3.3051 | 5.2734
2304.9062 | 121.5271 | -0.68665 | 120.7352 | 0.032425 | 6.8483 | 0.064536 | 0.086146 | -0.0024995 | 0.0041294 | 0.01536 | 0.0062865 | 0.015503 | -1.3937 | 0.083824 | -0.004768 | 0.015748 | 0.0072419 | 2.6321 | 120.639 | -0.60883 | 120.7031 | 1.5564 | 0.27008 | 1.5198 | 4.6463 | 120.575 | -0.65002 | 120.5063 | 0.92468 | 4.9026 | 1.0941 | 0.07782 | -0.09613 | -0.032043 | 2.243 | 2.2064 | 0.95673 | 2.1286 | 0.87891 | 0.036622 | -0.16022 | -0.22888 | 1.6113 | 1.7807 | 5.5893 | 1.7441 | 5.5527 | 2.1652 | 121.312 | 1.5747 | 121.1563 | 121.2479 | 121.225 | 121.3257 | 121.2616 | -121.344 | -121.3852 | 121.3898 | 121.1929 | 3.3188 | 5.3329
2306.6875 | 121.4859 | -0.70496 | 120.7764 | 0.047683 | 6.8556 | 0.066031 | 0.086359 | 0.0028411 | 0.0039158 | 0.012796 | 0.021545 | 0.019775 | -1.3918 | 0.075706 | -0.0066906 | 0.017244 | 0.011087 | 2.623 | 120.6665 | -0.64545 | 120.6848 | 1.4877 | 0.25635 | 1.506 | 4.6829 | 120.607 | -0.66834 | 120.4651 | 0.94299 | 4.9896 | 1.1078 | 0.059509 | -0.10986 | -0.091553 | 2.1927 | 2.211 | 0.9613 | 2.1515 | 0.9018 | 0.036621 | -0.16937 | -0.31128 | 1.6479 | 1.8127 | 5.6946 | 1.7761 | 5.658 | 2.1332 | 121.3303 | 1.6113 | 121.1334 | 121.312 | 121.2753 | 121.3715 | 121.312 | -121.4218 | -121.4447 | 121.3898 | 121.17 | 3.3279 | 5.3879
2308.4062 | 121.4447 | -0.71411 | 120.7855 | 0.0095369 | 6.8607 | 0.065817 | 0.085718 | 0.0017731 | 0.0013522 | 0.010233 | -0.0028687 | 0.018066 | -1.3929 | 0.069938 | -0.0056226 | 0.017671 | 0.010446 | 2.623 | 120.6757 | -0.60425 | 120.6985 | 1.5106 | 0.2243 | 1.4969 | 4.7882 | 120.6253 | -0.63629 | 120.4651 | 0.97046 | 5.1361 | 1.1536 | 0.10986 | -0.10986 | -0.086975 | 2.2247 | 2.211 | 0.93841 | 2.1011 | 0.82855 | 0.077819 | -0.16022 | -0.32043 | 1.6846 | 1.8677 | 5.8502 | 1.7899 | 5.7724 | 2.1149 | 121.3028 | 1.6068 | 121.1014 | 121.2799 | 121.2616 | 121.3898 | 121.3394 | -121.3898 | -121.4218 | 121.4127 | 121.1792 | 3.3371 | 5.5023
2310.1875 | 121.5225 | -0.67291 | 120.726 | 0.047683 | 6.8586 | 0.067099 | 0.086359 | 0.00070491 | 0.0034884 | 0.017709 | 0.0093383 | 0.019348 | -1.392 | 0.090873 | -0.006477 | 0.018739 | 0.015359 | 2.6184 | 120.6711 | -0.59052 | 120.7169 | 1.5884 | 0.29297 | 1.5564 | 4.9026 | 120.5566 | -0.65918 | 120.5109 | 1.0757 | 5.3513 | 1.2497 | 0.082398 | -0.054931 | -0.009155 | 2.2614 | 2.2293 | 0.96588 | 2.1469 | 0.88348 | 0.013733 | -0.16937 | -0.21515 | 1.7487 | 1.9226 | 6.0242 | 1.9089 | 6.0104 | 2.179 | 121.3074 | 1.7349 | 121.17 | 121.2616 | 121.2158 | 121.344 | 121.2296 | -121.3165 | -121.3852 | 121.3898 | 121.1838 | 3.2913 | 5.5756
2311.9688 | 121.5637 | -0.67291 | 120.7169 | -0.0057221 | 6.8626 | 0.06539 | 0.085291 | 0.00049131 | 0.0030612 | 0.014719 | -0.0089723 | 0.017852 | -1.3937 | 0.085746 | -0.0066906 | 0.018525 | 0.014078 | 2.5955 | 120.6253 | -0.5722 | 120.7489 | 1.6067 | 0.33417 | 1.5839 | 5.0262 | 120.5566 | -0.64087 | 120.52 | 1.1719 | 5.5573 | 1.3367 | 0.10071 | -0.091553 | 0.032043 | 2.2797 | 2.2568 | 1.0071 | 2.1561 | 0.90637 | 0.032044 | -0.16022 | -0.19684 | 1.8448 | 2.0096 | 6.2302 | 1.9775 | 6.1981 | 2.179 | 121.3211 | 1.8127 | 121.1609 | 121.1975 | 121.1975 | 121.2982 | 121.2296 | -121.2891 | -121.3577 | 121.4218 | 121.1929 | 3.2684 | 5.6992
2313.6875 | 121.5134 | -0.70038 | 120.7535 | 0.017166 | 6.8584 | 0.064108 | 0.085078 | 0.0043365 | 0.0019932 | 0.016641 | 0.0093383 | 0.018493 | -1.3944 | 0.082542 | -0.004768 | 0.01938 | 0.013437 | 2.5635 | 120.6299 | -0.59052 | 120.6894 | 1.5335 | 0.2655 | 1.5472 | 5.04 | 120.5475 | -0.6546 | 120.4788 | 1.149 | 5.6717 | 1.3504 | 0.10986 | -0.1236 | -0.064087 | 2.2339 | 2.2476 | 0.96588 | 2.1378 | 0.85602 | 0.045776 | -0.20599 | -0.27466 | 1.8494 | 2.0508 | 6.3721 | 2.005 | 6.3263 | 2.124 | 121.2799 | 1.8036 | 121.1334 | 121.2204 | 121.2021 | 121.3303 | 121.2479 | -121.344 | -121.4081 | 121.3898 | 121.1792 | 3.2639 | 5.7404
2315.4688 | 121.5546 | -0.68207 | 120.7123 | 0.062942 | 6.8784 | 0.06774 | 0.087855 | 0.0049773 | 0.0049838 | 0.014719 | 0.018494 | 0.02127 | -1.3901 | 0.086814 | -0.0039136 | 0.01703 | 0.01301 | 2.6276 | 120.6436 | -0.60425 | 120.7764 | 1.6296 | 0.33417 | 1.6022 | 5.2368 | 120.575 | -0.6546 | 120.5429 | 1.2543 | 5.864 | 1.4374 | 0.07782 | -0.068664 | 0.064087 | 2.3117 | 2.2842 | 1.0162 | 2.2064 | 0.93841 | 0.027466 | -0.13733 | -0.16937 | 1.9363 | 2.1194 | 6.546 | 2.092 | 6.5186 | 2.2339 | 121.3806 | 1.9089 | 121.1975 | 121.2479 | 121.2296 | 121.3257 | 121.257 | -121.3165 | -121.3669 | 121.4584 | 121.225 | 3.3096 | 5.9189
2317.1875 | 121.4905 | -0.71869 | 120.7443 | -0.0057221 | 6.881 | 0.066458 | 0.082514 | 0.0015595 | 0.0015658 | 0.01301 | -0.0059205 | 0.019561 | -1.3925 | 0.087028 | -0.0062634 | 0.016175 | 0.0098053 | 2.5543 | 120.5933 | -0.56763 | 120.7214 | 1.5793 | 0.32044 | 1.5747 | 5.2551 | 120.5795 | -0.64087 | 120.4605 | 1.2726 | 5.9784 | 1.4557 | 0.15106 | -0.15106 | -0.022888 | 2.298 | 2.2934 | 1.0391 | 2.1423 | 0.88806 | 0.07782 | -0.1648 | -0.28381 | 1.9913 | 2.1744 | 6.6971 | 2.0966 | 6.6193 | 2.1469 | 121.2891 | 1.9135 | 121.1014 | 121.1609 | 121.2204 | 121.312 | 121.2982 | -121.312 | -121.3852 | 121.4401 | 121.1792 | 3.273 | 5.9738
2318.9531 | 121.5134 | -0.69122 | 120.7397 | 0.017166 | 6.8759 | 0.066458 | 0.088923 | -0.0016449 | 0.0017796 | 0.012155 | 0.0032349 | 0.021484 | -1.3918 | 0.085746 | -0.0049818 | 0.01938 | 0.015146 | 2.4902 | 120.639 | -0.59509 | 120.7031 | 1.5381 | 0.28839 | 1.5564 | 5.3192 | 120.5887 | -0.65918 | 120.4697 | 1.3138 | 6.1661 | 1.5244 | 0.09613 | -0.10071 | -0.036621 | 2.2293 | 2.2476 | 0.97961 | 2.1515 | 0.88348 | 0.032043 | -0.15106 | -0.27008 | 2.005 | 2.2156 | 6.8573 | 2.1835 | 6.8253 | 2.1332 | 121.2982 | 1.973 | 121.1288 | 121.2341 | 121.2479 | 121.3303 | 121.2799 | -121.3348 | -121.3989 | 121.3943 | 121.1609 | 3.1815 | 6.0104
2320.7344 | 121.5271 | -0.71869 | 120.7214 | -0.0057221 | 6.8814 | 0.064322 | 0.085505 | 0.00091851 | 0.0015658 | 0.014078 | -0.0028687 | 0.020202 | -1.3929 | 0.089164 | -0.0058362 | 0.016816 | 0.014505 | 2.536 | 120.5887 | -0.56763 | 120.7306 | 1.5976 | 0.3479 | 1.6159 | 5.4886 | 120.5246 | -0.63629 | 120.4926 | 1.4282 | 6.3995 | 1.6159 | 0.15106 | -0.13275 | 0.009155 | 2.3163 | 2.3346 | 1.0666 | 2.1835 | 0.91553 | 0.082397 | -0.19684 | -0.22888 | 2.1469 | 2.3346 | 7.1182 | 2.2522 | 7.0358 | 2.1652 | 121.2982 | 2.0645 | 121.1288 | 121.1563 | 121.1609 | 121.3074 | 121.2433 | -121.2891 | -121.3577 | 121.4493 | 121.2112 | 3.2547 | 6.2073
2322.5 | 121.4905 | -0.72327 | 120.726 | 0.0095369 | 6.8864 | 0.063254 | 0.089136 | 0.00091851 | 0.0034884 | 0.01301 | 0.00018312 | 0.020202 | -1.3925 | 0.081046 | -0.0015638 | 0.017671 | 0.010019 | 2.4216 | 120.6482 | -0.6134 | 120.6116 | 1.4557 | 0.19684 | 1.4877 | 5.4977 | 120.5475 | -0.69122 | 120.4559 | 1.4053 | 6.5048 | 1.6434 | 0.10986 | -0.07782 | -0.11444 | 2.179 | 2.211 | 0.9201 | 2.1011 | 0.81024 | 0.032044 | -0.17853 | -0.27008 | 2.1286 | 2.3666 | 7.2281 | 2.3346 | 7.196 | 2.0691 | 121.225 | 2.0966 | 121.1472 | 121.2616 | 121.2387 | 121.3715 | 121.2708 | -121.3394 | -121.4172 | 121.3348 | 121.1792 | 3.1448 | 6.221
2324.2188 | 121.5271 | -0.63629 | 120.7718 | -0.0057221 | 6.8947 | 0.065604 | 0.086146 | 0.0036957 | 0.0019932 | 0.014719 | -0.0059205 | 0.02127 | -1.3929 | 0.095146 | -0.001991 | 0.019807 | 0.013864 | 2.4857 | 120.7031 | -0.53558 | 120.7214 | 1.5839 | 0.32501 | 1.6113 | 5.69 | 120.5933 | -0.59509 | 120.5841 | 1.5747 | 6.8024 | 1.8265 | 0.10071 | -0.068665 | -0.050354 | 2.2202 | 2.2476 | 0.9613 | 2.1469 | 0.86059 | 0.041199 | -0.17853 | -0.18768 | 2.211 | 2.4628 | 7.4387 | 2.4216 | 7.3975 | 2.1194 | 121.257 | 2.1698 | 121.1792 | 121.2387 | 121.1884 | 121.3394 | 121.2296 | -121.3074 | -121.3669 | 121.3577 | 121.2204 | 3.1219 | 6.3263
2326 | 121.55 | -0.51727 | 120.8542 | 0.0019074 | 6.893 | 0.065604 | 0.086573 | 0.0022003 | 0.0034884 | 0.013437 | -0.0059205 | 0.021484 | -1.392 | 0.094932 | -0.0015638 | 0.022584 | 0.015359 | 2.6367 | 120.7718 | -0.40741 | 120.8725 | 1.7487 | 0.48981 | 1.7715 | 5.9647 | 120.7306 | -0.5127 | 120.6848 | 1.7532 | 7.1091 | 2.0096 | 0.10986 | -0.082397 | 0.018311 | 2.2659 | 2.2888 | 1.0071 | 2.179 | 0.89722 | 0.004578 | -0.1236 | -0.16937 | 2.2705 | 2.5269 | 7.6263 | 2.5223 | 7.6218 | 2.1561 | 121.2799 | 2.2659 | 121.1975 | 121.1792 | 121.2433 | 121.2891 | 121.2479 | -121.2616 | -121.3669 | 121.3898 | 121.2021 | 3.154 | 6.4819
2327.7656 | 121.4172 | -0.75531 | 120.7443 | -0.0057221 | 6.8981 | 0.066245 | 0.085078 | 0.00027771 | 0.0015658 | 0.012369 | 0.00018312 | 0.024261 | -1.3922 | 0.082115 | -0.0086132 | 0.016603 | 0.01835 | 2.3483 | 120.6207 | -0.62256 | 120.5795 | 1.442 | 0.2243 | 1.5015 | 5.7312 | 120.5429 | -0.68665 | 120.3552 | 1.5427 | 7.0312 | 1.7807 | 0.13275 | -0.1236 | -0.1648 | 2.1973 | 2.2568 | 0.97961 | 2.124 | 0.84686 | 0.068664 | -0.20142 | -0.3891 | 2.298 | 2.536 | 7.7866 | 2.4673 | 7.7179 | 2.0645 | 121.2021 | 2.2293 | 121.0419 | 121.2433 | 121.2296 | 121.376 | 121.2982 | -121.3669 | -121.431 | 121.3348 | 121.1105 | 3.1036 | 6.4865
2329.5312 | 121.4172 | -0.75531 | 120.7352 | -0.0057221 | 6.8958 | 0.066458 | 0.088068 | -0.00014949 | 0.0045566 | 0.012369 | -0.0028687 | 0.025116 | -1.392 | 0.080833 | -0.0060498 | 0.019807 | 0.015573 | 2.3483 | 120.6162 | -0.62256 | 120.5475 | 1.4053 | 0.18768 | 1.4877 | 5.809 | 120.5338 | -0.68207 | 120.3827 | 1.5701 | 7.1869 | 1.8356 | 0.13275 | -0.11902 | -0.18768 | 2.1606 | 2.243 | 0.94299 | 2.1103 | 0.81024 | 0.073242 | -0.20142 | -0.35248 | 2.3254 | 2.5909 | 7.9422 | 2.5177 | 7.869 | 2.0279 | 121.17 | 2.2522 | 121.0648 | 121.2387 | 121.2158 | 121.3715 | 121.2891 | -121.3577 | -121.4172 | 121.3028 | 121.138 | 3.1036 | 6.5643
2331.2656 | 121.5088 | -0.6958 | 120.7031 | 0.0019074 | 6.8949 | 0.063254 | 0.086146 | 0.00027771 | 0.002634 | 0.012796 | 0.00018312 | 0.024261 | -1.3937 | 0.08831 | -0.0028454 | 0.020662 | 0.01835 | 2.3483 | 120.6116 | -0.62714 | 120.6024 | 1.4877 | 0.23346 | 1.5472 | 5.9921 | 120.5246 | -0.68207 | 120.4697 | 1.7624 | 7.457 | 2.0004 | 0.068665 | -0.091553 | -0.10071 | 2.1835 | 2.243 | 0.92926 | 2.1744 | 0.86059 | 0.013733 | -0.17853 | -0.23346 | 2.4582 | 2.6962 | 8.1528 | 2.6825 | 8.139 | 2.1149 | 121.2296 | 2.4445 | 121.1517 | 121.2387 | 121.2067 | 121.3074 | 121.2204 | -121.3303 | -121.3852 | 121.2982 | 121.1655 | 3.0441 | 6.6879
2333.0469 | 121.5454 | -0.70496 | 120.6619 | 0.0019074 | 6.8949 | 0.065817 | 0.087855 | 0.0036957 | 0.0030612 | 0.016 | -0.0059205 | 0.022766 | -1.3937 | 0.092582 | -0.0028454 | 0.020021 | 0.017068 | 2.4078 | 120.6024 | -0.59967 | 120.6757 | 1.561 | 0.31586 | 1.6067 | 6.1386 | 120.488 | -0.65002 | 120.4971 | 1.8631 | 7.695 | 2.092 | 0.10529 | -0.059509 | 0.013733 | 2.2659 | 2.3117 | 1.0208 | 2.2064 | 0.91553 | 0.054932 | -0.17395 | -0.16479 | 2.5681 | 2.7969 | 8.4 | 2.742 | 8.345 | 2.1606 | 121.2753 | 2.5131 | 121.1472 | 121.2021 | 121.138 | 121.3074 | 121.1929 | -121.2616 | -121.3119 | 121.3806 | 121.2021 | 3.1128 | 6.8436
2334.75 | 121.463 | -0.74158 | 120.6848 | 0.070572 | 6.8998 | 0.068594 | 0.089991 | 0.0024139 | 0.0028476 | 0.014932 | 0.01239 | 0.02832 | -1.3905 | 0.083396 | -0.0077588 | 0.018312 | 0.019632 | 2.3895 | 120.6436 | -0.68207 | 120.6345 | 1.4923 | 0.28839 | 1.5884 | 6.1615 | 120.5658 | -0.70496 | 120.4147 | 1.8631 | 7.814 | 2.0828 | 0.059509 | -0.041198 | -0.050354 | 2.2339 | 2.33 | 1.03 | 2.2705 | 0.97046 | 0.036621 | -0.11902 | -0.27008 | 2.6047 | 2.8244 | 8.5556 | 2.7878 | 8.519 | 2.1744 | 121.3165 | 2.5681 | 121.1197 | 121.3257 | 121.2708 | 121.3852 | 121.3074 | -121.3669 | -121.3898 | 121.376 | 121.1563 | 3.1311 | 6.9031
2336.5312 | 121.3943 | -0.75989 | 120.7077 | -0.013352 | 6.9011 | 0.066672 | 0.087214 | 0.0049773 | 0.0019932 | 0.015146 | -0.0089723 | 0.025543 | -1.3908 | 0.088096 | -0.0045544 | 0.018312 | 0.015146 | 2.2934 | 120.6253 | -0.62256 | 120.5338 | 1.4053 | 0.18768 | 1.4969 | 6.189 | 120.52 | -0.69122 | 120.3781 | 1.8539 | 7.9651 | 2.1332 | 0.13733 | -0.082398 | -0.17395 | 2.1652 | 2.2568 | 0.94757 | 2.1194 | 0.81024 | 0.068665 | -0.18768 | -0.32959 | 2.6138 | 2.8931 | 8.725 | 2.8244 | 8.6563 | 2.0279 | 121.1563 | 2.5452 | 121.0693 | 121.2479 | 121.2112 | 121.3852 | 121.2799 | -121.3303 | -121.3989 | 121.2936 | 121.138 | 3.0533 | 6.9489
2338.3125 | 121.4539 | -0.76446 | 120.7031 | -0.0057221 | 6.8994 | 0.065817 | 0.083582 | 0.0017731 | 0.0047702 | 0.013864 | -0.0028687 | 0.026611 | -1.391 | 0.092796 | -0.0039136 | 0.018953 | 0.01835 | 2.3621 | 120.5338 | -0.60883 | 120.6345 | 1.5335 | 0.33417 | 1.6251 | 6.3675 | 120.4926 | -0.67749 | 120.3918 | 2.0096 | 8.2306 | 2.2293 | 0.15564 | -0.16937 | -0.068665 | 2.298 | 2.3895 | 1.0986 | 2.2339 | 0.94299 | 0.086975 | -0.21057 | -0.31128 | 2.774 | 2.9938 | 8.9951 | 2.9068 | 8.9081 | 2.1423 | 121.2433 | 2.6871 | 121.0693 | 121.1426 | 121.17 | 121.2982 | 121.257 | -121.312 | -121.3806 | 121.3989 | 121.1563 | 3.1265 | 7.132
2340.0156 | 121.431 | -0.75531 | 120.7169 | 0.062942 | 6.9045 | 0.063681 | 0.089136 | 0.0024139 | 0.0049838 | 0.017069 | 0.018494 | 0.030029 | -1.3893 | 0.095359 | -0.007118 | 0.019166 | 0.019632 | 2.3575 | 120.607 | -0.66834 | 120.5978 | 1.474 | 0.29755 | 1.6159 | 6.3995 | 120.5704 | -0.72327 | 120.3644 | 2.0416 | 8.3496 | 2.2797 | 0.086975 | -0.10986 | -0.11902 | 2.2293 | 2.3712 | 1.0529 | 2.2842 | 0.96588 | 0.032043 | -0.14648 | -0.35248 | 2.7969 | 3.035 | 9.1049 | 3.0029 | 9.0729 | 2.1423 | 121.2662 | 2.7649 | 121.0876 | 121.2753 | 121.2936 | 121.3623 | 121.3257 | -121.3852 | -121.4401 | 121.3531 | 121.1197 | 3.1128 | 7.1548
2341.7812 | 121.4081 | -0.74158 | 120.7077 | 0.0019074 | 6.8998 | 0.06774 | 0.086146 | 0.0026275 | 0.0049838 | 0.016428 | -0.0059205 | 0.03067 | -1.3927 | 0.09365 | -0.0058362 | 0.020234 | 0.016 | 2.3575 | 120.5978 | -0.61798 | 120.6116 | 1.4832 | 0.27008 | 1.5839 | 6.4636 | 120.5154 | -0.66834 | 120.3873 | 2.1378 | 8.4869 | 2.3666 | 0.1236 | -0.10986 | -0.096131 | 2.2247 | 2.3254 | 1.0117 | 2.2018 | 0.88806 | 0.073242 | -0.19226 | -0.32043 | 2.8793 | 3.1082 | 9.2285 | 3.035 | 9.1553 | 2.1011 | 121.2296 | 2.8061 | 121.0556 | 121.2158 | 121.1838 | 121.3394 | 121.257 | -121.3257 | -121.376 | 121.3531 | 121.1288 | 3.0991 | 7.2052
2343.5469 | 121.431 | -0.75073 | 120.726 | 0.047683 | 6.8994 | 0.06539 | 0.087427 | 0.0017731 | 0.0015658 | 0.017709 | 0.027649 | 0.031311 | -1.3903 | 0.087669 | -0.0060498 | 0.018739 | 0.020486 | 2.2751 | 120.6528 | -0.68207 | 120.5933 | 1.4832 | 0.3067 | 1.6434 | 6.5598 | 120.5704 | -0.737 | 120.3827 | 2.2293 | 8.7067 | 2.4445 | 0.068664 | -0.073242 | -0.13275 | 2.2339 | 2.3941 | 1.0574 | 2.3254 | 0.98877 | 0.013732 | -0.15564 | -0.34332 | 2.98 | 3.1952 | 9.4574 | 3.1815 | 9.4437 | 2.1652 | 121.2753 | 2.9663 | 121.1197 | 121.3348 | 121.3074 | 121.4035 | 121.3211 | -121.4081 | -121.463 | 121.344 | 121.1334 | 3.0258 | 7.3105
2345.3125 | 121.5363 | -0.70038 | 120.6573 | -0.0057221 | 6.8992 | 0.064322 | 0.085291 | -0.0037811 | 0.0013522 | 0.015146 | -0.0089723 | 0.029602 | -1.3899 | 0.10561 | -0.0058362 | 0.018953 | 0.021768 | 2.2888 | 120.5246 | -0.57678 | 120.6848 | 1.6296 | 0.41199 | 1.7075 | 6.7429 | 120.4788 | -0.64545 | 120.4697 | 2.4261 | 8.9905 | 2.6001 | 0.1236 | -0.13275 | 0.027465 | 2.33 | 2.4078 | 1.1124 | 2.2842 | 0.98877 | 0.054931 | -0.17853 | -0.18768 | 3.1265 | 3.3005 | 9.6909 | 3.2455 | 9.6359 | 2.2064 | 121.2616 | 3.0716 | 121.1151 | 121.1014 | 121.1243 | 121.225 | 121.1792 | -121.2341 | -121.3028 | 121.3852 | 121.17 | 2.9892 | 7.4432
2347.0781 | 121.4447 | -0.74158 | 120.6848 | 0.062942 | 6.9026 | 0.066245 | 0.090204 | 0.0013459 | 0.0034884 | 0.017709 | 0.01239 | 0.031952 | -1.3897 | 0.094077 | -0.0037 | 0.022584 | 0.022623 | 2.2705 | 120.6162 | -0.67749 | 120.6024 | 1.5015 | 0.32044 | 1.6434 | 6.7245 | 120.5521 | -0.70496 | 120.4056 | 2.4033 | 9.0683 | 2.6138 | 0.064087 | -0.068664 | -0.082397 | 2.243 | 2.3849 | 1.062 | 2.3209 | 0.99793 | 0.036621 | -0.13275 | -0.27923 | 3.1448 | 3.3554 | 9.8099 | 3.3188 | 9.7733 | 2.179 | 121.2799 | 3.1082 | 121.1105 | 121.2936 | 121.257 | 121.3577 | 121.2936 | -121.3623 | -121.3898 | 121.344 | 121.1472 | 3.0121 | 7.4661
2348.7812 | 121.4584 | -0.737 | 120.6985 | 0.017166 | 6.9026 | 0.066672 | 0.087 | -0.00036309 | 0.004343 | 0.017709 | 0.01239 | 0.030883 | -1.3897 | 0.091728 | -0.0032728 | 0.019166 | 0.020914 | 2.243 | 120.5704 | -0.63629 | 120.5887 | 1.5152 | 0.33417 | 1.6617 | 6.8573 | 120.5292 | -0.69122 | 120.4102 | 2.4902 | 9.2606 | 2.6779 | 0.10071 | -0.12817 | -0.10986 | 2.2522 | 2.3987 | 1.0712 | 2.298 | 0.97046 | 0.045777 | -0.16937 | -0.28839 | 3.2272 | 3.4149 | 9.9976 | 3.3691 | 9.9518 | 2.1515 | 121.225 | 3.1815 | 121.1014 | 121.2067 | 121.2204 | 121.3074 | 121.2662 | -121.3348 | -121.3898 | 121.3257 | 121.1472 | 2.98 | 7.5943
2350.5469 | 121.4218 | -0.7782 | 120.6802 | 0.070572 | 6.9066 | 0.066672 | 0.087855 | -0.0022857 | 0.002634 | 0.017282 | 0.018494 | 0.031524 | -1.3893 | 0.091728 | -0.0066906 | 0.020875 | 0.018564 | 2.1927 | 120.6253 | -0.66834 | 120.5704 | 1.4832 | 0.32501 | 1.6525 | 6.8893 | 120.5429 | -0.73242 | 120.3552 | 2.5177 | 9.4299 | 2.6825 | 0.10986 | -0.054932 | -0.10986 | 2.2614 | 2.4307 | 1.1032 | 2.3209 | 0.99335 | 0.045776 | -0.13733 | -0.32501 | 3.2959 | 3.4607 | 10.2081 | 3.4149 | 10.1624 | 2.1515 | 121.2387 | 3.2501 | 121.0876 | 121.2936 | 121.2753 | 121.4035 | 121.3211 | -121.3486 | -121.4127 | 121.3486 | 121.1334 | 2.9709 | 7.6675
2352.3281 | 121.4264 | -0.74616 | 120.6619 | 0.0019074 | 6.9079 | 0.06539 | 0.088495 | -0.00057689 | 0.002634 | 0.014291 | -0.0028687 | 0.031097 | -1.3922 | 0.099418 | -0.003059 | 0.023225 | 0.023477 | 2.1469 | 120.5887 | -0.61798 | 120.5338 | 1.442 | 0.27008 | 1.6022 | 6.9763 | 120.5154 | -0.67291 | 120.3781 | 2.5955 | 9.6176 | 2.7969 | 0.12817 | -0.073242 | -0.12817 | 2.1881 | 2.3483 | 1.0162 | 2.2202 | 0.88806 | 0.073242 | -0.14648 | -0.28381 | 3.3417 | 3.5431 | 10.3638 | 3.4698 | 10.2905 | 2.0599 | 121.1517 | 3.2684 | 121.051 | 121.2067 | 121.1884 | 121.3348 | 121.2616 | -121.2799 | -121.3348 | 121.2799 | 121.1243 | 2.8931 | 7.7225
2354.0469 | 121.5317 | -0.68665 | 120.639 | 0.0019074 | 6.9094 | 0.066885 | 0.090632 | 0.0024139 | 0.0051974 | 0.018778 | 0.027649 | 0.033233 | -1.3886 | 0.10155 | -0.0011364 | 0.02173 | 0.0254 | 2.2247 | 120.5383 | -0.59967 | 120.7031 | 1.6434 | 0.44403 | 1.767 | 7.2556 | 120.5154 | -0.68207 | 120.4697 | 2.8107 | 9.9289 | 2.9388 | 0.086976 | -0.10071 | 0.064087 | 2.33 | 2.4536 | 1.1307 | 2.3666 | 1.0437 | 0.004578 | -0.1236 | -0.16937 | 3.4973 | 3.6255 | 10.6155 | 3.6209 | 10.611 | 2.243 | 121.3028 | 3.4927 | 121.1517 | 121.138 | 121.1975 | 121.225 | 121.2021 | -121.2387 | -121.3211 | 121.3898 | 121.1563 | 2.9114 | 7.9422
2355.8281 | 121.4035 | -0.74158 | 120.694 | -0.0057221 | 6.9148 | 0.064536 | 0.088495 | 0.00091851 | 0.0041294 | 0.015787 | 0.0032349 | 0.033447 | -1.3905 | 0.1022 | -0.0015638 | 0.023225 | 0.023691 | 2.1194 | 120.5704 | -0.65002 | 120.52 | 1.4374 | 0.25635 | 1.5976 | 7.1503 | 120.5063 | -0.68665 | 120.3415 | 2.7512 | 9.9884 | 2.9068 | 0.091553 | -0.1236 | -0.17395 | 2.179 | 2.3392 | 0.99793 | 2.2476 | 0.90637 | 0.054931 | -0.18768 | -0.35248 | 3.4927 | 3.6484 | 10.73 | 3.5934 | 10.675 | 2.0874 | 121.17 | 3.4378 | 121.0281 | 121.2204 | 121.1929 | 121.312 | 121.2479 | -121.344 | -121.3806 | 121.2616 | 121.0831 | 2.861 | 7.8918
2357.5469 | 121.4859 | -0.71411 | 120.6253 | 0.055313 | 6.9195 | 0.068808 | 0.087855 | 0.00091851 | 0.0039158 | 0.018778 | 0.018494 | 0.033447 | -1.3876 | 0.10348 | -0.0011364 | 0.023866 | 0.021982 | 2.2476 | 120.5795 | -0.63171 | 120.6757 | 1.6205 | 0.41657 | 1.7624 | 7.4387 | 120.5109 | -0.69122 | 120.4285 | 2.9572 | 10.2951 | 3.0579 | 0.082397 | -0.045776 | 0.050354 | 2.3346 | 2.4765 | 1.1307 | 2.3941 | 1.0483 | 0.022888 | -0.11444 | -0.19684 | 3.6713 | 3.772 | 11.0092 | 3.7491 | 10.9863 | 2.2522 | 121.3074 | 3.6484 | 121.1197 | 121.2112 | 121.2021 | 121.2936 | 121.225 | -121.257 | -121.3165 | 121.3898 | 121.1426 | 2.9617 | 8.1528
2359.3125 | 121.4401 | -0.71869 | 120.7077 | 0.047683 | 6.9201 | 0.066458 | 0.089991 | 0.0062591 | 0.006052 | 0.016855 | 0.015442 | 0.034942 | -1.3865 | 0.097282 | -0.006477 | 0.022798 | 0.025613 | 2.1927 | 120.607 | -0.65918 | 120.6162 | 1.5152 | 0.37079 | 1.6891 | 7.4295 | 120.5475 | -0.70496 | 120.3735 | 2.9892 | 10.4279 | 3.0808 | 0.059509 | -0.10071 | -0.091553 | 2.2339 | 2.4078 | 1.0895 | 2.3483 | 1.03 | 0.013733 | -0.16022 | -0.33417 | 3.7079 | 3.7994 | 11.1465 | 3.7857 | 11.1328 | 2.1744 | 121.2753 | 3.6942 | 121.0785 | 121.2662 | 121.2524 | 121.3257 | 121.2662 | -121.3669 | -121.4127 | 121.3348 | 121.0922 | 2.9114 | 8.1482
2361.0938 | 121.4722 | -0.74158 | 120.6116 | 0.0095369 | 6.9163 | 0.066245 | 0.088282 | -0.0059173 | 0.0034884 | 0.014505 | 0.00018312 | 0.032806 | -1.3901 | 0.10625 | -0.0043408 | 0.024934 | 0.027109 | 2.124 | 120.5383 | -0.64087 | 120.5612 | 1.506 | 0.34332 | 1.68 | 7.489 | 120.4559 | -0.69122 | 120.3873 | 3.1082 | 10.6384 | 3.1448 | 0.10071 | -0.073242 | -0.050354 | 2.2476 | 2.4216 | 1.0849 | 2.3209 | 0.98419 | 0.050354 | -0.15564 | -0.2243 | 3.8498 | 3.8864 | 11.38 | 3.8361 | 11.3297 | 2.1469 | 121.2021 | 3.7994 | 121.0785 | 121.1792 | 121.1472 | 121.2799 | 121.1975 | -121.2524 | -121.3028 | 121.3028 | 121.1288 | 2.8656 | 8.2306
2362.8594 | 121.3989 | -0.7782 | 120.6665 | -0.0057221 | 6.9156 | 0.063895 | 0.088923 | -0.0050629 | 0.00071136 | 0.01536 | -0.0059205 | 0.034301 | -1.3903 | 0.10027 | -0.0073316 | 0.021516 | 0.026468 | 2.0828 | 120.52 | -0.62714 | 120.5338 | 1.4648 | 0.32044 | 1.6434 | 7.4753 | 120.5063 | -0.6958 | 120.3003 | 3.1174 | 10.6979 | 3.1219 | 0.15106 | -0.14648 | -0.13275 | 2.243 | 2.4216 | 1.0986 | 2.2705 | 0.94757 | 0.082397 | -0.16022 | -0.36621 | 3.8956 | 3.9001 | 11.4761 | 3.8177 | 11.3937 | 2.092 | 121.1609 | 3.8132 | 120.9961 | 121.1472 | 121.2021 | 121.2982 | 121.2845 | -121.2936 | -121.3623 | 121.312 | 121.0785 | 2.861 | 8.2535
2364.5781 | 121.3898 | -0.75531 | 120.6573 | 0.0019074 | 6.9212 | 0.063681 | 0.088709 | 0.0049773 | 0.0034884 | 0.013437 | 0.0032349 | 0.036224 | -1.3865 | 0.097709 | -0.0026318 | 0.021089 | 0.024118 | 2.1149 | 120.5338 | -0.65918 | 120.5658 | 1.4786 | 0.32044 | 1.6479 | 7.5714 | 120.4926 | -0.67749 | 120.3506 | 3.2089 | 10.8124 | 3.2089 | 0.09613 | -0.1236 | -0.091553 | 2.2339 | 2.4033 | 1.0757 | 2.3071 | 0.97962 | 0.07782 | -0.16479 | -0.3067 | 3.9642 | 3.9642 | 11.5677 | 3.8864 | 11.4899 | 2.1378 | 121.225 | 3.8864 | 121.0281 | 121.1929 | 121.17 | 121.2891 | 121.2479 | -121.3165 | -121.3348 | 121.3211 | 121.106 | 2.8702 | 8.3267
2366.3594 | 121.4722 | -0.737 | 120.607 | -0.0057221 | 6.9188 | 0.064322 | 0.086359 | -0.0014313 | 0.0013522 | 0.014078 | -0.0028687 | 0.034515 | -1.391 | 0.10818 | -0.0045544 | 0.023866 | 0.021982 | 2.1011 | 120.4742 | -0.62256 | 120.6299 | 1.5656 | 0.42572 | 1.7303 | 7.7225 | 120.4422 | -0.66376 | 120.3964 | 3.3829 | 11.0413 | 3.3234 | 0.11444 | -0.13275 | 0.022888 | 2.3026 | 2.4673 | 1.1627 | 2.3529 | 1.0483 | 0.073243 | -0.16479 | -0.21057 | 4.1199 | 4.0604 | 11.7783 | 3.9871 | 11.705 | 2.1881 | 121.2524 | 4.0466 | 121.0602 | 121.0968 | 121.106 | 121.2112 | 121.1792 | -121.2296 | -121.2708 | 121.3669 | 121.1334 | 2.8381 | 8.4595
2368.0625 | 121.4081 | -0.75989 | 120.6573 | 0.047683 | 6.9197 | 0.066031 | 0.091913 | -0.0016449 | 0.0034884 | 0.016855 | 0.018494 | 0.038147 | -1.3839 | 0.098136 | -0.006477 | 0.021089 | 0.027322 | 2.0645 | 120.5887 | -0.70038 | 120.5383 | 1.4557 | 0.34332 | 1.6708 | 7.7087 | 120.5246 | -0.75531 | 120.3232 | 3.3829 | 11.0916 | 3.3325 | 0.05951 | -0.068665 | -0.11902 | 2.2156 | 2.4307 | 1.1032 | 2.3712 | 1.0437 | 0.004578 | -0.13275 | -0.33417 | 4.1428 | 4.0924 | 11.8515 | 4.0878 | 11.8469 | 2.1561 | 121.2387 | 4.1382 | 121.0785 | 121.2891 | 121.2799 | 121.3486 | 121.2845 | -121.3577 | -121.4127 | 121.2982 | 121.0831 | 2.8244 | 8.4686
2369.8281 | 121.431 | -0.76446 | 120.6528 | 0.040054 | 6.9261 | 0.068167 | 0.089991 | 0.0022003 | 0.004343 | 0.017496 | 0.0062865 | 0.037506 | -1.3888 | 0.096641 | -0.005409 | 0.020234 | 0.029886 | 2.0737 | 120.5658 | -0.68665 | 120.5658 | 1.4877 | 0.36621 | 1.6983 | 7.8415 | 120.5154 | -0.70496 | 120.3552 | 3.511 | 11.2518 | 3.4241 | 0.077819 | -0.086975 | -0.086975 | 2.2522 | 2.4628 | 1.1307 | 2.3849 | 1.0529 | 0.059509 | -0.13733 | -0.29755 | 4.2755 | 4.1885 | 12.0163 | 4.129 | 11.9568 | 2.1744 | 121.2524 | 4.216 | 121.0602 | 121.2524 | 121.2204 | 121.3303 | 121.2799 | -121.3394 | -121.3577 | 121.3303 | 121.1197 | 2.8381 | 8.606
2371.5469 | 121.4172 | -0.76446 | 120.6573 | 0.024795 | 6.9203 | 0.06539 | 0.090204 | 0.0015595 | 0.0039158 | 0.018564 | 0.0032349 | 0.037292 | -1.3867 | 0.10604 | -0.0049818 | 0.021943 | 0.027963 | 2.0645 | 120.5521 | -0.68207 | 120.5704 | 1.4786 | 0.36621 | 1.6983 | 7.9422 | 120.5017 | -0.70953 | 120.369 | 3.598 | 11.4395 | 3.4607 | 0.082397 | -0.10529 | -0.086975 | 2.243 | 2.4628 | 1.1307 | 2.3804 | 1.0483 | 0.054931 | -0.15564 | -0.28839 | 4.3625 | 4.2252 | 12.204 | 4.1702 | 12.149 | 2.1606 | 121.2524 | 4.3076 | 121.0785 | 121.2341 | 121.2112 | 121.3165 | 121.2662 | -121.3394 | -121.3669 | 121.3348 | 121.1334 | 2.829 | 8.7067
2373.3125 | 121.3623 | -0.76904 | 120.6436 | -0.0057221 | 6.921 | 0.06539 | 0.087 | -0.0027131 | 0.00071136 | 0.016855 | -0.0059205 | 0.037506 | -1.389 | 0.1022 | -0.006477 | 0.023011 | 0.026681 | 1.9913 | 120.5246 | -0.65002 | 120.5063 | 1.4374 | 0.33417 | 1.6479 | 7.9742 | 120.4559 | -0.6958 | 120.3049 | 3.6346 | 11.5631 | 3.4332 | 0.11902 | -0.11902 | -0.13733 | 2.2064 | 2.417 | 1.1032 | 2.298 | 0.98419 | 0.073242 | -0.18768 | -0.33874 | 4.4037 | 4.2023 | 12.3322 | 4.129 | 12.2589 | 2.0874 | 121.1563 | 4.3304 | 121.0007 | 121.1746 | 121.1517 | 121.2936 | 121.225 | -121.2936 | -121.3394 | 121.2753 | 121.0739 | 2.7603 | 8.7433
2375.0156 | 121.4996 | -0.72784 | 120.5887 | -0.0057221 | 6.9178 | 0.064749 | 0.084864 | -0.0012177 | 0.002634 | 0.013651 | 0.00018312 | 0.036865 | -1.3873 | 0.10924 | -0.0037 | 0.024934 | 0.026895 | 2.0325 | 120.4468 | -0.60425 | 120.6299 | 1.5839 | 0.4715 | 1.7853 | 8.2993 | 120.3873 | -0.68207 | 120.4422 | 3.8956 | 11.8744 | 3.6072 | 0.1236 | -0.14191 | 0.041199 | 2.3117 | 2.5131 | 1.1993 | 2.3895 | 1.0757 | 0.045776 | -0.20142 | -0.14648 | 4.6234 | 4.335 | 12.6022 | 4.2892 | 12.5565 | 2.1881 | 121.2341 | 4.5776 | 121.1243 | 121.051 | 121.0693 | 121.1746 | 121.1151 | -121.1929 | -121.2708 | 121.3577 | 121.17 | 2.7603 | 9.0271
2376.7969 | 121.4584 | -0.75073 | 120.6436 | 0.0019074 | 6.9201 | 0.063895 | 0.086786 | 0.0015595 | 0.002634 | 0.015573 | -0.0028687 | 0.03836 | -1.3869 | 0.11031 | -0.0028454 | 0.022798 | 0.026254 | 1.973 | 120.5246 | -0.6546 | 120.52 | 1.4465 | 0.31128 | 1.6663 | 8.3084 | 120.4651 | -0.68665 | 120.369 | 3.9093 | 11.9293 | 3.6346 | 0.09613 | -0.11902 | -0.1236 | 2.1973 | 2.417 | 1.062 | 2.3209 | 0.96588 | 0.064086 | -0.17853 | -0.27466 | 4.66 | 4.3854 | 12.6801 | 4.3213 | 12.616 | 2.1011 | 121.1746 | 4.5959 | 121.0556 | 121.1792 | 121.1517 | 121.2753 | 121.2158 | -121.2982 | -121.3303 | 121.2708 | 121.1197 | 2.7237 | 9.0591
2378.5781 | 121.4493 | -0.737 | 120.5933 | 0.062942 | 6.9248 | 0.068381 | 0.088068 | -0.00014949 | 0.0066928 | 0.018137 | 0.021545 | 0.039215 | -1.3854 | 0.10967 | -0.00092279 | 0.022584 | 0.028604 | 2.0737 | 120.5017 | -0.64545 | 120.6345 | 1.5793 | 0.43945 | 1.7715 | 8.5648 | 120.4697 | -0.737 | 120.3918 | 4.0604 | 12.1216 | 3.7125 | 0.091553 | -0.091553 | 0.041198 | 2.3163 | 2.5085 | 1.1765 | 2.417 | 1.0849 | 0 | -0.1236 | -0.20142 | 4.7974 | 4.4495 | 12.8586 | 4.4495 | 12.8586 | 2.2247 | 121.2799 | 4.7974 | 121.1288 | 121.1472 | 121.2067 | 121.2387 | 121.2067 | -121.2387 | -121.3303 | 121.3715 | 121.1288 | 2.8107 | 9.3018
2380.3594 | 121.3806 | -0.76904 | 120.6253 | -0.013352 | 6.922 | 0.06304 | 0.087427 | -0.00079049 | 0.0028476 | 0.015146 | -0.0028687 | 0.037719 | -1.3897 | 0.10796 | -0.005409 | 0.023652 | 0.026041 | 1.9958 | 120.4926 | -0.63629 | 120.5521 | 1.4786 | 0.39368 | 1.7166 | 8.4961 | 120.4422 | -0.70038 | 120.3094 | 4.0421 | 12.1902 | 3.6987 | 0.13275 | -0.13275 | -0.073242 | 2.2476 | 2.4857 | 1.1627 | 2.3529 | 1.03 | 0.068665 | -0.1831 | -0.31586 | 4.8111 | 4.4678 | 12.9593 | 4.3991 | 12.8906 | 2.1149 | 121.1884 | 4.7424 | 121.0098 | 121.1288 | 121.1426 | 121.2616 | 121.2112 | -121.2616 | -121.3257 | 121.3211 | 121.0785 | 2.7649 | 9.2651
2382.1406 | 121.4035 | -0.76904 | 120.6207 | 0.024795 | 6.9261 | 0.063681 | 0.0917 | 0.00027771 | 0.0032748 | 0.017282 | 0.0093383 | 0.041137 | -1.3882 | 0.098777 | -0.0045544 | 0.024293 | 0.032663 | 1.9913 | 120.5429 | -0.66376 | 120.5566 | 1.4969 | 0.39825 | 1.7029 | 8.6243 | 120.4788 | -0.70953 | 120.3506 | 4.1473 | 12.2681 | 3.7949 | 0.10529 | -0.07782 | -0.064087 | 2.2659 | 2.4719 | 1.1673 | 2.3666 | 1.062 | 0.059509 | -0.14191 | -0.27008 | 4.9164 | 4.5639 | 13.0371 | 4.5044 | 12.9776 | 2.1606 | 121.2204 | 4.8569 | 121.0602 | 121.2067 | 121.1884 | 121.312 | 121.2479 | -121.2845 | -121.3303 | 121.3257 | 121.1197 | 2.7603 | 9.3933
2383.9062 | 121.4355 | -0.74616 | 120.6162 | 0.024795 | 6.9246 | 0.064963 | 0.088709 | -0.00036309 | 0.006052 | 0.017923 | 0.0093383 | 0.039642 | -1.3865 | 0.10625 | -0.004768 | 0.02408 | 0.029031 | 1.9547 | 120.5109 | -0.65918 | 120.5612 | 1.506 | 0.41199 | 1.7395 | 8.757 | 120.4239 | -0.70038 | 120.3461 | 4.2618 | 12.4191 | 3.8132 | 0.086975 | -0.10529 | -0.054932 | 2.2522 | 2.4857 | 1.1581 | 2.3987 | 1.0712 | 0.045777 | -0.19226 | -0.27008 | 5.0079 | 4.5593 | 13.1653 | 4.5135 | 13.1195 | 2.1652 | 121.2204 | 4.9622 | 121.0464 | 121.17 | 121.1243 | 121.257 | 121.17 | -121.2753 | -121.3165 | 121.3074 | 121.0922 | 2.7008 | 9.5032
2385.6719 | 121.344 | -0.79193 | 120.6665 | -0.0057221 | 6.9246 | 0.067313 | 0.089777 | -0.0018585 | 0.0051974 | 0.017709 | 0.033752 | 0.044128 | -1.3841 | 0.10882 | -0.0077588 | 0.023439 | 0.031168 | 1.886 | 120.5292 | -0.70496 | 120.52 | 1.4557 | 0.38452 | 1.6983 | 8.7845 | 120.4834 | -0.77362 | 120.2728 | 4.2664 | 12.4832 | 3.7994 | 0.086975 | -0.13733 | -0.14648 | 2.2476 | 2.4902 | 1.1765 | 2.4033 | 1.0895 | 0.01831 | -0.18311 | -0.39368 | 5.0583 | 4.5914 | 13.2751 | 4.5731 | 13.2568 | 2.1606 | 121.225 | 5.04 | 121.0464 | 121.2341 | 121.257 | 121.3211 | 121.2753 | -121.3715 | -121.4401 | 121.312 | 121.0648 | 2.6779 | 9.5764
2387.3906 | 121.3669 | -0.76446 | 120.6207 | 0.0019074 | 6.9244 | 0.065176 | 0.088282 | -0.0016449 | 0.0032748 | 0.017709 | -0.0059205 | 0.041778 | -1.3856 | 0.10348 | -0.0043408 | 0.023652 | 0.028177 | 1.918 | 120.5017 | -0.66834 | 120.5292 | 1.4603 | 0.35248 | 1.6754 | 8.9127 | 120.4514 | -0.70953 | 120.3049 | 4.3304 | 12.6114 | 3.8727 | 0.09613 | -0.11902 | -0.091553 | 2.2247 | 2.4399 | 1.1169 | 2.3438 | 1.0208 | 0.054931 | -0.16937 | -0.31586 | 5.0949 | 4.6371 | 13.3759 | 4.5822 | 13.3209 | 2.1286 | 121.1975 | 5.04 | 121.0144 | 121.17 | 121.1609 | 121.2662 | 121.2158 | -121.2891 | -121.3303 | 121.2936 | 121.0693 | 2.6825 | 9.6771
2389.1719 | 121.4127 | -0.78735 | 120.607 | 0.032425 | 6.9261 | 0.067099 | 0.090204 | 0.0015595 | 0.0037022 | 0.015573 | 0.0093383 | 0.041992 | -1.3858 | 0.10903 | -0.0043408 | 0.02408 | 0.030313 | 1.918 | 120.5338 | -0.66834 | 120.5292 | 1.4786 | 0.38452 | 1.7166 | 9.1187 | 120.4376 | -0.70496 | 120.3369 | 4.4449 | 12.8494 | 3.9413 | 0.11902 | -0.073243 | -0.07782 | 2.2659 | 2.504 | 1.1719 | 2.3849 | 1.0529 | 0.082398 | -0.16937 | -0.27008 | 5.2322 | 4.7287 | 13.6368 | 4.6463 | 13.5544 | 2.1469 | 121.1975 | 5.1498 | 121.0419 | 121.2021 | 121.1426 | 121.3211 | 121.225 | -121.2753 | -121.312 | 121.3165 | 121.1243 | 2.7054 | 9.906
2390.9375 | 121.431 | -0.75531 | 120.5933 | 0.040054 | 6.9276 | 0.067526 | 0.089991 | -0.00057689 | 0.005411 | 0.016855 | 0.027649 | 0.042205 | -1.3852 | 0.10326 | -0.0032728 | 0.025789 | 0.032022 | 1.9363 | 120.4971 | -0.6546 | 120.6024 | 1.5701 | 0.44403 | 1.7899 | 9.3155 | 120.4285 | -0.72327 | 120.3506 | 4.5319 | 13.0005 | 4.0329 | 0.10071 | -0.096131 | 0.009155 | 2.3254 | 2.5452 | 1.1993 | 2.4445 | 1.0986 | 0.032043 | -0.16479 | -0.24262 | 5.2872 | 4.7882 | 13.7558 | 4.7562 | 13.7238 | 2.2247 | 121.257 | 5.2551 | 121.0739 | 121.1517 | 121.1517 | 121.2524 | 121.1838 | -121.2479 | -121.3165 | 121.3577 | 121.106 | 2.6917 | 10.0708
2392.7188 | 121.4539 | -0.72784 | 120.575 | -0.013352 | 6.9267 | 0.064536 | 0.091913 | 0.0017731 | 0.005411 | 0.011728 | -0.0059205 | 0.040924 | -1.3846 | 0.11159 | -0.00070919 | 0.02408 | 0.032449 | 1.886 | 120.488 | -0.66834 | 120.5292 | 1.4786 | 0.38452 | 1.7212 | 9.375 | 120.3873 | -0.68207 | 120.3827 | 4.6234 | 13.1378 | 4.1199 | 0.059509 | -0.086975 | -0.045776 | 2.2064 | 2.449 | 1.1124 | 2.3895 | 1.0529 | 0.045776 | -0.18768 | -0.19226 | 5.3513 | 4.8477 | 13.8657 | 4.8019 | 13.8199 | 2.1469 | 121.1975 | 5.3055 | 121.0648 | 121.1563 | 121.0693 | 121.2158 | 121.1151 | -121.2433 | -121.257 | 121.257 | 121.1105 | 2.6138 | 10.1028
2394.4219 | 121.3531 | -0.79651 | 120.6253 | -0.0057221 | 6.9289 | 0.066885 | 0.087855 | -0.0016449 | 0.0032748 | 0.017496 | -0.0028687 | 0.042205 | -1.3843 | 0.10775 | -0.0051954 | 0.024507 | 0.031381 | 1.8539 | 120.5017 | -0.65918 | 120.4468 | 1.3641 | 0.30212 | 1.6525 | 9.3842 | 120.4376 | -0.72784 | 120.2728 | 4.5547 | 13.147 | 4.0833 | 0.13733 | -0.1236 | -0.17853 | 2.1606 | 2.449 | 1.0986 | 2.3117 | 0.9613 | 0.068665 | -0.18768 | -0.35248 | 5.3513 | 4.8798 | 13.9435 | 4.8111 | 13.8748 | 2.0233 | 121.106 | 5.2826 | 121.0007 | 121.1609 | 121.1655 | 121.2982 | 121.2341 | -121.2845 | -121.3531 | 121.2433 | 121.0693 | 2.6505 | 10.1807
2396.2188 | 121.3486 | -0.80109 | 120.6162 | -0.02861 | 6.9263 | 0.065604 | 0.086786 | 0.0032685 | 0.0028476 | 0.015146 | 0.030701 | 0.044555 | -1.3841 | 0.10967 | -0.0069044 | 0.023225 | 0.02775 | 1.8173 | 120.4834 | -0.68207 | 120.4971 | 1.4282 | 0.39368 | 1.7166 | 9.5169 | 120.488 | -0.78278 | 120.2408 | 4.6417 | 13.2797 | 4.1245 | 0.11902 | -0.13275 | -0.11902 | 2.2293 | 2.5177 | 1.1948 | 2.3987 | 1.0757 | 0.01831 | -0.12817 | -0.37537 | 5.4428 | 4.9255 | 14.0808 | 4.9072 | 14.0625 | 2.1103 | 121.1792 | 5.4245 | 121.0236 | 121.1655 | 121.2708 | 121.2845 | 121.2891 | -121.2982 | -121.3989 | 121.2982 | 121.0419 | 2.6184 | 10.318
2397.9844 | 121.4493 | -0.75073 | 120.575 | -0.013352 | 6.9269 | 0.063681 | 0.086573 | 0.0047637 | 0.0039158 | 0.014719 | 0.00018312 | 0.040069 | -1.3854 | 0.10989 | -0.0062634 | 0.023011 | 0.033945 | 1.9043 | 120.4376 | -0.63629 | 120.575 | 1.5381 | 0.46234 | 1.7807 | 9.7183 | 120.3781 | -0.68665 | 120.3644 | 4.8157 | 13.5498 | 4.2618 | 0.11444 | -0.13733 | 0 | 2.2888 | 2.5314 | 1.2131 | 2.417 | 1.0986 | 0.064086 | -0.19684 | -0.21057 | 5.5664 | 5.0125 | 14.3005 | 4.9484 | 14.2365 | 2.1744 | 121.2112 | 5.5023 | 121.051 | 121.0739 | 121.0648 | 121.1884 | 121.1288 | -121.2112 | -121.2616 | 121.3257 | 121.1151 | 2.655 | 10.4691
2399.7031 | 121.4447 | -0.74616 | 120.5521 | 0.0019074 | 6.9242 | 0.063895 | 0.087855 | -0.0016449 | 0.0034884 | 0.014932 | 0.00018312 | 0.042205 | -1.3878 | 0.11053 | -0.0039136 | 0.026216 | 0.033517 | 1.8768 | 120.4193 | -0.6546 | 120.5109 | 1.4603 | 0.42114 | 1.7395 | 9.787 | 120.3918 | -0.70496 | 120.3552 | 4.8523 | 13.6734 | 4.2938 | 0.091553 | -0.13275 | -0.041199 | 2.2064 | 2.4857 | 1.1673 | 2.3941 | 1.0757 | 0.041199 | -0.16022 | -0.19684 | 5.5984 | 5.04 | 14.4196 | 4.9988 | 14.3784 | 2.1149 | 121.1655 | 5.5573 | 121.0602 | 121.0739 | 121.0968 | 121.1655 | 121.138 | -121.2067 | -121.257 | 121.257 | 121.1014 | 2.623 | 10.5331
2401.4844 | 121.3348 | -0.80109 | 120.607 | 0.08583 | 6.9321 | 0.066245 | 0.0917 | -0.0010041 | 0.0064792 | 0.015573 | 0.024597 | 0.046478 | -1.3841 | 0.11159 | -0.0079724 | 0.02408 | 0.034372 | 1.8585 | 120.52 | -0.74616 | 120.4697 | 1.4099 | 0.37537 | 1.712 | 9.8007 | 120.4514 | -0.7782 | 120.2316 | 4.7653 | 13.6963 | 4.2343 | 0.054931 | -0.086975 | -0.13733 | 2.211 | 2.5131 | 1.1765 | 2.4582 | 1.1215 | 0.022888 | -0.15564 | -0.37537 | 5.5664 | 5.0354 | 14.4974 | 5.0125 | 14.4745 | 2.1561 | 121.2158 | 5.5435 | 121.0098 | 121.2662 | 121.2296 | 121.3211 | 121.2524 | -121.3531 | -121.3852 | 121.2708 | 121.0327 | 2.6596 | 10.6018
2403.2656 | 121.4584 | -0.76446 | 120.5566 | 0.0019074 | 6.9308 | 0.063895 | 0.090845 | 0.0011321 | 0.0032748 | 0.015787 | -0.0028687 | 0.043487 | -1.385 | 0.12676 | 0.0012134 | 0.026429 | 0.03309 | 1.8356 | 120.4697 | -0.6546 | 120.4742 | 1.4328 | 0.35248 | 1.7075 | 9.9792 | 120.3598 | -0.71411 | 120.3323 | 4.9622 | 13.9572 | 4.3854 | 0.10986 | -0.086975 | -0.082398 | 2.1973 | 2.4719 | 1.1169 | 2.3621 | 1.0071 | 0.050354 | -0.19684 | -0.22431 | 5.7266 | 5.1498 | 14.7217 | 5.0995 | 14.6713 | 2.0874 | 121.1288 | 5.6763 | 121.0464 | 121.1243 | 121.0739 | 121.2341 | 121.1243 | -121.2112 | -121.2708 | 121.2387 | 121.0968 | 2.6001 | 10.7437
2404.9688 | 121.4355 | -0.77362 | 120.5566 | 0.0019074 | 6.931 | 0.064536 | 0.091913 | 6.4114e-05 | 0.0037022 | 0.014719 | -0.0028687 | 0.042846 | -1.3841 | 0.10796 | -0.0043408 | 0.027284 | 0.033945 | 1.8265 | 120.4422 | -0.69122 | 120.4559 | 1.4053 | 0.32959 | 1.6891 | 10.0388 | 120.3873 | -0.72327 | 120.3049 | 4.9576 | 14.0625 | 4.3808 | 0.082398 | -0.11444 | -0.10071 | 2.179 | 2.4628 | 1.1032 | 2.3804 | 1.0208 | 0.050354 | -0.16937 | -0.25177 | 5.7312 | 5.1544 | 14.8361 | 5.1041 | 14.7858 | 2.0966 | 121.1472 | 5.6808 | 121.0281 | 121.1334 | 121.1105 | 121.2158 | 121.1609 | -121.2479 | -121.2799 | 121.2296 | 121.0785 | 2.6001 | 10.8124
2406.7656 | 121.3806 | -0.80566 | 120.5566 | 0.055313 | 6.9355 | 0.064108 | 0.091273 | 0.0028411 | 0.0045566 | 0.017282 | 0.027649 | 0.046264 | -1.3809 | 0.10818 | -0.0058362 | 0.025148 | 0.033731 | 1.8311 | 120.4834 | -0.74158 | 120.4834 | 1.4145 | 0.39825 | 1.7166 | 10.1486 | 120.4514 | -0.76446 | 120.2591 | 5.0079 | 14.1998 | 4.3716 | 0.064087 | -0.073243 | -0.073243 | 2.2202 | 2.5223 | 1.2039 | 2.4582 | 1.1398 | 0.041199 | -0.10529 | -0.29755 | 5.8136 | 5.1773 | 15.0055 | 5.1361 | 14.9643 | 2.1561 | 121.225 | 5.7724 | 121.0236 | 121.225 | 121.2158 | 121.2891 | 121.257 | -121.2982 | -121.3211 | 121.2891 | 121.0648 | 2.6367 | 10.9543
2408.4688 | 121.3394 | -0.80109 | 120.5612 | -0.013352 | 6.9329 | 0.064536 | 0.086359 | -0.00079049 | 0.0013522 | 0.015573 | -0.0059205 | 0.04306 | -1.3863 | 0.11224 | -0.0073316 | 0.02472 | 0.035867 | 1.8265 | 120.3964 | -0.66834 | 120.488 | 1.474 | 0.42114 | 1.7487 | 10.2264 | 120.3369 | -0.72327 | 120.2271 | 5.0766 | 14.3875 | 4.4128 | 0.13275 | -0.16479 | -0.073242 | 2.2751 | 2.5497 | 1.2222 | 2.417 | 1.0895 | 0.077819 | -0.2243 | -0.33417 | 5.8777 | 5.2139 | 15.1886 | 5.1361 | 15.1108 | 2.1423 | 121.1563 | 5.7999 | 120.9503 | 121.0648 | 121.0602 | 121.1975 | 121.138 | -121.2296 | -121.2845 | 121.2891 | 121.0281 | 2.6276 | 11.0275
2410.2344 | 121.376 | -0.81024 | 120.5475 | 0.062942 | 6.9363 | 0.06539 | 0.091486 | -0.00079049 | 0.0066928 | 0.017496 | 0.018494 | 0.047973 | -1.3822 | 0.10946 | -0.0041272 | 0.024934 | 0.033731 | 1.8219 | 120.4742 | -0.74158 | 120.488 | 1.4008 | 0.39825 | 1.7258 | 10.2859 | 120.3873 | -0.7782 | 120.2545 | 5.1132 | 14.5111 | 4.4907 | 0.068665 | -0.073242 | -0.059509 | 2.211 | 2.536 | 1.2085 | 2.4673 | 1.1398 | 0.032044 | -0.16022 | -0.29297 | 5.9235 | 5.3009 | 15.3214 | 5.2689 | 15.2893 | 2.1423 | 121.2296 | 5.8914 | 121.0327 | 121.2158 | 121.1655 | 121.2845 | 121.1975 | -121.2891 | -121.3257 | 121.2982 | 121.0648 | 2.6321 | 11.0962
2412.0156 | 121.3715 | -0.8194 | 120.5338 | 0.062942 | 6.9387 | 0.064749 | 0.091486 | 0.0051911 | 0.0051974 | 0.018991 | 0.015442 | 0.04541 | -1.3824 | 0.11288 | -0.0032728 | 0.024934 | 0.031168 | 1.8311 | 120.4376 | -0.75989 | 120.4605 | 1.4008 | 0.39825 | 1.7166 | 10.3271 | 120.401 | -0.78278 | 120.2408 | 5.1498 | 14.6713 | 4.5547 | 0.059509 | -0.09613 | -0.073242 | 2.2202 | 2.536 | 1.2177 | 2.4765 | 1.1581 | 0.036621 | -0.13275 | -0.29297 | 5.9692 | 5.3741 | 15.4907 | 5.3375 | 15.4541 | 2.1606 | 121.2204 | 5.9326 | 121.0236 | 121.1975 | 121.1838 | 121.257 | 121.2204 | -121.2936 | -121.3165 | 121.2799 | 121.0602 | 2.6505 | 11.1465
2413.75 | 121.3165 | -0.8194 | 120.5612 | -0.013352 | 6.9363 | 0.067313 | 0.089777 | 0.0026275 | 0.0030612 | 0.012582 | 0.00018312 | 0.045837 | -1.3816 | 0.12185 | -0.0024182 | 0.025789 | 0.03544 | 1.7624 | 120.4468 | -0.70038 | 120.3781 | 1.3046 | 0.28839 | 1.6388 | 10.3638 | 120.3644 | -0.77362 | 120.2133 | 5.1086 | 14.7354 | 4.5364 | 0.11902 | -0.11444 | -0.1831 | 2.124 | 2.4582 | 1.1078 | 2.3392 | 0.98877 | 0.045776 | -0.19684 | -0.3479 | 5.928 | 5.3558 | 15.5548 | 5.3101 | 15.509 | 2.005 | 121.0785 | 5.8823 | 120.9869 | 121.1472 | 121.138 | 121.2662 | 121.1838 | -121.2616 | -121.3348 | 121.1975 | 121.0327 | 2.5818 | 11.1832
2415.5156 | 121.4401 | -0.78735 | 120.5063 | -0.0057221 | 6.9368 | 0.065604 | 0.087 | -0.0022857 | 0.0045566 | 0.012369 | -0.0028687 | 0.044555 | -1.3839 | 0.11437 | -0.0066906 | 0.025789 | 0.032876 | 1.8173 | 120.3735 | -0.66834 | 120.5063 | 1.5015 | 0.46692 | 1.7944 | 10.6247 | 120.314 | -0.72784 | 120.2911 | 5.3055 | 14.9872 | 4.7058 | 0.11902 | -0.13275 | 0 | 2.2888 | 2.5818 | 1.2543 | 2.4628 | 1.1353 | 0.05951 | -0.19226 | -0.21515 | 6.0928 | 5.4932 | 15.7745 | 5.4337 | 15.715 | 2.1698 | 121.1746 | 6.0333 | 121.019 | 121.0419 | 121.0419 | 121.1609 | 121.1014 | -121.1746 | -121.2341 | 121.2936 | 121.0785 | 2.6047 | 11.412
2417.25 | 121.3348 | -0.8194 | 120.5154 | 0.024795 | 6.9402 | 0.067313 | 0.089136 | 0.0022003 | 0.0049838 | 0.014719 | 0.00018312 | 0.045837 | -1.3843 | 0.11779 | -0.0013502 | 0.023866 | 0.034585 | 1.8082 | 120.4056 | -0.70953 | 120.433 | 1.3916 | 0.37079 | 1.712 | 10.6064 | 120.3461 | -0.74616 | 120.2133 | 5.2231 | 14.9551 | 4.6692 | 0.10986 | -0.10986 | -0.082398 | 2.211 | 2.5314 | 1.1902 | 2.4216 | 1.0803 | 0.073242 | -0.16937 | -0.30212 | 6.0425 | 5.4886 | 15.7745 | 5.4153 | 15.7013 | 2.1011 | 121.1426 | 5.9692 | 120.9595 | 121.1151 | 121.0922 | 121.225 | 121.1655 | -121.225 | -121.2616 | 121.2524 | 121.0327 | 2.6276 | 11.4258
2419.0156 | 121.3257 | -0.8194 | 120.5429 | -0.013352 | 6.94 | 0.064749 | 0.089136 | -0.00079049 | 0.0015658 | 0.015787 | -0.0028687 | 0.046478 | -1.3833 | 0.11843 | -0.006477 | 0.023439 | 0.03779 | 1.7853 | 120.3644 | -0.68207 | 120.4239 | 1.3733 | 0.40283 | 1.7212 | 10.6613 | 120.3552 | -0.76446 | 120.1904 | 5.2734 | 15.1291 | 4.6921 | 0.13733 | -0.17853 | -0.11902 | 2.1927 | 2.5406 | 1.2222 | 2.4033 | 1.0849 | 0.054932 | -0.18768 | -0.35248 | 6.0928 | 5.5115 | 15.9485 | 5.4565 | 15.8936 | 2.0554 | 121.106 | 6.0379 | 120.9549 | 121.0464 | 121.1197 | 121.1838 | 121.1746 | -121.225 | -121.3074 | 121.2433 | 121.0098 | 2.6047 | 11.4807
2420.7969 | 121.3531 | -0.81024 | 120.5338 | 0.017166 | 6.9408 | 0.065604 | 0.089564 | 0.0041229 | 0.0047702 | 0.016214 | 0.0093383 | 0.046905 | -1.3816 | 0.11181 | -0.0039136 | 0.022584 | 0.033731 | 1.8082 | 120.4239 | -0.737 | 120.4468 | 1.387 | 0.39825 | 1.7578 | 10.8215 | 120.3598 | -0.74158 | 120.2408 | 5.3329 | 15.303 | 4.7928 | 0.073242 | -0.10986 | -0.086975 | 2.1973 | 2.5681 | 1.2085 | 2.4948 | 1.1353 | 0.068665 | -0.17395 | -0.29297 | 6.1432 | 5.603 | 16.1133 | 5.5344 | 16.0446 | 2.124 | 121.1838 | 6.0745 | 120.9824 | 121.1609 | 121.1014 | 121.2341 | 121.17 | -121.2708 | -121.2753 | 121.257 | 121.051 | 2.6184 | 11.6318
2422.5156 | 121.4035 | -0.80109 | 120.488 | 0.017166 | 6.9406 | 0.064108 | 0.088282 | -0.0029267 | 0.0028476 | 0.01835 | 0.0062865 | 0.04541 | -1.3843 | 0.11629 | -0.0024182 | 0.025361 | 0.038858 | 1.7715 | 120.3735 | -0.6958 | 120.4239 | 1.3641 | 0.41199 | 1.7624 | 10.8032 | 120.3049 | -0.75531 | 120.2545 | 5.4245 | 15.4678 | 4.8477 | 0.10528 | -0.11444 | -0.064087 | 2.1652 | 2.5635 | 1.2131 | 2.4582 | 1.1078 | 0.045776 | -0.1831 | -0.23346 | 6.2256 | 5.6488 | 16.2689 | 5.603 | 16.2231 | 2.0599 | 121.1197 | 6.1798 | 121.0098 | 121.0693 | 121.0602 | 121.1746 | 121.106 | -121.1838 | -121.2433 | 121.225 | 121.0556 | 2.5726 | 11.6043
2424.3125 | 121.4218 | -0.79193 | 120.4697 | -0.0057221 | 6.9404 | 0.065817 | 0.088709 | -0.0031403 | 0.0064792 | 0.013864 | -0.0059205 | 0.045196 | -1.3826 | 0.11993 | -0.00070919 | 0.027711 | 0.041208 | 1.7807 | 120.369 | -0.68207 | 120.4651 | 1.3962 | 0.41657 | 1.767 | 10.9222 | 120.3049 | -0.73242 | 120.282 | 5.4749 | 15.5685 | 4.9438 | 0.10986 | -0.10071 | -0.004578 | 2.1881 | 2.5589 | 1.2085 | 2.449 | 1.0986 | 0.059509 | -0.16479 | -0.18768 | 6.2668 | 5.7358 | 16.3605 | 5.6763 | 16.301 | 2.0782 | 121.1472 | 6.2073 | 121.0144 | 121.051 | 121.0373 | 121.1609 | 121.0968 | -121.1517 | -121.2021 | 121.257 | 121.0739 | 2.5726 | 11.7142
2426.0938 | 121.2845 | -0.86517 | 120.5109 | -0.013352 | 6.94 | 0.06304 | 0.088495 | -0.0037811 | 0.0037022 | 0.017496 | 0.00018312 | 0.047546 | -1.3822 | 0.11437 | -0.0086132 | 0.025575 | 0.039499 | 1.6891 | 120.369 | -0.72327 | 120.3461 | 1.2772 | 0.33875 | 1.6983 | 10.8078 | 120.3186 | -0.77362 | 120.1355 | 5.3833 | 15.5548 | 4.866 | 0.14191 | -0.14191 | -0.16479 | 2.1423 | 2.5635 | 1.2039 | 2.4216 | 1.062 | 0.091552 | -0.19226 | -0.37537 | 6.2485 | 5.7312 | 16.42 | 5.6396 | 16.3284 | 2.0004 | 121.0693 | 6.1569 | 120.9091 | 121.0922 | 121.0922 | 121.2341 | 121.1838 | -121.2341 | -121.2845 | 121.2112 | 121.0007 | 2.5543 | 11.673
2427.875 | 121.3028 | -0.85602 | 120.4788 | 0.062942 | 6.9402 | 0.068594 | 0.091059 | -0.00014949 | 0.0056248 | 0.014719 | 0.021545 | 0.049469 | -1.3805 | 0.11929 | -0.0060498 | 0.024293 | 0.038431 | 1.7349 | 120.4102 | -0.80566 | 120.3644 | 1.268 | 0.36163 | 1.7212 | 10.8765 | 120.3415 | -0.83771 | 120.1309 | 5.397 | 15.6738 | 4.9026 | 0.050354 | -0.068665 | -0.11444 | 2.124 | 2.5772 | 1.2177 | 2.5269 | 1.1673 | 0.01831 | -0.13733 | -0.3479 | 6.2531 | 5.7587 | 16.5298 | 5.7404 | 16.5115 | 2.0737 | 121.17 | 6.2347 | 120.9686 | 121.2158 | 121.1792 | 121.2662 | 121.1975 | -121.2845 | -121.3165 | 121.2204 | 120.9869 | 2.5909 | 11.7325
2429.5938 | 121.3943 | -0.83313 | 120.4376 | 0.0019074 | 6.9408 | 0.065817 | 0.090418 | 0.00070491 | 0.004343 | 0.015787 | -0.0028687 | 0.044342 | -1.3839 | 0.11095 | -0.0028454 | 0.02707 | 0.034372 | 1.712 | 120.3598 | -0.72784 | 120.3918 | 1.2955 | 0.3479 | 1.7075 | 11.0184 | 120.2728 | -0.77362 | 120.2362 | 5.5161 | 15.8386 | 5.0125 | 0.10529 | -0.07782 | -0.045776 | 2.1286 | 2.5406 | 1.181 | 2.4353 | 1.0757 | 0.059509 | -0.16479 | -0.20142 | 6.3492 | 5.8456 | 16.6718 | 5.7861 | 16.6122 | 2.0233 | 121.1197 | 6.2897 | 121.0098 | 121.0876 | 121.0464 | 121.1929 | 121.106 | -121.1655 | -121.2112 | 121.225 | 121.0693 | 2.5452 | 11.8515
2431.375 | 121.3715 | -0.82855 | 120.4468 | -0.0057221 | 6.9427 | 0.064322 | 0.089777 | -0.0046357 | 0.0030612 | 0.015146 | -0.0059205 | 0.045196 | -1.3831 | 0.11672 | -0.0062634 | 0.02707 | 0.039072 | 1.7532 | 120.3003 | -0.71869 | 120.4193 | 1.387 | 0.44403 | 1.7853 | 11.1008 | 120.2499 | -0.7782 | 120.2042 | 5.5618 | 15.976 | 5.0262 | 0.10986 | -0.14648 | -0.027465 | 2.2156 | 2.6138 | 1.2726 | 2.504 | 1.1627 | 0.050354 | -0.19684 | -0.24261 | 6.3904 | 5.8548 | 16.8045 | 5.8044 | 16.7541 | 2.1057 | 121.138 | 6.34 | 120.9824 | 121.019 | 121.0281 | 121.1288 | 121.0785 | -121.1655 | -121.225 | 121.2479 | 121.0327 | 2.5818 | 11.9293
2433.1094 | 121.4264 | -0.83771 | 120.4193 | -0.0057221 | 6.9421 | 0.066245 | 0.08935 | -0.0031403 | 0.0045566 | 0.017069 | -0.0028687 | 0.045196 | -1.3829 | 0.12463 | -0.0041272 | 0.025148 | 0.040567 | 1.7395 | 120.3186 | -0.72784 | 120.4102 | 1.3641 | 0.42572 | 1.7899 | 11.1557 | 120.2271 | -0.77362 | 120.2271 | 5.6213 | 16.1224 | 5.1086 | 0.10986 | -0.10071 | -0.009156 | 2.2018 | 2.6276 | 1.2634 | 2.5177 | 1.1536 | 0.064087 | -0.19226 | -0.19226 | 6.459 | 5.9464 | 16.9601 | 5.8823 | 16.8961 | 2.092 | 121.138 | 6.395 | 121.0007 | 121.0464 | 121.0007 | 121.1563 | 121.0648 | -121.1472 | -121.1929 | 121.2479 | 121.0648 | 2.5772 | 11.9934
2434.875 | 121.2936 | -0.89264 | 120.4697 | -0.020981 | 6.9445 | 0.066885 | 0.094691 | 0.0043365 | 0.0056248 | 0.01835 | 0.033752 | 0.048614 | -1.3816 | 0.11031 | -0.005409 | 0.025575 | 0.040781 | 1.712 | 120.401 | -0.83313 | 120.3278 | 1.2405 | 0.35706 | 1.6937 | 11.1008 | 120.3323 | -0.86975 | 120.0806 | 5.4932 | 16.0767 | 5.0308 | 0.059509 | -0.068665 | -0.14191 | 2.1332 | 2.5864 | 1.2497 | 2.5269 | 1.1902 | 0.022888 | -0.13733 | -0.3891 | 6.3858 | 5.9235 | 16.9693 | 5.9006 | 16.9464 | 2.0737 | 121.1609 | 6.3629 | 120.9503 | 121.2341 | 121.2021 | 121.2936 | 121.225 | -121.3028 | -121.3394 | 121.2204 | 120.9732 | 2.6047 | 11.9934
2436.6562 | 121.2845 | -0.91095 | 120.4376 | -0.013352 | 6.9434 | 0.062613 | 0.088495 | -0.0010041 | 0.0045566 | 0.013651 | -0.0028687 | 0.047546 | -1.3799 | 0.11907 | -0.0060498 | 0.025148 | 0.044839 | 1.68 | 120.2637 | -0.77362 | 120.282 | 1.2314 | 0.32044 | 1.6663 | 11.142 | 120.2316 | -0.85144 | 120.0623 | 5.5435 | 16.1819 | 5.0491 | 0.13733 | -0.17395 | -0.15564 | 2.1423 | 2.5772 | 1.2314 | 2.4399 | 1.0941 | 0.05951 | -0.20599 | -0.37537 | 6.4545 | 5.9601 | 17.0929 | 5.9006 | 17.0334 | 2.005 | 121.0556 | 6.395 | 120.9137 | 121.0373 | 121.0831 | 121.1746 | 121.1426 | -121.2112 | -121.2891 | 121.1929 | 120.9732 | 2.5909 | 12.0529
2438.4375 | 121.3211 | -1.4923 | 119.7144 | 0.024795 | 6.9425 | 0.065817 | 0.089777 | -0.00079049 | 0.0041294 | 0.019418 | 0.0062865 | 0.046051 | -1.3818 | 0.11822 | -0.0037 | 0.027497 | 0.039712 | 1.0162 | 119.5862 | -1.4694 | 119.6503 | 0.60425 | -0.29297 | 1.0757 | 10.6979 | 119.5404 | -1.4648 | 119.4901 | 5.0949 | 15.7608 | 4.5319 | 0.022889 | -0.12817 | -0.064086 | 2.0966 | 2.5681 | 1.1993 | 2.5452 | 1.1765 | 0.027466 | -0.17395 | -0.2243 | 6.5872 | 6.0242 | 17.2531 | 5.9967 | 17.2256 | 2.0737 | 121.1197 | 6.5598 | 120.9549 | 121.0556 | 121.0052 | 121.0785 | 121.0327 | -121.1838 | -121.1792 | 121.1426 | 120.9824 | 2.5085 | 12.1902
2440.2188 | 121.3257 | -1.4603 | 119.7372 | -0.0057221 | 6.9447 | 0.063895 | 0.08935 | -0.0024995 | 0.0037022 | 0.017923 | -0.0028687 | 0.046264 | -1.3809 | 0.11523 | -0.0066906 | 0.025361 | 0.03544 | 1.1215 | 119.5908 | -1.3412 | 119.7372 | 0.72327 | -0.18768 | 1.1581 | 10.7712 | 119.5633 | -1.4099 | 119.5129 | 5.1498 | 15.9073 | 4.6143 | 0.11902 | -0.14648 | 0 | 2.1835 | 2.6184 | 1.2726 | 2.4994 | 1.1536 | 0.050354 | -0.17395 | -0.22431 | 6.6101 | 6.0745 | 17.3676 | 6.0242 | 17.3172 | 2.0645 | 121.0785 | 6.5598 | 120.9229 | 120.932 | 120.9732 | 121.051 | 121.0236 | -121.0785 | -121.1472 | 121.1975 | 120.9732 | 2.5818 | 12.2314
2441.9219 | 121.1929 | -1.506 | 119.7189 | 0.0019074 | 6.9445 | 0.063895 | 0.091486 | 0.0036957 | 0.0030612 | 0.015787 | -0.0028687 | 0.048614 | -1.3794 | 0.11309 | -0.0026318 | 0.026429 | 0.039926 | 1.0712 | 119.6228 | -1.3733 | 119.6136 | 0.60425 | -0.31586 | 1.0437 | 10.6522 | 119.5724 | -1.4236 | 119.3985 | 5.04 | 15.7883 | 4.541 | 0.13275 | -0.09613 | -0.10529 | 2.1103 | 2.5497 | 1.1902 | 2.417 | 1.0574 | 0.082397 | -0.14648 | -0.32043 | 6.546 | 6.0471 | 17.2943 | 5.9647 | 17.2119 | 1.9775 | 120.9869 | 6.4636 | 120.8221 | 120.9961 | 120.9961 | 121.1288 | 121.0785 | -121.0922 | -121.1426 | 121.1197 | 120.9045 | 2.5772 | 12.1582
2443.7031 | 121.2753 | -1.506 | 119.6411 | 0.040054 | 6.9474 | 0.067526 | 0.08935 | 0.0015595 | 0.0062656 | 0.018564 | 0.018494 | 0.048187 | -1.3803 | 0.11715 | -0.0034864 | 0.028352 | 0.041635 | 1.0803 | 119.5129 | -1.4374 | 119.6594 | 0.72784 | -0.2243 | 1.1215 | 10.8032 | 119.5038 | -1.506 | 119.4122 | 5.1178 | 15.9668 | 4.6097 | 0.068664 | -0.12817 | 0.018311 | 2.2339 | 2.6276 | 1.2817 | 2.5589 | 1.2131 | 0 | -0.13733 | -0.22888 | 6.6238 | 6.1157 | 17.4728 | 6.1157 | 17.4728 | 2.1652 | 121.0968 | 6.6238 | 120.9183 | 120.9503 | 121.0098 | 121.019 | 121.0098 | -121.0785 | -121.1472 | 121.1655 | 120.9183 | 2.5864 | 12.3093
2445.4688 | 121.2204 | -1.5976 | 119.5541 | 0.0019074 | 6.9457 | 0.066672 | 0.090632 | -0.0014313 | 0.005411 | 0.015573 | 0.00018312 | 0.047332 | -1.3843 | 0.12185 | -0.0066906 | 0.026643 | 0.039285 | 0.98877 | 119.4305 | -1.4786 | 119.5496 | 0.59052 | -0.30212 | 1.0254 | 10.7117 | 119.3848 | -1.5335 | 119.2932 | 5.0812 | 16.0172 | 4.5639 | 0.11902 | -0.1236 | -0.004577 | 2.1881 | 2.623 | 1.2955 | 2.504 | 1.1765 | 0.064087 | -0.16937 | -0.26093 | 6.6788 | 6.1615 | 17.6147 | 6.0974 | 17.5507 | 2.0691 | 121.0281 | 6.6147 | 120.8267 | 120.9091 | 120.9183 | 121.0281 | 120.9824 | -121.0327 | -121.0876 | 121.1472 | 120.8908 | 2.5864 | 12.3093
2447.1875 | 121.2479 | -1.6708 | 119.4717 | 0.047683 | 6.9447 | 0.06774 | 0.092768 | 0.0026275 | 0.0022068 | 0.020273 | 0.0093383 | 0.047119 | -1.382 | 0.11544 | -0.0041272 | 0.026216 | 0.042917 | 0.90179 | 119.3756 | -1.5701 | 119.458 | 0.49896 | -0.40283 | 0.93384 | 10.6796 | 119.3161 | -1.6205 | 119.2337 | 4.9942 | 16.0538 | 4.5319 | 0.10071 | -0.096131 | -0.013733 | 2.1698 | 2.6047 | 1.268 | 2.504 | 1.1673 | 0.050354 | -0.15564 | -0.23804 | 6.665 | 6.2027 | 17.7246 | 6.1523 | 17.6743 | 2.0691 | 121.0281 | 6.6147 | 120.8542 | 120.9457 | 120.9366 | 121.0464 | 120.9869 | -121.0419 | -121.0922 | 121.1288 | 120.9045 | 2.5726 | 12.3505
2448.9531 | 121.2433 | -1.712 | 119.371 | 0.08583 | 6.95 | 0.068381 | 0.090632 | -0.00079049 | 0.0049838 | 0.017709 | 0.018494 | 0.047973 | -1.3816 | 0.11993 | -0.003059 | 0.028352 | 0.037149 | 0.89722 | 119.2932 | -1.6571 | 119.4168 | 0.50812 | -0.41657 | 0.91095 | 10.7483 | 119.2474 | -1.712 | 119.1879 | 5.0079 | 16.1545 | 4.5319 | 0.054932 | -0.07782 | 0.045776 | 2.2202 | 2.623 | 1.2955 | 2.5681 | 1.2405 | 0 | -0.1236 | -0.18311 | 6.72 | 6.2439 | 17.8665 | 6.2439 | 17.8665 | 2.1652 | 121.0739 | 6.72 | 120.9 | 120.9503 | 120.9595 | 121.0052 | 120.9595 | -121.0281 | -121.0831 | 121.1288 | 120.9 | 2.6093 | 12.4603
2450.7188 | 121.2341 | -1.8494 | 119.252 | -0.0057221 | 6.946 | 0.065176 | 0.088923 | 0.00070491 | 0.0045566 | 0.015573 | -0.0028687 | 0.04776 | -1.3801 | 0.12035 | -0.00049559 | 0.028779 | 0.038858 | 0.70038 | 119.1193 | -1.7715 | 119.1879 | 0.29297 | -0.61798 | 0.72784 | 10.5698 | 119.0643 | -1.7807 | 119.0506 | 4.8889 | 16.1041 | 4.4632 | 0.07782 | -0.13275 | -0.064087 | 2.1423 | 2.5772 | 1.2314 | 2.4994 | 1.1536 | 0.068664 | -0.18768 | -0.20142 | 6.7383 | 6.3126 | 17.9535 | 6.2439 | 17.8848 | 2.0645 | 120.9595 | 6.6696 | 120.8313 | 120.8908 | 120.845 | 120.9686 | 120.9137 | -121.0236 | -121.0327 | 121.0373 | 120.9 | 2.5497 | 12.4191
2452.4219 | 121.1151 | -1.973 | 119.1467 | 0.070572 | 6.9502 | 0.066245 | 0.092768 | 0.0066863 | 0.0037022 | 0.019632 | 0.018494 | 0.049255 | -1.3799 | 0.11544 | -0.008186 | 0.027284 | 0.041421 | 0.59967 | 119.0598 | -1.9135 | 119.0414 | 0.14648 | -0.73242 | 0.6134 | 10.4279 | 119.0506 | -1.9638 | 118.8171 | 4.7012 | 16.0172 | 4.2984 | 0.059509 | -0.086976 | -0.10529 | 2.1194 | 2.5864 | 1.2405 | 2.5269 | 1.181 | 0.009155 | -0.096131 | -0.32959 | 6.6742 | 6.2714 | 17.9901 | 6.2622 | 17.981 | 2.0599 | 120.9549 | 6.665 | 120.7809 | 120.9732 | 121.0144 | 121.0327 | 121.0236 | -121.0602 | -121.1105 | 121.0144 | 120.7901 | 2.5726 | 12.4008
2454.1875 | 121.1563 | -2.3804 | 118.6752 | -0.013352 | 6.9474 | 0.063467 | 0.088923 | -0.0057037 | 0.0045566 | 0.014291 | 0.00018312 | 0.045196 | -1.3831 | 0.12163 | -0.0069044 | 0.028779 | 0.036081 | 0.20142 | 118.5196 | -2.2476 | 118.6752 | -0.14648 | -1.062 | 0.25635 | 10.2081 | 118.483 | -2.3071 | 118.4463 | 4.4632 | 15.8386 | 3.9413 | 0.13275 | -0.15564 | 0 | 2.2339 | 2.6367 | 1.3184 | 2.504 | 1.1856 | 0.073242 | -0.19226 | -0.22888 | 6.8436 | 6.3217 | 18.219 | 6.2485 | 18.1458 | 2.1011 | 120.9229 | 6.7703 | 120.7535 | 120.7672 | 120.7901 | 120.9 | 120.8633 | -120.9229 | -120.9824 | 121.0556 | 120.8267 | 2.5818 | 12.5885
2455.9688 | 121.0785 | -2.8427 | 118.2037 | 0.062942 | 6.9515 | 0.066458 | 0.09405 | 0.0024139 | 0.006052 | 0.019418 | 0.01239 | 0.050964 | -1.3782 | 0.11416 | -0.007118 | 0.027711 | 0.044839 | -0.2655 | 118.1351 | -2.774 | 118.1259 | -0.68665 | -1.5884 | -0.24261 | 9.787 | 118.0756 | -2.8107 | 117.9108 | 4.0375 | 15.4266 | 3.5156 | 0.068664 | -0.068664 | -0.077819 | 2.1561 | 2.6001 | 1.2543 | 2.5314 | 1.1856 | 0.032043 | -0.12817 | -0.29297 | 6.8802 | 6.3583 | 18.2693 | 6.3263 | 18.2373 | 2.0874 | 120.9 | 6.8481 | 120.7214 | 120.9091 | 120.8862 | 120.9778 | 120.9183 | -120.9778 | -121.0144 | 120.9686 | 120.7535 | 2.5772 | 12.6297
2457.6875 | 121.0602 | -4.8523 | 116.0294 | -0.013352 | 6.9449 | 0.064322 | 0.087214 | -0.0014313 | 0.004343 | 0.016428 | -0.0059205 | 0.044342 | -1.3818 | 0.12057 | -0.0075452 | 0.027925 | 0.043558 | -2.2385 | 115.8829 | -4.7104 | 116.1072 | -2.5681 | -3.4836 | -2.1698 | 8.313 | 115.8783 | -4.747 | 115.8554 | 2.5085 | 13.8794 | 1.6159 | 0.14191 | -0.14648 | 0.07782 | 2.2842 | 2.6825 | 1.3687 | 2.5406 | 1.2268 | 0.10529 | -0.15106 | -0.17395 | 7.3608 | 6.4682 | 18.7317 | 6.3629 | 18.6264 | 2.1423 | 120.8176 | 7.2556 | 120.6024 | 120.5933 | 120.6253 | 120.7352 | 120.7306 | -120.7397 | -120.7764 | 120.9595 | 120.7077 | 2.6138 | 13.1653
2459.4531 | 120.9274 | -4.4357 | 116.3589 | 0.047683 | 6.9494 | 0.06774 | 0.090204 | 0.00070491 | 0.0047702 | 0.015787 | 0.0062865 | 0.045623 | -1.3792 | 0.12356 | -0.0028454 | 0.030488 | 0.042917 | -1.799 | 116.3086 | -4.303 | 116.4505 | -2.1652 | -3.1586 | -1.7715 | 8.6426 | 116.2262 | -4.3625 | 116.1575 | 2.7695 | 14.2639 | 2.0462 | 0.13275 | -0.050354 | 0.091552 | 2.2705 | 2.6642 | 1.2772 | 2.5314 | 1.1444 | 0.073242 | -0.13275 | -0.20142 | 7.2052 | 6.4819 | 18.6996 | 6.4087 | 18.6264 | 2.1378 | 120.7535 | 7.132 | 120.52 | 120.6116 | 120.5887 | 120.7443 | 120.6619 | -120.6619 | -120.7214 | 120.8862 | 120.5933 | 2.6367 | 13.0783
2461.1719 | 120.7855 | -6.5048 | 114.1525 | 0.0095369 | 6.947 | 0.065817 | 0.087641 | -0.0014313 | 0.0024204 | 0.017923 | -0.0028687 | 0.046264 | -1.3782 | 0.11971 | -0.0079724 | 0.027925 | 0.039285 | -3.6667 | 113.9832 | -6.427 | 113.8504 | -4.4174 | -5.2368 | -4.0878 | 6.6513 | 113.6536 | -6.6147 | 114.1434 | 1.0117 | 12.2452 | 0.19684 | 0.07782 | -0.16937 | -0.30212 | 2.0874 | 2.417 | 1.268 | 2.3392 | 1.1902 | -0.10986 | -0.49896 | -0.009155 | 7.5165 | 6.7017 | 18.75 | 6.8115 | 18.8599 | 2.0096 | 120.2774 | 7.6263 | 120.7581 | 120.4102 | 120.2682 | 120.488 | 120.1584 | -120.5795 | -120.7672 | 120.3552 | 120.6482 | 2.8381 | 13.1561
2462.9375 | 120.694 | -7.9926 | 112.5092 | 0.047683 | 6.9496 | 0.063895 | 0.088709 | -0.00014949 | 0.0047702 | 0.017709 | 0.0093383 | 0.045623 | -1.3773 | 0.1227 | -0.0041272 | 0.027497 | 0.045694 | -5.4153 | 112.4313 | -7.8964 | 112.5 | -5.8411 | -6.7429 | -5.4428 | 5.7449 | 112.3672 | -7.9697 | 112.4084 | -0.09613 | 11.2335 | -1.3962 | 0.096131 | -0.07782 | -0.009155 | 2.1515 | 2.5497 | 1.2497 | 2.4536 | 1.1536 | 0.022888 | -0.14191 | -0.10071 | 7.8964 | 6.5964 | 19.2261 | 6.5735 | 19.2032 | 2.0554 | 120.3964 | 7.8735 | 120.3781 | 120.3278 | 120.3369 | 120.4239 | 120.3598 | -120.4056 | -120.4788 | 120.4926 | 120.401 | 2.5772 | 13.7375
2464.7188 | 121.1014 | -0.40741 | 120.607 | 0.017166 | 6.9477 | 0.064749 | 0.091486 | -0.00036309 | 0.006052 | 0.017709 | 0.0032349 | 0.046478 | -1.3822 | 0.12633 | -0.004768 | 0.026857 | 0.043771 | 2.092 | 120.4926 | -0.31128 | 120.5566 | 1.7441 | 0.86517 | 2.2202 | 11.9202 | 120.4422 | -0.3479 | 120.369 | 6.1066 | 17.9352 | 6.0837 | 0.096131 | -0.11444 | -0.050354 | 2.1515 | 2.6276 | 1.2726 | 2.5314 | 1.1765 | 0.05951 | -0.16479 | -0.23804 | 6.514 | 6.4911 | 18.3426 | 6.4316 | 18.2831 | 2.0554 | 120.8679 | 6.4545 | 120.7169 | 120.8038 | 120.7901 | 120.9 | 120.8496 | -120.9183 | -120.9549 | 120.9641 | 120.7764 | 2.4994 | 12.3276
2466.4219 | 121.17 | -0.40741 | 120.6711 | 0.0019074 | 6.9481 | 0.064322 | 0.088282 | 0.0026275 | 0.0024204 | 0.012582 | 0.00018312 | 0.048187 | -1.3805 | 0.11694 | -0.0058362 | 0.027925 | 0.044839 | 2.1194 | 120.5109 | -0.2655 | 120.6757 | 1.8127 | 0.91553 | 2.243 | 11.9797 | 120.4971 | -0.34332 | 120.4514 | 6.1707 | 18.0267 | 6.1478 | 0.14191 | -0.16022 | 0.004577 | 2.2202 | 2.6505 | 1.3229 | 2.5085 | 1.181 | 0.064087 | -0.17395 | -0.21973 | 6.5781 | 6.5552 | 18.4341 | 6.4911 | 18.3701 | 2.0782 | 120.9412 | 6.514 | 120.7947 | 120.7764 | 120.8405 | 120.9183 | 120.9045 | -120.9366 | -121.0144 | 121.0831 | 120.8588 | 2.5269 | 12.3871
2468.2031 | 121.2341 | -0.39368 | 120.7169 | -0.013352 | 6.9453 | 0.063895 | 0.090204 | -0.0014313 | 0.0034884 | 0.013437 | -0.0059205 | 0.04776 | -1.3846 | 0.1321 | -0.0051954 | 0.027284 | 0.04313 | 2.0737 | 120.5566 | -0.28839 | 120.6665 | 1.7349 | 0.88806 | 2.2247 | 11.9843 | 120.5246 | -0.33417 | 120.4742 | 6.1523 | 18.1137 | 6.1661 | 0.10529 | -0.16022 | -0.050354 | 2.1286 | 2.6184 | 1.2817 | 2.5131 | 1.1765 | 0.05951 | -0.19226 | -0.24262 | 6.546 | 6.5598 | 18.5074 | 6.5002 | 18.4479 | 2.0233 | 120.9549 | 6.4865 | 120.8084 | 120.845 | 120.8588 | 120.9503 | 120.9183 | -121.0052 | -121.051 | 121.0602 | 120.8679 | 2.4673 | 12.3779
2469.9688 | 121.1105 | -0.43488 | 120.7764 | 0.0019074 | 6.9496 | 0.066245 | 0.092982 | 0.0024139 | 0.0081882 | 0.017282 | -0.0028687 | 0.047973 | -1.3829 | 0.12014 | -0.004768 | 0.02942 | 0.042703 | 2.037 | 120.639 | -0.32044 | 120.6024 | 1.6251 | 0.75073 | 2.1103 | 11.911 | 120.5704 | -0.37994 | 120.3918 | 6.0059 | 18.0542 | 6.0837 | 0.11444 | -0.13733 | -0.17395 | 2.0599 | 2.5452 | 1.1856 | 2.4307 | 1.0712 | 0.054931 | -0.20599 | -0.38452 | 6.4407 | 6.5186 | 18.4891 | 6.4636 | 18.4341 | 1.9455 | 120.9229 | 6.3858 | 120.7718 | 120.9595 | 120.9503 | 121.0739 | 121.0052 | -121.0968 | -121.1563 | 121.0373 | 120.8267 | 2.4719 | 12.3459
2471.6875 | 121.2891 | -0.41199 | 120.7214 | -0.013352 | 6.95 | 0.064536 | 0.08935 | -0.0054901 | 0.0030612 | 0.013651 | -0.0059205 | 0.047973 | -1.3822 | 0.1227 | -0.0037 | 0.026643 | 0.041849 | 2.0691 | 120.5887 | -0.28839 | 120.7169 | 1.7944 | 0.91553 | 2.2476 | 12.1536 | 120.5429 | -0.36621 | 120.5292 | 6.2119 | 18.3472 | 6.2256 | 0.1236 | -0.13275 | -0.004578 | 2.2064 | 2.6596 | 1.3275 | 2.536 | 1.2039 | 0.045776 | -0.17853 | -0.19226 | 6.6238 | 6.6376 | 18.7592 | 6.5918 | 18.7134 | 2.0828 | 121.0052 | 6.5781 | 120.8954 | 120.8771 | 120.9091 | 121.0007 | 120.9549 | -121.0098 | -121.0876 | 121.1288 | 120.9412 | 2.4811 | 12.5656
2473.4531 | 121.2158 | -0.41657 | 120.7535 | -0.013352 | 6.95 | 0.065176 | 0.089991 | -0.0031403 | 0.0039158 | 0.0207 | -0.0059205 | 0.047546 | -1.3805 | 0.1274 | -0.0073316 | 0.027497 | 0.042276 | 2.1149 | 120.5795 | -0.29297 | 120.7214 | 1.7944 | 0.91095 | 2.243 | 12.1353 | 120.5612 | -0.3479 | 120.488 | 6.1661 | 18.3609 | 6.2027 | 0.1236 | -0.17395 | -0.032043 | 2.211 | 2.6596 | 1.3275 | 2.536 | 1.2039 | 0.068665 | -0.19226 | -0.2655 | 6.5826 | 6.6193 | 18.7775 | 6.5506 | 18.7088 | 2.0874 | 121.0144 | 6.514 | 120.8359 | 120.8725 | 120.9091 | 120.9961 | 120.9778 | -121.0464 | -121.1014 | 121.138 | 120.9045 | 2.5314 | 12.5519
2475.2344 | 121.1517 | -0.44861 | 120.7809 | -0.02861 | 6.9504 | 0.064536 | 0.090632 | 0.0043365 | 0.0032748 | 0.017282 | 0.00018312 | 0.051178 | -1.3811 | 0.11779 | -0.007118 | 0.026216 | 0.048044 | 2.005 | 120.6528 | -0.32044 | 120.6253 | 1.6754 | 0.8194 | 2.1423 | 12.0483 | 120.6528 | -0.45776 | 120.401 | 6.0791 | 18.3701 | 6.1661 | 0.12817 | -0.12817 | -0.15564 | 2.124 | 2.5909 | 1.268 | 2.4628 | 1.1398 | -0.009156 | -0.12817 | -0.37994 | 6.5277 | 6.6147 | 18.8187 | 6.6238 | 18.8278 | 1.9959 | 120.9457 | 6.5369 | 120.8588 | 120.9732 | 121.1105 | 121.1014 | 121.1014 | -121.1014 | -121.2387 | 121.0739 | 120.8496 | 2.4536 | 12.4969
2476.9375 | 121.2021 | -0.43945 | 120.7672 | -0.0057221 | 6.9524 | 0.065176 | 0.089991 | -0.0031403 | 0.0041294 | 0.014505 | -0.0059205 | 0.049469 | -1.3822 | 0.12121 | -0.007118 | 0.029847 | 0.043771 | 2.0737 | 120.6162 | -0.30212 | 120.6802 | 1.7395 | 0.88348 | 2.1927 | 12.1353 | 120.5841 | -0.35706 | 120.433 | 6.1478 | 18.4982 | 6.189 | 0.13733 | -0.15106 | -0.086975 | 2.179 | 2.6321 | 1.3229 | 2.4948 | 1.1856 | 0.082397 | -0.18311 | -0.33417 | 6.5872 | 6.6284 | 18.9377 | 6.546 | 18.8553 | 2.0416 | 120.9824 | 6.5048 | 120.7901 | 120.9183 | 120.9412 | 121.0556 | 121.0236 | -121.0693 | -121.1243 | 121.1197 | 120.8725 | 2.5131 | 12.5748
2478.7031 | 121.2296 | -0.42572 | 120.7581 | 0.047683 | 6.9545 | 0.067313 | 0.093622 | 0.0019867 | 0.005411 | 0.016641 | 0.015442 | 0.05075 | -1.3805 | 0.12142 | -0.0062634 | 0.026429 | 0.043344 | 2.0782 | 120.6665 | -0.36163 | 120.7031 | 1.7303 | 0.85602 | 2.1835 | 12.1765 | 120.6162 | -0.38452 | 120.4788 | 6.1844 | 18.5898 | 6.2439 | 0.064087 | -0.091553 | -0.054932 | 2.1561 | 2.6093 | 1.2817 | 2.5452 | 1.2177 | 0.041199 | -0.14191 | -0.27924 | 6.6101 | 6.6696 | 19.0155 | 6.6284 | 18.9743 | 2.092 | 121.0648 | 6.5689 | 120.8633 | 121.0281 | 121.0007 | 121.0922 | 121.0419 | -121.1197 | -121.1426 | 121.1288 | 120.9045 | 2.504 | 12.6022
2480.4688 | 121.3028 | -0.41657 | 120.7672 | -0.0057221 | 6.9528 | 0.064108 | 0.090845 | -0.0035675 | 0.0017796 | 0.015146 | 0.00018312 | 0.049896 | -1.3799 | 0.1227 | -0.005409 | 0.028993 | 0.046548 | 2.092 | 120.607 | -0.29755 | 120.7626 | 1.8036 | 0.95215 | 2.2614 | 12.2818 | 120.5704 | -0.35706 | 120.5383 | 6.2851 | 18.7225 | 6.34 | 0.11902 | -0.16022 | -0.004578 | 2.2202 | 2.6779 | 1.3687 | 2.5589 | 1.2497 | 0.059509 | -0.19684 | -0.22888 | 6.7017 | 6.7566 | 19.1391 | 6.6971 | 19.0796 | 2.1011 | 121.0602 | 6.6422 | 120.8954 | 120.9045 | 120.9274 | 121.0236 | 120.9869 | -121.0648 | -121.1243 | 121.1792 | 120.9549 | 2.5085 | 12.6984
2482.1875 | 121.225 | -0.44403 | 120.7718 | -0.013352 | 6.9549 | 0.065604 | 0.090204 | -0.00014949 | 0.0019932 | 0.016 | -0.0028687 | 0.050323 | -1.382 | 0.12441 | -0.00092279 | 0.030702 | 0.04548 | 2.005 | 120.6528 | -0.36621 | 120.6345 | 1.6342 | 0.80566 | 2.1332 | 12.236 | 120.5978 | -0.37994 | 120.5154 | 6.189 | 18.7225 | 6.3126 | 0.07782 | -0.11902 | -0.13733 | 2.0782 | 2.5772 | 1.2497 | 2.4994 | 1.1719 | 0.064087 | -0.17395 | -0.25635 | 6.633 | 6.7566 | 19.1666 | 6.6925 | 19.1025 | 2.0004 | 121.0007 | 6.5689 | 120.8954 | 121.019 | 120.9778 | 121.0968 | 121.0419 | -121.138 | -121.1517 | 121.0785 | 120.9595 | 2.449 | 12.6801
2483.9688 | 121.1975 | -8.876 | 112.2345 | 0.0019074 | 6.9524 | 0.06539 | 0.088495 | -0.0067719 | 0.0024204 | 0.013223 | -0.0028687 | 0.046051 | -1.3784 | 0.12313 | -0.0049818 | 0.030061 | 0.046976 | -6.2714 | 112.0605 | -8.7479 | 112.1796 | -6.7062 | -7.608 | -6.2668 | 5.5206 | 111.9965 | -8.8303 | 112.0056 | -0.49896 | 11.6043 | -1.8631 | 0.12817 | -0.17395 | -0.054932 | 2.1698 | 2.6093 | 1.268 | 2.4811 | 1.1398 | 0.045777 | -0.23804 | -0.22888 | 8.3771 | 7.0129 | 20.4803 | 6.9672 | 20.4346 | 2.0416 | 120.9274 | 8.3313 | 120.8359 | 120.8084 | 120.8267 | 120.9366 | 120.8725 | -120.9824 | -121.0648 | 121.0556 | 120.8817 | 2.6047 | 14.3967
2485.6719 | 121.1288 | -8.9264 | 112.2391 | 0.0019074 | 6.9551 | 0.064536 | 0.0917 | 0.0019867 | 0.0039158 | 0.017923 | 0.00018312 | 0.050537 | -1.3771 | 0.12121 | -0.0028454 | 0.02942 | 0.04249 | -6.3217 | 112.1201 | -8.7891 | 112.088 | -6.8344 | -7.7408 | -6.3995 | 5.397 | 112.0468 | -8.8623 | 111.9186 | -0.6546 | 11.4761 | -1.9501 | 0.13733 | -0.11902 | -0.15106 | 2.092 | 2.5269 | 1.1856 | 2.3895 | 1.0483 | 0.064087 | -0.19226 | -0.32044 | 8.2718 | 6.9763 | 20.4025 | 6.9122 | 20.3384 | 1.9546 | 120.8771 | 8.2077 | 120.7809 | 120.9091 | 120.9091 | 121.0464 | 120.9732 | -121.0281 | -121.1014 | 121.0144 | 120.845 | 2.6047 | 14.3234
2487.4375 | 121.138 | -8.8257 | 112.3764 | 0.0019074 | 6.9507 | 0.064322 | 0.090845 | 0.0017731 | 0.002634 | 0.018564 | -0.0059205 | 0.048828 | -1.3779 | 0.11629 | -0.006477 | 0.030702 | 0.048257 | -6.2302 | 112.1567 | -8.7158 | 112.2345 | -6.6696 | -7.576 | -6.2347 | 5.5206 | 112.1429 | -8.7753 | 111.9965 | -0.53558 | 11.6684 | -1.8723 | 0.10986 | -0.21973 | -0.14191 | 2.1561 | 2.5909 | 1.2497 | 2.4811 | 1.1398 | 0.050354 | -0.23346 | -0.37994 | 8.2901 | 6.9534 | 20.4941 | 6.9031 | 20.4437 | 2.0462 | 120.9503 | 8.2397 | 120.7718 | 120.8725 | 120.9183 | 120.9824 | 120.9686 | -121.0922 | -121.1517 | 121.0602 | 120.8221 | 2.5955 | 14.3463
2489.1406 | 121.2341 | -10.0937 | 111.0626 | 0.0095369 | 6.9558 | 0.063681 | 0.090418 | 0.00070491 | 0.0062656 | 0.019418 | 0.00018312 | 0.047546 | -1.3749 | 0.118 | -0.0051954 | 0.029847 | 0.047189 | -6.3629 | 112.0605 | -8.8623 | 111.7722 | -6.9305 | -7.7957 | -6.3812 | 5.4977 | 111.9553 | -9.0408 | 110.8932 | -1.4099 | 10.8215 | -2.829 | 1.2314 | 0.99792 | 0.70953 | 3.1631 | 3.7125 | 2.298 | 2.4811 | 1.0666 | 1.0529 | 0.89264 | -0.16937 | 8.6838 | 7.2647 | 20.9152 | 6.2119 | 19.8624 | 1.9318 | 120.6345 | 7.6309 | 119.9341 | 120.9229 | 120.9961 | 122.1542 | 122.0489 | -119.9249 | -120.1035 | 121.8658 | 120.9869 | 3.7308 | 15.5914
2490.9219 | 121.1838 | -18.4433 | 103.7384 | -0.0057221 | 6.9549 | 0.066672 | 0.091059 | -0.0042083 | 0.0039158 | 0.016214 | 0.00018312 | 0.046264 | -1.3745 | 0.12249 | 0.00014521 | 0.033906 | 0.047616 | -13.7512 | 104.5715 | -16.008 | 102.4017 | -17.2211 | -16.3651 | -12.735 | 0.3891 | 104.6677 | -16.2735 | 102.5116 | -9.6588 | 2.5589 | -10.9268 | 2.4353 | 0.83313 | -1.3367 | 1.2222 | 5.7083 | 2.0782 | 3.273 | -0.35706 | 2.1698 | 0.92926 | -1.2268 | 8.7845 | 7.5165 | 21.0022 | 5.3467 | 18.8324 | -1.2131 | 118.4097 | 6.6147 | 118.7851 | 120.5795 | 120.9412 | 123.0148 | 123.111 | -119.7464 | -120.0119 | 120.845 | 120.9549 | 4.6921 | 18.8324
2492.7031 | 121.0236 | -70.9305 | 49.6674 | 0.032425 | 6.953 | 0.065817 | 0.093409 | 0.00091851 | 0.0058384 | 0.017496 | 0.0093383 | 0.03836 | -1.3442 | 0.11416 | -0.0058362 | 0.03946 | 0.058084 | -67.9779 | 49.3881 | -71.1731 | 50.2258 | -68.3166 | -69.9738 | -68.6691 | -43.4235 | 49.5712 | -70.9534 | 49.9512 | -49.649 | -41.1758 | -62.4298 | -0.24262 | -0.27923 | 0.55847 | 2.6138 | 2.2614 | 0.95673 | 2.504 | 1.1993 | -0.022888 | -0.09613 | 0.28381 | 21.2814 | 8.5007 | 29.7546 | 8.5236 | 29.7775 | 2.8564 | 121.3989 | 21.3043 | 120.9045 | 120.5612 | 120.5246 | 120.3186 | 120.5017 | -120.8405 | -120.6207 | 121.1563 | 120.8817 | 2.9526 | 27.507
2494.4844 | 120.8542 | -80.8319 | 39.6194 | 0.070572 | 6.9568 | 0.07009 | 0.09405 | -0.0010041 | 0.00947 | 0.020059 | 0.024597 | 0.037933 | -1.3356 | 0.11138 | -0.0026318 | 0.040956 | 0.059152 | -77.6688 | 39.5508 | -80.7953 | 39.6698 | -78.3554 | -79.6921 | -78.6301 | -51.2512 | 39.2303 | -81.2119 | 39.8529 | -57.3166 | -49.5071 | -72.0291 | 0.036621 | -0.068665 | 0.050354 | 2.4765 | 2.2018 | 1.1398 | 2.1652 | 1.1032 | -0.37994 | -0.3891 | 0.23346 | 23.5153 | 8.8028 | 31.3248 | 9.1827 | 31.7047 | 2.4399 | 120.4651 | 23.8953 | 121.0648 | 120.3461 | 120.4422 | 120.3827 | 120.0623 | -120.4147 | -120.8313 | 120.5017 | 120.6848 | 3.1631 | 29.5807
2496.2188 | 120.6894 | -86.2564 | 34.1721 | -0.013352 | 6.9541 | 0.068381 | 0.092768 | -0.00014949 | 0.0062656 | 0.017282 | -0.0089723 | 0.036438 | -1.3344 | 0.11544 | -0.0026318 | 0.040101 | 0.06022 | -81.9672 | 34.9457 | -85.5148 | 34.3735 | -83.7433 | -85.0296 | -83.6105 | -55.2841 | 34.3689 | -86.0596 | 34.1446 | -61.6104 | -54.0115 | -77.0554 | 0.74158 | 0.77362 | 0.20142 | 2.5131 | 2.6459 | 1.2268 | 1.9043 | 0.48523 | 0.19684 | 0.19684 | -0.027466 | 24.646 | 9.2011 | 32.2449 | 9.0042 | 32.048 | 1.7715 | 119.8883 | 24.4492 | 120.2042 | 120.4605 | 120.4285 | 121.2021 | 120.6253 | -119.6869 | -120.2316 | 120.6299 | 120.401 | 4.2892 | 30.9723
2498 | 120.4514 | -85.4782 | 34.7763 | -0.0057221 | 6.9562 | 0.065817 | 0.092982 | -0.0010041 | 0.0051974 | 0.017496 | -0.0059205 | 0.037078 | -1.3348 | 0.1101 | -0.0049818 | 0.039033 | 0.060861 | -79.0924 | 37.3077 | -82.5485 | 37.0239 | -80.8319 | -81.8665 | -80.3787 | -53.5812 | 36.8866 | -83.6609 | 34.8587 | -60.9558 | -53.1143 | -75.9567 | 2.9297 | 2.5314 | 2.2476 | 4.6463 | 5.0995 | 3.6118 | 2.1698 | 0.68207 | 1.8173 | 2.1103 | 0.082398 | 24.5224 | 9.5215 | 32.3639 | 7.7042 | 30.5466 | 1.7166 | 119.5724 | 22.7051 | 118.5196 | 119.8563 | 120.5475 | 122.7859 | 122.3648 | -117.3248 | -118.4372 | 122.5021 | 120.3369 | 6.3858 | 31.897
2499.7812 | 120.2316 | -87.7579 | 32.4142 | 0.0019074 | 6.9564 | 0.066885 | 0.090632 | 0.0015595 | 0.0049838 | 0.017282 | 0.0062865 | 0.036438 | -1.3359 | 0.11779 | -0.0056226 | 0.038179 | 0.065134 | -84.0408 | 32.2952 | -87.4649 | 32.4921 | -84.2789 | -85.3455 | -83.9859 | -56.1859 | 33.1833 | -87.1719 | 31.7322 | -63.1714 | -55.3391 | -78.4287 | 0.29297 | -0.11902 | 0.077819 | 3.479 | 3.772 | 2.4124 | 3.479 | 2.1194 | 0.58594 | 0.76904 | -0.68207 | 24.5865 | 9.3292 | 32.4188 | 8.7433 | 31.8329 | 3.186 | 119.957 | 24.0005 | 118.9041 | 119.7601 | 120.3552 | 120.0531 | 120.9412 | -119.8792 | -119.5862 | 120.2499 | 119.4901 | 3.717 | 31.572
2501.5 | 120.9183 | -119.5312 | 1.149 | 0.055313 | 6.9568 | 0.069876 | 0.092982 | -0.00014949 | 0.0066928 | 0.017923 | 0.015442 | 0.029388 | -1.3145 | 0.10519 | -0.0017774 | 0.046724 | 0.070901 | -115.5121 | 1.0025 | -119.4672 | 1.1627 | -116.5237 | -118.103 | -116.9266 | -81.3904 | 1.0712 | -119.7052 | 1.1719 | -87.3917 | -81.8573 | -109.1904 | 0.064087 | -0.14648 | 0.013733 | 3.0075 | 2.6047 | 1.4282 | 2.5406 | 1.3641 | -0.17395 | -0.07782 | 0.022888 | 32.1396 | 10.3409 | 37.674 | 10.5148 | 37.8479 | 2.9434 | 120.6299 | 32.3135 | 120.8771 | 120.4697 | 120.7764 | 120.5338 | 120.6024 | -120.6162 | -120.8542 | 120.694 | 120.7031 | 4.0192 | 38.1409
2503.2969 | 121.0648 | -119.014 | 1.7349 | -0.013352 | 6.9541 | 0.066458 | 0.090204 | 0.0022003 | 0.0028476 | 0.017709 | -0.0028687 | 0.026825 | -1.3158 | 0.11053 | -0.0051954 | 0.044587 | 0.07261 | -115.0177 | 1.5198 | -118.9041 | 1.7303 | -116.0019 | -117.5766 | -116.3864 | -81.1386 | 1.593 | -119.165 | 1.7441 | -86.9019 | -81.3446 | -108.6365 | 0.10986 | -0.21515 | -0.004577 | 3.0121 | 2.6276 | 1.4374 | 2.5177 | 1.3275 | -0.15106 | -0.14191 | 0.009156 | 32.1121 | 10.3775 | 37.6694 | 10.5286 | 37.8204 | 2.9022 | 120.6345 | 32.2632 | 120.9091 | 120.4239 | 120.7581 | 120.5338 | 120.607 | -120.639 | -120.9 | 120.7443 | 120.7581 | 3.9963 | 37.8754
2505 | 121.0052 | -118.5608 | 2.2202 | 0.032425 | 6.9551 | 0.064963 | 0.089991 | -0.0024995 | 0.0058384 | 0.018137 | 0.0062865 | 0.028747 | -1.3143 | 0.11138 | -0.004768 | 0.045869 | 0.068979 | -114.6057 | 2.0279 | -118.4692 | 2.1606 | -115.6494 | -117.1783 | -115.9882 | -80.9738 | 2.1286 | -118.7164 | 2.179 | -86.6501 | -81.0471 | -108.2428 | 0.091553 | -0.19226 | -0.059509 | 2.9114 | 2.5726 | 1.3824 | 2.4811 | 1.2909 | -0.15564 | -0.091553 | -0.041199 | 31.9107 | 10.318 | 37.5137 | 10.4736 | 37.6694 | 2.8198 | 120.6299 | 32.0663 | 120.8954 | 120.4971 | 120.845 | 120.5887 | 120.6894 | -120.6894 | -120.9366 | 120.7214 | 120.7397 | 3.9551 | 37.587
2506.7969 | 121.0876 | -117.9337 | 2.8519 | 0.0019074 | 6.9549 | 0.067313 | 0.090632 | -0.0014313 | 0.006052 | 0.015787 | -0.0059205 | 0.028961 | -1.3175 | 0.11416 | -0.001991 | 0.043519 | 0.070047 | -113.9465 | 2.6688 | -117.8329 | 2.8473 | -114.9994 | -116.5512 | -115.3702 | -80.5756 | 2.742 | -118.0573 | 2.8976 | -86.1282 | -80.5115 | -107.5607 | 0.10071 | -0.18311 | -0.004578 | 2.9343 | 2.5635 | 1.3824 | 2.4628 | 1.2817 | -0.1236 | -0.10986 | 0.045776 | 31.8054 | 10.3729 | 37.4222 | 10.4965 | 37.5458 | 2.8336 | 120.6802 | 31.929 | 120.9549 | 120.5017 | 120.7993 | 120.6024 | 120.6757 | -120.6848 | -120.9091 | 120.7809 | 120.8313 | 3.9871 | 37.3581
2508.5156 | 121.0144 | -117.7826 | 3.0441 | 0.055313 | 6.9558 | 0.066885 | 0.092768 | 0.0030547 | 0.0081882 | 0.021341 | 0.015442 | 0.032165 | -1.3143 | 0.10583 | -0.008827 | 0.04416 | 0.069833 | -113.8092 | 2.9068 | -117.7505 | 2.9984 | -114.8849 | -116.4047 | -115.2145 | -80.6076 | 2.9892 | -117.952 | 2.9617 | -86.0458 | -80.452 | -107.4509 | 0.032044 | -0.13733 | -0.045776 | 2.8976 | 2.5681 | 1.3779 | 2.536 | 1.3458 | -0.16937 | -0.054931 | -0.082397 | 31.7368 | 10.3317 | 37.3306 | 10.5011 | 37.5 | 2.8656 | 120.7489 | 31.9061 | 120.9137 | 120.6573 | 120.9412 | 120.6894 | 120.7718 | -120.7947 | -120.9961 | 120.7809 | 120.7443 | 3.9734 | 37.175
2510.2812 | 121.0144 | -117.897 | 2.9892 | 0.055313 | 6.9577 | 0.068167 | 0.092768 | 6.4114e-05 | 0.008829 | 0.021768 | 0.021545 | 0.029815 | -1.3134 | 0.10668 | -0.007118 | 0.043092 | 0.069192 | -113.9282 | 2.8336 | -117.8696 | 2.861 | -114.9948 | -116.5283 | -115.3107 | -80.7632 | 2.9114 | -118.0847 | 2.8336 | -86.1099 | -80.5115 | -107.5607 | 0.027466 | -0.15564 | -0.12817 | 2.9022 | 2.5864 | 1.3687 | 2.5589 | 1.3412 | -0.18768 | -0.07782 | -0.15564 | 31.7871 | 10.3363 | 37.3856 | 10.524 | 37.5732 | 2.8748 | 120.7306 | 31.9748 | 120.9183 | 120.7031 | 120.9961 | 120.7306 | 120.8084 | -120.8588 | -121.0739 | 120.7581 | 120.7306 | 3.9688 | 37.1338
2512.0469 | 121.0007 | -117.9474 | 2.9663 | 0.078201 | 6.9575 | 0.068808 | 0.091059 | 0.00091851 | 0.00712 | 0.018137 | 0.021545 | 0.029174 | -1.3134 | 0.10476 | -0.0051954 | 0.041383 | 0.074319 | -113.9511 | 2.8473 | -117.8833 | 2.8381 | -115.004 | -116.5283 | -115.3473 | -80.8548 | 2.8748 | -118.1122 | 2.8381 | -86.0962 | -80.5298 | -107.5928 | 0.064087 | -0.11902 | -0.12817 | 2.9434 | 2.6001 | 1.4191 | 2.536 | 1.355 | -0.16479 | -0.091553 | -0.12817 | 31.8512 | 10.3546 | 37.4176 | 10.5194 | 37.5824 | 2.8793 | 120.7214 | 32.016 | 120.9503 | 120.7306 | 120.9869 | 120.7947 | 120.8221 | -120.8496 | -121.0785 | 120.7855 | 120.7855 | 3.9963 | 37.0926
2513.7656 | 120.9824 | -117.8833 | 3.0167 | -0.013352 | 6.9583 | 0.06774 | 0.092127 | -0.00014949 | 0.0039158 | 0.015573 | -0.0028687 | 0.029174 | -1.3147 | 0.11758 | -0.0049818 | 0.045442 | 0.068552 | -113.9603 | 2.8381 | -117.7826 | 2.829 | -115.0589 | -116.6061 | -115.3931 | -81.0379 | 2.8885 | -118.0206 | 2.8885 | -86.1145 | -80.5435 | -107.5653 | 0.10071 | -0.17853 | -0.18768 | 2.8244 | 2.4902 | 1.2772 | 2.3895 | 1.1765 | -0.13733 | -0.12817 | -0.12817 | 31.7688 | 10.318 | 37.3398 | 10.4553 | 37.4771 | 2.7237 | 120.6116 | 31.9061 | 120.9091 | 120.6207 | 120.9091 | 120.7214 | 120.7718 | -120.7993 | -121.0373 | 120.7123 | 120.7718 | 3.923 | 36.8454
2515.5312 | 121.1426 | -117.8146 | 3.0121 | -0.0057221 | 6.9568 | 0.064749 | 0.090632 | -0.0039947 | 0.0047702 | 0.014932 | -0.0028687 | 0.029174 | -1.3162 | 0.10946 | -0.0056226 | 0.044587 | 0.073892 | -113.8641 | 2.7878 | -117.7277 | 3.0212 | -114.7888 | -116.3635 | -115.1825 | -80.8823 | 2.8793 | -117.9565 | 3.035 | -85.9039 | -80.3421 | -107.4463 | 0.086975 | -0.2243 | 0.009155 | 3.0258 | 2.6321 | 1.4511 | 2.5452 | 1.3641 | -0.14191 | -0.13275 | 0.022888 | 31.9107 | 10.3683 | 37.4725 | 10.5103 | 37.6144 | 2.9388 | 120.7489 | 32.0526 | 120.9915 | 120.5154 | 120.8359 | 120.6024 | 120.694 | -120.7397 | -120.9686 | 120.8359 | 120.8496 | 3.9505 | 36.9324
2517.25 | 121.0922 | -117.8513 | 3.0396 | -0.02861 | 6.9579 | 0.066458 | 0.088282 | -0.00057689 | 0.005411 | 0.014932 | -0.0059205 | 0.028534 | -1.3147 | 0.11245 | -0.0060498 | 0.04416 | 0.070047 | -113.855 | 2.8198 | -117.7368 | 2.9984 | -114.8483 | -116.3864 | -115.2145 | -81.0562 | 2.8931 | -117.9657 | 2.9755 | -85.9131 | -80.4245 | -107.5012 | 0.11444 | -0.21973 | -0.041199 | 3.0029 | 2.6367 | 1.4648 | 2.5223 | 1.3504 | -0.11444 | -0.14648 | -0.064087 | 31.9382 | 10.35 | 37.4268 | 10.4645 | 37.5412 | 2.8885 | 120.7352 | 32.0526 | 120.9412 | 120.5566 | 120.8588 | 120.6711 | 120.7443 | -120.7764 | -121.0052 | 120.8496 | 120.8267 | 3.9963 | 36.795
2519.0312 | 121.0556 | -117.6636 | 3.1952 | 0.0095369 | 6.9588 | 0.066458 | 0.091913 | 0.0017731 | 0.0058384 | 0.018991 | 0.0032349 | 0.030243 | -1.3153 | 0.10583 | -0.007118 | 0.043092 | 0.067697 | -113.7177 | 2.9984 | -117.6224 | 3.1219 | -114.7385 | -116.2994 | -115.0772 | -81.0379 | 3.0899 | -117.7963 | 3.1403 | -85.8582 | -80.3421 | -107.3364 | 0.041199 | -0.19684 | -0.073242 | 2.9251 | 2.5864 | 1.3641 | 2.5452 | 1.3229 | -0.13275 | -0.10529 | -0.054931 | 31.8054 | 10.3271 | 37.3215 | 10.4599 | 37.4542 | 2.8839 | 120.7443 | 31.9382 | 120.9366 | 120.6207 | 120.8862 | 120.6619 | 120.7535 | -120.8176 | -120.9915 | 120.7855 | 120.8038 | 3.9459 | 36.6257
2520.7344 | 121.1472 | -117.7094 | 3.1219 | 0.08583 | 6.9601 | 0.072012 | 0.092554 | 0.0058319 | 0.00947 | 0.019846 | 0.021545 | 0.029815 | -1.3139 | 0.11651 | -0.00028199 | 0.045015 | 0.071329 | -113.6765 | 2.9572 | -117.6636 | 3.1677 | -114.6973 | -116.2811 | -115.0726 | -81.1111 | 3.0441 | -117.8696 | 3.154 | -85.8032 | -80.3284 | -107.3318 | 0.045777 | -0.1648 | 0.045777 | 3.0121 | 2.6367 | 1.4282 | 2.5909 | 1.3824 | -0.16022 | -0.07782 | 0.032044 | 31.9061 | 10.3775 | 37.381 | 10.5377 | 37.5412 | 2.9663 | 120.8313 | 32.0663 | 121.0236 | 120.6207 | 120.9137 | 120.6665 | 120.7535 | -120.7855 | -120.9915 | 120.8771 | 120.8633 | 4.0329 | 36.5982
2522.5 | 121.0693 | -117.7505 | 3.1357 | 0.047683 | 6.9603 | 0.067099 | 0.091486 | 0.0077545 | 0.0047702 | 0.017496 | 0.01239 | 0.031738 | -1.3139 | 0.11266 | -0.0037 | 0.043733 | 0.072183 | -113.7634 | 2.9343 | -117.7048 | 3.0579 | -114.8163 | -116.3498 | -115.1367 | -81.3629 | 3.035 | -117.9062 | 3.0533 | -85.8856 | -80.4062 | -107.3914 | 0.045776 | -0.20142 | -0.07782 | 2.9343 | 2.6138 | 1.4008 | 2.5681 | 1.355 | -0.15564 | -0.10071 | -0.082397 | 31.8649 | 10.3592 | 37.3444 | 10.5148 | 37.5 | 2.8885 | 120.7626 | 32.0206 | 120.9595 | 120.639 | 120.9412 | 120.6848 | 120.7855 | -120.8405 | -121.0419 | 120.8084 | 120.8038 | 3.9871 | 36.3876
2524.2188 | 121.0098 | -117.7505 | 3.154 | -0.0057221 | 6.959 | 0.06774 | 0.091486 | -0.0010041 | 0.0047702 | 0.013437 | -0.0089723 | 0.029174 | -1.3139 | 0.11373 | -0.0045544 | 0.045015 | 0.071329 | -113.8 | 2.9617 | -117.6636 | 2.9663 | -114.9124 | -116.4642 | -115.2237 | -81.4636 | 3.0441 | -117.8833 | 3.0441 | -85.9497 | -80.4382 | -107.3685 | 0.086975 | -0.19226 | -0.18768 | 2.8381 | 2.5269 | 1.2863 | 2.4399 | 1.1993 | -0.13275 | -0.10986 | -0.10986 | 31.8008 | 10.3821 | 37.3123 | 10.5148 | 37.4451 | 2.7512 | 120.6299 | 31.9336 | 120.9274 | 120.6253 | 120.9274 | 120.7123 | 120.7947 | -120.8176 | -121.0373 | 120.7169 | 120.7947 | 3.9505 | 36.2869
2525.9844 | 121.0373 | -117.8787 | 3.035 | -0.013352 | 6.9583 | 0.066245 | 0.089991 | -0.0039947 | 0.0032748 | 0.017923 | -0.0059205 | 0.028534 | -1.3145 | 0.10647 | -0.0069044 | 0.043519 | 0.067483 | -113.8733 | 2.8152 | -117.7689 | 2.9572 | -114.8758 | -116.4368 | -115.2512 | -81.5277 | 2.9114 | -117.9886 | 2.9388 | -85.9131 | -80.4977 | -107.4371 | 0.10986 | -0.21973 | -0.07782 | 3.0029 | 2.6276 | 1.442 | 2.5177 | 1.3321 | -0.10986 | -0.1236 | -0.09613 | 31.9656 | 10.4416 | 37.381 | 10.5515 | 37.4908 | 2.8931 | 120.726 | 32.0755 | 120.9274 | 120.5841 | 120.9 | 120.694 | 120.7901 | -120.8038 | -121.0236 | 120.8359 | 120.8176 | 4.0054 | 36.351
2527.7656 | 121.0922 | -117.7734 | 3.1036 | 0.017166 | 6.9581 | 0.066672 | 0.0917 | 0.00027771 | 0.0051974 | 0.021768 | 0.0093383 | 0.029388 | -1.3151 | 0.11629 | -0.0049818 | 0.045442 | 0.073892 | -113.8046 | 2.8839 | -117.6956 | 3.0533 | -114.8026 | -116.3635 | -115.155 | -81.5277 | 2.9984 | -117.9153 | 3.0624 | -85.7849 | -80.3925 | -107.3044 | 0.077819 | -0.21973 | -0.050354 | 2.9709 | 2.6184 | 1.4099 | 2.5406 | 1.3321 | -0.14191 | -0.10529 | -0.041199 | 31.9885 | 10.4691 | 37.381 | 10.611 | 37.5229 | 2.8931 | 120.7489 | 32.1304 | 120.9778 | 120.5795 | 120.9137 | 120.6573 | 120.7718 | -120.7993 | -121.019 | 120.8267 | 120.8359 | 3.9688 | 36.2457
2529.5469 | 121.1105 | -117.8421 | 3.0075 | 0.047683 | 6.9583 | 0.067099 | 0.091273 | -0.0016449 | 0.0079746 | 0.018778 | 0.0062865 | 0.029602 | -1.3151 | 0.11352 | -0.0037 | 0.044801 | 0.069406 | -113.855 | 2.8198 | -117.8055 | 2.9755 | -114.8712 | -116.4368 | -115.2191 | -81.6742 | 2.9022 | -117.9886 | 2.98 | -85.8032 | -80.452 | -107.3593 | 0.036621 | -0.18768 | -0.032043 | 2.9709 | 2.623 | 1.4053 | 2.5864 | 1.3687 | -0.14648 | -0.10528 | -0.027465 | 32.0389 | 10.4828 | 37.3901 | 10.6293 | 37.5366 | 2.9343 | 120.7809 | 32.1854 | 120.9686 | 120.6253 | 120.8908 | 120.6619 | 120.7443 | -120.813 | -120.9961 | 120.8176 | 120.8221 | 3.9871 | 36.1679
2531.3281 | 121.0236 | -117.9199 | 3.0167 | 0.0019074 | 6.9573 | 0.064963 | 0.094691 | -0.0016449 | 0.0051974 | 0.019418 | 0.027649 | 0.032165 | -1.3111 | 0.11053 | -0.007118 | 0.044374 | 0.073251 | -113.8824 | 2.8656 | -117.8925 | 2.9068 | -114.949 | -116.4825 | -115.274 | -81.7932 | 2.9343 | -118.0618 | 2.8702 | -85.8673 | -80.5435 | -107.3914 | 0.027466 | -0.15106 | -0.10986 | 2.9709 | 2.6459 | 1.4374 | 2.6184 | 1.4099 | -0.14191 | -0.082398 | -0.14648 | 32.0526 | 10.5286 | 37.3764 | 10.6705 | 37.5183 | 2.9434 | 120.7993 | 32.1945 | 120.932 | 120.7581 | 120.9961 | 120.7855 | 120.8542 | -120.9091 | -121.0785 | 120.8267 | 120.7901 | 4.0375 | 36.1267
2533.0312 | 121.0556 | -117.9153 | 2.9709 | 0.0019074 | 6.9568 | 0.063681 | 0.089777 | -0.0029267 | 0.0056248 | 0.016641 | -0.0059205 | 0.028747 | -1.3147 | 0.11629 | -0.0060498 | 0.043946 | 0.066843 | -113.8596 | 2.7512 | -117.8146 | 2.9388 | -114.8941 | -116.4597 | -115.2557 | -81.7886 | 2.8381 | -118.0115 | 2.9114 | -85.7986 | -80.4749 | -107.3685 | 0.10071 | -0.21973 | -0.032043 | 3.0212 | 2.6596 | 1.4557 | 2.5589 | 1.355 | -0.096131 | -0.13275 | -0.059509 | 32.1167 | 10.5469 | 37.4405 | 10.643 | 37.5366 | 2.9205 | 120.7535 | 32.2128 | 120.9229 | 120.5658 | 120.8496 | 120.6665 | 120.7535 | -120.7855 | -120.9824 | 120.8542 | 120.8267 | 4.0558 | 36.1267
2534.8281 | 121.1151 | -115.0085 | 5.7953 | 0.055313 | 6.9611 | 0.069235 | 0.092127 | -0.00057689 | 0.0064792 | 0.018137 | 0.018494 | 0.032165 | -1.3151 | 0.11736 | -0.0011364 | 0.044801 | 0.06962 | -110.9482 | 5.6168 | -114.9994 | 5.896 | -111.9827 | -113.5849 | -112.3627 | -79.422 | 5.6946 | -115.1916 | 5.8502 | -83.5052 | -77.9343 | -104.5303 | 0.009155 | -0.17853 | 0.10071 | 3.0258 | 2.6459 | 1.4236 | 2.6367 | 1.4145 | -0.1831 | -0.10071 | 0.054932 | 31.5033 | 10.4782 | 37.0743 | 10.6613 | 37.2574 | 3.0167 | 120.8954 | 31.6864 | 121.0419 | 120.6162 | 120.8862 | 120.6253 | 120.7031 | -120.7947 | -120.9869 | 120.9045 | 120.8588 | 4.0604 | 35.5865
2536.6094 | 121.138 | -115.0589 | 5.7632 | 0.0019074 | 6.9579 | 0.07009 | 0.091486 | 0.0045501 | 0.010324 | 0.017069 | 0.027649 | 0.031738 | -1.3132 | 0.12035 | -0.003059 | 0.04416 | 0.070901 | -111.0214 | 5.5481 | -114.9719 | 5.864 | -111.9781 | -113.5986 | -112.3764 | -79.5044 | 5.658 | -115.2237 | 5.8319 | -83.4778 | -77.9022 | -104.5166 | 0.086975 | -0.21515 | 0.10071 | 3.0807 | 2.6825 | 1.4603 | 2.5955 | 1.3733 | -0.16479 | -0.10529 | 0.068664 | 31.5811 | 10.5423 | 37.1567 | 10.7071 | 37.3215 | 2.9938 | 120.8359 | 31.7459 | 121.0556 | 120.52 | 120.8817 | 120.607 | 120.7169 | -120.7352 | -120.9869 | 120.9229 | 120.8908 | 4.0375 | 35.5545
2538.3906 | 121.1517 | -115.3336 | 5.4703 | 0.0019074 | 6.9571 | 0.064963 | 0.090418 | -0.00057689 | 0.0037022 | 0.019418 | -0.0028687 | 0.030029 | -1.3166 | 0.12142 | -0.0037 | 0.045869 | 0.070474 | -111.3144 | 5.2689 | -115.2832 | 5.5435 | -112.2894 | -113.8916 | -112.6648 | -79.7928 | 5.3421 | -115.48 | 5.5115 | -83.7158 | -78.0945 | -104.7775 | 0.050354 | -0.20142 | 0.073242 | 3.0441 | 2.6688 | 1.442 | 2.6184 | 1.3916 | -0.14648 | -0.12817 | 0.041199 | 31.6177 | 10.556 | 37.2391 | 10.7025 | 37.3856 | 2.9938 | 120.8267 | 31.7642 | 120.9915 | 120.5521 | 120.8221 | 120.6024 | 120.6757 | -120.7535 | -120.9503 | 120.8771 | 120.845 | 4.0192 | 35.5408
2540.0938 | 121.1792 | -115.6403 | 5.159 | -0.013352 | 6.9588 | 0.066672 | 0.091913 | -0.0020721 | 0.0075474 | 0.018564 | -0.0028687 | 0.029174 | -1.3147 | 0.11565 | -0.006477 | 0.042878 | 0.071329 | -111.6074 | 4.9622 | -115.5807 | 5.2231 | -112.5961 | -114.2075 | -112.9578 | -80.0858 | 5.0583 | -115.773 | 5.246 | -83.9127 | -78.3051 | -105.0247 | 0.059509 | -0.19684 | 0.064086 | 3.0441 | 2.6825 | 1.4328 | 2.623 | 1.3733 | -0.13275 | -0.10071 | 0.086975 | 31.7276 | 10.6155 | 37.3352 | 10.7483 | 37.468 | 2.9846 | 120.8038 | 31.8604 | 121.019 | 120.5429 | 120.8313 | 120.6024 | 120.6985 | -120.7397 | -120.932 | 120.8633 | 120.8862 | 4.0329 | 35.5545
2541.8594 | 121.138 | -115.4572 | 5.3833 | 0.0019074 | 6.9577 | 0.067954 | 0.092127 | -0.0014313 | 0.005411 | 0.016855 | -0.0028687 | 0.029174 | -1.3151 | 0.11629 | -0.0045544 | 0.044374 | 0.069406 | -111.4334 | 5.1773 | -115.3976 | 5.365 | -112.4725 | -114.0793 | -112.8113 | -80.0812 | 5.2597 | -115.6036 | 5.3833 | -83.7982 | -78.1494 | -104.8416 | 0.059509 | -0.20599 | -0.018311 | 2.9846 | 2.6459 | 1.3779 | 2.5864 | 1.3184 | -0.14648 | -0.1236 | 0 | 31.6589 | 10.6155 | 37.3077 | 10.762 | 37.4542 | 2.9251 | 120.7626 | 31.8054 | 120.9869 | 120.575 | 120.8633 | 120.6345 | 120.7169 | -120.7809 | -120.9869 | 120.8221 | 120.8405 | 4.0237 | 35.376
2543.5781 | 121.0007 | -115.7272 | 5.1819 | -0.013352 | 6.9613 | 0.066245 | 0.094477 | -0.00014949 | 0.0084018 | 0.018778 | -0.0028687 | 0.032165 | -1.3147 | 0.11843 | -0.0049818 | 0.043519 | 0.068124 | -111.6302 | 4.9713 | -115.6174 | 5.0766 | -112.7655 | -114.3997 | -113.1134 | -80.4199 | 5.0583 | -115.8463 | 5.0674 | -84.0729 | -78.4882 | -105.1346 | 0.10986 | -0.21057 | -0.10529 | 2.9617 | 2.6138 | 1.3275 | 2.504 | 1.2177 | -0.11902 | -0.1236 | -0.11444 | 31.6544 | 10.5927 | 37.2391 | 10.7117 | 37.3581 | 2.8519 | 120.694 | 31.7734 | 120.9137 | 120.5887 | 120.9045 | 120.6985 | 120.7855 | -120.7993 | -121.0281 | 120.8038 | 120.7947 | 4.097 | 35.3073
2545.3438 | 121.1655 | -116.1484 | 4.6783 | -0.013352 | 6.9566 | 0.064322 | 0.08935 | -0.0014313 | 0.0051974 | 0.01536 | -0.0089723 | 0.030883 | -1.3158 | 0.11245 | -0.0045544 | 0.042451 | 0.06962 | -112.0743 | 4.4678 | -116.1118 | 4.7241 | -113.0768 | -114.7018 | -113.4567 | -80.6808 | 4.5456 | -116.272 | 4.7241 | -84.2514 | -78.6713 | -105.4642 | 0.036621 | -0.21057 | 0.045776 | 3.0716 | 2.6916 | 1.4465 | 2.655 | 1.4099 | -0.1236 | -0.13275 | 0.045776 | 31.897 | 10.6842 | 37.4771 | 10.8078 | 37.6007 | 3.035 | 120.8359 | 32.0206 | 120.9961 | 120.5795 | 120.8176 | 120.6161 | 120.694 | -120.7901 | -120.9503 | 120.8725 | 120.8725 | 4.0741 | 35.4675
2547.0938 | 121.0144 | -116.3132 | 4.6051 | -0.0057221 | 6.9618 | 0.067526 | 0.092127 | 0.00070491 | 0.0062656 | 0.018778 | -0.0059205 | 0.03302 | -1.3121 | 0.11587 | -0.0058362 | 0.043733 | 0.070688 | -112.1887 | 4.39 | -116.2354 | 4.4998 | -113.3102 | -114.9628 | -113.7177 | -80.9738 | 4.4907 | -116.423 | 4.4769 | -84.4345 | -78.9139 | -105.6519 | 0.077819 | -0.21515 | -0.10529 | 3.0029 | 2.5955 | 1.3504 | 2.5177 | 1.2726 | -0.10986 | -0.11444 | -0.12817 | 31.8787 | 10.6613 | 37.3993 | 10.7712 | 37.5092 | 2.9251 | 120.7352 | 31.9885 | 120.9 | 120.6253 | 120.9137 | 120.7031 | 120.8038 | -120.8405 | -121.0281 | 120.813 | 120.7901 | 4.1244 | 35.3394
2548.8281 | 121.1517 | -116.7664 | 4.0878 | -0.020981 | 6.9573 | 0.066245 | 0.090845 | -0.00057689 | 0.0047702 | 0.022409 | -0.0059205 | 0.03067 | -1.3134 | 0.11202 | -0.0062634 | 0.044587 | 0.071756 | -112.6419 | 3.8498 | -116.7023 | 4.1153 | -113.6627 | -115.3061 | -114.0793 | -81.2897 | 3.9505 | -116.9083 | 4.1016 | -84.6313 | -79.1336 | -106.0455 | 0.064086 | -0.23804 | 0.027465 | 3.1036 | 2.6871 | 1.4603 | 2.623 | 1.3962 | -0.14191 | -0.13733 | 0.013732 | 32.135 | 10.7208 | 37.6328 | 10.8627 | 37.7747 | 3.0396 | 120.8176 | 32.2769 | 121.0098 | 120.5521 | 120.8588 | 120.6161 | 120.7169 | -120.7901 | -120.9961 | 120.8817 | 120.8679 | 4.1244 | 35.4767
2550.5938 | 121.051 | -115.6082 | 5.3238 | 0.055313 | 6.9613 | 0.068167 | 0.094691 | -0.0024995 | 0.0047702 | 0.022623 | 0.021545 | 0.034729 | -1.31 | 0.11523 | -0.0062634 | 0.041597 | 0.073251 | -111.4883 | 5.1544 | -115.5624 | 5.2185 | -112.5824 | -114.2075 | -112.944 | -80.4611 | 5.2139 | -115.7913 | 5.191 | -83.7708 | -78.2227 | -104.9652 | 0.045776 | -0.16937 | -0.10529 | 3.0258 | 2.6642 | 1.4008 | 2.6184 | 1.355 | -0.18311 | -0.10986 | -0.13275 | 31.8375 | 10.643 | 37.3856 | 10.8261 | 37.5687 | 2.98 | 120.7809 | 32.0206 | 120.9824 | 120.7169 | 121.0052 | 120.7626 | 120.8221 | -120.8862 | -121.1151 | 120.8267 | 120.7993 | 4.1199 | 35.1471
2552.2969 | 121.0739 | -115.8142 | 5.1086 | 0.062942 | 6.9618 | 0.06774 | 0.092768 | -0.00079049 | 0.0045566 | 0.017923 | 0.01239 | 0.031952 | -1.3109 | 0.11138 | -0.0060498 | 0.043092 | 0.070688 | -111.6348 | 4.9438 | -115.7776 | 5.0308 | -112.7335 | -114.3906 | -113.1409 | -80.5893 | 4.9988 | -115.9607 | 5.0354 | -83.8394 | -78.3325 | -105.0888 | 0.036621 | -0.16479 | -0.07782 | 3.0808 | 2.6733 | 1.4236 | 2.6367 | 1.387 | -0.14648 | -0.10986 | -0.073243 | 31.9748 | 10.7254 | 37.4817 | 10.8719 | 37.6282 | 3.0441 | 120.8084 | 32.1213 | 120.9961 | 120.7214 | 120.9595 | 120.7581 | 120.813 | -120.8862 | -121.0693 | 120.845 | 120.8496 | 4.1794 | 35.2249
2554.0625 | 121.0464 | -116.0019 | 4.9255 | -0.020981 | 6.9596 | 0.065176 | 0.0917 | 0.00027771 | 0.0049838 | 0.021555 | -0.0089723 | 0.030883 | -1.3153 | 0.11715 | -0.0079724 | 0.043092 | 0.073251 | -111.8591 | 4.6829 | -115.9012 | 4.834 | -112.9395 | -114.5874 | -113.3377 | -80.7587 | 4.7745 | -116.1438 | 4.7882 | -83.9859 | -78.4607 | -105.2811 | 0.10071 | -0.24262 | -0.091553 | 3.0624 | 2.6642 | 1.4145 | 2.5635 | 1.3138 | -0.14191 | -0.15106 | -0.13733 | 32.016 | 10.7208 | 37.5412 | 10.8627 | 37.6831 | 2.9617 | 120.7352 | 32.1579 | 120.932 | 120.5841 | 120.9183 | 120.6848 | 120.7764 | -120.8267 | -121.0693 | 120.8359 | 120.7901 | 4.1428 | 35.2432
2555.8438 | 121.0785 | -116.1484 | 4.7424 | 0.047683 | 6.9643 | 0.069663 | 0.093622 | 0.0017731 | 0.0062656 | 0.017069 | 0.01239 | 0.035156 | -1.313 | 0.11053 | -0.005409 | 0.043519 | 0.074747 | -111.9644 | 4.5776 | -116.1163 | 4.6921 | -113.0722 | -114.7247 | -113.4842 | -80.8136 | 4.6463 | -116.3315 | 4.6738 | -83.9676 | -78.5477 | -105.3772 | 0.032043 | -0.16479 | -0.050354 | 3.0762 | 2.6642 | 1.4236 | 2.6321 | 1.3916 | -0.18311 | -0.096131 | -0.068665 | 32.1808 | 10.7712 | 37.6007 | 10.9543 | 37.7838 | 3.0441 | 120.8084 | 32.3639 | 121.0052 | 120.694 | 120.9778 | 120.726 | 120.7947 | -120.8588 | -121.0739 | 120.8405 | 120.8221 | 4.184 | 35.3348
2557.5469 | 121.051 | -116.3498 | 4.5685 | -0.013352 | 6.9633 | 0.067313 | 0.093409 | 0.00049131 | 0.0045566 | 0.020273 | -0.0059205 | 0.031524 | -1.3128 | 0.11501 | -0.004768 | 0.046083 | 0.073679 | -112.1933 | 4.3716 | -116.2674 | 4.4312 | -113.3469 | -115.0131 | -113.7268 | -81.0196 | 4.4495 | -116.478 | 4.454 | -84.1415 | -78.7262 | -105.5557 | 0.082397 | -0.19684 | -0.13733 | 3.0029 | 2.623 | 1.3367 | 2.5406 | 1.2543 | -0.12817 | -0.11902 | -0.11444 | 32.2083 | 10.7941 | 37.6236 | 10.9222 | 37.7518 | 2.9205 | 120.6985 | 32.3364 | 120.932 | 120.639 | 120.9274 | 120.7214 | 120.7993 | -120.8359 | -121.0464 | 120.7809 | 120.8038 | 4.1565 | 35.3302
2559.3125 | 121.0281 | -116.5009 | 4.39 | -0.013352 | 6.9609 | 0.064536 | 0.09405 | 0.0034821 | 0.006052 | 0.019205 | 0.00018312 | 0.032165 | -1.3132 | 0.11993 | -0.0022046 | 0.044587 | 0.076028 | -112.3672 | 4.1931 | -116.4276 | 4.2618 | -113.53 | -115.2054 | -113.9008 | -81.189 | 4.2801 | -116.6336 | 4.2847 | -84.2651 | -78.8773 | -105.6885 | 0.073242 | -0.19684 | -0.12817 | 2.9709 | 2.6001 | 1.2955 | 2.5269 | 1.2222 | -0.13275 | -0.10986 | -0.10529 | 32.2357 | 10.8124 | 37.6236 | 10.9451 | 37.7563 | 2.8976 | 120.6894 | 32.3685 | 120.9183 | 120.6207 | 120.9137 | 120.694 | 120.7809 | -120.8176 | -121.0236 | 120.7626 | 120.7855 | 4.1336 | 35.3119
2561.0312 | 121.0327 | -116.6702 | 4.2252 | -0.0057221 | 6.9624 | 0.067099 | 0.092127 | -0.0027131 | 0.0064792 | 0.018564 | -0.0028687 | 0.031952 | -1.3109 | 0.10882 | -0.0028454 | 0.045015 | 0.073038 | -112.4588 | 4.0192 | -116.597 | 4.1382 | -113.5849 | -115.2878 | -114.0244 | -81.3217 | 4.097 | -116.7892 | 4.1245 | -84.3109 | -79.01 | -105.8075 | 0.073242 | -0.20599 | -0.086975 | 3.0853 | 2.6459 | 1.3824 | 2.5726 | 1.3092 | -0.11902 | -0.12817 | -0.10071 | 32.3593 | 10.8627 | 37.6602 | 10.9818 | 37.7792 | 3.0121 | 120.7352 | 32.4783 | 120.9137 | 120.6162 | 120.8862 | 120.6894 | 120.7672 | -120.8221 | -121.0144 | 120.8084 | 120.7947 | 4.2114 | 35.3485
2562.7969 | 121.1288 | -116.272 | 4.5593 | -0.013352 | 6.962 | 0.067954 | 0.091913 | -0.0018585 | 0.0073338 | 0.019632 | -0.0028687 | 0.030883 | -1.313 | 0.11202 | -0.0022046 | 0.046937 | 0.076669 | -112.0926 | 4.422 | -116.1896 | 4.5502 | -113.1638 | -114.8758 | -113.6032 | -80.9555 | 4.4586 | -116.3818 | 4.5822 | -83.8806 | -78.5614 | -105.3543 | 0.082398 | -0.13733 | -0.009155 | 3.1082 | 2.6688 | 1.3962 | 2.5864 | 1.3138 | -0.10986 | -0.10071 | 0.022888 | 32.3914 | 10.9177 | 37.7106 | 11.0275 | 37.8204 | 3.0258 | 120.7397 | 32.5012 | 120.9641 | 120.6116 | 120.8405 | 120.694 | 120.7306 | -120.7489 | -120.9412 | 120.8221 | 120.8542 | 4.1794 | 35.3165
2564.5781 | 121.1746 | -117.1417 | 3.6987 | -0.013352 | 6.9622 | 0.06539 | 0.089777 | -0.0022857 | 0.0062656 | 0.017496 | -0.0059205 | 0.031952 | -1.3126 | 0.11394 | -0.0026318 | 0.045015 | 0.072824 | -112.944 | 3.4653 | -117.1005 | 3.6987 | -113.9923 | -115.6906 | -114.4272 | -81.6193 | 3.5614 | -117.2882 | 3.7216 | -84.4528 | -79.2068 | -106.1508 | 0.041199 | -0.23346 | 0 | 3.1494 | 2.7145 | 1.4511 | 2.6733 | 1.4099 | -0.14648 | -0.13733 | 0.022889 | 32.6889 | 10.9909 | 37.9349 | 11.1374 | 38.0814 | 3.1082 | 120.7993 | 32.8354 | 121.0098 | 120.5658 | 120.8496 | 120.607 | 120.7031 | -120.7993 | -120.9869 | 120.8405 | 120.8633 | 4.1977 | 35.5225
2566.2969 | 121.0831 | -116.629 | 4.2755 | 0.040054 | 6.965 | 0.06774 | 0.092982 | -0.00014949 | 0.0047702 | 0.020486 | 0.0093383 | 0.033233 | -1.3115 | 0.11352 | -0.0062634 | 0.043733 | 0.074747 | -112.3901 | 4.097 | -116.6016 | 4.2206 | -113.4842 | -115.1871 | -113.9053 | -81.1798 | 4.1656 | -116.7938 | 4.2114 | -84.0637 | -78.7766 | -105.6152 | 0.027466 | -0.17853 | -0.054932 | 3.1448 | 2.7237 | 1.442 | 2.6962 | 1.4145 | -0.16479 | -0.10986 | -0.064087 | 32.5653 | 11.0138 | 37.8525 | 11.1786 | 38.0173 | 3.1174 | 120.8221 | 32.7301 | 121.0052 | 120.6985 | 120.9595 | 120.726 | 120.7947 | -120.8771 | -121.0693 | 120.8496 | 120.8405 | 4.2389 | 35.4492
2568.0469 | 121.1609 | -116.2811 | 4.5364 | -0.0057221 | 6.9611 | 0.066672 | 0.093622 | -0.00079049 | 0.004343 | 0.017496 | -0.0028687 | 0.03067 | -1.3113 | 0.11843 | -0.0017774 | 0.046083 | 0.072183 | -112.0514 | 4.3488 | -116.2262 | 4.5639 | -113.1317 | -114.8575 | -113.5529 | -80.9097 | 4.422 | -116.4185 | 4.5959 | -83.7021 | -78.4241 | -105.2353 | 0.054932 | -0.18768 | 0.027466 | 3.1494 | 2.7283 | 1.4236 | 2.6733 | 1.3687 | -0.13733 | -0.11444 | 0.059509 | 32.579 | 11.0458 | 37.8571 | 11.1832 | 37.9944 | 3.0945 | 120.7901 | 32.7164 | 121.0144 | 120.575 | 120.8405 | 120.6299 | 120.7031 | -120.7626 | -120.9549 | 120.845 | 120.8771 | 4.2297 | 35.3714
2569.8281 | 121.1243 | -116.2994 | 4.5547 | -0.0057221 | 6.963 | 0.066031 | 0.093409 | 0.0030547 | 0.006052 | 0.017069 | -0.0059205 | 0.032165 | -1.3113 | 0.11138 | -0.004768 | 0.046937 | 0.073892 | -112.0926 | 4.39 | -116.2262 | 4.509 | -113.1866 | -114.9124 | -113.6032 | -80.9601 | 4.454 | -116.4276 | 4.5776 | -83.725 | -78.3966 | -105.1849 | 0.073242 | -0.16479 | -0.045777 | 3.1128 | 2.6962 | 1.387 | 2.623 | 1.3138 | -0.12817 | -0.10071 | 0.022888 | 32.5745 | 11.1145 | 37.9028 | 11.2427 | 38.031 | 3.0396 | 120.7352 | 32.7026 | 121.0052 | 120.6162 | 120.8817 | 120.6894 | 120.7535 | -120.7809 | -120.9824 | 120.8084 | 120.8771 | 4.2068 | 35.3394
2571.5938 | 121.019 | -116.185 | 4.7195 | -0.013352 | 6.9624 | 0.065176 | 0.093409 | 0.0047637 | 0.0041294 | 0.022836 | 0.027649 | 0.032165 | -1.3083 | 0.11288 | -0.0096814 | 0.043946 | 0.074747 | -111.937 | 4.5136 | -116.1072 | 4.66 | -113.0035 | -114.7064 | -113.4201 | -80.8319 | 4.66 | -116.3315 | 4.5959 | -83.6517 | -78.3005 | -105.1163 | 0.07782 | -0.20599 | -0.059509 | 3.1815 | 2.7649 | 1.4786 | 2.6871 | 1.4008 | -0.14648 | -0.059509 | -0.1236 | 32.5333 | 11.0687 | 37.8845 | 11.2152 | 38.031 | 3.1036 | 120.7672 | 32.6797 | 120.9274 | 120.6207 | 120.9915 | 120.6985 | 120.845 | -120.8267 | -121.051 | 120.845 | 120.7809 | 4.248 | 35.3531
2573.3594 | 121.0739 | -116.4322 | 4.4861 | 0.032425 | 6.9645 | 0.067954 | 0.090632 | 0.0011321 | 0.0056248 | 0.01835 | 0.018494 | 0.034301 | -1.3092 | 0.11715 | -0.0066906 | 0.043519 | 0.074319 | -112.1384 | 4.3167 | -116.4093 | 4.3762 | -113.2874 | -114.9811 | -113.6856 | -80.9967 | 4.3854 | -116.6153 | 4.3671 | -83.7616 | -78.4012 | -105.2765 | 0.022888 | -0.16937 | -0.10986 | 3.1448 | 2.7466 | 1.4511 | 2.7237 | 1.4282 | -0.1831 | -0.10071 | -0.11902 | 32.6706 | 11.1557 | 38.031 | 11.3388 | 38.2141 | 3.1219 | 120.7855 | 32.8537 | 120.9824 | 120.726 | 121.0007 | 120.7489 | 120.8176 | -120.8954 | -121.1014 | 120.8084 | 120.7993 | 4.2938 | 35.4355
2575.1406 | 121.051 | -116.5375 | 4.3945 | 0.0019074 | 6.9645 | 0.066031 | 0.092554 | 0.0036957 | 0.0066928 | 0.01835 | -0.0089723 | 0.033233 | -1.3109 | 0.11886 | -0.004768 | 0.043306 | 0.074533 | -112.207 | 4.1885 | -116.4459 | 4.3213 | -113.3423 | -115.1138 | -113.768 | -81.0287 | 4.2664 | -116.6382 | 4.3076 | -83.7662 | -78.4378 | -105.304 | 0.091553 | -0.20599 | -0.073242 | 3.1952 | 2.7695 | 1.4236 | 2.6779 | 1.3321 | -0.10071 | -0.12817 | -0.086975 | 32.7713 | 11.2335 | 38.0997 | 11.3342 | 38.2004 | 3.1036 | 120.7672 | 32.872 | 120.9457 | 120.6345 | 120.9045 | 120.726 | 120.8038 | -120.8405 | -121.0327 | 120.8588 | 120.845 | 4.3304 | 35.5087
2576.8594 | 121.0419 | -116.4368 | 4.5044 | 0.070572 | 6.9656 | 0.068808 | 0.093195 | 0.0015595 | 0.00712 | 0.019846 | 0.018494 | 0.034088 | -1.3106 | 0.11501 | -0.0069044 | 0.04416 | 0.076242 | -112.1063 | 4.3304 | -116.4001 | 4.4037 | -113.2645 | -114.9765 | -113.6673 | -81.0013 | 4.39 | -116.5924 | 4.3762 | -83.638 | -78.3325 | -105.1987 | 0.036622 | -0.17395 | -0.10071 | 3.1723 | 2.7695 | 1.4603 | 2.7328 | 1.4236 | -0.15564 | -0.11444 | -0.12817 | 32.7988 | 11.2381 | 38.1042 | 11.3937 | 38.2599 | 3.1357 | 120.8038 | 32.9544 | 120.9686 | 120.7306 | 120.9824 | 120.7672 | 120.8267 | -120.9045 | -121.0968 | 120.8405 | 120.813 | 4.3304 | 35.4355
2578.625 | 121.0327 | -116.4093 | 4.4952 | -0.013352 | 6.963 | 0.066031 | 0.092341 | -0.00014949 | 0.0032748 | 0.019418 | -0.0059205 | 0.030243 | -1.3124 | 0.10775 | -0.0066906 | 0.044587 | 0.076242 | -112.1338 | 4.2755 | -116.3452 | 4.3808 | -113.2782 | -115.004 | -113.6765 | -81.0104 | 4.3854 | -116.5375 | 4.3625 | -83.5876 | -78.2684 | -105.1666 | 0.064087 | -0.21973 | -0.11444 | 3.1311 | 2.7328 | 1.4053 | 2.6688 | 1.3412 | -0.12817 | -0.10986 | -0.13275 | 32.8217 | 11.2427 | 38.1409 | 11.3709 | 38.269 | 3.067 | 120.726 | 32.9498 | 120.9 | 120.6207 | 120.9229 | 120.6848 | 120.7947 | -120.8405 | -121.0327 | 120.7901 | 120.7718 | 4.2755 | 35.3989
2580.4062 | 121.0693 | -116.3681 | 4.5456 | 0.017166 | 6.9656 | 0.067526 | 0.094263 | 0.00049131 | 0.0066928 | 0.020914 | 0.0032349 | 0.034088 | -1.3092 | 0.12099 | -0.0058362 | 0.043092 | 0.072397 | -112.0056 | 4.3579 | -116.2674 | 4.5136 | -113.1546 | -114.9033 | -113.562 | -80.7999 | 4.4357 | -116.4597 | 4.5044 | -83.4229 | -78.1174 | -105.0201 | 0.10071 | -0.18768 | -0.032043 | 3.2135 | 2.8061 | 1.4648 | 2.7054 | 1.3641 | -0.091553 | -0.10986 | -0.041198 | 32.9453 | 11.348 | 38.2507 | 11.4395 | 38.3423 | 3.1128 | 120.7809 | 33.0368 | 120.9641 | 120.6253 | 120.8954 | 120.726 | 120.8038 | -120.813 | -121.0052 | 120.8817 | 120.8725 | 4.3625 | 35.5682
2582.1094 | 121.0693 | -116.3361 | 4.5639 | 0.032425 | 6.9656 | 0.066458 | 0.093836 | 0.0069001 | 0.006052 | 0.021982 | 0.015442 | 0.03302 | -1.3092 | 0.11736 | -0.0045544 | 0.047578 | 0.073465 | -111.969 | 4.3625 | -116.3223 | 4.4952 | -113.1546 | -114.8941 | -113.5437 | -80.8182 | 4.4678 | -116.4825 | 4.4769 | -83.3633 | -78.0441 | -104.9606 | 0.013733 | -0.20142 | -0.068665 | 3.1815 | 2.7924 | 1.442 | 2.7786 | 1.4282 | -0.14648 | -0.096131 | -0.086975 | 32.9727 | 11.3754 | 38.2919 | 11.5219 | 38.4384 | 3.1677 | 120.8176 | 33.1192 | 120.9595 | 120.6848 | 120.9503 | 120.6985 | 120.8038 | -120.8862 | -121.0464 | 120.8313 | 120.813 | 4.3671 | 35.5179
2583.8906 | 121.0968 | -116.423 | 4.4724 | -0.013352 | 6.9654 | 0.068594 | 0.092127 | -0.0022857 | 0.0037022 | 0.0207 | -0.0028687 | 0.030883 | -1.3089 | 0.1148 | -0.005409 | 0.043306 | 0.073892 | -112.0377 | 4.2343 | -116.3086 | 4.4678 | -113.1592 | -114.9078 | -113.5666 | -80.864 | 4.3396 | -116.5192 | 4.4449 | -83.3084 | -78.0075 | -104.9835 | 0.11444 | -0.23804 | -0.004578 | 3.2639 | 2.8564 | 1.5152 | 2.742 | 1.4008 | -0.09613 | -0.13275 | -0.027466 | 33.1146 | 11.4395 | 38.4155 | 11.5356 | 38.5117 | 3.1494 | 120.7764 | 33.2108 | 120.9641 | 120.5429 | 120.8588 | 120.6573 | 120.7626 | -120.7809 | -120.9915 | 120.8908 | 120.8679 | 4.3854 | 35.5591
2585.6719 | 121.0922 | -116.4871 | 4.4128 | 0.070572 | 6.968 | 0.067313 | 0.094904 | -0.0012177 | 0.0047702 | 0.021341 | 0.01239 | 0.03601 | -1.3062 | 0.1148 | -0.0043408 | 0.045228 | 0.074533 | -112.0651 | 4.2572 | -116.4505 | 4.3488 | -113.3011 | -115.036 | -113.6536 | -80.9326 | 4.3304 | -116.6061 | 4.3488 | -83.2581 | -78.0441 | -105.0247 | 0.036622 | -0.15564 | -0.064087 | 3.186 | 2.8336 | 1.4511 | 2.7969 | 1.4145 | -0.11902 | -0.082398 | -0.064087 | 33.2291 | 11.4624 | 38.443 | 11.5814 | 38.562 | 3.1494 | 120.7993 | 33.3481 | 120.9549 | 120.7077 | 120.9366 | 120.7443 | 120.8176 | -120.8633 | -121.019 | 120.8359 | 120.8359 | 4.422 | 35.5545
2587.4375 | 121.1563 | -116.3315 | 4.4815 | -0.013352 | 6.9656 | 0.066672 | 0.090418 | -0.0031403 | 0.0066928 | 0.020486 | -0.0089723 | 0.030456 | -1.3087 | 0.12676 | -0.005409 | 0.045442 | 0.077951 | -111.9644 | 4.2709 | -116.2445 | 4.541 | -113.1042 | -114.8346 | -113.4842 | -80.7724 | 4.3854 | -116.4459 | 4.5181 | -83.0063 | -77.7924 | -104.8279 | 0.086975 | -0.21057 | 0.05951 | 3.2272 | 2.8473 | 1.4969 | 2.7603 | 1.4099 | -0.11444 | -0.09613 | 0.036621 | 33.3252 | 11.5036 | 38.5391 | 11.618 | 38.6536 | 3.1403 | 120.7855 | 33.4396 | 120.964 | 120.5154 | 120.8313 | 120.6024 | 120.7169 | -120.726 | -120.9274 | 120.8725 | 120.8496 | 4.3671 | 35.5591
2589.1562 | 121.1197 | -116.4597 | 4.3762 | -0.0057221 | 6.966 | 0.065817 | 0.09405 | 0.0047637 | 0.006052 | 0.018778 | -0.0059205 | 0.03302 | -1.3094 | 0.12847 | -0.0022046 | 0.048433 | 0.073038 | -112.1338 | 4.2114 | -116.423 | 4.3304 | -113.3331 | -115.0772 | -113.6673 | -80.8868 | 4.2755 | -116.597 | 4.3991 | -83.075 | -77.8793 | -104.9423 | 0.036621 | -0.16479 | -0.045777 | 3.1265 | 2.7924 | 1.3824 | 2.7557 | 1.3458 | -0.13733 | -0.10071 | 0.022888 | 33.3847 | 11.5173 | 38.5803 | 11.6547 | 38.7177 | 3.0899 | 120.7535 | 33.522 | 120.9961 | 120.6345 | 120.8725 | 120.6711 | 120.7352 | -120.7993 | -120.9732 | 120.7901 | 120.8588 | 4.3259 | 35.5728
2590.9375 | 121.0144 | -116.1667 | 4.7379 | -0.013352 | 6.9648 | 0.066031 | 0.092982 | 0.0034821 | 0.00712 | 0.020059 | -0.0059205 | 0.034942 | -1.3111 | 0.12804 | -0.0028454 | 0.044801 | 0.07731 | -111.8546 | 4.5136 | -116.1118 | 4.5868 | -113.1134 | -114.83 | -113.4201 | -80.7129 | 4.6005 | -116.2949 | 4.6371 | -82.8415 | -77.6505 | -104.631 | 0.054932 | -0.2243 | -0.15106 | 3.0533 | 2.7466 | 1.3367 | 2.6916 | 1.2817 | -0.12817 | -0.13733 | -0.10071 | 33.3252 | 11.5356 | 38.5162 | 11.6638 | 38.6444 | 2.9984 | 120.6985 | 33.4534 | 120.932 | 120.6253 | 120.8954 | 120.6802 | 120.7672 | -120.8496 | -121.0327 | 120.7535 | 120.8038 | 4.3121 | 35.4538
2592.7188 | 121.0098 | -116.3864 | 4.5181 | -0.013352 | 6.9656 | 0.06774 | 0.092127 | 0.0015595 | 0.00712 | 0.017282 | -0.0059205 | 0.030243 | -1.3085 | 0.11608 | -0.0041272 | 0.048219 | 0.079233 | -112.0148 | 4.3213 | -116.3086 | 4.3762 | -113.2874 | -115.0177 | -113.6215 | -80.8456 | 4.4037 | -116.4917 | 4.4128 | -82.8964 | -77.7008 | -104.8553 | 0.07782 | -0.19684 | -0.14191 | 3.0991 | 2.7649 | 1.3687 | 2.6871 | 1.2909 | -0.10528 | -0.11444 | -0.10528 | 33.49 | 11.5311 | 38.6856 | 11.6364 | 38.7909 | 3.0212 | 120.6848 | 33.5953 | 120.9045 | 120.6299 | 120.8954 | 120.7077 | 120.7901 | -120.8267 | -121.0098 | 120.7626 | 120.7993 | 4.3716 | 35.5408
2594.5 | 121.0785 | -116.4368 | 4.454 | 0.032425 | 6.9699 | 0.069022 | 0.092768 | 0.0077545 | 0.0066928 | 0.0207 | 0.0032349 | 0.033447 | -1.3066 | 0.11779 | -0.004768 | 0.044801 | 0.076883 | -112.0285 | 4.2618 | -116.4047 | 4.3945 | -113.2187 | -114.9765 | -113.5895 | -80.7129 | 4.3579 | -116.5741 | 4.4128 | -82.7911 | -77.5864 | -104.8141 | 0.032044 | -0.19226 | -0.05951 | 3.2181 | 2.8473 | 1.4603 | 2.8152 | 1.4282 | -0.13733 | -0.096131 | -0.041199 | 33.6456 | 11.6226 | 38.8504 | 11.7599 | 38.9877 | 3.186 | 120.7993 | 33.783 | 120.9869 | 120.6665 | 120.932 | 120.6985 | 120.7947 | -120.8588 | -121.0281 | 120.8313 | 120.8496 | 4.4083 | 35.7239
2596.2344 | 121.0556 | -111.1816 | 9.7412 | 0.062942 | 6.9688 | 0.070303 | 0.095118 | 0.0064727 | 0.00712 | 0.021555 | 0.01239 | 0.035583 | -1.31 | 0.11373 | -0.0056226 | 0.045228 | 0.076883 | -106.842 | 9.5764 | -111.1404 | 9.7137 | -108.046 | -109.7122 | -108.3069 | -76.474 | 9.6405 | -111.3007 | 9.6634 | -78.7079 | -73.0362 | -99.6872 | 0.041199 | -0.16479 | -0.027466 | 3.1357 | 2.8748 | 1.4694 | 2.8336 | 1.4282 | -0.11902 | -0.10071 | -0.07782 | 32.4738 | 11.4944 | 38.1454 | 11.6135 | 38.2645 | 3.0945 | 120.8542 | 32.5928 | 120.9641 | 120.7169 | 120.9412 | 120.7581 | 120.8221 | -120.8817 | -121.0419 | 120.8954 | 120.845 | 4.3396 | 34.7076
2598 | 121.1334 | -112.6831 | 8.139 | 0.078201 | 6.9703 | 0.070517 | 0.095759 | 0.0049773 | 0.00712 | 0.021127 | 0.027649 | 0.034515 | -1.3111 | 0.12142 | -0.0032728 | 0.047151 | 0.077524 | -108.3115 | 7.9697 | -112.6694 | 8.2352 | -109.4376 | -111.2137 | -109.7763 | -77.5681 | 8.0338 | -112.8571 | 8.1894 | -79.7745 | -74.2493 | -101.1063 | 0.013732 | -0.16937 | 0.09613 | 3.2455 | 2.9068 | 1.4694 | 2.8931 | 1.4557 | -0.17395 | -0.10529 | 0.050354 | 32.9086 | 11.5768 | 38.4338 | 11.7508 | 38.6078 | 3.2318 | 120.9045 | 33.0826 | 121.0464 | 120.639 | 120.8908 | 120.6528 | 120.7169 | -120.8084 | -120.9961 | 120.9183 | 120.8725 | 4.3716 | 35.1151
2599.7812 | 121.0236 | -114.2029 | 6.6879 | -0.0057221 | 6.966 | 0.064536 | 0.092127 | -0.0020721 | 0.0041294 | 0.020059 | -0.0059205 | 0.034942 | -1.3089 | 0.118 | -0.0094678 | 0.04416 | 0.077951 | -109.8724 | 6.4819 | -114.1525 | 6.6055 | -111.0489 | -112.7838 | -111.3602 | -78.9185 | 6.5918 | -114.2944 | 6.5826 | -80.9189 | -75.5173 | -102.6123 | 0.050354 | -0.20599 | -0.082397 | 3.154 | 2.8427 | 1.4191 | 2.7924 | 1.3687 | -0.091553 | -0.09613 | -0.10529 | 33.284 | 11.5906 | 38.6856 | 11.6821 | 38.7772 | 3.1036 | 120.7581 | 33.3755 | 120.8771 | 120.6345 | 120.8862 | 120.6848 | 120.7947 | -120.8405 | -120.9824 | 120.8084 | 120.7855 | 4.3304 | 35.2844
2601.5625 | 121.0464 | -114.8712 | 6.0516 | 0.0019074 | 6.9669 | 0.064963 | 0.090845 | -0.00036309 | 0.005411 | 0.018991 | -0.0059205 | 0.031524 | -1.3081 | 0.11715 | -0.0086132 | 0.044374 | 0.078805 | -110.4538 | 5.7999 | -114.8071 | 5.9784 | -111.6806 | -113.4201 | -111.9919 | -79.3488 | 5.896 | -114.949 | 5.9326 | -81.3217 | -75.9521 | -103.2166 | 0.064087 | -0.25177 | -0.073242 | 3.1906 | 2.8793 | 1.4511 | 2.8152 | 1.387 | -0.07782 | -0.15564 | -0.11902 | 33.5495 | 11.6547 | 38.9191 | 11.7325 | 38.9969 | 3.1265 | 120.7855 | 33.6273 | 120.8817 | 120.607 | 120.845 | 120.6711 | 120.7672 | -120.8588 | -121.0007 | 120.8496 | 120.8038 | 4.4174 | 35.5225
2603.3438 | 121.0693 | -111.5204 | 9.343 | 0.032425 | 6.9697 | 0.069449 | 0.093195 | 0.0017731 | 0.0049838 | 0.022409 | 0.0093383 | 0.037078 | -1.3085 | 0.12527 | -0.004768 | 0.044587 | 0.077524 | -107.1213 | 9.1965 | -111.4517 | 9.4208 | -108.3023 | -110.051 | -108.5953 | -76.5518 | 9.2606 | -111.5982 | 9.3521 | -78.6804 | -73.027 | -99.9115 | 0.068665 | -0.14649 | 0.077819 | 3.2181 | 2.9251 | 1.4694 | 2.8564 | 1.4008 | -0.07782 | -0.082398 | 0.009155 | 32.84 | 11.6089 | 38.4933 | 11.6867 | 38.5712 | 3.1494 | 120.8725 | 32.9178 | 120.9503 | 120.6482 | 120.8588 | 120.7169 | 120.7809 | -120.7947 | -120.9412 | 120.9412 | 120.8725 | 4.3991 | 34.9686
2605.0469 | 121.1014 | -111.3968 | 9.4025 | 0.062942 | 6.9673 | 0.070517 | 0.093622 | -0.0063447 | 0.008829 | 0.020486 | 0.0093383 | 0.034088 | -1.3077 | 0.13189 | -0.0034864 | 0.043733 | 0.081583 | -107.0892 | 9.2148 | -111.4105 | 9.4437 | -108.252 | -109.996 | -108.5632 | -76.4603 | 9.2606 | -111.5662 | 9.4345 | -78.5431 | -72.8439 | -99.7879 | -0.013732 | -0.18768 | 0.041199 | 3.1448 | 2.8336 | 1.4008 | 2.8473 | 1.4145 | -0.16937 | -0.14191 | 0.032043 | 32.8537 | 11.6089 | 38.5529 | 11.7783 | 38.7222 | 3.1586 | 120.8542 | 33.0231 | 121.0007 | 120.6253 | 120.8267 | 120.6116 | 120.6573 | -120.813 | -120.9686 | 120.8405 | 120.8313 | 4.3076 | 34.9365
2606.8125 | 121.1288 | -111.9324 | 8.8715 | 0.070572 | 6.9701 | 0.070517 | 0.094904 | 0.0041229 | 0.0096836 | 0.021768 | 0.018494 | 0.03302 | -1.3042 | 0.12014 | -0.003059 | 0.048219 | 0.075387 | -107.515 | 8.6884 | -111.8958 | 8.9905 | -108.696 | -110.463 | -109.0073 | -76.7441 | 8.7708 | -112.0834 | 8.9539 | -78.8681 | -73.201 | -100.2411 | 0.036621 | -0.18311 | 0.11902 | 3.2364 | 2.9251 | 1.4694 | 2.8885 | 1.4328 | -0.15106 | -0.10071 | 0.082397 | 33.0643 | 11.6913 | 38.7314 | 11.8423 | 38.8824 | 3.1998 | 120.8862 | 33.2153 | 121.0373 | 120.5841 | 120.8542 | 120.6207 | 120.7031 | -120.7672 | -120.9549 | 120.9229 | 120.8862 | 4.4174 | 35.1883
2608.5781 | 121.1655 | -112.294 | 8.5007 | -0.0057221 | 6.9656 | 0.068594 | 0.094263 | -0.00036309 | 0.0075474 | 0.020059 | -0.0059205 | 0.03537 | -1.3064 | 0.12441 | -0.0026318 | 0.047151 | 0.077524 | -107.8995 | 8.2947 | -112.2711 | 8.5648 | -109.1263 | -110.8795 | -109.4147 | -77.0416 | 8.3588 | -112.4084 | 8.5968 | -79.1199 | -73.4161 | -100.5524 | 0.022888 | -0.20599 | 0.064087 | 3.1677 | 2.8793 | 1.4145 | 2.8564 | 1.3916 | -0.11444 | -0.14191 | 0.096131 | 33.1741 | 11.7416 | 38.8779 | 11.8561 | 38.9923 | 3.1448 | 120.8359 | 33.2886 | 121.0052 | 120.5658 | 120.7672 | 120.5887 | 120.6528 | -120.7718 | -120.9091 | 120.8588 | 120.8908 | 4.3945 | 35.2524
2610.3594 | 121.0739 | -112.532 | 8.3084 | 0.0019074 | 6.9682 | 0.066031 | 0.091913 | 0.00049131 | 0.0058384 | 0.01835 | -0.0089723 | 0.034729 | -1.3083 | 0.12142 | -0.008827 | 0.045442 | 0.080087 | -108.0826 | 8.0887 | -112.4542 | 8.345 | -109.3185 | -111.0443 | -109.5978 | -77.1606 | 8.1985 | -112.6099 | 8.3084 | -79.2572 | -73.5489 | -100.7767 | 0.077819 | -0.21973 | 0.036621 | 3.2135 | 2.9343 | 1.4877 | 2.8564 | 1.4099 | -0.07782 | -0.10986 | 0 | 33.2748 | 11.7554 | 38.9832 | 11.8332 | 39.061 | 3.1357 | 120.7993 | 33.3527 | 120.9183 | 120.5429 | 120.8084 | 120.6207 | 120.7306 | -120.7626 | -120.9183 | 120.8771 | 120.8405 | 4.4495 | 35.3714
2612.0469 | 121.0922 | -112.5229 | 8.2901 | 0.024795 | 6.9639 | 0.070731 | 0.093836 | 0.0028411 | 0.008829 | 0.018137 | 0.0093383 | 0.033447 | -1.307 | 0.12099 | -0.0041272 | 0.046724 | 0.074747 | -108.1512 | 8.0887 | -112.5183 | 8.3267 | -109.3826 | -111.113 | -109.6252 | -77.1561 | 8.1848 | -112.6648 | 8.2764 | -79.2755 | -73.4802 | -100.7767 | 0.004577 | -0.20142 | 0.036621 | 3.1403 | 2.8976 | 1.4099 | 2.8931 | 1.4053 | -0.14191 | -0.10529 | -0.013733 | 33.2474 | 11.7462 | 39.0427 | 11.8881 | 39.1846 | 3.1357 | 120.845 | 33.3893 | 120.9412 | 120.607 | 120.8496 | 120.6116 | 120.7077 | -120.8084 | -120.9549 | 120.8496 | 120.7993 | 4.3716 | 35.3668
2613.8281 | 121.1517 | -111.232 | 9.5673 | 0.0095369 | 6.9658 | 0.066672 | 0.092127 | 0.0036957 | 0.0075474 | 0.020273 | 0.033752 | 0.037292 | -1.3079 | 0.12441 | -0.00092279 | 0.047364 | 0.07966 | -106.8008 | 9.3292 | -111.1954 | 9.7137 | -108.0048 | -109.7488 | -108.252 | -75.9018 | 9.4666 | -111.3922 | 9.6588 | -78.1357 | -72.2626 | -99.4354 | 0.036621 | -0.23804 | 0.14648 | 3.2272 | 2.98 | 1.4832 | 2.9434 | 1.4465 | -0.16022 | -0.10071 | 0.091552 | 33.0963 | 11.7966 | 38.9694 | 11.9568 | 39.1296 | 3.1906 | 120.9091 | 33.2565 | 121.051 | 120.5246 | 120.8588 | 120.5612 | 120.6985 | -120.7626 | -120.9595 | 120.9457 | 120.8908 | 4.4312 | 35.3302
2615.6094 | 121.0876 | -111.8408 | 8.9859 | -0.0057221 | 6.9669 | 0.066245 | 0.093622 | 0.0036957 | 0.006052 | 0.019205 | -0.0089723 | 0.037078 | -1.3087 | 0.11352 | -0.003059 | 0.046724 | 0.078805 | -107.4463 | 8.7891 | -111.7905 | 8.9676 | -108.7555 | -110.5041 | -108.9706 | -76.5015 | 8.8348 | -111.9644 | 9.0225 | -78.6118 | -72.7295 | -100.0259 | 0.050354 | -0.19684 | -0.018311 | 3.0853 | 2.8702 | 1.3367 | 2.8198 | 1.2863 | -0.1236 | -0.15106 | 0.036621 | 33.2291 | 11.8149 | 39.1113 | 11.9385 | 39.2349 | 3.035 | 120.7581 | 33.3527 | 120.9869 | 120.5795 | 120.7993 | 120.6299 | 120.6757 | -120.7764 | -120.9503 | 120.8084 | 120.8633 | 4.3945 | 35.3394
2617.3125 | 121.1334 | -112.0834 | 8.7112 | -0.0057221 | 6.9667 | 0.066245 | 0.093836 | 0.00091851 | 0.0090426 | 0.019846 | -0.0059205 | 0.034301 | -1.3074 | 0.12463 | -0.0045544 | 0.048433 | 0.07966 | -107.6843 | 8.5052 | -112.0605 | 8.7753 | -108.9432 | -110.6827 | -109.1721 | -76.5472 | 8.5739 | -112.2162 | 8.7982 | -78.685 | -72.8073 | -100.2182 | 0.022888 | -0.20599 | 0.064087 | 3.1403 | 2.9114 | 1.4008 | 2.8885 | 1.3779 | -0.13275 | -0.13733 | 0.086975 | 33.3984 | 11.8652 | 39.2761 | 11.998 | 39.4089 | 3.1174 | 120.8359 | 33.5312 | 121.0144 | 120.5658 | 120.7901 | 120.5887 | 120.6573 | -120.7718 | -120.9274 | 120.8588 | 120.8817 | 4.3991 | 35.5362
2619.0781 | 121.0144 | -87.4832 | 33.4671 | 0.055313 | 6.9701 | 0.067313 | 0.094691 | 0.0017731 | 0.0079746 | 0.021127 | 0.018494 | 0.042633 | -1.3209 | 0.1242 | -0.0079724 | 0.042665 | 0.073892 | -83.3954 | 33.2886 | -87.3734 | 33.5403 | -84.4986 | -86.0458 | -84.5169 | -56.6757 | 33.3344 | -87.4741 | 33.4579 | -59.8801 | -51.915 | -76.3779 | 0.10986 | -0.17853 | 0.073242 | 2.9846 | 2.9663 | 1.4374 | 2.8564 | 1.3275 | 0.009155 | -0.13275 | -0.009155 | 27.6031 | 11.1053 | 35.5682 | 11.0962 | 35.5591 | 2.8748 | 120.9137 | 27.594 | 120.932 | 120.6619 | 120.8084 | 120.7718 | 120.8176 | -120.8405 | -120.9412 | 121.0236 | 120.9412 | 4.0878 | 30.8075
2620.8594 | 121.0144 | -89.4196 | 31.4941 | 0.0095369 | 6.9703 | 0.066885 | 0.092768 | 0.0026275 | 0.006052 | 0.024759 | 0.00018312 | 0.04071 | -1.3218 | 0.12548 | -0.006477 | 0.042024 | 0.075815 | -85.405 | 31.2607 | -89.3463 | 31.5033 | -86.5036 | -88.0829 | -86.5448 | -58.223 | 31.2744 | -89.4745 | 31.4941 | -61.3541 | -53.5309 | -78.2639 | 0.073243 | -0.23346 | 0.009155 | 2.916 | 2.8748 | 1.3367 | 2.8015 | 1.2634 | -0.054931 | -0.21973 | 0 | 28.0655 | 11.1557 | 35.8887 | 11.2106 | 35.9436 | 2.8427 | 120.8496 | 28.1204 | 120.9686 | 120.607 | 120.7489 | 120.6802 | 120.694 | -120.8405 | -120.9686 | 120.9229 | 120.9137 | 4.0146 | 31.1966
2622.5781 | 121.1243 | -91.7404 | 29.0451 | -0.0057221 | 6.9673 | 0.066458 | 0.090204 | -0.00079049 | 0.006052 | 0.0207 | -0.0028687 | 0.038574 | -1.3215 | 0.12655 | -0.007118 | 0.042878 | 0.073679 | -87.6434 | 28.8849 | -91.6489 | 29.1916 | -88.7329 | -90.3534 | -88.7787 | -59.9991 | 28.8391 | -91.8732 | 29.1595 | -62.9929 | -55.3391 | -80.4337 | 0.091552 | -0.16022 | 0.14648 | 3.0075 | 2.9617 | 1.387 | 2.8702 | 1.2955 | -0.13275 | -0.20599 | 0.11444 | 28.7476 | 11.3068 | 36.4014 | 11.4395 | 36.5341 | 2.916 | 120.8405 | 28.8803 | 121.0327 | 120.5338 | 120.7123 | 120.6253 | 120.5795 | -120.694 | -120.9183 | 120.932 | 120.9 | 4.097 | 31.7413
2624.3594 | 121.0876 | -94.4275 | 26.3992 | 0.0019074 | 6.9671 | 0.066245 | 0.092768 | 0.0019867 | 0.0073338 | 0.019632 | 0.0093383 | 0.037506 | -1.3175 | 0.12826 | -0.005409 | 0.042451 | 0.077737 | -90.3351 | 26.1841 | -94.4138 | 26.4771 | -91.4658 | -93.0908 | -91.5115 | -62.1414 | 26.2115 | -94.5374 | 26.4267 | -65.0574 | -57.6187 | -83.0521 | 0.013733 | -0.21515 | 0.07782 | 2.9617 | 2.916 | 1.3367 | 2.9022 | 1.3229 | -0.10986 | -0.18768 | 0.027466 | 29.3701 | 11.3754 | 36.8088 | 11.4853 | 36.9186 | 2.948 | 120.8908 | 29.48 | 120.9641 | 120.5978 | 120.7489 | 120.6116 | 120.639 | -120.813 | -120.9366 | 120.9045 | 120.8542 | 4.0924 | 32.2861
2626.0781 | 121.106 | -92.0837 | 28.7338 | 0.0095369 | 6.9697 | 0.066458 | 0.093409 | 0.0017731 | 0.0058384 | 0.0207 | -0.0028687 | 0.039642 | -1.316 | 0.12933 | -0.0079724 | 0.044374 | 0.080301 | -88.0096 | 28.5416 | -92.0288 | 28.862 | -89.1403 | -90.7562 | -89.1495 | -60.2554 | 28.5873 | -92.1753 | 28.7796 | -63.2355 | -55.5771 | -80.7404 | 0.054931 | -0.19226 | 0.12817 | 2.9434 | 2.9343 | 1.3275 | 2.8793 | 1.2726 | -0.091553 | -0.14649 | 0.045776 | 28.8483 | 11.3434 | 36.5067 | 11.4349 | 36.5982 | 2.8885 | 120.8908 | 28.9398 | 120.9549 | 120.5704 | 120.7626 | 120.6253 | 120.6711 | -120.7626 | -120.9091 | 120.9457 | 120.8633 | 4.0741 | 31.8283
2627.8594 | 121.0464 | -89.7675 | 31.0776 | 0.032425 | 6.9682 | 0.067954 | 0.09405 | -0.0010041 | 0.0069064 | 0.020486 | 0.015442 | 0.042205 | -1.3192 | 0.12548 | -0.0043408 | 0.042665 | 0.074106 | -85.7071 | 30.8899 | -89.7629 | 31.1874 | -86.8332 | -88.4354 | -86.8378 | -58.3374 | 30.9448 | -89.8499 | 31.0867 | -61.4639 | -53.6041 | -78.4653 | 0.004578 | -0.18768 | 0.10986 | 2.9343 | 2.9297 | 1.3321 | 2.9251 | 1.3275 | -0.082398 | -0.13275 | 0.009155 | 28.3035 | 11.3022 | 36.1633 | 11.3846 | 36.2457 | 2.9297 | 120.9503 | 28.3859 | 120.9366 | 120.6528 | 120.7947 | 120.6573 | 120.7123 | -120.8405 | -120.9274 | 120.9549 | 120.8542 | 4.0604 | 31.4301
2629.5781 | 121.1426 | -87.8311 | 32.9773 | 0.0019074 | 6.9645 | 0.068167 | 0.091059 | -0.0016449 | 0.0039158 | 0.018564 | -0.0059205 | 0.040496 | -1.3207 | 0.12313 | -0.0069044 | 0.04181 | 0.078165 | -83.8486 | 32.7805 | -87.7762 | 33.1146 | -84.8969 | -86.4716 | -84.8557 | -56.7581 | 32.8125 | -87.8906 | 33.0688 | -59.8984 | -51.8372 | -76.5198 | 0.054932 | -0.19684 | 0.13733 | 2.9343 | 2.9755 | 1.3596 | 2.9205 | 1.3046 | -0.059509 | -0.16479 | 0.091553 | 27.9327 | 11.3113 | 35.994 | 11.3709 | 36.0535 | 2.8793 | 120.8908 | 27.9922 | 120.9595 | 120.5566 | 120.7031 | 120.6116 | 120.6436 | -120.7535 | -120.8679 | 120.9457 | 120.9 | 3.9825 | 31.073
2631.3594 | 121.1197 | -87.6755 | 33.1055 | -0.0057221 | 6.9692 | 0.066245 | 0.094263 | 0.0022003 | 0.0084018 | 0.024545 | 0.030701 | 0.043914 | -1.3205 | 0.13232 | -0.003059 | 0.042451 | 0.074533 | -83.67 | 32.8857 | -87.6389 | 33.3481 | -84.7 | -86.3113 | -84.6771 | -56.4972 | 32.9773 | -87.8082 | 33.2153 | -59.7656 | -51.6586 | -76.3824 | 0.036621 | -0.21973 | 0.24261 | 2.9755 | 2.9984 | 1.3641 | 2.9617 | 1.3275 | -0.13275 | -0.12817 | 0.10986 | 27.9099 | 11.293 | 36.0168 | 11.4258 | 36.1496 | 2.9388 | 120.9869 | 28.0426 | 121.0236 | 120.5246 | 120.7855 | 120.5612 | 120.6528 | -120.7443 | -120.9137 | 121.0236 | 120.8908 | 4.0054 | 31.1783
2633.125 | 121.0007 | -87.7716 | 33.0963 | -0.013352 | 6.9707 | 0.067313 | 0.09704 | -0.0016449 | 0.0073338 | 0.021127 | 0.00018312 | 0.043274 | -1.3203 | 0.12014 | -0.0034864 | 0.043733 | 0.076669 | -83.7616 | 32.9178 | -87.7121 | 33.0917 | -84.9655 | -86.5585 | -84.8923 | -56.6849 | 32.9269 | -87.8448 | 33.0414 | -59.8846 | -51.7776 | -76.4969 | 0.059509 | -0.17853 | -0.004577 | 2.8061 | 2.8793 | 1.2131 | 2.8198 | 1.1536 | -0.073243 | -0.16937 | -0.054931 | 27.887 | 11.2747 | 35.994 | 11.348 | 36.0672 | 2.7466 | 120.8038 | 27.9602 | 120.8862 | 120.6299 | 120.7718 | 120.6894 | 120.6985 | -120.8084 | -120.9412 | 120.8633 | 120.813 | 4.01 | 31.0867
2634.9062 | 121.019 | -92.0151 | 28.775 | 0.0095369 | 6.9714 | 0.069022 | 0.095331 | 6.4114e-05 | 0.0075474 | 0.022409 | -0.0028687 | 0.042419 | -1.3177 | 0.12441 | -0.0049818 | 0.042665 | 0.079233 | -87.9318 | 28.537 | -92.0471 | 28.8025 | -89.1632 | -90.7745 | -89.0945 | -59.9899 | 28.5965 | -92.1478 | 29.0955 | -62.851 | -55.2841 | -80.6305 | -0.032043 | -0.23804 | 0.027466 | 2.8519 | 2.9205 | 1.2405 | 2.9526 | 1.2726 | -0.13275 | -0.17853 | 0.32044 | 29.1641 | 11.3846 | 36.731 | 11.5173 | 36.8637 | 2.8839 | 120.8496 | 29.2969 | 121.2433 | 120.5841 | 120.7443 | 120.5521 | 120.6116 | -120.8221 | -120.9229 | 120.8176 | 121.1105 | 4.0833 | 32.0251
2636.6875 | 120.9869 | -92.6102 | 28.1616 | 0.040054 | 6.9731 | 0.068167 | 0.096613 | -0.0020721 | 0.007761 | 0.018991 | 0.00018312 | 0.041351 | -1.3149 | 0.13082 | -0.0043408 | 0.042451 | 0.077524 | -88.4033 | 28.006 | -92.569 | 28.2852 | -89.6347 | -91.2506 | -89.5935 | -60.3561 | 28.0197 | -92.7063 | 28.1891 | -63.3774 | -55.632 | -81.0562 | 0.041198 | -0.15564 | 0.1236 | 2.9755 | 3.0167 | 1.3596 | 2.9755 | 1.3184 | -0.096131 | -0.14191 | 0.027466 | 29.2328 | 11.554 | 36.9781 | 11.6501 | 37.0743 | 2.9343 | 120.8542 | 29.3289 | 120.8954 | 120.575 | 120.726 | 120.6161 | 120.6299 | -120.7306 | -120.8679 | 120.8954 | 120.7993 | 4.2068 | 32.254
2638.4688 | 120.9412 | -91.8549 | 28.9215 | 0.0019074 | 6.9688 | 0.066458 | 0.096186 | 0.0056183 | 0.0062656 | 0.020273 | -0.0028687 | 0.040924 | -1.3171 | 0.12099 | -0.0041272 | 0.045015 | 0.081155 | -87.7258 | 28.7201 | -91.8045 | 28.8986 | -89.0305 | -90.6326 | -88.9297 | -59.8022 | 28.7247 | -91.9418 | 28.8849 | -62.851 | -55.0507 | -80.365 | 0.050354 | -0.20142 | -0.022888 | 2.8244 | 2.9251 | 1.2222 | 2.8748 | 1.1719 | -0.086975 | -0.19684 | -0.036621 | 29.0039 | 11.4899 | 36.8042 | 11.5768 | 36.8912 | 2.774 | 120.7031 | 29.0909 | 120.8267 | 120.5246 | 120.6665 | 120.575 | 120.5795 | -120.726 | -120.8633 | 120.7535 | 120.7397 | 4.129 | 32.0526
2640.1875 | 120.9366 | -91.8869 | 28.8986 | 0.0019074 | 6.9684 | 0.065604 | 0.089991 | -0.0018585 | 0.0051974 | 0.018778 | -0.0089723 | 0.040283 | -1.3183 | 0.12911 | -0.008827 | 0.043092 | 0.075387 | -87.6846 | 28.656 | -91.7999 | 28.981 | -88.8931 | -90.509 | -88.829 | -59.7015 | 28.7247 | -91.9235 | 28.8712 | -62.7365 | -54.9225 | -80.3284 | 0.086975 | -0.24261 | 0.082397 | 2.9938 | 3.0579 | 1.3779 | 2.9709 | 1.2909 | -0.036621 | -0.17395 | -0.027466 | 29.1504 | 11.5585 | 36.9644 | 11.5952 | 37.001 | 2.9068 | 120.7809 | 29.187 | 120.7947 | 120.4559 | 120.6482 | 120.5429 | 120.6116 | -120.6985 | -120.8221 | 120.8679 | 120.7581 | 4.2023 | 32.1854
2641.9688 | 121.0327 | -91.6901 | 28.981 | -0.013352 | 6.9662 | 0.066458 | 0.092554 | -0.00079049 | 0.0073338 | 0.01835 | -0.0028687 | 0.039856 | -1.3175 | 0.12591 | -0.0051954 | 0.041169 | 0.07496 | -87.4786 | 28.7933 | -91.6489 | 29.1916 | -88.623 | -90.271 | -88.5956 | -59.3903 | 28.8208 | -91.7404 | 29.1183 | -62.4435 | -54.6249 | -80.0583 | 0.041198 | -0.18768 | 0.21057 | 3.067 | 3.0945 | 1.4191 | 3.0533 | 1.3779 | -0.050354 | -0.16022 | 0.13733 | 29.2465 | 11.6318 | 37.0651 | 11.6821 | 37.1155 | 3.0258 | 120.8405 | 29.2969 | 120.8588 | 120.4422 | 120.5612 | 120.4834 | 120.5109 | -120.6299 | -120.7214 | 120.8817 | 120.8084 | 4.2114 | 32.2998
2643.75 | 120.9045 | -91.9373 | 28.8162 | -0.013352 | 6.9688 | 0.066031 | 0.096827 | 0.0015595 | 0.0079746 | 0.023477 | 0.024597 | 0.044555 | -1.3177 | 0.13189 | -0.0045544 | 0.040315 | 0.078165 | -87.7625 | 28.6148 | -91.8732 | 28.8986 | -88.9572 | -90.5548 | -88.8474 | -59.61 | 28.7338 | -92.0197 | 28.7567 | -62.6907 | -54.8767 | -80.3513 | 0.064087 | -0.20142 | 0.082398 | 2.98 | 3.0899 | 1.3824 | 3.0258 | 1.3184 | -0.082397 | -0.082397 | -0.059509 | 29.2465 | 11.586 | 37.0605 | 11.6684 | 37.1429 | 2.916 | 120.7718 | 29.3289 | 120.7764 | 120.488 | 120.7535 | 120.5521 | 120.6711 | -120.6894 | -120.8359 | 120.8359 | 120.694 | 4.1748 | 32.3273
2645.5312 | 120.9824 | -40.8417 | 80.0812 | 0.0019074 | 6.9705 | 0.063681 | 0.092554 | -0.0063447 | 0.0041294 | 0.018137 | -0.0028687 | 0.0531 | -1.35 | 0.13467 | -0.0062634 | 0.035188 | 0.068124 | -37.6648 | 79.8065 | -40.7135 | 80.1682 | -38.3469 | -39.6103 | -37.8204 | -18.718 | 79.8386 | -40.7318 | 79.9438 | -23.8998 | -11.7188 | -31.0638 | 0.12817 | -0.27466 | 0.086975 | 2.4948 | 3.0212 | 1.2314 | 2.8931 | 1.1032 | 0.10986 | -0.24262 | -0.13733 | 16.9418 | 9.7778 | 29.1229 | 9.668 | 29.0131 | 2.3666 | 120.8817 | 16.832 | 120.6757 | 120.52 | 120.5704 | 120.6482 | 120.6802 | -120.7947 | -120.813 | 121.0098 | 120.7855 | 3.1769 | 22.1237
2647.25 | 121.1014 | -40.5945 | 80.3055 | 0.0095369 | 6.968 | 0.066031 | 0.092554 | -0.0016449 | 0.005411 | 0.018778 | -0.0059205 | 0.054382 | -1.35 | 0.13958 | -0.0043408 | 0.037538 | 0.06962 | -37.4863 | 80.0995 | -40.4892 | 80.4199 | -38.1134 | -39.4135 | -37.5961 | -18.3975 | 80.0995 | -40.535 | 80.2414 | -23.5977 | -11.38 | -30.7709 | 0.10529 | -0.20599 | 0.11444 | 2.4811 | 2.9984 | 1.181 | 2.8931 | 1.0757 | 0.059509 | -0.20599 | -0.064087 | 16.9968 | 9.8236 | 29.2145 | 9.7641 | 29.155 | 2.3758 | 120.9091 | 16.9373 | 120.7764 | 120.5887 | 120.6345 | 120.694 | 120.694 | -120.7947 | -120.8405 | 121.0144 | 120.8359 | 3.1082 | 22.197
2649.0469 | 121.0968 | -40.4434 | 80.4474 | 0.055313 | 6.9712 | 0.067526 | 0.097681 | -0.0029267 | 0.0075474 | 0.019632 | 0.021545 | 0.059082 | -1.3472 | 0.13702 | -0.003059 | 0.036042 | 0.06727 | -37.3489 | 80.2734 | -40.4297 | 80.5847 | -37.999 | -39.3036 | -37.4863 | -18.2144 | 80.2689 | -40.4709 | 80.3513 | -23.5336 | -11.293 | -30.6931 | 0.013733 | -0.17395 | 0.13733 | 2.4445 | 2.9572 | 1.1398 | 2.9434 | 1.1261 | -0.027466 | -0.17853 | -0.096131 | 16.9098 | 9.7504 | 29.1504 | 9.7778 | 29.1779 | 2.4307 | 121.0144 | 16.9373 | 120.8221 | 120.7031 | 120.7397 | 120.7169 | 120.7123 | -120.8771 | -120.9183 | 121.0281 | 120.7947 | 3.0945 | 22.229
2650.7656 | 121.0556 | -40.3656 | 80.5801 | 0.0095369 | 6.9701 | 0.065176 | 0.095759 | 0.0022003 | 0.0056248 | 0.020914 | -0.0028687 | 0.058227 | -1.3506 | 0.13232 | -0.0051954 | 0.036897 | 0.064706 | -37.2849 | 80.4062 | -40.329 | 80.6305 | -38.0264 | -39.3127 | -37.4817 | -18.219 | 80.397 | -40.3519 | 80.4016 | -23.497 | -11.2152 | -30.6107 | 0.036622 | -0.17395 | 0.050354 | 2.3392 | 2.8839 | 1.0529 | 2.8473 | 1.0162 | 0.013733 | -0.1831 | -0.17853 | 16.8686 | 9.7549 | 29.1504 | 9.7412 | 29.1367 | 2.3026 | 120.9595 | 16.8549 | 120.7535 | 120.7352 | 120.7489 | 120.7718 | 120.7626 | -120.9091 | -120.932 | 120.9961 | 120.7672 | 3.0807 | 22.1466
2652.5312 | 121.1609 | -40.2466 | 80.6717 | 0.040054 | 6.9688 | 0.066672 | 0.095972 | -0.0042083 | 0.0058384 | 0.021341 | 0.0032349 | 0.056305 | -1.3485 | 0.13552 | -0.004768 | 0.038606 | 0.071542 | -37.1887 | 80.5389 | -40.2008 | 80.7632 | -37.8799 | -39.1525 | -37.3032 | -18.0588 | 80.4749 | -40.2374 | 80.5756 | -23.3368 | -10.9955 | -30.4367 | 0.045776 | -0.13275 | 0.091553 | 2.3666 | 2.9434 | 1.0941 | 2.8976 | 1.0483 | 0.009155 | -0.19684 | -0.09613 | 16.9098 | 9.8099 | 29.2511 | 9.8007 | 29.2419 | 2.3209 | 120.9641 | 16.9006 | 120.813 | 120.7397 | 120.7123 | 120.7855 | 120.7214 | -120.8725 | -120.9091 | 121.0098 | 120.8221 | 3.0579 | 22.1878
2654.2969 | 121.1746 | -40.1184 | 80.8182 | -0.0057221 | 6.9705 | 0.06539 | 0.093622 | -0.0020721 | 0.0030612 | 0.019632 | 0.00018312 | 0.053955 | -1.3508 | 0.13787 | -0.008186 | 0.038179 | 0.064493 | -37.0514 | 80.6213 | -40.0681 | 80.9235 | -37.7289 | -38.9877 | -37.1841 | -17.8574 | 80.6168 | -40.1413 | 80.722 | -23.1445 | -10.8124 | -30.304 | 0.050354 | -0.19684 | 0.10529 | 2.3895 | 2.9343 | 1.1307 | 2.8839 | 1.0803 | -0.022888 | -0.20142 | -0.09613 | 16.9739 | 9.8145 | 29.306 | 9.8373 | 29.3289 | 2.3392 | 120.9915 | 16.9968 | 120.8633 | 120.6894 | 120.7581 | 120.7397 | 120.7352 | -120.8862 | -120.9595 | 121.0419 | 120.8405 | 3.067 | 22.261
2656.0312 | 121.1655 | -40.0314 | 80.928 | 0.062942 | 6.9707 | 0.067099 | 0.095545 | -0.00014949 | 0.0045566 | 0.021341 | 0.0093383 | 0.058868 | -1.3459 | 0.12954 | -0.0037 | 0.039674 | 0.069406 | -36.969 | 80.7266 | -40.0269 | 81.0242 | -37.6556 | -38.9328 | -37.088 | -17.7475 | 80.7449 | -40.0681 | 80.8044 | -23.0804 | -10.7025 | -30.1941 | 0.004578 | -0.20142 | 0.09613 | 2.3758 | 2.9434 | 1.0986 | 2.9388 | 1.0941 | -0.036621 | -0.18311 | -0.1236 | 16.951 | 9.8373 | 29.3289 | 9.874 | 29.3655 | 2.3712 | 121.051 | 16.9876 | 120.8725 | 120.7535 | 120.813 | 120.7581 | 120.7764 | -120.9549 | -120.9961 | 121.0556 | 120.8359 | 3.0624 | 22.2839
2657.7969 | 121.1151 | -39.9536 | 81.0745 | -0.0057221 | 6.9722 | 0.065817 | 0.095759 | -0.0016449 | 0.0056248 | 0.0207 | -0.0059205 | 0.058868 | -1.3491 | 0.13296 | -0.0041272 | 0.03882 | 0.067483 | -36.9232 | 80.9097 | -39.8849 | 81.0379 | -37.6923 | -38.9694 | -37.0789 | -17.6743 | 80.8868 | -39.9445 | 80.8731 | -23.0392 | -10.6247 | -30.13 | 0.068664 | -0.16479 | -0.036621 | 2.2614 | 2.8748 | 0.98419 | 2.8061 | 0.91553 | 0.009155 | -0.18768 | -0.20142 | 16.9144 | 9.8236 | 29.3289 | 9.8145 | 29.3198 | 2.1927 | 120.9229 | 16.9052 | 120.8176 | 120.7947 | 120.8313 | 120.8633 | 120.8405 | -120.9595 | -121.019 | 120.9915 | 120.8267 | 3.0304 | 22.2794
2659.5625 | 121.2708 | -39.7888 | 81.134 | -0.020981 | 6.9692 | 0.065604 | 0.096613 | -0.0024995 | 0.0056248 | 0.020486 | -0.0028687 | 0.056945 | -1.3495 | 0.14407 | -0.0013502 | 0.040101 | 0.06962 | -36.7401 | 80.9738 | -39.7522 | 81.2576 | -37.4176 | -38.7039 | -36.8591 | -17.3813 | 80.928 | -39.7934 | 81.0974 | -22.7737 | -10.3363 | -29.8874 | 0.036621 | -0.16022 | 0.1236 | 2.3712 | 2.9297 | 1.0849 | 2.8931 | 1.0483 | -0.004578 | -0.20599 | -0.036621 | 17.0151 | 9.9014 | 29.4525 | 9.906 | 29.4571 | 2.3346 | 121.0098 | 17.0197 | 120.8908 | 120.726 | 120.7214 | 120.7626 | 120.7169 | -120.8862 | -120.9274 | 121.0464 | 120.8862 | 3.0487 | 22.4075
2661.2656 | 121.2067 | -39.7202 | 81.2439 | 0.017166 | 6.9703 | 0.066885 | 0.095972 | 0.0015595 | 0.0062656 | 0.018778 | 0.0032349 | 0.055664 | -1.35 | 0.13723 | -0.0062634 | 0.03882 | 0.067483 | -36.6852 | 81.0883 | -39.679 | 81.3354 | -37.3672 | -38.6627 | -36.7676 | -17.3035 | 81.0425 | -39.7568 | 81.1249 | -22.7234 | -10.2402 | -29.8462 | 0.041199 | -0.15564 | 0.091553 | 2.3529 | 2.9526 | 1.0574 | 2.9114 | 1.0162 | -0.036621 | -0.20142 | -0.11902 | 16.9968 | 9.874 | 29.48 | 9.9106 | 29.5166 | 2.3117 | 121.0144 | 17.0334 | 120.8817 | 120.7672 | 120.7993 | 120.8084 | 120.7626 | -120.9229 | -121.0007 | 121.0556 | 120.845 | 3.035 | 22.4167
2663.0469 | 121.2799 | -39.6057 | 81.3721 | -0.013352 | 6.9697 | 0.064749 | 0.095118 | 6.4114e-05 | 0.0034884 | 0.021341 | -0.0028687 | 0.057373 | -1.3482 | 0.13467 | -0.007118 | 0.038606 | 0.067483 | -36.5341 | 81.1752 | -39.5554 | 81.5002 | -37.1704 | -38.475 | -36.6211 | -17.0471 | 81.1432 | -39.5874 | 81.2988 | -22.5357 | -9.9747 | -29.6814 | 0.050354 | -0.19684 | 0.12817 | 2.4353 | 2.9846 | 1.1307 | 2.9343 | 1.0803 | 0.018311 | -0.22888 | -0.073242 | 17.07 | 9.9243 | 29.631 | 9.906 | 29.6127 | 2.3849 | 121.0556 | 17.0517 | 120.8862 | 120.7306 | 120.7306 | 120.7809 | 120.7489 | -120.9274 | -120.9595 | 121.106 | 120.9045 | 3.0716 | 22.5586
2664.8281 | 121.225 | -39.5279 | 81.4865 | 0.017166 | 6.9697 | 0.06539 | 0.095759 | -0.0020721 | 0.005411 | 0.0207 | 0.0062865 | 0.056732 | -1.3478 | 0.1415 | -0.0058362 | 0.036897 | 0.071115 | -36.4609 | 81.3171 | -39.4913 | 81.5735 | -37.1429 | -38.4293 | -36.5479 | -17.0105 | 81.2988 | -39.5279 | 81.3766 | -22.4854 | -9.8694 | -29.6036 | 0.036621 | -0.16937 | 0.086975 | 2.3849 | 2.98 | 1.0986 | 2.9434 | 1.062 | 0 | -0.18768 | -0.10986 | 17.0425 | 9.9243 | 29.6585 | 9.9243 | 29.6585 | 2.3483 | 121.0648 | 17.0425 | 120.9045 | 120.8084 | 120.8267 | 120.845 | 120.8267 | -120.9778 | -121.0144 | 121.1014 | 120.9045 | 3.067 | 22.5174
2666.6094 | 121.2204 | -39.2303 | 81.7657 | 0.024795 | 6.9722 | 0.066885 | 0.098109 | 0.0019867 | 0.0056248 | 0.022195 | 0.0062865 | 0.059509 | -1.348 | 0.13168 | -0.0086132 | 0.038179 | 0.065774 | -36.2 | 81.5506 | -39.299 | 81.7474 | -36.9644 | -38.2782 | -36.3556 | -16.7816 | 81.5277 | -39.3631 | 81.7474 | -22.197 | -9.5901 | -29.3518 | -0.068664 | -0.21515 | -0.01831 | 2.2659 | 2.8748 | 0.95215 | 2.9434 | 1.0208 | -0.13275 | -0.23804 | -0.01831 | 17.0334 | 9.8785 | 29.6402 | 10.0113 | 29.7729 | 2.3346 | 121.0464 | 17.1661 | 121.1105 | 120.8496 | 120.8908 | 120.7809 | 120.7581 | -121.0648 | -121.1288 | 120.9778 | 120.9778 | 3.0304 | 22.4487
2668.3125 | 121.225 | -32.1213 | 88.9526 | 0.0019074 | 6.9716 | 0.067954 | 0.093622 | -0.0037811 | 0.0047702 | 0.022409 | -0.0089723 | 0.059936 | -1.3529 | 0.13744 | -0.0094678 | 0.037324 | 0.066202 | -29.1779 | 88.71 | -32.0709 | 89.003 | -29.7592 | -31.0226 | -29.1046 | -11.0367 | 88.7054 | -32.103 | 88.7787 | -16.8686 | -3.6255 | -22.4533 | 0.050354 | -0.24262 | 0.050354 | 2.3621 | 3.0167 | 1.0986 | 2.9663 | 1.0483 | 0.018311 | -0.24719 | -0.17395 | 15.2527 | 9.668 | 28.4958 | 9.6497 | 28.4775 | 2.3117 | 121.0739 | 15.2344 | 120.8817 | 120.7809 | 120.8084 | 120.8313 | 120.8267 | -121.0236 | -121.0556 | 121.1243 | 120.9 | 2.9434 | 21.0846
2670.0938 | 121.2982 | -31.929 | 89.0762 | -0.0057221 | 6.9703 | 0.063895 | 0.09405 | -0.0037811 | 0.0056248 | 0.022195 | -0.0028687 | 0.057586 | -1.3527 | 0.14342 | -0.0060498 | 0.037111 | 0.068979 | -28.981 | 88.9023 | -31.8558 | 89.2136 | -29.567 | -30.8166 | -28.8986 | -10.7941 | 88.8702 | -31.9199 | 89.0076 | -16.6443 | -3.3371 | -22.197 | 0.073242 | -0.17395 | 0.13733 | 2.3621 | 3.0304 | 1.1124 | 2.9572 | 1.0391 | 0.009155 | -0.20599 | -0.068665 | 15.2847 | 9.7321 | 28.5919 | 9.7229 | 28.5828 | 2.2888 | 121.0693 | 15.2756 | 120.9274 | 120.7581 | 120.7901 | 120.8313 | 120.7993 | -120.932 | -120.9961 | 121.1426 | 120.9366 | 2.948 | 21.1349
2671.875 | 121.2753 | -35.9299 | 85.0891 | 0.024795 | 6.9712 | 0.066245 | 0.095972 | -0.0029267 | 0.00712 | 0.022195 | 0.00018312 | 0.058441 | -1.3497 | 0.15133 | -0.0049818 | 0.037324 | 0.066843 | -32.8903 | 84.9289 | -35.8704 | 85.1852 | -33.5724 | -34.8724 | -32.9361 | -14.0121 | 84.9335 | -35.8978 | 84.9884 | -19.7433 | -6.7062 | -26.088 | 0.05951 | -0.16022 | 0.096131 | 2.3575 | 2.9938 | 1.0574 | 2.9343 | 0.99792 | 0.032044 | -0.15564 | -0.10071 | 16.1865 | 9.8419 | 29.2236 | 9.8099 | 29.1916 | 2.298 | 121.0556 | 16.1545 | 120.8862 | 120.7993 | 120.8313 | 120.8588 | 120.8633 | -120.9595 | -120.9869 | 121.1151 | 120.9183 | 3.0396 | 21.9177
2673.6719 | 121.2708 | -29.892 | 91.1499 | -0.0057221 | 6.9729 | 0.064536 | 0.092768 | 0.0022003 | 0.002634 | 0.022409 | -0.0059205 | 0.059295 | -1.3566 | 0.13531 | -0.0069044 | 0.035188 | 0.063211 | -26.9485 | 90.9393 | -29.8462 | 91.2598 | -27.5116 | -28.7704 | -26.8433 | -9.0363 | 90.9485 | -29.8462 | 91.0355 | -15.0513 | -1.5427 | -20.2194 | 0.045777 | -0.21057 | 0.10986 | 2.3804 | 3.0487 | 1.1215 | 3.0029 | 1.0757 | 0.045777 | -0.20142 | -0.11444 | 14.8407 | 9.6725 | 28.3493 | 9.6268 | 28.3035 | 2.3346 | 121.106 | 14.7949 | 120.8817 | 120.7855 | 120.7947 | 120.8313 | 120.8405 | -120.9961 | -120.9961 | 121.1517 | 120.9274 | 2.9434 | 20.8557
2675.4375 | 121.2799 | -29.1275 | 91.9235 | 0.070572 | 6.9699 | 0.067526 | 0.095331 | 0.0011321 | 0.0073338 | 0.019846 | 0.01239 | 0.061859 | -1.3534 | 0.14385 | -0.0051954 | 0.036897 | 0.062997 | -26.1612 | 91.8137 | -29.0543 | 92.038 | -26.7746 | -28.0518 | -26.0788 | -8.075 | 91.7633 | -29.1275 | 91.7816 | -14.0717 | -0.65918 | -19.4092 | 0.073242 | -0.10986 | 0.11444 | 2.3529 | 3.0487 | 1.0757 | 2.9755 | 1.0025 | 0 | -0.16022 | -0.14191 | 15.0558 | 9.7183 | 28.4683 | 9.7183 | 28.4683 | 2.2797 | 121.0922 | 15.0558 | 120.9091 | 120.8679 | 120.8908 | 120.9412 | 120.8908 | -120.9778 | -121.051 | 121.1655 | 120.9091 | 2.9663 | 21.0526
2677.1562 | 121.2021 | -29.0085 | 92.1295 | 0.08583 | 6.9742 | 0.067099 | 0.098322 | 0.0058319 | 0.0058384 | 0.023477 | 0.018494 | 0.064209 | -1.3529 | 0.13744 | -0.007118 | 0.033906 | 0.067911 | -26.0559 | 91.983 | -29.0085 | 92.1112 | -26.6922 | -27.951 | -25.9827 | -8.1848 | 91.9601 | -29.0222 | 91.832 | -14.1632 | -0.70038 | -19.3542 | 0 | -0.14649 | -0.018311 | 2.3163 | 3.0258 | 1.0574 | 3.0258 | 1.0574 | -0.013733 | -0.16937 | -0.29755 | 14.8453 | 9.6542 | 28.3081 | 9.668 | 28.3218 | 2.3163 | 121.1197 | 14.859 | 120.8542 | 120.9915 | 120.9824 | 120.9915 | 120.9686 | -121.138 | -121.1517 | 121.1197 | 120.8405 | 2.9526 | 20.8237
2678.9375 | 121.2158 | -28.3905 | 92.7292 | -0.0057221 | 6.9703 | 0.064963 | 0.095759 | 0.0028411 | 0.004343 | 0.020273 | -0.0059205 | 0.060363 | -1.3534 | 0.13723 | -0.0043408 | 0.036683 | 0.069406 | -25.4654 | 92.5873 | -28.3173 | 92.6788 | -26.1703 | -27.4246 | -25.4288 | -7.5027 | 92.5232 | -28.3813 | 92.4912 | -13.4811 | -0.073242 | -18.6813 | 0.073242 | -0.14191 | -0.050354 | 2.2202 | 2.9617 | 0.96588 | 2.8885 | 0.89264 | 0.009155 | -0.20599 | -0.23804 | 14.9094 | 9.7092 | 28.3173 | 9.7 | 28.3081 | 2.1469 | 120.9961 | 14.9002 | 120.8725 | 120.9045 | 120.9045 | 120.9778 | 120.9137 | -121.0464 | -121.1105 | 121.0693 | 120.8817 | 2.9251 | 20.8878
2680.7188 | 121.2433 | -27.3331 | 93.7958 | 0.040054 | 6.9733 | 0.067954 | 0.096827 | 0.0024139 | 0.0058384 | 0.023477 | 0.018494 | 0.062713 | -1.3521 | 0.14001 | -0.0069044 | 0.036256 | 0.066202 | -24.4171 | 93.6539 | -27.3148 | 93.7912 | -25.0626 | -26.2802 | -24.3027 | -5.9052 | 93.6493 | -27.3514 | 93.5532 | -11.7645 | 1.4236 | -17.5049 | 0.018311 | -0.14191 | -0.004577 | 2.2705 | 3.0304 | 1.0529 | 3.0121 | 1.0345 | -0.01831 | -0.14648 | -0.24261 | 15.5685 | 9.8282 | 28.7567 | 9.8465 | 28.775 | 2.2522 | 121.106 | 15.5869 | 120.9045 | 120.9686 | 121.0007 | 120.9869 | 120.9824 | -121.1105 | -121.1472 | 121.1243 | 120.8862 | 2.916 | 21.4279
2682.4844 | 121.3394 | -28.1021 | 92.9443 | -0.0057221 | 6.9707 | 0.064963 | 0.095759 | 0.00091851 | 0.004343 | 0.020914 | 0.030701 | 0.064422 | -1.3485 | 0.13659 | -0.00049559 | 0.03882 | 0.066629 | -25.1541 | 92.7887 | -28.0518 | 93.0588 | -25.7492 | -27.0401 | -25.0626 | -6.3812 | 92.775 | -28.1433 | 92.8848 | -12.291 | 0.85144 | -18.1686 | 0.050354 | -0.15564 | 0.11444 | 2.3529 | 3.0396 | 1.062 | 2.9892 | 1.0117 | -0.041199 | -0.16937 | -0.059509 | 15.8112 | 9.9335 | 28.9536 | 9.9747 | 28.9948 | 2.3026 | 121.1105 | 15.8524 | 121.0281 | 120.8405 | 120.9183 | 120.8908 | 120.8771 | -120.9961 | -121.0876 | 121.1609 | 120.9869 | 2.948 | 21.7209
2684.2031 | 121.3531 | -27.7634 | 93.2785 | -0.013352 | 6.9705 | 0.064536 | 0.095331 | -0.0024995 | 0.0041294 | 0.023691 | -0.0059205 | 0.060363 | -1.3517 | 0.1383 | -0.0058362 | 0.035615 | 0.065988 | -24.8383 | 93.1183 | -27.7039 | 93.4067 | -25.3601 | -26.651 | -24.678 | -6.0059 | 93.0679 | -27.7634 | 93.219 | -11.879 | 1.2589 | -17.8162 | 0.05951 | -0.16022 | 0.12817 | 2.4033 | 3.0853 | 1.1124 | 3.0258 | 1.0529 | 0 | -0.21057 | -0.059509 | 15.8844 | 9.9472 | 29.0222 | 9.9472 | 29.0222 | 2.3438 | 121.1105 | 15.8844 | 120.9824 | 120.8221 | 120.8313 | 120.8817 | 120.8313 | -120.9824 | -121.0419 | 121.17 | 120.9824 | 2.9251 | 21.7575
2685.9844 | 121.3211 | -24.1425 | 96.9635 | 0.0095369 | 6.9724 | 0.067526 | 0.09405 | -0.0044221 | 0.0037022 | 0.022836 | -0.0028687 | 0.061004 | -1.3514 | 0.14278 | -0.0060498 | 0.037538 | 0.067697 | -21.2906 | 96.7804 | -24.0875 | 96.9818 | -21.8307 | -23.0759 | -21.08 | -2.6093 | 96.73 | -24.1196 | 96.7987 | -8.4183 | 4.7241 | -14.1724 | 0.054932 | -0.1831 | 0.018311 | 2.3117 | 3.0624 | 1.0666 | 3.0075 | 1.0117 | 0.022888 | -0.23346 | -0.16479 | 15.7242 | 9.9701 | 28.8666 | 9.9472 | 28.8437 | 2.2568 | 121.0693 | 15.7013 | 120.9183 | 120.8679 | 120.8496 | 120.9229 | 120.8725 | -121.051 | -121.0831 | 121.1243 | 120.9412 | 2.8519 | 21.5332
2687.75 | 121.3257 | -24.3622 | 96.7667 | 0.0019074 | 6.9712 | 0.063895 | 0.094904 | -0.0037811 | 0.0032748 | 0.022623 | -0.0059205 | 0.059936 | -1.351 | 0.14364 | -0.0062634 | 0.037324 | 0.067056 | -21.4828 | 96.5927 | -24.2798 | 96.8033 | -22.0047 | -23.2498 | -21.2585 | -2.7832 | 96.5286 | -24.3073 | 96.6248 | -8.6105 | 4.5547 | -14.36 | 0.082398 | -0.17395 | 0.036621 | 2.3575 | 3.1036 | 1.1124 | 3.0212 | 1.03 | 0.054932 | -0.23804 | -0.14191 | 15.7516 | 10.0021 | 28.9169 | 9.9472 | 28.862 | 2.2751 | 121.0831 | 15.6967 | 120.932 | 120.8725 | 120.8359 | 120.9549 | 120.8908 | -121.0464 | -121.0739 | 121.1655 | 120.9869 | 2.8793 | 21.579
2689.4531 | 121.3348 | -24.0875 | 96.9589 | -0.0057221 | 6.9729 | 0.06539 | 0.097895 | -0.0012177 | 0.0049838 | 0.023264 | -0.0059205 | 0.063141 | -1.3525 | 0.15047 | -0.0026318 | 0.039674 | 0.068338 | -21.2402 | 96.8399 | -24.0692 | 97.023 | -21.8033 | -23.085 | -21.0709 | -2.5497 | 96.817 | -24.0646 | 96.8445 | -8.3588 | 4.7882 | -14.1037 | 0.01831 | -0.11902 | 0.064087 | 2.2842 | 3.0167 | 1.0025 | 2.9984 | 0.98419 | 0.022888 | -0.14191 | -0.11444 | 15.7288 | 9.9838 | 28.8757 | 9.9609 | 28.8528 | 2.2659 | 121.0922 | 15.7059 | 120.9091 | 120.9091 | 120.8817 | 120.9274 | 120.9045 | -121.0281 | -121.0236 | 121.1105 | 120.932 | 2.8473 | 21.5378
2691.2969 | 121.2067 | -23.9868 | 97.1832 | -0.0057221 | 6.9742 | 0.063681 | 0.09704 | -0.0010041 | 0.0051974 | 0.021768 | -0.0028687 | 0.063141 | -1.3525 | 0.1368 | -0.0039136 | 0.037965 | 0.067056 | -21.1166 | 97.0596 | -23.9365 | 97.1146 | -21.7758 | -23.0209 | -20.9839 | -2.5406 | 96.9955 | -23.941 | 96.9177 | -8.3267 | 4.834 | -14.0167 | 0.050354 | -0.1236 | -0.068665 | 2.211 | 3.0029 | 0.96588 | 2.9526 | 0.91553 | 0.045776 | -0.18768 | -0.2655 | 15.6601 | 9.9701 | 28.8208 | 9.9243 | 28.775 | 2.1606 | 121.051 | 15.6143 | 120.8588 | 120.9961 | 120.9366 | 121.0464 | 120.9824 | -121.1197 | -121.1243 | 121.1014 | 120.9045 | 2.8702 | 21.4462
2693.0781 | 121.257 | -23.8724 | 97.261 | 0.062942 | 6.9735 | 0.066245 | 0.098322 | -0.0039947 | 0.0047702 | 0.022836 | 0.024597 | 0.063568 | -1.35 | 0.13659 | -0.008186 | 0.036897 | 0.064706 | -20.9656 | 97.142 | -23.8678 | 97.2427 | -21.5836 | -22.8241 | -20.8054 | -2.3804 | 97.1008 | -23.9182 | 96.9955 | -8.2031 | 4.9667 | -13.916 | 0.004577 | -0.11902 | -0.01831 | 2.2888 | 3.067 | 1.0483 | 3.0624 | 1.0437 | -0.045777 | -0.16022 | -0.2655 | 15.6693 | 9.9564 | 28.8391 | 10.0021 | 28.8849 | 2.2842 | 121.1105 | 15.715 | 120.9137 | 121.0098 | 121.019 | 121.0144 | 120.9732 | -121.1288 | -121.1792 | 121.1151 | 120.8679 | 2.9068 | 21.492
2694.8594 | 121.3257 | -24.7101 | 96.3913 | 0.055313 | 6.9739 | 0.068167 | 0.097895 | 0.00049131 | 0.007761 | 0.021982 | 0.01239 | 0.061859 | -1.3504 | 0.14107 | -0.0037 | 0.03647 | 0.063638 | -21.7941 | 96.2402 | -24.7055 | 96.4645 | -22.348 | -23.6526 | -21.6156 | -3.067 | 96.199 | -24.7101 | 96.2402 | -8.9081 | 4.2755 | -14.6988 | 0.004578 | -0.15106 | 0.073243 | 2.3621 | 3.0945 | 1.0574 | 3.0899 | 1.0529 | 0 | -0.19226 | -0.15106 | 15.802 | 10.0113 | 28.9856 | 10.0113 | 28.9856 | 2.3575 | 121.17 | 15.802 | 120.9503 | 120.9457 | 120.9091 | 120.9503 | 120.9091 | -121.0968 | -121.1014 | 121.1746 | 120.9503 | 2.916 | 21.6431
2696.5781 | 121.3303 | -24.1287 | 97.0001 | 0.062942 | 6.9729 | 0.068808 | 0.097681 | 0.0013459 | 0.0037022 | 0.023477 | 0.01239 | 0.062286 | -1.3506 | 0.14342 | -0.0039136 | 0.037538 | 0.068979 | -21.1807 | 96.8399 | -24.1013 | 97.0459 | -21.7484 | -23.0667 | -21.048 | -2.5085 | 96.7941 | -24.1425 | 96.8124 | -8.3725 | 4.8523 | -14.09 | 0.027466 | -0.16022 | 0.045776 | 2.3804 | 3.0807 | 1.062 | 3.0533 | 1.0345 | -0.013733 | -0.20599 | -0.18768 | 15.7562 | 10.0388 | 28.981 | 10.0525 | 28.9948 | 2.3529 | 121.1472 | 15.77 | 120.9549 | 120.9412 | 120.9366 | 120.9686 | 120.9229 | -121.1014 | -121.1426 | 121.1746 | 120.9412 | 2.948 | 21.6202
2698.3438 | 121.344 | -24.3027 | 96.7575 | 0.062942 | 6.9742 | 0.067526 | 0.096827 | 0.0024139 | 0.008829 | 0.021555 | 0.021545 | 0.064209 | -1.3506 | 0.14513 | -0.0049818 | 0.037538 | 0.066629 | -21.3364 | 96.666 | -24.2889 | 96.9086 | -21.904 | -23.2224 | -21.2173 | -2.6001 | 96.6156 | -24.321 | 96.6476 | -8.519 | 4.7333 | -14.2548 | 0.013733 | -0.091552 | 0.15106 | 2.3987 | 3.0853 | 1.0803 | 3.0716 | 1.0666 | -0.018311 | -0.14191 | -0.10986 | 15.7837 | 10.0479 | 29.0359 | 10.0662 | 29.0543 | 2.3849 | 121.1975 | 15.802 | 120.9686 | 120.9549 | 120.9366 | 120.9686 | 120.9183 | -121.0464 | -121.0785 | 121.2112 | 120.9503 | 2.9663 | 21.7026
2700.0469 | 121.2845 | -24.5453 | 96.611 | -0.013352 | 6.9705 | 0.064322 | 0.093836 | -0.0024995 | 0.0017796 | 0.018564 | -0.0028687 | 0.061432 | -1.3506 | 0.14129 | -0.0077588 | 0.034974 | 0.067483 | -21.5515 | 96.4371 | -24.4629 | 96.6522 | -22.1603 | -23.4512 | -21.4828 | -2.8839 | 96.3638 | -24.5316 | 96.3867 | -8.7021 | 4.5547 | -14.4791 | 0.082397 | -0.17395 | 0.041199 | 2.3849 | 3.0624 | 1.0941 | 2.98 | 1.0117 | 0.013733 | -0.24719 | -0.2243 | 15.8432 | 10.0662 | 29.1 | 10.0525 | 29.0863 | 2.3026 | 121.1151 | 15.8295 | 120.9183 | 120.9 | 120.8954 | 120.9824 | 120.9091 | -121.0739 | -121.1426 | 121.1975 | 120.932 | 2.9938 | 21.6614
2701.8281 | 121.3303 | -23.2773 | 97.8653 | 0.017166 | 6.9727 | 0.065604 | 0.096186 | 0.00049131 | 0.005411 | 0.021127 | 0.0032349 | 0.061218 | -1.3502 | 0.14385 | -0.004768 | 0.039033 | 0.071115 | -20.343 | 97.7005 | -23.2132 | 97.9065 | -20.8832 | -22.2153 | -20.1645 | -1.6525 | 97.6959 | -23.2544 | 97.6868 | -7.4707 | 5.8044 | -13.1699 | 0.064087 | -0.16479 | 0.041199 | 2.3941 | 3.1128 | 1.062 | 3.0487 | 0.99792 | 0.022888 | -0.16937 | -0.17853 | 15.8066 | 10.1074 | 29.0817 | 10.0845 | 29.0588 | 2.33 | 121.1197 | 15.7837 | 120.9412 | 120.9137 | 120.9503 | 120.9778 | 120.9732 | -121.0785 | -121.1197 | 121.1838 | 120.9641 | 2.9343 | 21.6248
2703.5469 | 121.2936 | -24.0784 | 97.0779 | 0.024795 | 6.975 | 0.066245 | 0.097681 | 0.0030547 | 0.0030612 | 0.023691 | -0.0028687 | 0.065918 | -1.351 | 0.14471 | -0.0045544 | 0.033479 | 0.068124 | -21.0709 | 96.9452 | -24.0189 | 97.1237 | -21.7026 | -23.0576 | -21.0251 | -2.4261 | 96.9223 | -24.0555 | 96.8765 | -8.2581 | 4.9988 | -13.9755 | 0.059509 | -0.13275 | 0.045776 | 2.3758 | 3.0533 | 1.0208 | 2.9938 | 0.9613 | 0.022888 | -0.15564 | -0.20142 | 15.8203 | 10.1028 | 29.0771 | 10.08 | 29.0543 | 2.3163 | 121.1426 | 15.7974 | 120.932 | 120.9641 | 120.9778 | 121.0236 | 121.0007 | -121.0968 | -121.1334 | 121.2021 | 120.9549 | 3.0075 | 21.6522
2705.3125 | 121.2662 | -24.0326 | 97.1512 | -0.0057221 | 6.9722 | 0.064963 | 0.095331 | -0.0020721 | 0.0037022 | 0.019418 | -0.0028687 | 0.062927 | -1.3508 | 0.14513 | -0.0092542 | 0.036256 | 0.065988 | -21.0663 | 96.9864 | -23.9502 | 97.1008 | -21.7026 | -23.0164 | -20.9793 | -2.4582 | 96.9635 | -23.9914 | 96.8765 | -8.2489 | 5.0537 | -13.9343 | 0.082398 | -0.16479 | -0.050354 | 2.33 | 3.0533 | 1.0162 | 2.9709 | 0.93384 | 0.041199 | -0.18768 | -0.27466 | 15.7837 | 10.0983 | 29.0863 | 10.0571 | 29.0451 | 2.2476 | 121.051 | 15.7425 | 120.8679 | 120.9366 | 120.9549 | 121.019 | 120.9961 | -121.1014 | -121.1426 | 121.1334 | 120.9091 | 2.9663 | 21.5744
2707.0938 | 121.4081 | -23.7808 | 97.3251 | 0.0095369 | 6.9722 | 0.063467 | 0.094477 | -0.00079049 | 0.0041294 | 0.021127 | -0.0028687 | 0.06015 | -1.3519 | 0.14214 | -0.005409 | 0.036897 | 0.073251 | -20.7733 | 97.2061 | -23.7122 | 97.4213 | -21.3501 | -22.6913 | -20.6772 | -2.0645 | 97.1329 | -23.7442 | 97.2336 | -7.869 | 5.4611 | -13.559 | 0.068665 | -0.11902 | 0.096131 | 2.4307 | 3.1036 | 1.0895 | 3.035 | 1.0208 | 0.036621 | -0.19226 | -0.091552 | 15.9119 | 10.2219 | 29.2419 | 10.1852 | 29.2053 | 2.3621 | 121.1334 | 15.8752 | 120.9778 | 120.9183 | 120.8771 | 120.9869 | 120.9137 | -121.0373 | -121.0693 | 121.2021 | 121.0144 | 3.0075 | 21.7163
2708.8125 | 121.3257 | -23.5519 | 97.6135 | 0.017166 | 6.9733 | 0.066031 | 0.098749 | 0.00070491 | 0.0039158 | 0.022195 | 0.0093383 | 0.064849 | -1.3508 | 0.13958 | -0.0066906 | 0.038392 | 0.071329 | -20.5032 | 97.4854 | -23.5199 | 97.6547 | -21.1578 | -22.5128 | -20.4849 | -1.8311 | 97.4396 | -23.5519 | 97.4121 | -7.6675 | 5.658 | -13.353 | 0.032044 | -0.12817 | 0.041199 | 2.3941 | 3.067 | 1.0391 | 3.035 | 1.0071 | 0 | -0.17395 | -0.20142 | 15.8844 | 10.199 | 29.2099 | 10.199 | 29.2099 | 2.3621 | 121.1746 | 15.8844 | 120.9641 | 121.0052 | 120.9915 | 121.0373 | 120.9915 | -121.1334 | -121.1655 | 121.2067 | 120.9641 | 3.0487 | 21.7209
2710.5938 | 121.3577 | -23.2864 | 97.847 | 0.017166 | 6.9729 | 0.068167 | 0.097895 | -0.00079049 | 0.0034884 | 0.023691 | 0.0093383 | 0.062286 | -1.3508 | 0.13894 | -0.0041272 | 0.037538 | 0.070901 | -20.2972 | 97.7142 | -23.2132 | 97.9019 | -20.8969 | -22.2427 | -20.192 | -1.5793 | 97.6593 | -23.2864 | 97.6822 | -7.402 | 5.9418 | -13.06 | 0.073242 | -0.13275 | 0.054932 | 2.3895 | 3.0945 | 1.0437 | 3.0212 | 0.97046 | 0 | -0.18768 | -0.16479 | 15.8844 | 10.2264 | 29.2282 | 10.2264 | 29.2282 | 2.3163 | 121.1151 | 15.8844 | 120.9686 | 120.9274 | 120.9457 | 121.0007 | 120.9457 | -121.0602 | -121.1334 | 121.1884 | 120.9686 | 2.9892 | 21.7072
2712.375 | 121.4035 | -23.2452 | 97.8745 | -0.0057221 | 6.9735 | 0.068167 | 0.096186 | 6.4114e-05 | 0.0062656 | 0.021768 | -0.0089723 | 0.064849 | -1.3536 | 0.14428 | -0.00028199 | 0.039033 | 0.067697 | -20.2332 | 97.7463 | -23.1903 | 97.9568 | -20.842 | -22.2244 | -20.1782 | -1.4969 | 97.6639 | -23.2269 | 97.7692 | -7.37 | 5.9784 | -12.9547 | 0.054931 | -0.12817 | 0.082397 | 2.4033 | 3.067 | 1.0208 | 3.0121 | 0.96588 | 0.01831 | -0.21057 | -0.10529 | 15.8752 | 10.2905 | 29.2236 | 10.2722 | 29.2053 | 2.3483 | 121.1472 | 15.8569 | 120.9961 | 120.9366 | 120.8908 | 120.9915 | 120.9091 | -121.0648 | -121.1014 | 121.2021 | 121.0144 | 3.0121 | 21.7484
2714.0938 | 121.312 | -22.7783 | 98.4009 | 0.062942 | 6.9752 | 0.065604 | 0.098749 | 0.00070491 | 0.0066928 | 0.021127 | 0.015442 | 0.066558 | -1.351 | 0.14257 | -0.0069044 | 0.037965 | 0.073038 | -19.7159 | 98.2819 | -22.728 | 98.4329 | -20.3613 | -21.7072 | -19.6701 | -1.0941 | 98.2407 | -22.7417 | 98.1903 | -6.9763 | 6.4087 | -12.4969 | 0.050354 | -0.11902 | 0.032043 | 2.417 | 3.1082 | 1.0712 | 3.0579 | 1.0208 | 0.036621 | -0.16022 | -0.21057 | 15.802 | 10.2814 | 29.187 | 10.2448 | 29.1504 | 2.3666 | 121.1609 | 15.7654 | 120.932 | 121.0098 | 120.9824 | 121.0602 | 121.019 | -121.1288 | -121.1426 | 121.2112 | 120.9686 | 3.0624 | 21.6843
2715.875 | 121.3074 | -24.0234 | 97.1512 | -0.0057221 | 6.9752 | 0.064749 | 0.097681 | -0.0035675 | 0.0064792 | 0.019418 | 0.00018312 | 0.06549 | -1.3506 | 0.14107 | -0.0039136 | 0.03647 | 0.070261 | -20.961 | 97.0367 | -23.9639 | 97.2885 | -21.5195 | -22.9065 | -20.8603 | -2.3346 | 97.0139 | -23.9639 | 96.9269 | -8.2397 | 5.1453 | -13.797 | 0.059509 | -0.11444 | 0.13733 | 2.504 | 3.1631 | 1.1169 | 3.1036 | 1.0574 | 0.059509 | -0.13733 | -0.2243 | 15.7837 | 10.2264 | 29.1687 | 10.1669 | 29.1092 | 2.4445 | 121.2524 | 15.7242 | 120.8908 | 121.0007 | 120.9778 | 121.0602 | 121.0373 | -121.1151 | -121.1151 | 121.3119 | 120.9503 | 3.0624 | 21.6888
2717.6562 | 121.3806 | -22.7325 | 98.3871 | -0.020981 | 6.972 | 0.062613 | 0.094691 | 0.00027771 | 0.0024204 | 0.021768 | -0.0059205 | 0.060791 | -1.3523 | 0.14706 | -0.0075452 | 0.038179 | 0.07197 | -19.7021 | 98.2407 | -22.673 | 98.4833 | -20.2698 | -21.6522 | -19.6152 | -1.0574 | 98.1812 | -22.728 | 98.2498 | -6.9946 | 6.4545 | -12.4832 | 0.059509 | -0.14648 | 0.09613 | 2.4628 | 3.1174 | 1.0803 | 3.0579 | 1.0208 | 0.004578 | -0.20599 | -0.13733 | 15.7379 | 10.2493 | 29.187 | 10.2448 | 29.1824 | 2.4033 | 121.1563 | 15.7333 | 120.9778 | 120.9137 | 120.9091 | 120.9732 | 120.9137 | -121.0602 | -121.1151 | 121.2158 | 120.9824 | 3.0304 | 21.6751
2719.375 | 121.2936 | -21.8719 | 99.3942 | 0.08583 | 6.9739 | 0.066672 | 0.098322 | 0.0045501 | 0.004343 | 0.025186 | 0.027649 | 0.065918 | -1.3489 | 0.14364 | -0.0060498 | 0.037965 | 0.068124 | -18.8004 | 99.2981 | -21.8307 | 99.3484 | -19.4641 | -20.8237 | -18.7408 | -0.27466 | 99.1974 | -21.8674 | 99.0601 | -6.2347 | 7.2144 | -11.6318 | 0.041198 | -0.09613 | -0.045776 | 2.4078 | 3.1311 | 1.0483 | 3.0899 | 1.0071 | 0.004577 | -0.19684 | -0.33417 | 15.6372 | 10.2402 | 29.0863 | 10.2356 | 29.0817 | 2.3666 | 121.1792 | 15.6326 | 120.9274 | 121.1288 | 121.0648 | 121.17 | 121.0693 | -121.225 | -121.2616 | 121.2204 | 120.932 | 3.0716 | 21.5973
2721.1562 | 121.344 | -21.2402 | 99.9664 | 0.024795 | 6.9739 | 0.067313 | 0.09704 | -0.00036309 | 0.0056248 | 0.020486 | 0.0032349 | 0.066772 | -1.3527 | 0.13851 | -0.0043408 | 0.03882 | 0.071756 | -18.1549 | 99.852 | -21.1395 | 99.9985 | -18.782 | -20.1691 | -18.1137 | 0.37079 | 99.7925 | -21.199 | 99.7559 | -5.722 | 7.7866 | -10.9817 | 0.10071 | -0.11444 | 0.032043 | 2.4582 | 3.1265 | 1.0712 | 3.0258 | 0.97046 | 0.041198 | -0.17395 | -0.21057 | 15.5182 | 10.2585 | 29.0268 | 10.2173 | 28.9856 | 2.3575 | 121.138 | 15.477 | 120.9549 | 120.9915 | 120.9915 | 121.0922 | 121.0327 | -121.106 | -121.1655 | 121.2387 | 120.9961 | 3.0853 | 21.611
2722.9375 | 121.3394 | -21.0205 | 100.1862 | -0.020981 | 6.9718 | 0.067099 | 0.095545 | 6.4114e-05 | 0.0039158 | 0.019632 | -0.0028687 | 0.064636 | -1.3508 | 0.14342 | -0.0017774 | 0.037538 | 0.070047 | -18.0267 | 100.0763 | -20.9381 | 100.1266 | -18.663 | -20.05 | -17.9626 | 0.48981 | 99.9756 | -20.9793 | 99.9664 | -5.452 | 7.9971 | -10.7346 | 0.082398 | -0.10986 | -0.059509 | 2.3575 | 3.0579 | 0.97046 | 2.9755 | 0.88806 | 0.041199 | -0.21057 | -0.21973 | 15.5685 | 10.2859 | 29.0176 | 10.2448 | 28.9764 | 2.2751 | 121.0648 | 15.5273 | 120.9457 | 121.0144 | 120.9549 | 121.0968 | 120.9961 | -121.1243 | -121.1655 | 121.1472 | 120.9869 | 2.9938 | 21.5103
2724.6562 | 121.4172 | -21.904 | 99.2477 | -0.0057221 | 6.9707 | 0.067099 | 0.09405 | -0.0052765 | 0.0024204 | 0.021341 | -0.0028687 | 0.063781 | -1.3538 | 0.14941 | -0.0051954 | 0.036042 | 0.070261 | -18.9011 | 99.0875 | -21.8445 | 99.3484 | -19.3909 | -20.8054 | -18.7454 | -0.20142 | 99.0143 | -21.8674 | 99.147 | -6.1661 | 7.2784 | -11.5768 | 0.05951 | -0.16022 | 0.10071 | 2.5131 | 3.1586 | 1.0986 | 3.0991 | 1.0391 | 0.036621 | -0.23346 | -0.10071 | 15.7379 | 10.3271 | 29.1824 | 10.2905 | 29.1458 | 2.4536 | 121.1929 | 15.7013 | 121.0144 | 120.932 | 120.8817 | 120.9915 | 120.9183 | -121.0922 | -121.1151 | 121.2524 | 121.051 | 3.0029 | 21.7026
2726.4375 | 121.3715 | -18.8049 | 102.42 | 0.032425 | 6.972 | 0.06774 | 0.094691 | 0.00027771 | 0.0066928 | 0.021555 | 0.00018312 | 0.064849 | -1.3512 | 0.14642 | -0.0056226 | 0.037538 | 0.069406 | -15.834 | 102.2598 | -18.7363 | 102.4429 | -16.3284 | -17.6926 | -15.6235 | 2.8839 | 102.2324 | -18.75 | 102.2141 | -3.0167 | 10.4233 | -8.4091 | 0.068665 | -0.16022 | 0.022888 | 2.4765 | 3.1815 | 1.1124 | 3.1128 | 1.0437 | 0.054932 | -0.18768 | -0.20599 | 15.7883 | 10.3958 | 29.2282 | 10.3409 | 29.1733 | 2.4078 | 121.1792 | 15.7333 | 120.9641 | 120.9961 | 120.9824 | 121.0648 | 121.0373 | -121.1563 | -121.17 | 121.2479 | 121.019 | 2.9709 | 21.6888
2728.1562 | 121.376 | -17.4728 | 103.7109 | 0.047683 | 6.9735 | 0.06774 | 0.097681 | -0.0020721 | 0.0051974 | 0.021768 | 0.0062865 | 0.06549 | -1.3514 | 0.14599 | -0.0045544 | 0.03647 | 0.06727 | -14.5432 | 103.5965 | -17.4179 | 103.775 | -14.9963 | -16.3696 | -14.2685 | 3.8544 | 103.5461 | -17.4362 | 103.5233 | -2.1332 | 11.4441 | -7.1182 | 0.054931 | -0.11444 | 0.064087 | 2.4765 | 3.2043 | 1.1032 | 3.1494 | 1.0483 | 0.036621 | -0.16479 | -0.18768 | 15.3397 | 10.3546 | 28.9169 | 10.318 | 28.8803 | 2.4216 | 121.1929 | 15.303 | 120.9595 | 121.0144 | 120.9824 | 121.0693 | 121.019 | -121.1288 | -121.1472 | 121.2479 | 120.9961 | 2.9297 | 21.3272
2729.9375 | 121.4355 | -16.8365 | 104.3655 | -0.020981 | 6.9739 | 0.066031 | 0.095331 | 0.00070491 | 0.0058384 | 0.021982 | -0.0059205 | 0.067199 | -1.3512 | 0.14342 | -0.00049559 | 0.037324 | 0.070261 | -13.916 | 104.2236 | -16.7541 | 104.4159 | -14.36 | -15.7242 | -13.6414 | 4.5456 | 104.1367 | -16.777 | 104.2145 | -1.4374 | 12.1353 | -6.4224 | 0.082398 | -0.14191 | 0.050354 | 2.4765 | 3.1952 | 1.1124 | 3.1128 | 1.03 | 0.059509 | -0.22888 | -0.15106 | 15.3992 | 10.4141 | 28.9719 | 10.3546 | 28.9124 | 2.3941 | 121.17 | 15.3397 | 120.9915 | 120.9778 | 120.9137 | 121.0602 | 120.9732 | -121.1197 | -121.1426 | 121.2524 | 121.051 | 2.9205 | 21.3821
2731.6562 | 121.3531 | -16.6534 | 104.5761 | 0.024795 | 6.9735 | 0.066245 | 0.0964 | 0.0015595 | 0.0047702 | 0.022836 | 0.0032349 | 0.074463 | -1.3517 | 0.14257 | -0.0045544 | 0.03647 | 0.068552 | -13.7054 | 104.4571 | -16.5939 | 104.5898 | -14.1907 | -15.564 | -13.4628 | 4.8248 | 104.4296 | -16.626 | 104.3518 | -1.149 | 12.3779 | -6.2393 | 0.059509 | -0.11902 | 0.013733 | 2.4628 | 3.1906 | 1.0895 | 3.1311 | 1.03 | 0.027465 | -0.14648 | -0.2243 | 15.5045 | 10.4141 | 29.0314 | 10.3867 | 29.0039 | 2.4033 | 121.1838 | 15.477 | 120.9778 | 121.051 | 121.0556 | 121.1105 | 121.0831 | -121.17 | -121.2021 | 121.2433 | 121.0052 | 2.948 | 21.4783
2733.4219 | 121.3211 | -14.7446 | 106.5353 | 0.070572 | 6.9739 | 0.067313 | 0.098322 | 0.0049773 | 0.005411 | 0.024973 | 0.021545 | 0.069549 | -1.351 | 0.14663 | -0.008186 | 0.034974 | 0.066629 | -11.8469 | 106.4484 | -14.6942 | 106.4713 | -12.3001 | -13.6185 | -11.5173 | 6.395 | 106.3751 | -14.7308 | 106.2149 | 0.36621 | 14.0305 | -4.3716 | 0.050354 | -0.086975 | -0.064087 | 2.4445 | 3.2272 | 1.1261 | 3.1769 | 1.0757 | 0.013733 | -0.16022 | -0.32043 | 15.1108 | 10.3729 | 28.775 | 10.3592 | 28.7613 | 2.3941 | 121.1655 | 15.097 | 120.9457 | 121.1426 | 121.106 | 121.1929 | 121.1197 | -121.2296 | -121.2662 | 121.2158 | 120.9595 | 2.8976 | 21.1395
2735.125 | 121.344 | -10.8627 | 110.4309 | 0.0019074 | 6.9729 | 0.066031 | 0.098109 | -0.0012177 | 0.002634 | 0.020059 | -0.0028687 | 0.069976 | -1.3534 | 0.14086 | -0.0028454 | 0.039033 | 0.069192 | -11.6135 | 108.0826 | -12.8082 | 110.1974 | -8.5419 | -9.938 | -7.695 | 9.6359 | 110.17 | -10.6842 | 110.1288 | 3.6301 | 17.3584 | -0.76904 | -1.9455 | -2.3483 | -0.23346 | 2.3209 | 3.1677 | 0.92468 | 5.1132 | 2.8702 | 0.17853 | -0.26093 | -0.30212 | 14.4928 | 10.0937 | 28.2211 | 9.9152 | 28.0426 | 4.2664 | 123.0057 | 14.3143 | 120.813 | 120.8908 | 120.8542 | 118.9453 | 121.0327 | -123.2391 | -121.1151 | 121.0602 | 120.9915 | -0.75073 | 20.4987
2736.9062 | 121.3257 | -12.5931 | 108.7372 | 0.062942 | 6.9731 | 0.066458 | 0.097681 | -0.00014949 | 0.0047702 | 0.024545 | 0.021545 | 0.090057 | -1.3474 | 0.14107 | -0.007118 | 0.035402 | 0.065988 | -9.6771 | 108.6044 | -12.5336 | 108.6685 | -10.0983 | -11.4212 | -9.3109 | 9.8831 | 108.5541 | -12.5748 | 108.3755 | 3.9825 | 17.2852 | -1.8997 | 0.05951 | -0.13275 | -0.068665 | 2.4948 | 3.2822 | 1.1719 | 3.2227 | 1.1124 | 0.018311 | -0.18311 | -0.36163 | 16.5756 | 10.6934 | 29.8782 | 10.675 | 29.8599 | 2.4353 | 121.2021 | 16.5573 | 120.9503 | 121.138 | 121.1288 | 121.1975 | 121.1472 | -121.2708 | -121.312 | 121.2616 | 120.9686 | 2.916 | 22.4762
2738.6719 | 121.4218 | -11.3388 | 107.6431 | 0.0095369 | 6.9737 | 0.064749 | 0.095545 | -0.0039947 | 0.005411 | 0.021341 | 0.00018312 | 0.068908 | -1.3587 | 0.15411 | -0.0017774 | 0.037751 | 0.069192 | -13.3804 | 104.7089 | -16.3696 | 105.7892 | -13.0188 | -14.4653 | -11.9293 | 10.7071 | 109.726 | -11.3846 | 112.7609 | 5.3925 | 17.8665 | -2.005 | -5.0308 | -2.9343 | -1.8539 | -1.68 | -0.59051 | -3.1265 | 4.4403 | 1.9043 | -0.045777 | 2.0828 | 5.1178 | 16.7313 | 9.3338 | 29.2053 | 9.3796 | 29.2511 | 3.3508 | 122.1588 | 16.777 | 124.1455 | 121.0785 | 121.1105 | 116.0477 | 121.0648 | -124.0128 | -119.0277 | 117.128 | 124.0997 | -2.0416 | 22.0459
2740.375 | 121.3623 | -10.1028 | 111.1588 | 0.040054 | 6.9733 | 0.064963 | 0.096827 | 0.0036957 | 0.0017796 | 0.022409 | 0.0062865 | 0.069549 | -1.3574 | 0.14214 | -0.0056226 | 0.038179 | 0.06492 | -7.1457 | 111.1679 | -9.9197 | 111.2045 | -7.5531 | -8.8898 | -6.7566 | 10.3088 | 111.0031 | -10.0388 | 110.8978 | 4.1977 | 18.0954 | 0.20599 | 0.1831 | 0.009156 | 0.045777 | 2.5497 | 3.3463 | 1.2131 | 3.1631 | 1.03 | 0.064087 | -0.15564 | -0.26093 | 14.3005 | 10.3088 | 28.1982 | 10.2448 | 28.1342 | 2.3666 | 121.1243 | 14.2365 | 120.9366 | 121.0876 | 121.0419 | 121.2708 | 121.106 | -121.0785 | -121.1975 | 121.3074 | 121.0007 | 2.9572 | 20.4117
2742.1562 | 121.344 | -9.6634 | 111.6623 | 0.055313 | 6.9748 | 0.064963 | 0.099604 | 0.0039093 | 0.0058384 | 0.022195 | 0.015442 | 0.069336 | -1.354 | 0.14471 | -0.007118 | 0.037538 | 0.068124 | -6.8024 | 111.5387 | -9.5993 | 111.5845 | -7.1732 | -8.4686 | -6.3446 | 10.6293 | 111.4929 | -9.6359 | 111.3281 | 4.5868 | 18.4799 | 0.67749 | 0.064087 | -0.1236 | -0.077819 | 2.4902 | 3.3188 | 1.1948 | 3.2547 | 1.1307 | 0.027466 | -0.16937 | -0.33417 | 14.2502 | 10.3409 | 28.1433 | 10.3134 | 28.1158 | 2.4261 | 121.1838 | 14.2227 | 120.9641 | 121.138 | 121.1288 | 121.2021 | 121.1563 | -121.2616 | -121.2982 | 121.2479 | 120.9915 | 2.861 | 20.2927
2743.875 | 121.3898 | -9.4116 | 111.8958 | 0.062942 | 6.9724 | 0.069235 | 0.095972 | 0.0022003 | 0.0066928 | 0.025827 | 0.0093383 | 0.069763 | -1.3549 | 0.15026 | -0.0034864 | 0.037324 | 0.070261 | -6.5369 | 111.7493 | -9.3384 | 111.8912 | -6.8344 | -8.1894 | -6.0333 | 10.9772 | 111.6531 | -9.375 | 111.6074 | 4.866 | 18.782 | 0.97504 | 0.073242 | -0.14648 | -0.004578 | 2.5772 | 3.3783 | 1.2222 | 3.3051 | 1.149 | 0.036621 | -0.24262 | -0.28839 | 14.2776 | 10.3867 | 28.1937 | 10.35 | 28.157 | 2.504 | 121.2296 | 14.241 | 120.9824 | 121.0876 | 121.0281 | 121.1609 | 121.0648 | -121.2341 | -121.2708 | 121.3028 | 121.019 | 2.8748 | 20.3888
2745.6562 | 121.431 | -13.3301 | 107.8766 | 0.070572 | 6.9746 | 0.066885 | 0.098109 | 0.0034821 | 0.00712 | 0.021127 | 0.015442 | 0.069336 | -1.3523 | 0.15282 | -0.0034864 | 0.035615 | 0.06962 | -10.3592 | 107.8079 | -13.2935 | 107.9727 | -10.7941 | -12.1948 | -10.0479 | 7.4615 | 107.7164 | -13.3255 | 107.7026 | 1.3962 | 15.1749 | -2.8656 | 0.036621 | -0.068665 | 0.09613 | 2.536 | 3.2822 | 1.1353 | 3.2455 | 1.0986 | 0.004578 | -0.16022 | -0.17395 | 14.7263 | 10.4645 | 28.5049 | 10.4599 | 28.5004 | 2.4994 | 121.2662 | 14.7217 | 121.0281 | 121.1014 | 121.0419 | 121.138 | 121.0464 | -121.17 | -121.2021 | 121.3028 | 121.0327 | 2.9709 | 20.7916
2747.4375 | 121.4081 | -11.9888 | 109.2133 | 0.078201 | 6.9722 | 0.066672 | 0.098749 | 6.4114e-05 | 0.0073338 | 0.021555 | 0.024597 | 0.1095 | -1.3467 | 0.14941 | -0.004768 | 0.038179 | 0.075174 | -9.0958 | 109.1217 | -11.9476 | 109.2819 | -9.4299 | -10.8261 | -8.6884 | 11.4258 | 109.053 | -11.9888 | 109.021 | 5.4886 | 18.6172 | -1.03 | 0.041199 | -0.091553 | 0.068664 | 2.5589 | 3.3005 | 1.1627 | 3.2593 | 1.1215 | 0 | -0.16022 | -0.19226 | 17.4774 | 10.9589 | 30.6061 | 10.9589 | 30.6061 | 2.5177 | 121.2296 | 17.4774 | 121.0098 | 121.0693 | 121.0419 | 121.1105 | 121.0419 | -121.1609 | -121.2021 | 121.2708 | 121.0098 | 2.8931 | 23.4146
2749.1562 | 121.3257 | -10.9726 | 110.3806 | 0.0019074 | 6.9742 | 0.066672 | 0.097468 | 0.00049131 | 0.004343 | 0.022623 | -0.0028687 | 0.11505 | -1.3476 | 0.14257 | -0.0045544 | 0.039674 | 0.069406 | -8.075 | 110.1974 | -10.881 | 110.2753 | -8.4686 | -9.8419 | -7.7133 | 12.0346 | 110.17 | -10.9039 | 110.0189 | 6.1157 | 19.3222 | -0.086975 | 0.091553 | -0.1831 | -0.10529 | 2.504 | 3.2593 | 1.1307 | 3.1677 | 1.0391 | 0.068664 | -0.21057 | -0.36163 | 17.0883 | 10.8856 | 30.2948 | 10.817 | 30.2261 | 2.4124 | 121.1563 | 17.0197 | 120.9229 | 121.0785 | 121.0739 | 121.17 | 121.1426 | -121.2616 | -121.2845 | 121.2479 | 120.9915 | 2.8976 | 23.0072
2750.9219 | 121.3531 | -11.6318 | 109.6802 | -0.013352 | 6.9733 | 0.063681 | 0.097895 | 6.4114e-05 | 0.0017796 | 0.019846 | -0.0059205 | 0.11932 | -1.3453 | 0.1415 | -0.0034864 | 0.038179 | 0.075387 | -8.7662 | 109.5474 | -11.554 | 109.5612 | -9.2148 | -10.5743 | -8.4091 | 11.7462 | 109.4421 | -11.5952 | 109.3414 | 6.0562 | 18.9926 | -0.60425 | 0.07782 | -0.13275 | -0.11902 | 2.417 | 3.2227 | 1.0574 | 3.1448 | 0.97961 | 0.036621 | -0.23804 | -0.33875 | 17.688 | 11.0275 | 30.6244 | 10.9909 | 30.5878 | 2.3392 | 121.1151 | 17.6514 | 120.9366 | 121.1014 | 121.0373 | 121.1792 | 121.0739 | -121.2341 | -121.2753 | 121.1929 | 120.9732 | 2.8656 | 23.378
2752.6406 | 121.4767 | -9.1782 | 112.0377 | -0.013352 | 6.9746 | 0.064749 | 0.095118 | 0.00091851 | 0.0028476 | 0.021555 | -0.0028687 | 0.076599 | -1.3555 | 0.15261 | -0.007118 | 0.037324 | 0.068338 | -6.34 | 111.9232 | -9.082 | 111.9873 | -8.3221 | -10.5881 | -8.5281 | 10.7346 | 111.2686 | -9.9838 | 111.85 | 4.8523 | 18.6768 | 1.0208 | 0.096131 | -0.11444 | -0.050354 | 0.85602 | 0.65003 | -1.4099 | 0.55389 | -1.506 | -0.80566 | -0.76904 | -0.18768 | 14.0305 | 10.199 | 27.8549 | 11.0046 | 28.6606 | 0.75989 | 121.0693 | 14.8361 | 121.8338 | 121.0052 | 121.2524 | 121.1014 | 120.4468 | -121.1197 | -122.0215 | 121.1655 | 121.0281 | 2.8381 | 19.9127
2754.4219 | 121.4264 | -11.3937 | 109.8358 | 0.024795 | 6.9722 | 0.065176 | 0.095118 | -0.0010041 | 0.0041294 | 0.023264 | 0.00018312 | 0.11975 | -1.3457 | 0.14364 | -0.0024182 | 0.039888 | 0.073038 | -8.519 | 109.7076 | -11.3297 | 109.8495 | -8.8943 | -10.2585 | -8.1345 | 11.3663 | 109.6527 | -11.3709 | 109.6115 | 5.6076 | 18.7729 | -0.3067 | 0.064087 | -0.12817 | 0.013733 | 2.4994 | 3.2593 | 1.1353 | 3.1952 | 1.0712 | 0.022888 | -0.1831 | -0.2243 | 17.0013 | 11.087 | 30.1666 | 11.0641 | 30.1437 | 2.4353 | 121.1792 | 16.9785 | 120.9824 | 121.0373 | 121.0236 | 121.1014 | 121.0464 | -121.1655 | -121.2067 | 121.2433 | 121.0052 | 2.8748 | 22.76
2756.1406 | 121.4676 | -12.735 | 108.4534 | 0.078201 | 6.978 | 0.067954 | 0.098322 | 0.0022003 | 0.0069064 | 0.023477 | 0.024597 | 0.19943 | -1.3331 | 0.14321 | -0.0028454 | 0.04181 | 0.077951 | -9.7687 | 108.3481 | -12.7213 | 108.5907 | -10.1532 | -11.5952 | -9.4437 | 14.4424 | 108.3023 | -12.7304 | 108.2794 | 9.1049 | 20.874 | -0.94757 | 0.013733 | -0.10529 | 0.13733 | 2.5818 | 3.2913 | 1.1398 | 3.2776 | 1.1261 | 0.004577 | -0.15106 | -0.17395 | 21.8399 | 11.7874 | 33.609 | 11.7828 | 33.6044 | 2.5681 | 121.3119 | 21.8353 | 121.0098 | 121.0693 | 121.0327 | 121.0831 | 121.0373 | -121.1746 | -121.1838 | 121.3257 | 121.0144 | 2.9663 | 27.1774
2757.9375 | 121.3623 | -12.5885 | 108.6777 | -0.0057221 | 6.9724 | 0.064322 | 0.095331 | 0.0017731 | 0.0030612 | 0.020914 | -0.0028687 | 0.23724 | -1.332 | 0.13702 | -0.0066906 | 0.041169 | 0.080301 | -9.5856 | 108.5403 | -12.4558 | 108.7601 | -10.0067 | -11.3754 | -9.256 | 15.6738 | 108.4946 | -12.4924 | 108.3984 | 10.8215 | 21.9589 | -0.53558 | 0.13275 | -0.13733 | 0.082398 | 2.5818 | 3.3325 | 1.2131 | 3.1998 | 1.0803 | 0.09613 | -0.1831 | -0.27924 | 23.41 | 12.0529 | 34.5474 | 11.9568 | 34.4513 | 2.449 | 121.2158 | 23.3139 | 120.8908 | 120.9961 | 120.9869 | 121.1288 | 121.0831 | -121.1334 | -121.17 | 121.3486 | 120.9869 | 3.0029 | 28.2623
2759.6562 | 121.4447 | -12.5015 | 108.6731 | -0.0057221 | 6.9724 | 0.066672 | 0.099817 | 0.0049773 | 0.0056248 | 0.023904 | 0.024597 | 0.28253 | -1.3235 | 0.15838 | -0.0024182 | 0.043306 | 0.095895 | -9.5901 | 108.4808 | -12.4786 | 108.7692 | -9.9609 | -11.4029 | -9.256 | 16.7267 | 108.49 | -12.5427 | 108.5037 | 14.5889 | 22.7646 | 2.1561 | 0.022888 | -0.19226 | 0.09613 | 2.5406 | 3.2455 | 1.0986 | 3.2227 | 1.0757 | -0.041199 | -0.18311 | -0.16937 | 27.0905 | 14.6576 | 35.2661 | 14.6988 | 35.3073 | 2.5177 | 121.2479 | 27.1317 | 121.0464 | 120.9595 | 121.0327 | 120.9824 | 120.9915 | -121.1517 | -121.2158 | 121.2708 | 121.0052 | 2.9114 | 29.2282
2761.4219 | 121.4767 | -8.9676 | 111.7813 | 0.0095369 | 6.9718 | 0.064322 | 0.096186 | 0.00070491 | 0.0022068 | 0.021555 | -0.0028687 | 0.090057 | -1.3564 | 0.15966 | -0.010963 | 0.036042 | 0.071542 | -4.5822 | 112.3535 | -9.5993 | 106.6498 | -10.0204 | -8.725 | -6.5689 | 9.8419 | 111.1176 | -9.7687 | 112.793 | 4.6967 | 17.6468 | 1.1169 | -0.63171 | 0.5722 | -5.1315 | -1.0529 | 2.3987 | 0.24261 | 3.0304 | 0.87433 | -0.80109 | -0.66376 | 1.0117 | 13.6642 | 10.0845 | 26.6144 | 10.8856 | 27.4155 | -0.42114 | 116.2491 | 14.4653 | 122.5616 | 121.9528 | 120.8862 | 121.3211 | 120.0851 | -121.3806 | -121.55 | 115.6174 | 121.7606 | 4.3854 | 18.8095
2763.1875 | 121.3303 | -6.3171 | 115.1459 | -0.0057221 | 6.975 | 0.064963 | 0.095545 | -0.0010041 | 0.0037022 | 0.021555 | 0.00018312 | 0.10095 | -1.3534 | 0.15197 | -0.0069044 | 0.035615 | 0.074106 | -10.3088 | 108.1879 | -13.2019 | 108.1512 | -9.3109 | -7.695 | -3.7949 | 10.2127 | 111.6028 | -8.7936 | 114.7339 | 6.6101 | 19.8944 | 3.3096 | -6.8848 | -6.958 | -6.9946 | -2.9938 | 2.5223 | -1.3779 | 9.407 | 5.5069 | -2.4765 | -3.5431 | -0.41199 | 12.9272 | 9.6268 | 26.2115 | 12.1033 | 28.688 | 3.891 | 121.3531 | 15.4037 | 123.5275 | 121.3898 | 120.3964 | 114.505 | 117.9199 | -128.3478 | -123.9395 | 114.4684 | 121.051 | -3.9917 | 16.5298
2764.8906 | 121.5225 | -4.8614 | 113.3881 | -0.0057221 | 6.9727 | 0.067526 | 0.09704 | 0.0013459 | 0.0045566 | 0.0207 | 0.00018312 | 0.11526 | -1.3534 | 0.17376 | -0.00070919 | 0.038179 | 0.082864 | -6.4407 | 112.9303 | -7.7499 | 113.1317 | -5.4611 | -6.9397 | -4.9805 | 12.4878 | 112.6144 | -8.4229 | 121.4081 | 10.9909 | 21.4554 | 4.6326 | -2.8885 | -0.45776 | -0.25635 | -0.59967 | -0.11902 | -2.0782 | 2.7695 | 0.81024 | -3.5614 | -0.77362 | 8.02 | 15.8524 | 9.494 | 26.3168 | 13.0554 | 29.8782 | 2.2888 | 120.8817 | 19.4138 | 129.8309 | 120.6802 | 121.0373 | 117.7917 | 117.4759 | -121.138 | -121.8109 | 117.9932 | 126.2695 | -1.5793 | 17.3492
2766.6719 | 121.3806 | -18.1274 | 103.1525 | 0.047683 | 6.9733 | 0.067099 | 0.095972 | 0.0026275 | 0.0066928 | 0.023477 | 0.01239 | 0.35068 | -1.3171 | 0.18316 | -0.0034864 | 0.04181 | 0.10764 | -12.4924 | 105.2765 | -15.3534 | 101.4404 | -17.3996 | -18.7134 | -16.9006 | 10.8856 | 100.9323 | -19.606 | 102.42 | 12.2635 | 17.7383 | -1.5106 | 2.774 | 2.124 | -1.712 | 0.72784 | 1.2268 | -0.58594 | -1.5472 | -3.36 | -1.4786 | -2.2202 | -0.73242 | 30.3909 | 16.6168 | 35.8658 | 18.0954 | 37.3444 | -2.0462 | 116.7938 | 31.8695 | 122.0261 | 120.6299 | 120.5383 | 123.4039 | 119.0598 | -118.5059 | -122.7585 | 119.5679 | 120.5475 | 5.6351 | 29.0131
2768.4375 | 121.3028 | -15.5228 | 105.8624 | 0.0019074 | 6.9759 | 0.064749 | 0.097895 | 0.0028411 | 0.0039158 | 0.021768 | 0.00018312 | 0.31415 | -1.3322 | 0.17953 | -0.0045544 | 0.041169 | 0.10038 | -12.2269 | 105.8899 | -15.1566 | 105.6244 | -12.886 | -14.09 | -11.9339 | 11.4532 | 105.7343 | -15.271 | 105.3268 | 12.2314 | 18.3792 | 4.4449 | 0.36621 | 0.027466 | -0.23804 | 2.6367 | 3.5889 | 1.4328 | 3.2227 | 1.0666 | 0.25177 | -0.12817 | -0.53558 | 27.7542 | 19.9677 | 33.902 | 19.7159 | 33.6502 | 2.2705 | 120.7809 | 27.5024 | 120.5978 | 121.0464 | 121.0052 | 121.4127 | 121.257 | -121.019 | -121.1334 | 121.1472 | 120.8496 | 3.2959 | 26.976
2770.1562 | 121.3898 | -9.6039 | 111.5662 | 0.0019074 | 6.9722 | 0.066885 | 0.096613 | 0.0049773 | 0.0064792 | 0.024545 | 0.027649 | 0.21973 | -1.3495 | 0.17654 | -0.004768 | 0.041383 | 0.10487 | -6.0654 | 111.9507 | -8.8898 | 112.1338 | -7.2281 | -10.7025 | -8.7936 | 12.7441 | 111.1679 | -10.0983 | 111.5387 | 7.0679 | 20.2377 | -13.2843 | 0.71411 | 0.38452 | 0.56763 | 2.3758 | 0.81024 | -1.0986 | 0.096131 | -1.8127 | -0.49438 | -0.39825 | -0.027466 | 16.6718 | -3.6804 | 29.8416 | -3.186 | 30.336 | 1.6617 | 121.0236 | 17.1661 | 121.637 | 120.8405 | 121.2662 | 121.5546 | 120.7718 | -120.4559 | -121.6644 | 121.7377 | 121.1426 | 3.5385 | 22.348
2771.9375 | 121.4081 | -20.5765 | 100.5615 | 0.08583 | 6.9735 | 0.070303 | 0.099817 | 0.0019867 | 0.0049838 | 0.022836 | 0.027649 | 0.54935 | -1.3079 | 0.17013 | -0.004768 | 0.048005 | 0.10807 | -17.2897 | 100.4837 | -20.5444 | 100.7263 | -17.9764 | -19.487 | -17.4042 | 13.3072 | 100.3738 | -20.5765 | 100.3647 | 15.8661 | 18.5074 | -3.8406 | 0.032043 | -0.077819 | 0.1648 | 2.6001 | 3.1723 | 1.0895 | 3.1403 | 1.0574 | 0 | -0.18768 | -0.19684 | 36.4426 | 16.7358 | 39.0839 | 16.7358 | 39.0839 | 2.5681 | 121.2708 | 36.4426 | 120.9412 | 121.0281 | 120.9503 | 121.0602 | 120.9503 | -121.106 | -121.138 | 121.3028 | 120.9412 | 3.2867 | 33.8837
2773.6562 | 121.3394 | -25.4288 | 95.7504 | 0.032425 | 6.975 | 0.066458 | 0.098322 | 0.00091851 | 0.0049838 | 0.022409 | 0.0093383 | 0.70615 | -1.31 | 0.14834 | -0.0049818 | 0.047151 | 0.098032 | -21.698 | 95.9381 | -25.0854 | 95.9564 | -22.6868 | -24.1287 | -22.0642 | 7.9559 | 95.7184 | -25.2548 | 95.3659 | 10.4507 | 13.2477 | -10.4599 | 0.34332 | 0.18768 | 0.20599 | 2.742 | 3.3646 | 1.3 | 3.0212 | 0.95673 | 0.17395 | -0.032043 | -0.38452 | 35.8795 | 14.9689 | 38.6765 | 14.7949 | 38.5025 | 2.3987 | 121.0419 | 35.7056 | 120.6207 | 121.0236 | 120.9732 | 121.3669 | 121.1472 | -120.8359 | -121.0052 | 121.3852 | 120.7947 | 3.7308 | 33.3847
2775.4062 | 121.3898 | -29.6631 | 91.2323 | -0.013352 | 6.9729 | 0.064108 | 0.095331 | -0.0035675 | 0.0041294 | 0.021341 | -0.0028687 | 0.87598 | -1.31 | 0.23464 | -0.0039136 | 0.044801 | 0.16233 | -26.7609 | 90.9851 | -29.9286 | 91.0629 | -27.5162 | -29.1275 | -26.9531 | 3.1219 | 90.9485 | -29.8279 | 91.6168 | 6.7703 | 8.3084 | -6.3629 | -0.2655 | -0.24719 | -0.16937 | 2.1469 | 2.71 | 0.53558 | 2.9755 | 0.80109 | -0.1648 | -0.28381 | 0.38452 | 36.4334 | 23.3002 | 37.9715 | 23.465 | 38.1363 | 2.4124 | 120.9915 | 36.5982 | 121.4447 | 120.9137 | 120.7764 | 120.6482 | 120.6116 | -121.1609 | -121.0602 | 120.726 | 121.2799 | 2.9022 | 32.785
2777.1406 | 121.3303 | -36.026 | 84.9792 | -0.0057221 | 6.9724 | 0.066672 | 0.096613 | -0.00036309 | 0.0045566 | 0.021768 | -0.0028687 | 1.1105 | -1.304 | 0.22503 | -0.0026318 | 0.046724 | 0.17173 | -32.3318 | 84.8282 | -36.0306 | 85.0983 | -33.4167 | -35.0464 | -32.9636 | -1.149 | 84.7641 | -35.9756 | 84.8236 | 4.7974 | 3.9276 | -16.2598 | -0.004578 | -0.15106 | 0.11902 | 2.6093 | 3.0624 | 0.97961 | 3.067 | 0.98419 | 0.050354 | -0.21515 | -0.15564 | 40.8234 | 19.7662 | 39.9536 | 19.7159 | 39.9033 | 2.6138 | 121.1288 | 40.773 | 120.7993 | 120.8588 | 120.7397 | 120.8542 | 120.7901 | -121.0098 | -120.9549 | 121.1243 | 120.8496 | 3.6942 | 34.877
2778.9062 | 121.3531 | -34.8907 | 86.1099 | -0.0057221 | 6.9714 | 0.067099 | 0.096186 | 0.0017731 | 0.0024204 | 0.020059 | -0.0028687 | 0.67987 | -1.3151 | 0.28164 | -0.0039136 | 0.043519 | 0.22685 | -20.9473 | 96.6705 | -24.3851 | 98.1903 | -20.5124 | -21.8307 | -21.9131 | -2.3529 | 88.4537 | -33.3801 | 86.1511 | 2.4536 | 3.598 | -0.62256 | 10.5057 | 10.5606 | 12.0804 | 14.3784 | 12.9776 | 13.06 | 2.4719 | 2.5543 | 1.5106 | 2.3438 | 0.041199 | 37.3444 | 34.2682 | 38.4888 | 32.7576 | 36.9781 | 3.8727 | 122.5754 | 35.8337 | 119.5312 | 121.0556 | 121.8338 | 131.5613 | 123.3444 | -110.495 | -119.4901 | 133.0811 | 121.0419 | 13.9435 | 32.5378
2780.6719 | 121.2341 | -32.515 | 88.5635 | -0.0057221 | 6.9724 | 0.064108 | 0.095331 | -0.0031403 | 0.0024204 | 0.022623 | -0.0028687 | 0.61557 | -1.3104 | 0.44613 | -0.008827 | 0.042878 | 0.36591 | -28.6926 | 88.6322 | -32.1991 | 89.2273 | -29.306 | -30.8487 | -28.7567 | -0.13733 | 88.8702 | -31.9382 | 88.2431 | 8.7204 | 5.1178 | 25.9186 | 0.31586 | 0.068664 | 0.66376 | 3.2089 | 3.7582 | 1.6663 | 3.4424 | 1.3504 | 0.57678 | 0.3067 | -0.32043 | 41.2354 | 58.4335 | 37.6328 | 57.8568 | 37.056 | 2.8931 | 121.4264 | 40.6586 | 120.1813 | 120.8313 | 120.8084 | 121.1472 | 121.3852 | -120.7626 | -120.5017 | 121.7422 | 120.7581 | 3.8223 | 32.3776
2782.4375 | 121.1334 | -29.7913 | 91.3239 | 0.0019074 | 6.9752 | 0.063895 | 0.094691 | 6.4114e-05 | 0.0028476 | 0.023904 | 0.00018312 | 1.1404 | -1.2859 | 0.40298 | -0.010109 | 0.047151 | 0.35993 | -25.9094 | 91.5115 | -29.3793 | 91.2003 | -27.1042 | -28.4271 | -26.3123 | 8.9493 | 91.3376 | -29.48 | 90.7745 | 20.6497 | 13.2568 | 22.6547 | 0.41199 | 0.18768 | -0.1236 | 2.6871 | 3.479 | 1.3641 | 3.067 | 0.95215 | 0.31128 | 0.013732 | -0.54932 | 50.441 | 52.446 | 43.0481 | 52.1347 | 42.7368 | 2.2751 | 120.5795 | 50.1297 | 120.2545 | 120.8908 | 120.8176 | 121.3028 | 121.1288 | -120.7031 | -120.8038 | 120.9915 | 120.5658 | 3.8818 | 38.7405
2784.1562 | 121.2524 | -45.1538 | 75.769 | -0.0057221 | 6.9709 | 0.066885 | 0.095972 | -0.0018585 | 0.0051974 | 0.019846 | -0.0028687 | 1.4684 | -1.2936 | 0.16842 | -0.003059 | 0.048646 | 0.13136 | -41.1484 | 75.4578 | -45.3186 | 75.0732 | -43.1625 | -44.6411 | -42.3477 | -6.5643 | 75.3433 | -45.2454 | 75.5997 | 1.0162 | -2.1561 | -26.7746 | -0.16479 | -0.31128 | -0.6958 | 1.9913 | 2.8061 | 0.5127 | 2.9709 | 0.67749 | -0.091552 | -0.42572 | -0.16937 | 46.17 | 18.3792 | 42.9977 | 18.4708 | 43.0893 | 2.1561 | 120.3918 | 46.2616 | 120.845 | 120.7764 | 120.5887 | 120.6116 | 120.4971 | -121.0876 | -121.0144 | 120.2271 | 120.7535 | 4.0054 | 38.5895
2785.9375 | 121.1334 | -45.3873 | 75.531 | -0.0057221 | 6.9737 | 0.066672 | 0.097254 | 0.0028411 | 0.0066928 | 0.021127 | 0.00018312 | 1.4705 | -1.2936 | 0.16308 | -0.0060498 | 0.048219 | 0.11704 | -41.0568 | 75.5264 | -45.2545 | 75.5722 | -42.746 | -44.4397 | -42.3935 | -8.2397 | 75.3204 | -45.3506 | 75.2518 | -0.19684 | -3.5614 | -28.7201 | 0.13275 | -0.004578 | 0.041199 | 2.6413 | 2.9938 | 0.94757 | 2.861 | 0.81482 | 0.036621 | -0.21057 | -0.27924 | 45.1904 | 16.6672 | 41.8259 | 16.6306 | 41.7892 | 2.5085 | 120.8267 | 45.1538 | 120.6024 | 120.7809 | 120.6711 | 120.9137 | 120.7077 | -120.7855 | -120.8817 | 120.9595 | 120.639 | 4.3304 | 37.1475
2787.7188 | 120.8908 | -20.4941 | 102.0905 | 0.040054 | 6.9756 | 0.066245 | 0.094904 | -0.0020721 | 0.0034884 | 0.023477 | 0.0062865 | 0.67517 | -1.3241 | 0.57516 | -0.0062634 | 0.040315 | 0.35182 | -16.5756 | 100.6897 | -20.0867 | 99.1653 | -18.4113 | -19.3359 | -17.9398 | 4.6188 | 99.4949 | -21.5881 | 98.3322 | 13.1058 | 12.1445 | 31.4987 | 0.40741 | -1.4008 | -2.9251 | 2.0828 | 2.5543 | 1.1581 | 2.1469 | 0.75073 | -1.0941 | -2.5955 | -3.7582 | 33.5999 | 51.9928 | 32.6386 | 53.0869 | 33.7326 | 1.6754 | 119.252 | 34.6939 | 119.9203 | 120.7764 | 121.0831 | 121.1838 | 119.989 | -122.1771 | -123.6786 | 119.6594 | 118.8263 | 3.9185 | 25.1129
2789.4844 | 121.2067 | -13.5086 | 108.2565 | -0.013352 | 6.975 | 0.062827 | 0.092554 | -0.0014313 | 0.0049838 | 0.019632 | -0.0028687 | 0.2962 | -1.3416 | 0.60335 | -0.0073316 | 0.039033 | 0.26914 | -10.8353 | 105.5511 | -15.4175 | 107.5882 | -10.3317 | -12.7213 | -9.9289 | 10.1807 | 108.3939 | -12.3596 | 106.929 | 16.8411 | 17.8482 | 29.8462 | -1.9089 | -2.7054 | -0.66833 | 3.1769 | 3.5797 | 0.78735 | 5.4886 | 2.6962 | 1.149 | 0.13733 | -1.3275 | 30.3497 | 43.3548 | 31.3568 | 42.2058 | 30.2078 | 5.0858 | 123.0057 | 29.2007 | 119.2886 | 120.9686 | 120.7535 | 119.0598 | 121.9025 | -123.674 | -120.6161 | 121.0968 | 120.4376 | 2.6733 | 23.6893
2791.2031 | 121.1655 | -37.2757 | 83.7616 | 0.070572 | 6.9733 | 0.067313 | 0.095972 | 0.0066863 | 0.0045566 | 0.023264 | 0.030701 | 1.1496 | -1.2923 | 0.19833 | -0.0056226 | 0.047364 | 0.12901 | -33.5587 | 83.3862 | -37.4908 | 83.2352 | -35.1379 | -36.4243 | -34.2819 | -1.6022 | 83.0658 | -37.6877 | 83.4457 | 9.4025 | 4.3533 | -21.8445 | -0.21515 | -0.37537 | -0.52643 | 2.1378 | 2.9938 | 0.85144 | 3.2089 | 1.0666 | -0.41199 | -0.6958 | -0.31586 | 46.6782 | 15.4312 | 41.629 | 15.8432 | 42.041 | 2.3529 | 120.726 | 47.0901 | 121.1334 | 120.8771 | 120.7535 | 120.6619 | 120.3415 | -121.2524 | -121.4493 | 120.5109 | 120.7214 | 3.717 | 35.6735
2792.9844 | 121.1746 | -44.87 | 75.9384 | 0.078201 | 6.9729 | 0.069235 | 0.09704 | 0.00049131 | 0.0037022 | 0.021341 | 0.015442 | 1.4367 | -1.2814 | 0.19448 | -0.0058362 | 0.049501 | 0.13328 | -40.6311 | 75.8286 | -44.989 | 76.0254 | -42.2287 | -43.8904 | -41.8671 | -3.6072 | 75.7095 | -44.9707 | 75.705 | 7.0038 | 1.1536 | -26.0788 | -0.11902 | -0.10986 | 0.086975 | 2.6413 | 3.0029 | 0.97961 | 3.1219 | 1.0986 | -0.10071 | -0.22888 | -0.23346 | 51.8738 | 18.7912 | 46.0236 | 18.8919 | 46.1243 | 2.7603 | 121.0144 | 51.9745 | 120.6757 | 120.8176 | 120.6802 | 120.6985 | 120.5795 | -120.9274 | -120.9091 | 120.8954 | 120.575 | 4.2389 | 41.2628
2794.75 | 121.138 | -48.4955 | 72.2809 | 0.062942 | 6.9774 | 0.067313 | 0.0964 | 0.0043365 | 0.0045566 | 0.024759 | 0.018494 | 1.6111 | -1.2756 | 0.2152 | -0.0062634 | 0.053773 | 0.15614 | -44.3253 | 71.8506 | -48.9853 | 72.6105 | -45.488 | -47.2321 | -45.1767 | -3.8589 | 72.29 | -48.3398 | 72.0474 | 5.8273 | -0.09613 | -26.8066 | -0.48981 | -0.4303 | 0.32959 | 3.0075 | 3.3188 | 1.2634 | 3.8086 | 1.7532 | 0.15564 | 0.009155 | -0.23346 | 54.3228 | 21.6888 | 48.3994 | 21.5332 | 48.2437 | 3.4973 | 121.5958 | 54.1672 | 120.3873 | 120.8359 | 120.6299 | 120.3461 | 120.7855 | -121.2662 | -120.6207 | 121.106 | 120.5429 | 4.1702 | 44.6365
2796.5156 | 121.2112 | -110.1791 | 10.8124 | -0.0057221 | 6.975 | 0.066672 | 0.093195 | -0.0010041 | 0.0066928 | 0.022836 | -0.0059205 | 0.40921 | -1.253 | 0.16949 | -0.0066906 | 0.059755 | 0.25248 | -102.7954 | 10.6201 | -110.1288 | 10.8673 | -106.4255 | -108.7189 | -106.897 | -57.811 | 10.6293 | -110.3027 | 10.7574 | -52.2858 | -55.4214 | -72.5784 | 0.050354 | -0.19226 | 0.054932 | 3.7537 | 3.2822 | 1.4603 | 3.2318 | 1.4099 | -0.1236 | -0.18311 | -0.054932 | 57.8934 | 37.6007 | 54.7577 | 37.7243 | 54.8813 | 3.7033 | 120.9961 | 58.017 | 121.0602 | 120.7489 | 120.932 | 120.7993 | 120.8084 | -120.9412 | -121.1151 | 121.0464 | 120.9366 | 7.3837 | 52.3682
2798.25 | 121.1655 | -91.7084 | 29.3243 | 0.070572 | 6.9737 | 0.070944 | 0.098963 | -0.0022857 | 0.0056248 | 0.023477 | 0.021545 | 0.52371 | -1.2495 | 0.41537 | -0.0058362 | 0.055055 | 0.63465 | -85.0113 | 29.2374 | -91.626 | 29.4342 | -88.2019 | -90.2618 | -88.3667 | -43.3456 | 29.155 | -91.6901 | 29.2465 | -19.3771 | -40.0635 | 2.8748 | 0.082397 | -0.086975 | 0.10986 | 3.5065 | 3.3417 | 1.4465 | 3.2593 | 1.3641 | 0.018311 | -0.16937 | -0.07782 | 72.3312 | 94.5831 | 51.6449 | 94.5648 | 51.6266 | 3.4241 | 121.0602 | 72.3129 | 120.9366 | 120.8633 | 120.845 | 120.9457 | 120.8633 | -120.9503 | -121.0144 | 121.1426 | 120.9549 | 6.6971 | 48.3627
2800.0312 | 121.1517 | -89.7217 | 31.3293 | 0.055313 | 6.9748 | 0.069449 | 0.097681 | 0.0041229 | 0.0037022 | 0.026468 | 0.021545 | 0.44446 | -1.2495 | 0.54205 | -0.0049818 | 0.055268 | 0.67695 | -83.0841 | 31.2469 | -89.5981 | 31.398 | -86.261 | -88.3163 | -86.4166 | -41.4322 | 31.1508 | -89.7079 | 31.2012 | -19.2581 | -37.8983 | 11.6455 | 0.1236 | -0.082398 | 0.068664 | 3.4607 | 3.3051 | 1.4053 | 3.1815 | 1.2817 | 0.013733 | -0.17853 | -0.12817 | 70.4636 | 101.3672 | 51.8234 | 101.3535 | 51.8097 | 3.3371 | 120.9961 | 70.4498 | 120.9091 | 120.845 | 120.8588 | 120.9686 | 120.8725 | -120.9274 | -121.0373 | 121.1197 | 120.9229 | 6.6376 | 48.2895
2801.75 | 121.106 | -85.9085 | 35.1013 | 0.0019074 | 6.9709 | 0.066458 | 0.093836 | -0.0029267 | 0.0049838 | 0.019846 | -0.0028687 | 0.65488 | -1.2555 | 0.25152 | -0.005409 | 0.056337 | 0.60731 | -79.4128 | 34.964 | -85.7437 | 35.2203 | -82.4753 | -84.5306 | -82.6355 | -39.4547 | 34.9503 | -85.8673 | 35.0281 | -19.5465 | -35.3348 | 4.6875 | 0.16479 | -0.13733 | 0.11902 | 3.4332 | 3.273 | 1.3779 | 3.1082 | 1.2131 | 0.041198 | -0.15106 | -0.073242 | 66.362 | 90.596 | 50.5737 | 90.5548 | 50.5325 | 3.2684 | 120.9641 | 66.3208 | 120.8954 | 120.7077 | 120.8176 | 120.8725 | 120.8588 | -120.845 | -120.9686 | 121.1288 | 120.9366 | 6.4957 | 46.4539
2803.5156 | 121.138 | -98.6938 | 22.2336 | -0.013352 | 6.9729 | 0.066885 | 0.093195 | 6.4114e-05 | 0.0069064 | 0.02305 | -0.0028687 | 0.70529 | -1.2363 | 0.27566 | -0.0026318 | 0.058686 | 0.63893 | -91.7679 | 22.0001 | -98.735 | 22.2473 | -95.2698 | -97.467 | -95.5902 | -47.1313 | 22.0367 | -98.8083 | 22.142 | -26.4267 | -44.3115 | -2.0691 | -0.041198 | -0.23346 | 0.013732 | 3.4241 | 3.1036 | 1.2268 | 3.1448 | 1.268 | -0.11444 | -0.19684 | -0.091553 | 72.2672 | 96.6248 | 54.3823 | 96.7392 | 54.4968 | 3.4653 | 120.9824 | 72.3816 | 120.9503 | 120.7352 | 120.845 | 120.694 | 120.7306 | -120.9686 | -121.0419 | 120.9412 | 120.8359 | 6.926 | 51.5625
2805.2344 | 121.1609 | -98.1216 | 22.8287 | -0.0057221 | 6.9754 | 0.068808 | 0.098109 | 0.00049131 | 0.0081882 | 0.021127 | -0.0028687 | 0.74631 | -1.2327 | 0.23058 | -0.0037 | 0.056977 | 0.64085 | -91.0858 | 22.7371 | -98.053 | 22.9477 | -94.6152 | -96.8033 | -94.899 | -46.8704 | 22.6913 | -98.1171 | 22.7509 | -25.6989 | -44.3298 | -1.6342 | 0.068664 | -0.091552 | 0.11902 | 3.5065 | 3.2227 | 1.3184 | 3.154 | 1.2497 | 0.004578 | -0.13733 | -0.07782 | 72.4228 | 96.4874 | 53.7918 | 96.4828 | 53.7872 | 3.4378 | 121.0007 | 72.4182 | 120.8679 | 120.7901 | 120.8084 | 120.8588 | 120.813 | -120.8817 | -120.9457 | 121.0693 | 120.8725 | 7.0358 | 51.2512
2807.0156 | 121.2433 | -96.0114 | 24.9252 | 0.017166 | 6.9739 | 0.071372 | 0.092982 | -0.00057689 | 0.0051974 | 0.022836 | -0.0028687 | 0.74396 | -1.2361 | 0.24084 | -0.0041272 | 0.060823 | 0.64469 | -88.9938 | 24.7787 | -95.9381 | 25.1266 | -92.4637 | -94.6472 | -92.7017 | -45.3781 | 24.7879 | -95.9839 | 24.9252 | -23.1125 | -42.9337 | 2.2842 | 0.073243 | -0.14648 | 0.20142 | 3.5477 | 3.3096 | 1.3641 | 3.2364 | 1.2909 | 0.027466 | -0.13733 | 0 | 72.8989 | 98.2956 | 53.0777 | 98.2681 | 53.0502 | 3.4744 | 121.0648 | 72.8714 | 120.9091 | 120.7169 | 120.7718 | 120.7901 | 120.7993 | -120.8633 | -120.9091 | 121.138 | 120.9366 | 7.0175 | 50.6332
2808.7969 | 121.2524 | -99.9252 | 20.9427 | 0.055313 | 6.9786 | 0.070944 | 0.097468 | 0.0054047 | 0.0081882 | 0.022836 | 0.018494 | 0.38806 | -1.2261 | 0.66573 | -0.0011364 | 0.058473 | 0.69532 | -92.6331 | 20.8374 | -99.8932 | 21.2082 | -96.2357 | -98.5062 | -96.6476 | -47.5616 | 20.8008 | -99.971 | 20.9702 | -23.7488 | -45.8633 | 6.1066 | 0.032044 | -0.10529 | 0.2655 | 3.6896 | 3.2776 | 1.4191 | 3.2455 | 1.387 | -0.045776 | -0.14191 | 0.027466 | 76.1765 | 106.0318 | 54.0619 | 106.0776 | 54.1077 | 3.6575 | 121.1014 | 76.2222 | 120.9412 | 120.7306 | 120.7718 | 120.7626 | 120.726 | -120.8359 | -120.9137 | 121.1334 | 120.8954 | 7.2922 | 52.3636
2810.5625 | 121.1609 | -98.4558 | 22.5174 | -0.0057221 | 6.9733 | 0.069449 | 0.095545 | 0.0019867 | 0.006052 | 0.021555 | -0.0059205 | 0.31842 | -1.2305 | 0.7467 | -0.0032728 | 0.058686 | 0.71028 | -90.9348 | 22.7097 | -98.3185 | 22.4258 | -95.3568 | -97.4716 | -95.6451 | -45.1584 | 22.2061 | -96.9864 | 22.3068 | -20.4208 | -43.3548 | 10.4736 | 0.13733 | 0.19226 | -0.091553 | 3.0991 | 2.8107 | 0.98419 | 2.6733 | 0.84686 | 1.4694 | -0.31128 | -0.21057 | 78.035 | 108.9294 | 55.101 | 107.46 | 53.6316 | 2.9617 | 120.7443 | 76.5656 | 119.2932 | 121.0281 | 119.1925 | 121.1655 | 120.6619 | -120.8359 | -119.5038 | 120.8817 | 120.7626 | 7.5211 | 53.2974
2812.3438 | 121.2387 | -100.296 | 20.5627 | 0.0019074 | 6.9729 | 0.069449 | 0.096613 | 0.0015595 | 0.007761 | 0.020914 | -0.0028687 | 0.40408 | -1.0678 | 0.80416 | -0.001991 | 0.038179 | 0.70664 | -92.9718 | 20.4483 | -100.2823 | 20.6726 | -96.7392 | -98.9594 | -97.1008 | -58.4839 | 20.3476 | -100.3326 | 20.5902 | -23.4879 | -72.908 | 8.8715 | 0.013733 | -0.11444 | 0.10986 | 3.5568 | 3.1952 | 1.3367 | 3.1815 | 1.3229 | -0.036621 | -0.21515 | 0.027466 | 76.8082 | 109.1675 | 27.388 | 109.2041 | 27.4246 | 3.5431 | 120.9549 | 76.8448 | 120.9229 | 120.7306 | 120.6802 | 120.7443 | 120.6436 | -120.845 | -120.8954 | 120.9686 | 120.8862 | 7.3242 | 41.8121
2814.0625 | 121.1288 | -100.8545 | 20.0729 | -0.0057221 | 6.9742 | 0.066672 | 0.094691 | -0.00057689 | 0.0073338 | 0.0207 | -0.0028687 | 0.38336 | -1.0579 | 0.83321 | -0.0041272 | 0.037324 | 0.71369 | -93.4479 | 19.8807 | -100.8499 | 20.0409 | -97.3618 | -99.5911 | -97.728 | -58.6761 | 19.8395 | -100.882 | 19.9448 | -23.0713 | -73.2971 | 9.7275 | 0.004577 | -0.19226 | -0.032043 | 3.4927 | 3.1265 | 1.2634 | 3.1219 | 1.2589 | -0.027466 | -0.23346 | -0.12817 | 77.7832 | 110.582 | 27.5574 | 110.6094 | 27.5848 | 3.4882 | 120.8908 | 77.8107 | 120.8267 | 120.7306 | 120.7214 | 120.7352 | 120.694 | -120.9229 | -120.9549 | 120.8954 | 120.7993 | 7.4066 | 42.1783
2815.8438 | 121.1563 | -86.6501 | 34.2773 | 0.0019074 | 6.9739 | 0.066672 | 0.0917 | 0.0019867 | 0.006052 | 0.022836 | -0.0089723 | 0.3699 | -1.0716 | 0.81612 | -0.0075452 | 0.033906 | 0.7122 | -79.8889 | 33.9615 | -86.6638 | 34.3918 | -83.226 | -85.2951 | -83.4229 | -49.4293 | 33.9844 | -86.6089 | 34.2133 | -14.3417 | -62.1323 | 24.4675 | -0.013733 | -0.31586 | 0.11444 | 3.4241 | 3.2272 | 1.355 | 3.241 | 1.3687 | 0.041198 | -0.29297 | -0.064087 | 72.3083 | 111.1176 | 24.5178 | 111.0764 | 24.4766 | 3.4378 | 121.0556 | 72.2672 | 120.8221 | 120.6253 | 120.5933 | 120.6116 | 120.6345 | -120.9412 | -120.8862 | 121.0419 | 120.8633 | 6.7612 | 37.2208
2817.625 | 121.1334 | -93.3426 | 27.5757 | 0.0019074 | 6.9722 | 0.067954 | 0.094263 | 0.0019867 | 0.00712 | 0.019846 | -0.0059205 | 0.28616 | -1.2267 | 0.78643 | -0.0051954 | 0.060609 | 0.71305 | -86.0321 | 27.4933 | -93.2098 | 27.5848 | -89.9506 | -92.0975 | -90.2298 | -40.979 | 27.3697 | -93.3746 | 27.4429 | -16.5344 | -38.3514 | 18.1641 | 0.13275 | -0.082398 | 0.009155 | 3.392 | 3.1128 | 1.2451 | 2.98 | 1.1124 | -0.032044 | -0.20599 | -0.13275 | 76.8082 | 111.5067 | 54.9912 | 111.5387 | 55.0232 | 3.2593 | 120.7947 | 76.8402 | 120.8176 | 120.7031 | 120.7443 | 120.8359 | 120.7123 | -120.7855 | -120.9503 | 120.9274 | 120.7855 | 7.3105 | 52.3636
2819.3281 | 121.1014 | -90.4266 | 30.5374 | 0.0019074 | 6.9752 | 0.068167 | 0.092127 | 0.00027771 | 0.0066928 | 0.0207 | -0.0028687 | 0.26715 | -1.2316 | 0.79732 | -0.006477 | 0.057618 | 0.70899 | -83.3405 | 30.3772 | -90.3442 | 30.5923 | -86.9751 | -89.1266 | -87.2681 | -39.4547 | 30.3223 | -90.4083 | 30.3864 | -16.5665 | -36.9507 | 21.2128 | 0.082398 | -0.16022 | 0.054931 | 3.4515 | 3.1586 | 1.3 | 3.0762 | 1.2177 | 0.018311 | -0.21515 | -0.15106 | 73.8602 | 111.6394 | 53.476 | 111.6211 | 53.4576 | 3.3691 | 120.9366 | 73.8419 | 120.7947 | 120.7214 | 120.7306 | 120.8038 | 120.7489 | -120.8817 | -120.9457 | 121.019 | 120.813 | 7.0862 | 50.972
2821.1094 | 121.2112 | -88.8748 | 32.0114 | 0.0019074 | 6.9722 | 0.067313 | 0.090845 | -0.0018585 | 0.0041294 | 0.021768 | -0.0059205 | 0.37161 | -1.0494 | 0.84774 | -0.006477 | 0.032624 | 0.70387 | -81.9534 | 31.7871 | -88.8794 | 32.0709 | -85.4645 | -87.5656 | -85.6888 | -50.148 | 31.7825 | -88.8336 | 31.9885 | -14.5432 | -63.3453 | 22.7875 | -0.004578 | -0.22431 | 0.059509 | 3.4103 | 3.186 | 1.3092 | 3.1906 | 1.3138 | 0.041199 | -0.22888 | -0.022889 | 74.3317 | 111.6623 | 25.5295 | 111.6211 | 25.4883 | 3.4149 | 120.9503 | 74.2905 | 120.8221 | 120.6665 | 120.6162 | 120.6619 | 120.6573 | -120.8908 | -120.845 | 120.9457 | 120.8633 | 6.9214 | 38.7268
2822.9062 | 121.2387 | -101.1566 | 19.6747 | 0.0019074 | 6.9722 | 0.068808 | 0.0917 | 6.4114e-05 | 0.0039158 | 0.021127 | -0.0059205 | 0.49893 | -1.0022 | 0.79092 | -0.0028454 | 0.036042 | 0.70686 | -93.5577 | 19.4321 | -101.1749 | 19.7617 | -97.5952 | -99.8291 | -98.0026 | -57.4951 | 19.4138 | -101.2253 | 19.6381 | -20.0226 | -72.4869 | 10.7529 | -0.018311 | -0.24262 | 0.086975 | 3.5614 | 3.154 | 1.3275 | 3.1723 | 1.3458 | -0.068665 | -0.26093 | -0.036621 | 81.134 | 111.9095 | 28.6697 | 111.9781 | 28.7384 | 3.5797 | 120.9366 | 81.2027 | 120.8633 | 120.607 | 120.639 | 120.5887 | 120.5704 | -120.8496 | -120.9 | 120.9183 | 120.7947 | 7.5989 | 43.6615
2824.6719 | 121.106 | -103.2028 | 17.6697 | -0.0057221 | 6.9752 | 0.069235 | 0.090632 | -0.0012177 | 0.0056248 | 0.02305 | -0.0059205 | 0.53397 | -0.94001 | 0.81911 | -0.0083996 | 0.037324 | 0.69938 | -95.3751 | 17.4774 | -103.1387 | 17.7246 | -99.5819 | -101.825 | -100.0259 | -58.4335 | 17.4637 | -103.2486 | 17.5232 | -20.0409 | -73.8693 | 8.2352 | 0.064087 | -0.19226 | 0.054931 | 3.6209 | 3.1769 | 1.3779 | 3.1128 | 1.3138 | -0.045776 | -0.20599 | -0.14649 | 83.1619 | 111.438 | 29.3335 | 111.4838 | 29.3793 | 3.5568 | 120.8633 | 83.2077 | 120.7718 | 120.6162 | 120.7123 | 120.6802 | 120.6665 | -120.8084 | -120.9183 | 120.9274 | 120.726 | 7.8278 | 44.7693
2826.3906 | 121.138 | -98.1995 | 22.6959 | 0.070572 | 6.9756 | 0.070944 | 0.096827 | 0.00091851 | 0.0049838 | 0.023477 | 0.033752 | 0.50726 | -0.97504 | 0.82787 | -0.008186 | 0.037751 | 0.6966 | -90.509 | 22.6364 | -98.1262 | 22.9294 | -94.6609 | -96.817 | -94.8807 | -54.9774 | 22.5677 | -98.1903 | 22.6044 | -15.8386 | -69.8685 | 13.7466 | 0.073242 | -0.059509 | 0.23346 | 3.5385 | 3.3188 | 1.3824 | 3.2455 | 1.3092 | 0.009155 | -0.12817 | -0.091553 | 82.3608 | 111.9461 | 28.331 | 111.937 | 28.3218 | 3.4653 | 121.0556 | 82.3517 | 120.7947 | 120.7626 | 120.7581 | 120.8359 | 120.7672 | -120.8221 | -120.8862 | 121.1288 | 120.8038 | 7.6904 | 43.222
2828.1719 | 121.1609 | -102.7405 | 18.1 | 0.017166 | 6.9739 | 0.067954 | 0.092768 | -0.00079049 | 0.005411 | 0.022623 | 0.00018312 | 0.55511 | -0.84068 | 0.90307 | -0.004768 | 0.037751 | 0.69169 | -94.8303 | 17.9398 | -102.681 | 18.2098 | -99.0463 | -101.326 | -99.4949 | -57.9208 | 17.9352 | -102.7176 | 18.0679 | -18.0405 | -73.2925 | 8.2031 | 0.05951 | -0.16022 | 0.10986 | 3.6942 | 3.2455 | 1.4145 | 3.186 | 1.355 | 0.022889 | -0.1648 | -0.032044 | 84.7 | 110.9436 | 29.4479 | 110.9207 | 29.425 | 3.6346 | 120.8908 | 84.6771 | 120.7855 | 120.6207 | 120.6528 | 120.6802 | 120.6757 | -120.7809 | -120.8176 | 120.9503 | 120.8084 | 7.9102 | 44.8196
2829.9531 | 121.225 | -101.1154 | 19.6701 | -0.0057221 | 6.9744 | 0.066672 | 0.092768 | -0.0031403 | 0.0051974 | 0.021341 | -0.0059205 | 0.6521 | -0.71464 | 0.93191 | -0.005409 | 0.052491 | 0.67268 | -93.4113 | 19.3771 | -101.1978 | 19.7617 | -97.5723 | -99.8062 | -97.8607 | -50.2213 | 19.3451 | -101.1063 | 19.5786 | -17.4042 | -54.7348 | 7.6996 | -0.082398 | -0.29297 | 0.091553 | 3.5431 | 3.2547 | 1.3092 | 3.3371 | 1.3916 | 0.009155 | -0.32501 | -0.091553 | 83.7112 | 108.815 | 46.3806 | 108.8058 | 46.3715 | 3.6255 | 120.9595 | 83.7021 | 120.6848 | 120.575 | 120.4514 | 120.4926 | 120.4605 | -120.8679 | -120.7764 | 120.8771 | 120.694 | 7.7042 | 50.8942
2831.6719 | 121.1517 | -100.3601 | 20.3979 | 0.10109 | 6.9765 | 0.071372 | 0.094263 | 0.00091851 | 0.010324 | 0.026041 | 0.018494 | 0.62027 | -0.93082 | 0.75289 | -0.0011364 | 0.053773 | 0.68806 | -92.4957 | 20.2469 | -100.4105 | 20.5536 | -96.7575 | -99.0097 | -97.2107 | -47.9507 | 20.1874 | -100.47 | 20.3476 | -15.5228 | -50.9949 | 11.911 | -0.050354 | -0.15106 | 0.15564 | 3.6026 | 3.1494 | 1.3504 | 3.1998 | 1.4008 | -0.10986 | -0.21057 | -0.050354 | 84.8373 | 112.2711 | 49.3652 | 112.381 | 49.4751 | 3.653 | 120.9641 | 84.9472 | 120.8176 | 120.6573 | 120.6573 | 120.607 | 120.5475 | -120.8084 | -120.8679 | 120.9137 | 120.7077 | 7.8644 | 52.4094
2833.4375 | 121.1609 | -100.3098 | 20.4758 | -0.013352 | 6.9701 | 0.066458 | 0.090845 | -0.0020721 | 0.0037022 | 0.021341 | -0.0028687 | 0.68158 | -0.87485 | 0.75738 | -0.0051954 | 0.038179 | 0.68699 | -92.4316 | 20.2789 | -100.3143 | 20.6726 | -96.698 | -98.9502 | -97.1329 | -54.895 | 20.2469 | -100.3189 | 20.4529 | -16.6534 | -70.2759 | 11.4395 | -0.004578 | -0.19684 | 0.19684 | 3.6118 | 3.1769 | 1.3596 | 3.1815 | 1.3641 | -0.009156 | -0.22888 | -0.022888 | 83.6563 | 111.7493 | 30.0339 | 111.7584 | 30.043 | 3.6163 | 120.9869 | 83.6655 | 120.7718 | 120.5933 | 120.5658 | 120.5887 | 120.5566 | -120.7901 | -120.7947 | 120.9824 | 120.7626 | 7.8781 | 45.4147
2835.1562 | 121.1472 | -98.5062 | 22.2977 | -0.0057221 | 6.9701 | 0.06774 | 0.089564 | -0.00036309 | 0.0037022 | 0.022623 | -0.0059205 | 0.84415 | -0.70182 | 0.74776 | -0.0060498 | 0.054414 | 0.684 | -90.6189 | 22.0825 | -98.4283 | 22.4945 | -94.8212 | -97.0688 | -95.2881 | -45.0943 | 22.1146 | -98.3963 | 22.2656 | -16.0217 | -48.7335 | 13.1973 | 0.07782 | -0.21515 | 0.19684 | 3.685 | 3.2181 | 1.4374 | 3.1403 | 1.3596 | 0.10986 | -0.18311 | -0.032043 | 82.4844 | 111.7035 | 49.7726 | 111.5936 | 49.6628 | 3.6072 | 120.9229 | 82.3746 | 120.6619 | 120.5109 | 120.5109 | 120.5887 | 120.6207 | -120.726 | -120.694 | 121.0007 | 120.7718 | 7.8873 | 53.4119
2836.9219 | 120.9595 | -29.4754 | 91.42 | 0.0019074 | 6.9699 | 0.064322 | 0.08935 | 0.0017731 | 0.002634 | 0.0207 | -0.0028687 | 0.019989 | -1.4542 | 0.00051063 | -0.0096814 | 0.013826 | 0.0021149 | -25.5798 | 90.9851 | -29.5166 | 91.3651 | -27.1362 | -28.6011 | -26.5594 | -0.068665 | 0.036621 | -0.004578 | 0.082397 | 0.068665 | 0.027466 | 0.15106 | -0.041199 | -0.43488 | -0.054932 | 2.3392 | 2.916 | 0.87433 | 2.9572 | 0.91553 | 29.4708 | -91.3834 | -91.3376 | 29.5441 | 29.6265 | 29.5029 | 0.15564 | 0.032044 | 2.3804 | 120.8817 | 0.073243 | 0.086975 | 120.5017 | 0.041199 | 120.4605 | 29.512 | -120.9366 | -91.4246 | 120.8405 | 29.5578 | 3.8956 | 29.4067
2838.7188 | 121.1609 | -5.4291 | 115.654 | -0.0057221 | 6.9744 | 0.062399 | 0.092554 | -0.0014313 | 0.0024204 | 0.014505 | -0.0059205 | 0.021057 | -1.4538 | -0.00483 | -0.0079724 | 0.01233 | 0.0025421 | -2.417 | 115.3931 | -5.365 | 115.6586 | -3.0396 | -4.2618 | -2.2156 | 0.46692 | 0.4303 | 0.40741 | 0.54016 | 0.52185 | 0.48981 | 0.59967 | 0.064087 | -0.26093 | 0.004577 | 2.3895 | 3.2135 | 1.1673 | 3.1494 | 1.1032 | 5.8365 | -115.2237 | -115.1138 | 5.9509 | 6.0287 | 5.9189 | 0.19226 | 0.082397 | 2.3254 | 121.0236 | 0.11444 | 0.13275 | 120.7581 | 0.022888 | 120.8221 | 5.8594 | -121.019 | -115.2466 | 121.0876 | 5.9692 | 3.0121 | 5.896
2840.4219 | 121.1884 | -5.3513 | 115.7639 | -0.013352 | 6.9756 | 0.064108 | 0.091486 | -0.0035675 | 0.0019932 | 0.019846 | -0.0028687 | 0.022766 | -1.4512 | -0.0052572 | -0.0062634 | 0.011903 | 0.0031829 | -2.3117 | 115.5807 | -5.2185 | 115.8371 | -2.948 | -4.1473 | -2.0874 | 0.3891 | 0.40741 | 0.38452 | 0.5127 | 0.48981 | 0.40283 | 0.55389 | 0.13275 | -0.18311 | 0.073242 | 2.4033 | 3.2639 | 1.2039 | 3.1311 | 1.0712 | 5.7358 | -115.3564 | -115.2512 | 5.8411 | 5.9052 | 5.7541 | 0.16937 | 0.018311 | 2.2705 | 121.0556 | 0.10529 | 0.12817 | 120.7993 | 0.022889 | 120.932 | 5.7587 | -120.9824 | -115.3793 | 121.1884 | 5.864 | 3.0396 | 5.7404
2842.2188 | 121.1563 | -5.1132 | 116.0934 | -0.013352 | 6.9735 | 0.064322 | 0.094263 | -0.0042083 | 0.00049776 | 0.01835 | -0.0028687 | 0.021911 | -1.4523 | -0.00077117 | -0.0090406 | 0.012971 | 0.00083309 | -2.0874 | 115.86 | -4.9896 | 116.0522 | -2.7786 | -3.9597 | -1.9089 | 0.33875 | 0.46692 | 0.40283 | 0.44861 | 0.42572 | 0.3479 | 0.53558 | 0.1236 | -0.23346 | -0.041199 | 2.3346 | 3.2043 | 1.1536 | 3.0807 | 1.03 | 5.5161 | -115.6265 | -115.6448 | 5.5389 | 5.6488 | 5.4611 | 0.13275 | -0.054932 | 2.211 | 121.0419 | 0.022888 | 0.045776 | 120.8496 | 0.064087 | 120.9732 | 5.5801 | -121.0831 | -115.6906 | 121.1655 | 5.5618 | 3.0258 | 5.452
2844 | 121.1609 | -5.0858 | 116.1255 | -0.0057221 | 6.9737 | 0.064749 | 0.097254 | -0.0012177 | 0.002634 | 0.017496 | -0.0089723 | 0.024047 | -1.4527 | 0.004783 | -0.0041272 | 0.01468 | 0.0025421 | -2.0966 | 115.9653 | -4.9942 | 116.0065 | -2.8793 | -4.0695 | -2.0004 | 0.31586 | 0.57678 | 0.46234 | 0.52643 | 0.4303 | 0.37079 | 0.59967 | 0.091552 | -0.16022 | -0.11902 | 2.2064 | 3.0853 | 1.0162 | 2.9938 | 0.92468 | 5.5481 | -115.5487 | -115.5991 | 5.5161 | 5.6854 | 5.4565 | 0.13733 | -0.091552 | 2.1149 | 121.0007 | -0.032043 | 0.064087 | 120.9595 | 0.11444 | 121.051 | 5.6625 | -121.1197 | -115.6631 | 121.0922 | 5.6122 | 2.9892 | 5.4016
2845.7188 | 121.3348 | -5.1132 | 116.0339 | 0.0019074 | 6.9709 | 0.064536 | 0.093409 | -0.0035675 | 0.0015658 | 0.017069 | -0.0059205 | 0.018707 | -1.4544 | 0.0052102 | -0.0062634 | 0.01233 | 0.0083099 | -2.1103 | 115.8371 | -5.0354 | 116.0889 | -2.7512 | -3.9642 | -1.9455 | 0.46234 | 0.4715 | 0.46692 | 0.56763 | 0.54932 | 0.50354 | 0.62714 | 0.07782 | -0.19684 | 0.054931 | 2.3621 | 3.1677 | 1.149 | 3.0899 | 1.0712 | 5.5801 | -115.5624 | -115.4663 | 5.6625 | 5.7404 | 5.6168 | 0.16022 | 0.036621 | 2.2842 | 121.1243 | 0.082397 | 0.10071 | 120.8725 | 0.004578 | 120.9503 | 5.5847 | -121.0693 | -115.567 | 121.2021 | 5.6808 | 3.0029 | 5.5756
2847.4844 | 121.2616 | -4.834 | 116.3727 | -0.013352 | 6.9746 | 0.065604 | 0.096186 | -0.0029267 | 0.005411 | 0.01835 | -0.0059205 | 0.019561 | -1.4499 | -0.0018394 | -0.0017774 | 0.013185 | 0.0023285 | -1.8768 | 116.2674 | -4.7699 | 116.2903 | -2.5955 | -3.8223 | -1.7487 | 0.37537 | 0.59509 | 0.52643 | 0.62714 | 0.52185 | 0.45319 | 0.67291 | 0.064087 | -0.10529 | -0.082398 | 2.2385 | 3.0853 | 1.0117 | 3.0212 | 0.94757 | 5.3604 | -115.7776 | -115.7455 | 5.3558 | 5.5069 | 5.2872 | 0.14648 | -0.073242 | 2.1744 | 121.0602 | -0.004577 | 0.10071 | 121.0373 | 0.068665 | 121.1014 | 5.4291 | -121.1426 | -115.8463 | 121.1243 | 5.4611 | 2.9572 | 5.2093
2849.2031 | 121.2982 | -4.8569 | 116.3132 | -0.013352 | 6.9748 | 0.067526 | 0.095331 | -0.0042083 | 0.0037022 | 0.017282 | -0.0059205 | 0.019775 | -1.4516 | 0.006492 | -0.0032728 | 0.013185 | 0.0044647 | -1.8585 | 116.1713 | -4.7791 | 116.3315 | -2.5589 | -3.7903 | -1.7349 | 0.3891 | 0.45776 | 0.45776 | 0.53101 | 0.4715 | 0.42114 | 0.58594 | 0.07782 | -0.14191 | 0.018311 | 2.298 | 3.1219 | 1.0666 | 3.0441 | 0.98877 | 5.3146 | -115.8554 | -115.7822 | 5.3284 | 5.4428 | 5.278 | 0.12817 | -0.036621 | 2.2202 | 121.1105 | 0.013733 | 0.073242 | 120.9503 | 0 | 121.0281 | 5.3146 | -121.0922 | -115.8554 | 121.1884 | 5.3879 | 2.9984 | 5.246
2850.9844 | 121.2708 | -4.6051 | 116.6428 | -0.0057221 | 6.9748 | 0.066245 | 0.095118 | -0.0027131 | 0.0039158 | 0.020486 | -0.0059205 | 0.023407 | -1.4521 | 0.0035012 | -0.0056226 | 0.012758 | 0.0019013 | -1.593 | 116.5283 | -4.5136 | 116.5924 | -2.3529 | -3.5202 | -1.474 | 0.32959 | 0.50354 | 0.43488 | 0.49439 | 0.43945 | 0.37994 | 0.54932 | 0.091553 | -0.11444 | -0.050354 | 2.2522 | 3.1311 | 1.0849 | 3.0396 | 0.99335 | 5.04 | -116.1392 | -116.1484 | 5.0446 | 5.1544 | 4.985 | 0.11444 | -0.054931 | 2.1606 | 121.106 | 0.004578 | 0.05951 | 121.0419 | 0.068665 | 121.1334 | 5.1086 | -121.1563 | -116.2079 | 121.1975 | 5.0995 | 3.0121 | 4.9347
2852.7812 | 121.3165 | -4.6875 | 116.5649 | -0.0057221 | 6.9714 | 0.064322 | 0.095759 | -0.0020721 | 0.0024204 | 0.017709 | -0.0028687 | 0.018707 | -1.4533 | 0.0039286 | -0.004768 | 0.012544 | 0.0014741 | -1.7258 | 116.3956 | -4.5776 | 116.5146 | -2.4353 | -3.6118 | -1.5656 | 0.31128 | 0.4303 | 0.43488 | 0.48523 | 0.41657 | 0.37994 | 0.53558 | 0.10986 | -0.16937 | -0.050354 | 2.2522 | 3.1219 | 1.0757 | 3.0121 | 0.96588 | 5.1224 | -116.1346 | -116.0797 | 5.1041 | 5.2231 | 5.0674 | 0.10071 | -0.054931 | 2.1423 | 121.0922 | -0.01831 | 0.050354 | 120.9732 | -0.004577 | 121.0831 | 5.1178 | -121.1426 | -116.1301 | 121.2021 | 5.1727 | 2.9617 | 4.9988
2854.5625 | 121.3715 | -5.04 | 116.1896 | 0.0019074 | 6.9746 | 0.065604 | 0.094477 | -0.0024995 | 0.0034884 | 0.01835 | 0.00018312 | 0.019989 | -1.451 | 0.0071328 | -0.0058362 | 0.01233 | -0.0025849 | -2.2842 | 115.7318 | -5.2414 | 116.0706 | -2.8519 | -4.0283 | -1.9409 | 0.41199 | 0.43488 | 0.44403 | 0.5722 | 0.46234 | 0.43945 | 0.58594 | -0.20142 | -0.45776 | -0.11902 | 2.1881 | 3.0991 | 1.0117 | 3.3005 | 1.2131 | 5.484 | -115.7547 | -115.6174 | 5.5023 | 5.6259 | 5.4794 | 0.14191 | -0.004578 | 2.3895 | 121.312 | 0.01831 | 0.12817 | 120.9732 | -0.009156 | 120.7718 | 5.4749 | -121.431 | -115.7455 | 121.1105 | 5.6122 | 2.7557 | 5.452
2856.3438 | 121.3028 | -4.7607 | 116.5283 | -0.013352 | 6.9727 | 0.064322 | 0.091486 | -0.0035675 | 0.0015658 | 0.01835 | -0.0059205 | 0.02127 | -1.4529 | -0.00077117 | -0.0060498 | 0.011476 | 0.00061949 | -1.7487 | 116.3315 | -4.66 | 116.4963 | -2.4857 | -3.6255 | -1.6067 | 0.36163 | 0.50354 | 0.44861 | 0.50354 | 0.42114 | 0.41657 | 0.56305 | 0.10071 | -0.19684 | -0.032043 | 2.2751 | 3.154 | 1.1353 | 3.0533 | 1.0345 | 5.2093 | -116.0248 | -116.0248 | 5.1819 | 5.3238 | 5.1773 | 0.11444 | -0.032043 | 2.1744 | 121.1563 | -0.027465 | 0.054932 | 120.9915 | 0.054932 | 121.0922 | 5.2643 | -121.1884 | -116.0797 | 121.257 | 5.2643 | 3.0121 | 5.1224
2858.0469 | 121.3074 | -4.7562 | 116.5466 | -0.0057221 | 6.975 | 0.068167 | 0.095118 | 0.0011321 | 0.002634 | 0.022409 | -0.0028687 | 0.023407 | -1.4529 | -0.003121 | -0.0043408 | 0.013612 | -0.00066231 | -1.767 | 116.4093 | -4.6555 | 116.4825 | -2.5406 | -3.6987 | -1.68 | 0.33875 | 0.50812 | 0.44861 | 0.52185 | 0.39825 | 0.35706 | 0.54932 | 0.10071 | -0.13733 | -0.064087 | 2.2156 | 3.0762 | 1.0574 | 2.9755 | 0.95673 | 5.2048 | -116.0385 | -116.0248 | 5.1544 | 5.3055 | 5.1132 | 0.10071 | -0.091552 | 2.1149 | 121.138 | -0.050354 | 0.073243 | 121.0648 | 0.05951 | 121.1655 | 5.2643 | -121.2021 | -116.098 | 121.2387 | 5.278 | 2.9892 | 5.0949
2859.8281 | 121.376 | -4.6509 | 116.5878 | 0.0019074 | 6.9759 | 0.06539 | 0.095118 | -0.0027131 | 0.0022068 | 0.017069 | -0.0028687 | 0.019989 | -1.4531 | 0.0088418 | -0.0026318 | 0.013826 | 0.0036103 | -1.6983 | 116.423 | -4.5639 | 116.6199 | -2.4078 | -3.566 | -1.5472 | 0.43488 | 0.44861 | 0.4715 | 0.59509 | 0.49439 | 0.45319 | 0.6134 | 0.086975 | -0.16479 | 0.032043 | 2.243 | 3.1036 | 1.0849 | 3.0167 | 0.99792 | 5.1224 | -116.1392 | -115.9927 | 5.1453 | 5.2643 | 5.1041 | 0.14191 | -0.018311 | 2.1561 | 121.1838 | 0.022888 | 0.1236 | 120.9869 | -0.022889 | 121.0739 | 5.0995 | -121.1517 | -116.1163 | 121.2708 | 5.246 | 2.9526 | 5.0858
2861.6094 | 121.3989 | -4.866 | 116.3864 | -0.0057221 | 6.9714 | 0.066458 | 0.0964 | 0.00027771 | 0.0032748 | 0.019846 | -0.0089723 | 0.022552 | -1.4516 | 0.00072423 | -0.0026318 | 0.014253 | -2.1314e-05 | -1.9684 | 116.2674 | -4.8248 | 116.3544 | -2.6962 | -3.8406 | -1.8173 | 0.36621 | 0.48523 | 0.44403 | 0.56305 | 0.45319 | 0.44403 | 0.60425 | 0.041199 | -0.11902 | -0.032044 | 2.1698 | 3.0487 | 1.0254 | 3.0075 | 0.98419 | 5.3101 | -115.9012 | -115.8234 | 5.3192 | 5.4703 | 5.3101 | 0.16022 | 0 | 2.1286 | 121.1792 | 0.009155 | 0.11902 | 121.0922 | 0.041198 | 121.1334 | 5.3513 | -121.2112 | -115.9424 | 121.2204 | 5.4291 | 2.8976 | 5.2322
2863.3906 | 121.4218 | -5.0812 | 116.1438 | 0.024795 | 6.9735 | 0.064963 | 0.097468 | -0.0027131 | 0.0037022 | 0.019632 | -0.0059205 | 0.019348 | -1.4531 | 0.0020058 | -0.0032728 | 0.015321 | 0.0021149 | -2.1103 | 116.0248 | -4.9759 | 116.2033 | -2.829 | -4.0009 | -1.9775 | 0.45776 | 0.48981 | 0.48523 | 0.62256 | 0.5127 | 0.48523 | 0.63629 | 0.10529 | -0.11902 | 0.059509 | 2.2522 | 3.1036 | 1.0803 | 2.9984 | 0.97504 | 5.5664 | -115.654 | -115.5212 | 5.5939 | 5.7175 | 5.5664 | 0.15106 | 0 | 2.1469 | 121.1792 | 0.027466 | 0.13733 | 121.0007 | 0.004578 | 121.106 | 5.571 | -121.1197 | -115.6586 | 121.2845 | 5.7037 | 2.9709 | 5.5389
2865.1094 | 121.3623 | -5.2597 | 116.066 | 0.0019074 | 6.975 | 0.064749 | 0.09405 | -0.0016449 | 0.0024204 | 0.017923 | -0.0028687 | 0.025329 | -1.4514 | -0.00013037 | -0.0058362 | 0.013185 | -0.00044851 | -2.2797 | 115.9195 | -5.1865 | 116.0065 | -3.0579 | -4.2023 | -2.1835 | 0.40741 | 0.52185 | 0.4715 | 0.55389 | 0.45776 | 0.44403 | 0.59509 | 0.073243 | -0.14648 | -0.059509 | 2.2018 | 3.0762 | 1.0574 | 3.0029 | 0.98419 | 5.7312 | -115.5441 | -115.5121 | 5.7175 | 5.8548 | 5.7037 | 0.1236 | -0.027466 | 2.1286 | 121.1929 | -0.013733 | 0.082397 | 121.106 | 0.050354 | 121.1792 | 5.7816 | -121.2524 | -115.5945 | 121.2662 | 5.8136 | 2.98 | 5.6671
2866.8906 | 121.3943 | -5.1178 | 116.1987 | -0.0057221 | 6.9742 | 0.064536 | 0.095759 | -0.0010041 | 0.0030612 | 0.018991 | -0.0059205 | 0.022552 | -1.4506 | -0.0078208 | -0.004768 | 0.015535 | 0.0012603 | -2.211 | 116.0889 | -5.0446 | 116.0751 | -3.0121 | -4.1428 | -2.1011 | 0.3479 | 0.50812 | 0.46692 | 0.54474 | 0.44403 | 0.40741 | 0.59967 | 0.073242 | -0.10986 | -0.1236 | 2.1057 | 3.0167 | 0.97504 | 2.9434 | 0.90179 | 5.5847 | -115.6906 | -115.654 | 5.5618 | 5.7175 | 5.5252 | 0.13275 | -0.059509 | 2.0325 | 121.1197 | -0.022888 | 0.07782 | 121.1334 | 0.041199 | 121.2067 | 5.6259 | -121.2433 | -115.7318 | 121.1929 | 5.6625 | 2.9068 | 5.4657
2868.6875 | 121.3715 | -4.9576 | 116.4047 | 0.0019074 | 6.9761 | 0.062613 | 0.095545 | 0.0022003 | 0.0051974 | 0.01835 | -0.0028687 | 0.021911 | -1.4527 | -0.0069662 | -0.0075452 | 0.011689 | 0.0021149 | -2.005 | 116.2399 | -4.8569 | 116.3086 | -2.774 | -3.891 | -1.886 | 0.3891 | 0.50354 | 0.4715 | 0.54016 | 0.46234 | 0.4303 | 0.59052 | 0.10071 | -0.16479 | -0.09613 | 2.1835 | 3.0716 | 1.0666 | 2.9709 | 0.96588 | 5.4291 | -115.9012 | -115.8646 | 5.4199 | 5.5481 | 5.3879 | 0.11902 | -0.041199 | 2.0828 | 121.1655 | -0.009156 | 0.068664 | 121.0968 | 0.032043 | 121.1975 | 5.4611 | -121.2616 | -115.9332 | 121.2662 | 5.4977 | 2.9526 | 5.3467
2870.4531 | 121.4264 | -5.3192 | 115.9836 | -0.013352 | 6.9748 | 0.06539 | 0.092982 | -0.0027131 | -0.00099764 | 0.019205 | -0.0028687 | 0.019134 | -1.4508 | -0.005471 | -0.004768 | 0.013826 | -0.00023491 | -2.3987 | 115.7959 | -5.2277 | 115.9882 | -3.1082 | -4.2068 | -2.2339 | 0.40741 | 0.44861 | 0.46692 | 0.52643 | 0.49439 | 0.4715 | 0.58594 | 0.091553 | -0.18768 | 0.004577 | 2.211 | 3.0853 | 1.1124 | 2.9938 | 1.0208 | 5.7861 | -115.535 | -115.4572 | 5.8136 | 5.9052 | 5.7907 | 0.11902 | 0.004578 | 2.1194 | 121.2158 | 0.027466 | 0.059509 | 121.0236 | -0.018311 | 121.1151 | 5.7678 | -121.2112 | -115.5167 | 121.3074 | 5.8456 | 2.9205 | 5.7266
2872.2344 | 121.4996 | -5.9784 | 115.2924 | -0.0057221 | 6.9742 | 0.063681 | 0.092554 | 0.00070491 | 0.0017796 | 0.019632 | 0.00018312 | 0.021484 | -1.451 | 0.0062784 | -0.004768 | 0.01468 | -0.0010895 | -3.0121 | 115.1367 | -5.9143 | 115.3152 | -3.7354 | -4.8706 | -2.8885 | 0.46234 | 0.42572 | 0.44861 | 0.55847 | 0.52185 | 0.49896 | 0.59967 | 0.064087 | -0.15564 | 0.022889 | 2.243 | 3.0899 | 1.1078 | 3.0258 | 1.0437 | 6.427 | -114.8666 | -114.7339 | 6.5002 | 6.5781 | 6.4774 | 0.15106 | 0.050354 | 2.179 | 121.2296 | 0.073243 | 0.10986 | 121.051 | -0.022888 | 121.1151 | 6.4041 | -121.2067 | -114.8438 | 121.2936 | 6.5369 | 2.9663 | 6.4407
2873.9531 | 121.431 | -6.221 | 115.1001 | -0.0057221 | 6.9744 | 0.065817 | 0.09405 | -0.0067719 | 0.0037022 | 0.017069 | 0.00018312 | 0.020202 | -1.4499 | 0.0022196 | -0.0051954 | 0.01468 | 0.0023285 | -3.1906 | 114.917 | -6.1295 | 115.036 | -4.0237 | -5.1682 | -3.1677 | 0.39368 | 0.43945 | 0.46692 | 0.52185 | 0.44403 | 0.44403 | 0.58594 | 0.091552 | -0.18311 | -0.064087 | 2.1973 | 3.0533 | 1.0529 | 2.9617 | 0.9613 | 6.6879 | -114.6606 | -114.5782 | 6.665 | 6.8069 | 6.665 | 0.11902 | -0.022888 | 2.1057 | 121.1655 | -0.022888 | 0.054932 | 121.0464 | -0.027466 | 121.138 | 6.6605 | -121.2296 | -114.6332 | 121.257 | 6.7429 | 3.0304 | 6.6147
2875.7344 | 121.3623 | -6.2942 | 115.0772 | -0.013352 | 6.9759 | 0.062613 | 0.097468 | 0.00027771 | 0.0028476 | 0.018991 | -0.0089723 | 0.024261 | -1.4523 | -0.0039756 | -0.0043408 | 0.015107 | -0.0045075 | -3.2364 | 114.917 | -6.2027 | 114.9399 | -4.1748 | -5.3009 | -3.3142 | 0.2243 | 0.39368 | 0.36163 | 0.35248 | 0.27924 | 0.23346 | 0.40741 | 0.091552 | -0.16022 | -0.13733 | 2.1194 | 2.98 | 0.99335 | 2.8885 | 0.90179 | 6.6559 | -114.6835 | -114.7247 | 6.5735 | 6.7017 | 6.5277 | 0.045777 | -0.12817 | 2.0279 | 121.1426 | -0.082397 | -0.009155 | 121.1197 | 0.032044 | 121.2112 | 6.6879 | -121.2799 | -114.7156 | 121.2341 | 6.6467 | 3.0579 | 6.5186
2877.5 | 121.5179 | -6.4133 | 114.8483 | -0.013352 | 6.9731 | 0.064749 | 0.093622 | 0.0024139 | 0.0013522 | 0.019632 | -0.0028687 | 0.019989 | -1.4508 | 0.0017922 | -0.0077588 | 0.013398 | -0.0015167 | -3.3783 | 114.679 | -6.3583 | 114.8621 | -4.2068 | -5.3329 | -3.3554 | 0.32501 | 0.28381 | 0.31586 | 0.4303 | 0.39825 | 0.39825 | 0.4715 | 0.054932 | -0.16937 | 0.013733 | 2.2064 | 3.0579 | 1.0803 | 3.0029 | 1.0254 | 6.7291 | -114.5645 | -114.418 | 6.8115 | 6.8848 | 6.8115 | 0.15564 | 0.082397 | 2.1515 | 121.2204 | 0.082397 | 0.11444 | 121.0373 | -0.032044 | 121.0922 | 6.6971 | -121.2067 | -114.5325 | 121.2753 | 6.8436 | 3.035 | 6.7383
2879.2188 | 121.3898 | -6.7612 | 114.6103 | -0.013352 | 6.9746 | 0.06304 | 0.094263 | -0.0012177 | 0.00092496 | 0.019632 | -0.0089723 | 0.022125 | -1.451 | 0.0071328 | -0.0096814 | 0.012544 | 0.0016877 | -3.6209 | 114.4547 | -6.6422 | 114.5737 | -4.5547 | -5.6763 | -3.717 | 0.14648 | 0.23346 | 0.22888 | 0.20599 | 0.21057 | 0.19226 | 0.29297 | 0.11902 | -0.15564 | -0.036622 | 2.2064 | 3.0441 | 1.0849 | 2.9251 | 0.96588 | 6.9901 | -114.3768 | -114.4043 | 6.9717 | 7.0541 | 6.9534 | 0.064087 | -0.036621 | 2.0874 | 121.2158 | -0.018311 | -0.022888 | 121.0968 | 0.004577 | 121.2158 | 6.9946 | -121.2524 | -114.3814 | 121.3348 | 6.9672 | 3.1403 | 6.9077
2881.0156 | 121.4035 | -7.4432 | 113.9053 | 0.0095369 | 6.975 | 0.065817 | 0.095972 | -0.0012177 | 0.0028476 | 0.016855 | -0.0028687 | 0.024047 | -1.4527 | 0.0011514 | -0.0041272 | 0.013185 | 0.00040589 | -4.2892 | 113.7863 | -7.3471 | 113.7955 | -5.3238 | -6.4499 | -4.4907 | 0.11444 | 0.21973 | 0.21057 | 0.21057 | 0.19226 | 0.14648 | 0.29297 | 0.09613 | -0.11902 | -0.10986 | 2.1194 | 2.9526 | 0.99335 | 2.8564 | 0.89722 | 7.6538 | -113.6856 | -113.6948 | 7.6355 | 7.7362 | 7.5897 | 0.082398 | -0.064087 | 2.0233 | 121.1426 | -0.01831 | 0 | 121.1334 | 0.009156 | 121.2296 | 7.663 | -121.2524 | -113.6948 | 121.2387 | 7.6538 | 3.154 | 7.5577
2882.7344 | 121.4218 | -7.489 | 113.8733 | -0.013352 | 6.9748 | 0.064536 | 0.09405 | 0.00091851 | 0.0013522 | 0.017069 | -0.0028687 | 0.020843 | -1.4548 | -0.003762 | -0.0058362 | 0.01233 | 0.0055329 | -4.3304 | 113.7405 | -7.4203 | 113.7497 | -5.3513 | -6.459 | -4.5227 | 0.07782 | 0.2243 | 0.20599 | 0.21515 | 0.20142 | 0.16937 | 0.29755 | 0.068665 | -0.13275 | -0.1236 | 2.1378 | 2.9663 | 1.03 | 2.8976 | 0.9613 | 7.695 | -113.649 | -113.6581 | 7.6904 | 7.7866 | 7.6584 | 0.091552 | -0.036621 | 2.0691 | 121.17 | -0.004578 | 0.009155 | 121.1609 | 0.01831 | 121.2296 | 7.7133 | -121.2936 | -113.6673 | 121.2387 | 7.7042 | 3.1586 | 7.5668
2884.5 | 121.4264 | -6.9122 | 114.4455 | 0.0019074 | 6.9746 | 0.064108 | 0.094263 | 0.00027771 | 0.0019932 | 0.021982 | -0.0028687 | 0.019775 | -1.4536 | -0.0052572 | -0.0062634 | 0.011903 | -2.1314e-05 | -3.7765 | 114.3402 | -6.8069 | 114.3906 | -4.7424 | -5.8594 | -3.9276 | 0.14191 | 0.21057 | 0.21057 | 0.21973 | 0.22888 | 0.19226 | 0.3067 | 0.10529 | -0.10529 | -0.054932 | 2.1698 | 2.9846 | 1.0529 | 2.8793 | 0.94757 | 7.1228 | -114.2349 | -114.2258 | 7.1411 | 7.2189 | 7.1045 | 0.096131 | -0.01831 | 2.0645 | 121.1975 | 0.018311 | 0.009156 | 121.1472 | 0 | 121.2524 | 7.1228 | -121.2524 | -114.2349 | 121.3028 | 7.132 | 3.1357 | 7.0541
2886.2344 | 121.4401 | -7.0038 | 114.3036 | -0.0057221 | 6.9724 | 0.063895 | 0.094904 | 0.0034821 | 0.0032748 | 0.017069 | -0.0028687 | 0.022339 | -1.4527 | 0.0028604 | -0.0015638 | 0.01468 | -0.00066231 | -3.9139 | 114.18 | -6.9534 | 114.212 | -4.921 | -6.0608 | -4.1336 | 0.14648 | 0.21515 | 0.21057 | 0.2655 | 0.24719 | 0.19684 | 0.32501 | 0.050354 | -0.1236 | -0.091553 | 2.0828 | 2.8702 | 0.94299 | 2.8198 | 0.89264 | 7.2144 | -114.0884 | -114.0381 | 7.251 | 7.3288 | 7.2006 | 0.11444 | -0.013733 | 2.0325 | 121.1655 | 0.036621 | 0.054932 | 121.1334 | 0.004578 | 121.1838 | 7.2189 | -121.257 | -114.093 | 121.2158 | 7.2693 | 3.0899 | 7.1503
2888 | 121.4035 | -6.752 | 114.7202 | -0.0057221 | 6.9769 | 0.065817 | 0.095759 | 0.0030547 | 0.0030612 | 0.021341 | 0.00018312 | 0.023407 | -1.4516 | -0.0046164 | -0.0069044 | 0.015535 | -2.1314e-05 | -3.6758 | 114.4043 | -6.7749 | 114.3082 | -4.8203 | -5.928 | -3.9413 | 0.036621 | 0.16937 | 0.17395 | 0.14648 | 0.1236 | 0.07782 | 0.21057 | -0.022888 | -0.31586 | -0.41199 | 1.9318 | 2.8107 | 0.82397 | 2.8336 | 0.84686 | 6.926 | -114.5508 | -114.5737 | 6.8756 | 6.9626 | 6.8298 | 0.036621 | -0.09613 | 1.9547 | 121.0831 | -0.050354 | -0.027466 | 121.1792 | -0.004577 | 121.1563 | 6.9214 | -121.4951 | -114.5462 | 121.0602 | 6.8985 | 3.0762 | 6.7886
2889.7969 | 121.4767 | -43.9499 | 77.0966 | -0.013352 | 6.9716 | 0.067526 | 0.092341 | -0.0027131 | 0.0030612 | 0.020486 | -0.0059205 | 0.019989 | -1.4538 | 0.003074 | -0.0056226 | 0.015321 | 0.0042511 | -38.6398 | 76.9638 | -43.9133 | 77.1927 | -41.4139 | -43.0389 | -41.2125 | 0.027466 | -0.050354 | -0.004578 | 0.027466 | 0.064087 | 0.036621 | 0.091553 | 0.036621 | -0.13275 | 0.09613 | 2.536 | 2.7374 | 0.91095 | 2.7008 | 0.87433 | 43.9453 | -77.1469 | -77.0691 | 44.014 | 44.0414 | 43.9865 | 0.096131 | 0.041199 | 2.4994 | 121.106 | 0.068665 | 0.032044 | 120.8771 | -0.045776 | 120.9137 | 43.8995 | -121.0098 | -77.1011 | 121.1426 | 43.9774 | 5.3101 | 43.9774
2891.5312 | 121.463 | -44.1238 | 77.0554 | 0.0019074 | 6.9744 | 0.06774 | 0.092768 | -0.0018585 | 0.0017796 | 0.017069 | -0.0028687 | 0.021484 | -1.4519 | 0.0026468 | -0.0069044 | 0.013398 | 0.00083309 | -38.7497 | 76.9272 | -44.0826 | 77.124 | -41.5833 | -43.1854 | -41.391 | -0.032043 | -0.036621 | 0 | -0.036621 | 0.018311 | -0.018311 | 0.041199 | 0.041198 | -0.12817 | 0.068664 | 2.5406 | 2.7328 | 0.93841 | 2.6917 | 0.89722 | 44.1238 | -77.092 | -77.092 | 44.1422 | 44.165 | 44.1055 | 0.041199 | -0.018311 | 2.4994 | 121.2067 | 0.018311 | -0.036621 | 121.0098 | -0.036621 | 121.051 | 44.0872 | -121.138 | -77.0554 | 121.2479 | 44.0872 | 5.3741 | 44.0918
2893.2969 | 121.4539 | -44.1788 | 77.092 | -0.013352 | 6.9724 | 0.065176 | 0.095331 | -0.0024995 | 0.0011386 | 0.021341 | -0.0028687 | 0.020843 | -1.4512 | -0.0029074 | -0.0083996 | 0.012544 | -0.0027985 | -38.7726 | 76.9775 | -44.1238 | 77.0645 | -41.6382 | -43.2266 | -41.423 | -0.10071 | 0 | -0.018311 | -0.027466 | -0.009155 | -0.045776 | 0.054932 | 0.054932 | -0.11444 | -0.027466 | 2.5406 | 2.7557 | 0.95215 | 2.7008 | 0.89722 | 44.1605 | -77.092 | -77.1194 | 44.1696 | 44.2337 | 44.133 | 0.073243 | -0.027465 | 2.4857 | 121.1884 | 0.009156 | -0.009155 | 121.1014 | 0.018311 | 121.1563 | 44.1788 | -121.2158 | -77.1103 | 121.2433 | 44.1513 | 5.4062 | 44.0781
2895.0781 | 121.5546 | -44.1101 | 77.1011 | 0.0019074 | 6.9727 | 0.066672 | 0.093622 | 0.0036957 | 0.0032748 | 0.018778 | -0.0028687 | 0.018707 | -1.4519 | -0.0033346 | -0.0056226 | 0.012758 | -0.00044851 | -38.6536 | 76.9547 | -44.046 | 77.2476 | -41.4413 | -43.0756 | -41.2994 | 0.086975 | -0.041199 | 0.032043 | 0.10071 | 0.13275 | 0.13275 | 0.16937 | 0.064086 | -0.14648 | 0.14648 | 2.6688 | 2.8107 | 1.0345 | 2.7466 | 0.97046 | 44.1422 | -77.1423 | -77.0004 | 44.2429 | 44.2795 | 44.2429 | 0.13733 | 0.10071 | 2.6047 | 121.2936 | 0.10071 | 0.068665 | 121.0007 | -0.073242 | 121.0648 | 44.0689 | -121.1472 | -77.0691 | 121.3577 | 44.2108 | 5.4565 | 44.1971
2896.8594 | 121.463 | -43.9957 | 77.2797 | -0.0057221 | 6.9742 | 0.068594 | 0.093409 | 6.4114e-05 | 0.0037022 | 0.017069 | -0.0028687 | 0.020202 | -1.4525 | -0.0056846 | -0.003059 | 0.014894 | 0.0023285 | -38.53 | 77.1606 | -43.9362 | 77.2614 | -41.4825 | -43.1076 | -41.2811 | -0.059509 | 0.013733 | 0.009155 | 0.018311 | 0 | -0.036621 | 0.07782 | 0.05951 | -0.11902 | -0.01831 | 2.5131 | 2.7145 | 0.88806 | 2.655 | 0.82855 | 44.0048 | -77.2659 | -77.2614 | 43.9957 | 44.0735 | 43.959 | 0.068665 | -0.045776 | 2.4536 | 121.1975 | -0.009155 | 0.009156 | 121.0968 | 0.004578 | 121.1563 | 44.0094 | -121.2158 | -77.2705 | 121.257 | 44.014 | 5.4657 | 43.9362
2898.6406 | 121.4355 | -43.9178 | 77.3849 | -0.013352 | 6.9744 | 0.067526 | 0.094263 | -0.0024995 | 0.004343 | 0.017709 | 0.00018312 | 0.022339 | -1.4508 | -0.0026938 | -0.0037 | 0.013398 | 0.0012603 | -38.3835 | 77.2339 | -43.8675 | 77.3804 | -41.3864 | -43.0069 | -41.2079 | -0.045776 | -0.009155 | 0.032043 | -0.004578 | -0.004578 | -0.041199 | 0.059509 | 0.050354 | -0.15106 | -0.004578 | 2.5314 | 2.71 | 0.91095 | 2.6596 | 0.8606 | 43.9499 | -77.3941 | -77.3895 | 43.9133 | 43.9774 | 43.8766 | 0.027466 | -0.073242 | 2.4811 | 121.2479 | -0.036621 | -0.036621 | 121.1014 | -0.041198 | 121.1517 | 43.9087 | -121.2524 | -77.3529 | 121.2982 | 43.9133 | 5.5344 | 43.8721
2900.3594 | 121.5225 | -43.7393 | 77.5131 | -0.013352 | 6.9744 | 0.067099 | 0.092341 | -0.0020721 | 0.0051974 | 0.019846 | -0.0059205 | 0.018493 | -1.4533 | 0.004783 | -0.0058362 | 0.014894 | -0.0017303 | -38.2141 | 77.3941 | -43.6615 | 77.5726 | -41.1484 | -42.7689 | -40.9882 | -0.018311 | -0.013733 | 0.022888 | 0.045776 | 0.086975 | 0.064087 | 0.11902 | 0.07782 | -0.11902 | 0.059509 | 2.5909 | 2.7512 | 0.97046 | 2.6733 | 0.89264 | 43.7622 | -77.5269 | -77.4673 | 43.8263 | 43.8583 | 43.8034 | 0.096131 | 0.041199 | 2.5131 | 121.2341 | 0.064087 | 0.022888 | 121.0556 | -0.036621 | 121.1334 | 43.7256 | -121.1746 | -77.4902 | 121.312 | 43.7851 | 5.5252 | 43.721
2902.1406 | 121.4859 | -43.959 | 77.3209 | -0.0057221 | 6.9759 | 0.066031 | 0.095545 | 0.0036957 | 0.0047702 | 0.019632 | -0.0028687 | 0.019989 | -1.4536 | -0.0056846 | -0.0037 | 0.012758 | 0.0076691 | -38.3972 | 77.2156 | -43.9087 | 77.2934 | -41.4551 | -43.0893 | -41.2811 | -0.064087 | -0.018311 | 0.009155 | 0.018311 | 0.032043 | -0.009155 | 0.086975 | 0.050354 | -0.10529 | -0.027466 | 2.504 | 2.6779 | 0.86975 | 2.6276 | 0.8194 | 43.9682 | -77.3392 | -77.3026 | 43.9911 | 44.046 | 43.9499 | 0.07782 | -0.01831 | 2.4536 | 121.2021 | 0.022888 | 0.009156 | 121.1243 | -0.027466 | 121.1746 | 43.9407 | -121.2296 | -77.3117 | 121.2524 | 43.9774 | 5.5618 | 43.895
2903.9219 | 121.5134 | -43.8766 | 77.3804 | -0.013352 | 6.9727 | 0.066885 | 0.091486 | -0.0037811 | 0.0058384 | 0.019205 | 0.00018312 | 0.01828 | -1.4527 | 0.0037148 | -0.0060498 | 0.013612 | 0.0016877 | -38.2187 | 77.2293 | -43.8126 | 77.4948 | -41.2399 | -42.8558 | -41.0843 | 0.045776 | -0.018311 | 0.027466 | 0.045776 | 0.11444 | 0.073242 | 0.11902 | 0.064087 | -0.15106 | 0.11444 | 2.6367 | 2.7924 | 1.0208 | 2.7283 | 0.95673 | 43.9041 | -77.3987 | -77.3346 | 43.9911 | 43.9957 | 43.9499 | 0.091553 | 0.045776 | 2.5726 | 121.3074 | 0.086975 | 0.01831 | 121.0419 | -0.045777 | 121.106 | 43.8583 | -121.1929 | -77.3529 | 121.3715 | 43.9224 | 5.658 | 43.9224
2905.6406 | 121.5546 | -43.6203 | 77.6276 | -0.020981 | 6.9731 | 0.067954 | 0.088923 | -0.0022857 | 0.002634 | 0.018564 | -0.0059205 | 0.017639 | -1.4514 | -0.00098477 | -0.008186 | 0.013398 | -0.00023491 | -37.9715 | 77.4994 | -43.5287 | 77.7878 | -40.9836 | -42.5858 | -40.8325 | 0.082397 | -0.041199 | 0.054932 | 0.09613 | 0.15564 | 0.13275 | 0.14191 | 0.091552 | -0.12817 | 0.16022 | 2.6367 | 2.7878 | 1.0345 | 2.6962 | 0.94299 | 43.6752 | -77.6688 | -77.5314 | 43.7759 | 43.7622 | 43.7531 | 0.086975 | 0.077819 | 2.5452 | 121.3165 | 0.10071 | 0.041198 | 121.0281 | -0.096131 | 121.1197 | 43.5791 | -121.1563 | -77.5726 | 121.4081 | 43.7164 | 5.6488 | 43.7027
2907.4062 | 121.5683 | -43.4921 | 77.774 | -0.0057221 | 6.9733 | 0.065604 | 0.092127 | 0.0024139 | 0.002634 | 0.020273 | 0.00018312 | 0.018493 | -1.4542 | -0.0011984 | -0.0037 | 0.014253 | -0.00044851 | -37.8525 | 77.6184 | -43.4189 | 77.829 | -40.9378 | -42.54 | -40.7501 | 0.022888 | -0.022888 | 0.059509 | 0.064087 | 0.11444 | 0.09613 | 0.14191 | 0.073242 | -0.15564 | 0.054931 | 2.5543 | 2.742 | 0.95215 | 2.6688 | 0.87891 | 43.5516 | -77.7969 | -77.71 | 43.6066 | 43.634 | 43.5883 | 0.082398 | 0.036621 | 2.4811 | 121.2479 | 0.054932 | 0.004578 | 121.0373 | -0.082397 | 121.1105 | 43.4692 | -121.1929 | -77.7145 | 121.3211 | 43.5562 | 5.6396 | 43.515
2909.2031 | 121.4676 | -44.2886 | 77.0508 | -0.013352 | 6.9767 | 0.064536 | 0.092554 | 0.00027771 | 0.0032748 | 0.01835 | -0.0028687 | 0.019775 | -1.4531 | -0.0041892 | -0.008827 | 0.012758 | 0.0027557 | -38.5574 | 76.9226 | -44.2017 | 77.037 | -41.7389 | -43.3273 | -41.5604 | -0.064087 | -0.004578 | 0.009155 | -0.027466 | 0.027466 | -0.027466 | 0.059509 | 0.086975 | -0.12817 | -0.013733 | 2.5497 | 2.7283 | 0.9613 | 2.6413 | 0.87433 | 44.2978 | -77.0554 | -77.0782 | 44.3161 | 44.3481 | 44.2612 | 0.050354 | -0.036621 | 2.4628 | 121.2387 | 0.018311 | -0.036621 | 121.1243 | -0.013733 | 121.2112 | 44.2841 | -121.2524 | -77.0416 | 121.3257 | 44.2612 | 5.7312 | 44.2245
2910.9219 | 121.5546 | -44.1788 | 77.0828 | -0.0057221 | 6.9748 | 0.06774 | 0.090204 | -0.0029267 | 0.0034884 | 0.016855 | 0.00018312 | 0.020843 | -1.4514 | -0.0022666 | -0.006477 | 0.014253 | -0.00066231 | -38.4018 | 76.9226 | -44.101 | 77.2064 | -41.5512 | -43.1808 | -41.3956 | 0.068665 | -0.027466 | 0.045776 | 0.068665 | 0.13275 | 0.091553 | 0.14191 | 0.07782 | -0.16022 | 0.1236 | 2.6276 | 2.7832 | 0.99793 | 2.7054 | 0.9201 | 44.2245 | -77.1103 | -77.0142 | 44.3115 | 44.3207 | 44.2703 | 0.096131 | 0.045777 | 2.5497 | 121.3074 | 0.086975 | 0.022889 | 121.0236 | -0.073242 | 121.1014 | 44.1513 | -121.1838 | -77.037 | 121.3852 | 44.2474 | 5.777 | 44.2474
2912.7031 | 121.4767 | -44.1376 | 77.179 | -0.0057221 | 6.9752 | 0.067526 | 0.092554 | 0.0028411 | 0.005411 | 0.018778 | -0.0028687 | 0.022979 | -1.4519 | 0.0039286 | -0.0028454 | 0.013398 | 0.0051057 | -38.3286 | 77.0462 | -44.0598 | 77.1973 | -41.5833 | -43.222 | -41.423 | 0 | 0.004578 | 0.050354 | 0.009155 | 0.041199 | -0.027466 | 0.091553 | 0.07782 | -0.13275 | 0.018311 | 2.5543 | 2.7145 | 0.91553 | 2.6367 | 0.83771 | 44.1879 | -77.1744 | -77.1698 | 44.1788 | 44.2291 | 44.1101 | 0.041199 | -0.07782 | 2.4765 | 121.257 | -0.009155 | -0.041199 | 121.106 | -0.045776 | 121.1838 | 44.1422 | -121.2387 | -77.1286 | 121.3348 | 44.1467 | 5.809 | 44.1376
2914.4219 | 121.5363 | -44.0277 | 77.2476 | -0.0057221 | 6.9735 | 0.067099 | 0.092768 | -0.0024995 | 0.004343 | 0.018564 | -0.0059205 | 0.019348 | -1.4548 | 0.0022196 | -0.0041272 | 0.012971 | -0.00087591 | -38.2278 | 77.1103 | -43.9453 | 77.3117 | -41.4642 | -43.0756 | -41.3132 | 0.027466 | -0.036621 | 0.036621 | 0.054932 | 0.09613 | 0.064087 | 0.10986 | 0.082398 | -0.13733 | 0.064087 | 2.5635 | 2.7145 | 0.95215 | 2.6321 | 0.86975 | 44.0643 | -77.2842 | -77.1927 | 44.1238 | 44.1376 | 44.0918 | 0.073242 | 0.027466 | 2.4811 | 121.257 | 0.059509 | 0.018311 | 121.0556 | -0.073242 | 121.138 | 43.9911 | -121.1929 | -77.211 | 121.3394 | 44.0826 | 5.7999 | 44.0552
2916.2031 | 121.6187 | -44.0094 | 77.2751 | -0.013352 | 6.9735 | 0.066245 | 0.092768 | -0.0022857 | 0.0032748 | 0.016855 | -0.0028687 | 0.01828 | -1.4536 | 0.0041422 | -0.0039136 | 0.011689 | -0.00044851 | -38.1592 | 77.1149 | -43.9407 | 77.3941 | -41.3406 | -42.9611 | -41.217 | 0.12817 | -0.036621 | 0.059509 | 0.11902 | 0.21057 | 0.15106 | 0.1831 | 0.068664 | -0.16022 | 0.11902 | 2.6688 | 2.7924 | 1.0483 | 2.7237 | 0.97961 | 44.0689 | -77.3117 | -77.1561 | 44.22 | 44.1925 | 44.1605 | 0.1236 | 0.091553 | 2.6001 | 121.3348 | 0.15106 | 0.05951 | 121.0556 | -0.09613 | 121.1243 | 43.9728 | -121.2158 | -77.2156 | 121.4035 | 44.1284 | 5.8502 | 44.1376
2917.9688 | 121.6095 | -44.1559 | 77.0966 | 0.0019074 | 6.9709 | 0.064322 | 0.091059 | -0.0033539 | 0.0041294 | 0.019418 | -0.0089723 | 0.02127 | -1.4542 | 0.0035012 | -0.006477 | 0.012971 | -0.0013031 | -38.3011 | 76.9226 | -44.1055 | 77.2202 | -41.5054 | -43.1396 | -41.3956 | 0.13733 | -0.027466 | 0.050354 | 0.10529 | 0.18768 | 0.14191 | 0.17853 | 0.050354 | -0.17395 | 0.1236 | 2.6505 | 2.7603 | 1.0162 | 2.71 | 0.96588 | 44.2062 | -77.124 | -76.9913 | 44.3436 | 44.3344 | 44.2978 | 0.12817 | 0.091553 | 2.6001 | 121.3257 | 0.13733 | 0.054932 | 121.0281 | -0.07782 | 121.0785 | 44.1284 | -121.2021 | -77.0462 | 121.376 | 44.2612 | 5.8548 | 44.2932
2919.75 | 121.6049 | -44.0186 | 77.2476 | 0.0019074 | 6.9752 | 0.066245 | 0.093409 | 0.0019867 | 0.0032748 | 0.021127 | -0.0028687 | 0.021057 | -1.4551 | 0.0058512 | -0.003059 | 0.014894 | 0.0010467 | -38.118 | 77.1011 | -43.9362 | 77.3849 | -41.4047 | -43.0481 | -41.2766 | 0.10986 | -0.045776 | 0.054932 | 0.11902 | 0.15564 | 0.091553 | 0.18768 | 0.082398 | -0.14648 | 0.13733 | 2.6138 | 2.742 | 0.97046 | 2.6596 | 0.88806 | 44.0735 | -77.2934 | -77.1286 | 44.1742 | 44.2062 | 44.1101 | 0.13275 | 0.036621 | 2.5314 | 121.3211 | 0.10071 | 0.064087 | 121.0373 | -0.10071 | 121.1197 | 43.9728 | -121.1838 | -77.1927 | 121.4035 | 44.1376 | 5.9006 | 44.1284
2921.5312 | 121.4767 | -43.9224 | 77.4307 | -0.0057221 | 6.9737 | 0.067526 | 0.09405 | 0.0032685 | 0.0024204 | 0.01835 | -0.0059205 | 0.02127 | -1.4529 | -0.0029074 | -0.0060498 | 0.013826 | -0.00087591 | -38.0539 | 77.2705 | -43.8492 | 77.4033 | -41.3956 | -43.0206 | -41.2811 | -0.07782 | 0.004578 | 0.013733 | -0.027466 | -0.018311 | -0.050354 | 0.064087 | 0.073242 | -0.16022 | -0.027466 | 2.5269 | 2.6413 | 0.90179 | 2.5681 | 0.82855 | 43.9362 | -77.4261 | -77.4582 | 43.9041 | 43.9865 | 43.8721 | 0.050354 | -0.064087 | 2.4536 | 121.2524 | -0.032044 | -0.041199 | 121.1197 | -0.009155 | 121.1929 | 43.927 | -121.2799 | -77.417 | 121.3257 | 43.895 | 5.8685 | 43.8446
2923.2344 | 121.6049 | -43.5928 | 77.7054 | -0.013352 | 6.9729 | 0.065817 | 0.090418 | -0.0027131 | 0.004343 | 0.017709 | -0.0059205 | 0.019348 | -1.4527 | 0.0058512 | -0.0058362 | 0.014466 | 0.0025421 | -37.7151 | 77.5497 | -43.5425 | 77.7832 | -40.9927 | -42.5949 | -40.8554 | 0.059509 | -0.013733 | 0.036621 | 0.091553 | 0.15106 | 0.1236 | 0.16937 | 0.050354 | -0.15564 | 0.07782 | 2.6001 | 2.7374 | 0.99792 | 2.6871 | 0.94757 | 43.6295 | -77.7191 | -77.6138 | 43.7439 | 43.7622 | 43.7164 | 0.13275 | 0.086975 | 2.5497 | 121.3257 | 0.11444 | 0.054932 | 121.0922 | -0.050354 | 121.1426 | 43.5791 | -121.2479 | -77.6688 | 121.376 | 43.6844 | 5.8777 | 43.6523
2925.0156 | 121.6049 | -43.5196 | 77.774 | -0.0057221 | 6.9733 | 0.064963 | 0.089564 | -0.0020721 | 0.0034884 | 0.021555 | -0.0028687 | 0.020416 | -1.4523 | 0.0056374 | -0.0086132 | 0.013398 | 0.0033967 | -37.5732 | 77.623 | -43.4326 | 77.9251 | -40.8371 | -42.4805 | -40.7639 | 0.09613 | -0.022888 | 0.064087 | 0.07782 | 0.17395 | 0.14191 | 0.14648 | 0.086975 | -0.15106 | 0.15106 | 2.6825 | 2.7557 | 1.0391 | 2.6688 | 0.95215 | 43.5837 | -77.7969 | -77.6962 | 43.6935 | 43.6661 | 43.6615 | 0.082397 | 0.07782 | 2.5955 | 121.3577 | 0.10986 | 0.013733 | 121.0556 | -0.086975 | 121.1426 | 43.4967 | -121.2067 | -77.71 | 121.4447 | 43.5974 | 5.9464 | 43.6157
2926.7344 | 121.5454 | -43.4967 | 77.8427 | 0.0019074 | 6.9756 | 0.064536 | 0.091913 | 0.0041229 | 0.0015658 | 0.019205 | -0.0059205 | 0.018921 | -1.454 | -0.0022666 | -0.0073316 | 0.013612 | 0.0031829 | -37.5137 | 77.6505 | -43.4052 | 77.9205 | -40.8783 | -42.485 | -40.7684 | 0.018311 | -0.032043 | 0.013733 | 0.009155 | 0.086975 | 0.032043 | 0.091553 | 0.091553 | -0.19226 | 0.07782 | 2.6184 | 2.7283 | 1.0117 | 2.6367 | 0.9201 | 43.5104 | -77.8748 | -77.8336 | 43.5837 | 43.5883 | 43.5287 | 0.07782 | 0.01831 | 2.5269 | 121.3257 | 0.073242 | -0.004578 | 121.0556 | -0.045776 | 121.1472 | 43.4647 | -121.2479 | -77.829 | 121.4172 | 43.5059 | 5.983 | 43.515
2928.5156 | 121.6187 | -43.4738 | 77.7924 | 0.0019074 | 6.9718 | 0.063467 | 0.090845 | -0.00079049 | 0.0011386 | 0.018778 | 0.00018312 | 0.019348 | -1.4546 | 0.0011514 | -0.0062634 | 0.014253 | 0.0046783 | -37.5366 | 77.6321 | -43.4601 | 77.916 | -40.8554 | -42.4896 | -40.7547 | 0.091553 | -0.041199 | 0.032043 | 0.11902 | 0.17853 | 0.13733 | 0.16937 | 0.013733 | -0.16022 | 0.1236 | 2.6184 | 2.7191 | 0.98419 | 2.7054 | 0.97046 | 43.5059 | -77.8336 | -77.6733 | 43.6523 | 43.6432 | 43.6111 | 0.13733 | 0.10529 | 2.6047 | 121.376 | 0.14648 | 0.086976 | 121.0922 | -0.073242 | 121.106 | 43.4326 | -121.2524 | -77.7603 | 121.3898 | 43.5928 | 5.9372 | 43.5654
2930.25 | 121.55 | -43.5059 | 77.8473 | -0.013352 | 6.975 | 0.066245 | 0.093195 | 0.0034821 | 0.0039158 | 0.018778 | -0.0028687 | 0.02362 | -1.454 | -0.0052572 | -0.0060498 | 0.011903 | 0.0019013 | -37.532 | 77.7008 | -43.4738 | 77.8702 | -40.9058 | -42.5583 | -40.8188 | 0.013733 | -0.009155 | 0.018311 | 0.022888 | 0.082397 | 0.018311 | 0.10071 | 0.032043 | -0.14648 | 0.022888 | 2.6001 | 2.6871 | 0.94757 | 2.655 | 0.91553 | 43.5242 | -77.8564 | -77.8244 | 43.5883 | 43.6066 | 43.5242 | 0.082397 | 0 | 2.5681 | 121.344 | 0.064086 | 0.004577 | 121.1746 | -0.027466 | 121.2067 | 43.4967 | -121.3211 | -77.829 | 121.376 | 43.5287 | 5.9738 | 43.5196
2932.0312 | 121.5866 | -43.4509 | 77.8198 | -0.013352 | 6.9742 | 0.066245 | 0.091486 | 0.00091851 | 0.0047702 | 0.01835 | -0.0028687 | 0.020416 | -1.4529 | 0.008201 | -0.0026318 | 0.015107 | -0.0032257 | -37.5046 | 77.6779 | -43.3731 | 77.9388 | -40.8371 | -42.5125 | -40.7776 | 0.050354 | -0.036621 | 0.036621 | 0.050354 | 0.091553 | 0.064087 | 0.1236 | 0.07782 | -0.14191 | 0.11902 | 2.6138 | 2.6733 | 0.93842 | 2.5955 | 0.8606 | 43.4875 | -77.8564 | -77.7695 | 43.5425 | 43.5745 | 43.515 | 0.086975 | 0.027466 | 2.536 | 121.312 | 0.054932 | 0.013733 | 121.051 | -0.073242 | 121.1288 | 43.4143 | -121.1929 | -77.7832 | 121.3898 | 43.5013 | 5.9463 | 43.5013
2933.75 | 121.5729 | -43.3456 | 77.9755 | -0.013352 | 6.9727 | 0.069022 | 0.091486 | 6.4114e-05 | 0.0024204 | 0.018564 | -0.0059205 | 0.019989 | -1.4523 | 0.0058512 | -0.0051954 | 0.014894 | -0.0013031 | -37.3764 | 77.8152 | -43.2861 | 78.0441 | -40.7593 | -42.4164 | -40.6677 | -0.004578 | -0.036621 | 0.018311 | 0.036621 | 0.082397 | 0.032043 | 0.09613 | 0.059509 | -0.16022 | 0.068664 | 2.5864 | 2.6779 | 0.92926 | 2.6184 | 0.86975 | 43.364 | -78.0121 | -77.9388 | 43.428 | 43.4418 | 43.3777 | 0.077819 | 0.013732 | 2.5269 | 121.3303 | 0.064086 | 0.01831 | 121.1014 | -0.054932 | 121.1609 | 43.309 | -121.2616 | -77.9572 | 121.3898 | 43.3823 | 5.9692 | 43.3411
2935.5156 | 121.4813 | -43.3456 | 78.0121 | -0.0057221 | 6.9756 | 0.06539 | 0.094691 | -0.0042083 | 0.0037022 | 0.019205 | -0.0028687 | 0.021484 | -1.4519 | 0.0067056 | -0.0062634 | 0.012758 | 0.0019013 | -37.381 | 77.8748 | -43.2907 | 77.9663 | -40.8508 | -42.5079 | -40.773 | -0.10986 | -0.004578 | 0.009155 | -0.032043 | 0 | -0.059509 | 0.050354 | 0.054932 | -0.13733 | -0.045776 | 2.4948 | 2.5726 | 0.83771 | 2.5177 | 0.78277 | 43.3548 | -78.0167 | -78.0441 | 43.3456 | 43.396 | 43.2861 | 0.041199 | -0.068664 | 2.4399 | 121.257 | -0.009155 | -0.041198 | 121.1655 | -0.013733 | 121.2204 | 43.3411 | -121.3028 | -78.0029 | 121.312 | 43.3136 | 5.9647 | 43.2358
2937.2344 | 121.5454 | -43.1671 | 78.186 | -0.0057221 | 6.9733 | 0.064749 | 0.0917 | -0.00014949 | 0.0032748 | 0.019205 | -0.0028687 | 0.022125 | -1.4516 | -0.0018394 | -0.008827 | 0.012758 | -0.0034393 | -37.1567 | 77.9984 | -43.1168 | 78.2364 | -40.5441 | -42.1875 | -40.4938 | 0.009155 | -0.018311 | 0.027466 | 0 | 0.082397 | 0.041199 | 0.07782 | 0.050354 | -0.18768 | 0.050354 | 2.623 | 2.6733 | 0.97961 | 2.623 | 0.92926 | 43.1946 | -78.2043 | -78.186 | 43.2495 | 43.2449 | 43.2083 | 0.050354 | 0.013733 | 2.5726 | 121.3531 | 0.054931 | -0.027466 | 121.1151 | -0.045777 | 121.1655 | 43.1488 | -121.3028 | -78.1586 | 121.4035 | 43.1671 | 6.0104 | 43.1763
2939.0156 | 121.4767 | -43.1717 | 78.2181 | -0.0057221 | 6.9739 | 0.069449 | 0.092554 | 0.00070491 | 0.0041294 | 0.019418 | 0.00018312 | 0.022552 | -1.4531 | 0.0049966 | -0.0043408 | 0.01468 | 0.0036103 | -37.1613 | 78.067 | -43.0939 | 78.1769 | -40.6357 | -42.3019 | -40.5716 | -0.11902 | -0.013733 | 0.013733 | -0.045776 | -0.018311 | -0.068665 | 0.045776 | 0.07782 | -0.15106 | -0.041199 | 2.536 | 2.6001 | 0.86975 | 2.5223 | 0.79193 | 43.1854 | -78.2318 | -78.2639 | 43.1534 | 43.2175 | 43.103 | 0.032043 | -0.082398 | 2.4582 | 121.2708 | -0.032044 | -0.059509 | 121.1609 | -0.027466 | 121.2387 | 43.158 | -121.312 | -78.2043 | 121.3486 | 43.1259 | 6.0104 | 43.0527
2940.7969 | 121.5775 | -43.0115 | 78.3646 | -0.0057221 | 6.9737 | 0.067526 | 0.0917 | -0.0033539 | 0.0032748 | 0.017496 | -0.0059205 | 0.021057 | -1.4527 | -0.0016256 | -0.0073316 | 0.014253 | -0.00087591 | -36.9415 | 78.1815 | -42.9199 | 78.4332 | -40.3381 | -41.9952 | -40.2969 | 0.018311 | -0.036621 | 0.032043 | 0.041199 | 0.10071 | 0.064087 | 0.10986 | 0.091553 | -0.1831 | 0.068665 | 2.6733 | 2.7145 | 1.0162 | 2.623 | 0.92468 | 43.0435 | -78.4012 | -78.3234 | 43.1122 | 43.1213 | 43.0756 | 0.07782 | 0.032044 | 2.5818 | 121.3531 | 0.068665 | 0.009156 | 121.1014 | -0.068664 | 121.1929 | 42.9749 | -121.2845 | -78.3325 | 121.4447 | 43.0527 | 6.0699 | 43.0298
2942.5156 | 121.5042 | -42.9932 | 78.4378 | -0.020981 | 6.9744 | 0.065176 | 0.092554 | -0.0020721 | 0.0039158 | 0.019846 | -0.0028687 | 0.022766 | -1.4546 | -0.003762 | -0.0086132 | 0.010408 | -0.0021575 | -36.9461 | 78.2501 | -42.9153 | 78.3783 | -40.3976 | -42.0639 | -40.3473 | -0.054932 | 0.022888 | 0.022888 | -0.050354 | 0.032043 | -0.009155 | 0.041199 | 0.07782 | -0.18768 | -0.059509 | 2.5955 | 2.6459 | 0.92926 | 2.5681 | 0.85144 | 43.0161 | -78.4149 | -78.4882 | 43.0252 | 43.0344 | 42.984 | 0.018311 | -0.032043 | 2.5177 | 121.2936 | 0.009155 | -0.073242 | 121.1655 | 0 | 121.2433 | 43.0161 | -121.3531 | -78.4149 | 121.3715 | 42.9428 | 6.0471 | 42.9382
2944.2969 | 121.6232 | -43.0115 | 78.2547 | -0.0057221 | 6.9748 | 0.069876 | 0.091273 | -0.00079049 | 0.0041294 | 0.021127 | -0.0089723 | 0.021484 | -1.4546 | 0.0026468 | -0.001991 | 0.014466 | 0.00061949 | -36.9278 | 78.1174 | -42.9794 | 78.4058 | -40.3748 | -42.0868 | -40.3564 | 0.10071 | -0.045776 | 0.064087 | 0.10529 | 0.17395 | 0.11444 | 0.17853 | 0.032044 | -0.13733 | 0.15106 | 2.6367 | 2.655 | 0.92468 | 2.623 | 0.89264 | 43.0756 | -78.3005 | -78.1494 | 43.1854 | 43.19 | 43.1259 | 0.11444 | 0.050354 | 2.6047 | 121.3852 | 0.10986 | 0.041199 | 121.0968 | -0.10986 | 121.1288 | 42.9657 | -121.2341 | -78.1906 | 121.4172 | 43.1168 | 6.0837 | 43.1122
2946.0781 | 121.6095 | -43.0527 | 78.2639 | -0.0057221 | 6.9763 | 0.067099 | 0.093195 | -0.0042083 | 0.0047702 | 0.014719 | -0.0059205 | 0.019134 | -1.4529 | 0.00051063 | -0.0066906 | 0.015321 | 0.0038239 | -36.937 | 78.1174 | -43.0115 | 78.3325 | -40.3976 | -42.128 | -40.4068 | 0.041199 | -0.045776 | 0.054932 | 0.068665 | 0.1236 | 0.086975 | 0.14191 | 0.041198 | -0.14648 | 0.068665 | 2.655 | 2.6459 | 0.92468 | 2.6047 | 0.88348 | 43.1076 | -78.3096 | -78.1952 | 43.1763 | 43.1946 | 43.1396 | 0.086975 | 0.032043 | 2.6138 | 121.344 | 0.068664 | 0.013733 | 121.1288 | -0.10071 | 121.17 | 43.0069 | -121.2753 | -78.2089 | 121.3852 | 43.1213 | 6.1157 | 43.0939
2947.8594 | 121.6187 | -43.0252 | 78.2593 | -0.0057221 | 6.9722 | 0.067099 | 0.092554 | 0.0019867 | 0.0045566 | 0.016214 | -0.0089723 | 0.019775 | -1.4525 | 0.0011514 | -0.0024182 | 0.015962 | 0.0012603 | -36.9141 | 78.154 | -43.0069 | 78.3325 | -40.4114 | -42.1417 | -40.4205 | 0.027466 | -0.027466 | 0.050354 | 0.086975 | 0.14648 | 0.082397 | 0.1831 | 0.018311 | -0.10528 | 0.073243 | 2.6138 | 2.6047 | 0.88348 | 2.5864 | 0.86517 | 43.0756 | -78.2867 | -78.1723 | 43.1717 | 43.2083 | 43.1076 | 0.13275 | 0.032043 | 2.5955 | 121.3394 | 0.09613 | 0.036621 | 121.1609 | -0.07782 | 121.1792 | 42.9977 | -121.2662 | -78.2089 | 121.3577 | 43.1122 | 6.1111 | 43.0527
2949.5781 | 121.6599 | -43.1671 | 78.1311 | -0.0057221 | 6.9718 | 0.066031 | 0.090845 | -0.0010041 | 0.0051974 | 0.020273 | -0.0028687 | 0.018493 | -1.4529 | 0.0032876 | -0.0051954 | 0.01233 | 0.0010467 | -36.9553 | 78.0121 | -43.0984 | 78.2913 | -40.4251 | -42.1463 | -40.4343 | 0.13275 | -0.027466 | 0.091553 | 0.10529 | 0.21515 | 0.14648 | 0.18768 | 0.068664 | -0.11902 | 0.16022 | 2.742 | 2.7328 | 1.0208 | 2.6642 | 0.95215 | 43.2587 | -78.1586 | -78.0258 | 43.3823 | 43.3548 | 43.3136 | 0.09613 | 0.054931 | 2.6733 | 121.3898 | 0.1236 | 0.013733 | 121.1105 | -0.11902 | 121.1792 | 43.1396 | -121.2296 | -78.0396 | 121.4584 | 43.2724 | 6.2119 | 43.2999
2951.3906 | 121.55 | -43.2678 | 78.1265 | -0.0057221 | 6.9739 | 0.067526 | 0.091486 | 0.00027771 | 0.0049838 | 0.020059 | -0.0059205 | 0.022339 | -1.4516 | 0.0056374 | -0.0056226 | 0.012758 | -0.0038665 | -37.0468 | 78.0075 | -43.2037 | 78.1174 | -40.6586 | -42.3614 | -40.6586 | -0.045776 | 0 | 0.036621 | 0.018311 | 0.059509 | -0.013733 | 0.09613 | 0.064087 | -0.11902 | -0.009155 | 2.6093 | 2.6093 | 0.90637 | 2.5452 | 0.84229 | 43.3044 | -78.1265 | -78.1082 | 43.3273 | 43.364 | 43.2541 | 0.059509 | -0.050354 | 2.5452 | 121.3211 | 0.022888 | -0.01831 | 121.2112 | -0.036621 | 121.2753 | 43.2678 | -121.3303 | -78.0899 | 121.3852 | 43.2861 | 6.221 | 43.222
2953.1094 | 121.6553 | -43.2678 | 78.0304 | -0.013352 | 6.9733 | 0.065176 | 0.091273 | -0.0027131 | 0.0030612 | 0.01835 | -0.0028687 | 0.020202 | -1.4525 | 0.0035012 | -0.0090406 | 0.01468 | -0.0017303 | -37.0514 | 77.9068 | -43.2266 | 78.1448 | -40.5899 | -42.2882 | -40.5853 | 0.054932 | -0.027466 | 0.054932 | 0.11444 | 0.16937 | 0.14648 | 0.20142 | 0.041198 | -0.1236 | 0.11444 | 2.6779 | 2.6825 | 0.97961 | 2.6413 | 0.93842 | 43.3228 | -78.0579 | -77.916 | 43.4372 | 43.4692 | 43.4143 | 0.14648 | 0.091552 | 2.6367 | 121.3715 | 0.11444 | 0.059509 | 121.1334 | -0.082398 | 121.1746 | 43.2404 | -121.257 | -77.9755 | 121.4127 | 43.3823 | 6.2164 | 43.3228
2954.9062 | 121.5408 | -43.3411 | 78.0533 | 0.0019074 | 6.9733 | 0.066031 | 0.092554 | -0.0037811 | 0.0039158 | 0.016428 | -0.0089723 | 0.024261 | -1.451 | -0.0016256 | -0.004768 | 0.013826 | 0.0029693 | -37.088 | 77.9343 | -43.3136 | 78.0167 | -40.7364 | -42.4622 | -40.7547 | -0.041199 | 0.022888 | 0.036621 | 0.009155 | 0.050354 | -0.009155 | 0.10529 | 0.027465 | -0.11902 | -0.036621 | 2.6047 | 2.5864 | 0.87891 | 2.5589 | 0.85144 | 43.3777 | -78.0304 | -78.0441 | 43.3914 | 43.4464 | 43.3319 | 0.068665 | -0.045776 | 2.5772 | 121.3303 | 0.013733 | -0.027466 | 121.2479 | -0.013733 | 121.2753 | 43.364 | -121.3669 | -78.0167 | 121.3577 | 43.3502 | 6.2531 | 43.2999
2956.6875 | 121.5363 | -43.3548 | 78.0579 | -0.02861 | 6.9752 | 0.067526 | 0.091059 | 0.0019867 | 0.0022068 | 0.017069 | -0.0028687 | 0.020843 | -1.4531 | -0.010171 | -0.010322 | 0.011049 | 0.00083309 | -37.0468 | 77.9251 | -43.2953 | 78.0533 | -40.686 | -42.4118 | -40.7227 | -0.045776 | 0.013733 | 0.036621 | -0.018311 | 0.054932 | 0.009155 | 0.091553 | 0.059509 | -0.13275 | -0.004577 | 2.6688 | 2.6321 | 0.94299 | 2.5726 | 0.88348 | 43.3914 | -78.0441 | -78.0762 | 43.4097 | 43.4463 | 43.364 | 0.054932 | -0.027466 | 2.6093 | 121.3486 | 0.018311 | -0.054932 | 121.2204 | -0.022888 | 121.2799 | 43.3685 | -121.3531 | -78.0212 | 121.4081 | 43.3365 | 6.308 | 43.309
2958.4531 | 121.6507 | -43.2724 | 78.0807 | 0.0019074 | 6.9748 | 0.064963 | 0.091273 | 0.0024139 | 0.0037022 | 0.021127 | -0.0089723 | 0.019775 | -1.4529 | 0.0041422 | -0.0073316 | 0.014039 | 0.0021149 | -36.9232 | 77.8793 | -43.1992 | 78.1952 | -40.5212 | -42.2607 | -40.5899 | 0.11902 | -0.018311 | 0.10071 | 0.11902 | 0.20599 | 0.16022 | 0.19226 | 0.073242 | -0.20142 | 0.11444 | 2.7512 | 2.6825 | 1.0117 | 2.6093 | 0.93842 | 43.3731 | -78.0991 | -77.9617 | 43.4784 | 43.4647 | 43.4326 | 0.091553 | 0.059509 | 2.6779 | 121.3943 | 0.10529 | 0.018311 | 121.0785 | -0.11902 | 121.1517 | 43.2541 | -121.2799 | -77.98 | 121.4676 | 43.3914 | 6.3492 | 43.3914
2960.1875 | 121.5454 | -43.3228 | 78.0899 | -0.0057221 | 6.9733 | 0.063681 | 0.091913 | -0.0024995 | 0.0030612 | 0.02305 | -0.0028687 | 0.021698 | -1.4514 | 0.0024332 | -0.0077588 | 0.012117 | 0.0010467 | -36.9598 | 77.9434 | -43.2632 | 78.0533 | -40.6723 | -42.3843 | -40.7227 | -0.054932 | 0.022888 | 0.050354 | 0.009155 | 0.073242 | 0.027466 | 0.1236 | 0.059509 | -0.14648 | -0.036621 | 2.6505 | 2.6001 | 0.93842 | 2.5406 | 0.87891 | 43.3731 | -78.067 | -78.0807 | 43.396 | 43.4464 | 43.3502 | 0.073242 | -0.022888 | 2.5909 | 121.3165 | 0.022888 | -0.041199 | 121.2067 | -0.027466 | 121.2662 | 43.3456 | -121.3531 | -78.0396 | 121.376 | 43.3319 | 6.3629 | 43.2678
2961.9688 | 121.5271 | -43.364 | 78.0029 | -0.013352 | 6.9769 | 0.066458 | 0.092982 | 0.0017731 | 0.0049838 | 0.016428 | -0.0059205 | 0.022979 | -1.4508 | -0.0018394 | -0.0051954 | 0.012971 | 0.0019013 | -36.9827 | 77.8748 | -43.3136 | 77.9846 | -40.7181 | -42.4896 | -40.8142 | -0.013733 | 0.027466 | 0.068665 | 0.027466 | 0.054932 | 0.004578 | 0.10986 | 0.050354 | -0.12817 | -0.018311 | 2.6459 | 2.5497 | 0.87433 | 2.4994 | 0.82398 | 43.4326 | -77.9755 | -77.9755 | 43.4189 | 43.4738 | 43.3685 | 0.041198 | -0.064087 | 2.5955 | 121.2982 | -0.013733 | -0.041199 | 121.1884 | -0.041199 | 121.2387 | 43.3914 | -121.3165 | -77.9343 | 121.3486 | 43.3914 | 6.3812 | 43.3502
2963.7656 | 121.669 | -43.2724 | 78.0029 | -0.020981 | 6.9737 | 0.063681 | 0.089991 | -0.00079049 | 0.0032748 | 0.021768 | -0.0059205 | 0.019348 | -1.4531 | 0.0015786 | -0.0066906 | 0.01468 | -2.1314e-05 | -36.8591 | 77.8473 | -43.2541 | 78.1677 | -40.5121 | -42.2791 | -40.6036 | 0.11902 | -0.009155 | 0.10071 | 0.11902 | 0.21973 | 0.1831 | 0.21515 | 0.018311 | -0.15564 | 0.16479 | 2.7603 | 2.6688 | 0.99335 | 2.6505 | 0.97504 | 43.3731 | -78.0121 | -77.8839 | 43.4921 | 43.4875 | 43.4555 | 0.11444 | 0.082397 | 2.742 | 121.4218 | 0.11902 | 0.018311 | 121.1014 | -0.10986 | 121.1197 | 43.2632 | -121.257 | -77.9022 | 121.4401 | 43.3914 | 6.4133 | 43.3914
2965.4844 | 121.5591 | -43.4143 | 77.9984 | -0.0057221 | 6.9744 | 0.065817 | 0.090845 | -0.0010041 | 0.0028476 | 0.016641 | -0.0028687 | 0.021057 | -1.451 | 0.0052102 | -0.0073316 | 0.01233 | 0.00061949 | -36.9232 | 77.8061 | -43.3502 | 78.0121 | -40.6952 | -42.4393 | -40.7776 | 0.004578 | 0.009155 | 0.068665 | 0.022888 | 0.09613 | 0.050354 | 0.10529 | 0.064087 | -0.19226 | 0.013733 | 2.7191 | 2.6367 | 0.97504 | 2.5726 | 0.91095 | 43.483 | -77.9892 | -77.9755 | 43.5104 | 43.5196 | 43.4647 | 0.036621 | -0.018311 | 2.655 | 121.3623 | 0.027465 | -0.045777 | 121.1563 | -0.05951 | 121.2204 | 43.4235 | -121.3486 | -77.9297 | 121.4264 | 43.4372 | 6.4911 | 43.4189
2967.2812 | 121.5363 | -43.3548 | 78.0487 | -0.013352 | 6.9731 | 0.066672 | 0.090204 | -0.0029267 | 0.0032748 | 0.018778 | 0.00018312 | 0.021698 | -1.4514 | -0.00098477 | -0.008827 | 0.011262 | -0.0015167 | -36.9049 | 77.8976 | -43.2999 | 78.0121 | -40.686 | -42.4118 | -40.7639 | -0.054932 | 0.022888 | 0.073242 | 0.004578 | 0.064087 | 0.032043 | 0.086975 | 0.054931 | -0.15106 | -0.036621 | 2.6688 | 2.5909 | 0.94299 | 2.536 | 0.88806 | 43.428 | -78.0258 | -78.0441 | 43.4189 | 43.4418 | 43.3868 | 0.013733 | -0.041199 | 2.6138 | 121.312 | -0.009155 | -0.068664 | 121.1975 | -0.050354 | 121.2524 | 43.3777 | -121.3486 | -77.9755 | 121.3669 | 43.3594 | 6.4499 | 43.2999
2969.0625 | 121.669 | -43.2861 | 77.98 | -0.013352 | 6.9754 | 0.066672 | 0.0917 | -0.0018585 | 0.0047702 | 0.014078 | 0.00018312 | 0.019561 | -1.4536 | 0.00051063 | -0.00028199 | 0.01468 | 0.0014741 | -36.8225 | 77.8885 | -43.2495 | 78.1357 | -40.5579 | -42.3431 | -40.6723 | 0.10529 | -0.009155 | 0.10071 | 0.15106 | 0.19226 | 0.14191 | 0.23804 | 0.036621 | -0.091553 | 0.15564 | 2.7283 | 2.6138 | 0.94299 | 2.5772 | 0.90637 | 43.3868 | -77.9892 | -77.829 | 43.4784 | 43.5242 | 43.428 | 0.13733 | 0.041199 | 2.6917 | 121.3852 | 0.091553 | 0.050354 | 121.138 | -0.10986 | 121.1746 | 43.277 | -121.2296 | -77.8793 | 121.4218 | 43.4372 | 6.4636 | 43.3914
2970.8594 | 121.5363 | -43.2632 | 78.1311 | -0.0057221 | 6.9769 | 0.069876 | 0.092768 | 0.0026275 | 0.0041294 | 0.016641 | 0.00018312 | 0.021698 | -1.4519 | -0.0044028 | -0.0062634 | 0.014466 | -0.00044851 | -36.7722 | 78.0029 | -43.1946 | 78.1174 | -40.6082 | -42.3889 | -40.7181 | -0.045776 | 0.027466 | 0.073242 | 0.022888 | 0.045776 | -0.009155 | 0.10529 | 0.068665 | -0.12817 | -0.013733 | 2.655 | 2.5452 | 0.87433 | 2.4765 | 0.80566 | 43.3365 | -78.1036 | -78.1082 | 43.309 | 43.3685 | 43.2541 | 0.032044 | -0.082397 | 2.5864 | 121.312 | -0.027466 | -0.050354 | 121.1975 | -0.045776 | 121.2662 | 43.2907 | -121.3257 | -78.0579 | 121.3806 | 43.2861 | 6.4911 | 43.2175
2972.5625 | 121.5363 | -43.309 | 78.1036 | -0.0057221 | 6.9769 | 0.067099 | 0.092341 | 0.00091851 | 0.0049838 | 0.019418 | -0.0059205 | 0.022766 | -1.4523 | -0.0086752 | -0.0043408 | 0.014466 | -0.0010895 | -36.8042 | 77.9984 | -43.2587 | 78.0441 | -40.6631 | -42.4438 | -40.773 | -0.068665 | 0.022888 | 0.068665 | 0.022888 | 0.045776 | -0.018311 | 0.10529 | 0.050354 | -0.10529 | -0.05951 | 2.6459 | 2.536 | 0.86517 | 2.4857 | 0.81482 | 43.3777 | -78.0808 | -78.0808 | 43.3548 | 43.4143 | 43.2907 | 0.036621 | -0.086976 | 2.5955 | 121.3028 | -0.022889 | -0.045777 | 121.257 | -0.045777 | 121.3074 | 43.3319 | -121.3623 | -78.035 | 121.3531 | 43.3319 | 6.5048 | 43.2404
2974.3438 | 121.637 | -43.2175 | 78.1494 | -0.020981 | 6.9722 | 0.066885 | 0.090632 | -0.0024995 | 0.0030612 | 0.018991 | -0.0089723 | 0.018707 | -1.4527 | -0.0011984 | -0.0041272 | 0.015748 | 0.0031829 | -36.6898 | 78.0167 | -43.1442 | 78.2227 | -40.4572 | -42.247 | -40.5945 | 0.032043 | 0.004578 | 0.091553 | 0.091553 | 0.15106 | 0.11444 | 0.18768 | 0.073242 | -0.13275 | 0.073242 | 2.7603 | 2.623 | 0.97046 | 2.5497 | 0.89722 | 43.309 | -78.1448 | -78.0579 | 43.3685 | 43.4052 | 43.3319 | 0.09613 | 0.022888 | 2.6871 | 121.3669 | 0.059509 | 0 | 121.1609 | -0.086975 | 121.2341 | 43.222 | -121.2936 | -78.0579 | 121.4401 | 43.309 | 6.5277 | 43.2495
2976.1406 | 121.6736 | -43.1946 | 78.1631 | -0.0057221 | 6.9739 | 0.069235 | 0.091059 | 0.00091851 | 0.0051974 | 0.018137 | -0.0028687 | 0.020416 | -1.4531 | 0.0035012 | -0.0045544 | 0.014253 | 0.0042511 | -36.5982 | 77.9984 | -43.1351 | 78.2776 | -40.3839 | -42.1875 | -40.5441 | 0.11444 | -0.009155 | 0.10071 | 0.1236 | 0.1831 | 0.15106 | 0.2243 | 0.059509 | -0.16479 | 0.11444 | 2.8107 | 2.6505 | 1.0071 | 2.5909 | 0.94757 | 43.2953 | -78.1723 | -78.0396 | 43.3777 | 43.4189 | 43.3456 | 0.1236 | 0.050354 | 2.7512 | 121.4127 | 0.082397 | 0.022888 | 121.1334 | -0.10986 | 121.1929 | 43.1854 | -121.2982 | -78.0624 | 121.4722 | 43.3182 | 6.5964 | 43.309
2977.9219 | 121.5591 | -43.1717 | 78.2639 | -0.020981 | 6.9731 | 0.064536 | 0.090418 | 0.0032685 | 0.0041294 | 0.018137 | -0.0059205 | 0.022552 | -1.4538 | -0.0058982 | -0.011604 | 0.011689 | -0.00023491 | -36.6165 | 78.1174 | -43.1305 | 78.1998 | -40.4526 | -42.2241 | -40.5899 | -0.054932 | 0.054932 | 0.07782 | 0.004578 | 0.068665 | 0.032043 | 0.10986 | 0.041199 | -0.14648 | -0.064087 | 2.7191 | 2.5818 | 0.94757 | 2.5406 | 0.90637 | 43.2495 | -78.2089 | -78.2593 | 43.2404 | 43.2816 | 43.2037 | 0.032043 | -0.045777 | 2.6779 | 121.3303 | -0.009155 | -0.073242 | 121.2479 | -0.022888 | 121.2891 | 43.2266 | -121.3943 | -78.186 | 121.3715 | 43.1763 | 6.5552 | 43.1168
2979.6875 | 121.5363 | -43.1763 | 78.2501 | -0.0057221 | 6.978 | 0.069022 | 0.093836 | 0.0039093 | 0.0049838 | 0.017282 | -0.0059205 | 0.022766 | -1.4514 | -0.00077117 | -0.0049818 | 0.014253 | -0.0025849 | -36.5616 | 78.1082 | -43.1213 | 78.2089 | -40.4984 | -42.3065 | -40.6448 | -0.07782 | 0.041199 | 0.068665 | 0.018311 | 0.027466 | 0 | 0.10986 | 0.054932 | -0.14191 | -0.041199 | 2.6779 | 2.5314 | 0.86975 | 2.4765 | 0.81482 | 43.2449 | -78.2089 | -78.2318 | 43.2037 | 43.2861 | 43.1763 | 0.041198 | -0.068665 | 2.623 | 121.3303 | -0.041199 | -0.050354 | 121.2296 | -0.027466 | 121.2845 | 43.2175 | -121.3715 | -78.1815 | 121.3852 | 43.1946 | 6.6147 | 43.0984
2981.4219 | 121.6599 | -43.071 | 78.3279 | -0.020981 | 6.972 | 0.067313 | 0.089136 | -0.0020721 | 0.005411 | 0.018564 | -0.0028687 | 0.019348 | -1.4533 | 0.0043558 | -0.0045544 | 0.013612 | -0.00066231 | -36.4288 | 78.1723 | -42.9886 | 78.3691 | -40.2878 | -42.1143 | -40.4755 | 0.027466 | 0.004578 | 0.086975 | 0.07782 | 0.16022 | 0.11902 | 0.16479 | 0.082398 | -0.15564 | 0.041199 | 2.7832 | 2.5955 | 0.95673 | 2.5131 | 0.87433 | 43.158 | -78.3234 | -78.2501 | 43.2312 | 43.2358 | 43.19 | 0.07782 | 0.032044 | 2.7008 | 121.3577 | 0.073242 | -0.009155 | 121.1609 | -0.082397 | 121.2433 | 43.0756 | -121.3165 | -78.241 | 121.4401 | 43.1488 | 6.6422 | 43.0984
2983.2031 | 121.6049 | -43.0252 | 78.3966 | 0.0019074 | 6.9767 | 0.066458 | 0.091913 | 0.0017731 | 0.0030612 | 0.018137 | -0.0028687 | 0.022125 | -1.4512 | 0.0024332 | -0.0056226 | 0.014466 | -0.00087591 | -36.2961 | 78.241 | -42.9657 | 78.4149 | -40.2328 | -42.0593 | -40.416 | 0.054932 | 0.022888 | 0.07782 | 0.082397 | 0.1236 | 0.082397 | 0.16937 | 0.05951 | -0.15564 | 0.018311 | 2.7924 | 2.6093 | 0.96588 | 2.5497 | 0.90637 | 43.103 | -78.3737 | -78.3142 | 43.1488 | 43.1946 | 43.1076 | 0.091553 | 0.004577 | 2.7328 | 121.3806 | 0.045776 | 0.004577 | 121.2067 | -0.054932 | 121.2662 | 43.0481 | -121.3623 | -78.3188 | 121.4401 | 43.1076 | 6.7291 | 43.0801
2984.9219 | 121.5546 | -43.1671 | 78.2867 | -0.013352 | 6.9748 | 0.065817 | 0.092341 | 0.0022003 | 0.002634 | 0.01835 | 0.00018312 | 0.020416 | -1.4531 | -0.0073936 | -0.0024182 | 0.01468 | 0.0044647 | -36.4563 | 78.1677 | -43.0847 | 78.2135 | -40.448 | -42.2745 | -40.6448 | -0.068665 | 0.027466 | 0.064087 | 0.022888 | 0.032043 | -0.009155 | 0.11444 | 0.082397 | -0.11902 | -0.073242 | 2.7191 | 2.5223 | 0.89264 | 2.4399 | 0.81024 | 43.2312 | -78.2593 | -78.2639 | 43.1992 | 43.2816 | 43.158 | 0.050354 | -0.073242 | 2.6367 | 121.2982 | -0.032044 | -0.041199 | 121.2524 | -0.036621 | 121.3348 | 43.1946 | -121.3715 | -78.2227 | 121.3806 | 43.19 | 6.7108 | 43.0984
2986.7188 | 121.7148 | -43.0298 | 78.3325 | -0.013352 | 6.9727 | 0.064108 | 0.088068 | -0.0018585 | 0.0013522 | 0.016428 | 0.00018312 | 0.022766 | -1.4546 | 0.0049966 | -0.006477 | 0.013612 | -0.0015167 | -36.2778 | 78.186 | -42.984 | 78.4561 | -40.1505 | -41.9952 | -40.3793 | 0.1236 | 0 | 0.09613 | 0.15564 | 0.21057 | 0.16479 | 0.22888 | 0.045776 | -0.14648 | 0.1236 | 2.8793 | 2.6505 | 1.0345 | 2.6047 | 0.98877 | 43.1259 | -78.3325 | -78.1769 | 43.2404 | 43.2587 | 43.1946 | 0.13275 | 0.068665 | 2.8336 | 121.4401 | 0.11444 | 0.05951 | 121.17 | -0.09613 | 121.2158 | 43.0298 | -121.3165 | -78.2364 | 121.4859 | 43.1854 | 6.752 | 43.1534
2988.4219 | 121.6873 | -42.952 | 78.4012 | 0.0019074 | 6.9742 | 0.066672 | 0.090632 | -0.00036309 | 0.0041294 | 0.016 | -0.0028687 | 0.019134 | -1.4519 | 0.0045694 | -0.0056226 | 0.013826 | -0.00087591 | -36.2091 | 78.2455 | -42.9016 | 78.4836 | -40.1321 | -41.9724 | -40.3427 | 0.073242 | -0.004578 | 0.07782 | 0.13275 | 0.21973 | 0.17395 | 0.21515 | 0.050354 | -0.15564 | 0.082398 | 2.8198 | 2.6093 | 0.97961 | 2.5589 | 0.92926 | 43.0298 | -78.4058 | -78.2684 | 43.1717 | 43.1671 | 43.1259 | 0.13733 | 0.09613 | 2.7695 | 121.3852 | 0.14191 | 0.054931 | 121.1472 | -0.082398 | 121.1975 | 42.9474 | -121.3028 | -78.3234 | 121.4355 | 43.0847 | 6.7429 | 43.0252
2990.2031 | 121.6873 | -42.9382 | 78.4058 | -0.013352 | 6.9739 | 0.063681 | 0.089777 | 0.0011321 | 0.0039158 | 0.018778 | -0.0028687 | 0.018493 | -1.4529 | 0.0060648 | -0.005409 | 0.013826 | -0.0025849 | -36.1359 | 78.241 | -42.8833 | 78.5431 | -40.0452 | -41.9174 | -40.3061 | 0.10986 | -0.009155 | 0.10071 | 0.13275 | 0.21973 | 0.16479 | 0.21057 | 0.054931 | -0.16479 | 0.13733 | 2.8931 | 2.6321 | 1.0208 | 2.5772 | 0.96588 | 43.0389 | -78.4149 | -78.273 | 43.158 | 43.1488 | 43.103 | 0.10986 | 0.064087 | 2.8381 | 121.4264 | 0.11902 | 0.032043 | 121.1243 | -0.10986 | 121.1792 | 42.9291 | -121.2891 | -78.3051 | 121.4813 | 43.071 | 6.8024 | 43.0481
2991.9844 | 121.5591 | -42.9153 | 78.511 | -0.0057221 | 6.9744 | 0.067526 | 0.094263 | -0.00014949 | 0.0041294 | 0.019205 | -0.0059205 | 0.022339 | -1.4525 | -0.0052572 | -0.0037 | 0.013185 | 0.0021149 | -36.1267 | 78.3508 | -42.9108 | 78.4332 | -40.1871 | -42.0776 | -40.4251 | -0.064087 | 0.022888 | 0.041199 | 0.009155 | 0.027466 | -0.022888 | 0.10986 | 0.004577 | -0.16022 | -0.077819 | 2.7283 | 2.4902 | 0.83771 | 2.4857 | 0.83313 | 42.9565 | -78.4882 | -78.5019 | 42.9428 | 43.0252 | 42.8925 | 0.068664 | -0.064087 | 2.7237 | 121.344 | -0.013733 | -0.032044 | 121.2616 | -0.018311 | 121.2662 | 42.9382 | -121.4218 | -78.4698 | 121.3486 | 42.9245 | 6.7886 | 42.8513
2993.7031 | 121.6873 | -42.8925 | 78.4744 | -0.02861 | 6.9731 | 0.065817 | 0.090418 | -0.0016449 | 0.0032748 | 0.017496 | -0.0028687 | 0.018921 | -1.4523 | 0.00093783 | -0.0079724 | 0.014466 | -0.00066231 | -35.9985 | 78.2959 | -42.8696 | 78.598 | -39.9628 | -41.8488 | -40.2512 | 0.11444 | -0.022888 | 0.10529 | 0.11902 | 0.20599 | 0.16022 | 0.20142 | 0.022888 | -0.17853 | 0.1236 | 2.9297 | 2.6413 | 1.0437 | 2.6184 | 1.0208 | 42.9977 | -78.4973 | -78.3554 | 43.0984 | 43.0939 | 43.0527 | 0.09613 | 0.054931 | 2.9068 | 121.4676 | 0.10071 | 0.013733 | 121.1655 | -0.12817 | 121.1884 | 42.8696 | -121.344 | -78.3691 | 121.4905 | 43.0115 | 6.8939 | 43.0069
2995.4688 | 121.6507 | -42.8421 | 78.5385 | 0.0019074 | 6.9748 | 0.067313 | 0.089777 | -0.0039947 | 0.0017796 | 0.01835 | -0.0028687 | 0.019775 | -1.4516 | 0.0069192 | -0.0039136 | 0.014466 | 0.0019013 | -35.9161 | 78.3829 | -42.746 | 78.6255 | -39.917 | -41.8488 | -40.2466 | 0.082397 | -0.009155 | 0.10071 | 0.10529 | 0.16479 | 0.10986 | 0.1831 | 0.09613 | -0.15564 | 0.086975 | 2.9251 | 2.5955 | 0.99335 | 2.4994 | 0.89722 | 42.9428 | -78.5477 | -78.4332 | 43.0069 | 43.0252 | 42.952 | 0.082397 | 0.009155 | 2.829 | 121.3715 | 0.064087 | 0.004578 | 121.1288 | -0.10986 | 121.225 | 42.8329 | -121.2845 | -78.4378 | 121.4676 | 42.9474 | 6.926 | 42.9245
2997.25 | 121.6599 | -42.8284 | 78.5385 | -0.013352 | 6.9744 | 0.067526 | 0.091059 | -0.0010041 | 0.0037022 | 0.018564 | -0.0028687 | 0.020843 | -1.4529 | 0.0022196 | -0.0090406 | 0.012117 | 0.0042511 | -35.8795 | 78.3691 | -42.7643 | 78.6621 | -39.9216 | -41.8259 | -40.2328 | 0.064087 | 0.004578 | 0.091553 | 0.10529 | 0.17853 | 0.12817 | 0.17395 | 0.064087 | -0.16937 | 0.1236 | 2.9068 | 2.5955 | 1.0025 | 2.5314 | 0.93841 | 42.9199 | -78.5339 | -78.4332 | 43.0069 | 43.0023 | 42.9565 | 0.082397 | 0.036621 | 2.8427 | 121.4264 | 0.086975 | 0.013733 | 121.1334 | -0.086975 | 121.1975 | 42.8329 | -121.3028 | -78.447 | 121.4905 | 42.9337 | 6.9489 | 42.8925
2999.0312 | 121.5912 | -42.9062 | 78.4836 | 0.0019074 | 6.9756 | 0.066245 | 0.092554 | 0.0043365 | 0.0037022 | 0.017923 | -0.0028687 | 0.021698 | -1.4512 | 0.0026468 | -0.0058362 | 0.012971 | 0.0029693 | -35.9482 | 78.3737 | -42.8925 | 78.479 | -40.1001 | -42.0227 | -40.4114 | -0.036621 | 0.032043 | 0.064087 | 0.032043 | 0.064087 | -0.004578 | 0.13733 | 0.013733 | -0.10986 | -0.004578 | 2.8061 | 2.4948 | 0.88348 | 2.4811 | 0.86975 | 42.9703 | -78.4515 | -78.4515 | 42.9703 | 43.0435 | 42.9016 | 0.073242 | -0.068665 | 2.7924 | 121.3715 | 0 | -0.032044 | 121.2662 | -0.032044 | 121.2799 | 42.9382 | -121.376 | -78.4195 | 121.3852 | 42.9382 | 6.958 | 42.8696
3000.75 | 121.6919 | -42.9016 | 78.4424 | -0.0057221 | 6.9709 | 0.068167 | 0.092554 | -0.0031403 | 0.0058384 | 0.016428 | -0.0028687 | 0.019775 | -1.4536 | 0.0058512 | -0.0026318 | 0.015107 | 0.00040589 | -35.9024 | 78.3554 | -42.8604 | 78.5385 | -40.0269 | -41.9632 | -40.3519 | 0.073242 | 0.004578 | 0.10071 | 0.13275 | 0.17395 | 0.11902 | 0.21973 | 0.041198 | -0.086975 | 0.09613 | 2.8748 | 2.5497 | 0.93841 | 2.5085 | 0.89722 | 43.0023 | -78.4378 | -78.3096 | 43.0756 | 43.1213 | 43.0206 | 0.11902 | 0.018311 | 2.8336 | 121.3989 | 0.073242 | 0.032043 | 121.2158 | -0.09613 | 121.257 | 42.9062 | -121.3028 | -78.3417 | 121.4401 | 43.0344 | 6.9992 | 42.9749
3002.5312 | 121.5683 | -42.8558 | 78.5934 | -0.0057221 | 6.9718 | 0.064749 | 0.089777 | -0.0039947 | 0.005411 | 0.017496 | -0.0059205 | 0.021057 | -1.4525 | -0.0018394 | -0.011177 | 0.012544 | 0.0019013 | -35.8292 | 78.447 | -42.8101 | 78.5477 | -40.0223 | -41.9128 | -40.3427 | -0.050354 | 0.050354 | 0.068665 | -0.004578 | 0.07782 | 0.018311 | 0.1236 | 0.045776 | -0.14648 | -0.045777 | 2.8336 | 2.5131 | 0.94299 | 2.4673 | 0.89722 | 42.9245 | -78.5431 | -78.598 | 42.9337 | 42.9794 | 42.8741 | 0.054931 | -0.050354 | 2.7878 | 121.3577 | 0.009155 | -0.073243 | 121.257 | -0.018311 | 121.3028 | 42.9062 | -121.4035 | -78.5248 | 121.4035 | 42.8513 | 7.0267 | 42.8055
3004.2656 | 121.7377 | -42.746 | 78.6026 | -0.013352 | 6.9729 | 0.065176 | 0.090845 | -0.0027131 | 0.0041294 | 0.019632 | -0.0028687 | 0.018066 | -1.4521 | 0.0086282 | -0.008827 | 0.014466 | 0.0021149 | -35.6552 | 78.4378 | -42.7139 | 78.7445 | -39.7659 | -41.7252 | -40.155 | 0.15106 | 0.009155 | 0.1236 | 0.14191 | 0.2243 | 0.17395 | 0.23346 | 0.032044 | -0.16479 | 0.14191 | 2.98 | 2.5909 | 1.0208 | 2.5589 | 0.98877 | 42.8696 | -78.5934 | -78.4607 | 42.9703 | 42.9794 | 42.9199 | 0.10986 | 0.050354 | 2.948 | 121.4584 | 0.10071 | 0.018311 | 121.1517 | -0.11444 | 121.1838 | 42.7551 | -121.3165 | -78.479 | 121.4905 | 42.8879 | 7.0908 | 42.897
3006.0469 | 121.5866 | -42.8192 | 78.6346 | 0.0019074 | 6.9742 | 0.066885 | 0.091059 | -0.0031403 | 0.0039158 | 0.016855 | 0.00018312 | 0.022552 | -1.4536 | 0.0028604 | -0.0077588 | 0.010835 | -2.1314e-05 | -35.6827 | 78.5019 | -42.7597 | 78.5889 | -39.9307 | -41.8625 | -40.2695 | -0.041199 | 0.041199 | 0.059509 | 0.018311 | 0.064087 | 0.032043 | 0.13275 | 0.059509 | -0.13275 | -0.045777 | 2.8885 | 2.5497 | 0.95673 | 2.4902 | 0.89722 | 42.8787 | -78.5934 | -78.6163 | 42.8833 | 42.952 | 42.8513 | 0.073242 | -0.027466 | 2.829 | 121.3486 | 0.004578 | -0.041198 | 121.2616 | -0.01831 | 121.3211 | 42.8604 | -121.3943 | -78.5751 | 121.4081 | 42.8375 | 7.1365 | 42.778
3007.7656 | 121.7148 | -42.7414 | 78.5934 | -0.0057221 | 6.9714 | 0.066031 | 0.088282 | -0.0033539 | 0.0028476 | 0.018778 | -0.0028687 | 0.02063 | -1.4521 | 0.0067056 | -0.0060498 | 0.015107 | -0.00044851 | -35.5774 | 78.4332 | -42.7094 | 78.7262 | -39.7751 | -41.7297 | -40.1825 | 0.10986 | -0.013733 | 0.10071 | 0.14648 | 0.23346 | 0.17853 | 0.21973 | 0.032043 | -0.16022 | 0.13275 | 2.9663 | 2.5589 | 1.0117 | 2.5269 | 0.97961 | 42.8421 | -78.6072 | -78.447 | 42.9749 | 42.9611 | 42.9199 | 0.11902 | 0.07782 | 2.9343 | 121.4355 | 0.13275 | 0.045776 | 121.1426 | -0.11444 | 121.1746 | 42.7277 | -121.3028 | -78.4927 | 121.4676 | 42.8879 | 7.164 | 42.8513
3009.5312 | 121.669 | -42.8467 | 78.5339 | 0.0019074 | 6.9746 | 0.068808 | 0.091273 | -0.0016449 | 0.0045566 | 0.018778 | -0.0059205 | 0.020416 | -1.4519 | -0.0071798 | -0.0043408 | 0.012544 | 0.0046783 | -35.6186 | 78.3463 | -42.7872 | 78.6438 | -39.8575 | -41.8488 | -40.2969 | 0.1236 | -0.027466 | 0.11444 | 0.14191 | 0.19226 | 0.14191 | 0.21515 | 0.05951 | -0.18768 | 0.10986 | 2.9892 | 2.5497 | 0.99793 | 2.4902 | 0.93842 | 42.9611 | -78.5614 | -78.392 | 43.0389 | 43.0618 | 42.9886 | 0.10071 | 0.027466 | 2.9297 | 121.431 | 0.07782 | 0.027466 | 121.1334 | -0.14191 | 121.1929 | 42.8192 | -121.3211 | -78.4195 | 121.4905 | 42.9886 | 7.2281 | 42.9703
3011.3281 | 121.6003 | -42.9291 | 78.511 | -0.0057221 | 6.9727 | 0.064963 | 0.091486 | -0.0012177 | 0.0028476 | 0.017923 | -0.0028687 | 0.021057 | -1.4521 | -0.00034397 | -0.0075452 | 0.012971 | -0.0015167 | -35.6873 | 78.3325 | -42.9108 | 78.4836 | -40.0497 | -41.9952 | -40.4434 | -0.059509 | 0.036621 | 0.073242 | 0.022888 | 0.086975 | 0.036621 | 0.13275 | 0.01831 | -0.17853 | -0.027465 | 2.8793 | 2.4857 | 0.93384 | 2.4673 | 0.91553 | 43.0023 | -78.4744 | -78.4882 | 43.0161 | 43.0618 | 42.9657 | 0.059509 | -0.036621 | 2.861 | 121.3943 | 0.013733 | -0.050354 | 121.2433 | -0.036621 | 121.2616 | 42.9657 | -121.4218 | -78.4378 | 121.4127 | 42.952 | 7.2418 | 42.8696
3013.0625 | 121.5866 | -42.5354 | 78.8818 | -0.0057221 | 6.9742 | 0.066458 | 0.092341 | 0.0015595 | 0.0028476 | 0.017923 | -0.0059205 | 0.024047 | -1.4525 | 0.0037148 | -0.0051954 | 0.016175 | 0.0029693 | -35.2753 | 78.7628 | -42.4667 | 78.9093 | -39.6011 | -41.5833 | -40.0406 | 0 | 0 | 0.059509 | 0.050354 | 0.073242 | 0.009155 | 0.11902 | 0.068664 | -0.11902 | 0.027466 | 2.9343 | 2.4948 | 0.95215 | 2.4261 | 0.88348 | 42.5949 | -78.8818 | -78.8315 | 42.6086 | 42.6544 | 42.5446 | 0.05951 | -0.050354 | 2.8656 | 121.376 | 0.013733 | -0.009155 | 121.2296 | -0.059509 | 121.2982 | 42.5354 | -121.3486 | -78.8223 | 121.4447 | 42.5858 | 7.2601 | 42.5354
3014.8438 | 121.5683 | -42.3065 | 79.1245 | 0.0019074 | 6.9718 | 0.069663 | 0.089991 | 0.00070491 | 0.0030612 | 0.018137 | -0.0059205 | 0.022125 | -1.4512 | -0.001412 | -0.0037 | 0.013185 | 0.0044647 | -35.0739 | 79.0329 | -42.215 | 79.0695 | -39.4592 | -41.423 | -39.8575 | -0.07782 | 0.018311 | 0.041199 | -0.013733 | 0.032043 | -0.050354 | 0.086975 | 0.091553 | -0.091553 | -0.054932 | 2.8473 | 2.449 | 0.88348 | 2.3575 | 0.79193 | 42.3477 | -79.1061 | -79.1382 | 42.3386 | 42.3935 | 42.2562 | 0.045776 | -0.091553 | 2.7557 | 121.2845 | -0.009156 | -0.054932 | 121.2479 | -0.022888 | 121.3394 | 42.3248 | -121.3394 | -79.0833 | 121.376 | 42.2928 | 7.2327 | 42.2287
3016.625 | 121.6873 | -42.2699 | 79.1336 | -0.0057221 | 6.9727 | 0.066458 | 0.088495 | -0.0024995 | 0.0030612 | 0.017282 | -0.0089723 | 0.021484 | -1.4563 | 0.0035012 | -0.0051954 | 0.013612 | -0.00087591 | -34.9869 | 78.923 | -42.2104 | 79.2206 | -39.2441 | -41.2491 | -39.7156 | 0.068665 | -0.045776 | 0.064087 | 0.07782 | 0.17395 | 0.12817 | 0.17395 | 0.059509 | -0.21057 | 0.086975 | 3.0258 | 2.5543 | 1.0208 | 2.4948 | 0.9613 | 42.334 | -79.1794 | -79.0558 | 42.4438 | 42.4438 | 42.3981 | 0.10986 | 0.064087 | 2.9663 | 121.431 | 0.10986 | 0.013733 | 121.1334 | -0.10986 | 121.1929 | 42.2241 | -121.344 | -79.0695 | 121.4905 | 42.3477 | 7.283 | 42.3386
3018.3281 | 121.6095 | -42.1921 | 79.2618 | -0.013352 | 6.9735 | 0.064749 | 0.091273 | -0.0012177 | 0.004343 | 0.017069 | 0.00018312 | 0.021698 | -1.4521 | 8.3226e-05 | -0.0069044 | 0.013612 | 0.0016877 | -34.8724 | 79.1336 | -42.1417 | 79.2526 | -39.2212 | -41.2079 | -39.679 | -0.07782 | -0.027466 | 0.013733 | 0.013733 | 0.059509 | -0.004578 | 0.10071 | 0.050354 | -0.12817 | -0.009155 | 2.9709 | 2.5131 | 0.98419 | 2.4628 | 0.93384 | 42.2058 | -79.2892 | -79.248 | 42.2516 | 42.2928 | 42.1875 | 0.086975 | -0.018311 | 2.9205 | 121.3943 | 0.045776 | 0 | 121.2753 | -0.041199 | 121.3257 | 42.1646 | -121.4035 | -79.248 | 121.4447 | 42.2058 | 7.3196 | 42.1143
3020.0938 | 121.7056 | -42.1371 | 79.2114 | -0.0057221 | 6.9718 | 0.066885 | 0.089991 | 0.0015595 | 0.0030612 | 0.018778 | -0.0089723 | 0.020202 | -1.4527 | -0.0018394 | -0.0024182 | 0.014466 | -0.00087591 | -34.7946 | 79.1061 | -42.0959 | 79.335 | -39.1388 | -41.1713 | -39.6423 | 0.032043 | -0.068665 | 0.045776 | 0.091553 | 0.16022 | 0.073242 | 0.16479 | 0.041199 | -0.10529 | 0.1236 | 2.9984 | 2.4948 | 0.96588 | 2.4536 | 0.92468 | 42.1829 | -79.2801 | -79.1199 | 42.2974 | 42.3019 | 42.2104 | 0.11902 | 0.027466 | 2.9572 | 121.431 | 0.11444 | 0.045777 | 121.2021 | -0.11444 | 121.2433 | 42.0685 | -121.3074 | -79.1656 | 121.4722 | 42.2287 | 7.3425 | 42.1692
3021.875 | 121.5729 | -42.247 | 79.2206 | 0.0019074 | 6.9724 | 0.066031 | 0.091273 | -0.0033539 | 0.0041294 | 0.018778 | -0.0059205 | 0.021698 | -1.4506 | 0.00029703 | -0.0083996 | 0.014039 | 0.0029693 | -34.9136 | 79.0787 | -42.1829 | 79.1702 | -39.2899 | -41.2903 | -39.7568 | -0.11902 | 0 | 0.004578 | -0.041199 | 0.022888 | -0.036621 | 0.064087 | 0.064087 | -0.14191 | -0.050354 | 2.9572 | 2.4902 | 0.95673 | 2.4261 | 0.89264 | 42.2516 | -79.2206 | -79.2618 | 42.2699 | 42.3111 | 42.2104 | 0.059509 | -0.041199 | 2.8931 | 121.3531 | 0.01831 | -0.045777 | 121.2616 | -0.004578 | 121.3257 | 42.247 | -121.4035 | -79.216 | 121.4172 | 42.2058 | 7.3334 | 42.128
3023.5781 | 121.5683 | -42.2195 | 79.2435 | -0.0057221 | 6.9729 | 0.067954 | 0.092768 | 0.00091851 | 0.0030612 | 0.017923 | -0.0059205 | 0.020202 | -1.4525 | 0.003074 | -0.0073316 | 0.014894 | 0.00061949 | -34.8495 | 79.1016 | -42.1555 | 79.1977 | -39.2624 | -41.2903 | -39.7751 | -0.054932 | -0.004578 | 0.059509 | -0.022888 | 0.027466 | -0.054932 | 0.07782 | 0.064086 | -0.14191 | -0.045776 | 2.9572 | 2.4445 | 0.92926 | 2.3804 | 0.86517 | 42.2791 | -79.248 | -79.2664 | 42.247 | 42.2974 | 42.1646 | 0.018311 | -0.11444 | 2.8931 | 121.3531 | -0.032043 | -0.082397 | 121.257 | -0.064087 | 121.3211 | 42.215 | -121.3989 | -79.184 | 121.4172 | 42.1967 | 7.37 | 42.1646
3025.3594 | 121.582 | -42.0868 | 79.3716 | 0.0019074 | 6.9742 | 0.067954 | 0.092554 | -0.0016449 | 0.0039158 | 0.018564 | -0.0089723 | 0.021057 | -1.4499 | 0.00093783 | -0.0090406 | 0.014039 | -0.0023713 | -34.6619 | 79.248 | -41.9907 | 79.3808 | -39.0427 | -41.1118 | -39.6286 | -0.036621 | 0.009155 | 0.054932 | 0.004578 | 0.054932 | -0.013733 | 0.091553 | 0.09613 | -0.1236 | 0.009155 | 3.0441 | 2.4582 | 0.97504 | 2.3621 | 0.87891 | 42.1417 | -79.3625 | -79.3671 | 42.1417 | 42.1783 | 42.0731 | 0.036621 | -0.068665 | 2.948 | 121.3715 | 0 | -0.050354 | 121.2387 | -0.045777 | 121.3348 | 42.0959 | -121.3623 | -79.3167 | 121.4676 | 42.0914 | 7.4249 | 42.0502
3027.1406 | 121.5591 | -42.0273 | 79.4449 | -0.0057221 | 6.9724 | 0.066458 | 0.091273 | -0.0029267 | 0.0037022 | 0.017923 | -0.0028687 | 0.021484 | -1.4521 | -0.00077117 | -0.007118 | 0.012758 | 0.0010467 | -34.6298 | 79.2801 | -41.9266 | 79.4037 | -39.0335 | -41.0477 | -39.5325 | -0.050354 | 0.009155 | 0.059509 | -0.018311 | 0.059509 | 0.004578 | 0.082397 | 0.10071 | -0.16479 | -0.041198 | 2.9938 | 2.4948 | 0.97961 | 2.3941 | 0.87891 | 42.0868 | -79.4357 | -79.4632 | 42.0868 | 42.1097 | 42.0319 | 0.022888 | -0.054931 | 2.8931 | 121.3303 | 0 | -0.07782 | 121.2067 | -0.050354 | 121.3074 | 42.0364 | -121.3715 | -79.3854 | 121.431 | 42.009 | 7.3975 | 41.9769
3028.9219 | 121.5591 | -41.8488 | 79.5822 | -0.0057221 | 6.975 | 0.069449 | 0.0917 | 0.0026275 | 0.0024204 | 0.018137 | 0.00018312 | 0.022766 | -1.4529 | -0.0026938 | -0.003059 | 0.013398 | -0.00044851 | -34.4421 | 79.4586 | -41.7892 | 79.5639 | -38.855 | -40.9332 | -39.4135 | -0.054932 | 0.013733 | 0.045776 | 0.009155 | 0.050354 | -0.027466 | 0.086975 | 0.059509 | -0.1236 | -0.01831 | 2.9938 | 2.4353 | 0.91553 | 2.3758 | 0.85602 | 41.8945 | -79.5685 | -79.5731 | 41.8991 | 41.9357 | 41.8213 | 0.041199 | -0.073242 | 2.9343 | 121.3531 | 0.004578 | -0.036621 | 121.2479 | -0.032043 | 121.3074 | 41.8625 | -121.3715 | -79.5364 | 121.4127 | 41.8579 | 7.4066 | 41.7938
3030.6875 | 121.6278 | -41.9357 | 79.5044 | -0.013352 | 6.9735 | 0.066245 | 0.08935 | -0.0044221 | 0.0019932 | 0.016214 | -0.0059205 | 0.019561 | -1.4519 | 0.0062784 | -0.0094678 | 0.014039 | 0.0036103 | -34.4559 | 79.3167 | -41.8625 | 79.5639 | -38.8046 | -40.8691 | -39.3906 | 0.032043 | -0.013733 | 0.073242 | 0.041199 | 0.13275 | 0.082397 | 0.13275 | 0.073242 | -0.18768 | 0.059509 | 3.1311 | 2.5452 | 1.0666 | 2.4719 | 0.99335 | 42.009 | -79.5181 | -79.4632 | 42.0685 | 42.0685 | 42.0181 | 0.059509 | 0.009155 | 3.0579 | 121.4264 | 0.059509 | -0.032043 | 121.1792 | -0.086975 | 121.2524 | 41.922 | -121.3669 | -79.4312 | 121.4996 | 41.9769 | 7.4799 | 41.9678
3032.4062 | 121.5683 | -41.7572 | 79.7241 | -0.0057221 | 6.9727 | 0.066458 | 0.090204 | 0.00027771 | 0.002634 | 0.017069 | -0.0059205 | 0.022979 | -1.4527 | -0.003762 | -0.0094678 | 0.013398 | -0.0021575 | -34.3231 | 79.5868 | -41.6656 | 79.6692 | -38.7085 | -40.773 | -39.2761 | -0.064087 | 0 | 0.022888 | -0.041199 | 0.050354 | -0.018311 | 0.086975 | 0.091553 | -0.13733 | -0.054932 | 3.0487 | 2.4811 | 0.98419 | 2.3895 | 0.89264 | 41.7801 | -79.7241 | -79.7653 | 41.8076 | 41.8442 | 41.7389 | 0.064087 | -0.041199 | 2.9572 | 121.3348 | 0.027466 | -0.064087 | 121.2524 | -0.022888 | 121.344 | 41.7572 | -121.3898 | -79.7012 | 121.4264 | 41.716 | 7.4341 | 41.6931
3034.2031 | 121.6873 | -40.3931 | 80.983 | -0.013352 | 6.9739 | 0.065604 | 0.089136 | -0.00057689 | 0.0030612 | 0.018778 | -0.0028687 | 0.019134 | -1.4555 | 0.0045694 | -0.0077588 | 0.012971 | 0.0021149 | -33.0734 | 80.8273 | -40.329 | 81.134 | -37.2849 | -39.3356 | -37.8708 | 0.064087 | -0.059509 | 0.050354 | 0.082397 | 0.17853 | 0.12817 | 0.16479 | 0.064087 | -0.15564 | 0.15106 | 3.1082 | 2.5223 | 1.0574 | 2.4582 | 0.99335 | 40.4434 | -81.0425 | -80.9006 | 40.5716 | 40.5579 | 40.5212 | 0.11444 | 0.07782 | 3.0441 | 121.463 | 0.12817 | 0.032043 | 121.1563 | -0.10986 | 121.2204 | 40.3336 | -121.3119 | -80.9326 | 121.5271 | 40.4755 | 7.3196 | 40.4572
3035.9844 | 121.6919 | -39.8026 | 81.5918 | 0.0019074 | 6.9712 | 0.067099 | 0.089136 | 0.00027771 | 0.0037022 | 0.016641 | -0.0089723 | 0.021057 | -1.4548 | 0.003074 | -0.00028199 | 0.014894 | 0.0023285 | -32.5699 | 81.4545 | -39.7202 | 81.6834 | -36.7767 | -38.8229 | -37.3261 | 0.036621 | -0.07782 | 0.036621 | 0.082397 | 0.13275 | 0.054932 | 0.16479 | 0.082397 | -0.13733 | 0.091553 | 3.0258 | 2.4765 | 0.97961 | 2.3941 | 0.89722 | 39.8392 | -81.6696 | -81.5094 | 39.9353 | 39.9673 | 39.8575 | 0.12817 | 0.018311 | 2.9434 | 121.4035 | 0.09613 | 0.045776 | 121.1746 | -0.11444 | 121.257 | 39.7247 | -121.312 | -81.5552 | 121.4859 | 39.8849 | 7.2327 | 39.8392
3037.7031 | 121.5637 | -39.8392 | 81.6284 | -0.013352 | 6.9733 | 0.066245 | 0.090418 | 0.0015595 | 0.0017796 | 0.017069 | -0.0028687 | 0.019134 | -1.451 | 0.0011514 | -0.0058362 | 0.014039 | -0.00087591 | -32.6202 | 81.459 | -39.8254 | 81.5598 | -36.8683 | -38.9099 | -37.4084 | -0.09613 | -0.022888 | 0 | -0.050354 | 0.009155 | -0.059509 | 0.045776 | 0.013733 | -0.16937 | -0.068665 | 2.9709 | 2.4307 | 0.92926 | 2.417 | 0.91553 | 39.8392 | -81.6513 | -81.6788 | 39.8483 | 39.8849 | 39.7797 | 0.045776 | -0.059509 | 2.9572 | 121.3852 | 0.009155 | -0.050354 | 121.2845 | -0.022888 | 121.2982 | 39.8163 | -121.4539 | -81.6284 | 121.3989 | 39.7888 | 7.2189 | 39.743
3039.4688 | 121.7102 | -39.1022 | 82.283 | -0.013352 | 6.9714 | 0.064963 | 0.087855 | 0.00027771 | 0.0019932 | 0.017923 | -0.0028687 | 0.020416 | -1.451 | -0.0011984 | -0.0049818 | 0.012971 | -0.0034393 | -31.9336 | 82.0953 | -39.0564 | 82.37 | -36.0397 | -38.0768 | -36.6028 | 0.032043 | -0.1236 | 0.004578 | 0.032043 | 0.13733 | 0.064087 | 0.13275 | 0.045777 | -0.18768 | 0.086975 | 3.0624 | 2.4994 | 1.0254 | 2.4536 | 0.97961 | 39.1068 | -82.4066 | -82.251 | 39.2395 | 39.2349 | 39.1663 | 0.12817 | 0.059509 | 3.0167 | 121.4264 | 0.13275 | 0.027465 | 121.1517 | -0.12817 | 121.1975 | 38.9786 | -121.3394 | -82.2784 | 121.4722 | 39.1342 | 7.1686 | 39.1342
3041.2656 | 121.5683 | -38.8458 | 82.6355 | -0.013352 | 6.9752 | 0.066672 | 0.090418 | -0.0012177 | 0.0041294 | 0.017069 | -0.0059205 | 0.021698 | -1.4521 | -0.0041892 | -0.008827 | 0.011689 | 0.0010467 | -31.6681 | 82.4158 | -38.8 | 82.5897 | -35.8521 | -37.8754 | -36.3876 | -0.12817 | -0.054932 | -0.022888 | -0.086975 | 0 | -0.050354 | 0.018311 | 0.045776 | -0.21973 | -0.045776 | 2.9938 | 2.4582 | 0.97046 | 2.4124 | 0.92468 | 38.8229 | -82.6904 | -82.7225 | 38.8458 | 38.8641 | 38.7955 | 0.041199 | -0.027466 | 2.948 | 121.3898 | 0.022888 | -0.064087 | 121.2158 | -0.032044 | 121.2616 | 38.7909 | -121.4355 | -82.6584 | 121.4355 | 38.7588 | 7.1777 | 38.7177
3042.9844 | 121.6873 | -38.0402 | 83.3496 | -0.0057221 | 6.9722 | 0.069663 | 0.090845 | 0.0036957 | 0.005411 | 0.019205 | -0.0028687 | 0.019775 | -1.4544 | 0.0052102 | -0.0028454 | 0.016389 | 0.00040589 | -30.9448 | 83.1894 | -38.0127 | 83.4274 | -35.0464 | -37.0834 | -35.5957 | -0.009155 | -0.13733 | -0.022888 | 0.027466 | 0.09613 | -0.004578 | 0.10986 | 0.027466 | -0.16022 | 0.07782 | 2.9938 | 2.4445 | 0.95673 | 2.417 | 0.92926 | 38.0173 | -83.4869 | -83.3221 | 38.1363 | 38.15 | 38.0356 | 0.13275 | 0.01831 | 2.9663 | 121.4401 | 0.11902 | 0.050354 | 121.2021 | -0.11444 | 121.2296 | 37.9028 | -121.3623 | -83.3725 | 121.4676 | 38.0676 | 7.0953 | 38.031
3044.6875 | 121.6827 | -37.1658 | 84.1919 | -0.0057221 | 6.9716 | 0.066245 | 0.090204 | 0.0026275 | 0.0041294 | 0.017709 | -0.0028687 | 0.020843 | -1.4533 | 0.0058512 | -0.007118 | 0.015107 | 0.00083309 | -30.2307 | 84.0637 | -37.1475 | 84.2468 | -34.227 | -36.232 | -34.7488 | -0.10071 | -0.15106 | -0.050354 | -0.050354 | 0.045776 | -0.036621 | 0.054932 | 0.018311 | -0.12817 | 0.054931 | 2.9388 | 2.417 | 0.93384 | 2.3987 | 0.91553 | 37.1155 | -84.343 | -84.2422 | 37.2116 | 37.2208 | 37.1292 | 0.10529 | 0.013733 | 2.9205 | 121.3943 | 0.09613 | 0 | 121.2112 | -0.10071 | 121.2296 | 37.0148 | -121.3394 | -84.2422 | 121.4127 | 37.1155 | 6.9351 | 37.0651
3046.4688 | 121.6553 | -36.7996 | 84.5856 | -0.0057221 | 6.9707 | 0.066672 | 0.088923 | 0.0024139 | 0.0049838 | 0.018564 | -0.0059205 | 0.019134 | -1.4525 | 0.0054238 | -0.0041272 | 0.012971 | 0.0042511 | -29.8828 | 84.4116 | -36.7493 | 84.6176 | -33.8791 | -35.8704 | -34.3872 | -0.09613 | -0.11444 | -0.032043 | -0.041199 | 0.036621 | -0.022888 | 0.050354 | 0.050354 | -0.17395 | 0.032044 | 2.9205 | 2.4124 | 0.92926 | 2.3621 | 0.87891 | 36.7676 | -84.7 | -84.6268 | 36.8362 | 36.85 | 36.7767 | 0.082397 | 0.009155 | 2.8702 | 121.3669 | 0.068664 | -0.009156 | 121.1609 | -0.082398 | 121.2112 | 36.6852 | -121.3348 | -84.6176 | 121.4172 | 36.7584 | 6.9168 | 36.7035
3048.25 | 121.5958 | -35.8154 | 85.6567 | -0.0057221 | 6.9737 | 0.065817 | 0.0917 | -0.0020721 | 0.0032748 | 0.01536 | -0.0028687 | 0.021911 | -1.4531 | 0.0011514 | -0.0056226 | 0.013398 | -0.0015167 | -28.9536 | 85.4736 | -35.7513 | 85.643 | -32.9224 | -34.877 | -33.3984 | -0.21515 | -0.15564 | -0.10529 | -0.14191 | -0.059509 | -0.14191 | -0.022888 | 0.064087 | -0.1831 | -0.013733 | 2.8931 | 2.417 | 0.93842 | 2.3529 | 0.87433 | 35.7101 | -85.8124 | -85.7986 | 35.7559 | 35.7925 | 35.6735 | 0.082398 | -0.036621 | 2.829 | 121.3943 | 0.045777 | -0.036621 | 121.225 | -0.050354 | 121.2891 | 35.6598 | -121.4081 | -85.762 | 121.4584 | 35.6735 | 6.8619 | 35.6003
3049.9688 | 121.637 | -35.8429 | 85.524 | -0.0057221 | 6.9729 | 0.068381 | 0.088923 | -0.0044221 | 0.0034884 | 0.015573 | -0.0059205 | 0.019989 | -1.4519 | 0.0071328 | -0.0049818 | 0.015321 | 0.0040375 | -28.9948 | 85.3592 | -35.8246 | 85.611 | -32.8812 | -34.9136 | -33.4396 | -0.054932 | -0.16022 | -0.045776 | -0.032043 | 0.041199 | -0.041199 | 0.041199 | 0.018311 | -0.1648 | 0.086975 | 2.9617 | 2.4033 | 0.92926 | 2.3849 | 0.91095 | 35.7971 | -85.6842 | -85.556 | 35.8841 | 35.8841 | 35.8017 | 0.086975 | 0.004577 | 2.9434 | 121.4355 | 0.086975 | 0.013733 | 121.1838 | -0.11444 | 121.2021 | 35.6827 | -121.3486 | -85.5698 | 121.4539 | 35.8109 | 6.8481 | 35.788
3051.75 | 121.5637 | -35.4721 | 85.9726 | 0.0019074 | 6.9742 | 0.066245 | 0.092554 | 0.0017731 | 0.0041294 | 0.017496 | -0.0028687 | 0.022552 | -1.4527 | -0.0080344 | -0.0041272 | 0.015107 | 0.00040589 | -28.6789 | 85.8078 | -35.4446 | 85.9039 | -32.6386 | -34.6298 | -33.1467 | -0.21515 | -0.12817 | -0.09613 | -0.14191 | -0.082397 | -0.1831 | -0.027466 | 0.027466 | -0.16479 | -0.068664 | 2.8336 | 2.3254 | 0.84229 | 2.298 | 0.81482 | 35.376 | -86.1008 | -86.1145 | 35.3897 | 35.4446 | 35.289 | 0.068664 | -0.086975 | 2.8061 | 121.3486 | 0.013733 | -0.045777 | 121.2524 | -0.032044 | 121.2799 | 35.3439 | -121.4172 | -86.0687 | 121.376 | 35.3302 | 6.7932 | 35.257
3053.5 | 121.637 | -34.9823 | 86.3892 | 0.0019074 | 6.9729 | 0.065176 | 0.089136 | 6.4114e-05 | 0.0041294 | 0.016 | -0.0028687 | 0.02063 | -1.4521 | 0.0020058 | -0.0051954 | 0.015748 | 0.0021149 | -28.212 | 86.2473 | -34.9228 | 86.4441 | -32.0343 | -34.0805 | -32.6019 | -0.13275 | -0.20599 | -0.082397 | -0.07782 | -0.009155 | -0.10071 | -0.004578 | 0.059509 | -0.14191 | 0.054932 | 2.948 | 2.3804 | 0.90179 | 2.3209 | 0.84229 | 34.8999 | -86.5952 | -86.467 | 34.9731 | 34.9777 | 34.8816 | 0.077819 | -0.018311 | 2.8885 | 121.3669 | 0.073242 | 0.004577 | 121.17 | -0.1236 | 121.2296 | 34.7763 | -121.312 | -86.4716 | 121.4264 | 34.9045 | 6.7703 | 34.8495
3055.2969 | 121.6782 | -34.5428 | 86.8469 | 0.0019074 | 6.9744 | 0.066458 | 0.092982 | 0.0036957 | 0.004343 | 0.018564 | -0.0059205 | 0.021484 | -1.4516 | 0.004783 | -0.0041272 | 0.014466 | 0.00083309 | -27.7451 | 86.673 | -34.4696 | 86.9385 | -31.5582 | -33.6044 | -32.1304 | -0.091553 | -0.2243 | -0.10071 | -0.07782 | 0.009155 | -0.10071 | 0.013733 | 0.073243 | -0.17395 | 0.091553 | 2.9846 | 2.4124 | 0.93842 | 2.3392 | 0.86517 | 34.4421 | -87.0712 | -86.9247 | 34.552 | 34.5566 | 34.4421 | 0.11444 | 0 | 2.9114 | 121.4081 | 0.10986 | 0.022888 | 121.1426 | -0.1236 | 121.2158 | 34.3185 | -121.3165 | -86.9476 | 121.4813 | 34.465 | 6.7978 | 34.4513
3057.0781 | 121.5591 | -34.5062 | 86.9568 | -0.013352 | 6.9742 | 0.068381 | 0.090632 | -0.00014949 | 0.0034884 | 0.016 | -0.0028687 | 0.022766 | -1.4531 | -0.009957 | -0.0075452 | 0.015321 | 0.00083309 | -27.7496 | 86.8332 | -34.4421 | 86.879 | -31.6956 | -33.6823 | -32.1945 | -0.27466 | -0.16479 | -0.13275 | -0.17395 | -0.12817 | -0.2243 | -0.059509 | 0.064087 | -0.1236 | -0.07782 | 2.8107 | 2.3117 | 0.82397 | 2.2476 | 0.75989 | 34.3735 | -87.1216 | -87.1307 | 34.3781 | 34.4467 | 34.2819 | 0.073242 | -0.091553 | 2.7466 | 121.3211 | 0.004577 | -0.041199 | 121.2753 | -0.032044 | 121.3394 | 34.3414 | -121.3989 | -87.0895 | 121.3852 | 34.3323 | 6.7566 | 34.2316
3058.8594 | 121.5683 | -34.3735 | 87.0895 | -0.013352 | 6.9716 | 0.066458 | 0.087427 | -0.0022857 | 0.0024204 | 0.01536 | -0.0028687 | 0.019775 | -1.4521 | -0.002053 | -0.0092542 | 0.011262 | 0.00019229 | -27.5986 | 86.9385 | -34.3094 | 87.0209 | -31.4758 | -33.4717 | -32.0068 | -0.26093 | -0.15564 | -0.13733 | -0.17395 | -0.10071 | -0.1831 | -0.059509 | 0.064087 | -0.15106 | -0.068665 | 2.8976 | 2.3666 | 0.90179 | 2.3026 | 0.83771 | 34.2361 | -87.2452 | -87.2635 | 34.2728 | 34.314 | 34.1904 | 0.07782 | -0.045776 | 2.8336 | 121.3303 | 0.036621 | -0.036621 | 121.2479 | -0.018311 | 121.312 | 34.2178 | -121.3989 | -87.2269 | 121.3943 | 34.1995 | 6.7749 | 34.1125
3060.5625 | 121.5683 | -34.4604 | 86.9934 | -0.013352 | 6.9767 | 0.067099 | 0.091059 | 0.0019867 | 0.0032748 | 0.015787 | 0.00018312 | 0.023407 | -1.4527 | 0.0032876 | -0.0069044 | 0.013612 | 0.0053193 | -27.626 | 86.8149 | -34.3735 | 86.9888 | -31.4667 | -33.5266 | -32.0755 | -0.14191 | -0.13733 | -0.068665 | -0.10071 | -0.059509 | -0.15564 | -0.018311 | 0.086975 | -0.17853 | -0.004577 | 2.9938 | 2.3849 | 0.93384 | 2.298 | 0.84686 | 34.3918 | -87.1307 | -87.0941 | 34.4009 | 34.4421 | 34.3048 | 0.050354 | -0.086975 | 2.9068 | 121.3623 | 0.009156 | -0.032043 | 121.1884 | -0.068664 | 121.2753 | 34.3231 | -121.3669 | -87.0621 | 121.4493 | 34.3597 | 6.8344 | 34.3185
3062.3438 | 121.6736 | -33.7784 | 87.5839 | -0.0057221 | 6.9724 | 0.067954 | 0.092127 | 0.0017731 | 0.0069064 | 0.016 | -0.0059205 | 0.020202 | -1.4536 | 0.0041422 | -0.0013502 | 0.015107 | 0.00061949 | -27.0401 | 87.4741 | -33.7143 | 87.6938 | -30.7938 | -32.8629 | -31.398 | -0.10986 | -0.20599 | -0.091553 | -0.041199 | 0.018311 | -0.07782 | 0.041199 | 0.064087 | -0.10986 | 0.10986 | 2.9846 | 2.3804 | 0.91553 | 2.3163 | 0.85144 | 33.6868 | -87.7899 | -87.6251 | 33.7967 | 33.8196 | 33.7006 | 0.13275 | 0.013733 | 2.9205 | 121.4081 | 0.10986 | 0.050354 | 121.1884 | -0.11444 | 121.2524 | 33.5724 | -121.2982 | -87.6755 | 121.4722 | 33.7372 | 6.7383 | 33.6685
3064.125 | 121.669 | -33.2611 | 88.0829 | -0.013352 | 6.9727 | 0.067526 | 0.091486 | 0.0036957 | 0.0049838 | 0.016428 | -0.0059205 | 0.02127 | -1.4516 | 0.003074 | -0.0032728 | 0.014894 | -0.0017303 | -26.5594 | 87.941 | -33.2336 | 88.179 | -30.2948 | -32.3593 | -30.9036 | -0.1236 | -0.24261 | -0.1236 | -0.073242 | -0.013733 | -0.1236 | 0.009155 | 0.027465 | -0.14191 | 0.09613 | 2.9663 | 2.3575 | 0.90179 | 2.33 | 0.87433 | 33.1375 | -88.3255 | -88.1561 | 33.2474 | 33.2703 | 33.1375 | 0.13275 | 0 | 2.9388 | 121.4127 | 0.10986 | 0.050354 | 121.1746 | -0.11902 | 121.2021 | 33.0185 | -121.3165 | -88.2065 | 121.4401 | 33.1879 | 6.7017 | 33.1375
3065.9062 | 121.5866 | -32.2632 | 89.1403 | -0.013352 | 6.9742 | 0.066245 | 0.08935 | -0.0016449 | 0.005411 | 0.017282 | 0.00018312 | 0.022339 | -1.4548 | 0.0052102 | -0.0079724 | 0.011476 | 0.00083309 | -25.6989 | 89.0167 | -32.222 | 89.1357 | -29.3976 | -31.366 | -29.9469 | -0.27008 | -0.20599 | -0.17395 | -0.19684 | -0.10529 | -0.21515 | -0.07782 | 0.041199 | -0.1236 | -0.004578 | 2.8656 | 2.3163 | 0.89722 | 2.2751 | 0.85602 | 32.0892 | -89.3463 | -89.3372 | 32.1579 | 32.1854 | 32.048 | 0.09613 | -0.041199 | 2.8244 | 121.3577 | 0.068664 | -0.022888 | 121.2387 | -0.032044 | 121.2799 | 32.0572 | -121.3623 | -89.3143 | 121.3989 | 32.0663 | 6.5643 | 31.9931
3067.6719 | 121.5454 | -31.5399 | 89.9094 | -0.0057221 | 6.9744 | 0.067526 | 0.091059 | 0.0045501 | 0.005411 | 0.017069 | 0.0032349 | 0.019775 | -1.4506 | 0.00093783 | -0.0058362 | 0.014466 | 0.0025421 | -25.0443 | 89.772 | -31.4667 | 89.8727 | -28.6697 | -30.661 | -29.2282 | -0.3067 | -0.25635 | -0.19684 | -0.24261 | -0.1831 | -0.31128 | -0.14648 | 0.073242 | -0.13733 | -0.036621 | 2.8702 | 2.3117 | 0.87891 | 2.2385 | 0.80566 | 31.3431 | -90.1657 | -90.152 | 31.3568 | 31.3934 | 31.2286 | 0.050354 | -0.11444 | 2.7969 | 121.3394 | 0.013733 | -0.045777 | 121.2387 | -0.05951 | 121.312 | 31.2836 | -121.376 | -90.1062 | 121.4127 | 31.2973 | 6.4957 | 31.2332
3069.3906 | 121.6507 | -30.9769 | 90.3854 | -0.013352 | 6.9727 | 0.06774 | 0.089564 | -0.0018585 | 0.0051974 | 0.021127 | -0.0059205 | 0.019348 | -1.4531 | 0.0035012 | -0.0037 | 0.015748 | 0.0025421 | -24.5956 | 90.2847 | -30.9357 | 90.4037 | -28.1342 | -30.1346 | -28.6743 | -0.29755 | -0.30212 | -0.20142 | -0.1831 | -0.10071 | -0.23804 | -0.07782 | 0.041199 | -0.10071 | 0.018311 | 2.8427 | 2.3026 | 0.84229 | 2.2614 | 0.80109 | 30.7755 | -90.6876 | -90.5685 | 30.8762 | 30.899 | 30.7388 | 0.1236 | -0.036621 | 2.8015 | 121.3394 | 0.10071 | 0.018311 | 121.2204 | -0.10071 | 121.2616 | 30.6747 | -121.3211 | -90.5869 | 121.3806 | 30.7938 | 6.3812 | 30.6793
3071.1875 | 121.5225 | -30.5969 | 90.8478 | -0.0057221 | 6.9739 | 0.068167 | 0.091913 | 0.0011321 | 0.0051974 | 0.017923 | -0.0028687 | 0.02063 | -1.4533 | 0.0058512 | -0.0045544 | 0.014253 | 0.00083309 | -24.2523 | 90.7379 | -30.5557 | 90.7516 | -27.8412 | -29.8096 | -28.331 | -0.49439 | -0.35706 | -0.32959 | -0.37994 | -0.31586 | -0.46234 | -0.27008 | 0.041199 | -0.10986 | -0.09613 | 2.7557 | 2.2659 | 0.78735 | 2.2247 | 0.74615 | 30.2673 | -91.2048 | -91.2277 | 30.2811 | 30.3268 | 30.1346 | 0.059509 | -0.13275 | 2.7145 | 121.3074 | 0.013733 | -0.050354 | 121.2936 | -0.027466 | 121.3348 | 30.2399 | -121.4035 | -91.1774 | 121.3486 | 30.217 | 6.3446 | 30.1025
3072.9219 | 121.6553 | -30.2216 | 91.1179 | -0.013352 | 6.9712 | 0.066031 | 0.088709 | -0.00079049 | 0.0039158 | 0.016 | -0.0059205 | 0.019561 | -1.4525 | 0.00051063 | -0.008186 | 0.015748 | 0.0036103 | -23.9182 | 90.9897 | -30.1666 | 91.2048 | -27.3376 | -29.2969 | -27.8641 | -0.32044 | -0.41199 | -0.3067 | -0.2655 | -0.13733 | -0.2655 | -0.15106 | 0.054932 | -0.12817 | 0.086975 | 2.8839 | 2.3575 | 0.92468 | 2.3026 | 0.86975 | 29.9149 | -91.5298 | -91.3834 | 30.0842 | 30.0705 | 29.9561 | 0.15564 | 0.041199 | 2.829 | 121.3715 | 0.16937 | 0.041199 | 121.1563 | -0.10529 | 121.2112 | 29.8096 | -121.2845 | -91.4246 | 121.4264 | 29.9561 | 6.3034 | 29.9011
3074.6875 | 121.5317 | -30.1987 | 91.2781 | -0.0057221 | 6.9739 | 0.063895 | 0.091486 | 0.0036957 | 0.0030612 | 0.013864 | -0.0059205 | 0.02127 | -1.4529 | -0.002053 | -0.009895 | 0.010194 | -0.00087591 | -23.8632 | 91.0812 | -30.1254 | 91.1911 | -27.3468 | -29.3243 | -27.8824 | -0.49439 | -0.41657 | -0.37079 | -0.44403 | -0.32044 | -0.48523 | -0.32959 | 0.073242 | -0.19684 | -0.086975 | 2.8519 | 2.3163 | 0.87433 | 2.243 | 0.80109 | 29.8279 | -91.6946 | -91.7221 | 29.8782 | 29.8691 | 29.7134 | 0.041199 | -0.11444 | 2.7786 | 121.3165 | 0.050354 | -0.073242 | 121.2067 | -0.045776 | 121.2799 | 29.7821 | -121.4035 | -91.6489 | 121.3898 | 29.7546 | 6.3354 | 29.7043
3076.4219 | 121.5179 | -30.1437 | 91.2964 | -0.0057221 | 6.975 | 0.067526 | 0.092768 | 0.0011321 | 0.0037022 | 0.016428 | -0.0028687 | 0.019989 | -1.4523 | 0.0045694 | -0.0060498 | 0.013398 | -0.0013031 | -23.8037 | 91.1865 | -30.0568 | 91.214 | -27.3331 | -29.3198 | -27.8778 | -0.54932 | -0.40741 | -0.37994 | -0.44403 | -0.35248 | -0.49896 | -0.29755 | 0.086975 | -0.10986 | -0.082398 | 2.8107 | 2.2659 | 0.82398 | 2.179 | 0.737 | 29.7638 | -91.7038 | -91.7404 | 29.7913 | 29.8462 | 29.6448 | 0.082398 | -0.11902 | 2.7237 | 121.2708 | 0.027466 | -0.064087 | 121.2433 | -0.027466 | 121.3303 | 29.7363 | -121.3531 | -91.6763 | 121.3577 | 29.6997 | 6.34 | 29.5944
3078.2188 | 121.5271 | -29.2877 | 92.1524 | 0.0019074 | 6.9759 | 0.066458 | 0.09405 | 0.0026275 | 0.0045566 | 0.014932 | -0.0028687 | 0.021484 | -1.4508 | -0.00055757 | -0.0066906 | 0.013612 | -0.00023491 | -23.0438 | 92.0334 | -29.2282 | 92.1021 | -26.4679 | -28.4317 | -26.9989 | -0.53558 | -0.47607 | -0.42572 | -0.48065 | -0.3891 | -0.55847 | -0.36621 | 0.05951 | -0.11902 | -0.050354 | 2.8198 | 2.2888 | 0.85602 | 2.2293 | 0.79651 | 28.862 | -92.6285 | -92.6331 | 28.8986 | 28.9215 | 28.7292 | 0.059509 | -0.13275 | 2.7603 | 121.3303 | 0.036621 | -0.054932 | 121.2616 | -0.050354 | 121.3211 | 28.8116 | -121.3806 | -92.5781 | 121.3898 | 28.8071 | 6.2439 | 28.7521
3080 | 121.6187 | -28.8437 | 92.5095 | -0.0057221 | 6.9744 | 0.069663 | 0.086786 | -0.0014313 | 0.0045566 | 0.014505 | -0.0089723 | 0.018921 | -1.4514 | -0.00055757 | -0.0058362 | 0.012971 | -0.00023491 | -22.6273 | 92.3813 | -28.7842 | 92.6147 | -25.946 | -27.9419 | -26.5137 | -0.43945 | -0.54474 | -0.39825 | -0.39368 | -0.2655 | -0.45776 | -0.27924 | 0.059509 | -0.12817 | 0.10529 | 2.8976 | 2.33 | 0.90179 | 2.2705 | 0.84229 | 28.4454 | -93.0542 | -92.9031 | 28.5782 | 28.5645 | 28.3859 | 0.11902 | -0.05951 | 2.8381 | 121.3989 | 0.13275 | 0.004577 | 121.1655 | -0.14648 | 121.225 | 28.299 | -121.2936 | -92.9077 | 121.4584 | 28.45 | 6.2164 | 28.4042
3081.7812 | 121.5546 | -27.4612 | 93.956 | -0.0057221 | 6.9742 | 0.066458 | 0.092982 | -0.0012177 | 0.0062656 | 0.016 | -0.0028687 | 0.020202 | -1.4506 | 0.0022196 | -0.0073316 | 0.01468 | -0.0010895 | -21.4508 | 93.8049 | -27.4429 | 93.9102 | -24.6872 | -26.6235 | -25.1862 | -0.54474 | -0.52643 | -0.43945 | -0.48065 | -0.36163 | -0.5722 | -0.36163 | 0.018311 | -0.15106 | -0.045777 | 2.774 | 2.2751 | 0.83771 | 2.2568 | 0.8194 | 27.0218 | -94.4824 | -94.4366 | 27.0996 | 27.0996 | 26.889 | 0.07782 | -0.13275 | 2.7557 | 121.3531 | 0.07782 | -0.041199 | 121.2479 | -0.086975 | 121.2662 | 26.9348 | -121.3989 | -94.3954 | 121.3715 | 26.9806 | 6.0104 | 26.9165
3083.4844 | 121.6415 | -27.0538 | 94.3588 | -0.0057221 | 6.9709 | 0.064749 | 0.088068 | -0.0010041 | 0.0011386 | 0.016214 | -0.0059205 | 0.017639 | -1.4527 | 0.0049966 | -0.0073316 | 0.012758 | -2.1314e-05 | -21.0709 | 94.1849 | -26.976 | 94.4183 | -24.1699 | -26.0971 | -24.6735 | -0.42572 | -0.55389 | -0.42572 | -0.41657 | -0.25635 | -0.43945 | -0.29297 | 0.07782 | -0.17395 | 0.059509 | 2.8839 | 2.3804 | 0.95673 | 2.3026 | 0.87891 | 26.6281 | -94.9127 | -94.7754 | 26.7975 | 26.7609 | 26.6144 | 0.13275 | -0.013733 | 2.8061 | 121.3943 | 0.16937 | 0.009155 | 121.1609 | -0.12817 | 121.2387 | 26.4999 | -121.3348 | -94.7845 | 121.4722 | 26.6373 | 5.983 | 26.6281
3085.2656 | 121.5179 | -26.6556 | 94.812 | -0.013352 | 6.9744 | 0.064536 | 0.091059 | 0.0017731 | 0.004343 | 0.016641 | -0.0059205 | 0.020202 | -1.451 | 0.00051063 | -0.0075452 | 0.014039 | 0.0053193 | -20.6909 | 94.6381 | -26.5549 | 94.7525 | -23.8449 | -25.7538 | -24.3347 | -0.59052 | -0.53558 | -0.46234 | -0.54932 | -0.40741 | -0.59509 | -0.42114 | 0.10071 | -0.17395 | -0.05951 | 2.8107 | 2.3209 | 0.90179 | 2.2202 | 0.80109 | 26.1932 | -95.3476 | -95.3613 | 26.2482 | 26.2344 | 26.0605 | 0.041198 | -0.13275 | 2.71 | 121.3074 | 0.054931 | -0.086975 | 121.1929 | -0.073242 | 121.2936 | 26.12 | -121.3669 | -95.2744 | 121.4081 | 26.1063 | 5.9647 | 26.0651
3087.0469 | 121.6141 | -26.5686 | 94.7891 | -0.013352 | 6.972 | 0.064963 | 0.090845 | -0.0027131 | 0.0032748 | 0.015146 | -0.0028687 | 0.018493 | -1.4529 | -0.0016256 | -0.0051954 | 0.014039 | -0.00044851 | -20.6772 | 94.6655 | -26.5274 | 94.8074 | -23.79 | -25.7126 | -24.2798 | -0.53558 | -0.52643 | -0.42572 | -0.46234 | -0.31128 | -0.5127 | -0.32044 | 0.041199 | -0.1236 | 0.01831 | 2.7786 | 2.2888 | 0.85602 | 2.2476 | 0.81482 | 26.1429 | -95.3156 | -95.2515 | 26.2573 | 26.2482 | 26.0559 | 0.10528 | -0.086975 | 2.7374 | 121.3348 | 0.11444 | -0.036621 | 121.1929 | -0.10071 | 121.2341 | 26.0422 | -121.3165 | -95.2148 | 121.376 | 26.1063 | 5.8914 | 26.033
3088.8281 | 121.6415 | -26.8982 | 94.455 | -0.013352 | 6.9746 | 0.066458 | 0.090418 | 0.00091851 | 0.00092496 | 0.017709 | -0.0059205 | 0.019348 | -1.4523 | -0.0016256 | -0.007118 | 0.013185 | -2.1314e-05 | -20.9473 | 94.281 | -26.8524 | 94.4824 | -24.0784 | -26.0147 | -24.5911 | -0.45319 | -0.50354 | -0.41199 | -0.39368 | -0.25177 | -0.42572 | -0.24719 | 0.045776 | -0.17395 | 0.027466 | 2.8198 | 2.3071 | 0.88348 | 2.2614 | 0.83771 | 26.4862 | -94.9585 | -94.8486 | 26.6464 | 26.651 | 26.4725 | 0.16479 | -0.013733 | 2.774 | 121.3348 | 0.16022 | 0.01831 | 121.1334 | -0.091553 | 121.1792 | 26.3947 | -121.3074 | -94.8669 | 121.3806 | 26.5045 | 5.9509 | 26.445
3090.5312 | 121.5408 | -26.6052 | 94.812 | -0.020981 | 6.9729 | 0.068808 | 0.0917 | -0.00079049 | 0.0032748 | 0.016428 | -0.0028687 | 0.022125 | -1.4519 | -0.002053 | -0.0043408 | 0.014039 | -2.1314e-05 | -20.6039 | 94.6701 | -26.5411 | 94.7891 | -23.8037 | -25.7446 | -24.3393 | -0.53101 | -0.4715 | -0.37994 | -0.48523 | -0.35706 | -0.59052 | -0.35706 | 0.064087 | -0.14191 | -0.022888 | 2.8015 | 2.2659 | 0.8606 | 2.2018 | 0.79651 | 26.2253 | -95.2835 | -95.2972 | 26.2482 | 26.2482 | 26.0147 | 0.022888 | -0.21057 | 2.7374 | 121.3303 | 0.022888 | -0.10529 | 121.2112 | -0.091553 | 121.2753 | 26.1337 | -121.3531 | -95.192 | 121.3943 | 26.12 | 6.0013 | 26.0742
3092.3281 | 121.463 | -47.3465 | 73.8007 | -0.0057221 | 6.9756 | 0.066031 | 0.090632 | 0.00049131 | 0.005411 | 0.01536 | -0.0028687 | 0.019348 | -1.4523 | 0.0049966 | -0.0037 | 0.014253 | 0.0012603 | -36.9736 | 75.9476 | -44.5221 | 73.6404 | -40.2924 | -44.9112 | -46.9482 | -0.9201 | -1.0208 | -0.88348 | -0.90179 | -0.71411 | -1.1215 | -0.7782 | 2.8244 | 2.1469 | -0.16022 | 7.0541 | 0.39825 | 2.4353 | -2.4261 | -0.3891 | 46.463 | -74.8215 | -74.7025 | 46.6324 | 46.5683 | 46.225 | 0.10529 | -0.23804 | 4.2297 | 118.1625 | 0.16937 | -0.01831 | 120.4697 | -0.13733 | 123.2941 | 46.3257 | -118.3228 | -74.6841 | 120.9869 | 46.4447 | 10.3729 | 46.4264
3094.0938 | 121.257 | -45.7809 | 75.3204 | -0.013352 | 6.9737 | 0.067099 | 0.085932 | -0.0020721 | 0.0034884 | 0.017709 | -0.0028687 | 0.019561 | -1.4548 | 0.00072423 | -0.0086132 | 0.012971 | -0.00044851 | -35.6277 | 76.7349 | -44.1376 | 76.149 | -41.0477 | -43.6432 | -42.4805 | -1.1261 | -1.1353 | -0.98877 | -1.0803 | -0.82398 | -1.236 | -0.9201 | 1.6434 | 1.4145 | 0.82855 | 4.7333 | 3.3005 | 2.1378 | 1.6571 | 0.49439 | 44.7922 | -76.4557 | -76.4008 | 44.957 | 44.8608 | 44.545 | 0.068665 | -0.24719 | 3.0899 | 120.2866 | 0.1648 | -0.091552 | 120.8725 | -0.14648 | 122.5159 | 44.6457 | -119.458 | -76.3092 | 121.9299 | 44.7006 | 10.1532 | 44.6548
3095.7969 | 121.1609 | -49.7726 | 71.2509 | -0.020981 | 6.9707 | 0.066672 | 0.090418 | 6.4114e-05 | 0.0032748 | 0.01835 | -0.0028687 | 0.019561 | -1.4525 | 0.0043558 | -0.0075452 | 0.012544 | -0.0015167 | -40.448 | 70.7108 | -50.0839 | 70.8893 | -45.9274 | -48.8663 | -47.612 | -1.3412 | -1.2451 | -1.1536 | -1.2222 | -0.96588 | -1.4191 | -1.0345 | -0.31128 | -0.54016 | -0.36163 | 3.8452 | 2.1606 | 0.90637 | 2.4719 | 1.2177 | 48.6191 | -72.496 | -72.4731 | 48.8068 | 48.7381 | 48.3536 | 0.11902 | -0.2655 | 4.1565 | 120.9732 | 0.18768 | -0.068665 | 120.7947 | -0.091553 | 120.4834 | 48.5275 | -121.3348 | -72.4045 | 120.6619 | 48.5504 | 9.3246 | 48.4314
3097.5781 | 121.2524 | -29.9789 | 91.9693 | -0.0057221 | 6.9733 | 0.067954 | 0.089777 | 0.0028411 | 0.0028476 | 0.017282 | -0.0059205 | 0.020843 | -1.4519 | 0.0041422 | -0.0043408 | 0.013398 | -0.00023491 | -23.1766 | 90.9576 | -29.6768 | 91.5161 | -26.5182 | -28.8345 | -27.4155 | -0.3067 | -0.43945 | -0.28381 | -0.29297 | -0.16479 | -0.36163 | -0.16479 | 0.30212 | -1.0117 | -0.45319 | 3.4607 | 2.5635 | 1.1444 | 2.2614 | 0.84228 | 29.6951 | -92.4088 | -92.2623 | 29.8141 | 29.8141 | 29.6173 | 0.11902 | -0.07782 | 3.1586 | 121.1929 | 0.11902 | -0.009156 | 120.6345 | -0.15564 | 120.9366 | 29.5395 | -121.6461 | -92.2531 | 121.4951 | 29.686 | 6.8024 | 29.6722
3099.3438 | 121.0693 | -53.7186 | 67.1951 | -0.020981 | 6.9703 | 0.068808 | 0.087 | -0.00079049 | 0.004343 | 0.016855 | -0.0059205 | 0.019134 | -1.4531 | 0.0058512 | -0.0062634 | 0.011476 | 0.0040375 | -42.9108 | 67.337 | -53.2242 | 67.8909 | -48.3032 | -51.7044 | -50.8026 | -0.86975 | -0.92468 | -0.7782 | -0.80566 | -0.5722 | -0.94299 | -0.63171 | 0.49439 | 0.14191 | 0.6958 | 5.4153 | 2.916 | 2.0142 | 2.4216 | 1.5198 | 52.9404 | -68.1198 | -68.0008 | 53.1464 | 53.0869 | 52.7756 | 0.14648 | -0.1648 | 4.921 | 121.1151 | 0.20599 | -0.027466 | 120.5612 | -0.14649 | 121.0556 | 52.7939 | -120.4193 | -67.9733 | 121.6095 | 52.9129 | 10.8078 | 52.8488
3101.0625 | 120.6299 | -79.6783 | 40.5991 | -0.013352 | 6.9742 | 0.071372 | 0.088282 | 0.0019867 | 0.0092564 | 0.019205 | -0.0059205 | 0.020202 | -1.4548 | -0.00013037 | -0.0062634 | 0.01233 | 0.0038239 | -64.7781 | 41.2766 | -79.1565 | 40.9836 | -73.4894 | -77.6505 | -76.7532 | -1.2451 | -1.1993 | -1.0666 | -1.1444 | -0.88348 | -1.4008 | -0.97504 | 0.52185 | 0.67749 | 0.38452 | 6.189 | 2.9251 | 2.0279 | 2.4033 | 1.506 | 78.6118 | -41.7984 | -41.7435 | 78.7949 | 78.7033 | 78.2776 | 0.091552 | -0.33417 | 5.6671 | 120.1401 | 0.1831 | -0.07782 | 120.433 | -0.13275 | 120.9549 | 78.479 | -119.7556 | -41.6656 | 120.6619 | 78.5339 | 14.9002 | 78.4332
3102.8594 | 120.2774 | -73.2651 | 46.8338 | -0.0057221 | 6.9731 | 0.070731 | 0.087427 | -0.00014949 | 0.0069064 | 0.013864 | -0.0028687 | 0.019134 | -1.4512 | 0.0035012 | -0.0079724 | 0.013398 | 0.0029693 | -59.404 | 46.9711 | -73.0179 | 46.962 | -67.6071 | -71.4432 | -70.4727 | -1.2177 | -1.1719 | -1.0529 | -1.1169 | -0.8606 | -1.3596 | -0.95673 | 0.24719 | 0.13733 | 0.12817 | 5.658 | 2.7924 | 1.8219 | 2.5452 | 1.5747 | 72.2122 | -48.0057 | -47.9507 | 72.4045 | 72.3083 | 71.9055 | 0.09613 | -0.3067 | 5.4108 | 119.9799 | 0.19226 | -0.064087 | 119.989 | -0.11902 | 120.2362 | 72.0932 | -119.8517 | -47.8867 | 120.2271 | 72.1481 | 13.8611 | 72.0474
3104.5781 | 120.0531 | -63.0341 | 57.2159 | 0.0019074 | 6.9742 | 0.06774 | 0.089564 | 0.0015595 | 0.005411 | 0.017069 | -0.0059205 | 0.019775 | -1.4527 | -0.0022666 | -0.0051954 | 0.012971 | -2.1314e-05 | -46.6736 | 61.8256 | -57.8018 | 62.1414 | -53.1692 | -56.488 | -56.6666 | -1.3184 | -1.2039 | -1.0895 | -1.2955 | -1.0208 | -1.5656 | -1.0895 | 5.2322 | 4.6097 | 4.9255 | 9.8648 | 6.3675 | 6.546 | 1.1353 | 1.3138 | 61.9446 | -58.4198 | -58.5114 | 62.0132 | 61.9446 | 61.4685 | 0 | -0.47607 | 4.6326 | 119.9432 | 0.068665 | -0.20599 | 119.6274 | -0.11444 | 124.8596 | 61.8301 | -115.0177 | -58.3054 | 125.1755 | 61.7386 | 16.3605 | 61.7157
3106.375 | 119.1513 | -59.7702 | 59.3033 | -0.020981 | 6.9742 | 0.066458 | 0.086786 | 0.0015595 | 0.0030612 | 0.018137 | -0.0028687 | 0.01828 | -1.4512 | 0.00029703 | -0.0066906 | 0.013398 | 0.0025421 | -48.1247 | 59.2896 | -59.523 | 59.3994 | -54.7623 | -58.2092 | -57.1335 | -1.4603 | -1.3275 | -1.2268 | -1.3412 | -1.0071 | -1.6159 | -1.1627 | 0.24719 | -0.013733 | 0.09613 | 5.0079 | 2.6367 | 1.561 | 2.3895 | 1.3138 | 58.5434 | -60.6308 | -60.6445 | 58.7631 | 58.6075 | 58.1543 | 0.064087 | -0.3891 | 4.7607 | 118.9224 | 0.21973 | -0.11444 | 118.8126 | -0.10071 | 119.0598 | 58.4427 | -118.8263 | -60.5301 | 119.1696 | 58.429 | 11.6455 | 58.3099
3108.0938 | 118.9041 | -68.7195 | 49.8825 | -0.0057221 | 6.9716 | 0.069449 | 0.082728 | -0.0014313 | 0.0075474 | 0.021127 | -0.0028687 | 0.018493 | -1.454 | 0.0049966 | -0.005409 | 0.011262 | -0.0038665 | -55.5908 | 49.823 | -68.5272 | 50.1755 | -63.0753 | -67.067 | -65.918 | -1.3046 | -1.3824 | -1.1765 | -1.2314 | -0.8606 | -1.4557 | -1.0529 | 0.19226 | -0.059509 | 0.29297 | 5.6442 | 2.8015 | 1.6525 | 2.6093 | 1.4603 | 67.543 | -51.265 | -51.1139 | 67.8589 | 67.6666 | 67.2638 | 0.1236 | -0.27924 | 5.452 | 118.7027 | 0.31586 | -0.054931 | 118.3502 | -0.20599 | 118.5425 | 67.337 | -118.4097 | -51.059 | 118.895 | 67.4881 | 13.1287 | 67.4149
3109.875 | 119.0094 | -61.9583 | 56.7947 | -0.013352 | 6.972 | 0.068167 | 0.085291 | -0.0029267 | 0.007761 | 0.015573 | -0.0059205 | 0.016784 | -1.4516 | 0.0045694 | -0.0062634 | 0.014466 | -2.1314e-05 | -50.1343 | 56.3187 | -62.146 | 57.0053 | -56.6986 | -60.5347 | -59.3719 | -0.9613 | -1.0529 | -0.85144 | -0.92468 | -0.59052 | -1.0712 | -0.73242 | -0.18768 | -0.47607 | 0.21057 | 5.2597 | 2.5864 | 1.4236 | 2.774 | 1.6113 | 61.1069 | -57.8476 | -57.7194 | 61.3678 | 61.2259 | 60.8871 | 0.11902 | -0.21973 | 5.4474 | 119.1513 | 0.26092 | -0.073243 | 118.4647 | -0.20142 | 118.277 | 60.9055 | -118.9407 | -57.6462 | 118.9636 | 61.0336 | 11.824 | 60.997
3111.5938 | 117.8879 | -48.4863 | 69.5206 | -0.0057221 | 6.9737 | 0.064536 | 0.086573 | -0.0039947 | 0.0039158 | 0.013651 | 0.00018312 | 0.02063 | -1.4553 | -0.0016256 | -0.010536 | 0.014253 | -0.0010895 | -38.8275 | 69.0125 | -48.5916 | 69.2642 | -44.3893 | -47.4472 | -46.3577 | -0.82398 | -0.75989 | -0.66376 | -0.79193 | -0.50354 | -0.91553 | -0.60425 | -0.10529 | -0.50812 | -0.25635 | 4.097 | 2.1286 | 1.0391 | 2.2339 | 1.1444 | 47.8226 | -70.2805 | -70.3125 | 47.9828 | 47.8821 | 47.5708 | 0.059509 | -0.25177 | 4.2023 | 117.8558 | 0.16022 | -0.12817 | 117.6041 | -0.096131 | 117.4988 | 47.7264 | -118.1122 | -70.1843 | 117.7505 | 47.6944 | 9.6588 | 47.6624
3113.3906 | 118.4143 | -42.4713 | 75.7462 | -0.0057221 | 6.9735 | 0.064963 | 0.088068 | -0.0024995 | 0.0049838 | 0.014719 | -0.0059205 | 0.016784 | -1.4544 | 0.0026468 | -0.0051954 | 0.013826 | -0.0019439 | -33.5724 | 75.7187 | -42.2241 | 76.0529 | -38.2233 | -41.1804 | -40.155 | -0.59052 | -0.75073 | -0.55389 | -0.59967 | -0.29297 | -0.65002 | -0.43488 | 0.24719 | -0.027466 | 0.3067 | 4.248 | 2.3163 | 1.2909 | 2.0691 | 1.0437 | 41.9174 | -76.4969 | -76.3458 | 42.1783 | 42.0364 | 41.8213 | 0.11902 | -0.09613 | 4.0009 | 118.277 | 0.26093 | -0.045776 | 117.9428 | -0.19684 | 118.19 | 41.7206 | -117.9703 | -76.3 | 118.5242 | 41.8716 | 8.8989 | 41.8808
3115.1094 | 117.4072 | -60.9375 | 56.0303 | -0.013352 | 6.9729 | 0.067099 | 0.085078 | -0.0063447 | 0.0066928 | 0.016214 | -0.0028687 | 0.018707 | -1.4546 | 0.0041422 | -0.0039136 | 0.014039 | -0.0015167 | -49.2783 | 55.6366 | -61.1801 | 56.3324 | -55.6915 | -59.5276 | -58.4747 | -0.36163 | -0.50812 | -0.35248 | -0.35706 | -0.1236 | -0.40283 | -0.20599 | -0.24262 | -0.39368 | 0.30212 | 5.246 | 2.4628 | 1.4099 | 2.7054 | 1.6525 | 60.585 | -56.5384 | -56.3873 | 60.8139 | 60.7315 | 60.5347 | 0.14648 | -0.050354 | 5.4886 | 117.5125 | 0.22888 | -0.004578 | 116.8167 | -0.15564 | 116.5741 | 60.4294 | -117.2104 | -56.3828 | 117.2699 | 60.5804 | 11.6592 | 60.5759
3116.8906 | 116.9952 | -60.6125 | 56.0852 | 0.0019074 | 6.9739 | 0.065817 | 0.086786 | -0.00014949 | 0.0073338 | 0.017069 | -0.0028687 | 0.022552 | -1.4529 | 0.00072423 | -0.001991 | 0.014039 | -0.0013031 | -48.9304 | 55.8609 | -60.672 | 56.2958 | -55.3848 | -59.1339 | -58.1223 | 0.004578 | 0.036621 | 0.086975 | 0.09613 | 0.11902 | 0.027466 | 0.18768 | -0.059509 | -0.2243 | 0.21057 | 5.2277 | 2.4902 | 1.4786 | 2.5497 | 1.5381 | 60.6995 | -56.0486 | -55.9891 | 60.7315 | 60.8002 | 60.64 | 0.10071 | -0.059509 | 5.2872 | 116.9678 | 0.032044 | 0.009155 | 116.5329 | -0.050354 | 116.4734 | 60.6491 | -116.7572 | -55.9982 | 116.9083 | 60.7086 | 11.6821 | 60.6171
3118.5938 | 118.6569 | -67.9047 | 50.2029 | -0.013352 | 6.9714 | 0.066245 | 0.084223 | -0.00036309 | 0.0066928 | 0.018778 | -0.0059205 | 0.020202 | -1.4514 | 0.0088418 | -0.0056226 | 0.013398 | -0.0010895 | -55.1743 | 49.6948 | -68.1747 | 50.3357 | -61.9904 | -66.5497 | -65.4282 | 0.56305 | 0.40283 | 0.49896 | 0.60425 | 0.62256 | 0.65002 | 0.66834 | -0.27008 | -0.50812 | 0.13275 | 5.9143 | 2.4765 | 1.355 | 2.7466 | 1.6251 | 68.4036 | -49.8001 | -49.5987 | 68.5272 | 68.573 | 68.5547 | 0.16937 | 0.15106 | 6.1844 | 118.5104 | 0.1236 | 0.10529 | 117.8696 | -0.09613 | 117.5995 | 68.3075 | -118.3777 | -49.704 | 118.2404 | 68.5089 | 12.7304 | 68.4677
3120.375 | 117.778 | -64.7186 | 52.8122 | 0.0019074 | 6.9746 | 0.068167 | 0.084437 | -0.0020721 | 0.0056248 | 0.019205 | -0.0028687 | 0.02127 | -1.451 | -0.003762 | -0.0062634 | 0.013398 | 0.0021149 | -52.0111 | 51.9196 | -65.0757 | 51.9836 | -60.0952 | -64.7919 | -63.9084 | -0.004578 | 0.10071 | 0.12817 | 0.086975 | 0.15564 | 0.022888 | 0.16937 | -0.35706 | -0.89264 | -0.82855 | 4.6234 | 0.81024 | -0.073242 | 1.1673 | 0.28381 | 64.8468 | -52.7115 | -52.7252 | 64.8743 | 64.888 | 64.7415 | 0.041199 | -0.10529 | 4.9805 | 117.0593 | 0.027466 | -0.041199 | 116.9952 | -0.027466 | 116.6382 | 64.8193 | -117.8879 | -52.684 | 116.7023 | 64.8056 | 12.7075 | 64.7141
3122.1562 | 117.4255 | -41.5421 | 75.3296 | -0.013352 | 6.975 | 0.067313 | 0.085932 | -0.0027131 | 0.0056248 | 0.015573 | -0.0059205 | 0.022552 | -1.4542 | 0.0045694 | -0.0037 | 0.014039 | 0.0027557 | -31.723 | 76.6342 | -40.3015 | 77.0233 | -36.026 | -39.7842 | -40.0085 | 1.355 | 1.2817 | 1.2314 | 1.5839 | 1.2817 | 1.561 | 1.5884 | 1.2405 | 1.3046 | 1.6937 | 5.5161 | 1.5335 | 1.7578 | 0.29297 | 0.51727 | 42.7734 | -74.0479 | -73.7457 | 42.8238 | 43.1305 | 43.103 | 0.35706 | 0.32959 | 4.2755 | 117.3248 | 0.050354 | 0.35248 | 116.9357 | 0.050354 | 118.1763 | 42.8238 | -115.6311 | -74.0982 | 118.5654 | 43.1259 | 9.819 | 42.897
3123.875 | 118.158 | -4.9072 | 113.3835 | 0.17738 | 6.9688 | 0.059836 | 0.090418 | -0.00079049 | 0.0017796 | 0.015573 | -0.0028687 | 0.021698 | -1.4533 | -0.0071798 | -0.0045544 | 0.014039 | -0.0019439 | -1.8265 | 113.9328 | -4.0283 | 113.9511 | -2.3071 | -3.9093 | -2.2476 | -0.16937 | -0.091553 | -0.045776 | -0.10986 | -0.022888 | -0.16937 | 0 | 0.87891 | 0.54932 | 0.56763 | 2.6001 | 2.6596 | 0.99792 | 1.7807 | 0.11902 | 4.8615 | -113.475 | -113.4933 | 4.8843 | 4.9072 | 4.7379 | 0.045776 | -0.1236 | 1.7212 | 117.9794 | 0.022888 | -0.064087 | 117.9611 | -0.045777 | 118.84 | 4.8157 | -117.4118 | -113.4293 | 118.8583 | 4.7974 | 3.0808 | 4.7379
3125.6406 | 118.634 | -9.3704 | 109.2453 | 0.0019074 | 6.972 | 0.06304 | 0.088495 | 0.00070491 | 0.0037022 | 0.01301 | -0.0028687 | 0.02063 | -1.4533 | 0.00756 | -0.0043408 | 0.015748 | 0.0016877 | -5.5252 | 109.2499 | -9.0591 | 109.4238 | -6.395 | -8.313 | -6.8115 | 0.95673 | 0.71869 | 0.81024 | 0.98877 | 0.84228 | 1.1353 | 1.03 | 0.31128 | 0.004578 | 0.17853 | 2.9755 | 2.5589 | 1.0574 | 2.2476 | 0.74615 | 10.1807 | -108.5266 | -108.2565 | 10.2127 | 10.4004 | 10.5057 | 0.21973 | 0.32501 | 2.6642 | 118.483 | 0.032043 | 0.17853 | 118.309 | -0.091553 | 118.6203 | 10.0891 | -118.3044 | -108.4351 | 118.7943 | 10.3592 | 3.8452 | 10.3271
3127.3438 | 117.3706 | -24.0189 | 93.1183 | 0.0019074 | 6.9722 | 0.064322 | 0.086786 | -0.0010041 | 0.0039158 | 0.014932 | -0.0059205 | 0.019775 | -1.4516 | 0.0041422 | -0.0060498 | 0.016389 | 0.0027557 | -19.2032 | 91.4566 | -25.4837 | 93.3197 | -20.8694 | -23.7991 | -22.2839 | 0.91553 | 0.86517 | 0.86517 | 1.0437 | 0.83313 | 1.0483 | 0.96588 | -1.4648 | -1.6617 | 0.20142 | 3.1494 | 1.7349 | 0.21973 | 3.1998 | 1.6846 | 24.884 | -92.2531 | -92.0746 | 24.852 | 24.9847 | 25.0671 | 0.10071 | 0.18311 | 4.6143 | 118.8034 | -0.032043 | 0.17853 | 116.9403 | 0 | 115.4755 | 24.884 | -118.602 | -92.2531 | 117.3386 | 25.0626 | 4.8157 | 24.9344
3129.1406 | 117.7185 | -20.8511 | 97.1924 | -0.0057221 | 6.9748 | 0.061758 | 0.089136 | -0.00014949 | 0.0037022 | 0.014078 | -0.0059205 | 0.020416 | -1.4514 | 0.00051063 | -0.0096814 | 0.014466 | 0.0021149 | -16.7541 | 95.1965 | -22.1787 | 95.4254 | -19.0338 | -21.3684 | -19.9905 | 0.18768 | 0.21973 | 0.25177 | 0.21057 | 0.23346 | 0.26093 | 0.3067 | -1.3275 | -1.9959 | -1.767 | 1.8173 | 0.86059 | -0.51727 | 2.1881 | 0.81024 | 21.1029 | -96.9727 | -96.9818 | 21.0846 | 21.1578 | 21.1121 | 0.054932 | 0.009155 | 3.1448 | 117.6041 | -0.018311 | -0.041199 | 117.3752 | -0.032043 | 116.0477 | 21.0709 | -119.371 | -96.9406 | 116.2766 | 21.0617 | 4.097 | 21.0388
3130.9375 | 117.6361 | -12.973 | 104.3976 | -0.0057221 | 6.9716 | 0.061118 | 0.090204 | -0.00036309 | 0.00092496 | 0.01301 | 0.00018312 | 0.016998 | -1.4529 | 0.0026468 | -0.0045544 | 0.014039 | 0.0059601 | -8.4091 | 104.9057 | -12.4924 | 103.9627 | -10.6613 | -12.0163 | -10.0067 | 0.086975 | 0.018311 | 0.11902 | 0.11444 | 0.1831 | 0.1236 | 0.21057 | 0.48065 | 0.50812 | -0.43487 | 2.3117 | 2.9663 | 0.95673 | 2.4857 | 0.47607 | 13.092 | -104.3793 | -104.2831 | 13.1561 | 13.1836 | 13.0966 | 0.091552 | 0.004577 | 1.8311 | 116.4551 | 0.064086 | -0.004578 | 117.3981 | -0.10071 | 117.8787 | 12.9913 | -116.89 | -104.2786 | 116.9357 | 13.0875 | 4.5639 | 13.06
3132.6562 | 116.7389 | -21.9818 | 94.4778 | -0.013352 | 6.9774 | 0.063467 | 0.086786 | 0.0024139 | 0.0013522 | 0.013864 | -0.0059205 | 0.022125 | -1.4533 | 0.0084146 | -0.006477 | 0.015748 | -0.0047211 | -16.3605 | 94.4275 | -22.0322 | 94.4733 | -19.0704 | -21.2585 | -20.0088 | 0.14648 | 0.12817 | 0.19226 | 0.16022 | 0.18768 | 0.16479 | 0.25635 | -0.050354 | -0.050354 | -0.004577 | 2.9114 | 1.973 | 0.72327 | 2.0233 | 0.77362 | 22.1741 | -94.3497 | -94.3176 | 22.1695 | 22.2382 | 22.1466 | 0.064087 | -0.027466 | 2.9617 | 116.5054 | -0.004578 | -0.032044 | 116.4597 | -0.064087 | 116.4093 | 22.11 | -116.51 | -94.2856 | 116.4551 | 22.142 | 5.6213 | 22.1283
3134.4219 | 118.4326 | -6.4316 | 111.9965 | -0.0057221 | 6.9731 | 0.061972 | 0.092554 | 0.0011321 | -0.00035684 | 0.011087 | 0.00018312 | 0.02127 | -1.451 | 0.006492 | -0.0079724 | 0.014253 | 0.0038239 | -2.4078 | 113.1729 | -5.0949 | 113.118 | -3.0304 | -4.66 | -3.2043 | -0.054932 | 0.004578 | 0.054932 | -0.004578 | 0.059509 | -0.004578 | 0.11444 | 1.3367 | 1.1765 | 1.1215 | 3.4012 | 3.2272 | 1.7715 | 1.8906 | 0.43488 | 6.4865 | -111.9919 | -112.001 | 6.4911 | 6.546 | 6.427 | 0.059509 | -0.05951 | 2.0645 | 118.2129 | 0.004577 | -0.05951 | 118.2678 | -0.050354 | 119.6045 | 6.4362 | -117.0914 | -111.9415 | 119.5496 | 6.427 | 4.0237 | 6.3766
3136.2031 | 117.6636 | -13.3026 | 103.894 | -0.0057221 | 6.9742 | 0.063254 | 0.086359 | 0.00027771 | 0.0028476 | 0.013864 | -0.0028687 | 0.018707 | -1.4544 | 0.0032876 | -0.0066906 | 0.014466 | 0.0019013 | -9.581 | 103.1662 | -14.1861 | 103.8666 | -10.6522 | -12.6526 | -11.0687 | 0.14648 | 0.073242 | 0.17395 | 0.18768 | 0.25177 | 0.24261 | 0.29297 | -0.88348 | -0.72784 | -0.027466 | 2.6505 | 2.2339 | 0.65002 | 3.1174 | 1.5335 | 13.4766 | -103.8208 | -103.7064 | 13.5544 | 13.5956 | 13.5452 | 0.11902 | 0.068665 | 3.5339 | 118.0527 | 0.07782 | 0.013733 | 117.3523 | -0.10071 | 116.4688 | 13.3759 | -118.0801 | -103.7201 | 117.1692 | 13.4903 | 3.7216 | 13.4491
3137.9844 | 118.5974 | -5.5252 | 112.8983 | -0.013352 | 6.9733 | 0.063895 | 0.089136 | 0.0011321 | 0.0032748 | 0.012155 | -0.0059205 | 0.022339 | -1.4553 | 0.0032876 | -0.001991 | 0.013185 | -0.0023713 | -2.4582 | 112.8891 | -5.3513 | 112.7289 | -3.1906 | -4.6463 | -3.2089 | 0.09613 | -0.064087 | 0.091553 | 0.11444 | 0.20142 | 0.1236 | 0.21515 | 0.17395 | -0.009155 | -0.16937 | 2.3346 | 2.3163 | 0.87891 | 2.1423 | 0.70496 | 5.6168 | -112.9623 | -112.7838 | 5.7266 | 5.7404 | 5.6488 | 0.1236 | 0.032043 | 2.1606 | 118.0801 | 0.10986 | 0.022888 | 118.2404 | -0.15564 | 118.4143 | 5.4611 | -118.2495 | -112.8067 | 118.2541 | 5.6396 | 3.067 | 5.6213
3139.7031 | 119.1834 | -0.58594 | 118.5791 | -0.020981 | 6.9742 | 0.062399 | 0.089777 | 0.0019867 | 0.0015658 | 0.016 | -0.0059205 | 0.021484 | -1.4512 | -0.00034397 | -0.007118 | 0.013612 | 0.0036103 | 1.5701 | 118.3914 | -0.4715 | 118.5608 | 1.6067 | 0.27924 | 1.7715 | 0.050354 | -0.059509 | 0.027466 | 0.018311 | 0.16479 | 0.073242 | 0.14191 | 0.11444 | -0.18768 | -0.018311 | 2.1927 | 2.3575 | 0.86517 | 2.243 | 0.75073 | 0.6134 | -118.6386 | -118.5608 | 0.75073 | 0.72784 | 0.65918 | 0.11444 | 0.045776 | 2.0782 | 119.0323 | 0.13733 | -0.009155 | 118.8629 | -0.086975 | 118.9774 | 0.52643 | -119.0506 | -118.5516 | 119.1467 | 0.60425 | 2.1561 | 0.63629
3141.5 | 119.2383 | -0.54474 | 118.7988 | -0.0057221 | 6.9739 | 0.060049 | 0.091913 | 0.0013459 | 0.00092496 | 0.011942 | -0.0059205 | 0.020843 | -1.4514 | 0.00029703 | -0.011177 | 0.014253 | 0.0014741 | 1.5564 | 118.6295 | -0.4715 | 118.6386 | 1.5472 | 0.23804 | 1.7212 | -0.12817 | -0.045776 | -0.004578 | -0.082397 | 0.027466 | -0.050354 | 0.050354 | 0.073242 | -0.16937 | -0.16022 | 2.092 | 2.2659 | 0.78278 | 2.1927 | 0.70953 | 0.54016 | -118.8446 | -118.8812 | 0.5722 | 0.59509 | 0.49438 | 0.054932 | -0.045776 | 2.0187 | 119.1101 | 0.032044 | -0.077819 | 119.101 | -0.041198 | 119.1742 | 0.49896 | -119.2703 | -118.8034 | 119.1834 | 0.46234 | 2.1011 | 0.41656
3143.2188 | 119.3619 | -0.73242 | 118.5104 | -0.0057221 | 6.9744 | 0.065176 | 0.092127 | 0.0017731 | -0.00099764 | 0.013223 | -0.0028687 | 0.021698 | -1.4516 | 0.0024332 | -0.0024182 | 0.015748 | -2.1314e-05 | 1.3641 | 118.3914 | -0.67749 | 118.4555 | 1.3779 | -0.013733 | 1.506 | 0 | -0.073242 | 0.036621 | 0.054932 | 0.14648 | 0.050354 | 0.16937 | 0.054932 | -0.11902 | -0.054932 | 2.1103 | 2.2385 | 0.71869 | 2.1835 | 0.66376 | 0.76904 | -118.5837 | -118.4555 | 0.87891 | 0.9018 | 0.78278 | 0.13275 | 0.013733 | 2.0554 | 119.133 | 0.10986 | 0.018311 | 119.0689 | -0.10986 | 119.1238 | 0.65918 | -119.1879 | -118.4738 | 119.1879 | 0.78735 | 2.0966 | 0.73242
3145 | 119.5129 | -0.48523 | 118.8995 | -0.013352 | 6.9746 | 0.06304 | 0.093836 | -0.0035675 | 0.00049776 | 0.016 | -0.0059205 | 0.020416 | -1.4523 | -0.0024802 | -0.004768 | 0.015321 | -0.0010895 | 1.5976 | 118.7622 | -0.42572 | 118.8675 | 1.6708 | 0.27924 | 1.7853 | 0.050354 | -0.10986 | 0.032043 | 0.064087 | 0.15106 | 0.050354 | 0.16937 | 0.059509 | -0.13733 | -0.032043 | 2.1561 | 2.2705 | 0.76446 | 2.211 | 0.70496 | 0.51727 | -119.0094 | -118.8354 | 0.63629 | 0.6546 | 0.53558 | 0.13733 | 0.018311 | 2.0966 | 119.2932 | 0.11902 | 0.032044 | 119.1879 | -0.14191 | 119.2474 | 0.37537 | -119.3253 | -118.8675 | 119.3527 | 0.54932 | 2.0828 | 0.53558
3146.7812 | 119.5541 | -0.48981 | 118.9407 | -0.013352 | 6.9718 | 0.062613 | 0.091059 | -0.00036309 | 7.0564e-05 | 0.014932 | -0.0059205 | 0.02063 | -1.4531 | 0.0045694 | -0.010536 | 0.014253 | -2.1314e-05 | 1.593 | 118.7622 | -0.41199 | 118.9407 | 1.6983 | 0.31586 | 1.8127 | 0.041199 | -0.082397 | 0.036621 | 0.032043 | 0.15106 | 0.07782 | 0.15106 | 0.07782 | -0.17853 | 0 | 2.1881 | 2.3026 | 0.80566 | 2.2247 | 0.72784 | 0.52643 | -119.0231 | -118.9087 | 0.64087 | 0.64087 | 0.56763 | 0.11444 | 0.041199 | 2.1103 | 119.3527 | 0.11444 | -0.004578 | 119.1742 | -0.11902 | 119.252 | 0.40741 | -119.3527 | -118.9041 | 119.4305 | 0.52185 | 2.0828 | 0.53101
3148.5 | 119.2932 | -2.742 | 116.4688 | -0.020981 | 6.9722 | 0.06304 | 0.089777 | -0.00079049 | 0.00071136 | 0.011942 | -0.0089723 | 0.018921 | -1.4499 | -0.00034397 | -0.0073316 | 0.015107 | 0.0014741 | -0.16479 | 116.4505 | -2.5131 | 116.4871 | -0.3067 | -1.8036 | -0.35706 | -0.027466 | -0.064087 | 0.032043 | -0.004578 | 0.10071 | 0.013733 | 0.13275 | 0.22888 | -0.018311 | 0.018311 | 2.4353 | 2.3849 | 0.93841 | 2.1561 | 0.70953 | 2.774 | -116.5329 | -116.4734 | 2.8427 | 2.8748 | 2.7557 | 0.10071 | -0.01831 | 2.2064 | 119.0002 | 0.068665 | -0.036621 | 118.9636 | -0.09613 | 119.1925 | 2.6779 | -118.9819 | -116.4368 | 119.2291 | 2.7374 | 2.5772 | 2.7145
3150.2812 | 119.5999 | -0.72784 | 118.8263 | -0.0057221 | 6.9737 | 0.062399 | 0.091486 | -0.0022857 | -0.00035684 | 0.014719 | -0.0059205 | 0.021484 | -1.4536 | 0.0045694 | -0.0086132 | 0.014039 | -0.0010895 | 1.474 | 118.6707 | -0.59509 | 118.7897 | 1.5656 | 0.14191 | 1.6022 | -0.004578 | -0.073242 | 0.018311 | -0.004578 | 0.1236 | 0.041199 | 0.11902 | 0.13275 | -0.15564 | -0.036621 | 2.2934 | 2.33 | 0.86975 | 2.1973 | 0.737 | 0.74616 | -118.8995 | -118.8309 | 0.85144 | 0.84686 | 0.76904 | 0.10071 | 0.022888 | 2.1606 | 119.3848 | 0.10528 | -0.022889 | 119.2657 | -0.091553 | 119.3985 | 0.6546 | -119.4214 | -118.808 | 119.5175 | 0.72327 | 2.2018 | 0.72327
3152.0469 | 119.6365 | -0.5127 | 119.0552 | -0.0057221 | 6.9752 | 0.061758 | 0.089777 | 0.00027771 | 0.0015658 | 0.014291 | -0.0028687 | 0.019348 | -1.4531 | 0.0052102 | -0.0077588 | 0.012971 | 0.0023285 | 1.6113 | 118.8995 | -0.41657 | 119.0369 | 1.7212 | 0.31586 | 1.799 | 0.013733 | -0.068665 | 0.027466 | -0.013733 | 0.13733 | 0.045776 | 0.11902 | 0.09613 | -0.15564 | -0.018311 | 2.2339 | 2.3117 | 0.82855 | 2.2156 | 0.73242 | 0.54016 | -119.1238 | -119.0689 | 0.65002 | 0.63171 | 0.55847 | 0.091553 | 0.01831 | 2.1378 | 119.4534 | 0.10986 | -0.041199 | 119.3161 | -0.096131 | 119.4122 | 0.44403 | -119.4717 | -119.0277 | 119.5496 | 0.49896 | 2.124 | 0.52643
3153.8281 | 119.6136 | -0.59967 | 119.0826 | -0.0057221 | 6.975 | 0.064536 | 0.092554 | 0.0051911 | -0.00078404 | 0.010446 | -0.0059205 | 0.021698 | -1.4529 | 0.00029703 | -0.0051954 | 0.012971 | 0.0033967 | 1.5015 | 118.9499 | -0.48523 | 118.9224 | 1.5335 | 0.10529 | 1.6067 | -0.11902 | -0.050354 | 0.004578 | -0.059509 | 0.009155 | -0.082397 | 0.064087 | 0.11444 | -0.13275 | -0.16022 | 2.1332 | 2.2064 | 0.70496 | 2.092 | 0.59052 | 0.60425 | -119.133 | -119.1422 | 0.60883 | 0.66376 | 0.51727 | 0.059509 | -0.086975 | 2.0187 | 119.4077 | 0.004577 | -0.064087 | 119.4351 | -0.054932 | 119.5496 | 0.54932 | -119.5679 | -119.0781 | 119.5221 | 0.54016 | 2.1011 | 0.48065
3155.6094 | 119.7739 | -0.60425 | 118.9957 | 0.0019074 | 6.9724 | 0.063254 | 0.0917 | 0.0036957 | 0.0030612 | 0.013437 | -0.0059205 | 0.019989 | -1.4523 | 0.0020058 | -0.0022046 | 0.015107 | 0.0023285 | 1.5884 | 118.9453 | -0.45319 | 119.046 | 1.6846 | 0.23346 | 1.7303 | 0.045776 | -0.073242 | 0.036621 | 0.073242 | 0.16022 | 0.068665 | 0.15564 | 0.15106 | -0.050355 | 0.050354 | 2.2888 | 2.3346 | 0.83771 | 2.1835 | 0.68664 | 0.64087 | -119.0689 | -118.9224 | 0.76446 | 0.75989 | 0.67291 | 0.11902 | 0.032044 | 2.1378 | 119.4992 | 0.1236 | 0.036621 | 119.3985 | -0.10986 | 119.5496 | 0.53101 | -119.4489 | -118.959 | 119.6503 | 0.67749 | 2.1927 | 0.65002
3157.3906 | 119.7876 | -0.64545 | 119.0277 | -0.013352 | 6.9742 | 0.063254 | 0.089991 | 0.0017731 | -0.0014248 | 0.014932 | -0.0059205 | 0.019775 | -1.4536 | 0.003074 | -0.004768 | 0.014039 | 0.0031829 | 1.4511 | 118.8766 | -0.58136 | 118.9774 | 1.5793 | 0.13733 | 1.6251 | -0.018311 | -0.082397 | 0.004578 | 0.027466 | 0.13275 | 0.054932 | 0.13733 | 0.064087 | -0.15106 | -0.050354 | 2.2247 | 2.2705 | 0.78278 | 2.2064 | 0.71869 | 0.65002 | -119.1101 | -119.0002 | 0.7782 | 0.78278 | 0.70038 | 0.13275 | 0.050354 | 2.1606 | 119.5587 | 0.12817 | 0.022888 | 119.458 | -0.086975 | 119.5221 | 0.56305 | -119.6091 | -119.0231 | 119.6228 | 0.67291 | 2.0966 | 0.62714
3159.125 | 119.8059 | -1.0757 | 118.5837 | 0.0019074 | 6.9752 | 0.063681 | 0.091486 | -0.0033539 | 7.0564e-05 | 0.013864 | -0.0059205 | 0.018921 | -1.4531 | 0.0056374 | -0.0062634 | 0.015962 | -0.00023491 | 1.1719 | 118.4463 | -0.97046 | 118.5471 | 1.2451 | -0.2655 | 1.2039 | 0.064087 | -0.10529 | 0.041199 | 0.073242 | 0.15564 | 0.07782 | 0.17395 | 0.10529 | -0.13733 | -0.036621 | 2.3209 | 2.2797 | 0.81024 | 2.1744 | 0.70496 | 1.1169 | -118.689 | -118.5104 | 1.2314 | 1.2497 | 1.1536 | 0.13275 | 0.036621 | 2.2156 | 119.5175 | 0.11444 | 0.032043 | 119.4168 | -0.14649 | 119.5221 | 0.97046 | -119.5541 | -118.5425 | 119.6228 | 1.149 | 2.2476 | 1.1398
3160.8906 | 119.6091 | -1.7807 | 117.9153 | 0.0019074 | 6.9735 | 0.061758 | 0.091059 | -0.00057689 | 0.00049776 | 0.012155 | -0.0059205 | 0.020843 | -1.451 | 0.0039286 | -0.008186 | 0.013612 | -0.0019439 | 0.54016 | 117.7872 | -1.6663 | 117.6361 | 0.47607 | -0.97961 | 0.50354 | -0.10071 | -0.045776 | -0.013733 | -0.054932 | 0.041199 | -0.032043 | 0.073242 | 0.11444 | -0.12817 | -0.27924 | 2.2568 | 2.2842 | 0.80109 | 2.1698 | 0.68665 | 1.767 | -117.9611 | -117.9703 | 1.8219 | 1.8539 | 1.7487 | 0.086975 | -0.01831 | 2.1423 | 119.3024 | 0.054932 | -0.041199 | 119.4534 | -0.032043 | 119.5679 | 1.7349 | -119.5816 | -117.9291 | 119.4168 | 1.7258 | 2.3209 | 1.68
3162.6094 | 119.7876 | -1.1627 | 118.5013 | -0.0057221 | 6.9722 | 0.066245 | 0.089777 | -0.0052765 | 0.00028416 | 0.013651 | 0.00018312 | 0.02127 | -1.4514 | 0.014823 | -0.0043408 | 0.013185 | -0.0013031 | 0.99792 | 118.3685 | -1.0666 | 118.4601 | 1.1444 | -0.44403 | 1.0437 | -0.018311 | -0.086975 | 0.041199 | 0.022888 | 0.11902 | 0.027466 | 0.13275 | 0.096131 | -0.13275 | -0.041199 | 2.3071 | 2.2064 | 0.71869 | 2.1103 | 0.62256 | 1.2039 | -118.5883 | -118.4784 | 1.2817 | 1.2955 | 1.1902 | 0.091552 | -0.013733 | 2.211 | 119.5267 | 0.07782 | -0.018311 | 119.4351 | -0.12817 | 119.5312 | 1.0757 | -119.5679 | -118.4601 | 119.6228 | 1.1856 | 2.1606 | 1.1444
3164.3906 | 119.7464 | -0.70038 | 119.0414 | -0.013352 | 6.9754 | 0.061758 | 0.095545 | -0.0037811 | 0.00071136 | 0.015787 | 0.00018312 | 0.021057 | -1.4514 | 0.0022196 | -0.0069044 | 0.01233 | -0.00023491 | 1.3916 | 118.9499 | -0.61798 | 118.8629 | 1.5152 | 0.027466 | 1.561 | -0.11444 | -0.045776 | 0 | -0.059509 | 0.054932 | -0.036621 | 0.073242 | 0.082397 | -0.091553 | -0.17853 | 2.2156 | 2.2614 | 0.72784 | 2.179 | 0.64545 | 0.70038 | -119.0872 | -119.101 | 0.75531 | 0.77362 | 0.66376 | 0.073242 | -0.036621 | 2.1332 | 119.4809 | 0.054932 | -0.059509 | 119.5679 | -0.045776 | 119.6503 | 0.6546 | -119.6594 | -119.0414 | 119.5633 | 0.64087 | 2.092 | 0.58594
3166.1875 | 119.7281 | -2.4811 | 116.9907 | -0.013352 | 6.9756 | 0.063681 | 0.090845 | 0.0032685 | 0.00092496 | 0.015146 | -0.0028687 | 0.018493 | -1.4555 | 0.0024332 | -0.0069044 | 0.014039 | 0.0019013 | 0.21973 | 117.247 | -2.3071 | 117.0547 | 0 | -1.6022 | -0.24261 | 0.018311 | -0.068665 | 0.054932 | 0.082397 | 0.19226 | 0.11444 | 0.18768 | 0.17395 | 0.25635 | 0.064087 | 2.4811 | 2.2385 | 0.87891 | 2.0645 | 0.70496 | 2.536 | -117.0593 | -116.9083 | 2.6733 | 2.6688 | 2.5955 | 0.13275 | 0.059509 | 2.3071 | 119.3619 | 0.13733 | 0.027465 | 119.5541 | -0.1236 | 119.7281 | 2.4124 | -119.2978 | -116.9357 | 119.5358 | 2.5635 | 2.7008 | 2.4994
3167.9062 | 119.5908 | -1.6846 | 117.9245 | 0.0095369 | 6.9739 | 0.062827 | 0.093409 | 0.0030547 | -0.0027066 | 0.013864 | -0.0028687 | 0.021057 | -1.4516 | -0.0022666 | -0.0083996 | 0.013398 | -0.00044851 | 0.51727 | 117.6544 | -1.6891 | 117.6498 | 0.62256 | -1.0117 | 0.48523 | -0.027466 | -0.036621 | 0.018311 | 0.009155 | 0.073242 | -0.009155 | 0.09613 | -0.004578 | -0.27008 | -0.27466 | 2.3071 | 2.1698 | 0.67291 | 2.1744 | 0.67749 | 1.7029 | -117.9611 | -117.9153 | 1.7578 | 1.7807 | 1.6754 | 0.077819 | -0.027466 | 2.3117 | 119.339 | 0.054931 | -0.009156 | 119.3436 | -0.054932 | 119.339 | 1.6479 | -119.6136 | -117.9062 | 119.3344 | 1.6937 | 2.2018 | 1.6571
3169.6719 | 119.4809 | -4.4678 | 114.7842 | -0.0057221 | 6.9707 | 0.062186 | 0.093409 | -0.0027131 | 0.0017796 | 0.012369 | 0.00018312 | 0.020416 | -1.4538 | 0.0035012 | -0.0073316 | 0.013612 | 0.0038239 | -1.6067 | 114.7064 | -4.3625 | 115.2008 | -1.4786 | -3.3875 | -1.9547 | 0.1236 | -0.050354 | 0.09613 | 0.12817 | 0.23346 | 0.17395 | 0.21057 | 0.10529 | -0.07782 | 0.41657 | 2.9892 | 2.5131 | 1.0803 | 2.4078 | 0.97504 | 4.5639 | -114.8346 | -114.6561 | 4.7012 | 4.6783 | 4.6417 | 0.11444 | 0.07782 | 2.8839 | 119.5633 | 0.13733 | 0.032044 | 119.0689 | -0.14648 | 119.1742 | 4.4174 | -119.1467 | -114.6881 | 119.6686 | 4.5959 | 2.861 | 4.5914
3171.3906 | 119.3527 | -5.127 | 114.1937 | 0.0019074 | 6.9756 | 0.064536 | 0.090632 | 0.0041229 | 0.0013522 | 0.01536 | -0.0059205 | 0.022339 | -1.4516 | -0.0056846 | -0.0028454 | 0.014894 | -0.0015167 | -2.6825 | 113.4384 | -5.6442 | 113.4293 | -3.0762 | -5.04 | -3.5431 | -0.004578 | 0.018311 | 0.07782 | 0.059509 | 0.1236 | 0.054932 | 0.14648 | -0.51727 | -0.75531 | -0.76447 | 2.0508 | 1.5839 | 0.086975 | 2.1011 | 0.60425 | 5.2048 | -114.1754 | -114.1342 | 5.2505 | 5.2734 | 5.1819 | 0.068664 | -0.022888 | 2.5681 | 119.0735 | 0.045776 | -0.018311 | 119.0826 | -0.059509 | 118.5654 | 5.1453 | -119.838 | -114.1159 | 118.5562 | 5.1865 | 2.4445 | 5.1224
3173.1719 | 119.1879 | -6.2622 | 112.912 | -0.0057221 | 6.9742 | 0.061972 | 0.092341 | -0.0014313 | 0.0011386 | 0.011087 | 0.00018312 | 0.022125 | -1.4514 | -0.00098477 | -0.008186 | 0.012544 | -0.00066231 | -3.0441 | 112.7884 | -6.1523 | 112.8479 | -3.511 | -5.4749 | -4.0695 | 0.022888 | 0.032043 | 0.086975 | 0.082397 | 0.14191 | 0.086975 | 0.17395 | 0.10986 | -0.1236 | -0.064087 | 2.7512 | 2.1927 | 0.78735 | 2.0828 | 0.67749 | 6.3492 | -112.8799 | -112.8296 | 6.4041 | 6.4362 | 6.3492 | 0.086975 | 0 | 2.6413 | 119.0002 | 0.054932 | -0.004578 | 118.9407 | -0.054932 | 119.0506 | 6.2942 | -119.0643 | -112.825 | 119.1101 | 6.3446 | 3.2181 | 6.2851
3174.9375 | 118.7851 | -11.0275 | 107.5607 | -0.0057221 | 6.9737 | 0.061545 | 0.088495 | -0.00057689 | -0.00057044 | 0.015787 | -0.0059205 | 0.02063 | -1.4504 | 0.0022196 | -0.0062634 | 0.012544 | -0.0019439 | -7.5485 | 106.6315 | -11.5952 | 106.9977 | -8.02 | -10.3912 | -9.0454 | 0.15564 | 0.045776 | 0.14648 | 0.1831 | 0.25635 | 0.2243 | 0.27008 | -0.56763 | -0.92926 | -0.56305 | 3.0075 | 1.9821 | 0.63629 | 2.5497 | 1.2039 | 11.174 | -107.515 | -107.3776 | 11.2839 | 11.2976 | 11.2518 | 0.1236 | 0.07782 | 3.5751 | 118.5928 | 0.10986 | 0.036621 | 118.2266 | -0.10071 | 117.659 | 11.0733 | -119.1559 | -107.4142 | 118.0252 | 11.2106 | 3.479 | 11.1832
3176.7188 | 118.8263 | -6.4957 | 112.4039 | -0.0057221 | 6.9754 | 0.064108 | 0.0917 | -0.0029267 | 7.0564e-05 | 0.013223 | -0.0059205 | 0.020843 | -1.4512 | 0.0054238 | -0.008827 | 0.010835 | 0.0014741 | -3.685 | 111.3922 | -7.1045 | 111.8866 | -4.2343 | -6.5369 | -5.0812 | -0.009155 | 0.027466 | 0.091553 | 0.036621 | 0.09613 | 0.050354 | 0.11444 | -0.60882 | -1.0117 | -0.51727 | 2.2614 | 1.4145 | -0.041198 | 2.0233 | 0.56763 | 6.5872 | -112.3764 | -112.3672 | 6.5918 | 6.6101 | 6.546 | 0.022888 | -0.041199 | 2.8702 | 118.9911 | 0.004577 | -0.054932 | 118.4967 | -0.064087 | 117.8879 | 6.5231 | -119.5084 | -112.3123 | 118.3823 | 6.5323 | 2.8107 | 6.4865
3178.5 | 118.8538 | -5.9509 | 112.7838 | -0.013352 | 6.9718 | 0.064749 | 0.091059 | 0.0024139 | 0.0017796 | 0.013651 | -0.0089723 | 0.02063 | -1.4523 | 0.00756 | -0.0039136 | 0.015321 | 0.0033967 | -2.6138 | 112.8387 | -5.6763 | 112.8891 | -3.0533 | -4.9393 | -3.5385 | 0.073242 | -0.027466 | 0.10529 | 0.10071 | 0.16479 | 0.11902 | 0.1831 | 0.27466 | 0.054932 | 0.10529 | 2.8976 | 2.4124 | 1.0117 | 2.1378 | 0.737 | 6.0562 | -112.8113 | -112.6831 | 6.1157 | 6.134 | 6.0699 | 0.077819 | 0.013733 | 2.623 | 118.5654 | 0.059509 | -0.004578 | 118.515 | -0.13275 | 118.7897 | 5.9235 | -118.4601 | -112.6785 | 118.84 | 6.0516 | 3.3371 | 6.0242
3180.2969 | 118.4555 | -8.0704 | 110.2432 | -0.0057221 | 6.9729 | 0.063467 | 0.091059 | -0.0010041 | -0.00014304 | 0.012796 | -0.0028687 | 0.02127 | -1.4521 | 0.0028604 | -0.005409 | 0.014894 | -0.0023713 | -4.6646 | 110.0693 | -8.075 | 109.9777 | -5.3604 | -7.5256 | -6.2027 | -0.054932 | 0.018311 | 0.059509 | 0.018311 | 0.059509 | 0.004578 | 0.1236 | -0.004577 | -0.17395 | -0.2655 | 2.71 | 1.8677 | 0.54474 | 1.8723 | 0.54932 | 8.1299 | -110.2249 | -110.2249 | 8.1299 | 8.194 | 8.075 | 0.064087 | -0.054931 | 2.7145 | 118.0527 | 0 | -0.041198 | 118.1442 | -0.041198 | 118.1396 | 8.0887 | -118.3182 | -110.1837 | 118.0481 | 8.0887 | 3.4058 | 8.0154
3182.0781 | 118.2541 | -11.7966 | 106.2744 | 0.0095369 | 6.9744 | 0.063254 | 0.091273 | 0.0036957 | 0.004343 | 0.014078 | -0.0059205 | 0.024047 | -1.4519 | 0.0067056 | -0.004768 | 0.013185 | 0.00061949 | -7.6035 | 106.1005 | -11.8652 | 106.0913 | -8.9264 | -11.0001 | -9.7412 | 0.041199 | 0.041199 | 0.10529 | 0.09613 | 0.14648 | 0.082397 | 0.1831 | -0.068664 | -0.17395 | -0.1831 | 2.8702 | 2.0554 | 0.79651 | 2.124 | 0.86517 | 11.9019 | -106.2332 | -106.1783 | 11.9431 | 11.9797 | 11.879 | 0.077819 | -0.022889 | 2.9388 | 117.9565 | 0.041198 | -0.009156 | 117.9657 | -0.064087 | 117.897 | 11.8378 | -118.1396 | -106.1691 | 117.8879 | 11.8927 | 4.1931 | 11.8378
3183.8594 | 117.6865 | -16.1499 | 101.4038 | -0.020981 | 6.9748 | 0.062827 | 0.0917 | 0.0017731 | 0.0024204 | 0.013223 | -0.0089723 | 0.022339 | -1.4491 | 0.0020058 | -0.007118 | 0.012971 | 0.0033967 | -10.7574 | 102.0264 | -15.39 | 102.1088 | -12.2772 | -14.8956 | -13.6276 | 0.07782 | 0.068665 | 0.12817 | 0.12817 | 0.14648 | 0.091553 | 0.19684 | 0.75989 | 0.62256 | 0.70496 | 3.8727 | 2.5223 | 1.2543 | 1.7624 | 0.49438 | 16.2781 | -101.3351 | -101.2756 | 16.2964 | 16.3467 | 16.2415 | 0.068664 | -0.036621 | 3.1128 | 117.4988 | 0.01831 | 0 | 117.4164 | -0.059509 | 118.1763 | 16.2186 | -116.7938 | -101.2756 | 118.2587 | 16.2781 | 5.3925 | 16.2277
3185.5938 | 117.8192 | -12.2635 | 105.368 | 0.0019074 | 6.9742 | 0.06539 | 0.090632 | 0.0062591 | 0.00028416 | 0.014932 | -0.0028687 | 0.019561 | -1.4523 | 0.003074 | -0.0028454 | 0.014466 | 0.0012603 | -7.9514 | 105.1437 | -12.1948 | 105.0568 | -9.407 | -11.5768 | -10.2493 | 0.13733 | -0.009155 | 0.12817 | 0.15564 | 0.2243 | 0.15564 | 0.24719 | 0.068665 | -0.2243 | -0.31128 | 2.8564 | 2.0142 | 0.68665 | 1.9455 | 0.61798 | 12.3917 | -105.3772 | -105.2124 | 12.4878 | 12.5107 | 12.4191 | 0.11902 | 0.027466 | 2.7878 | 117.2516 | 0.09613 | 0.027466 | 117.3386 | -0.13733 | 117.4072 | 12.2543 | -117.5629 | -105.2399 | 117.3203 | 12.4191 | 4.3121 | 12.4008
3187.3594 | 119.0094 | -0.55389 | 118.4052 | -0.013352 | 6.9731 | 0.060904 | 0.091913 | -0.0018585 | -0.0020658 | 0.014291 | -0.0028687 | 0.020202 | -1.4533 | 0.0043558 | -0.007118 | 0.015962 | 0.0033967 | 1.561 | 118.2358 | -0.45319 | 118.3823 | 1.9684 | 0.2655 | 1.7075 | 0.045776 | -0.091553 | 0.036621 | 0.050354 | 0.16937 | 0.086975 | 0.15564 | 0.10071 | -0.16937 | -0.022888 | 2.5223 | 2.2614 | 0.8194 | 2.1606 | 0.71869 | 0.59052 | -118.4967 | -118.3548 | 0.72327 | 0.70953 | 0.64087 | 0.11902 | 0.050354 | 2.4216 | 118.8354 | 0.13275 | 0.013733 | 118.689 | -0.12817 | 118.7897 | 0.46234 | -118.8583 | -118.3685 | 118.9362 | 0.60425 | 2.1149 | 0.59967
3189.0781 | 119.3893 | -0.59967 | 118.8263 | -0.013352 | 6.9744 | 0.063254 | 0.093195 | -0.0024995 | 0.00049776 | 0.012796 | 0.00018312 | 0.021911 | -1.4529 | -0.00013037 | -0.0077588 | 0.014466 | 0.0033967 | 1.5518 | 118.7256 | -0.49896 | 118.7347 | 1.886 | 0.16022 | 1.6296 | -0.032043 | -0.045776 | 0.022888 | -0.004578 | 0.09613 | -0.009155 | 0.10986 | 0.10071 | -0.10071 | -0.091553 | 2.4857 | 2.2293 | 0.75989 | 2.1286 | 0.65918 | 0.62256 | -118.8721 | -118.8309 | 0.6958 | 0.70953 | 0.59052 | 0.086975 | -0.032043 | 2.3849 | 119.2337 | 0.073242 | -0.027466 | 119.2245 | -0.068664 | 119.3253 | 0.55389 | -119.3253 | -118.8034 | 119.3344 | 0.59509 | 2.1515 | 0.56763
3190.8594 | 119.5129 | -0.60425 | 118.9865 | -0.0057221 | 6.9774 | 0.06304 | 0.091913 | 0.00070491 | -0.0014248 | 0.013223 | 0.00018312 | 0.022125 | -1.4504 | 0.0022196 | -0.004768 | 0.014039 | 0.0010467 | 1.5564 | 118.7897 | -0.49896 | 118.8538 | 1.886 | 0.16022 | 1.6296 | -0.009155 | -0.041199 | 0.032043 | 0.018311 | 0.10986 | 0.009155 | 0.11444 | 0.10529 | -0.19684 | -0.13275 | 2.4902 | 2.2339 | 0.76446 | 2.1286 | 0.65918 | 0.63629 | -119.0277 | -118.9682 | 0.71411 | 0.71869 | 0.6134 | 0.082398 | -0.022888 | 2.3849 | 119.3527 | 0.07782 | -0.013732 | 119.2886 | -0.073242 | 119.3939 | 0.56305 | -119.4855 | -118.9545 | 119.458 | 0.62256 | 2.1606 | 0.59509
3192.5781 | 119.5999 | -0.60883 | 118.9957 | -0.0057221 | 6.9739 | 0.064963 | 0.092982 | 0.0022003 | -0.0014248 | 0.013651 | -0.0028687 | 0.023193 | -1.4533 | -0.0050436 | -0.006477 | 0.012117 | -0.00087591 | 1.5335 | 118.8629 | -0.53558 | 118.8766 | 1.8311 | 0.10529 | 1.5701 | -0.041199 | -0.027466 | 0.036621 | -0.004578 | 0.10986 | 0.022888 | 0.11902 | 0.073243 | -0.13275 | -0.11902 | 2.4399 | 2.179 | 0.71411 | 2.1057 | 0.64087 | 0.64545 | -119.0231 | -119.0002 | 0.71869 | 0.72784 | 0.63171 | 0.082398 | -0.013733 | 2.3666 | 119.4122 | 0.073242 | -0.041199 | 119.3985 | -0.064087 | 119.4717 | 0.58136 | -119.5312 | -118.959 | 119.4855 | 0.60425 | 2.1423 | 0.56763
3194.3594 | 118.4784 | -5.5527 | 112.9578 | -0.0057221 | 6.9737 | 0.064108 | 0.091913 | -0.0016449 | 0.0017796 | 0.014719 | -0.0028687 | 0.021057 | -1.4519 | 0.011192 | -0.0075452 | 0.014039 | 0.00061949 | -2.2659 | 113.1088 | -5.2826 | 112.532 | -2.861 | -4.6326 | -3.2272 | -0.091553 | -0.009155 | 0.027466 | -0.022888 | 0.032043 | -0.032043 | 0.09613 | 0.27008 | 0.15106 | -0.42572 | 2.6917 | 2.3254 | 0.92011 | 2.0554 | 0.65003 | 5.5801 | -112.9669 | -112.9807 | 5.5847 | 5.6488 | 5.5206 | 0.068664 | -0.059509 | 2.4216 | 117.8146 | 0.004577 | -0.050354 | 118.3914 | -0.036621 | 118.6615 | 5.5435 | -118.2404 | -112.9303 | 118.0847 | 5.5298 | 3.2867 | 5.4611
3196.1406 | 119.6274 | -0.63171 | 118.9224 | 0.0019074 | 6.975 | 0.064108 | 0.090845 | 0.00070491 | 0.0022068 | 0.014078 | -0.0028687 | 0.021057 | -1.4529 | -0.0026938 | -0.0079724 | 0.01233 | 0.0019013 | 1.5244 | 118.7439 | -0.54016 | 118.8858 | 1.9089 | 0.17395 | 1.6067 | 0.054932 | -0.064087 | 0.050354 | 0.050354 | 0.17395 | 0.10529 | 0.17853 | 0.091553 | -0.17853 | -0.036621 | 2.5406 | 2.2385 | 0.80566 | 2.1469 | 0.71411 | 0.68207 | -118.9865 | -118.8721 | 0.80566 | 0.81024 | 0.737 | 0.12817 | 0.054932 | 2.449 | 119.426 | 0.1236 | 0 | 119.2841 | -0.11444 | 119.3756 | 0.56763 | -119.4626 | -118.8721 | 119.5175 | 0.68207 | 2.1561 | 0.68665
3197.9062 | 119.5221 | -0.72327 | 118.7851 | -0.0057221 | 6.9737 | 0.064536 | 0.091273 | -0.0016449 | -0.0016384 | 0.014932 | 0.00018312 | 0.018707 | -1.4527 | 0.0015786 | -0.0060498 | 0.014039 | -2.1314e-05 | 1.4923 | 118.602 | -0.59509 | 118.7851 | 1.8494 | 0.1236 | 1.5381 | 0.091553 | -0.045776 | 0.073242 | 0.10529 | 0.21515 | 0.13733 | 0.20599 | 0.12817 | -0.1831 | 0 | 2.5726 | 2.2614 | 0.84686 | 2.1332 | 0.71869 | 0.79651 | -118.8309 | -118.6798 | 0.93842 | 0.92926 | 0.8606 | 0.13275 | 0.064087 | 2.4445 | 119.3802 | 0.14191 | 0.032044 | 119.1971 | -0.11902 | 119.3253 | 0.67749 | -119.3802 | -118.7119 | 119.5084 | 0.82855 | 2.2156 | 0.81482
3199.625 | 119.632 | -0.73242 | 118.9728 | -0.013352 | 6.9737 | 0.061972 | 0.092554 | 0.00049131 | -0.0020658 | 0.01301 | 0.00018312 | 0.021698 | -1.4533 | -0.0033346 | -0.008186 | 0.013826 | 0.0016877 | 1.442 | 118.7988 | -0.61798 | 118.7485 | 1.6983 | 0.045776 | 1.4786 | -0.059509 | -0.004578 | 0.032043 | -0.027466 | 0.073242 | 0.018311 | 0.10071 | 0.11444 | -0.17395 | -0.2243 | 2.4307 | 2.211 | 0.7782 | 2.0966 | 0.66376 | 0.76447 | -118.9774 | -119.0002 | 0.80566 | 0.83313 | 0.75073 | 0.068665 | -0.013732 | 2.3163 | 119.3665 | 0.041199 | -0.059509 | 119.4168 | -0.036621 | 119.5312 | 0.72784 | -119.5908 | -118.9407 | 119.4809 | 0.70496 | 2.1744 | 0.67291
3201.4062 | 119.6228 | -0.71869 | 118.9911 | -0.013352 | 6.9731 | 0.06304 | 0.091486 | -0.0014313 | -0.0016384 | 0.012155 | -0.0059205 | 0.021911 | -1.4523 | 0.0020058 | -0.0090406 | 0.014039 | 0.00019229 | 1.3824 | 118.7439 | -0.69122 | 118.8171 | 1.7075 | -0.032043 | 1.442 | -0.07782 | -0.013733 | 0.022888 | -0.036621 | 0.068665 | -0.004578 | 0.082397 | 0.027466 | -0.24719 | -0.17395 | 2.4261 | 2.1606 | 0.68665 | 2.1332 | 0.65918 | 0.74158 | -119.0048 | -119.0277 | 0.78735 | 0.80109 | 0.71411 | 0.059509 | -0.027466 | 2.3987 | 119.5084 | 0.045777 | -0.059509 | 119.4351 | -0.036621 | 119.4626 | 0.70496 | -119.6823 | -118.9682 | 119.5358 | 0.68207 | 2.1011 | 0.64087
3203.125 | 119.8242 | -0.70496 | 119.0277 | -0.03624 | 6.9731 | 0.06304 | 0.091486 | -0.0018585 | -0.00099764 | 0.015787 | -0.0059205 | 0.018493 | -1.4531 | -0.00055757 | -0.0037 | 0.013185 | 0.0019013 | 1.4557 | 118.9178 | -0.60883 | 118.9865 | 1.7944 | 0.032043 | 1.474 | 0.013733 | -0.064087 | 0.064087 | 0.036621 | 0.14191 | 0.073242 | 0.15106 | 0.09613 | -0.10986 | -0.041199 | 2.4994 | 2.179 | 0.737 | 2.0828 | 0.64087 | 0.76904 | -119.0918 | -118.9911 | 0.84686 | 0.85602 | 0.7782 | 0.086975 | 0.009155 | 2.4033 | 119.5953 | 0.07782 | -0.027466 | 119.5267 | -0.12817 | 119.6228 | 0.64087 | -119.6365 | -118.9636 | 119.6915 | 0.74158 | 2.1606 | 0.71869
3204.9062 | 119.7784 | -0.72327 | 119.1376 | -0.0057221 | 6.9754 | 0.062827 | 0.092982 | -0.0031403 | 7.0564e-05 | 0.011728 | -0.0059205 | 0.021911 | -1.4527 | 0.0035012 | -0.0049818 | 0.012971 | 0.00019229 | 1.4465 | 118.9774 | -0.6546 | 118.9865 | 1.7349 | -0.041199 | 1.4236 | -0.032043 | -0.013733 | 0.045776 | 0.004578 | 0.068665 | -0.018311 | 0.10071 | 0.068665 | -0.16022 | -0.15106 | 2.4582 | 2.1469 | 0.68207 | 2.0782 | 0.6134 | 0.76904 | -119.1513 | -119.133 | 0.79193 | 0.82398 | 0.70496 | 0.054932 | -0.064087 | 2.3895 | 119.6411 | 0.022889 | -0.041198 | 119.632 | -0.059509 | 119.7006 | 0.70953 | -119.7922 | -119.0918 | 119.7098 | 0.72784 | 2.1698 | 0.69122
3206.6875 | 119.9707 | -0.6958 | 119.1193 | -0.0057221 | 6.9729 | 0.063895 | 0.092982 | -0.00014949 | 0.0017796 | 0.012582 | 0.00018312 | 0.01828 | -1.4521 | -0.0033346 | -0.0051954 | 0.014039 | 0.0055329 | 1.5015 | 118.9774 | -0.58594 | 119.1055 | 1.8356 | 0.045776 | 1.5106 | 0.09613 | -0.032043 | 0.09613 | 0.11902 | 0.19226 | 0.1236 | 0.20599 | 0.10986 | -0.14191 | -0.013733 | 2.5314 | 2.2064 | 0.74158 | 2.0966 | 0.63171 | 0.79193 | -119.1513 | -119.0002 | 0.88806 | 0.9018 | 0.8194 | 0.10986 | 0.027466 | 2.4216 | 119.6915 | 0.096131 | 0.022889 | 119.5633 | -0.12817 | 119.6732 | 0.66376 | -119.7052 | -119.0231 | 119.8013 | 0.81482 | 2.1973 | 0.79193
3208.3906 | 119.1147 | -7.6218 | 111.2457 | -0.0057221 | 6.9724 | 0.063254 | 0.08935 | -0.0044221 | -0.00014304 | 0.01301 | 0.00018312 | 0.019561 | -1.4525 | 0.0056374 | -0.0062634 | 0.012971 | -0.0036529 | -4.0329 | 111.2412 | -7.4936 | 111.4563 | -4.4724 | -6.6742 | -5.6076 | 0.10986 | -0.013733 | 0.09613 | 0.11444 | 0.24261 | 0.16937 | 0.2243 | 0.12817 | -0.004578 | 0.21057 | 3.1494 | 2.0142 | 0.94757 | 1.886 | 0.8194 | 7.7179 | -111.2595 | -111.1313 | 7.8644 | 7.8461 | 7.7911 | 0.12817 | 0.073243 | 3.0212 | 118.9499 | 0.14649 | 0.018311 | 118.7347 | -0.10986 | 118.8629 | 7.608 | -118.7393 | -111.1496 | 119.0781 | 7.7362 | 3.5889 | 7.7316
3210.1719 | 119.0277 | -3.9825 | 114.9994 | -0.0057221 | 6.9739 | 0.061758 | 0.092982 | -0.0050629 | 0.00071136 | 0.013223 | -0.0059205 | 0.022125 | -1.454 | -0.00034397 | -0.0090406 | 0.013612 | -0.00087591 | -1.1536 | 114.9582 | -3.8361 | 114.9902 | -1.3 | -3.0899 | -1.6434 | -0.041199 | 0.004578 | 0.045776 | 0.004578 | 0.09613 | 0.045776 | 0.15564 | 0.14648 | -0.041199 | -0.009156 | 2.6825 | 2.3392 | 0.89264 | 2.1927 | 0.74615 | 4.0283 | -114.9948 | -114.9948 | 4.0787 | 4.1382 | 4.0283 | 0.10986 | 0 | 2.536 | 118.8263 | 0.050354 | -0.041198 | 118.7943 | -0.041198 | 118.9407 | 3.9871 | -118.8355 | -114.9536 | 118.9728 | 3.9871 | 2.829 | 3.9413
3211.9531 | 118.1946 | -10.936 | 107.1945 | -0.0057221 | 6.9748 | 0.064108 | 0.092768 | 0.0013459 | 0.0024204 | 0.014291 | 0.00018312 | 0.02127 | -1.4523 | -0.00077117 | -0.0039136 | 0.012544 | -0.0027985 | -6.1752 | 107.4417 | -10.5972 | 108.3618 | -7.2968 | -9.9655 | -8.8806 | -0.059509 | -0.018311 | 0.07782 | 0.018311 | 0.054932 | 0.009155 | 0.1236 | 0.33874 | 0.24719 | 1.1673 | 3.6392 | 2.0554 | 0.97046 | 1.7166 | 0.63171 | 11.0138 | -107.2128 | -107.1762 | 10.9909 | 11.0596 | 10.9451 | 0.045776 | -0.068665 | 3.3005 | 118.959 | -0.022888 | -0.059509 | 118.0389 | -0.096131 | 118.3777 | 10.9177 | -117.7917 | -107.1167 | 119.2978 | 10.9543 | 4.7607 | 10.8765
3213.7188 | 118.6752 | -5.4428 | 113.0585 | 0.0019074 | 6.9724 | 0.062399 | 0.091273 | 0.0039093 | 0.0017796 | 0.013223 | -0.0089723 | 0.021057 | -1.4542 | 0.010764 | -0.0026318 | 0.014039 | 0.0025421 | -2.3026 | 113.2324 | -5.2094 | 113.5574 | -2.4902 | -4.747 | -3.6896 | 0.036621 | 0 | 0.07782 | 0.11444 | 0.1831 | 0.11444 | 0.20142 | 0.23346 | 0.17395 | 0.49896 | 2.9526 | 1.7532 | 0.6958 | 1.5198 | 0.46234 | 5.5206 | -113.0585 | -112.944 | 5.6259 | 5.6442 | 5.5573 | 0.1236 | 0.036621 | 2.7191 | 118.7668 | 0.10528 | 0.036621 | 118.4418 | -0.07782 | 118.6752 | 5.4428 | -118.2678 | -112.9807 | 119.0002 | 5.5573 | 3.1403 | 5.4794
3215.4375 | 118.5287 | -6.3492 | 112.1017 | -0.020981 | 6.9709 | 0.064108 | 0.090204 | -0.0029267 | -0.00099764 | 0.016 | -0.0028687 | 0.018493 | -1.4527 | 0.003074 | -0.005409 | 0.015107 | -0.00087591 | -3.0579 | 112.0789 | -6.2302 | 112.1201 | -3.5522 | -5.7312 | -4.2297 | 0.009155 | -0.009155 | 0.10529 | 0.068665 | 0.16022 | 0.091553 | 0.20142 | 0.11902 | -0.022889 | 0.01831 | 2.7969 | 2.1194 | 0.61798 | 2.0004 | 0.49896 | 6.4545 | -112.1109 | -112.0331 | 6.5094 | 6.5506 | 6.4407 | 0.09613 | -0.013733 | 2.6779 | 118.3502 | 0.054931 | -0.036621 | 118.309 | -0.11444 | 118.428 | 6.34 | -118.3319 | -111.9965 | 118.4692 | 6.4178 | 3.2913 | 6.3583
3217.2188 | 119.4901 | -0.67291 | 118.7897 | -0.013352 | 6.9739 | 0.064108 | 0.092982 | -0.00057689 | 0.0017796 | 0.014078 | -0.0028687 | 0.019348 | -1.4529 | 0.0028604 | -0.0049818 | 0.015107 | -0.00066231 | 1.4877 | 118.6111 | -0.55847 | 118.6798 | 1.8127 | 0.082397 | 1.5335 | 0.027466 | -0.050354 | 0.09613 | 0.054932 | 0.14191 | 0.091553 | 0.15564 | 0.11444 | -0.17853 | -0.10986 | 2.4857 | 2.2064 | 0.75531 | 2.092 | 0.64087 | 0.76904 | -118.84 | -118.7347 | 0.81482 | 0.82855 | 0.76447 | 0.05951 | -0.004577 | 2.3712 | 119.2383 | 0.045777 | -0.041198 | 119.1696 | -0.14648 | 119.2841 | 0.62256 | -119.3481 | -118.6935 | 119.3527 | 0.72784 | 2.1606 | 0.70038
3219.0156 | 118.1076 | -11.2335 | 106.8604 | -0.0057221 | 6.9744 | 0.06304 | 0.091486 | -0.00036309 | 7.0564e-05 | 0.012796 | -0.0028687 | 0.022766 | -1.4527 | -0.00098477 | -0.0062634 | 0.015748 | 0.0016877 | -6.9489 | 106.7596 | -11.1786 | 107.0343 | -8.0017 | -10.3363 | -8.9996 | 0.004578 | 0.013733 | 0.10071 | 0.082397 | 0.1236 | 0.068665 | 0.17395 | 0.054932 | -0.10071 | 0.17395 | 3.2318 | 2.2339 | 0.89722 | 2.179 | 0.84229 | 11.3342 | -106.8466 | -106.778 | 11.3571 | 11.4075 | 11.3022 | 0.073242 | -0.032043 | 3.1769 | 118.2129 | 0.022888 | -0.018311 | 117.9382 | -0.086975 | 117.9932 | 11.2473 | -118.0389 | -106.7596 | 118.2678 | 11.3159 | 4.2847 | 11.2381
3220.7344 | 119.1055 | -2.4307 | 116.5878 | -0.013352 | 6.9729 | 0.064108 | 0.092554 | -0.0031403 | 0.00049776 | 0.013864 | -0.0028687 | 0.017852 | -1.4527 | -0.0029074 | -0.004768 | 0.015321 | 0.0019013 | 0.09613 | 116.4734 | -2.3254 | 116.6016 | 0.14648 | -1.6525 | -0.27466 | 0.009155 | -0.032043 | 0.07782 | 0.059509 | 0.13275 | 0.086975 | 0.15106 | 0.10529 | -0.11444 | 0.013732 | 2.5772 | 2.1561 | 0.7782 | 2.0508 | 0.67291 | 2.5085 | -116.6199 | -116.5283 | 2.5635 | 2.5818 | 2.5177 | 0.073242 | 0.009155 | 2.4719 | 118.927 | 0.054931 | -0.018311 | 118.7988 | -0.10986 | 118.9041 | 2.3987 | -118.9133 | -116.51 | 119.0323 | 2.4902 | 2.5269 | 2.4399
3222.5312 | 119.5404 | -1.355 | 118.0939 | -0.013352 | 6.9756 | 0.063254 | 0.092127 | 0.0022003 | 0.00071136 | 0.011728 | -0.0089723 | 0.020416 | -1.4536 | 0.0035012 | -0.0045544 | 0.015962 | 0.0012603 | 0.96588 | 118.0893 | -1.2497 | 118.0573 | 1.1536 | -0.68207 | 0.7782 | 0 | -0.027466 | 0.064087 | 0.041199 | 0.10986 | 0.050354 | 0.16022 | 0.10529 | -0.004578 | -0.036621 | 2.5085 | 2.1332 | 0.67291 | 2.0279 | 0.56763 | 1.4191 | -118.1213 | -118.0527 | 1.4648 | 1.5152 | 1.4053 | 0.09613 | -0.013733 | 2.4033 | 119.3069 | 0.045776 | -0.022888 | 119.339 | -0.091553 | 119.4443 | 1.3275 | -119.3436 | -118.0298 | 119.4122 | 1.3962 | 2.3209 | 1.355
3224.2656 | 118.9774 | -6.5872 | 112.3581 | -0.0057221 | 6.9752 | 0.063681 | 0.09405 | -0.00079049 | -0.0016384 | 0.013651 | -0.0028687 | 0.020416 | -1.4514 | -0.0076072 | -0.0075452 | 0.013612 | 0.0019013 | -3.3051 | 112.1384 | -6.6055 | 112.2757 | -3.9368 | -6.0654 | -4.7104 | -0.045776 | 0.013733 | 0.073242 | 0.009155 | 0.10529 | 0.041199 | 0.14191 | -0.018311 | -0.21973 | -0.082397 | 2.6505 | 1.8768 | 0.52185 | 1.8951 | 0.54016 | 6.6605 | -112.3444 | -112.3489 | 6.6925 | 6.7291 | 6.6284 | 0.068665 | -0.032043 | 2.6688 | 118.8812 | 0.032044 | -0.064087 | 118.7439 | -0.059509 | 118.7256 | 6.601 | -118.9636 | -112.2849 | 118.8629 | 6.5964 | 3.2822 | 6.5414
3226.0312 | 118.8766 | -2.6413 | 116.1758 | -0.013352 | 6.9735 | 0.062399 | 0.092982 | -0.0010041 | 0.0017796 | 0.012582 | -0.0059205 | 0.02127 | -1.4525 | -0.00098477 | -0.0073316 | 0.015748 | 0.0016877 | 0.20599 | 116.423 | -2.2934 | 116.4139 | 0.14191 | -1.6617 | -0.31586 | 0 | -0.004578 | 0.059509 | 0.045776 | 0.11444 | 0.068665 | 0.15106 | 0.3479 | 0.24719 | 0.23804 | 2.7832 | 2.3254 | 0.97961 | 1.9775 | 0.63171 | 2.7008 | -116.1804 | -116.1301 | 2.7557 | 2.7924 | 2.71 | 0.091553 | 0.009156 | 2.4353 | 118.7073 | 0.054932 | -0.013733 | 118.7164 | -0.064087 | 119.0643 | 2.6367 | -118.4692 | -116.1163 | 119.0552 | 2.6871 | 2.8473 | 2.6413
3227.8125 | 118.6523 | -7.3883 | 111.4105 | -0.0057221 | 6.972 | 0.061758 | 0.089564 | -0.0010041 | -0.0020658 | 0.01301 | -0.0089723 | 0.020416 | -1.451 | 0.0022196 | -0.012245 | 0.010621 | 0.00083309 | -4.4632 | 109.7122 | -8.6746 | 113.2599 | -5.7404 | -9.0775 | -7.6401 | -0.045776 | 0.018311 | 0.064087 | -0.004578 | 0.086975 | 0.022888 | 0.11902 | -1.2863 | -1.6983 | 1.8494 | 1.6479 | -0.25177 | -1.6891 | 1.0345 | -0.40283 | 7.4524 | -111.3922 | -111.4151 | 7.4753 | 7.5073 | 7.4112 | 0.054932 | -0.041199 | 2.9343 | 121.9345 | 0.022888 | -0.068665 | 118.3868 | -0.045776 | 117.1005 | 7.4066 | -120.0851 | -111.3464 | 120.6482 | 7.3837 | 2.9251 | 7.3425
3229.5938 | 119.1422 | -4.5181 | 114.4363 | -0.020981 | 6.9722 | 0.063467 | 0.089777 | -0.00036309 | -0.00014304 | 0.013651 | -0.0059205 | 0.020843 | -1.4497 | 0.010337 | -0.0056226 | 0.013612 | 0.0055329 | -1.4832 | 114.1754 | -4.6188 | 114.1525 | -1.6251 | -3.772 | -2.4765 | 0.045776 | -0.032043 | 0.082397 | 0.09613 | 0.19684 | 0.13275 | 0.21515 | -0.10071 | -0.26093 | -0.28381 | 2.8931 | 2.0416 | 0.74615 | 2.1423 | 0.84686 | 4.6005 | -114.4684 | -114.3402 | 4.715 | 4.7333 | 4.6509 | 0.13275 | 0.050354 | 2.9938 | 118.7714 | 0.11444 | 0.013733 | 118.7943 | -0.11444 | 118.6935 | 4.4861 | -119.0552 | -114.3539 | 118.6707 | 4.6143 | 3.035 | 4.5639
3231.3594 | 119.0964 | -1.7212 | 117.0456 | -0.0057221 | 6.9748 | 0.061118 | 0.090845 | -0.0016449 | -0.0014248 | 0.010873 | -0.0059205 | 0.019348 | -1.4531 | 0.003074 | -0.0069044 | 0.016389 | -0.00023491 | 0.73242 | 117.1692 | -1.5884 | 117.16 | 0.76904 | -1.0117 | 0.48523 | 0.041199 | -0.050354 | 0.073242 | 0.082397 | 0.1831 | 0.13733 | 0.20142 | 0.13275 | 0.1236 | 0.11444 | 2.4902 | 2.2064 | 0.70953 | 2.0737 | 0.57678 | 1.7944 | -117.0959 | -116.9632 | 1.9043 | 1.9226 | 1.8585 | 0.12817 | 0.064087 | 2.3575 | 118.7485 | 0.10986 | 0.009155 | 118.7576 | -0.1236 | 118.8904 | 1.6708 | -118.634 | -116.9724 | 118.8812 | 1.8036 | 2.4536 | 1.7624
3233.0781 | 119.1376 | -1.0208 | 118.0527 | 0.0019074 | 6.9724 | 0.064108 | 0.090418 | 0.0054047 | 0.00049776 | 0.010446 | -0.0059205 | 0.021911 | -1.4531 | 0.0060648 | -0.0056226 | 0.014466 | 0.0025421 | 1.3412 | 117.9245 | -0.92468 | 118.0389 | 1.5656 | -0.32959 | 1.1444 | 0.09613 | -0.045776 | 0.091553 | 0.10071 | 0.17395 | 0.10986 | 0.18768 | 0.09613 | -0.12817 | -0.013733 | 2.5864 | 2.1652 | 0.69122 | 2.0691 | 0.59509 | 1.1124 | -118.0984 | -117.952 | 1.1948 | 1.2085 | 1.1307 | 0.09613 | 0.01831 | 2.4902 | 118.9636 | 0.082397 | 0.009155 | 118.8492 | -0.13733 | 118.9453 | 0.97504 | -118.9774 | -117.9611 | 119.0598 | 1.1215 | 2.3621 | 1.1169
3234.8438 | 118.3823 | -11.3205 | 107.3547 | -0.013352 | 6.9735 | 0.062613 | 0.088923 | -0.00079049 | -0.00099764 | 0.013437 | -0.0059205 | 0.020202 | -1.4527 | -0.00013037 | -0.008186 | 0.011262 | -0.00087591 | -4.8981 | 108.6227 | -9.343 | 109.3323 | -5.896 | -7.8094 | -6.926 | 0.050354 | -0.004578 | 0.091553 | 0.032043 | 0.1236 | 0.086975 | 0.14191 | 1.9775 | 1.268 | 1.9775 | 5.4245 | 4.3945 | 3.511 | 2.417 | 1.5335 | 11.412 | -107.3593 | -107.3227 | 11.4441 | 11.4624 | 11.4075 | 0.050354 | -0.004578 | 3.447 | 118.6752 | 0.032043 | -0.05951 | 117.9657 | -0.096131 | 119.9432 | 11.3159 | -116.6977 | -107.2632 | 120.6528 | 11.3525 | 6.4224 | 11.3709
3236.5625 | 119.3298 | -12.9089 | 106.5857 | -0.013352 | 6.9709 | 0.066031 | 0.090204 | -0.0018585 | 0.00049776 | 0.011301 | -0.0059205 | 0.020202 | -1.4533 | -0.0011984 | -0.0086132 | 0.013826 | 0.0019013 | -9.2148 | 103.5324 | -14.3829 | 104.7821 | -10.5057 | -12.8403 | -11.8149 | 0.14648 | -0.009155 | 0.1236 | 0.11902 | 0.24261 | 0.17853 | 0.21973 | -1.474 | -3.0533 | -1.8036 | 2.4033 | 1.0941 | 0.068665 | 2.5681 | 1.5427 | 13.0325 | -106.5948 | -106.4667 | 13.1516 | 13.1287 | 13.0875 | 0.096131 | 0.054932 | 3.8773 | 119.165 | 0.11902 | -0.004577 | 117.9153 | -0.13275 | 116.4413 | 12.8998 | -120.9686 | -106.4621 | 117.691 | 13.028 | 3.6942 | 13.0554
3238.3281 | 118.2587 | -14.328 | 103.5049 | -0.013352 | 6.9722 | 0.064322 | 0.089991 | -0.0024995 | 7.0564e-05 | 0.010873 | -0.0059205 | 0.018707 | -1.4533 | 0.0022196 | -0.0062634 | 0.01233 | 0.00061949 | -9.5169 | 103.2257 | -14.4562 | 105.3955 | -9.8145 | -12.8311 | -11.1374 | 0.12817 | -0.022888 | 0.10071 | 0.14191 | 0.23346 | 0.18768 | 0.23804 | -0.12817 | -0.27924 | 1.8906 | 4.5136 | 3.1906 | 1.4969 | 3.3188 | 1.6251 | 14.4287 | -103.5278 | -103.363 | 14.5615 | 14.566 | 14.5157 | 0.13733 | 0.086975 | 4.6417 | 119.8517 | 0.13275 | 0.041199 | 117.6819 | -0.1236 | 117.5537 | 14.3051 | -117.9611 | -103.4042 | 119.7235 | 14.4699 | 4.8111 | 14.4562
3240.0469 | 119.0369 | -7.0496 | 111.9507 | -0.013352 | 6.975 | 0.063895 | 0.093195 | -0.0016449 | 0.00071136 | 0.014719 | -0.0028687 | 0.020843 | -1.4538 | -0.0011984 | -0.0058362 | 0.013185 | 0.0023285 | -3.8544 | 111.4838 | -7.045 | 111.4975 | -4.3442 | -6.7749 | -5.1727 | -0.068665 | -0.013733 | 0.041199 | -0.004578 | 0.045776 | -0.009155 | 0.11902 | 0.004578 | -0.46692 | -0.45319 | 2.7054 | 1.8768 | 0.27466 | 1.8723 | 0.27008 | 7.0908 | -111.9644 | -111.9553 | 7.0953 | 7.1686 | 7.0404 | 0.07782 | -0.050354 | 2.7008 | 118.5425 | 0.004577 | -0.045777 | 118.5287 | -0.054932 | 118.5333 | 7.0358 | -118.9957 | -111.9095 | 118.5471 | 7.045 | 3.1952 | 6.9809
3241.7812 | 119.3115 | -2.3987 | 116.7572 | -0.013352 | 6.9748 | 0.06539 | 0.092554 | 0.0034821 | 0.0017796 | 0.011728 | 0.00018312 | 0.02127 | -1.4538 | 0.0015786 | -0.0056226 | 0.01468 | -0.0017303 | 0.29755 | 116.7343 | -2.1561 | 116.5466 | 0.041199 | -1.6296 | -0.33875 | 0.086975 | -0.041199 | 0.073242 | 0.11444 | 0.1831 | 0.1236 | 0.21515 | 0.24261 | -0.022888 | -0.21057 | 2.4399 | 2.0599 | 0.76904 | 1.8173 | 0.52643 | 2.4719 | -116.7984 | -116.6428 | 2.5818 | 2.6138 | 2.5223 | 0.14191 | 0.050354 | 2.1973 | 118.7027 | 0.10986 | 0.041199 | 118.8904 | -0.11444 | 119.133 | 2.3575 | -118.9133 | -116.684 | 118.9453 | 2.5131 | 2.6962 | 2.4857
3243.5 | 119.0598 | -2.5497 | 116.6107 | -0.0057221 | 6.9727 | 0.062613 | 0.090845 | 0.0011321 | -0.00078404 | 0.016855 | -0.0028687 | 0.02063 | -1.4533 | -0.0018394 | -0.005409 | 0.016175 | -0.0015167 | 0.041199 | 116.2537 | -2.504 | 116.5421 | 0.25635 | -1.799 | -0.64087 | 0.064087 | -0.036621 | 0.07782 | 0.07782 | 0.16479 | 0.091553 | 0.16937 | 0.045777 | -0.35706 | -0.068665 | 2.8061 | 1.9089 | 0.75073 | 1.8631 | 0.70496 | 2.6276 | -116.6473 | -116.5329 | 2.7145 | 2.7191 | 2.6413 | 0.091553 | 0.013733 | 2.7603 | 119.046 | 0.086975 | 0 | 118.7576 | -0.11444 | 118.8034 | 2.5131 | -119.1147 | -116.5329 | 119.0918 | 2.6276 | 2.5909 | 2.6138
3245.2812 | 119.1376 | -4.509 | 114.4684 | -0.013352 | 6.9754 | 0.064322 | 0.091486 | -0.0039947 | -0.00014304 | 0.012155 | -0.0028687 | 0.02127 | -1.451 | 0.00093783 | -0.0066906 | 0.013826 | 0.00019229 | -1.1856 | 114.4089 | -4.3213 | 114.7018 | -1.6846 | -3.3234 | -2.1057 | 0.054932 | -0.064087 | 0.073242 | 0.068665 | 0.1831 | 0.10986 | 0.17853 | 0.18768 | -0.059509 | 0.23346 | 2.8244 | 2.4033 | 1.1856 | 2.2156 | 0.99792 | 4.5822 | -114.5325 | -114.3997 | 4.6921 | 4.6875 | 4.6188 | 0.10529 | 0.036621 | 2.6367 | 119.0231 | 0.10986 | -0.004577 | 118.7302 | -0.13733 | 118.9178 | 4.4449 | -118.7897 | -114.3951 | 119.2108 | 4.5776 | 3.3234 | 4.5639
3247.0625 | 118.959 | -3.5339 | 115.5075 | 0.0019074 | 6.9746 | 0.063681 | 0.091913 | -0.0020721 | 0.0011386 | 0.013864 | -0.0059205 | 0.021911 | -1.4523 | 0.0035012 | -0.0049818 | 0.01233 | -0.0025849 | -0.65002 | 115.3656 | -3.4332 | 115.3839 | -0.92468 | -2.7328 | -1.4191 | 0.009155 | -0.013733 | 0.059509 | 0.009155 | 0.10071 | 0.027466 | 0.11444 | 0.10071 | -0.14191 | -0.1236 | 2.6093 | 2.1149 | 0.80109 | 2.0142 | 0.70038 | 3.5934 | -115.5212 | -115.4984 | 3.6346 | 3.6484 | 3.5614 | 0.054932 | -0.032043 | 2.5085 | 118.8171 | 0.041199 | -0.050354 | 118.7988 | -0.073242 | 118.8995 | 3.5202 | -118.9407 | -115.448 | 118.9178 | 3.5431 | 2.8839 | 3.5431
3248.7812 | 119.2108 | -2.8381 | 116.3361 | -0.013352 | 6.9729 | 0.060904 | 0.090845 | -0.0027131 | -0.00035684 | 0.012582 | -0.0028687 | 0.018921 | -1.4538 | 0.0084146 | -0.0073316 | 0.013826 | 0.0029693 | -0.21057 | 116.0522 | -2.829 | 116.2262 | -0.22888 | -2.0187 | -0.67291 | 0.059509 | -0.045776 | 0.086975 | 0.07782 | 0.20599 | 0.14191 | 0.1831 | 0.009156 | -0.28381 | -0.10986 | 2.6093 | 2.1652 | 0.8194 | 2.1561 | 0.81024 | 2.9251 | -116.3818 | -116.2582 | 3.0441 | 3.0212 | 2.98 | 0.09613 | 0.054932 | 2.6001 | 119.0552 | 0.11902 | -0.009155 | 118.8812 | -0.13275 | 118.8904 | 2.7924 | -119.165 | -116.2491 | 119.0643 | 2.916 | 2.6276 | 2.8976
3250.5 | 119.0186 | -4.8157 | 114.0335 | 0.0019074 | 6.9756 | 0.063681 | 0.091273 | 6.4114e-05 | 0.00092496 | 0.010446 | -0.0059205 | 0.019134 | -1.4536 | 0.0032876 | -0.0056226 | 0.015535 | -0.0010895 | -1.7899 | 113.6215 | -4.9484 | 114.418 | -1.9318 | -4.1382 | -2.7695 | 0.086975 | -0.022888 | 0.091553 | 0.10071 | 0.1831 | 0.13733 | 0.18768 | -0.13275 | -0.41199 | 0.38452 | 2.8839 | 2.0462 | 0.67749 | 2.179 | 0.81024 | 4.9072 | -114.0564 | -113.9328 | 4.9988 | 5.0034 | 4.953 | 0.09613 | 0.045776 | 3.0167 | 119.3665 | 0.091552 | 0.009155 | 118.5699 | -0.11444 | 118.4372 | 4.7928 | -118.9819 | -113.942 | 119.2337 | 4.9164 | 3.0258 | 4.9026
3252.2969 | 119.0186 | -4.454 | 114.6011 | -0.0057221 | 6.9739 | 0.063467 | 0.091059 | 0.0013459 | 0.00071136 | 0.011087 | -0.0089723 | 0.020843 | -1.4508 | -0.00055757 | -0.0028454 | 0.014039 | 0.0012603 | -0.86975 | 115.0452 | -3.7216 | 115.1733 | -1.1169 | -3.0441 | -1.6434 | 0.11902 | -0.032043 | 0.07782 | 0.12817 | 0.19684 | 0.13275 | 0.21973 | 0.73242 | 0.44403 | 0.5722 | 3.3371 | 2.8107 | 1.4099 | 2.0782 | 0.67749 | 4.5319 | -114.6332 | -114.473 | 4.6509 | 4.6738 | 4.5868 | 0.14191 | 0.054931 | 2.6047 | 118.895 | 0.11902 | 0.050354 | 118.7668 | -0.10986 | 119.4992 | 4.422 | -118.3228 | -114.5233 | 119.6274 | 4.5822 | 3.5843 | 4.5731
3254.0781 | 118.8904 | -5.6534 | 113.3148 | 0.0019074 | 6.9752 | 0.06304 | 0.092554 | -0.0029267 | 0.00028416 | 0.016214 | -0.0059205 | 0.021057 | -1.4512 | -0.00483 | -0.0060498 | 0.015107 | 0.00040589 | -2.2705 | 113.0539 | -5.5252 | 112.7151 | -3.0396 | -5.0034 | -3.7765 | -0.022888 | 0.013733 | 0.045776 | -0.009155 | 0.059509 | 0.013733 | 0.10071 | 0.12817 | -0.26093 | -0.59967 | 2.6138 | 1.8768 | 0.65002 | 1.7487 | 0.52185 | 5.6992 | -113.3011 | -113.324 | 5.7129 | 5.7541 | 5.6671 | 0.054932 | -0.032043 | 2.4857 | 118.2404 | 0.013733 | -0.054931 | 118.5791 | -0.032043 | 118.7073 | 5.6671 | -118.84 | -113.269 | 118.3685 | 5.6442 | 3.3829 | 5.6305
3255.8594 | 118.2358 | -9.8557 | 108.3069 | 0.0019074 | 6.9724 | 0.063254 | 0.087641 | -0.0024995 | 0.00092496 | 0.012155 | -0.0059205 | 0.019134 | -1.4523 | 0.0020058 | -0.0051954 | 0.01233 | 0.0016877 | -5.7816 | 107.9224 | -9.9792 | 108.3618 | -6.7383 | -9.2743 | -7.9056 | 0.004578 | 0.018311 | 0.054932 | 0.009155 | 0.11444 | 0.059509 | 0.1236 | -0.1236 | -0.38452 | 0.054931 | 3.1174 | 1.9501 | 0.58136 | 2.0737 | 0.70496 | 9.9106 | -108.2886 | -108.2977 | 9.9701 | 9.9792 | 9.9152 | 0.068664 | 0.004577 | 3.241 | 118.3411 | 0.059509 | -0.045777 | 117.9016 | -0.036621 | 117.778 | 9.874 | -118.2861 | -108.252 | 118.2175 | 9.8648 | 4.0741 | 9.8602
3257.5781 | 118.2266 | -9.787 | 108.3252 | -0.0057221 | 6.9733 | 0.065176 | 0.091059 | -0.0010041 | 0.0051974 | 0.011942 | -0.0059205 | 0.021698 | -1.4529 | 0.00072423 | -0.0039136 | 0.015321 | -0.00087591 | -6.2759 | 107.3914 | -10.5377 | 107.6843 | -7.4432 | -9.7549 | -8.3862 | 0.054932 | -0.036621 | 0.091553 | 0.10529 | 0.17395 | 0.11902 | 0.21515 | -0.75073 | -0.93384 | -0.64087 | 2.3438 | 1.4008 | 0.032043 | 2.1515 | 0.78278 | 9.8785 | -108.3618 | -108.2199 | 9.9609 | 10.0021 | 9.906 | 0.1236 | 0.027466 | 3.0945 | 118.222 | 0.082397 | 0.013733 | 117.9291 | -0.12817 | 117.1783 | 9.7504 | -118.8629 | -108.2336 | 117.4713 | 9.8923 | 3.511 | 9.8419
3259.375 | 117.5858 | -14.3646 | 102.9739 | -0.013352 | 6.9761 | 0.061545 | 0.088495 | -0.0048493 | 0.0019932 | 0.014291 | -0.0089723 | 0.02063 | -1.451 | -0.00077117 | -0.0092542 | 0.012971 | 0.00040589 | -9.407 | 102.9419 | -14.4379 | 103.1708 | -11.2244 | -13.6093 | -11.9064 | -0.041199 | 0.027466 | 0.059509 | -0.018311 | 0.09613 | 0.045776 | 0.10071 | -0.073242 | -0.032043 | 0.19684 | 3.1403 | 2.4582 | 0.75531 | 2.5314 | 0.82855 | 14.4241 | -102.9465 | -102.9922 | 14.4608 | 14.4653 | 14.4104 | 0.041199 | -0.013733 | 3.2135 | 117.6086 | 0.036621 | -0.07782 | 117.3798 | -0.032043 | 117.3065 | 14.3921 | -117.4118 | -102.9144 | 117.5354 | 14.3463 | 4.9576 | 14.3234
3261.1562 | 117.7917 | -14.5569 | 103.1387 | -0.0057221 | 6.9752 | 0.062613 | 0.090845 | 0.00070491 | 0.0030612 | 0.010873 | 0.00018312 | 0.020202 | -1.4512 | 0.006492 | -0.0056226 | 0.016389 | 0.0016877 | -9.288 | 102.8778 | -14.3005 | 103.0746 | -11.3525 | -13.7466 | -12.323 | 0.068665 | -0.032043 | 0.10529 | 0.082397 | 0.15564 | 0.1236 | 0.17395 | 0.25635 | -0.26093 | -0.064087 | 3.2043 | 2.2339 | 0.81024 | 1.9775 | 0.55389 | 14.6622 | -103.1708 | -103.0563 | 14.7125 | 14.7308 | 14.6805 | 0.068664 | 0.01831 | 2.948 | 117.3752 | 0.050354 | -0.022889 | 117.1783 | -0.13733 | 117.4347 | 14.5248 | -117.4393 | -103.0334 | 117.6315 | 14.6393 | 5.2689 | 14.6255
3262.8594 | 117.7963 | -9.2422 | 108.7372 | -0.0057221 | 6.9746 | 0.063254 | 0.096613 | -0.00057689 | 0.0022068 | 0.01301 | -0.0059205 | 0.021698 | -1.4525 | -0.0061118 | -0.0066906 | 0.014039 | 0.00040589 | -2.9251 | 111.0168 | -7.5073 | 111.7355 | -3.2318 | -5.5664 | -3.8132 | 0.036621 | -0.013733 | 0.054932 | 0.054932 | 0.14191 | 0.07782 | 0.14191 | 1.7349 | 2.2797 | 2.9984 | 6.0104 | 5.4291 | 3.6758 | 3.6942 | 1.9409 | 9.2972 | -108.7509 | -108.6823 | 9.3842 | 9.3842 | 9.3201 | 0.086975 | 0.022888 | 4.2755 | 119.2429 | 0.086975 | 0 | 118.5242 | -0.068665 | 120.2591 | 9.2285 | -116.2445 | -108.6823 | 120.9778 | 9.2972 | 6.3171 | 9.2789
3264.6562 | 117.8833 | -10.6476 | 107.0938 | -0.013352 | 6.9742 | 0.06069 | 0.090845 | 0.0034821 | 0.00092496 | 0.015146 | -0.0059205 | 0.02063 | -1.4516 | -0.00055757 | -0.0086132 | 0.013185 | 0.0044647 | -6.4499 | 107.1579 | -10.4828 | 107.373 | -7.4066 | -9.5673 | -8.1345 | -0.045776 | 0.004578 | 0.059509 | -0.013733 | 0.07782 | 0.050354 | 0.10529 | 0.16479 | 0.064087 | 0.27924 | 3.241 | 2.5131 | 1.0803 | 2.3483 | 0.91553 | 10.7071 | -107.0892 | -107.1075 | 10.7254 | 10.7529 | 10.6979 | 0.045777 | -0.009155 | 3.0762 | 117.8558 | 0.018311 | -0.073242 | 117.6407 | -0.054931 | 117.8055 | 10.6522 | -117.5766 | -107.0343 | 118.0206 | 10.6338 | 4.1977 | 10.6018
3266.375 | 118.1076 | -8.8257 | 109.0118 | -0.020981 | 6.9754 | 0.062613 | 0.095118 | 0.0036957 | 0.00028416 | 0.011514 | -0.0028687 | 0.022552 | -1.4508 | -0.002053 | -0.0049818 | 0.014253 | 0.0048919 | -4.8981 | 109.2041 | -8.6884 | 108.8379 | -5.6671 | -7.8918 | -6.6193 | -0.041199 | 0.013733 | 0.064087 | 0.004578 | 0.059509 | 0.013733 | 0.11444 | 0.13733 | 0.19226 | -0.17395 | 3.1586 | 2.2064 | 0.93384 | 2.0691 | 0.79651 | 8.8898 | -108.9981 | -109.0073 | 8.8852 | 8.9401 | 8.8394 | 0.050354 | -0.050354 | 3.0212 | 117.5262 | -0.004578 | -0.059509 | 117.8925 | -0.050354 | 118.0298 | 8.8394 | -117.7002 | -108.9478 | 117.6636 | 8.8303 | 3.9276 | 8.7845
3268.1562 | 117.1188 | -8.7799 | 108.2932 | -0.020981 | 6.975 | 0.061758 | 0.087855 | -0.00057689 | -0.0020658 | 0.012155 | -0.0028687 | 0.020416 | -1.4533 | 0.0058512 | -0.0058362 | 0.015321 | 0.0040375 | -4.6829 | 108.7463 | -8.9676 | 110.0647 | -4.7333 | -7.2052 | -8.0978 | 0.064087 | -0.032043 | 0.073242 | 0.091553 | 0.19684 | 0.15106 | 0.19684 | -0.18768 | 0.45319 | 1.7715 | 4.0466 | 0.68207 | 1.5747 | 0.86975 | 1.7624 | 8.8531 | -108.3252 | -108.2016 | 8.9767 | 8.9767 | 8.931 | 0.1236 | 0.07782 | 4.2343 | 119.0323 | 0.1236 | 0.018311 | 117.7139 | -0.10529 | 117.5262 | 8.7479 | -117.2607 | -108.2199 | 118.8446 | 8.8715 | 4.097 | 8.844
3269.875 | 118.5928 | -7.9514 | 111.0947 | -0.013352 | 6.9748 | 0.062613 | 0.092341 | 0.00027771 | 0.0019932 | 0.013651 | -0.0059205 | 0.02127 | -1.4551 | 0.0037148 | -0.0015638 | 0.016389 | -0.0021575 | -6.4545 | 108.7372 | -8.3862 | 109.7351 | -5.6122 | -7.9285 | -7.0816 | 0.086975 | -0.054932 | 0.073242 | 0.1236 | 0.19684 | 0.13275 | 0.21057 | -0.43487 | -2.3575 | -1.3596 | 2.3392 | 0.86975 | 0.022888 | 1.3046 | 0.45776 | 8.0246 | -111.1496 | -110.9711 | 8.1482 | 8.1619 | 8.0841 | 0.13733 | 0.059509 | 2.774 | 118.1213 | 0.1236 | 0.050354 | 117.1234 | -0.12817 | 116.6885 | 7.8964 | -119.4809 | -111.0214 | 117.6865 | 8.075 | 1.4969 | 8.0383
3271.6562 | 117.8101 | -10.3775 | 107.3639 | -0.0057221 | 6.975 | 0.063467 | 0.090845 | -0.0022857 | 0.0019932 | 0.011728 | -0.0028687 | 0.022979 | -1.4533 | -0.0022666 | -0.0086132 | 0.014039 | -2.1314e-05 | -6.134 | 107.0801 | -10.524 | 107.4829 | -7.3517 | -9.7092 | -8.3496 | 0.022888 | -0.013733 | 0.064087 | 0.004578 | 0.10986 | 0.064087 | 0.11444 | -0.14649 | -0.28381 | 0.11902 | 3.0258 | 2.0279 | 0.66833 | 2.1744 | 0.81482 | 10.4416 | -107.3776 | -107.3593 | 10.4874 | 10.4919 | 10.4416 | 0.050354 | 0 | 3.1723 | 118.0069 | 0.045776 | -0.059509 | 117.6041 | -0.07782 | 117.4576 | 10.3638 | -117.8879 | -107.2998 | 117.8604 | 10.3821 | 4.2435 | 10.4004
3273.375 | 117.8284 | -8.6197 | 109.0256 | 0.0019074 | 6.9735 | 0.064322 | 0.092127 | 6.4114e-05 | 0.0017796 | 0.012155 | -0.0059205 | 0.022125 | -1.4521 | -0.0076072 | -0.0049818 | 0.014039 | -0.00066231 | -3.9917 | 109.9411 | -8.0292 | 108.8837 | -5.8273 | -7.5165 | -6.2759 | -0.050354 | 0 | 0.036621 | -0.009155 | 0.045776 | -0.013733 | 0.09613 | 0.59051 | 0.91553 | -0.14191 | 2.7924 | 2.3438 | 1.1032 | 1.7532 | 0.5127 | 8.6563 | -109.0256 | -109.0347 | 8.6655 | 8.7158 | 8.606 | 0.059509 | -0.050354 | 2.2018 | 116.9128 | 0.009155 | -0.045776 | 117.9703 | -0.036621 | 118.5608 | 8.6197 | -117.0547 | -108.989 | 117.5034 | 8.6105 | 4.628 | 8.5693
3275.1562 | 117.2333 | -15.9897 | 101.0788 | -0.013352 | 6.9735 | 0.060263 | 0.088495 | -0.00079049 | 0.00092496 | 0.012369 | -0.0089723 | 0.021911 | -1.451 | -0.00034397 | -0.0079724 | 0.013185 | 0.0023285 | -10.2585 | 102.2232 | -14.7263 | 100.4837 | -12.9135 | -14.8636 | -13.7833 | -0.054932 | 0.004578 | 0.059509 | -0.004578 | 0.09613 | 0.032043 | 0.11444 | 1.2634 | 1.1444 | -0.59509 | 3.0762 | 2.2064 | 1.1261 | 0.94299 | -0.13733 | 16.0492 | -101.0742 | -101.0834 | 16.0858 | 16.1041 | 16.0217 | 0.054932 | -0.027466 | 1.8127 | 115.21 | 0.036621 | -0.064087 | 116.9495 | -0.054931 | 118.2129 | 15.9943 | -115.8051 | -101.0193 | 116.4734 | 15.9851 | 5.7312 | 15.9348
3276.9375 | 118.0115 | -11.3022 | 106.8832 | -0.0057221 | 6.9737 | 0.06304 | 0.089991 | 0.00049131 | -0.00014304 | 0.011728 | -0.0059205 | 0.022125 | -1.4514 | -0.0016256 | -0.008827 | 0.013612 | 0.0048919 | -6.633 | 106.7963 | -10.7437 | 106.4896 | -7.8461 | -10.2036 | -8.9951 | -0.07782 | 0.004578 | 0.050354 | -0.022888 | 0.073242 | 0.022888 | 0.091553 | 0.55847 | -0.086975 | -0.39368 | 3.4561 | 2.3071 | 1.0986 | 1.7487 | 0.54016 | 11.3525 | -106.8787 | -106.9061 | 11.3754 | 11.3937 | 11.3251 | 0.041199 | -0.027466 | 2.8976 | 117.2333 | 0.022888 | -0.073242 | 117.54 | -0.045776 | 118.0984 | 11.3068 | -117.627 | -106.8329 | 117.7917 | 11.2793 | 4.6692 | 11.2244
3278.7188 | 117.5491 | -14.4424 | 102.8687 | 0.0095369 | 6.9709 | 0.063254 | 0.087427 | 0.0024139 | 0.0022068 | 0.010233 | -0.0028687 | 0.020416 | -1.4516 | 8.3226e-05 | -0.0017774 | 0.01468 | -0.00044851 | -9.1415 | 102.6947 | -14.3326 | 102.9144 | -11.0504 | -13.4811 | -12.1765 | 0.091553 | -0.050354 | 0.054932 | 0.11444 | 0.17395 | 0.11902 | 0.1831 | 0.10986 | -0.17395 | 0.045777 | 3.392 | 2.2659 | 0.9613 | 2.1561 | 0.85144 | 14.4974 | -102.919 | -102.7542 | 14.6164 | 14.6255 | 14.5615 | 0.12817 | 0.064087 | 3.2822 | 117.247 | 0.11902 | 0.059509 | 117.0273 | -0.10529 | 117.1371 | 14.3921 | -117.2012 | -102.8137 | 117.3569 | 14.5569 | 5.3009 | 14.534
3280.4375 | 116.7618 | -7.814 | 107.785 | 0.0019074 | 6.9712 | 0.062186 | 0.090845 | -0.0018585 | 0.00092496 | 0.011301 | -0.0059205 | 0.021057 | -1.4523 | -0.003121 | -0.003059 | 0.013398 | 0.00019229 | -3.3234 | 110.8383 | -7.1274 | 111.0489 | -4.0741 | -6.0196 | -4.8431 | -0.041199 | -0.018311 | 0.036621 | 0.018311 | 0.073242 | 0 | 0.1236 | 0.68665 | 3.0533 | 3.2639 | 3.7399 | 2.9709 | 1.7944 | 2.2842 | 1.1078 | 7.8506 | -107.8033 | -107.7667 | 7.8873 | 7.9376 | 7.814 | 0.086975 | -0.036621 | 3.0533 | 118.1763 | 0.036621 | -0.01831 | 117.9657 | -0.054932 | 118.6523 | 7.7957 | -114.9124 | -107.7484 | 118.8629 | 7.8323 | 4.4907 | 7.7728
3282.2188 | 118.0206 | -9.5718 | 108.2108 | 0.0019074 | 6.9671 | 0.063254 | 0.090845 | 0.0043365 | -0.00014304 | 0.011301 | -0.0028687 | 0.020843 | -1.4538 | 0.003074 | -0.0086132 | 0.015321 | -0.00066231 | -5.0766 | 108.5037 | -9.1324 | 107.7255 | -6.5826 | -8.3221 | -6.8069 | 0.073242 | -0.073242 | 0.068665 | 0.10071 | 0.20599 | 0.14648 | 0.18768 | 0.43945 | 0.29297 | -0.48523 | 2.9892 | 2.7649 | 1.2497 | 2.3254 | 0.81024 | 9.6405 | -108.284 | -108.11 | 9.7778 | 9.7595 | 9.7183 | 0.11902 | 0.077819 | 2.5497 | 116.8579 | 0.13733 | 0.032043 | 117.6361 | -0.14191 | 118.0756 | 9.4986 | -117.3431 | -108.1421 | 117.2974 | 9.6725 | 4.4952 | 9.6451
3283.9844 | 118.5837 | -2.504 | 115.9653 | -0.013352 | 6.9714 | 0.061972 | 0.092341 | 0.0013459 | -0.00035684 | 0.013864 | -0.0028687 | 0.019775 | -1.4525 | 0.0022196 | -0.0051954 | 0.017244 | -0.00023491 | -0.19226 | 116.0522 | -1.9592 | 116.1804 | 0.48065 | -2.1194 | -0.67749 | -0.009155 | -0.064087 | 0.036621 | 0.018311 | 0.10529 | 0.045776 | 0.1236 | 0.54474 | 0.086975 | 0.21515 | 2.9846 | 1.8265 | 0.38452 | 1.2817 | -0.16022 | 2.5406 | -116.0294 | -115.947 | 2.6093 | 2.6276 | 2.5497 | 0.086975 | 0.009155 | 2.4399 | 118.1396 | 0.068665 | -0.01831 | 118.0115 | -0.10071 | 118.5562 | 2.4399 | -117.9245 | -115.9287 | 118.6844 | 2.5223 | 2.3117 | 2.4948
3285.7656 | 118.7576 | -5.8319 | 112.9486 | -0.0057221 | 6.9703 | 0.063254 | 0.092982 | -0.0014313 | -0.00035684 | 0.012796 | -0.0028687 | 0.022339 | -1.4531 | -0.00034397 | -0.0069044 | 0.015321 | 0.00019229 | -2.211 | 113.0997 | -5.5115 | 112.8067 | -3.0029 | -4.9484 | -3.4744 | -0.064087 | -0.018311 | 0.018311 | -0.009155 | 0.045776 | -0.027466 | 0.086975 | 0.32043 | 0.15106 | -0.14191 | 2.829 | 2.3575 | 0.88348 | 2.037 | 0.56305 | 5.8502 | -112.9669 | -112.9578 | 5.8777 | 5.9189 | 5.8044 | 0.068664 | -0.045777 | 2.5085 | 118.3182 | 0.027465 | -0.027466 | 118.6111 | -0.036622 | 118.9316 | 5.8136 | -118.4601 | -112.9303 | 118.6386 | 5.8228 | 3.6209 | 5.7678
3287.5469 | 119.371 | -0.90179 | 118.5287 | 0.0019074 | 6.9682 | 0.061972 | 0.094691 | 0.0036957 | 0.0017796 | 0.013223 | -0.0059205 | 0.023193 | -1.4525 | -0.0026938 | -0.008827 | 0.014253 | 0.0014741 | 1.5472 | 118.4006 | -0.7782 | 118.4235 | 1.6663 | -0.13733 | 1.2268 | -0.009155 | -0.045776 | 0.027466 | 0.009155 | 0.10071 | 0.032043 | 0.10986 | 0.1236 | -0.12817 | -0.10529 | 2.5681 | 2.1286 | 0.76446 | 2.005 | 0.64087 | 0.92926 | -118.5745 | -118.5196 | 1.0025 | 1.0117 | 0.93384 | 0.082397 | 0.004577 | 2.4445 | 119.2017 | 0.073242 | -0.018311 | 119.1788 | -0.073242 | 119.3024 | 0.85602 | -119.3069 | -118.5013 | 119.3253 | 0.91095 | 2.449 | 0.89264
3289.2656 | 119.5679 | -0.76904 | 118.6615 | -0.013352 | 6.9692 | 0.061758 | 0.090632 | -0.0022857 | 7.0564e-05 | 0.01066 | 0.00018312 | 0.02063 | -1.4555 | 0.00093783 | -0.0062634 | 0.015748 | 0.0023285 | 1.5793 | 118.5287 | -0.68665 | 118.6249 | 1.7761 | 0.004578 | 1.3824 | 0.036621 | -0.059509 | 0.036621 | 0.068665 | 0.17395 | 0.11444 | 0.17395 | 0.082397 | -0.13275 | -0.036621 | 2.5452 | 2.1515 | 0.77362 | 2.0691 | 0.69122 | 0.80566 | -118.721 | -118.5928 | 0.94299 | 0.94299 | 0.88348 | 0.13733 | 0.07782 | 2.4628 | 119.3115 | 0.13733 | 0.032044 | 119.2154 | -0.09613 | 119.2978 | 0.70953 | -119.3481 | -118.6249 | 119.3939 | 0.83771 | 2.3483 | 0.80566
3291.0469 | 119.3344 | -1.3275 | 118.0618 | -0.0057221 | 6.9684 | 0.060263 | 0.090418 | -0.0018585 | 7.0564e-05 | 0.011942 | -0.0028687 | 0.020843 | -1.4525 | -0.00483 | -0.010536 | 0.014466 | 0.0027557 | 1.0986 | 117.9245 | -1.268 | 118.1213 | 1.2268 | -0.71869 | 0.78735 | -0.054932 | -0.041199 | 0.027466 | -0.032043 | 0.064087 | -0.022888 | 0.050354 | 0.05951 | -0.13733 | 0.059509 | 2.5543 | 2.1149 | 0.60883 | 2.0554 | 0.54932 | 1.355 | -118.103 | -118.0939 | 1.3916 | 1.3779 | 1.3046 | 0.022888 | -0.050354 | 2.4948 | 119.3893 | 0.036621 | -0.059509 | 119.1925 | -0.068665 | 119.252 | 1.2863 | -119.3298 | -118.0344 | 119.4489 | 1.2955 | 2.4261 | 1.2726
3292.8281 | 119.6869 | -0.84686 | 118.7439 | -0.0057221 | 6.9677 | 0.061118 | 0.09405 | -0.0033539 | 0.00049776 | 0.013864 | -0.0059205 | 0.019348 | -1.4538 | 0.0041422 | -0.0058362 | 0.014253 | -0.0030121 | 1.4969 | 118.5928 | -0.75073 | 118.6707 | 1.6846 | -0.11902 | 1.2634 | -0.032043 | -0.068665 | 0.022888 | 0.027466 | 0.09613 | 0.036621 | 0.1236 | 0.096131 | -0.15106 | -0.073242 | 2.5314 | 2.1103 | 0.72784 | 2.0142 | 0.63171 | 0.86975 | -118.8126 | -118.7164 | 0.94299 | 0.97046 | 0.88348 | 0.10071 | 0.013733 | 2.4353 | 119.4214 | 0.073242 | 0.004578 | 119.3436 | -0.091553 | 119.4397 | 0.7782 | -119.4946 | -118.721 | 119.5175 | 0.87433 | 2.3438 | 0.81482
3294.6094 | 119.7647 | -0.99792 | 118.602 | -0.020981 | 6.9682 | 0.06069 | 0.092768 | 0.00049131 | -0.00014304 | 0.012582 | 0.00018312 | 0.018493 | -1.4533 | -0.003121 | -0.0066906 | 0.013185 | 0.0042511 | 1.4694 | 118.4692 | -0.90637 | 118.6432 | 1.6342 | -0.20599 | 1.1856 | 0.07782 | -0.073242 | 0.036621 | 0.073242 | 0.18768 | 0.11902 | 0.15564 | 0.091553 | -0.13275 | 0.041198 | 2.6321 | 2.1835 | 0.79193 | 2.092 | 0.70038 | 1.0345 | -118.6752 | -118.5287 | 1.1856 | 1.1536 | 1.1169 | 0.11902 | 0.082398 | 2.5406 | 119.5496 | 0.15106 | 0.036621 | 119.3756 | -0.10986 | 119.4672 | 0.92468 | -119.5084 | -118.5654 | 119.6411 | 1.0712 | 2.4673 | 1.0757
3296.3906 | 119.8425 | -0.81024 | 118.9178 | -0.013352 | 6.9686 | 0.061331 | 0.090632 | -0.0050629 | -0.00035684 | 0.013864 | 0.00018312 | 0.019348 | -1.4548 | 0.0056374 | -0.0086132 | 0.012971 | 0.0021149 | 1.6205 | 118.7576 | -0.70953 | 118.9087 | 1.8082 | 0 | 1.387 | 0.064087 | -0.07782 | 0.041199 | 0.059509 | 0.19226 | 0.10986 | 0.16479 | 0.10071 | -0.16022 | -0.009156 | 2.6184 | 2.1973 | 0.81024 | 2.0966 | 0.70953 | 0.85144 | -118.9957 | -118.8583 | 1.0025 | 0.97504 | 0.92011 | 0.1236 | 0.068664 | 2.5177 | 119.6182 | 0.15106 | 0.01831 | 119.4672 | -0.11902 | 119.5679 | 0.73242 | -119.6274 | -118.8766 | 119.7189 | 0.86975 | 2.4307 | 0.87433
3298.0938 | 119.9066 | -0.78735 | 118.9316 | 0.0019074 | 6.9699 | 0.06069 | 0.093195 | 0.0043365 | -0.00099764 | 0.011728 | -0.0059205 | 0.018921 | -1.4523 | 0.0039286 | -0.00092279 | 0.013185 | -0.0015167 | 1.6251 | 118.8492 | -0.70038 | 118.927 | 1.7624 | -0.068665 | 1.3504 | 0.054932 | -0.073242 | 0.013733 | 0.07782 | 0.16022 | 0.082397 | 0.15106 | 0.086976 | -0.082398 | -0.004578 | 2.5497 | 2.1378 | 0.71869 | 2.0508 | 0.63171 | 0.80109 | -119.0048 | -118.8538 | 0.94757 | 0.93842 | 0.86975 | 0.13733 | 0.068664 | 2.4628 | 119.6274 | 0.14648 | 0.064087 | 119.5496 | -0.086975 | 119.6365 | 0.71411 | -119.632 | -118.9178 | 119.7144 | 0.86517 | 2.4124 | 0.84229
3299.875 | 119.8013 | -0.85602 | 119.0277 | -0.013352 | 6.9707 | 0.06304 | 0.09405 | 0.00091851 | 0.0017796 | 0.01301 | 0.00018312 | 0.022339 | -1.4531 | 0.0039286 | -0.0037 | 0.014253 | -2.1314e-05 | 1.5701 | 118.9407 | -0.737 | 118.8766 | 1.6251 | -0.20599 | 1.2268 | -0.13733 | -0.045776 | 0 | -0.054932 | 0.009155 | -0.07782 | 0.054932 | 0.11902 | -0.086975 | -0.15106 | 2.4811 | 2.0828 | 0.65002 | 1.9638 | 0.53101 | 0.85602 | -119.0735 | -119.0826 | 0.86517 | 0.91095 | 0.7782 | 0.054932 | -0.07782 | 2.3621 | 119.6136 | 0.009155 | -0.054932 | 119.6777 | -0.045776 | 119.7968 | 0.81024 | -119.7647 | -119.0277 | 119.7327 | 0.80109 | 2.4261 | 0.71869
3301.6094 | 119.8563 | -0.86517 | 119.0781 | -0.0057221 | 6.9697 | 0.064322 | 0.094691 | 0.00027771 | -0.001852 | 0.01066 | -0.0028687 | 0.02362 | -1.4516 | -0.0016256 | -0.0051954 | 0.015535 | 0.00061949 | 1.5472 | 118.9636 | -0.75989 | 118.9087 | 1.5976 | -0.22888 | 1.2222 | -0.11902 | -0.045776 | 0.013733 | -0.050354 | -0.004578 | -0.064087 | 0.054932 | 0.10528 | -0.11444 | -0.16937 | 2.4628 | 2.0874 | 0.63629 | 1.9821 | 0.53101 | 0.87891 | -119.1238 | -119.1284 | 0.86059 | 0.9201 | 0.80109 | 0.041199 | -0.07782 | 2.3575 | 119.6686 | -0.018311 | -0.064087 | 119.7235 | -0.059509 | 119.8288 | 0.8194 | -119.838 | -119.0643 | 119.7739 | 0.81482 | 2.4124 | 0.74615
3303.3906 | 119.9158 | -0.86975 | 119.1284 | -0.013352 | 6.9707 | 0.064749 | 0.093622 | -0.0029267 | 7.0564e-05 | 0.011514 | 0.00018312 | 0.023407 | -1.4516 | -0.00098477 | -0.006477 | 0.015321 | -0.0030121 | 1.5244 | 119.0002 | -0.76446 | 118.9087 | 1.6205 | -0.21057 | 1.2222 | -0.1236 | -0.032043 | -0.004578 | -0.036621 | 0.013733 | -0.07782 | 0.068665 | 0.10529 | -0.12817 | -0.21973 | 2.4902 | 2.092 | 0.65918 | 1.9867 | 0.55389 | 0.86517 | -119.1605 | -119.165 | 0.88348 | 0.93842 | 0.79193 | 0.073243 | -0.073242 | 2.3849 | 119.6732 | 0.018311 | -0.032043 | 119.7647 | -0.027465 | 119.87 | 0.83771 | -119.8929 | -119.133 | 119.7784 | 0.83313 | 2.3941 | 0.74616
3305.125 | 119.9707 | -0.90637 | 119.1147 | -0.0057221 | 6.9675 | 0.063467 | 0.0964 | -0.0027131 | 0.00049776 | 0.014932 | -0.0059205 | 0.023193 | -1.4527 | -0.0078208 | -0.0056226 | 0.014894 | 0.00040589 | 1.5198 | 119.0186 | -0.79651 | 118.9453 | 1.6251 | -0.23804 | 1.1948 | -0.1236 | -0.045776 | 0.013733 | -0.032043 | 0.009155 | -0.07782 | 0.064087 | 0.10986 | -0.09613 | -0.16937 | 2.5314 | 2.1011 | 0.66833 | 1.9913 | 0.55847 | 0.9201 | -119.1605 | -119.1467 | 0.91553 | 0.97046 | 0.82855 | 0.050354 | -0.091553 | 2.4216 | 119.7418 | -0.004578 | -0.045776 | 119.8151 | -0.059509 | 119.9249 | 0.8606 | -119.9112 | -119.101 | 119.8517 | 0.87433 | 2.4261 | 0.78278
3306.9062 | 120.0943 | -0.83771 | 119.1238 | 0.0019074 | 6.9697 | 0.064536 | 0.093622 | 0.00027771 | 7.0564e-05 | 0.011942 | -0.012024 | 0.020416 | -1.4529 | 8.3226e-05 | -0.0041272 | 0.014466 | -0.00087591 | 1.5701 | 119.0231 | -0.75531 | 119.0964 | 1.7944 | -0.11902 | 1.3046 | 0.041199 | -0.082397 | 0.027466 | 0.054932 | 0.13733 | 0.068665 | 0.12817 | 0.082398 | -0.10071 | -0.027465 | 2.6321 | 2.1423 | 0.71869 | 2.0599 | 0.63629 | 0.86517 | -119.2062 | -119.0689 | 0.97504 | 0.96588 | 0.90637 | 0.10071 | 0.041199 | 2.5497 | 119.8517 | 0.10986 | 0.027466 | 119.7784 | -0.10986 | 119.8608 | 0.75531 | -119.8791 | -119.0964 | 119.9341 | 0.89264 | 2.4078 | 0.87891
3308.625 | 120.0394 | -0.89264 | 119.1696 | -0.013352 | 6.9692 | 0.064749 | 0.096613 | -0.0039947 | 0.0013522 | 0.014719 | -0.0028687 | 0.021484 | -1.4521 | -0.0016256 | -0.0075452 | 0.016603 | -0.0015167 | 1.5656 | 119.0964 | -0.81482 | 119.0735 | 1.6983 | -0.19226 | 1.2268 | -0.059509 | -0.054932 | 0.018311 | -0.036621 | 0.050354 | -0.050354 | 0.068665 | 0.07782 | -0.073242 | -0.096131 | 2.5909 | 2.1194 | 0.70038 | 2.0416 | 0.62256 | 0.91095 | -119.2245 | -119.2062 | 0.94299 | 0.9613 | 0.84228 | 0.050354 | -0.068665 | 2.5131 | 119.8883 | 0.032043 | -0.054932 | 119.9112 | -0.073243 | 119.989 | 0.83771 | -119.9844 | -119.1513 | 119.9661 | 0.85602 | 2.4582 | 0.83313
3310.4062 | 120.1859 | -0.86975 | 119.1925 | -0.0057221 | 6.966 | 0.063895 | 0.092127 | -0.0020721 | -0.00035684 | 0.014719 | -0.0059205 | 0.019134 | -1.4536 | 0.00756 | -0.006477 | 0.013826 | 0.0036103 | 1.5518 | 119.0598 | -0.76904 | 119.1193 | 1.7303 | -0.13275 | 1.2863 | -0.018311 | -0.086975 | 0.013733 | 0.036621 | 0.1236 | 0.050354 | 0.12817 | 0.10071 | -0.13275 | -0.073242 | 2.6001 | 2.1561 | 0.737 | 2.0554 | 0.63629 | 0.88348 | -119.2795 | -119.1559 | 0.99335 | 0.99793 | 0.92011 | 0.11444 | 0.036621 | 2.4994 | 119.8883 | 0.10986 | 0.022888 | 119.8288 | -0.10071 | 119.9295 | 0.78278 | -119.9615 | -119.1788 | 119.989 | 0.90637 | 2.4216 | 0.85144
3312.125 | 120.1172 | -0.90179 | 119.2657 | -0.0057221 | 6.969 | 0.064322 | 0.095331 | 0.0043365 | 7.0564e-05 | 0.010019 | -0.0059205 | 0.022766 | -1.4519 | 0.0035012 | -0.0051954 | 0.01468 | 0.0023285 | 1.5244 | 119.1788 | -0.81482 | 119.0918 | 1.6525 | -0.24261 | 1.1948 | -0.086975 | -0.054932 | 0 | -0.041199 | 0.018311 | -0.07782 | 0.050354 | 0.086975 | -0.086975 | -0.17395 | 2.5543 | 2.0966 | 0.65918 | 2.0096 | 0.5722 | 0.90179 | -119.3207 | -119.3069 | 0.9201 | 0.95215 | 0.82397 | 0.050354 | -0.07782 | 2.4673 | 119.9066 | 0.018311 | -0.041199 | 119.9936 | -0.054932 | 120.0806 | 0.84686 | -120.0806 | -119.2657 | 119.9936 | 0.86059 | 2.4261 | 0.81482
3313.9062 | 120.1813 | -0.92926 | 119.2657 | 0.0095369 | 6.9695 | 0.065176 | 0.093622 | -0.00057689 | 0.00028416 | 0.014932 | -0.0028687 | 0.020202 | -1.4531 | -0.0044028 | -0.0060498 | 0.014253 | 0.0033967 | 1.5701 | 119.1834 | -0.81482 | 119.1605 | 1.712 | -0.1831 | 1.2405 | -0.018311 | -0.059509 | 0.022888 | 0.004578 | 0.07782 | -0.013733 | 0.07782 | 0.11444 | -0.082397 | -0.10529 | 2.6413 | 2.1698 | 0.74616 | 2.0554 | 0.63171 | 0.95215 | -119.3253 | -119.2612 | 1.0071 | 1.0071 | 0.91553 | 0.054932 | -0.036621 | 2.5269 | 119.9753 | 0.054932 | -0.01831 | 119.9982 | -0.082397 | 120.1126 | 0.86975 | -120.0806 | -119.2429 | 120.0897 | 0.93384 | 2.4994 | 0.91095
3315.7031 | 120.3186 | -0.90637 | 119.2566 | -0.013352 | 6.9695 | 0.064108 | 0.093195 | 0.00049131 | 0.00028416 | 0.013864 | -0.0028687 | 0.02063 | -1.4512 | 0.006492 | -0.0041272 | 0.015321 | -0.0030121 | 1.6159 | 119.1422 | -0.80566 | 119.2474 | 1.7853 | -0.15564 | 1.2863 | 0.068665 | -0.073242 | 0.032043 | 0.07782 | 0.15564 | 0.082397 | 0.16937 | 0.10071 | -0.11444 | -0.009155 | 2.6917 | 2.1927 | 0.75073 | 2.092 | 0.65002 | 0.93841 | -119.3298 | -119.1788 | 1.062 | 1.0757 | 0.98877 | 0.13733 | 0.050354 | 2.5909 | 120.0531 | 0.1236 | 0.045777 | 119.9478 | -0.10529 | 120.0485 | 0.83313 | -120.0623 | -119.2245 | 120.1538 | 0.98419 | 2.5223 | 0.97504
3317.4688 | 120.3003 | -0.93384 | 119.2612 | -0.02861 | 6.9677 | 0.06539 | 0.093409 | 0.0030547 | 0.00049776 | 0.01301 | -0.0059205 | 0.019989 | -1.4544 | -0.00077117 | -0.0058362 | 0.016175 | -2.1314e-05 | 1.593 | 119.165 | -0.82398 | 119.252 | 1.7532 | -0.17853 | 1.2634 | 0.068665 | -0.086975 | 0.045776 | 0.068665 | 0.12817 | 0.064087 | 0.13275 | 0.10986 | -0.09613 | -0.009155 | 2.6871 | 2.1973 | 0.75531 | 2.0874 | 0.64545 | 0.97961 | -119.3481 | -119.1925 | 1.062 | 1.0666 | 0.99792 | 0.086975 | 0.018311 | 2.5772 | 120.076 | 0.082398 | 0.022889 | 119.989 | -0.13275 | 120.0989 | 0.84686 | -120.0851 | -119.2154 | 120.1859 | 1.0025 | 2.5269 | 1.0025
3319.2031 | 120.3781 | -0.95673 | 119.2886 | -0.013352 | 6.9686 | 0.063681 | 0.092982 | -0.0024995 | -0.001852 | 0.012796 | -0.0028687 | 0.017852 | -1.4527 | -0.00055757 | -0.0075452 | 0.01468 | 0.0023285 | 1.5656 | 119.1467 | -0.8606 | 119.2383 | 1.7212 | -0.17853 | 1.2634 | 0.050354 | -0.082397 | 0.018311 | 0.054932 | 0.15564 | 0.10986 | 0.15106 | 0.09613 | -0.14191 | -0.050354 | 2.6779 | 2.2202 | 0.7782 | 2.124 | 0.68207 | 0.97504 | -119.371 | -119.2337 | 1.1124 | 1.1078 | 1.0666 | 0.13275 | 0.091552 | 2.5818 | 120.0989 | 0.13733 | 0.036621 | 120.0073 | -0.10071 | 120.1035 | 0.87433 | -120.1492 | -119.2703 | 120.195 | 1.0117 | 2.5223 | 1.0071
3320.9844 | 120.2957 | -1.0071 | 119.339 | -0.0057221 | 6.9688 | 0.062827 | 0.09405 | -0.0039947 | -0.00078404 | 0.010019 | -0.0028687 | 0.020202 | -1.454 | 0.003074 | -0.010536 | 0.013612 | 0.0010467 | 1.5656 | 119.1834 | -0.87433 | 119.2017 | 1.6708 | -0.26093 | 1.1765 | -0.073242 | -0.045776 | -0.009155 | -0.068665 | 0.041199 | -0.032043 | 0.036621 | 0.13275 | -0.15564 | -0.13733 | 2.6779 | 2.1835 | 0.74615 | 2.0508 | 0.6134 | 0.99792 | -119.3848 | -119.4077 | 1.0483 | 1.0437 | 0.97504 | 0.045776 | -0.022888 | 2.5452 | 120.076 | 0.050354 | -0.05951 | 120.0577 | -0.036621 | 120.1904 | 0.9613 | -120.2133 | -119.3481 | 120.2087 | 0.93841 | 2.5726 | 0.93384
3322.7656 | 120.4605 | -0.97961 | 119.2932 | -0.013352 | 6.9686 | 0.064749 | 0.09405 | -0.0022857 | 0.0028476 | 0.013437 | -0.0028687 | 0.019561 | -1.4529 | 0.0037148 | -0.0024182 | 0.014894 | -0.0027985 | 1.6113 | 119.1971 | -0.86975 | 119.2932 | 1.7212 | -0.2243 | 1.2314 | 0.068665 | -0.082397 | 0.022888 | 0.07782 | 0.15106 | 0.073242 | 0.16022 | 0.10986 | -0.09613 | 0 | 2.7008 | 2.211 | 0.75531 | 2.1011 | 0.64545 | 1.0025 | -119.3756 | -119.2154 | 1.1307 | 1.1398 | 1.0529 | 0.13733 | 0.050354 | 2.5909 | 120.163 | 0.12817 | 0.054932 | 120.0668 | -0.10528 | 120.1767 | 0.89722 | -120.163 | -119.2703 | 120.2728 | 1.0574 | 2.5909 | 1.0483
3324.5469 | 120.4788 | -0.97961 | 119.3527 | -0.0057221 | 6.9692 | 0.063467 | 0.094904 | -0.0016449 | -0.0016384 | 0.010019 | -0.0028687 | 0.020202 | -1.4531 | 0.0043558 | -0.0073316 | 0.013185 | -2.1314e-05 | 1.5839 | 119.2337 | -0.89722 | 119.2978 | 1.7029 | -0.20142 | 1.2451 | 0.045776 | -0.086975 | 0.027466 | 0.073242 | 0.15106 | 0.091553 | 0.15106 | 0.082397 | -0.11902 | -0.054931 | 2.6825 | 2.2247 | 0.7782 | 2.1423 | 0.6958 | 1.0071 | -119.4397 | -119.2795 | 1.1307 | 1.1307 | 1.0712 | 0.1236 | 0.064087 | 2.6001 | 120.195 | 0.1236 | 0.045776 | 120.1309 | -0.11444 | 120.2133 | 0.89264 | -120.2499 | -119.3253 | 120.2774 | 1.0529 | 2.5635 | 1.0254
3326.3438 | 120.369 | -1.0208 | 119.3939 | 0.0019074 | 6.968 | 0.061972 | 0.09939 | 0.0066863 | -0.00014304 | 0.014719 | -0.0028687 | 0.025329 | -1.4508 | -0.0024802 | -0.0056226 | 0.01468 | 0.0021149 | 1.5427 | 119.2886 | -0.9201 | 119.2291 | 1.5976 | -0.3479 | 1.1032 | -0.10071 | -0.045776 | 0.004578 | -0.045776 | 0.009155 | -0.073242 | 0.045776 | 0.10071 | -0.10529 | -0.1648 | 2.6184 | 2.124 | 0.67291 | 2.0233 | 0.5722 | 1.0254 | -119.4397 | -119.4397 | 1.03 | 1.0666 | 0.94757 | 0.041198 | -0.07782 | 2.5177 | 120.1492 | 0.004577 | -0.050354 | 120.2087 | -0.050354 | 120.3094 | 0.97504 | -120.314 | -119.3893 | 120.2499 | 0.97504 | 2.5635 | 0.9201
3328.0469 | 120.3918 | -1.0254 | 119.4077 | -0.013352 | 6.9695 | 0.063681 | 0.097468 | 0.0049773 | 0.00071136 | 0.013651 | 0.00018312 | 0.024475 | -1.4523 | -0.0063254 | -0.0073316 | 0.014466 | -0.0015167 | 1.5656 | 119.3253 | -0.92468 | 119.2383 | 1.6067 | -0.36621 | 1.1124 | -0.11902 | -0.050354 | -0.022888 | -0.045776 | -0.004578 | -0.07782 | 0.032043 | 0.10071 | -0.082398 | -0.16937 | 2.6321 | 2.1378 | 0.65918 | 2.037 | 0.55847 | 1.0025 | -119.458 | -119.4534 | 1.0208 | 1.0574 | 0.94757 | 0.054931 | -0.054932 | 2.5314 | 120.163 | 0.01831 | -0.022888 | 120.2499 | -0.027466 | 120.3506 | 0.97504 | -120.3323 | -119.4305 | 120.2637 | 0.97961 | 2.5909 | 0.90637
3329.8281 | 120.4651 | -3.3463 | 117.0547 | -0.0057221 | 6.9673 | 0.061545 | 0.097468 | 0.0032685 | -0.00078404 | 0.017496 | -0.0028687 | 0.021698 | -1.4529 | -0.0035482 | -0.0075452 | 0.014894 | 0.00040589 | -0.082397 | 116.954 | -3.2639 | 116.9357 | -0.4303 | -2.5726 | -1.1673 | -0.28381 | -0.2243 | -0.19226 | -0.21057 | -0.11902 | -0.22888 | -0.10986 | 0.082397 | -0.10071 | -0.11902 | 2.916 | 2.179 | 0.77362 | 2.0966 | 0.69122 | 3.154 | -117.2791 | -117.2653 | 3.2272 | 3.2364 | 3.1174 | 0.082398 | -0.036621 | 2.8336 | 120.1996 | 0.073242 | -0.01831 | 120.2179 | -0.032043 | 120.3003 | 3.1219 | -120.3186 | -117.247 | 120.282 | 3.1357 | 3.2639 | 3.0624
3331.5469 | 120.4056 | -5.2917 | 115.1093 | -0.0057221 | 6.9682 | 0.061972 | 0.0964 | -0.00079049 | -0.0012112 | 0.011514 | -0.0059205 | 0.021484 | -1.4527 | -0.003121 | -0.009895 | 0.012544 | 0.0010467 | -1.5564 | 114.9948 | -5.191 | 114.9673 | -2.1881 | -4.4861 | -3.0945 | -0.43945 | -0.39825 | -0.36621 | -0.41657 | -0.29755 | -0.41657 | -0.32501 | 0.10071 | -0.11444 | -0.14191 | 3.1036 | 2.1973 | 0.80566 | 2.0966 | 0.70496 | 4.9255 | -115.5075 | -115.5258 | 4.9942 | 4.9667 | 4.8752 | 0.041199 | -0.050354 | 3.0029 | 120.1584 | 0.068665 | -0.050354 | 120.1859 | -0.032043 | 120.2866 | 4.8935 | -120.3003 | -115.4755 | 120.2591 | 4.8752 | 3.7354 | 4.8523
3333.3125 | 120.433 | -6.459 | 113.9648 | -0.0057221 | 6.9692 | 0.064536 | 0.094691 | -0.00057689 | 0.00028416 | 0.015146 | -0.0059205 | 0.022125 | -1.4523 | -0.00077117 | -0.008186 | 0.011476 | -0.00044851 | -2.417 | 113.8733 | -6.3766 | 113.7955 | -3.2593 | -5.6442 | -4.2664 | -0.52185 | -0.49896 | -0.46692 | -0.51727 | -0.39368 | -0.50354 | -0.41657 | 0.082397 | -0.091553 | -0.16937 | 3.1998 | 2.1927 | 0.81482 | 2.1103 | 0.73242 | 5.9921 | -114.4638 | -114.4821 | 6.0654 | 6.0425 | 5.9555 | 0.050354 | -0.036621 | 3.1174 | 120.1721 | 0.073242 | -0.050354 | 120.2499 | -0.032043 | 120.3323 | 5.9601 | -120.3415 | -114.4318 | 120.2545 | 5.9418 | 4.0421 | 5.9372
3335.0156 | 120.5292 | -7.6355 | 112.7151 | -0.0057221 | 6.9705 | 0.065604 | 0.095545 | 0.0047637 | 0.0028476 | 0.012796 | -0.0028687 | 0.022339 | -1.4529 | -0.0039756 | -0.0037 | 0.015748 | 0.0029693 | -3.3325 | 112.6465 | -7.576 | 112.6465 | -4.335 | -6.8207 | -5.4657 | -0.4715 | -0.56305 | -0.46692 | -0.45776 | -0.3479 | -0.48523 | -0.36163 | 0.059509 | -0.068665 | -0.068665 | 3.3005 | 2.1698 | 0.81482 | 2.1103 | 0.75531 | 7.1686 | -113.2782 | -113.1729 | 7.2876 | 7.2739 | 7.1503 | 0.10529 | -0.01831 | 3.241 | 120.2225 | 0.11902 | 0.009155 | 120.2225 | -0.09613 | 120.282 | 7.0724 | -120.2911 | -113.1821 | 120.282 | 7.1777 | 4.303 | 7.164
3336.8125 | 120.4285 | -6.9855 | 113.443 | -0.013352 | 6.9707 | 0.066245 | 0.095759 | -0.0012177 | 0.0022068 | 0.014719 | -0.0059205 | 0.022125 | -1.4527 | 0.0017922 | -0.005409 | 0.014039 | 0.0051057 | -2.7512 | 113.3972 | -6.8756 | 113.3102 | -3.7262 | -6.189 | -4.8203 | -0.53558 | -0.49439 | -0.42572 | -0.51727 | -0.42572 | -0.54474 | -0.40283 | 0.10986 | -0.045776 | -0.13275 | 3.2593 | 2.1652 | 0.79651 | 2.0554 | 0.68665 | 6.5598 | -113.9374 | -113.9603 | 6.5598 | 6.5826 | 6.4407 | 0.022888 | -0.11902 | 3.1494 | 120.1859 | 0 | -0.091553 | 120.2728 | -0.068665 | 120.3827 | 6.4911 | -120.3186 | -113.8687 | 120.2957 | 6.4682 | 4.2343 | 6.4499
3338.5938 | 120.4788 | -6.5186 | 113.9648 | -0.013352 | 6.9701 | 0.062613 | 0.093836 | 0.0034821 | -0.00099764 | 0.014291 | -0.0089723 | 0.019561 | -1.4519 | -0.0011984 | -0.0096814 | 0.014466 | -2.1314e-05 | -2.3621 | 113.8184 | -6.3995 | 113.8367 | -3.2181 | -5.6534 | -4.2892 | -0.55847 | -0.58136 | -0.49896 | -0.5722 | -0.42572 | -0.56763 | -0.50354 | 0.11902 | -0.14648 | -0.12817 | 3.3005 | 2.2293 | 0.86517 | 2.1103 | 0.74615 | 6.0196 | -114.5462 | -114.537 | 6.0928 | 6.015 | 5.9509 | -0.004578 | -0.068665 | 3.1815 | 120.2362 | 0.073242 | -0.073243 | 120.2179 | -0.082398 | 120.3369 | 5.9372 | -120.3644 | -114.4638 | 120.3552 | 5.9463 | 4.1565 | 5.9601
3340.375 | 120.4788 | -10.08 | 110.408 | -0.013352 | 6.9695 | 0.065176 | 0.09405 | -0.00014949 | 0.0028476 | 0.012369 | -0.0028687 | 0.021698 | -1.4516 | -0.0018394 | -0.0079724 | 0.011903 | -0.0010895 | -5.1636 | 110.2707 | -9.9747 | 110.2295 | -6.5964 | -9.2331 | -7.869 | -0.72327 | -0.73242 | -0.68207 | -0.72327 | -0.59052 | -0.73242 | -0.63171 | 0.10529 | -0.13733 | -0.17853 | 3.4836 | 2.211 | 0.84686 | 2.1057 | 0.74158 | 9.3979 | -111.1404 | -111.1313 | 9.4894 | 9.4482 | 9.3475 | 0.050354 | -0.050354 | 3.3783 | 120.2042 | 0.091553 | -0.041199 | 120.2454 | -0.050354 | 120.3506 | 9.3475 | -120.3827 | -111.0901 | 120.3094 | 9.3567 | 4.9164 | 9.3567
3342.1094 | 120.6116 | -11.618 | 108.6823 | -0.0057221 | 6.9677 | 0.064536 | 0.092768 | -0.0029267 | 0.0017796 | 0.01301 | -0.0059205 | 0.018493 | -1.4533 | 0.0039286 | -0.0077588 | 0.012971 | 0.00061949 | -6.3721 | 108.6136 | -11.5356 | 108.7326 | -7.9742 | -10.6842 | -9.3796 | -0.75531 | -0.99335 | -0.85144 | -0.82398 | -0.62256 | -0.8194 | -0.737 | 0.082397 | -0.068665 | 0.050354 | 3.6438 | 2.2385 | 0.93384 | 2.1561 | 0.85144 | 10.7666 | -109.6756 | -109.5062 | 10.9955 | 10.881 | 10.7986 | 0.11444 | 0.032043 | 3.5614 | 120.2683 | 0.22888 | 0.027465 | 120.1492 | -0.14191 | 120.2316 | 10.6247 | -120.2179 | -109.5337 | 120.3506 | 10.7941 | 5.246 | 10.8627
3343.875 | 120.4468 | -16.4795 | 103.8757 | -0.0057221 | 6.968 | 0.066672 | 0.093836 | 0.0015595 | 0.0013522 | 0.014932 | -0.0028687 | 0.019989 | -1.4514 | -0.0095298 | -0.0077588 | 0.012117 | -0.00023491 | -10.2585 | 103.7201 | -16.4291 | 103.7567 | -12.5977 | -15.5823 | -14.3051 | -1.0986 | -1.1581 | -1.0941 | -1.1536 | -0.95215 | -1.181 | -1.0529 | 0.050354 | -0.15564 | -0.11902 | 3.8818 | 2.1744 | 0.89722 | 2.124 | 0.84686 | 15.3854 | -105.0339 | -105.0293 | 15.5273 | 15.4266 | 15.2985 | 0.041199 | -0.086975 | 3.8315 | 120.1859 | 0.14191 | -0.059509 | 120.1492 | -0.064087 | 120.1996 | 15.3214 | -120.3049 | -104.9698 | 120.2362 | 15.3259 | 6.221 | 15.3809
3345.6562 | 120.5154 | -11.7828 | 108.5449 | -0.0057221 | 6.9686 | 0.066885 | 0.093195 | -0.0010041 | 0.0015658 | 0.014505 | 0.00018312 | 0.018707 | -1.4531 | 0.0069192 | -0.0041272 | 0.018525 | 0.0010467 | -6.427 | 108.4717 | -11.6226 | 108.5999 | -8.0383 | -10.8307 | -9.5306 | -0.75989 | -0.96588 | -0.83313 | -0.82398 | -0.66376 | -0.86517 | -0.75073 | 0.16022 | -0.073242 | 0.054932 | 3.7445 | 2.2522 | 0.95215 | 2.092 | 0.79193 | 10.9497 | -109.5108 | -109.3689 | 11.1191 | 11.0321 | 10.9177 | 0.082398 | -0.032043 | 3.5843 | 120.2225 | 0.16937 | 0.009155 | 120.0943 | -0.13275 | 120.2545 | 10.817 | -120.1675 | -109.3781 | 120.3827 | 10.9589 | 5.3558 | 11.0229
3347.3594 | 120.4697 | -16.0629 | 104.2282 | -0.0057221 | 6.9682 | 0.065817 | 0.093409 | -0.0016449 | 0.0011386 | 0.016641 | -0.0028687 | 0.020843 | -1.4536 | -0.00483 | -0.0066906 | 0.016603 | 0.0010467 | -9.9197 | 104.1229 | -15.9805 | 104.1916 | -12.1582 | -15.1245 | -13.8702 | -0.97046 | -1.1215 | -1.0025 | -1.0162 | -0.84686 | -1.0254 | -0.91553 | 0.082397 | -0.10529 | -0.036621 | 3.9047 | 2.1927 | 0.93841 | 2.1103 | 0.85602 | 15.0604 | -105.3497 | -105.2444 | 15.2161 | 15.1474 | 15.0375 | 0.086975 | -0.022889 | 3.8223 | 120.1721 | 0.15564 | -0.013733 | 120.1035 | -0.11902 | 120.1859 | 14.9414 | -120.2087 | -105.2307 | 120.2545 | 15.0467 | 6.1432 | 15.0925
3349.1406 | 120.575 | -6.5048 | 113.9465 | -0.0057221 | 6.9675 | 0.06539 | 0.096186 | -0.0031403 | 7.0564e-05 | 0.014505 | 0.0032349 | 0.021698 | -1.4533 | -0.001412 | -0.0049818 | 0.013612 | -0.0015167 | -2.3071 | 113.8092 | -6.395 | 113.9374 | -3.1128 | -5.6305 | -4.2206 | -0.34332 | -0.54016 | -0.41199 | -0.37079 | -0.2655 | -0.42114 | -0.31586 | 0.10986 | -0.13733 | -0.009155 | 3.392 | 2.2842 | 0.87433 | 2.1744 | 0.76446 | 6.0928 | -114.4867 | -114.3173 | 6.2393 | 6.189 | 6.0837 | 0.09613 | -0.009156 | 3.2822 | 120.3323 | 0.14648 | 0.041198 | 120.2042 | -0.12817 | 120.314 | 5.9647 | -120.3415 | -114.3585 | 120.4422 | 6.134 | 4.1977 | 6.1615
3350.9062 | 120.5292 | -5.6946 | 114.8529 | -0.013352 | 6.9677 | 0.063681 | 0.095118 | -0.0012177 | 0.00028416 | 0.017069 | -0.0028687 | 0.022125 | -1.4531 | -0.0088888 | -0.0083996 | 0.014039 | 0.0012603 | -1.6754 | 114.6652 | -5.6076 | 114.7202 | -2.3895 | -4.8203 | -3.4012 | -0.3891 | -0.42572 | -0.34332 | -0.40283 | -0.27924 | -0.39825 | -0.31586 | 0.086975 | -0.18768 | -0.13275 | 3.3051 | 2.2934 | 0.87433 | 2.2064 | 0.78735 | 5.3513 | -115.2786 | -115.2557 | 5.4153 | 5.3787 | 5.2963 | 0.027466 | -0.054931 | 3.2181 | 120.3278 | 0.064087 | -0.059509 | 120.2728 | -0.082397 | 120.3598 | 5.2689 | -120.4605 | -115.1962 | 120.4147 | 5.2917 | 4.0192 | 5.3055
3352.625 | 120.5704 | -7.1503 | 113.3835 | -0.013352 | 6.9701 | 0.064536 | 0.097681 | 0.0013459 | 0.002634 | 0.015573 | 0.00018312 | 0.021911 | -1.4525 | -0.0016256 | -0.0058362 | 0.015535 | 0.00061949 | -2.8107 | 113.2599 | -7.077 | 113.3102 | -3.7216 | -6.2714 | -4.8935 | -0.44403 | -0.54474 | -0.48065 | -0.47607 | -0.35248 | -0.52643 | -0.42572 | 0.073243 | -0.1236 | -0.073242 | 3.4286 | 2.2568 | 0.87891 | 2.1835 | 0.80566 | 6.6696 | -113.9282 | -113.8596 | 6.7978 | 6.7245 | 6.6238 | 0.054932 | -0.045776 | 3.3554 | 120.3873 | 0.12817 | 0.004578 | 120.3369 | -0.064087 | 120.4102 | 6.6055 | -120.4605 | -113.8641 | 120.4605 | 6.6742 | 4.3396 | 6.7062
3354.4062 | 120.4926 | -15.3946 | 105.0613 | -0.0057221 | 6.9714 | 0.067099 | 0.098109 | 0.0026275 | 0.002634 | 0.014291 | -0.0028687 | 0.019134 | -1.4516 | -0.0076072 | -0.0058362 | 0.015748 | -0.00066231 | -9.1873 | 105.1575 | -15.1016 | 105.1209 | -11.348 | -14.328 | -13.0142 | -0.98877 | -0.99335 | -0.94757 | -1.0529 | -0.8606 | -1.0941 | -0.93384 | 0.29297 | 0.096131 | 0.05951 | 4.0466 | 2.3804 | 1.0666 | 2.0874 | 0.77362 | 14.447 | -106.0547 | -106.1142 | 14.534 | 14.4608 | 14.3005 | 0.013733 | -0.14648 | 3.7537 | 120.2225 | 0.086975 | -0.10528 | 120.2591 | -0.045776 | 120.5521 | 14.4012 | -120.163 | -106.0089 | 120.5154 | 14.3417 | 6.2073 | 14.4058
3356.1406 | 120.5109 | -8.9172 | 111.5845 | 0.0019074 | 6.9684 | 0.063681 | 0.0964 | -0.0016449 | 0.0022068 | 0.013651 | -0.0059205 | 0.02063 | -1.4531 | 0.0026468 | -0.005409 | 0.015321 | 0.0029693 | -4.248 | 111.3831 | -8.9127 | 111.3007 | -5.5344 | -8.2123 | -6.8253 | -0.64545 | -0.67291 | -0.63171 | -0.66376 | -0.54932 | -0.70953 | -0.58594 | 0.004577 | -0.20142 | -0.28381 | 3.3829 | 2.092 | 0.70496 | 2.0874 | 0.70038 | 8.2855 | -112.2574 | -112.2482 | 8.3679 | 8.3313 | 8.2077 | 0.045777 | -0.07782 | 3.3783 | 120.2133 | 0.082398 | -0.032043 | 120.2957 | -0.041199 | 120.3003 | 8.2443 | -120.4971 | -112.2162 | 120.2179 | 8.2535 | 4.6692 | 8.2718
3357.9062 | 120.4468 | -28.1708 | 91.9235 | -0.013352 | 6.9667 | 0.066672 | 0.08935 | 0.00091851 | 0.0032748 | 0.017496 | -0.0059205 | 0.018707 | -1.454 | -0.0046164 | -0.0069044 | 0.015107 | -2.1314e-05 | -19.4778 | 91.7679 | -28.157 | 91.9647 | -23.291 | -27.0493 | -25.9689 | -1.561 | -1.9089 | -1.7487 | -1.8585 | -1.5289 | -1.8631 | -1.7761 | 0.013733 | -0.15564 | 0.041199 | 4.8798 | 2.2018 | 1.1215 | 2.1881 | 1.1078 | 26.4221 | -93.8324 | -93.782 | 26.6418 | 26.3947 | 26.3077 | -0.027466 | -0.11444 | 4.866 | 120.1218 | 0.21973 | -0.10986 | 119.9249 | -0.16022 | 119.9387 | 26.2619 | -120.0806 | -93.6722 | 120.1355 | 26.3123 | 8.6929 | 26.6098
3359.6875 | 120.3232 | -33.4671 | 86.5173 | -0.020981 | 6.9692 | 0.066885 | 0.089777 | -0.0037811 | 0.0049838 | 0.015146 | -0.0028687 | 0.018707 | -1.4542 | -0.00077117 | -0.0066906 | 0.014894 | -0.00044851 | -23.5931 | 86.4532 | -33.3389 | 86.673 | -28.157 | -32.1625 | -31.1234 | -2.092 | -2.4857 | -2.33 | -2.3941 | -2.0187 | -2.4124 | -2.3026 | 0.12817 | -0.064087 | 0.15564 | 5.3101 | 2.3437 | 1.3046 | 2.2156 | 1.1765 | 31.1371 | -89.003 | -88.9114 | 31.4484 | 31.1646 | 31.0547 | 0.027466 | -0.082398 | 5.1819 | 120.0119 | 0.31128 | -0.064087 | 119.7922 | -0.15564 | 119.9203 | 30.9814 | -119.8563 | -88.8474 | 120.1401 | 31.073 | 9.874 | 31.3751
3361.4688 | 120.4239 | -31.3477 | 88.6597 | -0.0057221 | 6.9682 | 0.069449 | 0.093195 | 0.0034821 | 0.0032748 | 0.01536 | -0.0028687 | 0.019561 | -1.4538 | 0.00051063 | -0.0011364 | 0.017671 | -0.0021575 | -21.6705 | 88.9252 | -31.0089 | 88.9984 | -26.1291 | -29.9377 | -28.8712 | -2.0325 | -2.4857 | -2.2705 | -2.3575 | -1.9592 | -2.3575 | -2.1973 | 0.33874 | 0.2655 | 0.33875 | 5.2185 | 2.4765 | 1.4099 | 2.1378 | 1.0712 | 29.0771 | -91.1453 | -91.0172 | 29.3884 | 29.1504 | 28.9902 | 0.073242 | -0.086975 | 4.8798 | 120.0073 | 0.31128 | -0.086975 | 119.9341 | -0.21515 | 120.2728 | 28.862 | -119.6686 | -90.9302 | 120.3461 | 28.9902 | 9.6771 | 29.3152
3363.1875 | 120.4559 | -14.5981 | 105.5603 | -0.013352 | 6.9684 | 0.066245 | 0.095331 | -0.0035675 | 0.002634 | 0.014719 | -0.0059205 | 0.020843 | -1.4523 | 0.0045694 | -0.003059 | 0.014253 | -0.0010895 | -8.6334 | 105.6473 | -14.4516 | 105.6427 | -10.6384 | -13.6597 | -12.3459 | -0.97961 | -1.1765 | -1.0254 | -1.0391 | -0.83771 | -1.0803 | -0.95673 | 0.14648 | 0.086975 | 0.082397 | 3.9597 | 2.2522 | 0.93842 | 2.1057 | 0.79193 | 13.5727 | -106.7368 | -106.5994 | 13.7604 | 13.6414 | 13.5178 | 0.068665 | -0.054931 | 3.8132 | 120.0943 | 0.18768 | -0.013733 | 120.0989 | -0.15106 | 120.2454 | 13.4216 | -120.0119 | -106.5857 | 120.2408 | 13.559 | 5.9647 | 13.6185
3364.9531 | 120.4147 | -21.2997 | 98.9365 | -0.013352 | 6.9686 | 0.067954 | 0.093195 | -0.0048493 | 0.0034884 | 0.012582 | -0.0059205 | 0.018921 | -1.4533 | 0.0028604 | -0.0060498 | 0.01703 | 0.0029693 | -14.0259 | 98.7717 | -21.2402 | 98.8724 | -16.9189 | -20.3156 | -19.1071 | -1.7029 | -2.0599 | -1.8814 | -1.9821 | -1.5839 | -1.9638 | -1.8127 | 0.05951 | -0.1648 | -0.064087 | 4.3808 | 2.1927 | 0.98419 | 2.1332 | 0.92468 | 19.4183 | -100.9964 | -100.9186 | 19.7159 | 19.487 | 19.3359 | 0.068665 | -0.082397 | 4.3213 | 120.1126 | 0.29755 | -0.10071 | 120.0119 | -0.17853 | 120.0714 | 19.2398 | -120.1767 | -100.8179 | 120.1721 | 19.3176 | 7.2739 | 19.5969
3366.75 | 120.575 | -11.8103 | 108.5266 | -0.0057221 | 6.9677 | 0.064322 | 0.092982 | 0.00070491 | 0.0015658 | 0.011301 | -0.0059205 | 0.017425 | -1.4551 | 0.0020058 | -0.0077588 | 0.015535 | -0.00023491 | -6.2897 | 108.4763 | -11.6638 | 108.7738 | -7.6904 | -10.6796 | -9.3018 | -0.70953 | -0.97504 | -0.82855 | -0.86517 | -0.60883 | -0.83313 | -0.72327 | 0.14649 | -0.050354 | 0.24719 | 4.1199 | 2.5085 | 1.1307 | 2.3621 | 0.98419 | 10.9818 | -109.5016 | -109.3918 | 11.2015 | 11.087 | 10.9772 | 0.10528 | -0.004578 | 3.9734 | 120.4376 | 0.21973 | -0.036621 | 120.1401 | -0.14649 | 120.2866 | 10.8353 | -120.1904 | -109.3552 | 120.5841 | 10.9451 | 5.5206 | 11.1008
3368.4688 | 120.3964 | -15.5731 | 104.8462 | -0.0057221 | 6.9686 | 0.064963 | 0.093409 | 0.0015595 | 0.0011386 | 0.013651 | -0.0028687 | 0.023407 | -1.4546 | 0.004783 | -0.011177 | 0.01233 | 0.0031829 | -9.4894 | 104.6906 | -15.2756 | 104.8874 | -11.2885 | -14.9048 | -13.3392 | -1.1215 | -1.2634 | -1.1627 | -1.3321 | -1.0117 | -1.2863 | -1.149 | 0.29755 | -0.15564 | 0.041199 | 4.2847 | 2.2339 | 0.66833 | 1.9363 | 0.37079 | 14.4104 | -106.1096 | -106.1783 | 14.5615 | 14.4241 | 14.2868 | 0.013733 | -0.1236 | 3.9871 | 120.163 | 0.15106 | -0.16937 | 119.9661 | -0.10071 | 120.2637 | 14.3097 | -120.1218 | -106.0089 | 120.4605 | 14.241 | 6.0837 | 14.4516
3370.25 | 120.0714 | -44.7372 | 75.0458 | 0.0019074 | 6.9669 | 0.069876 | 0.091486 | 0.0024139 | 0.0069064 | 0.017282 | -0.0028687 | 0.022766 | -1.4525 | -0.0044028 | -0.0043408 | 0.01468 | -0.00066231 | -32.3593 | 75.119 | -44.5679 | 75.0778 | -38.5849 | -43.3044 | -42.3798 | -3.1815 | -3.6163 | -3.447 | -3.6804 | -3.1219 | -3.6209 | -3.4653 | 0.16937 | 0.073243 | 0.032044 | 6.1523 | 2.3575 | 1.4328 | 2.1881 | 1.2634 | 41.2903 | -78.6621 | -78.7262 | 41.6153 | 41.272 | 41.1163 | -0.018311 | -0.17395 | 5.983 | 119.6457 | 0.32501 | -0.23346 | 119.6869 | -0.16937 | 119.8563 | 41.1209 | -119.6136 | -78.4927 | 119.8151 | 41.0568 | 12.3779 | 41.5558
3372.0312 | 120.5017 | -0.27466 | 120.2362 | -0.013352 | 6.9709 | 0.061118 | 0.097468 | 0.0017731 | -0.00078404 | 0.014505 | -0.0059205 | 0.022979 | -1.4533 | -0.0026938 | -0.005409 | 0.014894 | 0.0025421 | 2.124 | 120.1309 | -0.16479 | 120.1584 | 2.4582 | 0.43945 | 1.9455 | 0.050354 | -0.032043 | 0.041199 | 0.064087 | 0.12817 | 0.045776 | 0.13733 | 0.10986 | -0.10529 | -0.07782 | 2.7328 | 2.2202 | 0.71411 | 2.1103 | 0.60425 | 0.31586 | -120.2682 | -120.1721 | 0.40283 | 0.41199 | 0.32043 | 0.09613 | 0.004577 | 2.623 | 120.3232 | 0.086975 | 0.022888 | 120.2957 | -0.073242 | 120.4056 | 0.24262 | -120.401 | -120.195 | 120.433 | 0.33875 | 2.3987 | 0.32501
3373.8125 | 120.607 | -0.28839 | 120.4285 | -0.0057221 | 6.9707 | 0.064963 | 0.096827 | 0.0034821 | -0.00035684 | 0.012155 | -0.0028687 | 0.021057 | -1.4531 | -0.002053 | -0.0066906 | 0.016816 | 0.00061949 | 2.0966 | 120.3003 | -0.16937 | 120.2454 | 2.4261 | 0.37994 | 1.9043 | -0.045776 | -0.004578 | 0.032043 | -0.009155 | 0.045776 | -0.036621 | 0.086975 | 0.11902 | -0.12817 | -0.18311 | 2.7145 | 2.1927 | 0.66834 | 2.0737 | 0.54932 | 0.32043 | -120.433 | -120.4376 | 0.33417 | 0.37537 | 0.25177 | 0.054932 | -0.068664 | 2.5955 | 120.4147 | 0.013733 | -0.041198 | 120.4697 | -0.036621 | 120.5887 | 0.28381 | -120.5978 | -120.3964 | 120.5338 | 0.27924 | 2.3849 | 0.24262
3375.5312 | 120.7306 | -0.24719 | 120.433 | -0.013352 | 6.972 | 0.064108 | 0.097254 | 0.0019867 | -0.00057044 | 0.011087 | -0.0059205 | 0.020416 | -1.4516 | 0.0037148 | -0.0058362 | 0.012971 | 0.00083309 | 2.1286 | 120.2911 | -0.14191 | 120.3278 | 2.5085 | 0.4715 | 2.0096 | 0.032043 | -0.050354 | 0.059509 | 0.073242 | 0.12817 | 0.073242 | 0.13733 | 0.10528 | -0.14191 | -0.10528 | 2.7557 | 2.2568 | 0.71869 | 2.1515 | 0.6134 | 0.3067 | -120.4834 | -120.3598 | 0.37537 | 0.38452 | 0.32043 | 0.07782 | 0.013733 | 2.6505 | 120.4697 | 0.068665 | 0.013733 | 120.433 | -0.10986 | 120.5383 | 0.19684 | -120.575 | -120.3735 | 120.575 | 0.32043 | 2.3758 | 0.27924
3377.3281 | 120.6802 | -0.28381 | 120.5292 | 0.0019074 | 6.9714 | 0.062827 | 0.10067 | -0.00014949 | -0.00035684 | 0.01301 | -0.0028687 | 0.021698 | -1.4536 | -0.0069662 | -0.0049818 | 0.01468 | -2.1314e-05 | 2.1103 | 120.401 | -0.15564 | 120.3232 | 2.4353 | 0.37537 | 1.918 | -0.068665 | -0.004578 | 0.036621 | -0.027466 | 0.022888 | -0.045776 | 0.07782 | 0.12817 | -0.12817 | -0.20599 | 2.7191 | 2.2018 | 0.65918 | 2.0737 | 0.53101 | 0.32043 | -120.5338 | -120.5566 | 0.3067 | 0.36163 | 0.23804 | 0.041199 | -0.082397 | 2.5909 | 120.4788 | -0.013733 | -0.064087 | 120.5566 | -0.041199 | 120.6848 | 0.27923 | -120.6848 | -120.4926 | 120.607 | 0.25635 | 2.3941 | 0.21515
3379.0938 | 120.7855 | -0.26093 | 120.5612 | -0.013352 | 6.9667 | 0.062186 | 0.098963 | 0.0039093 | -0.0016384 | 0.015146 | -0.0028687 | 0.021698 | -1.4514 | -0.0026938 | -0.0075452 | 0.013185 | 0.0012603 | 2.1332 | 120.4056 | -0.17395 | 120.4193 | 2.5223 | 0.46692 | 1.9867 | 0.050354 | -0.009155 | 0.036621 | 0.050354 | 0.1236 | 0.045776 | 0.11902 | 0.086975 | -0.15564 | -0.14191 | 2.7832 | 2.2476 | 0.72784 | 2.1606 | 0.64087 | 0.29755 | -120.5704 | -120.5109 | 0.38452 | 0.37994 | 0.3067 | 0.082398 | 0.009155 | 2.6962 | 120.5933 | 0.086975 | 0.013733 | 120.5795 | -0.045776 | 120.6665 | 0.25177 | -120.7352 | -120.5246 | 120.6802 | 0.31128 | 2.3941 | 0.31128
3380.875 | 120.8954 | -0.23804 | 120.5154 | -0.013352 | 6.9682 | 0.064108 | 0.097681 | 0.0019867 | -0.00099764 | 0.014291 | -0.0059205 | 0.020202 | -1.4527 | 0.0032876 | -0.0049818 | 0.016603 | 0.00061949 | 2.1194 | 120.4468 | -0.15106 | 120.4468 | 2.5589 | 0.48981 | 2.0142 | 0.073242 | -0.027466 | 0.054932 | 0.12817 | 0.17395 | 0.091553 | 0.20142 | 0.086975 | -0.068665 | -0.068665 | 2.7969 | 2.2522 | 0.72784 | 2.1652 | 0.64087 | 0.29297 | -120.5429 | -120.3873 | 0.41199 | 0.43945 | 0.32959 | 0.14648 | 0.036621 | 2.71 | 120.5978 | 0.11902 | 0.073242 | 120.5978 | -0.082398 | 120.6848 | 0.21057 | -120.6665 | -120.4605 | 120.6848 | 0.36621 | 2.3575 | 0.31128
3382.6562 | 120.8817 | -0.24719 | 120.5933 | -0.013352 | 6.9667 | 0.063895 | 0.096613 | -0.0027131 | 0.00092496 | 0.012796 | -0.0059205 | 0.018066 | -1.4542 | -0.00077117 | -0.0069044 | 0.014894 | 0.0042511 | 2.1561 | 120.4193 | -0.14191 | 120.5017 | 2.6001 | 0.54016 | 2.0508 | 0.073242 | -0.036621 | 0.054932 | 0.059509 | 0.16479 | 0.10071 | 0.15106 | 0.10528 | -0.17395 | -0.091553 | 2.8473 | 2.298 | 0.78735 | 2.1927 | 0.68207 | 0.30212 | -120.6299 | -120.5338 | 0.41199 | 0.39825 | 0.3479 | 0.09613 | 0.045776 | 2.742 | 120.6436 | 0.10986 | 0.004577 | 120.5612 | -0.091553 | 120.6665 | 0.21057 | -120.7352 | -120.5383 | 120.7489 | 0.3067 | 2.4033 | 0.32043
3384.4375 | 120.8359 | -0.27466 | 120.5887 | -0.013352 | 6.9701 | 0.062613 | 0.098536 | 0.00070491 | 7.0564e-05 | 0.012155 | -0.0028687 | 0.019348 | -1.4538 | 0.00029703 | -0.0086132 | 0.015107 | 0.00019229 | 2.1286 | 120.4239 | -0.16937 | 120.4834 | 2.5497 | 0.48523 | 2.0142 | 0 | -0.032043 | 0.036621 | 0 | 0.07782 | 0.027466 | 0.086975 | 0.10529 | -0.16479 | -0.10529 | 2.8244 | 2.2888 | 0.75989 | 2.1835 | 0.6546 | 0.31128 | -120.6207 | -120.5887 | 0.35248 | 0.36163 | 0.30212 | 0.050354 | -0.009155 | 2.7191 | 120.6528 | 0.041199 | -0.036621 | 120.5933 | -0.068664 | 120.6985 | 0.24262 | -120.7581 | -120.5521 | 120.7581 | 0.27466 | 2.4033 | 0.27466
3386.2344 | 120.9824 | -0.24719 | 120.5566 | -0.0057221 | 6.9669 | 0.063895 | 0.0964 | 0.00027771 | -0.0012112 | 0.011087 | -0.0059205 | 0.01828 | -1.4523 | 0.0035012 | -0.0062634 | 0.012117 | 0.0019013 | 2.1011 | 120.4147 | -0.16479 | 120.5154 | 2.5909 | 0.5127 | 2.0691 | 0.064087 | -0.059509 | 0.064087 | 0.082397 | 0.18768 | 0.13733 | 0.1831 | 0.082397 | -0.14191 | -0.041199 | 2.8381 | 2.3163 | 0.75989 | 2.2339 | 0.67749 | 0.31128 | -120.6162 | -120.4742 | 0.43488 | 0.4303 | 0.38452 | 0.11902 | 0.073242 | 2.7557 | 120.6802 | 0.1236 | 0.01831 | 120.5795 | -0.1236 | 120.6619 | 0.18768 | -120.7214 | -120.4926 | 120.7626 | 0.32959 | 2.3483 | 0.31128
3387.9375 | 120.9366 | -0.24719 | 120.5978 | -0.013352 | 6.9675 | 0.064536 | 0.099177 | -0.0042083 | 0.00049776 | 0.013223 | -0.0028687 | 0.018707 | -1.4525 | 8.3226e-05 | -0.007118 | 0.013612 | -0.0025849 | 2.092 | 120.4971 | -0.17395 | 120.5109 | 2.5269 | 0.46692 | 2.0142 | 0.013733 | -0.036621 | 0.054932 | 0.064087 | 0.13275 | 0.064087 | 0.13275 | 0.073242 | -0.10071 | -0.086975 | 2.774 | 2.2614 | 0.71411 | 2.1881 | 0.64087 | 0.30212 | -120.6345 | -120.5338 | 0.37994 | 0.37994 | 0.31128 | 0.077819 | 0.009155 | 2.7008 | 120.6848 | 0.077819 | 0.009155 | 120.6711 | -0.091553 | 120.7443 | 0.21057 | -120.7718 | -120.5429 | 120.7581 | 0.31128 | 2.3392 | 0.26093
3389.7188 | 121.019 | -0.23346 | 120.5933 | -0.013352 | 6.9671 | 0.062399 | 0.09704 | 6.4114e-05 | -0.00099764 | 0.011514 | -0.0028687 | 0.01828 | -1.4527 | -0.00013037 | -0.0066906 | 0.015748 | -0.0015167 | 2.1378 | 120.4697 | -0.15564 | 120.6024 | 2.6367 | 0.55847 | 2.1057 | 0.10986 | -0.059509 | 0.059509 | 0.10986 | 0.21057 | 0.14648 | 0.19684 | 0.077819 | -0.1236 | 0.009155 | 2.8702 | 2.3392 | 0.79193 | 2.2614 | 0.71411 | 0.29297 | -120.6528 | -120.4834 | 0.44403 | 0.4303 | 0.37994 | 0.13733 | 0.086975 | 2.7924 | 120.7581 | 0.15106 | 0.050354 | 120.6253 | -0.11902 | 120.7031 | 0.17395 | -120.7489 | -120.5338 | 120.8359 | 0.34332 | 2.3712 | 0.34332
3391.4375 | 120.9686 | -0.25635 | 120.6436 | -0.013352 | 6.9675 | 0.062613 | 0.099817 | 0.0013459 | -0.00078404 | 0.014505 | -0.0028687 | 0.020202 | -1.4533 | -0.0024802 | -0.0049818 | 0.014039 | 0.0051057 | 2.1103 | 120.5246 | -0.14648 | 120.5704 | 2.5543 | 0.48065 | 2.0508 | 0.036621 | -0.036621 | 0.027466 | 0.050354 | 0.09613 | 0.050354 | 0.13733 | 0.10986 | -0.11902 | -0.073242 | 2.8107 | 2.3071 | 0.737 | 2.1973 | 0.62714 | 0.28381 | -120.6802 | -120.5933 | 0.35248 | 0.39368 | 0.3067 | 0.10986 | 0.022888 | 2.7008 | 120.7169 | 0.068664 | 0.022888 | 120.6711 | -0.064087 | 120.7809 | 0.21973 | -120.7901 | -120.6161 | 120.8267 | 0.3067 | 2.3666 | 0.29297
3393.2031 | 121.0098 | -0.24719 | 120.6619 | -0.013352 | 6.9684 | 0.06304 | 0.098749 | -0.0035675 | 0.0028476 | 0.012582 | -0.0089723 | 0.019775 | -1.4523 | 0.0022196 | -0.007118 | 0.01468 | 0.0016877 | 2.1606 | 120.5292 | -0.15106 | 120.639 | 2.6413 | 0.54016 | 2.092 | 0.073242 | -0.050354 | 0.050354 | 0.07782 | 0.15564 | 0.09613 | 0.14648 | 0.09613 | -0.13275 | -0.022888 | 2.8885 | 2.3392 | 0.78735 | 2.243 | 0.69122 | 0.29755 | -120.7123 | -120.5841 | 0.40283 | 0.39368 | 0.34332 | 0.09613 | 0.045776 | 2.7924 | 120.7901 | 0.10529 | 0.027466 | 120.6802 | -0.10071 | 120.7764 | 0.19684 | -120.813 | -120.6116 | 120.8862 | 0.32501 | 2.4078 | 0.32043
3394.9688 | 121.0419 | -0.23804 | 120.6619 | -0.013352 | 6.9673 | 0.064108 | 0.10024 | -0.0046357 | -0.0027066 | 0.0095918 | -0.0059205 | 0.020843 | -1.4544 | -0.00077117 | -0.0073316 | 0.014466 | 0.0019013 | 2.1652 | 120.5429 | -0.14191 | 120.6665 | 2.6779 | 0.55847 | 2.1194 | 0.10071 | -0.050354 | 0.050354 | 0.10071 | 0.20142 | 0.11902 | 0.17853 | 0.09613 | -0.11902 | 0.004578 | 2.916 | 2.3575 | 0.79651 | 2.2614 | 0.70038 | 0.28839 | -120.7123 | -120.5612 | 0.43945 | 0.41656 | 0.35706 | 0.12817 | 0.068665 | 2.8198 | 120.8084 | 0.15106 | 0.050354 | 120.6848 | -0.10071 | 120.7809 | 0.18768 | -120.8038 | -120.6116 | 120.9045 | 0.33875 | 2.4033 | 0.33875
3396.7656 | 121.019 | -0.27008 | 120.7169 | -0.0057221 | 6.9677 | 0.063681 | 0.10174 | -0.0069855 | 0.00071136 | 0.014932 | -0.0059205 | 0.02127 | -1.4529 | -0.00098477 | -0.0094678 | 0.011689 | 0.0010467 | 2.1652 | 120.5475 | -0.15106 | 120.6757 | 2.6413 | 0.54016 | 2.1103 | 0.050354 | -0.032043 | 0.050354 | 0.045776 | 0.14648 | 0.068665 | 0.14191 | 0.11902 | -0.16937 | -0.041199 | 2.9114 | 2.3804 | 0.81024 | 2.2614 | 0.69122 | 0.32044 | -120.7489 | -120.6711 | 0.41657 | 0.41199 | 0.33875 | 0.091553 | 0.018311 | 2.7924 | 120.8267 | 0.09613 | -0.004578 | 120.6985 | -0.082397 | 120.8176 | 0.23804 | -120.8679 | -120.6665 | 120.9457 | 0.31586 | 2.4353 | 0.32044
3398.5469 | 120.9778 | -0.28381 | 120.7214 | -0.0057221 | 6.9692 | 0.061758 | 0.10067 | -0.0016449 | -0.00057044 | 0.013223 | -0.0028687 | 0.019775 | -1.4536 | -0.00483 | -0.010322 | 0.012544 | 0.0010467 | 2.1652 | 120.5795 | -0.16022 | 120.6345 | 2.6138 | 0.50354 | 2.0828 | -0.018311 | -0.013733 | 0.041199 | -0.004578 | 0.068665 | 0.009155 | 0.07782 | 0.1236 | -0.14191 | -0.086976 | 2.8976 | 2.3666 | 0.78735 | 2.243 | 0.66376 | 0.32501 | -120.7352 | -120.726 | 0.35248 | 0.36163 | 0.29297 | 0.036621 | -0.032044 | 2.774 | 120.7947 | 0.027466 | -0.045777 | 120.7397 | -0.054932 | 120.8633 | 0.27008 | -120.8817 | -120.6802 | 120.9183 | 0.27923 | 2.449 | 0.2655
3400.2656 | 121.0419 | -0.25177 | 120.7397 | -0.0057221 | 6.9669 | 0.06304 | 0.10238 | -0.0012177 | -0.00078404 | 0.01301 | -0.0028687 | 0.021911 | -1.4516 | -0.003121 | -0.0037 | 0.013185 | 0.0029693 | 2.1332 | 120.6482 | -0.1831 | 120.6116 | 2.5681 | 0.39825 | 2.0416 | 0.004578 | -0.032043 | 0.036621 | 0.054932 | 0.11444 | 0.041199 | 0.12817 | 0.068665 | -0.091553 | -0.12817 | 2.8198 | 2.2934 | 0.65002 | 2.2247 | 0.58136 | 0.28839 | -120.7718 | -120.6848 | 0.36621 | 0.37994 | 0.29297 | 0.091553 | 0.004578 | 2.7512 | 120.7947 | 0.07782 | 0.018311 | 120.8313 | -0.068664 | 120.9 | 0.21973 | -120.9229 | -120.7031 | 120.8633 | 0.3067 | 2.3849 | 0.25635
3402.0469 | 121.0464 | -0.26093 | 120.7672 | 0.0019074 | 6.968 | 0.062827 | 0.10153 | -0.0010041 | -0.0033474 | 0.014932 | -0.0028687 | 0.019989 | -1.4555 | -0.0033346 | -0.0075452 | 0.013826 | 0.00040589 | 2.1606 | 120.6528 | -0.16937 | 120.6619 | 2.6138 | 0.46692 | 2.0737 | 0.013733 | -0.013733 | 0.032043 | 0.059509 | 0.10986 | 0.036621 | 0.1236 | 0.091552 | -0.11444 | -0.10529 | 2.8748 | 2.3346 | 0.72784 | 2.243 | 0.63629 | 0.29297 | -120.7809 | -120.7077 | 0.37079 | 0.38452 | 0.29755 | 0.091553 | 0.004578 | 2.7832 | 120.8313 | 0.07782 | 0.027466 | 120.8221 | -0.045776 | 120.9137 | 0.24719 | -120.9366 | -120.7352 | 120.9229 | 0.32043 | 2.4216 | 0.27466
3403.8281 | 121.0236 | -0.27466 | 120.7718 | 0.0019074 | 6.9677 | 0.064108 | 0.10131 | 0.0030547 | -0.00078404 | 0.012582 | -0.0059205 | 0.02127 | -1.4523 | 0.00072423 | -0.0073316 | 0.015321 | 0.0021149 | 2.1332 | 120.6985 | -0.20599 | 120.607 | 2.5543 | 0.40283 | 2.0279 | -0.059509 | -0.022888 | 0.032043 | -0.004578 | 0.050354 | -0.027466 | 0.091553 | 0.068664 | -0.073243 | -0.16479 | 2.829 | 2.3026 | 0.67749 | 2.2339 | 0.60883 | 0.3067 | -120.7947 | -120.7764 | 0.32501 | 0.36621 | 0.24719 | 0.05951 | -0.059509 | 2.7603 | 120.813 | 0.018311 | -0.036621 | 120.9045 | -0.054931 | 120.9732 | 0.25177 | -120.9778 | -120.7397 | 120.8817 | 0.27008 | 2.4078 | 0.21515
3405.5469 | 121.0236 | -0.28381 | 120.8038 | -0.0057221 | 6.9709 | 0.065604 | 0.10281 | 0.00027771 | -0.00078404 | 0.014932 | 0.00018312 | 0.020843 | -1.4536 | -0.00077117 | -0.0060498 | 0.015321 | 0.0014741 | 2.1378 | 120.7031 | -0.18768 | 120.6024 | 2.536 | 0.37537 | 2.0096 | -0.091553 | 0.009155 | 0.009155 | -0.004578 | 0.022888 | -0.045776 | 0.073242 | 0.09613 | -0.10071 | -0.20142 | 2.8198 | 2.2934 | 0.65918 | 2.1973 | 0.56305 | 0.29297 | -120.7947 | -120.8084 | 0.3067 | 0.35706 | 0.23804 | 0.064087 | -0.054931 | 2.7237 | 120.7901 | 0.013733 | -0.013733 | 120.8908 | 0 | 120.9869 | 0.29297 | -120.9915 | -120.7947 | 120.8862 | 0.27923 | 2.4216 | 0.19226
3407.3281 | 121.0648 | -0.27008 | 120.8405 | 0.0019074 | 6.9701 | 0.061972 | 0.10195 | 0.0022003 | 0.00092496 | 0.013651 | -0.0059205 | 0.021057 | -1.4521 | -0.0029074 | -0.0062634 | 0.015748 | 0.0038239 | 2.1973 | 120.6894 | -0.15106 | 120.6757 | 2.6276 | 0.45776 | 2.0782 | -0.009155 | -0.018311 | 0.027466 | 0.013733 | 0.07782 | -0.013733 | 0.091553 | 0.11902 | -0.15106 | -0.16479 | 2.8976 | 2.3483 | 0.72785 | 2.2293 | 0.60883 | 0.29755 | -120.8588 | -120.8267 | 0.3479 | 0.36163 | 0.25635 | 0.064087 | -0.041199 | 2.7786 | 120.8267 | 0.050354 | -0.013733 | 120.8405 | -0.045777 | 120.9595 | 0.25177 | -120.9915 | -120.813 | 120.9457 | 0.28381 | 2.4673 | 0.26093
3409.0469 | 121.1929 | -0.25177 | 120.7947 | -0.0057221 | 6.9677 | 0.064963 | 0.10024 | 6.4114e-05 | 0.0011386 | 0.015787 | -0.0028687 | 0.019561 | -1.4519 | 0.0026468 | -0.0058362 | 0.012971 | -0.0021575 | 2.2247 | 120.694 | -0.12817 | 120.7626 | 2.7374 | 0.51727 | 2.1606 | 0.082397 | -0.059509 | 0.068665 | 0.1236 | 0.16937 | 0.10986 | 0.17853 | 0.1236 | -0.10071 | -0.032044 | 2.9892 | 2.4124 | 0.76904 | 2.2888 | 0.64545 | 0.32044 | -120.8542 | -120.6711 | 0.42114 | 0.4303 | 0.36163 | 0.10986 | 0.041198 | 2.8656 | 120.8908 | 0.10071 | 0.054931 | 120.8221 | -0.12817 | 120.9457 | 0.19226 | -120.9229 | -120.726 | 121.0144 | 0.37537 | 2.4765 | 0.33417
3410.8281 | 121.2067 | -0.25177 | 120.8038 | -0.013352 | 6.9675 | 0.062399 | 0.10131 | -0.0024995 | -0.0029202 | 0.01301 | -0.0028687 | 0.019134 | -1.4542 | 0.0037148 | -0.0077588 | 0.016389 | 0.0042511 | 2.2293 | 120.6848 | -0.16022 | 120.7764 | 2.774 | 0.58136 | 2.1881 | 0.10529 | -0.054932 | 0.050354 | 0.11902 | 0.2243 | 0.1236 | 0.18768 | 0.091553 | -0.11902 | -0.027466 | 3.0258 | 2.4399 | 0.83313 | 2.3483 | 0.74158 | 0.30212 | -120.8588 | -120.6848 | 0.47607 | 0.43945 | 0.37537 | 0.13733 | 0.073242 | 2.9343 | 120.9366 | 0.17395 | 0.068665 | 120.845 | -0.10529 | 120.9366 | 0.19684 | -120.9641 | -120.7535 | 121.0281 | 0.37079 | 2.4811 | 0.35706
3412.625 | 121.2021 | -0.25635 | 120.8221 | -0.0057221 | 6.9688 | 0.064108 | 0.10217 | 0.0013459 | -0.00014304 | 0.013651 | -0.0028687 | 0.020202 | -1.4546 | 0.0032876 | -0.0026318 | 0.015107 | 0.0010467 | 2.211 | 120.7443 | -0.16479 | 120.7535 | 2.6962 | 0.49896 | 2.1332 | 0.064087 | -0.050354 | 0.050354 | 0.09613 | 0.16022 | 0.07782 | 0.17853 | 0.091553 | -0.07782 | -0.068665 | 2.9526 | 2.3895 | 0.75531 | 2.298 | 0.66376 | 0.3067 | -120.8725 | -120.726 | 0.41657 | 0.43488 | 0.33417 | 0.12817 | 0.027466 | 2.861 | 120.9183 | 0.10986 | 0.045776 | 120.9091 | -0.10071 | 121.0007 | 0.20599 | -120.9869 | -120.7718 | 121.0098 | 0.35248 | 2.4673 | 0.32044
3414.4062 | 121.1426 | -0.29755 | 120.8633 | -0.0057221 | 6.9688 | 0.06304 | 0.10238 | -0.00014949 | 0.002634 | 0.013437 | 0.00018312 | 0.021057 | -1.4489 | 0.0011514 | -0.008186 | 0.01468 | 0.00083309 | 2.2064 | 120.7855 | -0.19684 | 120.7214 | 2.655 | 0.4715 | 2.092 | -0.027466 | -0.013733 | 0.022888 | 0.027466 | 0.086975 | 0.018311 | 0.1236 | 0.10071 | -0.07782 | -0.14191 | 2.9526 | 2.3895 | 0.76904 | 2.2888 | 0.66834 | 0.32043 | -120.8771 | -120.8359 | 0.38452 | 0.42114 | 0.31586 | 0.10071 | -0.004577 | 2.8519 | 120.9183 | 0.064087 | 0.004578 | 120.9824 | -0.036621 | 121.0831 | 0.28381 | -121.0602 | -120.8405 | 121.019 | 0.32501 | 2.504 | 0.27008
3416.125 | 121.106 | -0.28381 | 120.8954 | -0.013352 | 6.969 | 0.064322 | 0.10345 | 0.0030547 | 0.0024204 | 0.013864 | -0.0028687 | 0.02127 | -1.4521 | 0.003074 | -0.0058362 | 0.012971 | -2.1314e-05 | 2.1973 | 120.7855 | -0.18768 | 120.6802 | 2.6047 | 0.41199 | 2.0737 | -0.091553 | -0.009155 | 0.032043 | -0.009155 | 0.018311 | -0.050354 | 0.086975 | 0.09613 | -0.10986 | -0.21515 | 2.8885 | 2.3575 | 0.6958 | 2.2614 | 0.59967 | 0.31586 | -120.9045 | -120.9045 | 0.30212 | 0.37079 | 0.23346 | 0.054932 | -0.082397 | 2.7924 | 120.8679 | -0.013732 | -0.041198 | 120.9732 | -0.041198 | 121.0693 | 0.27466 | -121.0831 | -120.8633 | 120.9641 | 0.27466 | 2.4811 | 0.19226
3417.9219 | 121.1517 | -0.28839 | 120.9229 | -0.013352 | 6.9677 | 0.061758 | 0.10281 | -0.0024995 | -0.00057044 | 0.012582 | -0.0028687 | 0.019775 | -1.4521 | -0.00013037 | -0.0073316 | 0.011689 | 0.00040589 | 2.2385 | 120.8084 | -0.1831 | 120.7077 | 2.6688 | 0.44861 | 2.1103 | -0.059509 | -0.032043 | 0.018311 | -0.018311 | 0.064087 | -0.013733 | 0.07782 | 0.10529 | -0.11444 | -0.21515 | 2.9572 | 2.3987 | 0.737 | 2.2934 | 0.63171 | 0.3067 | -120.9549 | -120.9412 | 0.35248 | 0.36621 | 0.27466 | 0.059509 | -0.032044 | 2.8519 | 120.8908 | 0.045776 | -0.036622 | 120.9915 | -0.050354 | 121.0968 | 0.25635 | -121.106 | -120.9045 | 120.9961 | 0.27008 | 2.5269 | 0.22888
3419.7031 | 121.1517 | -0.28839 | 120.9137 | -0.013352 | 6.9665 | 0.064749 | 0.10174 | 0.0047637 | -0.0022794 | 0.014291 | -0.0059205 | 0.021057 | -1.4508 | 0.0043558 | -0.0096814 | 0.013398 | 0.0014741 | 2.2842 | 120.7809 | -0.16937 | 120.7626 | 2.7237 | 0.47607 | 2.1378 | -0.032043 | -0.013733 | 0.018311 | -0.009155 | 0.064087 | -0.004578 | 0.068665 | 0.11902 | -0.13275 | -0.15106 | 3.0121 | 2.4261 | 0.76446 | 2.3071 | 0.64545 | 0.3067 | -120.9274 | -120.9229 | 0.35248 | 0.35706 | 0.28381 | 0.050354 | -0.022889 | 2.8931 | 120.932 | 0.045776 | -0.027466 | 120.9503 | -0.032044 | 121.0693 | 0.27466 | -121.0831 | -120.8954 | 121.051 | 0.27924 | 2.5726 | 0.25635
3421.4688 | 121.2387 | -0.24261 | 120.8496 | -0.020981 | 6.968 | 0.064963 | 0.10324 | 0.0034821 | 7.0564e-05 | 0.014291 | -0.0028687 | 0.019348 | -1.4533 | 0.0017922 | -0.0043408 | 0.015321 | 0.0014741 | 2.3071 | 120.7764 | -0.13733 | 120.8221 | 2.8107 | 0.51727 | 2.1835 | 0.041199 | -0.050354 | 0.050354 | 0.07782 | 0.13275 | 0.068665 | 0.13733 | 0.10529 | -0.073242 | -0.027465 | 3.0533 | 2.4261 | 0.75989 | 2.3209 | 0.6546 | 0.29297 | -120.9 | -120.7718 | 0.37537 | 0.37994 | 0.31128 | 0.086975 | 0.018311 | 2.948 | 120.9595 | 0.082397 | 0.027466 | 120.9137 | -0.10071 | 121.019 | 0.19226 | -120.9869 | -120.7993 | 121.0648 | 0.32044 | 2.5497 | 0.28381
3423.1875 | 121.1655 | -0.28381 | 120.9641 | -0.0057221 | 6.9671 | 0.063467 | 0.10259 | -0.0027131 | -0.0016384 | 0.014291 | 0.00018312 | 0.021057 | -1.4536 | -0.0018394 | -0.008827 | 0.013612 | 0.0029693 | 2.2614 | 120.8176 | -0.20142 | 120.7397 | 2.7008 | 0.46692 | 2.124 | -0.07782 | -0.022888 | 0.022888 | -0.027466 | 0.045776 | -0.027466 | 0.064087 | 0.082397 | -0.14648 | -0.2243 | 2.9846 | 2.4078 | 0.75073 | 2.3254 | 0.66834 | 0.3067 | -120.9869 | -120.9915 | 0.32959 | 0.3479 | 0.25635 | 0.041199 | -0.050354 | 2.9022 | 120.9412 | 0.022888 | -0.050354 | 121.019 | -0.045776 | 121.1014 | 0.26092 | -121.1655 | -120.9412 | 121.0236 | 0.25635 | 2.5452 | 0.20599
3424.9531 | 121.2891 | -0.25635 | 120.9229 | -0.0057221 | 6.9667 | 0.065817 | 0.1011 | -0.0018585 | 0.00092496 | 0.012582 | -0.0059205 | 0.019561 | -1.4544 | -0.0018394 | -0.0060498 | 0.015107 | 0.0019013 | 2.33 | 120.8221 | -0.15564 | 120.8038 | 2.7878 | 0.52185 | 2.211 | 0.013733 | -0.032043 | 0.045776 | 0.07782 | 0.13733 | 0.07782 | 0.15106 | 0.10071 | -0.10071 | -0.11902 | 3.0441 | 2.4673 | 0.7782 | 2.3666 | 0.67749 | 0.30212 | -120.9549 | -120.845 | 0.39368 | 0.40741 | 0.33417 | 0.10529 | 0.032044 | 2.9434 | 120.9595 | 0.091553 | 0.032044 | 120.9778 | -0.077819 | 121.0785 | 0.22431 | -121.0785 | -120.8771 | 121.0602 | 0.33417 | 2.5864 | 0.27008
3426.7344 | 121.2936 | -0.23346 | 120.9091 | -0.0057221 | 6.9703 | 0.065817 | 0.099817 | -0.00057689 | -0.00035684 | 0.015787 | -0.0028687 | 0.020416 | -1.4553 | -0.00055757 | -0.0034864 | 0.016389 | 0.0042511 | 2.3804 | 120.8176 | -0.14648 | 120.8908 | 2.8702 | 0.54016 | 2.2293 | 0.09613 | -0.036621 | 0.041199 | 0.10529 | 0.14648 | 0.086975 | 0.15564 | 0.086975 | -0.091553 | -0.018311 | 3.1036 | 2.4628 | 0.77362 | 2.3758 | 0.68664 | 0.27466 | -120.9457 | -120.8038 | 0.37994 | 0.3891 | 0.32043 | 0.11444 | 0.045776 | 3.0167 | 121.0373 | 0.10529 | 0.064087 | 120.9641 | -0.07782 | 121.051 | 0.19684 | -121.0556 | -120.8679 | 121.1243 | 0.33875 | 2.6138 | 0.32959
3428.4531 | 121.2433 | -0.28381 | 120.9549 | -0.0057221 | 6.9707 | 0.064536 | 0.10195 | 0.0015595 | 0.0013522 | 0.01301 | 0.00018312 | 0.020416 | -1.4521 | -0.00483 | -0.0066906 | 0.014466 | -0.0015167 | 2.3666 | 120.8679 | -0.18768 | 120.8359 | 2.8015 | 0.49439 | 2.1881 | 0.018311 | -0.032043 | 0.018311 | 0.045776 | 0.10986 | 0.027466 | 0.12817 | 0.09613 | -0.086975 | -0.11902 | 3.0853 | 2.4719 | 0.7782 | 2.3758 | 0.68207 | 0.30212 | -120.9869 | -120.9091 | 0.39368 | 0.41199 | 0.31128 | 0.10986 | 0.009155 | 2.9892 | 121.0236 | 0.091552 | 0.027465 | 121.0556 | -0.050354 | 121.1517 | 0.25177 | -121.1426 | -120.9366 | 121.1197 | 0.32959 | 2.6505 | 0.30212
3430.25 | 121.2891 | -0.24719 | 120.9595 | -0.013352 | 6.9695 | 0.063895 | 0.10089 | -0.0042083 | 0.002634 | 0.015787 | -0.0059205 | 0.019775 | -1.4521 | 0.0032876 | -0.009895 | 0.012758 | 0.00061949 | 2.4033 | 120.8038 | -0.15564 | 120.9183 | 2.8702 | 0.5722 | 2.2659 | 0.050354 | -0.041199 | 0.050354 | 0.045776 | 0.14191 | 0.068665 | 0.13275 | 0.091552 | -0.15564 | -0.041199 | 3.1174 | 2.5131 | 0.8194 | 2.4216 | 0.72784 | 0.29755 | -121.0007 | -120.9137 | 0.3891 | 0.37994 | 0.31586 | 0.082397 | 0.018311 | 3.0258 | 121.0739 | 0.091553 | -0.004578 | 120.9595 | -0.091553 | 121.051 | 0.20599 | -121.1151 | -120.9091 | 121.1655 | 0.29297 | 2.6505 | 0.29755
3432.0312 | 121.2433 | -0.27008 | 120.9732 | -0.020981 | 6.9684 | 0.063895 | 0.10003 | -0.0010041 | -0.00014304 | 0.013223 | -0.0059205 | 0.02063 | -1.4533 | -0.00077117 | -0.0066906 | 0.013612 | -0.0010895 | 2.4124 | 120.8405 | -0.16937 | 120.8908 | 2.8656 | 0.54932 | 2.243 | 0 | -0.050354 | 0.041199 | 0.004578 | 0.073242 | 0.013733 | 0.086975 | 0.10071 | -0.13275 | -0.082398 | 3.1357 | 2.5131 | 0.8194 | 2.4124 | 0.71869 | 0.31128 | -121.0236 | -120.9686 | 0.34332 | 0.35706 | 0.28381 | 0.045776 | -0.027466 | 3.035 | 121.0602 | 0.032043 | -0.036621 | 121.0098 | -0.091553 | 121.1105 | 0.21973 | -121.1426 | -120.932 | 121.1609 | 0.27466 | 2.6825 | 0.27008
3433.8281 | 121.3486 | -0.25177 | 120.9595 | -0.013352 | 6.9686 | 0.065176 | 0.10473 | -0.0048493 | 0.00092496 | 0.013864 | -0.0059205 | 0.021484 | -1.4544 | 0.0017922 | -0.0049818 | 0.016603 | 0.0012603 | 2.4033 | 120.8908 | -0.18768 | 120.8679 | 2.861 | 0.48065 | 2.211 | 0.018311 | -0.050354 | 0.045776 | 0.086975 | 0.1236 | 0.041199 | 0.15564 | 0.064087 | -0.068665 | -0.091553 | 3.1128 | 2.4628 | 0.73242 | 2.3987 | 0.66834 | 0.29755 | -121.0098 | -120.8725 | 0.37537 | 0.40741 | 0.29297 | 0.10986 | -0.004577 | 3.0487 | 121.0556 | 0.07782 | 0.041199 | 121.0785 | -0.09613 | 121.1426 | 0.20142 | -121.1472 | -120.9137 | 121.1197 | 0.33874 | 2.655 | 0.27008
3435.6094 | 121.2479 | -0.29755 | 121.0052 | 0.0019074 | 6.9669 | 0.064322 | 0.10516 | 0.0051911 | -0.00035684 | 0.016428 | -0.0089723 | 0.021911 | -1.4516 | -0.0022666 | -0.0034864 | 0.015107 | 0.0033967 | 2.3849 | 120.9137 | -0.19226 | 120.813 | 2.7924 | 0.42572 | 2.1561 | -0.082397 | -0.032043 | 0.022888 | -0.009155 | 0.022888 | -0.050354 | 0.064087 | 0.10528 | -0.091553 | -0.19226 | 3.0899 | 2.4536 | 0.72327 | 2.3483 | 0.61798 | 0.32043 | -121.0373 | -121.0144 | 0.32043 | 0.36163 | 0.24719 | 0.041199 | -0.073242 | 2.9846 | 121.0052 | 0 | -0.032043 | 121.106 | -0.054931 | 121.2112 | 0.2655 | -121.1975 | -120.9824 | 121.1105 | 0.28839 | 2.6825 | 0.21515
3437.3906 | 121.2616 | -0.29755 | 121.0281 | -0.0057221 | 6.9695 | 0.06304 | 0.10324 | 0.0028411 | -0.0039884 | 0.012369 | -0.0059205 | 0.020416 | -1.4521 | -0.0069662 | -0.0086132 | 0.013185 | 0.00040589 | 2.3438 | 120.8954 | -0.20599 | 120.8267 | 2.8244 | 0.48065 | 2.179 | -0.086975 | -0.013733 | 0 | -0.022888 | 0.032043 | -0.027466 | 0.082397 | 0.091552 | -0.13275 | -0.20142 | 3.1219 | 2.4765 | 0.7782 | 2.3849 | 0.68665 | 0.29755 | -121.0419 | -121.051 | 0.32959 | 0.37994 | 0.27008 | 0.082397 | -0.027466 | 3.0304 | 121.0327 | 0.032043 | -0.022888 | 121.1014 | -0.013733 | 121.1929 | 0.28381 | -121.2341 | -121.0281 | 121.1243 | 0.27466 | 2.6413 | 0.21057
3439.1094 | 121.2982 | -0.28381 | 121.0144 | -0.0057221 | 6.9686 | 0.066458 | 0.1058 | -0.0014313 | -0.00078404 | 0.016641 | 0.0032349 | 0.020416 | -1.4521 | -0.0071798 | -0.003059 | 0.014894 | -0.0017303 | 2.3804 | 120.9229 | -0.20599 | 120.8496 | 2.8198 | 0.43945 | 2.179 | -0.073242 | -0.032043 | 0.013733 | 0.013733 | 0.045776 | -0.018311 | 0.10986 | 0.077819 | -0.091552 | -0.16479 | 3.1036 | 2.4628 | 0.72327 | 2.3849 | 0.64545 | 0.29755 | -121.0464 | -121.0007 | 0.32959 | 0.39368 | 0.2655 | 0.09613 | -0.032044 | 3.0258 | 121.0556 | 0.032043 | 0 | 121.1288 | -0.045776 | 121.2067 | 0.25177 | -121.2204 | -121.0007 | 121.1334 | 0.29755 | 2.6642 | 0.21057
3440.9062 | 121.2799 | -0.28839 | 121.0464 | -0.0057221 | 6.9692 | 0.06304 | 0.10366 | 0.0017731 | -0.0029202 | 0.014505 | -0.0028687 | 0.019561 | -1.4516 | -0.0084616 | -0.0075452 | 0.012544 | 0.0021149 | 2.3666 | 120.9366 | -0.20599 | 120.8542 | 2.8564 | 0.4715 | 2.2018 | -0.091553 | -0.013733 | 0.009155 | -0.027466 | 0.022888 | -0.027466 | 0.054932 | 0.082397 | -0.10986 | -0.19226 | 3.1448 | 2.4902 | 0.75989 | 2.4078 | 0.67749 | 0.29755 | -121.0602 | -121.0739 | 0.31128 | 0.34332 | 0.26093 | 0.045777 | -0.036621 | 3.0624 | 121.0602 | 0.013733 | -0.036621 | 121.1426 | -0.022888 | 121.225 | 0.27466 | -121.2524 | -121.0373 | 121.1426 | 0.26093 | 2.655 | 0.19684
3442.6406 | 121.4264 | -0.24261 | 121.0236 | -0.020981 | 6.9675 | 0.063467 | 0.10324 | -0.0031403 | 0.0011386 | 0.014291 | -0.0059205 | 0.019348 | -1.4533 | 0.0037148 | -0.0066906 | 0.015748 | -0.00087591 | 2.449 | 120.8908 | -0.14191 | 121.0098 | 3.0487 | 0.62714 | 2.3438 | 0.07782 | -0.059509 | 0.054932 | 0.10529 | 0.17395 | 0.11902 | 0.16022 | 0.10071 | -0.13275 | -0.013733 | 3.2913 | 2.5864 | 0.86975 | 2.4857 | 0.76904 | 0.29755 | -121.0831 | -120.9183 | 0.41656 | 0.40283 | 0.36163 | 0.10528 | 0.064087 | 3.1906 | 121.1517 | 0.11902 | 0.050354 | 121.0327 | -0.11444 | 121.1334 | 0.18311 | -121.1655 | -120.9686 | 121.2524 | 0.3479 | 2.6917 | 0.32044
3444.4219 | 121.3211 | -0.28839 | 121.0373 | -0.0057221 | 6.969 | 0.062827 | 0.10623 | 0.0034821 | 0.0011386 | 0.015787 | -0.0059205 | 0.021484 | -1.4548 | 0.0015786 | -0.0022046 | 0.013612 | -0.00023491 | 2.4033 | 120.9503 | -0.20599 | 120.8679 | 2.8519 | 0.44403 | 2.2018 | -0.068665 | -0.027466 | 0.018311 | 0.004578 | 0.027466 | -0.032043 | 0.082397 | 0.082397 | -0.086975 | -0.16937 | 3.1403 | 2.4902 | 0.73242 | 2.4078 | 0.65003 | 0.3067 | -121.0648 | -121.0327 | 0.31586 | 0.37079 | 0.25635 | 0.064086 | -0.050354 | 3.0579 | 121.0739 | 0.009155 | -0.013733 | 121.1563 | -0.045777 | 121.2387 | 0.26093 | -121.2433 | -121.019 | 121.1563 | 0.29297 | 2.6916 | 0.21973
3446.1406 | 121.3165 | -0.32044 | 121.0464 | -0.013352 | 6.9701 | 0.063895 | 0.10409 | -0.0012177 | -0.0014248 | 0.014505 | -0.0028687 | 0.020416 | -1.4527 | -0.006539 | -0.01075 | 0.013185 | 0.0021149 | 2.4033 | 120.932 | -0.19684 | 120.8817 | 2.9068 | 0.48981 | 2.2476 | -0.09613 | -0.027466 | 0 | -0.045776 | 0.036621 | -0.036621 | 0.032043 | 0.1236 | -0.11444 | -0.16479 | 3.2272 | 2.5681 | 0.81024 | 2.4445 | 0.68664 | 0.32044 | -121.0739 | -121.0922 | 0.35706 | 0.35248 | 0.28381 | 0.032043 | -0.036621 | 3.1036 | 121.0785 | 0.036621 | -0.045776 | 121.1288 | -0.027466 | 121.2524 | 0.29297 | -121.2433 | -121.0464 | 121.2021 | 0.27466 | 2.7237 | 0.22431
3447.9219 | 121.3348 | -0.30212 | 121.0648 | -0.0057221 | 6.9699 | 0.063681 | 0.1043 | -0.0027131 | 0.0024204 | 0.013437 | -0.0059205 | 0.018707 | -1.4553 | -0.00098477 | -0.0083996 | 0.015321 | 0.0010467 | 2.4719 | 120.9412 | -0.17395 | 120.9503 | 2.9984 | 0.54016 | 2.2934 | -0.054932 | -0.041199 | 0.022888 | -0.013733 | 0.050354 | 0.004578 | 0.064087 | 0.12817 | -0.1236 | -0.11444 | 3.3005 | 2.5955 | 0.84228 | 2.4673 | 0.71411 | 0.32501 | -121.106 | -121.0785 | 0.35248 | 0.36621 | 0.3067 | 0.041199 | -0.01831 | 3.1723 | 121.1243 | 0.027466 | -0.036621 | 121.1151 | -0.064087 | 121.2433 | 0.26093 | -121.2387 | -121.0419 | 121.2524 | 0.28839 | 2.774 | 0.24719
3449.6875 | 121.4584 | -0.24261 | 121.0373 | -0.020981 | 6.9656 | 0.063895 | 0.1058 | -0.0042083 | -0.0037746 | 0.01301 | 0.00018312 | 0.018493 | -1.4529 | 0.0067056 | -0.0060498 | 0.014253 | 0.00061949 | 2.536 | 120.9366 | -0.16937 | 121.0327 | 3.1311 | 0.6134 | 2.3621 | 0.082397 | -0.054932 | 0.036621 | 0.09613 | 0.1831 | 0.10529 | 0.15106 | 0.073242 | -0.10071 | -0.004577 | 3.3737 | 2.6047 | 0.85602 | 2.5314 | 0.78278 | 0.27924 | -121.0922 | -120.9412 | 0.42572 | 0.39368 | 0.3479 | 0.11444 | 0.068665 | 3.3005 | 121.2021 | 0.14648 | 0.059509 | 121.106 | -0.091553 | 121.1792 | 0.18768 | -121.2067 | -121.0007 | 121.2753 | 0.33874 | 2.7786 | 0.32501
3451.3906 | 121.344 | -0.29297 | 121.106 | -0.020981 | 6.9673 | 0.064749 | 0.10537 | -0.0057037 | 0.00092496 | 0.017282 | -0.0059205 | 0.022552 | -1.4527 | -0.0044028 | -0.0077588 | 0.014039 | 0.0023285 | 2.4582 | 120.9549 | -0.19226 | 120.8908 | 2.9617 | 0.48981 | 2.2659 | -0.09613 | -0.036621 | -0.004578 | -0.032043 | 0.022888 | -0.032043 | 0.068665 | 0.10071 | -0.15106 | -0.21515 | 3.2547 | 2.5589 | 0.78278 | 2.4582 | 0.68207 | 0.28839 | -121.1426 | -121.138 | 0.31586 | 0.36163 | 0.26093 | 0.073243 | -0.027465 | 3.154 | 121.0831 | 0.027466 | -0.027465 | 121.1472 | -0.032043 | 121.2479 | 0.25635 | -121.2982 | -121.1105 | 121.1838 | 0.26093 | 2.7512 | 0.19684
3453.1719 | 121.4401 | -0.27466 | 121.0739 | 0.0019074 | 6.9682 | 0.063467 | 0.10794 | -0.00014949 | -0.00078404 | 0.014505 | -0.012024 | 0.018921 | -1.4516 | 0.0071328 | -0.0049818 | 0.014466 | 0.0048919 | 2.5085 | 120.9503 | -0.17853 | 120.9595 | 3.0579 | 0.53558 | 2.3209 | -0.013733 | -0.064087 | 0.036621 | 0.050354 | 0.11444 | 0.064087 | 0.11902 | 0.09613 | -0.1236 | -0.11444 | 3.3325 | 2.5955 | 0.81024 | 2.4994 | 0.71411 | 0.31128 | -121.138 | -121.0236 | 0.3891 | 0.39368 | 0.33875 | 0.082398 | 0.027466 | 3.2364 | 121.138 | 0.07782 | 0.013733 | 121.1288 | -0.10071 | 121.225 | 0.21057 | -121.2524 | -121.0373 | 121.2341 | 0.32501 | 2.7832 | 0.26093
3454.9531 | 121.4859 | -0.25177 | 121.051 | -0.013352 | 6.9682 | 0.061972 | 0.10623 | 0.0017731 | -0.00035684 | 0.016214 | -0.0028687 | 0.019348 | -1.4555 | 0.0043558 | -0.0041272 | 0.013826 | 0.0044647 | 2.5955 | 120.9778 | -0.15106 | 121.0419 | 3.1494 | 0.57678 | 2.3804 | 0.050354 | -0.054932 | 0.054932 | 0.10986 | 0.13733 | 0.07782 | 0.16479 | 0.10071 | -0.073242 | -0.009155 | 3.4012 | 2.6321 | 0.82855 | 2.5314 | 0.72784 | 0.3067 | -121.106 | -120.9412 | 0.3891 | 0.41656 | 0.32959 | 0.10986 | 0.022888 | 3.3005 | 121.1929 | 0.082397 | 0.054931 | 121.1288 | -0.10986 | 121.2296 | 0.19684 | -121.2021 | -120.9961 | 121.2936 | 0.36163 | 2.8473 | 0.30212
3456.6719 | 121.3806 | -0.31128 | 121.0968 | -0.013352 | 6.9695 | 0.062827 | 0.10708 | -0.0057037 | 7.0564e-05 | 0.015146 | -0.0028687 | 0.021911 | -1.4525 | -0.0039756 | -0.0073316 | 0.013185 | 0.00019229 | 2.5131 | 121.0144 | -0.21057 | 120.9229 | 3.0533 | 0.50354 | 2.3163 | -0.11902 | -0.022888 | 0 | -0.032043 | 0.036621 | -0.041199 | 0.059509 | 0.10071 | -0.082398 | -0.17395 | 3.3646 | 2.6276 | 0.81482 | 2.5269 | 0.71411 | 0.31128 | -121.1197 | -121.1288 | 0.3479 | 0.37079 | 0.27008 | 0.059509 | -0.041199 | 3.2639 | 121.1334 | 0.036621 | -0.032043 | 121.225 | -0.022888 | 121.3257 | 0.28839 | -121.3074 | -121.0968 | 121.2341 | 0.27924 | 2.8244 | 0.19226
3458.4531 | 121.5088 | -0.2655 | 121.0922 | -0.013352 | 6.9658 | 0.064536 | 0.10623 | 0.0017731 | -0.0014248 | 0.011301 | -0.0028687 | 0.017212 | -1.4546 | -0.0052572 | -0.0077588 | 0.015748 | 0.00040589 | 2.5864 | 120.9869 | -0.16022 | 121.0419 | 3.1952 | 0.60883 | 2.417 | 0.036621 | -0.064087 | 0.013733 | 0.091553 | 0.14191 | 0.09613 | 0.16479 | 0.10529 | -0.10529 | -0.050354 | 3.4607 | 2.6825 | 0.87433 | 2.5772 | 0.76904 | 0.27924 | -121.1563 | -121.0007 | 0.40741 | 0.4303 | 0.36163 | 0.15106 | 0.082397 | 3.3554 | 121.2021 | 0.12817 | 0.07782 | 121.1472 | -0.07782 | 121.2524 | 0.20142 | -121.2524 | -121.0785 | 121.3074 | 0.35706 | 2.8519 | 0.30212
3460.2344 | 121.5088 | -0.24719 | 121.106 | -0.0057221 | 6.9673 | 0.065817 | 0.10986 | 0.00049131 | 7.0564e-05 | 0.017923 | -0.0059205 | 0.020202 | -1.4544 | 0.003074 | -0.0045544 | 0.01703 | 0.0016877 | 2.655 | 120.9915 | -0.16937 | 121.051 | 3.2318 | 0.58594 | 2.4216 | 0.059509 | -0.082397 | 0.045776 | 0.11444 | 0.13275 | 0.064087 | 0.17853 | 0.077819 | -0.11444 | -0.054932 | 3.479 | 2.6688 | 0.83313 | 2.5909 | 0.75531 | 0.29297 | -121.1884 | -120.9915 | 0.37994 | 0.42572 | 0.31128 | 0.13275 | 0.018311 | 3.4012 | 121.2204 | 0.086975 | 0.068665 | 121.1609 | -0.12817 | 121.2387 | 0.16479 | -121.2753 | -121.0602 | 121.2982 | 0.36163 | 2.9022 | 0.3067
3462.0156 | 121.4951 | -0.24719 | 121.1014 | 0.0019074 | 6.9669 | 0.066245 | 0.10772 | 0.00070491 | 0.0011386 | 0.017709 | -0.0059205 | 0.021484 | -1.4514 | 0.0039286 | -0.004768 | 0.016175 | 0.00040589 | 2.6917 | 120.9869 | -0.16937 | 121.0922 | 3.2776 | 0.59509 | 2.449 | 0.054932 | -0.07782 | 0.050354 | 0.091553 | 0.15106 | 0.059509 | 0.15106 | 0.077819 | -0.11444 | -0.009155 | 3.5248 | 2.6962 | 0.84228 | 2.6184 | 0.76447 | 0.29755 | -121.1792 | -121.0098 | 0.39825 | 0.39825 | 0.3067 | 0.10071 | 0.009155 | 3.447 | 121.2616 | 0.10071 | 0.041199 | 121.1563 | -0.12817 | 121.2341 | 0.16937 | -121.2708 | -121.051 | 121.3394 | 0.33874 | 2.9388 | 0.30212
3463.75 | 121.5134 | -0.2655 | 121.1105 | -0.0057221 | 6.9682 | 0.062827 | 0.10729 | 0.00027771 | -0.00099764 | 0.016428 | -0.0028687 | 0.019989 | -1.4525 | 0.0024332 | -0.0069044 | 0.015748 | 0.0027557 | 2.6688 | 121.0007 | -0.16479 | 121.0602 | 3.2639 | 0.59967 | 2.4582 | 0.018311 | -0.054932 | 0.018311 | 0.073242 | 0.14648 | 0.07782 | 0.15106 | 0.10071 | -0.10986 | -0.050354 | 3.5294 | 2.7237 | 0.86517 | 2.623 | 0.76447 | 0.28381 | -121.1655 | -121.0373 | 0.41199 | 0.41656 | 0.34332 | 0.13275 | 0.059509 | 3.4286 | 121.225 | 0.12817 | 0.054931 | 121.1655 | -0.073243 | 121.2662 | 0.21057 | -121.2753 | -121.0922 | 121.3257 | 0.33874 | 2.9343 | 0.28381
3465.5312 | 121.5179 | -0.26093 | 121.1243 | -0.013352 | 6.9675 | 0.066031 | 0.10836 | -0.0052765 | 0.00028416 | 0.013864 | -0.0059205 | 0.018921 | -1.4546 | 0.0020058 | -0.0069044 | 0.015321 | 0.00061949 | 2.7008 | 120.9778 | -0.17853 | 121.1105 | 3.3554 | 0.63171 | 2.4994 | 0.041199 | -0.064087 | 0.018311 | 0.064087 | 0.14648 | 0.091553 | 0.15106 | 0.082397 | -0.14648 | -0.013733 | 3.6163 | 2.7603 | 0.89264 | 2.6779 | 0.81024 | 0.27924 | -121.1884 | -121.0602 | 0.40741 | 0.41199 | 0.35248 | 0.13275 | 0.073242 | 3.5339 | 121.2891 | 0.12817 | 0.045776 | 121.1563 | -0.082398 | 121.2387 | 0.19684 | -121.3028 | -121.106 | 121.3715 | 0.32501 | 2.9617 | 0.30212
3467.3125 | 121.5546 | -0.26093 | 121.138 | -0.020981 | 6.9684 | 0.066245 | 0.10922 | -0.0037811 | 0.00071136 | 0.016641 | -0.0028687 | 0.02127 | -1.4533 | 0.0026468 | -0.0069044 | 0.013185 | -0.0025849 | 2.7008 | 121.0144 | -0.1831 | 121.0968 | 3.3279 | 0.63629 | 2.5131 | 0.054932 | -0.073242 | 0.027466 | 0.091553 | 0.16479 | 0.091553 | 0.16479 | 0.07782 | -0.1236 | -0.041198 | 3.5889 | 2.774 | 0.89722 | 2.6962 | 0.8194 | 0.28839 | -121.2112 | -121.0464 | 0.42572 | 0.42572 | 0.35248 | 0.13733 | 0.064087 | 3.511 | 121.2799 | 0.13733 | 0.064087 | 121.1975 | -0.10071 | 121.2753 | 0.18768 | -121.3211 | -121.1105 | 121.3577 | 0.35248 | 2.9617 | 0.31586
3469.1094 | 121.4218 | -0.28381 | 121.1838 | -0.0057221 | 6.9692 | 0.066672 | 0.11114 | 0.00049131 | 0.0013522 | 0.017709 | 0.00018312 | 0.022125 | -1.4523 | -0.0035482 | -0.004768 | 0.012758 | -0.00066231 | 2.6596 | 121.0831 | -0.21057 | 120.9732 | 3.1952 | 0.48523 | 2.3849 | -0.12817 | -0.036621 | 0.009155 | -0.022888 | -0.022888 | -0.07782 | 0.054932 | 0.073242 | -0.10071 | -0.21057 | 3.479 | 2.6688 | 0.76904 | 2.5955 | 0.6958 | 0.29297 | -121.2204 | -121.2067 | 0.26092 | 0.33874 | 0.20599 | 0.045777 | -0.086975 | 3.4058 | 121.1838 | -0.032043 | -0.032043 | 121.2936 | -0.045776 | 121.3669 | 0.24719 | -121.3943 | -121.1746 | 121.257 | 0.26092 | 2.9434 | 0.15564
3470.8281 | 121.4813 | -0.30212 | 121.1884 | -0.0057221 | 6.9675 | 0.062613 | 0.10943 | 0.00070491 | -0.0016384 | 0.017923 | -0.0028687 | 0.02063 | -1.4538 | 0.0049966 | -0.011177 | 0.014039 | -0.00066231 | 2.6962 | 121.1014 | -0.20599 | 121.0281 | 3.2547 | 0.56305 | 2.4536 | -0.09613 | -0.032043 | 0.009155 | -0.009155 | 0.054932 | -0.009155 | 0.07782 | 0.09613 | -0.086975 | -0.16022 | 3.5568 | 2.7557 | 0.86517 | 2.6596 | 0.76904 | 0.31128 | -121.2204 | -121.1975 | 0.35706 | 0.37994 | 0.29297 | 0.068665 | -0.01831 | 3.4607 | 121.2341 | 0.045777 | -0.01831 | 121.3074 | -0.041198 | 121.4035 | 0.27008 | -121.3943 | -121.1792 | 121.3303 | 0.29297 | 2.9984 | 0.20599
3472.6094 | 121.55 | -0.25635 | 121.1472 | -0.013352 | 6.9682 | 0.065176 | 0.10879 | -0.0035675 | 0.0028476 | 0.0207 | -0.0028687 | 0.019134 | -1.4538 | 0.0058512 | -0.0086132 | 0.011689 | 0.00061949 | 2.7603 | 121.0556 | -0.16479 | 121.1288 | 3.4332 | 0.65002 | 2.5818 | 0.050354 | -0.07782 | 0.054932 | 0.068665 | 0.14648 | 0.091553 | 0.13275 | 0.091553 | -0.091553 | -0.018311 | 3.6896 | 2.8381 | 0.90637 | 2.7466 | 0.81482 | 0.31128 | -121.225 | -121.0785 | 0.40283 | 0.3891 | 0.3479 | 0.077819 | 0.036621 | 3.598 | 121.2936 | 0.091552 | 0.013733 | 121.2204 | -0.13275 | 121.312 | 0.17853 | -121.312 | -121.0922 | 121.3852 | 0.32501 | 3.0167 | 0.3067
3474.3906 | 121.4447 | -0.29755 | 121.2067 | 0.0019074 | 6.9697 | 0.063467 | 0.11285 | -0.0010041 | 7.0564e-05 | 0.016 | -0.0059205 | 0.021698 | -1.4525 | -0.0024802 | -0.005409 | 0.015107 | -0.0015167 | 2.7008 | 121.1014 | -0.19226 | 121.0052 | 3.2318 | 0.46234 | 2.4353 | -0.11444 | -0.027466 | -0.018311 | -0.036621 | -0.013733 | -0.086975 | 0.054932 | 0.10528 | -0.10529 | -0.20142 | 3.5294 | 2.7328 | 0.75989 | 2.6276 | 0.6546 | 0.27923 | -121.2341 | -121.2433 | 0.28381 | 0.35248 | 0.21057 | 0.073243 | -0.068664 | 3.4241 | 121.1975 | 0.004578 | -0.01831 | 121.2936 | -0.009155 | 121.3989 | 0.27008 | -121.3989 | -121.225 | 121.3028 | 0.26092 | 2.9984 | 0.1831
3476.1094 | 121.5775 | -0.25177 | 121.1609 | -0.020981 | 6.9692 | 0.064963 | 0.11306 | 0.00049131 | 7.0564e-05 | 0.016214 | -0.0028687 | 0.018921 | -1.4521 | 0.0058512 | -0.0017774 | 0.015321 | -2.1314e-05 | 2.7832 | 121.0648 | -0.16022 | 121.1334 | 3.447 | 0.60883 | 2.5955 | 0.059509 | -0.07782 | 0.045776 | 0.10986 | 0.13733 | 0.07782 | 0.15564 | 0.091553 | -0.096131 | -0.027466 | 3.6987 | 2.8473 | 0.8606 | 2.7557 | 0.76904 | 0.29755 | -121.2387 | -121.051 | 0.3891 | 0.40741 | 0.32959 | 0.10986 | 0.032044 | 3.6072 | 121.2936 | 0.091553 | 0.064087 | 121.225 | -0.1236 | 121.3165 | 0.17395 | -121.3211 | -121.1151 | 121.3852 | 0.36163 | 3.035 | 0.31128
3477.9062 | 121.5179 | -0.31128 | 121.2112 | -0.013352 | 6.9705 | 0.062827 | 0.11199 | 0.0019867 | -0.0016384 | 0.015787 | -0.0028687 | 0.022339 | -1.4538 | 0.00029703 | -0.0086132 | 0.014253 | 0.0010467 | 2.7466 | 121.0968 | -0.20142 | 121.0876 | 3.3966 | 0.58594 | 2.5772 | -0.036621 | -0.041199 | 0.009155 | 0.004578 | 0.064087 | 0 | 0.09613 | 0.10986 | -0.11444 | -0.1236 | 3.7079 | 2.8885 | 0.89722 | 2.7786 | 0.78735 | 0.32043 | -121.2524 | -121.2067 | 0.37537 | 0.40741 | 0.31128 | 0.086975 | -0.009155 | 3.598 | 121.2891 | 0.054932 | -0.004577 | 121.2982 | -0.050354 | 121.4081 | 0.27008 | -121.4127 | -121.2021 | 121.3989 | 0.31586 | 3.0579 | 0.27466
3479.6875 | 121.5775 | -0.27466 | 121.2021 | 0.0019074 | 6.9688 | 0.064536 | 0.11328 | 0.00070491 | 0.0019932 | 0.014291 | 0.00018312 | 0.021911 | -1.4529 | -0.0063254 | -0.0045544 | 0.015748 | 0.00019229 | 2.7374 | 121.1105 | -0.20142 | 121.0876 | 3.4378 | 0.58136 | 2.6138 | 0.009155 | -0.07782 | 0.013733 | 0.073242 | 0.09613 | 0.041199 | 0.14648 | 0.073242 | -0.091552 | -0.11444 | 3.7125 | 2.8885 | 0.85602 | 2.8152 | 0.78278 | 0.28839 | -121.2799 | -121.1288 | 0.37079 | 0.42114 | 0.31586 | 0.13275 | 0.027466 | 3.6392 | 121.2891 | 0.082397 | 0.059509 | 121.312 | -0.091553 | 121.3852 | 0.19684 | -121.4035 | -121.1884 | 121.3623 | 0.3479 | 3.0121 | 0.28381
3481.4688 | 121.5408 | -0.27466 | 121.1975 | -0.020981 | 6.9701 | 0.065604 | 0.109 | 0.00070491 | -0.00099764 | 0.017709 | 0.00018312 | 0.019775 | -1.4544 | -0.009957 | -0.0094678 | 0.012544 | -0.00087591 | 2.7924 | 121.0922 | -0.1831 | 121.1517 | 3.5248 | 0.66376 | 2.6871 | 0 | -0.068665 | 0.013733 | 0.027466 | 0.10071 | 0.045776 | 0.10071 | 0.091553 | -0.10529 | -0.045777 | 3.7994 | 2.9617 | 0.93841 | 2.8702 | 0.84686 | 0.28839 | -121.2662 | -121.17 | 0.37537 | 0.37537 | 0.32043 | 0.086975 | 0.032043 | 3.7079 | 121.3348 | 0.086975 | 0.013733 | 121.2753 | -0.082398 | 121.3669 | 0.20599 | -121.3806 | -121.1838 | 121.4264 | 0.30212 | 3.067 | 0.27466
3483.1875 | 121.582 | -0.26093 | 121.2112 | -0.020981 | 6.968 | 0.066245 | 0.11328 | 0.0013459 | 7.0564e-05 | 0.018137 | -0.0059205 | 0.017639 | -1.4531 | 8.3226e-05 | -0.0051954 | 0.014466 | 0.0029693 | 2.7969 | 121.0739 | -0.15106 | 121.1472 | 3.5568 | 0.63629 | 2.6962 | 0.050354 | -0.07782 | 0.027466 | 0.054932 | 0.09613 | 0.045776 | 0.11902 | 0.10986 | -0.13733 | -0.064087 | 3.8177 | 2.9572 | 0.89722 | 2.8473 | 0.78735 | 0.28839 | -121.2891 | -121.1563 | 0.35706 | 0.37994 | 0.3067 | 0.091553 | 0.01831 | 3.7079 | 121.2982 | 0.068664 | 0.027466 | 121.225 | -0.10529 | 121.3348 | 0.18311 | -121.3623 | -121.1838 | 121.4081 | 0.31586 | 3.0579 | 0.31128
3484.9688 | 121.6095 | -0.26093 | 121.2112 | -0.013352 | 6.9654 | 0.064108 | 0.1137 | -0.0022857 | -0.00057044 | 0.019846 | -0.0059205 | 0.018707 | -1.4531 | 0.00072423 | -0.0092542 | 0.016816 | -0.00087591 | 2.8152 | 121.0831 | -0.16479 | 121.17 | 3.6072 | 0.67749 | 2.742 | 0.041199 | -0.07782 | 0.036621 | 0.064087 | 0.15564 | 0.07782 | 0.14191 | 0.09613 | -0.12817 | -0.041199 | 3.8681 | 3.0029 | 0.93841 | 2.9068 | 0.84229 | 0.29755 | -121.2891 | -121.1472 | 0.41657 | 0.40283 | 0.33875 | 0.10529 | 0.041199 | 3.772 | 121.3348 | 0.11902 | 0.027466 | 121.2479 | -0.11444 | 121.344 | 0.18311 | -121.376 | -121.1746 | 121.431 | 0.32501 | 3.0762 | 0.30212
3486.75 | 121.5088 | -0.31128 | 121.2112 | -0.0057221 | 6.9692 | 0.066245 | 0.11776 | -0.00036309 | 0.0019932 | 0.01835 | -0.0028687 | 0.022339 | -1.4525 | -0.003121 | -0.005409 | 0.014466 | -0.0023713 | 2.7557 | 121.1243 | -0.2243 | 121.0327 | 3.4378 | 0.51727 | 2.6367 | -0.1236 | -0.036621 | 0 | -0.050354 | -0.009155 | -0.086975 | 0.045776 | 0.086975 | -0.086975 | -0.17853 | 3.7491 | 2.948 | 0.82855 | 2.861 | 0.74158 | 0.31128 | -121.2479 | -121.2616 | 0.30212 | 0.35705 | 0.2243 | 0.045776 | -0.086975 | 3.6621 | 121.257 | -0.009155 | -0.050354 | 121.3486 | -0.036621 | 121.4355 | 0.27466 | -121.4355 | -121.2112 | 121.344 | 0.26092 | 3.067 | 0.18768
3488.4688 | 121.6278 | -0.29297 | 121.2204 | -0.013352 | 6.9665 | 0.064536 | 0.11242 | -0.0012177 | -0.00014304 | 0.019846 | -0.0028687 | 0.018066 | -1.4529 | 0.0062784 | -0.005409 | 0.015107 | 0.0014741 | 2.8061 | 121.1243 | -0.18768 | 121.1334 | 3.6209 | 0.64545 | 2.7695 | -0.013733 | -0.073242 | 0 | 0.054932 | 0.12817 | 0.064087 | 0.13733 | 0.10529 | -0.09613 | -0.086975 | 3.9139 | 3.0624 | 0.93842 | 2.9572 | 0.83313 | 0.29297 | -121.2936 | -121.1655 | 0.42114 | 0.4303 | 0.35706 | 0.13733 | 0.064087 | 3.8086 | 121.3211 | 0.12817 | 0.054932 | 121.312 | -0.073242 | 121.4172 | 0.21973 | -121.4081 | -121.2204 | 121.4264 | 0.3479 | 3.0991 | 0.27924
3490.25 | 121.5729 | -0.29297 | 121.2753 | -0.013352 | 6.9688 | 0.062399 | 0.11456 | -0.0033539 | 0.00092496 | 0.016641 | -0.0028687 | 0.020416 | -1.4536 | -0.0088888 | -0.0077588 | 0.014894 | -0.00023491 | 2.8748 | 121.0876 | -0.19684 | 121.1655 | 3.6621 | 0.67291 | 2.7832 | 0 | -0.068665 | 0.013733 | 0.004578 | 0.07782 | 0.036621 | 0.10529 | 0.096131 | -0.18768 | -0.10986 | 3.9551 | 3.0762 | 0.96588 | 2.98 | 0.86975 | 0.3067 | -121.344 | -121.2708 | 0.37079 | 0.39825 | 0.32959 | 0.091553 | 0.022888 | 3.8589 | 121.3623 | 0.064087 | -0.009155 | 121.2845 | -0.082398 | 121.3806 | 0.2243 | -121.4722 | -121.2616 | 121.4584 | 0.29755 | 3.1677 | 0.29297
3492.0312 | 121.637 | -0.2655 | 121.2158 | -0.020981 | 6.968 | 0.06539 | 0.11434 | -0.0057037 | 0.0024204 | 0.017709 | -0.0028687 | 0.019348 | -1.4544 | 0.0090554 | -0.0073316 | 0.014894 | 0.00040589 | 2.8793 | 121.0876 | -0.17853 | 121.225 | 3.7491 | 0.70953 | 2.8427 | 0.045776 | -0.068665 | 0.022888 | 0.064087 | 0.14191 | 0.082397 | 0.15564 | 0.086975 | -0.12817 | 0.009156 | 4.0146 | 3.1082 | 0.97504 | 3.0212 | 0.88806 | 0.28839 | -121.2845 | -121.1517 | 0.40741 | 0.42114 | 0.3479 | 0.13275 | 0.059509 | 3.9276 | 121.4035 | 0.11902 | 0.041199 | 121.2662 | -0.091553 | 121.3531 | 0.19684 | -121.3943 | -121.1929 | 121.4905 | 0.32959 | 3.1448 | 0.31128
3493.8125 | 121.6049 | -0.29755 | 121.2387 | -0.013352 | 6.9695 | 0.064963 | 0.11627 | -0.0029267 | 0.0030612 | 0.018991 | 0.00018312 | 0.020202 | -1.4536 | 0.0096964 | -0.004768 | 0.01468 | 0.0023285 | 2.8519 | 121.1105 | -0.1831 | 121.1472 | 3.6896 | 0.63629 | 2.8244 | -0.036621 | -0.073242 | 0.018311 | 0.036621 | 0.073242 | 0.013733 | 0.10071 | 0.11444 | -0.12817 | -0.091552 | 3.9871 | 3.1219 | 0.93384 | 3.0075 | 0.8194 | 0.31586 | -121.3119 | -121.2021 | 0.37079 | 0.39825 | 0.31128 | 0.082397 | -0.004578 | 3.8727 | 121.3303 | 0.054931 | 0.01831 | 121.2936 | -0.091553 | 121.4081 | 0.2243 | -121.4218 | -121.2204 | 121.4447 | 0.33417 | 3.1494 | 0.26092
3495.5938 | 121.4996 | -0.31586 | 121.2708 | 0.0019074 | 6.9729 | 0.067954 | 0.11883 | 0.0022003 | 0.00028416 | 0.019418 | -0.0028687 | 0.02127 | -1.4514 | -0.003121 | -0.0051954 | 0.013398 | 0.0027557 | 2.8381 | 121.1517 | -0.21515 | 121.0831 | 3.6209 | 0.55389 | 2.7695 | -0.14191 | -0.041199 | 0 | -0.050354 | -0.018311 | -0.10529 | 0.018311 | 0.10071 | -0.11902 | -0.18768 | 3.9368 | 3.0853 | 0.86975 | 2.9846 | 0.76904 | 0.31586 | -121.312 | -121.3211 | 0.29755 | 0.33417 | 0.21057 | 0.018311 | -0.10529 | 3.8361 | 121.2982 | -0.018311 | -0.050354 | 121.3669 | -0.041199 | 121.4676 | 0.27466 | -121.4859 | -121.2708 | 121.3989 | 0.2655 | 3.154 | 0.17395
3497.3594 | 121.6187 | -0.27924 | 121.2387 | -0.0057221 | 6.9682 | 0.067526 | 0.11648 | -0.0035675 | 0.002634 | 0.022409 | -0.0028687 | 0.019775 | -1.4531 | -0.0069662 | -0.0066906 | 0.015962 | 0.00019229 | 2.8931 | 121.1197 | -0.16479 | 121.1929 | 3.8269 | 0.66834 | 2.9205 | 0.022888 | -0.091553 | 0.022888 | 0.054932 | 0.091553 | 0.036621 | 0.10529 | 0.11444 | -0.11902 | -0.045776 | 4.1061 | 3.1998 | 0.94757 | 3.0853 | 0.83313 | 0.30212 | -121.3303 | -121.1838 | 0.37079 | 0.38452 | 0.31586 | 0.082398 | 0.013733 | 3.9917 | 121.3577 | 0.068665 | 0.032044 | 121.2845 | -0.11444 | 121.3989 | 0.18768 | -121.4035 | -121.2158 | 121.4722 | 0.33417 | 3.1723 | 0.30212
3499.0938 | 121.6278 | -0.29297 | 121.2479 | -0.020981 | 6.9671 | 0.065817 | 0.11691 | -0.0037811 | 0.0045566 | 0.016855 | -0.0028687 | 0.019775 | -1.4555 | 0.00051063 | -0.0060498 | 0.014039 | -0.00066231 | 2.8885 | 121.17 | -0.18768 | 121.1517 | 3.8177 | 0.65002 | 2.9343 | -0.036621 | -0.073242 | 0.013733 | 0.013733 | 0.073242 | 0 | 0.086975 | 0.10529 | -0.07782 | -0.096131 | 4.1107 | 3.2272 | 0.94299 | 3.1219 | 0.83771 | 0.3067 | -121.3211 | -121.2341 | 0.36621 | 0.37994 | 0.29297 | 0.073242 | -0.013733 | 4.0054 | 121.3394 | 0.059509 | 0 | 121.3577 | -0.086975 | 121.463 | 0.21973 | -121.4355 | -121.2341 | 121.4447 | 0.3067 | 3.1815 | 0.25635
3500.875 | 121.6003 | -0.30212 | 121.2708 | -0.013352 | 6.9695 | 0.065176 | 0.11755 | 0.0015595 | 0.00028416 | 0.019418 | -0.0059205 | 0.022125 | -1.4538 | 0.0011514 | -0.008186 | 0.013398 | -0.0023713 | 2.8793 | 121.17 | -0.21973 | 121.1472 | 3.804 | 0.63629 | 2.9388 | -0.027466 | -0.036621 | -0.004578 | 0.009155 | 0.064087 | -0.004578 | 0.082397 | 0.082397 | -0.10071 | -0.1236 | 4.1061 | 3.241 | 0.93842 | 3.1586 | 0.85602 | 0.29755 | -121.3074 | -121.2616 | 0.36621 | 0.38452 | 0.29755 | 0.086975 | 0 | 4.0237 | 121.3669 | 0.068665 | 0.013733 | 121.3898 | -0.032043 | 121.4722 | 0.2655 | -121.4905 | -121.2753 | 121.4493 | 0.31128 | 3.1815 | 0.27466
3502.6406 | 121.6003 | -0.32044 | 121.2662 | -0.013352 | 6.9675 | 0.066245 | 0.12011 | 0.0030547 | 0.002634 | 0.019205 | -0.0028687 | 0.021057 | -1.4508 | 0.0022196 | -0.0069044 | 0.015107 | -0.00044851 | 2.8885 | 121.1563 | -0.21057 | 121.1472 | 3.8361 | 0.65918 | 2.9709 | -0.041199 | -0.059509 | 0.004578 | 0.009155 | 0.036621 | -0.022888 | 0.073242 | 0.10986 | -0.10986 | -0.11902 | 4.1565 | 3.2913 | 0.97962 | 3.1815 | 0.86975 | 0.32501 | -121.3257 | -121.257 | 0.35706 | 0.39368 | 0.29755 | 0.068664 | -0.027466 | 4.0466 | 121.3577 | 0.032043 | 0.004577 | 121.3669 | -0.064087 | 121.4767 | 0.26093 | -121.4767 | -121.2616 | 121.4676 | 0.32959 | 3.2089 | 0.27924
3504.4219 | 121.5683 | -0.34332 | 121.2982 | -0.0057221 | 6.9686 | 0.063681 | 0.11947 | -0.0037811 | -0.00014304 | 0.021127 | -0.0028687 | 0.020416 | -1.4523 | -0.006539 | -0.011604 | 0.013185 | 0.00083309 | 2.8198 | 121.1609 | -0.23804 | 121.0968 | 3.7994 | 0.63171 | 2.9709 | -0.12817 | -0.022888 | -0.013733 | -0.068665 | 0 | -0.054932 | 0.027466 | 0.10529 | -0.13733 | -0.20142 | 4.1428 | 3.3142 | 0.97504 | 3.2089 | 0.86975 | 0.32959 | -121.3211 | -121.3669 | 0.34332 | 0.37079 | 0.28839 | 0.041199 | -0.041199 | 4.0375 | 121.3348 | 0.013733 | -0.054932 | 121.3989 | -0.009155 | 121.5042 | 0.32043 | -121.5363 | -121.312 | 121.4401 | 0.27466 | 3.1631 | 0.21515
3506.1406 | 121.6461 | -0.29755 | 121.2753 | -0.0057221 | 6.968 | 0.065817 | 0.11883 | -0.00079049 | 0.0019932 | 0.021555 | -0.0028687 | 0.017852 | -1.4527 | 0.001365 | -0.0041272 | 0.015535 | -0.0021575 | 2.8839 | 121.1334 | -0.1831 | 121.1563 | 3.9139 | 0.67291 | 3.0716 | -0.064087 | -0.09613 | 0.018311 | 0.004578 | 0.073242 | 0.009155 | 0.091553 | 0.11444 | -0.14191 | -0.11902 | 4.2114 | 3.3691 | 0.97046 | 3.2547 | 0.85602 | 0.31586 | -121.3715 | -121.2708 | 0.37079 | 0.3891 | 0.3067 | 0.073242 | -0.009156 | 4.097 | 121.3394 | 0.054931 | -0.013733 | 121.3165 | -0.11444 | 121.431 | 0.20142 | -121.4584 | -121.257 | 121.4539 | 0.30212 | 3.1815 | 0.23346
3507.9219 | 121.5912 | -0.31128 | 121.312 | -0.0057221 | 6.9671 | 0.06539 | 0.12268 | -0.00079049 | 7.0564e-05 | 0.021341 | -0.0059205 | 0.02127 | -1.4536 | -0.003762 | -0.0094678 | 0.012758 | -0.0021575 | 2.8793 | 121.1563 | -0.23804 | 121.106 | 3.8681 | 0.65002 | 3.0533 | -0.13275 | -0.041199 | -0.009155 | -0.041199 | 0.009155 | -0.059509 | 0.050354 | 0.073242 | -0.15564 | -0.20599 | 4.1794 | 3.3646 | 0.9613 | 3.2913 | 0.88806 | 0.30212 | -121.3531 | -121.3531 | 0.32043 | 0.36163 | 0.25177 | 0.059509 | -0.050354 | 4.1061 | 121.344 | 0.01831 | -0.032044 | 121.3943 | -0.032044 | 121.4676 | 0.27008 | -121.55 | -121.3211 | 121.4172 | 0.27008 | 3.1906 | 0.17853
3509.7031 | 121.6095 | -0.32044 | 121.2845 | -0.0057221 | 6.9701 | 0.065176 | 0.12246 | 6.4114e-05 | 0.0037022 | 0.021127 | -0.0028687 | 0.022125 | -1.451 | 0.003074 | -0.0041272 | 0.015748 | 0.00040589 | 2.8793 | 121.1884 | -0.21057 | 121.1014 | 3.9276 | 0.61798 | 3.0899 | -0.10529 | -0.054932 | -0.013733 | -0.009155 | 0.004578 | -0.064087 | 0.068665 | 0.10986 | -0.096131 | -0.18311 | 4.248 | 3.4103 | 0.93842 | 3.3005 | 0.82855 | 0.3067 | -121.3394 | -121.2936 | 0.32501 | 0.3891 | 0.25635 | 0.082398 | -0.050354 | 4.1382 | 121.3119 | 0.018311 | 0.004578 | 121.3989 | -0.041199 | 121.5088 | 0.2655 | -121.4951 | -121.2982 | 121.4218 | 0.31128 | 3.1998 | 0.21515
3511.4219 | 121.6782 | -0.29297 | 121.2753 | 0.0019074 | 6.968 | 0.066458 | 0.12268 | -0.0044221 | 0.0015658 | 0.021555 | -0.0089723 | 0.017852 | -1.4542 | 0.00029703 | -0.0051954 | 0.015107 | 0.00040589 | 2.9526 | 121.1609 | -0.20142 | 121.2067 | 4.1199 | 0.72784 | 3.2089 | 0.009155 | -0.073242 | 0.022888 | 0.054932 | 0.09613 | 0.027466 | 0.10071 | 0.091553 | -0.11444 | -0.068665 | 4.4128 | 3.5019 | 1.0208 | 3.4103 | 0.92926 | 0.31586 | -121.3486 | -121.2204 | 0.3891 | 0.39368 | 0.32043 | 0.07782 | 0.004578 | 4.3213 | 121.4081 | 0.073242 | 0.032044 | 121.3623 | -0.09613 | 121.4539 | 0.21973 | -121.4767 | -121.2524 | 121.4996 | 0.3479 | 3.2455 | 0.30212
3513.2031 | 121.6507 | -0.33417 | 121.3348 | -0.013352 | 6.9684 | 0.06539 | 0.12225 | 0.0039093 | -0.00035684 | 0.022836 | -0.0028687 | 0.022766 | -1.4523 | -0.0086752 | -0.008186 | 0.014253 | -0.00087591 | 2.9572 | 121.2204 | -0.21973 | 121.1746 | 4.0787 | 0.6958 | 3.1906 | -0.054932 | -0.073242 | 0 | -0.004578 | 0.036621 | -0.018311 | 0.086975 | 0.11444 | -0.11444 | -0.16022 | 4.4128 | 3.5248 | 1.03 | 3.4103 | 0.91553 | 0.33417 | -121.4081 | -121.3394 | 0.37079 | 0.42114 | 0.31586 | 0.086975 | -0.018311 | 4.2984 | 121.3943 | 0.036621 | -0.004578 | 121.4401 | -0.073242 | 121.5546 | 0.26092 | -121.5546 | -121.3348 | 121.5088 | 0.32959 | 3.2913 | 0.27924
3514.9844 | 121.6553 | -0.32044 | 121.3257 | -0.0057221 | 6.9701 | 0.065176 | 0.12524 | 0.0013459 | 0.0022068 | 0.021341 | 0.00018312 | 0.021484 | -1.4521 | -0.003762 | -0.008186 | 0.013612 | 0.00083309 | 2.9984 | 121.1929 | -0.21515 | 121.17 | 4.1519 | 0.71411 | 3.241 | -0.027466 | -0.054932 | -0.004578 | 0.009155 | 0.054932 | -0.009155 | 0.09613 | 0.10529 | -0.13275 | -0.15564 | 4.4724 | 3.5614 | 1.0345 | 3.4561 | 0.92926 | 0.31586 | -121.3806 | -121.3165 | 0.37537 | 0.41657 | 0.31128 | 0.10071 | -0.004577 | 4.3671 | 121.3852 | 0.05951 | 0.013733 | 121.4081 | -0.050354 | 121.5134 | 0.2655 | -121.5408 | -121.3303 | 121.4905 | 0.32959 | 3.3188 | 0.29297
3516.7031 | 121.7422 | -0.29297 | 121.2982 | -0.02861 | 6.9669 | 0.065604 | 0.12524 | -0.0022857 | 0.00028416 | 0.021982 | -0.0028687 | 0.018707 | -1.4531 | 0.0024332 | -0.0077588 | 0.015107 | -2.1314e-05 | 3.0121 | 121.1426 | -0.19684 | 121.225 | 4.2892 | 0.82398 | 3.3691 | 0.045776 | -0.10071 | -0.004578 | 0.073242 | 0.16022 | 0.11444 | 0.16022 | 0.096131 | -0.15564 | -0.073242 | 4.5822 | 3.6621 | 1.1169 | 3.566 | 1.0208 | 0.28839 | -121.3989 | -121.225 | 0.45319 | 0.45319 | 0.40741 | 0.16479 | 0.11902 | 4.4861 | 121.4218 | 0.16479 | 0.07782 | 121.3394 | -0.09613 | 121.4355 | 0.19226 | -121.4951 | -121.3028 | 121.5179 | 0.36621 | 3.3051 | 0.33874
3518.5 | 121.5958 | -0.34332 | 121.3394 | -0.013352 | 6.9686 | 0.066458 | 0.12887 | 0.0028411 | 0.0013522 | 0.021341 | -0.0028687 | 0.021484 | -1.4548 | 8.3226e-05 | -0.0034864 | 0.016603 | -0.0015167 | 2.98 | 121.2433 | -0.24719 | 121.1197 | 4.1519 | 0.66376 | 3.2593 | -0.13275 | -0.050354 | -0.009155 | -0.045776 | -0.018311 | -0.09613 | 0.022888 | 0.096131 | -0.096131 | -0.21973 | 4.4952 | 3.6026 | 1.0071 | 3.5065 | 0.91095 | 0.33417 | -121.3898 | -121.3852 | 0.32501 | 0.36621 | 0.24719 | 0.032043 | -0.086975 | 4.3991 | 121.3669 | -0.009156 | -0.036621 | 121.4905 | -0.041199 | 121.5866 | 0.29297 | -121.5866 | -121.3486 | 121.463 | 0.29755 | 3.3234 | 0.21057
3520.2812 | 121.6278 | -0.33417 | 121.3394 | -0.020981 | 6.9677 | 0.066245 | 0.12695 | 0.0017731 | 0.0015658 | 0.023477 | -0.0059205 | 0.021057 | -1.4529 | -0.00034397 | -0.0051954 | 0.014466 | 0.0012603 | 2.9892 | 121.2112 | -0.24261 | 121.1151 | 4.2389 | 0.6546 | 3.3005 | -0.10986 | -0.064087 | -0.009155 | -0.018311 | -0.009155 | -0.082397 | 0.064087 | 0.091552 | -0.12817 | -0.22431 | 4.5731 | 3.6346 | 0.98877 | 3.5431 | 0.89722 | 0.32501 | -121.4035 | -121.3577 | 0.32501 | 0.39825 | 0.25177 | 0.073242 | -0.073242 | 4.4815 | 121.3577 | 0 | -0.009156 | 121.4539 | -0.054932 | 121.5454 | 0.27008 | -121.582 | -121.3486 | 121.4493 | 0.31586 | 3.3234 | 0.2243
3522.0156 | 121.7422 | -0.31586 | 121.3348 | -0.020981 | 6.9709 | 0.064536 | 0.12802 | -0.0039947 | 0.0019932 | 0.021982 | 0.00018312 | 0.018493 | -1.4551 | 0.0022196 | -0.010536 | 0.016175 | 0.0036103 | 3.0762 | 121.17 | -0.19684 | 121.2616 | 4.4449 | 0.85144 | 3.479 | 0.009155 | -0.091553 | 0.013733 | 0.054932 | 0.12817 | 0.064087 | 0.1236 | 0.11902 | -0.16479 | -0.073242 | 4.7607 | 3.7949 | 1.1673 | 3.6758 | 1.0483 | 0.32959 | -121.4264 | -121.2799 | 0.44403 | 0.43945 | 0.37994 | 0.10986 | 0.050354 | 4.6417 | 121.4584 | 0.11444 | 0.041199 | 121.3669 | -0.10529 | 121.4859 | 0.2243 | -121.5317 | -121.3211 | 121.5775 | 0.37079 | 3.392 | 0.32501
3523.7969 | 121.7606 | -0.31128 | 121.3211 | -0.0057221 | 6.9707 | 0.064322 | 0.1293 | 0.00091851 | 0.0011386 | 0.022836 | 0.00018312 | 0.018707 | -1.4512 | 0.0045694 | -0.0037 | 0.014039 | -0.00066231 | 3.067 | 121.2296 | -0.23804 | 121.2067 | 4.4403 | 0.75989 | 3.4515 | -0.027466 | -0.068665 | -0.009155 | 0.050354 | 0.09613 | 0.032043 | 0.1236 | 0.073242 | -0.091553 | -0.11444 | 4.7516 | 3.7628 | 1.0712 | 3.6896 | 0.99792 | 0.30212 | -121.3898 | -121.2708 | 0.40741 | 0.43487 | 0.34332 | 0.13275 | 0.041198 | 4.6783 | 121.4447 | 0.10528 | 0.059509 | 121.4676 | -0.05951 | 121.5408 | 0.24261 | -121.5591 | -121.3303 | 121.5179 | 0.36163 | 3.3783 | 0.28381
3525.5781 | 121.7651 | -0.32044 | 121.2753 | -0.013352 | 6.9688 | 0.066031 | 0.1278 | -0.00079049 | 0.0015658 | 0.022623 | -0.0089723 | 0.019134 | -1.4563 | 0.0073464 | -0.0094678 | 0.015321 | -0.0013031 | 3.1357 | 121.1792 | -0.21973 | 121.2708 | 4.6417 | 0.89722 | 3.6026 | 0.059509 | -0.091553 | 0.009155 | 0.050354 | 0.14191 | 0.073242 | 0.13275 | 0.10071 | -0.096131 | -0.004578 | 4.9622 | 3.923 | 1.2177 | 3.8223 | 1.1169 | 0.32959 | -121.3669 | -121.225 | 0.46234 | 0.45319 | 0.39368 | 0.1236 | 0.064087 | 4.8615 | 121.4905 | 0.13275 | 0.041199 | 121.3989 | -0.10071 | 121.4996 | 0.22888 | -121.4951 | -121.2662 | 121.5912 | 0.37079 | 3.4561 | 0.37994
3527.2812 | 121.6461 | -0.34332 | 121.3394 | -0.0057221 | 6.9697 | 0.06539 | 0.13357 | -0.00014949 | 0.0049838 | 0.024759 | -0.0059205 | 0.020843 | -1.4514 | 8.3226e-05 | -0.0045544 | 0.015748 | -0.0034393 | 3.0853 | 121.2204 | -0.26093 | 121.1243 | 4.4678 | 0.70953 | 3.4698 | -0.15106 | -0.054932 | -0.036621 | -0.045776 | -0.027466 | -0.09613 | 0.009155 | 0.082398 | -0.11902 | -0.21515 | 4.8111 | 3.8132 | 1.0529 | 3.7308 | 0.97046 | 0.3067 | -121.3943 | -121.3852 | 0.31586 | 0.35248 | 0.24719 | 0.045776 | -0.059509 | 4.7287 | 121.3852 | 0.009155 | -0.009155 | 121.4813 | -0.018311 | 121.5637 | 0.28839 | -121.6003 | -121.376 | 121.4676 | 0.29755 | 3.4286 | 0.19226
3529.0781 | 121.6553 | -0.36163 | 121.3623 | -0.013352 | 6.9697 | 0.066031 | 0.1325 | -0.00014949 | 0.0013522 | 0.025613 | -0.0059205 | 0.022339 | -1.4531 | -0.0041892 | -0.010963 | 0.012544 | -2.1314e-05 | 3.1906 | 121.2341 | -0.23804 | 121.1609 | 4.7058 | 0.80109 | 3.598 | -0.11902 | -0.064087 | -0.018311 | -0.068665 | 0 | -0.064087 | 0.004578 | 0.1236 | -0.12817 | -0.20142 | 5.0674 | 3.9597 | 1.1627 | 3.8361 | 1.0391 | 0.34332 | -121.4264 | -121.431 | 0.36163 | 0.36621 | 0.29755 | 0.022889 | -0.045776 | 4.9438 | 121.3989 | 0.018311 | -0.050354 | 121.4722 | -0.045776 | 121.5958 | 0.29755 | -121.6003 | -121.3806 | 121.5225 | 0.29297 | 3.5522 | 0.24261
3530.8594 | 121.7926 | -0.31586 | 121.3348 | -0.020981 | 6.9688 | 0.064536 | 0.13378 | 0.0036957 | 0.0017796 | 0.027536 | -0.0059205 | 0.019989 | -1.4523 | 0.0017922 | -0.0062634 | 0.013612 | 0.0019013 | 3.2913 | 121.1975 | -0.20142 | 121.2936 | 4.9393 | 0.93384 | 3.7262 | 0.036621 | -0.091553 | 0.013733 | 0.050354 | 0.13733 | 0.07782 | 0.11902 | 0.11444 | -0.13733 | -0.041199 | 5.2551 | 4.0421 | 1.2497 | 3.9276 | 1.1353 | 0.32959 | -121.4264 | -121.2845 | 0.45319 | 0.43488 | 0.39368 | 0.10529 | 0.064087 | 5.1407 | 121.4951 | 0.1236 | 0.036621 | 121.3989 | -0.10529 | 121.5134 | 0.2243 | -121.5363 | -121.3211 | 121.6095 | 0.36621 | 3.6072 | 0.35248
3532.5781 | 121.6736 | -0.35706 | 121.3348 | 0.0019074 | 6.9701 | 0.066458 | 0.13507 | 0.00027771 | 0.0011386 | 0.025827 | 0.00018312 | 0.022552 | -1.4523 | -0.00013037 | -0.0066906 | 0.016816 | 0.0010467 | 3.2089 | 121.2616 | -0.27924 | 121.1426 | 4.834 | 0.76904 | 3.6346 | -0.12817 | -0.073242 | -0.022888 | -0.041199 | -0.009155 | -0.07782 | 0.032043 | 0.07782 | -0.073242 | -0.19226 | 5.191 | 3.9917 | 1.1261 | 3.9139 | 1.0483 | 0.33417 | -121.4081 | -121.376 | 0.3479 | 0.3891 | 0.27924 | 0.054931 | -0.054932 | 5.1132 | 121.4218 | 0.013733 | -0.018311 | 121.5408 | -0.050354 | 121.6187 | 0.28381 | -121.6141 | -121.3577 | 121.4996 | 0.31586 | 3.566 | 0.22888
3534.375 | 121.669 | -0.37079 | 121.3531 | -0.013352 | 6.9699 | 0.06774 | 0.1387 | -0.0018585 | 0.004343 | 0.027109 | -0.0059205 | 0.021911 | -1.4514 | 0.003074 | -0.0045544 | 0.015107 | 0.00083309 | 3.2364 | 121.2753 | -0.25635 | 121.1517 | 4.9118 | 0.78735 | 3.6804 | -0.11902 | -0.059509 | -0.041199 | -0.036621 | -0.041199 | -0.09613 | 0.032043 | 0.11444 | -0.077819 | -0.20142 | 5.2826 | 4.0512 | 1.1581 | 3.9368 | 1.0437 | 0.32959 | -121.4127 | -121.3898 | 0.32959 | 0.40283 | 0.27466 | 0.073242 | -0.054931 | 5.1682 | 121.4081 | 0 | 0.004578 | 121.5317 | -0.01831 | 121.6461 | 0.31128 | -121.6095 | -121.3943 | 121.5225 | 0.33417 | 3.6072 | 0.25177
3536.1406 | 121.7834 | -0.32501 | 121.3165 | 0.0019074 | 6.9667 | 0.064108 | 0.13549 | 0.0032685 | 0.0022068 | 0.0254 | -0.0059205 | 0.018066 | -1.4551 | -0.0022666 | -0.0066906 | 0.01468 | -0.0017303 | 3.3005 | 121.1975 | -0.23804 | 121.2479 | 5.1544 | 0.94299 | 3.8406 | -0.009155 | -0.086975 | -0.018311 | 0.041199 | 0.1236 | 0.054932 | 0.1236 | 0.086975 | -0.11902 | -0.068664 | 5.4794 | 4.1656 | 1.268 | 4.0787 | 1.181 | 0.3067 | -121.4035 | -121.2753 | 0.44861 | 0.44861 | 0.37994 | 0.14191 | 0.073243 | 5.3925 | 121.4859 | 0.14191 | 0.05951 | 121.4355 | -0.068664 | 121.5225 | 0.23804 | -121.5546 | -121.3348 | 121.5729 | 0.36621 | 3.6255 | 0.31586
3537.8594 | 121.7972 | -0.31128 | 121.312 | -0.0057221 | 6.9703 | 0.066672 | 0.14105 | -0.0012177 | 0.0041294 | 0.029245 | -0.0059205 | 0.022552 | -1.454 | 0.0017922 | -0.0049818 | 0.016816 | -0.0025849 | 3.36 | 121.2204 | -0.26093 | 121.2433 | 5.2734 | 0.92468 | 3.8681 | 0.004578 | -0.086975 | 0.009155 | 0.059509 | 0.10986 | 0.041199 | 0.13275 | 0.050354 | -0.091553 | -0.068665 | 5.5847 | 4.1794 | 1.236 | 4.129 | 1.1856 | 0.32043 | -121.3989 | -121.2524 | 0.42114 | 0.44403 | 0.35248 | 0.1236 | 0.032044 | 5.5344 | 121.5042 | 0.10071 | 0.050354 | 121.4813 | -0.09613 | 121.5317 | 0.2243 | -121.5729 | -121.3028 | 121.5546 | 0.37079 | 3.6713 | 0.31586
3539.6406 | 121.7239 | -0.37079 | 121.3394 | -0.013352 | 6.9714 | 0.067526 | 0.14511 | 0.0026275 | 0.0032748 | 0.027109 | -0.0028687 | 0.022766 | -1.4533 | -0.0026938 | -0.0069044 | 0.013398 | -0.0010895 | 3.4012 | 121.2616 | -0.25635 | 121.1929 | 5.3741 | 0.9201 | 3.8818 | -0.059509 | -0.07782 | -0.009155 | -0.004578 | 0.041199 | -0.036621 | 0.050354 | 0.11444 | -0.07782 | -0.14648 | 5.7449 | 4.2526 | 1.2909 | 4.1382 | 1.1765 | 0.36163 | -121.4172 | -121.344 | 0.41199 | 0.42114 | 0.33417 | 0.059509 | -0.027466 | 5.6305 | 121.4493 | 0.050354 | 0.004577 | 121.5179 | -0.068665 | 121.6324 | 0.29297 | -121.5958 | -121.3486 | 121.5637 | 0.36621 | 3.772 | 0.31128
3541.4219 | 121.756 | -0.93842 | 120.726 | -0.0057221 | 6.9699 | 0.071799 | 0.29614 | -0.0014313 | 0.0084018 | 0.034586 | -0.0028687 | 0.019561 | -1.4533 | -0.0024802 | -0.0083996 | 0.011476 | 0.0021149 | 6.3995 | 120.5887 | -0.82855 | 120.6253 | 9.0454 | 1.3412 | 4.2938 | -0.091553 | -0.18768 | -0.10071 | -0.07782 | 0 | -0.10529 | -0.009155 | 0.10986 | -0.13733 | -0.10071 | 9.9838 | 5.2322 | 2.2797 | 5.1224 | 2.1698 | 0.83771 | -120.9137 | -120.8038 | 0.93842 | 0.92926 | 0.83313 | 0.091553 | -0.004578 | 9.874 | 121.4539 | 0.10071 | 0.022888 | 121.4172 | -0.086975 | 121.5271 | 0.75073 | -121.5546 | -120.8267 | 121.5637 | 0.8606 | 7.338 | 0.84686
3543.2031 | 121.8018 | -0.98419 | 120.6573 | -0.013352 | 6.969 | 0.074362 | 0.30981 | -0.00014949 | 0.011179 | 0.035013 | -0.0028687 | 0.019775 | -1.4519 | 0.00029703 | -0.003059 | 0.017457 | -0.00023491 | 6.6238 | 120.5795 | -0.90637 | 120.4971 | 9.3887 | 1.3504 | 4.3121 | -0.12817 | -0.21973 | -0.1236 | -0.068665 | -0.004578 | -0.12817 | -0.004578 | 0.07782 | -0.07782 | -0.16022 | 10.3729 | 5.2963 | 2.3346 | 5.2185 | 2.2568 | 0.8606 | -120.8771 | -120.726 | 0.97961 | 0.97961 | 0.85602 | 0.11902 | -0.004578 | 10.2951 | 121.4035 | 0.11902 | 0.054931 | 121.4859 | -0.096131 | 121.5637 | 0.76446 | -121.5637 | -120.7809 | 121.4813 | 0.91553 | 7.608 | 0.85602
3544.9219 | 121.7514 | -1.0574 | 120.5887 | -0.0057221 | 6.9699 | 0.073721 | 0.32797 | -0.0010041 | 0.0098972 | 0.035013 | -0.0028687 | 0.018921 | -1.4506 | 0.00991 | -0.0083996 | 0.015748 | 0.0016877 | 6.6422 | 120.4651 | -0.97046 | 120.4193 | 9.5215 | 1.3641 | 4.3488 | -0.1831 | -0.20599 | -0.12817 | -0.1236 | -0.045776 | -0.16022 | -0.032043 | 0.086975 | -0.1236 | -0.16937 | 10.5789 | 5.4062 | 2.4216 | 5.3192 | 2.3346 | 0.92926 | -120.7947 | -120.7123 | 1.0117 | 1.0254 | 0.89722 | 0.096131 | -0.032043 | 10.4919 | 121.3898 | 0.082398 | 0.004578 | 121.4355 | -0.07782 | 121.5225 | 0.85144 | -121.5591 | -120.7169 | 121.4767 | 0.93384 | 7.6996 | 0.87433
3546.7031 | 121.8063 | -1.0895 | 120.52 | -0.013352 | 6.9714 | 0.074149 | 0.33779 | 0.0034821 | 0.013742 | 0.03544 | -0.0059205 | 0.019775 | -1.4531 | 0.0035012 | -0.0043408 | 0.015962 | -0.0036529 | 6.7154 | 120.4468 | -1.0071 | 120.433 | 9.7229 | 1.4328 | 4.4083 | -0.10529 | -0.21973 | -0.14191 | -0.059509 | -0.009155 | -0.13275 | -0.009155 | 0.082398 | -0.073243 | -0.086976 | 10.8124 | 5.4977 | 2.5223 | 5.4153 | 2.4399 | 0.94757 | -120.7397 | -120.5795 | 1.0803 | 1.0803 | 0.95673 | 0.13275 | 0.009156 | 10.73 | 121.4401 | 0.13275 | 0.082398 | 121.4539 | -0.07782 | 121.5363 | 0.86975 | -121.5271 | -120.6619 | 121.5225 | 1.03 | 7.8049 | 0.98419
3548.4688 | 121.7697 | -1.1765 | 120.5246 | -0.013352 | 6.9703 | 0.073294 | 0.35211 | -0.0012177 | 0.0090426 | 0.038004 | -0.0028687 | 0.02127 | -1.4519 | -0.00077117 | -0.0049818 | 0.015535 | 0.0021149 | 6.6559 | 120.4422 | -1.0666 | 120.2774 | 9.7275 | 1.3641 | 4.3533 | -0.20142 | -0.21973 | -0.16022 | -0.11902 | -0.054932 | -0.19684 | -0.036621 | 0.10986 | -0.082397 | -0.24719 | 10.9039 | 5.5298 | 2.5406 | 5.4199 | 2.4307 | 1.0162 | -120.7443 | -120.6436 | 1.1215 | 1.1398 | 0.97961 | 0.1236 | -0.036621 | 10.7941 | 121.344 | 0.10528 | 0.041198 | 121.5088 | -0.05951 | 121.6187 | 0.95673 | -121.5912 | -120.6848 | 121.4539 | 1.0574 | 7.8323 | 0.97504
3550.1875 | 121.8109 | -0.94757 | 120.7123 | 0.0095369 | 6.9699 | 0.075644 | 0.30618 | 0.0036957 | 0.014383 | 0.03544 | -0.0028687 | 0.019134 | -1.4525 | 0.0026468 | -0.0034864 | 0.016816 | -0.00044851 | 7.3105 | 120.607 | -0.84686 | 120.607 | 10.5698 | 1.8082 | 4.7882 | -0.082397 | -0.21973 | -0.09613 | -0.022888 | 0.022888 | -0.091553 | 0.027466 | 0.10071 | -0.10529 | -0.10529 | 11.5173 | 5.7358 | 2.7557 | 5.6351 | 2.655 | 0.85144 | -120.932 | -120.7352 | 0.97046 | 0.97504 | 0.85602 | 0.1236 | 0.004577 | 11.4166 | 121.4539 | 0.11902 | 0.073242 | 121.4539 | -0.1236 | 121.5546 | 0.72784 | -121.5591 | -120.8084 | 121.5546 | 0.92468 | 8.2581 | 0.86517
3551.9688 | 121.7285 | -0.96588 | 120.7352 | -0.0057221 | 6.9707 | 0.075003 | 0.31707 | 0.0026275 | 0.014383 | 0.038431 | -0.0028687 | 0.024261 | -1.4527 | -0.00055757 | -0.009895 | 0.013612 | 0.0027557 | 7.3105 | 120.5978 | -0.90637 | 120.52 | 10.643 | 1.8448 | 4.7791 | -0.15106 | -0.16479 | -0.12817 | -0.10986 | -0.045776 | -0.15106 | -0.045776 | 0.059509 | -0.13733 | -0.21515 | 11.6089 | 5.7449 | 2.8107 | 5.6854 | 2.7512 | 0.83771 | -120.9 | -120.845 | 0.9201 | 0.9201 | 0.81482 | 0.082398 | -0.022888 | 11.5494 | 121.4264 | 0.082398 | 0.018311 | 121.5042 | -0.036621 | 121.5637 | 0.80109 | -121.6415 | -120.8633 | 121.4859 | 0.85602 | 8.2764 | 0.81482
3553.75 | 121.8018 | -0.99335 | 120.6573 | -0.020981 | 6.9697 | 0.076712 | 0.32305 | 0.0028411 | 0.014383 | 0.038217 | -0.0028687 | 0.018707 | -1.4512 | -0.00098477 | -0.0045544 | 0.015535 | 0.0027557 | 7.3746 | 120.5521 | -0.90179 | 120.5521 | 10.8627 | 1.9363 | 4.8843 | -0.068665 | -0.2243 | -0.11444 | -0.050354 | 0.022888 | -0.10986 | 0.009155 | 0.091553 | -0.10529 | -0.10529 | 11.8561 | 5.8777 | 2.9297 | 5.7861 | 2.8381 | 0.87891 | -120.8817 | -120.7077 | 1.0162 | 1.0025 | 0.88348 | 0.1236 | 0.004578 | 11.7645 | 121.4539 | 0.13733 | 0.064087 | 121.4539 | -0.10986 | 121.5454 | 0.76904 | -121.5591 | -120.7718 | 121.5454 | 0.94299 | 8.3679 | 0.92468
3555.5312 | 121.6873 | -1.2085 | 120.52 | -0.0057221 | 6.9718 | 0.075644 | 0.36535 | -0.0027131 | 0.015665 | 0.036508 | -0.0028687 | 0.022766 | -1.4527 | -0.0016256 | -0.0073316 | 0.011903 | 0.00083309 | 7.0908 | 120.3964 | -1.1215 | 120.2362 | 10.5377 | 1.7075 | 4.6188 | -0.27008 | -0.19684 | -0.16937 | -0.20142 | -0.16937 | -0.28381 | -0.11444 | 0.086975 | -0.1236 | -0.28381 | 11.7462 | 5.8273 | 2.916 | 5.7404 | 2.829 | 1.0391 | -120.7169 | -120.7214 | 1.0391 | 1.0941 | 0.92468 | 0.054932 | -0.11444 | 11.6592 | 121.3577 | 0 | -0.032043 | 121.5179 | -0.027465 | 121.6049 | 1.0117 | -121.6415 | -120.6894 | 121.4447 | 1.0071 | 8.2993 | 0.93841
3557.2344 | 121.7743 | -0.81482 | 120.8679 | -0.013352 | 6.9722 | 0.074576 | 0.26815 | 0.0011321 | 0.0098972 | 0.033304 | -0.0059205 | 0.021911 | -1.4525 | 0.0024332 | -0.0077588 | 0.015321 | 0.0029693 | 5.365 | 120.7809 | -0.75531 | 120.6573 | 8.4549 | 1.5015 | 4.5914 | -0.16022 | -0.14648 | -0.091553 | -0.068665 | -0.036621 | -0.12817 | 0.004578 | 0.059509 | -0.086975 | -0.21057 | 9.2697 | 5.4062 | 2.3163 | 5.3467 | 2.2568 | 0.72327 | -121.0144 | -120.9366 | 0.7782 | 0.8194 | 0.68664 | 0.096131 | -0.036621 | 9.2102 | 121.4127 | 0.054932 | 0.022888 | 121.5363 | -0.054931 | 121.5958 | 0.66833 | -121.6232 | -120.9595 | 121.4722 | 0.74615 | 6.1798 | 0.6546
3559.0312 | 121.7102 | -1.1078 | 120.6436 | -0.0057221 | 6.9705 | 0.076071 | 0.33523 | -0.0010041 | 0.016092 | 0.039499 | -0.0059205 | 0.021911 | -1.4491 | -0.0011984 | -0.0075452 | 0.016816 | -0.0034393 | 7.2052 | 120.5612 | -1.0025 | 120.3735 | 10.8765 | 1.9775 | 4.8889 | -0.21973 | -0.21057 | -0.14648 | -0.14648 | -0.11444 | -0.23346 | -0.082397 | 0.10529 | -0.082398 | -0.27008 | 11.9843 | 5.9967 | 3.0853 | 5.8914 | 2.98 | 0.9613 | -120.8542 | -120.7901 | 0.99335 | 1.0254 | 0.87433 | 0.064087 | -0.086975 | 11.879 | 121.376 | 0.032043 | 0 | 121.5637 | -0.064087 | 121.669 | 0.89722 | -121.6461 | -120.7901 | 121.4813 | 0.9613 | 8.313 | 0.88806
3560.8125 | 121.8201 | -1.1765 | 120.5109 | 0.0019074 | 6.969 | 0.075003 | 0.36428 | -0.0014313 | 0.019297 | 0.041422 | -0.0059205 | 0.019775 | -1.4542 | -0.0041892 | -0.0039136 | 0.01703 | 0.00040589 | 7.3975 | 120.4147 | -1.0757 | 120.3598 | 11.2656 | 2.1881 | 4.985 | -0.13275 | -0.25635 | -0.16479 | -0.07782 | -0.032043 | -0.15106 | -0.013733 | 0.10071 | -0.09613 | -0.15106 | 12.442 | 6.1615 | 3.3646 | 6.0608 | 3.2639 | 1.0117 | -120.7672 | -120.5887 | 1.1444 | 1.1627 | 1.0254 | 0.15106 | 0.013733 | 12.3413 | 121.4355 | 0.13275 | 0.086975 | 121.4905 | -0.091553 | 121.5912 | 0.9201 | -121.5866 | -120.6757 | 121.5363 | 1.0986 | 8.5739 | 1.0437
3562.5938 | 121.8338 | -1.7395 | 119.9295 | -0.0057221 | 6.9697 | 0.073935 | 0.49352 | -0.0035675 | 0.015879 | 0.041208 | -0.0059205 | 0.017639 | -1.4529 | 0.0015786 | -0.008186 | 0.01703 | -0.00087591 | 6.3675 | 119.7784 | -1.6571 | 119.7189 | 10.2585 | 1.6663 | 4.4037 | -0.21057 | -0.3067 | -0.23346 | -0.16479 | -0.068665 | -0.21973 | -0.10529 | 0.082398 | -0.15106 | -0.21057 | 11.998 | 6.1432 | 3.4058 | 6.0608 | 3.3234 | 1.506 | -120.2362 | -120.0943 | 1.6708 | 1.6342 | 1.5198 | 0.12817 | 0.013732 | 11.9156 | 121.376 | 0.16479 | 0.068664 | 121.4355 | -0.073243 | 121.5179 | 1.4328 | -121.5866 | -120.163 | 121.4584 | 1.5747 | 8.107 | 1.5289
3564.375 | 121.7651 | -1.8585 | 119.8013 | -0.0057221 | 6.9709 | 0.07244 | 0.50805 | 0.00070491 | 0.013956 | 0.037363 | -0.0028687 | 0.021484 | -1.4544 | 0.001365 | -0.0066906 | 0.015107 | 0.0014741 | 5.3467 | 119.6457 | -1.799 | 119.577 | 8.5556 | 0.70496 | 3.7216 | -0.27466 | -0.33875 | -0.24719 | -0.22888 | -0.14191 | -0.29297 | -0.15564 | 0.05951 | -0.15564 | -0.22431 | 10.4141 | 5.5801 | 2.5635 | 5.5206 | 2.504 | 1.6113 | -120.1401 | -120.0302 | 1.7166 | 1.7029 | 1.5656 | 0.091552 | -0.045777 | 10.3546 | 121.376 | 0.10528 | 0.01831 | 121.4447 | -0.091553 | 121.5042 | 1.5198 | -121.6003 | -120.0485 | 121.4355 | 1.6296 | 7.2052 | 1.5839
3566.1406 | 121.8155 | -1.8082 | 119.8288 | -0.0057221 | 6.9701 | 0.073294 | 0.49801 | -0.00036309 | 0.013315 | 0.039285 | -0.0059205 | 0.019989 | -1.4553 | 0.012687 | -0.0092542 | 0.01468 | 0.0014741 | 4.6646 | 119.7144 | -1.7212 | 119.6823 | 8.5144 | 1.1353 | 3.9963 | -0.19226 | -0.32044 | -0.23346 | -0.15564 | -0.073242 | -0.19684 | -0.091553 | 0.086976 | -0.11444 | -0.14648 | 10.3226 | 5.8044 | 2.9434 | 5.7175 | 2.8564 | 1.5747 | -120.1492 | -119.9844 | 1.7349 | 1.7166 | 1.6113 | 0.14191 | 0.036621 | 10.2356 | 121.4035 | 0.16022 | 0.077819 | 121.4355 | -0.086976 | 121.5225 | 1.4877 | -121.55 | -120.0623 | 121.4905 | 1.6525 | 6.4728 | 1.6159
3567.9219 | 121.7606 | -1.8448 | 119.8471 | -0.013352 | 6.972 | 0.073508 | 0.50997 | -0.00036309 | 0.016947 | 0.038644 | -0.0028687 | 0.02127 | -1.4519 | 0.0022196 | -0.0073316 | 0.013398 | -2.1314e-05 | 4.6234 | 119.696 | -1.7624 | 119.6457 | 8.6563 | 1.0803 | 4.0054 | -0.2243 | -0.30212 | -0.23804 | -0.21515 | -0.12817 | -0.27008 | -0.15106 | 0.082398 | -0.15106 | -0.20142 | 10.5011 | 5.8502 | 2.9251 | 5.7678 | 2.8427 | 1.6068 | -120.1492 | -120.0623 | 1.7166 | 1.6937 | 1.5747 | 0.086975 | -0.032044 | 10.4187 | 121.4081 | 0.10986 | 0.022888 | 121.4584 | -0.064087 | 121.5408 | 1.5427 | -121.6095 | -120.0851 | 121.4905 | 1.6296 | 6.4682 | 1.6205
3569.6562 | 121.7651 | -2.2614 | 119.4168 | -0.0057221 | 6.9697 | 0.074149 | 0.61401 | -0.00014949 | 0.021219 | 0.036722 | -0.0028687 | 0.021057 | -1.4542 | 0.0041422 | -0.0056226 | 0.015962 | 0.0010467 | 5.3604 | 119.2337 | -2.1652 | 119.1605 | 9.5947 | 1.3824 | 4.0558 | -0.31586 | -0.35706 | -0.27008 | -0.25635 | -0.19226 | -0.3479 | -0.21515 | 0.096131 | -0.1831 | -0.25635 | 11.8561 | 6.3171 | 3.6438 | 6.221 | 3.5477 | 1.9913 | -119.7739 | -119.6732 | 2.0691 | 2.0462 | 1.9135 | 0.054932 | -0.077819 | 11.7599 | 121.3257 | 0.07782 | 0.013733 | 121.3989 | -0.086975 | 121.4951 | 1.9043 | -121.582 | -119.6869 | 121.4218 | 2.005 | 7.6218 | 1.9455
3571.4375 | 121.7697 | -2.0325 | 119.6182 | 0.0095369 | 6.9718 | 0.074362 | 0.56231 | -0.0046357 | 0.018656 | 0.040567 | -0.0028687 | 0.020416 | -1.4551 | 0.0045694 | -0.0069044 | 0.015321 | 0.0023285 | 4.9713 | 119.4717 | -1.9455 | 119.4168 | 9.2926 | 1.4099 | 4.1336 | -0.23804 | -0.37079 | -0.25635 | -0.24261 | -0.14648 | -0.31128 | -0.16479 | 0.086975 | -0.14648 | -0.20142 | 11.3251 | 6.1661 | 3.4424 | 6.0791 | 3.3554 | 1.7761 | -119.989 | -119.8608 | 1.886 | 1.8677 | 1.7212 | 0.091553 | -0.054931 | 11.2381 | 121.3623 | 0.10986 | 0.013733 | 121.4172 | -0.11444 | 121.5042 | 1.6617 | -121.5637 | -119.8746 | 121.4493 | 1.7899 | 7.0038 | 1.7944
3573.2188 | 121.7148 | -2.0462 | 119.6915 | 0.0019074 | 6.9748 | 0.076498 | 0.55783 | 0.0013459 | 0.018228 | 0.045694 | 0.00018312 | 0.019775 | -1.4531 | -0.0067526 | -0.006477 | 0.014253 | -0.00087591 | 4.9942 | 119.545 | -1.9455 | 119.4214 | 9.4482 | 1.506 | 4.1885 | -0.27924 | -0.3067 | -0.25635 | -0.24719 | -0.1831 | -0.34332 | -0.1831 | 0.10071 | -0.14648 | -0.27008 | 11.4944 | 6.2347 | 3.5522 | 6.134 | 3.4515 | 1.7899 | -119.9982 | -119.9387 | 1.8631 | 1.8631 | 1.7029 | 0.073243 | -0.086975 | 11.3937 | 121.3669 | 0.073243 | 0.009156 | 121.4905 | -0.050354 | 121.5912 | 1.7395 | -121.637 | -119.9478 | 121.4676 | 1.799 | 7.0404 | 1.767
3574.9531 | 121.8201 | -2.2614 | 119.4214 | -0.013352 | 6.9742 | 0.075858 | 0.61529 | -0.0061311 | 0.019297 | 0.039926 | 0.00018312 | 0.019348 | -1.4519 | 0.004783 | -0.010322 | 0.013398 | 0.0027557 | 5.571 | 119.2474 | -2.1469 | 119.2429 | 10.2814 | 1.8265 | 4.3259 | -0.22888 | -0.35248 | -0.28381 | -0.19684 | -0.10529 | -0.27924 | -0.16022 | 0.11444 | -0.17395 | -0.17853 | 12.5427 | 6.5872 | 4.0878 | 6.4728 | 3.9734 | 1.9775 | -119.7739 | -119.6182 | 2.1561 | 2.1011 | 1.9821 | 0.1236 | 0.004577 | 12.4283 | 121.3898 | 0.17853 | 0.086975 | 121.3943 | -0.068665 | 121.5088 | 1.9089 | -121.5683 | -119.7052 | 121.5042 | 2.0645 | 7.8323 | 2.0325
3576.7344 | 121.7468 | -2.655 | 119.046 | -0.0057221 | 6.9746 | 0.07543 | 0.72018 | -0.00036309 | 0.030405 | 0.04484 | -0.0059205 | 0.02127 | -1.4555 | -0.0084616 | -0.0077588 | 0.011689 | 0.0027557 | 6.4224 | 118.8995 | -2.5406 | 118.7256 | 11.3709 | 2.4948 | 4.3625 | -0.36621 | -0.37994 | -0.33875 | -0.31586 | -0.23346 | -0.42114 | -0.2655 | 0.11444 | -0.14648 | -0.32043 | 14.0259 | 7.0175 | 5.1498 | 6.9031 | 5.0354 | 2.3163 | -119.426 | -119.3619 | 2.4216 | 2.3895 | 2.2339 | 0.073242 | -0.082398 | 13.9114 | 121.2662 | 0.10529 | 0.022888 | 121.4401 | -0.041199 | 121.5546 | 2.2751 | -121.5866 | -119.3848 | 121.3806 | 2.3392 | 9.0775 | 2.2888
3578.5 | 121.6873 | -2.6688 | 119.0186 | -0.020981 | 7.0998 | 0.17049 | 1.1301 | 0.0026275 | 0.44868 | 0.071756 | 0.00018312 | 0.020843 | -1.4533 | 0.011833 | -0.0079724 | 0.013185 | 0.0014741 | 32.579 | 118.808 | -2.5085 | 118.7759 | 114.7476 | 64.5218 | 8.0887 | -0.34332 | -0.36621 | -0.33875 | -0.29297 | -0.21057 | -0.3891 | -0.23346 | 0.16022 | -0.21057 | -0.24262 | 117.4164 | 10.7574 | 67.1906 | 10.5972 | 67.0303 | 2.33 | -119.3848 | -119.3115 | 2.4582 | 2.4353 | 2.2797 | 0.10529 | -0.050354 | 117.2562 | 121.2845 | 0.12817 | 0.045776 | 121.3165 | -0.027466 | 121.4767 | 2.3026 | -121.5271 | -119.3573 | 121.4447 | 2.3758 | 35.2478 | 2.3254
3580.2344 | 121.6827 | -2.7969 | 118.7988 | 0.0019074 | 7.1004 | 0.1675 | 1.2158 | -0.0012177 | 0.49867 | 0.074319 | 0.00018312 | 0.01828 | -1.4527 | 0.00051063 | -0.0058362 | 0.01468 | -0.0013031 | 35.527 | 118.6249 | -2.6321 | 118.5791 | 114.8117 | 71.6171 | 8.226 | -0.36621 | -0.39368 | -0.32044 | -0.30212 | -0.21973 | -0.37079 | -0.23804 | 0.1648 | -0.17395 | -0.21973 | 117.6086 | 11.0229 | 74.4141 | 10.8582 | 74.2493 | 2.4765 | -119.1925 | -119.101 | 2.5772 | 2.5589 | 2.4261 | 0.082398 | -0.050354 | 117.4438 | 121.2112 | 0.10071 | 0.018311 | 121.257 | -0.073242 | 121.4218 | 2.4033 | -121.431 | -119.1193 | 121.376 | 2.4948 | 38.324 | 2.4307
3582.0469 | 121.6232 | -2.9114 | 118.7439 | -0.013352 | 7.1002 | 0.16665 | 1.2559 | -0.0035675 | 0.51341 | 0.076242 | -0.0059205 | 0.021484 | -1.4504 | -0.002053 | -0.0092542 | 0.015107 | 0.0051057 | 36.5387 | 118.5287 | -2.7603 | 118.428 | 114.6469 | 74.025 | 8.3267 | -0.46692 | -0.36163 | -0.37537 | -0.37537 | -0.28839 | -0.43945 | -0.3067 | 0.15106 | -0.21515 | -0.31586 | 117.5583 | 11.2381 | 76.9363 | 11.087 | 76.7853 | 2.536 | -119.1055 | -119.1193 | 2.623 | 2.6047 | 2.4719 | 0.068664 | -0.064087 | 117.4072 | 121.1884 | 0.086975 | 0 | 121.2891 | 0.013733 | 121.4401 | 2.5497 | -121.5042 | -119.1193 | 121.3394 | 2.536 | 39.4501 | 2.4445
3583.8281 | 121.6736 | -2.9572 | 118.6111 | -0.013352 | 7.0978 | 0.16772 | 1.2938 | -0.0020721 | 0.53028 | 0.076028 | -0.0028687 | 0.02127 | -1.4533 | 8.3226e-05 | -0.0094678 | 0.013826 | 0.0010467 | 37.7014 | 118.3777 | -2.8107 | 118.4326 | 114.7476 | 76.7532 | 8.638 | -0.31128 | -0.41199 | -0.3479 | -0.28381 | -0.20142 | -0.33875 | -0.23804 | 0.14648 | -0.23346 | -0.17853 | 117.7048 | 11.5952 | 79.7104 | 11.4487 | 79.5639 | 2.6093 | -119.0231 | -118.895 | 2.7557 | 2.7191 | 2.6184 | 0.10986 | 0.009155 | 117.5583 | 121.2433 | 0.14648 | 0.064087 | 121.1884 | -0.064087 | 121.3348 | 2.5452 | -121.4218 | -118.959 | 121.3898 | 2.6733 | 40.6586 | 2.6459
3585.5469 | 121.6644 | -3.0396 | 118.5196 | -0.013352 | 7.0987 | 0.17071 | 1.3237 | -0.00036309 | 0.53904 | 0.076028 | -0.0028687 | 0.018707 | -1.4559 | -0.003121 | -0.008186 | 0.013398 | -0.00044851 | 38.3057 | 118.2953 | -2.8885 | 118.3456 | 114.5828 | 78.1631 | 8.8348 | -0.32044 | -0.40741 | -0.32501 | -0.28839 | -0.21057 | -0.3479 | -0.26093 | 0.15106 | -0.2243 | -0.17395 | 117.6224 | 11.8744 | 81.2027 | 11.7233 | 81.0516 | 2.7145 | -118.927 | -118.808 | 2.829 | 2.7786 | 2.6917 | 0.064087 | -0.022888 | 117.4713 | 121.2341 | 0.11444 | 0.036621 | 121.1838 | -0.082398 | 121.3348 | 2.6321 | -121.4081 | -118.8446 | 121.3852 | 2.7512 | 41.3452 | 2.7191
3587.3125 | 121.7056 | -3.0808 | 118.428 | -0.0057221 | 7.1021 | 0.17306 | 1.3457 | 0.0024139 | 0.54118 | 0.08201 | -0.0059205 | 0.016998 | -1.4536 | 0.001365 | -0.0026318 | 0.015535 | -0.0034393 | 38.475 | 118.2312 | -2.9297 | 118.2678 | 114.7293 | 78.4103 | 9.1644 | -0.29297 | -0.40283 | -0.32501 | -0.23804 | -0.19684 | -0.3479 | -0.2243 | 0.15106 | -0.19684 | -0.16022 | 117.8101 | 12.2452 | 81.4911 | 12.0941 | 81.34 | 2.7557 | -118.8309 | -118.6661 | 2.8839 | 2.8564 | 2.7329 | 0.10071 | -0.022888 | 117.659 | 121.1975 | 0.12817 | 0.086975 | 121.1609 | -0.07782 | 121.312 | 2.6779 | -121.3577 | -118.7531 | 121.3486 | 2.8427 | 41.5558 | 2.7878
3589.0781 | 121.6461 | -3.1586 | 118.3777 | -0.013352 | 7.1034 | 0.17177 | 1.3657 | -0.00079049 | 0.54417 | 0.084787 | -0.0028687 | 0.020202 | -1.4536 | -0.00077117 | -0.0060498 | 0.014894 | 0.0027557 | 38.6902 | 118.1442 | -3.0212 | 118.1992 | 114.6652 | 78.9688 | 9.5352 | -0.34332 | -0.42114 | -0.3479 | -0.31586 | -0.23804 | -0.37537 | -0.2655 | 0.13733 | -0.23346 | -0.17853 | 117.8238 | 12.6938 | 82.1274 | 12.5565 | 81.9901 | 2.8107 | -118.7988 | -118.6935 | 2.9205 | 2.8931 | 2.7832 | 0.082397 | -0.027466 | 117.6865 | 121.2204 | 0.10986 | 0.032043 | 121.1655 | -0.073243 | 121.3028 | 2.7374 | -121.3989 | -118.7256 | 121.3577 | 2.8427 | 41.8488 | 2.8152
3590.875 | 121.6187 | -3.186 | 118.3868 | -0.020981 | 7.1051 | 0.16964 | 1.3551 | -0.00014949 | 0.52986 | 0.087351 | -0.0028687 | 0.021057 | -1.4523 | 0.0037148 | -0.0056226 | 0.013826 | -0.00044851 | 37.9944 | 118.1854 | -3.035 | 118.1305 | 114.6332 | 77.1881 | 9.668 | -0.3891 | -0.36621 | -0.36163 | -0.31586 | -0.27008 | -0.41199 | -0.28381 | 0.15106 | -0.20142 | -0.25635 | 117.8192 | 12.854 | 80.3741 | 12.7029 | 80.2231 | 2.8244 | -118.7531 | -118.7027 | 2.916 | 2.9022 | 2.774 | 0.07782 | -0.050354 | 117.6682 | 121.1655 | 0.091552 | 0.045776 | 121.2204 | -0.004578 | 121.3715 | 2.8198 | -121.4218 | -118.7485 | 121.3165 | 2.8702 | 41.1804 | 2.7969
3592.5938 | 121.6599 | -3.9139 | 117.572 | -0.013352 | 7.0923 | 0.17113 | 1.6347 | -0.0033539 | 0.49461 | 0.21211 | 0.00018312 | 0.020416 | -1.4536 | 0.0017922 | -0.0077588 | 0.014894 | -0.0015167 | 35.1059 | 117.3523 | -3.7949 | 117.3248 | 114.0289 | 71.2555 | 20.8054 | -0.44403 | -0.46234 | -0.43488 | -0.36621 | -0.28839 | -0.45319 | -0.32044 | 0.11902 | -0.21973 | -0.24719 | 117.9428 | 24.7192 | 75.1694 | 24.6002 | 75.0504 | 3.479 | -118.0344 | -117.9382 | 3.6255 | 3.5934 | 3.4607 | 0.11444 | -0.018311 | 117.8238 | 121.1197 | 0.14648 | 0.068664 | 121.1472 | -0.027466 | 121.2662 | 3.4515 | -121.3669 | -118.0069 | 121.2387 | 3.5477 | 39.0198 | 3.4698
3594.375 | 121.6324 | -3.5751 | 118.0435 | -0.0057221 | 7.0735 | 0.17711 | 0.96627 | -0.00036309 | -0.002493 | 0.091196 | -0.0028687 | 0.020843 | -1.4548 | -0.0033346 | -0.0079724 | 0.012971 | -0.0030121 | 51.2054 | 117.8329 | -3.4607 | 117.8009 | 114.505 | 108.2016 | 102.8229 | -0.42572 | -0.39368 | -0.40283 | -0.36621 | -0.30212 | -0.45776 | -0.3067 | 0.11444 | -0.21057 | -0.24262 | 118.0801 | 106.398 | 111.7767 | 106.2836 | 111.6623 | 3.1723 | -118.4372 | -118.4097 | 3.273 | 3.2684 | 3.1174 | 0.09613 | -0.054932 | 117.9657 | 121.2616 | 0.10071 | 0.036621 | 121.2936 | 0.009155 | 121.4081 | 3.1815 | -121.5042 | -118.4464 | 121.376 | 3.2089 | 54.7806 | 3.1494
3596.1094 | 121.6553 | -7.7133 | 113.7268 | -0.013352 | 7.0795 | 0.17669 | 1.9425 | 0.0026275 | -0.001852 | 0.082864 | -0.0059205 | 0.018921 | -1.4536 | -0.005471 | -0.0034864 | 0.016816 | 0.0010467 | 42.6956 | 113.4201 | -7.6401 | 113.4796 | 110.321 | 94.368 | 90.2115 | -0.74616 | -0.85602 | -0.82855 | -0.67291 | -0.64545 | -0.89264 | -0.71869 | 0.073242 | -0.3067 | -0.24719 | 118.0344 | 97.9248 | 102.0813 | 97.8516 | 102.0081 | 6.8848 | -114.5828 | -114.3997 | 7.0679 | 6.9946 | 6.8207 | 0.10986 | -0.064087 | 117.9611 | 121.1197 | 0.1831 | 0.15564 | 121.0602 | -0.027466 | 121.1334 | 6.8573 | -121.3669 | -114.5554 | 121.1929 | 7.0404 | 50.4089 | 6.9672
3597.8906 | 121.6003 | -3.8727 | 117.7048 | -0.02861 | 7.0756 | 0.17669 | 1.0171 | 0.0049773 | -0.004202 | 0.088846 | -0.0028687 | 0.021484 | -1.4521 | 0.00072423 | -0.0090406 | 0.014253 | -0.00087591 | 51.1322 | 117.5308 | -3.7674 | 117.4576 | 114.3173 | 108.0185 | 103.0106 | -0.49896 | -0.42114 | -0.43488 | -0.40741 | -0.34332 | -0.49896 | -0.36621 | 0.10529 | -0.17395 | -0.24719 | 118.19 | 106.8832 | 111.8912 | 106.778 | 111.7859 | 3.4378 | -118.1259 | -118.1122 | 3.5294 | 3.5065 | 3.3737 | 0.068664 | -0.064087 | 118.0847 | 121.225 | 0.091552 | 0.027465 | 121.2982 | 0.013732 | 121.4035 | 3.4515 | -121.4722 | -118.1396 | 121.3303 | 3.4653 | 55.0049 | 3.3737
3599.6719 | 121.6141 | -4.1885 | 117.3615 | -0.020981 | 7.0756 | 0.17818 | 1.0797 | 0.00027771 | -0.0050564 | 0.089914 | 0.00018312 | 0.019561 | -1.4519 | 0.0028604 | -0.005409 | 0.013185 | -0.00044851 | 50.116 | 117.2195 | -4.0878 | 117.1738 | 114.0015 | 106.4392 | 101.0971 | -0.45319 | -0.46234 | -0.45319 | -0.37994 | -0.34332 | -0.49439 | -0.36163 | 0.10071 | -0.14191 | -0.18768 | 118.19 | 105.2856 | 110.6277 | 105.1849 | 110.527 | 3.7354 | -117.8238 | -117.7414 | 3.8452 | 3.8269 | 3.6942 | 0.091553 | -0.041199 | 118.0893 | 121.2616 | 0.10986 | 0.073242 | 121.3074 | -0.009155 | 121.4081 | 3.7262 | -121.4493 | -117.8146 | 121.3623 | 3.8086 | 54.3045 | 3.7354
3601.4375 | 121.7102 | -4.3121 | 117.2379 | -0.013352 | 7.0763 | 0.17605 | 1.1154 | 0.0030547 | -0.0027066 | 0.088632 | -0.0059205 | 0.019989 | -1.4542 | 0.00051063 | -0.0079724 | 0.014253 | 0.0040375 | 49.8505 | 117.0364 | -4.1794 | 117.0731 | 113.9465 | 105.9769 | 100.8774 | -0.39825 | -0.50812 | -0.45319 | -0.31586 | -0.28381 | -0.41657 | -0.32959 | 0.13275 | -0.20142 | -0.16479 | 118.2587 | 105.1895 | 110.289 | 105.0568 | 110.1562 | 3.8589 | -117.746 | -117.5537 | 4.0283 | 3.9825 | 3.8956 | 0.1236 | 0.036621 | 118.1259 | 121.2524 | 0.16937 | 0.13733 | 121.2158 | -0.054932 | 121.3486 | 3.804 | -121.4172 | -117.691 | 121.3852 | 3.9963 | 54.1626 | 3.9139
3603.1562 | 121.6827 | -4.3808 | 117.1143 | -0.0057221 | 7.0784 | 0.17882 | 1.1378 | 0.0015595 | -0.0022794 | 0.089487 | -0.0059205 | 0.017425 | -1.4529 | -0.00483 | -0.004768 | 0.016175 | 0.00083309 | 49.5621 | 116.9403 | -4.2755 | 117.0044 | 113.8779 | 105.455 | 100.5386 | -0.39825 | -0.50812 | -0.43945 | -0.35248 | -0.31586 | -0.45776 | -0.3479 | 0.10529 | -0.17395 | -0.10986 | 118.2587 | 104.9194 | 109.8358 | 104.8141 | 109.7305 | 3.9413 | -117.6224 | -117.4667 | 4.0649 | 4.0329 | 3.923 | 0.091553 | -0.018311 | 118.1534 | 121.2799 | 0.1236 | 0.086975 | 121.2158 | -0.068665 | 121.3211 | 3.8727 | -121.3898 | -117.5537 | 121.3852 | 4.0283 | 53.9429 | 3.9825
3604.9375 | 121.6919 | -4.5181 | 116.9724 | 0.0019074 | 7.0773 | 0.17946 | 1.1726 | 0.0034821 | -0.0044156 | 0.090341 | -0.0089723 | 0.01828 | -1.454 | 0.0026468 | -0.008827 | 0.014894 | 0.0042511 | 49.3561 | 116.7389 | -4.4312 | 116.8121 | 113.768 | 105.0476 | 100.4791 | -0.43488 | -0.50812 | -0.45319 | -0.35248 | -0.29297 | -0.45776 | -0.35248 | 0.086975 | -0.23346 | -0.16022 | 118.2861 | 104.9973 | 109.5657 | 104.9103 | 109.4788 | 4.0649 | -117.4805 | -117.3248 | 4.2252 | 4.1656 | 4.0604 | 0.10071 | -0.004578 | 118.1992 | 121.2433 | 0.16022 | 0.10071 | 121.17 | -0.054932 | 121.257 | 4.01 | -121.4035 | -117.4255 | 121.3303 | 4.1656 | 53.8742 | 4.0833
3606.6562 | 121.6095 | -6.3858 | 115.0635 | -0.013352 | 7.0788 | 0.17733 | 1.6108 | -0.0039947 | -0.0033474 | 0.085428 | -0.0059205 | 0.019775 | -1.4516 | -0.001412 | -0.0058362 | 0.017244 | 0.00083309 | 30.0751 | 114.8209 | -6.2942 | 114.8438 | 111.7493 | 52.5879 | 94.1116 | -0.65002 | -0.6958 | -0.68207 | -0.55847 | -0.54474 | -0.75073 | -0.59967 | 0.091553 | -0.24262 | -0.21973 | 118.1351 | 100.4974 | 58.9737 | 100.4059 | 58.8821 | 5.7037 | -115.7593 | -115.6219 | 5.8411 | 5.7861 | 5.6351 | 0.082398 | -0.068664 | 118.0435 | 121.138 | 0.13733 | 0.1236 | 121.1151 | -0.013733 | 121.2067 | 5.69 | -121.3577 | -115.7455 | 121.2296 | 5.8273 | 36.4609 | 5.7358
3608.4219 | 121.6095 | -8.2214 | 113.1454 | -0.0057221 | 7.0807 | 0.17605 | 2.072 | 0.0017731 | -0.0020658 | 0.080087 | -0.0089723 | 0.018921 | -1.4538 | -0.00055757 | -0.0037 | 0.01468 | 0.0036103 | 26.5366 | 112.8937 | -8.1299 | 112.9303 | 109.8587 | 46.8796 | 89.6988 | -0.7782 | -0.85602 | -0.86975 | -0.70038 | -0.70038 | -0.94757 | -0.76904 | 0.091553 | -0.25177 | -0.21515 | 118.0801 | 97.9202 | 55.101 | 97.8287 | 55.0095 | 7.3517 | -114.0015 | -113.8458 | 7.5211 | 7.4524 | 7.2739 | 0.10071 | -0.07782 | 117.9886 | 121.0602 | 0.16937 | 0.16937 | 121.0236 | 0.013733 | 121.1151 | 7.3654 | -121.2753 | -114.0152 | 121.1517 | 7.5211 | 34.758 | 7.4432
3610.1562 | 121.5179 | -8.3496 | 113.0219 | -0.013352 | 7.0816 | 0.1737 | 2.1021 | -0.0022857 | -0.0031338 | 0.083292 | -0.0089723 | 0.01828 | -1.4514 | 0.00029703 | -0.006477 | 0.015321 | 0.0016877 | 22.7737 | 112.7563 | -8.2764 | 112.7106 | 109.7809 | 35.9161 | 91.0629 | -0.85144 | -0.8194 | -0.87891 | -0.75073 | -0.71869 | -0.94757 | -0.78278 | 0.073242 | -0.2655 | -0.31128 | 118.1305 | 99.4125 | 44.2657 | 99.3393 | 44.1925 | 7.4707 | -113.8412 | -113.7726 | 7.6309 | 7.5668 | 7.402 | 0.09613 | -0.068665 | 118.0573 | 120.9869 | 0.16022 | 0.12817 | 121.0327 | 0.059509 | 121.106 | 7.5302 | -121.2982 | -113.9008 | 121.0602 | 7.5989 | 31.1234 | 7.4982
3611.9375 | 121.4355 | -10.8261 | 110.5499 | -0.0057221 | 7.082 | 0.17583 | 2.7334 | 0.0028411 | -0.004202 | 0.083933 | -0.0059205 | 0.020202 | -1.4521 | 0.00051063 | -0.0073316 | 0.014253 | -0.0015167 | 22.9156 | 110.2295 | -10.7391 | 110.1608 | 107.0938 | 40.1505 | 86.6821 | -1.1215 | -1.0208 | -1.1398 | -1.0025 | -1.0254 | -1.3367 | -1.1032 | 0.086975 | -0.32044 | -0.3891 | 117.9199 | 97.5082 | 50.9766 | 97.4213 | 50.8896 | 9.6863 | -111.5707 | -111.5524 | 9.8007 | 9.7229 | 9.4894 | 0.036622 | -0.19684 | 117.8329 | 120.9 | 0.11444 | 0.13733 | 120.9686 | 0.11902 | 121.0556 | 9.8053 | -121.2891 | -111.6898 | 120.9869 | 9.8236 | 33.7418 | 9.7046
3613.7188 | 121.4905 | -9.169 | 112.1613 | -0.020981 | 7.0758 | 0.18352 | 2.3734 | -0.0033539 | -0.0050564 | 0.086923 | -0.0059205 | 0.019561 | -1.4536 | 0.009269 | -0.0075452 | 0.014253 | 0.0027557 | 37.8616 | 111.9003 | -9.0317 | 111.8408 | 108.8745 | 68.7881 | 93.8965 | -0.94757 | -0.91553 | -0.95673 | -0.81482 | -0.79651 | -1.062 | -0.86517 | 0.13733 | -0.26093 | -0.32044 | 118.0435 | 103.0655 | 77.9572 | 102.9282 | 77.8198 | 8.2123 | -113.0768 | -112.9761 | 8.3725 | 8.3038 | 8.107 | 0.091553 | -0.10529 | 117.9062 | 120.8725 | 0.16022 | 0.14191 | 120.932 | 0.041199 | 121.0693 | 8.2535 | -121.1929 | -113.118 | 121.0098 | 8.3542 | 47.0306 | 8.2214
3615.4531 | 121.4218 | -9.9976 | 111.3419 | -0.013352 | 7.0775 | 0.17968 | 2.6932 | -0.00036309 | -0.0014248 | 0.086923 | -0.0059205 | 0.018493 | -1.4508 | 0.0041422 | -0.0077588 | 0.015107 | 0.0025421 | 30.9631 | 110.7285 | -10.0845 | 110.8383 | 107.8812 | 52.7115 | 92.8894 | -0.9613 | -0.99792 | -1.0345 | -0.85144 | -0.85144 | -1.149 | -0.94299 | -0.086975 | -0.6134 | -0.50354 | 117.8787 | 102.887 | 62.709 | 102.9739 | 62.796 | 8.963 | -112.3398 | -112.1933 | 9.1461 | 9.0546 | 8.8486 | 0.091553 | -0.11444 | 117.9657 | 120.9229 | 0.18311 | 0.18311 | 120.813 | 0.036621 | 120.726 | 8.9996 | -121.4264 | -112.3764 | 120.8359 | 9.1461 | 40.9607 | 9.0363
3617.2344 | 121.3348 | -11.4532 | 109.8404 | -0.020981 | 7.0803 | 0.18523 | 3.0555 | 0.0034821 | -0.003561 | 0.083292 | -0.0059205 | 0.022552 | -1.4531 | -0.0044028 | -0.0049818 | 0.012758 | -0.0019439 | 35.5042 | 109.5474 | -11.293 | 109.3552 | 106.7139 | 64.0915 | 90.6143 | -1.2177 | -1.1581 | -1.2909 | -1.1261 | -1.1261 | -1.5427 | -1.2131 | 0.16022 | -0.29297 | -0.48523 | 118.1671 | 102.0676 | 75.5447 | 101.9073 | 75.3845 | 10.1624 | -110.9985 | -110.9665 | 10.3271 | 10.2402 | 9.9106 | 0.07782 | -0.25177 | 118.0069 | 120.6482 | 0.1648 | 0.1648 | 120.8405 | 0.13275 | 121.0007 | 10.2951 | -121.1334 | -111.1313 | 120.8084 | 10.3271 | 46.9574 | 10.2356
3619.0156 | 121.4401 | -12.9227 | 108.2153 | -0.013352 | 7.081 | 0.18075 | 3.4966 | 0.0015595 | -0.0014248 | 0.082864 | 0.00018312 | 0.021484 | -1.4544 | 0.001365 | -0.0028454 | 0.016389 | -0.0010895 | 28.6697 | 107.9132 | -12.8494 | 107.8629 | 104.9194 | 51.9699 | 87.8357 | -1.3412 | -1.3641 | -1.4923 | -1.2222 | -1.2085 | -1.7258 | -1.355 | 0.073242 | -0.30212 | -0.35248 | 117.8421 | 100.7584 | 64.8926 | 100.6851 | 64.8193 | 11.4304 | -109.5795 | -109.4376 | 11.7142 | 11.5677 | 11.1969 | 0.13733 | -0.23346 | 117.7689 | 120.7123 | 0.28381 | 0.27008 | 120.7626 | 0.12817 | 120.8359 | 11.5585 | -121.0648 | -109.7076 | 120.7855 | 11.7004 | 41.5924 | 11.5814
3620.7344 | 121.3211 | -13.8519 | 107.3135 | -0.0057221 | 7.0758 | 0.1878 | 3.8011 | 0.0049773 | -0.0033474 | 0.093759 | -0.0028687 | 0.020416 | -1.4527 | 0.004783 | -0.0045544 | 0.014039 | 0.0023285 | 36.7813 | 107.0068 | -13.6963 | 106.7413 | 103.9719 | 67.7261 | 92.4774 | -1.4786 | -1.4328 | -1.5976 | -1.355 | -1.3596 | -1.8951 | -1.506 | 0.15564 | -0.3067 | -0.5722 | 117.8238 | 106.3293 | 81.5781 | 106.1737 | 81.4224 | 12.2543 | -108.7463 | -108.6685 | 12.4924 | 12.3459 | 11.9568 | 0.091553 | -0.29755 | 117.6682 | 120.4376 | 0.23804 | 0.24262 | 120.7031 | 0.1648 | 120.8588 | 12.4191 | -121.0098 | -108.9111 | 120.5933 | 12.4969 | 50.6332 | 12.3734
3622.5156 | 121.3211 | -16.246 | 104.7775 | -0.020981 | 7.0748 | 0.18331 | 4.5699 | -0.00014949 | -0.00527 | 0.087137 | -0.0028687 | 0.018921 | -1.4555 | 0.00072423 | -0.0090406 | 0.012758 | 0.0019013 | 32.5974 | 104.2786 | -16.2003 | 104.2191 | 101.4496 | 60.9512 | 88.1516 | -1.6205 | -1.6754 | -1.8585 | -1.5244 | -1.4786 | -2.1286 | -1.7303 | 0.045777 | -0.49896 | -0.55847 | 117.6956 | 104.3976 | 77.1973 | 104.3518 | 77.1515 | 14.3875 | -106.4529 | -106.3019 | 14.7675 | 14.5157 | 14.1174 | 0.12817 | -0.27008 | 117.6498 | 120.4193 | 0.37994 | 0.33417 | 120.4788 | 0.18311 | 120.5246 | 14.5706 | -120.9778 | -106.636 | 120.4651 | 14.7217 | 48.8434 | 14.6256
3624.3125 | 121.2479 | -11.499 | 109.7351 | 0.0019074 | 7.0801 | 0.18523 | 3.1871 | -0.0012177 | -0.0046292 | 0.088846 | 0.00018312 | 0.020843 | -1.4538 | 0.0015786 | -0.012031 | 0.011903 | 0.0021149 | 36.2549 | 109.4055 | -11.3663 | 109.2682 | 106.4713 | 63.8306 | 92.0883 | -1.2543 | -1.1078 | -1.2772 | -1.1353 | -1.1078 | -1.5335 | -1.2314 | 0.13275 | -0.32959 | -0.46692 | 117.9703 | 103.5873 | 75.3296 | 103.4546 | 75.1968 | 10.2219 | -110.8429 | -110.8704 | 10.3912 | 10.2676 | 9.9655 | 0.045777 | -0.25635 | 117.8375 | 120.6345 | 0.16937 | 0.14191 | 120.7718 | 0.16937 | 120.9045 | 10.3912 | -121.1014 | -111.0123 | 120.7672 | 10.3638 | 47.7539 | 10.2448
3626.0312 | 121.3989 | -9.3704 | 111.795 | 0.0019074 | 7.081 | 0.18459 | 2.6144 | -0.00057689 | -0.0029202 | 0.087991 | -0.0059205 | 0.019561 | -1.4529 | 0.0039286 | -0.0075452 | 0.014039 | 0.00040589 | 40.155 | 111.5021 | -9.3109 | 111.5021 | 108.8196 | 73.732 | 95.6223 | -0.89722 | -0.93842 | -0.99792 | -0.79651 | -0.75989 | -1.1032 | -0.86975 | 0.059509 | -0.29297 | -0.29297 | 118.19 | 104.9927 | 83.1024 | 104.9332 | 83.0429 | 8.3725 | -112.7335 | -112.5916 | 8.6105 | 8.5007 | 8.2672 | 0.12817 | -0.10529 | 118.1305 | 120.813 | 0.23804 | 0.20142 | 120.813 | 0.059509 | 120.8725 | 8.432 | -121.106 | -112.793 | 120.8725 | 8.5739 | 49.5255 | 8.4732
3627.8125 | 121.1929 | -15.6143 | 105.4871 | -0.013352 | 7.084 | 0.18352 | 4.3719 | -0.00057689 | -0.0027066 | 0.088205 | -0.0059205 | 0.022979 | -1.4542 | -0.00077117 | -0.009895 | 0.013185 | -0.0013031 | 26.8799 | 105.0613 | -15.509 | 104.8782 | 102.4384 | 49.704 | 86.5494 | -1.5701 | -1.3779 | -1.6205 | -1.4282 | -1.4374 | -1.8997 | -1.5656 | 0.10529 | -0.42572 | -0.60883 | 118.0527 | 102.1637 | 65.3183 | 102.0584 | 65.213 | 13.9938 | -106.8649 | -106.9153 | 14.1769 | 14.0488 | 13.7146 | 0.054931 | -0.27924 | 117.9474 | 120.3873 | 0.1831 | 0.19226 | 120.5704 | 0.24261 | 120.6757 | 14.2364 | -120.9961 | -107.1075 | 120.4926 | 14.1861 | 42.4942 | 14.0442
3629.5938 | 121.051 | -17.514 | 103.3997 | -0.013352 | 7.0859 | 0.18438 | 4.9568 | 0.0024139 | -0.0033474 | 0.087137 | -0.0059205 | 0.024047 | -1.4525 | 0.0011514 | -0.0049818 | 0.013612 | 0.0046783 | 25.5203 | 103.418 | -17.0883 | 103.038 | 100.4379 | 47.7081 | 85.5103 | -1.6937 | -1.4832 | -1.6983 | -1.474 | -1.593 | -1.9958 | -1.6891 | 0.42572 | 0.018311 | -0.36163 | 117.952 | 103.0243 | 65.2222 | 102.5986 | 64.7964 | 15.8157 | -104.8828 | -104.8737 | 15.921 | 15.8249 | 15.5182 | 0.009155 | -0.29755 | 117.5262 | 120.1263 | 0.10528 | 0.2243 | 120.5063 | 0.21515 | 120.932 | 16.0309 | -120.488 | -105.098 | 120.5521 | 16.04 | 43.0344 | 15.8203
3631.375 | 121.0098 | -23.6252 | 97.2107 | -0.0057221 | 7.081 | 0.18288 | 6.9783 | -0.0020721 | -0.0046292 | 0.087778 | -0.0059205 | 0.021057 | -1.4506 | -0.0041892 | -0.0073316 | 0.012971 | -0.00066231 | 21.6476 | 96.5652 | -23.5428 | 96.2997 | 93.0176 | 47.1588 | 78.7308 | -2.092 | -1.8997 | -2.1835 | -1.8677 | -1.9684 | -2.4078 | -2.1561 | 0.082397 | -0.64545 | -0.91095 | 116.6428 | 102.356 | 70.784 | 102.2736 | 70.7016 | 21.4416 | -99.1104 | -99.0784 | 21.6568 | 21.4691 | 21.2173 | 0.027466 | -0.2243 | 116.5604 | 119.8425 | 0.21515 | 0.31586 | 120.108 | 0.28381 | 120.1904 | 21.7255 | -120.7535 | -99.3942 | 119.9249 | 21.7575 | 45.2728 | 21.5332
3633.1094 | 120.9549 | -21.7667 | 99.0555 | -0.013352 | 7.0916 | 0.18545 | 6.667 | -0.00014949 | -0.0039884 | 0.079019 | -0.0059205 | 0.023834 | -1.4514 | -0.0046164 | -0.0041272 | 0.014894 | 0.0027557 | 21.492 | 98.3826 | -21.7392 | 98.1171 | 94.7845 | 46.7194 | 71.1548 | -2.1561 | -1.8631 | -2.211 | -1.8448 | -2.0325 | -2.3987 | -2.1744 | 0.027466 | -0.67291 | -0.93842 | 116.5512 | 92.9214 | 68.486 | 92.894 | 68.4586 | 19.5557 | -100.9186 | -100.9003 | 19.7342 | 19.5923 | 19.368 | 0.036622 | -0.18768 | 116.5237 | 119.8563 | 0.17853 | 0.36621 | 120.1218 | 0.3479 | 120.1492 | 19.9036 | -120.7947 | -101.2665 | 119.8837 | 19.9219 | 43.2587 | 19.6106
3634.8906 | 120.9366 | -23.1583 | 97.5128 | -0.020981 | 7.0899 | 0.19057 | 6.9783 | 0.0049773 | -0.0061246 | 0.08201 | -0.0028687 | 0.018066 | -1.454 | 0.0043558 | -0.008827 | 0.014039 | -0.0017303 | 22.2977 | 96.9406 | -22.8928 | 96.5927 | 93.576 | 39.2944 | 74.4095 | -2.0737 | -1.9501 | -2.2385 | -1.8036 | -1.9501 | -2.3346 | -2.1881 | 0.2655 | -0.5722 | -0.9201 | 116.7343 | 97.5677 | 62.4527 | 97.3022 | 62.1872 | 20.9198 | -99.4629 | -99.3164 | 21.2082 | 20.9702 | 20.8237 | 0.050354 | -0.096131 | 116.4688 | 119.4855 | 0.28839 | 0.43487 | 119.8334 | 0.28839 | 120.0989 | 21.2082 | -120.4056 | -99.7513 | 119.751 | 21.3547 | 45.4559 | 21.0846
3636.6719 | 120.7535 | -22.2839 | 98.2361 | -0.013352 | 7.0914 | 0.34203 | 6.9783 | -0.00057689 | -0.0037746 | 0.084573 | -0.0059205 | 0.019775 | -1.4548 | -0.00034397 | -0.0073316 | 0.015107 | 0.0040375 | 24.765 | 97.3846 | -22.2244 | 97.2977 | 94.0521 | 34.845 | 78.4744 | -1.9089 | -1.8768 | -2.0966 | -1.7258 | -1.8311 | -2.2385 | -2.0416 | 0.05951 | -0.85144 | -0.93842 | 116.3361 | 100.7584 | 57.1289 | 100.6989 | 57.0694 | 20.1874 | -100.1129 | -99.9619 | 20.4529 | 20.2423 | 20.0455 | 0.054932 | -0.14191 | 116.2766 | 119.5221 | 0.2655 | 0.37079 | 119.6091 | 0.21973 | 119.6686 | 20.4071 | -120.4605 | -100.3326 | 119.5816 | 20.5582 | 47.049 | 20.3751
3638.375 | 120.7443 | -20.7825 | 99.678 | -0.020981 | 7.0934 | 0.23864 | 6.9783 | -0.0010041 | -0.0039884 | 0.090768 | -0.0059205 | 0.017639 | -1.4557 | 0.006492 | -0.0060498 | 0.01468 | 0.00061949 | 11.8057 | 98.6847 | -20.9518 | 98.3917 | 95.105 | 28.949 | 85.0571 | -1.799 | -1.7395 | -2.005 | -1.5793 | -1.6983 | -2.0874 | -1.918 | -0.16937 | -0.99335 | -1.2863 | 115.8875 | 105.8395 | 49.7314 | 106.0089 | 49.9008 | 18.7775 | -101.4175 | -101.2573 | 19.0842 | 18.8644 | 18.6951 | 0.086975 | -0.082397 | 116.0568 | 119.3436 | 0.3067 | 0.42572 | 119.6365 | 0.2655 | 119.4672 | 19.043 | -120.6299 | -101.683 | 119.1742 | 19.2032 | 32.5882 | 18.9835
3640.1562 | 120.5658 | -24.559 | 95.9427 | -0.020981 | 7.0955 | 0.29546 | 6.9783 | -0.0012177 | -0.0071926 | 0.090128 | -0.0059205 | 0.024047 | -1.4514 | -0.0067526 | -0.0049818 | 0.013612 | -0.00044851 | 20.1691 | 94.8944 | -24.4812 | 94.7342 | 91.1224 | 33.0688 | 80.0766 | -2.2522 | -1.9455 | -2.3438 | -1.9638 | -2.1652 | -2.6138 | -2.3483 | 0.07782 | -1.0483 | -1.2085 | 115.6815 | 104.6356 | 57.6279 | 104.5578 | 57.55 | 22.2153 | -97.8882 | -97.9065 | 22.3938 | 22.2107 | 21.9452 | -0.004578 | -0.27008 | 115.6036 | 119.2154 | 0.17853 | 0.37994 | 119.3756 | 0.39825 | 119.4534 | 22.6135 | -120.4239 | -98.2864 | 119.2932 | 22.5952 | 44.7281 | 22.3068
3641.9375 | 120.4056 | -21.048 | 99.1974 | -0.013352 | 7.125 | 3.1027 | 6.9783 | 0.0054047 | -0.0031338 | 0.082864 | -0.0089723 | 0.021484 | -1.4527 | 0.0069192 | -0.0056226 | 0.015321 | -0.00066231 | 10.1807 | 98.2727 | -20.549 | 97.4533 | 94.6518 | 18.5577 | 78.891 | -1.7715 | -1.6525 | -1.9089 | -1.5656 | -1.7212 | -2.092 | -1.8951 | 0.49896 | -0.92468 | -1.7441 | 115.6998 | 99.939 | 39.6057 | 99.44 | 39.1068 | 19.1391 | -100.8499 | -100.7629 | 19.3268 | 19.1528 | 18.956 | 0.013733 | -0.1831 | 115.2008 | 118.0023 | 0.18768 | 0.34332 | 118.8217 | 0.25635 | 119.3207 | 19.3954 | -119.7464 | -101.1063 | 118.5013 | 19.4824 | 31.2286 | 19.2764
3643.7188 | 120.0119 | -24.4171 | 95.5307 | -0.013352 | 7.6037 | 7.1109 | 6.9783 | 0.0026275 | -0.0033474 | 0.067697 | -0.0059205 | 0.024475 | -1.4527 | -0.0029074 | -0.0056226 | 0.012971 | 0.0023285 | 6.1523 | 93.5532 | -23.7625 | 92.7155 | 55.1697 | 10.1486 | 56.7032 | -2.1606 | -1.9363 | -2.3117 | -1.8723 | -2.1011 | -2.5177 | -2.2842 | 0.6546 | -1.9775 | -2.8152 | 79.5868 | 81.1203 | 34.5657 | 80.4657 | 33.9111 | 22.1054 | -97.467 | -97.403 | 22.316 | 22.1329 | 21.8994 | 0.027466 | -0.20599 | 78.9322 | 116.478 | 0.21057 | 0.43945 | 117.3157 | 0.37537 | 117.9703 | 22.4808 | -119.2932 | -97.8424 | 117.1326 | 22.5449 | 30.5695 | 22.2565
3645.5 | 121.0602 | -0.11444 | 120.8954 | -0.0057221 | 6.987 | 0.025443 | 0.02035 | -0.00057689 | -0.0033474 | 0.00083317 | -0.0059205 | 0.018921 | -1.4523 | 0.0022196 | -0.0045544 | 0.015535 | 0.00019229 | -0.064087 | -0.10529 | 0.027466 | -0.004578 | 0.10986 | -0.004578 | -0.032043 | 0.022888 | -0.10986 | 0.036621 | 0.045776 | 0.09613 | 0.022888 | 0.11444 | 0.14191 | -121.0007 | -120.9 | 0.2243 | 0.082398 | 0.10986 | -0.059509 | -0.032044 | 0.15106 | -121.0052 | -120.8496 | 0.21057 | 0.22888 | 0.13733 | 0.07782 | -0.013733 | 0.082397 | -0.032044 | 0.059509 | 0.009155 | -0.13275 | -0.14648 | 0.009155 | 0.004578 | -120.8679 | -120.8588 | 0.10986 | 0.16022 | 0.050354 | 0.13733
3647.2188 | 121.0693 | -0.15106 | 121.0602 | -0.020981 | 6.987 | 0.022665 | 0.021631 | 0.0039093 | -0.0027066 | -2.1434e-05 | -0.0059205 | 0.019989 | -1.4525 | -0.0071798 | -0.010322 | 0.015535 | -0.00087591 | -0.14191 | -0.073242 | -0.022888 | -0.10529 | -0.027466 | -0.045776 | -0.10071 | -0.13275 | -0.054932 | -0.022888 | -0.064087 | -0.004578 | -0.059509 | 0.027466 | 0.12817 | -121.1334 | -121.1655 | 0.1236 | 0.050354 | 0.10529 | -0.07782 | -0.022888 | 0.12817 | -121.1151 | -121.1243 | 0.14648 | 0.17853 | 0.091553 | 0.050354 | -0.036621 | -0.004578 | -0.082398 | 0.01831 | -0.041199 | -0.050354 | -0.032044 | 0.07782 | 0.09613 | -121.0831 | -121.0831 | 0.045776 | 0.086975 | 0.009155 | 0.018311
3649 | 121.2753 | -0.11902 | 121.0373 | -0.013352 | 6.9874 | 0.022025 | 0.020991 | -0.0033539 | -0.002493 | -0.0010894 | -0.0059205 | 0.019775 | -1.4544 | 0.0032876 | -0.0060498 | 0.014253 | 0.0014741 | -0.059509 | -0.14191 | 0.022888 | 0.013733 | 0.13733 | 0.064087 | 0.022888 | 0.054932 | -0.09613 | 0.032043 | 0.064087 | 0.16937 | 0.10986 | 0.16937 | 0.14191 | -121.1792 | -121.0236 | 0.25635 | 0.14191 | 0.18311 | 0 | 0.041199 | 0.15106 | -121.1334 | -120.9732 | 0.28839 | 0.28839 | 0.22888 | 0.13733 | 0.07782 | 0.11444 | -0.009155 | 0.13733 | 0.032044 | -0.16479 | -0.12817 | -0.022888 | 0.022889 | -121.0144 | -121.0052 | 0.13275 | 0.18311 | 0.05951 | 0.17395
3650.7812 | 121.257 | -0.12817 | 121.1105 | -0.020981 | 6.9885 | 0.020956 | 0.02035 | -0.0010041 | -0.00527 | 0.00019217 | -0.0089723 | 0.020416 | -1.4531 | 0.0045694 | -0.0075452 | 0.014039 | 0.00061949 | -0.045776 | -0.1236 | 0.004578 | 0.009155 | 0.11902 | 0.050354 | -0.009155 | -0.018311 | -0.086975 | 0.009155 | 0.004578 | 0.10529 | 0.059509 | 0.09613 | 0.13275 | -121.2341 | -121.1014 | 0.24719 | 0.11902 | 0.17853 | -0.013733 | 0.045776 | 0.13733 | -121.1975 | -121.106 | 0.23346 | 0.2243 | 0.18768 | 0.086975 | 0.050354 | 0.11444 | 0.004577 | 0.096131 | -0.004577 | -0.12817 | -0.09613 | 0.004578 | 0.041199 | -121.106 | -121.1014 | 0.13733 | 0.13275 | 0.082398 | 0.10986
3652.5625 | 121.2112 | -0.14648 | 121.138 | -0.013352 | 6.9883 | 0.019034 | 0.022272 | -0.0061311 | -0.0037746 | -2.1434e-05 | -0.0059205 | 0.022552 | -1.4523 | -0.00055757 | -0.0083996 | 0.011049 | -0.0013031 | -0.10071 | -0.1236 | 0 | -0.091553 | 0.022888 | -0.041199 | -0.068665 | -0.10986 | -0.068665 | -0.022888 | -0.068665 | 0.018311 | -0.050354 | 0.027466 | 0.14648 | -121.2616 | -121.2296 | 0.16937 | 0.077819 | 0.10529 | -0.068665 | -0.041199 | 0.1236 | -121.2067 | -121.2067 | 0.16479 | 0.17395 | 0.09613 | 0.050354 | -0.027466 | 0.022888 | -0.091553 | 0.041199 | -0.045777 | -0.1236 | -0.045777 | 0.022888 | 0.077819 | -121.138 | -121.1609 | 0.054931 | 0.077819 | 0.045776 | 0.036621
3654.3438 | 121.3165 | -0.11902 | 121.1609 | -0.013352 | 6.9859 | 0.019888 | 0.021418 | 0.0026275 | -0.0027066 | 0.002115 | -0.0028687 | 0.01828 | -1.4533 | 0.0032876 | -0.0086132 | 0.014894 | -0.0017303 | -0.041199 | -0.1236 | 0.018311 | 0.013733 | 0.10986 | 0.050354 | 0.009155 | -0.004578 | -0.10071 | 0.009155 | 0.022888 | 0.10071 | 0.059509 | 0.10529 | 0.13733 | -121.2845 | -121.1472 | 0.22888 | 0.12817 | 0.16937 | -0.009156 | 0.032043 | 0.12817 | -121.2616 | -121.138 | 0.21973 | 0.22431 | 0.17853 | 0.096131 | 0.050354 | 0.091552 | -0.004578 | 0.091553 | 0.013733 | -0.14191 | -0.10986 | -0.004577 | 0.018311 | -121.1426 | -121.1517 | 0.13275 | 0.14191 | 0.07782 | 0.11444
3656.0781 | 121.3394 | -0.1236 | 121.1838 | -0.0057221 | 6.9868 | 0.018179 | 0.021418 | -0.00014949 | -0.002493 | -0.00066223 | -0.0059205 | 0.019134 | -1.4531 | -0.005471 | -0.0060498 | 0.015748 | 0.00083309 | -0.050354 | -0.15564 | 0.018311 | -0.004578 | 0.10986 | 0.050354 | 0 | -0.004578 | -0.09613 | 0.004578 | 0.004578 | 0.10529 | 0.050354 | 0.10986 | 0.14191 | -121.3394 | -121.1884 | 0.23346 | 0.1236 | 0.17395 | -0.018311 | 0.032043 | 0.12817 | -121.2799 | -121.1792 | 0.22888 | 0.23346 | 0.17395 | 0.10529 | 0.045776 | 0.091552 | -0.022889 | 0.10071 | 0 | -0.17395 | -0.10071 | -0.032044 | 0.027466 | -121.1655 | -121.1792 | 0.11902 | 0.12817 | 0.073242 | 0.11902
3657.875 | 121.3715 | -0.1236 | 121.1838 | -0.0057221 | 6.9831 | 0.017539 | 0.022913 | -0.0033539 | -0.005911 | -0.00087583 | -0.0059205 | 0.019775 | -1.4538 | 0.010551 | -0.0039136 | 0.015535 | 0.0023285 | -0.082397 | -0.14648 | 0 | -0.045776 | 0.064087 | -0.013733 | -0.050354 | -0.054932 | -0.09613 | 0.013733 | 0 | 0.059509 | 0.022888 | 0.091553 | 0.1236 | -121.3303 | -121.2296 | 0.18768 | 0.073242 | 0.10986 | -0.050354 | -0.013733 | 0.13733 | -121.2799 | -121.1838 | 0.1831 | 0.21515 | 0.14648 | 0.07782 | 0.009155 | 0.064087 | -0.045776 | 0.045776 | -0.013733 | -0.14648 | -0.10986 | -0.022888 | 0.027466 | -121.1838 | -121.17 | 0.07782 | 0.1236 | 0.041199 | 0.068664
3659.5938 | 121.4355 | -0.10986 | 121.2112 | -0.0057221 | 6.9878 | 0.018607 | 0.024622 | 0.0019867 | -0.0029202 | 0.0012604 | -0.0059205 | 0.018066 | -1.4533 | -0.00013037 | -0.003059 | 0.015962 | 0.0019013 | -0.082397 | -0.10986 | -0.018311 | -0.050354 | 0.045776 | -0.036621 | -0.050354 | -0.013733 | -0.10529 | 0.013733 | 0.054932 | 0.10986 | 0.054932 | 0.13733 | 0.091552 | -121.3211 | -121.2616 | 0.15564 | 0.059509 | 0.073242 | -0.032043 | -0.01831 | 0.1236 | -121.3165 | -121.1563 | 0.21973 | 0.24719 | 0.16479 | 0.1236 | 0.041199 | 0.064087 | -0.032043 | 0.09613 | 0.041199 | -0.091552 | -0.11902 | 0 | 0.004577 | -121.2296 | -121.1975 | 0.059509 | 0.16479 | 0.027466 | 0.09613
3661.3594 | 121.4264 | -0.10986 | 121.1838 | -0.013352 | 6.9883 | 0.01647 | 0.023127 | 0.00070491 | -0.001852 | -0.001944 | -0.0059205 | 0.020843 | -1.4516 | -0.0024802 | -0.005409 | 0.017244 | 0.00019229 | -0.050354 | -0.15564 | 0.013733 | 0 | 0.13275 | 0.013733 | -0.022888 | 0.027466 | -0.091553 | 0.004578 | 0.064087 | 0.11444 | 0.059509 | 0.12817 | 0.1236 | -121.3394 | -121.1838 | 0.24261 | 0.086975 | 0.1236 | -0.036621 | 0 | 0.11444 | -121.2753 | -121.1197 | 0.2243 | 0.23804 | 0.16937 | 0.1236 | 0.054931 | 0.11902 | -0.013733 | 0.10986 | 0.059509 | -0.16937 | -0.096131 | -0.045777 | 0.01831 | -121.17 | -121.1792 | 0.10986 | 0.17395 | 0.059509 | 0.13733
3663.1406 | 121.3348 | -0.17395 | 121.2524 | -0.013352 | 6.988 | 0.01647 | 0.021418 | 0.0015595 | -0.0012112 | 0.0023286 | -0.0028687 | 0.021484 | -1.4531 | -0.00013037 | -0.0069044 | 0.014253 | -0.0036529 | -0.11444 | -0.11444 | -0.041199 | -0.1236 | -0.041199 | -0.10071 | -0.13733 | -0.15564 | -0.045776 | -0.022888 | -0.073242 | -0.045776 | -0.09613 | 0.022888 | 0.13275 | -121.3669 | -121.376 | 0.13275 | 0.036621 | 0.073242 | -0.09613 | -0.059509 | 0.15106 | -121.2982 | -121.3257 | 0.12817 | 0.19684 | 0.07782 | 0.045776 | -0.073242 | 0 | -0.082397 | -0.022888 | -0.050354 | -0.073242 | -0.022888 | 0.059509 | 0.12817 | -121.2936 | -121.2753 | 0.050354 | 0.10071 | 0.059509 | 0.01831
3664.8594 | 121.3806 | -0.16937 | 121.2616 | -0.0057221 | 6.9861 | 0.01583 | 0.022272 | 0.0017731 | -0.0046292 | 0.00061957 | -0.0028687 | 0.02127 | -1.4529 | -0.0052572 | -0.008827 | 0.015321 | 0.0016877 | -0.11902 | -0.10529 | -0.041199 | -0.1236 | -0.027466 | -0.082397 | -0.09613 | -0.14648 | -0.059509 | -0.009155 | -0.050354 | 0.004578 | -0.032043 | 0.054932 | 0.12817 | -121.3669 | -121.3852 | 0.14191 | 0.073243 | 0.086976 | -0.054931 | -0.041198 | 0.16022 | -121.3211 | -121.312 | 0.17395 | 0.22431 | 0.13733 | 0.064087 | -0.022888 | 0.013733 | -0.082397 | 0.013733 | -0.041199 | -0.064087 | -0.050354 | 0.064087 | 0.10986 | -121.3028 | -121.2708 | 0.045777 | 0.11902 | 0.050354 | 0.022889
3666.6406 | 121.463 | -0.10986 | 121.2616 | -0.020981 | 6.9861 | 0.018607 | 0.022486 | -0.00036309 | -0.0022794 | -0.0015166 | 0.00018312 | 0.019561 | -1.4553 | 0.0020058 | -0.0058362 | 0.017671 | 0.0048919 | -0.11444 | -0.13275 | 0.004578 | -0.059509 | 0.050354 | -0.022888 | -0.050354 | -0.045776 | -0.091553 | 0.013733 | 0.004578 | 0.064087 | -0.004578 | 0.086975 | 0.11444 | -121.3943 | -121.3211 | 0.16022 | 0.059509 | 0.086975 | -0.054932 | -0.027466 | 0.1236 | -121.3531 | -121.257 | 0.17395 | 0.19684 | 0.10529 | 0.073242 | -0.018311 | 0.045776 | -0.064087 | 0.050354 | -0.009155 | -0.13733 | -0.10529 | -0.022888 | 0.01831 | -121.257 | -121.2479 | 0.050354 | 0.11444 | -0.004578 | 0.064087
3668.4062 | 121.4401 | -0.14648 | 121.2799 | -0.013352 | 6.987 | 0.018179 | 0.022486 | 0.0013459 | -0.0044156 | -2.1434e-05 | -0.0059205 | 0.02127 | -1.4531 | -0.00034397 | -0.004768 | 0.015321 | 0.0010467 | -0.1236 | -0.11902 | -0.013733 | -0.11902 | -0.018311 | -0.10529 | -0.11444 | -0.09613 | -0.064087 | 0 | -0.004578 | 0.032043 | -0.045776 | 0.091553 | 0.13275 | -121.3989 | -121.3989 | 0.12817 | 0.032043 | 0.041198 | -0.10071 | -0.091553 | 0.14648 | -121.344 | -121.2845 | 0.17853 | 0.23804 | 0.10071 | 0.091553 | -0.045776 | -0.004578 | -0.10529 | 0.032043 | -0.004578 | -0.10529 | -0.064087 | 0.027465 | 0.082397 | -121.2936 | -121.2799 | 0.027465 | 0.14191 | 0.022888 | 0.050354
3670.1875 | 121.4996 | -0.12817 | 121.2753 | -0.013352 | 6.9855 | 0.018607 | 0.019495 | -0.0016449 | -0.004202 | -0.003012 | 0.00018312 | 0.019561 | -1.4508 | 0.0015786 | -0.0060498 | 0.01703 | 0.0010467 | -0.064087 | -0.14191 | 0.004578 | -0.009155 | 0.10071 | -0.009155 | -0.022888 | -0.022888 | -0.10071 | 0.013733 | 0.013733 | 0.064087 | 0.036621 | 0.10986 | 0.13275 | -121.4172 | -121.2845 | 0.22888 | 0.10529 | 0.11902 | -0.027466 | -0.013733 | 0.14191 | -121.376 | -121.2616 | 0.19226 | 0.23804 | 0.1648 | 0.09613 | 0.022888 | 0.09613 | -0.013733 | 0.050354 | 0 | -0.14649 | -0.11444 | -0.013733 | 0.027466 | -121.2708 | -121.2616 | 0.11902 | 0.14191 | 0.064087 | 0.10529
3671.9844 | 121.5408 | -0.10529 | 121.2982 | -0.020981 | 6.9838 | 0.015616 | 0.023127 | 0.00070491 | -0.0029202 | -0.00066223 | -0.0059205 | 0.020416 | -1.4519 | -0.0022666 | -0.0028454 | 0.016175 | 0.0010467 | -0.10529 | -0.13733 | 0.004578 | -0.036621 | 0.059509 | -0.032043 | -0.045776 | 0 | -0.07782 | 0.009155 | 0.073242 | 0.10071 | 0.041199 | 0.14191 | 0.10986 | -121.4355 | -121.3348 | 0.16479 | 0.05951 | 0.073243 | -0.050354 | -0.036621 | 0.11444 | -121.376 | -121.225 | 0.20599 | 0.24719 | 0.14649 | 0.13275 | 0.032044 | 0.054931 | -0.041199 | 0.091553 | 0.064087 | -0.14191 | -0.086975 | -0.032043 | 0.027466 | -121.2936 | -121.2891 | 0.068665 | 0.17853 | 0 | 0.10529
3673.7031 | 121.4127 | -0.16022 | 121.3486 | -0.0057221 | 6.9883 | 0.019675 | 0.021418 | -0.00079049 | -0.001852 | -0.0010894 | -0.0028687 | 0.02127 | -1.4514 | -0.0033346 | -0.008186 | 0.015321 | -0.0021575 | -0.086975 | -0.10529 | -0.032043 | -0.10071 | -0.009155 | -0.086975 | -0.10986 | -0.12817 | -0.054932 | -0.013733 | -0.050354 | -0.027466 | -0.091553 | 0.027466 | 0.12817 | -121.4539 | -121.4493 | 0.15106 | 0.050354 | 0.073242 | -0.07782 | -0.054932 | 0.14648 | -121.4035 | -121.3989 | 0.13275 | 0.18768 | 0.068664 | 0.041199 | -0.07782 | 0.022888 | -0.068665 | -0.013733 | -0.036621 | -0.073243 | -0.041199 | 0.054931 | 0.10528 | -121.3806 | -121.3623 | 0.059509 | 0.10986 | 0.073242 | 0.032043
3675.4688 | 121.4813 | -0.14191 | 121.3669 | 0.0019074 | 6.987 | 0.018179 | 0.022486 | 0.0022003 | -0.003561 | -0.001303 | -0.0028687 | 0.021484 | -1.4536 | 0.0017922 | -0.007118 | 0.015107 | 0.00040589 | -0.086975 | -0.13275 | -0.027466 | -0.068665 | 0.059509 | -0.027466 | -0.054932 | -0.054932 | -0.073242 | -0.009155 | -0.013733 | 0.036621 | 0 | 0.07782 | 0.11444 | -121.4996 | -121.4355 | 0.20142 | 0.086975 | 0.11444 | -0.027466 | 0 | 0.13275 | -121.4401 | -121.3806 | 0.17853 | 0.21973 | 0.14191 | 0.086975 | 0.009155 | 0.086975 | -0.041199 | 0.045776 | -0.004578 | -0.10529 | -0.064087 | 0.009156 | 0.068665 | -121.3943 | -121.376 | 0.073242 | 0.12817 | 0.054932 | 0.086975
3677.25 | 121.5958 | -0.09613 | 121.3303 | -0.020981 | 6.9857 | 0.01882 | 0.023127 | 6.4114e-05 | 0.00049776 | -0.0010894 | -0.012024 | 0.019134 | -1.4501 | 0.0045694 | -0.0024182 | 0.016175 | -0.00087591 | -0.054932 | -0.16022 | 0.022888 | -0.004578 | 0.11902 | 0 | -0.018311 | 0.036621 | -0.10529 | 0.032043 | 0.082397 | 0.11902 | 0.054932 | 0.15106 | 0.11902 | -121.4905 | -121.3348 | 0.21515 | 0.077819 | 0.09613 | -0.041199 | -0.022888 | 0.12817 | -121.4355 | -121.2479 | 0.21515 | 0.24719 | 0.15106 | 0.11902 | 0.022889 | 0.096131 | -0.027466 | 0.086976 | 0.050354 | -0.1831 | -0.13733 | -0.064087 | -0.009156 | -121.3074 | -121.2982 | 0.091552 | 0.17853 | 0.041198 | 0.13275
3678.9688 | 121.582 | -0.10986 | 121.3165 | -0.013352 | 6.9863 | 0.017325 | 0.0227 | -0.0050629 | -0.00014304 | -0.00066223 | -0.0059205 | 0.018066 | -1.4523 | 0.010124 | -0.0041272 | 0.017244 | -0.0023713 | -0.054932 | -0.17853 | 0.022888 | 0 | 0.12817 | 0.018311 | 0 | 0.036621 | -0.11444 | 0.018311 | 0.045776 | 0.10986 | 0.059509 | 0.13733 | 0.13275 | -121.4951 | -121.3165 | 0.23804 | 0.10986 | 0.12817 | -0.022888 | -0.004577 | 0.12817 | -121.431 | -121.2708 | 0.21973 | 0.24719 | 0.16937 | 0.11902 | 0.041198 | 0.10529 | -0.022888 | 0.091552 | 0.027465 | -0.20142 | -0.13275 | -0.068665 | -0.004578 | -121.2936 | -121.2982 | 0.10986 | 0.15564 | 0.054931 | 0.14648
3680.75 | 121.5866 | -0.13733 | 121.3531 | -0.013352 | 6.9838 | 0.014761 | 0.020991 | 0.0024139 | -0.002493 | 0.002115 | -0.0028687 | 0.019989 | -1.4506 | -0.0022666 | -0.007118 | 0.016389 | -0.00023491 | -0.10529 | -0.1831 | 0.004578 | -0.050354 | 0.068665 | -0.013733 | -0.059509 | -0.041199 | -0.091553 | 0.004578 | 0.009155 | 0.050354 | 0.009155 | 0.086975 | 0.14191 | -121.5363 | -121.4035 | 0.20599 | 0.07782 | 0.1236 | -0.064087 | -0.018311 | 0.14191 | -121.4447 | -121.344 | 0.18768 | 0.2243 | 0.14648 | 0.082397 | 0.004577 | 0.064087 | -0.054932 | 0.045776 | 0.004577 | -0.18768 | -0.096131 | -0.045776 | 0.045776 | -121.3486 | -121.3486 | 0.086975 | 0.14648 | 0.032043 | 0.09613
3682.5312 | 121.6141 | -0.10529 | 121.3577 | -0.013352 | 6.9859 | 0.016684 | 0.020777 | 0.00091851 | -0.002493 | 0.0012604 | -0.0059205 | 0.02127 | -1.4529 | 0.003074 | -0.0037 | 0.016816 | 0.0014741 | -0.068665 | -0.16937 | 0.009155 | 0.004578 | 0.11902 | 0.013733 | -0.022888 | 0.027466 | -0.10071 | 0.032043 | 0.054932 | 0.10071 | 0.050354 | 0.1236 | 0.11444 | -121.5271 | -121.3531 | 0.22431 | 0.082398 | 0.11902 | -0.032043 | 0.004578 | 0.13733 | -121.4584 | -121.3028 | 0.20599 | 0.22888 | 0.15564 | 0.091553 | 0.018311 | 0.10986 | -0.004577 | 0.068665 | 0.022889 | -0.17853 | -0.13275 | -0.064087 | 0.004578 | -121.3486 | -121.3257 | 0.10986 | 0.16022 | 0.036621 | 0.13275
3684.25 | 121.6003 | -0.13733 | 121.3623 | -0.013352 | 6.9865 | 0.014761 | 0.02035 | 0.0015595 | -0.0020658 | -0.0032256 | -0.0059205 | 0.019134 | -1.4521 | 0.0045694 | -0.0066906 | 0.013185 | -0.00066231 | -0.07782 | -0.16937 | 0.004578 | 0 | 0.09613 | -0.013733 | -0.036621 | 0 | -0.10071 | 0.018311 | 0.032043 | 0.07782 | 0.036621 | 0.086975 | 0.14191 | -121.5317 | -121.3623 | 0.23346 | 0.10071 | 0.1236 | -0.041199 | -0.018311 | 0.15564 | -121.463 | -121.3303 | 0.21515 | 0.2243 | 0.17395 | 0.068664 | 0.01831 | 0.091552 | -0.004578 | 0.059509 | 0.013732 | -0.17395 | -0.11902 | -0.032044 | 0.036621 | -121.3577 | -121.344 | 0.13733 | 0.16937 | 0.059509 | 0.13733
3686.0156 | 121.5912 | -0.14191 | 121.3989 | -0.020981 | 6.9865 | 0.017966 | 0.020991 | 0.0011321 | -0.0016384 | -0.00044863 | -0.0059205 | 0.019775 | -1.4544 | 0.0037148 | -0.007118 | 0.014253 | 0.0027557 | -0.10529 | -0.17853 | 0 | -0.050354 | 0.054932 | -0.013733 | -0.041199 | -0.036621 | -0.10071 | 0.013733 | 0.009155 | 0.054932 | 0.013733 | 0.082397 | 0.14191 | -121.5775 | -121.4493 | 0.19684 | 0.10071 | 0.12817 | -0.041199 | -0.013733 | 0.15564 | -121.4996 | -121.3898 | 0.19684 | 0.2243 | 0.15564 | 0.068664 | 0 | 0.054932 | -0.050354 | 0.041199 | -0.004578 | -0.17853 | -0.11444 | -0.036621 | 0.041199 | -121.3989 | -121.3852 | 0.091553 | 0.15106 | 0.036621 | 0.10529
3687.7969 | 121.5179 | -0.17853 | 121.4172 | -0.020981 | 6.9883 | 0.016684 | 0.023981 | 0.0015595 | -0.0022794 | -0.00044863 | 0.00018312 | 0.022125 | -1.4523 | -0.002053 | -0.0079724 | 0.014894 | 0.00019229 | -0.13275 | -0.14191 | -0.050354 | -0.15106 | -0.086975 | -0.13733 | -0.15564 | -0.16937 | -0.045776 | -0.022888 | -0.059509 | -0.050354 | -0.086975 | 0.032043 | 0.12817 | -121.5591 | -121.5683 | 0.091553 | 0.022888 | 0.041199 | -0.10529 | -0.086975 | 0.15564 | -121.463 | -121.4767 | 0.12817 | 0.21057 | 0.091553 | 0.054931 | -0.064087 | -0.036621 | -0.10071 | -0.027466 | -0.036621 | -0.091553 | -0.022888 | 0.036621 | 0.13275 | -121.4676 | -121.4401 | 0.027466 | 0.11902 | 0.045777 | 0.009155
3689.5 | 121.6507 | -0.10986 | 121.376 | -0.020981 | 6.9846 | 0.015402 | 0.019495 | -0.0014313 | -0.0012112 | -0.00044863 | -0.0028687 | 0.019989 | -1.4523 | 0.001365 | -0.0075452 | 0.016389 | -0.00023491 | -0.11902 | -0.16479 | -0.013733 | -0.036621 | 0.082397 | 0.013733 | -0.027466 | -0.018311 | -0.09613 | -0.013733 | 0.045776 | 0.10529 | 0.073242 | 0.12817 | 0.09613 | -121.5408 | -121.4127 | 0.19226 | 0.082397 | 0.1236 | -0.013733 | 0.027466 | 0.09613 | -121.4722 | -121.3303 | 0.21515 | 0.23804 | 0.18311 | 0.14191 | 0.086975 | 0.09613 | -0.022888 | 0.11902 | 0.059509 | -0.15106 | -0.082397 | -0.054932 | 0.013733 | -121.3898 | -121.3898 | 0.073242 | 0.15564 | -0.009156 | 0.091552
3691.2812 | 121.5546 | -0.15564 | 121.4401 | -0.013352 | 6.99 | 0.017325 | 0.021631 | -0.00014949 | -0.0016384 | -0.00066223 | -0.0089723 | 0.02127 | -1.4533 | 0.0011514 | -0.0069044 | 0.014894 | -0.0034393 | -0.09613 | -0.13733 | -0.022888 | -0.10529 | -0.013733 | -0.10071 | -0.13275 | -0.12817 | -0.064087 | -0.004578 | -0.059509 | -0.032043 | -0.082397 | 0.022888 | 0.13275 | -121.5775 | -121.5454 | 0.14191 | 0.022889 | 0.054932 | -0.10986 | -0.07782 | 0.15106 | -121.5042 | -121.4996 | 0.1236 | 0.17853 | 0.073243 | 0.027466 | -0.077819 | 0.009155 | -0.082398 | -0.027465 | -0.054931 | -0.11444 | -0.059509 | 0.018311 | 0.091553 | -121.463 | -121.4447 | 0.050354 | 0.096131 | 0.05951 | 0.027466
3693.0469 | 121.5225 | -0.17853 | 121.4539 | -0.0057221 | 6.9908 | 0.017325 | 0.0227 | 0.0034821 | -0.0022794 | -0.00066223 | -0.0028687 | 0.021698 | -1.4548 | -0.00034397 | -0.0075452 | 0.015535 | 0.0027557 | -0.14191 | -0.12817 | -0.059509 | -0.13275 | -0.050354 | -0.1236 | -0.13275 | -0.17395 | -0.064087 | -0.018311 | -0.07782 | -0.045776 | -0.11902 | 0.032043 | 0.11902 | -121.582 | -121.5866 | 0.12817 | 0.045777 | 0.054932 | -0.073242 | -0.064087 | 0.16022 | -121.5179 | -121.5317 | 0.13275 | 0.21057 | 0.059509 | 0.050354 | -0.10071 | 0.009155 | -0.073242 | -0.027465 | -0.059509 | -0.068665 | -0.045776 | 0.050354 | 0.11444 | -121.5134 | -121.4722 | 0.045777 | 0.10071 | 0.036621 | 0.004578
3694.8281 | 121.5775 | -0.17395 | 121.4905 | -0.013352 | 6.987 | 0.015189 | 0.019282 | -0.0031403 | -0.0061246 | -0.0017304 | -0.0028687 | 0.019775 | -1.4551 | 0.001365 | -0.0079724 | 0.012971 | -0.00044851 | -0.10986 | -0.15106 | -0.013733 | -0.086975 | 0.027466 | -0.018311 | -0.073242 | -0.10986 | -0.068665 | -0.009155 | -0.059509 | 0.004578 | -0.045776 | 0.036621 | 0.16022 | -121.6415 | -121.5775 | 0.20142 | 0.10071 | 0.15564 | -0.059509 | -0.004578 | 0.16479 | -121.5591 | -121.55 | 0.17853 | 0.21057 | 0.12817 | 0.045776 | -0.036621 | 0.041199 | -0.073242 | 0.013733 | -0.050354 | -0.13733 | -0.05951 | 0.022888 | 0.10528 | -121.5042 | -121.4996 | 0.086975 | 0.11444 | 0.064087 | 0.064087
3696.5625 | 121.6278 | -0.15564 | 121.4813 | -0.0057221 | 6.9876 | 0.01348 | 0.020991 | 6.4114e-05 | -0.0054836 | -0.00023503 | -0.0028687 | 0.020843 | -1.4533 | -0.00483 | -0.008827 | 0.015107 | -0.0021575 | -0.13733 | -0.14191 | -0.045776 | -0.12817 | -0.022888 | -0.064087 | -0.10071 | -0.13733 | -0.059509 | -0.009155 | -0.045776 | 0.004578 | -0.027466 | 0.064087 | 0.10986 | -121.6232 | -121.6095 | 0.13275 | 0.054932 | 0.091553 | -0.054932 | -0.018311 | 0.14649 | -121.5408 | -121.5271 | 0.16022 | 0.21973 | 0.12817 | 0.073242 | -0.018311 | 0.022888 | -0.082398 | 0.013733 | -0.036621 | -0.096131 | -0.050354 | 0.013733 | 0.096131 | -121.5271 | -121.4905 | 0.027466 | 0.10986 | 0.018311 | 0.018311
3698.3438 | 121.6782 | -0.13733 | 121.4447 | -0.0057221 | 6.9865 | 0.018179 | 0.0227 | -0.0016449 | -0.00078404 | -0.0027984 | -0.0059205 | 0.018066 | -1.4527 | 0.0017922 | -0.0051954 | 0.01468 | 0.0023285 | -0.091553 | -0.16937 | 0.004578 | -0.027466 | 0.082397 | -0.036621 | -0.022888 | -0.027466 | -0.091553 | 0 | 0.013733 | 0.064087 | 0.018311 | 0.10071 | 0.14191 | -121.6141 | -121.4722 | 0.21973 | 0.11444 | 0.10071 | -0.027466 | -0.041199 | 0.13733 | -121.5363 | -121.431 | 0.20142 | 0.23804 | 0.15564 | 0.10071 | 0.018311 | 0.077819 | -0.032044 | 0.064087 | 0.013733 | -0.17395 | -0.091553 | -0.032044 | 0.045776 | -121.4401 | -121.4447 | 0.10986 | 0.15106 | 0.045776 | 0.10986
3700.125 | 121.6049 | -0.15564 | 121.4676 | -0.013352 | 6.9874 | 0.015616 | 0.02334 | 0.0017731 | -0.0014248 | 0.001474 | -0.0028687 | 0.021911 | -1.4516 | -0.0016256 | -0.0045544 | 0.01468 | 0.0016877 | -0.13275 | -0.13275 | -0.041199 | -0.14191 | -0.050354 | -0.10529 | -0.15106 | -0.13733 | -0.068665 | -0.013733 | -0.050354 | -0.022888 | -0.07782 | 0.041199 | 0.11444 | -121.6003 | -121.6095 | 0.10529 | 0.004578 | 0.050354 | -0.10986 | -0.064087 | 0.14191 | -121.5363 | -121.5179 | 0.13275 | 0.19684 | 0.07782 | 0.054932 | -0.064087 | -0.009155 | -0.10071 | -0.009155 | -0.036621 | -0.091552 | -0.054932 | 0.022889 | 0.086975 | -121.5088 | -121.4813 | 0.013733 | 0.10529 | 0.022889 | 0.018311
3701.8438 | 121.7148 | -0.11902 | 121.4401 | -0.013352 | 6.9857 | 0.016684 | 0.0227 | 0.00049131 | -0.0039884 | -0.0010894 | -0.0089723 | 0.01828 | -1.4527 | 0.010764 | -0.0043408 | 0.017457 | -0.0036529 | -0.07782 | -0.16937 | -0.022888 | -0.032043 | 0.091553 | 0 | -0.050354 | 0.004578 | -0.09613 | 0.018311 | 0.059509 | 0.11444 | 0.059509 | 0.15106 | 0.096131 | -121.6095 | -121.4722 | 0.21057 | 0.068665 | 0.11902 | -0.027466 | 0.022888 | 0.13733 | -121.5363 | -121.3806 | 0.23346 | 0.27008 | 0.17853 | 0.13275 | 0.041198 | 0.11444 | -0.009155 | 0.09613 | 0.041198 | -0.14649 | -0.11444 | -0.050354 | 0.022889 | -121.463 | -121.4218 | 0.086976 | 0.17853 | 0.041199 | 0.1236
3703.5469 | 121.6553 | -0.13733 | 121.4859 | -0.013352 | 6.9861 | 0.014548 | 0.0227 | -0.0018585 | -0.0016384 | 0.00040597 | -0.0059205 | 0.021057 | -1.4527 | -0.00098477 | -0.007118 | 0.01468 | -0.00087591 | -0.091553 | -0.14191 | -0.027466 | -0.086975 | 0.032043 | -0.050354 | -0.086975 | -0.059509 | -0.064087 | -0.018311 | -0.004578 | 0.045776 | -0.009155 | 0.07782 | 0.10986 | -121.6278 | -121.5729 | 0.16937 | 0.050354 | 0.086975 | -0.059509 | -0.022888 | 0.11902 | -121.55 | -121.4905 | 0.18311 | 0.21515 | 0.12817 | 0.096131 | 0.009156 | 0.059509 | -0.059509 | 0.064087 | 0.013733 | -0.11444 | -0.045776 | -0.004578 | 0.073242 | -121.5134 | -121.5042 | 0.050354 | 0.13275 | 0.045776 | 0.07782
3705.3281 | 121.6507 | -0.15564 | 121.4859 | -0.0057221 | 6.9865 | 0.013266 | 0.021418 | 0.0051911 | -0.0020658 | 0.0042512 | -0.0028687 | 0.021484 | -1.4516 | -0.0011984 | -0.0086132 | 0.014466 | -0.0036529 | -0.13733 | -0.13275 | -0.041199 | -0.12817 | -0.041199 | -0.064087 | -0.10986 | -0.13275 | -0.068665 | -0.018311 | -0.045776 | 0.032043 | -0.032043 | 0.059509 | 0.11444 | -121.6187 | -121.6141 | 0.11444 | 0.045777 | 0.091553 | -0.068664 | -0.022888 | 0.13733 | -121.5546 | -121.5317 | 0.18768 | 0.21515 | 0.1236 | 0.07782 | -0.013732 | 0 | -0.086975 | 0.050354 | -0.027465 | -0.091552 | -0.050354 | 0.022889 | 0.086975 | -121.5271 | -121.5042 | 0.027466 | 0.10986 | 0.018311 | 0.022889
3707.0625 | 121.6232 | -0.15106 | 121.5179 | -0.013352 | 6.9872 | 0.014761 | 0.023127 | 0.0058319 | -0.0020658 | 0.00061957 | -0.0059205 | 0.021484 | -1.4525 | -0.0016256 | -0.0079724 | 0.014894 | 0.0031829 | -0.10986 | -0.14191 | -0.036621 | -0.086975 | -0.009155 | -0.09613 | -0.12817 | -0.10986 | -0.07782 | 0.004578 | -0.045776 | -0.004578 | -0.07782 | 0.036621 | 0.11444 | -121.6599 | -121.6049 | 0.14191 | 0.022888 | 0.054932 | -0.091553 | -0.059509 | 0.15564 | -121.5958 | -121.5637 | 0.14648 | 0.18768 | 0.073242 | 0.032043 | -0.082398 | 0.027466 | -0.050354 | -0.009156 | -0.050354 | -0.10529 | -0.082398 | 0.009155 | 0.073242 | -121.5546 | -121.5134 | 0.064087 | 0.10529 | 0.041199 | 0.041199
3708.8594 | 121.7194 | -0.13733 | 121.5042 | -0.020981 | 6.9872 | 0.014121 | 0.019282 | 0.00027771 | -0.0039884 | 0.00083317 | -0.0028687 | 0.018066 | -1.4546 | 0.0022196 | -0.0075452 | 0.01233 | -0.0013031 | -0.082397 | -0.19226 | -0.009155 | -0.013733 | 0.10529 | 0.045776 | 0 | -0.018311 | -0.091553 | 0.009155 | 0.032043 | 0.09613 | 0.064087 | 0.11444 | 0.12817 | -121.6965 | -121.5179 | 0.24262 | 0.13733 | 0.18311 | 0.009155 | 0.054931 | 0.14648 | -121.5958 | -121.4722 | 0.23346 | 0.25177 | 0.20142 | 0.10529 | 0.054932 | 0.11444 | -0.004578 | 0.086975 | 0.022888 | -0.18311 | -0.10071 | -0.054932 | 0.045776 | -121.5134 | -121.4951 | 0.1236 | 0.16937 | 0.054932 | 0.11902
3710.5781 | 121.7514 | -0.14191 | 121.5042 | 0.0019074 | 6.9831 | 0.016043 | 0.023127 | 0.0019867 | -0.0050564 | -0.0021576 | -0.0028687 | 0.021698 | -1.4544 | 0.0035012 | -0.0039136 | 0.013612 | 0.00019229 | -0.12817 | -0.16937 | -0.018311 | -0.07782 | 0.009155 | -0.07782 | -0.082397 | -0.068665 | -0.07782 | -0.004578 | 0.041199 | 0.073242 | 0.022888 | 0.11902 | 0.1236 | -121.6736 | -121.582 | 0.15106 | 0.05951 | 0.064087 | -0.064086 | -0.059509 | 0.13733 | -121.582 | -121.463 | 0.21515 | 0.26093 | 0.16479 | 0.1236 | 0.027466 | 0.027466 | -0.059509 | 0.07782 | 0.045777 | -0.15106 | -0.073242 | -0.027466 | 0.064087 | -121.5225 | -121.5088 | 0.064087 | 0.18311 | 0.013733 | 0.073242
3712.3438 | 121.7651 | -0.15564 | 121.4996 | -0.013352 | 6.9874 | 0.014548 | 0.022272 | -0.00079049 | -0.0022794 | -0.003012 | -0.0028687 | 0.018066 | -1.4514 | -0.0022666 | -0.004768 | 0.014039 | -0.00066231 | -0.091553 | -0.14648 | -0.004578 | -0.041199 | 0.082397 | -0.022888 | -0.059509 | -0.013733 | -0.09613 | 0.013733 | 0.054932 | 0.10071 | 0.054932 | 0.12817 | 0.15106 | -121.6461 | -121.5408 | 0.23804 | 0.096131 | 0.13275 | -0.054931 | -0.01831 | 0.16937 | -121.5958 | -121.4447 | 0.25635 | 0.28381 | 0.21057 | 0.11444 | 0.041199 | 0.086975 | -0.036621 | 0.086975 | 0.041199 | -0.14191 | -0.10986 | 0.009156 | 0.05951 | -121.5042 | -121.4859 | 0.11444 | 0.21057 | 0.064087 | 0.14191
3714.125 | 121.669 | -0.16479 | 121.5363 | -0.013352 | 6.9859 | 0.01348 | 0.019068 | -0.0014313 | -0.0033474 | 0.00040597 | -0.0089723 | 0.020843 | -1.4531 | -0.0044028 | -0.008827 | 0.014253 | 0.0014741 | -0.14648 | -0.15564 | -0.027466 | -0.13275 | -0.018311 | -0.068665 | -0.10529 | -0.13733 | -0.064087 | -0.018311 | -0.073242 | 0 | -0.054932 | 0.013733 | 0.13733 | -121.6919 | -121.669 | 0.14648 | 0.059509 | 0.09613 | -0.07782 | -0.041199 | 0.14648 | -121.6003 | -121.6095 | 0.16479 | 0.17853 | 0.10986 | 0.032044 | -0.036621 | 0.009155 | -0.10529 | 0.018311 | -0.054931 | -0.12817 | -0.045776 | 0.009155 | 0.10071 | -121.5637 | -121.5546 | 0.032044 | 0.091553 | 0.018311 | 0.027466
3715.9062 | 121.7056 | -0.14648 | 121.5683 | -0.0057221 | 6.9874 | 0.015402 | 0.023127 | 0.0032685 | -0.00099764 | 0.00061957 | 0.00018312 | 0.021911 | -1.4533 | -0.0046164 | -0.0062634 | 0.014466 | -0.0027985 | -0.086975 | -0.15106 | -0.041199 | -0.073242 | 0.018311 | -0.045776 | -0.07782 | -0.045776 | -0.068665 | -0.004578 | -0.013733 | 0.041199 | -0.009155 | 0.073242 | 0.10529 | -121.7194 | -121.6415 | 0.16479 | 0.068664 | 0.10071 | -0.036621 | -0.004577 | 0.14191 | -121.637 | -121.582 | 0.18768 | 0.21973 | 0.13733 | 0.07782 | -0.004577 | 0.05951 | -0.032043 | 0.045777 | -0.009155 | -0.10986 | -0.064087 | -0.004578 | 0.077819 | -121.6095 | -121.5729 | 0.073242 | 0.13275 | 0.059509 | 0.10071
3717.6719 | 121.7331 | -0.1236 | 121.5454 | -0.0057221 | 6.9863 | 0.01647 | 0.02035 | -0.0033539 | -0.004202 | -0.00023503 | -0.0059205 | 0.018493 | -1.4531 | 8.3226e-05 | -0.0090406 | 0.017884 | 0.0038239 | -0.10071 | -0.18768 | -0.013733 | -0.082397 | 0.045776 | -0.036621 | -0.064087 | -0.082397 | -0.091553 | 0 | -0.009155 | 0.036621 | 0.027466 | 0.082397 | 0.10986 | -121.7331 | -121.6278 | 0.16937 | 0.059509 | 0.086975 | -0.050354 | -0.022888 | 0.1236 | -121.637 | -121.5546 | 0.16022 | 0.20599 | 0.15106 | 0.082397 | 0.027466 | 0.059509 | -0.068664 | 0.036621 | -0.009155 | -0.17395 | -0.091553 | -0.064087 | 0.032043 | -121.5591 | -121.5454 | 0.041199 | 0.11444 | 0.022888 | 0.041199
3719.3906 | 121.8338 | -0.14191 | 121.5271 | -0.013352 | 6.9883 | 0.014121 | 0.019495 | -0.0044221 | -0.0044156 | 0.00040597 | -0.0028687 | 0.016357 | -1.4538 | 0.0022196 | -0.0066906 | 0.016603 | -0.00044851 | -0.082397 | -0.19226 | 0.004578 | -0.004578 | 0.13275 | 0.059509 | 0.004578 | 0.059509 | -0.10529 | 0.018311 | 0.073242 | 0.15564 | 0.09613 | 0.14191 | 0.14649 | -121.7194 | -121.5317 | 0.27466 | 0.14649 | 0.20142 | 0 | 0.054931 | 0.16022 | -121.6324 | -121.4539 | 0.29755 | 0.28381 | 0.23804 | 0.1236 | 0.077819 | 0.12817 | -0.009156 | 0.13733 | 0.054931 | -0.19684 | -0.1236 | -0.050354 | 0.036621 | -121.5225 | -121.5088 | 0.13733 | 0.21515 | 0.05951 | 0.20142
3721.1719 | 121.6736 | -0.16022 | 121.5775 | -0.0057221 | 6.9878 | 0.014761 | 0.022486 | 0.0030547 | -0.0027066 | -0.0032256 | -0.0059205 | 0.022766 | -1.4538 | -0.003121 | -0.0075452 | 0.016175 | 0.00061949 | -0.1236 | -0.16022 | -0.050354 | -0.13733 | -0.059509 | -0.13733 | -0.15564 | -0.16937 | -0.068665 | -0.009155 | -0.073242 | -0.050354 | -0.091553 | 0.018311 | 0.10986 | -121.7377 | -121.7148 | 0.10071 | 0.004577 | 0.022888 | -0.10529 | -0.086975 | 0.15106 | -121.6461 | -121.6507 | 0.10986 | 0.17853 | 0.068664 | 0.027466 | -0.082398 | -0.009155 | -0.086975 | -0.041199 | -0.064087 | -0.10986 | -0.05951 | 0 | 0.091552 | -121.6278 | -121.5866 | 0.022888 | 0.086975 | 0.036621 | -0.009156
3722.9531 | 121.7331 | -0.16937 | 121.5958 | -0.013352 | 6.9863 | 0.014761 | 0.023127 | 0.0011321 | -0.0046292 | -0.0010894 | -0.0089723 | 0.019989 | -1.451 | 0.0022196 | -0.0032728 | 0.014039 | -0.0013031 | -0.14191 | -0.14191 | -0.054932 | -0.13733 | -0.032043 | -0.082397 | -0.1236 | -0.14648 | -0.082397 | -0.022888 | -0.054932 | -0.004578 | -0.045776 | 0.041199 | 0.11444 | -121.7377 | -121.7331 | 0.13733 | 0.045777 | 0.086976 | -0.068664 | -0.027465 | 0.14649 | -121.6782 | -121.6507 | 0.16479 | 0.21057 | 0.1236 | 0.064087 | -0.022888 | 0.022889 | -0.082397 | 0.01831 | -0.032044 | -0.086975 | -0.059509 | 0.027466 | 0.086976 | -121.6507 | -121.6187 | 0.032044 | 0.11444 | 0.027466 | 0.022889
3724.6719 | 121.7697 | -0.13733 | 121.5546 | -0.013352 | 6.9857 | 0.015402 | 0.021845 | -0.0016449 | -0.002493 | 0.00040597 | -0.0028687 | 0.018707 | -1.4521 | 0.00093783 | -0.0051954 | 0.015748 | 0.00083309 | -0.09613 | -0.1831 | -0.004578 | -0.068665 | 0.068665 | -0.022888 | -0.059509 | -0.022888 | -0.10529 | 0 | 0.027466 | 0.054932 | 0.022888 | 0.086975 | 0.13275 | -121.7377 | -121.6232 | 0.20599 | 0.07782 | 0.11444 | -0.054931 | -0.01831 | 0.13733 | -121.6599 | -121.5271 | 0.19226 | 0.2243 | 0.16022 | 0.086975 | 0.022888 | 0.073243 | -0.064087 | 0.054932 | 0.027466 | -0.17853 | -0.10529 | -0.045776 | 0.032043 | -121.5591 | -121.5546 | 0.068664 | 0.16479 | 0.041199 | 0.11444
3726.4375 | 121.6965 | -0.16937 | 121.6049 | -0.0057221 | 6.9861 | 0.013266 | 0.02334 | -0.0033539 | -0.0027066 | 0.0019012 | -0.0059205 | 0.02127 | -1.451 | -0.0039756 | -0.0075452 | 0.014894 | -0.00087591 | -0.11444 | -0.16479 | -0.041199 | -0.1236 | -0.027466 | -0.11902 | -0.13733 | -0.1236 | -0.073242 | -0.022888 | -0.045776 | -0.004578 | -0.064087 | 0.036621 | 0.12817 | -121.7697 | -121.7285 | 0.14191 | 0.032044 | 0.050354 | -0.09613 | -0.07782 | 0.14649 | -121.6782 | -121.6507 | 0.16479 | 0.20599 | 0.10529 | 0.059509 | -0.041199 | 0.013733 | -0.082397 | 0.01831 | -0.022888 | -0.1236 | -0.050354 | 0.004578 | 0.096131 | -121.6461 | -121.6278 | 0.045777 | 0.1236 | 0.054932 | 0.045777
3728.2188 | 121.6965 | -0.17853 | 121.5866 | -0.0057221 | 6.9848 | 0.014761 | 0.021418 | -0.0016449 | -0.0027066 | -0.0045074 | -0.0059205 | 0.022125 | -1.4538 | 0.0032876 | -0.0032728 | 0.014466 | -0.00066231 | -0.16479 | -0.15106 | -0.045776 | -0.16937 | -0.10071 | -0.14191 | -0.15106 | -0.16479 | -0.068665 | -0.022888 | -0.064087 | -0.018311 | -0.10071 | 0.032043 | 0.13275 | -121.7377 | -121.756 | 0.07782 | 0.027466 | 0.036621 | -0.10529 | -0.096131 | 0.15564 | -121.6553 | -121.6507 | 0.16022 | 0.21057 | 0.07782 | 0.054931 | -0.07782 | -0.054932 | -0.1236 | 0.004577 | -0.041199 | -0.10529 | -0.045777 | 0.027466 | 0.10986 | -121.6324 | -121.6095 | 0.009155 | 0.11444 | 0.013733 | 0.013733
3730 | 121.6873 | -0.19226 | 121.6003 | -0.013352 | 6.9889 | 0.014334 | 0.024622 | 0.0032685 | -0.0029202 | -0.00023503 | -0.0028687 | 0.020202 | -1.451 | -0.0035482 | -0.0092542 | 0.015107 | 0.0012603 | -0.16022 | -0.16022 | -0.045776 | -0.16937 | -0.086975 | -0.15106 | -0.16937 | -0.1831 | -0.059509 | -0.027466 | -0.064087 | -0.054932 | -0.086975 | 0.036621 | 0.14648 | -121.7606 | -121.7697 | 0.10529 | 0.022888 | 0.041199 | -0.1236 | -0.10529 | 0.16479 | -121.6599 | -121.6644 | 0.13733 | 0.22888 | 0.10529 | 0.064087 | -0.059509 | -0.041199 | -0.1236 | -0.027466 | -0.036621 | -0.11444 | -0.032043 | 0.032044 | 0.13275 | -121.6461 | -121.6278 | 0.022888 | 0.12817 | 0.032044 | 0.009156
3731.7344 | 121.7148 | -0.18768 | 121.6095 | -0.020981 | 6.987 | 0.015189 | 0.022272 | 0.00070491 | -0.0014248 | -0.00087583 | -0.0059205 | 0.020843 | -1.4546 | 0.0011514 | -0.0056226 | 0.014253 | 0.0016877 | -0.14648 | -0.16022 | -0.022888 | -0.15106 | -0.054932 | -0.1236 | -0.15564 | -0.14648 | -0.07782 | -0.018311 | -0.064087 | -0.045776 | -0.091553 | 0.018311 | 0.16479 | -121.7697 | -121.7606 | 0.13275 | 0.032043 | 0.064087 | -0.13275 | -0.10071 | 0.16937 | -121.6873 | -121.6736 | 0.14191 | 0.20599 | 0.09613 | 0.036622 | -0.073242 | -0.032044 | -0.12817 | -0.027465 | -0.045776 | -0.13733 | -0.059509 | 0.027466 | 0.10986 | -121.6324 | -121.6278 | 0.036621 | 0.1236 | 0.041199 | 0.041199
3733.5 | 121.7789 | -0.16022 | 121.6049 | -0.0057221 | 6.9868 | 0.013052 | 0.021204 | -0.0027131 | -0.002493 | -0.0032256 | -0.0059205 | 0.019989 | -1.4525 | -0.00055757 | -0.0066906 | 0.013826 | 0.0027557 | -0.16937 | -0.16937 | -0.050354 | -0.15106 | -0.059509 | -0.13733 | -0.14191 | -0.1236 | -0.068665 | -0.041199 | -0.009155 | 0.004578 | -0.050354 | 0.064087 | 0.10986 | -121.7743 | -121.756 | 0.10071 | 0.01831 | 0.022888 | -0.091553 | -0.086975 | 0.11902 | -121.6736 | -121.6141 | 0.16479 | 0.2243 | 0.10986 | 0.10529 | -0.009155 | -0.009155 | -0.10071 | 0.045777 | 0.032044 | -0.11902 | -0.027466 | -0.009156 | 0.091552 | -121.6553 | -121.6461 | 0.009155 | 0.15106 | -0.009156 | 0.036621
3735.2812 | 121.756 | -0.1831 | 121.6141 | -0.0057221 | 6.9861 | 0.011343 | 0.021845 | -0.00079049 | -0.002493 | -0.00044863 | -0.012024 | 0.018707 | -1.4531 | -0.003762 | -0.0086132 | 0.014894 | 0.0033967 | -0.13275 | -0.19226 | -0.036621 | -0.11444 | 0.013733 | -0.045776 | -0.091553 | -0.10529 | -0.068665 | -0.032043 | -0.045776 | -0.004578 | -0.045776 | 0.032043 | 0.14648 | -121.8063 | -121.7285 | 0.19684 | 0.091552 | 0.13733 | -0.054932 | -0.009155 | 0.15106 | -121.6827 | -121.6599 | 0.17853 | 0.21515 | 0.13733 | 0.064086 | -0.013733 | 0.050354 | -0.07782 | 0.027465 | -0.013733 | -0.15564 | -0.036622 | -0.009156 | 0.11444 | -121.6507 | -121.6461 | 0.068664 | 0.13733 | 0.050354 | 0.077819
3737.0156 | 121.7651 | -0.17853 | 121.6187 | -0.013352 | 6.9904 | 0.012625 | 0.023768 | 0.00027771 | -0.0012112 | -0.0015166 | -0.0059205 | 0.019775 | -1.4548 | 0.0020058 | -0.0086132 | 0.013612 | 0.0010467 | -0.1236 | -0.18768 | -0.027466 | -0.11902 | 0 | -0.086975 | -0.11902 | -0.082397 | -0.086975 | -0.004578 | -0.041199 | 0.009155 | -0.050354 | 0.045776 | 0.15106 | -121.8063 | -121.7377 | 0.17853 | 0.059509 | 0.091553 | -0.091553 | -0.059509 | 0.17395 | -121.7056 | -121.6599 | 0.18768 | 0.2243 | 0.12817 | 0.050354 | -0.045776 | 0.027466 | -0.091553 | 0.013733 | -0.036621 | -0.16022 | -0.082397 | -0.009155 | 0.091553 | -121.6461 | -121.6232 | 0.059509 | 0.13733 | 0.054932 | 0.096131
3738.7969 | 121.7926 | -0.16022 | 121.6232 | -0.020981 | 6.9861 | 0.01113 | 0.022059 | -0.00079049 | -0.001852 | -2.1434e-05 | -0.0028687 | 0.020416 | -1.4516 | 0.0024332 | -0.0066906 | 0.016603 | 0.0010467 | -0.1236 | -0.18768 | -0.045776 | -0.10986 | 0 | -0.082397 | -0.10071 | -0.064087 | -0.082397 | -0.004578 | -0.009155 | 0.032043 | -0.018311 | 0.068665 | 0.11444 | -121.8109 | -121.7331 | 0.16022 | 0.059509 | 0.07782 | -0.054932 | -0.036621 | 0.15564 | -121.7056 | -121.6324 | 0.19226 | 0.22888 | 0.14191 | 0.073243 | -0.013733 | 0.045776 | -0.064087 | 0.036621 | -0.004577 | -0.14191 | -0.077819 | -0.027466 | 0.07782 | -121.669 | -121.6278 | 0.050354 | 0.15106 | 0.036621 | 0.09613
3740.5 | 121.8796 | -0.13733 | 121.5912 | 0.0019074 | 6.987 | 0.012625 | 0.021845 | 0.0026275 | -0.0048428 | -0.00044863 | -0.0059205 | 0.019348 | -1.4531 | 0.0017922 | -0.0026318 | 0.015962 | 0.0023285 | -0.10986 | -0.21515 | -0.004578 | -0.068665 | 0.054932 | -0.036621 | -0.059509 | 0.004578 | -0.11902 | 0.018311 | 0.068665 | 0.10986 | 0.064087 | 0.15564 | 0.13275 | -121.8063 | -121.6599 | 0.19226 | 0.07782 | 0.10071 | -0.054931 | -0.032043 | 0.15564 | -121.7102 | -121.5225 | 0.24719 | 0.29297 | 0.20142 | 0.13733 | 0.045776 | 0.05951 | -0.064087 | 0.091552 | 0.050354 | -0.21057 | -0.13733 | -0.07782 | 0.01831 | -121.5958 | -121.5729 | 0.068664 | 0.20599 | 0.027466 | 0.14191
3742.2812 | 121.7651 | -0.1831 | 121.6599 | -0.0057221 | 6.9838 | 0.011771 | 0.019922 | -0.0035675 | -0.0029202 | -0.00023503 | -0.0059205 | 0.018921 | -1.4531 | 0.0039286 | -0.01139 | 0.012117 | -0.0049347 | -0.16022 | -0.18768 | -0.050354 | -0.15564 | -0.041199 | -0.091553 | -0.13733 | -0.13275 | -0.064087 | -0.022888 | -0.073242 | -0.013733 | -0.045776 | 0.013733 | 0.13275 | -121.8475 | -121.8155 | 0.14191 | 0.045776 | 0.091552 | -0.086975 | -0.041199 | 0.16022 | -121.7239 | -121.7331 | 0.16937 | 0.19684 | 0.13733 | 0.036621 | -0.022888 | 0.009155 | -0.10529 | 0.009155 | -0.050354 | -0.13733 | -0.041199 | -0.004578 | 0.11902 | -121.7102 | -121.6827 | 0.027465 | 0.10986 | 0.022888 | 0.050354
3744.0469 | 121.7697 | -0.1831 | 121.6599 | -0.0057221 | 6.9855 | 0.0098479 | 0.021845 | -0.0029267 | -0.0022794 | -0.0034392 | -0.0059205 | 0.019775 | -1.4525 | -0.0016256 | -0.011177 | 0.014894 | 0.0014741 | -0.18768 | -0.19226 | -0.045776 | -0.16022 | -0.045776 | -0.10071 | -0.13275 | -0.15106 | -0.059509 | -0.032043 | -0.068665 | -0.009155 | -0.041199 | 0.018311 | 0.13733 | -121.8521 | -121.8201 | 0.13733 | 0.050354 | 0.082397 | -0.086975 | -0.054932 | 0.15106 | -121.7194 | -121.7285 | 0.17395 | 0.20142 | 0.14191 | 0.050354 | -0.009156 | 0 | -0.11444 | 0.022888 | -0.036622 | -0.14648 | -0.027466 | -0.009156 | 0.1236 | -121.7056 | -121.6919 | 0.022888 | 0.11444 | -0.004578 | 0.032043
3745.7812 | 121.7926 | -0.19226 | 121.6232 | -0.0057221 | 6.9859 | 0.011984 | 0.023554 | -0.00036309 | -0.003561 | -0.00023503 | -0.0089723 | 0.021911 | -1.4529 | 0.0015786 | -0.0045544 | 0.014894 | 0.0010467 | -0.16937 | -0.17853 | -0.050354 | -0.17395 | -0.07782 | -0.16022 | -0.15106 | -0.13733 | -0.064087 | -0.018311 | -0.032043 | -0.018311 | -0.07782 | 0.050354 | 0.14191 | -121.8018 | -121.7972 | 0.11444 | 0.041199 | 0.032044 | -0.10071 | -0.10986 | 0.17395 | -121.6873 | -121.6553 | 0.17395 | 0.24261 | 0.11444 | 0.068665 | -0.059509 | -0.027466 | -0.1236 | 0 | -0.013732 | -0.12817 | -0.045776 | 0.013733 | 0.12817 | -121.6736 | -121.6415 | 0.018311 | 0.16022 | 0.022888 | 0.054932
3747.5625 | 121.7834 | -0.20142 | 121.6644 | -0.013352 | 6.985 | 0.012198 | 0.019922 | 0.0013459 | -0.0048428 | -2.1434e-05 | -0.0028687 | 0.019775 | -1.4553 | -0.0016256 | -0.0086132 | 0.012758 | 0.0014741 | -0.13733 | -0.20142 | -0.036621 | -0.1236 | 0.004578 | -0.059509 | -0.10071 | -0.10071 | -0.073242 | -0.004578 | -0.059509 | 0.013733 | -0.032043 | 0.027466 | 0.1648 | -121.8658 | -121.788 | 0.20599 | 0.10071 | 0.14191 | -0.064087 | -0.022888 | 0.19684 | -121.7377 | -121.7239 | 0.21515 | 0.22888 | 0.16937 | 0.032044 | -0.027465 | 0.041199 | -0.086975 | 0.018311 | -0.054931 | -0.1648 | -0.068664 | 0 | 0.12817 | -121.701 | -121.669 | 0.07782 | 0.14191 | 0.064087 | 0.10071
3749.3438 | 121.8338 | -0.16022 | 121.6644 | -0.0057221 | 6.987 | 0.013266 | 0.025263 | -0.00014949 | -0.003561 | 0.00019217 | -0.0028687 | 0.019989 | -1.4508 | -0.00077117 | -0.0083996 | 0.013612 | -0.00066231 | -0.12817 | -0.19226 | -0.036621 | -0.091553 | 0.004578 | -0.073242 | -0.10986 | -0.064087 | -0.068665 | -0.018311 | -0.009155 | 0.050354 | -0.009155 | 0.068665 | 0.1236 | -121.8567 | -121.756 | 0.16479 | 0.050354 | 0.086975 | -0.073242 | -0.036621 | 0.14191 | -121.7331 | -121.6736 | 0.21057 | 0.22888 | 0.15106 | 0.086976 | 0.009156 | 0.041199 | -0.054932 | 0.068665 | 0.009156 | -0.15564 | -0.050354 | -0.032044 | 0.091552 | -121.701 | -121.6827 | 0.068664 | 0.15106 | 0.032043 | 0.09613
3751.0781 | 121.8338 | -0.16937 | 121.6599 | -0.0057221 | 6.9878 | 0.010062 | 0.023127 | -0.0037811 | -0.0022794 | -2.1434e-05 | -0.0059205 | 0.021484 | -1.4531 | -0.0024802 | -0.006477 | 0.015535 | -2.1314e-05 | -0.16479 | -0.19226 | -0.050354 | -0.14648 | -0.036621 | -0.09613 | -0.1236 | -0.11444 | -0.059509 | -0.027466 | -0.022888 | 0.027466 | -0.022888 | 0.059509 | 0.11902 | -121.8521 | -121.8063 | 0.13275 | 0.045777 | 0.073243 | -0.073242 | -0.045776 | 0.14191 | -121.7194 | -121.6827 | 0.19684 | 0.22888 | 0.14649 | 0.086975 | 0.004578 | 0.013733 | -0.09613 | 0.054932 | 0.004578 | -0.14191 | -0.032043 | -0.022888 | 0.10986 | -121.7102 | -121.6873 | 0.022889 | 0.14649 | 0.004578 | 0.054932
3752.8594 | 121.7926 | -0.20142 | 121.6827 | -0.013352 | 6.985 | 0.010703 | 0.021845 | -0.0012177 | -0.002493 | 0.00040597 | -0.0028687 | 0.019775 | -1.4531 | 0.0056374 | -0.0090406 | 0.011903 | -0.00023491 | -0.16479 | -0.18768 | -0.041199 | -0.16022 | -0.036621 | -0.10071 | -0.13275 | -0.14648 | -0.064087 | -0.027466 | -0.068665 | -0.004578 | -0.059509 | 0.022888 | 0.16022 | -121.8704 | -121.843 | 0.1648 | 0.068665 | 0.10071 | -0.091552 | -0.059509 | 0.17395 | -121.7468 | -121.7514 | 0.19684 | 0.2243 | 0.14191 | 0.050354 | -0.032043 | 0.004578 | -0.11902 | 0.022888 | -0.041199 | -0.14648 | -0.036621 | 0.013733 | 0.13733 | -121.7239 | -121.7102 | 0.041199 | 0.13275 | 0.036621 | 0.054932
3754.5781 | 121.8979 | -0.15106 | 121.6415 | -0.0057221 | 6.9818 | 0.012412 | 0.022059 | 0.00070491 | -0.0046292 | -0.001944 | -0.0028687 | 0.02063 | -1.4529 | 0.0024332 | -0.0034864 | 0.014039 | 0.0012603 | -0.15106 | -0.21057 | -0.022888 | -0.11444 | 0 | -0.068665 | -0.082397 | -0.073242 | -0.09613 | -0.018311 | 0.004578 | 0.064087 | 0.022888 | 0.10071 | 0.12817 | -121.8521 | -121.756 | 0.15106 | 0.068665 | 0.082397 | -0.059509 | -0.045777 | 0.13275 | -121.7377 | -121.637 | 0.21515 | 0.25177 | 0.17395 | 0.11902 | 0.041199 | 0.022888 | -0.091553 | 0.082398 | 0.022889 | -0.18768 | -0.077819 | -0.059509 | 0.054932 | -121.6644 | -121.6599 | 0.036621 | 0.15564 | 0 | 0.07782
3756.3438 | 121.9162 | -0.14191 | 121.6599 | -0.0057221 | 6.9853 | 0.0096343 | 0.019282 | -0.0010041 | -0.0029202 | -0.00087583 | -0.0059205 | 0.017425 | -1.4529 | 0.008201 | -0.007118 | 0.016175 | -0.00087591 | -0.13275 | -0.2243 | -0.022888 | -0.086975 | 0.032043 | -0.041199 | -0.054932 | -0.032043 | -0.10529 | 0 | 0.032043 | 0.091553 | 0.054932 | 0.1236 | 0.11902 | -121.8842 | -121.7468 | 0.17395 | 0.086975 | 0.10071 | -0.032044 | -0.018311 | 0.14191 | -121.7651 | -121.6278 | 0.23346 | 0.2655 | 0.19684 | 0.1236 | 0.054932 | 0.054931 | -0.064087 | 0.091553 | 0.032043 | -0.20142 | -0.10529 | -0.082397 | 0.036621 | -121.6827 | -121.6599 | 0.054932 | 0.17395 | 0.009156 | 0.10986
3758.125 | 121.9574 | -0.15106 | 121.6461 | -0.013352 | 6.9855 | 0.011771 | 0.022059 | -0.0010041 | -0.0029202 | -0.003012 | -0.0028687 | 0.019775 | -1.454 | -0.0016256 | -0.0051954 | 0.015962 | 0.0012603 | -0.11444 | -0.19684 | -0.022888 | -0.050354 | 0.068665 | 0.004578 | -0.022888 | 0.032043 | -0.11902 | 0.004578 | 0.064087 | 0.12817 | 0.086975 | 0.1236 | 0.12817 | -121.843 | -121.6965 | 0.21973 | 0.12817 | 0.15564 | 0 | 0.027466 | 0.15564 | -121.7651 | -121.582 | 0.27924 | 0.27466 | 0.23804 | 0.11902 | 0.082397 | 0.091553 | -0.027466 | 0.1236 | 0.059509 | -0.17395 | -0.1236 | -0.045776 | 0.032043 | -121.669 | -121.6415 | 0.10071 | 0.21515 | 0.036621 | 0.18311
3759.8438 | 121.8109 | -0.17395 | 121.6782 | -0.020981 | 6.9883 | 0.012625 | 0.022486 | -0.0018585 | -0.003561 | -0.001944 | 0.00018312 | 0.02127 | -1.4519 | 0.0060648 | -0.0045544 | 0.016389 | 0.0040375 | -0.14648 | -0.1831 | -0.054932 | -0.15564 | -0.091553 | -0.15106 | -0.19226 | -0.17853 | -0.064087 | -0.027466 | -0.068665 | -0.054932 | -0.11444 | 0.022888 | 0.11902 | -121.8613 | -121.8338 | 0.082397 | -0.018311 | 0.022888 | -0.13733 | -0.09613 | 0.14648 | -121.7422 | -121.7468 | 0.11902 | 0.19684 | 0.059509 | 0.050354 | -0.086975 | -0.036621 | -0.10071 | -0.027466 | -0.041199 | -0.12817 | -0.036621 | -0.009155 | 0.10986 | -121.7331 | -121.7056 | 0.01831 | 0.10528 | 0.027466 | -0.004578
3761.625 | 121.9254 | -0.15106 | 121.6782 | -0.013352 | 6.9855 | 0.011557 | 0.019495 | 0.0011321 | -0.0027066 | -0.001303 | 0.00018312 | 0.017425 | -1.4529 | -0.0035482 | -0.0086132 | 0.016389 | 0.00040589 | -0.10071 | -0.22888 | -0.004578 | -0.009155 | 0.10071 | -0.004578 | -0.032043 | 0.004578 | -0.10986 | 0.009155 | 0.059509 | 0.11902 | 0.07782 | 0.12817 | 0.14648 | -121.907 | -121.6873 | 0.25177 | 0.11902 | 0.14648 | -0.027465 | 0 | 0.16022 | -121.788 | -121.6187 | 0.27008 | 0.27924 | 0.22888 | 0.11902 | 0.068665 | 0.10529 | -0.004577 | 0.10986 | 0.050354 | -0.2243 | -0.11902 | -0.07782 | 0.041199 | -121.6827 | -121.669 | 0.14191 | 0.21057 | 0.050354 | 0.15564
3763.4062 | 121.9528 | -0.12817 | 121.6553 | -0.013352 | 6.9844 | 0.013907 | 0.022059 | -0.0016449 | -0.0039884 | -0.0027984 | -0.0059205 | 0.019561 | -1.4538 | 0.010124 | -0.0069044 | 0.014253 | 0.0038239 | -0.12817 | -0.20599 | -0.018311 | -0.09613 | 0.027466 | -0.041199 | -0.068665 | -0.036621 | -0.10529 | 0.013733 | 0.045776 | 0.10071 | 0.064087 | 0.1236 | 0.10986 | -121.8613 | -121.7514 | 0.15564 | 0.059509 | 0.086975 | -0.050354 | -0.022888 | 0.14191 | -121.7606 | -121.6095 | 0.22888 | 0.25177 | 0.19226 | 0.10986 | 0.050354 | 0.045777 | -0.077819 | 0.086975 | 0.032043 | -0.18768 | -0.11902 | -0.07782 | 0.022888 | -121.6736 | -121.6415 | 0.032044 | 0.17395 | 0 | 0.091553
3765.125 | 121.9711 | -0.14191 | 121.6873 | -0.013352 | 6.9865 | 0.0096343 | 0.018641 | -0.0033539 | -0.0033474 | 0.00061957 | -0.0028687 | 0.020202 | -1.4516 | 0.0017922 | -0.0079724 | 0.015748 | 0.0010467 | -0.09613 | -0.23346 | -0.013733 | -0.018311 | 0.10071 | 0.013733 | -0.032043 | 0.032043 | -0.091553 | 0.013733 | 0.036621 | 0.12817 | 0.091553 | 0.12817 | 0.12817 | -121.9208 | -121.7056 | 0.24262 | 0.10986 | 0.15564 | -0.01831 | 0.027466 | 0.15564 | -121.7789 | -121.6507 | 0.27008 | 0.27008 | 0.23346 | 0.11444 | 0.07782 | 0.11444 | -0.004578 | 0.11444 | 0.022888 | -0.21973 | -0.10529 | -0.091552 | 0.050354 | -121.701 | -121.6736 | 0.1236 | 0.17853 | 0.045777 | 0.17395
3766.9062 | 121.8567 | -0.19226 | 121.6965 | -0.013352 | 6.9861 | 0.011343 | 0.020563 | -0.0020721 | -0.0027066 | -0.0042938 | -0.0059205 | 0.020416 | -1.4546 | -0.00034397 | -0.006477 | 0.016389 | 0.0010467 | -0.11902 | -0.21515 | -0.013733 | -0.09613 | 0 | -0.064087 | -0.10071 | -0.10986 | -0.07782 | -0.009155 | -0.050354 | 0 | -0.032043 | 0.018311 | 0.17853 | -121.9116 | -121.7926 | 0.19226 | 0.091553 | 0.12817 | -0.086975 | -0.050354 | 0.18311 | -121.7743 | -121.7468 | 0.19226 | 0.21057 | 0.16022 | 0.027466 | -0.022888 | 0.013733 | -0.082397 | 0.009155 | -0.041199 | -0.20142 | -0.068665 | -0.022888 | 0.11444 | -121.7102 | -121.7056 | 0.096131 | 0.14191 | 0.073242 | 0.082398
3768.6875 | 121.9803 | -0.16022 | 121.6873 | -0.020981 | 6.9865 | 0.013052 | 0.019282 | 0.0013459 | -0.0037746 | 0.0010468 | -0.0059205 | 0.018707 | -1.454 | 0.0056374 | -0.005409 | 0.015962 | 0.0014741 | -0.1236 | -0.19684 | -0.032043 | -0.054932 | 0.059509 | -0.004578 | -0.041199 | -0.004578 | -0.10071 | 0 | 0.064087 | 0.10529 | 0.07782 | 0.13275 | 0.12817 | -121.8842 | -121.7422 | 0.21973 | 0.11902 | 0.15564 | -0.009156 | 0.027465 | 0.16022 | -121.788 | -121.6232 | 0.2655 | 0.29297 | 0.23804 | 0.13275 | 0.07782 | 0.091552 | -0.022889 | 0.10529 | 0.064087 | -0.1648 | -0.10071 | -0.036621 | 0.059509 | -121.7194 | -121.6873 | 0.10528 | 0.2243 | 0.036621 | 0.15564
3770.4531 | 121.9208 | -0.15564 | 121.6919 | -0.013352 | 6.9861 | 0.011343 | 0.021631 | 0.0043365 | -0.0033474 | -0.0027984 | -0.0028687 | 0.017425 | -1.4525 | -0.0046164 | -0.0060498 | 0.01468 | 0.0059601 | -0.13733 | -0.21057 | -0.027466 | -0.10986 | 0 | -0.073242 | -0.09613 | -0.07782 | -0.10529 | -0.009155 | -0.004578 | 0.027466 | -0.018311 | 0.082397 | 0.12817 | -121.9025 | -121.8018 | 0.15564 | 0.05951 | 0.082398 | -0.068664 | -0.045776 | 0.14649 | -121.7972 | -121.6965 | 0.18311 | 0.23804 | 0.13733 | 0.091552 | -0.009156 | 0.027466 | -0.082397 | 0.036621 | 0.004577 | -0.18311 | -0.096131 | -0.054931 | 0.050354 | -121.7194 | -121.7011 | 0.045777 | 0.15106 | 0.018311 | 0.07782
3772.1875 | 121.8979 | -0.17395 | 121.7194 | -0.0057221 | 6.9863 | 0.01113 | 0.022059 | 0.0011321 | -0.0044156 | -0.00044863 | -0.0059205 | 0.024047 | -1.4531 | -0.00013037 | -0.006477 | 0.015321 | 0.0027557 | -0.12817 | -0.20142 | -0.050354 | -0.091553 | 0.004578 | -0.082397 | -0.10529 | -0.068665 | -0.059509 | -0.013733 | -0.013733 | 0.036621 | -0.009155 | 0.068665 | 0.1236 | -121.9208 | -121.8109 | 0.17853 | 0.068664 | 0.091553 | -0.054932 | -0.032043 | 0.16022 | -121.7789 | -121.7331 | 0.21057 | 0.24261 | 0.16479 | 0.082398 | 0.004578 | 0.054932 | -0.041199 | 0.050354 | 0 | -0.15106 | -0.045776 | -0.027466 | 0.11444 | -121.7697 | -121.7331 | 0.082397 | 0.16022 | 0.045776 | 0.10528
3773.9844 | 121.9894 | -0.14191 | 121.7056 | -0.0057221 | 6.9857 | 0.011557 | 0.018213 | -0.0027131 | -0.0033474 | -0.00087583 | -0.0028687 | 0.020843 | -1.4516 | -0.00034397 | -0.0079724 | 0.013612 | -0.0015167 | -0.10986 | -0.2243 | -0.018311 | -0.022888 | 0.10986 | 0.004578 | -0.004578 | 0.036621 | -0.10071 | 0 | 0.064087 | 0.1236 | 0.082397 | 0.1236 | 0.1236 | -121.9299 | -121.7285 | 0.25177 | 0.13733 | 0.14649 | 0.013733 | 0.022889 | 0.14191 | -121.8063 | -121.6415 | 0.2655 | 0.2655 | 0.2243 | 0.1236 | 0.082397 | 0.12817 | -0.004577 | 0.1236 | 0.064087 | -0.20599 | -0.10071 | -0.082397 | 0.041199 | -121.7239 | -121.7056 | 0.11902 | 0.20599 | 0.032044 | 0.17853
3775.7656 | 121.9986 | -0.12817 | 121.701 | -0.0057221 | 6.9861 | 0.011984 | 0.022272 | 0.0041229 | -0.0031338 | -0.0010894 | -0.0059205 | 0.019775 | -1.4557 | 0.0024332 | -0.0028454 | 0.017457 | 0.0023285 | -0.059509 | -0.23346 | -0.013733 | -0.032043 | 0.064087 | -0.027466 | -0.064087 | 0 | -0.11902 | 0.018311 | 0.073242 | 0.09613 | 0.054932 | 0.13733 | 0.11444 | -121.9345 | -121.7331 | 0.19226 | 0.064087 | 0.10071 | -0.050354 | -0.013733 | 0.14649 | -121.8201 | -121.6278 | 0.2243 | 0.2655 | 0.18311 | 0.11902 | 0.036621 | 0.07782 | -0.01831 | 0.077819 | 0.054931 | -0.21973 | -0.13733 | -0.10528 | 0.009155 | -121.7148 | -121.6827 | 0.096131 | 0.20142 | 0.068665 | 0.12817
3777.4688 | 121.9711 | -0.13275 | 121.7285 | -0.013352 | 6.9844 | 0.010489 | 0.018854 | -0.00014949 | -0.0033474 | -0.0015166 | -0.0059205 | 0.020202 | -1.4531 | 0.0011514 | -0.0083996 | 0.015535 | -0.0015167 | -0.11444 | -0.24261 | -0.018311 | -0.009155 | 0.10071 | 0.018311 | -0.018311 | 0.004578 | -0.09613 | 0.013733 | 0.041199 | 0.10986 | 0.082397 | 0.1236 | 0.11444 | -121.9711 | -121.7377 | 0.23346 | 0.11444 | 0.15106 | 0 | 0.036622 | 0.14648 | -121.8246 | -121.6873 | 0.24261 | 0.25635 | 0.21515 | 0.10986 | 0.068664 | 0.11902 | 0.009156 | 0.09613 | 0.027466 | -0.2243 | -0.10986 | -0.10986 | 0.036621 | -121.7468 | -121.7148 | 0.1236 | 0.17395 | 0.01831 | 0.13733
3779.2656 | 121.9528 | -0.15106 | 121.7331 | 0.0019074 | 6.9861 | 0.013693 | 0.021418 | 0.00049131 | -0.0029202 | 0.00019217 | -0.0089723 | 0.021057 | -1.4521 | -0.0022666 | -0.0079724 | 0.014253 | -2.1314e-05 | -0.14648 | -0.21515 | -0.013733 | -0.09613 | -0.004578 | -0.07782 | -0.086975 | -0.082397 | -0.10071 | -0.009155 | -0.009155 | 0.059509 | 0.022888 | 0.091553 | 0.13733 | -121.9482 | -121.8292 | 0.14648 | 0.064087 | 0.073242 | -0.073242 | -0.064087 | 0.14191 | -121.8338 | -121.7422 | 0.21057 | 0.24261 | 0.17395 | 0.10071 | 0.032043 | 0.009155 | -0.082397 | 0.068664 | 0 | -0.20142 | -0.091553 | -0.064087 | 0.050354 | -121.7468 | -121.7422 | 0.054932 | 0.14191 | 0.004578 | 0.068665
3781.0469 | 121.8475 | -0.19226 | 121.7514 | -0.0057221 | 6.9876 | 0.012839 | 0.025049 | 0.00070491 | -0.003561 | 0.0016876 | 0.00018312 | 0.022552 | -1.4527 | -0.0073936 | -0.0069044 | 0.011262 | -0.00087591 | -0.14191 | -0.20599 | -0.045776 | -0.13733 | -0.054932 | -0.13275 | -0.16479 | -0.13733 | -0.07782 | -0.027466 | -0.064087 | -0.041199 | -0.091553 | 0.018311 | 0.14648 | -121.9574 | -121.8887 | 0.13733 | 0.027466 | 0.05951 | -0.11902 | -0.086975 | 0.16479 | -121.8292 | -121.8155 | 0.15106 | 0.21057 | 0.10071 | 0.045777 | -0.064087 | -0.009156 | -0.091553 | -0.013733 | -0.036621 | -0.16022 | -0.050354 | -0.013733 | 0.11444 | -121.7972 | -121.7789 | 0.054932 | 0.12817 | 0.050354 | 0.054932
3782.8281 | 121.962 | -0.14191 | 121.7194 | -0.013352 | 6.9855 | 0.011771 | 0.021204 | 0.00091851 | -0.00035684 | 0.00040597 | -0.0028687 | 0.020202 | -1.4519 | -0.0016256 | -0.0066906 | 0.017244 | -0.0010895 | -0.13275 | -0.22888 | -0.013733 | -0.07782 | 0.059509 | -0.068665 | -0.073242 | -0.022888 | -0.10529 | -0.018311 | 0.004578 | 0.059509 | 0.009155 | 0.082397 | 0.12817 | -121.9482 | -121.7972 | 0.20142 | 0.068665 | 0.073242 | -0.059509 | -0.054932 | 0.1236 | -121.8246 | -121.7148 | 0.20142 | 0.2243 | 0.15106 | 0.10071 | 0.027466 | 0.073242 | -0.064087 | 0.07782 | 0.022889 | -0.21515 | -0.086975 | -0.086975 | 0.036621 | -121.7331 | -121.7377 | 0.064087 | 0.14649 | 0.009156 | 0.11902
3784.6094 | 121.8842 | -0.18768 | 121.7789 | -0.0057221 | 6.9891 | 0.013266 | 0.022272 | 0.00091851 | -0.002493 | -2.1434e-05 | -0.0028687 | 0.020416 | -1.4512 | 0.0054238 | -0.0075452 | 0.015748 | 0.0014741 | -0.12817 | -0.1831 | -0.036621 | -0.10986 | -0.032043 | -0.11444 | -0.13275 | -0.082397 | -0.091553 | -0.022888 | -0.045776 | -0.009155 | -0.068665 | 0.013733 | 0.15106 | -121.962 | -121.8887 | 0.15564 | 0.054932 | 0.073242 | -0.09613 | -0.07782 | 0.16479 | -121.8704 | -121.8246 | 0.17853 | 0.20142 | 0.11902 | 0.036621 | -0.045777 | 0.004578 | -0.073242 | 0.013733 | -0.022888 | -0.14648 | -0.068665 | 0.004578 | 0.09613 | -121.8155 | -121.8018 | 0.07782 | 0.14191 | 0.059509 | 0.10529
3786.3906 | 121.994 | -0.13275 | 121.7285 | -0.013352 | 6.9874 | 0.013052 | 0.023127 | 0.00091851 | -0.0027066 | -0.0015166 | -0.0059205 | 0.020843 | -1.4519 | 0.0020058 | -0.0032728 | 0.018312 | 0.0021149 | -0.13275 | -0.21973 | -0.013733 | -0.068665 | 0.041199 | -0.054932 | -0.086975 | -0.013733 | -0.10986 | -0.004578 | 0.050354 | 0.10529 | 0.036621 | 0.14191 | 0.11902 | -121.9482 | -121.7972 | 0.17395 | 0.045776 | 0.077819 | -0.073242 | -0.041199 | 0.12817 | -121.8384 | -121.6782 | 0.23804 | 0.27466 | 0.16937 | 0.14649 | 0.041199 | 0.054932 | -0.054932 | 0.10986 | 0.054932 | -0.20599 | -0.10529 | -0.086976 | 0.022888 | -121.7422 | -121.7331 | 0.064086 | 0.18311 | 0 | 0.11902
3788.1875 | 122.0123 | -0.13275 | 121.7285 | -0.013352 | 6.9848 | 0.011557 | 0.021204 | 0.0049773 | -0.0022794 | 0.002115 | -0.0028687 | 0.019348 | -1.4521 | -0.0058982 | -0.0041272 | 0.015962 | 0.00019229 | -0.12817 | -0.21057 | -0.018311 | -0.045776 | 0.041199 | -0.054932 | -0.059509 | -0.018311 | -0.10986 | -0.004578 | 0.059509 | 0.091553 | 0.041199 | 0.13733 | 0.11444 | -121.9391 | -121.7743 | 0.17395 | 0.073242 | 0.077819 | -0.041198 | -0.036621 | 0.12817 | -121.8384 | -121.669 | 0.2243 | 0.27008 | 0.17395 | 0.14191 | 0.045777 | 0.05951 | -0.027465 | 0.096131 | 0.064087 | -0.19226 | -0.10529 | -0.07782 | 0.022888 | -121.7468 | -121.7331 | 0.086975 | 0.19226 | 0.004577 | 0.11444
3789.9062 | 121.875 | -0.17853 | 121.7651 | -0.0057221 | 6.9859 | 0.013693 | 0.0227 | -0.00057689 | -0.003561 | -0.0010894 | 0.00018312 | 0.021057 | -1.4504 | -0.011452 | -0.0083996 | 0.015107 | -2.1314e-05 | -0.16937 | -0.1831 | -0.068665 | -0.16479 | -0.10986 | -0.16937 | -0.17853 | -0.20599 | -0.068665 | -0.036621 | -0.064087 | -0.050354 | -0.09613 | 0.018311 | 0.10986 | -121.9482 | -121.9299 | 0.068665 | 0 | 0.009155 | -0.10986 | -0.10071 | 0.14191 | -121.8338 | -121.8292 | 0.12817 | 0.19684 | 0.082398 | 0.054932 | -0.059509 | -0.041198 | -0.09613 | -0.013733 | -0.027466 | -0.11444 | -0.032044 | -0.004577 | 0.10986 | -121.8338 | -121.8018 | 0.013733 | 0.11444 | 0.009155 | -0.027466
3791.6875 | 122.0261 | -0.11444 | 121.7468 | -0.020981 | 6.9823 | 0.011557 | 0.018854 | 0.0013459 | -0.003561 | 0.00061957 | -0.0028687 | 0.019348 | -1.4525 | 0.0020058 | -0.0092542 | 0.015748 | 0.0046783 | -0.1236 | -0.22888 | -0.013733 | -0.018311 | 0.13733 | 0.013733 | -0.004578 | 0.036621 | -0.10071 | 0.004578 | 0.041199 | 0.1236 | 0.086975 | 0.1236 | 0.10071 | -121.9757 | -121.7651 | 0.25177 | 0.10986 | 0.12817 | 0.009155 | 0.027466 | 0.11902 | -121.8475 | -121.7056 | 0.23804 | 0.23804 | 0.20142 | 0.11902 | 0.082397 | 0.15106 | -0.004578 | 0.11902 | 0.036621 | -0.21515 | -0.10529 | -0.11444 | 0.013733 | -121.7606 | -121.7422 | 0.09613 | 0.15564 | -0.009155 | 0.15106
3793.4062 | 121.9162 | -0.17395 | 121.7834 | -0.013352 | 6.9859 | 0.010703 | 0.022486 | -0.0010041 | -0.002493 | -0.0034392 | 0.00018312 | 0.021057 | -1.4523 | 0.01226 | -0.0083996 | 0.015321 | -0.0025849 | -0.17395 | -0.17853 | -0.050354 | -0.16479 | -0.073242 | -0.17395 | -0.16022 | -0.14191 | -0.086975 | -0.027466 | -0.059509 | -0.041199 | -0.073242 | 0.045776 | 0.1236 | -121.962 | -121.9482 | 0.10071 | 0.013733 | 0 | -0.10986 | -0.1236 | 0.14648 | -121.8704 | -121.843 | 0.13275 | 0.21973 | 0.10071 | 0.073242 | -0.045776 | -0.022888 | -0.11444 | -0.013733 | -0.032043 | -0.12817 | -0.059509 | -0.004578 | 0.086975 | -121.8338 | -121.8109 | 0.009155 | 0.11444 | 0 | 0.032043
3795.2031 | 121.9162 | -0.1831 | 121.7926 | -0.020981 | 6.984 | 0.01113 | 0.022272 | 0.0032685 | -0.001852 | 0.00040597 | -0.0028687 | 0.021484 | -1.4514 | 0.0069192 | -0.0092542 | 0.015962 | 0.0027557 | -0.16479 | -0.17853 | -0.050354 | -0.17395 | -0.068665 | -0.16479 | -0.15564 | -0.15564 | -0.07782 | -0.032043 | -0.064087 | -0.032043 | -0.082397 | 0.032043 | 0.13275 | -121.9711 | -121.9666 | 0.11444 | 0.027465 | 0.01831 | -0.10529 | -0.11444 | 0.15106 | -121.8704 | -121.8567 | 0.15106 | 0.21515 | 0.10071 | 0.064086 | -0.050354 | -0.018311 | -0.1236 | 0 | -0.032044 | -0.12817 | -0.045777 | 0.004577 | 0.10528 | -121.843 | -121.8246 | 0.009155 | 0.11902 | 0.01831 | 0.027465
3796.9844 | 121.9894 | -0.14648 | 121.7834 | -0.013352 | 6.9848 | 0.011557 | 0.021418 | 0.00070491 | -0.0031338 | -0.0021576 | -0.0059205 | 0.018921 | -1.4551 | -0.0073936 | -0.007118 | 0.014253 | -0.00044851 | -0.16022 | -0.21057 | -0.018311 | -0.10529 | 0 | -0.082397 | -0.09613 | -0.07782 | -0.086975 | -0.013733 | -0.009155 | 0.050354 | 0.022888 | 0.09613 | 0.12817 | -121.994 | -121.8887 | 0.14648 | 0.050354 | 0.064087 | -0.077819 | -0.064086 | 0.13275 | -121.8704 | -121.7926 | 0.19684 | 0.24261 | 0.16937 | 0.10986 | 0.036621 | 0.018311 | -0.086975 | 0.064087 | 0.004578 | -0.19226 | -0.073242 | -0.064087 | 0.059509 | -121.8018 | -121.7972 | 0.041198 | 0.13733 | -0.013733 | 0.068664
3798.7031 | 121.9208 | -0.18768 | 121.8338 | -0.013352 | 6.9833 | 0.010703 | 0.02035 | -0.0039947 | -0.0033474 | -0.0038666 | -0.0089723 | 0.019989 | -1.4536 | -0.003121 | -0.010322 | 0.013185 | -0.0019439 | -0.18768 | -0.17853 | -0.054932 | -0.15564 | -0.064087 | -0.11444 | -0.12817 | -0.16022 | -0.064087 | -0.045776 | -0.082397 | -0.036621 | -0.073242 | 0.018311 | 0.13275 | -122.0123 | -121.9894 | 0.1236 | 0.059509 | 0.073242 | -0.073242 | -0.059509 | 0.14191 | -121.8979 | -121.9162 | 0.15106 | 0.20599 | 0.11444 | 0.064087 | -0.027466 | -0.009155 | -0.10071 | 0.009155 | -0.036621 | -0.1236 | -0.018311 | 0.009155 | 0.1236 | -121.8887 | -121.8796 | 0.032043 | 0.10529 | 0 | 0.027466
3800.4688 | 121.9254 | -0.17853 | 121.8201 | 0.0019074 | 6.9825 | 0.0087799 | 0.02035 | -0.0029267 | -0.0037746 | -0.003012 | -0.0059205 | 0.019775 | -1.4529 | -0.0097434 | -0.0090406 | 0.012117 | -0.0023713 | -0.15564 | -0.18768 | -0.041199 | -0.14191 | -0.036621 | -0.09613 | -0.13275 | -0.15106 | -0.054932 | -0.036621 | -0.068665 | -0.009155 | -0.059509 | 0 | 0.13733 | -122.0078 | -121.962 | 0.14191 | 0.045777 | 0.082398 | -0.091552 | -0.054931 | 0.14191 | -121.875 | -121.8887 | 0.16937 | 0.17853 | 0.11902 | 0.036621 | -0.022888 | 0.004578 | -0.10071 | 0.027466 | -0.032044 | -0.14648 | -0.018311 | -0.009155 | 0.1236 | -121.8613 | -121.8567 | 0.036621 | 0.10986 | 0.022888 | 0.027466
3802.25 | 121.9345 | -0.20599 | 121.8018 | -0.013352 | 6.984 | 0.010489 | 0.021418 | 0.0036957 | -0.0031338 | -0.001303 | -0.0059205 | 0.020843 | -1.4523 | -0.002053 | -0.0090406 | 0.013612 | -0.00066231 | -0.14191 | -0.21515 | -0.022888 | -0.11444 | -0.004578 | -0.073242 | -0.10529 | -0.10529 | -0.07782 | -0.004578 | -0.082397 | -0.018311 | -0.054932 | 0.022888 | 0.18311 | -122.0169 | -121.9162 | 0.20142 | 0.10071 | 0.13275 | -0.082398 | -0.050354 | 0.20142 | -121.8796 | -121.8842 | 0.18768 | 0.22888 | 0.15106 | 0.027466 | -0.050354 | 0.01831 | -0.091553 | -0.013733 | -0.077819 | -0.19226 | -0.073242 | -0.009155 | 0.12817 | -121.8246 | -121.8063 | 0.091553 | 0.1236 | 0.064087 | 0.10071
3803.9844 | 121.9482 | -0.14648 | 121.8201 | -0.0057221 | 6.9848 | 0.011343 | 0.023127 | -0.0035675 | -0.0037746 | -0.0010894 | -0.0028687 | 0.021484 | -1.4523 | -0.0076072 | -0.004768 | 0.013185 | -0.0036529 | -0.11902 | -0.19226 | -0.041199 | -0.11902 | -0.018311 | -0.10071 | -0.13275 | -0.10529 | -0.086975 | -0.022888 | -0.041199 | -0.009155 | -0.073242 | 0.036621 | 0.10529 | -122.0123 | -121.9391 | 0.12817 | 0.013733 | 0.045776 | -0.091552 | -0.059509 | 0.1236 | -121.907 | -121.8613 | 0.13733 | 0.18311 | 0.073242 | 0.059509 | -0.050354 | 0.022888 | -0.07782 | 0.013733 | -0.018311 | -0.15106 | -0.064087 | -0.045777 | 0.059509 | -121.8613 | -121.843 | 0.027465 | 0.10529 | 0.027465 | 0.041198
3805.7812 | 121.9345 | -0.20599 | 121.8063 | -0.013352 | 6.9842 | 0.010489 | 0.02035 | -0.0024995 | -0.0031338 | -0.0038666 | -0.0028687 | 0.021911 | -1.454 | -0.0041892 | -0.008827 | 0.012117 | 0.0036103 | -0.18768 | -0.19226 | -0.064087 | -0.16937 | -0.068665 | -0.091553 | -0.15106 | -0.15106 | -0.068665 | -0.041199 | -0.086975 | -0.022888 | -0.059509 | 0.027466 | 0.14191 | -121.9986 | -121.9757 | 0.13733 | 0.054932 | 0.11444 | -0.086975 | -0.027466 | 0.1648 | -121.875 | -121.8933 | 0.18311 | 0.23346 | 0.14649 | 0.068665 | -0.01831 | -0.004578 | -0.10529 | 0.018311 | -0.045776 | -0.12817 | -0.027466 | 0.013733 | 0.13733 | -121.8704 | -121.8475 | 0.036621 | 0.11902 | 0.018311 | 0.054932
3807.5 | 121.9437 | -0.1831 | 121.8155 | -0.0057221 | 6.9853 | 0.013266 | 0.023127 | 0.00027771 | -0.0031338 | 0.0010468 | -0.0028687 | 0.022552 | -1.4531 | 0.00029703 | -0.0039136 | 0.015535 | 0.0025421 | -0.14191 | -0.20599 | -0.045776 | -0.14191 | -0.045776 | -0.1236 | -0.12817 | -0.13733 | -0.07782 | -0.018311 | -0.050354 | -0.018311 | -0.086975 | 0.022888 | 0.13733 | -122.0215 | -121.9574 | 0.13733 | 0.054931 | 0.059509 | -0.082398 | -0.07782 | 0.16479 | -121.8933 | -121.8658 | 0.16479 | 0.20599 | 0.09613 | 0.041199 | -0.068664 | 0 | -0.096131 | 0 | -0.032043 | -0.16022 | -0.059509 | -0.022889 | 0.10528 | -121.8613 | -121.8338 | 0.041198 | 0.13275 | 0.041198 | 0.045776
3809.2812 | 122.0673 | -0.12817 | 121.7972 | -0.0057221 | 6.9821 | 0.011771 | 0.021631 | -0.0044221 | -0.0029202 | -0.001303 | -0.0059205 | 0.01828 | -1.4521 | -0.0046164 | -0.0058362 | 0.014894 | -0.0036529 | -0.12817 | -0.21057 | -0.022888 | -0.054932 | 0.054932 | -0.009155 | -0.045776 | -0.013733 | -0.10529 | 0 | 0.054932 | 0.1236 | 0.086975 | 0.12817 | 0.10529 | -122.0078 | -121.8521 | 0.18311 | 0.082398 | 0.11902 | -0.022888 | 0.013733 | 0.12817 | -121.9025 | -121.7422 | 0.25177 | 0.25635 | 0.21515 | 0.12817 | 0.086975 | 0.07782 | -0.032044 | 0.1236 | 0.054932 | -0.18768 | -0.10529 | -0.082397 | 0.022888 | -121.8201 | -121.7972 | 0.073242 | 0.18311 | 0 | 0.11444
3811.0625 | 121.9849 | -0.16022 | 121.7926 | -0.013352 | 6.9848 | 0.012412 | 0.024836 | 0.0032685 | -0.0033474 | -0.0017304 | -0.0028687 | 0.019989 | -1.4538 | -0.014016 | -0.005409 | 0.015748 | -0.0013031 | -0.1236 | -0.21057 | -0.045776 | -0.091553 | 0.009155 | -0.073242 | -0.11444 | -0.054932 | -0.082397 | -0.018311 | -0.004578 | 0.041199 | -0.018311 | 0.068665 | 0.11444 | -122.0032 | -121.8842 | 0.16937 | 0.045776 | 0.086975 | -0.068665 | -0.027466 | 0.14191 | -121.875 | -121.7972 | 0.20142 | 0.22888 | 0.14191 | 0.086976 | 0 | 0.054931 | -0.045777 | 0.05951 | 0.013733 | -0.1648 | -0.064086 | -0.050354 | 0.07782 | -121.8384 | -121.8109 | 0.068664 | 0.15564 | 0.036621 | 0.10528
3812.8594 | 121.9437 | -0.19226 | 121.8384 | -0.013352 | 6.9838 | 0.012839 | 0.021845 | 0.00091851 | -0.002493 | 0.0019012 | -0.0059205 | 0.021484 | -1.4529 | -0.003121 | -0.0058362 | 0.015748 | -0.00023491 | -0.14648 | -0.18768 | -0.050354 | -0.14648 | -0.059509 | -0.11902 | -0.16022 | -0.13733 | -0.068665 | -0.013733 | -0.068665 | -0.032043 | -0.086975 | 0.022888 | 0.14191 | -122.0261 | -121.9849 | 0.13275 | 0.032044 | 0.073242 | -0.10986 | -0.068665 | 0.17853 | -121.907 | -121.907 | 0.16022 | 0.21515 | 0.10529 | 0.036621 | -0.073242 | -0.009155 | -0.09613 | -0.01831 | -0.054932 | -0.13733 | -0.054932 | 0.004578 | 0.1236 | -121.8887 | -121.8521 | 0.045777 | 0.1236 | 0.045777 | 0.054932
3814.5625 | 121.9803 | -0.16937 | 121.8063 | -0.013352 | 6.9814 | 0.011557 | 0.02035 | -0.0063447 | -0.002493 | 0.001474 | -0.0059205 | 0.018493 | -1.4548 | 8.3226e-05 | -0.0075452 | 0.014039 | 0.0053193 | -0.1236 | -0.22888 | -0.009155 | -0.082397 | 0.045776 | -0.013733 | -0.064087 | -0.07782 | -0.086975 | -0.009155 | -0.022888 | 0.022888 | -0.013733 | 0.059509 | 0.16022 | -122.0352 | -121.8887 | 0.21515 | 0.10529 | 0.15564 | -0.054932 | -0.004578 | 0.16022 | -121.8933 | -121.8292 | 0.19226 | 0.22888 | 0.15564 | 0.068664 | -0.004578 | 0.054931 | -0.073242 | 0.032043 | -0.013733 | -0.21973 | -0.07782 | -0.059509 | 0.082398 | -121.8155 | -121.8155 | 0.086976 | 0.14649 | 0.045777 | 0.091553
3816.3438 | 122.0535 | -0.14191 | 121.8109 | -0.0057221 | 6.9842 | 0.0089935 | 0.021418 | 0.0022003 | -0.0048428 | -0.0010894 | -0.0028687 | 0.020416 | -1.4525 | 0.0035012 | -0.0032728 | 0.014894 | -0.00087591 | -0.14191 | -0.19226 | -0.054932 | -0.12817 | -0.018311 | -0.10986 | -0.11902 | -0.059509 | -0.10529 | 0 | 0.036621 | 0.054932 | 0.022888 | 0.11902 | 0.086975 | -122.0032 | -121.9391 | 0.1236 | 0.022888 | 0.032044 | -0.064087 | -0.054931 | 0.14191 | -121.9162 | -121.7743 | 0.19684 | 0.26093 | 0.16479 | 0.11902 | 0.022888 | 0.036621 | -0.073242 | 0.054932 | 0.036621 | -0.13733 | -0.10529 | -0.050354 | 0.036621 | -121.8658 | -121.8109 | 0.013733 | 0.17853 | 0 | 0.082398
3818.0469 | 121.9666 | -0.17853 | 121.8338 | -0.02861 | 6.9863 | 0.013266 | 0.019495 | -0.0010041 | -0.0039884 | -0.0015166 | 0.00018312 | 0.022339 | -1.4516 | -0.0056846 | -0.0073316 | 0.014466 | 0.00040589 | -0.17395 | -0.17395 | -0.059509 | -0.16479 | -0.07782 | -0.1236 | -0.13733 | -0.15564 | -0.064087 | -0.018311 | -0.068665 | -0.018311 | -0.054932 | 0.027466 | 0.11902 | -122.0078 | -121.9986 | 0.10071 | 0.041199 | 0.054932 | -0.07782 | -0.064087 | 0.16022 | -121.8979 | -121.9025 | 0.16022 | 0.20599 | 0.1236 | 0.045777 | -0.036621 | -0.018311 | -0.10529 | 0 | -0.050354 | -0.11444 | -0.045776 | 0.004578 | 0.11444 | -121.8933 | -121.8521 | 0.013733 | 0.10986 | 0.004578 | 0.022888
3819.8438 | 121.994 | -0.17395 | 121.8384 | -0.013352 | 6.9846 | 0.0096343 | 0.023768 | -0.0054901 | -0.0016384 | 0.0012604 | -0.0059205 | 0.021698 | -1.4538 | -0.009957 | -0.0062634 | 0.016175 | -0.00023491 | -0.14648 | -0.21057 | -0.041199 | -0.12817 | -0.036621 | -0.082397 | -0.1236 | -0.09613 | -0.054932 | -0.018311 | -0.027466 | 0.018311 | -0.022888 | 0.068665 | 0.13275 | -122.049 | -121.9666 | 0.13733 | 0.050354 | 0.091553 | -0.082397 | -0.041198 | 0.15564 | -121.8933 | -121.8658 | 0.19226 | 0.24261 | 0.15106 | 0.086976 | -0.004577 | 0.004578 | -0.086975 | 0.036622 | -0.009155 | -0.16937 | -0.036621 | -0.036621 | 0.11902 | -121.8796 | -121.8567 | 0.045776 | 0.14648 | 0.027466 | 0.07782
3821.625 | 121.994 | -0.16937 | 121.8567 | -0.013352 | 6.9857 | 0.013052 | 0.022059 | -0.0012177 | -0.001852 | 0.00019217 | -0.0059205 | 0.021484 | -1.4516 | -0.0052572 | -0.0045544 | 0.015962 | 0.0036103 | -0.16937 | -0.19226 | -0.059509 | -0.19226 | -0.073242 | -0.15106 | -0.15106 | -0.14191 | -0.068665 | -0.018311 | -0.045776 | -0.022888 | -0.073242 | 0.045776 | 0.10986 | -122.049 | -122.049 | 0.096131 | 0.018311 | 0.018311 | -0.091553 | -0.091553 | 0.15106 | -121.9254 | -121.9025 | 0.14649 | 0.21515 | 0.096131 | 0.064087 | -0.054931 | -0.013733 | -0.13275 | -0.004577 | -0.027465 | -0.13275 | -0.050354 | -0.022888 | 0.10071 | -121.9162 | -121.875 | -0.022888 | 0.1236 | 0 | 0.027466
3823.3906 | 122.0581 | -0.15106 | 121.8155 | 0.0019074 | 6.985 | 0.013052 | 0.0227 | 0.0011321 | -0.0027066 | -0.0042938 | -0.0028687 | 0.018066 | -1.4529 | -0.00013037 | -0.0049818 | 0.01703 | 0.00040589 | -0.11444 | -0.23804 | -0.004578 | -0.059509 | 0.073242 | -0.059509 | -0.054932 | -0.022888 | -0.10986 | -0.004578 | 0.032043 | 0.064087 | 0.027466 | 0.086975 | 0.14648 | -122.0535 | -121.875 | 0.2243 | 0.09613 | 0.091553 | -0.050354 | -0.054931 | 0.14648 | -121.9254 | -121.7834 | 0.21515 | 0.23804 | 0.17853 | 0.091553 | 0.032044 | 0.07782 | -0.054931 | 0.068665 | 0.036621 | -0.23346 | -0.10529 | -0.086975 | 0.041199 | -121.8201 | -121.8201 | 0.091553 | 0.18311 | 0.036621 | 0.12817
3825.1875 | 122.0215 | -0.16937 | 121.8521 | -0.013352 | 6.9844 | 0.013052 | 0.02035 | 0.0028411 | -0.0048428 | -0.00087583 | -0.0059205 | 0.022766 | -1.4536 | -0.0011984 | -0.0075452 | 0.014039 | 0.00083309 | -0.13733 | -0.18768 | -0.064087 | -0.11444 | -0.009155 | -0.086975 | -0.11902 | -0.068665 | -0.07782 | -0.013733 | -0.013733 | 0.032043 | -0.018311 | 0.073242 | 0.10529 | -122.0398 | -121.9666 | 0.16022 | 0.050354 | 0.082398 | -0.054932 | -0.022888 | 0.15564 | -121.9299 | -121.8658 | 0.20142 | 0.24261 | 0.15106 | 0.086975 | -0.004578 | 0.054932 | -0.050354 | 0.045776 | 0 | -0.1236 | -0.064087 | -0.01831 | 0.091553 | -121.9162 | -121.8658 | 0.054932 | 0.15564 | 0.032044 | 0.10071
3826.9062 | 122.113 | -0.13275 | 121.8246 | -0.013352 | 6.9829 | 0.010062 | 0.019922 | 0.0047637 | -0.0039884 | -0.0017304 | -0.0028687 | 0.017212 | -1.451 | 0.00093783 | -0.008186 | 0.016603 | -0.0010895 | -0.12817 | -0.21973 | -0.027466 | -0.054932 | 0.073242 | 0.009155 | -0.027466 | -0.013733 | -0.11444 | 0.009155 | 0.050354 | 0.11902 | 0.09613 | 0.13733 | 0.10529 | -122.0444 | -121.8796 | 0.20599 | 0.10529 | 0.14191 | 0 | 0.036621 | 0.14191 | -121.9391 | -121.7743 | 0.25177 | 0.27008 | 0.22888 | 0.12817 | 0.086975 | 0.10071 | -0.027466 | 0.10986 | 0.041199 | -0.19226 | -0.1236 | -0.086976 | 0.01831 | -121.8521 | -121.8155 | 0.077819 | 0.18311 | 0.004577 | 0.11902
3828.7031 | 122.1176 | -0.14648 | 121.8201 | -0.0057221 | 6.9821 | 0.011984 | 0.019495 | 6.4114e-05 | -0.002493 | -0.0015166 | -0.0028687 | 0.020843 | -1.4519 | 0.00051063 | -0.0069044 | 0.015962 | -0.0013031 | -0.10071 | -0.2243 | -0.027466 | -0.054932 | 0.07782 | 0.009155 | -0.036621 | 0.032043 | -0.10986 | -0.009155 | 0.050354 | 0.1236 | 0.09613 | 0.13733 | 0.11902 | -122.0444 | -121.875 | 0.2243 | 0.10986 | 0.15564 | -0.009155 | 0.036621 | 0.13733 | -121.9299 | -121.7697 | 0.27008 | 0.28381 | 0.24261 | 0.14648 | 0.10528 | 0.10529 | -0.027466 | 0.13275 | 0.059509 | -0.19684 | -0.10071 | -0.07782 | 0.036621 | -121.8475 | -121.8292 | 0.091552 | 0.19684 | 0.045776 | 0.17853
3830.4062 | 122.1313 | -0.15106 | 121.8109 | -0.013352 | 6.9806 | 0.0098479 | 0.018854 | 0.0022003 | -0.0048428 | -0.0010894 | -0.0089723 | 0.02063 | -1.4559 | 0.0041422 | -0.0056226 | 0.013398 | 0.0019013 | -0.10071 | -0.23346 | -0.013733 | -0.045776 | 0.091553 | 0.022888 | -0.009155 | 0.036621 | -0.11902 | 0.013733 | 0.054932 | 0.13733 | 0.10529 | 0.14648 | 0.13733 | -122.0444 | -121.8567 | 0.24261 | 0.14191 | 0.17395 | 0.004578 | 0.036621 | 0.16479 | -121.9299 | -121.756 | 0.28839 | 0.29755 | 0.25635 | 0.13275 | 0.091553 | 0.10529 | -0.032043 | 0.1236 | 0.041199 | -0.21973 | -0.13275 | -0.082397 | 0.032043 | -121.8246 | -121.7972 | 0.10529 | 0.20599 | 0.050354 | 0.18768
3832.1875 | 121.962 | -0.1831 | 121.875 | -0.020981 | 6.984 | 0.012839 | 0.022059 | -0.00036309 | -0.004202 | -0.001303 | -0.0028687 | 0.019989 | -1.4559 | 0.00029703 | -0.0051954 | 0.015321 | 0.0016877 | -0.16937 | -0.18768 | -0.059509 | -0.16937 | -0.10986 | -0.16937 | -0.17853 | -0.18768 | -0.07782 | -0.036621 | -0.068665 | -0.059509 | -0.091553 | 0.022888 | 0.1236 | -122.0627 | -122.0444 | 0.073242 | 0.004577 | 0.013732 | -0.11902 | -0.10986 | 0.14648 | -121.9528 | -121.9437 | 0.1236 | 0.20599 | 0.091552 | 0.059509 | -0.054932 | -0.050354 | -0.10986 | -0.022888 | -0.032044 | -0.12817 | -0.041199 | -0.004578 | 0.10528 | -121.9345 | -121.9116 | 0.013732 | 0.11444 | 0.013732 | -0.004578
3833.9688 | 122.0856 | -0.15106 | 121.843 | -0.013352 | 6.9821 | 0.011557 | 0.022272 | -0.0061311 | -0.0061246 | 0.00019217 | -0.0059205 | 0.018493 | -1.4536 | -0.0041892 | -0.010109 | 0.015962 | 0.0031829 | -0.10529 | -0.23346 | -0.018311 | -0.032043 | 0.068665 | 0 | -0.050354 | -0.022888 | -0.10529 | 0.004578 | 0.009155 | 0.07782 | 0.059509 | 0.09613 | 0.13275 | -122.0764 | -121.875 | 0.21973 | 0.10071 | 0.15106 | -0.032043 | 0.018311 | 0.15564 | -121.9482 | -121.8338 | 0.22888 | 0.24719 | 0.21057 | 0.091552 | 0.054931 | 0.086976 | -0.013732 | 0.073242 | 0.004577 | -0.21515 | -0.10986 | -0.082397 | 0.045776 | -121.8613 | -121.8384 | 0.11902 | 0.16022 | 0.045776 | 0.12817
3835.7656 | 122.1451 | -0.13733 | 121.8201 | -0.013352 | 6.9816 | 0.010062 | 0.021204 | -0.0020721 | -0.0037746 | -0.00066223 | -0.0059205 | 0.019775 | -1.4544 | 0.0067056 | -0.0062634 | 0.014894 | 0.00019229 | -0.11902 | -0.24261 | -0.036621 | -0.036621 | 0.10071 | 0.018311 | -0.004578 | 0.027466 | -0.11444 | 0.018311 | 0.054932 | 0.12817 | 0.09613 | 0.14191 | 0.10071 | -122.0627 | -121.8567 | 0.23804 | 0.13275 | 0.15564 | 0.032043 | 0.054932 | 0.15564 | -121.9345 | -121.7651 | 0.2655 | 0.27924 | 0.23346 | 0.1236 | 0.077819 | 0.13733 | 0 | 0.10986 | 0.036621 | -0.20599 | -0.13275 | -0.10529 | 0.022888 | -121.8567 | -121.8018 | 0.10071 | 0.19226 | 0.01831 | 0.16479
3837.5469 | 122.1039 | -0.14191 | 121.8246 | -0.0057221 | 6.9821 | 0.012625 | 0.021204 | -0.00057689 | -0.0044156 | -0.00087583 | -0.0089723 | 0.018066 | -1.4531 | -0.0022666 | -0.008186 | 0.014894 | -0.00087591 | -0.13733 | -0.23346 | -0.032043 | -0.082397 | 0.013733 | -0.041199 | -0.082397 | -0.045776 | -0.10529 | -0.004578 | 0.018311 | 0.059509 | 0.054932 | 0.10071 | 0.10986 | -122.0581 | -121.907 | 0.15564 | 0.05951 | 0.10071 | -0.050354 | -0.009156 | 0.13733 | -121.9299 | -121.8063 | 0.20142 | 0.24262 | 0.19684 | 0.10529 | 0.05951 | 0.045776 | -0.050354 | 0.064087 | 0.022889 | -0.20142 | -0.10071 | -0.091552 | 0.036621 | -121.8567 | -121.8292 | 0.05951 | 0.16022 | 0.004578 | 0.096131
3839.2812 | 122.0627 | -0.16022 | 121.875 | -0.020981 | 6.9825 | 0.011771 | 0.021418 | 0.0022003 | -0.003561 | -0.0025848 | -0.0028687 | 0.018921 | -1.4527 | 0.00093783 | -0.006477 | 0.014894 | 0.0023285 | -0.15564 | -0.23346 | -0.009155 | -0.07782 | 0.009155 | -0.054932 | -0.082397 | -0.064087 | -0.09613 | 0.013733 | -0.022888 | 0.018311 | -0.004578 | 0.082397 | 0.15106 | -122.1085 | -121.9528 | 0.16937 | 0.07782 | 0.10528 | -0.073242 | -0.045777 | 0.17395 | -121.9711 | -121.8979 | 0.17853 | 0.24261 | 0.15564 | 0.068664 | -0.018311 | 0.01831 | -0.068665 | 0.004578 | -0.036621 | -0.2243 | -0.10986 | -0.073242 | 0.064087 | -121.8842 | -121.8613 | 0.082397 | 0.13733 | 0.004577 | 0.09613
3841.0781 | 122.0215 | -0.19226 | 121.9025 | -0.020981 | 6.9836 | 0.012198 | 0.021418 | -0.00057689 | -0.002493 | -0.00044863 | -0.0059205 | 0.023407 | -1.4516 | 0.0071328 | -0.010536 | 0.014039 | 0.0019013 | -0.12817 | -0.2243 | -0.022888 | -0.09613 | -0.009155 | -0.050354 | -0.09613 | -0.10529 | -0.07782 | -0.013733 | -0.07782 | -0.018311 | -0.045776 | 0.018311 | 0.16937 | -122.1268 | -121.9986 | 0.18311 | 0.096131 | 0.14191 | -0.073242 | -0.027466 | 0.17853 | -121.9803 | -121.9803 | 0.17395 | 0.21057 | 0.14648 | 0.032044 | -0.032043 | 0.013733 | -0.073242 | -0.004578 | -0.064087 | -0.20142 | -0.064087 | -0.032043 | 0.11444 | -121.9254 | -121.9162 | 0.096131 | 0.11444 | 0.064087 | 0.086975
3842.875 | 122.1359 | -0.14191 | 121.8475 | -0.0057221 | 6.9842 | 0.010703 | 0.022272 | -0.0016449 | -0.00099764 | -0.00044863 | -0.0059205 | 0.020202 | -1.4514 | 0.0045694 | -0.003059 | 0.016175 | -0.00023491 | -0.09613 | -0.23346 | -0.027466 | -0.018311 | 0.068665 | -0.041199 | -0.045776 | 0.013733 | -0.1236 | 0.018311 | 0.073242 | 0.086975 | 0.064087 | 0.13275 | 0.11444 | -122.081 | -121.8658 | 0.21057 | 0.096131 | 0.10071 | -0.01831 | -0.013733 | 0.16022 | -121.9711 | -121.7743 | 0.22888 | 0.27466 | 0.20599 | 0.11444 | 0.045776 | 0.096131 | 0.009155 | 0.068664 | 0.054931 | -0.20599 | -0.14191 | -0.091552 | 0.018311 | -121.875 | -121.8292 | 0.1236 | 0.21515 | 0.045777 | 0.15564
3844.5938 | 122.0352 | -0.18768 | 121.9162 | -0.013352 | 6.9829 | 0.01113 | 0.020991 | -0.0012177 | -0.0048428 | -0.00044863 | -0.0028687 | 0.022979 | -1.454 | -0.0039756 | -0.010963 | 0.014894 | -0.00044851 | -0.16479 | -0.19684 | -0.059509 | -0.16479 | -0.068665 | -0.12817 | -0.14648 | -0.15106 | -0.064087 | -0.032043 | -0.068665 | -0.027466 | -0.050354 | 0.036621 | 0.12817 | -122.113 | -122.081 | 0.11902 | 0.041199 | 0.059509 | -0.086975 | -0.068665 | 0.15564 | -121.9803 | -121.9849 | 0.16022 | 0.2243 | 0.13733 | 0.068664 | -0.018311 | -0.009156 | -0.10529 | 0.004577 | -0.036622 | -0.13733 | -0.032044 | -0.009155 | 0.1236 | -121.9757 | -121.9482 | 0.022888 | 0.11902 | 0.022888 | 0.036621
3846.375 | 122.0306 | -0.19684 | 121.9162 | -0.020981 | 6.9816 | 0.010062 | 0.018854 | -0.0035675 | -0.003561 | -0.0025848 | -0.0089723 | 0.022125 | -1.4551 | -0.0076072 | -0.0083996 | 0.012758 | 0.0025421 | -0.1831 | -0.18768 | -0.064087 | -0.15564 | -0.068665 | -0.11902 | -0.15106 | -0.14648 | -0.073242 | -0.027466 | -0.073242 | -0.036621 | -0.073242 | 0.032043 | 0.13275 | -122.1039 | -122.0718 | 0.12817 | 0.045776 | 0.077819 | -0.086975 | -0.054932 | 0.16937 | -121.9894 | -121.9894 | 0.16022 | 0.22888 | 0.1236 | 0.059509 | -0.045776 | -0.004578 | -0.091553 | -0.009155 | -0.045776 | -0.1236 | -0.045776 | 0.009155 | 0.1236 | -121.9803 | -121.9437 | 0.041198 | 0.1236 | 0.013733 | 0.050354
3848.1719 | 122.1405 | -0.14648 | 121.8475 | -0.013352 | 6.9814 | 0.012412 | 0.019068 | -0.0027131 | -0.00099764 | -0.00087583 | -0.0028687 | 0.01828 | -1.4533 | -0.00013037 | -0.0073316 | 0.01468 | 0.00019229 | -0.14648 | -0.22888 | -0.032043 | -0.09613 | 0.018311 | -0.032043 | -0.082397 | -0.041199 | -0.12817 | 0 | 0.018311 | 0.086975 | 0.064087 | 0.11444 | 0.11444 | -122.0764 | -121.9437 | 0.16479 | 0.064087 | 0.11444 | -0.050354 | 0 | 0.14648 | -121.9757 | -121.8292 | 0.23346 | 0.26093 | 0.21057 | 0.11444 | 0.064087 | 0.050354 | -0.064087 | 0.086975 | 0.018311 | -0.19684 | -0.12817 | -0.082398 | 0.01831 | -121.8796 | -121.8475 | 0.050354 | 0.16479 | 0 | 0.10529
3849.9531 | 122.1634 | -0.14648 | 121.8704 | -0.0057221 | 6.9801 | 0.011343 | 0.021418 | -0.0010041 | -0.004202 | -0.0015166 | -0.0089723 | 0.018921 | -1.4536 | 0.0028604 | -0.0094678 | 0.014894 | -0.0010895 | -0.086975 | -0.25177 | -0.004578 | -0.022888 | 0.10071 | 0.022888 | -0.027466 | 0.018311 | -0.13275 | 0.004578 | 0.054932 | 0.13275 | 0.07782 | 0.13275 | 0.14191 | -122.1222 | -121.8933 | 0.24719 | 0.11902 | 0.16937 | -0.022888 | 0.027466 | 0.15106 | -122.0032 | -121.8155 | 0.27924 | 0.27924 | 0.2243 | 0.12817 | 0.073242 | 0.10529 | -0.01831 | 0.12817 | 0.050354 | -0.24719 | -0.13733 | -0.10529 | 0.013733 | -121.875 | -121.8658 | 0.1236 | 0.20142 | 0.059509 | 0.16479
3851.6719 | 122.0673 | -0.16937 | 121.8887 | -0.0057221 | 6.9836 | 0.011771 | 0.023981 | 0.00027771 | -0.0048428 | -0.0015166 | -0.0089723 | 0.022339 | -1.4531 | 0.0022196 | -0.0092542 | 0.014894 | -0.0053619 | -0.1236 | -0.20599 | -0.027466 | -0.10986 | -0.004578 | -0.082397 | -0.11902 | -0.082397 | -0.073242 | -0.009155 | -0.032043 | 0 | -0.045776 | 0.050354 | 0.14191 | -122.0947 | -121.9986 | 0.16479 | 0.050354 | 0.086976 | -0.091553 | -0.054931 | 0.16022 | -121.962 | -121.9208 | 0.16937 | 0.21973 | 0.1236 | 0.059509 | -0.036621 | 0.022888 | -0.082397 | 0.009155 | -0.022888 | -0.17853 | -0.064087 | -0.036621 | 0.096131 | -121.9162 | -121.8979 | 0.05951 | 0.13733 | 0.045777 | 0.086976
3853.4531 | 122.1039 | -0.15106 | 121.8658 | -0.02861 | 6.9821 | 0.010916 | 0.019282 | -0.0042083 | -0.0020658 | 0.002115 | -0.0059205 | 0.019561 | -1.4536 | 0.0054238 | -0.0049818 | 0.014039 | 0.0016877 | -0.15106 | -0.22888 | -0.018311 | -0.09613 | 0.004578 | -0.054932 | -0.086975 | -0.07782 | -0.09613 | 0.004578 | 0 | 0.036621 | 0.009155 | 0.073242 | 0.13275 | -122.0947 | -121.962 | 0.15564 | 0.064087 | 0.09613 | -0.068664 | -0.036621 | 0.15564 | -121.962 | -121.8658 | 0.18768 | 0.2243 | 0.16022 | 0.068664 | 0.004577 | 0.022889 | -0.077819 | 0.032043 | -0.004578 | -0.21057 | -0.10071 | -0.07782 | 0.054932 | -121.8842 | -121.8613 | 0.054932 | 0.15106 | 0 | 0.073242
3855.1875 | 122.0352 | -0.19684 | 121.8933 | -0.0057221 | 6.9814 | 0.013693 | 0.02569 | -0.00014949 | -0.00057044 | -0.001944 | -0.0028687 | 0.022979 | -1.4553 | 0.0017922 | -0.0058362 | 0.015748 | 0.00019229 | -0.16022 | -0.19226 | -0.054932 | -0.16937 | -0.091553 | -0.14648 | -0.16479 | -0.14648 | -0.059509 | -0.027466 | -0.050354 | -0.050354 | -0.086975 | 0.027466 | 0.14191 | -122.0856 | -122.0627 | 0.10529 | 0.032043 | 0.050354 | -0.10986 | -0.091552 | 0.16937 | -121.9528 | -121.9437 | 0.14648 | 0.2243 | 0.10986 | 0.054932 | -0.059509 | -0.036621 | -0.11444 | -0.022888 | -0.022888 | -0.13733 | -0.032043 | 0.004577 | 0.13733 | -121.9482 | -121.9208 | 0.027465 | 0.14648 | 0.036621 | 0.050354
3856.9844 | 122.0398 | -0.16479 | 121.8842 | -0.013352 | 6.9829 | 0.01113 | 0.023127 | 0.0051911 | -0.0056972 | -0.0010894 | -0.0028687 | 0.022125 | -1.4523 | -0.00077117 | -0.005409 | 0.015321 | -0.0010895 | -0.13275 | -0.21515 | -0.032043 | -0.12817 | -0.022888 | -0.10529 | -0.14191 | -0.11902 | -0.073242 | -0.027466 | -0.054932 | -0.027466 | -0.073242 | 0.022888 | 0.13275 | -122.0993 | -122.0123 | 0.14191 | 0.022888 | 0.059509 | -0.10986 | -0.073243 | 0.13733 | -121.9574 | -121.9391 | 0.13733 | 0.18768 | 0.091553 | 0.050354 | -0.045776 | 0.009155 | -0.096131 | 0 | -0.027466 | -0.18311 | -0.045776 | -0.050354 | 0.091553 | -121.9162 | -121.9116 | 0.036621 | 0.10986 | 0.032044 | 0.045776
3858.7812 | 122.168 | -0.14648 | 121.8887 | 0.0019074 | 6.9801 | 0.011771 | 0.021418 | -0.0020721 | -0.0048428 | -0.0010894 | -0.0028687 | 0.019989 | -1.4533 | 8.3226e-05 | -0.008827 | 0.015748 | 0.0046783 | -0.10529 | -0.23346 | -0.013733 | -0.004578 | 0.11444 | 0.018311 | -0.032043 | 0.013733 | -0.10529 | 0.004578 | 0.036621 | 0.1236 | 0.082397 | 0.12817 | 0.13275 | -122.1222 | -121.8933 | 0.26093 | 0.11444 | 0.16479 | -0.01831 | 0.032044 | 0.15106 | -121.994 | -121.8521 | 0.27008 | 0.27466 | 0.22888 | 0.1236 | 0.077819 | 0.12817 | 0.009155 | 0.11902 | 0.032043 | -0.21973 | -0.10986 | -0.086975 | 0.041198 | -121.9025 | -121.8842 | 0.14191 | 0.18311 | 0.041198 | 0.16022
3860.5781 | 122.113 | -0.16022 | 121.8887 | -0.0057221 | 6.9791 | 0.010916 | 0.020563 | -0.0010041 | -0.003561 | -0.0015166 | -0.0059205 | 0.019134 | -1.4531 | 0.0017922 | -0.0060498 | 0.016389 | -0.00023491 | -0.15106 | -0.22888 | -0.022888 | -0.086975 | 0.013733 | -0.059509 | -0.082397 | -0.07782 | -0.11902 | -0.004578 | -0.018311 | 0.041199 | 0 | 0.091553 | 0.13733 | -122.1176 | -121.9757 | 0.17395 | 0.07782 | 0.10071 | -0.059509 | -0.036621 | 0.15564 | -122.0078 | -121.907 | 0.20142 | 0.25177 | 0.16022 | 0.096131 | 0.004578 | 0.036621 | -0.064087 | 0.045777 | -0.013733 | -0.20599 | -0.11444 | -0.068665 | 0.041198 | -121.9116 | -121.8933 | 0.073242 | 0.14191 | 0.009155 | 0.082397
3862.375 | 122.0947 | -0.17853 | 121.907 | -0.020981 | 6.9823 | 0.012839 | 0.018427 | -0.0027131 | -0.00527 | -0.00044863 | -0.0028687 | 0.020843 | -1.4553 | -0.0067526 | -0.0083996 | 0.014894 | 0.0023285 | -0.091553 | -0.23804 | -0.009155 | -0.050354 | 0.045776 | -0.004578 | -0.054932 | -0.050354 | -0.091553 | 0 | -0.027466 | 0.036621 | -0.018311 | 0.054932 | 0.16937 | -122.1451 | -121.9574 | 0.2243 | 0.1236 | 0.17395 | -0.045777 | 0.004577 | 0.17853 | -121.9986 | -121.9345 | 0.21515 | 0.23346 | 0.16022 | 0.054932 | -0.018311 | 0.054931 | -0.041199 | 0.036621 | -0.027466 | -0.22888 | -0.091553 | -0.059509 | 0.086975 | -121.9162 | -121.907 | 0.12817 | 0.15106 | 0.086975 | 0.12817
3864.0938 | 122.1863 | -0.13275 | 121.9116 | -0.020981 | 6.9797 | 0.012839 | 0.020136 | -0.0039947 | -0.0027066 | -0.0015166 | -0.0089723 | 0.016357 | -1.4542 | 0.00072423 | -0.006477 | 0.015962 | 0.00083309 | -0.10986 | -0.23804 | -0.018311 | -0.036621 | 0.07782 | 0.022888 | -0.022888 | 0.032043 | -0.11444 | -0.009155 | 0.054932 | 0.1236 | 0.09613 | 0.14648 | 0.11444 | -122.1497 | -121.9482 | 0.21057 | 0.10986 | 0.15564 | -0.004577 | 0.041199 | 0.1236 | -122.0261 | -121.8567 | 0.25635 | 0.27924 | 0.22888 | 0.15564 | 0.10528 | 0.096131 | -0.01831 | 0.13275 | 0.064087 | -0.21973 | -0.10529 | -0.10529 | 0.01831 | -121.9299 | -121.9208 | 0.09613 | 0.18768 | 0.022888 | 0.16479
3865.8906 | 122.1039 | -0.16937 | 121.9208 | -0.013352 | 6.9806 | 0.013693 | 0.0227 | 0.00049131 | -0.0020658 | -0.0017304 | -0.0089723 | 0.020843 | -1.4542 | -0.0033346 | -0.0049818 | 0.015535 | 0.0021149 | -0.17853 | -0.21057 | -0.041199 | -0.13733 | -0.059509 | -0.14191 | -0.15106 | -0.09613 | -0.09613 | -0.027466 | -0.022888 | 0 | -0.041199 | 0.064087 | 0.12817 | -122.1313 | -122.0581 | 0.10986 | 0.018311 | 0.027466 | -0.10986 | -0.10071 | 0.14191 | -122.0169 | -121.9437 | 0.16937 | 0.23346 | 0.12817 | 0.091553 | -0.013733 | -0.01831 | -0.09613 | 0.027466 | 0.004578 | -0.16937 | -0.068664 | -0.041198 | 0.073243 | -121.962 | -121.9482 | 0.032044 | 0.14649 | -0.009155 | 0.073243
3867.6719 | 122.1542 | -0.15106 | 121.9162 | -0.013352 | 6.9812 | 0.01113 | 0.020136 | 6.4114e-05 | -0.0029202 | -0.0023712 | -0.0028687 | 0.019561 | -1.4514 | 0.0037148 | -0.0079724 | 0.012758 | 0.00019229 | -0.10529 | -0.23346 | -0.022888 | -0.036621 | 0.07782 | 0.004578 | -0.032043 | -0.018311 | -0.11444 | -0.009155 | 0.004578 | 0.09613 | 0.032043 | 0.091553 | 0.12817 | -122.1497 | -121.9528 | 0.22888 | 0.11902 | 0.15564 | -0.009155 | 0.027466 | 0.14191 | -122.0306 | -121.9116 | 0.24719 | 0.24261 | 0.18311 | 0.10071 | 0.041198 | 0.10071 | -0.013733 | 0.10528 | 0.013733 | -0.21057 | -0.10529 | -0.082397 | 0.036621 | -121.9391 | -121.9254 | 0.11444 | 0.15564 | 0.045776 | 0.13275
3869.4531 | 122.0673 | -0.20599 | 121.9666 | 0.0019074 | 6.9825 | 0.0094207 | 0.022272 | 6.4114e-05 | -0.0029202 | -0.001944 | -0.0059205 | 0.022125 | -1.454 | -0.010171 | -0.008827 | 0.010408 | 0.0031829 | -0.16479 | -0.20142 | -0.054932 | -0.15106 | -0.073242 | -0.11444 | -0.12817 | -0.14648 | -0.059509 | -0.022888 | -0.064087 | -0.018311 | -0.059509 | 0.027466 | 0.15106 | -122.168 | -122.1176 | 0.13275 | 0.07782 | 0.091553 | -0.073242 | -0.059509 | 0.18311 | -122.0261 | -122.0306 | 0.18768 | 0.23346 | 0.14649 | 0.050354 | -0.036621 | -0.01831 | -0.09613 | 0.004577 | -0.041199 | -0.14648 | -0.036621 | 0.004578 | 0.14649 | -122.0215 | -121.9894 | 0.054932 | 0.14191 | 0.041199 | 0.05951
3871.1719 | 122.1039 | -0.17853 | 121.9208 | -0.020981 | 6.9814 | 0.011557 | 0.023127 | 0.0026275 | -0.0022794 | -0.00044863 | 0.00018312 | 0.020416 | -1.454 | -0.0024802 | -0.0073316 | 0.013185 | -0.0030121 | -0.14191 | -0.21057 | -0.059509 | -0.11902 | -0.032043 | -0.068665 | -0.10529 | -0.10529 | -0.086975 | -0.009155 | -0.032043 | 0.027466 | -0.032043 | 0.07782 | 0.11902 | -122.1313 | -122.0398 | 0.14648 | 0.073242 | 0.10986 | -0.045777 | -0.009156 | 0.16937 | -122.0078 | -121.9528 | 0.20599 | 0.25635 | 0.14648 | 0.086975 | -0.022888 | 0.027466 | -0.05951 | 0.036621 | -0.022888 | -0.15106 | -0.07782 | -0.032043 | 0.091553 | -121.9803 | -121.9299 | 0.059509 | 0.14648 | 0.036621 | 0.073242
3872.9531 | 122.2046 | -0.14648 | 121.9025 | -0.013352 | 6.9793 | 0.011984 | 0.019282 | -0.0035675 | -0.0037746 | -0.00023503 | -0.0059205 | 0.019775 | -1.4546 | 0.0017922 | -0.0073316 | 0.015748 | 0.0036103 | -0.10529 | -0.24261 | -0.041199 | -0.041199 | 0.10071 | 0.027466 | -0.018311 | 0.032043 | -0.091553 | -0.004578 | 0.059509 | 0.1236 | 0.086975 | 0.12817 | 0.10529 | -122.1451 | -121.9437 | 0.24719 | 0.12817 | 0.17395 | 0.022888 | 0.068665 | 0.14191 | -121.994 | -121.843 | 0.27008 | 0.27466 | 0.23346 | 0.13275 | 0.091553 | 0.14191 | 0 | 0.12817 | 0.064087 | -0.20142 | -0.086975 | -0.096131 | 0.054931 | -121.9437 | -121.907 | 0.10529 | 0.20599 | 0.041198 | 0.17853
3874.75 | 122.113 | -0.1831 | 121.9574 | -0.0057221 | 6.9838 | 0.011557 | 0.023554 | 0.0019867 | -0.0029202 | -2.1434e-05 | -0.0028687 | 0.020843 | -1.4536 | -0.002053 | -0.0062634 | 0.014466 | -0.0030121 | -0.14191 | -0.20142 | -0.054932 | -0.10529 | -0.009155 | -0.073242 | -0.11444 | -0.07782 | -0.091553 | -0.022888 | -0.013733 | 0.018311 | -0.027466 | 0.073242 | 0.12817 | -122.1588 | -122.0627 | 0.17395 | 0.068664 | 0.10986 | -0.059509 | -0.01831 | 0.16022 | -122.049 | -121.9711 | 0.20142 | 0.25635 | 0.15564 | 0.09613 | -0.004578 | 0.045777 | -0.050354 | 0.041199 | 0.009155 | -0.14648 | -0.068665 | -0.018311 | 0.091552 | -122.0123 | -121.9803 | 0.077819 | 0.16937 | 0.041198 | 0.10528
3876.4688 | 122.113 | -0.20142 | 121.9666 | -0.020981 | 6.9808 | 0.011557 | 0.023554 | 0.0043365 | -0.0033474 | 0.0016876 | -0.0028687 | 0.021911 | -1.4536 | -0.0035482 | -0.0073316 | 0.012544 | 0.00040589 | -0.17395 | -0.18768 | -0.045776 | -0.15106 | -0.054932 | -0.091553 | -0.14648 | -0.14191 | -0.064087 | -0.027466 | -0.054932 | -0.013733 | -0.059509 | 0.050354 | 0.15564 | -122.1542 | -122.1176 | 0.14648 | 0.054932 | 0.10986 | -0.10071 | -0.045777 | 0.17395 | -122.0306 | -122.0215 | 0.18768 | 0.25177 | 0.14191 | 0.07782 | -0.032043 | -0.009156 | -0.10529 | 0.013733 | -0.027466 | -0.14191 | -0.036621 | 0.013733 | 0.13733 | -122.0123 | -121.994 | 0.050354 | 0.14648 | 0.027466 | 0.059509
3878.2656 | 122.1268 | -0.1831 | 121.9666 | -0.0057221 | 6.984 | 0.010916 | 0.023554 | -0.0012177 | -0.0054836 | 0.0023286 | -0.0059205 | 0.019348 | -1.4525 | 0.00072423 | -0.0079724 | 0.013612 | 0.0027557 | -0.14191 | -0.20142 | -0.050354 | -0.1236 | -0.022888 | -0.082397 | -0.11444 | -0.091553 | -0.086975 | -0.018311 | -0.036621 | 0.036621 | -0.018311 | 0.068665 | 0.13275 | -122.168 | -122.0901 | 0.16022 | 0.068664 | 0.10071 | -0.064087 | -0.032043 | 0.16479 | -122.0535 | -122.0032 | 0.21973 | 0.25177 | 0.16479 | 0.086976 | 0 | 0.027466 | -0.073242 | 0.054932 | -0.01831 | -0.15106 | -0.068664 | -0.018311 | 0.09613 | -122.0169 | -121.9849 | 0.059509 | 0.14648 | 0.041198 | 0.091552
3880 | 122.0718 | -0.17853 | 121.9666 | -0.0057221 | 6.9825 | 0.012198 | 0.02334 | -0.00036309 | -0.0022794 | 0.0012604 | -0.0059205 | 0.020202 | -1.4519 | -0.0080344 | -0.0060498 | 0.01468 | -0.0030121 | -0.14191 | -0.20142 | -0.036621 | -0.14191 | -0.041199 | -0.14648 | -0.15564 | -0.12817 | -0.086975 | -0.018311 | -0.073242 | -0.045776 | -0.086975 | 0.013733 | 0.14191 | -122.168 | -122.1085 | 0.13733 | 0.022888 | 0.032044 | -0.11902 | -0.10986 | 0.16022 | -122.0535 | -122.0398 | 0.13275 | 0.19226 | 0.091553 | 0.032044 | -0.068664 | -0.004578 | -0.10529 | -0.027465 | -0.054931 | -0.1648 | -0.068664 | -0.022888 | 0.091553 | -122.0032 | -121.9849 | 0.036621 | 0.10529 | 0.036621 | 0.050354
3881.7812 | 122.2092 | -0.14191 | 121.9437 | -0.020981 | 6.9816 | 0.013266 | 0.019709 | -0.0022857 | -0.0014248 | 0.0010468 | -0.0028687 | 0.019348 | -1.4533 | 0.0043558 | -0.0024182 | 0.018312 | -0.00023491 | -0.086975 | -0.25177 | 0 | -0.045776 | 0.073242 | -0.027466 | -0.059509 | 0.018311 | -0.12817 | 0.004578 | 0.059509 | 0.10986 | 0.054932 | 0.13733 | 0.14191 | -122.1954 | -121.9894 | 0.21515 | 0.082398 | 0.11444 | -0.059509 | -0.027466 | 0.14649 | -122.0718 | -121.8842 | 0.25177 | 0.27924 | 0.19684 | 0.13275 | 0.050354 | 0.073242 | -0.045776 | 0.10529 | 0.054931 | -0.25177 | -0.13275 | -0.10986 | 0.013733 | -121.9437 | -121.9391 | 0.096131 | 0.20142 | 0.054932 | 0.16022
3883.5625 | 122.168 | -0.15564 | 121.9574 | -0.013352 | 6.9831 | 0.010275 | 0.021418 | -0.0033539 | -0.0050564 | 0.0012604 | -0.0059205 | 0.019348 | -1.4527 | -0.001412 | -0.010536 | 0.015535 | 0.0029693 | -0.10986 | -0.23804 | -0.009155 | -0.054932 | 0.07782 | 0.004578 | -0.036621 | -0.022888 | -0.11902 | 0.013733 | 0.013733 | 0.073242 | 0.041199 | 0.091553 | 0.14649 | -122.1954 | -122.0123 | 0.23346 | 0.11902 | 0.16022 | -0.027466 | 0.013733 | 0.16937 | -122.0764 | -121.9437 | 0.22888 | 0.24719 | 0.19684 | 0.07782 | 0.027466 | 0.086975 | -0.045777 | 0.059509 | 0 | -0.22888 | -0.13275 | -0.082397 | 0.036621 | -121.9666 | -121.9437 | 0.10071 | 0.16937 | 0.045777 | 0.13275
3885.375 | 122.1039 | -0.17853 | 121.962 | 0.0019074 | 6.9814 | 0.011557 | 0.021631 | -0.0010041 | -0.002493 | 0.0023286 | -0.0059205 | 0.021698 | -1.4555 | -0.011239 | -0.005409 | 0.015107 | -0.0010895 | -0.17395 | -0.20142 | -0.050354 | -0.17853 | -0.068665 | -0.15564 | -0.15564 | -0.14191 | -0.073242 | -0.018311 | -0.064087 | -0.036621 | -0.086975 | 0.036621 | 0.12817 | -122.1634 | -122.1405 | 0.10986 | 0.022888 | 0.022888 | -0.10529 | -0.10529 | 0.16022 | -122.0352 | -122.0261 | 0.14191 | 0.21515 | 0.091553 | 0.054932 | -0.068664 | -0.018311 | -0.12817 | -0.01831 | -0.045776 | -0.15106 | -0.054931 | -0.022888 | 0.10529 | -122.0123 | -121.9803 | 0 | 0.11444 | 0.004578 | 0.036621
3887.0938 | 122.1313 | -0.16479 | 121.9666 | -0.013352 | 6.9816 | 0.011771 | 0.02035 | -0.0012177 | -0.0022794 | -0.0010894 | 0.00018312 | 0.019775 | -1.4551 | -0.00098477 | -0.007118 | 0.015962 | -0.0049347 | -0.13275 | -0.21515 | -0.041199 | -0.10071 | 0 | -0.068665 | -0.10071 | -0.059509 | -0.082397 | -0.018311 | -0.018311 | 0.032043 | -0.009155 | 0.073242 | 0.1236 | -122.1817 | -122.0673 | 0.16479 | 0.064087 | 0.09613 | -0.059509 | -0.027466 | 0.14648 | -122.049 | -121.9849 | 0.19684 | 0.23804 | 0.15564 | 0.091553 | 0.009156 | 0.041199 | -0.059509 | 0.050354 | 0 | -0.17395 | -0.064086 | -0.050354 | 0.082398 | -122.0078 | -121.9849 | 0.064087 | 0.14648 | 0.032044 | 0.10529
3888.875 | 122.0947 | -0.18768 | 121.9574 | -0.013352 | 6.9801 | 0.012198 | 0.020777 | -0.0016449 | -0.003561 | -0.00066223 | -0.0059205 | 0.018921 | -1.4533 | -0.005471 | -0.010536 | 0.013612 | 0.0019013 | -0.19684 | -0.19226 | -0.050354 | -0.17395 | -0.059509 | -0.11902 | -0.13275 | -0.15564 | -0.064087 | -0.027466 | -0.07782 | -0.022888 | -0.059509 | 0.004578 | 0.13733 | -122.1497 | -122.1313 | 0.12817 | 0.054932 | 0.068664 | -0.082397 | -0.068665 | 0.16022 | -122.0215 | -122.0352 | 0.16479 | 0.19226 | 0.12817 | 0.032044 | -0.032043 | -0.009155 | -0.1236 | 0.004578 | -0.050354 | -0.14191 | -0.036621 | -0.004578 | 0.1236 | -122.0078 | -121.9849 | 0.013733 | 0.10986 | -0.009155 | 0.032043
3890.6562 | 122.1542 | -0.15564 | 121.9528 | -0.013352 | 6.9821 | 0.010916 | 0.019282 | -0.00036309 | -0.0031338 | -0.00044863 | -0.0028687 | 0.019989 | -1.4536 | -0.002053 | -0.0096814 | 0.015107 | -0.00087591 | -0.09613 | -0.24719 | -0.022888 | -0.064087 | 0.059509 | -0.013733 | -0.059509 | -0.064087 | -0.10071 | -0.013733 | -0.036621 | 0.032043 | -0.009155 | 0.059509 | 0.13275 | -122.2 | -122.0169 | 0.21515 | 0.096131 | 0.14191 | -0.036621 | 0.009155 | 0.14191 | -122.0535 | -121.9894 | 0.18768 | 0.21515 | 0.14649 | 0.073242 | 0.004578 | 0.082397 | -0.041199 | 0.045776 | -0.022888 | -0.2243 | -0.086975 | -0.091552 | 0.054932 | -121.9757 | -121.9666 | 0.091553 | 0.11902 | 0.05951 | 0.091553
3892.375 | 122.2321 | -0.16022 | 121.9345 | -0.0057221 | 6.9799 | 0.013052 | 0.019922 | 0.0017731 | -0.0031338 | 0.0019012 | -0.012024 | 0.019134 | -1.4536 | 0.0020058 | -0.0058362 | 0.014894 | -2.1314e-05 | -0.12817 | -0.23346 | -0.009155 | -0.050354 | 0.082397 | 0.022888 | -0.018311 | 0.027466 | -0.10529 | 0.004578 | 0.054932 | 0.11902 | 0.086975 | 0.12817 | 0.15106 | -122.168 | -121.9849 | 0.24261 | 0.14191 | 0.1831 | -0.009156 | 0.032043 | 0.16479 | -122.0398 | -121.8796 | 0.27924 | 0.28839 | 0.24719 | 0.1236 | 0.082397 | 0.091552 | -0.041199 | 0.11444 | 0.050354 | -0.2243 | -0.10986 | -0.073242 | 0.054931 | -121.9437 | -121.9299 | 0.10986 | 0.21515 | 0.032043 | 0.18768
3894.1719 | 122.1725 | -0.15106 | 121.9437 | -0.013352 | 6.9808 | 0.011771 | 0.021204 | 0.0011321 | -0.0020658 | -0.001944 | -0.0089723 | 0.021057 | -1.4516 | 0.00093783 | -0.0028454 | 0.016603 | -0.0010895 | -0.17395 | -0.20599 | -0.032043 | -0.14648 | -0.054932 | -0.14648 | -0.13733 | -0.082397 | -0.073242 | 0 | -0.004578 | 0.027466 | -0.032043 | 0.073242 | 0.11902 | -122.1497 | -122.0901 | 0.09613 | 0.013733 | 0.004578 | -0.10529 | -0.11444 | 0.15106 | -122.0169 | -121.9482 | 0.17853 | 0.2243 | 0.11902 | 0.073242 | -0.032043 | -0.022889 | -0.11444 | 0.027466 | -0.004578 | -0.17395 | -0.073242 | -0.054932 | 0.07782 | -121.9757 | -121.9437 | 0.004578 | 0.14648 | -0.022888 | 0.068665
3895.9062 | 122.1771 | -0.17395 | 121.9757 | -0.0057221 | 6.9818 | 0.011984 | 0.018641 | -0.0012177 | -0.003561 | -0.0015166 | -0.0059205 | 0.019348 | -1.4551 | 0.0022196 | -0.0096814 | 0.014466 | 0.0029693 | -0.09613 | -0.25177 | -0.009155 | -0.050354 | 0.050354 | 0.009155 | -0.032043 | -0.018311 | -0.11444 | 0 | -0.022888 | 0.059509 | 0.022888 | 0.073242 | 0.16479 | -122.2275 | -122.0261 | 0.2243 | 0.14191 | 0.1831 | -0.022888 | 0.01831 | 0.17395 | -122.0901 | -121.9986 | 0.23346 | 0.24719 | 0.19684 | 0.073242 | 0.022888 | 0.059509 | -0.041199 | 0.059509 | -0.022888 | -0.24261 | -0.11444 | -0.07782 | 0.059509 | -121.9849 | -121.9757 | 0.1236 | 0.15106 | 0.07782 | 0.15564
3897.6719 | 122.2366 | -0.11902 | 121.9482 | -0.0057221 | 6.9816 | 0.014121 | 0.020777 | 0.0015595 | -0.0014248 | -2.1434e-05 | -0.0059205 | 0.019989 | -1.4508 | 0.0062784 | -0.0037 | 0.015321 | -0.0017303 | -0.073242 | -0.23804 | -0.013733 | -0.018311 | 0.073242 | -0.036621 | -0.050354 | 0.027466 | -0.11902 | 0.004578 | 0.064087 | 0.09613 | 0.059509 | 0.13733 | 0.10529 | -122.1863 | -121.9666 | 0.19226 | 0.068665 | 0.082398 | -0.036621 | -0.022888 | 0.1236 | -122.0673 | -121.8842 | 0.21515 | 0.25635 | 0.17853 | 0.13275 | 0.054931 | 0.086975 | -0.004578 | 0.091552 | 0.059509 | -0.2243 | -0.1236 | -0.11902 | 0 | -121.962 | -121.9437 | 0.10071 | 0.18311 | 0.045777 | 0.14649
3899.3906 | 122.1497 | -0.18768 | 121.9986 | -0.020981 | 6.9801 | 0.010703 | 0.021204 | 0.0047637 | -0.0044156 | -0.00023503 | -0.0028687 | 0.022125 | -1.4551 | -0.0039756 | -0.007118 | 0.013612 | 0.0010467 | -0.10529 | -0.24261 | -0.022888 | -0.07782 | 0.050354 | -0.022888 | -0.059509 | -0.045776 | -0.09613 | -0.009155 | -0.054932 | 0.009155 | -0.004578 | 0.050354 | 0.16479 | -122.2412 | -122.0764 | 0.23804 | 0.12817 | 0.16479 | -0.036621 | 0 | 0.17853 | -122.0947 | -122.0535 | 0.19684 | 0.23804 | 0.1831 | 0.059509 | 0.004577 | 0.073242 | -0.054932 | 0.01831 | -0.045777 | -0.21973 | -0.086975 | -0.054932 | 0.091553 | -122.0215 | -122.0078 | 0.10986 | 0.13275 | 0.082397 | 0.14191
3901.1719 | 122.1725 | -0.1831 | 121.9894 | -0.020981 | 6.9808 | 0.012198 | 0.023768 | 0.0013459 | -0.002493 | 0.00019217 | 0.00018312 | 0.020202 | -1.4531 | 0.0035012 | -0.0073316 | 0.014253 | -0.0023713 | -0.1236 | -0.21515 | -0.054932 | -0.09613 | -0.004578 | -0.086975 | -0.091553 | -0.064087 | -0.10986 | -0.036621 | -0.022888 | 0.009155 | -0.027466 | 0.059509 | 0.12817 | -122.2046 | -122.0856 | 0.17853 | 0.091552 | 0.09613 | -0.036621 | -0.032043 | 0.14648 | -122.0993 | -122.0123 | 0.19226 | 0.24261 | 0.15564 | 0.09613 | 0.009155 | 0.050354 | -0.041198 | 0.045776 | 0.013733 | -0.16022 | -0.073242 | -0.032044 | 0.073242 | -122.0444 | -122.0261 | 0.086975 | 0.16022 | 0.059509 | 0.11902
3902.9531 | 122.2412 | -0.15106 | 121.9711 | -0.013352 | 6.9799 | 0.0096343 | 0.018427 | -0.0016449 | -0.0061246 | -0.00023503 | -0.0059205 | 0.019134 | -1.4531 | -0.0039756 | -0.005409 | 0.014253 | -0.00023491 | -0.13733 | -0.21973 | -0.013733 | -0.073242 | 0.032043 | -0.032043 | -0.059509 | -0.045776 | -0.10529 | -0.004578 | 0.032043 | 0.07782 | 0.073242 | 0.12817 | 0.13733 | -122.1909 | -122.0444 | 0.18311 | 0.091553 | 0.11902 | -0.045776 | -0.01831 | 0.14648 | -122.0764 | -121.9391 | 0.22888 | 0.27924 | 0.2243 | 0.13275 | 0.07782 | 0.045776 | -0.059509 | 0.082398 | 0.036621 | -0.20599 | -0.10071 | -0.068665 | 0.045776 | -121.9849 | -121.9757 | 0.07782 | 0.18311 | 0.013733 | 0.10529
3904.7344 | 122.1268 | -0.16479 | 121.9803 | -0.0057221 | 6.9821 | 0.012412 | 0.024195 | 0.0079681 | -0.00099764 | -0.0017304 | -0.0059205 | 0.021698 | -1.4527 | -0.0022666 | -0.007118 | 0.015107 | -0.0010895 | -0.1236 | -0.21973 | -0.041199 | -0.11902 | -0.013733 | -0.10986 | -0.15564 | -0.10071 | -0.086975 | -0.018311 | -0.050354 | -0.041199 | -0.082397 | 0.013733 | 0.1236 | -122.2 | -122.0993 | 0.15106 | 0.009155 | 0.054932 | -0.11444 | -0.068664 | 0.14648 | -122.0673 | -122.0306 | 0.1236 | 0.17853 | 0.082398 | 0.032044 | -0.064086 | 0.027466 | -0.07782 | -0.022888 | -0.032043 | -0.17853 | -0.068664 | -0.054932 | 0.07782 | -122.0215 | -121.9986 | 0.045776 | 0.11444 | 0.041199 | 0.064087
3906.4531 | 122.2137 | -0.11444 | 121.9254 | 0.0019074 | 6.9793 | 0.012198 | 0.022272 | 6.4114e-05 | -0.0014248 | 0.0010468 | -0.0059205 | 0.019561 | -1.4531 | 0.00051063 | -0.004768 | 0.015321 | 0.00083309 | -0.10986 | -0.24261 | -0.018311 | -0.036621 | 0.073242 | -0.013733 | -0.045776 | 0.027466 | -0.1236 | 0.013733 | 0.050354 | 0.086975 | 0.045776 | 0.10986 | 0.09613 | -122.168 | -121.962 | 0.18768 | 0.068665 | 0.10071 | -0.027465 | 0.004578 | 0.12817 | -122.049 | -121.875 | 0.20142 | 0.2243 | 0.16022 | 0.09613 | 0.032043 | 0.091553 | -0.01831 | 0.073242 | 0.036621 | -0.2243 | -0.13733 | -0.12817 | -0.009155 | -121.9437 | -121.9116 | 0.07782 | 0.16479 | 0.004578 | 0.14191
3908.2656 | 122.1268 | -0.19684 | 122.0032 | -0.013352 | 6.9838 | 0.010489 | 0.020563 | -0.00057689 | -0.0037746 | 0.00040597 | -0.0028687 | 0.020202 | -1.4527 | -0.00483 | -0.01075 | 0.01468 | 0.0044647 | -0.18768 | -0.19684 | -0.036621 | -0.15564 | -0.054932 | -0.10986 | -0.13275 | -0.15564 | -0.09613 | -0.045776 | -0.086975 | -0.041199 | -0.064087 | 0.013733 | 0.16022 | -122.2 | -122.1588 | 0.14191 | 0.064087 | 0.086975 | -0.09613 | -0.073242 | 0.15106 | -122.0993 | -122.0901 | 0.15564 | 0.21057 | 0.13275 | 0.059509 | -0.018311 | -0.018311 | -0.11902 | 0.004577 | -0.041199 | -0.16022 | -0.050354 | 0 | 0.10071 | -122.0398 | -122.049 | 0.041198 | 0.10986 | 0.009155 | 0.041198
3909.9844 | 122.2549 | -0.13275 | 121.9757 | -0.0057221 | 6.9801 | 0.0087799 | 0.018213 | -0.0012177 | -0.0048428 | -0.0015166 | -0.0089723 | 0.01828 | -1.4561 | 0.0041422 | -0.0051954 | 0.017457 | 0.00061949 | -0.09613 | -0.23346 | -0.027466 | -0.022888 | 0.10071 | 0.018311 | -0.018311 | 0.009155 | -0.1236 | -0.004578 | 0.027466 | 0.11444 | 0.07782 | 0.12817 | 0.10529 | -122.2092 | -121.9986 | 0.23346 | 0.11444 | 0.15106 | 0.009155 | 0.045777 | 0.12817 | -122.0993 | -121.9482 | 0.24719 | 0.26093 | 0.21057 | 0.13275 | 0.082398 | 0.12817 | 0.004578 | 0.11902 | 0.032044 | -0.20599 | -0.11902 | -0.10071 | 0.009155 | -122.0032 | -121.9803 | 0.10986 | 0.16022 | 0.036621 | 0.14191
3911.7656 | 122.2458 | -0.15106 | 121.9894 | -0.013352 | 6.9778 | 0.010062 | 0.019068 | -0.0014313 | -0.0037746 | 0.0025422 | -0.0059205 | 0.019775 | -1.454 | 0.0011514 | -0.0069044 | 0.014039 | -2.1314e-05 | -0.13733 | -0.23804 | -0.013733 | -0.064087 | 0.041199 | -0.036621 | -0.045776 | -0.009155 | -0.13275 | 0 | 0.027466 | 0.086975 | 0.068665 | 0.10986 | 0.13733 | -122.2275 | -122.0535 | 0.19226 | 0.10529 | 0.11444 | -0.032043 | -0.022888 | 0.15106 | -122.1222 | -121.962 | 0.23804 | 0.26093 | 0.21973 | 0.10986 | 0.068665 | 0.054932 | -0.050354 | 0.086975 | 0.027466 | -0.2243 | -0.13275 | -0.086975 | 0.018311 | -122.0032 | -121.9894 | 0.086975 | 0.17853 | 0.013733 | 0.14191
3913.5469 | 122.2687 | -0.12817 | 121.9711 | -0.0057221 | 6.9786 | 0.012839 | 0.021631 | 0.00027771 | -0.0029202 | -0.0010894 | -0.0059205 | 0.019989 | -1.4542 | 0.003074 | -0.004768 | 0.01703 | 0.0010467 | -0.11444 | -0.25177 | -0.027466 | -0.045776 | 0.050354 | -0.059509 | -0.073242 | -0.004578 | -0.1236 | 0.022888 | 0.045776 | 0.082397 | 0.045776 | 0.13733 | 0.10071 | -122.2229 | -122.0169 | 0.17853 | 0.054932 | 0.068665 | -0.045776 | -0.032043 | 0.15106 | -122.0947 | -121.9254 | 0.21057 | 0.2655 | 0.17395 | 0.11444 | 0.022888 | 0.07782 | -0.01831 | 0.059509 | 0.022888 | -0.2243 | -0.14648 | -0.1236 | 0.004578 | -121.9986 | -121.9482 | 0.082398 | 0.17395 | 0.013733 | 0.1236
3915.3594 | 122.2549 | -0.1236 | 122.0032 | -0.020981 | 6.9797 | 0.012198 | 0.019282 | -0.0031403 | -0.0020658 | -0.0010894 | -0.0059205 | 0.018921 | -1.4514 | 0.00093783 | -0.008827 | 0.015962 | 0.00083309 | -0.091553 | -0.23804 | -0.027466 | -0.036621 | 0.10071 | 0.018311 | -0.027466 | 0.036621 | -0.13275 | 0.009155 | 0.032043 | 0.11444 | 0.091553 | 0.1236 | 0.09613 | -122.2412 | -122.0398 | 0.2243 | 0.09613 | 0.14191 | 0 | 0.045777 | 0.13275 | -122.1359 | -121.9711 | 0.23804 | 0.24719 | 0.21515 | 0.11444 | 0.082398 | 0.12817 | -0.009155 | 0.10529 | 0.022888 | -0.21057 | -0.14191 | -0.11444 | -0.009155 | -122.0306 | -121.994 | 0.086975 | 0.15564 | 0.032043 | 0.16022
3917.1562 | 122.2046 | -0.15106 | 122.0215 | -0.013352 | 6.9793 | 0.010489 | 0.020136 | -0.0033539 | -0.0033474 | -0.001303 | -0.0059205 | 0.019561 | -1.4533 | 0.00093783 | -0.0079724 | 0.013398 | -0.00087591 | -0.10529 | -0.23346 | 0 | -0.036621 | 0.064087 | -0.013733 | -0.045776 | -0.041199 | -0.1236 | -0.013733 | -0.036621 | 0.041199 | 0.013733 | 0.073242 | 0.15106 | -122.2549 | -122.0581 | 0.21515 | 0.10529 | 0.13733 | -0.045776 | -0.013733 | 0.13733 | -122.1451 | -122.0581 | 0.19226 | 0.2243 | 0.16479 | 0.086975 | 0.027466 | 0.064087 | -0.036621 | 0.054932 | -0.022888 | -0.23346 | -0.10986 | -0.082397 | 0.027466 | -122.0215 | -122.0352 | 0.11444 | 0.11444 | 0.045776 | 0.10986
3918.9375 | 122.2641 | -0.14191 | 121.9986 | -0.013352 | 6.9806 | 0.012625 | 0.022913 | 0.0054047 | -0.002493 | -0.00023503 | -0.0059205 | 0.018921 | -1.4542 | -0.003121 | -0.0069044 | 0.014253 | -0.0023713 | -0.073242 | -0.2655 | -0.013733 | -0.032043 | 0.082397 | -0.032043 | -0.041199 | 0.027466 | -0.13275 | 0.018311 | 0.036621 | 0.091553 | 0.050354 | 0.11902 | 0.12817 | -122.2641 | -122.0306 | 0.2243 | 0.10071 | 0.10986 | -0.027466 | -0.01831 | 0.16022 | -122.1313 | -121.962 | 0.23346 | 0.26093 | 0.19226 | 0.10071 | 0.032043 | 0.09613 | -0.01831 | 0.073242 | 0.01831 | -0.25177 | -0.15106 | -0.1236 | 0.009156 | -122.0123 | -121.9803 | 0.10986 | 0.17853 | 0.068665 | 0.16937
3920.6562 | 122.1497 | -0.16937 | 122.0215 | -0.013352 | 6.9823 | 0.01348 | 0.022486 | 0.0011321 | -0.0056972 | -0.00023503 | 0.00018312 | 0.02362 | -1.4519 | 0.00072423 | -0.0066906 | 0.014039 | 0.0042511 | -0.12817 | -0.21973 | -0.036621 | -0.10529 | -0.018311 | -0.10529 | -0.12817 | -0.09613 | -0.086975 | -0.018311 | -0.064087 | -0.036621 | -0.068665 | 0.027466 | 0.13275 | -122.2412 | -122.1268 | 0.15106 | 0.041199 | 0.064087 | -0.091553 | -0.068665 | 0.15106 | -122.1085 | -122.0856 | 0.13275 | 0.19684 | 0.10071 | 0.045777 | -0.050354 | 0.01831 | -0.068665 | -0.01831 | -0.045776 | -0.18311 | -0.068664 | -0.050354 | 0.082398 | -122.0581 | -122.0398 | 0.064087 | 0.10529 | 0.041199 | 0.073243
3922.4375 | 122.1313 | -0.18768 | 122.0169 | -0.013352 | 6.9803 | 0.012625 | 0.022272 | -0.00057689 | -0.001852 | -0.0021576 | -0.0028687 | 0.021484 | -1.4512 | -0.003762 | -0.007118 | 0.015535 | 0.0010467 | -0.12817 | -0.20142 | -0.050354 | -0.11902 | -0.050354 | -0.13733 | -0.16479 | -0.11902 | -0.073242 | -0.032043 | -0.068665 | -0.050354 | -0.07782 | 0 | 0.13733 | -122.2183 | -122.1359 | 0.13733 | 0.022888 | 0.050354 | -0.11444 | -0.086975 | 0.15564 | -122.0901 | -122.0856 | 0.13733 | 0.18768 | 0.10986 | 0.032043 | -0.045777 | 0 | -0.068665 | -0.018311 | -0.036622 | -0.15106 | -0.041199 | -0.013733 | 0.11444 | -122.0673 | -122.049 | 0.068664 | 0.11902 | 0.059509 | 0.068664
3924.1562 | 122.2321 | -0.16022 | 122.0123 | -0.020981 | 6.9799 | 0.012625 | 0.019282 | -0.0027131 | -0.0029202 | -0.0023712 | 0.00018312 | 0.018921 | -1.4538 | 0.0035012 | -0.01139 | 0.013398 | 0.0014741 | -0.10529 | -0.22888 | -0.009155 | -0.013733 | 0.09613 | 0 | -0.036621 | -0.004578 | -0.1236 | 0 | 0 | 0.086975 | 0.050354 | 0.082397 | 0.15106 | -122.2412 | -122.0261 | 0.25635 | 0.1236 | 0.16022 | -0.027466 | 0.009155 | 0.16022 | -122.1359 | -122.0123 | 0.24719 | 0.24261 | 0.21057 | 0.082397 | 0.050354 | 0.10528 | -0.004578 | 0.086975 | 0 | -0.21973 | -0.1236 | -0.068665 | 0.036621 | -122.0215 | -122.0123 | 0.14648 | 0.16022 | 0.054931 | 0.15564
3925.9375 | 122.1542 | -0.18768 | 122.0123 | -0.013352 | 6.9829 | 0.011343 | 0.021845 | -0.00036309 | -0.004202 | -0.00044863 | -0.0059205 | 0.020416 | -1.4521 | -0.0091024 | -0.0056226 | 0.015321 | -0.0021575 | -0.16479 | -0.21057 | -0.045776 | -0.13275 | -0.054932 | -0.14648 | -0.16022 | -0.1236 | -0.07782 | -0.027466 | -0.07782 | -0.064087 | -0.09613 | 0.022888 | 0.14191 | -122.2229 | -122.1451 | 0.13275 | 0.027466 | 0.041199 | -0.11444 | -0.10071 | 0.16022 | -122.0901 | -122.0901 | 0.1236 | 0.21057 | 0.091553 | 0.050354 | -0.068664 | -0.009156 | -0.086975 | -0.036621 | -0.050354 | -0.1648 | -0.050354 | -0.022888 | 0.10986 | -122.0581 | -122.0398 | 0.054932 | 0.10986 | 0.022888 | 0.064087
3927.7188 | 122.2092 | -0.16022 | 122.0123 | -0.02861 | 6.9825 | 0.012625 | 0.020563 | 0.0045501 | -0.0048428 | -2.1434e-05 | -0.0028687 | 0.019989 | -1.4538 | 0.00093783 | -0.005409 | 0.015962 | 0.00083309 | -0.13733 | -0.21057 | -0.041199 | -0.09613 | -0.004578 | -0.086975 | -0.10071 | -0.068665 | -0.091553 | -0.032043 | -0.027466 | 0.027466 | -0.013733 | 0.059509 | 0.11902 | -122.2229 | -122.1085 | 0.15564 | 0.059509 | 0.073242 | -0.059509 | -0.045776 | 0.12817 | -122.1039 | -122.0398 | 0.18768 | 0.21973 | 0.14648 | 0.091552 | 0.01831 | 0.036621 | -0.054931 | 0.059509 | 0.004577 | -0.16937 | -0.05951 | -0.050354 | 0.068664 | -122.0535 | -122.0444 | 0.064087 | 0.13275 | 0.022888 | 0.091552
3929.4375 | 122.1909 | -0.1831 | 122.0032 | 0.0019074 | 6.9823 | 0.013266 | 0.022059 | 6.4114e-05 | -0.0014248 | -2.1434e-05 | -0.0059205 | 0.020843 | -1.4525 | -0.0069662 | -0.0094678 | 0.013612 | -0.0015167 | -0.13275 | -0.2243 | -0.036621 | -0.10529 | 0.013733 | -0.064087 | -0.11902 | -0.068665 | -0.068665 | -0.022888 | -0.022888 | -0.009155 | -0.050354 | 0.050354 | 0.14648 | -122.2275 | -122.1085 | 0.19684 | 0.064086 | 0.11902 | -0.082398 | -0.027466 | 0.16022 | -122.0718 | -122.0261 | 0.17395 | 0.23346 | 0.13275 | 0.073242 | -0.027466 | 0.050354 | -0.068665 | 0.013733 | 0 | -0.18768 | -0.045777 | -0.041199 | 0.11444 | -122.0398 | -122.0261 | 0.077819 | 0.16022 | 0.050354 | 0.11444
3931.2344 | 122.1863 | -0.17853 | 122.0352 | -0.013352 | 6.9827 | 0.011984 | 0.021631 | -0.0014313 | -0.0056972 | -0.0015166 | 0.00018312 | 0.020843 | -1.4523 | -0.006539 | -0.01139 | 0.016175 | 0.0029693 | -0.1831 | -0.20142 | -0.054932 | -0.17853 | -0.064087 | -0.1236 | -0.14191 | -0.16022 | -0.082397 | -0.036621 | -0.082397 | -0.022888 | -0.050354 | 0.027466 | 0.1236 | -122.2366 | -122.2137 | 0.11444 | 0.036621 | 0.054932 | -0.086975 | -0.068664 | 0.14191 | -122.1176 | -122.1176 | 0.15564 | 0.20599 | 0.12817 | 0.064087 | -0.013733 | -0.009155 | -0.1236 | 0.013733 | -0.045776 | -0.14648 | -0.045776 | -0.022888 | 0.096131 | -122.0901 | -122.0718 | 0 | 0.096131 | -0.004577 | 0.018311
3933.0156 | 122.2504 | -0.14191 | 121.9986 | 0.0019074 | 6.9803 | 0.014548 | 0.020777 | 0.0013459 | -0.0029202 | 0.00083317 | -0.0089723 | 0.015716 | -1.4521 | 0.0011514 | -0.0049818 | 0.015107 | 0.0042511 | -0.11902 | -0.25177 | -0.004578 | -0.041199 | 0.082397 | -0.041199 | -0.068665 | 0.013733 | -0.11902 | -0.013733 | 0.036621 | 0.082397 | 0.045776 | 0.11902 | 0.13733 | -122.2504 | -122.0398 | 0.2243 | 0.073242 | 0.10071 | -0.064087 | -0.036621 | 0.12817 | -122.1176 | -121.962 | 0.2243 | 0.26093 | 0.18768 | 0.13275 | 0.059509 | 0.086975 | -0.036621 | 0.09613 | 0.050354 | -0.24719 | -0.10529 | -0.10986 | 0.022888 | -122.0032 | -122.0123 | 0.10071 | 0.17853 | 0.022888 | 0.15564
3934.7969 | 122.2092 | -0.16937 | 122.0398 | -0.020981 | 6.9814 | 0.012839 | 0.022486 | -0.00057689 | -0.0031338 | -0.00087583 | -0.0028687 | 0.022979 | -1.4514 | -0.0016256 | -0.0086132 | 0.014894 | -0.0015167 | -0.12817 | -0.2243 | -0.036621 | -0.09613 | 0 | -0.082397 | -0.11444 | -0.068665 | -0.10071 | -0.009155 | -0.032043 | 0.013733 | -0.032043 | 0.059509 | 0.13275 | -122.2641 | -122.1359 | 0.16937 | 0.054932 | 0.086976 | -0.07782 | -0.045776 | 0.16022 | -122.1405 | -122.0718 | 0.18311 | 0.22888 | 0.13733 | 0.068664 | -0.022888 | 0.036621 | -0.059509 | 0.022888 | -0.022888 | -0.18768 | -0.091553 | -0.054931 | 0.068665 | -122.0764 | -122.049 | 0.073243 | 0.13733 | 0.041199 | 0.10071
3936.5 | 122.2549 | -0.14191 | 122.0169 | -0.020981 | 6.9782 | 0.0096343 | 0.0227 | -0.0022857 | -0.0056972 | -0.00066223 | -0.0089723 | 0.017639 | -1.4527 | 0.0041422 | -0.006477 | 0.015748 | 0.0066009 | -0.15564 | -0.2243 | -0.027466 | -0.11444 | 0.004578 | -0.064087 | -0.091553 | -0.068665 | -0.09613 | -0.013733 | 0.004578 | 0.054932 | 0.027466 | 0.086975 | 0.11444 | -122.2412 | -122.1313 | 0.14649 | 0.050354 | 0.07782 | -0.064087 | -0.036621 | 0.12817 | -122.113 | -122.0123 | 0.19684 | 0.22888 | 0.16937 | 0.10071 | 0.041199 | 0.032044 | -0.086975 | 0.068665 | 0.018311 | -0.19684 | -0.082397 | -0.082397 | 0.045777 | -122.0444 | -122.0306 | 0.027466 | 0.14649 | -0.013733 | 0.073242
3938.2812 | 122.2641 | -0.16022 | 122.0078 | -0.013352 | 6.9761 | 0.010703 | 0.019922 | -0.0014313 | -0.0031338 | 0.00040597 | -0.012024 | 0.016784 | -1.4536 | 0.00051063 | -0.0073316 | 0.015962 | -0.00023491 | -0.16022 | -0.24261 | -0.041199 | -0.10071 | 0.013733 | -0.054932 | -0.091553 | -0.073242 | -0.11444 | -0.009155 | 0.004578 | 0.041199 | 0.013733 | 0.07782 | 0.11902 | -122.2504 | -122.1085 | 0.17395 | 0.068664 | 0.10528 | -0.050354 | -0.013733 | 0.15106 | -122.1222 | -122.0032 | 0.20142 | 0.23804 | 0.17395 | 0.086975 | 0.022888 | 0.054932 | -0.059509 | 0.050354 | 0.013733 | -0.20142 | -0.10529 | -0.082398 | 0.045776 | -122.049 | -122.0169 | 0.059509 | 0.16479 | 0 | 0.086975
3940.0625 | 122.1497 | -0.17853 | 122.0718 | -0.013352 | 6.9836 | 0.010916 | 0.02334 | 0.0034821 | -0.00035684 | 0.002115 | -0.0089723 | 0.021484 | -1.4536 | -0.0050436 | -0.0039136 | 0.014039 | 0.0010467 | -0.16479 | -0.20599 | -0.041199 | -0.16479 | -0.10529 | -0.16022 | -0.17853 | -0.17853 | -0.064087 | -0.032043 | -0.082397 | -0.082397 | -0.11444 | 0.004578 | 0.13733 | -122.2778 | -122.2366 | 0.073242 | 0 | 0.018311 | -0.13733 | -0.11902 | 0.14648 | -122.1359 | -122.1542 | 0.096131 | 0.18311 | 0.064087 | 0.036621 | -0.082398 | -0.064087 | -0.1236 | -0.050354 | -0.050354 | -0.1648 | -0.032044 | -0.027466 | 0.11444 | -122.113 | -122.1039 | 0.013733 | 0.096131 | 0.013733 | 0
3941.7812 | 122.2595 | -0.13733 | 122.0306 | -0.0057221 | 6.9803 | 0.011984 | 0.019282 | 0.0017731 | -0.001852 | -0.001944 | -0.0059205 | 0.018493 | -1.4525 | 0.0017922 | -0.0062634 | 0.016816 | 0.0019013 | -0.10986 | -0.25177 | -0.027466 | -0.041199 | 0.064087 | -0.036621 | -0.054932 | 0.013733 | -0.1236 | -0.013733 | 0.009155 | 0.050354 | 0.018311 | 0.09613 | 0.10986 | -122.2824 | -122.0718 | 0.20142 | 0.082397 | 0.10071 | -0.027466 | -0.009155 | 0.1236 | -122.1542 | -122.0215 | 0.18768 | 0.23346 | 0.15564 | 0.10986 | 0.032044 | 0.091553 | -0.013733 | 0.064087 | 0.022888 | -0.2243 | -0.10986 | -0.11444 | 0.013733 | -122.0581 | -122.0444 | 0.09613 | 0.14648 | 0.027466 | 0.15106
3943.5 | 122.2183 | -0.17395 | 122.0169 | -0.013352 | 6.9812 | 0.010703 | 0.02334 | 0.0024139 | -0.002493 | -0.0025848 | -0.0028687 | 0.022766 | -1.4533 | -0.0018394 | -0.0096814 | 0.014039 | 0.0016877 | -0.13275 | -0.20599 | -0.064087 | -0.11444 | -0.018311 | -0.091553 | -0.11444 | -0.091553 | -0.09613 | -0.022888 | -0.022888 | 0.018311 | -0.022888 | 0.064087 | 0.10986 | -122.2229 | -122.1313 | 0.15564 | 0.059509 | 0.082397 | -0.050354 | -0.027466 | 0.15106 | -122.113 | -122.0398 | 0.19226 | 0.23804 | 0.15106 | 0.086975 | 0 | 0.045776 | -0.050354 | 0.041199 | 0 | -0.14191 | -0.073242 | -0.032044 | 0.07782 | -122.081 | -122.0398 | 0.059509 | 0.15106 | 0.041199 | 0.082397
3945.2812 | 122.3007 | -0.13275 | 122.0032 | -0.013352 | 6.9803 | 0.011771 | 0.020136 | -0.0018585 | -0.0029202 | -0.0025848 | -0.0059205 | 0.019775 | -1.4514 | 0.0079874 | -0.0045544 | 0.016389 | -0.00044851 | -0.11902 | -0.24261 | -0.036621 | -0.054932 | 0.041199 | -0.045776 | -0.064087 | 0.013733 | -0.11444 | -0.013733 | 0.054932 | 0.086975 | 0.045776 | 0.13275 | 0.09613 | -122.2458 | -122.0581 | 0.17395 | 0.068664 | 0.086975 | -0.027466 | -0.009155 | 0.11902 | -122.1176 | -121.9482 | 0.21973 | 0.2655 | 0.17853 | 0.14648 | 0.059509 | 0.07782 | -0.018311 | 0.10071 | 0.068665 | -0.20599 | -0.10071 | -0.10986 | 0.01831 | -122.0398 | -122.0169 | 0.077819 | 0.18768 | 0.013732 | 0.14648
3947.0625 | 122.1954 | -0.16937 | 122.0856 | 0.0095369 | 6.981 | 0.011557 | 0.023127 | 0.00070491 | -0.002493 | -0.0025848 | -0.0028687 | 0.021698 | -1.4531 | -0.0018394 | -0.0075452 | 0.014039 | 0.0053193 | -0.17853 | -0.19684 | -0.045776 | -0.17853 | -0.091553 | -0.15106 | -0.16479 | -0.14191 | -0.086975 | -0.032043 | -0.068665 | -0.059509 | -0.086975 | 0.027466 | 0.1236 | -122.2824 | -122.2641 | 0.07782 | 0.004578 | 0.018311 | -0.11902 | -0.10529 | 0.13733 | -122.1725 | -122.1542 | 0.10986 | 0.19684 | 0.082398 | 0.059509 | -0.054932 | -0.045777 | -0.13275 | -0.027466 | -0.036622 | -0.15106 | -0.054932 | -0.027465 | 0.082398 | -122.1313 | -122.1176 | -0.009155 | 0.10071 | -0.009155 | 0.027466
3948.8438 | 122.2137 | -0.18768 | 122.0215 | -0.013352 | 6.9778 | 0.012198 | 0.020777 | 0.00049131 | -0.004202 | -0.0017304 | -0.0059205 | 0.019134 | -1.4533 | -0.0018394 | -0.01075 | 0.016175 | 0.0016877 | -0.17395 | -0.20599 | -0.064087 | -0.14191 | -0.050354 | -0.10986 | -0.1236 | -0.12817 | -0.09613 | -0.036621 | -0.064087 | -0.018311 | -0.032043 | 0.050354 | 0.1236 | -122.2275 | -122.1634 | 0.13733 | 0.064087 | 0.07782 | -0.059509 | -0.045776 | 0.15106 | -122.1176 | -122.0856 | 0.16937 | 0.23804 | 0.15564 | 0.086975 | 0.004578 | 0.013733 | -0.07782 | 0.01831 | -0.027466 | -0.14191 | -0.059509 | -0.018311 | 0.091553 | -122.0856 | -122.0581 | 0.045776 | 0.1236 | 0.013733 | 0.059509
3950.5469 | 122.2687 | -0.15564 | 122.0444 | -0.0057221 | 6.9786 | 0.014548 | 0.021845 | -0.00036309 | -0.0031338 | -0.0017304 | -0.0028687 | 0.021484 | -1.4529 | -0.0046164 | -0.004768 | 0.014894 | -0.0015167 | -0.16937 | -0.2243 | -0.050354 | -0.12817 | -0.036621 | -0.12817 | -0.11902 | -0.068665 | -0.10529 | -0.022888 | 0.004578 | 0.027466 | 0 | 0.10071 | 0.10529 | -122.2687 | -122.1725 | 0.11902 | 0.036621 | 0.027466 | -0.068665 | -0.07782 | 0.13275 | -122.1497 | -122.0398 | 0.18311 | 0.25635 | 0.15564 | 0.1236 | 0.022888 | 0.013733 | -0.07782 | 0.050354 | 0.027466 | -0.17395 | -0.082398 | -0.068664 | 0.050354 | -122.0947 | -122.0673 | 0.027466 | 0.16022 | -0.013733 | 0.086975
3952.3281 | 122.168 | -0.17853 | 122.0535 | -0.013352 | 6.9784 | 0.010916 | 0.021631 | 0.0028411 | -0.0027066 | 0.0016876 | -0.0059205 | 0.020202 | -1.4544 | -0.001412 | -0.0075452 | 0.015321 | -0.0042939 | -0.15106 | -0.23804 | -0.054932 | -0.14648 | -0.054932 | -0.14648 | -0.16937 | -0.15106 | -0.086975 | -0.022888 | -0.091553 | -0.064087 | -0.10529 | 0.013733 | 0.1236 | -122.2916 | -122.2 | 0.1236 | 0.009155 | 0.032044 | -0.11444 | -0.091552 | 0.15564 | -122.1405 | -122.1451 | 0.11444 | 0.19226 | 0.073242 | 0.036621 | -0.082398 | 0 | -0.091552 | -0.041199 | -0.068665 | -0.1831 | -0.064087 | -0.059509 | 0.091553 | -122.1085 | -122.0764 | 0.032044 | 0.086975 | 0.027466 | 0.027466
3954.1094 | 122.2778 | -0.14648 | 122.0261 | -0.013352 | 6.9782 | 0.014121 | 0.021845 | -0.0035675 | -0.00057044 | -2.1434e-05 | -0.0059205 | 0.01828 | -1.4533 | -0.0011984 | -0.0058362 | 0.014466 | 0.0036103 | -0.13275 | -0.25635 | -0.013733 | -0.059509 | 0.064087 | -0.059509 | -0.059509 | -0.013733 | -0.12817 | 0.004578 | 0.004578 | 0.050354 | 0.018311 | 0.091553 | 0.13275 | -122.2824 | -122.0856 | 0.21057 | 0.086975 | 0.086975 | -0.045776 | -0.045776 | 0.15106 | -122.1542 | -122.0215 | 0.19684 | 0.23804 | 0.16479 | 0.086975 | 0.013733 | 0.07782 | -0.045776 | 0.045776 | 0 | -0.24262 | -0.13275 | -0.10986 | 0.01831 | -122.0398 | -122.0215 | 0.086975 | 0.15106 | 0.013733 | 0.13275
3955.9062 | 122.3099 | -0.14191 | 122.0261 | -0.013352 | 6.9793 | 0.010916 | 0.019495 | 0.0013459 | -0.0046292 | 0.00040597 | -0.0028687 | 0.01828 | -1.4533 | -0.0016256 | -0.008827 | 0.014039 | -0.00066231 | -0.10529 | -0.23804 | -0.009155 | -0.022888 | 0.091553 | 0.009155 | -0.022888 | 0.013733 | -0.10986 | 0 | 0.032043 | 0.10071 | 0.086975 | 0.10071 | 0.13275 | -122.2641 | -122.0489 | 0.23346 | 0.11902 | 0.15106 | -0.013733 | 0.01831 | 0.14191 | -122.1359 | -121.994 | 0.24262 | 0.24262 | 0.22888 | 0.10071 | 0.086975 | 0.10071 | -0.013733 | 0.10071 | 0.032043 | -0.22888 | -0.10986 | -0.09613 | 0.032044 | -122.0352 | -122.0261 | 0.11902 | 0.17395 | 0.036621 | 0.15564
3957.625 | 122.2458 | -0.17395 | 122.049 | -0.020981 | 6.9803 | 0.012625 | 0.020563 | -0.0052765 | -0.0029202 | 0.0012604 | -0.0028687 | 0.021911 | -1.454 | -0.0086752 | -0.0086132 | 0.013612 | -0.0023713 | -0.15106 | -0.21973 | -0.068665 | -0.11902 | -0.036621 | -0.082397 | -0.11902 | -0.10529 | -0.082397 | -0.027466 | -0.045776 | 0.004578 | -0.018311 | 0.059509 | 0.10528 | -122.2687 | -122.168 | 0.13733 | 0.054931 | 0.091553 | -0.050354 | -0.013732 | 0.14648 | -122.1313 | -122.0947 | 0.17853 | 0.23346 | 0.15564 | 0.086975 | 0.009155 | 0.032044 | -0.050354 | 0.032044 | -0.01831 | -0.15106 | -0.054931 | -0.045777 | 0.091553 | -122.1176 | -122.0764 | 0.054931 | 0.12817 | 0.022888 | 0.068664
3959.4062 | 122.3145 | -0.13275 | 122.0352 | -0.0057221 | 6.978 | 0.012198 | 0.017145 | -0.0035675 | -0.0046292 | -0.0017304 | -0.0059205 | 0.017639 | -1.4542 | -0.0091024 | -0.0069044 | 0.01468 | -0.00023491 | -0.10986 | -0.24719 | -0.032043 | -0.032043 | 0.1236 | 0.027466 | -0.009155 | 0.018311 | -0.11902 | 0 | 0.032043 | 0.091553 | 0.082397 | 0.11902 | 0.10071 | -122.2824 | -122.0673 | 0.25635 | 0.1236 | 0.16022 | 0.022888 | 0.059509 | 0.13275 | -122.1542 | -122.0032 | 0.2243 | 0.25177 | 0.21515 | 0.11902 | 0.082397 | 0.15564 | 0 | 0.091553 | 0.032043 | -0.21515 | -0.11902 | -0.11444 | 0.013732 | -122.0673 | -122.0352 | 0.10071 | 0.16479 | 0.022888 | 0.15106
3961.2031 | 122.2092 | -0.17395 | 122.1039 | -0.0057221 | 6.981 | 0.011557 | 0.021418 | 0.00027771 | -0.0046292 | -0.003012 | -0.0089723 | 0.021698 | -1.4538 | -0.00034397 | -0.0086132 | 0.014253 | 0.0036103 | -0.11444 | -0.22888 | -0.036621 | -0.10986 | 0.004578 | -0.054932 | -0.09613 | -0.10986 | -0.10071 | -0.027466 | -0.082397 | -0.013733 | -0.068665 | 0.013733 | 0.13733 | -122.3328 | -122.2137 | 0.17853 | 0.07782 | 0.11902 | -0.059509 | -0.018311 | 0.14648 | -122.2046 | -122.1863 | 0.16022 | 0.18768 | 0.10528 | 0.041199 | -0.041199 | 0.041199 | -0.073242 | 0.013733 | -0.054931 | -0.19226 | -0.073242 | -0.054932 | 0.073242 | -122.1405 | -122.1313 | 0.064087 | 0.091553 | 0.059509 | 0.064087

## Thermal Data
Fire Time | B Position - Tray - Middle | B Position - Kerite 10c w | C Position - 3' | C Position - Middle | C Position - 7' | C Position - Kerite 9c wo - 3' | C Position - Kerite 9c wo - 5'
-0.7458 | 6.9459 | 6.5455 | 6.9914 | 7.2213 | 7.0329 | 6.7228 | 6.8222
0.2542 | 6.9455 | 6.5436 | 6.9937 | 7.2202 | 7.0358 | 6.7205 | 6.8177
1.2542 | 6.9468 | 6.5485 | 6.9969 | 7.2181 | 7.029 | 6.7213 | 6.8243
2.2542 | 6.9465 | 6.5478 | 7.0033 | 7.2262 | 7.0326 | 6.7201 | 6.8147
3.2542 | 6.9509 | 6.5469 | 7.0092 | 7.2266 | 7.0423 | 6.7214 | 6.8239
4.2542 | 6.9506 | 6.5495 | 7.0036 | 7.2282 | 7.0355 | 6.73 | 6.8166
5.2542 | 6.9509 | 6.5572 | 7.0058 | 7.2359 | 7.0429 | 6.7231 | 6.8121
6.2542 | 6.9773 | 6.5516 | 7.0078 | 7.2319 | 7.0399 | 6.7246 | 6.8154
7.2542 | 7.0348 | 6.5425 | 7.0088 | 7.2339 | 7.0457 | 6.7213 | 6.8118
8.2542 | 7.0484 | 6.5535 | 7.011 | 7.3001 | 7.0543 | 6.7273 | 6.813
9.2542 | 7.0588 | 6.5508 | 7.0006 | 7.4777 | 7.105 | 6.7313 | 6.8089
10.2542 | 7.103 | 6.5431 | 7.1219 | 7.477 | 7.1169 | 6.7281 | 6.8
11.2542 | 7.2094 | 6.5438 | 7.1855 | 7.6948 | 7.14 | 6.7309 | 6.7956
12.2542 | 7.5569 | 6.5412 | 7.304 | 8.2099 | 7.2221 | 6.7342 | 6.7897
13.2542 | 8.8426 | 6.54 | 7.563 | 8.5462 | 7.3512 | 6.7303 | 6.7741
14.2542 | 9.6693 | 6.545 | 7.7673 | 8.9959 | 7.6475 | 6.7391 | 6.76
15.2542 | 11.341 | 6.5465 | 8.1486 | 9.5822 | 8.687 | 6.7466 | 6.7469
16.2542 | 13.3611 | 6.5485 | 9.59 | 10.4633 | 9.6805 | 6.7612 | 6.7304
17.2542 | 15.8833 | 6.5474 | 10.4086 | 11.2484 | 10.3039 | 6.7561 | 6.7181
18.2542 | 17.628 | 6.5549 | 11.0298 | 13.4245 | 11.3543 | 6.7717 | 6.6907
19.2542 | 18.8576 | 6.5434 | 12.1129 | 14.3951 | 12.1259 | 6.7707 | 6.6806
20.2542 | 21.6899 | 6.5378 | 13.1295 | 15.8318 | 13.1123 | 6.7747 | 6.6729
21.2542 | 24.1217 | 6.528 | 15.0614 | 17.7202 | 13.6728 | 6.7829 | 6.6602
22.2542 | 25.0984 | 6.5347 | 15.7705 | 19.7484 | 14.308 | 6.7737 | 6.6616
23.2542 | 27.1843 | 6.5356 | 16.9007 | 21.6799 | 15.0786 | 6.7916 | 6.6393
24.2542 | 27.9831 | 6.5273 | 17.8707 | 23.8629 | 15.6637 | 6.8044 | 6.6686
25.2542 | 30.2741 | 6.5354 | 18.5838 | 26.3846 | 16.526 | 6.8025 | 6.6626
26.2542 | 32.5357 | 6.537 | 20.2643 | 28.2265 | 19.3815 | 6.8088 | 6.6649
27.2542 | 34.7383 | 6.5448 | 21.3764 | 30.426 | 20.5407 | 6.8028 | 6.6756
28.2542 | 37.4092 | 6.5493 | 23.0077 | 33.2593 | 22.8231 | 6.8087 | 6.649
29.2542 | 39.3317 | 6.5486 | 24.9229 | 35.2882 | 23.9886 | 6.8166 | 6.6528
30.2542 | 42.1964 | 6.5555 | 25.4433 | 37.7062 | 25.0062 | 6.818 | 6.6429
31.2542 | 45.1644 | 6.5571 | 25.9407 | 39.4146 | 26.5602 | 6.8129 | 6.6281
32.2542 | 48.3349 | 6.5628 | 27.2482 | 41.4408 | 28.0524 | 6.8195 | 6.655
33.2542 | 50.8008 | 6.568 | 27.9811 | 44.402 | 28.5047 | 6.8368 | 6.6536
34.2542 | 52.7783 | 6.5706 | 28.4002 | 47.2561 | 28.8682 | 6.8444 | 6.6576
35.2542 | 54.6426 | 6.5787 | 29.4369 | 49.0613 | 30.4269 | 6.8429 | 6.643
36.2542 | 56.5045 | 6.59 | 30.2103 | 51.4614 | 32.0836 | 6.8539 | 6.6834
37.2542 | 57.8451 | 6.595 | 31.3272 | 53.6275 | 33.2464 | 6.8607 | 6.6861
38.2542 | 59.7615 | 6.6069 | 32.4985 | 55.8601 | 34.2692 | 6.8699 | 6.6624
39.2542 | 60.4924 | 6.6092 | 33.3001 | 57.6286 | 36.039 | 6.8768 | 6.6888
40.2542 | 61.4304 | 6.6123 | 34.2745 | 60.1118 | 38.9724 | 6.9099 | 6.667
41.2542 | 62.9922 | 6.6161 | 34.7399 | 62.636 | 40.4397 | 6.9074 | 6.6852
42.2542 | 64.6949 | 6.627 | 35.7567 | 65.4043 | 41.5289 | 6.9168 | 6.6987
43.2542 | 65.8914 | 6.6393 | 37.0365 | 67.0128 | 43.0406 | 6.92 | 6.7105
44.2542 | 68.2582 | 6.6475 | 38.581 | 68.1582 | 44.6941 | 6.9418 | 6.6984
45.2542 | 69.8379 | 6.6543 | 39.666 | 69.5349 | 45.7061 | 6.9534 | 6.686
46.2542 | 70.9742 | 6.6717 | 40.0104 | 70.2201 | 47.1377 | 6.9646 | 6.7063
47.2542 | 72.9734 | 6.6704 | 41.0189 | 70.8696 | 48.7756 | 6.9819 | 6.704
48.2542 | 74.4852 | 6.6715 | 41.766 | 72.3552 | 49.8471 | 7.0038 | 6.7009
49.2542 | 75.3463 | 6.6751 | 42.3976 | 73.2851 | 50.5899 | 7.0309 | 6.6985
50.2542 | 75.6454 | 6.6905 | 43.6866 | 74.1363 | 51.1885 | 7.0401 | 6.7125
51.2542 | 76.5501 | 6.6993 | 44.6491 | 75.7589 | 52.6114 | 7.0628 | 6.7244
52.2542 | 77.6396 | 6.7185 | 45.6059 | 77.9176 | 53.6338 | 7.0609 | 6.7273
53.2542 | 79.0915 | 6.7183 | 46.7129 | 79.4053 | 54.472 | 7.0832 | 6.6967
54.2542 | 80.521 | 6.7387 | 47.5502 | 80.7263 | 55.3528 | 7.0846 | 6.7149
55.2542 | 81.0083 | 6.7513 | 47.9824 | 81.4389 | 56.5644 | 7.1012 | 6.7405
56.2542 | 82.7023 | 6.7582 | 48.8358 | 82.2406 | 57.3584 | 7.1168 | 6.7395
57.2542 | 83.2151 | 6.7622 | 50.4066 | 83.45 | 59.4337 | 7.1464 | 6.7413
58.2542 | 83.9446 | 6.7767 | 51.3821 | 85.4174 | 62.0181 | 7.1602 | 6.7525
59.2542 | 84.5425 | 6.7889 | 51.9581 | 86.3072 | 62.6413 | 7.1975 | 6.7197
60.2542 | 84.2358 | 6.7939 | 52.4834 | 87.4649 | 62.9506 | 7.1987 | 6.7543
61.2542 | 85.7218 | 6.8198 | 52.5068 | 88.2835 | 63.4946 | 7.2193 | 6.7626
62.2542 | 86.426 | 6.8311 | 52.722 | 89.5235 | 64.2081 | 7.2469 | 6.7462
63.2542 | 86.9851 | 6.8413 | 54.0265 | 90.5917 | 66.7105 | 7.2674 | 6.7573
64.2542 | 88.7346 | 6.852 | 54.1369 | 91.5116 | 67.3961 | 7.2881 | 6.7534
65.2542 | 89.7996 | 6.8519 | 54.244 | 92.3449 | 67.824 | 7.306 | 6.7351
66.2542 | 90.9134 | 6.8592 | 54.7791 | 92.7258 | 68.7589 | 7.3284 | 6.7702
67.2542 | 92.8963 | 6.8745 | 54.8528 | 93.0279 | 69.9269 | 7.3594 | 6.7611
68.2542 | 93.2311 | 6.8869 | 55.6164 | 93.8316 | 70.4619 | 7.3754 | 6.728
69.2542 | 94.3379 | 6.8867 | 56.5891 | 94.4529 | 70.6359 | 7.4051 | 6.7635
70.2542 | 95.1889 | 6.9062 | 57.3885 | 95.1354 | 71.0954 | 7.4194 | 6.7428
71.2542 | 96.04 | 6.9074 | 58.7986 | 96.0737 | 71.8805 | 7.4504 | 6.7545
72.2542 | 96.8629 | 6.9251 | 59.6378 | 96.9502 | 71.985 | 7.4791 | 6.7409
73.2542 | 96.2415 | 6.9376 | 60.0713 | 98.4019 | 73.1836 | 7.5119 | 6.7641
74.2542 | 96.3362 | 6.9595 | 61.4135 | 100.0357 | 73.0961 | 7.5364 | 6.7257
75.2542 | 97.0661 | 6.9634 | 62.1961 | 101.1281 | 73.6192 | 7.5569 | 6.7647
76.2542 | 97.8939 | 6.9844 | 63.5014 | 102.3125 | 74.9341 | 7.5752 | 6.7818
77.2542 | 98.0117 | 6.9976 | 65.0557 | 103.5759 | 75.5703 | 7.6014 | 6.7902
78.2542 | 98.7829 | 7.0009 | 65.5802 | 104.6716 | 76.0072 | 7.6281 | 6.7528
79.2542 | 99.8439 | 7.0153 | 66.7217 | 105.578 | 76.889 | 7.6645 | 6.779
80.2542 | 101.0172 | 7.0226 | 69.0316 | 106.7081 | 78.722 | 7.6882 | 6.7616
81.2542 | 101.8575 | 7.0308 | 69.8156 | 106.7788 | 79.3931 | 7.7101 | 6.7524
82.2542 | 102.6192 | 7.0493 | 70.197 | 107.6918 | 79.8653 | 7.7429 | 6.7606
83.2542 | 103.3014 | 7.0718 | 70.4204 | 108.1948 | 80.5692 | 7.768 | 6.7546
84.2542 | 103.4777 | 7.0807 | 71.3213 | 108.6596 | 80.6706 | 7.7925 | 6.7709
85.2542 | 103.8378 | 7.105 | 72.1196 | 109.196 | 82.1221 | 7.8364 | 6.8048
86.2542 | 103.2477 | 7.1056 | 72.5573 | 109.916 | 83.7057 | 7.8733 | 6.77
87.2542 | 103.6961 | 7.1255 | 73.9893 | 110.9087 | 84.2198 | 7.8916 | 6.7882
88.2542 | 104.0243 | 7.1449 | 74.8396 | 111.963 | 85.192 | 7.9201 | 6.7938
89.2542 | 104.4681 | 7.1651 | 74.8984 | 112.4413 | 86.4612 | 7.9293 | 6.8351
90.2542 | 105.0805 | 7.1659 | 75.7124 | 112.828 | 87.8792 | 7.9726 | 6.8074
91.2542 | 105.5012 | 7.1796 | 76.1189 | 113.3344 | 88.6595 | 8.0143 | 6.7986
92.2542 | 105.7708 | 7.204 | 76.0419 | 113.8704 | 89.5171 | 8.0441 | 6.7902
93.2542 | 106.5532 | 7.2205 | 75.756 | 113.9975 | 89.7838 | 8.0886 | 6.766
94.2542 | 107.4135 | 7.2311 | 75.6518 | 114.0813 | 90.4552 | 8.1141 | 6.77
95.2542 | 107.9708 | 7.2477 | 76.2942 | 114.6355 | 90.5506 | 8.1431 | 6.7904
96.2542 | 108.1415 | 7.2618 | 76.7355 | 115.3345 | 91.0343 | 8.1637 | 6.7935
97.2542 | 108.1932 | 7.2838 | 78.0713 | 116.5301 | 91.0837 | 8.2031 | 6.7863
98.2542 | 108.1525 | 7.3067 | 78.6946 | 117.6672 | 92.6761 | 8.2231 | 6.8174
99.2542 | 108.0724 | 7.3224 | 78.5918 | 118.8912 | 93.3499 | 8.2546 | 6.8077
100.2542 | 108.7019 | 7.3531 | 78.3901 | 119.1071 | 94.2827 | 8.3006 | 6.8262
101.2542 | 109.6354 | 7.3755 | 80.2516 | 119.2613 | 94.8735 | 8.3151 | 6.8058
102.2542 | 109.912 | 7.3942 | 80.5624 | 119.9088 | 95.6798 | 8.3443 | 6.803
103.2542 | 109.8025 | 7.4087 | 80.9067 | 120.5774 | 95.6021 | 8.364 | 6.795
104.2542 | 110.12 | 7.4397 | 80.9153 | 121.0127 | 96.7719 | 8.4115 | 6.7928
105.2542 | 111.0456 | 7.447 | 80.9267 | 121.3465 | 97.8755 | 8.4392 | 6.8113
106.2542 | 112.2332 | 7.4691 | 80.3015 | 122.1305 | 97.977 | 8.4814 | 6.7718
107.2542 | 113.3235 | 7.4796 | 79.7844 | 122.5982 | 99.3196 | 8.5011 | 6.81
108.2542 | 114.0595 | 7.5079 | 79.6614 | 122.9181 | 99.4786 | 8.5464 | 6.7988
109.2542 | 114.8071 | 7.5263 | 81.3726 | 123.4685 | 99.9464 | 8.5741 | 6.7964
110.2542 | 115.6443 | 7.5456 | 82.0726 | 123.7447 | 100.4772 | 8.6123 | 6.7791
111.2542 | 115.5504 | 7.5739 | 82.1491 | 124.0856 | 101.0409 | 8.648 | 6.7957
112.2542 | 116.0658 | 7.6 | 82.8202 | 124.3726 | 101.4605 | 8.686 | 6.8
113.2542 | 115.8282 | 7.6223 | 83.8594 | 125.0074 | 101.6718 | 8.7065 | 6.8303
114.2542 | 115.7138 | 7.6551 | 85.7095 | 125.3412 | 102.2298 | 8.7304 | 6.8234
115.2542 | 116.1885 | 7.6862 | 87.1183 | 125.2315 | 102.167 | 8.7705 | 6.8511
116.2542 | 116.1467 | 7.6993 | 87.6322 | 125.3407 | 102.2115 | 8.8035 | 6.8389
117.2542 | 116.4033 | 7.7275 | 88.2349 | 125.8538 | 102.3783 | 8.8293 | 6.8396
118.2542 | 116.0215 | 7.7619 | 88.0965 | 126.0861 | 102.5207 | 8.8692 | 6.8537
119.2542 | 116.8627 | 7.7671 | 88.3356 | 126.8677 | 103.2101 | 8.9047 | 6.8287
120.2542 | 116.996 | 7.7883 | 87.6637 | 127.4985 | 103.3528 | 8.9343 | 6.8359
121.2542 | 117.4754 | 7.815 | 87.3178 | 127.4433 | 103.7075 | 8.9676 | 6.8498
122.2542 | 118.1413 | 7.8371 | 87.5025 | 127.7861 | 104.4715 | 8.9986 | 6.8447
123.2542 | 118.3314 | 7.8585 | 87.8841 | 128.5381 | 106.7556 | 9.0286 | 6.8505
124.2542 | 118.3443 | 7.8894 | 88.5061 | 128.6361 | 107.113 | 9.0594 | 6.8671
125.2542 | 117.9652 | 7.9232 | 89.1207 | 128.7853 | 107.3364 | 9.0801 | 6.8665
126.2542 | 118.2608 | 7.927 | 88.9217 | 128.6723 | 107.4075 | 9.1439 | 6.8509
127.2542 | 117.884 | 7.9725 | 89.1208 | 128.4366 | 107.2735 | 9.1717 | 6.8632
128.2542 | 117.9555 | 7.9916 | 89.6049 | 128.6391 | 106.4489 | 9.1982 | 6.8536
129.2542 | 118.1521 | 8.0217 | 90.6248 | 128.981 | 106.3126 | 9.2379 | 6.8457
130.2542 | 117.852 | 8.0465 | 91.1139 | 129.2126 | 106.7448 | 9.2841 | 6.8784
131.2542 | 118.1427 | 8.0544 | 91.5085 | 129.4595 | 106.4549 | 9.3138 | 6.8574
132.2542 | 118.209 | 8.0917 | 92.4044 | 129.9379 | 106.7173 | 9.3522 | 6.8416
133.2542 | 118.6518 | 8.122 | 92.7877 | 130.7572 | 107.3875 | 9.3873 | 6.858
134.2542 | 119.2052 | 8.1449 | 92.2716 | 131.0459 | 107.7728 | 9.4169 | 6.8707
135.2542 | 118.8616 | 8.1678 | 92.1441 | 131.5077 | 107.6324 | 9.4527 | 6.8617
136.2542 | 118.5203 | 8.1991 | 93.2461 | 131.8383 | 108.0467 | 9.4821 | 6.8699
137.2542 | 118.1272 | 8.2413 | 92.4915 | 131.7569 | 108.0384 | 9.5171 | 6.8946
138.2542 | 118.5329 | 8.2608 | 92.2004 | 131.6119 | 108.6524 | 9.5576 | 6.8847
139.2542 | 119.1377 | 8.3042 | 91.6204 | 131.6558 | 108.6658 | 9.5879 | 6.8954
140.2542 | 119.6419 | 8.3182 | 91.8095 | 131.8688 | 108.9726 | 9.6111 | 6.9029
141.2542 | 120.335 | 8.3444 | 91.2231 | 131.9171 | 109.3517 | 9.6495 | 6.8875
142.2542 | 120.9305 | 8.3648 | 90.7126 | 132.3443 | 109.6317 | 9.6916 | 6.8835
143.2542 | 121.2083 | 8.3972 | 90.1959 | 132.3046 | 110.0515 | 9.7312 | 6.8648
144.2542 | 120.9238 | 8.4277 | 90.2151 | 132.548 | 110.2728 | 9.7693 | 6.8745
145.2542 | 121.5384 | 8.4529 | 90.5236 | 132.8314 | 111.0368 | 9.7868 | 6.8827
146.2542 | 122.3675 | 8.4802 | 90.785 | 133.139 | 111.4273 | 9.8304 | 6.8837
147.2542 | 122.6261 | 8.5089 | 90.8639 | 133.3982 | 111.8955 | 9.8625 | 6.8895
148.2542 | 122.5429 | 8.5314 | 90.1463 | 134.1781 | 111.9089 | 9.8985 | 6.8923
149.2542 | 122.6202 | 8.5595 | 90.7783 | 134.8999 | 111.5371 | 9.9305 | 6.8832
150.2542 | 123.503 | 8.5908 | 90.9824 | 135.2082 | 111.8954 | 9.9749 | 6.9107
151.2542 | 123.1682 | 8.6086 | 90.8324 | 135.1879 | 112.4549 | 9.9972 | 6.9077
152.2542 | 123.1844 | 8.6395 | 90.7417 | 135.7222 | 112.1293 | 10.0389 | 6.8877
153.2542 | 123.489 | 8.6692 | 91.1061 | 135.8992 | 112.5019 | 10.0774 | 6.9066
154.2542 | 123.9866 | 8.6949 | 91.2082 | 136.2497 | 112.8614 | 10.1264 | 6.9386
155.2542 | 124.4334 | 8.7316 | 91.0277 | 136.3285 | 112.5296 | 10.151 | 6.9447
156.2542 | 125.3481 | 8.7589 | 90.9066 | 136.2509 | 112.5582 | 10.1935 | 6.9617
157.2542 | 125.544 | 8.7877 | 91.5265 | 136.1361 | 112.5009 | 10.2292 | 6.9405
158.2542 | 126.009 | 8.8187 | 90.8025 | 136.0937 | 112.3196 | 10.2726 | 6.9367
159.2542 | 125.7384 | 8.8525 | 90.3294 | 136.2496 | 111.8617 | 10.3122 | 6.9569
160.2542 | 126.0279 | 8.8904 | 90.477 | 136.1614 | 111.6513 | 10.3476 | 6.9687
161.2542 | 126.0776 | 8.9232 | 90.1273 | 135.8582 | 111.8391 | 10.39 | 6.9657
162.2542 | 126.3958 | 8.9588 | 89.4418 | 135.5166 | 112.1648 | 10.4485 | 6.9456
163.2542 | 126.5799 | 8.9871 | 89.1508 | 135.2433 | 112.3123 | 10.4815 | 6.9447
164.2542 | 126.5273 | 9.0183 | 88.733 | 135.4017 | 112.3535 | 10.5313 | 6.9582
165.2542 | 127.185 | 9.0703 | 88.9698 | 135.4997 | 112.0718 | 10.5668 | 6.9768
166.2542 | 127.0154 | 9.0915 | 89.1567 | 135.6131 | 112.2301 | 10.6064 | 6.9942
167.2542 | 127.2835 | 9.1146 | 88.8769 | 135.9427 | 112.2736 | 10.6548 | 6.9539
168.2542 | 127.7558 | 9.157 | 88.5785 | 136.3506 | 112.4641 | 10.6916 | 6.9722
169.2542 | 128.091 | 9.1923 | 88.655 | 136.1293 | 112.4481 | 10.7373 | 6.9662
170.2542 | 128.5905 | 9.2179 | 89.1939 | 135.8843 | 112.1924 | 10.7716 | 6.9977
171.2542 | 128.3036 | 9.2639 | 89.2196 | 135.7224 | 112.304 | 10.8224 | 6.9555
172.2542 | 128.4204 | 9.3023 | 89.4584 | 135.6712 | 112.4905 | 10.8521 | 6.953
173.2542 | 128.4884 | 9.335 | 89.2324 | 135.5618 | 112.6991 | 10.9049 | 6.9636
174.2542 | 128.712 | 9.3566 | 89.2108 | 136.0569 | 112.5524 | 10.9542 | 6.9895
175.2542 | 129.3063 | 9.3951 | 89.6184 | 136.2017 | 113.6186 | 11.016 | 6.9843
176.2542 | 129.6364 | 9.4318 | 89.9075 | 136.1247 | 113.5856 | 11.0683 | 6.9821
177.2542 | 130.2139 | 9.469 | 89.9026 | 136.2345 | 113.324 | 11.1066 | 6.9856
178.2542 | 130.9931 | 9.5073 | 90.6629 | 136.8084 | 113.5707 | 11.1553 | 6.9906
179.2542 | 130.9299 | 9.5351 | 91.2954 | 137.0739 | 114.3934 | 11.2127 | 7.0027
180.2542 | 131.3731 | 9.5599 | 92.1836 | 137.1816 | 115.3651 | 11.2409 | 7.0009
181.2542 | 131.4027 | 9.5987 | 91.8098 | 138.2904 | 115.3775 | 11.2997 | 7.0022
182.2542 | 131.0217 | 9.6324 | 91.661 | 138.8897 | 115.405 | 11.3386 | 7.0056
183.2542 | 130.5374 | 9.6698 | 91.9599 | 139.3494 | 115.3595 | 11.4044 | 6.9955
184.2542 | 129.6084 | 9.7051 | 93.2154 | 139.6735 | 115.6367 | 11.4454 | 6.999
185.2542 | 129.7689 | 9.7396 | 93.0782 | 139.8632 | 116.0148 | 11.488 | 7.0189
186.2542 | 130.2065 | 9.7712 | 93.7064 | 140.3703 | 116.0035 | 11.543 | 7.0305
187.2542 | 130.057 | 9.8136 | 94.5473 | 140.9504 | 115.5386 | 11.5794 | 7.0603
188.2542 | 130.0498 | 9.8514 | 95.1415 | 141.5215 | 115.545 | 11.609 | 7.0405
189.2542 | 129.4355 | 9.9049 | 95.7029 | 141.8446 | 116.1737 | 11.6599 | 7.0448
190.2542 | 129.4128 | 9.9372 | 96.7365 | 142.1887 | 116.695 | 11.7043 | 7.0261
191.2542 | 129.7493 | 9.9772 | 96.9787 | 142.152 | 117.4646 | 11.7502 | 7.0272
192.2542 | 129.6148 | 10.0133 | 97.613 | 141.8205 | 118.0423 | 11.7942 | 7.0574
193.2542 | 129.9145 | 10.052 | 98.5704 | 142.1698 | 118.1878 | 11.8324 | 7.0749
194.2542 | 130.3033 | 10.0816 | 98.5393 | 142.5863 | 118.0907 | 11.8904 | 7.0789
195.2542 | 130.2307 | 10.1391 | 98.4389 | 142.9326 | 118.6965 | 11.934 | 7.065
196.2542 | 130.6218 | 10.1645 | 98.0611 | 143.2002 | 119.152 | 11.9856 | 7.0746
197.2542 | 130.8616 | 10.2109 | 98.2857 | 143.9947 | 119.6786 | 12.0133 | 7.0933
198.2542 | 131.173 | 10.2503 | 98.5202 | 144.4576 | 119.6994 | 12.068 | 7.1008
199.2542 | 131.8837 | 10.2771 | 99.8756 | 144.49 | 119.7041 | 12.1208 | 7.096
200.2542 | 132.1969 | 10.328 | 101.5166 | 144.7779 | 120.3912 | 12.1568 | 7.0843
201.2542 | 132.7069 | 10.365 | 101.6138 | 144.9872 | 120.241 | 12.2068 | 7.0733
202.2542 | 133.426 | 10.4094 | 101.6452 | 145.3435 | 120.9009 | 12.2596 | 7.0877
203.2542 | 133.9439 | 10.4295 | 102.6618 | 145.5691 | 120.765 | 12.2835 | 7.1329
204.2542 | 133.6783 | 10.4804 | 102.8177 | 145.7887 | 120.6175 | 12.3205 | 7.1247
205.2542 | 133.7644 | 10.5175 | 102.8796 | 145.3337 | 120.4728 | 12.3679 | 7.1045
206.2542 | 134.1298 | 10.5673 | 102.2654 | 145.236 | 120.7496 | 12.4123 | 7.1126
207.2542 | 134.232 | 10.6138 | 102.4739 | 145.7367 | 120.4927 | 12.4507 | 7.1159
208.2542 | 134.4922 | 10.6483 | 102.0873 | 146.2494 | 120.454 | 12.5037 | 7.1307
209.2542 | 134.2211 | 10.6835 | 101.9183 | 146.4442 | 120.4882 | 12.557 | 7.1268
210.2542 | 134.6769 | 10.7207 | 101.8324 | 146.4953 | 120.6181 | 12.614 | 7.1428
211.2542 | 135.3138 | 10.7753 | 102.2005 | 146.6265 | 121.3261 | 12.6559 | 7.148
212.2542 | 135.3055 | 10.8075 | 102.0877 | 146.9659 | 121.0297 | 12.7033 | 7.1604
213.2542 | 136.1358 | 10.8497 | 102.1463 | 147.2687 | 121.021 | 12.7546 | 7.1718
214.2542 | 136.9314 | 10.895 | 101.9628 | 147.6129 | 121.2025 | 12.8088 | 7.1762
215.2542 | 137.7777 | 10.9448 | 101.8736 | 147.8106 | 121.4917 | 12.8507 | 7.2194
216.2542 | 137.6193 | 10.9751 | 101.4654 | 148.0954 | 121.0122 | 12.8982 | 7.1987
217.2542 | 137.8738 | 11.0168 | 101.908 | 148.1226 | 121.5157 | 12.9511 | 7.2096
218.2542 | 138.3137 | 11.0522 | 101.9163 | 148.351 | 121.6952 | 12.9983 | 7.1778
219.2542 | 138.3866 | 11.0886 | 102.1264 | 148.3684 | 121.7897 | 13.0371 | 7.2018
220.2542 | 139.5323 | 11.1404 | 102.6623 | 148.8668 | 121.8221 | 13.0791 | 7.2257
221.2542 | 140.0861 | 11.1903 | 102.7547 | 149.3513 | 122.3598 | 13.1516 | 7.2186
222.2542 | 139.6529 | 11.2401 | 102.5391 | 150.4959 | 122.3158 | 13.194 | 7.2144
223.2542 | 139.6013 | 11.2839 | 102.8413 | 150.9826 | 122.5879 | 13.251 | 7.2233
224.2542 | 140.0122 | 11.3244 | 103.5112 | 151.6116 | 122.8585 | 13.2848 | 7.2269
225.2542 | 140.8018 | 11.3742 | 103.8588 | 152.3916 | 122.3786 | 13.3515 | 7.229
226.2542 | 140.6459 | 11.435 | 104.0148 | 152.5217 | 123.2312 | 13.3979 | 7.2523
227.2542 | 141.4726 | 11.4815 | 103.4748 | 152.6195 | 123.2438 | 13.4537 | 7.2614
228.2542 | 142.0752 | 11.5247 | 102.9735 | 152.975 | 123.5162 | 13.4789 | 7.2534
229.2542 | 142.1384 | 11.5709 | 102.3998 | 152.849 | 124.7678 | 13.5273 | 7.2725
230.2542 | 142.3757 | 11.6143 | 102.5771 | 152.5743 | 124.7722 | 13.5782 | 7.2645
231.2542 | 142.3541 | 11.6592 | 102.2785 | 152.4207 | 125.3675 | 13.6174 | 7.3029
232.2542 | 141.906 | 11.7134 | 102.4686 | 152.0857 | 125.0648 | 13.6644 | 7.2934
233.2542 | 141.521 | 11.7558 | 102.8028 | 151.706 | 125.6677 | 13.709 | 7.3093
234.2542 | 141.6386 | 11.8065 | 102.6476 | 151.5293 | 125.2035 | 13.7597 | 7.295
235.2542 | 141.7815 | 11.85 | 103.096 | 151.5873 | 125.7709 | 13.8073 | 7.2882
236.2542 | 142.2247 | 11.9021 | 103.4198 | 152.1248 | 125.9434 | 13.8526 | 7.311
237.2542 | 143.7872 | 11.9581 | 103.7727 | 152.6212 | 126.4282 | 13.8819 | 7.321
238.2542 | 143.5703 | 12.0025 | 104.6943 | 152.662 | 126.1679 | 13.9206 | 7.3137
239.2542 | 144.1859 | 12.0624 | 106.0318 | 153.5137 | 126.4446 | 13.9733 | 7.358
240.2542 | 144.6507 | 12.103 | 106.586 | 153.2515 | 127.0414 | 14.0428 | 7.332
241.2542 | 144.9339 | 12.1576 | 106.3612 | 153.3873 | 127.09 | 14.0787 | 7.363
242.2542 | 145.8769 | 12.2118 | 106.3814 | 153.8485 | 127.8938 | 14.1408 | 7.3622
243.2542 | 146.6693 | 12.2544 | 107.7894 | 154.331 | 128.146 | 14.1856 | 7.3603
244.2542 | 147.364 | 12.3039 | 107.7717 | 154.4064 | 128.8254 | 14.2463 | 7.3815
245.2542 | 147.9487 | 12.3603 | 107.8464 | 155.0565 | 129.7227 | 14.3052 | 7.3868
246.2542 | 147.8347 | 12.4062 | 108.619 | 155.7417 | 129.4609 | 14.3485 | 7.4001
247.2542 | 148.1893 | 12.4497 | 109.1986 | 156.1093 | 129.7423 | 14.3893 | 7.3933
248.2542 | 148.9532 | 12.5135 | 110.589 | 156.5924 | 130.8923 | 14.4435 | 7.413
249.2542 | 149.5598 | 12.5585 | 110.3131 | 156.9061 | 131.159 | 14.4906 | 7.4179
250.2542 | 148.8064 | 12.6081 | 110.3073 | 157.3552 | 131.6808 | 14.5482 | 7.4086
251.2542 | 149.1975 | 12.6575 | 110.1046 | 157.3229 | 131.7148 | 14.6111 | 7.4229
252.2542 | 149.8699 | 12.7082 | 110.1001 | 157.4055 | 132.0878 | 14.6508 | 7.4374
253.2542 | 150.6378 | 12.7631 | 109.6335 | 157.921 | 132.0423 | 14.7056 | 7.4482
254.2542 | 152.1117 | 12.8226 | 110.1462 | 158.4244 | 131.8755 | 14.7425 | 7.4658
255.2542 | 152.8888 | 12.8803 | 110.3262 | 158.8272 | 131.5184 | 14.7984 | 7.4529
256.2542 | 153.6365 | 12.9263 | 110.4069 | 159.4136 | 131.7144 | 14.8399 | 7.4773
257.2542 | 154.8611 | 12.9818 | 110.7521 | 160.6353 | 132.3098 | 14.8994 | 7.4803
258.2542 | 154.6792 | 13.0363 | 111.4016 | 159.9775 | 132.5887 | 14.9488 | 7.4867
259.2542 | 155.082 | 13.0917 | 111.3475 | 160.0289 | 132.6235 | 14.9941 | 7.498
260.2542 | 156.2522 | 13.1362 | 112.395 | 160.389 | 133.2527 | 15.0535 | 7.5096
261.2542 | 156.9243 | 13.197 | 113.3179 | 160.8239 | 133.706 | 15.1042 | 7.5282
262.2542 | 157.3066 | 13.2489 | 113.507 | 161.2129 | 134.5396 | 15.1608 | 7.5413
263.2542 | 157.7076 | 13.3023 | 113.8529 | 161.4412 | 135.2748 | 15.2166 | 7.5322
264.2542 | 158.7449 | 13.3594 | 113.4354 | 161.6987 | 135.9605 | 15.2808 | 7.5474
265.2542 | 159.1868 | 13.4242 | 113.5624 | 161.8637 | 136.3077 | 15.3238 | 7.5605
266.2542 | 160.1986 | 13.4751 | 114.7638 | 161.5829 | 137.1074 | 15.3954 | 7.5621
267.2542 | 160.5446 | 13.5336 | 115.3785 | 162.8556 | 137.3268 | 15.4479 | 7.5892
268.2542 | 161.3931 | 13.5936 | 115.1336 | 163.2095 | 137.3208 | 15.5059 | 7.5848
269.2542 | 161.9616 | 13.6636 | 114.8839 | 164.8136 | 137.4377 | 15.5527 | 7.5835
270.2542 | 162.1318 | 13.7052 | 114.7115 | 164.7986 | 138.3494 | 15.6131 | 7.6083
271.2542 | 162.0845 | 13.7565 | 114.5671 | 165.1226 | 138.6809 | 15.6624 | 7.6109
272.2542 | 164.2934 | 13.8142 | 114.0634 | 165.4522 | 138.9173 | 15.7155 | 7.6258
273.2542 | 163.81 | 13.8812 | 115.2121 | 165.3912 | 139.4287 | 15.7819 | 7.6246
274.2542 | 163.4945 | 13.9272 | 115.4224 | 165.8791 | 139.2682 | 15.8224 | 7.6361
275.2542 | 163.3382 | 13.9922 | 115.3398 | 166.0434 | 140.0381 | 15.8819 | 7.6409
276.2542 | 164.4009 | 14.0578 | 114.9977 | 166.2735 | 140.2115 | 15.9364 | 7.654
277.2542 | 165.2535 | 14.102 | 115.0315 | 167.1524 | 139.8451 | 15.9805 | 7.6656
278.2542 | 165.5277 | 14.155 | 115.0365 | 167.3148 | 140.0881 | 16.0364 | 7.6789
279.2542 | 165.6013 | 14.217 | 114.8539 | 167.4889 | 140.5548 | 16.0894 | 7.6887
280.2542 | 165.3045 | 14.2773 | 114.4136 | 167.8644 | 140.329 | 16.1309 | 7.6996
281.2542 | 165.3463 | 14.3278 | 114.4635 | 168.1986 | 140.9192 | 16.1896 | 7.7112
282.2542 | 165.9931 | 14.4028 | 115.1649 | 168.6492 | 141.8097 | 16.2401 | 7.7145
283.2542 | 166.6732 | 14.4411 | 116.2964 | 168.4222 | 142.3392 | 16.2911 | 7.7278
284.2542 | 168.5725 | 14.5031 | 116.2341 | 168.8426 | 142.2619 | 16.3419 | 7.7473
285.2542 | 169.6027 | 14.5646 | 118.081 | 169.0578 | 142.6192 | 16.3881 | 7.7464
286.2542 | 169.5999 | 14.6212 | 118.1661 | 170.019 | 142.8844 | 16.4341 | 7.7685
287.2542 | 169.9067 | 14.6714 | 118.5391 | 169.907 | 143.184 | 16.4895 | 7.7816
288.2542 | 171.0726 | 14.7358 | 118.7968 | 170.1515 | 143.4001 | 16.5429 | 7.7943
289.2542 | 171.3304 | 14.782 | 119.326 | 170.4583 | 143.5829 | 16.5795 | 7.7979
290.2542 | 171.9041 | 14.8429 | 119.3859 | 170.8556 | 143.1415 | 16.6318 | 7.8038
291.2542 | 172.2425 | 14.9002 | 120.5522 | 171.271 | 142.8245 | 16.6862 | 7.8186
292.2542 | 172.5902 | 14.9513 | 122.1146 | 171.7723 | 143.1255 | 16.7384 | 7.824
293.2542 | 173.0131 | 15.0102 | 122.1176 | 173.2937 | 143.4011 | 16.7884 | 7.8249
294.2542 | 172.1985 | 15.0567 | 121.795 | 173.6451 | 143.4945 | 16.8618 | 7.8432
295.2542 | 172.3428 | 15.1264 | 121.6665 | 173.5766 | 143.2774 | 16.9219 | 7.8785
296.2542 | 173.2629 | 15.1711 | 122.5055 | 173.6273 | 144.2743 | 16.9674 | 7.8784
297.2542 | 174.8422 | 15.2236 | 122.6568 | 174.5146 | 144.7163 | 17.0279 | 7.8936
298.2542 | 175.3897 | 15.273 | 122.1178 | 174.1864 | 144.6137 | 17.0557 | 7.8983
299.2542 | 176.0923 | 15.3326 | 122.7759 | 173.8293 | 144.4648 | 17.123 | 7.9122
300.2542 | 177.2907 | 15.372 | 123.7023 | 173.793 | 144.7802 | 17.1778 | 7.9123
301.2542 | 176.8609 | 15.447 | 123.968 | 174.0178 | 145.0808 | 17.2239 | 7.9209
302.2542 | 176.8877 | 15.495 | 124.2977 | 174.1921 | 145.6344 | 17.2757 | 7.9392
303.2542 | 177.1503 | 15.5482 | 125.0414 | 175.1854 | 146.1206 | 17.341 | 7.9475
304.2542 | 177.1859 | 15.5959 | 124.6646 | 175.6857 | 146.0141 | 17.3972 | 7.9794
305.2542 | 177.2765 | 15.6418 | 124.1386 | 176.1503 | 146.364 | 17.4499 | 8.0044
306.2542 | 177.0857 | 15.7018 | 124.3521 | 176.5948 | 146.6443 | 17.5094 | 8.0052
307.2542 | 177.3609 | 15.7549 | 124.4211 | 176.6762 | 146.8576 | 17.565 | 8.0188
308.2542 | 176.9304 | 15.8106 | 123.88 | 176.9484 | 147.1983 | 17.6213 | 8.0315
309.2542 | 178.0395 | 15.8691 | 123.2656 | 177.0614 | 147.3014 | 17.684 | 8.04
310.2542 | 179.0844 | 15.9148 | 124.1381 | 176.9705 | 148.1069 | 17.7339 | 8.052
311.2542 | 179.8117 | 15.9782 | 123.9591 | 177.2498 | 148.7405 | 17.7899 | 8.0662
312.2542 | 179.9913 | 16.0205 | 123.3358 | 177.3422 | 148.8912 | 17.864 | 8.0726
313.2542 | 180.0479 | 16.0653 | 123.5639 | 177.2161 | 148.7255 | 17.9184 | 8.0829
314.2542 | 180.0976 | 16.1225 | 124.6661 | 177.21 | 148.834 | 17.9996 | 8.1021
315.2542 | 181.0973 | 16.1805 | 124.1995 | 177.7195 | 149.5813 | 18.0656 | 8.1267
316.2542 | 181.9488 | 16.2448 | 123.7976 | 177.8471 | 149.4841 | 18.1261 | 8.1273
317.2542 | 181.7908 | 16.2958 | 123.6978 | 177.2355 | 149.6773 | 18.2009 | 8.1462
318.2542 | 183.6548 | 16.3553 | 122.9939 | 177.0538 | 150.5518 | 18.2609 | 8.1563
319.2542 | 185.388 | 16.4194 | 122.3828 | 177.4225 | 150.8468 | 18.3227 | 8.1652
320.2542 | 186.7288 | 16.4671 | 121.9718 | 177.9182 | 151.1332 | 18.3836 | 8.1893
321.2542 | 187.5627 | 16.5174 | 121.9831 | 178.1662 | 150.7589 | 18.4448 | 8.2071
322.2542 | 189.1103 | 16.5746 | 122.2111 | 178.4316 | 151.455 | 18.5074 | 8.204
323.2542 | 188.6867 | 16.6328 | 121.9755 | 179.3882 | 151.9153 | 18.5736 | 8.2286
324.2542 | 188.2564 | 16.6735 | 122.1928 | 180.0969 | 151.8979 | 18.6358 | 8.1913
325.2542 | 188.4437 | 16.7298 | 121.8037 | 179.9473 | 152.6824 | 18.6956 | 8.2477
326.2542 | 188.1618 | 16.7901 | 121.6983 | 179.8474 | 153.2733 | 18.7478 | 8.2782
327.2542 | 189.2271 | 16.848 | 121.7712 | 179.9116 | 153.3829 | 18.8098 | 8.2734
328.2542 | 190.8055 | 16.9017 | 121.866 | 179.8174 | 153.6979 | 18.8623 | 8.2656
329.2542 | 191.6297 | 16.9569 | 122.4577 | 180.0797 | 154.0101 | 18.9321 | 8.2895
330.2542 | 192.2689 | 17.0238 | 122.405 | 180.8215 | 154.4558 | 19.0051 | 8.2922
331.2542 | 192.7835 | 17.0794 | 121.8833 | 181.5367 | 155.1422 | 19.0701 | 8.3165
332.2542 | 193.739 | 17.1432 | 121.8589 | 181.2835 | 155.886 | 19.1196 | 8.3379
333.2542 | 194.6136 | 17.1889 | 121.7681 | 181.3616 | 156.2937 | 19.1858 | 8.3549
334.2542 | 195.604 | 17.2425 | 121.8391 | 181.286 | 156.9487 | 19.2638 | 8.3731
335.2542 | 196.7622 | 17.317 | 121.3068 | 181.0663 | 157.3684 | 19.3469 | 8.4093
336.2542 | 197.6397 | 17.3839 | 121.0208 | 181.0547 | 157.4023 | 19.4131 | 8.4164
337.2542 | 199.8193 | 17.4428 | 121.4673 | 181.167 | 157.5832 | 19.4785 | 8.4172
338.2542 | 200.7245 | 17.5007 | 121.4996 | 181.5609 | 158.1649 | 19.5496 | 8.4262
339.2542 | 202.3435 | 17.5558 | 121.7369 | 181.7127 | 158.4761 | 19.6127 | 8.4341
340.2542 | 203.7535 | 17.615 | 121.6047 | 182.2583 | 158.761 | 19.687 | 8.4315
341.2542 | 204.9229 | 17.6809 | 121.3729 | 182.578 | 160.6063 | 19.7594 | 8.471
342.2542 | 206.1327 | 17.7313 | 122.7911 | 183.1651 | 162.7288 | 19.8406 | 8.482
343.2542 | 206.8303 | 17.7948 | 123.1409 | 184.3285 | 163.6342 | 19.9042 | 8.4973
344.2542 | 206.9289 | 17.8604 | 125.1611 | 185.9119 | 164.4803 | 19.9633 | 8.5071
345.2542 | 207.6328 | 17.9297 | 125.6028 | 186.4721 | 164.8675 | 20.0479 | 8.5386
346.2542 | 207.9181 | 17.9875 | 125.7012 | 187.4515 | 165.6235 | 20.104 | 8.5497
347.2542 | 208.4823 | 18.0426 | 125.6744 | 187.4963 | 165.9605 | 20.181 | 8.5594
348.2542 | 209.9329 | 18.1161 | 125.7381 | 187.8811 | 165.9403 | 20.2435 | 8.5477
349.2542 | 210.3222 | 18.1739 | 126.3248 | 188.6041 | 165.812 | 20.3085 | 8.5837
350.2542 | 210.4626 | 18.2366 | 127.379 | 189.0994 | 165.9459 | 20.3757 | 8.6033
351.2542 | 210.9638 | 18.2958 | 128.4043 | 189.0992 | 166.1672 | 20.4357 | 8.6024
352.2542 | 210.5449 | 18.3402 | 129.1827 | 190.0136 | 166.4488 | 20.5104 | 8.633
353.2542 | 210.1217 | 18.4124 | 130.2782 | 190.0085 | 166.3126 | 20.5891 | 8.6258
354.2542 | 210.6509 | 18.4717 | 132.8431 | 189.7965 | 166.5399 | 20.6454 | 8.6759
355.2542 | 210.1274 | 18.5433 | 133.2552 | 190.7729 | 166.6095 | 20.7169 | 8.691
356.2542 | 209.7229 | 18.6047 | 133.3558 | 191.2211 | 167.6972 | 20.7811 | 8.7247
357.2542 | 209.8697 | 18.6604 | 134.2126 | 191.7488 | 168.4788 | 20.8425 | 8.7414
358.2542 | 210.1387 | 18.719 | 134.1812 | 191.9313 | 168.7682 | 20.9025 | 8.7605
359.2542 | 210.5283 | 18.7821 | 135.3882 | 192.376 | 169.0498 | 20.9764 | 8.7662
360.2542 | 211.2038 | 18.8471 | 136.8352 | 192.4485 | 169.0912 | 21.0607 | 8.7719
361.2542 | 211.0537 | 18.9021 | 138.3583 | 192.6564 | 169.2839 | 21.1311 | 8.7721
362.2542 | 210.7056 | 18.9685 | 137.8802 | 193.2418 | 169.6613 | 21.2006 | 8.8193
363.2542 | 211.0477 | 19.0393 | 137.378 | 193.4154 | 169.6077 | 21.2702 | 8.8134
364.2542 | 212.0488 | 19.1 | 137.3803 | 193.6932 | 170.0787 | 21.3518 | 8.8472
365.2542 | 212.36 | 19.1759 | 137.0005 | 192.5917 | 169.9383 | 21.4079 | 8.8603
366.2542 | 212.6644 | 19.2299 | 136.8435 | 192.1789 | 170.0239 | 21.4729 | 8.8792
367.2542 | 213.2388 | 19.2833 | 137.4359 | 191.9351 | 169.9289 | 21.5436 | 8.8996
368.2542 | 214.0421 | 19.349 | 138.4073 | 191.3152 | 169.7348 | 21.6044 | 8.9177
369.2542 | 214.8115 | 19.4225 | 138.5484 | 190.9204 | 169.8036 | 21.7045 | 8.926
370.2542 | 216.2136 | 19.4987 | 138.6665 | 190.6624 | 169.509 | 21.7682 | 8.9491
371.2542 | 215.4113 | 19.57 | 138.9802 | 190.9449 | 169.7494 | 21.8359 | 8.9696
372.2542 | 216.2895 | 19.6208 | 139.2192 | 191.599 | 170.6054 | 21.9124 | 8.9753
373.2542 | 216.6254 | 19.6723 | 139.1311 | 192.6932 | 170.5406 | 21.9939 | 8.9916
374.2542 | 217.1153 | 19.7467 | 138.9324 | 192.3341 | 170.1868 | 22.0515 | 9.0017
375.2542 | 217.2808 | 19.8045 | 139.1019 | 192.6538 | 169.9765 | 22.1201 | 9.0449
376.2542 | 217.7203 | 19.8695 | 138.8498 | 192.4092 | 169.5152 | 22.1888 | 9.0387
377.2542 | 218.0197 | 19.9365 | 138.3252 | 193.103 | 169.341 | 22.2476 | 9.0423
378.2542 | 218.0206 | 19.9943 | 137.4714 | 193.353 | 169.4928 | 22.31 | 9.0743
379.2542 | 218.2157 | 20.0719 | 138.1507 | 193.3809 | 169.7749 | 22.3699 | 9.1245
380.2542 | 218.5764 | 20.1366 | 137.6269 | 193.5484 | 169.6562 | 22.4253 | 9.1273
381.2542 | 218.177 | 20.1896 | 137.831 | 193.405 | 170.4465 | 22.4841 | 9.1329
382.2542 | 218.3916 | 20.2465 | 138.0435 | 193.2931 | 170.9544 | 22.5516 | 9.1473
383.2542 | 219.2707 | 20.3106 | 137.5794 | 193.2624 | 171.2212 | 22.6174 | 9.176
384.2542 | 218.617 | 20.3858 | 136.9691 | 193.5853 | 172.1769 | 22.6688 | 9.2007
385.2542 | 218.9489 | 20.4502 | 136.5216 | 193.4578 | 171.9349 | 22.7409 | 9.2061
386.2542 | 219.9556 | 20.5106 | 136.6586 | 193.657 | 171.7975 | 22.8064 | 9.2395
387.2542 | 220.4891 | 20.5753 | 136.9927 | 193.4252 | 172.2253 | 22.8705 | 9.2625
388.2542 | 220.4241 | 20.6398 | 137.1839 | 193.7662 | 173.1924 | 22.9311 | 9.2924
389.2542 | 219.709 | 20.7132 | 137.3403 | 194.6725 | 173.5113 | 22.9852 | 9.2864
390.2542 | 221.046 | 20.7757 | 137.608 | 196.1506 | 175.0651 | 23.0525 | 9.3549
391.2542 | 220.9709 | 20.8341 | 138.0673 | 196.6774 | 175.1475 | 23.1139 | 9.365
392.2542 | 220.915 | 20.8878 | 138.741 | 197.2545 | 175.6089 | 23.1696 | 9.3749
393.2542 | 221.1635 | 20.9391 | 139.5727 | 198.0727 | 176.7048 | 23.2442 | 9.3987
394.2542 | 221.1435 | 20.9914 | 140.4234 | 198.3903 | 176.9342 | 23.3182 | 9.4174
395.2542 | 221.9622 | 21.0572 | 141.7101 | 198.9971 | 176.9098 | 23.3787 | 9.4408
396.2542 | 223.0785 | 21.1303 | 141.7068 | 199.0105 | 177.4185 | 23.4492 | 9.4363
397.2542 | 224.7087 | 21.2013 | 141.6471 | 199.2003 | 177.501 | 23.5246 | 9.459
398.2542 | 224.938 | 21.2688 | 142.0214 | 199.215 | 177.6006 | 23.5969 | 9.4909
399.2542 | 224.535 | 21.3445 | 142.1122 | 198.8231 | 177.6742 | 23.6592 | 9.5082
400.2542 | 224.995 | 21.403 | 141.6535 | 198.3087 | 177.766 | 23.7169 | 9.5211
401.2542 | 226.0875 | 21.4768 | 141.2596 | 198.9944 | 177.9255 | 23.7762 | 9.538
402.2542 | 226.4949 | 21.5409 | 141.2916 | 199.1322 | 177.9519 | 23.826 | 9.5474
403.2542 | 227.3647 | 21.6009 | 141.5069 | 199.5514 | 177.6704 | 23.9009 | 9.6091
404.2542 | 229.0437 | 21.6575 | 141.7219 | 199.413 | 178.5013 | 23.9664 | 9.6399
405.2542 | 229.8103 | 21.7226 | 141.4955 | 199.4095 | 177.9748 | 24.0354 | 9.6507
406.2542 | 230.0985 | 21.7726 | 141.0543 | 199.243 | 177.6076 | 24.098 | 9.6769
407.2542 | 229.7577 | 21.8405 | 141.7315 | 199.3643 | 177.9016 | 24.1476 | 9.689
408.2542 | 230.1095 | 21.9182 | 142.202 | 199.7456 | 178.5582 | 24.2086 | 9.715
409.2542 | 230.2348 | 21.9873 | 142.7972 | 199.7241 | 178.8591 | 24.2691 | 9.7261
410.2542 | 230.1714 | 22.0614 | 143.1201 | 199.0244 | 179.1633 | 24.3317 | 9.7446
411.2542 | 230.2005 | 22.1173 | 143.2867 | 199.2124 | 178.9004 | 24.4 | 9.7616
412.2542 | 230.2485 | 22.1817 | 143.0614 | 199.0177 | 178.7273 | 24.4612 | 9.8003
413.2542 | 230.9034 | 22.2439 | 143.4732 | 198.6662 | 178.7829 | 24.5323 | 9.8141
414.2542 | 231.6511 | 22.3174 | 143.2908 | 198.6543 | 179.0053 | 24.5919 | 9.8364
415.2542 | 231.2889 | 22.3919 | 143.3026 | 198.9721 | 178.8929 | 24.6568 | 9.8578
416.2542 | 230.2735 | 22.4462 | 144.022 | 199.5523 | 178.4584 | 24.7225 | 9.8703
417.2542 | 230.622 | 22.5078 | 144.7801 | 199.5965 | 178.4468 | 24.7833 | 9.8881
418.2542 | 230.7826 | 22.5555 | 144.9401 | 200.5346 | 178.4496 | 24.8425 | 9.9056
419.2542 | 232.4672 | 22.6286 | 144.5331 | 201.3552 | 178.55 | 24.9051 | 9.917
420.2542 | 234.1515 | 22.6807 | 144.4904 | 201.5327 | 178.1575 | 24.9618 | 9.9385
421.2542 | 234.363 | 22.7537 | 144.6624 | 201.1191 | 178.71 | 25.0373 | 9.9648
422.2542 | 235.5932 | 22.8389 | 144.3713 | 201.4861 | 178.4384 | 25.0972 | 9.9848
423.2542 | 235.4738 | 22.914 | 143.6913 | 201.6748 | 179.7332 | 25.1788 | 10.0093
424.2542 | 236.6257 | 22.9667 | 143.6702 | 201.5477 | 179.6312 | 25.2378 | 10.0302
425.2542 | 238.0648 | 23.0331 | 144.123 | 201.2346 | 180.9657 | 25.3215 | 10.0678
426.2542 | 238.1109 | 23.1132 | 144.577 | 201.2859 | 181.5059 | 25.3599 | 10.1157
427.2542 | 238.9746 | 23.1697 | 146.3271 | 201.4964 | 180.804 | 25.433 | 10.1307
428.2542 | 238.7182 | 23.2341 | 146.6674 | 201.5961 | 180.5189 | 25.5073 | 10.1595
429.2542 | 238.4981 | 23.3115 | 146.7922 | 201.5402 | 181.0258 | 25.5774 | 10.1792
430.2542 | 239.4088 | 23.3956 | 146.651 | 201.5452 | 181.1252 | 25.6379 | 10.1883
431.2542 | 238.9949 | 23.476 | 146.7241 | 201.8008 | 181.2147 | 25.7062 | 10.2194
432.2542 | 237.9172 | 23.5644 | 146.6506 | 201.3919 | 180.251 | 25.7705 | 10.2169
433.2542 | 238.0516 | 23.6295 | 146.3249 | 201.2494 | 180.7565 | 25.8423 | 10.2526
434.2542 | 237.8968 | 23.7089 | 146.1427 | 201.2477 | 180.4584 | 25.911 | 10.2774
435.2542 | 238.2312 | 23.7588 | 145.9837 | 200.8961 | 180.5555 | 25.9764 | 10.3015
436.2542 | 239.7996 | 23.8396 | 145.2923 | 200.781 | 182.8631 | 26.0423 | 10.3394
437.2542 | 241.1115 | 23.9215 | 144.7295 | 201.3565 | 182.5649 | 26.102 | 10.3689
438.2542 | 241.1109 | 23.9997 | 144.7469 | 201.9377 | 182.1737 | 26.1672 | 10.3922
439.2542 | 241.8635 | 24.0554 | 145.6525 | 203.3598 | 182.4319 | 26.2307 | 10.4135
440.2542 | 241.8197 | 24.1318 | 146.9997 | 203.8703 | 182.4052 | 26.2939 | 10.4314
441.2542 | 243.0221 | 24.2119 | 147.4541 | 204.027 | 182.3798 | 26.3458 | 10.4572
442.2542 | 243.6951 | 24.2698 | 148.2521 | 204.6469 | 182.49 | 26.4174 | 10.4688
443.2542 | 244.1461 | 24.3469 | 148.78 | 205.2835 | 182.7168 | 26.4788 | 10.5114
444.2542 | 244.8395 | 24.4174 | 148.3202 | 205.6402 | 182.7875 | 26.5416 | 10.5279
445.2542 | 246.2116 | 24.4788 | 148.015 | 205.2535 | 182.3651 | 26.6022 | 10.5585
446.2542 | 246.6053 | 24.5497 | 147.795 | 204.9153 | 182.3379 | 26.6525 | 10.5941
447.2542 | 247.2175 | 24.6133 | 147.4769 | 204.7471 | 182.1399 | 26.712 | 10.6056
448.2542 | 247.5439 | 24.6838 | 147.2041 | 204.1945 | 182.1879 | 26.783 | 10.6353
449.2542 | 248.9077 | 24.7598 | 147.1091 | 204.0249 | 182.7966 | 26.8513 | 10.666
450.2542 | 249.594 | 24.836 | 146.8165 | 204.2708 | 182.7004 | 26.9001 | 10.693
451.2542 | 250.1317 | 24.9031 | 146.7909 | 204.0201 | 183.5402 | 26.9632 | 10.7261
452.2542 | 250.7064 | 24.9699 | 146.9094 | 203.712 | 184.8485 | 27.0363 | 10.7409
453.2542 | 251.2946 | 25.0446 | 146.2661 | 203.6792 | 184.8488 | 27.0915 | 10.778
454.2542 | 251.2527 | 25.1049 | 146.0207 | 203.6885 | 184.472 | 27.1661 | 10.8012
455.2542 | 250.1217 | 25.1735 | 145.5886 | 203.4253 | 185.5896 | 27.2409 | 10.8226
456.2542 | 249.7619 | 25.2452 | 145.8521 | 203.0411 | 186.0442 | 27.3003 | 10.8345
457.2542 | 248.9148 | 25.3205 | 145.6169 | 202.8025 | 186.9708 | 27.3667 | 10.8554
458.2542 | 249.113 | 25.3864 | 145.3111 | 203.517 | 187.2728 | 27.4296 | 10.8908
459.2542 | 249.2732 | 25.456 | 144.8467 | 203.7676 | 188.6804 | 27.5024 | 10.9118
460.2542 | 250.6243 | 25.5345 | 145.4744 | 204.0279 | 188.5502 | 27.5551 | 10.9403
461.2542 | 251.8076 | 25.5965 | 145.2898 | 204.2351 | 189.1823 | 27.6179 | 10.9958
462.2542 | 252.2057 | 25.6668 | 144.911 | 205.3858 | 189.1083 | 27.6952 | 11.0049
463.2542 | 250.6574 | 25.7495 | 144.9893 | 205.2117 | 188.9182 | 27.7643 | 11.053
464.2542 | 250.4828 | 25.8126 | 146.361 | 205.9371 | 189.5929 | 27.8325 | 11.0639
465.2542 | 250.2997 | 25.8931 | 147.6004 | 206.0786 | 189.5512 | 27.9003 | 11.0835
466.2542 | 249.7981 | 25.9604 | 148.3606 | 206.414 | 189.575 | 27.9533 | 11.1319
467.2542 | 250.409 | 26.0362 | 149.1167 | 206.4514 | 190.7645 | 28.0405 | 11.1482
468.2542 | 251.6647 | 26.1016 | 149.2677 | 207.1202 | 191.113 | 28.1082 | 11.1662
469.2542 | 251.6293 | 26.1561 | 149.7166 | 206.5294 | 192.5476 | 28.1751 | 11.1903
470.2542 | 252.3225 | 26.2211 | 150.0262 | 206.0998 | 193.3962 | 28.2352 | 11.2191
471.2542 | 252.1141 | 26.2969 | 149.6211 | 205.931 | 193.0517 | 28.2885 | 11.2626
472.2542 | 252.6617 | 26.3747 | 149.7402 | 206.0722 | 193.0932 | 28.3488 | 11.291
473.2542 | 253.6323 | 26.4551 | 149.906 | 206.1979 | 192.8036 | 28.4146 | 11.3203
474.2542 | 253.2776 | 26.5381 | 150.0328 | 206.6313 | 192.178 | 28.4813 | 11.3551
475.2542 | 253.3511 | 26.6152 | 149.728 | 206.4961 | 192.2229 | 28.5592 | 11.3606
476.2542 | 252.1216 | 26.6915 | 149.8083 | 206.1263 | 192.1681 | 28.6215 | 11.3939
477.2542 | 252.5284 | 26.7674 | 149.9375 | 206.0745 | 192.3697 | 28.6812 | 11.4177
478.2542 | 252.4298 | 26.8379 | 150.4115 | 205.7826 | 192.5596 | 28.7311 | 11.4598
479.2542 | 251.6892 | 26.9172 | 150.409 | 205.8505 | 192.8386 | 28.793 | 11.5026
480.2542 | 252.6018 | 26.9976 | 150.2768 | 206.038 | 193.8744 | 28.8715 | 11.5165
481.2542 | 252.6308 | 27.0916 | 150.1272 | 206.1899 | 194.7048 | 28.9366 | 11.536
482.2542 | 253.4435 | 27.171 | 150.4952 | 206.7319 | 194.9255 | 29.0091 | 11.5711
483.2542 | 253.2443 | 27.2484 | 152.5454 | 206.3407 | 194.6402 | 29.0701 | 11.5845
484.2542 | 253.0868 | 27.3292 | 152.9664 | 206.4795 | 194.764 | 29.1381 | 11.6327
485.2542 | 254.2263 | 27.4022 | 154.1039 | 206.4604 | 194.6131 | 29.1864 | 11.6605
486.2542 | 254.2631 | 27.4826 | 154.8933 | 206.4304 | 194.0638 | 29.2522 | 11.6931
487.2542 | 255.5816 | 27.5724 | 155.9342 | 206.1696 | 193.7519 | 29.3104 | 11.7288
488.2542 | 255.6566 | 27.6575 | 156.0213 | 205.9742 | 193.2347 | 29.372 | 11.7492
489.2542 | 255.12 | 27.74 | 155.7366 | 206.0173 | 192.9573 | 29.4346 | 11.7999
490.2542 | 254.9638 | 27.8276 | 156.8773 | 206.3611 | 193.0295 | 29.4947 | 11.822
491.2542 | 254.5463 | 27.9107 | 156.4065 | 206.5316 | 192.7868 | 29.5638 | 11.8625
492.2542 | 253.7941 | 27.9936 | 156.2416 | 206.2753 | 192.4231 | 29.6365 | 11.8883
493.2542 | 253.5235 | 28.0896 | 155.9523 | 206.3256 | 192.3978 | 29.6995 | 11.9021
494.2542 | 253.9222 | 28.1537 | 155.6848 | 206.2696 | 192.2727 | 29.7742 | 11.9326
495.2542 | 253.6633 | 28.1976 | 155.6873 | 206.4423 | 191.8701 | 29.8559 | 11.9368
496.2542 | 255.7827 | 28.2768 | 155.4767 | 206.3533 | 191.7847 | 29.9173 | 11.9593
497.2542 | 256.209 | 28.3561 | 154.9225 | 206.3554 | 191.7183 | 29.9817 | 11.9764
498.2542 | 256.1447 | 28.4459 | 154.1735 | 206.1217 | 191.7559 | 30.0583 | 12.0289
499.2542 | 256.3761 | 28.5275 | 154.0433 | 207.0192 | 191.9148 | 30.1165 | 12.055
500.2542 | 256.3158 | 28.6208 | 153.6947 | 206.682 | 191.994 | 30.1777 | 12.099
501.2542 | 257.5452 | 28.6983 | 153.0249 | 207.0667 | 192.9395 | 30.2489 | 12.1222
502.2542 | 257.236 | 28.7918 | 152.482 | 208.7619 | 193.4074 | 30.312 | 12.1313
503.2542 | 256.2096 | 28.8536 | 153.9987 | 208.89 | 193.5373 | 30.3901 | 12.1892
504.2542 | 255.7546 | 28.9554 | 153.8387 | 208.4732 | 194.7738 | 30.4669 | 12.2173
505.2542 | 258.1178 | 29.025 | 153.8524 | 209.1217 | 194.2897 | 30.5254 | 12.2487
506.2542 | 256.9024 | 29.1109 | 154.3698 | 210.669 | 193.1552 | 30.5942 | 12.2731
507.2542 | 256.5133 | 29.1836 | 155.4823 | 210.8582 | 193.3086 | 30.648 | 12.306
508.2542 | 256.9849 | 29.2789 | 155.1504 | 210.4318 | 193.0648 | 30.7256 | 12.3134
509.2542 | 257.1144 | 29.3609 | 154.7325 | 210.051 | 192.9147 | 30.7901 | 12.367
510.2542 | 257.4636 | 29.4512 | 154.9238 | 209.8778 | 192.6343 | 30.8514 | 12.4002
511.2542 | 258.8855 | 29.5468 | 155.2204 | 209.6406 | 192.1647 | 30.9147 | 12.4274
512.2542 | 261.8508 | 29.6431 | 155.487 | 209.2914 | 192.2405 | 30.9729 | 12.461
513.2542 | 262.4538 | 29.7285 | 154.8578 | 209.0774 | 192.3694 | 31.029 | 12.5025
514.2542 | 262.204 | 29.8089 | 155.0147 | 209.2369 | 192.4582 | 31.1009 | 12.5219
515.2542 | 260.9213 | 29.897 | 155.5943 | 209.4477 | 192.763 | 31.163 | 12.5796
516.2542 | 260.4736 | 29.9711 | 157.1297 | 209.505 | 193.4745 | 31.2311 | 12.6172
517.2542 | 260.1236 | 30.067 | 157.1133 | 209.8041 | 193.8927 | 31.291 | 12.6511
518.2542 | 258.6992 | 30.1714 | 156.786 | 209.9208 | 194.2156 | 31.3436 | 12.685
519.2542 | 257.4302 | 30.2731 | 156.0934 | 213.1498 | 194.753 | 31.4149 | 12.72
520.2542 | 258.3431 | 30.3638 | 156.7996 | 212.4612 | 195.1419 | 31.4624 | 12.762
521.2542 | 259.5191 | 30.4659 | 156.971 | 212.0727 | 196.5129 | 31.5207 | 12.7972
522.2542 | 259.9697 | 30.5431 | 157.281 | 211.9895 | 196.1864 | 31.5771 | 12.8231
523.2542 | 259.1282 | 30.6295 | 157.6388 | 211.7128 | 195.5688 | 31.6358 | 12.8464
524.2542 | 259.5552 | 30.7249 | 158.1425 | 211.3811 | 195.9305 | 31.6992 | 12.8779
525.2542 | 261.0517 | 30.8269 | 158.0158 | 211.0585 | 195.2707 | 31.7506 | 12.9161
526.2542 | 260.4217 | 30.8976 | 157.8494 | 211.1777 | 195.7473 | 31.8093 | 12.9395
527.2542 | 261.3573 | 30.9736 | 157.0842 | 211.5254 | 196.6052 | 31.874 | 12.9766
528.2542 | 259.1207 | 31.0711 | 156.8832 | 211.2849 | 196.2457 | 31.9279 | 13
529.2542 | 258.6933 | 31.156 | 156.1072 | 210.9662 | 196.721 | 31.9813 | 13.0156
530.2542 | 259.487 | 31.2555 | 155.9315 | 212.7599 | 196.9149 | 32.0304 | 13.0707
531.2542 | 259.2822 | 31.3586 | 157.1318 | 212.8502 | 196.7906 | 32.1024 | 13.1081
532.2542 | 260.8014 | 31.4265 | 157.1012 | 213.066 | 196.6598 | 32.1562 | 13.1536
533.2542 | 260.1918 | 31.5002 | 158.0748 | 213.2134 | 196.8615 | 32.2055 | 13.1631
534.2542 | 261.5223 | 31.5688 | 157.9442 | 212.6166 | 196.9661 | 32.2464 | 13.217
535.2542 | 260.8783 | 31.6511 | 158.3308 | 212.451 | 198.2371 | 32.3113 | 13.2379
536.2542 | 260.1463 | 31.7254 | 158.2719 | 212.529 | 198.5598 | 32.3695 | 13.2802
537.2542 | 260.3108 | 31.8072 | 157.9331 | 212.3706 | 199.8783 | 32.4257 | 13.3156
538.2542 | 259.98 | 31.9185 | 157.2773 | 212.0155 | 200.132 | 32.4799 | 13.351
539.2542 | 260.4806 | 32.0171 | 157.3417 | 212.0964 | 199.7013 | 32.5292 | 13.3751
540.2542 | 261.1899 | 32.1047 | 158.1372 | 211.874 | 198.9451 | 32.5685 | 13.4413
541.2542 | 261.4944 | 32.1946 | 157.7011 | 212.0414 | 199.5269 | 32.6384 | 13.4776
542.2542 | 261.0207 | 32.2915 | 157.823 | 212.6574 | 201.0655 | 32.6938 | 13.531
543.2542 | 260.7911 | 32.3722 | 158.3049 | 213.1839 | 201.8133 | 32.7349 | 13.5509
544.2542 | 260.6357 | 32.4671 | 158.2615 | 213.1393 | 201.4771 | 32.7954 | 13.5872
545.2542 | 259.5873 | 32.5583 | 158.6082 | 212.6701 | 201.5238 | 32.8451 | 13.6205
546.2542 | 259.6584 | 32.6609 | 158.5755 | 212.4255 | 200.8617 | 32.9001 | 13.6409
547.2542 | 260.331 | 32.7607 | 158.4262 | 212.4922 | 202.5136 | 32.9664 | 13.6961
548.2542 | 260.8877 | 32.8694 | 159.3488 | 212.7725 | 201.8631 | 33.0158 | 13.7395
549.2542 | 261.9205 | 32.9835 | 160.474 | 212.6303 | 202.0506 | 33.0839 | 13.7709
550.2542 | 261.7191 | 33.0763 | 159.6597 | 212.7087 | 202.9994 | 33.1327 | 13.8195
551.2542 | 261.9112 | 33.2011 | 158.8892 | 212.4113 | 203.1889 | 33.1918 | 13.8351
552.2542 | 262.0983 | 33.3129 | 158.6867 | 211.919 | 202.4297 | 33.242 | 13.8766
553.2542 | 262.2982 | 33.4167 | 158.2958 | 211.4979 | 202.3038 | 33.2984 | 13.9144
554.2542 | 262.187 | 33.5218 | 158.8505 | 211.3546 | 202.9018 | 33.3571 | 13.9401
555.2542 | 262.659 | 33.6128 | 160.4027 | 211.5769 | 203.5387 | 33.4184 | 13.9729
556.2542 | 263.9097 | 33.7119 | 161.1844 | 211.8569 | 203.6416 | 33.4646 | 14.0072
557.2542 | 264.7355 | 33.8181 | 160.942 | 212.3338 | 203.7257 | 33.5153 | 14.0788
558.2542 | 265.4892 | 33.9331 | 160.5781 | 212.4754 | 203.2085 | 33.5591 | 14.0993
559.2542 | 265.2269 | 34.0261 | 160.3748 | 212.303 | 203.1611 | 33.6154 | 14.1368
560.2542 | 265.5482 | 34.1364 | 160.3246 | 212.4216 | 202.4929 | 33.6842 | 14.1775
561.2542 | 267.0746 | 34.2533 | 160.3041 | 212.3577 | 202.1795 | 33.7381 | 14.2082
562.2542 | 266.6931 | 34.3458 | 159.4899 | 212.2835 | 202.45 | 33.7921 | 14.2314
563.2542 | 265.1591 | 34.4467 | 158.7542 | 212.6759 | 203.6484 | 33.8295 | 14.2657
564.2542 | 265.0924 | 34.5477 | 157.8096 | 213.2907 | 203.6273 | 33.8777 | 14.3068
565.2542 | 265.9507 | 34.6524 | 157.8812 | 214.0418 | 203.1804 | 33.9356 | 14.3248
566.2542 | 266.0872 | 34.7524 | 157.7976 | 213.4682 | 203.8178 | 34.0006 | 14.4057
567.2542 | 268.0979 | 34.8372 | 157.1587 | 213.2431 | 204.3625 | 34.0522 | 14.421
568.2542 | 269.7272 | 34.9368 | 156.4931 | 213.3759 | 204.5225 | 34.1057 | 14.4547
569.2542 | 269.4158 | 35.0519 | 155.5744 | 213.2047 | 204.0889 | 34.1565 | 14.504
570.2542 | 268.9358 | 35.1659 | 155.1846 | 212.9292 | 203.9689 | 34.2102 | 14.5379
571.2542 | 270.039 | 35.2683 | 155.6462 | 213.0095 | 203.4087 | 34.2729 | 14.5775
572.2542 | 270.073 | 35.3503 | 156.103 | 212.9552 | 202.9842 | 34.3184 | 14.6147
573.2542 | 270.0803 | 35.4559 | 156.3817 | 212.5308 | 202.4695 | 34.3689 | 14.6775
574.2542 | 270.0204 | 35.5628 | 156.7483 | 212.5926 | 203.1082 | 34.4307 | 14.7042
575.2542 | 270.4689 | 35.687 | 156.7535 | 212.7289 | 203.0868 | 34.4783 | 14.7545
576.2542 | 271.4613 | 35.8196 | 157.4573 | 212.4245 | 203.3544 | 34.5326 | 14.7822
577.2542 | 271.8721 | 35.9131 | 158.6794 | 211.7403 | 204.1609 | 34.5832 | 14.8048
578.2542 | 271.3357 | 36.024 | 158.6149 | 211.9174 | 204.5696 | 34.62 | 14.8473
579.2542 | 271.0092 | 36.1164 | 158.5234 | 212.8 | 204.3884 | 34.6816 | 14.8762
580.2542 | 271.4324 | 36.2335 | 159.2278 | 213.4408 | 203.8058 | 34.728 | 14.9201
581.2542 | 271.8451 | 36.3511 | 159.6815 | 213.0618 | 204.2728 | 34.7839 | 14.9677
582.2542 | 272.4219 | 36.4227 | 160.598 | 213.6261 | 204.8863 | 34.8327 | 15.0026
583.2542 | 273.221 | 36.5569 | 160.8767 | 213.9576 | 205.2419 | 34.886 | 15.0597
584.2542 | 273.2522 | 36.6473 | 161.31 | 214.7503 | 205.7146 | 34.9392 | 15.076
585.2542 | 272.1688 | 36.7599 | 161.9225 | 215.7583 | 205.9637 | 35.0125 | 15.1184
586.2542 | 272.3558 | 36.8586 | 162.3391 | 216.2391 | 206.1473 | 35.0693 | 15.1572
587.2542 | 272.0503 | 36.9628 | 163.5997 | 216.3254 | 206.0006 | 35.1297 | 15.197
588.2542 | 269.8309 | 37.0658 | 163.0793 | 216.2134 | 206.3994 | 35.1843 | 15.2448
589.2542 | 268.9369 | 37.1624 | 163.083 | 216.6322 | 206.9916 | 35.2458 | 15.2786
590.2542 | 269.105 | 37.2532 | 163.3541 | 218.4139 | 206.6732 | 35.3124 | 15.3283
591.2542 | 269.5477 | 37.3638 | 163.8406 | 218.5432 | 208.1235 | 35.3825 | 15.3618
592.2542 | 270.7097 | 37.4744 | 163.7439 | 218.2227 | 208.2477 | 35.4401 | 15.412
593.2542 | 271.6911 | 37.5983 | 162.9269 | 217.7169 | 207.2333 | 35.4938 | 15.4592
594.2542 | 273.2071 | 37.6812 | 162.1729 | 217.7207 | 206.5492 | 35.5488 | 15.4934
595.2542 | 274.4374 | 37.7879 | 162.6596 | 217.6583 | 205.6297 | 35.6145 | 15.5213
596.2542 | 274.206 | 37.901 | 162.8502 | 217.2308 | 205.1904 | 35.7204 | 15.5034
597.2542 | 274.6215 | 37.9774 | 162.6078 | 217.1534 | 204.5038 | 35.8059 | 15.5514
598.2542 | 274.1635 | 38.0505 | 163.0896 | 217.3927 | 204.4188 | 35.8623 | 15.5643
599.2542 | 273.9184 | 38.1682 | 162.7222 | 217.246 | 203.7115 | 35.9126 | 15.5982
600.2542 | 274.498 | 38.2741 | 162.9424 | 217.3754 | 203.8848 | 35.9758 | 15.6432
601.2542 | 276.3119 | 38.412 | 162.2919 | 217.1217 | 203.3727 | 35.9996 | 15.7044
602.2542 | 275.705 | 38.4958 | 162.0145 | 217.0862 | 202.9348 | 36.0974 | 15.7059
603.2542 | 275.6507 | 38.6111 | 161.2668 | 216.8265 | 203.097 | 36.1714 | 15.752
604.2542 | 275.1449 | 38.7102 | 160.4813 | 216.8787 | 203.4248 | 36.2396 | 15.7638
605.2542 | 274.6189 | 38.8225 | 160.7333 | 217.6713 | 203.8216 | 36.3189 | 15.8199
606.2542 | 273.4693 | 38.9221 | 161.3911 | 218.1698 | 204.738 | 36.3842 | 15.844
607.2542 | 273.4991 | 39.062 | 161.295 | 217.7298 | 204.9112 | 36.3511 | 15.9407
608.2542 | 274.6938 | 39.1441 | 160.9325 | 217.5185 | 205.2671 | 36.4663 | 15.9598
609.2542 | 274.9362 | 39.2274 | 162.4814 | 217.6348 | 204.9847 | 36.5391 | 15.9832
610.2542 | 275.7365 | 39.3393 | 162.4654 | 217.4044 | 205.0821 | 36.6138 | 15.9942
611.2542 | 274.8632 | 39.4704 | 162.6859 | 217.619 | 205.2476 | 36.6689 | 16.051
612.2542 | 273.6904 | 39.5941 | 162.3899 | 218.1803 | 205.0355 | 36.7245 | 16.0798
613.2542 | 274.5287 | 39.6789 | 162.6961 | 218.6097 | 205.5068 | 36.794 | 16.0964
614.2542 | 277.1903 | 39.7741 | 162.4759 | 218.3825 | 205.3801 | 36.8554 | 16.1199
615.2542 | 276.3278 | 39.8717 | 162.7989 | 218.3117 | 205.2789 | 36.9075 | 16.1696
616.2542 | 276.2641 | 39.9949 | 163.2772 | 218.5172 | 205.5793 | 36.9672 | 16.2131
617.2542 | 276.1588 | 40.103 | 163.9221 | 218.4688 | 206.6158 | 36.9992 | 16.2759
618.2542 | 277.9429 | 40.2245 | 164.5105 | 218.3259 | 206.4865 | 37.0333 | 16.3228
619.2542 | 276.7164 | 40.348 | 164.9344 | 218.8236 | 206.1058 | 37.0815 | 16.3717
620.2542 | 277.7903 | 40.4676 | 165.5342 | 218.5967 | 205.6176 | 37.1365 | 16.4013
621.2542 | 278.6351 | 40.5983 | 166.1529 | 218.63 | 205.7604 | 37.1952 | 16.4233
622.2542 | 279.2979 | 40.6957 | 166.6235 | 218.5434 | 206.5387 | 37.2663 | 16.4545
623.2542 | 279.5941 | 40.7531 | 166.3161 | 218.2597 | 206.6168 | 37.3253 | 16.4923
624.2542 | 279.0348 | 40.8614 | 167.2639 | 218.7948 | 207.3535 | 37.3685 | 16.5492
625.2542 | 278.7496 | 40.9647 | 167.4302 | 220.1304 | 207.244 | 37.4143 | 16.5987
626.2542 | 278.728 | 41.0948 | 167.1552 | 220.7075 | 206.9994 | 37.4642 | 16.6089
627.2542 | 278.929 | 41.2043 | 167.656 | 220.9435 | 206.8815 | 37.5225 | 16.6614
628.2542 | 279.5868 | 41.3015 | 167.3573 | 221.0571 | 206.7195 | 37.5724 | 16.698
629.2542 | 278.0226 | 41.4135 | 166.7575 | 221.0738 | 206.7917 | 37.6166 | 16.7571
630.2542 | 277.8007 | 41.5288 | 166.0225 | 221.2666 | 206.9927 | 37.6628 | 16.8039
631.2542 | 278.3601 | 41.665 | 165.6079 | 221.5983 | 207.0797 | 37.7161 | 16.8535
632.2542 | 281.437 | 41.8109 | 165.3045 | 221.3287 | 206.9974 | 37.7946 | 16.8336
633.2542 | 280.8028 | 41.8931 | 164.9239 | 222.364 | 207.3046 | 37.8547 | 16.8677
634.2542 | 281.071 | 41.9997 | 165.9023 | 222.9442 | 54.9621 | 37.9164 | 16.8842
635.2542 | 281.13 | 42.1194 | 166.156 | 222.9267 | 13.2008 | 37.9698 | 16.9151
636.2542 | 281.8834 | 42.2676 | 166.2452 | 222.7003 | 174.2415 | 38.0142 | 16.9758
637.2542 | 281.6305 | 42.3975 | 169.1627 | 222.7646 | 9.6965 | 38.0723 | 16.9935
638.2542 | 280.1021 | 42.4982 | 168.7613 | 222.2536 | 23.4323 | 38.1255 | 17.0408
639.2542 | 279.472 | 42.6145 | 170.1047 | 221.449 | 179.2664 | 38.1844 | 17.0992
640.2542 | 279.3999 | 42.7265 | 170.2984 | 221.5688 | 9.3697 | 38.2411 | 17.1234
641.2542 | 280.5048 | 42.844 | 169.6232 | 222.8836 | 9.134 | 38.3061 | 17.1572
642.2542 | 280.7628 | 42.967 | 170.3419 | 223.509 | 9.1234 | 38.3475 | 17.1568
643.2542 | 279.8712 | 43.0989 | 170.3251 | 223.2415 | 9.1111 | 38.4064 | 17.2097
644.2542 | 280.0632 | 43.2251 | 170.7018 | 223.5511 | 9.1135 | 38.4673 | 17.2566
645.2542 | 280.6215 | 43.3447 | 171.0021 | 223.5391 | 11.305 | 38.5096 | 17.3108
646.2542 | 280.178 | 43.4577 | 170.2368 | 223.6527 | 87.8926 | 38.5587 | 17.3737
647.2542 | 280.9604 | 43.5544 | 169.3803 | 223.6305 | 39.4208 | 38.6227 | 17.4188
648.2542 | 279.0463 | 43.6608 | 168.9296 | 223.8868 | 21.5798 | 38.6736 | 17.439
649.2542 | 280.1259 | 43.7949 | 169.2167 | 223.794 | 42.3046 | 38.7334 | 17.492
650.2542 | 281.5968 | 43.9066 | 170.1572 | 224.3277 | 9.1246 | 38.7886 | 17.5426
651.2542 | 280.6989 | 44.0235 | 170.4835 | 223.9854 | 9.1201 | 38.8585 | 17.5632
652.2542 | 279.6675 | 44.1447 | 170.9687 | 224.3816 | 9.1186 | 38.921 | 17.5839
653.2542 | 278.9365 | 44.2699 | 170.9342 | 224.607 | 9.1139 | 38.9845 | 17.6237
654.2542 | 278.6554 | 44.3679 | 170.4865 | 224.241 | 9.1195 | 39.0424 | 17.6692
655.2542 | 278.006 | 44.5062 | 170.6527 | 223.9858 | 24.487 | 39.0871 | 17.7626
656.2542 | 277.7659 | 44.6367 | 171.3947 | 224.1634 | 9.1132 | 39.1563 | 17.7589
657.2542 | 278.3613 | 44.7784 | 170.7757 | 223.7862 | 17.5388 | 39.2149 | 17.8139
658.2542 | 278.4474 | 44.9158 | 170.197 | 223.5321 | 96.3236 | 39.2733 | 17.8844
659.2542 | 278.2123 | 45.0192 | 169.745 | 223.4791 | 14.713 | 39.3112 | 17.9335
660.2542 | 277.4614 | 45.1407 | 169.3944 | 223.3772 | 15.427 | 39.3804 | 17.9587
661.2542 | 276.9639 | 45.2534 | 169.3605 | 223.3935 | 9.1426 | 39.4498 | 17.9782
662.2542 | 276.7963 | 45.3799 | 168.4327 | 222.7409 | 9.1291 | 39.4984 | 18.0208
663.2542 | 278.9017 | 45.5893 | 167.6167 | 221.3072 | 208.0579 | 39.453 | 18.2509
664.2542 | 280.1184 | 45.7265 | 167.0203 | 221.3627 | 207.5289 | 39.5021 | 18.3058
665.2542 | 281.9441 | 45.8243 | 167.0179 | 220.8695 | 206.8736 | 39.555 | 18.3089
666.2542 | 282.9044 | 45.9684 | 166.9994 | 220.7921 | 206.9923 | 39.602 | 18.3674
667.2542 | 284.2165 | 46.0773 | 167.459 | 220.7064 | 207.0914 | 39.6546 | 18.4012
668.2542 | 283.7013 | 46.1991 | 167.7952 | 222.3877 | 208.3614 | 39.7098 | 18.4562
669.2542 | 282.9788 | 46.3116 | 167.8059 | 223.0034 | 208.7601 | 39.7657 | 18.4879
670.2542 | 282.1475 | 46.4635 | 170.765 | 223.1726 | 209.1046 | 39.8173 | 18.5386
671.2542 | 282.8423 | 46.582 | 170.5858 | 223.7124 | 209.5281 | 39.875 | 18.5713
672.2542 | 283.5646 | 46.6834 | 171.8422 | 223.7851 | 210.1242 | 39.9376 | 18.6021
673.2542 | 284.8453 | 46.802 | 171.0715 | 223.9852 | 210.3768 | 39.9908 | 18.643
674.2542 | 285.5479 | 46.9517 | 170.3102 | 223.9015 | 210.0271 | 40.049 | 18.7012
675.2542 | 285.5059 | 47.0927 | 169.7392 | 223.7181 | 210.0749 | 40.1095 | 18.7389
676.2542 | 285.3992 | 47.1838 | 169.5388 | 223.699 | 209.8342 | 40.1804 | 18.7421
677.2542 | 286.0429 | 47.3188 | 169.4958 | 223.6069 | 210.2903 | 40.2547 | 18.7748
678.2542 | 283.8314 | 47.4487 | 169.2799 | 223.6485 | 210.4676 | 40.3114 | 18.8146
679.2542 | 283.608 | 47.5979 | 169.5756 | 223.8365 | 210.3011 | 40.3808 | 18.8648
680.2542 | 282.9963 | 47.7236 | 169.3887 | 224.0742 | 210.0313 | 40.4472 | 18.9109
681.2542 | 284.0073 | 47.8457 | 169.9917 | 224.3404 | 210.5201 | 40.5278 | 18.9492
682.2542 | 284.1026 | 47.9682 | 171.4455 | 224.4253 | 210.8744 | 40.5884 | 18.9996
683.2542 | 283.2335 | 48.0966 | 172.1311 | 224.4416 | 211.2326 | 40.6563 | 19.0394
684.2542 | 283.5253 | 48.2234 | 172.7312 | 225.1391 | 211.3563 | 40.722 | 19.0874
685.2542 | 284.0561 | 48.3308 | 172.4743 | 224.7293 | 211.7145 | 40.7886 | 19.1352
686.2542 | 285.7564 | 48.4506 | 172.6856 | 224.8098 | 211.6017 | 40.8547 | 19.1713
687.2542 | 285.2263 | 48.5878 | 173.3378 | 225.1391 | 211.9994 | 40.9222 | 19.2214
688.2542 | 286.7891 | 48.6966 | 173.75 | 225.6425 | 213.0735 | 40.9958 | 19.2734
689.2542 | 285.5698 | 48.7922 | 173.7542 | 226.2373 | 213.7507 | 41.0546 | 19.3267
690.2542 | 284.247 | 48.9479 | 173.5808 | 226.1035 | 213.7942 | 41.1213 | 19.3726
691.2542 | 285.5014 | 49.0702 | 174.0645 | 226.6126 | 214.7055 | 41.1928 | 19.3937
692.2542 | 285.0102 | 49.1959 | 174.3225 | 226.7808 | 214.3125 | 41.2585 | 19.4014
693.2542 | 285.3519 | 49.3246 | 174.8172 | 227.4155 | 215.0308 | 41.3198 | 19.4423
694.2542 | 286.0809 | 49.4707 | 175.1568 | 228.3657 | 215.5115 | 41.3806 | 19.4865
695.2542 | 285.2449 | 49.5817 | 175.1463 | 227.4817 | 215.4759 | 41.4413 | 19.5357
696.2542 | 285.1054 | 49.7228 | 175.4847 | 227.9965 | 214.7277 | 41.5068 | 19.569
697.2542 | 284.3459 | 49.8641 | 175.8575 | 227.7734 | 215.0671 | 41.5657 | 19.6284
698.2542 | 285.3193 | 50.0056 | 176.7737 | 227.438 | 215.3877 | 41.6323 | 19.6596
699.2542 | 284.8752 | 50.1453 | 176.8163 | 226.6118 | 215.6181 | 41.6866 | 19.7024
700.2542 | 284.355 | 50.2833 | 177.212 | 226.3271 | 215.6587 | 41.7471 | 19.7371
701.2542 | 285.9054 | 50.4126 | 177.7561 | 226.2704 | 216.1005 | 41.7926 | 19.8269
702.2542 | 285.8329 | 50.5598 | 177.8363 | 225.996 | 216.4233 | 41.8503 | 19.8799
703.2542 | 285.3141 | 50.6883 | 177.3784 | 225.4504 | 216.7633 | 41.9046 | 19.9194
704.2542 | 287.9955 | 50.8296 | 177.2489 | 225.4499 | 216.6381 | 41.9659 | 19.9646
705.2542 | 289.9107 | 50.9408 | 176.8584 | 225.6985 | 216.7446 | 42.0151 | 20.0018
706.2542 | 289.7517 | 51.0757 | 176.7479 | 225.4926 | 216.6465 | 42.0676 | 20.0618
707.2542 | 288.2071 | 51.2249 | 177.129 | 225.2304 | 216.8474 | 42.1315 | 20.1133
708.2542 | 287.941 | 51.3608 | 177.169 | 225.2144 | 217.5733 | 42.1817 | 20.1561
709.2542 | 288.7874 | 51.5024 | 177.3865 | 225.0686 | 218.0356 | 42.2415 | 20.1821
710.2542 | 289.5703 | 51.6266 | 177.5616 | 225.2459 | 217.9803 | 42.2982 | 20.2421
711.2542 | 291.6858 | 51.7498 | 176.9959 | 225.4778 | 217.7784 | 42.3609 | 20.289
712.2542 | 291.4452 | 51.8813 | 176.6291 | 225.7131 | 218.1689 | 42.4203 | 20.32
713.2542 | 290.0882 | 52.012 | 176.6291 | 225.2608 | 218.6603 | 42.4813 | 20.3646
714.2542 | 290.9769 | 52.1167 | 176.0198 | 225.431 | 218.6484 | 42.5397 | 20.4186
715.2542 | 290.4467 | 52.2395 | 175.7872 | 226.2597 | 220.1227 | 42.6024 | 20.4721
716.2542 | 290.467 | 52.3513 | 175.3539 | 225.9256 | 218.9348 | 42.6689 | 20.5148
717.2542 | 291.1895 | 52.5107 | 175.1158 | 225.1995 | 219.1871 | 42.7342 | 20.5756
718.2542 | 292.909 | 52.6501 | 176.043 | 224.715 | 218.3945 | 42.7979 | 20.6208
719.2542 | 291.7996 | 52.7912 | 176.6078 | 224.8592 | 218.0647 | 42.8647 | 20.6599
720.2542 | 290.7893 | 52.9184 | 176.5986 | 225.2651 | 217.6816 | 42.922 | 20.6942
721.2542 | 290.8884 | 53.0648 | 176.1818 | 225.1887 | 217.8916 | 42.9878 | 20.7476
722.2542 | 290.8737 | 53.1984 | 175.9175 | 225.0703 | 218.0484 | 43.0537 | 20.7828
723.2542 | 290.0844 | 53.344 | 176.3808 | 225.9908 | 218.6989 | 43.1079 | 20.8327
724.2542 | 291.8852 | 53.4496 | 176.6526 | 226.2497 | 218.8876 | 43.1662 | 20.8799
725.2542 | 290.237 | 53.5674 | 176.8446 | 226.4854 | 219.0669 | 43.2226 | 20.9256
726.2542 | 289.9023 | 53.6888 | 176.9843 | 227.0327 | 219.5052 | 43.2854 | 20.975
727.2542 | 289.6738 | 53.8152 | 177.1493 | 227.3479 | 220.3453 | 43.3629 | 21.0375
728.2542 | 290.237 | 53.9459 | 177.7792 | 227.3159 | 219.9649 | 43.4363 | 21.0659
729.2542 | 290.2656 | 54.0924 | 178.2811 | 226.9786 | 220.0736 | 43.505 | 21.105
730.2542 | 289.3118 | 54.2425 | 179.9468 | 226.4421 | 220.4402 | 43.5708 | 21.1141
731.2542 | 289.1226 | 54.3768 | 179.8078 | 226.1136 | 220.1865 | 43.6392 | 21.1692
732.2542 | 289.3737 | 54.4926 | 179.8397 | 226.0728 | 220.1428 | 43.6977 | 21.2408
733.2542 | 290.2964 | 54.6405 | 180.5637 | 225.9882 | 220.7982 | 43.7608 | 21.2739
734.2542 | 290.127 | 54.7553 | 180.9103 | 226.3562 | 220.6585 | 43.8312 | 21.322
735.2542 | 291.9771 | 54.8858 | 181.4457 | 227.144 | 220.6527 | 43.8947 | 21.3451
736.2542 | 291.118 | 55.0401 | 181.4637 | 226.9538 | 221.9532 | 43.9598 | 21.4197
737.2542 | 290.9054 | 55.1574 | 181.4998 | 226.8985 | 222.1714 | 44.0237 | 21.479
738.2542 | 291.2742 | 55.2906 | 182.7516 | 227.3866 | 222.1382 | 44.0961 | 21.525
739.2542 | 290.5608 | 55.4226 | 183.4447 | 227.228 | 221.7461 | 44.1519 | 21.5739
740.2542 | 290.026 | 55.5594 | 183.2921 | 227.4313 | 221.8767 | 44.2189 | 21.6053
741.2542 | 290.6484 | 55.7353 | 182.9496 | 227.6102 | 222.7103 | 44.2785 | 21.6621
742.2542 | 290.8959 | 55.8765 | 181.9932 | 228.4628 | 223.3396 | 44.357 | 21.6972
743.2542 | 292.1746 | 56.0032 | 180.8652 | 228.9592 | 223.7556 | 44.3943 | 21.7155
744.2542 | 291.8552 | 56.1499 | 180.8844 | 228.7622 | 222.8448 | 44.4478 | 21.7618
745.2542 | 292.0771 | 56.3006 | 180.2841 | 228.5049 | 222.2688 | 44.5231 | 21.837
746.2542 | 292.7333 | 56.4391 | 179.9646 | 228.4421 | 222.203 | 44.5907 | 21.8781
747.2542 | 293.2202 | 56.5762 | 179.4636 | 227.8005 | 222.3029 | 44.6512 | 21.923
748.2542 | 292.5103 | 56.6906 | 180.6372 | 227.9723 | 221.9857 | 44.7055 | 21.9832
749.2542 | 292.1538 | 56.8225 | 180.9327 | 228.6317 | 221.8254 | 44.7591 | 22.0208
750.2542 | 290.9076 | 56.958 | 180.9845 | 229.0431 | 221.8915 | 44.8256 | 22.048
751.2542 | 291.6895 | 57.1193 | 180.9025 | 230.078 | 222.1226 | 44.8898 | 22.1149
752.2542 | 292.3022 | 57.267 | 180.8536 | 230.596 | 222.2734 | 44.9402 | 22.1491
753.2542 | 293.9542 | 57.3967 | 181.0475 | 231.6974 | 223.2476 | 45.0082 | 22.2079
754.2542 | 292.9303 | 57.5189 | 181.7093 | 232.4985 | 223.6503 | 45.0688 | 22.2714
755.2542 | 293.838 | 57.6532 | 181.2974 | 232.0459 | 223.2175 | 45.1288 | 22.2908
756.2542 | 293.38 | 57.7919 | 180.7504 | 231.7264 | 223.0626 | 45.1856 | 22.3409
757.2542 | 293.2344 | 57.9366 | 180.9111 | 231.8634 | 223.4224 | 45.2461 | 22.3779
758.2542 | 294.0698 | 58.0956 | 181.2709 | 231.2849 | 223.0003 | 45.3102 | 22.4326
759.2542 | 294.6058 | 58.2333 | 180.6917 | 230.9546 | 222.5967 | 45.3718 | 22.4785
760.2542 | 296.1623 | 58.3351 | 180.4547 | 230.5836 | 222.8702 | 45.4322 | 22.5238
761.2542 | 295.6335 | 58.4659 | 179.7475 | 229.8713 | 222.7565 | 45.4956 | 22.5623
762.2542 | 295.936 | 58.6054 | 178.937 | 230.8061 | 222.8152 | 45.5479 | 22.6157
763.2542 | 294.9406 | 58.7549 | 179.354 | 230.5819 | 222.6348 | 45.6045 | 22.6486
764.2542 | 295.4846 | 58.894 | 178.8224 | 230.7297 | 222.6967 | 45.6664 | 22.7144
765.2542 | 296.1089 | 59.0211 | 178.5737 | 230.7202 | 222.7772 | 45.722 | 22.7539
766.2542 | 296.0376 | 59.1559 | 179.0788 | 230.6723 | 222.911 | 45.7798 | 22.8066
767.2542 | 295.4161 | 59.3259 | 179.0314 | 231.0529 | 222.9077 | 45.8223 | 22.8345
768.2542 | 295.0443 | 59.4785 | 179.1519 | 230.7751 | 223.1746 | 45.8878 | 22.8998
769.2542 | 295.4001 | 59.6384 | 180.3275 | 231.5539 | 223.782 | 45.9455 | 22.9419
770.2542 | 294.9994 | 59.7904 | 180.5368 | 232.2156 | 223.3059 | 45.994 | 22.998
771.2542 | 295.17 | 59.9228 | 180.4509 | 232.2206 | 223.7858 | 46.0556 | 23.0423
772.2542 | 295.1473 | 60.0767 | 181.1708 | 232.0413 | 223.589 | 46.1095 | 23.0978
773.2542 | 294.8714 | 60.1882 | 181.3745 | 231.8077 | 223.1901 | 46.174 | 23.1165
774.2542 | 294.7148 | 60.316 | 181.3752 | 231.1265 | 222.4856 | 46.228 | 23.1743
775.2542 | 293.633 | 60.4506 | 180.9635 | 231.078 | 221.4633 | 46.3021 | 23.2175
776.2542 | 292.2732 | 60.5925 | 180.6297 | 231.1138 | 221.5151 | 46.3515 | 23.2732
777.2542 | 291.51 | 60.7222 | 180.7331 | 230.9203 | 220.6748 | 46.4116 | 23.3183
778.2542 | 292.3323 | 60.8538 | 181.0237 | 231.0938 | 220.8485 | 46.4689 | 23.3682
779.2542 | 292.0124 | 60.9861 | 181.087 | 231.6498 | 220.6 | 46.5237 | 23.4168
780.2542 | 291.8126 | 61.0967 | 180.7238 | 232.5511 | 219.9991 | 46.5734 | 23.4607
781.2542 | 291.4861 | 61.2311 | 180.7174 | 231.6008 | 219.4396 | 46.6306 | 23.5038
782.2542 | 292.364 | 61.3555 | 180.6392 | 231.3237 | 219.1144 | 46.685 | 23.547
783.2542 | 292.7105 | 61.4883 | 180.2904 | 230.7292 | 218.3338 | 46.7334 | 23.5933
784.2542 | 292.4792 | 61.621 | 180.2558 | 230.2267 | 218.0572 | 46.7852 | 23.6538
785.2542 | 292.5522 | 61.7589 | 180.1277 | 229.9752 | 217.6559 | 46.8423 | 23.6873
786.2542 | 291.9403 | 61.9273 | 179.7947 | 229.6084 | 217.9372 | 46.8868 | 23.7535
787.2542 | 290.8192 | 62.0542 | 179.706 | 229.308 | 217.4193 | 46.9412 | 23.7906
788.2542 | 290.3912 | 62.1898 | 179.1481 | 229.196 | 217.1352 | 46.9871 | 23.838
789.2542 | 289.2449 | 62.3452 | 178.6345 | 229.0485 | 217.2077 | 47.0433 | 23.8814
790.2542 | 291.0118 | 62.5064 | 178.8126 | 228.6595 | 217.1837 | 47.0987 | 23.9174
791.2542 | 290.388 | 62.6379 | 178.6304 | 228.514 | 217.5273 | 47.1475 | 23.9642
792.2542 | 290.5644 | 62.7772 | 178.7872 | 228.2458 | 217.8114 | 47.2048 | 24.0029
793.2542 | 289.4974 | 62.9137 | 179.1274 | 228.3723 | 217.4442 | 47.2548 | 24.0576
794.2542 | 289.2436 | 63.0712 | 179.4382 | 228.5015 | 217.6776 | 47.3069 | 24.1052
795.2542 | 289.3367 | 63.2155 | 179.1507 | 229.4143 | 218.0676 | 47.3584 | 24.1589
796.2542 | 288.5374 | 63.3539 | 179.1151 | 229.3362 | 217.8895 | 47.4128 | 24.2069
797.2542 | 288.2092 | 63.475 | 179.0453 | 229.2332 | 217.2625 | 47.4622 | 24.2476
798.2542 | 287.7755 | 63.6122 | 179.3249 | 228.7642 | 217.6184 | 47.5084 | 24.2972
799.2542 | 288.3277 | 63.7377 | 179.3514 | 227.8884 | 217.554 | 47.5651 | 24.3428
800.2542 | 287.5754 | 63.8602 | 179.5347 | 227.5907 | 217.4278 | 47.6107 | 24.3917
801.2542 | 286.9919 | 63.9776 | 180.3309 | 227.4615 | 217.11 | 47.6601 | 24.4447
802.2542 | 287.1695 | 64.1036 | 179.7098 | 227.9813 | 217.4648 | 47.708 | 24.5138
803.2542 | 286.6433 | 64.2197 | 179.4598 | 228.0333 | 217.9011 | 47.7561 | 24.5558
804.2542 | 285.9054 | 64.3404 | 179.0661 | 227.8198 | 218.0823 | 47.7987 | 24.6061
805.2542 | 286.0395 | 64.4876 | 179.0546 | 227.9575 | 218.6303 | 47.8486 | 24.6557
806.2542 | 284.8586 | 64.6148 | 179.6399 | 228.4277 | 218.8288 | 47.8991 | 24.6952
807.2542 | 284.3519 | 64.7493 | 179.2671 | 228.2027 | 219.5339 | 47.9486 | 24.7363
808.2542 | 284.3943 | 64.9013 | 179.0215 | 227.8681 | 219.6028 | 47.9959 | 24.786
809.2542 | 283.3511 | 65.0343 | 178.7162 | 227.5325 | 219.3667 | 48.0422 | 24.8282
810.2542 | 282.952 | 65.1734 | 178.5666 | 227.0243 | 219.1894 | 48.086 | 24.8897
811.2542 | 282.0702 | 65.3122 | 178.9258 | 226.967 | 219.7632 | 48.1436 | 24.9457
812.2542 | 281.1402 | 65.4398 | 178.998 | 227.4469 | 219.9835 | 48.1772 | 24.9829
813.2542 | 281.1001 | 65.5765 | 179.3335 | 228.6715 | 219.6197 | 48.2244 | 25.0306
814.2542 | 280.9459 | 65.7187 | 180.5667 | 228.8931 | 220.0852 | 48.2713 | 25.0776
815.2542 | 281.3386 | 65.8604 | 180.4733 | 229.1897 | 220.4206 | 48.3171 | 25.1321
816.2542 | 281.7992 | 65.9836 | 180.6108 | 230.0889 | 221.6638 | 48.3694 | 25.1906
817.2542 | 281.6184 | 66.1251 | 181.6528 | 230.0919 | 222.2373 | 48.4191 | 25.2343
818.2542 | 281.7855 | 66.2701 | 181.4797 | 229.8214 | 221.9917 | 48.4635 | 25.2787
819.2542 | 281.073 | 66.414 | 181.2141 | 229.5299 | 221.6124 | 48.5166 | 25.3371
820.2542 | 282.7967 | 66.5663 | 181.4987 | 230.5751 | 222.0826 | 48.5647 | 25.3797
821.2542 | 282.6164 | 66.71 | 181.1137 | 230.983 | 221.9115 | 48.622 | 25.4395
822.2542 | 281.9368 | 66.8258 | 181.5649 | 231.3732 | 221.9129 | 48.6629 | 25.478
823.2542 | 281.2131 | 66.9429 | 182.3181 | 231.2238 | 221.777 | 48.7179 | 25.5193
824.2542 | 280.5991 | 67.0788 | 182.3546 | 230.8068 | 221.7663 | 48.763 | 25.5813
825.2542 | 279.4017 | 67.2094 | 181.7583 | 230.6787 | 222.1413 | 48.8119 | 25.6098
826.2542 | 279.2042 | 67.3499 | 181.8107 | 230.1111 | 222.0733 | 48.8601 | 25.6734
827.2542 | 278.6016 | 67.4773 | 181.3881 | 229.6131 | 222.4673 | 48.8913 | 25.7173
828.2542 | 279.2296 | 67.6212 | 181.0311 | 229.924 | 222.4485 | 48.9416 | 25.771
829.2542 | 279.1064 | 67.7509 | 180.7967 | 229.5863 | 223.0216 | 48.9688 | 25.8601
830.2542 | 280.2163 | 67.883 | 180.8538 | 229.929 | 223.3278 | 49.0284 | 25.8889
831.2542 | 282.9593 | 68.0048 | 181.1014 | 229.8063 | 223.4582 | 49.0727 | 25.9265
832.2542 | 284.4397 | 68.14 | 181.8916 | 230.0811 | 223.6148 | 49.1283 | 25.9765
833.2542 | 285.0036 | 68.2726 | 182.2125 | 231.3561 | 224.0066 | 49.1793 | 26.0318
834.2542 | 284.6437 | 68.3953 | 182.3367 | 231.2058 | 223.795 | 49.2371 | 26.0656
835.2542 | 285.4525 | 68.5287 | 183.275 | 231.713 | 225.303 | 49.2899 | 26.1118
836.2542 | 285.9162 | 68.6634 | 183.3214 | 231.6647 | 224.9777 | 49.3397 | 26.1781
837.2542 | 285.5689 | 68.7919 | 183.7938 | 231.5251 | 224.44 | 49.3904 | 26.2065
838.2542 | 286.8658 | 68.9302 | 183.5214 | 231.1619 | 224.4247 | 49.4409 | 26.2707
839.2542 | 287.1081 | 69.0753 | 184.1116 | 230.6659 | 224.0406 | 49.4936 | 26.3132
840.2542 | 287.2951 | 69.1981 | 184.8846 | 229.9861 | 224.1253 | 49.5444 | 26.3548
841.2542 | 286.5037 | 69.328 | 184.617 | 229.7931 | 224.089 | 49.6001 | 26.4185
842.2542 | 286.5434 | 69.4513 | 183.9766 | 229.7592 | 223.6523 | 49.6511 | 26.4756
843.2542 | 287.436 | 69.5866 | 183.5698 | 229.7054 | 223.7337 | 49.7051 | 26.5082
844.2542 | 287.703 | 69.7062 | 183.3011 | 229.7871 | 223.0647 | 49.7433 | 26.5678
845.2542 | 287.8869 | 69.8339 | 182.9275 | 229.7051 | 222.5475 | 49.7966 | 26.6063
846.2542 | 287.4389 | 69.9773 | 182.7737 | 229.5534 | 222.5121 | 49.8451 | 26.6763
847.2542 | 287.6248 | 70.1138 | 182.5039 | 229.505 | 222.0477 | 49.8957 | 26.7125
848.2542 | 287.9582 | 70.2542 | 182.4287 | 230.2884 | 221.9032 | 49.9465 | 26.7652
849.2542 | 288.4512 | 70.377 | 182.0022 | 230.8803 | 222.8522 | 49.9834 | 26.8163
850.2542 | 289.3032 | 70.5175 | 181.9504 | 231.3573 | 222.7939 | 50.0343 | 26.8581
851.2542 | 288.1537 | 70.644 | 181.9824 | 231.4961 | 223.1924 | 50.0856 | 26.9133
852.2542 | 288.2396 | 70.7569 | 182.3239 | 231.7152 | 223.6895 | 50.1331 | 26.9481
853.2542 | 288.2875 | 70.8919 | 182.0198 | 231.4603 | 224.1393 | 50.1886 | 27.0057
854.2542 | 288.0394 | 71.0031 | 181.8528 | 231.406 | 224.3455 | 50.2409 | 27.0501
855.2542 | 287.9688 | 71.1295 | 181.648 | 231.5971 | 224.7358 | 50.2969 | 27.1011
856.2542 | 289.4808 | 71.2631 | 181.406 | 231.1823 | 224.714 | 50.3517 | 27.1539
857.2542 | 289.9656 | 71.3885 | 181.3224 | 230.9512 | 224.9623 | 50.3965 | 27.1891
858.2542 | 289.0582 | 71.514 | 181.7475 | 231.1016 | 225.0546 | 50.4427 | 27.2513
859.2542 | 288.5724 | 71.6505 | 182.1755 | 231.2263 | 225.321 | 50.5033 | 27.3016
860.2542 | 288.68 | 71.7841 | 181.9446 | 231.0739 | 225.7992 | 50.5468 | 27.3511
861.2542 | 288.0003 | 71.9111 | 181.6536 | 231.1677 | 224.9775 | 50.6061 | 27.4008
862.2542 | 287.8143 | 72.0388 | 182.135 | 231.2137 | 224.4266 | 50.6636 | 27.4524
863.2542 | 287.174 | 72.1654 | 181.8655 | 230.9204 | 224.6714 | 50.7161 | 27.4991
864.2542 | 286.1029 | 72.3018 | 182.8757 | 230.8592 | 224.1775 | 50.773 | 27.5428
865.2542 | 287.398 | 72.4186 | 182.9447 | 230.1652 | 223.3555 | 50.8228 | 27.5919
866.2542 | 287.8487 | 72.5498 | 184.7136 | 230.06 | 223.0388 | 50.8821 | 27.6374
867.2542 | 288.6171 | 72.6676 | 185.7453 | 229.5991 | 222.5984 | 50.929 | 27.7001
868.2542 | 289.0048 | 72.7954 | 186.888 | 229.6617 | 222.3221 | 50.9848 | 27.733
869.2542 | 288.2726 | 72.9228 | 186.4171 | 229.9719 | 222.4419 | 51.0354 | 27.794
870.2542 | 288.1438 | 73.0475 | 186.4797 | 229.9604 | 222.6773 | 51.0941 | 27.852
871.2542 | 288.3181 | 73.1759 | 186.1674 | 229.8828 | 222.6207 | 51.1419 | 27.8957
872.2542 | 289.5957 | 73.2946 | 185.6107 | 230.2764 | 222.2141 | 51.1984 | 27.9344
873.2542 | 290.1412 | 73.4104 | 185.244 | 230.8105 | 222.5376 | 51.2476 | 27.999
874.2542 | 289.589 | 73.5313 | 184.9378 | 231.1421 | 223.0036 | 51.287 | 28.0394
875.2542 | 288.0241 | 73.6663 | 184.8469 | 231.8836 | 223.6952 | 51.3453 | 28.109
876.2542 | 286.822 | 73.7918 | 184.8948 | 231.7053 | 223.8769 | 51.3847 | 28.1509
877.2542 | 287.1626 | 73.9019 | 184.6983 | 231.8789 | 223.77 | 51.4377 | 28.2123
878.2542 | 287.8252 | 74.0185 | 184.3677 | 231.4747 | 224.1277 | 51.4799 | 28.2479
879.2542 | 288.5091 | 74.1438 | 185.0518 | 232.0223 | 223.6947 | 51.5323 | 28.3024
880.2542 | 287.4604 | 74.2843 | 184.8958 | 232.6347 | 223.422 | 51.5785 | 28.3483
881.2542 | 286.6432 | 74.4077 | 184.8404 | 232.2961 | 222.9057 | 51.6283 | 28.3758
882.2542 | 285.5981 | 74.5383 | 184.6532 | 232.3461 | 223.4212 | 51.6779 | 28.4476
883.2542 | 285.8917 | 74.6621 | 184.7156 | 232.1669 | 224.1856 | 51.7228 | 28.5024
884.2542 | 285.3738 | 74.7835 | 184.5226 | 232.3064 | 224.3913 | 51.7712 | 28.5505
885.2542 | 284.8475 | 74.9092 | 185.2107 | 232.709 | 224.4496 | 51.821 | 28.5938
886.2542 | 287.1245 | 75.0219 | 186.0071 | 232.7245 | 224.6725 | 51.8618 | 28.6611
887.2542 | 286.9717 | 75.1586 | 186.6617 | 232.7369 | 224.9256 | 51.9218 | 28.7121
888.2542 | 286.2862 | 75.2706 | 185.8644 | 231.9558 | 224.6524 | 51.9614 | 28.7713
889.2542 | 285.6969 | 75.3953 | 184.9204 | 231.2988 | 224.8296 | 52.0113 | 28.7992
890.2542 | 286.4661 | 75.5163 | 184.0027 | 230.9618 | 224.8051 | 52.0638 | 28.8572
891.2542 | 285.3407 | 75.64 | 183.7853 | 232.0985 | 224.71 | 52.105 | 28.9117
892.2542 | 286.7091 | 75.7622 | 183.5137 | 232.127 | 225.4662 | 52.1556 | 28.9544
893.2542 | 287.0278 | 75.8931 | 184.7262 | 232.0411 | 225.5821 | 52.2086 | 29.0073
894.2542 | 289.6108 | 76.0085 | 184.6963 | 232.2208 | 225.4814 | 52.2547 | 29.0519
895.2542 | 290.1986 | 76.1334 | 184.3034 | 232.0505 | 225.7214 | 52.303 | 29.1072
896.2542 | 289.3426 | 76.2656 | 184.0373 | 232.036 | 225.8859 | 52.3465 | 29.1507
897.2542 | 288.1116 | 76.3785 | 183.7457 | 232.4693 | 225.3934 | 52.3968 | 29.2125
898.2542 | 287.0806 | 76.4906 | 184.2341 | 232.6884 | 225.3464 | 52.4486 | 29.2646
899.2542 | 286.8057 | 76.6077 | 184.1672 | 232.2974 | 225.164 | 52.4933 | 29.3053
900.2542 | 287.2485 | 76.7392 | 184.8243 | 232.5847 | 225.4717 | 52.5478 | 29.3482
901.2542 | 288.6856 | 76.8628 | 185.0681 | 232.8963 | 225.6955 | 52.593 | 29.3915
902.2542 | 287.8964 | 76.9861 | 185.3557 | 232.6583 | 226.1444 | 52.6409 | 29.4486
903.2542 | 287.4121 | 77.1185 | 185.3 | 233.3607 | 226.5258 | 52.6935 | 29.5111
904.2542 | 287.6757 | 77.2481 | 185.6391 | 232.8549 | 226.9115 | 52.7434 | 29.5589
905.2542 | 287.578 | 77.3666 | 185.8818 | 233.3755 | 226.7605 | 52.79 | 29.6079
906.2542 | 287.992 | 77.4923 | 186.0777 | 233.3086 | 226.6177 | 52.8562 | 29.6464
907.2542 | 290.1686 | 77.6205 | 186.543 | 233.0659 | 226.1675 | 52.9077 | 29.7013
908.2542 | 291.3397 | 77.7473 | 186.9167 | 233.4604 | 226.7635 | 52.9682 | 29.7637
909.2542 | 291.2718 | 77.8736 | 187.2546 | 234.3801 | 227.3636 | 53.0246 | 29.8
910.2542 | 290.1372 | 78.0029 | 187.7761 | 234.8662 | 227.6536 | 53.0826 | 29.8523
911.2542 | 291.1803 | 78.123 | 187.9449 | 234.3415 | 228.5392 | 53.1483 | 29.9078
912.2542 | 292.9078 | 78.2577 | 188.3971 | 234.0347 | 229.7459 | 53.2054 | 29.9672
913.2542 | 292.0676 | 78.3849 | 188.5991 | 233.7219 | 229.4929 | 53.2507 | 29.9976
914.2542 | 294.0017 | 78.5023 | 189.2099 | 233.5555 | 229.7312 | 53.3103 | 30.0502
915.2542 | 295.6358 | 78.6269 | 189.5422 | 233.7269 | 230.0896 | 53.363 | 30.1025
916.2542 | 297.7302 | 78.7595 | 190.0962 | 236.4905 | 230.4843 | 53.4116 | 30.153
917.2542 | 298.098 | 78.8771 | 190.3081 | 236.3589 | 232.0336 | 53.4712 | 30.2173
918.2542 | 298.3364 | 78.9818 | 190.5771 | 236.9125 | 232.3875 | 53.5185 | 30.2628
919.2542 | 298.4995 | 79.0953 | 191.4502 | 237.966 | 232.9918 | 53.5611 | 30.2894
920.2542 | 300.5108 | 79.2237 | 191.3053 | 238.795 | 232.8602 | 53.6163 | 30.3409
921.2542 | 300.3119 | 79.3321 | 191.465 | 239.2168 | 233.2008 | 53.6728 | 30.3699
922.2542 | 300.6523 | 79.4497 | 191.6594 | 239.2911 | 233.2524 | 53.7317 | 30.4315
923.2542 | 300.4371 | 79.5712 | 192.5429 | 239.5107 | 233.2921 | 53.7725 | 30.48
924.2542 | 300.0158 | 79.6977 | 192.6102 | 240.2911 | 233.2597 | 53.8195 | 30.535
925.2542 | 300.3389 | 79.8196 | 192.7045 | 239.9703 | 233.3126 | 53.879 | 30.5845
926.2542 | 301.2268 | 79.9397 | 193.2327 | 241.2744 | 232.9026 | 53.9376 | 30.6393
927.2542 | 301.5193 | 80.0658 | 193.8116 | 240.882 | 232.8639 | 53.9964 | 30.6981
928.2542 | 301.0516 | 80.1879 | 194.4586 | 241.1119 | 235.501 | 54.0602 | 30.7525
929.2542 | 302.8441 | 80.3131 | 194.5169 | 241.7034 | 234.606 | 54.1196 | 30.8058
930.2542 | 304.6035 | 80.4302 | 193.9615 | 242.0722 | 234.1334 | 54.1885 | 30.8339
931.2542 | 304.4119 | 80.5462 | 193.6197 | 241.8478 | 235.001 | 54.2463 | 30.894
932.2542 | 306.8257 | 80.6704 | 193.3602 | 241.3087 | 233.9031 | 54.2907 | 30.9208
933.2542 | 308.1322 | 80.7935 | 192.9081 | 240.7804 | 234.0625 | 54.3592 | 30.9852
934.2542 | 308.9688 | 80.9133 | 193.1561 | 240.7255 | 233.7348 | 54.4184 | 31.0467
935.2542 | 311.0071 | 81.0288 | 192.8804 | 241.1915 | 233.4195 | 54.4781 | 31.0977
936.2542 | 311.0878 | 81.1489 | 192.5667 | 240.8607 | 232.7034 | 54.5364 | 31.1442
937.2542 | 311.1631 | 81.2559 | 192.1868 | 240.5662 | 232.7267 | 54.5859 | 31.1927
938.2542 | 311.3149 | 81.3684 | 192.1732 | 240.4826 | 232.9277 | 54.6435 | 31.235
939.2542 | 311.1828 | 81.4885 | 192.2209 | 240.3667 | 232.2277 | 54.7004 | 31.3096
940.2542 | 311.127 | 81.612 | 192.0776 | 240.1964 | 231.9829 | 54.7526 | 31.3408
941.2542 | 312.5967 | 81.7305 | 192.0835 | 240.2041 | 231.6634 | 54.8097 | 31.3941
942.2542 | 313.5799 | 81.842 | 192.1977 | 240.2586 | 232.9392 | 54.8619 | 31.4446
943.2542 | 314.3027 | 81.9621 | 192.2658 | 240.6995 | 233.4888 | 54.9175 | 31.4987
944.2542 | 314.973 | 82.0818 | 193.3078 | 240.7358 | 233.9164 | 54.9758 | 31.541
945.2542 | 314.4284 | 82.1849 | 194.203 | 240.8424 | 233.6725 | 55.016 | 31.5904
946.2542 | 314.1823 | 82.3011 | 194.744 | 241.2065 | 234.7614 | 55.0648 | 31.6359
947.2542 | 313.6053 | 82.4147 | 195.1803 | 242.074 | 235.2939 | 55.1248 | 31.6938
948.2542 | 313.9957 | 82.5289 | 196.2268 | 241.5428 | 235.4504 | 55.1875 | 31.7419
949.2542 | 315.7803 | 82.6368 | 196.1433 | 241.0171 | 235.4938 | 55.2356 | 31.7985
950.2542 | 317.8245 | 82.7613 | 196.379 | 241.3226 | 235.3873 | 55.2953 | 31.8534
951.2542 | 318.4154 | 82.8791 | 196.3238 | 242.0548 | 235.8025 | 55.3535 | 31.9169
952.2542 | 318.2787 | 82.9882 | 196.6898 | 243.0974 | 235.4832 | 55.4096 | 31.9641
953.2542 | 318.1041 | 83.1005 | 196.9172 | 243.7002 | 236.6153 | 55.4534 | 32.0249
954.2542 | 316.5872 | 83.2147 | 197.3702 | 243.7615 | 236.4346 | 55.5061 | 32.0532
955.2542 | 315.7258 | 83.3243 | 197.2691 | 243.9271 | 236.6221 | 55.5651 | 32.1049
956.2542 | 315.0902 | 83.4418 | 197.0056 | 244.6686 | 236.7857 | 55.63 | 32.1507
957.2542 | 316.4466 | 83.5689 | 197.6219 | 244.4025 | 236.3046 | 55.6784 | 32.2085
958.2542 | 317.6808 | 83.6857 | 197.7622 | 244.0774 | 236.7504 | 55.7436 | 32.2552
959.2542 | 319.5291 | 83.8091 | 198.4162 | 244.3424 | 238.1238 | 55.8079 | 32.314
960.2542 | 319.1661 | 83.9297 | 198.7394 | 244.629 | 237.7852 | 55.8613 | 32.3745
961.2542 | 318.7296 | 84.0633 | 198.5475 | 245.0818 | 236.98 | 55.9247 | 32.4246
962.2542 | 320.5529 | 84.1919 | 198.2061 | 244.854 | 236.6703 | 55.9867 | 32.4766
963.2542 | 321.2742 | 84.3028 | 198.5125 | 244.8816 | 236.6077 | 56.0524 | 32.526
964.2542 | 321.4491 | 84.4247 | 198.3538 | 244.6721 | 236.8189 | 56.1122 | 32.5862
965.2542 | 320.6431 | 84.5381 | 197.9206 | 245.1773 | 236.7767 | 56.1673 | 32.6245
966.2542 | 320.895 | 84.6509 | 198.262 | 245.126 | 238.1265 | 56.2202 | 32.6845
967.2542 | 320.4547 | 84.7709 | 198.3281 | 244.7013 | 237.6751 | 56.2802 | 32.7249
968.2542 | 320.7527 | 84.8845 | 198.2222 | 244.7559 | 238.0921 | 56.3416 | 32.7826
969.2542 | 321.1395 | 85.0074 | 199.2093 | 244.5788 | 239.0526 | 56.3991 | 32.8456
970.2542 | 320.5272 | 85.1223 | 199.0896 | 244.6891 | 238.9664 | 56.4568 | 32.8935
971.2542 | 320.4849 | 85.2405 | 198.6545 | 244.5055 | 239.388 | 56.5176 | 32.9409
972.2542 | 321.504 | 85.3634 | 198.5077 | 244.054 | 239.5252 | 56.5723 | 32.9739
973.2542 | 322.1236 | 85.4664 | 198.7732 | 243.4012 | 239.3705 | 56.6345 | 33.0452
974.2542 | 323.12 | 85.5885 | 198.5876 | 243.352 | 238.8517 | 56.6927 | 33.1069
975.2542 | 322.8519 | 85.7023 | 198.0982 | 243.7623 | 238.9941 | 56.755 | 33.14
976.2542 | 322.2689 | 85.8089 | 198.6279 | 243.9559 | 239.3819 | 56.8034 | 33.2022
977.2542 | 321.4844 | 85.9388 | 199.329 | 245.2619 | 239.0514 | 56.8584 | 33.2496
978.2542 | 322.0692 | 86.0439 | 200.0957 | 245.4324 | 238.7391 | 56.9262 | 33.2962
979.2542 | 322.12 | 86.1645 | 200.5687 | 245.4975 | 238.8341 | 56.9741 | 33.3586
980.2542 | 322.3423 | 86.273 | 200.8523 | 245.4625 | 239.4945 | 57.0342 | 33.39
981.2542 | 322.8139 | 86.3834 | 200.9539 | 245.4419 | 239.6138 | 57.0914 | 33.4409
982.2542 | 321.7788 | 86.498 | 200.7747 | 246.1178 | 239.3335 | 57.1433 | 33.5095
983.2542 | 321.4472 | 86.6266 | 200.4327 | 246.6563 | 239.3171 | 57.2043 | 33.5409
984.2542 | 321.5125 | 86.7497 | 200.2237 | 246.3195 | 239.5827 | 57.2603 | 33.5947
985.2542 | 322.3657 | 86.8704 | 199.8895 | 246.3848 | 239.8166 | 57.3169 | 33.6577
986.2542 | 320.5784 | 86.9833 | 199.6019 | 245.7486 | 239.2557 | 57.3731 | 33.7036
987.2542 | 319.6967 | 87.1149 | 199.5979 | 245.7533 | 239.3451 | 57.4281 | 33.7543
988.2542 | 321.723 | 87.2437 | 199.8875 | 246.4693 | 239.0841 | 57.4885 | 33.7964
989.2542 | 322.4994 | 87.3654 | 200.3371 | 246.0542 | 239.7409 | 57.5447 | 33.846
990.2542 | 325.1839 | 87.4844 | 199.7016 | 245.9307 | 239.9959 | 57.6046 | 33.889
991.2542 | 324.8039 | 87.6077 | 199.9772 | 246.2792 | 240.71 | 57.6618 | 33.9357
992.2542 | 324.0756 | 87.7231 | 199.8206 | 246.5586 | 240.8732 | 57.718 | 34.0026
993.2542 | 325.349 | 87.8446 | 200.2128 | 246.3123 | 240.6902 | 57.7671 | 34.066
994.2542 | 325.2144 | 87.9596 | 200.4671 | 246.998 | 240.7194 | 57.8206 | 34.1171
995.2542 | 324.7368 | 88.0655 | 201.3688 | 247.0211 | 240.3352 | 57.8811 | 34.1553
996.2542 | 325.3408 | 88.1908 | 201.8259 | 246.7899 | 240.292 | 57.9356 | 34.2225
997.2542 | 325.6461 | 88.3113 | 201.5089 | 247.071 | 240.198 | 57.9917 | 34.2794
998.2542 | 326.901 | 88.4322 | 201.7484 | 247.169 | 240.1531 | 58.0443 | 34.3354
999.2542 | 326.8112 | 88.5527 | 201.2139 | 247.3118 | 240.2481 | 58.1108 | 34.3739
1000.2542 | 328.0782 | 88.6766 | 201.1067 | 247.5242 | 240.5578 | 58.1656 | 34.4005
1001.2542 | 328.77 | 88.8076 | 200.7384 | 247.7024 | 241.2041 | 58.2242 | 34.4575
1002.2542 | 327.4432 | 88.9285 | 200.5896 | 247.6238 | 240.7351 | 58.2754 | 34.51
1003.2542 | 327.1548 | 89.0502 | 200.9221 | 249.3869 | 240.7067 | 58.3382 | 34.5373
1004.2542 | 326.8491 | 89.1761 | 201.2276 | 248.9918 | 241.0165 | 58.393 | 34.5642
1005.2542 | 326.3854 | 89.3023 | 201.2542 | 248.5826 | 241.3255 | 58.452 | 34.6484
1006.2542 | 325.802 | 89.4237 | 201.7265 | 248.2837 | 242.2572 | 58.4981 | 34.6897
1007.2542 | 325.0905 | 89.549 | 201.8554 | 247.8071 | 242.1241 | 58.5576 | 34.7322
1008.2542 | 325.1459 | 89.6575 | 201.4444 | 248.0185 | 242.6626 | 58.6219 | 34.7878
1009.2542 | 323.951 | 89.7887 | 201.2334 | 248.5537 | 243.046 | 58.6805 | 34.8403
1010.2542 | 323.1148 | 89.9081 | 201.2305 | 248.3603 | 243.2982 | 58.7307 | 34.889
1011.2542 | 322.5202 | 90.0362 | 201.033 | 248.1032 | 243.4625 | 58.7957 | 34.9406
1012.2542 | 322.957 | 90.1619 | 200.8025 | 247.6875 | 244.0338 | 58.8514 | 34.976
1013.2542 | 322.7562 | 90.2937 | 201.0325 | 247.084 | 244.2096 | 58.9162 | 35.009
1014.2542 | 322.3352 | 90.4244 | 201.8501 | 246.7497 | 243.8058 | 58.9748 | 35.0676
1015.2542 | 322.6666 | 90.5524 | 202.7438 | 246.8085 | 245.3538 | 59.0365 | 35.1246
1016.2542 | 323.4133 | 90.6771 | 203.4496 | 247.7497 | 245.4704 | 59.0873 | 35.173
1017.2542 | 324.3648 | 90.8137 | 204.2871 | 249.1723 | 245.1215 | 59.1469 | 35.2272
1018.2542 | 325.8572 | 90.9441 | 206.1382 | 249.3198 | 246.575 | 59.2048 | 35.2624
1019.2542 | 327.7349 | 91.0773 | 206.0369 | 248.8448 | 247.8917 | 59.2664 | 35.311
1020.2542 | 328.2586 | 91.1947 | 206.5805 | 248.5075 | 247.8388 | 59.3288 | 35.3573
1021.2542 | 329.4519 | 91.3271 | 207.7025 | 248.3416 | 247.3159 | 59.3816 | 35.4013
1022.2542 | 330.6305 | 91.4593 | 208.5265 | 248.8261 | 247.4025 | 59.4508 | 35.4491
1023.2542 | 331.9195 | 91.5844 | 208.1198 | 249.2262 | 246.7981 | 59.501 | 35.5151
1024.2542 | 332.4789 | 91.7142 | 208.0843 | 249.4472 | 246.9374 | 59.5715 | 35.578
1025.2542 | 333.0505 | 91.8495 | 208.0387 | 249.2228 | 247.5309 | 59.627 | 35.6226
1026.2542 | 332.5609 | 91.9721 | 207.9719 | 249.6424 | 247.6148 | 59.6837 | 35.6508
1027.2542 | 332.3883 | 92.0906 | 207.7035 | 249.7908 | 247.468 | 59.748 | 35.6996
1028.2542 | 333.5706 | 92.2219 | 207.7942 | 250.7662 | 247.5575 | 59.8067 | 35.7432
1029.2542 | 333.0018 | 92.344 | 208.0643 | 250.6397 | 246.7328 | 59.8704 | 35.8007
1030.2542 | 332.9079 | 92.4755 | 207.8373 | 250.7716 | 247.5476 | 59.9304 | 35.8554
1031.2542 | 333.6336 | 92.5947 | 207.9191 | 250.4713 | 247.8421 | 59.9863 | 35.8882
1032.2542 | 334.0892 | 92.7139 | 208.417 | 250.228 | 247.4617 | 60.0494 | 35.9181
1033.2542 | 334.1633 | 92.8344 | 210.7904 | 250.7726 | 247.4154 | 60.1078 | 35.992
1034.2542 | 334.1112 | 92.9617 | 211.0445 | 252.2726 | 248.527 | 60.1658 | 36.0487
1035.2542 | 336.6072 | 93.0875 | 211.2911 | 251.9861 | 247.735 | 60.2259 | 36.0663
1036.2542 | 336.9671 | 93.2069 | 211.2112 | 251.7665 | 247.6913 | 60.285 | 36.1435
1037.2542 | 339.2404 | 93.3304 | 211.2861 | 251.8352 | 247.5417 | 60.3514 | 36.1928
1038.2542 | 340.3262 | 93.4535 | 211.1708 | 252.13 | 247.5033 | 60.4101 | 36.2443
1039.2542 | 341.1331 | 93.5813 | 211.0684 | 252.2631 | 247.4739 | 60.4661 | 36.2826
1040.2542 | 340.4729 | 93.7071 | 211.6207 | 253.2152 | 247.7225 | 60.5208 | 36.3296
1041.2542 | 340.237 | 93.8262 | 212.5281 | 253.5236 | 247.9307 | 60.5828 | 36.3782
1042.2542 | 340.2013 | 93.9455 | 212.4899 | 254.7506 | 248.2932 | 60.6416 | 36.4414
1043.2542 | 339.4885 | 94.0738 | 213.1811 | 254.9637 | 249.4347 | 60.7019 | 36.4967
1044.2542 | 339.9048 | 94.1864 | 212.9547 | 255.0027 | 249.581 | 60.7643 | 36.5499
1045.2542 | 342.2774 | 94.3067 | 213.9741 | 254.3464 | 250.3073 | 60.8298 | 36.5945
1046.2542 | 344.284 | 94.4239 | 214.1732 | 254.4834 | 249.7629 | 60.8943 | 36.6297
1047.2542 | 346.2066 | 94.563 | 213.8412 | 254.2663 | 250.1676 | 60.9606 | 36.6661
1048.2542 | 345.5388 | 94.6916 | 213.6787 | 254.1485 | 250.0498 | 61.0244 | 36.7193
1049.2542 | 345.3634 | 94.8162 | 213.4275 | 253.7218 | 250.1963 | 61.0749 | 36.7825
1050.2542 | 346.5364 | 94.9274 | 213.9427 | 254.0527 | 250.535 | 61.0791 | 36.831
1051.2542 | 345.0496 | 95.0487 | 214.5 | 254.074 | 250.6963 | 61.1475 | 36.8936
1052.2542 | 347.0905 | 95.1667 | 215.8931 | 254.0945 | 250.7787 | 61.2115 | 36.9194
1053.2542 | 348.4337 | 95.2831 | 216.3511 | 255.7505 | 250.9839 | 61.2704 | 36.9605
1054.2542 | 347.1991 | 95.4002 | 216.7783 | 257.0743 | 251.132 | 61.3512 | 37.021
1055.2542 | 346.689 | 95.5258 | 216.5468 | 257.552 | 252.1296 | 61.423 | 37.063
1056.2542 | 347.6562 | 95.6412 | 217.1403 | 258.2509 | 253.1978 | 61.4943 | 37.1132
1057.2542 | 347.3078 | 95.7585 | 217.8261 | 257.9577 | 253.0104 | 61.5528 | 37.172
1058.2542 | 348.7384 | 95.8854 | 217.5473 | 257.7 | 253.3208 | 61.6264 | 37.231
1059.2542 | 348.1471 | 96.0039 | 217.737 | 257.7164 | 253.9431 | 61.6986 | 37.2911
1060.2542 | 349.8231 | 96.1218 | 217.3398 | 257.6886 | 254.0166 | 61.7498 | 37.3283
1061.2542 | 348.4679 | 96.2417 | 217.0535 | 258.0315 | 253.7307 | 61.8263 | 37.3603
1062.2542 | 348.7216 | 96.3687 | 217.7628 | 259.6904 | 253.5524 | 61.9029 | 37.4232
1063.2542 | 349.7798 | 96.4876 | 217.2101 | 261.3203 | 254.6817 | 61.9731 | 37.4747
1064.2542 | 351.3283 | 96.6026 | 216.4839 | 260.6677 | 255.4129 | 62.0534 | 37.5159
1065.2542 | 350.268 | 96.7255 | 216.1247 | 260.5602 | 254.6735 | 62.1268 | 37.566
1066.2542 | 352.414 | 96.8398 | 215.609 | 260.0727 | 255.5003 | 62.2047 | 37.6242
1067.2542 | 352.5284 | 96.9517 | 216.2493 | 260.4475 | 256.8794 | 62.2906 | 37.677
1068.2542 | 352.5269 | 97.0771 | 217.2295 | 260.4746 | 257.2393 | 62.352 | 37.7328
1069.2542 | 351.5629 | 97.2056 | 217.6112 | 260.5446 | 257.4198 | 62.4204 | 37.8026
1070.2542 | 351.2028 | 97.3178 | 217.134 | 259.5653 | 256.3012 | 62.5036 | 37.852
1071.2542 | 353.1511 | 97.4414 | 216.638 | 259.2183 | 255.8487 | 62.5855 | 37.8941
1072.2542 | 353.4909 | 97.5748 | 216.6045 | 258.8841 | 256.4819 | 62.6635 | 37.951
1073.2542 | 354.1763 | 97.7115 | 216.4335 | 258.7272 | 256.3147 | 62.7341 | 38.0015
1074.2542 | 355.5092 | 97.828 | 216.5361 | 258.3911 | 256.2001 | 62.8046 | 38.0337
1075.2542 | 354.8354 | 97.946 | 216.5172 | 259.832 | 256.7995 | 62.8822 | 38.0877
1076.2542 | 354.4586 | 98.0721 | 216.2563 | 261.6906 | 256.8957 | 62.9635 | 38.1491
1077.2542 | 354.4485 | 98.1897 | 216.2678 | 261.4802 | 257.1301 | 63.0394 | 38.2064
1078.2542 | 353.7948 | 98.3146 | 216.0606 | 261.8413 | 256.9236 | 63.1147 | 38.2573
1079.2542 | 354.5943 | 98.437 | 215.9544 | 261.4217 | 257.0567 | 63.2015 | 38.3067
1080.2542 | 353.7147 | 98.554 | 215.3018 | 261.4967 | 257.3615 | 63.2779 | 38.3512
1081.2542 | 355.2058 | 98.6838 | 215.0416 | 261.5383 | 257.5205 | 63.362 | 38.419
1082.2542 | 356.6973 | 98.797 | 216.0211 | 261.9381 | 257.211 | 63.4393 | 38.4796
1083.2542 | 356.4962 | 98.9281 | 215.5478 | 262.2318 | 257.2425 | 63.5238 | 38.5101
1084.2542 | 356.5274 | 99.0579 | 216.2654 | 262.2449 | 258.0403 | 63.5993 | 38.5571
1085.2542 | 358.1474 | 99.1784 | 216.0229 | 262.0801 | 258.3258 | 63.6837 | 38.6125
1086.2542 | 358.4488 | 99.3003 | 215.6735 | 261.882 | 258.2559 | 63.7544 | 38.6673
1087.2542 | 358.297 | 99.4339 | 215.2794 | 261.6853 | 258.4702 | 63.827 | 38.7247
1088.2542 | 355.6779 | 99.5562 | 215.2529 | 261.5271 | 258.3026 | 63.898 | 38.7847
1089.2542 | 355.0397 | 99.6827 | 214.9792 | 261.2766 | 258.2013 | 63.978 | 38.8264
1090.2542 | 354.9313 | 99.8125 | 214.7582 | 261.1102 | 258.3511 | 64.0444 | 38.8831
1091.2542 | 353.6639 | 99.916 | 214.9896 | 260.8172 | 257.5309 | 64.1223 | 38.932
1092.2542 | 355.3563 | 100.0453 | 215.415 | 260.4706 | 257.1539 | 64.1938 | 38.9825
1093.2542 | 354.0822 | 100.1623 | 215.4805 | 260.3217 | 257.042 | 64.2706 | 39.05
1094.2542 | 353.5071 | 100.2757 | 215.189 | 260.3641 | 257.2599 | 64.3454 | 39.0954
1095.2542 | 353.5847 | 100.4107 | 214.9185 | 261.1516 | 257.1416 | 64.4273 | 39.1341
1096.2542 | 354.1114 | 100.5465 | 215.2455 | 262.4096 | 257.354 | 64.4943 | 39.1714
1097.2542 | 352.8241 | 100.6628 | 215.3254 | 262.075 | 257.0856 | 64.5759 | 39.2345
1098.2542 | 350.87 | 100.7791 | 215.5795 | 261.3719 | 257.2002 | 64.6457 | 39.2833
1099.2542 | 351.0613 | 100.9063 | 215.843 | 260.9218 | 256.4406 | 64.7267 | 39.335
1100.2542 | 350.8094 | 101.0234 | 215.5626 | 261.7022 | 256.2779 | 64.8036 | 39.4027
1101.2542 | 353.058 | 101.1528 | 216.0237 | 261.4755 | 255.9233 | 64.8828 | 39.4516
1102.2542 | 354.2178 | 101.2802 | 215.8875 | 260.8444 | 255.527 | 64.9674 | 39.5136
1103.2542 | 354.7275 | 101.4124 | 216.3951 | 261.4372 | 255.3652 | 65.0438 | 39.5532
1104.2542 | 355.9267 | 101.5348 | 216.9327 | 261.5209 | 255.4732 | 65.1231 | 39.609
1105.2542 | 356.6675 | 101.6572 | 217.1596 | 261.0671 | 255.2713 | 65.2041 | 39.6629
1106.2542 | 356.5191 | 101.7846 | 217.3827 | 261.6376 | 255.4461 | 65.2649 | 39.7211
1107.2542 | 354.7269 | 101.8953 | 217.3494 | 262.1603 | 255.6096 | 65.3408 | 39.7602
1108.2542 | 353.5822 | 102.017 | 216.7733 | 262.0961 | 255.144 | 65.4032 | 39.8206
1109.2542 | 353.7264 | 102.1334 | 217.0824 | 262.0644 | 255.4718 | 65.4815 | 39.877
1110.2542 | 352.8153 | 102.26 | 217.1165 | 262.4224 | 255.5487 | 65.5546 | 39.9268
1111.2542 | 352.7028 | 102.3766 | 217.7089 | 262.9085 | 255.4619 | 65.6247 | 39.9918
1112.2542 | 351.4111 | 102.4905 | 217.9288 | 263.1752 | 255.9474 | 65.6978 | 40.0215
1113.2542 | 352.8556 | 102.6145 | 217.8209 | 263.429 | 257.1582 | 65.7666 | 40.0993
1114.2542 | 353.1327 | 102.7377 | 217.9036 | 264.0772 | 257.0289 | 65.8451 | 40.1403
1115.2542 | 354.5065 | 102.8665 | 217.5266 | 263.8494 | 257.1727 | 65.9146 | 40.1939
1116.2542 | 355.499 | 102.9737 | 217.8026 | 264.6973 | 257.3174 | 65.9825 | 40.2482
1117.2542 | 356.4762 | 103.0701 | 217.0079 | 264.9155 | 257.3776 | 66.0476 | 40.2995
1118.2542 | 358.1461 | 103.1824 | 217.76 | 265.6008 | 257.6254 | 66.121 | 40.355
1119.2542 | 359.0804 | 103.3105 | 218.3658 | 266.2786 | 258.598 | 66.1908 | 40.3935
1120.2542 | 361.9013 | 103.4374 | 218.7679 | 266.5254 | 258.2819 | 66.2529 | 40.456
1121.2542 | 362.542 | 103.5642 | 219.2904 | 266.6442 | 258.971 | 66.3256 | 40.521
1122.2542 | 363.6626 | 103.6871 | 219.7003 | 266.5531 | 259.7047 | 66.4006 | 40.5944
1123.2542 | 365.2474 | 103.8088 | 219.9678 | 266.7356 | 259.2456 | 66.4819 | 40.6408
1124.2542 | 365.5955 | 103.9301 | 219.963 | 267.0257 | 259.3332 | 66.5503 | 40.6849
1125.2542 | 365.2853 | 104.0519 | 220.4351 | 266.8231 | 259.4953 | 66.6216 | 40.7314
1126.2542 | 363.8036 | 104.1809 | 220.9606 | 267.5994 | 259.1557 | 66.6923 | 40.7724
1127.2542 | 363.7979 | 104.3135 | 222.0455 | 268.2234 | 259.9038 | 66.7702 | 40.8395
1128.2542 | 364.4778 | 104.4351 | 221.9305 | 268.7054 | 259.7789 | 66.8348 | 40.8677
1129.2542 | 364.3761 | 104.5476 | 221.687 | 268.594 | 260.3238 | 66.9103 | 40.9414
1130.2542 | 363.5263 | 104.6874 | 221.5341 | 268.5274 | 260.0501 | 66.9807 | 40.9981
1131.2542 | 362.1729 | 104.8069 | 221.4084 | 268.9651 | 260.5451 | 67.0516 | 41.0466
1132.2542 | 361.8552 | 104.932 | 221.7906 | 269.1791 | 260.5017 | 67.1208 | 41.1078
1133.2542 | 361.1619 | 105.0577 | 221.9339 | 269.0818 | 260.5784 | 67.1992 | 41.1696
1134.2542 | 362.4578 | 105.1693 | 221.7891 | 269.1839 | 261.2691 | 67.2562 | 41.2259
1135.2542 | 362.8668 | 105.3081 | 222.4139 | 269.3547 | 261.3128 | 67.3404 | 41.2888
1136.2542 | 363.0418 | 105.4316 | 222.4688 | 269.2131 | 261.3639 | 67.4107 | 41.3268
1137.2542 | 364.2632 | 105.5656 | 222.2191 | 268.6746 | 261.199 | 67.4798 | 41.3685
1138.2542 | 363.7442 | 105.6897 | 221.541 | 268.3503 | 261.6153 | 67.5579 | 41.4387
1139.2542 | 362.9077 | 105.8121 | 221.5377 | 269.1174 | 261.3602 | 67.6315 | 41.4876
1140.2542 | 362.3907 | 105.9444 | 221.6843 | 269.5534 | 261.0984 | 67.7152 | 41.546
1141.2542 | 362.95 | 106.0596 | 221.701 | 270.5004 | 261.6274 | 67.7879 | 41.5946
1142.2542 | 363.418 | 106.1877 | 221.5517 | 270.966 | 262.5693 | 67.8688 | 41.6607
1143.2542 | 362.6033 | 106.3004 | 221.7588 | 271.5675 | 262.538 | 67.9548 | 41.703
1144.2542 | 361.7235 | 106.425 | 221.3302 | 271.1623 | 262.3496 | 68.0292 | 41.7559
1145.2542 | 361.8185 | 106.5513 | 221.4431 | 271.4366 | 263.5293 | 68.1033 | 41.8204
1146.2542 | 362.2288 | 106.667 | 221.9907 | 271.5135 | 263.6718 | 68.1758 | 41.8616
1147.2542 | 364.8971 | 106.7899 | 222.3092 | 271.3218 | 263.1257 | 68.2558 | 41.9367
1148.2542 | 365.7044 | 106.9039 | 222.3457 | 271.0451 | 264.6335 | 68.335 | 41.985
1149.2542 | 367.856 | 107.0256 | 222.4222 | 271.7404 | 264.1621 | 68.4078 | 42.0493
1150.2542 | 368.5511 | 107.1457 | 222.5996 | 271.4734 | 265.0636 | 68.4808 | 42.1068
1151.2542 | 367.684 | 107.2587 | 222.9701 | 271.8585 | 266.5444 | 68.5622 | 42.1538
1152.2542 | 368.749 | 107.3848 | 223.4431 | 272.574 | 265.7592 | 68.6309 | 42.2179
1153.2542 | 370.6804 | 107.5038 | 223.5024 | 272.6528 | 265.5787 | 68.7045 | 42.2851
1154.2542 | 369.2933 | 107.6306 | 223.6505 | 273.1268 | 264.8526 | 68.7829 | 42.3421
1155.2542 | 367.3591 | 107.7515 | 223.9998 | 273.2216 | 265.8764 | 68.873 | 42.3935
1156.2542 | 365.7104 | 107.8705 | 223.7852 | 273.3092 | 265.1374 | 68.9498 | 42.4498
1157.2542 | 365.7424 | 108.0065 | 223.7236 | 273.6013 | 265.4517 | 69.0188 | 42.5016
1158.2542 | 365.4348 | 108.1219 | 223.7874 | 274.1844 | 265.4264 | 69.0982 | 42.5712
1159.2542 | 365.072 | 108.2509 | 223.636 | 273.6117 | 265.0739 | 69.1744 | 42.6233
1160.2542 | 365.3923 | 108.368 | 223.8696 | 273.5867 | 264.8012 | 69.2573 | 42.6857
1161.2542 | 366.1328 | 108.4943 | 223.5563 | 273.8018 | 264.5561 | 69.3419 | 42.7344
1162.2542 | 367.0327 | 108.6186 | 224.3662 | 273.5418 | 265.1175 | 69.4154 | 42.7868
1163.2542 | 367.0078 | 108.736 | 224.6352 | 273.5123 | 264.9763 | 69.4949 | 42.8361
1164.2542 | 367.1166 | 108.8584 | 224.6658 | 273.6448 | 265.0284 | 69.5778 | 42.9052
1165.2542 | 367.8529 | 108.9762 | 224.8309 | 274.1116 | 266.3694 | 69.6572 | 42.9655
1166.2542 | 369.3718 | 109.0958 | 225.1506 | 273.695 | 266.044 | 69.7322 | 43.0083
1167.2542 | 368.8113 | 109.2239 | 225.5076 | 273.199 | 265.6962 | 69.808 | 43.0628
1168.2542 | 369.766 | 109.3426 | 225.1279 | 272.79 | 265.1868 | 69.8945 | 43.1168
1169.2542 | 370.4907 | 109.4546 | 225.4966 | 272.416 | 265.5523 | 69.9658 | 43.2005
1170.2542 | 370.6149 | 109.5827 | 226.0952 | 272.7725 | 265.7577 | 70.0436 | 43.2473
1171.2542 | 373.0325 | 109.7016 | 226.3184 | 274.2289 | 265.3235 | 70.1219 | 43.306
1172.2542 | 372.9622 | 109.8217 | 227.1331 | 274.785 | 267.0687 | 70.1911 | 43.3629
1173.2542 | 372.4381 | 109.9519 | 226.9 | 274.5129 | 268.3374 | 70.2759 | 43.4181
1174.2542 | 371.7894 | 110.0706 | 227.0203 | 274.1132 | 268.0504 | 70.3499 | 43.4904
1175.2542 | 371.5474 | 110.1943 | 226.7258 | 274.1551 | 267.3681 | 70.4279 | 43.5483
1176.2542 | 371.3931 | 110.328 | 226.712 | 273.6997 | 267.2996 | 70.504 | 43.5898
1177.2542 | 372.8423 | 110.4599 | 227.4756 | 273.3947 | 267.2874 | 70.5793 | 43.6657
1178.2542 | 373.2015 | 110.5829 | 227.5648 | 273.0212 | 267.143 | 70.6528 | 43.7274
1179.2542 | 373.8303 | 110.7175 | 228.0423 | 273.0832 | 267.0208 | 70.7255 | 43.7692
1180.2542 | 374.8088 | 110.829 | 228.3032 | 273.2212 | 267.3386 | 70.7991 | 43.8225
1181.2542 | 374.6029 | 110.9574 | 228.183 | 273.447 | 267.4571 | 70.8807 | 43.8887
1182.2542 | 374.6519 | 111.0812 | 228.0615 | 273.8257 | 269.4558 | 70.9496 | 43.9439
1183.2542 | 375.1172 | 111.212 | 228.3025 | 273.7465 | 269.4912 | 71.0095 | 43.9934
1184.2542 | 375.5366 | 111.3373 | 228.5316 | 273.5563 | 269.2344 | 71.103 | 44.0661
1185.2542 | 375.7307 | 111.4592 | 228.8064 | 273.3969 | 269.037 | 71.1675 | 44.127
1186.2542 | 375.6435 | 111.5811 | 229.63 | 273.7046 | 268.5264 | 71.2542 | 44.1972
1187.2542 | 376.1867 | 111.7137 | 229.5461 | 273.8599 | 269.188 | 71.3267 | 44.2517
1188.2542 | 378.0291 | 111.8364 | 229.423 | 273.2205 | 269.0245 | 71.4144 | 44.3084
1189.2542 | 376.7988 | 111.9592 | 229.3998 | 272.7197 | 269.0162 | 71.4892 | 44.3762
1190.2542 | 377.83 | 112.0886 | 229.407 | 272.6924 | 269.1933 | 71.5693 | 44.426
1191.2542 | 376.382 | 112.2204 | 228.9442 | 272.9154 | 269.5034 | 71.6522 | 44.4936
1192.2542 | 373.9975 | 112.3389 | 228.7237 | 272.8886 | 269.4716 | 71.7353 | 44.5594
1193.2542 | 373.7071 | 112.4523 | 228.843 | 272.2564 | 268.9566 | 71.8118 | 44.6157
1194.2542 | 374.1099 | 112.5776 | 228.6503 | 272.0005 | 268.7264 | 71.8933 | 44.666
1195.2542 | 374.7661 | 112.7135 | 228.7168 | 271.8809 | 268.8519 | 71.9793 | 44.729
1196.2542 | 374.3203 | 112.8404 | 228.5096 | 271.9732 | 268.5458 | 72.055 | 44.791
1197.2542 | 372.9021 | 112.9608 | 228.3599 | 273.2852 | 268.2058 | 72.1388 | 44.8378
1198.2542 | 373.1385 | 113.0844 | 229.1897 | 273.782 | 267.8179 | 72.2179 | 44.9003
1199.2542 | 372.7391 | 113.2159 | 228.8596 | 273.538 | 267.6578 | 72.2945 | 44.9488
1200.2542 | 372.6624 | 113.3552 | 228.4177 | 273.1576 | 267.6966 | 72.3729 | 45.0073
1201.2542 | 374.2839 | 113.4863 | 228.3558 | 272.6543 | 267.8655 | 72.4527 | 45.0719
1202.2542 | 373.8427 | 113.6102 | 228.5326 | 272.0528 | 267.4826 | 72.5288 | 45.1183
1203.2542 | 373.7551 | 113.7346 | 228.4724 | 271.5629 | 267.3037 | 72.6091 | 45.1702
1204.2542 | 374.0078 | 113.8575 | 229.0066 | 271.3981 | 267.5416 | 72.6857 | 45.2319
1205.2542 | 375.2364 | 113.99 | 228.7981 | 271.099 | 267.6559 | 72.7554 | 45.3043
1206.2542 | 375.9274 | 114.1356 | 228.7646 | 271.9393 | 267.5148 | 72.8346 | 45.371
1207.2542 | 374.4496 | 114.2648 | 228.5607 | 272.078 | 267.674 | 72.9183 | 45.4307
1208.2542 | 373.3689 | 114.3909 | 228.0754 | 272.0292 | 268.1143 | 72.9948 | 45.4935
1209.2542 | 373.7502 | 114.5144 | 228.6972 | 273.2913 | 268.4685 | 73.0745 | 45.5566
1210.2542 | 373.1963 | 114.6482 | 228.495 | 273.5156 | 268.1536 | 73.1521 | 45.6215
1211.2542 | 372.5636 | 114.777 | 228.7636 | 273.5667 | 267.5494 | 73.2413 | 45.6701
1212.2542 | 370.7231 | 114.9 | 228.8934 | 273.9687 | 267.5027 | 73.3191 | 45.7266
1213.2542 | 370.1543 | 115.0257 | 228.8289 | 273.9834 | 267.369 | 73.4049 | 45.7893
1214.2542 | 368.7189 | 115.1512 | 228.6627 | 273.7904 | 266.7491 | 73.4873 | 45.8361
1215.2542 | 367.3348 | 115.2732 | 228.9209 | 273.4746 | 266.9957 | 73.5734 | 45.8954
1216.2542 | 368.5846 | 115.4133 | 228.4186 | 273.0364 | 266.5941 | 73.6434 | 45.9565
1217.2542 | 369.812 | 115.5384 | 229.0904 | 273.2011 | 266.5543 | 73.727 | 46.0344
1218.2542 | 372.46 | 115.6606 | 230.3969 | 273.2667 | 267.9182 | 73.8018 | 46.0751
1219.2542 | 374.2228 | 115.8002 | 230.5672 | 273.5408 | 267.4383 | 73.8874 | 46.1387
1220.2542 | 374.9556 | 115.9426 | 230.7931 | 274.3727 | 268.2648 | 73.9706 | 46.2085
1221.2542 | 376.3256 | 116.07 | 230.946 | 274.3726 | 268.697 | 74.0479 | 46.2612
1222.2542 | 377.2271 | 116.1982 | 230.7727 | 273.9887 | 269.8568 | 74.1318 | 46.3384
1223.2542 | 377.7196 | 116.3341 | 231.5949 | 273.6846 | 269.4287 | 74.2144 | 46.3972
1224.2542 | 378.9553 | 116.4732 | 231.1612 | 273.2483 | 269.1704 | 74.295 | 46.4571
1225.2542 | 381.4729 | 116.6146 | 231.1186 | 273.2739 | 268.3587 | 74.3758 | 46.5087
1226.2542 | 382.3853 | 116.7562 | 231.3265 | 273.0851 | 267.6957 | 74.4611 | 46.5709
1227.2542 | 381.0318 | 116.8895 | 231.786 | 272.6788 | 267.9572 | 74.5557 | 46.6283
1228.2542 | 381.6277 | 117.0369 | 231.6038 | 273.1014 | 268.3906 | 74.638 | 46.69
1229.2542 | 382.4918 | 117.1847 | 231.8392 | 273.6248 | 268.3799 | 74.7219 | 46.7563
1230.2542 | 382.4196 | 117.3214 | 231.8211 | 274.3943 | 269.2954 | 74.8104 | 46.8261
1231.2542 | 382.491 | 117.4711 | 231.5627 | 274.458 | 269.4278 | 74.8927 | 46.8975
1232.2542 | 384.2184 | 117.6165 | 231.3869 | 274.5774 | 269.3148 | 74.9712 | 46.9567
1233.2542 | 385.1779 | 117.7604 | 232.2216 | 276.123 | 269.8116 | 75.052 | 47.0011
1234.2542 | 385.1852 | 117.9176 | 231.8366 | 275.9257 | 270.0737 | 75.1424 | 47.0591
1235.2542 | 387.0267 | 118.0484 | 231.5335 | 276.4364 | 270.342 | 75.2156 | 47.1313
1236.2542 | 385.6747 | 118.2008 | 231.7453 | 276.6556 | 270.3789 | 75.3036 | 47.1929
1237.2542 | 385.9794 | 118.3433 | 231.6375 | 276.8427 | 270.0243 | 75.3897 | 47.2534
1238.2542 | 387.1618 | 118.489 | 231.2603 | 276.3739 | 269.5412 | 75.4714 | 47.3197
1239.2542 | 386.9448 | 118.6291 | 231.8419 | 276.0422 | 270.2722 | 75.5547 | 47.3823
1240.2542 | 386.222 | 118.7884 | 231.7773 | 275.8398 | 270.4274 | 75.6336 | 47.4575
1241.2542 | 387.2559 | 118.9267 | 231.9905 | 276.0882 | 270.9855 | 75.7179 | 47.5098
1242.2542 | 385.9787 | 119.0609 | 232.6089 | 277.195 | 271.2974 | 75.8068 | 47.5776
1243.2542 | 386.7487 | 119.2063 | 232.9428 | 279.2368 | 270.8237 | 75.8881 | 47.6388
1244.2542 | 387.7784 | 119.3533 | 232.8862 | 279.0027 | 271.1399 | 75.9712 | 47.6891
1245.2542 | 388.1169 | 119.491 | 232.6031 | 278.7732 | 271.0901 | 76.0534 | 47.7467
1246.2542 | 388.0229 | 119.6403 | 233.794 | 278.4804 | 271.4196 | 76.1344 | 47.842
1247.2542 | 385.8113 | 119.7801 | 234.2022 | 278.5241 | 272.0626 | 76.2317 | 47.8931
1248.2542 | 384.859 | 119.9252 | 234.3636 | 278.6067 | 271.677 | 76.3092 | 47.945
1249.2542 | 384.5528 | 120.0737 | 234.3899 | 278.7351 | 272.1694 | 76.3938 | 48.0066
1250.2542 | 383.0881 | 120.2223 | 234.1003 | 279.4168 | 271.7372 | 76.4726 | 48.0777
1251.2542 | 383.4813 | 120.3647 | 233.7127 | 280.657 | 271.5206 | 76.5668 | 48.1313
1252.2542 | 384.0749 | 120.5088 | 233.765 | 280.6473 | 272.1063 | 76.654 | 48.1961
1253.2542 | 383.5201 | 120.6577 | 234.2697 | 280.4339 | 272.9183 | 76.736 | 48.2657
1254.2542 | 382.1579 | 120.8071 | 233.8603 | 280.1721 | 272.9998 | 76.8243 | 48.3209
1255.2542 | 382.4696 | 120.9494 | 233.7554 | 281.3072 | 272.2762 | 76.9141 | 48.3764
1256.2542 | 384.0692 | 121.1023 | 233.5374 | 280.523 | 272.5849 | 76.998 | 48.4563
1257.2542 | 382.8092 | 121.2481 | 234.2967 | 280.0579 | 272.7566 | 77.0793 | 48.5294
1258.2542 | 382.096 | 121.3971 | 235.3343 | 279.7405 | 273.0696 | 77.161 | 48.5823
1259.2542 | 384.7213 | 121.5431 | 235.1999 | 279.6785 | 272.3383 | 77.2489 | 48.6382
1260.2542 | 384.6287 | 121.6921 | 234.5897 | 279.6973 | 272.4703 | 77.3492 | 48.7174
1261.2542 | 385.2615 | 121.8349 | 234.2355 | 280.2584 | 272.4078 | 77.4246 | 48.773
1262.2542 | 383.2473 | 121.9851 | 234.5463 | 280.7818 | 272.0492 | 77.5003 | 48.8261
1263.2542 | 384.4965 | 122.1286 | 235.2028 | 280.631 | 271.7636 | 77.5866 | 48.8961
1264.2542 | 382.2815 | 122.2708 | 235.336 | 280.0228 | 271.5744 | 77.6625 | 48.9757
1265.2542 | 380.9899 | 122.4163 | 235.1512 | 279.0939 | 271.4385 | 77.75 | 49.0333
1266.2542 | 380.9317 | 122.5652 | 235.4776 | 278.9757 | 272.3228 | 77.8256 | 49.0807
1267.2542 | 381.4573 | 122.7132 | 235.3407 | 278.7643 | 272.2124 | 77.9122 | 49.1627
1268.2542 | 381.6556 | 122.8609 | 235.954 | 278.4895 | 272.4608 | 77.9895 | 49.2302
1269.2542 | 381.9765 | 123.0011 | 236.6199 | 278.4307 | 272.8047 | 78.0709 | 49.3024
1270.2542 | 384.5249 | 123.1473 | 236.2747 | 278.5023 | 272.5094 | 78.1536 | 49.3629
1271.2542 | 383.9232 | 123.2944 | 237.018 | 278.8711 | 273.0702 | 78.2387 | 49.4343
1272.2542 | 384.8475 | 123.4359 | 237.1492 | 278.8683 | 273.1387 | 78.3118 | 49.5018
1273.2542 | 385.1521 | 123.5831 | 237.2313 | 278.6969 | 273.5735 | 78.3985 | 49.5541
1274.2542 | 388.565 | 123.7285 | 236.6526 | 278.2718 | 273.4172 | 78.4725 | 49.6385
1275.2542 | 388.7467 | 123.8733 | 236.7599 | 278.8252 | 273.5021 | 78.5615 | 49.7045
1276.2542 | 388.4121 | 124.0141 | 236.3849 | 279.1528 | 273.9664 | 78.6468 | 49.7725
1277.2542 | 387.5592 | 124.1738 | 236.4417 | 279.4238 | 273.8041 | 78.7235 | 49.8351
1278.2542 | 387.1441 | 124.3077 | 236.5565 | 279.3196 | 273.483 | 78.8125 | 49.9119
1279.2542 | 386.9447 | 124.4632 | 236.946 | 280.1466 | 274.7048 | 78.9023 | 49.9732
1280.2542 | 387.5958 | 124.6133 | 237.3216 | 280.507 | 274.5285 | 78.9782 | 50.0491
1281.2542 | 387.2864 | 124.7647 | 237.1226 | 280.0689 | 274.8377 | 79.0613 | 50.103
1282.2542 | 387.1025 | 124.9072 | 237.2215 | 280.4973 | 274.8053 | 79.1535 | 50.1776
1283.2542 | 387.558 | 125.0647 | 237.67 | 280.7394 | 274.474 | 79.2318 | 50.2516
1284.2542 | 389.1646 | 125.2008 | 237.6092 | 280.9635 | 276.692 | 79.3072 | 50.318
1285.2542 | 389.9943 | 125.3644 | 237.8643 | 281.2894 | 276.2371 | 79.3914 | 50.3974
1286.2542 | 390.2476 | 125.51 | 237.8818 | 281.2027 | 276.7653 | 79.4766 | 50.4541
1287.2542 | 390.1777 | 125.6588 | 238.161 | 281.6629 | 277.1226 | 79.5593 | 50.5163
1288.2542 | 389.6344 | 125.8104 | 238.3202 | 281.4875 | 277.8128 | 79.646 | 50.5831
1289.2542 | 386.7546 | 125.9575 | 238.4738 | 283.4486 | 278.5386 | 79.7289 | 50.657
1290.2542 | 384.5951 | 126.1151 | 239.3679 | 283.5188 | 278.8217 | 79.8218 | 50.7191
1291.2542 | 384.2753 | 126.2684 | 239.0221 | 283.2093 | 279.2228 | 79.9004 | 50.7877
1292.2542 | 383.6711 | 126.4201 | 238.2197 | 282.9121 | 279.0192 | 79.983 | 50.8446
1293.2542 | 387.1648 | 126.5807 | 237.6655 | 282.7293 | 278.5349 | 80.0706 | 50.9425
1294.2542 | 387.305 | 126.7315 | 238.1754 | 282.2151 | 278.4168 | 80.1607 | 51.0126
1295.2542 | 388.2105 | 126.8824 | 237.8838 | 282.7026 | 278.622 | 80.247 | 51.0691
1296.2542 | 387.2289 | 127.0323 | 238.475 | 283.1648 | 278.0371 | 80.3434 | 51.1521
1297.2542 | 385.0725 | 127.1853 | 238.3827 | 283.1406 | 277.8509 | 80.4361 | 51.2134
1298.2542 | 385.8909 | 127.3435 | 238.5917 | 283.2531 | 277.4843 | 80.5169 | 51.299
1299.2542 | 384.3256 | 127.4998 | 238.2547 | 283.8024 | 277.4392 | 80.6085 | 51.3737
1300.2542 | 384.6624 | 127.6546 | 238.3526 | 283.7286 | 277.231 | 80.6949 | 51.4442
1301.2542 | 383.2695 | 127.829 | 238.2511 | 283.6382 | 277.6033 | 80.7806 | 51.4834
1302.2542 | 382.0098 | 127.9781 | 238.1767 | 283.6824 | 277.097 | 80.8746 | 51.5555
1303.2542 | 381.6417 | 128.1386 | 237.8053 | 283.0187 | 276.86 | 80.954 | 51.6315
1304.2542 | 381.8069 | 128.2872 | 237.6439 | 283.2099 | 277.4607 | 81.0426 | 51.7164
1305.2542 | 380.1811 | 128.4579 | 237.0732 | 283.3107 | 277.3336 | 81.1193 | 51.784
1306.2542 | 378.4134 | 128.6165 | 236.6398 | 282.9819 | 277.3119 | 81.2024 | 51.8592
1307.2542 | 376.8582 | 128.776 | 235.9691 | 283.4732 | 277.5339 | 81.2764 | 51.9268
1308.2542 | 376.3783 | 128.9249 | 236.0619 | 284.1549 | 277.8231 | 81.3617 | 51.9931
1309.2542 | 375.9819 | 129.0751 | 235.7862 | 283.6821 | 277.1637 | 81.4437 | 52.0808
1310.2542 | 375.2328 | 129.2322 | 235.748 | 283.2739 | 277.3922 | 81.5284 | 52.152
1311.2542 | 375.3981 | 129.3907 | 236.07 | 283.5536 | 277.1184 | 81.6211 | 52.2187
1312.2542 | 374.1713 | 129.539 | 236.173 | 284.1197 | 277.297 | 81.7012 | 52.2922
1313.2542 | 375.0803 | 129.6923 | 236.0637 | 284.1342 | 276.9191 | 81.7755 | 52.3453
1314.2542 | 374.9464 | 129.8477 | 236.2385 | 284.2038 | 277.1157 | 81.8474 | 52.433
1315.2542 | 374.1803 | 129.9978 | 236.2881 | 285.0388 | 276.8845 | 81.9229 | 52.5087
1316.2542 | 373.3309 | 130.1567 | 236.7169 | 285.8597 | 276.9358 | 82 | 52.584
1317.2542 | 372.9274 | 130.3073 | 236.4831 | 285.5469 | 277.1929 | 82.0814 | 52.6535
1318.2542 | 373.3788 | 130.4628 | 237.1026 | 285.0537 | 277.2751 | 82.1504 | 52.7193
1319.2542 | 373.0589 | 130.6171 | 236.8426 | 284.8282 | 276.9613 | 82.2265 | 52.7839
1320.2542 | 373.8658 | 130.779 | 237.0472 | 284.9695 | 277.179 | 82.2921 | 52.8598
1321.2542 | 373.9657 | 130.9238 | 237.0435 | 285.136 | 276.9915 | 82.3676 | 52.9496
1322.2542 | 373.6277 | 131.0745 | 237.0147 | 285.1032 | 277.3869 | 82.4366 | 53.0399
1323.2542 | 372.7197 | 131.2292 | 237.3646 | 285.0135 | 277.0539 | 82.518 | 53.1246
1324.2542 | 373.2013 | 131.3798 | 237.4935 | 285.0489 | 277.79 | 82.5854 | 53.1974
1325.2542 | 373.0781 | 131.5364 | 237.6334 | 285.063 | 278.9143 | 82.6641 | 53.2821
1326.2542 | 373.5644 | 131.695 | 237.8591 | 284.7674 | 278.8303 | 82.7404 | 53.3471
1327.2542 | 374.3435 | 131.8511 | 237.8737 | 285.621 | 278.5977 | 82.8073 | 53.4307
1328.2542 | 374.5714 | 132.0029 | 237.858 | 285.0157 | 278.656 | 82.8795 | 53.5044
1329.2542 | 374.7562 | 132.1588 | 238.1096 | 285.4907 | 278.5058 | 82.9535 | 53.5812
1330.2542 | 375.5156 | 132.3182 | 237.8945 | 285.9776 | 278.1381 | 83.0275 | 53.6459
1331.2542 | 375.2214 | 132.4735 | 237.6447 | 286.0626 | 278.2938 | 83.1015 | 53.7134
1332.2542 | 373.7105 | 132.6213 | 237.7018 | 284.9968 | 277.977 | 83.1761 | 53.793
1333.2542 | 373.2511 | 132.7796 | 237.926 | 284.3376 | 278.2741 | 83.2416 | 53.8702
1334.2542 | 373.0192 | 132.9446 | 237.9488 | 284.0542 | 278.329 | 83.3149 | 53.9428
1335.2542 | 375.4199 | 133.0848 | 238.0311 | 283.388 | 277.9071 | 83.3938 | 54.0288
1336.2542 | 375.8281 | 133.2439 | 237.7028 | 283.0473 | 277.8705 | 83.4656 | 54.086
1337.2542 | 374.1928 | 133.3954 | 237.9233 | 283.2205 | 278.1757 | 83.5476 | 54.1556
1338.2542 | 373.4375 | 133.5545 | 237.6693 | 282.6375 | 277.6642 | 83.6178 | 54.2522
1339.2542 | 374.7602 | 133.7072 | 237.6773 | 282.4732 | 277.6646 | 83.701 | 54.3209
1340.2542 | 373.704 | 133.8616 | 238.5613 | 282.7044 | 278.0184 | 83.7772 | 54.3945
1341.2542 | 371.8838 | 134.0199 | 238.2052 | 282.6783 | 278.1729 | 83.8512 | 54.4532
1342.2542 | 369.9621 | 134.1802 | 238.618 | 282.0887 | 277.7528 | 83.9307 | 54.5156
1343.2542 | 369.7073 | 134.3233 | 238.7229 | 281.716 | 276.8815 | 83.9988 | 54.5964
1344.2542 | 370.8703 | 134.4885 | 238.8216 | 281.3481 | 276.9239 | 84.079 | 54.6649
1345.2542 | 372.5679 | 134.633 | 238.0716 | 281.5714 | 278.3648 | 84.1492 | 54.743
1346.2542 | 373.0908 | 134.7934 | 238.5743 | 282.1075 | 277.8195 | 84.2343 | 54.8168
1347.2542 | 374.5758 | 134.95 | 237.9037 | 281.8589 | 277.1944 | 84.3122 | 54.8937
1348.2542 | 375.0925 | 135.1091 | 237.6642 | 281.4403 | 277.8745 | 84.3896 | 54.9625
1349.2542 | 375.4966 | 135.26 | 237.1355 | 281.1372 | 277.9419 | 84.4696 | 55.0558
1350.2542 | 372.8652 | 135.4252 | 237.195 | 281.4194 | 277.2833 | 84.5332 | 55.1346
1351.2542 | 373.0766 | 135.5665 | 237.1804 | 281.471 | 276.9868 | 84.6142 | 55.2141
1352.2542 | 371.4567 | 135.7243 | 237.6932 | 281.3963 | 277.1919 | 84.685 | 55.2786
1353.2542 | 370.9018 | 135.8875 | 237.698 | 281.4304 | 278.1601 | 84.7604 | 55.361
1354.2542 | 370.1913 | 136.0304 | 237.8608 | 281.449 | 278.8348 | 84.8432 | 55.4558
1355.2542 | 371.0005 | 136.1983 | 238.0411 | 281.4469 | 278.4216 | 84.9217 | 55.5191
1356.2542 | 369.8904 | 136.3499 | 238.1505 | 281.3302 | 278.2306 | 84.9893 | 55.597
1357.2542 | 368.7257 | 136.5131 | 238.0384 | 281.2997 | 278.0075 | 85.0801 | 55.6722
1358.2542 | 368.3962 | 136.6728 | 239.1226 | 281.0281 | 277.0655 | 85.1502 | 55.7359
1359.2542 | 368.4209 | 136.8307 | 238.8283 | 280.7687 | 277.0219 | 85.2371 | 55.8082
1360.2542 | 369.1457 | 136.9808 | 239.0103 | 281.3007 | 276.5001 | 85.3079 | 55.8642
1361.2542 | 371.2969 | 137.1359 | 239.1202 | 281.3657 | 276.6273 | 85.3895 | 55.947
1362.2542 | 369.9364 | 137.2928 | 239.4939 | 281.5188 | 276.8375 | 85.4605 | 56.0259
1363.2542 | 370.4361 | 137.4444 | 239.4293 | 281.4079 | 276.5393 | 85.5273 | 56.1019
1364.2542 | 370.3395 | 137.6056 | 239.7393 | 281.3665 | 276.6755 | 85.6099 | 56.1773
1365.2542 | 371.4316 | 137.7552 | 239.6148 | 281.3525 | 276.9047 | 85.6931 | 56.241
1366.2542 | 372.5757 | 137.9007 | 239.8216 | 282.5727 | 276.9102 | 85.7658 | 56.3225
1367.2542 | 371.7525 | 138.0747 | 239.6641 | 282.7825 | 276.8463 | 85.848 | 56.4069
1368.2542 | 371.9163 | 138.23 | 239.6618 | 282.9848 | 277.0507 | 85.9209 | 56.4809
1369.2542 | 371.3515 | 138.3879 | 239.8549 | 283.9832 | 276.7763 | 85.999 | 56.5514
1370.2542 | 369.7385 | 138.5404 | 240.6989 | 283.8522 | 276.8322 | 86.081 | 56.6337
1371.2542 | 368.9196 | 138.6924 | 240.908 | 283.3155 | 277.3006 | 86.1569 | 56.7083
1372.2542 | 367.4328 | 138.8521 | 241.05 | 282.6193 | 276.9087 | 86.2232 | 56.7956
1373.2542 | 365.5037 | 139.0032 | 241.0346 | 283.1768 | 277.6778 | 86.2985 | 56.8606
1374.2542 | 364.1668 | 139.163 | 241.0313 | 283.5213 | 277.504 | 86.3853 | 56.935
1375.2542 | 362.5105 | 139.3161 | 241.4756 | 283.5223 | 277.0202 | 86.4589 | 57.012
1376.2542 | 362.0684 | 139.4687 | 241.7601 | 283.6758 | 277.1337 | 86.5319 | 57.0802
1377.2542 | 362.5423 | 139.6224 | 241.627 | 283.5774 | 276.4487 | 86.6157 | 57.1522
1378.2542 | 363.5625 | 139.7746 | 242.1939 | 283.4039 | 276.2471 | 86.693 | 57.2116
1379.2542 | 363.685 | 139.9423 | 242.0725 | 284.0174 | 276.0586 | 86.775 | 57.2709
1380.2542 | 363.8141 | 140.0944 | 242.0076 | 283.7117 | 276.0568 | 86.8466 | 57.3646
1381.2542 | 363.4884 | 140.2512 | 242.2096 | 283.6707 | 276.3694 | 86.9283 | 57.4398
1382.2542 | 363.563 | 140.4035 | 242.8045 | 283.8307 | 277.6027 | 87.0028 | 57.5146
1383.2542 | 363.7968 | 140.5559 | 242.5549 | 283.6856 | 277.5715 | 87.0782 | 57.5865
1384.2542 | 365.0335 | 140.712 | 242.6151 | 284.1169 | 277.8399 | 87.1571 | 57.655
1385.2542 | 365.9605 | 140.8628 | 242.6829 | 284.3643 | 277.7321 | 87.2343 | 57.7441
1386.2542 | 366.5268 | 141.0235 | 242.3497 | 285.3394 | 277.8205 | 87.3177 | 57.8215
1387.2542 | 366.6503 | 141.1774 | 242.2241 | 285.429 | 277.9051 | 87.3906 | 57.8921
1388.2542 | 367.8494 | 141.3373 | 241.9795 | 285.2984 | 278.0089 | 87.4606 | 57.9489
1389.2542 | 368.8396 | 141.4858 | 242.1667 | 285.0379 | 278.1857 | 87.5416 | 58.0465
1390.2542 | 371.3693 | 141.6362 | 241.6169 | 285.0699 | 278.1052 | 87.6132 | 58.1171
1391.2542 | 372.759 | 141.8 | 242.112 | 284.7268 | 277.8788 | 87.6954 | 58.188
1392.2542 | 374.8744 | 141.9583 | 242.2226 | 285.2777 | 277.9791 | 87.7646 | 58.2751
1393.2542 | 374.8367 | 142.1191 | 242.1914 | 285.2167 | 277.8315 | 87.8366 | 58.3412
1394.2542 | 374.9177 | 142.2811 | 242.2343 | 286.4034 | 277.8662 | 87.9159 | 58.4246
1395.2542 | 376.5306 | 142.4253 | 242.1357 | 286.3297 | 277.432 | 87.9934 | 58.4922
1396.2542 | 376.1111 | 142.5848 | 242.3557 | 286.7273 | 277.4219 | 88.0514 | 58.5517
1397.2542 | 376.0717 | 142.7438 | 242.7025 | 287.6962 | 277.9915 | 88.1397 | 58.6452
1398.2542 | 376.8188 | 142.8922 | 243.1079 | 287.6966 | 278.2713 | 88.2053 | 58.7392
1399.2542 | 375.7015 | 143.0562 | 243.875 | 288.7522 | 278.6653 | 88.2885 | 58.8081
1400.2542 | 376.053 | 143.2102 | 244.4061 | 288.4694 | 278.2962 | 88.3654 | 58.8732
1401.2542 | 378.4996 | 143.3679 | 244.6554 | 288.704 | 279.1171 | 88.4508 | 58.9457
1402.2542 | 378.8851 | 143.5213 | 244.5551 | 288.4947 | 279.5776 | 88.5253 | 59.027
1403.2542 | 381.778 | 143.6673 | 244.736 | 288.7453 | 278.8256 | 88.6002 | 59.1085
1404.2542 | 383.636 | 143.8205 | 245.0552 | 288.5701 | 279.4427 | 88.6834 | 59.1805
1405.2542 | 384.67 | 143.975 | 245.0226 | 288.6434 | 279.607 | 88.7676 | 59.2698
1406.2542 | 385.4798 | 144.1398 | 245.6621 | 288.637 | 279.1665 | 88.8423 | 59.3353
1407.2542 | 386.4234 | 144.2982 | 245.054 | 288.5156 | 279.8585 | 88.9214 | 59.3942
1408.2542 | 385.5371 | 144.4559 | 245.0125 | 289.096 | 280.6064 | 89.0099 | 59.4721
1409.2542 | 386.0516 | 144.6133 | 245.5041 | 288.791 | 280.2757 | 89.0901 | 59.5333
1410.2542 | 384.4022 | 144.769 | 244.9192 | 288.7074 | 280.7562 | 89.1707 | 59.6253
1411.2542 | 384.0384 | 144.9292 | 245.4113 | 288.6689 | 281.5259 | 89.2448 | 59.7025
1412.2542 | 383.5503 | 145.0792 | 244.9186 | 288.3672 | 280.8409 | 89.3297 | 59.7836
1413.2542 | 384.0688 | 145.2393 | 245.3426 | 288.1105 | 281.871 | 89.4075 | 59.8798
1414.2542 | 384.1652 | 145.3972 | 245.205 | 288.4354 | 281.4241 | 89.4834 | 59.9466
1415.2542 | 384.033 | 145.5522 | 245.2034 | 288.8967 | 280.7434 | 89.5622 | 60.0048
1416.2542 | 383.1824 | 145.7099 | 245.3449 | 289.0469 | 280.726 | 89.6524 | 60.0797
1417.2542 | 381.982 | 145.8664 | 245.8778 | 289.6699 | 280.8677 | 89.7273 | 60.1402
1418.2542 | 383.4951 | 146.0298 | 246.3554 | 289.3238 | 280.8558 | 89.8039 | 60.2246
1419.2542 | 384.7698 | 146.1801 | 246.1108 | 289.5741 | 280.9151 | 89.8855 | 60.2992
1420.2542 | 385.4334 | 146.3275 | 246.2546 | 290.2257 | 280.5693 | 89.9711 | 60.3853
1421.2542 | 387.3274 | 146.4942 | 246.7134 | 291.6341 | 280.6943 | 90.0549 | 60.4539
1422.2542 | 387.6657 | 146.6388 | 246.8905 | 291.8605 | 280.5164 | 90.1331 | 60.5115
1423.2542 | 387.8382 | 146.8053 | 246.851 | 291.1279 | 280.3202 | 90.2121 | 60.5908
1424.2542 | 387.1252 | 146.9596 | 247.5301 | 290.3426 | 280.7176 | 90.2889 | 60.6571
1425.2542 | 387.384 | 147.1091 | 249.1059 | 290.2143 | 281.2043 | 90.368 | 60.7486
1426.2542 | 388.6783 | 147.2628 | 249.0579 | 290.4646 | 280.8826 | 90.4453 | 60.8351
1427.2542 | 388.0596 | 147.4256 | 249.392 | 290.0571 | 281.4307 | 90.5184 | 60.9095
1428.2542 | 389.0376 | 147.5849 | 249.4424 | 290.2607 | 280.9823 | 90.6025 | 60.9757
1429.2542 | 388.7721 | 147.7423 | 249.4223 | 289.873 | 280.9277 | 90.6832 | 61.0495
1430.2542 | 389.6248 | 147.8961 | 249.953 | 289.2075 | 281.2221 | 90.7613 | 61.1181
1431.2542 | 388.8478 | 148.0528 | 249.5753 | 288.7233 | 281.2368 | 90.8514 | 61.1998
1432.2542 | 388.3404 | 148.2079 | 248.829 | 289.3363 | 281.21 | 90.9404 | 61.2805
1433.2542 | 387.6504 | 148.3602 | 248.0351 | 289.2514 | 281.414 | 91.0281 | 61.3624
1434.2542 | 388.3237 | 148.5216 | 247.7018 | 289.5471 | 281.2003 | 91.1106 | 61.4447
1435.2542 | 388.0242 | 148.6841 | 247.4786 | 289.4057 | 281.0185 | 91.2005 | 61.5075
1436.2542 | 388.4351 | 148.8234 | 247.8228 | 289.2394 | 281.2237 | 91.2765 | 61.5805
1437.2542 | 389.0811 | 148.9956 | 247.7829 | 288.9089 | 280.8425 | 91.3611 | 61.6692
1438.2542 | 389.0528 | 149.1471 | 247.856 | 288.6498 | 281.0513 | 91.4478 | 61.7501
1439.2542 | 390.976 | 149.3019 | 248.2123 | 288.4611 | 280.7343 | 91.5212 | 61.8254
1440.2542 | 390.4383 | 149.4569 | 248.277 | 288.1111 | 280.5709 | 91.6022 | 61.907
1441.2542 | 390.4441 | 149.6149 | 248.3342 | 288.2403 | 281.016 | 91.6846 | 61.9901
1442.2542 | 390.2716 | 149.7666 | 248.6048 | 288.44 | 281.3546 | 91.7583 | 62.058
1443.2542 | 390.4801 | 149.9207 | 248.3778 | 288.6507 | 281.61 | 91.8379 | 62.1396
1444.2542 | 389.1246 | 150.0846 | 248.2945 | 288.2835 | 281.8357 | 91.9246 | 62.2166
1445.2542 | 388.7825 | 150.2403 | 248.0492 | 288.6667 | 281.6437 | 92.0017 | 62.2835
1446.2542 | 389.0052 | 150.3997 | 248.1865 | 288.0217 | 281.5573 | 92.083 | 62.3613
1447.2542 | 388.9734 | 150.5529 | 248.66 | 287.7489 | 280.7081 | 92.1673 | 62.4238
1448.2542 | 387.5053 | 150.711 | 249.2357 | 287.6294 | 281.4127 | 92.2401 | 62.5027
1449.2542 | 385.5291 | 150.8639 | 249.1623 | 287.3185 | 281.6073 | 92.3167 | 62.5695
1450.2542 | 385.8795 | 151.0171 | 248.8514 | 287.262 | 282.1752 | 92.4035 | 62.6526
1451.2542 | 384.3789 | 151.1765 | 248.7932 | 287.1081 | 282.3008 | 92.4809 | 62.704
1452.2542 | 384.373 | 151.3265 | 248.7972 | 287.3087 | 282.3242 | 92.5587 | 62.8083
1453.2542 | 384.697 | 151.4767 | 249.4317 | 287.6091 | 282.3419 | 92.6383 | 62.8775
1454.2542 | 384.623 | 151.6349 | 249.4954 | 287.5642 | 281.6272 | 92.7123 | 62.9762
1455.2542 | 384.6068 | 151.7869 | 249.5873 | 288.3083 | 281.8393 | 92.7907 | 63.0497
1456.2698 | 383.6022 | 151.9519 | 249.5608 | 288.4465 | 282.3091 | 92.8796 | 63.1157
1457.2542 | 384.1346 | 152.1007 | 249.4131 | 288.8272 | 282.5997 | 92.9568 | 63.1864
1458.2542 | 383.6111 | 152.2678 | 249.2441 | 289.4312 | 281.7653 | 93.0289 | 63.26
1459.2542 | 383.5767 | 152.4181 | 249.1401 | 289.6345 | 282.7363 | 93.1029 | 63.3388
1460.2542 | 385.554 | 152.5732 | 249.5598 | 289.8042 | 282.8914 | 93.1839 | 63.4178
1461.2542 | 386.5916 | 152.736 | 249.4546 | 291.1028 | 282.4341 | 93.2538 | 63.4825
1462.2542 | 388.5608 | 152.8997 | 249.4906 | 290.5771 | 282.804 | 93.3422 | 63.5641
1463.2542 | 388.5564 | 153.0486 | 249.9546 | 290.2519 | 282.9494 | 93.4254 | 63.6306
1464.2542 | 387.9652 | 153.2088 | 250.1662 | 290.0139 | 282.7414 | 93.5049 | 63.7121
1465.2542 | 387.4284 | 153.367 | 250.0268 | 290.4357 | 283.328 | 93.5824 | 63.7917
1466.2542 | 388.1334 | 153.518 | 249.8613 | 290.0277 | 283.2666 | 93.6506 | 63.8601
1467.2542 | 388.8862 | 153.6776 | 250.1957 | 289.7251 | 283.4313 | 93.7215 | 63.9475
1468.2542 | 390.3479 | 153.8336 | 250.3935 | 289.6361 | 283.112 | 93.8058 | 64.0236
1469.2542 | 391.3271 | 153.9916 | 250.535 | 289.8561 | 282.6553 | 93.8813 | 64.0893
1470.2542 | 392.0877 | 154.1517 | 250.6244 | 291.3517 | 282.7775 | 93.9595 | 64.1545
1471.2542 | 391.5435 | 154.3063 | 250.7537 | 291.3785 | 282.5823 | 94.0129 | 64.2425
1472.2542 | 390.2449 | 154.4648 | 250.8682 | 291.0875 | 282.2068 | 94.0788 | 64.3303
1473.2542 | 388.8082 | 154.6151 | 251.0383 | 291.5567 | 282.0708 | 94.1621 | 64.4015
1474.2542 | 388.0903 | 154.7755 | 250.9354 | 291.7076 | 282.0384 | 94.2638 | 64.4892
1475.2542 | 387.7652 | 154.9304 | 250.9693 | 291.8056 | 282.1307 | 94.3599 | 64.5642
1476.2542 | 386.9316 | 155.0764 | 250.8742 | 292.7412 | 282.3708 | 94.4603 | 64.6339
1477.2542 | 386.7543 | 155.2451 | 250.641 | 293.4539 | 282.2029 | 94.5601 | 64.7134
1478.2542 | 387.7486 | 155.3942 | 250.7813 | 293.9366 | 282.2194 | 94.6563 | 64.7709
1479.2542 | 387.8798 | 155.5605 | 250.7294 | 295.1737 | 283.798 | 94.7453 | 64.8557
1480.2542 | 388.4073 | 155.7223 | 250.9564 | 294.8619 | 283.3902 | 94.8286 | 64.9358
1481.2542 | 387.7145 | 155.8667 | 251.0026 | 294.8391 | 284.6738 | 94.9264 | 65.0278
1482.2542 | 387.9606 | 156.0149 | 251.5207 | 294.962 | 284.6344 | 95.0098 | 65.1048
1483.2542 | 389.5326 | 156.168 | 251.2836 | 294.4497 | 284.7689 | 95.1108 | 65.1965
1484.2542 | 389.0161 | 156.3381 | 251.2895 | 294.3492 | 285.7408 | 95.2039 | 65.2556
1485.2542 | 390.6957 | 156.4965 | 251.7278 | 294.6517 | 285.7382 | 95.3019 | 65.3185
1486.2542 | 391.3679 | 156.6535 | 252.0659 | 295.68 | 286.0491 | 94.8983 | 65.4001
1487.2542 | 393.7058 | 156.8131 | 252.6519 | 295.452 | 286.2089 | 95.2288 | 65.4683
1488.2542 | 392.3038 | 156.9758 | 252.7248 | 296.4391 | 286.5069 | 95.352 | 65.5415
1489.2542 | 391.9762 | 157.132 | 253.1383 | 296.9802 | 286.94 | 95.4893 | 65.613
1490.2542 | 391.2203 | 157.2948 | 253.5822 | 296.7457 | 287.3386 | 95.614 | 65.6918
1491.2542 | 390.6345 | 157.4453 | 253.8014 | 297.094 | 287.135 | 95.755 | 65.7686
1492.2542 | 391.1609 | 157.6112 | 253.9516 | 296.5039 | 286.6782 | 95.8599 | 65.8364
1493.2542 | 391.9644 | 157.7777 | 254.0879 | 297.1933 | 286.9268 | 95.9584 | 65.9046
1494.2542 | 392.6303 | 157.9316 | 254.1453 | 297.8234 | 286.8163 | 96.112 | 66.0065
1495.2542 | 391.0086 | 158.0956 | 254.1327 | 297.7428 | 286.6854 | 96.2405 | 66.0769
1496.2542 | 389.1649 | 158.2523 | 254.0858 | 297.6818 | 286.4213 | 96.3657 | 66.1609
1497.2542 | 388.1208 | 158.4116 | 253.7215 | 298.2969 | 286.5579 | 96.4662 | 66.2415
1498.2542 | 389.1302 | 158.5654 | 253.7236 | 297.7819 | 286.5289 | 96.5809 | 66.3294
1499.2542 | 388.8024 | 158.7206 | 253.6867 | 298.0529 | 287.0684 | 96.6888 | 66.3956
1500.2542 | 388.0752 | 158.8869 | 253.6602 | 298.2222 | 287.6793 | 96.7961 | 66.4841
1501.2542 | 387.9643 | 159.0369 | 254.1284 | 298.7543 | 286.991 | 96.9083 | 66.5539
1502.2542 | 387.3163 | 159.205 | 254.0302 | 299.0034 | 287.0068 | 96.9936 | 66.624
1503.2542 | 387.5452 | 159.3643 | 253.8227 | 298.6799 | 287.2439 | 97.1199 | 66.7082
1504.2542 | 388.9757 | 159.5302 | 254.2931 | 298.5552 | 286.8373 | 97.2068 | 66.7899
1505.2542 | 389.0602 | 159.6848 | 254.1704 | 298.3514 | 287.6826 | 97.2942 | 66.871
1506.2542 | 390.1059 | 159.8407 | 254.5959 | 298.8703 | 288.2631 | 97.395 | 66.9352
1507.2542 | 390.4104 | 160.0011 | 254.5954 | 299.3132 | 287.9395 | 97.4798 | 67.001
1508.2542 | 390.0176 | 160.1616 | 254.7397 | 299.3236 | 288.5104 | 97.5625 | 67.0788
1509.2542 | 391.001 | 160.3241 | 255.3899 | 299.4666 | 288.528 | 97.6448 | 67.152
1510.2542 | 393.8907 | 160.4817 | 255.9956 | 300.0012 | 288.389 | 97.7416 | 67.2346
1511.2542 | 395.4015 | 160.6466 | 256.5109 | 300.2053 | 288.0571 | 97.8442 | 67.3111
1512.2542 | 396.1535 | 160.805 | 256.7289 | 300.7908 | 288.359 | 97.9384 | 67.3917
1513.2542 | 399.7903 | 160.9657 | 256.9057 | 300.5159 | 287.92 | 98.0314 | 67.4789
1514.2542 | 401.1014 | 161.1297 | 257.6245 | 300.3341 | 288.2902 | 98.1101 | 67.551
1515.2542 | 399.839 | 161.2829 | 257.8517 | 300.3625 | 288.0969 | 98.2139 | 67.6312
1516.2542 | 401.2082 | 161.4644 | 258.321 | 300.0893 | 287.8729 | 98.3082 | 67.6915
1517.2542 | 402.4208 | 161.6233 | 258.5443 | 299.9294 | 288.0623 | 98.4039 | 67.7792
1518.2542 | 402.9925 | 161.7757 | 259.3518 | 299.7003 | 288.3947 | 98.5002 | 67.8631
1519.2542 | 405.3165 | 161.9348 | 259.1477 | 300.0683 | 287.7546 | 98.5799 | 67.9465
1520.2542 | 404.8584 | 162.1026 | 258.8132 | 300.1057 | 288.6574 | 98.6644 | 68.0125
1521.2542 | 407.4619 | 162.2558 | 259.1619 | 300.2329 | 289.1848 | 98.7628 | 68.0856
1522.2542 | 409.2829 | 162.4094 | 258.5946 | 300.4852 | 288.963 | 98.8638 | 68.1581
1523.2542 | 410.7523 | 162.5719 | 259.0179 | 300.9529 | 289.5961 | 98.9564 | 68.239
1524.2542 | 410.4301 | 162.7363 | 259.5301 | 301.093 | 289.2566 | 99.0459 | 68.314
1525.2542 | 410.4892 | 162.9007 | 260.1369 | 300.861 | 289.2894 | 99.1642 | 68.404
1526.2542 | 407.9987 | 163.0552 | 259.9873 | 301.0667 | 289.8401 | 99.2629 | 68.4729
1527.2542 | 406.2636 | 163.2081 | 260.3441 | 301.7483 | 289.697 | 99.3588 | 68.5654
1528.2542 | 405.7082 | 163.3721 | 260.9208 | 301.7748 | 289.9543 | 99.4612 | 68.6361
1529.2542 | 407.3538 | 163.5362 | 261.0649 | 302.7552 | 291.2797 | 99.5723 | 68.7235
1530.2542 | 408.4048 | 163.7038 | 261.0497 | 302.8607 | 290.4451 | 99.6733 | 68.7824
1531.2542 | 407.5403 | 163.8712 | 261.3153 | 302.8348 | 289.7366 | 99.7818 | 68.8671
1532.2542 | 406.7877 | 164.0303 | 261.4681 | 303.5283 | 289.5867 | 99.8828 | 68.9593
1533.2542 | 408.5427 | 164.1929 | 261.4588 | 303.7567 | 289.6071 | 99.9926 | 69.0377
1534.2542 | 411.2965 | 164.3521 | 262.4747 | 303.1012 | 290.5029 | 100.0967 | 69.1272
1535.2542 | 412.6913 | 164.5198 | 262.7728 | 303.1296 | 290.0694 | 100.1934 | 69.1995
1536.2542 | 414.5993 | 164.6688 | 263.5516 | 304.5686 | 291.0814 | 100.2991 | 69.2681
1537.2542 | 414.9938 | 164.8394 | 264.0886 | 304.7806 | 292.5761 | 100.4152 | 69.3625
1538.2542 | 415.8834 | 165.0071 | 264.3471 | 304.6431 | 293.3554 | 100.5236 | 69.4339
1539.2542 | 416.3618 | 165.1516 | 264.1536 | 304.7343 | 293.2507 | 100.6241 | 69.5375
1540.2542 | 417.7533 | 165.3117 | 264.6086 | 305.5319 | 293.6439 | 100.7186 | 69.6058
1541.2542 | 419.3435 | 165.4785 | 265.1979 | 306.1236 | 294.074 | 100.8169 | 69.6834
1542.2542 | 419.7745 | 165.6367 | 265.3305 | 307.24 | 294.1053 | 100.9255 | 69.7361
1543.2542 | 422.2101 | 165.7966 | 265.4627 | 308.5939 | 294.2045 | 101.0252 | 69.8331
1544.2542 | 424.9859 | 165.9617 | 265.9739 | 309.6641 | 294.1968 | 101.1241 | 69.8995
1545.2542 | 425.0147 | 166.1283 | 266.1552 | 308.8691 | 294.214 | 101.2363 | 70.0016
1546.2542 | 424.763 | 166.2944 | 266.1445 | 308.7492 | 294.8629 | 101.3365 | 70.0745
1547.2542 | 424.4143 | 166.4669 | 266.0237 | 308.5738 | 295.145 | 101.4285 | 70.1499
1548.2542 | 425.7698 | 166.6206 | 267.0785 | 309.9473 | 295.048 | 101.5355 | 70.2413
1549.2542 | 424.6468 | 166.7894 | 266.6946 | 309.387 | 294.9984 | 101.6442 | 70.3072
1550.2542 | 426.2664 | 166.9593 | 266.7082 | 309.6968 | 296.4449 | 101.7555 | 70.3919
1551.2542 | 425.689 | 167.1122 | 266.5199 | 309.9762 | 296.6712 | 101.843 | 70.4721
1552.2542 | 425.2581 | 167.287 | 266.6134 | 309.7372 | 296.5932 | 101.9335 | 70.5492
1553.2542 | 427.0895 | 167.4567 | 266.6302 | 308.9011 | 296.5771 | 102.0315 | 70.6288
1554.2542 | 425.3749 | 167.6184 | 266.243 | 308.6029 | 297.0177 | 102.1099 | 70.7092
1555.2542 | 423.2525 | 167.7771 | 265.7994 | 308.4576 | 297.6951 | 102.1419 | 70.7894
1556.2542 | 422.142 | 167.9443 | 265.9688 | 308.6007 | 298.0663 | 102.2907 | 70.8434
1557.2542 | 420.232 | 168.1176 | 265.9699 | 308.5637 | 298.1769 | 102.4061 | 70.935
1558.2542 | 420.7952 | 168.272 | 266.1028 | 309.0142 | 298.5882 | 102.5221 | 71.0271
1559.2542 | 421.5323 | 168.4426 | 266.5363 | 309.6233 | 298.1762 | 102.6318 | 71.11
1560.2542 | 422.9963 | 168.6001 | 267.0025 | 309.6871 | 298.292 | 102.7452 | 71.2068
1561.2542 | 423.4401 | 168.7567 | 266.7151 | 309.8461 | 298.5138 | 102.8567 | 71.275
1562.2542 | 425.7151 | 168.928 | 266.9572 | 310.3581 | 299.1058 | 102.9654 | 71.3396
1563.2542 | 425.9225 | 169.1014 | 266.9161 | 310.0369 | 299.1202 | 103.0672 | 71.4202
1564.2542 | 426.277 | 169.264 | 267.2381 | 309.6996 | 299.0446 | 103.1854 | 71.5022
1565.2542 | 426.8381 | 169.4336 | 268.1976 | 309.5412 | 299.3094 | 103.2819 | 71.5803
1566.2542 | 426.6476 | 169.594 | 268.8487 | 309.3743 | 299.3239 | 103.3792 | 71.651
1567.2542 | 427.3736 | 169.758 | 269.5199 | 309.6861 | 299.352 | 103.4869 | 71.7404
1568.2542 | 426.1812 | 169.9272 | 269.3638 | 309.8822 | 298.6825 | 103.5923 | 71.8348
1569.2542 | 427.5017 | 170.0898 | 269.9595 | 310.6152 | 298.9493 | 103.7031 | 71.9056
1570.2542 | 429.1131 | 170.2523 | 270.2723 | 310.872 | 299.0737 | 103.7925 | 71.9757
1571.2542 | 428.9985 | 170.4111 | 270.1896 | 311.8365 | 299.3089 | 103.9036 | 72.0686
1572.2542 | 427.3839 | 170.5862 | 270.5713 | 312.2024 | 299.3667 | 103.9996 | 72.1506
1573.2542 | 430.1491 | 170.7597 | 269.9516 | 312.3603 | 299.9314 | 104.101 | 72.2398
1574.2542 | 430.1368 | 170.9319 | 269.8756 | 312.9688 | 300.6215 | 104.2026 | 72.3098
1575.2542 | 429.6479 | 171.0985 | 270.7309 | 313.8223 | 300.5976 | 104.3082 | 72.3937
1576.2542 | 428.8356 | 171.2645 | 270.7491 | 313.988 | 300.1765 | 104.3912 | 72.4726
1577.2542 | 432.1364 | 171.4317 | 271.3805 | 314.2663 | 300.4307 | 104.5004 | 72.5612
1578.2542 | 432.98 | 171.5962 | 272.2388 | 314.5267 | 301.3055 | 104.5916 | 72.6518
1579.2542 | 432.8959 | 171.7666 | 272.6223 | 314.8465 | 301.0289 | 104.7016 | 72.7364
1580.2542 | 431.4801 | 171.911 | 273.0448 | 314.8052 | 300.8014 | 104.8125 | 72.8142
1581.2542 | 435.7465 | 172.0749 | 273.501 | 314.9659 | 300.9807 | 104.9058 | 72.8877
1582.2542 | 435.6736 | 172.2645 | 273.3984 | 314.8391 | 301.3795 | 104.9956 | 72.9705
1583.2542 | 435.1082 | 172.42 | 273.083 | 314.8683 | 301.546 | 105.0947 | 73.052
1584.2542 | 437 | 172.5866 | 272.7651 | 314.6526 | 301.9246 | 105.1832 | 73.1521
1585.2542 | 439.7379 | 172.7631 | 272.3169 | 314.6117 | 301.5858 | 105.1914 | 73.2294
1586.2542 | 437.7277 | 172.9427 | 272.3235 | 314.362 | 300.9542 | 105.3068 | 73.3035
1587.2542 | 440.107 | 173.1108 | 272.2342 | 314.773 | 300.9708 | 105.4462 | 73.3658
1588.2542 | 440.3081 | 173.2834 | 272.6542 | 315.1352 | 300.2444 | 105.5758 | 73.4726
1589.2542 | 441.6721 | 173.4518 | 272.9194 | 315.4604 | 301.5854 | 105.6718 | 73.5543
1590.2542 | 442.0841 | 173.6223 | 272.3793 | 315.6381 | 301.4179 | 105.7893 | 73.6474
1591.2542 | 442.5308 | 173.7985 | 271.9151 | 315.499 | 302.0799 | 105.9019 | 73.7232
1592.2542 | 442.7616 | 173.9769 | 272.2023 | 316.0296 | 302.3473 | 105.9971 | 73.8003
1593.2542 | 445.1418 | 174.1373 | 272.5208 | 315.3391 | 302.0449 | 106.084 | 73.89
1594.2542 | 449.0083 | 174.3136 | 272.5385 | 314.9346 | 302.419 | 106.1803 | 73.9731
1595.2542 | 452.7772 | 174.4841 | 272.9115 | 314.5099 | 302.5863 | 106.2622 | 74.0423
1596.2542 | 449.2161 | 174.6561 | 273.4229 | 314.2744 | 302.2212 | 106.3491 | 74.118
1597.2542 | 450.8653 | 174.8278 | 273.1973 | 314.347 | 302.7266 | 106.3842 | 74.2182
1598.2542 | 454.6731 | 174.9872 | 273.3845 | 314.2846 | 303.1792 | 106.4718 | 74.3088
1599.2542 | 452.466 | 175.1577 | 273.5117 | 314.0588 | 303.3657 | 106.5895 | 74.3637
1600.2542 | 454.9181 | 175.3269 | 273.7316 | 315.446 | 303.406 | 106.7024 | 74.4423
1601.2542 | 452.3927 | 175.4803 | 273.7774 | 315.6217 | 303.0634 | 106.8054 | 74.5317
1602.2542 | 449.6579 | 175.6559 | 273.8085 | 315.7022 | 303.7241 | 106.9216 | 74.6165
1603.2542 | 450.4914 | 175.8372 | 274.3302 | 315.275 | 304.03 | 107.0226 | 74.6821
1604.2542 | 451.2341 | 176.0059 | 274.5686 | 315.4655 | 304.2113 | 107.1262 | 74.784
1605.2542 | 450.7229 | 176.1774 | 274.6122 | 315.8166 | 304.042 | 107.2391 | 74.869
1606.2542 | 454.0369 | 176.3535 | 274.6341 | 315.6545 | 303.2954 | 107.3478 | 74.9491
1607.2542 | 456.4239 | 176.5215 | 274.8603 | 316.1319 | 303.4755 | 107.4404 | 75.0376
1608.2542 | 451.6625 | 176.6979 | 275.1852 | 316.3317 | 303.8082 | 107.5475 | 75.1569
1609.2542 | 447.252 | 176.869 | 274.9251 | 316.0829 | 304.3118 | 107.659 | 75.2083
1610.2542 | 448.8648 | 177.0523 | 274.6523 | 315.7132 | 304.2337 | 107.7671 | 75.2831
1611.2542 | 457.0053 | 177.2385 | 274.2737 | 315.466 | 304.0462 | 107.8713 | 75.3623
1612.2542 | 456.9024 | 177.4111 | 274.1731 | 315.2016 | 305.5214 | 107.9712 | 75.4532
1613.2542 | 460.9398 | 177.5907 | 274.0126 | 314.878 | 305.5955 | 108.0766 | 75.5295
1614.2542 | 465.0131 | 177.7727 | 273.9544 | 314.3095 | 305.6742 | 108.1717 | 75.614
1615.2542 | 465.6576 | 177.9567 | 274.4431 | 313.8949 | 305.1188 | 108.2783 | 75.6932
1616.2542 | 466.2223 | 178.1369 | 275.0301 | 314.1539 | 304.9349 | 108.3808 | 75.7743
1617.2542 | 465.7882 | 178.3162 | 274.9247 | 314.2828 | 304.5885 | 108.4875 | 75.8589
1618.2542 | 469.1268 | 178.4987 | 275.0533 | 314.4824 | 304.718 | 108.5885 | 75.9528
1619.2542 | 474.4264 | 178.6848 | 275.4463 | 314.124 | 304.7664 | 108.6837 | 76.0374
1620.2542 | 468.8972 | 178.8644 | 276.2669 | 314.7516 | 304.7471 | 108.781 | 76.1332
1621.2542 | 468.6945 | 179.0529 | 276.1965 | 315.1916 | 304.5185 | 108.8815 | 76.2101
1622.2542 | 476.6868 | 179.2438 | 275.9938 | 315.1062 | 304.6739 | 108.9745 | 76.3136
1623.2542 | 483.2196 | 179.4278 | 275.4259 | 315.6785 | 305.156 | 109.0626 | 76.4099
1624.2542 | 473.8736 | 179.6081 | 276.3921 | 316.1376 | 305.5982 | 109.1702 | 76.487
1625.2542 | 475.5076 | 179.7938 | 276.7201 | 316.149 | 305.7671 | 109.269 | 76.5584
1626.2542 | 472.2249 | 179.9708 | 276.8427 | 317.1194 | 306.0814 | 109.3628 | 76.6525
1627.2542 | 477.6693 | 180.1646 | 277.2221 | 317.7468 | 306.5197 | 109.4709 | 76.7236
1628.2542 | 469.516 | 180.3504 | 277.5353 | 318.2351 | 306.7024 | 109.5724 | 76.8068
1629.2542 | 467.8351 | 180.5408 | 278.0487 | 318.2316 | 307.3879 | 109.6886 | 76.891
1630.2542 | 465.5446 | 180.7324 | 278.5748 | 318.8373 | 307.7428 | 109.7888 | 76.9633
1631.2542 | 464.5154 | 180.9205 | 279.3762 | 319.8927 | 307.2476 | 109.8965 | 77.0236
1632.2542 | 458.6427 | 181.1123 | 279.6774 | 322.0761 | 307.2533 | 110.0197 | 77.1226
1633.2542 | 459.4647 | 181.3016 | 280.0769 | 321.6907 | 307.7401 | 110.132 | 77.2054
1634.2542 | 461.5912 | 181.487 | 280.0308 | 321.039 | 307.5106 | 110.2403 | 77.2757
1635.2542 | 461.0369 | 181.6753 | 280.4594 | 320.926 | 307.6791 | 110.3468 | 77.3755
1636.2542 | 460.8526 | 181.86 | 280.2964 | 320.7002 | 307.3089 | 110.4579 | 77.4787
1637.2542 | 466.0308 | 182.0444 | 280.2807 | 321.297 | 306.4147 | 110.5631 | 77.5549
1638.2542 | 467.5363 | 182.2385 | 280.2278 | 321.1144 | 305.8818 | 110.6831 | 77.6456
1639.2542 | 465.1996 | 182.4364 | 280.2408 | 320.3541 | 306.3207 | 110.7842 | 77.7269
1640.2542 | 469.7486 | 182.615 | 280.2067 | 320.1391 | 305.667 | 110.8955 | 77.8165
1641.2542 | 471.3546 | 182.8137 | 280.2278 | 319.9505 | 306.3336 | 110.9986 | 77.8913
1642.2542 | 467.3051 | 183.0048 | 281.2104 | 319.9916 | 306.5549 | 111.1032 | 77.9703
1643.2542 | 465.693 | 183.1901 | 281.4597 | 320.3517 | 307.6875 | 111.2109 | 78.0424
1644.2542 | 468.6781 | 183.3847 | 282.2614 | 321.5291 | 308.3518 | 111.321 | 78.139
1645.2542 | 466.8401 | 183.5785 | 282.3804 | 322.3542 | 309.0206 | 111.4196 | 78.2273
1646.2542 | 463.6601 | 183.7647 | 282.1005 | 322.4404 | 309.0849 | 111.5197 | 78.3112
1647.2542 | 462.8305 | 183.9581 | 282.1215 | 323.0677 | 309.6915 | 111.6365 | 78.4003
1648.2542 | 461.1156 | 184.1497 | 281.8457 | 324.1306 | 310.1467 | 111.756 | 78.4758
1649.2542 | 459.3245 | 184.3397 | 281.9655 | 324.1364 | 310.6266 | 111.8607 | 78.5722
1650.2542 | 454.3703 | 184.5356 | 282.2268 | 323.826 | 311.136 | 111.9734 | 78.6427
1651.2542 | 453.3258 | 184.7234 | 282.8092 | 323.3139 | 311.7899 | 112.0781 | 78.7269
1652.2542 | 450.6377 | 184.8823 | 283.2461 | 323.4983 | 311.4081 | 112.1841 | 78.8185
1653.2542 | 453.0779 | 185.065 | 283.9036 | 324.3909 | 311.6678 | 112.3008 | 78.8734
1654.2542 | 448.2508 | 185.2528 | 283.9785 | 324.8776 | 311.104 | 112.4269 | 78.9747
1655.2542 | 450.0264 | 185.4259 | 283.8016 | 325.4701 | 310.7879 | 112.5444 | 79.055
1656.2542 | 450.263 | 185.5949 | 284.3002 | 326.3528 | 311.6408 | 112.6494 | 79.1474
1657.2698 | 447.1694 | 185.758 | 285.0191 | 326.7672 | 311.8995 | 112.769 | 79.2381
1658.2542 | 451.1741 | 185.9458 | 284.9042 | 326.5476 | 312.3536 | 112.8779 | 79.3192
1659.2542 | 451.3715 | 186.1248 | 285.489 | 325.9745 | 312.3312 | 112.9825 | 79.3972
1660.2542 | 449.316 | 186.3115 | 284.9449 | 325.6045 | 312.0571 | 113.0896 | 79.4701
1661.2542 | 451.1621 | 186.4915 | 285.185 | 325.3716 | 311.9418 | 113.1976 | 79.5577
1662.2542 | 450.9691 | 186.692 | 284.9853 | 325.1595 | 311.493 | 113.3226 | 79.6481
1663.2542 | 449.5187 | 186.9151 | 284.8865 | 324.7331 | 310.5613 | 113.4213 | 79.7287
1664.2542 | 451.3984 | 187.1078 | 284.8003 | 324.4875 | 310.1 | 113.5269 | 79.8304
1665.2542 | 447.6163 | 187.3049 | 284.4555 | 323.7968 | 310.1321 | 113.6217 | 79.9001
1666.2542 | 448.3653 | 187.4886 | 284.8757 | 323.6857 | 310.0931 | 113.7269 | 79.9808
1667.2542 | 448.0145 | 187.6917 | 284.9448 | 324.936 | 310.8627 | 113.8147 | 80.0557
1668.2542 | 446.1411 | 187.8757 | 285.2891 | 325.0927 | 310.4058 | 113.9299 | 80.1602
1669.2542 | 445.078 | 188.0806 | 284.913 | 324.9948 | 310.2924 | 114.0544 | 80.2452
1670.2542 | 443.5148 | 188.2776 | 285.063 | 324.6592 | 310.3339 | 114.1686 | 80.3088
1671.2542 | 442.8092 | 188.4758 | 284.6729 | 324.512 | 309.8138 | 114.2947 | 80.4075
1672.2542 | 442.7449 | 188.6716 | 284.8777 | 324.7302 | 309.9529 | 114.3956 | 80.4842
1673.2542 | 443.0121 | 188.8729 | 285.5497 | 324.6588 | 309.359 | 114.5034 | 80.5912
1674.2542 | 449.1793 | 189.0486 | 285.0361 | 324.626 | 309.3579 | 114.6215 | 80.6614
1675.2542 | 454.8314 | 189.237 | 284.8852 | 324.3467 | 309.3451 | 114.7314 | 80.7523
1676.2542 | 457.7686 | 189.4318 | 285.0587 | 324.3168 | 309.5126 | 114.8409 | 80.8351
1677.2542 | 471.2587 | 189.6224 | 284.7523 | 324.9738 | 309.4841 | 114.9395 | 80.9218
1678.2542 | 470.0961 | 189.8236 | 284.545 | 325.534 | 308.9955 | 115.0404 | 81.0293
1679.2542 | 474.0701 | 189.9901 | 284.684 | 325.7529 | 308.6064 | 115.1424 | 81.1074
1680.2542 | 472.5577 | 190.2141 | 285.054 | 326.0491 | 308.8656 | 115.2512 | 81.2037
1681.2542 | 475.0612 | 190.4137 | 285.3986 | 325.9481 | 308.3212 | 115.3512 | 81.2922
1682.2542 | 472.4087 | 190.6044 | 285.5586 | 325.8288 | 308.4623 | 115.4547 | 81.3789
1683.2542 | 469.9581 | 190.8058 | 285.5496 | 325.8664 | 309.5649 | 115.5669 | 81.45
1684.2542 | 467.3534 | 190.9918 | 285.5328 | 326.1043 | 309.4831 | 115.6702 | 81.5343
1685.2542 | 465.7983 | 191.1951 | 285.7752 | 326.1378 | 310.1749 | 115.7782 | 81.6522
1686.2542 | 463.8451 | 191.39 | 285.6077 | 326.885 | 311.3366 | 115.8921 | 81.7432
1687.2542 | 463.045 | 191.5698 | 285.7581 | 327.9224 | 310.3105 | 116.0051 | 81.8245
1688.2542 | 461.3225 | 191.77 | 287.1872 | 327.715 | 310.8428 | 116.1183 | 81.8935
1689.2542 | 462.0661 | 191.9613 | 287.9434 | 327.3269 | 310.5634 | 116.2199 | 82.0025
1690.2542 | 462.412 | 192.1649 | 287.785 | 327.0734 | 311.2314 | 116.3321 | 82.0906
1691.2542 | 462.3637 | 192.3614 | 288.2088 | 328.0221 | 311.1066 | 116.4491 | 82.1834
1692.2542 | 461.7373 | 192.5618 | 288.7902 | 327.7021 | 311.7076 | 116.5569 | 82.2832
1693.2542 | 458.8899 | 192.7499 | 288.7355 | 327.7209 | 312.2995 | 116.6568 | 82.3668
1694.2542 | 457.0202 | 192.9504 | 288.9838 | 327.1493 | 312.7238 | 116.7657 | 82.4445
1695.2542 | 453.23 | 193.1498 | 288.7233 | 326.8467 | 313.2422 | 116.8877 | 82.5161
1696.2542 | 450.004 | 193.3418 | 288.7962 | 326.6405 | 312.8418 | 117.0009 | 82.5981
1697.2542 | 447.479 | 193.5522 | 289.0361 | 327.0251 | 312.2873 | 117.1117 | 82.6852
1698.2542 | 445.162 | 193.7441 | 289.9393 | 327.4909 | 313.4476 | 117.2192 | 82.7732
1699.2542 | 444.8917 | 193.9425 | 289.8389 | 327.8074 | 313.5066 | 117.3322 | 82.8456
1700.2542 | 446.1007 | 194.12 | 289.5074 | 326.9218 | 313.425 | 117.4483 | 82.9435
1701.2542 | 444.5276 | 194.3129 | 289.502 | 326.9372 | 314.2775 | 117.5649 | 83.026
1702.2542 | 444.9323 | 194.5026 | 289.3598 | 326.6818 | 313.722 | 117.6681 | 83.1182
1703.2542 | 447.875 | 194.7027 | 289.6996 | 326.5933 | 313.7317 | 117.784 | 83.2124
1704.2542 | 448.5194 | 194.912 | 289.0555 | 327.3712 | 313.5387 | 117.8997 | 83.304
1705.2542 | 448.1451 | 195.114 | 289.0319 | 328.4902 | 315.0705 | 118.0166 | 83.3896
1706.2542 | 447.1408 | 195.2951 | 290.2254 | 328.5944 | 315.6768 | 118.1107 | 83.4726
1707.2542 | 448.9182 | 195.4929 | 290.4848 | 329.2536 | 315.0366 | 118.2127 | 83.5701
1708.2542 | 449.328 | 195.688 | 290.8728 | 329.8048 | 314.9015 | 118.329 | 83.6713
1709.2542 | 448.6748 | 195.8837 | 290.7873 | 329.4075 | 315.1169 | 118.4449 | 83.757
1710.2542 | 446.9597 | 196.0914 | 291.0425 | 330.1218 | 315.9448 | 118.5529 | 83.8402
1711.2542 | 445.0886 | 196.2797 | 291.3569 | 330.3046 | 315.4244 | 118.6513 | 83.941
1712.2542 | 441.5251 | 196.4489 | 291.9638 | 330.7972 | 314.8472 | 118.764 | 84.0154
1713.2542 | 438.9638 | 196.6521 | 292.3605 | 330.5277 | 313.8466 | 118.8937 | 84.1124
1714.2542 | 436.2607 | 196.8554 | 292.9527 | 330.4162 | 314.154 | 119.0006 | 84.1804
1715.2542 | 434.4785 | 197.067 | 293.3524 | 330.6103 | 314.4888 | 119.1029 | 84.2794
1716.2542 | 433.8621 | 197.2722 | 293.9893 | 331.4354 | 314.008 | 119.2203 | 84.3883
1717.2542 | 432.7261 | 197.4613 | 294.1101 | 331.7306 | 313.2124 | 119.3271 | 84.4754
1718.2542 | 431.4071 | 197.6448 | 294.1231 | 332.6025 | 313.2118 | 119.4406 | 84.5535
1719.2542 | 431.5705 | 197.8651 | 293.6405 | 332.3457 | 312.6166 | 119.5497 | 84.632
1720.2542 | 430.0638 | 198.0743 | 293.4937 | 332.29 | 313.5785 | 119.6491 | 84.7311
1721.2542 | 427.6428 | 198.2609 | 293.8092 | 331.936 | 312.997 | 119.7602 | 84.8136
1722.2542 | 426.4595 | 198.456 | 293.9564 | 331.2158 | 312.5774 | 119.8584 | 84.9141
1723.2542 | 426.0896 | 198.6465 | 294.2388 | 331.3918 | 312.4009 | 119.9637 | 84.9946
1724.2542 | 426.4994 | 198.8416 | 294.119 | 331.6444 | 312.0669 | 120.0615 | 85.1152
1725.2542 | 428.3795 | 199.0377 | 293.8366 | 331.4497 | 311.9203 | 120.1684 | 85.1568
1726.2542 | 427.4904 | 199.248 | 294.004 | 331.3456 | 312.0399 | 120.2715 | 85.2547
1727.2542 | 427.0507 | 199.4321 | 294.3837 | 331.2564 | 312.2273 | 120.3681 | 85.3368
1728.2542 | 426.0158 | 199.6398 | 294.7284 | 330.7943 | 312.8612 | 120.4668 | 85.4282
1729.2542 | 426.7442 | 199.8263 | 294.3539 | 330.1338 | 313.54 | 120.5632 | 85.492
1730.2542 | 427.0844 | 200.0225 | 294.8342 | 329.886 | 313.9332 | 120.6649 | 85.595
1731.2542 | 426.8517 | 200.2075 | 294.9978 | 330.1659 | 315.1511 | 120.7566 | 85.6973
1732.2542 | 427.9515 | 200.4089 | 295.0607 | 329.6952 | 314.3969 | 120.8713 | 85.8017
1733.2542 | 428.5739 | 200.6003 | 295.0013 | 329.9325 | 314.6489 | 120.9635 | 85.8997
1734.2542 | 428.4451 | 200.7904 | 294.8338 | 330.0568 | 314.4927 | 121.0608 | 85.987
1735.2542 | 426.956 | 200.9869 | 294.8719 | 330.065 | 314.7062 | 121.1592 | 86.0624
1736.2542 | 427.598 | 201.1682 | 295.2237 | 331.2679 | 315.47 | 121.2407 | 86.1479
1737.2542 | 429.0023 | 201.3544 | 295.2346 | 332.0949 | 315.3882 | 121.3201 | 86.2306
1738.2542 | 432.2634 | 201.5396 | 295.6128 | 332.6184 | 315.8035 | 121.4235 | 86.3252
1739.2542 | 431.038 | 201.7378 | 296.0512 | 332.5756 | 317.3267 | 121.5206 | 86.4075
1740.2542 | 434.5466 | 201.9234 | 295.7099 | 332.5938 | 316.7941 | 121.6213 | 86.4961
1741.2542 | 434.2549 | 202.1256 | 295.4793 | 333.4982 | 316.202 | 121.7281 | 86.5803
1742.2542 | 434.1131 | 202.2943 | 295.5844 | 335.2592 | 316.4266 | 121.8436 | 86.6609
1743.2542 | 434.3878 | 202.4733 | 295.5862 | 335.582 | 317.3139 | 121.9545 | 86.7567
1744.2542 | 434.9981 | 202.6712 | 295.8774 | 335.3398 | 317.2481 | 122.0506 | 86.8803
1745.2542 | 433.5177 | 202.8532 | 296.8181 | 335.6622 | 318.2917 | 122.147 | 86.9629
1746.2542 | 435.7617 | 203.0485 | 296.8231 | 335.4159 | 317.6646 | 122.2386 | 87.0638
1747.2542 | 434.2119 | 203.2222 | 296.92 | 334.5803 | 317.7374 | 122.3514 | 87.1264
1748.2542 | 434.3815 | 203.4172 | 296.8224 | 335.1419 | 317.185 | 122.4631 | 87.2105
1749.2542 | 432.4464 | 203.5939 | 296.8106 | 334.3743 | 317.7566 | 122.5608 | 87.2894
1750.2542 | 430.7258 | 203.7737 | 296.6259 | 333.7213 | 317.8047 | 122.643 | 87.3907
1751.2542 | 429.031 | 203.9605 | 296.6185 | 333.4257 | 316.7389 | 122.7593 | 87.4801
1752.2542 | 427.396 | 204.1448 | 296.6029 | 332.7056 | 315.5644 | 122.8673 | 87.5809
1753.2542 | 424.8714 | 204.3264 | 297.6141 | 332.6593 | 314.7506 | 122.9821 | 87.6985
1754.2542 | 424.1685 | 204.4953 | 298.4761 | 333.1872 | 314.3825 | 123.0809 | 87.7688
1755.2542 | 421.1019 | 204.6868 | 298.9247 | 332.8282 | 314.1871 | 123.1791 | 87.8501
1756.2542 | 419.3575 | 204.8661 | 299.1104 | 332.9188 | 313.5243 | 123.2867 | 87.9455
1757.2542 | 417.7782 | 205.0422 | 298.5239 | 332.6794 | 313.3037 | 123.3834 | 88.047
1758.2542 | 416.9757 | 205.2389 | 298.3856 | 332.6627 | 312.6168 | 123.4874 | 88.1467
1759.2542 | 416.7349 | 205.4085 | 299.3386 | 332.686 | 312.1199 | 123.5926 | 88.2278
1760.2542 | 415.3353 | 205.5809 | 299.5473 | 332.7403 | 312.7027 | 123.6954 | 88.3024
1761.2542 | 414.7618 | 205.7646 | 299.3285 | 334.2022 | 312.8697 | 123.7735 | 88.39
1762.2542 | 413.7324 | 205.9406 | 299.2925 | 333.45 | 312.1955 | 123.8604 | 88.4926
1763.2542 | 412.8798 | 206.1234 | 299.0815 | 334.1551 | 311.231 | 123.9433 | 88.5879
1764.2542 | 412.304 | 206.287 | 298.8567 | 334.1037 | 311.9623 | 124.0377 | 88.6877
1765.2542 | 414.0975 | 206.4436 | 298.7582 | 333.8271 | 311.1846 | 124.113 | 88.7839
1766.2542 | 415.9677 | 206.6309 | 298.9322 | 333.2873 | 310.9972 | 124.1552 | 88.8833
1767.2542 | 416.5102 | 206.7789 | 298.8289 | 333.2372 | 310.7994 | 124.2752 | 88.9679
1768.2542 | 415.8438 | 206.965 | 298.5634 | 334.0215 | 309.9857 | 124.3871 | 89.0857
1769.2542 | 416.075 | 207.1448 | 298.8698 | 334.1618 | 310.3049 | 124.4897 | 89.1801
1770.2542 | 414.9033 | 207.3151 | 299.0158 | 333.8744 | 311.3206 | 124.5915 | 89.267
1771.2542 | 414.9026 | 207.4399 | 298.9555 | 333.9344 | 311.7278 | 124.6904 | 89.3686
1772.2542 | 415.9248 | 207.6218 | 299.3174 | 333.9096 | 312.3507 | 124.7716 | 89.452
1773.2542 | 415.8343 | 207.7896 | 299.7197 | 334.7858 | 312.5004 | 124.8668 | 89.546
1774.2542 | 416.0615 | 207.9612 | 299.5629 | 334.163 | 312.8448 | 124.9581 | 89.6504
1775.2542 | 416.1211 | 208.1262 | 299.7309 | 334.2279 | 312.2597 | 125.0475 | 89.7461
1776.2542 | 416.1022 | 208.3073 | 299.6345 | 334.7667 | 312.0401 | 125.1469 | 89.832
1777.2542 | 417.7972 | 208.4753 | 299.4618 | 335.1939 | 311.5868 | 125.2266 | 89.9213
1778.2542 | 418.7265 | 208.6437 | 299.6329 | 334.5116 | 312.6219 | 125.3236 | 90.0429
1779.2542 | 419.8185 | 208.8135 | 300.5987 | 335.6416 | 312.0746 | 125.4135 | 90.1349
1780.2542 | 418.9006 | 208.9802 | 300.6959 | 335.5203 | 311.4823 | 125.5083 | 90.24
1781.2542 | 421.0434 | 209.1397 | 300.3536 | 335.153 | 311.4783 | 125.5973 | 90.353
1782.2542 | 420.3314 | 209.3043 | 300.6904 | 334.952 | 313.1692 | 125.6967 | 90.4609
1783.2542 | 420.18 | 209.4523 | 300.3796 | 335.6197 | 312.6998 | 125.7914 | 90.5615
1784.2542 | 421.4112 | 209.6258 | 300.2224 | 335.9348 | 313.0108 | 125.8824 | 90.6581
1785.2542 | 420.3535 | 209.797 | 300.4284 | 336.453 | 313.3753 | 125.9672 | 90.7345
1786.2542 | 420.9536 | 209.9595 | 300.4614 | 335.9723 | 313.8843 | 126.0634 | 90.8549
1787.2542 | 420.7734 | 210.1126 | 300.5614 | 336.0478 | 315.3992 | 126.1605 | 90.9507
1788.2542 | 420.39 | 210.2767 | 301.3666 | 336.7575 | 316.1384 | 126.2509 | 91.0515
1789.2542 | 421.8455 | 210.4378 | 300.9671 | 336.7168 | 316.301 | 126.3422 | 91.1573
1790.2542 | 426.6074 | 210.5977 | 301.5689 | 337.4873 | 318.064 | 126.4305 | 91.2573
1791.2542 | 430.436 | 210.7574 | 301.9139 | 337.855 | 317.8267 | 126.5239 | 91.3513
1792.2542 | 428.819 | 210.9303 | 301.7076 | 337.4664 | 317.9448 | 126.6108 | 91.4794
1793.2542 | 428.6913 | 211.0829 | 301.9121 | 337.2479 | 318.3551 | 126.645 | 91.5841
1794.2542 | 427.867 | 211.215 | 302.7833 | 338.6223 | 319.9581 | 126.7557 | 91.689
1795.2542 | 427.6153 | 211.3939 | 302.6152 | 338.6618 | 321.2288 | 126.8587 | 91.8049
1796.2542 | 425.1026 | 211.5331 | 302.7474 | 339.0125 | 321.3393 | 126.9573 | 91.8962
1797.2542 | 422.8649 | 211.7025 | 304.124 | 338.7643 | 320.5318 | 127.0585 | 91.9956
1798.2542 | 421.8981 | 211.8656 | 304.3551 | 339.1108 | 319.9245 | 127.1507 | 92.1179
1799.2542 | 425.5673 | 212.0242 | 304.3597 | 338.1638 | 319.3694 | 127.246 | 92.2455
1800.2542 | 424.396 | 212.1831 | 304.5456 | 337.4279 | 318.4917 | 127.3378 | 92.3465
1801.2542 | 424.477 | 212.34 | 304.4192 | 337.2029 | 317.7457 | 127.434 | 92.4579
1802.2542 | 423.9694 | 212.4828 | 304.2582 | 337.1545 | 317.5723 | 127.5248 | 92.551
1803.2542 | 424.5486 | 212.6377 | 303.8033 | 336.9053 | 317.1511 | 127.6202 | 92.6693
1804.2542 | 425.2961 | 212.795 | 303.7347 | 337.1258 | 317.0698 | 127.712 | 92.7721
1805.2542 | 428.43 | 212.9616 | 304.1502 | 337.1239 | 316.1302 | 127.7946 | 92.8875
1806.2542 | 431.0127 | 213.1159 | 303.8475 | 337.5938 | 316.021 | 127.8782 | 93.0061
1807.2542 | 432.248 | 213.2597 | 304.6716 | 337.2646 | 315.8052 | 127.9696 | 93.122
1808.2542 | 431.8845 | 213.412 | 305.0207 | 336.1576 | 315.7558 | 128.0608 | 93.2293
1809.2542 | 431.5714 | 213.5932 | 304.322 | 335.0604 | 316.1461 | 128.1515 | 93.329
1810.2542 | 433.4422 | 213.7518 | 304.7387 | 334.9145 | 316.2536 | 128.235 | 93.4413
1811.2542 | 436.8467 | 213.9019 | 304.8725 | 334.547 | 315.8204 | 128.3215 | 93.5293
1812.2542 | 437.4257 | 214.0661 | 305.7848 | 334.1559 | 316.106 | 128.4087 | 93.6289
1813.2542 | 439.7256 | 214.2175 | 305.5934 | 334.609 | 316.5344 | 128.4835 | 93.7149
1814.2542 | 440.3184 | 214.3553 | 305.5424 | 334.5645 | 317.9919 | 128.5652 | 93.829
1815.2542 | 439.3613 | 214.5105 | 306.2758 | 334.1652 | 317.1258 | 128.677 | 93.9558
1816.2542 | 439.4492 | 214.682 | 306.7147 | 334.6897 | 317.5351 | 128.7601 | 94.054
1817.2542 | 439.3715 | 214.8375 | 306.3161 | 334.403 | 317.6886 | 128.862 | 94.188
1818.2542 | 440.361 | 214.98 | 306.508 | 334.391 | 317.667 | 128.9553 | 94.3073
1819.2542 | 441.6905 | 215.1452 | 306.4502 | 335.7619 | 317.14 | 129.0414 | 94.3951
1820.2542 | 440.0316 | 215.2967 | 306.6255 | 335.2131 | 317.4646 | 129.1377 | 94.5107
1821.2542 | 440.1968 | 215.4605 | 307.2204 | 335.7619 | 317.8685 | 129.2376 | 94.607
1822.2542 | 439.2129 | 215.5967 | 307.49 | 336.6664 | 317.3493 | 129.3324 | 94.7194
1823.2542 | 437.4561 | 215.7509 | 307.5224 | 337.3836 | 317.9565 | 129.4204 | 94.829
1824.2542 | 435.7122 | 215.9209 | 307.6124 | 337.6916 | 318.3112 | 129.507 | 94.95
1825.2542 | 433.8718 | 216.077 | 307.6987 | 337.6657 | 318.2886 | 129.5999 | 95.0264
1826.2542 | 433.9972 | 216.2379 | 307.914 | 337.6357 | 318.3393 | 129.6898 | 95.1497
1827.2542 | 433.0499 | 216.3968 | 307.9642 | 337.2261 | 318.3267 | 129.7825 | 95.2531
1828.2542 | 433.686 | 216.5417 | 308.3767 | 336.9131 | 319.0664 | 129.8753 | 95.3764
1829.2542 | 435.7793 | 216.698 | 308.262 | 336.414 | 318.6696 | 129.9677 | 95.4946
1830.2542 | 436.2773 | 216.8492 | 308.0055 | 336.697 | 318.3447 | 130.0598 | 95.6064
1831.2542 | 438.4155 | 217.01 | 307.5936 | 336.5647 | 318.2273 | 130.1463 | 95.7008
1832.2542 | 436.9638 | 217.1333 | 307.9383 | 337.0641 | 318.9152 | 130.248 | 95.8075
1833.2542 | 437.0018 | 217.276 | 307.7973 | 338.1317 | 319.355 | 130.3158 | 95.9244
1834.2542 | 437.4732 | 217.4379 | 308.0567 | 337.8942 | 320.2121 | 130.4011 | 96.0338
1835.2542 | 438.2152 | 217.5809 | 307.9291 | 338.1839 | 319.8204 | 130.4861 | 96.1494
1836.2542 | 439.2196 | 217.7337 | 307.9675 | 337.4396 | 320.3084 | 130.5688 | 96.2543
1837.2542 | 439.9747 | 217.8792 | 308.2515 | 337.6319 | 320.5106 | 130.6575 | 96.369
1838.2542 | 439.2529 | 218.0369 | 308.2279 | 337.8231 | 319.8382 | 130.7396 | 96.4633
1839.2542 | 441.0176 | 218.1815 | 308.3758 | 338.3609 | 319.5255 | 130.8272 | 96.5582
1840.2542 | 440.9177 | 218.3419 | 308.4652 | 339.0373 | 319.3688 | 130.9108 | 96.6604
1841.2542 | 440.2008 | 218.4961 | 308.4917 | 339.1861 | 318.7256 | 131.0015 | 96.7731
1842.2542 | 439.722 | 218.6474 | 308.3124 | 339.4687 | 318.91 | 131.0857 | 96.8935
1843.2542 | 438.9703 | 218.7804 | 308.5232 | 339.1794 | 320.138 | 131.1754 | 96.9779
1844.2542 | 440.3231 | 218.9234 | 308.3061 | 338.7719 | 320.4065 | 131.2568 | 97.0919
1845.2542 | 440.4835 | 219.0604 | 308.5341 | 338.4378 | 320.4562 | 131.3347 | 97.1969
1846.2542 | 440.1065 | 219.1999 | 308.4055 | 338.3217 | 320.9388 | 131.4156 | 97.2899
1847.2542 | 439.9696 | 219.3403 | 308.2736 | 338.5193 | 322.0044 | 131.4946 | 97.3928
1848.2542 | 439.8206 | 219.4901 | 308.2246 | 338.9878 | 323.0002 | 131.578 | 97.5068
1849.2542 | 439.0825 | 219.6337 | 308.4994 | 339.0625 | 322.8162 | 131.6773 | 97.6082
1850.2542 | 437.2316 | 219.7391 | 309.1924 | 339.6689 | 322.2013 | 131.7551 | 97.7115
1851.2542 | 436.7443 | 219.9108 | 308.5581 | 340.2223 | 322.2154 | 131.8461 | 97.8107
1852.2542 | 436.2804 | 220.0234 | 308.3817 | 339.5971 | 322.5716 | 131.9249 | 97.9102
1853.2542 | 435.2139 | 220.164 | 308.9263 | 339.8592 | 322.2804 | 132.0056 | 98.0111
1854.2542 | 435.6543 | 220.3214 | 309.6496 | 340.527 | 322.2773 | 132.0966 | 98.108
1855.2542 | 436.5931 | 220.4726 | 310.1818 | 341.562 | 322.9712 | 132.1723 | 98.215
1856.2542 | 436.8757 | 220.6134 | 310.2106 | 341.8755 | 324.0535 | 132.2555 | 98.3138
1857.2542 | 435.02 | 220.7654 | 310.2344 | 342.0776 | 323.3582 | 132.3405 | 98.4117
1858.2542 | 435.8966 | 220.9057 | 310.2758 | 341.713 | 323.6335 | 132.4317 | 98.5096
1859.2542 | 434.484 | 221.0518 | 310.8115 | 341.8186 | 323.0946 | 132.5153 | 98.5928
1860.2542 | 433.4718 | 221.1839 | 310.9537 | 342.0483 | 323.1659 | 132.6094 | 98.6937
1861.2542 | 433.9725 | 221.3222 | 311.277 | 343.3817 | 323.1221 | 132.6858 | 98.8019
1862.2542 | 437.9394 | 221.462 | 311.3757 | 343.8058 | 324.0859 | 132.782 | 98.8874
1863.2542 | 439.5009 | 221.5907 | 311.6543 | 343.2885 | 324.0869 | 132.8665 | 98.9933
1864.2542 | 441.1523 | 221.7292 | 312.1011 | 343.2443 | 324.3561 | 132.9459 | 99.1071
1865.2542 | 441.447 | 221.8604 | 313.2308 | 342.8198 | 323.9574 | 133.0317 | 99.1917
1866.2542 | 440.3222 | 222.0218 | 313.3885 | 342.9829 | 323.9679 | 133.1127 | 99.2798
1867.2542 | 440.659 | 222.1437 | 313.03 | 342.64 | 323.3351 | 133.1969 | 99.3707
1868.2542 | 442.1871 | 222.279 | 313.0464 | 341.6771 | 323.6004 | 133.2694 | 99.476
1869.2542 | 440.6556 | 222.4196 | 313.4385 | 341.0036 | 323.8538 | 133.3484 | 99.5636
1870.2542 | 440.1045 | 222.5506 | 313.9159 | 341.3408 | 323.3308 | 133.443 | 99.6817
1871.2542 | 439.3563 | 222.6955 | 313.8235 | 340.7999 | 323.1794 | 133.5259 | 99.7492
1872.2542 | 442.9818 | 222.8376 | 313.6428 | 340.5771 | 324.2287 | 133.6101 | 99.8624
1873.2542 | 443.5226 | 222.961 | 313.2709 | 340.8397 | 324.556 | 133.706 | 99.9625
1874.2542 | 441.0644 | 223.099 | 313.3555 | 341.9741 | 324.8918 | 133.7803 | 100.025
1875.2542 | 440.8774 | 223.2332 | 313.091 | 342.1767 | 324.0326 | 133.8541 | 100.1293
1876.2542 | 440.5847 | 223.3612 | 313.3999 | 341.8283 | 324.1104 | 133.9536 | 100.2074
1877.2542 | 437.6337 | 223.4961 | 314.1451 | 343.0938 | 324.395 | 134.0319 | 100.3121
1878.2542 | 436.0167 | 223.6301 | 314.327 | 342.778 | 323.5568 | 134.1225 | 100.4186
1879.2542 | 435.1843 | 223.7608 | 313.796 | 342.061 | 323.433 | 134.2105 | 100.5117
1880.2542 | 434.0858 | 223.8896 | 313.9271 | 341.4754 | 323.4036 | 134.2295 | 100.5949
1881.2542 | 432.3771 | 224.0228 | 314.1701 | 342.3657 | 323.1494 | 134.4305 | 100.6767
1882.2542 | 431.9655 | 224.1432 | 314.2971 | 342.6471 | 322.65 | 134.5293 | 100.7491
1883.2542 | 431.4626 | 224.272 | 313.8972 | 342.4066 | 322.4082 | 134.5694 | 100.8775
1884.2542 | 431.5074 | 224.3555 | 313.8468 | 342.2774 | 322.5354 | 134.688 | 100.9822
1885.2542 | 430.4588 | 224.5006 | 314.5669 | 342.5371 | 323.0743 | 134.7843 | 101.0652
1886.2542 | 429.4269 | 224.6054 | 314.7751 | 342.447 | 323.1487 | 134.8817 | 101.1507
1887.2542 | 427.5409 | 224.7277 | 315.0203 | 342.5282 | 322.7829 | 134.9779 | 101.2292
1888.2542 | 426.5694 | 224.8574 | 315.4003 | 342.9217 | 323.1839 | 135.0541 | 101.3079
1889.2542 | 433.6816 | 224.9922 | 315.7251 | 342.822 | 323.579 | 135.1517 | 101.4186
1890.2542 | 431.8074 | 225.0998 | 316.295 | 342.3192 | 323.6298 | 135.2413 | 101.5006
1891.2542 | 430.1756 | 225.2168 | 316.2222 | 341.7118 | 323.6678 | 135.3281 | 101.5879
1892.2542 | 429.2257 | 225.3164 | 315.9931 | 341.4838 | 323.7822 | 135.4127 | 101.6714
1893.2542 | 428.0884 | 225.4408 | 316.1447 | 341.4527 | 324.44 | 135.5045 | 101.7629
1894.2542 | 426.1358 | 225.567 | 315.7608 | 341.7826 | 326.0942 | 135.5917 | 101.846
1895.2542 | 425.6203 | 225.6885 | 316.7036 | 342.5775 | 326.3972 | 135.6663 | 101.9397
1896.2542 | 425.6804 | 225.8136 | 316.331 | 341.9331 | 325.7419 | 135.7539 | 102.0257
1897.2542 | 425.9121 | 225.9304 | 315.9436 | 341.3073 | 325.7278 | 135.8451 | 102.1133
1898.2542 | 425.4104 | 226.0643 | 315.7213 | 341.2555 | 325.2023 | 135.9249 | 102.1986
1899.2542 | 424.9266 | 226.1906 | 315.6863 | 341.6163 | 325.3827 | 136.0031 | 102.2908
1900.2542 | 424.1761 | 226.3175 | 315.7505 | 342.0492 | 326.0727 | 136.0883 | 102.3872
1901.2542 | 423.7852 | 226.4288 | 315.4065 | 341.7201 | 325.3004 | 136.1568 | 102.471
1902.2542 | 421.9494 | 226.5243 | 315.541 | 341.2698 | 325.179 | 136.2382 | 102.5442
1903.2542 | 421.6021 | 226.6006 | 315.5291 | 341.1208 | 325.5484 | 136.3074 | 102.6424
1904.2542 | 421.4408 | 226.7339 | 315.8778 | 340.5885 | 325.6855 | 136.3942 | 102.7045
1905.2542 | 421.9931 | 226.8572 | 315.8815 | 340.2181 | 324.7939 | 136.4594 | 102.8011
1906.2542 | 423.9502 | 226.9858 | 315.8696 | 340.4382 | 324.3306 | 136.5364 | 102.8924
1907.2542 | 425.7323 | 227.1077 | 315.0681 | 339.9314 | 323.7049 | 136.6125 | 102.9869
1908.2542 | 429.146 | 227.2549 | 315.5103 | 340.7994 | 323.2603 | 136.6741 | 103.0751
1909.2542 | 429.6998 | 227.373 | 315.0175 | 340.9955 | 323.4781 | 136.7452 | 103.1535
1910.2542 | 431.4393 | 227.4927 | 315.0073 | 340.6088 | 323.2816 | 136.8235 | 103.2499
1911.2542 | 435.538 | 227.6133 | 315.3113 | 339.8868 | 323.6085 | 136.8953 | 103.3204
1912.2542 | 435.7466 | 227.7371 | 315.1904 | 340.1534 | 324.4443 | 136.9761 | 103.4119
1913.2542 | 436.5107 | 227.8642 | 315.4209 | 341.0369 | 324.8572 | 137.0504 | 103.5078
1914.2542 | 436.8032 | 227.9779 | 315.5686 | 342.0025 | 325.1058 | 137.1264 | 103.5838
1915.2542 | 437.1207 | 228.0922 | 315.6481 | 342.6502 | 325.13 | 137.1989 | 103.6757
1916.2542 | 438.0501 | 228.2285 | 315.9906 | 343.3985 | 325.4483 | 137.2665 | 103.7635
1917.2542 | 437.4705 | 228.3469 | 316.4175 | 344.5822 | 324.6325 | 137.3372 | 103.8441
1918.2542 | 438.5487 | 228.4644 | 316.77 | 344.7826 | 323.9091 | 137.4196 | 103.9346
1919.2542 | 438.8464 | 228.5857 | 317.1949 | 344.7432 | 323.8926 | 137.4925 | 104.0044
1920.2542 | 439.672 | 228.7094 | 317.5054 | 344.6798 | 323.6388 | 137.5641 | 104.0935
1921.2542 | 439.5633 | 228.8388 | 317.6779 | 344.7783 | 323.5295 | 137.6378 | 104.1796
1922.2542 | 439.6151 | 228.9584 | 317.7385 | 344.1072 | 323.922 | 137.7145 | 104.2745
1923.2542 | 440.3623 | 228.9494 | 318.0387 | 344.571 | 323.6945 | 137.7818 | 104.3642
1924.2542 | 442.6013 | 229.0745 | 317.9601 | 344.7897 | 323.351 | 137.8659 | 104.4469
1925.2542 | 443.7621 | 229.1954 | 318.5453 | 344.8383 | 322.7886 | 137.9199 | 104.523
1926.2542 | 445.5763 | 229.3261 | 318.6961 | 345.3049 | 322.6572 | 137.997 | 104.6166
1927.2542 | 445.6931 | 229.4297 | 318.8437 | 345.3109 | 322.5989 | 138.0785 | 104.6966
1928.2542 | 444.9692 | 229.5712 | 319.1142 | 345.3536 | 322.3914 | 138.1646 | 104.7843
1929.2542 | 445.5722 | 229.6869 | 319.0094 | 345.058 | 324.0599 | 138.2396 | 104.8875
1930.2542 | 447.3343 | 229.8217 | 319.1471 | 345.1325 | 323.8164 | 138.3197 | 104.9706
1931.2542 | 448.065 | 229.9339 | 318.9427 | 345.2886 | 324.317 | 138.3886 | 105.0546
1932.2542 | 447.3638 | 230.067 | 318.7353 | 346.0786 | 324.3612 | 138.4685 | 105.1405
1933.2542 | 449.1694 | 230.183 | 318.4589 | 346.5436 | 324.0961 | 138.545 | 105.2186
1934.2542 | 449.591 | 230.2906 | 318.4813 | 347.1302 | 324.103 | 138.6199 | 105.3046
1935.2542 | 451.5817 | 230.4145 | 318.4399 | 347.2095 | 323.8728 | 138.6909 | 105.4062
1936.2542 | 451.1959 | 230.5337 | 318.6183 | 347.1285 | 324.0491 | 138.7737 | 105.4967
1937.2542 | 451.6017 | 230.6702 | 318.4662 | 347.9655 | 325.082 | 138.852 | 105.5868
1938.2542 | 452.2852 | 230.7799 | 318.7121 | 348.0344 | 324.4465 | 138.9286 | 105.6668
1939.2542 | 452.55 | 230.8901 | 319.1529 | 347.6358 | 325.1376 | 139.0201 | 105.7555
1940.2542 | 452.3638 | 231.0068 | 319.4477 | 347.1429 | 325.5164 | 139.0992 | 105.8348
1941.2542 | 453.7256 | 231.1283 | 319.4922 | 347.7654 | 325.9741 | 139.1759 | 105.9239
1942.2542 | 455.6259 | 231.245 | 319.4099 | 348.2963 | 325.8282 | 139.2491 | 106.0188
1943.2542 | 454.2396 | 231.3656 | 319.9015 | 348.4535 | 326.8011 | 139.3296 | 106.098
1944.2542 | 454.1625 | 231.4924 | 320.7585 | 349.9504 | 326.7598 | 139.4041 | 106.1908
1945.2542 | 451.4076 | 231.6063 | 320.5789 | 349.3103 | 327.0333 | 139.4805 | 106.2709
1946.2542 | 450.5433 | 231.7247 | 320.6819 | 349.2411 | 327.7326 | 139.5576 | 106.3707
1947.2542 | 450.6212 | 231.8407 | 320.4752 | 349.8484 | 328.419 | 139.6297 | 106.4544
1948.2542 | 450.8048 | 231.9604 | 320.8336 | 349.9904 | 328.0921 | 139.719 | 106.5444
1949.2542 | 449.9999 | 232.0643 | 320.9671 | 349.6696 | 327.8565 | 139.7915 | 106.6397
1950.2542 | 450.3275 | 232.1707 | 320.7805 | 349.6597 | 327.4068 | 139.8681 | 106.713
1951.2542 | 451.4123 | 232.2994 | 320.6633 | 350.1962 | 327.4038 | 139.9428 | 106.8115
1952.2542 | 451.9122 | 232.4246 | 321.0352 | 349.9135 | 327.4829 | 140.0152 | 106.9097
1953.2542 | 453.2574 | 232.5447 | 321.0643 | 350.5243 | 327.8583 | 140.0968 | 106.9612
1954.2542 | 454.8068 | 232.6642 | 321.0618 | 350.0385 | 328.689 | 140.1699 | 107.0471
1955.2542 | 452.2435 | 232.7888 | 321.0344 | 349.4743 | 329.3296 | 140.2519 | 107.1629
1956.2542 | 451.4549 | 232.8937 | 320.8887 | 349.872 | 329.8891 | 140.3219 | 107.2532
1957.2542 | 451.2882 | 233.0043 | 320.7052 | 349.9345 | 329.2989 | 140.3942 | 107.3476
1958.2542 | 449.9316 | 233.0951 | 320.8243 | 349.4292 | 328.7101 | 140.4653 | 107.4371
1959.2542 | 448.4651 | 233.2038 | 320.5788 | 349.4721 | 329.0292 | 140.5316 | 107.5246
1960.2542 | 448.1719 | 233.3299 | 320.709 | 349.941 | 328.8219 | 140.5984 | 107.6071
1961.2542 | 446.3782 | 233.4476 | 321.5301 | 349.9974 | 328.2432 | 140.6808 | 107.689
1962.2542 | 444.9432 | 233.5686 | 321.7054 | 349.6483 | 328.3363 | 140.7493 | 107.7433
1963.2542 | 445.7771 | 233.6711 | 321.9877 | 350.1871 | 327.8179 | 140.8415 | 107.8405
1964.2542 | 443.9514 | 233.7889 | 322.4124 | 350.3242 | 327.076 | 140.9175 | 107.9356
1965.2542 | 444.0703 | 233.9059 | 322.6637 | 350.5129 | 326.4644 | 140.9966 | 108.0239
1966.2542 | 443.1236 | 234.0103 | 322.8356 | 350.3999 | 325.9129 | 141.0618 | 108.0979
1967.2542 | 441.8909 | 234.1235 | 323.198 | 350.1177 | 326.2116 | 141.1381 | 108.2012
1968.2542 | 441.399 | 234.2327 | 322.6986 | 349.5893 | 325.9005 | 141.2145 | 108.2964
1969.2542 | 441.6843 | 234.3529 | 322.1704 | 348.7889 | 327.3253 | 141.2941 | 108.3987
1970.2542 | 440.2618 | 234.4309 | 322.6098 | 349.8428 | 327.4471 | 141.3739 | 108.4815
1971.2542 | 437.708 | 234.5391 | 323.1206 | 350.3136 | 327.7818 | 141.4483 | 108.5638
1972.2542 | 436.8916 | 234.6523 | 322.8426 | 350.3502 | 327.7777 | 141.5329 | 108.6543
1973.2542 | 436.0444 | 234.7529 | 323.2599 | 351.7809 | 327.2596 | 141.5917 | 108.7144
1974.2542 | 437.202 | 234.8721 | 323.645 | 351.8902 | 326.6371 | 141.6647 | 108.8109
1975.2542 | 435.7959 | 234.9724 | 324.0713 | 352.8557 | 328.4891 | 141.7324 | 108.8964
1976.2542 | 434.5563 | 235.0798 | 324.0253 | 352.8778 | 327.9664 | 141.8105 | 108.9904
1977.2542 | 436.1592 | 235.1894 | 323.8404 | 352.8672 | 327.4151 | 141.8824 | 109.077
1978.2542 | 436.3689 | 235.2898 | 324.321 | 352.8723 | 327.0478 | 141.9566 | 109.1413
1979.2542 | 436.4023 | 235.4048 | 323.8665 | 354.0103 | 327.0055 | 142.0325 | 109.2372
1980.2542 | 435.997 | 235.5175 | 323.9205 | 353.5715 | 327.1534 | 142.1065 | 109.3137
1981.2542 | 435.6718 | 235.6142 | 324.1401 | 353.7021 | 327.5886 | 142.1782 | 109.377
1982.2542 | 434.0814 | 235.7229 | 324.2629 | 354.4044 | 327.0058 | 142.2396 | 109.4591
1983.2542 | 433.047 | 235.8247 | 324.5955 | 354.1547 | 328.0609 | 142.3183 | 109.5327
1984.2542 | 433.207 | 235.9446 | 324.9257 | 355.6747 | 328.4031 | 142.3863 | 109.6002
1985.2542 | 432.66 | 236.0426 | 326.0217 | 355.4649 | 328.7767 | 142.4641 | 109.732
1986.2542 | 432.0796 | 236.1295 | 326.5346 | 355.2498 | 328.4688 | 142.5393 | 109.8202
1987.2542 | 430.4967 | 236.2317 | 326.0699 | 354.6523 | 328.9993 | 142.6062 | 109.8903
1988.2542 | 429.6417 | 236.3362 | 326.2451 | 354.974 | 329.4759 | 142.6629 | 109.9824
1989.2698 | 432.0323 | 236.4333 | 327.1163 | 354.3892 | 328.8322 | 142.7413 | 110.0576
1990.2542 | 431.142 | 236.5414 | 327.3084 | 354.3441 | 328.7599 | 142.813 | 110.147
1991.2542 | 427.7071 | 236.6412 | 327.183 | 354.0948 | 328.3121 | 142.882 | 110.2449
1992.2542 | 427.9684 | 236.7371 | 327.2457 | 353.7509 | 328.3723 | 142.9664 | 110.3253
1993.2542 | 428.586 | 236.84 | 327.5699 | 354.831 | 329.0807 | 143.0365 | 110.3816
1994.2542 | 430.9759 | 236.9425 | 327.5962 | 354.5456 | 329.1644 | 143.1134 | 110.4915
1995.2542 | 433.4087 | 237.038 | 327.5454 | 354.4649 | 330.5571 | 143.1799 | 110.5652
1996.2542 | 432.8295 | 237.1003 | 327.8917 | 355.1012 | 330.504 | 143.2492 | 110.6597
1997.2542 | 431.7465 | 237.1626 | 327.9244 | 355.1255 | 330.3825 | 143.316 | 110.7367
1998.2542 | 431.8072 | 237.2364 | 327.8172 | 354.9203 | 331.112 | 143.3985 | 110.8149
1999.2542 | 432.9571 | 237.3304 | 328.0772 | 355.3302 | 330.9768 | 143.4683 | 110.8995
2000.2542 | 433.3799 | 237.4326 | 328.8074 | 356.6156 | 331.0653 | 143.5415 | 110.982
2001.2542 | 432.8229 | 237.515 | 328.8208 | 357.3004 | 330.4964 | 143.6043 | 111.0429
2002.2542 | 432.4371 | 237.6196 | 329.0689 | 357.5882 | 331.4388 | 143.6863 | 111.1494
2003.2542 | 432.1667 | 237.7145 | 329.0388 | 357.7041 | 332.2018 | 143.7606 | 111.2309
2004.2542 | 432.9663 | 237.8089 | 328.9857 | 357.1464 | 331.7358 | 143.8299 | 111.3132
2005.2542 | 434.2355 | 237.8739 | 328.7208 | 356.561 | 331.5452 | 143.9014 | 111.3978
2006.2542 | 435.3169 | 237.9756 | 328.8631 | 357.0821 | 331.6916 | 143.9606 | 111.4817
2007.2542 | 436.4356 | 238.0418 | 328.8939 | 357.3256 | 331.0245 | 144.0482 | 111.5761
2008.2542 | 437.6251 | 238.1309 | 328.9021 | 358.1563 | 331.0232 | 144.112 | 111.6356
2009.2542 | 437.0322 | 238.2419 | 330.2054 | 359.4728 | 330.7357 | 144.1845 | 111.7073
2010.2542 | 436.3986 | 238.3431 | 330.8711 | 359.2962 | 330.9488 | 144.2659 | 111.8151
2011.2542 | 436.4007 | 238.4289 | 331.481 | 359.3768 | 331.0831 | 144.3536 | 111.8815
2012.2542 | 437.3533 | 238.518 | 331.685 | 359.4336 | 330.7244 | 144.4318 | 111.9598
2013.2542 | 437.1017 | 238.6084 | 332.8887 | 360.3014 | 330.3274 | 144.5063 | 112.0476
2014.2542 | 437.2702 | 238.6625 | 333.4021 | 359.5839 | 330.2664 | 144.5916 | 112.1335
2015.2542 | 439.1862 | 238.7769 | 333.5588 | 360.4071 | 330.6234 | 144.6673 | 112.2029
2016.2542 | 438.7485 | 238.8662 | 333.8402 | 360.7696 | 331.0368 | 144.7481 | 112.2961
2017.2542 | 439.1051 | 238.9564 | 333.5748 | 361.234 | 331.2962 | 144.8308 | 112.3818
2018.2542 | 440.0937 | 239.0562 | 333.7689 | 360.7066 | 331.3731 | 144.9071 | 112.4685
2019.2542 | 440.9868 | 239.1035 | 334.0713 | 360.4742 | 330.9831 | 144.9831 | 112.5462
2020.2542 | 440.4986 | 239.2054 | 334.5184 | 360.6139 | 330.5811 | 145.0612 | 112.642
2021.2542 | 439.5024 | 239.2935 | 333.676 | 360.1841 | 330.3518 | 145.1385 | 112.7128
2022.2542 | 439.1102 | 239.394 | 333.6511 | 360.4363 | 330.1927 | 145.2103 | 112.7918
2023.2542 | 439.1076 | 239.4903 | 334.5498 | 360.1651 | 330.4501 | 145.2819 | 112.8751
2024.2542 | 438.3023 | 239.5772 | 334.4434 | 360.1851 | 329.7409 | 145.3627 | 112.9566
2025.2542 | 438.2764 | 239.6713 | 334.4312 | 360.2502 | 329.2555 | 145.4304 | 113.0447
2026.2542 | 438.3083 | 239.7504 | 334.661 | 361.8298 | 329.4016 | 145.512 | 113.1307
2027.2542 | 437.124 | 239.8539 | 335.5624 | 362.6113 | 329.1512 | 145.579 | 113.2309
2028.2542 | 436.8779 | 239.9429 | 335.537 | 362.49 | 329.2489 | 145.6581 | 113.3091
2029.2542 | 436.4938 | 240.0291 | 336.3241 | 362.5922 | 329.4234 | 145.7229 | 113.3856
2030.2542 | 436.1591 | 240.0996 | 336.8828 | 362.6687 | 330.3022 | 145.7975 | 113.4744
2031.2542 | 442.7004 | 240.1886 | 336.8374 | 363.3399 | 330.7081 | 145.866 | 113.5646
2032.2542 | 441.3097 | 240.291 | 337.2121 | 363.8489 | 330.4551 | 145.9414 | 113.6374
2033.2542 | 439.9726 | 240.3851 | 337.9024 | 363.9665 | 330.395 | 146.0295 | 113.7141
2034.2542 | 437.9795 | 240.4682 | 337.8492 | 364.0315 | 330.2052 | 146.0938 | 113.7812
2035.2542 | 436.2524 | 240.5412 | 338.1915 | 365.0445 | 329.8831 | 146.184 | 113.8907
2036.2542 | 436.0815 | 240.6381 | 338.2149 | 364.4656 | 329.5338 | 146.2551 | 113.9655
2037.2542 | 434.9315 | 240.7193 | 337.9716 | 364.5153 | 329.5335 | 146.3285 | 114.0149
2038.2542 | 433.4818 | 240.8026 | 337.2459 | 364.6202 | 329.3871 | 146.403 | 114.1134
2039.2542 | 433.6625 | 240.8928 | 337.0935 | 365.1111 | 329.3389 | 146.4751 | 114.2136
2040.2542 | 434.2882 | 240.9687 | 337.5595 | 364.583 | 329.8115 | 146.5616 | 114.3155
2041.2542 | 433.3825 | 241.0531 | 338.5381 | 365.0082 | 329.6175 | 146.632 | 114.4015
2042.2542 | 432.6836 | 241.1026 | 338.114 | 364.4906 | 329.6338 | 146.7087 | 114.4668
2043.2542 | 431.6578 | 241.1941 | 338.0019 | 365.1374 | 329.5652 | 146.7769 | 114.5493
2044.2542 | 432.4259 | 241.2685 | 337.9705 | 364.461 | 329.9854 | 146.8527 | 114.6386
2045.2542 | 432.0207 | 241.3661 | 337.9912 | 364.3862 | 330.0461 | 146.9356 | 114.7127
2046.2542 | 434.5075 | 241.4641 | 337.811 | 365.7105 | 330.2386 | 147.0066 | 114.8046
2047.2542 | 434.5318 | 241.5587 | 339.1333 | 365.7366 | 330.6692 | 147.0778 | 114.9053
2048.2542 | 434.6754 | 241.6406 | 339.147 | 365.174 | 330.8101 | 147.1735 | 114.9862
2049.2542 | 434.8518 | 241.7196 | 338.712 | 365.9827 | 330.8331 | 147.2419 | 115.0568
2050.2542 | 435.8404 | 241.812 | 338.7349 | 366.8005 | 331.0883 | 147.3266 | 115.1419
2051.2542 | 435.5165 | 241.9097 | 338.7808 | 366.1873 | 330.9257 | 147.4044 | 115.2507
2052.2542 | 436.3234 | 242.0024 | 338.9017 | 366.0867 | 331.0901 | 147.4809 | 115.3133
2053.2542 | 436.2485 | 242.0942 | 339.1738 | 366.5832 | 331.3061 | 147.5542 | 115.3945
2054.2542 | 436.7276 | 242.1815 | 339.2764 | 367.0331 | 331.7092 | 147.6413 | 115.4875
2055.2542 | 437.6604 | 242.2584 | 340.0694 | 367.0812 | 332.1135 | 147.718 | 115.585
2056.2542 | 438.2453 | 242.3478 | 340.4085 | 367.987 | 332.5794 | 147.7935 | 115.6555
2057.2542 | 437.375 | 242.4299 | 341.0944 | 368.4754 | 332.5296 | 147.8685 | 115.7369
2058.2542 | 437.6953 | 242.5182 | 341.9017 | 368.4684 | 332.7337 | 147.944 | 115.8274
2059.2542 | 438.4197 | 242.6027 | 342.2015 | 368.8292 | 332.7675 | 148.0382 | 115.9105
2060.2542 | 436.8708 | 242.6859 | 343.0835 | 368.7143 | 332.628 | 148.121 | 115.9959
2061.2542 | 437.1406 | 242.7775 | 343.2137 | 368.6687 | 332.5138 | 148.2016 | 116.094
2062.2542 | 435.3392 | 242.8698 | 343.1759 | 369.0702 | 332.6505 | 148.285 | 116.1773
2063.2542 | 434.3562 | 242.9516 | 343.4857 | 370.6485 | 332.5469 | 148.36 | 116.252
2064.2542 | 434.0472 | 243.0401 | 343.5539 | 369.3767 | 332.4205 | 148.4429 | 116.343
2065.2542 | 433.5969 | 243.1275 | 343.3652 | 368.7506 | 332.424 | 148.5358 | 116.4279
2066.2542 | 433.45 | 243.222 | 342.9264 | 368.8648 | 332.311 | 148.6184 | 116.5037
2067.2542 | 434.6435 | 243.2828 | 342.6341 | 369.1671 | 332.2068 | 148.7052 | 116.5893
2068.2542 | 435.0512 | 243.3728 | 342.1802 | 369.4356 | 332.1143 | 148.7929 | 116.6835
2069.2542 | 435.581 | 243.4599 | 342.4882 | 369.1598 | 332.1118 | 148.8664 | 116.7694
2070.2542 | 435.6211 | 243.5493 | 342.0036 | 368.286 | 332.5305 | 148.9517 | 116.8591
2071.2542 | 434.6407 | 243.6453 | 342.4215 | 368.9851 | 332.334 | 149.0265 | 116.9474
2072.2542 | 433.8872 | 243.7186 | 342.5608 | 369.008 | 332.5148 | 149.108 | 117.0319
2073.2542 | 434.7438 | 243.7783 | 343.2197 | 368.3287 | 332.6211 | 149.1908 | 117.1008
2074.2542 | 434.1194 | 243.8564 | 343.057 | 368.9445 | 332.4781 | 149.2688 | 117.1937
2075.2542 | 434.9008 | 243.9343 | 343.8626 | 369.9379 | 332.337 | 149.35 | 117.2853
2076.2542 | 435.5206 | 244.0017 | 343.5138 | 369.5081 | 332.5764 | 149.4295 | 117.3634
2077.2542 | 434.5339 | 244.0953 | 343.7285 | 369.1186 | 333.1315 | 149.507 | 117.4741
2078.2542 | 435.1463 | 244.1378 | 343.5773 | 369.3079 | 333.1766 | 149.5798 | 117.5306
2079.2542 | 435.2506 | 244.2391 | 343.0426 | 369.8904 | 333.4459 | 149.6604 | 117.6324
2080.2542 | 435.5141 | 244.321 | 343.4639 | 370.2208 | 333.9656 | 149.7472 | 117.7135
2081.2542 | 435.9482 | 244.4081 | 343.7359 | 370.3722 | 334.0346 | 149.8375 | 117.7984
2082.2542 | 435.3236 | 244.5031 | 344.344 | 370.1378 | 334.3312 | 149.9119 | 117.8548
2083.2542 | 435.7187 | 244.593 | 343.5975 | 369.3436 | 334.6878 | 149.9933 | 117.9656
2084.2542 | 436.5511 | 244.6744 | 343.6764 | 369.6445 | 334.5995 | 150.0625 | 118.0276
2085.2542 | 437.1439 | 244.7676 | 343.7219 | 369.2249 | 335.1012 | 150.1583 | 118.1347
2086.2542 | 436.6676 | 244.8421 | 344.3233 | 369.5088 | 335.3415 | 150.2435 | 118.239
2087.2542 | 436.4045 | 244.9392 | 344.4767 | 369.4178 | 335.3822 | 150.322 | 118.3306
2088.2542 | 435.9302 | 245.0213 | 344.825 | 369.8542 | 335.6658 | 150.4083 | 118.4181
2089.2542 | 436.6223 | 245.1073 | 344.6732 | 370.5159 | 335.7518 | 150.482 | 118.5124
2090.2542 | 435.8121 | 245.1878 | 345.0049 | 370.6966 | 335.866 | 150.5688 | 118.5906
2091.2542 | 436.773 | 245.2507 | 345.8094 | 371.0711 | 336.1244 | 150.6472 | 118.6792
2092.2542 | 438.0592 | 245.3497 | 346.0352 | 370.2036 | 336.2553 | 150.7254 | 118.7661
2093.2542 | 438.8512 | 245.4396 | 346.258 | 370.4333 | 336.2254 | 150.8076 | 118.8416
2094.2542 | 438.5786 | 245.5504 | 346.0704 | 370.3563 | 336.7395 | 150.89 | 118.9347
2095.2542 | 437.9573 | 245.6452 | 345.9055 | 370.7381 | 337.044 | 150.972 | 119.0308
2096.2542 | 439.0617 | 245.7469 | 346.419 | 370.4721 | 337.3238 | 151.049 | 119.1014
2097.2542 | 440.2368 | 245.834 | 347.1571 | 369.5743 | 337.2556 | 151.1369 | 119.203
2098.2542 | 442.6247 | 245.9154 | 347.1242 | 369.3689 | 337.5492 | 151.2107 | 119.2962
2099.2542 | 444.1466 | 246.0181 | 347.7561 | 369.2132 | 338.1405 | 151.2764 | 119.3801
2100.2542 | 445.6722 | 246.0967 | 348.3712 | 370.0692 | 338.4138 | 151.363 | 119.4632
2101.2542 | 445.5542 | 246.1849 | 349.3973 | 371.6431 | 338.7945 | 151.444 | 119.5401
2102.2542 | 447.721 | 246.279 | 349.588 | 372.339 | 339.1455 | 151.4974 | 119.6234
2103.2542 | 447.7059 | 246.3685 | 350.535 | 373.4735 | 339.445 | 151.5749 | 119.7221
2104.2542 | 447.6344 | 246.4372 | 350.6565 | 373.3452 | 339.8373 | 151.671 | 119.8176
2105.2542 | 447.8945 | 246.5317 | 350.9065 | 373.4017 | 340.1204 | 151.7479 | 119.909
2106.2542 | 447.599 | 246.5873 | 351.0825 | 373.9769 | 340.5139 | 151.8271 | 119.9937
2107.2542 | 449.067 | 246.6867 | 350.6869 | 374.9519 | 341.1236 | 151.9089 | 120.0759
2108.2542 | 448.8737 | 246.775 | 351.0156 | 375.3014 | 341.3782 | 151.9911 | 120.1796
2109.2542 | 449.5395 | 246.8648 | 351.7035 | 376.4258 | 341.6269 | 152.0702 | 120.2903
2110.2542 | 450.2896 | 246.9478 | 351.7698 | 376.528 | 341.872 | 152.1639 | 120.3762
2111.2542 | 450.441 | 246.9941 | 352.2707 | 377.3662 | 342.0409 | 152.2413 | 120.4701
2112.2542 | 451.6394 | 247.0927 | 352.3772 | 378.408 | 342.1075 | 152.3264 | 120.5457
2113.2542 | 452.4226 | 247.1813 | 352.2399 | 378.9098 | 342.5719 | 152.4113 | 120.6462
2114.2542 | 452.2519 | 247.2818 | 352.6176 | 380.1022 | 343.2557 | 152.4953 | 120.7252
2115.2542 | 451.5045 | 247.3653 | 353.0018 | 381.0402 | 343.7382 | 152.5746 | 120.8119
2116.2542 | 451.3278 | 247.4484 | 353.3024 | 381.3389 | 344.2205 | 152.6611 | 120.8952
2117.2542 | 452.5161 | 247.5333 | 353.8328 | 381.4616 | 344.8671 | 152.7469 | 120.9877
2118.2542 | 453.6314 | 247.592 | 354.1731 | 382.7587 | 345.3058 | 152.8313 | 121.0657
2119.2542 | 454.2806 | 247.6672 | 355.3488 | 382.7472 | 345.4432 | 152.921 | 121.1871
2120.2542 | 454.4357 | 247.7583 | 355.7113 | 383.3713 | 345.5356 | 153.0076 | 121.2487
2121.2542 | 453.5626 | 247.8414 | 356.15 | 383.1476 | 345.5979 | 153.0959 | 121.3617
2122.2542 | 455.8693 | 247.9349 | 356.1542 | 382.8805 | 345.8202 | 153.1846 | 121.4325
2123.2542 | 458.5796 | 248.0238 | 355.9306 | 383.3555 | 345.9639 | 153.2623 | 121.4868
2124.2542 | 459.5895 | 248.1029 | 356.0183 | 384.1759 | 346.226 | 153.3494 | 121.5725
2125.2542 | 461.3084 | 248.1943 | 355.9332 | 384.001 | 346.3151 | 153.4403 | 121.6968
2126.2542 | 461.6283 | 248.2833 | 356.1187 | 385.3192 | 346.7763 | 153.5348 | 121.786
2127.2542 | 459.9434 | 248.3195 | 356.1514 | 384.732 | 346.8559 | 153.6129 | 121.8634
2128.2542 | 458.9094 | 248.421 | 356.2149 | 384.6219 | 347.2494 | 153.6967 | 121.9459
2129.2542 | 459.9885 | 248.4993 | 356.362 | 384.5444 | 347.4352 | 153.7927 | 122.0432
2130.2542 | 460.1559 | 248.5534 | 357.0096 | 385.8616 | 347.5711 | 153.8695 | 122.158
2131.2542 | 460.0723 | 248.6478 | 357.3204 | 385.5646 | 347.7827 | 153.9702 | 122.2634
2132.2542 | 457.7649 | 248.7378 | 357.4304 | 386.6381 | 348.0824 | 154.0623 | 122.3229
2133.2542 | 457.4295 | 248.8059 | 357.9354 | 387.0774 | 348.4838 | 154.1391 | 122.4217
2134.2542 | 455.3086 | 248.8849 | 358.1127 | 386.9979 | 348.7189 | 154.2365 | 122.5153
2135.2542 | 454.3783 | 248.9881 | 358.447 | 387.0172 | 349.1935 | 154.323 | 122.5932
2136.2542 | 451.0585 | 249.0675 | 358.8912 | 387.0934 | 349.3363 | 154.4152 | 122.6977
2137.2542 | 449.138 | 249.1375 | 359.116 | 386.3409 | 349.4291 | 154.4936 | 122.7948
2138.2542 | 448.6289 | 249.1918 | 359.4225 | 387.3563 | 349.7807 | 154.5856 | 122.8938
2139.2542 | 449.4951 | 249.2791 | 359.3193 | 386.3877 | 350.3026 | 154.6765 | 122.9601
2140.2542 | 451.4629 | 249.3593 | 359.8327 | 386.913 | 350.7794 | 154.7664 | 123.0769
2141.2542 | 452.7287 | 249.4449 | 360.1182 | 387.1328 | 350.9345 | 154.8475 | 123.1367
2142.2542 | 454.7151 | 249.5304 | 360.7564 | 388.0966 | 351.0612 | 154.9478 | 123.2525
2143.2542 | 455.4763 | 249.6166 | 361.3273 | 388.4056 | 351.7465 | 155.0385 | 123.34
2144.2542 | 456.8726 | 249.7023 | 361.8205 | 388.9646 | 351.945 | 155.1226 | 123.4137
2145.2542 | 457.2948 | 249.7751 | 362.1468 | 389.5779 | 352.4821 | 155.207 | 123.5164
2146.2542 | 456.5968 | 249.8481 | 362.7928 | 389.166 | 352.7237 | 155.3076 | 123.6106
2147.2542 | 457.8302 | 249.9177 | 362.8235 | 389.1892 | 353.0845 | 155.3883 | 123.6823
2148.2542 | 457.902 | 250.008 | 363.2715 | 389.8429 | 353.7091 | 155.4826 | 123.7691
2149.2542 | 458.5073 | 250.0764 | 362.9259 | 390.2498 | 354.39 | 155.571 | 123.8886
2150.2542 | 459.6396 | 250.1493 | 363.117 | 391.3006 | 354.6702 | 155.6652 | 123.9692
2151.2542 | 460.9244 | 250.2426 | 363.0357 | 391.0991 | 354.9939 | 155.7535 | 124.0642
2152.2542 | 461.3279 | 250.3224 | 363.4833 | 391.5123 | 355.191 | 155.8436 | 124.1506
2153.2542 | 460.851 | 250.402 | 364.0293 | 392.0541 | 355.5304 | 155.9259 | 124.2482
2154.2542 | 460.5045 | 250.4811 | 364.5647 | 392.9991 | 355.8682 | 156.0304 | 124.3787
2155.2542 | 462.243 | 250.5577 | 364.6642 | 392.2014 | 356.2163 | 156.1122 | 124.453
2156.2542 | 460.7233 | 250.6651 | 364.8185 | 393.6582 | 356.5754 | 156.2058 | 124.547
2157.2542 | 461.7129 | 250.747 | 364.5645 | 394.1751 | 357.4081 | 156.2994 | 124.6331
2158.2542 | 463.051 | 250.8296 | 364.877 | 394.4059 | 357.9166 | 156.4032 | 124.7202
2159.2542 | 464.065 | 250.9109 | 365.5441 | 396.6092 | 358.8118 | 156.4899 | 124.8015
2160.2542 | 464.9882 | 250.967 | 366.1283 | 396.5379 | 359.0993 | 156.5956 | 124.9022
2161.2542 | 465.8521 | 251.0433 | 366.0948 | 396.6752 | 359.4892 | 156.6912 | 124.9926
2162.2542 | 466.9634 | 251.1377 | 366.4684 | 396.8804 | 360.1321 | 156.7785 | 125.0823
2163.2542 | 468.601 | 251.2244 | 367.0016 | 396.3876 | 360.2947 | 156.8797 | 125.1822
2164.2542 | 469.4031 | 251.3061 | 367.4597 | 397.4705 | 360.9529 | 156.9745 | 125.267
2165.2542 | 469.0306 | 251.3847 | 367.81 | 397.6081 | 361.8163 | 157.0675 | 125.3698
2166.2542 | 469.6903 | 251.4827 | 367.7592 | 397.5064 | 362.0309 | 157.1747 | 125.4913
2167.2542 | 469.8997 | 251.5681 | 368.1501 | 399.3004 | 363.0852 | 157.265 | 125.5836
2168.2542 | 471.009 | 251.6682 | 368.7682 | 398.9818 | 363.3199 | 157.37 | 125.6615
2169.2542 | 471.14 | 251.7263 | 368.7615 | 398.4506 | 363.565 | 157.4702 | 125.7464
2170.2542 | 470.9411 | 251.8072 | 369.3712 | 398.1634 | 363.7607 | 157.5606 | 125.8308
2171.2542 | 472.6179 | 251.8951 | 369.5864 | 399.5125 | 364.0061 | 157.6518 | 125.9515
2172.2542 | 472.9583 | 251.9782 | 369.936 | 399.3092 | 364.3015 | 157.7659 | 126.0675
2173.2542 | 474.495 | 252.0678 | 370.7774 | 400.5239 | 364.3823 | 157.8526 | 126.1421
2174.2542 | 474.2503 | 252.1515 | 371.0994 | 400.6593 | 364.4132 | 157.9521 | 126.2243
2175.2542 | 475.0171 | 252.2115 | 371.1237 | 400.9887 | 364.7685 | 158.0527 | 126.3269
2176.2542 | 475.9743 | 252.3078 | 371.1605 | 401.9872 | 365.3413 | 158.1548 | 126.4135
2177.2542 | 476.1888 | 252.3764 | 371.6204 | 403.6917 | 366.0553 | 158.2586 | 126.4916
2178.2542 | 476.2494 | 252.4348 | 372.0025 | 403.888 | 366.5438 | 158.358 | 126.5947
2179.2542 | 477.0972 | 252.5181 | 372.4305 | 404.0103 | 366.9507 | 158.4474 | 126.669
2180.2542 | 479.1567 | 252.5778 | 373.3209 | 405.1582 | 367.2084 | 158.5646 | 126.8013
2181.2542 | 478.8212 | 252.6097 | 373.7535 | 405.1435 | 367.4561 | 158.6596 | 126.8849
2182.2542 | 480.2397 | 252.6557 | 373.592 | 404.3046 | 367.4551 | 158.7567 | 126.982
2183.2542 | 483.9287 | 252.756 | 374.328 | 406.5948 | 367.8692 | 158.8506 | 127.0703
2184.2542 | 485.7722 | 252.8554 | 374.673 | 406.0802 | 368.6669 | 158.9543 | 127.1495
2185.2542 | 485.9153 | 252.9597 | 374.7817 | 405.4028 | 369.2835 | 159.0515 | 127.2615
2186.2542 | 485.9595 | 253.0684 | 375.9069 | 408.3469 | 369.5768 | 159.1469 | 127.3595
2187.2542 | 485.6179 | 253.1148 | 375.7561 | 408.8075 | 370.2087 | 159.2458 | 127.4618
2188.2542 | 487.0735 | 253.1978 | 376.4355 | 408.5089 | 370.5475 | 159.3488 | 127.5662
2189.2542 | 488.8101 | 253.1985 | 377.1266 | 408.7144 | 371.1627 | 159.4334 | 127.6545
2190.2542 | 492.7678 | 253.296 | 377.7451 | 410.0148 | 371.9332 | 159.5448 | 127.7589
2191.2542 | 493.2487 | 253.3873 | 378.7565 | 410.2958 | 372.5067 | 159.5981 | 127.8544
2192.2542 | 491.8389 | 253.4691 | 380.3996 | 411.3001 | 372.8535 | 159.7106 | 127.9538
2193.2542 | 493.0901 | 253.578 | 380.6395 | 411.7685 | 373.0929 | 159.8084 | 128.0539
2194.2542 | 499.0181 | 253.6709 | 380.9589 | 413.0629 | 373.2786 | 159.9141 | 128.1403
2195.2542 | 499.3145 | 253.7722 | 381.03 | 411.915 | 373.3042 | 160.0158 | 128.2457
2196.2542 | 500.0208 | 253.8596 | 381.7215 | 411.3037 | 373.4917 | 160.1164 | 128.3405
2197.2542 | 499.4366 | 253.9481 | 382.0788 | 411.9841 | 373.7614 | 160.2201 | 128.4415
2198.2542 | 497.9857 | 254.0415 | 382.2964 | 412.0058 | 373.8304 | 160.3218 | 128.5612
2199.2542 | 495.8768 | 254.1179 | 382.5296 | 412.8981 | 373.9572 | 160.427 | 128.6871
2200.2542 | 496.8491 | 254.183 | 382.5476 | 412.3585 | 374.0899 | 160.5264 | 128.772
2201.2542 | 497.5463 | 254.2415 | 383.1112 | 413.5719 | 374.1321 | 160.6293 | 128.8578
2202.2542 | 498.9581 | 254.3106 | 383.1933 | 413.0414 | 374.0403 | 160.7368 | 128.9486
2203.2542 | 498.1045 | 254.4447 | 383.5087 | 414.7943 | 373.9915 | 160.8343 | 129.0379
2204.2542 | 496.9093 | 254.5662 | 383.6277 | 413.7284 | 373.8309 | 160.9396 | 129.1321
2205.2542 | 495.7074 | 254.6687 | 383.4933 | 412.5331 | 374.0239 | 161.0359 | 129.217
2206.2542 | 494.8352 | 254.7553 | 383.4322 | 411.6951 | 373.8545 | 161.142 | 129.3205
2207.2542 | 494.317 | 254.8552 | 384.6091 | 411.7722 | 373.6769 | 161.2438 | 129.43
2208.2542 | 493.48 | 254.8854 | 384.4365 | 410.9821 | 373.3981 | 161.342 | 129.5348
2209.2542 | 495.6919 | 254.9826 | 384.7239 | 410.9761 | 373.3866 | 161.4415 | 129.6366
2210.2542 | 498.2942 | 254.8648 | 385.3706 | 411.1553 | 374.0296 | 161.5386 | 129.7317
2211.2542 | 500.6203 | 254.9531 | 386.6241 | 411.2258 | 374.0726 | 161.6313 | 129.8332
2212.2542 | 501.2438 | 255.0544 | 386.7559 | 411.3791 | 374.0852 | 161.7414 | 129.9586
2213.2542 | 500.8378 | 255.1205 | 386.9909 | 411.3519 | 374.0123 | 161.834 | 130.0493
2214.2542 | 500.273 | 255.2418 | 387.6095 | 411.9669 | 374.0029 | 161.9152 | 130.1341
2215.2542 | 500.8304 | 255.3142 | 388.2811 | 412.2046 | 374.052 | 162.0171 | 130.2381
2216.2542 | 500.7994 | 255.4199 | 388.9502 | 412.5546 | 374.0775 | 162.12 | 130.3293
2217.2542 | 500.0384 | 255.437 | 390.1424 | 413.7084 | 374.3388 | 162.209 | 130.4593
2218.2542 | 500.2424 | 255.5434 | 390.5326 | 414.1684 | 374.3805 | 162.3098 | 130.5404
2219.2542 | 503.2484 | 255.6451 | 390.4753 | 414.8312 | 374.659 | 162.3982 | 130.6267
2220.2542 | 503.3175 | 255.7202 | 391.3783 | 414.824 | 374.7173 | 162.4963 | 130.7602
2221.2542 | 503.1508 | 255.7841 | 392.1352 | 417.5089 | 374.9868 | 162.5924 | 130.849
2222.2542 | 503.7296 | 255.8773 | 392.7725 | 417.6462 | 375.3793 | 162.6907 | 130.9535
2223.2542 | 502.3333 | 255.985 | 393.1695 | 418.5457 | 375.8057 | 162.7843 | 131.0369
2224.2542 | 503.1651 | 256.0687 | 393.6594 | 419.2549 | 376.1418 | 162.8612 | 131.1275
2225.2542 | 502.4002 | 256.1717 | 393.9916 | 419.0752 | 376.2542 | 162.9629 | 131.2347
2226.2542 | 502.1278 | 256.2568 | 393.7914 | 418.7098 | 376.4818 | 163.0644 | 131.3506
2227.2542 | 504.3016 | 256.3592 | 393.5762 | 418.1898 | 377.0593 | 163.167 | 131.4553
2228.2542 | 503.9254 | 256.4346 | 393.9116 | 417.3789 | 377.2018 | 163.2622 | 131.5326
2229.2542 | 501.8917 | 256.4879 | 394.6197 | 416.4944 | 377.6922 | 163.356 | 131.6408
2230.2542 | 500.857 | 256.5627 | 394.2405 | 417.6389 | 378.0474 | 163.4332 | 131.757
2231.2542 | 500.254 | 256.6681 | 394.333 | 417.27 | 378.2335 | 163.5303 | 131.8619
2232.2542 | 500.0423 | 256.7625 | 394.4138 | 417.3728 | 378.2318 | 163.6339 | 131.9463
2233.2542 | 500.2797 | 256.8504 | 395.0359 | 418.0905 | 378.4299 | 163.7307 | 132.0675
2234.2542 | 501.4302 | 256.9422 | 395.408 | 418.2226 | 378.6758 | 163.8254 | 132.1705
2235.2542 | 503.3125 | 257.0317 | 395.9625 | 420.1602 | 379.0117 | 163.926 | 132.2649
2236.2542 | 505.2904 | 257.1027 | 395.9288 | 419.8907 | 379.4163 | 164.0292 | 132.3628
2237.2542 | 507.1814 | 257.2046 | 396.3743 | 419.6904 | 379.6474 | 164.1265 | 132.464
2238.2542 | 507.9952 | 257.2978 | 396.9168 | 419.2725 | 379.9384 | 164.2264 | 132.5837
2239.2542 | 507.6299 | 257.393 | 396.8456 | 419.7373 | 380.2909 | 164.3226 | 132.6836
2240.2542 | 508.7184 | 257.4519 | 397.0444 | 421.0738 | 380.4916 | 164.4183 | 132.7801
2241.2542 | 507.855 | 257.5334 | 397.0208 | 421.6635 | 380.825 | 164.518 | 132.8792
2242.2542 | 509.0785 | 257.6034 | 397.5026 | 422.0003 | 381.1061 | 164.6119 | 132.9804
2243.2542 | 510.4424 | 257.7063 | 398.3709 | 423.3367 | 381.6441 | 164.7228 | 133.0965
2244.2542 | 510.6212 | 257.7915 | 398.5767 | 422.9837 | 382.0047 | 164.8272 | 133.1929
2245.2542 | 509.9121 | 257.8532 | 398.8137 | 423.6225 | 382.6919 | 164.9234 | 133.2912
2246.2542 | 509.6786 | 257.9094 | 398.7665 | 423.123 | 383.0463 | 165.028 | 133.4048
2247.2542 | 508.5859 | 257.9825 | 398.7438 | 424.043 | 383.3539 | 165.1229 | 133.5068
2248.2542 | 508.2145 | 258.0505 | 398.6572 | 422.542 | 383.5031 | 165.2317 | 133.6066
2249.2542 | 509.5536 | 258.1496 | 398.7467 | 423.8712 | 383.5079 | 165.3279 | 133.7265
2250.2542 | 509.3283 | 258.2543 | 399.182 | 423.7542 | 384.0675 | 165.4408 | 133.8154
2251.2542 | 510.5801 | 258.3465 | 399.1654 | 423.6375 | 384.1156 | 165.5478 | 133.9345
2252.2542 | 511.0507 | 258.4339 | 399.884 | 424.0427 | 384.063 | 165.6485 | 134.0142
2253.2542 | 509.8786 | 258.5269 | 399.598 | 424.7869 | 384.1756 | 165.757 | 134.1096
2254.2542 | 510.0381 | 258.6218 | 399.7823 | 424.0574 | 384.4133 | 165.8569 | 134.1981
2255.2542 | 511.2175 | 258.6756 | 400.0375 | 424.3233 | 384.5224 | 165.9652 | 134.3103
2256.2542 | 513.2965 | 258.7672 | 400.2717 | 424.3523 | 385.1919 | 166.0662 | 134.406
2257.2542 | 511.8411 | 258.8483 | 400.4626 | 424.8402 | 385.3426 | 166.1785 | 134.5338
2258.2542 | 509.2418 | 258.931 | 400.8673 | 424.4028 | 385.7423 | 166.2827 | 134.6511
2259.2542 | 507.9668 | 258.976 | 400.6668 | 424.6972 | 386.1435 | 166.3777 | 134.7397
2260.2542 | 507.4918 | 259.0506 | 400.6675 | 424.8975 | 386.2604 | 166.4878 | 134.8414
2261.2542 | 506.4149 | 259.1296 | 401.3991 | 426.7415 | 386.7527 | 166.5893 | 134.9412
2262.2542 | 505.8064 | 259.1946 | 401.8129 | 427.017 | 386.8994 | 166.6736 | 135.039
2263.2542 | 504.5199 | 259.2782 | 402.0822 | 426.9373 | 387.0638 | 166.7843 | 135.1592
2264.2542 | 503.9601 | 259.3893 | 403.2537 | 426.748 | 387.0264 | 166.8855 | 135.2855
2265.2542 | 504.9907 | 259.5007 | 404.953 | 427.543 | 387.0948 | 166.9851 | 135.3857
2266.2542 | 505.3932 | 259.6069 | 405.9122 | 427.0884 | 387.1281 | 167.0914 | 135.4903
2267.2542 | 504.6431 | 259.7257 | 406.1657 | 426.2166 | 387.206 | 167.1874 | 135.5922
2268.2542 | 505.0119 | 259.7972 | 406.2791 | 426.2573 | 387.2889 | 167.2878 | 135.6769
2269.2542 | 505.1474 | 259.6947 | 406.0685 | 426.3757 | 387.4418 | 167.3861 | 135.7854
2270.2542 | 506.6442 | 259.7675 | 406.9955 | 425.635 | 387.4849 | 167.5001 | 135.9037
2271.2542 | 508.3151 | 259.8983 | 407.2495 | 426.6893 | 387.525 | 167.5929 | 136.0167
2272.2542 | 507.9036 | 260.0544 | 407.9118 | 428.1021 | 387.8165 | 167.6982 | 136.1315
2273.2542 | 507.542 | 260.021 | 407.4051 | 427.1377 | 388.1909 | 167.7867 | 136.223
2274.2542 | 510.8363 | 260.158 | 407.8352 | 426.5812 | 388.5125 | 167.8853 | 136.336
2275.2542 | 511.0886 | 260.0804 | 407.9441 | 427.69 | 388.9486 | 167.9819 | 136.4305
2276.2542 | 510.903 | 260.2016 | 408.6942 | 428.6491 | 389.0341 | 168.0889 | 136.5388
2277.2542 | 511.9052 | 260.3186 | 408.9746 | 429.7166 | 389.3795 | 168.1911 | 136.665
2278.2542 | 511.7153 | 260.2678 | 409.4502 | 431.1643 | 389.8035 | 168.2889 | 136.7628
2279.2542 | 512.666 | 260.321 | 409.6176 | 430.8447 | 390.0237 | 168.3925 | 136.8744
2280.2542 | 511.2133 | 260.417 | 409.9338 | 431.8584 | 390.1681 | 168.5009 | 136.9806
2281.2542 | 513.0295 | 260.5187 | 410.4514 | 432.3926 | 390.2138 | 168.5921 | 137.0919
2282.2542 | 513.4882 | 260.6054 | 411.1672 | 432.5485 | 390.3195 | 168.6856 | 137.192
2283.2542 | 515.9468 | 260.698 | 411.4397 | 433.1725 | 390.4978 | 168.8006 | 137.2794
2284.2542 | 518.2928 | 260.7905 | 412.1937 | 433.7519 | 390.7458 | 168.9005 | 137.3922
2285.2542 | 519.8647 | 260.8794 | 412.9061 | 434.269 | 390.9528 | 169.007 | 137.5076
2286.2542 | 522.3801 | 260.9581 | 413.6905 | 434.5759 | 390.9382 | 169.1066 | 137.6118
2287.2542 | 522.9062 | 261.0558 | 415.0283 | 434.9573 | 391.3066 | 169.2051 | 137.7139
2288.2542 | 525.5604 | 261.1415 | 415.1849 | 436.7247 | 391.7327 | 169.3157 | 137.8211
2289.2542 | 524.8848 | 261.2307 | 415.5973 | 437.3819 | 392.4295 | 169.4173 | 137.9184
2290.2542 | 523.4117 | 261.3264 | 416.4334 | 437.4045 | 392.891 | 169.5186 | 138.0243
2291.2542 | 523.8643 | 261.427 | 416.2167 | 437.5508 | 393.5452 | 169.6222 | 138.1279
2292.2542 | 527.5317 | 261.5854 | 416.8298 | 438.2411 | 393.9653 | 169.7349 | 138.2415
2293.2542 | 528.7525 | 261.7937 | 417.996 | 439.3084 | 394.3183 | 169.8405 | 138.3654
2294.2542 | 526.561 | 261.9426 | 418.678 | 439.4935 | 395.1512 | 169.9439 | 138.4507
2295.2542 | 525.1541 | 262.0408 | 418.7066 | 440.7554 | 395.2665 | 170.0509 | 138.5546
2296.2542 | 524.9773 | 262.1438 | 418.7229 | 440.5088 | 395.4832 | 170.1622 | 138.6612
2297.2542 | 526.3874 | 262.1742 | 419.0572 | 440.3814 | 395.6643 | 170.2667 | 138.772
2298.2542 | 526.0353 | 262.2858 | 419.0316 | 441.9637 | 395.6988 | 170.3721 | 138.8855
2299.2542 | 529.3678 | 262.1436 | 418.8639 | 441.4656 | 395.9052 | 170.4772 | 139.0087
2300.2542 | 533.5838 | 262.2443 | 418.9933 | 441.9737 | 396.3586 | 170.5884 | 139.1045
2301.2542 | 534.8913 | 262.3395 | 419.2768 | 442.2577 | 396.8944 | 170.6999 | 139.2078
2302.2542 | 536.9806 | 262.4306 | 419.8254 | 442.5721 | 397.1615 | 170.8116 | 139.3136
2303.2542 | 539.4765 | 262.528 | 420.3476 | 442.7458 | 397.167 | 170.9163 | 139.4363
2304.2542 | 538.9972 | 262.6198 | 420.7404 | 442.6815 | 397.2058 | 171.0245 | 139.548
2305.2542 | 537.3001 | 262.7145 | 420.5861 | 443.4044 | 397.4239 | 171.1379 | 139.6576
2306.2542 | 538.1396 | 262.8062 | 420.4273 | 443.5121 | 397.8559 | 171.2498 | 139.7593
2307.2542 | 537.7733 | 262.8943 | 420.4898 | 442.5296 | 398.0384 | 171.3567 | 139.8634
2308.2542 | 538.7509 | 262.9853 | 420.4938 | 442.1766 | 398.3118 | 171.4612 | 139.9767
2309.2542 | 539.6151 | 263.097 | 420.587 | 442.651 | 398.5696 | 171.582 | 140.0726
2310.2542 | 538.9453 | 263.1911 | 420.6935 | 441.7554 | 398.6199 | 171.69 | 140.1856
2311.2542 | 537.9792 | 263.2805 | 420.3408 | 441.7535 | 398.5936 | 171.8047 | 140.3026
2312.2542 | 536.4261 | 263.3781 | 420.5207 | 441.7022 | 398.6861 | 171.9193 | 140.4118
2313.2542 | 537.8545 | 263.4782 | 420.5363 | 442.6157 | 398.8552 | 172.0302 | 140.5215
2314.2542 | 537.794 | 263.565 | 421.0086 | 442.7611 | 399.3256 | 172.1418 | 140.6263
2315.2542 | 538.4183 | 263.6709 | 421.8779 | 444.0904 | 399.7262 | 172.2563 | 140.737
2316.2542 | 540.4216 | 263.7744 | 421.9423 | 443.8552 | 400.2816 | 172.3679 | 140.8399
2317.2542 | 538.1029 | 263.8783 | 422.4777 | 443.5768 | 400.4209 | 172.4858 | 140.9547
2318.2542 | 537.2302 | 263.9914 | 422.6476 | 443.4686 | 400.5208 | 172.5953 | 141.0678
2319.2542 | 536.1811 | 264.131 | 422.9767 | 444.1868 | 400.813 | 172.7154 | 141.1769
2320.2542 | 536.1097 | 264.2625 | 423.4382 | 444.6507 | 400.9299 | 172.8377 | 141.2749
2321.2542 | 536.7638 | 264.3131 | 424.1176 | 444.7801 | 401.8201 | 172.9579 | 141.3778
2322.2542 | 537.8724 | 264.3542 | 424.4337 | 445.6471 | 402.1568 | 173.0737 | 141.4995
2323.2542 | 536.3219 | 264.4602 | 424.4726 | 447.2973 | 402.2728 | 173.1959 | 141.607
2324.2542 | 535.4578 | 264.5562 | 424.5381 | 449.1782 | 402.6057 | 173.3073 | 141.7137
2325.2542 | 535.5646 | 264.6553 | 424.8768 | 449.6469 | 402.8592 | 173.4251 | 141.8269
2326.2542 | 534.8447 | 264.7632 | 424.9822 | 450.3251 | 402.7646 | 173.5427 | 141.9352
2327.2542 | 532.1641 | 264.8724 | 425.4114 | 451.0323 | 402.7913 | 173.6644 | 142.0354
2328.2542 | 531.4968 | 264.9682 | 425.4007 | 451.2567 | 403.0055 | 173.7821 | 142.1417
2329.2542 | 530.6234 | 265.0961 | 425.4423 | 450.6733 | 403.332 | 173.901 | 142.2626
2330.2542 | 531.9346 | 265.1843 | 424.8713 | 449.8167 | 403.4823 | 174.0099 | 142.3626
2331.2542 | 533.5118 | 265.2976 | 425.7392 | 449.005 | 403.5392 | 174.1394 | 142.4658
2332.2542 | 533.0843 | 265.411 | 426.103 | 451.129 | 403.9739 | 174.2582 | 142.565
2333.2542 | 532.3467 | 265.5152 | 426.9724 | 450.7855 | 404.4257 | 174.3834 | 142.6659
2334.2542 | 531.6707 | 265.619 | 427.5003 | 450.9217 | 404.5527 | 174.4896 | 142.7627
2335.2542 | 532.4743 | 265.7247 | 427.4323 | 451.4612 | 405.1006 | 174.6148 | 142.8867
2336.2542 | 535.6595 | 265.8168 | 427.3879 | 452.1487 | 405.5937 | 174.7351 | 142.9993
2337.2542 | 537.8866 | 265.924 | 427.4138 | 450.6418 | 405.7148 | 174.8496 | 143.1079
2338.2542 | 537.8036 | 266.0339 | 427.8927 | 451.7093 | 406.2599 | 174.9763 | 143.2182
2339.2542 | 536.7077 | 266.1386 | 428.4498 | 451.9678 | 406.8614 | 175.0985 | 143.3378
2340.2542 | 536.4696 | 266.2375 | 429.2898 | 451.5034 | 407.1071 | 175.227 | 143.4327
2341.2542 | 538.7967 | 266.3494 | 429.9034 | 451.3789 | 407.4061 | 175.3488 | 143.5333
2342.2542 | 539.2388 | 266.4842 | 430.5501 | 451.9232 | 407.6974 | 175.4718 | 143.6448
2343.2542 | 539.0605 | 266.6168 | 431.5841 | 453.1615 | 408.4069 | 175.6007 | 143.7589
2344.2542 | 537.0625 | 266.7169 | 432.0561 | 452.8845 | 408.8275 | 175.7297 | 143.857
2345.2542 | 536.0648 | 266.8316 | 431.7446 | 453.6365 | 409.4053 | 175.8498 | 143.9755
2346.2542 | 538.6442 | 266.9411 | 432.14 | 453.717 | 409.8744 | 175.9792 | 144.0827
2347.2542 | 542.0556 | 267.0659 | 433.3218 | 454.682 | 410.3323 | 176.1152 | 144.1909
2348.2542 | 543.0919 | 267.18 | 433.421 | 454.4144 | 410.6403 | 176.2574 | 144.3077
2349.2542 | 543.6909 | 267.2907 | 433.5084 | 455.1315 | 410.9234 | 176.4025 | 144.4047
2350.2542 | 545.7065 | 267.3978 | 433.3271 | 456.1755 | 411.1745 | 176.5452 | 144.5205
2351.2542 | 542.5004 | 267.5241 | 433.937 | 456.1172 | 411.5086 | 176.6872 | 144.6279
2352.2542 | 542.1068 | 267.632 | 433.4562 | 456.3677 | 411.7836 | 176.8284 | 144.7354
2353.2542 | 542.5182 | 267.7248 | 433.4446 | 455.5821 | 412.3557 | 176.955 | 144.8453
2354.2542 | 542.7972 | 267.8413 | 433.6828 | 456.3958 | 412.2385 | 177.1073 | 144.9716
2355.2542 | 542.9691 | 267.9772 | 434.0915 | 456.1576 | 412.3646 | 177.2479 | 145.066
2356.2542 | 543.2963 | 268.0793 | 434.4101 | 455.5185 | 412.2637 | 177.3888 | 145.1737
2357.2542 | 542.953 | 268.2053 | 434.6013 | 455.4515 | 412.2708 | 177.542 | 145.3022
2358.2542 | 542.354 | 268.3322 | 434.9867 | 456.4615 | 412.5751 | 177.6846 | 145.4014
2359.2542 | 542.9239 | 268.4312 | 435.1707 | 456.8325 | 412.8679 | 177.819 | 145.5057
2360.2542 | 543.2161 | 268.5541 | 436.253 | 456.8649 | 412.9784 | 177.9579 | 145.6075
2361.2542 | 542.9388 | 268.6724 | 436.4535 | 457.0179 | 413.0108 | 178.1007 | 145.719
2362.2542 | 543.6248 | 268.7691 | 436.5237 | 456.2369 | 412.9761 | 178.2509 | 145.8177
2363.2542 | 545.0326 | 268.8998 | 437.0462 | 457.6466 | 412.9901 | 178.3952 | 145.9378
2364.2542 | 543.4176 | 269.0207 | 437.3734 | 458.1558 | 412.922 | 178.5407 | 146.044
2365.2542 | 542.7003 | 269.1402 | 437.2292 | 459.3628 | 413.1411 | 178.6799 | 146.1492
2366.2542 | 540.8627 | 269.2765 | 437.2908 | 458.6675 | 413.2425 | 178.8248 | 146.2589
2367.2542 | 540.6969 | 269.3738 | 436.697 | 459.5892 | 413.2159 | 178.9665 | 146.3633
2368.2542 | 543.6074 | 269.4185 | 436.6895 | 458.8441 | 413.3044 | 179.1079 | 146.4724
2369.2542 | 543.8501 | 269.538 | 436.6899 | 459.0374 | 413.3898 | 179.2489 | 146.5803
2370.2542 | 543.2662 | 269.6782 | 436.4844 | 459.2114 | 413.2685 | 179.3868 | 146.7104
2371.2542 | 544.2211 | 269.8009 | 436.7858 | 459.4883 | 413.7214 | 179.5248 | 146.8231
2372.2542 | 546.3573 | 269.9307 | 437.3239 | 460.7166 | 413.9874 | 179.6657 | 146.9294
2373.2542 | 546.6064 | 270.0525 | 438.8647 | 461.4026 | 414.2054 | 179.8009 | 147.0363
2374.2542 | 544.6916 | 270.1607 | 439.4672 | 461.2858 | 414.3811 | 179.9416 | 147.1308
2375.2542 | 543.3714 | 270.2699 | 439.8404 | 461.436 | 414.4979 | 180.0851 | 147.2225
2376.2542 | 542.2613 | 270.3443 | 440.5201 | 461.6489 | 414.7682 | 180.2223 | 147.3472
2377.2542 | 541.9504 | 270.4145 | 440.6008 | 461.7275 | 414.9785 | 180.3621 | 147.4684
2378.2542 | 542.51 | 270.5097 | 441.3107 | 462.2689 | 415.451 | 180.4957 | 147.5755
2379.2542 | 543.8667 | 270.6565 | 442.0381 | 463.3957 | 415.8365 | 180.632 | 147.6843
2380.2542 | 545.1113 | 270.7863 | 442.451 | 463.187 | 416.0185 | 180.76 | 147.7956
2381.2542 | 544.9872 | 270.9149 | 442.2533 | 462.7053 | 416.204 | 180.8918 | 147.9138
2382.2542 | 543.3533 | 271.058 | 442.5851 | 462.3559 | 416.2285 | 181.0373 | 148.0221
2383.2542 | 542.7968 | 271.1784 | 442.4359 | 462.9142 | 416.0439 | 181.1683 | 148.1374
2384.2542 | 541.0642 | 271.344 | 442.5292 | 462.0355 | 415.9438 | 181.3009 | 148.2517
2385.2542 | 542.659 | 271.4694 | 442.7371 | 463.2587 | 415.8738 | 181.4337 | 148.3527
2386.2542 | 544.0668 | 271.5762 | 443.5544 | 462.4753 | 415.9168 | 181.5721 | 148.4613
2387.2542 | 544.4299 | 271.7064 | 443.7176 | 462.0733 | 416.163 | 181.6988 | 148.5702
2388.2542 | 544.7015 | 271.8124 | 444.3656 | 461.6531 | 416.3257 | 181.8325 | 148.6799
2389.2542 | 543.4358 | 271.946 | 444.5966 | 461.2735 | 416.3586 | 181.9688 | 148.787
2390.2542 | 543.2818 | 272.0788 | 445.032 | 460.9995 | 416.2965 | 182.1083 | 148.8832
2391.2542 | 545.7226 | 272.1779 | 445.5844 | 461.842 | 416.4276 | 182.2369 | 149.0082
2392.2542 | 547.5244 | 272.3154 | 445.7297 | 462.4415 | 416.4316 | 182.3728 | 149.1194
2393.2542 | 548.5689 | 272.4511 | 445.874 | 462.0586 | 416.4222 | 182.5075 | 149.2424
2394.2542 | 553.415 | 272.554 | 445.974 | 462.4914 | 416.4186 | 182.6387 | 149.3497
2395.2542 | 553.3002 | 272.674 | 446.4734 | 462.9442 | 416.6218 | 182.7537 | 149.4633
2396.2542 | 555.6387 | 272.7963 | 446.9071 | 464.4417 | 416.8763 | 182.891 | 149.5734
2397.2542 | 557.6341 | 272.9161 | 447.7639 | 464.4428 | 416.9432 | 183.0197 | 149.6857
2398.2542 | 559.0365 | 273.0292 | 449.6224 | 465.0133 | 417.0181 | 183.1529 | 149.7927
2399.2542 | 558.5313 | 273.1571 | 449.8654 | 465.8593 | 417.3041 | 183.2838 | 149.8948
2400.2542 | 560.1483 | 273.2635 | 450.7158 | 465.8919 | 417.6489 | 183.4222 | 150.0068
2401.2542 | 558.3517 | 273.3011 | 451.5424 | 466.759 | 418.1914 | 183.5428 | 150.1175
2402.2542 | 557.7053 | 273.4059 | 452.026 | 466.6781 | 418.4586 | 183.6791 | 150.2275
2403.2542 | 556.3823 | 273.6013 | 451.8072 | 466.6464 | 418.6464 | 183.8105 | 150.3343
2404.2542 | 559.0403 | 273.718 | 451.9102 | 467.2915 | 419.0281 | 183.9335 | 150.4507
2405.2542 | 561.4268 | 273.8535 | 451.7758 | 466.8396 | 419.3426 | 184.0614 | 150.5453
2406.2542 | 561.0619 | 273.9885 | 451.2443 | 467.2007 | 419.5082 | 184.1866 | 150.667
2407.2542 | 564.0287 | 274.0886 | 451.3286 | 466.5881 | 419.8694 | 184.3199 | 150.7775
2408.2542 | 565.5099 | 274.2143 | 451.1975 | 466.8632 | 420.3859 | 184.4348 | 150.8826
2409.2542 | 567.2224 | 274.3404 | 451.065 | 467.4249 | 420.7043 | 184.5692 | 151.0091
2410.2542 | 565.5351 | 274.4699 | 451.1672 | 467.3804 | 421.308 | 184.7037 | 151.1039
2411.2542 | 565.8087 | 274.5829 | 452.016 | 467.1829 | 421.6622 | 184.836 | 151.2288
2412.2542 | 567.7378 | 274.7243 | 452.1282 | 468.5208 | 421.8835 | 184.9714 | 151.333
2413.2542 | 569.5641 | 274.8439 | 452.0465 | 468.2227 | 422.1114 | 185.102 | 151.4549
2414.2542 | 572.201 | 274.9688 | 452.4014 | 469.3969 | 422.648 | 185.2205 | 151.5577
2415.2542 | 576.8527 | 275.0721 | 452.7051 | 468.9456 | 423.0262 | 185.34 | 151.6735
2416.2542 | 577.8651 | 275.1853 | 452.9036 | 468.405 | 423.4259 | 185.4772 | 151.788
2417.2542 | 575.8325 | 275.3177 | 453.2835 | 469.2185 | 423.7487 | 185.6079 | 151.8927
2418.2542 | 574.0904 | 275.4362 | 453.2824 | 468.598 | 424.3233 | 185.7082 | 152.0035
2419.2542 | 575.7706 | 275.5513 | 453.4374 | 468.5313 | 424.5682 | 185.8437 | 152.1149
2420.2542 | 573.8338 | 275.6732 | 453.5195 | 469.717 | 424.6847 | 185.9689 | 152.2203
2421.2542 | 575.7288 | 275.8103 | 453.599 | 469.915 | 424.77 | 186.099 | 152.3327
2422.2542 | 574.9643 | 275.9291 | 454.3097 | 470.6236 | 424.996 | 186.2346 | 152.4355
2423.2542 | 574.9707 | 276.0362 | 455.0063 | 471.3987 | 425.2102 | 186.3601 | 152.5417
2424.2542 | 571.9219 | 276.1453 | 455.2296 | 470.6624 | 425.4689 | 186.4838 | 152.656
2425.2542 | 575.4191 | 276.2515 | 454.8882 | 469.7909 | 425.6692 | 186.6189 | 152.7687
2426.2542 | 581.1959 | 276.3691 | 455.6015 | 469.2757 | 426.0785 | 186.7441 | 152.8733
2427.2542 | 584.6139 | 276.4719 | 456.3212 | 469.8514 | 426.2194 | 186.8762 | 152.9915
2428.2542 | 583.2315 | 276.5231 | 457.2194 | 470.7432 | 426.5945 | 186.9931 | 153.1027
2429.2542 | 579.6289 | 276.6619 | 457.1697 | 470.1339 | 426.8417 | 187.0942 | 153.2032
2430.2542 | 585.7266 | 276.8264 | 456.9301 | 469.6434 | 427.3912 | 187.2117 | 153.3166
2431.2542 | 587.7395 | 276.9135 | 457.4268 | 471.5122 | 427.5063 | 187.3464 | 153.4384
2432.2542 | 588.5988 | 277.0275 | 458.5133 | 471.4954 | 427.8093 | 187.4765 | 153.5395
2433.2542 | 588.1175 | 277.0835 | 459.1069 | 471.1443 | 427.9199 | 187.6028 | 153.6397
2434.2542 | 587.7881 | 277.2628 | 458.8535 | 470.6986 | 427.8921 | 187.7299 | 153.753
2435.2542 | 585.585 | 277.4 | 458.9062 | 470.0517 | 427.7561 | 187.8615 | 153.8691
2436.2542 | 586.6907 | 277.5369 | 458.5713 | 469.5836 | 427.732 | 187.9954 | 153.9811
2437.2542 | 583.2828 | 277.6433 | 458.7797 | 469.2111 | 427.7238 | 188.1104 | 154.0888
2438.2542 | 581.6552 | 277.7826 | 459.4468 | 469.0847 | 427.8381 | 188.228 | 154.2148
2439.2542 | 581.3985 | 277.8766 | 460.2976 | 470.2015 | 427.8306 | 188.3558 | 154.3131
2440.2542 | 578.8861 | 278.0205 | 460.5307 | 470.3916 | 427.7122 | 188.4859 | 154.419
2441.2542 | 576.2096 | 278.1576 | 461.1729 | 471.1993 | 427.5367 | 188.6123 | 154.5443
2442.2542 | 575.2555 | 278.2778 | 461.5317 | 471.0131 | 427.607 | 188.7287 | 154.6588
2443.2542 | 570.8661 | 278.4426 | 462.3298 | 471.1936 | 427.692 | 188.5394 | 154.7746
2444.2542 | 571.2193 | 278.5569 | 462.8396 | 472.3801 | 427.7096 | 188.7108 | 154.8741
2445.2542 | 571.5949 | 278.657 | 463.3214 | 472.5261 | 427.8861 | 188.8708 | 154.9931
2446.2542 | 569.4109 | 278.7584 | 464.0931 | 472.9442 | 428.1017 | 188.9978 | 155.1166
2447.2542 | 567.6963 | 278.8712 | 464.0311 | 473.1427 | 428.1314 | 189.1425 | 155.2157
2448.2542 | 566.9804 | 278.8949 | 464.6851 | 472.3177 | 428.1301 | 189.2652 | 155.3225
2449.2542 | 565.8038 | 279.0278 | 465.2669 | 473.4488 | 428.3871 | 189.4042 | 155.443
2450.2542 | 567.8162 | 279.1237 | 465.4638 | 473.1713 | 428.3901 | 189.5343 | 155.5508
2451.2542 | 570.4926 | 279.2727 | 465.8822 | 474.0098 | 428.4029 | 189.6594 | 155.6617
2452.2542 | 569.9116 | 279.4079 | 466.5527 | 473.9099 | 428.4602 | 189.7884 | 155.7789
2453.2542 | 569.2248 | 279.5576 | 466.69 | 473.4138 | 428.36 | 189.9188 | 155.8899
2454.2542 | 566.3362 | 279.6888 | 467.6981 | 475.6062 | 428.8461 | 190.036 | 156.0115
2455.2542 | 564.8146 | 279.8194 | 468.5232 | 475.5714 | 429.3277 | 190.1794 | 156.1213
2456.2542 | 561.7779 | 279.9564 | 468.8552 | 476.9242 | 429.5757 | 190.3101 | 156.224
2457.2542 | 571.2116 | 280.0833 | 469.5116 | 477.4417 | 430.0523 | 190.4435 | 156.3292
2458.2542 | 569.0175 | 280.213 | 468.8891 | 476.8073 | 430.3175 | 190.5733 | 156.4465
2459.2542 | 568.636 | 280.2975 | 468.9937 | 477.32 | 430.3829 | 190.6928 | 156.5457
2460.2542 | 571.175 | 280.4534 | 469.0909 | 478.8186 | 430.5204 | 190.8113 | 156.6767
2461.2542 | 576.4759 | 280.5698 | 469.2951 | 478.6223 | 430.5401 | 190.9286 | 156.7935
2462.2542 | 582.3999 | 280.6816 | 469.8868 | 478.4663 | 430.682 | 191.0434 | 156.8942
2463.2542 | 582.6759 | 280.7827 | 469.7814 | 478.3632 | 430.8661 | 191.1635 | 157.0086
2464.2542 | 580.6548 | 280.9144 | 470.3655 | 479.3494 | 430.8058 | 191.2843 | 157.1207
2465.2542 | 579.6337 | 281.0142 | 470.529 | 480.1045 | 430.771 | 191.4032 | 157.2283
2466.2542 | 578.0865 | 281.1378 | 470.438 | 479.898 | 430.8674 | 191.5167 | 157.3596
2467.2542 | 576.4739 | 281.262 | 470.016 | 480.6356 | 431.0504 | 191.6316 | 157.4537
2468.2542 | 577.2677 | 281.3317 | 469.7438 | 479.3947 | 431.2704 | 191.7355 | 157.5618
2469.2542 | 586.4362 | 281.439 | 469.7051 | 479.8547 | 431.604 | 191.8418 | 157.6871
2470.2542 | 592.551 | 281.7065 | 470.1385 | 479.966 | 432.0233 | 191.9806 | 157.8061
2471.2542 | 593.5063 | 281.7784 | 469.9217 | 479.2456 | 432.0635 | 192.0869 | 157.9239
2472.2542 | 593.0285 | 281.8993 | 470.1956 | 478.3565 | 432.1093 | 192.1911 | 158.0471
2473.2542 | 590.6502 | 282.0191 | 469.4824 | 478.7516 | 432.102 | 192.3093 | 158.1489
2474.2542 | 589.9349 | 282.1633 | 469.5314 | 479.1014 | 432.1676 | 192.426 | 158.2666
2475.2542 | 589.8272 | 282.2621 | 469.4394 | 478.6137 | 432.2205 | 192.5373 | 158.37
2476.2542 | 589.9562 | 282.3885 | 469.4203 | 479.8423 | 432.6646 | 192.6561 | 158.4815
2477.2542 | 589.0616 | 282.538 | 470.1001 | 480.4392 | 433.0712 | 192.7538 | 158.6035
2478.2542 | 589.9519 | 282.6484 | 470.4669 | 481.0598 | 433.3528 | 192.8682 | 158.7193
2479.2542 | 588.3578 | 282.7658 | 471.0647 | 481.3352 | 433.7192 | 192.9421 | 158.8248
2480.2542 | 592.1469 | 282.8609 | 471.374 | 481.4176 | 433.9075 | 192.9875 | 158.9547
2481.2542 | 591.1467 | 282.9964 | 471.1324 | 481.136 | 434.025 | 193.0999 | 159.0747
2482.2542 | 593.0903 | 283.1098 | 471.3035 | 481.3656 | 434.0293 | 193.2151 | 159.1812
2483.2542 | 595.1699 | 283.2212 | 471.6699 | 481.0105 | 433.8647 | 193.3277 | 159.3002
2484.2542 | 595.0809 | 283.3366 | 472.1337 | 481.7425 | 433.8089 | 193.4332 | 159.4093
2485.2542 | 595.3125 | 283.4498 | 473.438 | 482.9786 | 433.8861 | 193.5475 | 159.5318
2486.2542 | 595.5106 | 283.5569 | 472.9093 | 483.0392 | 434.0153 | 193.6589 | 159.6409
2487.2542 | 595.0223 | 283.6608 | 472.5531 | 483.6375 | 434.1081 | 193.7616 | 159.7561
2488.2542 | 594.4774 | 283.7697 | 472.7217 | 482.6531 | 434.1505 | 193.8615 | 159.8702
2489.2542 | 593.1889 | 283.9346 | 471.9945 | 483.4295 | 434.2026 | 193.9219 | 160.0062
2490.2542 | 595.6042 | 283.9967 | 472.6358 | 482.6608 | 434.4912 | 194.0981 | 160.0753
2491.2542 | 595.2174 | 284.1012 | 473.3421 | 483.7543 | 434.7325 | 194.1885 | 160.1909
2492.2542 | 594.5951 | 284.2028 | 473.5368 | 483.1445 | 434.8851 | 194.3012 | 160.2891
2493.2542 | 596.5938 | 284.3063 | 473.9877 | 482.4324 | 434.9037 | 194.4123 | 160.4063
2494.2542 | 595.9385 | 284.4199 | 474.0356 | 483.4342 | 435.0724 | 194.516 | 160.5256
2495.2542 | 598.6594 | 284.5259 | 475.0657 | 483.3088 | 435.1249 | 194.6301 | 160.6388
2496.2542 | 600.6534 | 284.6309 | 474.9618 | 483.246 | 435.1845 | 194.7179 | 160.7637
2497.2542 | 600.242 | 284.7736 | 474.8837 | 483.1305 | 435.2093 | 194.8034 | 160.9175
2498.2542 | 596.0802 | 284.923 | 474.9356 | 488.1748 | 435.0338 | 195.0837 | 160.8806
2499.2542 | 593.2997 | 285.0989 | 474.8688 | 490.4921 | 434.7303 | 195.0294 | 160.9278
2500.2542 | 594.5269 | 285.2025 | 474.3757 | 489.1924 | 434.4914 | 195.1394 | 161.0475
2501.2542 | 591.8296 | 285.2703 | 474.3169 | 491.8321 | 434.5677 | 195.4098 | 161.1327
2502.2542 | 592.5266 | 285.371 | 474.9159 | 490.7705 | 434.6029 | 195.5745 | 161.3726
2503.2542 | 592.4593 | 285.4966 | 475.4307 | 491.8841 | 434.5043 | 195.6047 | 161.3549
2504.2542 | 597.7066 | 285.6 | 475.8322 | 492.5235 | 434.3605 | 195.7598 | 161.4251
2505.2542 | 596.4562 | 285.7074 | 475.6579 | 491.6316 | 434.4555 | 195.8804 | 161.5794
2506.2542 | 597.3918 | 285.8264 | 474.7063 | 491.0348 | 434.3105 | 195.9133 | 161.6636
2507.2542 | 598.2502 | 285.7836 | 474.3398 | 495.5136 | 434.3026 | 196.1454 | 161.6919
2508.2542 | 598.7633 | 285.8534 | 474.7451 | 497.1232 | 434.3254 | 196.2623 | 161.8135
2509.2542 | 596.534 | 285.9958 | 473.91 | 497.4967 | 434.2204 | 196.3678 | 161.9332
2510.2542 | 603.9601 | 286.0991 | 473.9795 | 497.2742 | 434.1069 | 196.4706 | 162.0503
2511.2542 | 604.9081 | 286.2007 | 474.799 | 497.4948 | 434.1922 | 196.5702 | 162.1575
2512.2542 | 606.2418 | 286.3014 | 474.3872 | 497.1773 | 434.1828 | 196.6523 | 162.265
2513.2542 | 616.1073 | 286.4063 | 474.8652 | 497.5109 | 434.2219 | 196.7548 | 162.3904
2514.2542 | 618.1102 | 286.4667 | 474.7191 | 498.6353 | 434.3171 | 196.867 | 162.4988
2515.2542 | 617.8627 | 286.5958 | 475.0561 | 499.5898 | 434.6398 | 196.9605 | 162.6246
2516.2542 | 616.8202 | 286.6895 | 475.2993 | 500.011 | 434.9179 | 197.0167 | 162.7368
2517.2542 | 614.9582 | 286.7709 | 475.1196 | 499.709 | 435.0732 | 197.1372 | 162.8387
2518.2542 | 613.1276 | 286.8737 | 475.6142 | 500.0001 | 435.3718 | 197.2517 | 162.9659
2519.2542 | 613.9803 | 286.9763 | 476.4646 | 501.0428 | 435.5298 | 197.3514 | 163.0942
2520.2542 | 613.0912 | 287.0715 | 477.3379 | 501.2689 | 435.796 | 197.3395 | 163.2044
2521.2542 | 614.2251 | 287.1856 | 477.8018 | 500.9436 | 435.9102 | 197.4609 | 163.3265
2522.2542 | 613.584 | 287.2706 | 478.4522 | 501.4873 | 435.9825 | 197.5766 | 163.4669
2523.2542 | 612.1683 | 287.3834 | 478.7561 | 500.9093 | 436.1966 | 197.6754 | 163.5667
2524.2542 | 620.4564 | 287.5051 | 478.8693 | 500.4808 | 436.2061 | 197.799 | 163.6605
2525.2542 | 622.8241 | 287.6183 | 479.2308 | 500.1267 | 435.9854 | 197.9054 | 163.7808
2526.2542 | 625.6771 | 287.7414 | 479.1247 | 500.5105 | 435.8787 | 198.0165 | 163.8853
2527.2542 | 621.2694 | 287.8725 | 479.0482 | 500.3868 | 435.7974 | 198.1139 | 164.0089
2528.2542 | 621.8341 | 288.0165 | 478.911 | 500.1686 | 435.4948 | 198.1681 | 164.1258
2529.2542 | 624.2891 | 288.1423 | 478.3776 | 499.433 | 435.3277 | 198.2796 | 164.2409
2530.2542 | 623.328 | 288.2729 | 478.195 | 499.3241 | 435.0064 | 198.3267 | 164.3601
2531.2542 | 628.6082 | 288.4071 | 478.1695 | 498.8726 | 434.7682 | 198.4374 | 164.4757
2532.2542 | 630.5039 | 288.5334 | 477.6661 | 498.6112 | 434.5813 | 198.5529 | 164.595
2533.2542 | 633.5338 | 288.6796 | 478.0375 | 498.2218 | 434.4113 | 198.6676 | 164.7138
2534.2542 | 639.9878 | 288.8029 | 478.0432 | 498.6287 | 434.308 | 198.7698 | 164.8222
2535.2542 | 639.0619 | 288.9246 | 478.5226 | 500.0838 | 434.4076 | 198.872 | 164.9382
2536.2542 | 638.7086 | 289.0609 | 479.3811 | 500.6037 | 434.4405 | 198.9821 | 165.0597
2537.2542 | 636.4009 | 289.2003 | 479.9163 | 500.3885 | 434.4843 | 199.0994 | 165.1673
2538.2542 | 630.2358 | 289.34 | 479.8089 | 500.0275 | 434.3024 | 199.2006 | 165.2884
2539.2542 | 627.6661 | 289.476 | 479.7067 | 500.0711 | 434.145 | 199.307 | 165.403
2540.2542 | 622.4926 | 289.6247 | 480.2796 | 500.0753 | 434.0372 | 199.4089 | 165.5162
2541.2542 | 621.0869 | 289.7706 | 480.5911 | 499.7592 | 433.765 | 199.4986 | 165.6456
2542.2542 | 620.8173 | 289.9292 | 480.6746 | 500.582 | 433.4265 | 199.6136 | 165.768
2543.2542 | 618.3662 | 290.0881 | 480.4745 | 500.8014 | 433.2831 | 199.7115 | 165.8818
2544.2542 | 612.2094 | 290.2273 | 480.4732 | 501.0323 | 433.2528 | 199.8243 | 165.9985
2545.2542 | 618.7669 | 290.3664 | 480.6193 | 501.3603 | 433.1631 | 199.9359 | 166.11
2546.2542 | 617.4947 | 290.5115 | 480.781 | 501.6882 | 433.0258 | 200.0384 | 166.2274
2547.2542 | 618.7125 | 290.6596 | 481.2753 | 501.3845 | 433.0881 | 200.1302 | 166.3422
2548.2542 | 621.9396 | 290.8062 | 481.1277 | 501.5869 | 432.9552 | 200.2342 | 166.4561
2549.2542 | 617.9612 | 290.9366 | 482.2251 | 501.8703 | 432.8657 | 200.3442 | 166.5684
2550.2542 | 615.9404 | 291.0774 | 483.0019 | 502.8286 | 432.9337 | 200.4542 | 166.6919
2551.2542 | 612.3018 | 291.2108 | 483.3997 | 503.5857 | 432.8373 | 200.5642 | 166.798
2552.2542 | 606.6573 | 291.3523 | 484.1773 | 503.6184 | 432.816 | 200.6671 | 166.9175
2553.2542 | 605.5956 | 291.4675 | 484.1658 | 503.6239 | 432.5884 | 200.7821 | 167.0291
2554.2542 | 615.2757 | 291.625 | 484.3964 | 503.1987 | 432.4475 | 200.8893 | 167.1383
2555.2542 | 616.6737 | 291.8122 | 483.8977 | 503.3003 | 432.2505 | 200.9999 | 167.2555
2556.2542 | 616.0436 | 291.967 | 484.2044 | 504.3442 | 432.2264 | 201.1004 | 167.3831
2557.2542 | 619.2713 | 292.1221 | 484.8551 | 504.9585 | 432.21 | 201.2125 | 167.5002
2558.2542 | 616.2355 | 292.2834 | 485.121 | 505.3621 | 432.203 | 201.329 | 167.6147
2559.2542 | 617.6302 | 292.4302 | 485.2881 | 505.5383 | 432.2711 | 201.4247 | 167.7287
2560.2542 | 619.567 | 292.5853 | 485.2344 | 505.088 | 432.3873 | 201.5534 | 167.8464
2561.2542 | 626.4154 | 292.7676 | 486.2596 | 505.4447 | 432.4304 | 201.5886 | 167.9626
2562.2542 | 630.1092 | 292.9236 | 486.553 | 505.8374 | 432.5133 | 201.6731 | 168.0752
2563.2542 | 631.3123 | 293.0832 | 486.3512 | 506.0422 | 432.4185 | 201.8051 | 168.1892
2564.2542 | 631.9665 | 293.2501 | 486.2842 | 505.7634 | 432.3223 | 201.9221 | 168.3139
2565.2542 | 628.2635 | 293.4153 | 486.0177 | 505.4588 | 432.3013 | 202.0419 | 168.4272
2566.2542 | 623.8563 | 293.5767 | 486.3903 | 506.6821 | 432.1215 | 202.1605 | 168.5434
2567.2542 | 621.4424 | 293.7251 | 487.1937 | 507.1823 | 432.0313 | 202.2748 | 168.6577
2568.2542 | 620.48 | 293.8985 | 487.4498 | 508.0863 | 432.0516 | 202.4 | 168.7884
2569.2542 | 631.7049 | 294.0714 | 487.789 | 508.1943 | 432.0863 | 202.5345 | 168.9043
2570.2542 | 632.2857 | 294.246 | 488.0463 | 508.0043 | 432.0402 | 202.6503 | 169.0215
2571.2542 | 629.302 | 294.4003 | 487.915 | 508.2698 | 432.0563 | 202.7572 | 169.1368
2572.2542 | 628.0203 | 294.5679 | 487.7664 | 508.3338 | 432.1338 | 202.8986 | 169.2534
2573.2542 | 628.8302 | 294.7318 | 488.1286 | 508.8141 | 432.2886 | 203.0177 | 169.3737
2574.2542 | 628.5982 | 294.8654 | 488.1067 | 509.0356 | 432.5784 | 203.1286 | 169.492
2575.2542 | 631.6227 | 295.0532 | 488.9784 | 510.0622 | 432.8818 | 203.2489 | 169.6171
2576.2542 | 636.1935 | 295.1942 | 488.9338 | 511.1911 | 433.0866 | 203.3765 | 169.7288
2577.2542 | 636.658 | 295.3401 | 488.8265 | 511.4606 | 433.1864 | 203.4866 | 169.8394
2578.2542 | 637.5039 | 295.5046 | 489.8627 | 513.3615 | 433.2563 | 203.6091 | 169.9538
2579.2542 | 640.0387 | 295.6485 | 491.1739 | 513.4343 | 433.3754 | 203.7334 | 170.0731
2580.2542 | 638.4573 | 295.7986 | 491.0757 | 513.8609 | 433.6175 | 203.8551 | 170.1816
2581.2542 | 638.2445 | 295.9558 | 490.8907 | 513.9027 | 433.7633 | 203.9877 | 170.3119
2582.2542 | 636.5844 | 296.1117 | 491.149 | 514.4337 | 433.8544 | 204.1064 | 170.4239
2583.2542 | 647.9486 | 296.2693 | 491.8914 | 514.8975 | 434.1314 | 204.2301 | 170.5417
2584.2542 | 648.1023 | 296.4247 | 491.9468 | 514.4625 | 434.2695 | 204.2651 | 170.6617
2585.2542 | 640.8291 | 296.5886 | 491.5661 | 514.3091 | 434.3009 | 204.3968 | 170.7853
2586.2542 | 641.717 | 296.7185 | 491.0466 | 514.943 | 434.4371 | 204.5298 | 170.8957
2587.2542 | 644.0751 | 296.8706 | 491.6406 | 515.6478 | 434.5601 | 204.6529 | 171.0111
2588.2542 | 643.9547 | 297.0198 | 492.2985 | 516.3963 | 434.2602 | 204.7841 | 171.1274
2589.2542 | 641.1709 | 297.134 | 492.6872 | 516.356 | 434.0491 | 204.9087 | 171.2436
2590.2542 | 643.0793 | 297.2844 | 493.253 | 516.5415 | 433.9159 | 205.033 | 171.3555
2591.2542 | 637.8785 | 297.4496 | 493.2458 | 517.0368 | 433.8353 | 205.161 | 171.4775
2592.2542 | 635.1616 | 297.6056 | 493.3811 | 518.0302 | 433.7524 | 205.2937 | 171.5929
2593.2542 | 630.7459 | 297.7355 | 493.6903 | 518.7262 | 433.7452 | 205.4214 | 171.7062
2594.2542 | 630.4555 | 297.8875 | 493.7144 | 519.7705 | 433.6471 | 205.5554 | 171.826
2595.2542 | 627.0782 | 298.0444 | 494.5952 | 519.3421 | 433.3768 | 205.6837 | 171.9468
2596.2542 | 625.9649 | 298.192 | 495.3559 | 519.7136 | 433.2802 | 205.8131 | 172.0651
2597.2542 | 631.8886 | 298.3314 | 496.1136 | 520.9641 | 433.1974 | 205.9469 | 172.1843
2598.2542 | 631.8818 | 298.485 | 497.3422 | 522.4234 | 433.323 | 206.0757 | 172.3152
2599.2542 | 629.6126 | 298.61 | 497.8115 | 523.0541 | 433.2801 | 206.2112 | 172.4182
2600.2542 | 627.236 | 298.7567 | 498.1398 | 523.7235 | 433.3459 | 206.3302 | 172.5421
2601.2542 | 622.5978 | 298.9212 | 498.8612 | 525.2396 | 433.3603 | 206.4709 | 172.6575
2602.2542 | 621.595 | 298.9953 | 499.0486 | 522.8762 | 433.3999 | 206.5769 | 172.7969
2603.2542 | 620.0776 | 299.1142 | 499.7013 | 525.0522 | 433.3611 | 206.7252 | 172.9129
2604.2542 | 622.1712 | 299.2343 | 499.6558 | 525.6775 | 433.276 | 206.8593 | 173.0291
2605.2542 | 619.925 | 299.3638 | 499.3373 | 527.8394 | 433.2962 | 206.984 | 173.1371
2606.2542 | 615.2336 | 299.4791 | 499.4927 | 529.178 | 433.175 | 207.121 | 173.2645
2607.2542 | 614.4374 | 299.6275 | 499.6737 | 530.8897 | 433.2398 | 207.2525 | 173.3762
2608.2542 | 618.0978 | 299.7696 | 499.9304 | 532.3992 | 433.2656 | 207.319 | 173.4927
2609.2542 | 614.6807 | 299.9055 | 499.8991 | 533.2593 | 433.1597 | 207.4567 | 173.6118
2610.2542 | 616.0325 | 300.0086 | 500.0851 | 532.6791 | 433.1814 | 207.5996 | 173.7578
2611.2542 | 616.6045 | 300.1576 | 500.6033 | 533.5941 | 433.177 | 207.754 | 173.8755
2612.2542 | 616.3005 | 300.2824 | 500.5626 | 535.555 | 433.2217 | 207.8835 | 173.9907
2613.2542 | 612.5387 | 300.4145 | 502.0635 | 536.7438 | 433.2436 | 208.0248 | 174.127
2614.2542 | 614.0227 | 300.54 | 502.4492 | 537.4269 | 433.1606 | 208.1639 | 174.2333
2615.2542 | 613.5117 | 300.6722 | 503.2157 | 538.5924 | 433.0203 | 208.3022 | 174.3623
2616.2542 | 615.1854 | 300.7933 | 503.6718 | 539.2188 | 432.9204 | 208.4455 | 174.4901
2617.2542 | 614.7018 | 300.9303 | 503.5507 | 538.7953 | 432.8825 | 208.5865 | 174.6084
2618.2542 | 621.0761 | 301.0751 | 504.4343 | 534.607 | 432.8952 | 208.7232 | 174.7334
2619.2542 | 620.516 | 301.1872 | 505.3623 | 535.2112 | 432.8042 | 208.8471 | 174.8685
2620.2542 | 617.6257 | 301.341 | 505.3908 | 536.7049 | 432.7599 | 208.9967 | 174.9927
2621.2542 | 616.5412 | 301.4731 | 505.9441 | 537.7094 | 432.6175 | 209.1297 | 175.1062
2622.2542 | 611.9356 | 301.6109 | 506.116 | 539.2974 | 432.5135 | 209.2728 | 175.2469
2623.2542 | 608.7556 | 301.7676 | 506.2344 | 540.2097 | 432.3156 | 209.3844 | 175.3725
2624.2542 | 607.7507 | 301.9097 | 506.2755 | 540.3999 | 432.3102 | 209.5358 | 175.4992
2625.2542 | 618.9211 | 302.0366 | 507.0056 | 531.4256 | 432.2627 | 209.6347 | 175.7149
2626.2542 | 617.059 | 302.2 | 506.7754 | 531.748 | 432.2182 | 209.773 | 175.8523
2627.2542 | 614.2778 | 302.366 | 506.7438 | 533.2337 | 432.1764 | 209.9149 | 175.9673
2628.2542 | 616.3872 | 302.5071 | 506.3832 | 534.4849 | 432.169 | 210.0412 | 176.0897
2629.2542 | 619.0587 | 302.651 | 506.1988 | 536.3531 | 432.0816 | 210.1838 | 176.2136
2630.2542 | 619.2518 | 302.7792 | 505.6778 | 537.1223 | 432.1119 | 210.3312 | 176.3309
2631.2542 | 624.6761 | 302.9247 | 505.4685 | 537.33 | 432.0121 | 210.4666 | 176.4565
2632.2542 | 625.917 | 303.0812 | 505.5771 | 535.391 | 431.8877 | 210.5968 | 176.597
2633.2542 | 624.3794 | 303.2249 | 506.0438 | 536.5235 | 431.8476 | 210.7348 | 176.7345
2634.2542 | 624.0756 | 303.362 | 506.3011 | 536.8573 | 431.8677 | 210.8673 | 176.8692
2635.2542 | 623.4509 | 303.4925 | 506.4954 | 536.6063 | 431.923 | 210.9967 | 177.0062
2636.2542 | 623.1812 | 303.6417 | 506.2603 | 537.0094 | 431.7646 | 211.1381 | 177.1416
2637.2542 | 622.6075 | 303.7781 | 506.0004 | 537.4129 | 431.7506 | 211.2717 | 177.273
2638.2542 | 619.7144 | 303.9252 | 506.163 | 538.8878 | 431.7478 | 211.4077 | 177.4015
2639.2542 | 619.4311 | 304.0775 | 506.2831 | 538.7759 | 431.7217 | 211.5425 | 177.5265
2640.2542 | 619.5796 | 304.2109 | 506.0528 | 539.5663 | 431.7129 | 211.6868 | 177.6675
2641.2542 | 620.0242 | 304.3497 | 505.5496 | 540.9036 | 431.6108 | 211.8129 | 177.7906
2642.2542 | 620.3136 | 304.499 | 505.4362 | 545.9422 | 431.7048 | 211.9551 | 177.8899
2643.2542 | 624.1572 | 304.6542 | 505.2575 | 545.9824 | 431.6663 | 212.0763 | 178.0271
2644.2542 | 622.1646 | 304.7728 | 505.3007 | 546.4191 | 431.6115 | 212.1908 | 178.1637
2645.2542 | 620.0122 | 304.9313 | 505.1839 | 546.4131 | 431.6851 | 212.3264 | 178.2914
2646.2542 | 616.2559 | 305.0788 | 505.4031 | 548.4071 | 431.7991 | 212.4503 | 178.4229
2647.2542 | 613.7506 | 305.2223 | 506.0513 | 548.5595 | 431.789 | 212.5692 | 178.5618
2648.2542 | 610.9379 | 305.364 | 505.9519 | 548.7092 | 431.8122 | 212.6951 | 178.7062
2649.2542 | 611.3584 | 305.5049 | 506.0911 | 549.6342 | 431.884 | 212.8276 | 178.8404
2650.2542 | 607.9427 | 305.6472 | 506.1555 | 551.6137 | 431.8534 | 212.9512 | 178.9669
2651.2542 | 610.9714 | 305.8045 | 506.4688 | 552.2028 | 431.8738 | 213.0805 | 179.1046
2652.2542 | 647.5088 | 305.9441 | 507.9565 | 514.3558 | 432.0335 | 213.0926 | 179.4928
2653.2542 | 650.2329 | 306.0923 | 507.9366 | 514.8786 | 432.0628 | 213.2181 | 179.6197
2654.2542 | 649.91 | 306.2419 | 508.172 | 515.2838 | 432.0936 | 213.3519 | 179.7576
2655.2542 | 650.3586 | 306.3988 | 508.8038 | 515.9535 | 432.1202 | 213.4794 | 179.8918
2656.2542 | 646.2186 | 306.5427 | 508.6743 | 516.5639 | 432.2137 | 213.6029 | 180.0364
2657.2542 | 641.2605 | 306.7049 | 508.3873 | 515.7716 | 432.2397 | 213.7286 | 180.1736
2658.2542 | 641.7487 | 306.8387 | 508.0604 | 515.0512 | 432.2545 | 213.8593 | 180.3117
2659.2542 | 638.7767 | 306.9702 | 508.1037 | 515.2102 | 432.3652 | 213.9939 | 180.4366
2660.2542 | 636.5426 | 307.1086 | 508.4182 | 515.0485 | 432.4173 | 214.12 | 180.5759
2661.2542 | 637.8475 | 307.2647 | 508.7177 | 515.5221 | 432.4989 | 214.2415 | 180.7048
2662.2542 | 636.2716 | 307.4328 | 508.6185 | 515.5839 | 432.5254 | 214.371 | 180.8568
2663.2542 | 636.369 | 307.5717 | 508.8575 | 515.7864 | 432.532 | 214.492 | 180.9826
2664.2542 | 629.2044 | 307.7246 | 509.1651 | 515.3547 | 432.6711 | 214.6161 | 181.1213
2665.2542 | 626.9407 | 307.8818 | 510.0745 | 515.0707 | 432.6552 | 214.742 | 181.2561
2666.2542 | 628.4268 | 308.0447 | 510.5826 | 515.0981 | 432.8945 | 214.8754 | 181.3915
2667.2542 | 633.2467 | 308.1931 | 511.449 | 515.2626 | 432.9951 | 214.9972 | 181.5409
2668.2542 | 637.3302 | 308.3469 | 512.0568 | 515.7071 | 433.153 | 215.1264 | 181.6701
2669.2542 | 639.8098 | 308.4792 | 512.3434 | 515.5176 | 433.2888 | 215.2446 | 181.8085
2670.2542 | 642.3459 | 308.6364 | 513.0937 | 516.7374 | 433.266 | 215.3755 | 181.9459
2671.2542 | 642.1885 | 308.7909 | 513.2571 | 516.7535 | 433.2565 | 215.504 | 182.0912
2672.2542 | 640.408 | 308.9487 | 512.7338 | 516.0753 | 433.2724 | 215.6248 | 182.2291
2673.2542 | 646.6818 | 309.1015 | 513.083 | 510.0297 | 433.2603 | 215.7296 | 182.4024
2674.2542 | 638.4302 | 309.2462 | 512.8271 | 514.977 | 433.2811 | 215.8462 | 182.489
2675.2542 | 642.476 | 309.3935 | 514.0954 | 515.4193 | 433.3828 | 215.9842 | 182.6712
2676.2542 | 657.5663 | 309.5505 | 515.131 | 510.9508 | 433.2699 | 216.0956 | 182.8272
2677.2542 | 663.4755 | 309.7089 | 515.4871 | 510.119 | 433.3988 | 216.2131 | 182.9775
2678.2542 | 659.0125 | 309.8929 | 515.219 | 514.6199 | 433.5369 | 216.3507 | 183.095
2679.2542 | 658.445 | 310.0492 | 515.177 | 508.537 | 433.5321 | 216.4575 | 183.2677
2680.2542 | 654.3874 | 310.1947 | 514.9681 | 509.2537 | 433.6169 | 216.5794 | 183.4132
2681.2542 | 657.6335 | 310.3591 | 515.0028 | 508.9941 | 433.792 | 216.7 | 183.5528
2682.2542 | 660.882 | 310.5343 | 515.4782 | 507.6181 | 434.0933 | 216.8117 | 183.702
2683.2542 | 660.5323 | 310.6881 | 514.9546 | 505.5178 | 434.1308 | 216.9413 | 183.8655
2684.2542 | 663.2044 | 310.8298 | 515.0443 | 506.4455 | 434.2861 | 217.0626 | 183.9879
2685.2542 | 661.117 | 310.985 | 515.6975 | 506.1964 | 434.518 | 217.1801 | 184.1365
2686.2542 | 660.9482 | 311.1595 | 516.601 | 505.1635 | 434.5565 | 217.302 | 184.2808
2687.2542 | 666.8508 | 311.3031 | 517.7547 | 504.6449 | 434.7182 | 217.4295 | 184.4374
2688.2542 | 669.1275 | 311.4617 | 519.2228 | 504.4906 | 434.7047 | 217.5526 | 184.5854
2689.2542 | 667.9068 | 311.5985 | 519.5662 | 506.1587 | 434.6882 | 217.6698 | 184.7231
2690.2542 | 666.5612 | 311.7573 | 518.7988 | 504.8427 | 434.6294 | 217.7948 | 184.8827
2691.2542 | 665.6701 | 311.9061 | 518.0843 | 504.6233 | 434.7361 | 217.9079 | 185.0238
2692.2542 | 666.19 | 312.0994 | 518.2636 | 498.991 | 434.7716 | 218.0273 | 185.1931
2693.2542 | 663.4164 | 312.2365 | 518.2009 | 498.644 | 434.9636 | 218.1432 | 185.3414
2694.2542 | 664.3549 | 312.4104 | 519.1798 | 498.6028 | 435.1123 | 218.2599 | 185.4883
2695.2542 | 671.8238 | 312.5692 | 519.8662 | 498.3084 | 435.1271 | 218.3717 | 185.6368
2696.2542 | 681.657 | 312.7381 | 520.2423 | 497.686 | 435.1658 | 218.4845 | 185.7875
2697.2542 | 685.876 | 312.9031 | 520.6743 | 496.4185 | 435.4338 | 218.6001 | 185.94
2698.2542 | 689.4897 | 313.082 | 521.0312 | 496.3963 | 435.5663 | 218.7232 | 186.0915
2699.2542 | 691.123 | 313.2281 | 521.9384 | 497.4866 | 435.7472 | 218.8385 | 186.2382
2700.2542 | 692.5659 | 313.3766 | 522.7393 | 496.4925 | 435.7626 | 218.9573 | 186.3936
2701.2542 | 694.1542 | 313.5322 | 522.7 | 496.0568 | 435.3821 | 219.0695 | 186.5462
2702.2542 | 695.6783 | 313.7046 | 522.5836 | 494.8897 | 435.6063 | 219.1896 | 186.6993
2703.2542 | 696.9265 | 313.8823 | 523.3503 | 494.9084 | 435.7977 | 219.2972 | 186.8505
2704.2542 | 693.3461 | 314.0449 | 523.4569 | 494.3412 | 436.1799 | 219.4267 | 187.0049
2705.2542 | 690.4559 | 314.2005 | 522.7989 | 494.7848 | 436.4463 | 219.5309 | 187.1507
2706.2542 | 687.5321 | 314.3682 | 523.0329 | 494.8627 | 436.8567 | 219.6587 | 187.3212
2707.2542 | 696.345 | 314.5651 | 524.1695 | 481.7599 | 437.2649 | 219.7581 | 187.4877
2708.2542 | 689.1105 | 314.7395 | 524.1232 | 488.3706 | 437.3839 | 219.8795 | 187.6609
2709.2542 | 679.8387 | 314.9171 | 524.5836 | 493.2573 | 437.5851 | 219.9695 | 187.7884
2710.2542 | 676.7202 | 315.0424 | 524.1826 | 493.9419 | 437.8534 | 220.0955 | 187.9376
2711.2542 | 680.7391 | 315.2031 | 524.7292 | 492.6405 | 438.3044 | 220.188 | 188.0915
2712.2542 | 680.9957 | 315.4041 | 524.2987 | 493.7547 | 438.8914 | 220.2927 | 188.2515
2713.2542 | 683.4465 | 315.5677 | 524.6101 | 491.5738 | 439.1506 | 220.3988 | 188.4153
2714.2542 | 680.5712 | 315.7514 | 523.9531 | 492.5769 | 439.1789 | 220.4866 | 188.577
2715.2542 | 686.682 | 315.8978 | 523.8857 | 490.8205 | 439.116 | 220.5991 | 188.7327
2716.2542 | 692.8367 | 316.081 | 523.8679 | 489.921 | 438.9247 | 220.7162 | 188.8972
2717.2542 | 694.3845 | 316.2099 | 523.4218 | 488.8776 | 438.8013 | 220.8283 | 189.0648
2718.2542 | 693.547 | 316.4619 | 523.2655 | 488.2884 | 439.0074 | 220.9465 | 189.2212
2719.2542 | 697.2531 | 316.6465 | 522.5537 | 487.5841 | 439.2323 | 221.0654 | 189.3752
2720.2542 | 700.2109 | 316.7635 | 522.0391 | 487.1984 | 439.5627 | 221.1867 | 189.5352
2721.2542 | 699.5032 | 317.0214 | 521.9121 | 489.2636 | 439.8517 | 221.2118 | 189.6997
2722.2542 | 701.3274 | 317.1877 | 522.0871 | 488.7857 | 439.9827 | 221.2928 | 189.8623
2723.2542 | 701.8374 | 317.3981 | 522.0895 | 489.8808 | 440.4843 | 221.4188 | 190.0138
2724.2542 | 702.5331 | 317.5986 | 521.6441 | 486.8849 | 440.0005 | 221.5501 | 190.1833
2725.2542 | 702.727 | 317.7838 | 521.4562 | 486.8641 | 439.6403 | 221.6668 | 190.3591
2726.2542 | 704.0933 | 318.0267 | 521.7007 | 484.6491 | 439.4463 | 221.7619 | 190.5145
2727.2542 | 704.6467 | 318.3038 | 521.4002 | 484.6863 | 439.7583 | 221.9006 | 190.6667
2728.2542 | 703.2029 | 318.4549 | 521.869 | 483.8333 | 440.5013 | 222.0228 | 190.8334
2729.2542 | 702.0311 | 318.7645 | 522.8934 | 482.8416 | 441.4136 | 222.1417 | 191.0042
2730.2542 | 701.2599 | 318.9324 | 523.2489 | 482.7296 | 441.7968 | 222.2542 | 191.1564
2731.2542 | 695.5379 | 319.139 | 523.2625 | 485.4673 | 442.3129 | 222.381 | 191.3212
2732.2542 | 702.6128 | 319.3544 | 523.7837 | 479.0496 | 443.2221 | 222.5084 | 191.4987
2733.2542 | 704.4461 | 319.5732 | 523.8763 | 476.0494 | 444.1792 | 222.6312 | 191.6643
2734.2542 | 707.7104 | 319.8418 | 524.4525 | 475.9557 | 444.2672 | 222.7663 | 191.8194
2735.2542 | 715.044 | 320.1097 | 524.5506 | 472.0361 | 444.7447 | 222.874 | 191.9949
2736.2542 | 724.4362 | 320.3619 | 525.619 | 469.959 | 444.8536 | 223.0009 | 192.163
2737.2542 | 733.2817 | 320.6306 | 526.3531 | 468.3864 | 445.4976 | 223.1226 | 192.3256
2738.2542 | 730.7639 | 320.8456 | 526.688 | 465.3115 | 446.0364 | 223.2499 | 192.4872
2739.2542 | 732.8168 | 321.1229 | 526.7875 | 460.0306 | 446.4051 | 223.3812 | 192.6593
2740.2542 | 741.2995 | 321.3261 | 526.8485 | 450.8919 | 447.1032 | 223.5221 | 192.8322
2741.2542 | 745.5191 | 321.6015 | 526.3856 | 447.3609 | 447.3058 | 223.6549 | 193.006
2742.2542 | 742.0311 | 321.8944 | 526.2851 | 451.5875 | 447.7234 | 223.7901 | 193.1591
2743.2542 | 756.5678 | 322.2023 | 527.5948 | 448.4199 | 447.8036 | 223.9224 | 193.3322
2744.2542 | 755.7643 | 322.4282 | 528.3964 | 443.5051 | 448.4038 | 224.0595 | 193.5014
2745.2542 | 760.3386 | 322.6836 | 529.04 | 442.2861 | 448.422 | 224.1744 | 193.6598
2746.2542 | 766.8759 | 322.8002 | 530.1958 | 436.5816 | 448.5787 | 224.2689 | 193.8377
2747.2542 | 776.0104 | 323.1571 | 530.6296 | 438.1047 | 448.3594 | 224.401 | 194.0058
2748.2542 | 780.6914 | 323.4128 | 530.7559 | 431.9763 | 448.4519 | 224.5512 | 194.1638
2749.2542 | 776.7562 | 323.6965 | 530.6791 | 431.5715 | 448.9704 | 224.6798 | 194.3406
2750.2542 | 772.8777 | 324.0052 | 530.8048 | 431.8136 | 449.3762 | 224.8124 | 194.5137
2751.2542 | 774.2348 | 324.2469 | 531.0526 | 430.3853 | 450.1734 | 224.9647 | 194.6644
2752.2542 | 776.2096 | 324.5313 | 531.0764 | 428.4998 | 451.4236 | 225.1041 | 194.8267
2753.2542 | 766.1656 | 324.8304 | 530.6335 | 436.2314 | 452.2455 | 225.2672 | 194.9883
2754.2542 | 774.0328 | 325.1111 | 531.2921 | 432.9726 | 453.1056 | 225.3932 | 195.158
2755.2542 | 784.6594 | 325.422 | 532.35 | 430.3345 | 454.1539 | 225.5342 | 195.3209
2756.2542 | 786.8564 | 325.646 | 532.9789 | 428.5709 | 454.1017 | 225.6835 | 195.4946
2757.2542 | 788.6702 | 325.9068 | 533.5001 | 427.3159 | 453.232 | 225.8256 | 195.6597
2758.2542 | 786.7471 | 326.1967 | 534.0312 | 422.2166 | 452.6217 | 225.9768 | 195.8262
2759.2542 | 786.2777 | 326.3496 | 533.5594 | 419.1068 | 451.9398 | 226.1244 | 196.0173
2760.2542 | 770.7423 | 326.6403 | 532.9521 | 428.1836 | 451.3461 | 226.2763 | 196.1768
2761.2542 | 780.7356 | 326.9534 | 532.4662 | 423.0567 | 450.5594 | 226.4168 | 196.3306
2762.2542 | 771.9693 | 327.303 | 531.3364 | 427.4687 | 450.3955 | 226.5648 | 196.4933
2763.2542 | 775.1777 | 327.6171 | 530.5347 | 423.2566 | 450.2253 | 226.7336 | 196.6799
2764.2542 | 776.3553 | 327.8064 | 531.1374 | 424.7446 | 449.7126 | 226.8525 | 196.8439
2765.2542 | 778.9746 | 328.0517 | 531.456 | 422.2884 | 449.9666 | 227.0166 | 197.0051
2766.2542 | 775.5343 | 328.2711 | 531.3664 | 421.1362 | 449.7988 | 227.1874 | 197.1869
2767.2542 | 772.4292 | 328.427 | 531.0953 | 421.82 | 450.2344 | 227.351 | 197.3582
2768.2542 | 796.7271 | 328.514 | 531.0194 | 396.0627 | 450.5818 | 227.508 | 197.561
2769.2542 | 796.3268 | 328.6707 | 530.3671 | 394.3705 | 450.9826 | 227.6666 | 197.7302
2770.2542 | 798.3658 | 328.8423 | 529.8246 | 391.4804 | 450.9165 | 227.7329 | 197.8877
2771.2542 | 802.6224 | 328.9898 | 529.7121 | 389.1973 | 451.1295 | 227.9247 | 198.0767
2772.2542 | 798.0293 | 329.1558 | 529.66 | 394.7489 | 451.1587 | 228.0971 | 198.2361
2773.2542 | 772.1334 | 329.4751 | 528.9932 | 420.7765 | 451.1288 | 228.2674 | 198.3928
2774.2542 | 776.5773 | 329.5698 | 528.5849 | 413.2154 | 451.8178 | 228.3998 | 198.5769
2775.2542 | 773.5527 | 329.7976 | 528.1579 | 416.6328 | 451.7064 | 228.5474 | 198.75
2776.2542 | 790.1954 | 329.8384 | 528.404 | 401.8357 | 452.6473 | 228.6925 | 198.9583
2777.2542 | 775.4108 | 330.0814 | 528.5788 | 414.548 | 453.0347 | 228.8767 | 199.1061
2778.2542 | 759.3291 | 330.1376 | 528.3339 | 435.7083 | 453.2798 | 229.0749 | 199.2899
2779.2542 | 745.3305 | 330.3366 | 528.3274 | 448.0264 | 453.3369 | 229.2389 | 199.4024
2780.2542 | 736.2669 | 330.6242 | 528.2061 | 457.8044 | 453.2415 | 229.4106 | 199.5659
2781.2542 | 703.4939 | 330.776 | 528.0856 | 488.8021 | 453.8076 | 229.5846 | 199.7137
2782.2542 | 712.3753 | 330.9334 | 528.2725 | 479.1228 | 453.885 | 229.7387 | 199.8992
2783.2542 | 664.6939 | 331.1185 | 527.9721 | 530.3902 | 453.7388 | 229.903 | 200.0167
2784.2542 | 663.9081 | 331.2654 | 528.0513 | 531.8076 | 453.7872 | 230.0798 | 200.1468
2785.2542 | 712.282 | 331.414 | 527.9953 | 481.6346 | 454.2945 | 230.2485 | 200.4169
2786.2542 | 722.9687 | 331.7249 | 527.2748 | 473.4205 | 454.9959 | 230.398 | 200.5805
2787.2542 | 736.94 | 331.8817 | 526.4027 | 455.7731 | 455.6729 | 230.5903 | 200.8312
2788.2542 | 674.0839 | 332.0167 | 525.9359 | 520.6204 | 455.7532 | 230.7361 | 200.8999
2789.2542 | 687.5582 | 332.1951 | 525.7704 | 506.4588 | 456.5606 | 230.8868 | 201.0888
2790.2542 | 649.577 | 332.4099 | 525.7754 | 545.9636 | 456.7867 | 231.049 | 201.2286
2791.2542 | 604.1893 | 332.6349 | 526.2259 | 593.6259 | 457.0381 | 231.2192 | 201.3556
2792.2542 | 630.9353 | 332.7656 | 526.9541 | 564.4796 | 457.5844 | 231.3953 | 201.5698
2793.2542 | 628.9131 | 332.9017 | 527.0981 | 568.1439 | 457.8934 | 231.5775 | 201.7624
2794.2542 | 711.5745 | 333.3122 | 526.9078 | 482.9588 | 458.5147 | 231.6719 | 202.0471
2795.2542 | 611.5245 | 333.6474 | 526.0175 | 585.4359 | 458.5066 | 231.7461 | 202.1613
2796.2542 | 786.5204 | 333.7278 | 526.0456 | 409.7794 | 459.0671 | 231.9905 | 202.5078
2797.2542 | 655.7017 | 333.8813 | 525.5376 | 545.9302 | 459.2674 | 232.2158 | 202.5013
2798.2542 | 675.7996 | 334.0511 | 525.8065 | 531.9044 | 458.9393 | 232.3602 | 202.6827
2799.2542 | 623.6213 | 334.2921 | 525.4323 | 592.6969 | 459.0031 | 232.5289 | 202.8248
2800.2542 | 656.5518 | 334.3542 | 524.8707 | 560.4366 | 458.7723 | 232.7049 | 202.9922
2801.2542 | 616.7538 | 334.6049 | 524.0232 | 600.5023 | 459.272 | 232.9026 | 203.1773
2802.2542 | 207.6693 | 334.9281 | 521.7824 | 1047.301 | 459.3157 | 233.0891 | 202.9196
2803.2542 | 217.4172 | 335.0486 | 521.207 | 1038.4548 | 458.8524 | 233.2819 | 203.0932
2804.2542 | 344.744 | 335.3607 | 521.948 | 903.0644 | 459.3281 | 233.433 | 203.4076
2805.2542 | 344.868 | 335.6056 | 522.0976 | 902.3614 | 460.0401 | 233.6383 | 203.5633
2806.2542 | 336.9854 | 335.7624 | 522.1678 | 906.6738 | 460.3084 | 233.7681 | 203.7643
2807.2542 | 347.8628 | 335.9406 | 522.0487 | 899.0866 | 460.2591 | 233.8749 | 203.9455
2808.2542 | 372.1144 | 336.1751 | 522.2555 | 880.2954 | 461.2688 | 234.0626 | 204.1667
2809.2542 | 289.8761 | 336.3694 | 522.4894 | 971.1402 | 461.2517 | 234.2696 | 204.2877
2810.2542 | 265.2327 | 336.5858 | 522.5792 | 994.5016 | 461.7537 | 234.437 | 204.4357
2811.2542 | 346.7934 | 336.8778 | 523.0285 | 894.2215 | 462.4022 | 234.5904 | 204.7407
2812.2542 | 276.3488 | 337.1734 | 523.0503 | 970.3043 | 463.2752 | 234.7498 | 204.8327
2813.2542 | 289.5206 | 337.299 | 523.7562 | 951.9257 | 464.0075 | 234.8588 | 205.121
2814.2542 | 268.7949 | 337.5831 | 523.5944 | 972.976 | 463.9279 | 235.0744 | 205.2036
2815.2542 | 256.8714 | 337.7254 | 523.619 | 986.4054 | 464.3158 | 235.2587 | 205.3808
2816.2542 | 238.9903 | 337.9436 | 523.317 | 1011.165 | 466.0192 | 235.4176 | 205.5459
2817.2542 | 266.7015 | 338.3705 | 523.1663 | 988.1151 | 466.2559 | 235.2383 | 206.243
2818.2542 | 240.241 | 338.3981 | 523.6379 | 1014.3353 | 467.2471 | 235.7439 | 205.9271
2819.2542 | 233.111 | 338.5667 | 523.5058 | 1024.4182 | 467.7279 | 235.946 | 206.0992
2820.2542 | 239.5654 | 338.7075 | 523.2188 | 1020.5741 | 467.8032 | 236.1347 | 206.2802
2821.2542 | 231.1252 | 339.0514 | 523.2816 | 1024.8395 | 468.096 | 236.3076 | 206.4725
2822.2542 | 351.8357 | 339.2285 | 523.8128 | 898.4383 | 467.9539 | 236.4812 | 206.785
2823.2542 | 342.7954 | 339.4943 | 522.9392 | 908.1636 | 467.77 | 236.6731 | 206.9604
2824.2542 | 309.7116 | 339.6583 | 522.2134 | 940.5248 | 467.5394 | 236.8669 | 207.1406
2825.2542 | 307.8103 | 339.8308 | 521.5627 | 942.1958 | 468.1694 | 237.0494 | 207.3213
2826.2542 | 300.0083 | 340.2222 | 520.8461 | 947.8244 | 468.0691 | 237.239 | 207.5138
2827.2542 | 300.7655 | 340.5375 | 520.594 | 942.5833 | 467.505 | 237.2548 | 207.8308
2828.2542 | 304.4352 | 340.7786 | 520.06 | 939.3915 | 467.2732 | 237.4889 | 207.9277
2829.2542 | 251.2311 | 340.8544 | 519.3781 | 1006.9363 | 467.5265 | 237.6696 | 208.068
2830.2542 | 227.7055 | 341.2166 | 518.8466 | 1033.0289 | 467.7519 | 237.8333 | 208.2419
2831.2542 | 217.651 | 341.3332 | 518.524 | 1041.7689 | 467.8773 | 237.9701 | 208.4446
2832.2542 | 224.2928 | 341.3552 | 518.3488 | 1045.3927 | 468.1005 | 238.1647 | 208.6619
2833.2542 | 229.0484 | 341.898 | 517.9818 | 1033.1229 | 467.9731 | 238.314 | 209.004
2834.2542 | 200.4981 | 341.9155 | 517.4014 | 1063.2814 | 468.6512 | 238.5854 | 209.0487
2835.2542 | 224.1372 | 342.1706 | 516.5395 | 1037.7426 | 468.9125 | 238.7902 | 209.2504
2836.2542 | 216.4574 | 342.4216 | 516.7322 | 1046.2926 | 468.8644 | 238.9395 | 209.5221
2837.2542 | 226.202 | 342.6507 | 516.0021 | 1031.3872 | 468.8522 | 239.1412 | 209.7384
2838.2542 | 229.8157 | 342.9192 | 515.3076 | 1029.4881 | 469.4133 | 239.3875 | 209.8828
2839.2542 | 226.4592 | 343.2477 | 514.7744 | 1030.6058 | 469.2316 | 239.5794 | 210.1209
2840.2542 | 228.6604 | 343.3776 | 514.5594 | 1037.0098 | 469.5351 | 239.7872 | 210.295
2841.2542 | 236.6125 | 343.5169 | 514.6963 | 1030.8261 | 469.6416 | 239.9566 | 210.5423
2842.2542 | 243.8135 | 343.9278 | 514.2286 | 1029.6305 | 471.2441 | 240.0996 | 210.8523
2843.2542 | 284.935 | 344.1285 | 513.9319 | 976.5909 | 471.3059 | 240.3739 | 210.9982
2844.2542 | 867.1786 | 344.448 | 515.9203 | 346.7837 | 473.6872 | 240.5766 | 211.7846
2845.2542 | 894.4082 | 344.661 | 515.3508 | 314.8585 | 474.3492 | 240.7397 | 212.0349
2846.2542 | 938.7219 | 344.9485 | 515.1018 | 268.5447 | 474.8457 | 240.9418 | 212.2773
2847.2542 | 935.7191 | 345.2312 | 514.4046 | 272.7612 | 474.7605 | 241.0977 | 212.4752
2848.2542 | 912.6268 | 345.3692 | 513.5978 | 305.5798 | 474.7654 | 241.2771 | 212.6498
2849.2542 | 946.6571 | 345.6592 | 513.2299 | 266.8984 | 474.7899 | 241.4963 | 212.9031
2850.2542 | 948.5292 | 345.855 | 513.1644 | 266.7223 | 475.115 | 241.6048 | 213.1093
2851.2542 | 944.939 | 346.1453 | 512.7743 | 264.7711 | 474.7849 | 241.7758 | 213.3275
2852.2542 | 946.0141 | 346.4397 | 512.1493 | 260.3884 | 474.2747 | 241.9782 | 213.5372
2853.2542 | 938.7891 | 346.7402 | 511.0368 | 263.5762 | 474.807 | 242.1689 | 213.7411
2854.2542 | 946.0499 | 347.0236 | 509.9639 | 260.3693 | 474.3434 | 242.3477 | 213.952
2855.2542 | 952.4886 | 347.2427 | 509.0806 | 253.6553 | 474.7071 | 242.4099 | 214.1667
2856.2542 | 960.8047 | 347.4753 | 507.9483 | 251.9602 | 474.6195 | 242.4203 | 214.3784
2857.2542 | 949.53 | 347.7515 | 507.2119 | 257.0806 | 474.3658 | 242.6342 | 214.586
2858.2542 | 946.4887 | 347.9685 | 507.1168 | 257.0855 | 474.1219 | 242.7726 | 214.7964
2859.2542 | 962.9048 | 348.2739 | 507.0738 | 244.1306 | 473.9164 | 242.6496 | 215.0051
2860.2542 | 963.778 | 348.4638 | 506.5778 | 240.6389 | 473.6969 | 242.8466 | 215.2275
2861.2542 | 969.9399 | 348.8368 | 505.6367 | 241.9932 | 474.2701 | 243.0234 | 215.4425
2862.2542 | 973.8856 | 349.0464 | 504.2741 | 233.3843 | 474.8127 | 243.1421 | 215.6541
2863.2542 | 975.1585 | 349.2663 | 502.9843 | 233.2359 | 475.686 | 243.2892 | 215.8799
2864.2542 | 976.5666 | 349.5246 | 502.3499 | 230.0965 | 477.1169 | 243.3855 | 216.0939
2865.2542 | 971.7871 | 349.9849 | 501.9959 | 237.1837 | 477.5023 | 243.6109 | 216.3057
2866.2542 | 978.2789 | 350.0828 | 501.4665 | 233.9453 | 477.6864 | 243.7704 | 216.5234
2867.2542 | 982.6518 | 350.4731 | 501.1193 | 226.2068 | 477.257 | 243.9768 | 216.7358
2868.2542 | 976.3666 | 350.5538 | 500.533 | 231.7952 | 477.8795 | 244.1992 | 216.9528
2869.2542 | 972.448 | 350.9386 | 500.1352 | 233.8219 | 478.059 | 244.4255 | 217.1565
2870.2542 | 966.9751 | 351.0329 | 499.831 | 234.617 | 477.9862 | 244.4543 | 217.383
2871.2542 | 960.8033 | 351.297 | 499.2595 | 235.8561 | 478.3293 | 244.5997 | 217.5939
2872.2542 | 965.339 | 351.6125 | 498.5154 | 234.0968 | 478.976 | 244.7317 | 217.8188
2873.2542 | 975.3784 | 351.9581 | 497.8347 | 229.6273 | 479.6697 | 244.9707 | 218.0513
2874.2542 | 976.9158 | 352.2639 | 497.0536 | 232.2029 | 479.703 | 245.1231 | 218.2746
2875.2542 | 981.8972 | 352.4385 | 496.5715 | 223.0502 | 479.352 | 245.3231 | 218.4955
2876.2542 | 988.5998 | 352.6059 | 495.9141 | 217.1509 | 478.937 | 245.5599 | 218.7098
2877.2542 | 995.4288 | 353.0919 | 495.3323 | 220.7749 | 479.7407 | 245.8064 | 218.9249
2878.2542 | 1002.1177 | 353.2036 | 495.3144 | 212.854 | 480.8312 | 245.6062 | 219.1371
2879.2542 | 986.3063 | 353.5553 | 494.872 | 217.7188 | 480.6678 | 245.9277 | 219.3603
2880.2542 | 981.4206 | 353.7738 | 494.7355 | 221.6167 | 480.4763 | 246.0034 | 219.5769
2881.2542 | 987.9557 | 354.2216 | 494.4602 | 213.0566 | 480.2549 | 246.2855 | 219.7909
2882.2542 | 982.8785 | 354.4281 | 494.3807 | 214.281 | 480.7379 | 246.5707 | 220.0036
2883.2542 | 972.0113 | 354.6472 | 494.4696 | 223.9161 | 481.005 | 246.7807 | 220.2243
2884.2542 | 970.7461 | 354.8742 | 494.2939 | 223.7075 | 482.2746 | 247.0555 | 220.4498
2885.2542 | 971.2311 | 355.1199 | 494.2969 | 222.6177 | 482.7374 | 247.3 | 220.6751
2886.2542 | 972.6741 | 355.3555 | 494.2437 | 223.9948 | 482.6646 | 247.3626 | 220.8854
2887.2542 | 969.0969 | 355.6189 | 494.0426 | 223.5853 | 482.5862 | 247.6815 | 221.0995
2888.2542 | 967.9596 | 355.8712 | 494.096 | 224.8489 | 482.7097 | 247.8851 | 221.3107
2889.2542 | 975.7645 | 356.2103 | 494.2914 | 222.3411 | 482.2055 | 248.1533 | 221.5186
2890.2542 | 974.2362 | 356.3991 | 494.1495 | 221.6656 | 481.488 | 248.4157 | 221.7412
2891.2542 | 986.5117 | 356.5556 | 494.1451 | 206.9812 | 481.0891 | 248.5911 | 221.9597
2892.2542 | 972.4269 | 356.5881 | 494.176 | 220.895 | 481.3595 | 248.8091 | 222.1613
2893.2542 | 985.5942 | 356.7826 | 494.0771 | 209.4967 | 480.9074 | 249.052 | 222.3829
2894.2542 | 961.6203 | 357.2442 | 493.8448 | 237.3199 | 480.7783 | 249.3038 | 222.5977
2895.2542 | 1002.9305 | 357.7205 | 493.7616 | 193.7723 | 481.6793 | 249.5496 | 222.8237
2896.2542 | 992.4815 | 358.0654 | 493.2677 | 202.5473 | 481.4136 | 249.6214 | 223.0428
2897.2542 | 637.183 | 358.2489 | 490.9531 | 576.49 | 480.4912 | 249.7214 | 222.917
2898.2542 | 634.3507 | 358.5315 | 490.5861 | 575.1434 | 480.627 | 249.9656 | 223.1356
2899.2542 | 640.2605 | 358.5957 | 489.5889 | 574.9561 | 480.7763 | 250.1501 | 223.3472
2900.2542 | 642.3479 | 359.0242 | 488.426 | 572.2959 | 482.23 | 250.1635 | 223.5618
2901.2542 | 647.4343 | 358.995 | 487.9602 | 572.8862 | 482.7493 | 250.3959 | 223.7704
2902.2542 | 644.9193 | 359.3097 | 487.7389 | 572.0957 | 482.7685 | 250.4706 | 223.9777
2903.2542 | 650.2567 | 359.5472 | 486.8092 | 574.0716 | 483.0381 | 250.6187 | 224.1827
2904.2542 | 649.8246 | 359.942 | 486.6535 | 571.2601 | 482.7375 | 250.939 | 224.3962
2905.2542 | 647.2211 | 360.2464 | 486.2313 | 570.8392 | 484.041 | 251.1902 | 224.6039
2906.2542 | 652.0533 | 360.5009 | 485.9212 | 569.8407 | 483.5698 | 251.3043 | 224.8114
2907.2542 | 654.0721 | 360.6871 | 486.4355 | 570.5017 | 483.2674 | 251.5648 | 225.0236
2908.2542 | 656.8249 | 360.7767 | 487.4521 | 572.2366 | 483.1063 | 251.5765 | 225.2293
2909.2542 | 656.2278 | 361.112 | 488.6662 | 572.0259 | 482.644 | 251.8169 | 225.4338
2910.2542 | 657.2178 | 361.0199 | 490.4715 | 568.2272 | 482.3862 | 252.0212 | 225.6465
2911.2542 | 650.4627 | 361.3277 | 491.8962 | 571.4951 | 482.1628 | 252.3149 | 225.8428
2912.2542 | 651.4003 | 361.6889 | 492.7864 | 572.342 | 482.3209 | 252.5952 | 226.053
2913.2542 | 651.7608 | 361.8005 | 493.587 | 570.5249 | 485.1186 | 252.8349 | 226.2494
2914.2542 | 651.5367 | 362.0153 | 494.3112 | 568.9426 | 485.7432 | 252.8464 | 226.4659
2915.2542 | 649.1138 | 362.4565 | 494.6574 | 570.3002 | 486.1104 | 253.1045 | 226.6593
2916.2542 | 646.2222 | 362.6066 | 494.9896 | 577.4425 | 487.4766 | 253.3661 | 226.861
2917.2542 | 650.5563 | 362.7179 | 495.5662 | 577.6167 | 487.327 | 253.6068 | 227.0504
2918.2542 | 645.827 | 363.0266 | 495.8253 | 576.9904 | 488.3732 | 253.8781 | 227.2745
2919.2542 | 644.9961 | 363.2221 | 496.1699 | 576.721 | 488.7361 | 254.1103 | 227.4792
2920.2542 | 646.419 | 363.4358 | 496.3048 | 576.0953 | 489.3086 | 254.3471 | 227.699
2921.2542 | 647.4999 | 363.6241 | 496.1311 | 573.02 | 489.3561 | 254.5777 | 227.9033
2922.2542 | 645.3095 | 363.8203 | 496.042 | 571.9689 | 489.022 | 254.6532 | 228.1063
2923.2542 | 649.8535 | 364.209 | 495.9632 | 573.9991 | 489.1229 | 254.8903 | 228.3002
2924.2542 | 649.5485 | 364.2622 | 495.8017 | 575.4099 | 489.1196 | 255.0479 | 228.5019
2925.2542 | 647.8427 | 364.5511 | 495.5691 | 575.2541 | 489.1846 | 255.0984 | 228.7051
2926.2542 | 647.8727 | 364.6958 | 495.5951 | 575.1988 | 488.7641 | 255.3706 | 228.8961
2927.2542 | 647.0649 | 364.9689 | 495.873 | 574.8624 | 488.6057 | 255.6072 | 229.0852
2928.2542 | 649.2967 | 365.3744 | 496.0333 | 574.7385 | 488.5986 | 255.7884 | 229.2836
2929.2542 | 649.3965 | 365.5655 | 495.8939 | 570.7803 | 488.6762 | 256.018 | 229.4819
2930.2542 | 649.0858 | 365.7349 | 495.8322 | 571.7809 | 488.4855 | 256.2435 | 229.6822
2931.2542 | 644.2424 | 365.9516 | 495.8383 | 575.2947 | 488.3691 | 256.4608 | 229.8876
2932.2542 | 642.3706 | 365.9784 | 496.1015 | 575.2757 | 487.542 | 256.6807 | 230.077
2933.2542 | 641.6716 | 366.5024 | 496.2847 | 575.7865 | 487.3367 | 256.8847 | 230.277
2934.2542 | 636.3964 | 366.5635 | 496.4872 | 579.1509 | 487.2445 | 257.057 | 230.4766
2935.2542 | 642.9249 | 366.5637 | 496.6345 | 577.0359 | 487.4254 | 257.1936 | 230.6794
2936.2542 | 643.6139 | 366.888 | 496.9454 | 580.2984 | 487.6049 | 257.3634 | 230.8777
2937.2542 | 642.571 | 367.246 | 497.0634 | 583.7957 | 487.3303 | 257.2697 | 231.0785
2938.2542 | 640.1916 | 367.4608 | 496.958 | 587.2873 | 487.8926 | 256.8274 | 231.2861
2939.2542 | 641.1122 | 367.6423 | 496.5769 | 587.8682 | 488.0544 | 256.7024 | 231.4812
2940.2542 | 643.2326 | 367.9274 | 496.1914 | 588.624 | 487.9637 | 256.7744 | 231.6955
2941.2542 | 644.9301 | 367.9657 | 495.9426 | 590.8886 | 487.714 | 257.0666 | 231.8996
2942.2542 | 645.7227 | 368.2231 | 495.9308 | 592.8599 | 487.7416 | 257.3476 | 232.0953
2943.2542 | 646.5302 | 368.3931 | 495.773 | 591.9975 | 487.8663 | 257.6127 | 232.3082
2944.2542 | 643.4252 | 368.6827 | 495.637 | 591.895 | 488.0725 | 257.7729 | 232.512
2945.2542 | 639.3312 | 368.7674 | 495.4402 | 590.3722 | 487.9924 | 258.0218 | 232.7185
2946.2542 | 633.4852 | 368.9947 | 494.9741 | 592.6624 | 487.7075 | 257.6793 | 232.9331
2947.2542 | 632.991 | 369.121 | 494.2688 | 593.4115 | 488.148 | 257.1197 | 233.1357
2948.2542 | 630.0016 | 369.4618 | 493.8579 | 595.4349 | 488.3775 | 257.1982 | 233.3338
2949.2542 | 626.3872 | 369.7273 | 493.3097 | 597.6021 | 488.0926 | 257.0339 | 233.5458
2950.2542 | 618.5136 | 370.0191 | 492.9021 | 600.4426 | 488.4417 | 257.1941 | 233.7522
2951.2542 | 609.936 | 370.2026 | 492.2736 | 609.2062 | 488.8295 | 257.2924 | 233.9535
2952.2542 | 611.1701 | 370.5819 | 491.8158 | 613.5319 | 489.212 | 257.3661 | 234.1595
2953.2542 | 613.4116 | 370.8226 | 491.3988 | 615.2891 | 490.2212 | 257.6617 | 234.3636
2954.2542 | 609.3626 | 371.0456 | 490.9031 | 619.0448 | 490.8178 | 257.889 | 234.5611
2955.2542 | 605.3775 | 371.2444 | 490.6792 | 623.2312 | 491.132 | 258.0738 | 234.7749
2956.2542 | 604.7741 | 371.5962 | 490.0796 | 628.0508 | 491.9823 | 258.268 | 234.9809
2957.2542 | 601.6221 | 371.6965 | 489.6673 | 631.2035 | 491.7389 | 258.2337 | 235.1838
2958.2542 | 596.4572 | 371.8715 | 489.2435 | 633.9407 | 492.3948 | 258.5557 | 235.3853
2959.2542 | 598.5701 | 371.9639 | 488.7456 | 637.1988 | 493.2764 | 258.8207 | 235.5782
2960.2542 | 595.8069 | 372.2654 | 488.2533 | 639.8437 | 493.95 | 258.8182 | 235.7705
2961.2542 | 590.8531 | 372.5557 | 487.8822 | 643.8596 | 493.612 | 258.8786 | 235.9892
2962.2542 | 592.7364 | 372.7033 | 487.3988 | 644.4915 | 493.3331 | 259.1279 | 236.1964
2963.2542 | 590.0991 | 372.7977 | 487.0529 | 645.5308 | 493.5669 | 259.1929 | 236.397
2964.2542 | 580.9829 | 373.0265 | 486.6458 | 649.2202 | 493.3695 | 259.4838 | 236.6042
2965.2542 | 577.0639 | 373.396 | 486.3254 | 651.8427 | 492.8766 | 259.748 | 236.8116
2966.2542 | 573.3909 | 373.5844 | 486.0531 | 653.2498 | 492.8359 | 260.0209 | 237.0179
2967.2542 | 570.7109 | 373.6978 | 485.8262 | 654.8518 | 493.4114 | 260.2459 | 237.231
2968.2542 | 566.6035 | 373.8571 | 485.6923 | 655.789 | 494.0331 | 260.4921 | 237.4454
2969.2542 | 565.9713 | 374.0151 | 485.6307 | 660.883 | 494.665 | 260.6372 | 237.6491
2970.2542 | 565.2166 | 374.3821 | 485.5681 | 664.662 | 495.1133 | 260.4123 | 237.8558
2971.2542 | 567.2661 | 374.5857 | 485.4711 | 665.564 | 495.6278 | 260.6299 | 238.0736
2972.2542 | 564.9776 | 374.7886 | 485.458 | 666.6273 | 495.5281 | 260.7006 | 238.2716
2973.2542 | 562.9492 | 375.0881 | 485.2851 | 667.0837 | 496.35 | 261.0431 | 238.4832
2974.2542 | 562.5921 | 375.319 | 485.06 | 668.1722 | 496.7961 | 261.1173 | 238.6913
2975.2542 | 567.7056 | 375.6132 | 484.8512 | 667.7341 | 496.9163 | 261.4138 | 238.8929
2976.2542 | 571.1283 | 375.8311 | 484.6231 | 667.9156 | 496.6861 | 261.6432 | 239.112
2977.2542 | 569.0996 | 376.0472 | 484.5589 | 668.887 | 496.9554 | 261.8616 | 239.3171
2978.2542 | 574.1022 | 376.3299 | 484.3202 | 667.4238 | 497.1053 | 262.0526 | 239.516
2979.2542 | 574.2861 | 376.4423 | 483.9835 | 668.0136 | 497.277 | 262.248 | 239.729
2980.2542 | 572.7891 | 376.7659 | 483.7346 | 669.4789 | 497.3028 | 262.3484 | 239.9309
2981.2542 | 570.5567 | 376.9539 | 483.6077 | 670.3628 | 496.9569 | 262.1459 | 240.1321
2982.2542 | 567.4705 | 377.2835 | 483.3362 | 672.4176 | 497.1055 | 262.3806 | 240.3366
2983.2542 | 563.6947 | 377.6255 | 483.1592 | 674.3482 | 497.2336 | 262.3168 | 240.5423
2984.2542 | 555.782 | 377.8614 | 482.9712 | 679.91 | 497.1061 | 262.4524 | 240.746
2985.2542 | 557.7483 | 378.3261 | 482.7688 | 681.395 | 497.2791 | 262.329 | 240.9578
2986.2542 | 557.2791 | 378.5942 | 482.5269 | 684.4573 | 497.3253 | 262.6387 | 241.1638
2987.2542 | 558.2717 | 378.7531 | 482.2064 | 686.2562 | 497.8974 | 262.7434 | 241.3634
2988.2542 | 565.7792 | 378.8132 | 481.8533 | 686.9406 | 497.9616 | 262.8011 | 241.585
2989.2542 | 557.3816 | 379.1616 | 481.6097 | 690.969 | 498.8018 | 262.9744 | 241.8051
2990.2542 | 555.2583 | 379.0574 | 481.2941 | 691.779 | 499.3349 | 263.0518 | 242.0134
2991.2542 | 551.2984 | 379.2463 | 481.0573 | 694.894 | 499.6694 | 262.8315 | 242.2009
2992.2542 | 545.8699 | 379.554 | 480.7504 | 701.992 | 499.974 | 263.2004 | 242.4108
2993.2542 | 539.9619 | 379.7549 | 480.3894 | 705.9349 | 500.0966 | 263.2226 | 242.6028
2994.2542 | 533.2629 | 379.9597 | 480.1278 | 709.1467 | 500.6569 | 263.491 | 242.807
2995.2542 | 534.9191 | 380.2844 | 479.8274 | 711.5627 | 500.8562 | 263.8015 | 243.0039
2996.2542 | 530.8646 | 380.3768 | 479.6464 | 715.8687 | 500.6236 | 263.7487 | 243.2161
2997.2542 | 527.7186 | 380.5556 | 479.6439 | 720.305 | 500.4949 | 263.9511 | 243.4224
2998.2542 | 524.3436 | 380.9501 | 479.4485 | 722.4566 | 500.8375 | 264.314 | 243.6157
2999.2542 | 517.7149 | 381.1021 | 479.0032 | 724.9538 | 500.9212 | 264.5575 | 243.8287
3000.2542 | 514.6675 | 381.4728 | 478.6244 | 729.2021 | 501.1221 | 264.606 | 244.0421
3001.2542 | 513.3185 | 381.8517 | 478.3645 | 727.1573 | 500.9269 | 264.8517 | 244.2489
3002.2542 | 505.7798 | 382.0758 | 478.0904 | 732.3327 | 500.4822 | 265.0853 | 244.442
3003.2542 | 502.6459 | 382.3022 | 477.8864 | 734.5563 | 500.4387 | 265.2724 | 244.6605
3004.2542 | 505.3035 | 382.5254 | 477.8303 | 734.4098 | 500.2652 | 265.4842 | 244.8521
3005.2542 | 500.9919 | 382.5447 | 477.773 | 740.5575 | 500.7766 | 265.4283 | 245.0618
3006.2542 | 494.816 | 383.1193 | 477.5931 | 749.7545 | 501.1274 | 265.3923 | 245.2636
3007.2542 | 489.4438 | 383.1504 | 477.3581 | 754.5715 | 501.4184 | 265.2142 | 245.4666
3008.2542 | 484.6475 | 382.9738 | 477.0878 | 760.0694 | 501.3033 | 265.441 | 245.6836
3009.2542 | 481.0008 | 383.2582 | 476.9419 | 761.7376 | 501.7613 | 265.6792 | 245.8635
3010.2542 | 480.3626 | 383.019 | 476.9186 | 765.7576 | 501.4475 | 265.9978 | 246.0686
3011.2542 | 477.3497 | 382.9607 | 476.8136 | 768.773 | 501.5752 | 265.8305 | 246.2786
3012.2542 | 469.2499 | 383.195 | 476.7082 | 776.4114 | 501.6127 | 265.7791 | 246.4911
3013.2542 | 464.0686 | 383.5317 | 476.6407 | 778.2251 | 502.191 | 265.9055 | 246.6963
3014.2542 | 460.4216 | 383.6904 | 476.5027 | 782.631 | 502.4724 | 265.8432 | 246.8942
3015.2542 | 450.1221 | 383.5678 | 476.4086 | 791.6403 | 502.7026 | 266.2358 | 247.0825
3016.2542 | 444.9322 | 383.6596 | 476.328 | 796.0132 | 502.811 | 266.4489 | 247.2695
3017.2542 | 435.9042 | 383.6446 | 476.2307 | 805.272 | 502.8384 | 266.6611 | 247.4705
3018.2542 | 432.0875 | 383.8216 | 476.2322 | 808.3152 | 503.0362 | 266.8265 | 247.6582
3019.2542 | 432.1928 | 384.4113 | 476.1622 | 811.6458 | 502.9322 | 266.72 | 247.8532
3020.2542 | 443.3951 | 384.2521 | 476.0731 | 798.6439 | 503.087 | 266.5875 | 248.0669
3021.2542 | 443.2204 | 384.3383 | 475.9426 | 799.0563 | 503.1323 | 266.4086 | 248.2413
3022.2542 | 439.676 | 384.2523 | 475.5854 | 804.4382 | 503.2598 | 266.2263 | 248.4296
3023.2542 | 441.0796 | 384.4761 | 475.0164 | 810.0643 | 503.3393 | 266.3567 | 248.6449
3024.2542 | 441.9013 | 384.8577 | 474.6627 | 811.1393 | 503.9248 | 266.0386 | 248.843
3025.2542 | 436.9417 | 384.8145 | 474.2961 | 815.0929 | 503.8055 | 266.0701 | 249.046
3026.2542 | 435.8203 | 385.2479 | 474.071 | 815.3414 | 504.5598 | 266.4276 | 249.2506
3027.2542 | 434.3995 | 385.3969 | 473.8478 | 817.6096 | 505.0525 | 266.5446 | 249.4308
3028.2542 | 428.046 | 385.2355 | 473.6477 | 825.3991 | 505.3666 | 266.8267 | 249.6173
3029.2542 | 419.7469 | 385.7479 | 473.4568 | 833.5922 | 506.3568 | 266.8018 | 249.8245
3030.2542 | 415.8025 | 385.8988 | 473.3262 | 834.0951 | 506.5126 | 266.8193 | 250.0233
3031.2542 | 412.7318 | 386.2108 | 473.28 | 834.2453 | 506.6514 | 266.3028 | 250.225
3032.2542 | 414.1807 | 386.0957 | 473.2012 | 835.1617 | 506.7397 | 265.8159 | 250.4306
3033.2542 | 412.7552 | 386.1372 | 473.2117 | 836.5565 | 506.8537 | 264.981 | 250.6131
3034.2542 | 415.6787 | 386.6914 | 473.3407 | 837.5432 | 507.143 | 263.7626 | 250.8323
3035.2542 | 420.7244 | 386.6529 | 473.4354 | 836.2104 | 507.0685 | 263.8884 | 251.0286
3036.2542 | 421.097 | 386.9736 | 473.5223 | 837.8115 | 507.4291 | 263.4323 | 251.2236
3037.2542 | 416.492 | 386.8733 | 473.5079 | 839.757 | 507.8131 | 263.5127 | 251.4236
3038.2542 | 409.4337 | 386.9412 | 473.5445 | 845.3282 | 508.927 | 263.626 | 251.6244
3039.2542 | 413.1093 | 387.3201 | 473.583 | 841.0008 | 508.9655 | 263.7449 | 251.8299
3040.2542 | 449.6656 | 387.3095 | 473.6778 | 798.707 | 509.1642 | 263.8582 | 252.0067
3041.2542 | 460.2358 | 387.4551 | 473.7686 | 789.091 | 508.9779 | 263.9857 | 252.2029
3042.2542 | 486.6507 | 387.5345 | 473.9275 | 760.4722 | 509.1936 | 264.0965 | 252.4175
3043.2542 | 488.4309 | 387.5328 | 474.1084 | 756.2643 | 509.5137 | 264.2357 | 252.5952
3044.2542 | 484.1177 | 387.4986 | 474.2827 | 760.5286 | 509.7153 | 264.3483 | 252.7944
3045.2542 | 488.5628 | 387.6348 | 474.3957 | 754.5756 | 509.5591 | 264.4706 | 252.9852
3046.2542 | 508.0359 | 387.7228 | 474.5542 | 733.3279 | 509.3348 | 264.6064 | 253.2084
3047.2542 | 519.0327 | 388.0203 | 474.6113 | 722.4444 | 508.8584 | 264.7288 | 253.4034
3048.2542 | 529.0256 | 387.9663 | 474.7273 | 711.1427 | 509.0663 | 264.8571 | 253.6026
3049.2542 | 546.2069 | 388.0568 | 474.8081 | 690.0447 | 509.267 | 264.9787 | 253.8077
3050.2542 | 556.7892 | 388.22 | 474.8166 | 678.7654 | 509.4405 | 265.0926 | 253.9906
3051.2542 | 578.6622 | 388.374 | 474.7127 | 658.3757 | 509.1179 | 265.2169 | 254.1827
3052.2542 | 571.2602 | 388.5578 | 474.6937 | 663.536 | 509.5185 | 265.33 | 254.401
3053.2542 | 594.9075 | 388.6099 | 474.7445 | 635.6108 | 510.3964 | 265.4525 | 254.5635
3054.2542 | 619.5222 | 388.5194 | 474.7948 | 608.0555 | 509.5652 | 265.5872 | 254.755
3055.2542 | 640.6092 | 388.4253 | 474.8795 | 584.8603 | 509.1058 | 265.7138 | 254.9171
3056.2542 | 630.1576 | 388.9537 | 474.9324 | 596.2349 | 509.2436 | 265.8339 | 255.0965
3057.2542 | 634.0626 | 389.0149 | 475.0459 | 589.5206 | 509.4103 | 265.9691 | 255.3047
3058.2542 | 648.2836 | 389.715 | 475.1441 | 572.667 | 509.5449 | 266.0924 | 255.4934
3059.2542 | 663.4398 | 389.6692 | 475.156 | 555.2499 | 509.3532 | 266.2181 | 255.7049
3060.2542 | 676.0429 | 390.298 | 475.2664 | 545.027 | 509.4569 | 266.3415 | 255.9047
3061.2542 | 688.2886 | 390.2503 | 475.4258 | 529.4258 | 509.003 | 266.46 | 256.155
3062.2542 | 693.2529 | 390.4424 | 475.6115 | 522.9644 | 508.487 | 266.5736 | 256.3822
3063.2542 | 698.0473 | 390.6433 | 475.7386 | 517.867 | 508.4056 | 266.704 | 256.6907
3064.2542 | 699.4317 | 391.042 | 475.9235 | 515.5524 | 508.6082 | 266.8222 | 256.978
3065.2542 | 702.7554 | 391.387 | 476.0793 | 510.7273 | 508.9582 | 266.9469 | 257.4401
3066.2542 | 712.4273 | 391.3748 | 476.2895 | 502.5133 | 508.7707 | 267.0724 | 257.853
3067.2542 | 695.7954 | 391.5865 | 476.4376 | 517.9335 | 509.0582 | 267.1909 | 258.2506
3068.2542 | 709.9137 | 391.8815 | 476.5573 | 502.7869 | 509.0974 | 267.2979 | 258.5869
3069.2542 | 725.1032 | 391.9255 | 476.6785 | 485.3891 | 509.1548 | 267.4155 | 258.8967
3070.2542 | 737.269 | 392.2562 | 476.8053 | 472.1133 | 509.3576 | 267.532 | 259.174
3071.2542 | 761.3606 | 392.4586 | 476.9743 | 451.8631 | 509.2004 | 267.6637 | 259.4548
3072.2542 | 804.6519 | 392.7789 | 477.1511 | 411.2779 | 508.6716 | 267.7957 | 259.755
3073.2542 | 817.887 | 392.8163 | 477.3759 | 396.0012 | 508.2777 | 267.9271 | 260.0485
3074.2542 | 839.313 | 393.1601 | 477.5892 | 370.3311 | 508.4732 | 268.0581 | 260.3724
3075.2542 | 866.4673 | 393.2439 | 477.777 | 341.771 | 508.8918 | 268.1924 | 260.6737
3076.2542 | 868.8017 | 393.6573 | 477.8889 | 334.4662 | 509.4706 | 268.3342 | 260.9955
3077.2542 | 885.9181 | 393.5189 | 478.0631 | 314.0451 | 509.3641 | 268.4673 | 261.2495
3078.2542 | 887.6904 | 393.7911 | 478.317 | 311.7524 | 509.2393 | 268.6058 | 261.4742
3079.2542 | 904.1825 | 394.0062 | 478.4346 | 292.2555 | 509.6241 | 268.7433 | 261.6962
3080.2542 | 915.9669 | 394.4464 | 478.4968 | 278.864 | 509.1798 | 268.8754 | 261.8933
3081.2542 | 912.8253 | 394.533 | 478.6571 | 282.0143 | 509.1588 | 269.0136 | 262.1491
3082.2542 | 922.2071 | 394.7123 | 478.798 | 271.4397 | 509.1279 | 269.1545 | 262.3219
3083.2542 | 925.7914 | 394.9374 | 478.9661 | 268.7052 | 509.6156 | 269.2887 | 262.5202
3084.2542 | 945.8445 | 395.0798 | 479.1634 | 252.0057 | 509.9582 | 269.4368 | 262.7949
3085.2542 | 978.8438 | 394.9776 | 479.3148 | 216.0287 | 510.5533 | 269.5687 | 263.0124
3086.2542 | 994.7458 | 395.1809 | 479.4114 | 198.1466 | 510.8533 | 269.708 | 263.228
3087.2542 | 1041.393 | 395.7091 | 479.575 | 153.057 | 510.2955 | 269.8664 | 263.482
3088.2542 | 1072.3762 | 396.1101 | 479.7744 | 120.9895 | 510.3674 | 270.0194 | 263.7394
3089.2542 | 1085.0229 | 396.4377 | 479.9057 | 110.8441 | 510.8311 | 270.1651 | 263.9616
3090.2542 | 1107.1232 | 396.6002 | 480.0276 | 88.716 | 511.3241 | 270.3258 | 264.1791
3091.2542 | 1118.0645 | 397.0219 | 480.1146 | 76.9205 | 511.7793 | 270.4768 | 264.4772
3092.2542 | 1136.7138 | 397.189 | 480.2562 | 59.6461 | 511.6602 | 270.638 | 264.7161
3093.2542 | 1150.4263 | 397.6177 | 480.3551 | 48.9247 | 511.5354 | 270.7949 | 264.9477
3094.2542 | 1152.9346 | 397.7378 | 480.5036 | 46.3901 | 511.0306 | 270.9525 | 265.1556
3095.2542 | 1160.1516 | 397.9389 | 480.6261 | 39.0047 | 511.1144 | 271.1203 | 265.4033
3096.2542 | 1147.4681 | 398.3698 | 480.772 | 50.6939 | 510.9563 | 271.2813 | 265.6687
3097.2542 | 1158.9373 | 398.4829 | 480.8388 | 40.5045 | 511.1257 | 271.4558 | 265.9107
3098.2542 | 1047.1212 | 398.5192 | 480.8758 | 151.9083 | 510.7577 | 271.6323 | 266.0867
3099.2542 | NaN | 398.2757 | 479.1123 | 1245.0033 | 510.2612 | 271.7491 | 266.2403
3100.2542 | NaN | 398.5761 | 479.6664 | 1245.0039 | 510.1065 | 271.9222 | 266.4386
3101.2542 | 592.6687 | 399.0195 | 480.6964 | 641.5808 | 510.6028 | 272.1432 | 266.7282
3102.2542 | 242.5691 | 398.9203 | 480.421 | 1034.596 | 510.9522 | 272.3167 | 266.9454
3103.2542 | 291.7342 | 398.7235 | 480.6357 | 980.6954 | 510.8202 | 272.5086 | 267.1443
3104.2542 | 693.7044 | 399.3961 | 481.2824 | 536.6894 | 510.9795 | 272.6967 | 267.3526
3105.2542 | 181.0933 | 398.9387 | 480.7488 | 1097.5341 | 511.3181 | 272.8574 | 267.5431
3106.2542 | 340.1952 | 398.2336 | 480.4074 | 1245.0122 | 511.3002 | 273.0199 | 267.7515
3107.2542 | NaN | 397.3299 | 479.8929 | 1245.0137 | 511.0899 | 273.1842 | 267.9507
3108.2542 | NaN | 398.6402 | 479.106 | 1245.015 | 511.3127 | 273.343 | 268.0974
3109.2542 | NaN | 398.6374 | 479.4956 | 1245.0167 | 511.7571 | 273.5205 | 268.3255
3110.2542 | NaN | 398.4513 | 480.264 | 1245.0184 | 511.7716 | 273.721 | 268.5684
3111.2542 | NaN | 397.0493 | 481.1079 | 1245.0183 | 511.2821 | 273.9276 | 268.8083
3112.2542 | NaN | 395.2188 | 481.1714 | 1245.0199 | 511.0967 | 274.1209 | 269.017
3113.2542 | NaN | 395.0964 | 481.0384 | 1245.0207 | 510.8565 | 274.3006 | 269.1751
3114.2542 | NaN | 395.5747 | 480.7179 | 1245.0226 | 511.763 | 274.4782 | 269.3779
3115.2542 | NaN | 394.3461 | 481.2087 | 1245.024 | 512.4414 | 274.6776 | 269.6043
3116.2542 | NaN | 391.3198 | 481.6206 | 1245.0255 | 512.2577 | 274.8764 | 269.7949
3117.2542 | NaN | 392.2932 | 481.8001 | 1245.0257 | 512.2375 | 275.0627 | 270.0621
3118.2542 | 143.7798 | 392.6545 | 482.7033 | 1245.0279 | 512.1313 | 275.2779 | 270.2559
3119.2542 | 73.9933 | 393.9696 | 483.1007 | 1218.1656 | 511.8649 | 275.456 | 270.4934
3120.2542 | 109.5647 | 396.1882 | 482.9993 | 1245.0302 | 511.7423 | 275.679 | 270.6814
3121.2542 | NaN | 401.7259 | 482.8913 | 1245.0326 | 511.4796 | 275.8741 | 270.9035
3122.2542 | NaN | 402.6709 | 482.3495 | 1245.0332 | 511.7105 | 276.0481 | 271.043
3123.2542 | NaN | 405.5453 | 482.9056 | 1245.0339 | 510.9905 | 276.2702 | 271.2788
3124.2542 | NaN | 404.8038 | 481.7745 | 1245.0365 | 510.8333 | 276.4296 | 271.4062
3125.2542 | NaN | 404.9298 | 481.8329 | 1245.0377 | 510.3278 | 276.662 | 271.6424
3126.2542 | NaN | 404.8217 | 481.4748 | 1245.0393 | 510.9394 | 276.8589 | 271.8467
3127.2542 | NaN | 405.884 | 480.5016 | 1245.0401 | 511.1074 | 277.0421 | 271.9987
3128.2542 | NaN | 408.2024 | 483.3777 | 1245.041 | 510.2661 | 277.301 | 272.3184
3129.2542 | 398.8605 | 407.3902 | 484.6944 | 840.1181 | 509.7121 | 277.5093 | 272.5553
3130.2542 | 1041.0009 | 406.587 | 485.8922 | 162.0134 | 509.7277 | 277.7415 | 272.7787
3131.2542 | 1244.7393 | 406.7094 | 487.0373 | NaN | 509.1311 | 277.9567 | 273.0079
3132.2542 | 1244.7405 | 406.4615 | 488.053 | NaN | 509.2398 | 278.1569 | 273.2554
3133.2542 | 1244.7425 | 406.9464 | 487.3437 | NaN | 508.9919 | 278.3584 | 273.4211
3134.2542 | 910.385 | 410.5218 | 485.8519 | 284.6117 | 509.5832 | 278.5306 | 273.6452
3135.2542 | 1244.745 | 406.3594 | 487.9686 | NaN | 509.7044 | 278.7719 | 273.8568
3136.2542 | 1244.7463 | 411.0807 | 487.0439 | 260.072 | 510.0569 | 278.9519 | 273.9906
3137.2542 | 1244.7477 | 411.0905 | 487.4047 | NaN | 510.3567 | 279.1586 | 274.1718
3138.2542 | 1234.7047 | 407.5239 | 487.3712 | -14.6662 | 509.8537 | 279.3738 | 274.4097
3139.2542 | 953.9499 | 409.075 | 486.7829 | 241.7746 | 510.0994 | 279.522 | 274.6089
3140.2542 | 1244.7521 | 406.6776 | 489.6464 | NaN | 509.3467 | 279.7991 | 274.7962
3141.2542 | 1244.7525 | 406.183 | 490.0533 | NaN | 509.1362 | 280.0074 | 274.9483
3142.2542 | 1244.7543 | 407.1873 | 490.0618 | NaN | 509.2091 | 280.2077 | 275.108
3143.2542 | 1244.7558 | 406.792 | 490.854 | NaN | 509.4782 | 280.4115 | 275.3327
3144.2542 | 1244.7569 | 407.1513 | 490.5249 | NaN | 509.1276 | 280.6182 | 275.524
3145.2542 | 1244.7579 | 407.0115 | 490.7607 | NaN | 509.0595 | 280.8135 | 275.6472
3146.2542 | 1244.7596 | 407.0746 | 491.4585 | NaN | 509.6694 | 281.0241 | 275.8253
3147.2542 | 1244.7603 | 407.7986 | 491.4077 | NaN | 509.117 | 281.2335 | 275.9265
3148.2542 | 1244.7619 | 407.6172 | 491.4288 | NaN | 508.5884 | 281.4342 | 276.0792
3149.2542 | 1244.7634 | 407.6936 | 491.9709 | NaN | 508.8054 | 281.6521 | 276.2207
3150.2542 | 1244.7636 | 408.0183 | 493.452 | NaN | 508.7058 | 281.8368 | 276.3747
3151.2542 | 1244.7655 | 408.2746 | 493.5279 | NaN | 508.8706 | 282.0333 | 276.5526
3152.2542 | 1244.7666 | 408.1201 | 493.8304 | NaN | 508.3403 | 282.2499 | 276.6957
3153.2542 | 1244.768 | 408.5313 | 493.835 | NaN | 508.1607 | 282.4599 | 276.8271
3154.2542 | 1244.7684 | 408.5305 | 494.0114 | NaN | 508.6251 | 282.6386 | 277.0416
3155.2542 | 1244.7701 | 409.1942 | 493.8593 | NaN | 508.4148 | 282.8437 | 277.1437
3156.2542 | 1244.772 | 408.4712 | 494.0717 | NaN | 508.1991 | 283.0642 | 277.2784
3157.2542 | 1244.7729 | 408.7229 | 494.2382 | NaN | 508.3272 | 283.2653 | 277.4675
3158.2542 | 1244.7743 | 408.7139 | 494.4967 | NaN | 508.9446 | 283.4744 | 277.5849
3159.2542 | 1244.7756 | 409.1567 | 494.8382 | NaN | 509.2602 | 283.6673 | 277.7917
3160.2542 | 1244.7768 | 409.2706 | 494.7152 | NaN | 509.2352 | 283.8671 | 277.9416
3161.2542 | 1244.7789 | 409.2284 | 495.1805 | NaN | 508.9028 | 284.0942 | 278.0337
3162.2542 | 1244.7799 | 409.5236 | 494.8248 | NaN | 509.3986 | 284.2915 | 278.1622
3163.2542 | 1244.7818 | 409.8121 | 494.9531 | NaN | 509.0485 | 284.5036 | 278.2733
3164.2542 | 1244.7834 | 410.1224 | 494.7319 | NaN | 508.8725 | 284.7006 | 278.4086
3165.2542 | 1244.7847 | 410.3943 | 494.8631 | NaN | 508.5117 | 284.9126 | 278.5665
3166.2542 | 1244.785 | 410.8422 | 495.1863 | NaN | 508.4545 | 285.1045 | 278.6945
3167.2542 | 1244.7857 | 410.4801 | 495.4167 | NaN | 508.6963 | 285.3119 | 278.8675
3168.2542 | 1244.7872 | 410.8946 | 495.4825 | NaN | 509.0708 | 285.5388 | 279.0007
3169.2542 | 1244.7892 | 411.1337 | 495.781 | NaN | 509.1386 | 285.737 | 279.2302
3170.2542 | 1244.7907 | 411.2392 | 495.9334 | NaN | 509.0408 | 285.9507 | 279.3608
3171.2542 | 1244.7922 | 410.9265 | 496.3274 | NaN | 508.6281 | 286.1796 | 279.4395
3172.2542 | 1244.7931 | 411.6647 | 497.5393 | NaN | 508.0576 | 286.3613 | 279.586
3173.2542 | 1244.7933 | 411.8771 | 497.5035 | NaN | 507.5094 | 286.6104 | 279.6342
3174.2542 | 1244.7946 | 412.0849 | 497.528 | NaN | 507.4609 | 286.8369 | 279.777
3175.2542 | 1244.7967 | 412.015 | 497.7642 | NaN | 506.8115 | 287.0425 | 279.9573
3176.2542 | 1244.7982 | 412.3658 | 497.8386 | NaN | 506.705 | 287.2418 | 280.1141
3177.2542 | 1244.7992 | 412.4071 | 497.7858 | NaN | 506.6663 | 287.4579 | 280.1476
3178.2542 | 1244.7995 | 412.3773 | 497.8337 | NaN | 507.0111 | 287.6692 | 280.316
3179.2542 | 1244.8019 | 413.0021 | 497.649 | NaN | 507.7515 | 287.8831 | 280.4244
3180.2542 | 1244.8016 | 412.9578 | 497.465 | NaN | 508.041 | 288.1133 | 280.5932
3181.2542 | 1244.8036 | 413.8103 | 497.1752 | NaN | 508.1147 | 288.3203 | 280.6878
3182.2542 | 1244.8051 | 413.6074 | 497.8516 | NaN | 507.9545 | 288.5398 | 280.832
3183.2542 | 1244.8061 | 413.3683 | 498.6429 | NaN | 507.0893 | 288.7568 | 281.0103
3184.2542 | 1244.8078 | 413.4733 | 498.4248 | NaN | 508.3239 | 288.9771 | 281.1396
3185.2542 | 1244.8089 | 413.2896 | 499.1645 | NaN | 507.689 | 289.192 | 281.2737
3186.2542 | 1244.8092 | 413.373 | 498.853 | NaN | 507.5042 | 289.4014 | 281.4045
3187.2542 | 1244.8114 | 413.2236 | 498.9728 | NaN | 507.8447 | 289.6149 | 281.7315
3188.2542 | 1244.813 | 413.9134 | 498.5418 | NaN | 507.9901 | 289.8356 | 281.7755
3189.2542 | 1244.8137 | 413.8732 | 498.7434 | NaN | 507.8442 | 290.0295 | 281.8471
3190.2542 | 1244.8153 | 414.1186 | 498.0683 | NaN | 507.9433 | 290.2554 | 281.9323
3191.2542 | 1244.8164 | 414.2352 | 499.1154 | NaN | 507.5309 | 290.4774 | 282.1152
3192.2542 | 1244.8164 | 414.9121 | 498.4508 | NaN | 507.3638 | 290.7091 | 282.3294
3193.2542 | 1244.8191 | 414.9013 | 498.2806 | NaN | 507.5395 | 290.9537 | 282.4305
3194.2542 | 1244.8212 | 414.4379 | 501.3999 | NaN | 506.1161 | 291.2283 | 282.5957
3195.2542 | 1244.8221 | 414.2982 | 501.5053 | NaN | 505.9512 | 291.4715 | 282.6875
3196.2542 | 1244.8234 | 414.5204 | 501.7985 | NaN | 505.7449 | 291.7153 | 282.789
3197.2542 | 1244.8252 | 414.6229 | 502.0899 | NaN | 505.2749 | 291.9518 | 282.9343
3198.2542 | 1244.8262 | 415.009 | 502.0183 | NaN | 504.7492 | 292.1937 | 283.0201
3199.2542 | 1244.8279 | 415.1571 | 502.6991 | NaN | 503.8869 | 292.4338 | 283.1132
3200.2542 | 1244.8275 | 415.473 | 501.6205 | NaN | 505.0964 | 292.6518 | 283.2919
3201.2542 | 1244.8273 | 415.8025 | 502.0437 | NaN | 504.6992 | 292.8847 | 283.4426
3202.2542 | 1244.8311 | 415.9664 | 503.3526 | NaN | 503.7007 | 293.1445 | 283.6821
3203.2542 | 1244.83 | 415.7618 | 502.1474 | NaN | 504.1172 | 293.3665 | 283.6941
3204.2542 | 1244.8325 | 416.1096 | 503.0144 | NaN | 503.2131 | 293.6067 | 283.8785
3205.2542 | 1244.8335 | 415.9811 | 503.8163 | NaN | 502.5939 | 293.8572 | 283.9593
3206.2542 | 1244.8357 | 416.1143 | 503.6504 | NaN | 502.007 | 294.1038 | 284.1054
3207.2542 | 1244.8372 | 416.6159 | 503.5428 | NaN | 501.9893 | 294.3738 | 284.1676
3208.2542 | 1244.8376 | 416.4657 | 504.2759 | NaN | 501.9694 | 294.618 | 284.3588
3209.2542 | 1244.8387 | 416.5315 | 504.71 | NaN | 501.8449 | 294.8721 | 284.4684
3210.2542 | 1244.8408 | 416.7505 | 505.3164 | NaN | 501.7117 | 295.1174 | 284.6249
3211.2542 | 1244.8415 | 417.0849 | 505.2158 | NaN | 501.9105 | 295.3591 | 284.6967
3212.2542 | 1244.8434 | 417.0584 | 505.2915 | NaN | 502.3053 | 295.6061 | 284.8365
3213.2542 | 1244.8435 | 417.3719 | 505.7144 | NaN | 502.5117 | 295.8554 | 285.0227
3214.2542 | 1244.8454 | 417.5576 | 505.6561 | NaN | 502.4448 | 296.0832 | 285.1444
3215.2542 | 1244.847 | 417.9 | 504.4833 | NaN | 503.619 | 296.3178 | 285.0976
3216.2542 | 1244.8477 | 418.0801 | 506.2408 | NaN | 503.2596 | 296.5584 | 285.1234
3217.2542 | 1244.8485 | 417.8729 | 505.9058 | NaN | 503.6281 | 296.7926 | 285.0995
3218.2542 | 1244.8495 | 418.2418 | 507.501 | NaN | 503.882 | 297.0034 | 285.1615
3219.2542 | 1244.8501 | 418.332 | 508.0277 | NaN | 503.9385 | 297.2061 | 285.1956
3220.2542 | 1244.8512 | 418.622 | 507.9108 | NaN | 503.8727 | 297.4087 | 285.3004
3221.2542 | 1244.853 | 419.0856 | 507.4386 | NaN | 503.4986 | 297.63 | 285.4475
3222.2542 | 1244.8545 | 419.4372 | 509.8401 | NaN | 503.5851 | 297.8615 | 285.3897
3223.2542 | 1244.8542 | 419.8367 | 508.5286 | NaN | 503.2977 | 298.1245 | 285.5254
3224.2542 | 1244.8564 | 419.7444 | 510.3504 | NaN | 503.2955 | 298.3941 | 285.6944
3225.2542 | 1244.8575 | 420.4119 | 507.7599 | NaN | 504.2992 | 298.698 | 285.5201
3226.2542 | 1244.8584 | 420.1443 | 510.0863 | NaN | 503.5922 | 298.9809 | 285.8378
3227.2542 | 1244.8594 | 420.0803 | 510.7027 | NaN | 503.4154 | 299.2432 | 285.9601
3228.2542 | 1244.8595 | 420.308 | 512.8874 | NaN | 502.9819 | 299.5122 | 286.081
3229.2542 | 1244.8617 | 421.1825 | 513.5967 | NaN | 504.0196 | 299.8124 | 286.1463
3230.2542 | 1244.8635 | 422.0336 | 513.5404 | NaN | 504.1598 | 300.0967 | 286.2421
3231.2542 | 1244.8649 | 423.4514 | 507.2279 | NaN | 505.4715 | 300.3748 | 285.9993
3232.2542 | 1244.8653 | 424.9159 | 512.1509 | NaN | 504.3747 | 300.6378 | 286.2613
3233.2542 | 1244.8664 | 426.5662 | 511.9345 | NaN | 505.6908 | 300.7958 | 286.5377
3234.2542 | 1244.8671 | 428.2408 | 511.3678 | NaN | 506.1351 | 301.1486 | 286.4918
3235.2542 | 1244.8691 | 429.6814 | 512.8472 | NaN | 505.7002 | 301.4364 | 286.7166
3236.2542 | 1244.8702 | 432.6493 | 510.103 | NaN | 505.6074 | 301.673 | 287.1203
3237.2542 | 1244.8711 | 435.1717 | 506.1717 | NaN | 506.768 | 301.9754 | 286.8976
3238.2542 | 1244.8733 | 437.9745 | 507.4686 | NaN | 506.8357 | 302.2402 | 287.29
3239.2542 | 1244.8746 | 438.8379 | 509.3825 | NaN | 506.1011 | 302.4689 | 287.9215
3240.2542 | 1244.8754 | 439.8095 | 509.3114 | NaN | 506.879 | 302.7768 | 287.6173
3241.2542 | 1244.8761 | 441.2104 | 509.7885 | NaN | 507.0155 | 303.0981 | 287.5858
3242.2542 | 1244.8775 | 442.1705 | 510.8843 | NaN | 505.9757 | 303.4796 | 287.8839
3243.2542 | 1244.8779 | 443.9132 | 510.6637 | NaN | 507.5473 | 303.7543 | 287.762
3244.2542 | 1244.8803 | 445.6982 | 512.7367 | NaN | 506.651 | 304.0787 | 288.0965
3245.2542 | 1244.8802 | 446.9231 | 510.4891 | NaN | 508.6592 | 304.357 | 288.1253
3246.2542 | 1244.8825 | 447.667 | 512.0126 | NaN | 508.3595 | 304.5572 | 288.7348
3247.2542 | 1244.8826 | 447.6053 | 513.3069 | NaN | 508.1036 | 304.8262 | 288.9289
3248.2542 | 1244.8852 | 448.9302 | 511.067 | NaN | 508.8907 | 305.0335 | 288.7027
3249.2542 | 1244.8855 | 450.3812 | 514.1838 | NaN | 507.9624 | 305.3281 | 289.0217
3250.2542 | 1244.8872 | 450.4574 | 512.6809 | NaN | 507.2968 | 305.5192 | 289.526
3251.2542 | 1244.8865 | 451.8469 | 513.6835 | NaN | 507.9696 | 305.7961 | 289.0816
3252.2542 | 1244.8887 | 452.8923 | 515.2248 | NaN | 508.2431 | 306.0111 | 289.1923
3253.2542 | 1244.8897 | 452.7207 | 514.8008 | NaN | 508.2327 | 306.2687 | 289.3961
3254.2542 | 1244.8905 | 454.2671 | 514.7721 | NaN | 508.0249 | 306.5135 | 289.356
3255.2542 | 1244.8917 | 454.5191 | 515.8331 | NaN | 507.8873 | 306.7783 | 289.6878
3256.2542 | 1244.8935 | 455.4634 | 516.0011 | NaN | 507.0786 | 306.8679 | 290.3838
3257.2542 | 1244.894 | 456.2805 | 514.6939 | NaN | 506.9187 | 307.2976 | 290.3741
3258.2542 | 1244.8946 | 456.2242 | 515.3188 | NaN | 507.528 | 307.6317 | 290.2147
3259.2542 | 1244.8957 | 455.8637 | 512.6808 | NaN | 507.702 | 307.983 | 290.7406
3260.2542 | 1244.8969 | 455.7233 | 513.1689 | NaN | 508.7614 | 308.2961 | 290.6201
3261.2542 | 1244.8979 | 456.3383 | 514.8994 | NaN | 509.6746 | 308.5861 | 290.488
3262.2542 | 1244.8983 | 456.643 | 513.02 | NaN | 509.7537 | 308.9046 | 291.1233
3263.2542 | 1244.9003 | 458.1123 | 515.3271 | NaN | 510.0505 | 309.1762 | 290.9869
3264.2542 | 1244.9018 | 457.6819 | 512.8656 | NaN | 508.8881 | 309.4348 | 291.7338
3265.2542 | 1244.9015 | 457.9036 | 519.4695 | NaN | 509.8218 | 309.7199 | 291.3921
3266.2542 | 1244.9027 | 459.3777 | 517.223 | NaN | 510.009 | 309.9751 | 291.3533
3267.2542 | 1244.905 | 460.2851 | 518.5588 | NaN | 509.5724 | 310.2434 | 291.4935
3268.2542 | 1244.9052 | 460.0496 | 519.1293 | NaN | 508.2231 | 310.5492 | 292.2843
3269.2542 | 1244.906 | 460.8255 | 520.5127 | NaN | 509.5532 | 310.8531 | 292.1524
3270.2542 | 1244.9081 | 461.3023 | 519.9218 | NaN | 509.7638 | 311.1927 | 292.4344
3271.2542 | 1244.9083 | 461.8623 | 522.4198 | NaN | 508.5949 | 311.5391 | 293.0461
3272.2542 | 1244.91 | 461.3197 | 520.9798 | NaN | 507.623 | 311.9115 | 293.5908
3273.2542 | 1244.9116 | 462.345 | 519.4055 | NaN | 507.5019 | 312.3324 | 293.6985
3274.2542 | 1244.9129 | 461.8781 | 519.6349 | NaN | 506.9424 | 312.7531 | 294.1078
3275.2542 | 1244.9146 | 458.4036 | 520.8695 | NaN | 506.7799 | 313.1547 | 294.3973
3276.2542 | 1244.914 | 458.1802 | 523.2891 | NaN | 506.8514 | 313.5475 | 294.3795
3277.2542 | 1244.9149 | 457.9657 | 519.7652 | NaN | 506.5919 | 313.9836 | 294.6248
3278.2542 | 1244.917 | 456.8992 | 520.9735 | NaN | 506.5099 | 314.4059 | 294.7882
3279.2542 | 1244.918 | 457.5275 | 521.7194 | NaN | 505.9941 | 314.839 | 295.0294
3280.2542 | 1244.9185 | 457.3847 | 519.5072 | NaN | 505.7237 | 315.2479 | 295.3294
3281.2542 | 1244.9197 | 457.7491 | 520.6563 | NaN | 505.2684 | 315.6875 | 295.4871
3282.2542 | 1244.9199 | 456.8426 | 519.2556 | NaN | 504.4402 | 316.1151 | 295.9357
3283.2542 | 1244.9213 | 459.0847 | 521.0076 | NaN | 503.9767 | 316.5441 | 295.9434
3284.2542 | 1244.923 | 459.1082 | 518.9236 | NaN | 504.2257 | 316.9749 | 296.1075
3285.2542 | 1244.9233 | 457.9364 | 517.9112 | NaN | 504.6324 | 317.3994 | 296.5451
3286.2542 | 1244.9251 | 458.495 | 521.4224 | NaN | 503.2555 | 317.8397 | 297.6328
3287.2542 | 1244.9257 | 457.463 | 521.2145 | NaN | 503.5664 | 318.2649 | 297.8875
3288.2542 | 1244.9266 | 458.4311 | 523.1105 | NaN | 503.3345 | 318.6358 | 298.5522
3289.2542 | 1244.9275 | 459.5177 | 521.7538 | NaN | 504.4212 | 319.0558 | 298.29
3290.2542 | 1244.9284 | 458.6959 | 519.7473 | NaN | 504.8158 | 319.4473 | 298.2923
3291.2542 | 1244.9311 | 460.1028 | 523.3548 | NaN | 504.0585 | 319.9091 | 298.9369
3292.2542 | 1244.9318 | 460.872 | 525.0228 | NaN | 502.5251 | 320.3556 | 300.1439
3293.2542 | 1244.933 | 461.4544 | 525.9936 | NaN | 502.1634 | 320.8007 | 300.5208
3294.2542 | 1244.9353 | 463.0372 | 525.939 | NaN | 501.9101 | 321.1964 | 300.9906
3295.2542 | 1244.9356 | 463.5484 | 529.4334 | NaN | 502.7956 | 321.5741 | 300.2986
3296.2542 | 1244.9358 | 464.3426 | 529.3365 | NaN | 502.5383 | 321.9352 | 300.4735
3297.2542 | 1244.9365 | 464.5661 | 529.6683 | NaN | 502.1789 | 322.242 | 301.1156
3298.2542 | 1244.9367 | 465.5562 | 528.8854 | NaN | 503.0342 | 322.6779 | 301.1432
3299.2542 | 1244.9378 | 465.5867 | 530.863 | NaN | 503.8515 | 323.0209 | 301.493
3300.2542 | 1244.9389 | 465.7053 | 534.171 | NaN | 505.2871 | 323.4675 | 300.982
3301.2542 | 1244.9403 | 465.6692 | 536.3125 | NaN | 506.6542 | 323.8116 | 300.9625
3302.2542 | 1244.9409 | 465.7898 | 537.1038 | NaN | 506.6137 | 324.1549 | 300.9205
3303.2542 | 1244.9421 | 466.7944 | 537.7885 | NaN | 507.0493 | 324.5323 | 301.0218
3304.2542 | 1244.9436 | 467.7085 | 536.9927 | NaN | 508.1312 | 324.9183 | 301.5028
3305.2542 | 1244.9448 | 469.5751 | 538.3437 | NaN | 508.9466 | 325.3144 | 301.6632
3306.2542 | 1244.9459 | 468.3994 | 539.7762 | NaN | 508.8968 | 325.6954 | 301.8957
3307.2542 | 1244.9466 | 467.3491 | 540.0947 | NaN | 509.0277 | 326.0847 | 302.0488
3308.2542 | 1244.9472 | 467.429 | 539.9165 | NaN | 508.8862 | 326.475 | 302.3734
3309.2542 | 1244.9485 | 468.0431 | 539.3786 | NaN | 508.9145 | 326.8543 | 302.7883
3310.2542 | 1244.9496 | 469.4211 | 538.7854 | NaN | 508.6968 | 327.2407 | 303.1548
3311.2542 | 1244.9501 | 471.1171 | 539.2778 | NaN | 508.1944 | 327.6053 | 303.2979
3312.2542 | 1244.9513 | 470.4144 | 539.6679 | NaN | 507.9002 | 327.9586 | 303.7082
3313.2542 | 1244.9526 | 470.9188 | 539.9922 | NaN | 507.6948 | 328.3256 | 304.0862
3314.2542 | 1244.9529 | 470.9347 | 540.9553 | NaN | 507.686 | 328.7156 | 304.3084
3315.2542 | 1244.9543 | 471.3435 | 541.1288 | NaN | 507.456 | 329.1023 | 304.4643
3316.2542 | 1244.9557 | 472.6358 | 542.3877 | NaN | 508.1807 | 329.4563 | 304.4629
3317.2542 | 1244.9566 | 472.8455 | 542.9033 | NaN | 508.0466 | 329.8417 | 304.9154
3318.2542 | 1244.9575 | 471.8434 | 543.1413 | NaN | 508.6103 | 330.2146 | 305.2573
3319.2542 | 1244.958 | 471.1904 | 542.4557 | NaN | 508.7659 | 330.6046 | 305.4752
3320.2542 | 1244.9592 | 470.635 | 543.3756 | NaN | 509.3081 | 330.9521 | 305.9005
3321.2542 | 1244.9604 | 470.9218 | 543.7586 | NaN | 510.2069 | 331.3407 | 306.2561
3322.2542 | 1244.9608 | 471.2817 | 543.5922 | NaN | 510.4301 | 331.6878 | 306.4721
3323.2542 | 1244.9614 | 471.6343 | 543.5291 | NaN | 510.2358 | 332.0229 | 306.8769
3324.2542 | 1244.9637 | 470.629 | 544.3928 | NaN | 509.5153 | 332.4176 | 307.1086
3325.2542 | 1244.9631 | 470.7499 | 545.0819 | NaN | 508.7209 | 332.7701 | 307.328
3326.2542 | 1244.9647 | 470.3317 | 544.5731 | NaN | 507.1911 | 333.1401 | 307.8499
3327.2542 | 1244.966 | 470.6271 | 544.7408 | NaN | 506.6196 | 333.5246 | 308.1192
3328.2542 | 1244.9673 | 469.9613 | 545.3909 | NaN | 506.3487 | 333.8835 | 308.4496
3329.2542 | 1244.9674 | 469.5464 | 545.0135 | NaN | 506.0005 | 334.1903 | 308.702
3330.2542 | 1244.9696 | 468.9075 | 544.9454 | NaN | 505.7073 | 334.5481 | 309.0501
3331.2542 | 1244.9696 | 469.3746 | 546.2673 | NaN | 505.4789 | 334.8949 | 309.4454
3332.2542 | 1244.971 | 468.79 | 546.5772 | NaN | 504.7449 | 335.2397 | 309.8429
3333.2542 | 1244.9715 | 468.17 | 546.5042 | NaN | 504.5891 | 335.6065 | 309.9805
3334.2542 | 1244.9734 | 468.8552 | 546.5987 | NaN | 505.63 | 335.9554 | 310.2495
3335.2542 | 1244.974 | 469.4199 | 546.7709 | NaN | 506.1431 | 336.2921 | 310.7913
3336.2542 | 1244.975 | 471.8377 | 551.3041 | NaN | 502.8833 | 336.731 | 310.0845
3337.2542 | 1244.9749 | 472.6392 | 558.2449 | NaN | 502.3488 | 337.0589 | 310.2805
3338.2542 | 1244.9775 | 474.6494 | 557.7885 | NaN | 501.3091 | 337.3984 | 310.2474
3339.2542 | 1244.9779 | 475.0427 | 558.3168 | NaN | 502.0169 | 337.7249 | 310.3097
3340.2542 | 1244.979 | 475.4637 | 556.2294 | NaN | 502.7803 | 338.0162 | 310.46
3341.2542 | 1244.9798 | 475.915 | 557.237 | NaN | 503.4666 | 338.2846 | 311.1305
3342.2542 | 1244.9805 | 476.3247 | 556.4215 | NaN | 503.6848 | 338.5907 | 311.6883
3343.2542 | 1244.981 | 476.533 | 557.6719 | NaN | 502.0202 | 338.9659 | 311.6639
3344.2542 | 1244.9828 | 474.7845 | 556.9116 | NaN | 499.4525 | 339.4168 | 312.1012
3345.2542 | 1244.9836 | 475.2525 | 558.1912 | NaN | 500.8539 | 339.6918 | 312.0384
3346.2542 | 1244.9847 | 476.8226 | 556.4103 | NaN | 502.547 | 339.9424 | 312.4319
3347.2542 | 1244.9858 | 479.4506 | 554.3228 | NaN | 503.4429 | 340.2038 | 312.7049
3348.2542 | 1244.9872 | 481.7171 | 552.031 | NaN | 504.6966 | 340.5066 | 313.2187
3349.2542 | 1244.9886 | 485.0681 | 548.0649 | NaN | 505.9923 | 340.7833 | 313.3618
3350.2542 | 1244.9881 | 484.168 | 549.2129 | NaN | 505.1596 | 341.1153 | 313.5541
3351.2542 | 1244.9891 | 490.3337 | 543.3534 | NaN | 506.8193 | 341.3287 | 313.5841
3352.2542 | 1244.989 | 485.4868 | 547.5402 | NaN | 503.6918 | 341.7202 | 314.1714
3353.2542 | 1244.992 | 492.1561 | 540.0282 | NaN | 506.7948 | 341.9189 | 313.7839
3354.2542 | 1244.9918 | 487.0035 | 544.4787 | NaN | 504.8897 | 342.3122 | 314.5987
3355.2542 | 1244.9927 | 478.2863 | 555.9342 | NaN | 499.9817 | 342.7937 | 315.3521
3356.2542 | 1244.9947 | 475.0239 | 561.1778 | NaN | 498.136 | 343.1902 | 315.7742
3357.2542 | 1244.9947 | 476.1433 | 563.0108 | NaN | 498.1327 | 343.5653 | 315.9142
3358.2542 | 1244.9962 | 476.3407 | 566.4936 | NaN | 496.3175 | 343.8835 | 315.62
3359.2542 | 1244.9976 | 476.8832 | 567.1684 | NaN | 496.8506 | 344.1619 | 315.7841
3360.2542 | 1244.9986 | 479.2787 | 576.7659 | NaN | 491.4581 | 344.5956 | 317.7848
3361.2542 | 1244.9985 | 482.6204 | 573.769 | NaN | 493.0166 | 344.8008 | 318.0753
3362.2542 | 1245.0015 | 482.9199 | 570.0186 | NaN | 493.8404 | 345.019 | 318.0478
3363.2542 | 1245.0006 | 482.2793 | 577.9971 | NaN | 489.0832 | 345.4612 | 318.9864
3364.2542 | 1245.0012 | 497.5819 | 547.2866 | NaN | 503.3491 | 345.168 | 317.0435
3365.2542 | 1245.0016 | 498.4747 | 542.7934 | NaN | 504.5943 | 345.3892 | 316.8656
3366.2542 | 1245.0026 | 498.0496 | 547.142 | NaN | 501.7988 | 345.8158 | 317.8271
3367.2542 | 1245.0038 | 495.5462 | 553.7339 | NaN | 497.9139 | 346.2571 | 318.7552
3368.2542 | 1245.0048 | 501.2295 | 548.8538 | NaN | 499.8547 | 346.425 | 318.6654
3369.2542 | 1245.0064 | 489.2798 | 569.2005 | NaN | 488.8612 | 347.1858 | 320.6534
3370.2542 | 1245.0074 | 487.5021 | 570.1642 | NaN | 489.4144 | 347.4372 | 320.8236
3371.2542 | 1245.009 | 491.1653 | 565.7482 | NaN | 491.7214 | 347.6437 | 320.7721
3372.2542 | 1245.009 | 492.9465 | 566.0232 | NaN | 490.6982 | 347.9176 | 321.0496
3373.2542 | 1245.0088 | 487.1767 | 576.374 | NaN | 486.0166 | 348.3682 | 322.0762
3374.2542 | 1245.0108 | 491.3765 | 571.2353 | NaN | 489.2066 | 348.4926 | 321.6989
3375.2542 | 1245.0116 | 491.9881 | 570.7291 | NaN | 488.2212 | 348.8596 | 322.3566
3376.2542 | 1245.0136 | 494.1719 | 565.8957 | NaN | 488.9179 | 349.1406 | 322.3503
3377.2542 | 1245.0133 | 502.1518 | 537.1049 | NaN | 502.8651 | 348.7042 | 320.4401
3378.2542 | 1245.0139 | 504.8073 | 527.4063 | NaN | 508.587 | 348.6856 | 319.8559
3379.2542 | 1115.6671 | 480.3017 | 514.0024 | 57.0504 | 524.7781 | 348.5412 | 317.8782
3380.2542 | 1113.4627 | 479.2439 | 514.1187 | 55.6745 | 524.7662 | 348.8373 | 318.1683
3381.2542 | 1113.753 | 478.6733 | 514.2829 | 53.9516 | 524.2616 | 349.1277 | 318.4614
3382.2542 | 1088.1569 | 477.0899 | 514.3692 | 77.9781 | 524.0694 | 349.4017 | 318.678
3383.2542 | 1100.3058 | 476.5676 | 514.5021 | 69.6484 | 524.0211 | 349.6723 | 319.0531
3384.2542 | 1105.7037 | 476.8608 | 514.2477 | 59.1087 | 524.4174 | 349.9341 | 319.372
3385.2542 | 1117.0426 | 477.5185 | 514.292 | 45.2883 | 524.3082 | 350.1987 | 319.6239
3386.2542 | 1138.2538 | 477.6444 | 514.2319 | 22.396 | 525.1135 | 350.5005 | 319.8677
3387.2542 | 1140.1931 | 477.2499 | 514.336 | 20.8895 | 525.3117 | 350.7655 | 320.0879
3388.2542 | 1150.7952 | 477.3765 | 514.3918 | 10.7228 | 524.9422 | 351.0211 | 320.3961
3389.2542 | 1153.5524 | 477.5214 | 514.4002 | 3.0788 | 524.7735 | 351.2674 | 320.6121
3390.2542 | 1162.6302 | 477.4654 | 514.5802 | -7.0586 | 525.7367 | 351.5004 | 320.8337
3391.2542 | 1177.6349 | 479.0472 | 514.8665 | NaN | 526.5238 | 351.7418 | 321.2172
3392.2542 | 1178.573 | 478.1349 | 514.9546 | NaN | 527.1153 | 351.99 | 321.4617
3393.2542 | 1195.7221 | 477.1888 | 515.1034 | NaN | 529.0139 | 352.2294 | 321.6502
3394.2542 | 1206.2831 | 478.0123 | 515.2989 | NaN | 531.3129 | 352.5049 | 321.7399
3395.2542 | 1218.4195 | 477.3556 | 515.2978 | NaN | 531.8054 | 352.697 | 321.7562
3396.2542 | 1245.0318 | 477.3679 | 515.3516 | NaN | 531.2417 | 352.9913 | 321.8604
3397.2542 | 1245.0325 | 476.7995 | 515.5447 | -16.2763 | 530.5356 | 353.1944 | 321.9406
3398.2542 | 1245.0333 | 477.6636 | 515.6803 | 49.2111 | 529.6263 | 353.3889 | 322.1351
3399.2542 | 1245.0343 | 477.5168 | 515.9626 | 457.7036 | 528.3572 | 353.6708 | 322.4148
3400.2542 | 1245.0358 | 477.4279 | 516.1867 | 807.3971 | 527.323 | 353.9575 | 322.4554
3401.2542 | 1245.0365 | 477.1142 | 516.322 | 1051.9214 | 526.8749 | 354.2284 | 322.6626
3402.2542 | 1245.0378 | 477.1238 | 516.3197 | NaN | 526.7593 | 354.5133 | 322.896
3403.2542 | 1245.0388 | 476.8107 | 516.4344 | NaN | 526.6117 | 354.7956 | 323.2615
3404.2542 | 1245.0405 | 476.8083 | 516.604 | NaN | 526.8502 | 355.0824 | 323.5415
3405.2542 | 1245.0406 | 477.2096 | 516.7665 | NaN | 527.8746 | 355.3598 | 323.6696
3406.2542 | 1245.0415 | 477.1384 | 516.8093 | NaN | 529.1223 | 355.6672 | 323.7788
3407.2542 | 1245.0429 | 477.256 | 516.9039 | NaN | 528.9809 | 355.8748 | 323.9867
3408.2542 | 1245.043 | 476.1117 | 517.1262 | NaN | 528.8987 | 356.1126 | 324.1067
3409.2542 | 1245.0458 | 475.9531 | 517.1791 | NaN | 528.8877 | 356.3114 | 324.38
3410.2542 | 1245.0464 | 475.6075 | 517.347 | NaN | 528.1112 | 356.5152 | 324.5586
3411.2542 | 1245.046 | 474.796 | 517.3905 | NaN | 527.9844 | 356.6266 | 324.7551
3412.2542 | 1245.0462 | 474.5971 | 517.5334 | NaN | 528.1963 | 356.7643 | 324.8836
3413.2542 | 1245.0487 | 475.3381 | 517.6906 | NaN | 528.2528 | 356.8772 | 325.0675
3414.2542 | 1245.0486 | 475.1071 | 517.7017 | NaN | 528.3336 | 356.9369 | 325.3323
3415.2542 | 1245.0495 | 473.5814 | 517.7956 | NaN | 528.6402 | 357.0148 | 325.5846
3416.2542 | 1245.0499 | 473.7841 | 517.777 | NaN | 528.6667 | 357.0578 | 325.749
3417.2542 | 1245.0517 | 474.4377 | 517.8895 | NaN | 529.3115 | 357.1289 | 325.8264
3418.2542 | 1245.0525 | 474.0904 | 517.9917 | NaN | 529.4602 | 357.2303 | 325.8406
3419.2542 | 1245.053 | 473.7163 | 517.9987 | NaN | 529.8829 | 357.352 | 325.9796
3420.2542 | 1245.0545 | 474.5204 | 517.9793 | NaN | 530.0599 | 357.5032 | 326.015
3421.2542 | 1245.0551 | 475.0643 | 517.9782 | NaN | 530.6909 | 357.6541 | 326.0408
3422.2542 | 1245.0566 | 475.0972 | 517.9586 | NaN | 530.5512 | 357.7898 | 325.9336
3423.2542 | 1245.0574 | 474.9911 | 517.9441 | NaN | 530.9089 | 357.9456 | 325.8675
3424.2542 | 1245.0582 | 475.5916 | 517.9904 | NaN | 530.2594 | 358.0915 | 326.1084
3425.2542 | 1245.0589 | 476.1597 | 518.0291 | NaN | 530.0044 | 358.2387 | 326.2512
3426.2542 | 1245.0601 | 477.4954 | 518.112 | NaN | 530.4708 | 358.4103 | 326.3598
3427.2542 | 1245.061 | 477.7548 | 518.1928 | NaN | 530.9059 | 358.5698 | 326.53
3428.2542 | 1245.0616 | 477.8863 | 518.2665 | NaN | 531.057 | 358.6891 | 327.204
3429.2542 | 1245.0611 | 477.2687 | 518.4692 | NaN | 530.8851 | 358.8647 | 327.3928
3430.2542 | 1245.064 | 476.8218 | 518.5046 | NaN | 530.169 | 359.0415 | 327.6071
3431.2542 | 1245.0652 | 477.1932 | 518.6197 | NaN | 530.4892 | 359.2094 | 327.7896
3432.2542 | 1245.0658 | 477.7599 | 518.6804 | NaN | 531.0195 | 359.358 | 327.9614
3433.2542 | 1245.0667 | 479.1559 | 518.5931 | NaN | 531.0478 | 359.5257 | 328.2722
3434.2542 | 1245.0668 | 479.8252 | 518.5739 | NaN | 531.3438 | 359.7397 | 328.4487
3435.2542 | 1245.068 | 479.9571 | 518.5146 | NaN | 531.0939 | 359.8816 | 328.2165
3436.2542 | 1245.0691 | 480.7791 | 518.6261 | NaN | 530.9158 | 360.0431 | 328.1464
3437.2542 | 1245.0704 | 481.1715 | 518.5966 | NaN | 532.3232 | 360.2043 | 328.3796
3438.2542 | 1245.0714 | 480.7761 | 518.7156 | NaN | 532.0067 | 360.3566 | 328.6436
3439.2542 | 1245.0723 | 481.0174 | 518.7682 | NaN | 532.1026 | 360.5015 | 328.9526
3440.2542 | 1245.0726 | 479.7687 | 518.8541 | NaN | 531.3852 | 360.6613 | 329.2019
3441.2542 | 1245.0738 | 479.5742 | 518.9655 | NaN | 531.3455 | 360.8354 | 329.4233
3442.2542 | 1245.0755 | 479.9663 | 519.0882 | NaN | 532.0003 | 361.1103 | 329.6591
3443.2542 | 1245.0768 | 481.0044 | 519.2403 | NaN | 531.8655 | 361.2196 | 329.803
3444.2542 | 1245.0771 | 482.1528 | 519.3664 | NaN | 532.1816 | 361.3685 | 329.991
3445.2542 | 1245.0783 | 482.9099 | 519.5092 | NaN | 531.6722 | 361.536 | 330.3143
3446.2542 | 1245.0793 | 483.2262 | 519.6947 | NaN | 531.6641 | 361.7214 | 330.5552
3447.2542 | 1245.081 | 483.4159 | 519.7847 | NaN | 531.3639 | 361.8695 | 330.9627
3448.2542 | 1245.0807 | 484.604 | 519.7916 | NaN | 530.9332 | 362.1344 | 331.21
3449.2542 | 1245.0819 | 484.0298 | 519.8883 | NaN | 530.5953 | 362.3361 | 331.3766
3450.2542 | 1245.0826 | 484.5897 | 519.8212 | NaN | 529.8802 | 362.5845 | 331.7004
3451.2542 | 1245.0839 | 485.7482 | 519.8911 | NaN | 529.9516 | 362.7465 | 332.0452
3452.2542 | 1245.0846 | 486.1402 | 519.9009 | NaN | 530.5801 | 362.9116 | 332.2453
3453.2542 | 1245.0857 | 486.8657 | 519.9794 | NaN | 530.7879 | 363.1493 | 332.5897
3454.2542 | 1245.0863 | 486.2737 | 519.9048 | NaN | 529.9979 | 363.3354 | 333.0063
3455.2542 | 1245.0878 | 485.9304 | 519.8986 | NaN | 529.0744 | 363.4959 | 333.2895
3456.2542 | 1245.0892 | 486.5601 | 520.0217 | NaN | 528.545 | 363.6534 | 333.275
3457.2542 | 1245.0907 | 487.4292 | 520.0739 | NaN | 528.1131 | 363.8224 | 333.3614
3458.2542 | 1245.0904 | 488.4644 | 520.0465 | NaN | 528.6123 | 364.0054 | 333.5983
3459.2542 | 1245.0916 | 488.371 | 519.9926 | NaN | 528.5168 | 364.1902 | 333.8326
3460.2542 | 1245.0931 | 487.5345 | 519.8975 | NaN | 529.7994 | 364.3423 | 334.0447
3461.2542 | 1245.0932 | 487.7156 | 520.0096 | NaN | 529.6697 | 364.4984 | 334.2915
3462.2542 | 1245.0946 | 486.7889 | 519.9743 | NaN | 530.1421 | 364.6893 | 334.4358
3463.2542 | 1245.0955 | 487.2265 | 519.9528 | NaN | 529.8608 | 364.8223 | 334.8533
3464.2542 | 1245.0974 | 486.4865 | 520.0809 | 1219.0539 | 530.3619 | 365.0397 | 335.1316
3465.2542 | 1245.0976 | 486.2767 | 520.2406 | 850.1826 | 530.3311 | 365.1875 | 335.2773
3466.2542 | 1245.0982 | 487.1106 | 520.3693 | 281.6333 | 530.1792 | 365.3883 | 335.4181
3467.2542 | 1245.0988 | 488.7324 | 520.4542 | 101.3996 | 530.5262 | 365.5308 | 335.5952
3468.2542 | 1245.1005 | 489.7062 | 520.5186 | -7.2183 | 530.8468 | 365.6909 | 335.9154
3469.2542 | 1244.1894 | 490.894 | 520.6118 | NaN | 530.7787 | 365.9162 | 336.1565
3470.2542 | 1210.3559 | 491.0067 | 520.623 | NaN | 532.0107 | 366.0393 | 336.3548
3471.2542 | 1205.5047 | 490.6964 | 520.6401 | NaN | 533.1346 | 366.2059 | 336.4934
3472.2542 | 1206.9143 | 489.825 | 520.6779 | NaN | 533.4054 | 366.3677 | 336.5843
3473.2542 | 1195.7102 | 489.9049 | 520.7159 | NaN | 534.4908 | 366.5363 | 336.8635
3474.2542 | 1181.6958 | 489.717 | 520.7069 | NaN | 534.7861 | 366.6986 | 337.1522
3475.2542 | 1167.8712 | 489.3794 | 520.7503 | NaN | 534.8603 | 366.8745 | 337.2591
3476.2542 | 1153.1123 | 488.9449 | 520.7904 | -16.2707 | 534.301 | 367.0823 | 337.5551
3477.2542 | 1128.6659 | 489.1156 | 520.9032 | 9.7412 | 534.1452 | 367.2239 | 338.1691
3478.2542 | 1129.9872 | 489.0062 | 520.8965 | 7.4332 | 533.4583 | 367.4098 | 338.104
3479.2542 | 1121.9149 | 489.1446 | 520.9622 | 13.8222 | 533.092 | 367.6156 | 338.3062
3480.2542 | 1120.7211 | 487.8809 | 521.0969 | 16.7496 | 532.1127 | 367.7961 | 338.6428
3481.2542 | 1113.9062 | 487.7372 | 521.0752 | 21.4666 | 531.4932 | 367.9671 | 338.8675
3482.2542 | 1099.8369 | 487.5069 | 521.0994 | 34.646 | 531.6166 | 368.1315 | 338.9218
3483.2542 | 1098.2251 | 487.9386 | 521.2996 | 35.4192 | 531.468 | 368.3209 | 339.1597
3484.2542 | 1094.7463 | 488.0737 | 521.3443 | 37.3487 | 532.0973 | 368.4859 | 339.5386
3485.2542 | 1094.5705 | 487.1715 | 521.3399 | 36.9821 | 531.7216 | 368.6716 | 339.8141
3486.2542 | 1103.0051 | 486.8872 | 521.3261 | 29.9669 | 531.402 | 368.8665 | 340.1758
3487.2542 | 1095.508 | 486.9725 | 521.2937 | 39.9697 | 530.9732 | 369.0323 | 340.2935
3488.2542 | 1092.216 | 487.4881 | 521.3305 | 44.1609 | 530.5245 | 369.1849 | 340.4097
3489.2542 | 1095.8945 | 486.5304 | 521.3164 | 42.8944 | 530.2337 | 369.3343 | 340.8214
3490.2542 | 1098.9384 | 486.0283 | 521.2459 | 39.4407 | 529.9593 | 369.5135 | 341.0934
3491.2542 | 1095.0708 | 485.5129 | 521.2593 | 42.3684 | 529.8011 | 369.72 | 341.3805
3492.2542 | 1084.3988 | 485.4589 | 521.1978 | 51.5551 | 529.5565 | 369.8781 | 341.64
3493.2542 | 1078.4492 | 485.7383 | 521.2615 | 57.6884 | 529.7469 | 370.0568 | 341.7588
3494.2542 | 1080.0636 | 486.1257 | 521.3526 | 54.9562 | 530.3505 | 370.2603 | 342.081
3495.2542 | 788.2846 | 486.4183 | 521.1034 | 392.7019 | 531.9643 | 370.4827 | 342.6777
3496.2542 | 788.1157 | 487.6416 | 521.1354 | 394.1577 | 532.176 | 370.5757 | 343.7214
3497.2542 | 789.0499 | 487.6535 | 521.1043 | 393.8958 | 532.6164 | 370.7026 | 343.8235
3498.2542 | 790.4748 | 487.5099 | 521.2286 | 392.5842 | 533.3343 | 370.902 | 344.0415
3499.2542 | 793.5672 | 486.6426 | 521.2491 | 389.8463 | 534.2151 | 371.1086 | 344.2758
3500.2542 | 792.0386 | 486.6282 | 521.3956 | 391.1163 | 534.51 | 371.3131 | 344.3767
3501.2542 | 792.5411 | 486.8995 | 521.549 | 389.9835 | 534.0993 | 371.5376 | 344.5452
3502.2542 | 793.1878 | 488.1198 | 521.7242 | 388.8575 | 535.2436 | 371.6402 | 345.2837
3503.2542 | 796.1706 | 488.2006 | 521.8234 | 387.058 | 535.1951 | 371.7967 | 345.6016
3504.2542 | 796.6938 | 487.9196 | 521.9033 | 388.8697 | 534.7293 | 371.9951 | 345.7092
3505.2542 | 796.8496 | 488.1639 | 522.1375 | 387.9376 | 534.5636 | 372.1666 | 345.7898
3506.2542 | 798.1318 | 489.0822 | 522.3198 | 386.7846 | 535.0751 | 372.3436 | 345.9623
3507.2542 | 797.6636 | 489.6082 | 522.3889 | 387.4821 | 534.8693 | 372.5418 | 346.113
3508.2542 | 797.82 | 488.296 | 522.4237 | 386.9766 | 534.9658 | 372.7241 | 346.3256
3509.2542 | 801.3854 | 488.5548 | 522.4946 | 385.3561 | 535.4504 | 372.8862 | 346.5193
3510.2542 | 805.5119 | 488.3054 | 522.5921 | 382.9256 | 534.4295 | 373.0857 | 346.8763
3511.2542 | 807.0379 | 488.4061 | 522.6839 | 380.8042 | 533.6609 | 373.2616 | 347.0996
3512.2542 | 808.3927 | 488.6892 | 522.8277 | 380.4333 | 533.4131 | 373.471 | 347.3544
3513.2542 | 807.8007 | 487.6613 | 522.9644 | 380.1317 | 534.0561 | 373.592 | 347.4866
3514.2542 | 811.8174 | 487.7381 | 523.1814 | 377.105 | 533.4833 | 373.8511 | 347.304
3515.2542 | 814.0172 | 488.1344 | 523.1704 | 375.3436 | 532.9002 | 374.1106 | 347.4853
3516.2542 | 816.1438 | 488.7157 | 523.1761 | 374.9958 | 533.6819 | 374.2065 | 348.2189
3517.2542 | 819.4825 | 488.7444 | 523.1324 | 374.205 | 533.5456 | 374.3467 | 348.4228
3518.2542 | 821.8496 | 488.1461 | 523.1771 | 373.5343 | 533.3494 | 374.5507 | 348.6121
3519.2542 | 822.3169 | 488.7188 | 523.1426 | 374.3903 | 533.4618 | 374.6734 | 348.5734
3520.2542 | 824.5594 | 489.1365 | 523.1951 | 371.6905 | 532.6026 | 374.8409 | 348.6368
3521.2542 | 826.5594 | 490.2575 | 523.1818 | 369.1727 | 532.6199 | 375.0192 | 348.9187
3522.2542 | 826.9604 | 489.8198 | 523.2703 | 366.7075 | 533.3525 | 375.1864 | 349.1435
3523.2542 | 832.2393 | 490.5338 | 523.1652 | 363.536 | 533.8138 | 375.3706 | 349.289
3524.2542 | 834.4652 | 490.3579 | 523.2102 | 361.1989 | 534.2668 | 375.547 | 349.6373
3525.2542 | 841.0638 | 491.1947 | 523.2717 | 358.3427 | 534.5703 | 375.7534 | 349.8541
3526.2542 | 842.9419 | 490.6466 | 523.1631 | 352.7765 | 533.9676 | 375.925 | 350.0115
3527.2542 | 851.0343 | 489.152 | 523.2734 | 345.3072 | 534.0736 | 376.1165 | 350.2993
3528.2542 | 853.7316 | 489.7486 | 523.3001 | 342.0115 | 534.4557 | 376.2343 | 350.4857
3529.2542 | 865.8206 | 489.0692 | 523.2573 | 330.7211 | 535.485 | 376.3773 | 350.7317
3530.2542 | 874.5729 | 489.6773 | 523.3732 | 324.3264 | 535.3044 | 376.5429 | 351.0669
3531.2542 | 888.3733 | 489.857 | 523.1426 | 311.3011 | 535.1114 | 376.7328 | 351.4405
3532.2542 | 894.6674 | 491.275 | 523.1266 | 305.4854 | 534.6418 | 376.9269 | 351.6359
3533.2542 | 900.3752 | 492.6107 | 523.149 | 302.7353 | 534.572 | 377.1006 | 351.8822
3534.2542 | 904.3441 | 493.3728 | 523.1013 | 298.7399 | 534.0148 | 377.2772 | 351.9551
3535.2542 | 906.7546 | 492.297 | 523.0573 | 294.8153 | 533.903 | 377.3955 | 352.2418
3536.2542 | 910.4042 | 492.4992 | 523.0008 | 290.9585 | 534.6155 | 377.5126 | 352.5061
3537.2542 | 912.3948 | 492.7126 | 522.9409 | 288.0982 | 534.1495 | 377.7527 | 352.5973
3538.2542 | 914.836 | 492.4315 | 522.8816 | 285.8629 | 534.2742 | 377.9529 | 353.1008
3539.2542 | 913.0244 | 492.689 | 522.8998 | 285.8207 | 533.9433 | 378.0501 | 353.2859
3540.2542 | 917.8127 | 491.6996 | 522.9776 | 281.8439 | 533.2958 | 378.1753 | 353.3929
3541.2542 | 920.527 | 491.3229 | 522.8236 | 276.988 | 532.5155 | 378.3407 | 353.5518
3542.2542 | 922.7253 | 490.3545 | 522.7874 | 271.6724 | 531.5723 | 378.5896 | 353.7928
3543.2542 | 927.1587 | 490.1093 | 522.6567 | 266.1819 | 531.4987 | 378.6826 | 354.0197
3544.2542 | 927.6977 | 490.4417 | 522.7139 | 262.2986 | 531.791 | 378.9213 | 354.2243
3545.2542 | 932.8915 | 489.6648 | 522.7238 | 261.831 | 532.7542 | 379.0249 | 354.2896
3546.2542 | 931.164 | 489.3073 | 522.7921 | 261.4802 | 533.0279 | 379.1656 | 354.4761
3547.2542 | 928.5451 | 488.6573 | 522.6972 | 264.2547 | 533.4212 | 379.4004 | 354.5331
3548.2542 | 985.0917 | 488.8458 | 522.1269 | 196.7231 | 533.891 | 379.3165 | 355.0713
3549.2542 | 988.4127 | 488.9979 | 522.1283 | 187.4583 | 533.7928 | 379.4963 | 355.2591
3550.2542 | 985.5377 | 488.9379 | 522.0867 | 188.8843 | 533.5988 | 379.5455 | 355.3811
3551.2542 | 986.6937 | 488.5189 | 522.2732 | 188.0959 | 534.9336 | 379.7616 | 355.6855
3552.2542 | 988.6348 | 489.4977 | 522.4745 | 187.073 | 535.6673 | 379.8795 | 356.0266
3553.2542 | 996.1913 | 490.6516 | 522.268 | 178.6338 | 535.6632 | 380.0446 | 356.0026
3554.2542 | 999.8758 | 491.5051 | 522.2844 | 175.8968 | 535.2215 | 380.2656 | 356.1828
3555.2542 | 996.3624 | 491.8141 | 522.4274 | 179.1383 | 535.2307 | 380.5091 | 356.4146
3556.2542 | 1001.6572 | 491.3789 | 522.7324 | 176.6338 | 536.6211 | 380.501 | 356.4642
3557.2542 | 1010.0418 | 490.4187 | 522.8689 | 169.293 | 538.5186 | 380.7397 | 356.681
3558.2542 | 1017.0153 | 489.9247 | 522.8365 | 164.5677 | 539.7501 | 380.731 | 356.7933
3559.2542 | 1015.1182 | 489.5117 | 522.8252 | 164.6522 | 540.0377 | 381.1521 | 356.9544
3560.2542 | 1012.7536 | 489.406 | 523.1434 | 166.1891 | 539.3988 | 381.2347 | 356.9393
3561.2542 | 1024.3772 | 489.2497 | 523.0318 | 151.34 | 538.8315 | 381.3649 | 357.2406
3562.2542 | 1020.097 | 489.2165 | 523.3678 | 147.8824 | 538.6086 | 381.4505 | 357.326
3563.2542 | 999.5215 | 489.0372 | 523.5475 | 179.7952 | 537.9988 | 381.8888 | 357.6226
3564.2542 | 1002.0341 | 489.517 | 523.4301 | 168.981 | 538.7157 | 381.7813 | 357.7412
3565.2542 | 1029.9983 | 489.8927 | 523.2826 | 139.5928 | 537.7636 | 382.0394 | 357.9703
3566.2542 | 1031.1763 | 490.6597 | 523.1721 | 138.4736 | 537.4562 | 382.3363 | 358.2735
3567.2542 | 1036.3973 | 491.1659 | 523.2785 | 131.3563 | 537.0142 | 382.3604 | 358.4006
3568.2542 | 1022.8366 | 490.2986 | 523.4756 | 125.8856 | 537.5223 | 382.232 | 358.4114
3569.2542 | 1021.7668 | 490.6327 | 523.2555 | 125.7091 | 538.4011 | 382.3068 | 358.684
3570.2542 | 1019.0711 | 491.6473 | 522.5612 | 114.7245 | 536.4623 | 382.4806 | 358.8528
3571.2542 | 1009.2489 | 491.9058 | 522.6992 | 129.0532 | 535.9385 | 382.6144 | 358.7681
3572.2542 | 1005.1301 | 490.9574 | 522.8385 | 130.1598 | 536.3832 | 382.8983 | 358.8606
3573.2542 | 1005.4741 | 491.6166 | 522.8215 | 123.8778 | 536.0332 | 383.1063 | 359.0574
3574.2542 | 1001.3458 | 490.5277 | 522.6948 | 130.7043 | 535.6831 | 383.2219 | 359.1589
3575.2542 | 1011.9219 | 491.4425 | 522.582 | 115.4465 | 534.9362 | 383.4814 | 359.5576
3576.2542 | 1028.1634 | 491.415 | 522.4799 | 102.2669 | 534.3939 | 383.6955 | 359.9013
3577.2542 | 1028.9532 | 492.3837 | 522.4584 | 91.3131 | 534.1959 | 383.8985 | 360.053
3578.2542 | 1016.2751 | 491.0777 | 522.6748 | 109.6723 | 533.8284 | 384.1838 | 360.0736
3579.2542 | 1008.1256 | 490.354 | 522.6896 | 119.5441 | 535.0038 | 384.3458 | 360.1669
3580.2542 | 1011.4265 | 490.2029 | 522.602 | 107.424 | 534.9649 | 384.4818 | 360.3292
3581.2542 | 1012.6403 | 491.1967 | 522.7817 | 109.0271 | 534.005 | 384.6162 | 360.3028
3582.2542 | 1014.7329 | 490.5194 | 522.8521 | 106.1445 | 533.0807 | 384.7164 | 360.548
3583.2542 | 1024.7381 | 491.2108 | 522.7588 | 86.9056 | 531.9373 | 384.869 | 360.8959
3584.2542 | 1017.8745 | 488.7499 | 523.3043 | 118.9727 | 532.0519 | 385.1991 | 361.0704
3585.2542 | 1220.3388 | 489.8444 | 522.0581 | NaN | 533.2095 | 385.3735 | 362.8148
3586.2542 | 1245.2094 | 488.9631 | 521.9146 | 245.1311 | 533.1588 | 385.6363 | 363.4055
3587.2542 | 1245.211 | 489.4803 | 521.8917 | 418.2435 | 533.7149 | 386.0346 | 363.5563
3588.2542 | 1245.2101 | 489.4224 | 521.9614 | 680.0199 | 533.9712 | 386.0151 | 364.1777
3589.2542 | 1245.2118 | 490.5048 | 521.8927 | 866.6648 | 533.4193 | 385.9914 | 364.3321
3590.2542 | 1245.2124 | 490.4674 | 521.9295 | 1113.3381 | 533.055 | 386.3524 | 364.6232
3591.2542 | 1245.2142 | 489.5902 | 522.0269 | 1344.3936 | 532.6481 | 386.5704 | 365.0262
3592.2542 | 1245.2139 | 489.8425 | 522.1633 | 1350.2002 | 532.5 | 386.679 | 365.376
3593.2542 | 1245.2145 | 491.2837 | 522.6249 | NaN | 532.6431 | 386.7386 | 365.4471
3594.2542 | 1245.2163 | 491.1007 | 522.5727 | 1192.5571 | 532.762 | 386.9893 | 365.5362
3595.2542 | 1245.2171 | 491.3476 | 522.7362 | NaN | 532.9312 | 387.3368 | 366.1018
3596.2542 | 1245.2178 | 490.1997 | 522.8345 | NaN | 535.0666 | 387.3007 | 366.0976
3597.2542 | 1245.2183 | 490.0136 | 523.1746 | NaN | 535.9763 | 387.4761 | 366.0473
3598.2542 | 1245.2192 | 491.6959 | 523.2548 | NaN | 536.2393 | 387.6222 | 366.3082
3599.2542 | 1245.2196 | 491.9225 | 523.9445 | NaN | 536.7873 | 387.4392 | 366.6829
3600.2542 | 1245.2204 | 494.3438 | 524.941 | NaN | 540.2694 | 387.5917 | 366.9004
3601.2542 | 1245.2219 | 491.9318 | 523.0465 | NaN | 540.1771 | 388.0784 | 368.1212
3602.2542 | 1223.4666 | 497.4314 | 526.2265 | NaN | 544.1374 | 388.1366 | 366.9526
3603.2542 | 1245.2228 | 496.2889 | 525.9072 | NaN | 544.1414 | 388.5113 | 366.1205
3604.2542 | 1245.2247 | 490.8572 | 524.1592 | NaN | 542.2868 | 388.6978 | 367.216
3605.2542 | 1245.2248 | 490.9693 | 524.513 | NaN | 542.8332 | 388.8409 | 367.504
3606.2542 | 1245.2265 | 492.2095 | 526.4501 | NaN | 545.9509 | 389.6867 | 367.1621
3607.2542 | 1245.2265 | 492.4201 | 526.7214 | NaN | 545.1956 | 389.8727 | 367.1803
3608.2542 | 1245.228 | 492.3806 | 526.8882 | NaN | 544.6999 | 390.0407 | 367.0637
3609.2542 | 1245.228 | 493.2679 | 526.9376 | NaN | 543.7407 | 390.0982 | 367.4064
3610.2542 | 1245.2289 | 493.6914 | 526.8304 | NaN | 543.8592 | 390.1487 | 367.5577
3611.2542 | 1245.2302 | 493.7335 | 527.0898 | NaN | 543.9462 | 390.3082 | 367.8527
3612.2542 | 1245.2318 | 493.4874 | 527.3552 | NaN | 543.3072 | 390.339 | 367.7384
3613.2542 | 1051.7635 | 498.2921 | 528.0515 | -0.1479 | 542.6151 | 390.1883 | 366.4186
3614.2542 | 1083.6618 | 497.969 | 527.8539 | 199.0058 | 542.796 | 390.4882 | 367.0472
3615.2542 | 936.7978 | 500.6458 | 528.7295 | NaN | 544.1287 | 390.5988 | 366.5322
3616.2542 | 979.6471 | 499.8193 | 528.6228 | NaN | 543.9674 | 390.9832 | 366.7214
3617.2542 | 977.5826 | 501.2789 | 528.8408 | NaN | 544.9774 | 391.0487 | 366.9427
3618.2542 | 938.9607 | 503.2839 | 529.2068 | NaN | 545.6627 | 391.1394 | 366.8813
3619.2542 | 904.3545 | 505.0569 | 529.7579 | NaN | 546.9371 | 391.1584 | 367.5375
3620.2542 | 848.5885 | 506.6737 | 530.0218 | NaN | 546.7573 | 391.2485 | 367.3529
3621.2542 | 795.2165 | 511.2543 | 530.9711 | NaN | 548.1247 | 391.3293 | 367.306
3622.2542 | 881.3853 | 507.1912 | 529.9001 | NaN | 546.7808 | 391.5805 | 367.8651
3623.2542 | 864.7686 | 508.8471 | 530.1295 | NaN | 547.7786 | 391.9777 | 368.0631
3624.2542 | 666.8968 | 514.4367 | 531.2482 | 29.5941 | 549.3704 | 391.8461 | 367.6135
3625.2542 | 755.4718 | 510.3815 | 530.4707 | 3.3878 | 547.4178 | 392.1497 | 368.0838
3626.2542 | 767.1395 | 512.4776 | 530.8028 | NaN | 549.2739 | 392.2921 | 368.4122
3627.2542 | 764.3594 | 513.7746 | 531.2572 | NaN | 550.7485 | 392.3688 | 368.3553
3628.2542 | 858.0583 | 511.6722 | 530.6584 | 23.6155 | 550.4072 | 392.5194 | 369.0418
3629.2542 | 584.8521 | 520.2755 | 532.7651 | 28.2337 | 553.8432 | 392.4889 | 368.0358
3630.2542 | 691.0293 | 517.0151 | 529.4481 | NaN | 571.3939 | 393.078 | 369.1973
3631.2542 | 886.272 | 508.7184 | 528.0978 | NaN | 567.2755 | 393.5067 | 369.8725
3632.2542 | 1035.38 | 504.2353 | 526.3153 | 538.1332 | 564.724 | 393.7621 | 370.6542
3633.2542 | 860.42 | 509.1093 | 527.314 | NaN | 567.3837 | 393.7671 | 370.5498
3634.2542 | 613.8221 | 516.0683 | 528.9354 | 17.8195 | 570.4448 | 393.586 | 369.7329
3635.2542 | 470.715 | 521.074 | 530.0633 | 61.8342 | 573.7326 | 393.6847 | 369.8714
3636.2542 | 380.1444 | 521.4272 | 530.4573 | 99.854 | 575.4639 | 393.6169 | 369.9637
3637.2542 | 340.5999 | 524.0014 | 530.2058 | 63.4603 | 575.8138 | 392.8895 | 370.1189
3638.2542 | NaN | 535.8331 | 533.3599 | 212.4654 | 585.3225 | 393.271 | 369.0211
3639.2542 | NaN | 531.1933 | 532.6234 | 213.5227 | 582.9826 | 393.5477 | 369.535
3640.2542 | NaN | 530.0456 | 532.5824 | 248.9581 | 582.3664 | 393.6848 | 369.526
3641.2542 | 112.2555 | 528.3434 | 531.6794 | 192.8771 | 582.2293 | 393.9818 | 369.8741
3642.2542 | 98.0302 | 527.9489 | 531.1871 | 185.071 | 584.138 | 392.8834 | 370.145
3643.2542 | 361.5012 | 533.6028 | 533.1774 | 307.4642 | 590.0566 | 392.8297 | 369.4048
3644.2542 | NaN | 537.2104 | 536.0034 | 446.084 | 599.1284 | 395.3898 | 368.6908
3645.2542 | 15.4082 | 526.3775 | 533.2125 | 286.5293 | 588.2053 | 395.4962 | 369.813
3646.2542 | 159.0078 | 522.7299 | 531.5293 | 208.6064 | 583.8103 | 395.5843 | 370.5857
3647.2542 | 189.3905 | 526.3554 | 530.3328 | 68.7433 | 581.3148 | 392.8391 | 371.6398
3648.2542 | NaN | 525.5316 | 533.2164 | 305.9123 | 590.7407 | 396.6909 | 370.7838
3649.2542 | 86.6814 | 519.8107 | 532.2564 | 297.2084 | 583.4563 | 396.9234 | 371.1167
3650.2542 | NaN | 522.615 | 531.8118 | 392.7253 | 583.4553 | 396.8689 | 370.3108
3651.2542 | 591.112 | 486.4182 | 527.4101 | 555.1104 | 536.9618 | 396.4237 | 369.6601
3652.2542 | 614.989 | 483.9402 | 527.3611 | 556.646 | 535.6664 | 396.4369 | 370.3131
3653.2542 | 621.1665 | 483.4775 | 527.3993 | 555.3248 | 535.4884 | 396.7257 | 370.5849
3654.2542 | 619.4105 | 483.2186 | 527.3975 | 554.6753 | 534.9728 | 396.9796 | 370.866
3655.2542 | 617.7939 | 483.5891 | 527.4057 | 554.0177 | 535.8714 | 396.9729 | 371.0821
3656.2542 | 617.1282 | 483.3907 | 527.4573 | 555.3538 | 535.622 | 397.0825 | 371.0784
3657.2542 | 614.2013 | 483.9111 | 527.4543 | 555.2851 | 535.1618 | 397.3789 | 371.3178
3658.2542 | 611.9461 | 484.1092 | 527.5977 | 555.1439 | 535.7103 | 397.5263 | 371.4261
3659.2542 | 610.2299 | 484.5577 | 527.5564 | 555.7535 | 534.4932 | 397.8311 | 371.697
3660.2542 | 611.5179 | 484.8134 | 527.5967 | 555.8307 | 534.1143 | 397.8784 | 372.1384
3661.2542 | 616.069 | 484.3188 | 527.4831 | 556.0857 | 535.6196 | 397.9161 | 372.3018
3662.2542 | 618.7091 | 484.1474 | 527.3781 | 555.687 | 535.2239 | 398.1365 | 372.3972
3663.2542 | 616.8662 | 484.9081 | 527.4437 | 555.4275 | 536.5235 | 398.3358 | 372.4176
3664.2542 | 618.8211 | 484.4223 | 527.4145 | 554.7304 | 536.2709 | 398.6042 | 372.8314
3665.2542 | 617.3224 | 484.2339 | 527.567 | 554.8754 | 535.3807 | 398.5474 | 372.9846
3666.2542 | 617.6492 | 483.5563 | 527.4919 | 554.9259 | 534.9782 | 398.7912 | 373.1293
3667.2542 | 620.2095 | 484.4255 | 527.5315 | 554.8102 | 535.6381 | 398.9803 | 373.2497
3668.2542 | 629.9266 | 484.739 | 527.4141 | 554.1743 | 535.3618 | 399.1699 | 373.5731
3669.2542 | 630.0273 | 484.6669 | 527.4994 | 553.6398 | 535.4197 | 399.3229 | 373.6636
3670.2542 | 627.4851 | 484.5471 | 527.5538 | 553.465 | 534.8107 | 399.5983 | 373.834
3671.2542 | 626.3266 | 483.9324 | 527.5157 | 553.3806 | 535.4764 | 399.7487 | 374.1774
3672.2542 | 625.8052 | 483.9461 | 527.4474 | 553.2381 | 535.1775 | 399.7813 | 374.3765
3673.2542 | 635.7949 | 483.958 | 527.38 | 554.3474 | 534.6527 | 399.892 | 374.384
3674.2542 | 632.4462 | 484.1721 | 527.3295 | 554.9199 | 533.8447 | 400.0632 | 374.5268
3675.2542 | 637.5559 | 485.3176 | 527.304 | 554.768 | 534.1341 | 400.0887 | 374.5876
3676.2542 | 638.7715 | 485.3488 | 527.1865 | 554.2559 | 533.753 | 400.227 | 374.7392
3677.2542 | 636.0381 | 485.4079 | 527.1435 | 553.9976 | 532.8005 | 400.5229 | 375.1365
3678.2542 | 637.8876 | 485.5658 | 527.0876 | 553.8802 | 531.9348 | 400.6558 | 375.1886
3679.2542 | 637.7892 | 486.5769 | 526.9717 | 554.7826 | 531.0899 | 400.8648 | 375.4581
3680.2542 | 639.0071 | 487.5454 | 526.9326 | 555.2105 | 531.3156 | 400.9284 | 375.6724
3681.2542 | 642.0877 | 487.7728 | 526.8426 | 555.5593 | 532.1082 | 401.164 | 376.0027
3682.2542 | 641.6951 | 488.0609 | 526.8157 | 555.419 | 532.9095 | 401.3048 | 376.2494
3683.2542 | 640.2462 | 488.0743 | 526.789 | 555.5521 | 532.3911 | 401.5627 | 376.3331
3684.2542 | 635.7985 | 489.4332 | 526.7287 | 554.9446 | 532.1354 | 401.7445 | 376.5027
3685.2542 | 632.3586 | 489.9285 | 526.6571 | 554.1949 | 532.5311 | 401.7706 | 376.4847
3686.2542 | 626.0285 | 489.9374 | 526.6552 | 554.1248 | 533.4451 | 401.8936 | 376.7266
3687.2542 | 621.2299 | 490.2946 | 526.7356 | 553.5901 | 532.8031 | 402.0318 | 376.7411
3688.2542 | 616.4555 | 491.0283 | 526.871 | 553.7857 | 531.941 | 402.342 | 376.8133
3689.2542 | 615.3825 | 491.1422 | 527.0003 | 554.2265 | 531.1409 | 402.4342 | 377.0638
3690.2542 | 612.7184 | 491.1045 | 527.1016 | 553.8917 | 531.0969 | 402.5601 | 377.28
3691.2542 | 619.7087 | 491.3983 | 527.1516 | 554.1962 | 530.9205 | 402.69 | 377.4807
3692.2542 | 629.5358 | 492.6535 | 527.3138 | 555.0389 | 530.059 | 402.7135 | 377.4574
3693.2542 | 641.1281 | 492.7388 | 527.1866 | 555.0948 | 529.8425 | 402.8208 | 377.5121
3694.2542 | 647.4008 | 493.5822 | 527.3179 | 554.9644 | 529.8056 | 403.1539 | 377.8992
3695.2542 | 647.7011 | 493.8948 | 527.3921 | 554.6853 | 530.5453 | 403.3486 | 378.2766
3696.2542 | 646.4632 | 493.7664 | 527.5203 | 553.9175 | 531.152 | 403.3935 | 378.5152
3697.2542 | 639.5558 | 493.6144 | 527.5346 | 553.4337 | 531.5113 | 403.6358 | 378.6096
3698.2542 | 636.032 | 493.6224 | 527.5317 | 553.6856 | 531.9862 | 403.8744 | 378.658
3699.2542 | 633.5044 | 493.0603 | 527.63 | 554.0673 | 533.2459 | 404.0462 | 378.7363
3700.2542 | 633.5902 | 492.616 | 527.798 | 554.1779 | 533.1707 | 404.2291 | 379.0195
3701.2542 | 634.7233 | 492.5549 | 527.9213 | 554.2981 | 532.9467 | 404.3522 | 379.0692
3702.2542 | 634.126 | 492.1423 | 527.9037 | 553.87 | 532.5588 | 404.5518 | 379.4063
3703.2542 | 632.228 | 491.5127 | 527.731 | 553.48 | 532.7407 | 404.8141 | 379.6851
3704.2542 | 628.9602 | 490.9993 | 527.6606 | 553.0521 | 533.1249 | 404.9609 | 380.0053
3705.2542 | 626.714 | 491.2622 | 527.5884 | 552.4338 | 533.0089 | 405.0687 | 380.0911
3706.2542 | 623.7878 | 491.3187 | 527.4918 | 552.0219 | 532.8779 | 405.2751 | 380.2233
3707.2542 | 623.3807 | 491.5849 | 527.658 | 553.1825 | 532.2738 | 405.4171 | 380.3058
3708.2542 | 635.2298 | 491.4789 | 527.8361 | 553.7724 | 532.1389 | 405.5566 | 380.7011
3709.2542 | 639.8926 | 492.0692 | 527.8244 | 553.2046 | 531.9699 | 405.6469 | 380.7029
3710.2542 | 646.2579 | 491.6879 | 527.5841 | 552.3844 | 532.7416 | 405.8462 | 381.1701
3711.2542 | 645.9985 | 491.6721 | 527.4765 | 551.8166 | 533.2368 | 405.9438 | 381.2294
3712.2542 | 643.0852 | 491.8082 | 527.3789 | 551.5249 | 534.2134 | 406.1472 | 381.3149
3713.2542 | 639.7353 | 491.7777 | 527.3423 | 551.4584 | 533.3499 | 406.3145 | 381.2908
3714.2542 | 643.9129 | 491.2604 | 527.505 | 551.2627 | 532.5553 | 406.6009 | 381.5572
3715.2542 | 646.6456 | 491.666 | 527.3969 | 551.289 | 532.6421 | 406.7795 | 381.7483
3716.2542 | 646.4696 | 491.2071 | 527.3688 | 551.5574 | 533.073 | 407.0406 | 382.0114
3717.2542 | 646.8451 | 491.6328 | 527.3758 | 551.8017 | 534.4506 | 407.1502 | 382.1102
3718.2542 | 640.3691 | 490.3856 | 527.3536 | 551.8223 | 534.6572 | 407.3103 | 382.4381
3719.2542 | 637.01 | 489.9642 | 527.3907 | 552.6919 | 534.1583 | 407.4492 | 382.3504
3720.2542 | 635.8902 | 490.6368 | 527.5352 | 552.7678 | 533.8193 | 407.6102 | 382.659
3721.2542 | 635.0316 | 489.7973 | 527.4833 | 552.3866 | 533.349 | 407.7013 | 382.7384
3722.2542 | 631.7382 | 490.2911 | 527.4229 | 551.7333 | 532.4245 | 407.9135 | 382.8669
3723.2542 | 632.1684 | 490.7494 | 527.3693 | 551.5848 | 532.1848 | 408.1268 | 383.1493
3724.2542 | 628.0161 | 491.766 | 527.3491 | 551.3835 | 532.6281 | 408.3216 | 383.4256
3725.2542 | 630.1696 | 491.3833 | 527.3774 | 551.3715 | 532.3981 | 408.4312 | 383.6185
3726.2542 | 632.4694 | 491.3027 | 527.2962 | 552.0422 | 533.7395 | 408.5607 | 383.5943
3727.2542 | 641.2487 | 490.9047 | 527.4197 | 551.6027 | 533.3567 | 408.7184 | 384.0184
3728.2542 | 648.8311 | 491.2172 | 527.4768 | 551.4522 | 533.005 | 408.8049 | 383.9726
3729.2542 | 653.7397 | 491.3234 | 527.4264 | 550.977 | 532.9737 | 409.0581 | 384.3203
3730.2542 | 656.3972 | 491.6218 | 527.5943 | 551.6406 | 533.1431 | 409.2448 | 384.4068
3731.2542 | 660.6683 | 492.2455 | 527.5949 | 551.672 | 533.1788 | 409.4254 | 384.8099
3732.2542 | 669.9986 | 491.567 | 527.7129 | 551.2071 | 535.4811 | 409.6998 | 385.9127
3733.2542 | 664.0662 | 491.6159 | 527.7828 | 550.8608 | 535.2945 | 409.9556 | 386.3407
3734.2542 | 659.6327 | 492.1237 | 527.7676 | 551.1881 | 535.8351 | 410.1478 | 386.615
3735.2542 | 659.6302 | 491.8206 | 527.8408 | 551.4507 | 536.545 | 410.2713 | 386.8226
3736.2542 | 653.597 | 492.3136 | 527.8555 | 551.1981 | 536.461 | 410.5241 | 386.9652
3737.2542 | 645.5202 | 492.4538 | 527.8456 | 550.6778 | 535.5568 | 410.8053 | 387.0616
3738.2542 | 639.812 | 493.1054 | 527.7084 | 550.3647 | 535.1116 | 411.0686 | 387.1831
3739.2542 | 636.3857 | 493.3382 | 527.6875 | 550.4413 | 534.8778 | 411.1978 | 387.2763
3740.2542 | 645.2338 | 493.8054 | 527.6581 | 550.0493 | 534.681 | 411.3082 | 387.1322
3741.2542 | 645.7228 | 494.2637 | 527.6767 | 549.3474 | 533.7827 | 411.5464 | 387.7289
3742.2542 | 650.5065 | 495.0753 | 527.6007 | 549.2409 | 533.7878 | 411.6629 | 387.814
3743.2542 | 652.8767 | 495.5704 | 527.5678 | 549.3138 | 533.9716 | 411.815 | 388.0061
3744.2542 | 654.4255 | 496.353 | 527.6863 | 550.3706 | 534.1316 | 412.0114 | 388.484
3745.2542 | 649.1477 | 496.647 | 527.5835 | 550.1311 | 535.1971 | 412.2499 | 388.6857
3746.2542 | 651.0967 | 497.834 | 527.6187 | 549.9938 | 534.8767 | 412.4378 | 389.2775
3747.2542 | 661.5014 | 498.5003 | 527.4574 | 549.8376 | 535.728 | 412.6477 | 389.3789
3748.2542 | 665.2533 | 498.4183 | 527.5175 | 549.1769 | 536.2756 | 412.8008 | 389.311
3749.2542 | 662.4028 | 498.8259 | 527.5815 | 548.4764 | 536.2016 | 412.878 | 389.7276
3750.2542 | 657.013 | 499.0992 | 527.5019 | 547.7477 | 535.7451 | 413.0834 | 390.1385
3751.2542 | 653.8591 | 499.7651 | 527.4976 | 547.8231 | 536.3258 | 413.3244 | 390.3154
3752.2542 | 657.4123 | 500.069 | 527.6015 | 548.1931 | 535.8144 | 413.4556 | 390.6913
3753.2542 | 659.6241 | 500.4023 | 527.5713 | 548.4803 | 534.9806 | 413.5475 | 390.8008
3754.2542 | 667.5114 | 500.8744 | 527.5691 | 542.5309 | 548.4608 | 413.7093 | 386.3132
3755.2542 | 664.4352 | 500.9318 | 527.4823 | 540.8584 | 552.5846 | 413.8249 | 385.7619
3756.2542 | 663.9541 | 501.2039 | 527.4228 | 540.4406 | 552.9553 | 413.95 | 386.0482
3757.2542 | 660.6718 | 501.2272 | 527.5036 | 540.3113 | 553.8368 | 414.06 | 386.341
3758.2542 | 657.796 | 501.1464 | 527.4606 | 540.2842 | 554.1578 | 414.2304 | 386.4633
3759.2542 | 655.917 | 501.1145 | 527.3143 | 540.1853 | 555.1227 | 414.4716 | 386.7903
3760.2542 | 657.9486 | 500.5811 | 527.3004 | 539.9652 | 554.4385 | 414.5602 | 386.6938
3761.2542 | 652.4184 | 500.8269 | 527.3705 | 539.6428 | 553.9929 | 414.7279 | 386.8247
3762.2542 | 649.0357 | 500.93 | 527.3957 | 538.9283 | 554.6885 | 414.9101 | 387.2168
3763.2542 | 650.2284 | 500.081 | 527.486 | 538.6499 | 554.0339 | 415.0731 | 387.3595
3764.2542 | 654.7667 | 499.8736 | 527.3107 | 539.7278 | 552.7094 | 415.1798 | 387.5503
3765.2542 | 653.2693 | 500.6529 | 527.3591 | 540.7722 | 552.0651 | 415.3784 | 387.5326
3766.2542 | 661.1683 | 500.4228 | 527.3978 | 541.0136 | 552.6377 | 415.4689 | 387.5029
3767.2542 | 657.0999 | 501.8357 | 527.4118 | 540.7718 | 552.215 | 415.6092 | 388.0412
3768.2542 | 651.9208 | 503.1932 | 527.5386 | 541.1509 | 552.0741 | 415.7909 | 387.9824
3769.2542 | 647.0164 | 502.7206 | 527.5093 | 541.4365 | 551.4021 | 415.8714 | 388.4146
3770.2542 | 652.814 | 502.7441 | 527.5719 | 541.8215 | 551.6875 | 416.0221 | 388.2753
3771.2542 | 652.1665 | 503.5016 | 527.5624 | 541.6016 | 551.493 | 416.138 | 388.5487
3772.2542 | 653.1743 | 503.0101 | 527.5656 | 542.2465 | 551.4913 | 416.3353 | 388.626
3773.2542 | 650.2308 | 502.6501 | 527.6606 | 542.6729 | 551.651 | 416.443 | 388.7668
3774.2542 | 650.5687 | 503.3557 | 527.6327 | 542.6603 | 551.4198 | 416.604 | 389.1832
3775.2542 | 653.618 | 504.0654 | 527.677 | 542.281 | 550.4155 | 416.8041 | 388.9749
3776.2542 | 655.166 | 504.5671 | 527.672 | 541.6635 | 549.5208 | 416.9739 | 389.2298
3777.2542 | 656.1524 | 503.995 | 527.6192 | 541.2445 | 548.9172 | 417.1049 | 389.4691
3778.2542 | 668.1677 | 505.0744 | 527.6696 | 541.1753 | 548.9776 | 417.1297 | 389.2321
3779.2542 | 673.9518 | 506.2246 | 527.8043 | 541.0324 | 549.5513 | 417.3161 | 389.6295
3780.2542 | 673.6111 | 506.9325 | 527.9181 | 541.2564 | 549.3547 | 417.4822 | 389.9614
3781.2542 | 662.5717 | 506.5828 | 528.0839 | 541.1616 | 548.6442 | 417.6221 | 390.0363
3782.2542 | 653.7118 | 505.9568 | 528.0968 | 541.3014 | 548.1538 | 417.7904 | 390.2907
3783.2542 | 656.0356 | 508.1145 | 528.1986 | 541.6922 | 548.4814 | 417.9459 | 390.2953
3784.2542 | 660.3279 | 508.0738 | 528.2545 | 542.3003 | 548.6976 | 418.1548 | 390.4479
3785.2542 | 655.6574 | 508.0739 | 528.3808 | 542.3896 | 548.9408 | 418.2921 | 390.7639
3786.2542 | 654.2072 | 508.2388 | 528.4268 | 541.9788 | 548.8617 | 418.442 | 390.9523
3787.2542 | 649.6506 | 509.0002 | 528.4695 | 541.7462 | 548.888 | 418.557 | 391.2683
3788.2542 | 653.8094 | 511.9246 | 528.5306 | 543.4468 | 548.553 | 418.7002 | 390.9888
3789.2542 | 646.993 | 513.9653 | 528.6147 | 543.3558 | 549.4352 | 418.8632 | 391.0704
3790.2542 | 649.2189 | 514.3325 | 528.7836 | 543.278 | 550.7682 | 418.9887 | 391.1727
3791.2542 | 651.4839 | 515.8667 | 528.8732 | 543.0472 | 550.6104 | 419.0818 | 391.7854
3792.2542 | 659.8986 | 513.748 | 528.9831 | 542.4778 | 550.3083 | 419.1993 | 391.8412
3793.2542 | 665.2938 | 503.4319 | 529.0127 | 542.1632 | 549.3679 | 419.3252 | 391.8803
3794.2542 | 668.2282 | 516.1161 | 529.0795 | 542.0109 | 548.8092 | 419.4219 | 391.9356
3795.2542 | 669.069 | 515.553 | 529.1478 | 543.2635 | 548.2617 | 419.5613 | 392.2814
3796.2542 | 671.5697 | 515.9704 | 529.1169 | 544.0507 | 549.2007 | 419.6519 | 392.118
3797.2542 | 662.2818 | 515.9652 | 529.0328 | 543.6105 | 550.648 | 419.8322 | 392.4978
3798.2542 | 653.4043 | 518.1078 | 529.0964 | 544.088 | 550.7975 | 420.0074 | 392.6236
3799.2542 | 647.984 | 519.8554 | 528.9619 | 543.6002 | 551.4484 | 420.0937 | 392.7108
3800.2542 | 655.0226 | 519.4026 | 528.8829 | 543.2106 | 550.7881 | 420.1716 | 393.1279
3801.2542 | 662.6682 | 519.3764 | 528.9244 | 543.7335 | 550.2661 | 420.327 | 393.0729
3802.2542 | 662.9448 | 520.0518 | 529.023 | 543.1907 | 549.8819 | 420.482 | 393.0728
3803.2542 | 664.412 | 483.7055 | 528.9747 | 542.8809 | 549.0866 | 420.4988 | 422.4938
3804.2542 | 667.5636 | 484.161 | 528.9193 | 542.6271 | 547.788 | 420.6005 | 422.5519
3805.2542 | 663.0775 | 486.3728 | 528.9434 | 543.42 | 548.6406 | 420.7405 | 423.1935
3806.2542 | 668.2351 | 486.4433 | 529.0469 | 543.8259 | 549.7881 | 420.9004 | 424.0124
3807.2542 | 663.3109 | 487.8731 | 529.0301 | 543.5689 | 549.2409 | 420.99 | 424.4051
3808.2542 | 654.8315 | 487.3788 | 528.966 | 544.0521 | 548.5385 | 421.0719 | 424.2252
3809.2542 | 652.1157 | 487.397 | 528.891 | 543.5232 | 548.3164 | 421.2518 | 424.4577
3810.2542 | 653.7939 | 487.5429 | 528.9368 | 543.272 | 548.6646 | 421.3335 | 424.835
3811.2542 | 650.5702 | 487.789 | 528.8422 | 542.7684 | 548.435 | 421.3967 | 425.1106
3812.2542 | 644.8388 | 488.9212 | 529.0021 | 542.2365 | 548.4573 | 421.4737 | 424.9384
3813.2542 | 641.3481 | 489.2148 | 529.0334 | 541.8149 | 548.0853 | 421.5333 | 424.3832
3814.2542 | 646.6013 | 491.2449 | 529.0185 | 541.1912 | 547.5589 | 421.6003 | 424.7485
3815.2542 | 650.2901 | 489.983 | 529.0189 | 540.6334 | 546.4653 | 421.7088 | 425.0744
3816.2542 | 645.5259 | 490.4293 | 529.0882 | 540.3856 | 545.3723 | 421.7985 | 424.9646
3817.2542 | 648.4284 | 489.7484 | 529.023 | 540.3957 | 544.5523 | 421.8832 | 425.5213
3818.2542 | 653.2871 | 489.5773 | 529.1627 | 539.8735 | 543.9185 | 421.9852 | 425.2934
3819.2542 | 657.3835 | 493.1775 | 529.2755 | 539.6129 | 542.9161 | 422.0498 | 425.2537
3820.2542 | 654.0882 | 494.384 | 529.3835 | 538.9582 | 542.3783 | 422.1623 | 425.7967
3821.2542 | 657.708 | 494.8806 | 529.4688 | 538.4276 | 541.9145 | 422.2476 | 425.622
3822.2542 | 649.8168 | 498.09 | 529.4612 | 538.4523 | 541.5543 | 422.3437 | 425.8499
3823.2542 | 651.3238 | 496.6642 | 529.3959 | 537.8219 | 541.385 | 422.4314 | 426.1986
3824.2542 | 643.1052 | 495.2085 | 529.4556 | 537.6907 | 541.8109 | 422.493 | 426.4472
3825.2542 | 637.0654 | 494.6775 | 529.4965 | 537.3835 | 542.512 | 422.6063 | 427.228
3826.2542 | 633.6466 | 493.1158 | 529.4104 | 537.2475 | 542.0425 | 422.6821 | 427.2702
3827.2542 | 649.0134 | 494.2182 | 529.2488 | 537.4182 | 542.4684 | 422.7703 | 427.5411
3828.2542 | 658.3762 | 494.6573 | 529.2503 | 537.5056 | 543.0129 | 422.8244 | 427.9152
3829.2542 | 650.0742 | 493.5668 | 529.2601 | 537.0092 | 542.5652 | 422.8749 | 428.0014
3830.2542 | 655.7117 | 493.5377 | 529.2494 | 537.1988 | 542.5673 | 422.9785 | 428.3158
3831.2542 | 662.1074 | 492.2231 | 529.1686 | 537.5811 | 542.8232 | 423.0755 | 428.0987
3832.2542 | 661.974 | 491.0861 | 529.1081 | 538.2469 | 543.4418 | 423.168 | 428.233
3833.2542 | 662.9746 | 490.6656 | 529.1355 | 538.7127 | 543.1923 | 423.2615 | 428.5762
3834.2542 | 662.1817 | 490.7606 | 528.9804 | 538.9137 | 542.8276 | 423.3415 | 428.38
3835.2542 | 676.0846 | 492.0848 | 528.8384 | 539.372 | 542.7616 | 423.4657 | 428.5546
3836.2542 | 666.6606 | 490.5189 | 528.7263 | 539.6899 | 541.8083 | 423.5268 | 428.5262
3837.2542 | 670.5745 | 490.1633 | 528.6947 | 540.7074 | 541.1713 | 423.6387 | 428.7953
3838.2542 | 663.5178 | 489.4688 | 528.6401 | 540.2877 | 541.3535 | 423.7061 | 429.3369
3839.2542 | 661.3309 | 489.655 | 528.538 | 541.5885 | 541.9563 | 423.8239 | 429.6708
3840.2542 | 660.7795 | 491.8414 | 528.4996 | 540.713 | 543.109 | 423.8848 | 430.0122
3841.2542 | 657.4257 | 493.0905 | 528.2967 | 540.7226 | 544.0884 | 423.8741 | 430.0801
3842.2542 | 666.8171 | 496.7804 | 528.2245 | 540.6816 | 544.0663 | 423.9185 | 430.0185
3843.2542 | 667.4846 | 496.4019 | 528.2484 | 541.044 | 543.6274 | 423.9168 | 429.7628
3844.2542 | 660.7339 | 498.5178 | 528.1273 | 541.5301 | 542.6424 | 423.936 | 429.7167
3845.2542 | 655.1351 | 498.9969 | 527.9695 | 541.3946 | 543.2114 | 423.9372 | 429.929
3846.2542 | 659.197 | 499.4337 | 527.9915 | 541.5186 | 544.1145 | 423.9044 | 430.6179
3847.2542 | 665.8668 | 499.2142 | 528.0227 | 541.1846 | 543.6045 | 423.8847 | 430.29
3848.2542 | 662.2577 | 498.8919 | 528.0344 | 541.6707 | 543.9815 | 423.9077 | 430.6542
3849.2542 | 658.8026 | 497.6012 | 527.9919 | 542.2335 | 544.5579 | 423.8954 | 430.89
3850.2542 | 658.6803 | 497.6119 | 527.9865 | 542.707 | 544.5108 | 423.8748 | 430.8998
3851.2542 | 651.278 | 500.6892 | 527.9354 | 542.4758 | 544.4981 | 423.8292 | 431.0618
3852.2542 | 663.6701 | 501.3462 | 527.974 | 543.1062 | 543.7743 | 423.7315 | 431.1804
3853.2542 | 662.5146 | 504.6297 | 527.9719 | 544.1804 | 543.8564 | 423.6731 | 431.4548
3854.2542 | 668.7046 | 506.2526 | 527.9017 | 543.8789 | 544.0353 | 423.5917 | 431.6732
3855.2542 | 677.2135 | 507.7778 | 528.0022 | 543.3598 | 543.5419 | 423.4868 | 431.7079
3856.2542 | 677.5103 | 509.7395 | 528.0357 | 544.0385 | 544.1678 | 423.3928 | 431.9122
3857.2542 | 678.0034 | 511.1264 | 527.928 | 544.2009 | 545.7744 | 423.3034 | 431.9711
3858.2542 | 675.868 | 509.6909 | 527.9052 | 544.7937 | 545.4373 | 423.22 | 432.2372
3859.2542 | 672.2514 | 508.2711 | 527.6263 | 544.3935 | 544.6272 | 423.1155 | 432.2022
3860.2542 | 673.9311 | 508.6423 | 527.4689 | 545.2104 | 543.5735 | 423.028 | 432.6068
3861.2542 | 676.0668 | 507.1168 | 527.3675 | 544.8435 | 542.3237 | 422.961 | 432.2326
3862.2542 | 665.2371 | 508.1208 | 527.3063 | 544.6745 | 543.0425 | 422.862 | 432.7426
3863.2542 | 659.4488 | 505.7631 | 527.2071 | 544.0814 | 542.6201 | 422.7615 | 432.3642
3864.2542 | 659.5501 | 506.5452 | 527.0735 | 544.0813 | 541.3006 | 422.5991 | 432.3537
3865.2542 | 668.609 | 509.7091 | 527.1045 | 544.4339 | 540.8088 | 422.5331 | 432.5395
3866.2542 | 673.0481 | 512.1852 | 527.0381 | 544.3437 | 539.7758 | 422.3676 | 432.3991
3867.2542 | 666.3722 | 513.9306 | 526.9626 | 543.9181 | 540.3165 | 422.2692 | 432.8759
3868.2542 | 657.2093 | 516.6352 | 526.971 | 543.5179 | 539.3258 | 422.2121 | 432.7321
3869.2542 | 649.6775 | 519.4196 | 526.8585 | 542.7991 | 537.3126 | 422.1028 | 432.4169
3870.2542 | 644.5548 | 521.305 | 526.8693 | 543.1044 | 537.7614 | 421.9604 | 432.3754
3871.2542 | 640.8364 | 523.3882 | 526.9015 | 541.856 | 535.3617 | 421.8333 | 431.722
3872.2542 | 641.8156 | 523.8249 | 526.8303 | 541.5517 | 536.0579 | 421.7503 | 432.1156
3873.2542 | 642.6 | 521.938 | 526.7576 | 541.1547 | 534.9204 | 421.6708 | 432.583
3874.2542 | 636.5724 | 519.5076 | 526.7102 | 541.4806 | 534.679 | 421.5169 | 432.4762
3875.2542 | 637.4531 | 518.1863 | 526.6503 | 540.8097 | 533.0142 | 421.4274 | 432.0634
3876.2542 | 631.3464 | 516.4587 | 526.5575 | 541.0424 | 532.4495 | 421.3491 | 432.1156
3877.2542 | 632.8633 | 516.2684 | 526.4779 | 541.3972 | 532.8396 | 421.2875 | 432.6828
3878.2542 | 634.457 | 514.9855 | 526.3182 | 541.3558 | 532.1911 | 421.1679 | 432.6526
3879.2542 | 629.3948 | 513.9503 | 526.3258 | 541.4336 | 533.7791 | 421.062 | 433.1145
3880.2542 | 626.4134 | 516.2867 | 526.2915 | 541.2273 | 534.6951 | 421.0354 | 433.1709
3881.2542 | 630.4757 | 517.4846 | 526.2813 | 541.3048 | 534.5048 | 420.9446 | 433.4197
3882.2542 | 643.9503 | 515.9071 | 526.266 | 541.4768 | 533.7294 | 420.8423 | 433.6531
3883.2542 | 644.7885 | 516.1715 | 526.1571 | 540.654 | 533.0045 | 420.8116 | 433.7545
3884.2542 | 642.777 | 518.1096 | 526.1478 | 539.4685 | 532.7785 | 420.6691 | 433.9673
3885.2542 | 638.5377 | 517.3797 | 526.2071 | 536.7585 | 532.742 | 420.5693 | 433.5321
3886.2542 | 639.3071 | 519.8081 | 526.396 | 536.082 | 532.8217 | 420.5579 | 434.4082
3887.2542 | 644.293 | 520.1882 | 526.5071 | 534.7398 | 534.936 | 420.5638 | 434.705
3888.2542 | 650.7195 | 520.5953 | 526.5703 | 530.128 | 535.144 | 420.5738 | 434.7202
3889.2542 | 646.8119 | 521.8984 | 526.5816 | 529.777 | 534.8099 | 420.5803 | 434.8871
3890.2542 | 658.6146 | 522.0293 | 526.6283 | 529.8129 | 533.9746 | 420.5176 | 434.7743
3891.2542 | 653.4169 | 524.4475 | 526.4794 | 529.9447 | 533.6446 | 420.4993 | 434.776
3892.2542 | 650.6537 | 525.3699 | 526.4551 | 530.0311 | 533.1144 | 420.3941 | 434.841
3893.2542 | 652.392 | 524.6697 | 526.4329 | 529.8695 | 532.2704 | 420.3615 | 434.7693
3894.2542 | 656.7546 | 523.3016 | 526.6023 | 530.0259 | 532.9328 | 420.3593 | 435.5042
3895.2542 | 658.6135 | 522.8951 | 526.6222 | 532.0034 | 532.0672 | 420.378 | 435.1187
3896.2542 | 649.5992 | 522.0431 | 526.7047 | 532.5714 | 531.4721 | 420.3632 | 434.9682
3897.2542 | 658.2215 | 523.2878 | 526.7576 | 531.7676 | 530.598 | 420.3051 | 434.8209
3898.2542 | 665.8235 | 522.6047 | 526.7255 | 531.0998 | 530.8832 | 420.2256 | 435.1134
3899.2542 | 664.3497 | 523.5524 | 526.8059 | 531.0077 | 531.0953 | 420.2178 | 435.3773
3900.2542 | 659.3091 | 523.1594 | 526.8736 | 531.4429 | 531.851 | 420.1544 | 435.497
3901.2542 | 656.9603 | 521.81 | 526.8744 | 532.43 | 531.6146 | 420.1699 | 435.4951
3902.2542 | 666.6595 | 520.3626 | 526.6973 | 533.6066 | 530.72 | 420.1607 | 435.1696
3903.2542 | 666.4488 | 517.5614 | 526.7407 | 533.7733 | 530.6212 | 420.0996 | 435.2534
3904.2542 | 672.5504 | 519.7172 | 526.7286 | 534.0686 | 530.6904 | 420.1584 | 435.4998
3905.2542 | 670.7315 | 517.604 | 526.7432 | 533.4918 | 531.3828 | 420.0852 | 435.6746
3906.2542 | 671.209 | 513.038 | 526.6921 | 533.3284 | 531.7991 | 420.0591 | 436.075
3907.2542 | 663.5653 | 510.2653 | 526.7283 | 533.9149 | 531.3146 | 420.0734 | 436.0456
3908.2542 | 659.0761 | 508.9401 | 526.6662 | 535.0179 | 530.9134 | 420.0959 | 436.2557
3909.2542 | 663.4642 | 511.5515 | 526.6855 | 534.5036 | 531.3566 | 420.0162 | 436.2969
3910.2542 | 664.6054 | 513.2329 | 526.623 | 533.8603 | 531.6445 | 420.0538 | 436.6121
3911.2542 | 654.4259 | 515.8385 | 526.5425 | 533.3698 | 531.5468 | 419.9913 | 436.6008
3912.2542 | 648.8103 | 516.9372 | 526.5357 | 532.7551 | 532.105 | 420.0352 | 437.0168
3913.2542 | 646.4601 | 518.2404 | 526.4364 | 532.2522 | 533.0924 | 420.0646 | 437.2584
3914.2542 | 641.5679 | 515.1845 | 526.402 | 532.0079 | 533.0941 | 419.9757 | 437.2041
3915.2542 | 647.1499 | 514.6676 | 526.377 | 531.8383 | 532.6998 | 419.9787 | 437.034
3916.2542 | 652.5846 | 513.2122 | 526.339 | 531.6093 | 532.5676 | 419.9576 | 436.9747
3917.2542 | 655.1214 | 513.2902 | 526.4079 | 532.1385 | 533.482 | 419.9112 | 437.5319
3918.2542 | 656.9064 | 516.4649 | 526.4708 | 531.9777 | 533.3694 | 419.9778 | 437.4878
3919.2542 | 661.3738 | 520.5061 | 526.5183 | 531.5327 | 533.0881 | 419.9988 | 437.6054
3920.2542 | 668.252 | 506.0485 | 526.595 | 531.0147 | 532.6669 | 420.0661 | 437.5449
3921.2542 | 661.844 | 499.2308 | 526.6608 | 530.8418 | 532.6158 | 420.0262 | 437.4885
3922.2542 | 665.2483 | 498.6055 | 526.7766 | 530.453 | 532.4301 | 420.0693 | 437.6229
3923.2542 | 665.4004 | 498.4798 | 526.809 | 530.0891 | 531.6473 | 420.0201 | 437.55
3924.2542 | 667.2283 | 497.6358 | 526.8061 | 529.7399 | 531.2262 | 420.0726 | 437.9886
3925.2542 | 656.1312 | 496.9085 | 526.799 | 529.8521 | 531.7169 | 420.0364 | 438.1062
3926.2542 | 648.521 | 496.6468 | 526.9415 | 530.1705 | 532.3095 | 420.1475 | 438.4643
3927.2542 | 648.9375 | 497.0738 | 526.9691 | 531.0186 | 531.9718 | 420.1889 | 438.5841
3928.2542 | 658.3488 | 499.5689 | 526.9854 | 531.4533 | 531.5626 | 420.213 | 438.3166
3929.2542 | 661.5974 | 500.6293 | 527.0438 | 531.5121 | 531.6026 | 420.2549 | 438.6178
3930.2542 | 659.8202 | 497.5126 | 527.1271 | 530.8282 | 531.3301 | 420.3588 | 438.5779
3931.2542 | 652.4318 | 495.1753 | 527.0639 | 530.7625 | 530.9003 | 420.4113 | 438.5599
3932.2542 | 647.278 | 492.448 | 527.0899 | 531.101 | 530.2044 | 420.3489 | 438.2589
3933.2542 | 642.1957 | 494.0775 | 526.9913 | 530.7687 | 530.1141 | 420.456 | 438.4672
3934.2542 | 639.5241 | 494.6232 | 527.0367 | 530.363 | 529.9755 | 420.4307 | 438.6099
3935.2542 | 642.3983 | 491.8822 | 526.9267 | 530.2549 | 529.5945 | 420.4704 | 438.8477
3936.2542 | 645.8077 | 490.7719 | 526.903 | 530.097 | 529.8061 | 420.5872 | 439.0489
3937.2542 | 644.9595 | 493.5741 | 526.9251 | 530.3831 | 530.3983 | 420.6926 | 439.181
3938.2542 | 641.2712 | 491.5413 | 526.881 | 530.3908 | 531.5012 | 420.8008 | 439.5132
3939.2542 | 644.3366 | 492.5197 | 526.822 | 531.9016 | 531.0608 | 420.8462 | 439.3065
3940.2542 | 644.2118 | 491.2615 | 526.8775 | 532.4224 | 531.6584 | 420.8884 | 439.8344
3941.2542 | 656.0602 | 490.3459 | 526.9111 | 533.0035 | 531.6349 | 420.9297 | 439.6083
3942.2542 | 661.7992 | 490.5398 | 526.9002 | 532.5798 | 531.9497 | 420.9496 | 439.8441
3943.2542 | 656.3799 | 492.3372 | 527.0089 | 532.7554 | 533.0725 | 420.9944 | 439.7867
3944.2542 | 655.887 | 493.5075 | 527.0814 | 532.3239 | 533.0562 | 421.0601 | 439.843
3945.2542 | 667.0617 | 493.4261 | 527.1147 | 531.9677 | 532.784 | 421.1546 | 439.7757
3946.2542 | 667.7321 | 495.3668 | 527.2548 | 531.5848 | 532.0865 | 421.3375 | 438.101
3947.2542 | 671.8467 | 493.6121 | 527.2223 | 531.5837 | 521.1647 | 421.4794 | 411.8434
3948.2542 | 675.6917 | 493.5951 | 527.3757 | 531.5195 | 520.1211 | 421.5801 | 410.536
3949.2542 | 674.1462 | 489.7831 | 527.5013 | 531.3996 | 519.9978 | 421.5813 | 410.1205
3950.2542 | 668.164 | 490.5574 | 527.6175 | 532.1353 | 519.7155 | 421.6966 | 410.1523
3951.2542 | 672.3249 | 489.3632 | 527.5928 | 532.0574 | 519.9005 | 421.8229 | 410.8505
3952.2542 | 663.3785 | 489.9057 | 527.6287 | 531.9541 | 520.3757 | 421.8031 | 411.103
3953.2542 | 660.2384 | 490.9678 | 527.7204 | 532.0547 | 519.9314 | 421.8442 | 411.1419
3954.2542 | 667.7031 | 491.1174 | 527.7811 | 531.7316 | 519.7154 | 421.9162 | 411.0654
3955.2542 | 665.6006 | 488.4314 | 527.6337 | 531.5724 | 519.8281 | 422.006 | 411.1193
3956.2542 | 662.6499 | 486.77 | 527.5767 | 531.0546 | 519.6931 | 422.1205 | 411.5586
3957.2542 | 657.5867 | 486.8222 | 527.4672 | 530.8061 | 519.8793 | 422.1363 | 419.2621
3958.2542 | 648.1158 | 484.5851 | 527.3966 | 530.6288 | 519.2018 | 422.279 | 419.2882
3959.2542 | 642.636 | 484.8333 | 527.2986 | 530.469 | 518.7848 | 422.4246 | 419.3683
3960.2542 | 645.4602 | 484.3606 | 527.0849 | 530.0678 | 518.8515 | 422.4615 | 419.5338