## Test Conditions
DESIREE-FIRE Intermediate Scale Test 10 - Circuit Simulator Data Only
Test Date: | 2010-03-25
DCSim DAQ Start Time | 10:11
DCSim Time for Synchronization | 10:40
Heat Source Synchronization | 0:00 | hour:minutes:seconds
Heat Source DAQ Start Time | 10:40
Fire Time | 11:27
Offset | 1:16 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 4560 | seconds
Heat Source Offset | 0:47 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2811 | seconds
Heat Source Stop Time | 12:33
Test Duration | 1:06 | hour:minutes:seconds
| 3960 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | Kerite, 12c, 12AWG, without zinc wrap |  | There are two cable TCs monitoring internal temperatures of the Kerite cable in C Position. Channels 8 and 9 are represented as "C Position - Kerite 12c wo - 3'" and "C Position - Kerite 12c wo - 5'" in the raw temperature files. | There are three TCs monitoring air temperatures along the middle of the tray in C Position. Channels 5, 6, and 7 are represented as "C Position - 3'", "C Position - Middle", and "C Position - 7'" in the raw temperature files.
SOV 2 | Kerite, 10c, 12AWG, without zinc wrap |  | Channel 4 represented as "B-Position - Kerite 10c wo" in the Temperature Data File is monitoring the center of the cable sample sitting within the tray. | Channel 1 represented as "B-Position - Tray - Middle" in the Temperature Data File is monitoring the air temperature in the middle of the tray at B Position.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.2812 | 121.9574 | -61.0931 | 60.498 | 1.4211e-13 | -0.0094827 | -0.00030992 | 0.064599 | -0.0022094 | 0.060742 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064913 | 0.0049678 | 0.064837 | -58.5794 | -0.021486 | -61.0735 | 60.4365 | 60.1033 | 60.1217 | -61.1459 | -61.0652 | -0.00422 | -61.1684 | 60.2551 | 60.3322 | 60.3537 | -61.1723 | -0.052771 | -0.061562 | 2.5137 | 0.019625 | 0.072396 | -0.39472 | -0.37639 | -0.079169 | -0.24296 | 0.027934 | -0.075252 | 0.003917 | -0.16583 | -0.14431 | 121.5296 | 121.1965 | 121.2148 | 61.0717 | -121.644 | 121.3482 | 121.4254 | 121.4469 | 61.0889 | -121.6704
0.46875 | 121.8567 | -61.1664 | 60.5072 | 1.4211e-13 | -0.0094827 | -0.00052352 | 0.065026 | -0.0026366 | 0.060956 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064913 | 0.0051816 | 0.064837 | -58.465 | -0.030644 | -61.0827 | 60.4411 | 60.1033 | 60.1217 | -61.1505 | -61.0606 | -0.00422 | -61.173 | 60.2551 | 60.3231 | 60.3583 | -61.1723 | 0.015892 | -0.066138 | 2.7014 | 0.08371 | 0.067818 | -0.40388 | -0.38554 | -0.005927 | -0.25211 | 0.10576 | -0.006588 | -0.000661 | -0.18414 | -0.14889 | 121.6074 | 121.2697 | 121.288 | 61.1357 | -121.6577 | 121.4215 | 121.4894 | 121.5247 | 61.1622 | -121.6795
2.2188 | 121.907 | -61.0977 | 60.5301 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064599 | -0.0026366 | 0.060956 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064699 | 0.0049678 | 0.064837 | -58.552 | -0.026065 | -61.0918 | 60.4411 | 60.0942 | 60.1262 | -61.1459 | -61.0606 | 0.004938 | -61.1638 | 60.2597 | 60.3276 | 60.3492 | -61.1723 | -0.048194 | -0.089026 | 2.5458 | 0.005889 | 0.054083 | -0.43593 | -0.40385 | -0.074592 | -0.27042 | 0.03709 | -0.066096 | 0.008496 | -0.20245 | -0.18094 | 121.5388 | 121.1919 | 121.224 | 61.0717 | -121.676 | 121.3574 | 121.4254 | 121.4469 | 61.1027 | -121.7024
3.9844 | 121.9666 | -61.0794 | 60.4935 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064812 | -0.0022094 | 0.060956 | 0.012972 | 0.00034614 | 0.00037167 | 0.065126 | 0.0047542 | 0.064624 | -58.584 | -0.030644 | -61.0827 | 60.4365 | 60.085 | 60.1217 | -61.1459 | -61.0606 | -0.008798 | -61.1684 | 60.2551 | 60.3276 | 60.3537 | -61.1769 | -0.066504 | -0.056984 | 2.4954 | -0.003265 | 0.063239 | -0.40846 | -0.37181 | -0.097481 | -0.23838 | 0.01878 | -0.088985 | 0.008496 | -0.16583 | -0.13974 | 121.5159 | 121.1644 | 121.2011 | 61.0488 | -121.6394 | 121.3345 | 121.407 | 121.4331 | 61.0706 | -121.6704
5.6719 | 121.9666 | -61.0748 | 60.5118 | 1.4211e-13 | -0.0096965 | -0.00030992 | 0.064812 | -0.002423 | 0.060956 | 0.012972 | 0.00034614 | -0.00026913 | 0.064913 | 0.0049678 | 0.064624 | -58.5748 | -0.026065 | -61.0781 | 60.4365 | 60.0942 | 60.1262 | -61.1413 | -61.0606 | 0.000359 | -61.1684 | 60.2597 | 60.3231 | 60.3537 | -61.1769 | -0.066503 | -0.075295 | 2.5 | -0.003265 | 0.063238 | -0.41762 | -0.38554 | -0.10206 | -0.25211 | 0.014202 | -0.093563 | 0.008496 | -0.18872 | -0.15805 | 121.5113 | 121.169 | 121.2011 | 61.0488 | -121.6531 | 121.3345 | 121.3979 | 121.4286 | 61.0752 | -121.6887
7.3438 | 121.8338 | -61.1114 | 60.5713 | 1.4211e-13 | -0.0099101 | -0.00052352 | 0.064599 | -0.002423 | 0.06117 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064699 | 0.0047542 | 0.065051 | -58.497 | -0.039801 | -61.0827 | 60.4411 | 60.0942 | 60.1217 | -61.1459 | -61.0606 | 0.000359 | -61.1592 | 60.2505 | 60.3276 | 60.34 | -61.1769 | -0.034461 | -0.13023 | 2.6144 | 0.028778 | 0.063239 | -0.47712 | -0.44963 | -0.065438 | -0.32078 | 0.050823 | -0.047784 | 0.017654 | -0.24365 | -0.23129 | 121.5525 | 121.2056 | 121.2331 | 61.0716 | -121.7172 | 121.362 | 121.4391 | 121.4514 | 61.1118 | -121.7482
9.0312 | 121.8018 | -61.1664 | 60.5072 | 1.4211e-13 | -0.010338 | -0.00073712 | 0.065026 | -0.0026366 | 0.060956 | -0.01755 | 0.00034614 | 0.00015807 | 0.065126 | 0.0049678 | 0.064837 | -58.465 | -0.039801 | -61.0872 | 60.4411 | 60.0896 | 60.1308 | -61.1368 | -61.0698 | 0.004938 | -61.1592 | 60.2551 | 60.3276 | 60.3583 | -61.1769 | 0.029629 | -0.066138 | 2.7014 | 0.079132 | 0.049503 | -0.41762 | -0.37639 | -0.010506 | -0.25211 | 0.096598 | 0.007148 | 0.017654 | -0.17956 | -0.14889 | 121.6074 | 121.256 | 121.2972 | 61.1266 | -121.644 | 121.4215 | 121.494 | 121.5247 | 61.1713 | -121.6841
10.7188 | 121.9162 | -61.1343 | 60.4202 | 1.4211e-13 | -0.0099101 | -9.6116e-05 | 0.064599 | -0.0026366 | 0.060956 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06534 | 0.0051816 | 0.06441 | -58.5153 | -0.026065 | -61.0827 | 60.4319 | 60.0942 | 60.1308 | -61.1413 | -61.056 | 0.000359 | -61.1592 | 60.2551 | 60.3231 | 60.3583 | -61.1723 | -0.006994 | 0.01168 | 2.619 | 0.051666 | 0.05866 | -0.32606 | -0.28941 | -0.037971 | -0.16513 | 0.07829 | -0.024896 | 0.013075 | -0.097168 | -0.061917 | 121.5662 | 121.2285 | 121.2652 | 61.1083 | -121.5616 | 121.3894 | 121.4574 | 121.4926 | 61.1347 | -121.5925
12.4531 | 121.9299 | -61.1664 | 60.4248 | 1.4211e-13 | -0.0099101 | -0.00030992 | 0.064599 | -0.002423 | 0.060956 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064699 | 0.0051816 | 0.064837 | -58.4924 | -0.021486 | -61.0781 | 60.4365 | 60.0942 | 60.1217 | -61.1368 | -61.0606 | 0.000359 | -61.1684 | 60.2551 | 60.3231 | 60.3492 | -61.1769 | 0.029629 | 0.01168 | 2.6739 | 0.088288 | 0.058659 | -0.33064 | -0.30315 | -0.010506 | -0.16971 | 0.10576 | -0.00201 | 0.008496 | -0.10175 | -0.075652 | 121.6029 | 121.2605 | 121.288 | 61.1449 | -121.5616 | 121.4215 | 121.4894 | 121.5155 | 61.1667 | -121.6017
14.1406 | 121.9482 | -61.1206 | 60.4477 | 1.4211e-13 | -0.0099101 | -0.00052352 | 0.064599 | -0.0022094 | 0.06117 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.065126 | 0.0047542 | 0.065051 | -58.5107 | -0.021486 | -61.0735 | 60.4319 | 60.085 | 60.1217 | -61.1459 | -61.0606 | 0.009516 | -61.1684 | 60.2597 | 60.3276 | 60.2759 | -61.1769 | -0.025306 | -0.015786 | 2.6099 | 0.04709 | 0.072396 | -0.36269 | -0.32603 | -0.056283 | -0.18802 | 0.059978 | -0.047787 | 0.008496 | -0.12006 | -0.1718 | 121.5525 | 121.2056 | 121.2423 | 61.0991 | -121.5936 | 121.3803 | 121.4482 | 121.3965 | 61.1301 | -121.6246
15.8125 | 121.8018 | -61.116 | 60.5576 | 1.4211e-13 | -0.0099101 | -0.00052352 | 0.064812 | -0.002423 | 0.060956 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0051816 | 0.064837 | -58.5107 | -0.030644 | -61.0735 | 60.4411 | 60.0896 | 60.1171 | -61.1413 | -61.0652 | 0.000359 | -61.1684 | 60.2551 | 60.3231 | 60.3583 | -61.1769 | -0.025304 | -0.11649 | 2.6053 | 0.042513 | 0.067817 | -0.46797 | -0.44048 | -0.06086 | -0.30246 | 0.050822 | -0.052364 | 0.008496 | -0.2345 | -0.19925 | 121.5571 | 121.2056 | 121.2331 | 61.0854 | -121.6989 | 121.3711 | 121.4391 | 121.4743 | 61.1164 | -121.7344
17.4844 | 121.8887 | -61.1389 | 60.4797 | 1.4211e-13 | -0.010338 | -0.00052352 | 0.065026 | -0.0028504 | 0.06117 | 0.012972 | 0.00013254 | 0.00037167 | 0.064913 | 0.0053952 | 0.064624 | -58.5428 | -0.026065 | -61.0735 | 60.4365 | 60.0942 | 60.1217 | -61.1368 | -61.056 | -0.00422 | -61.1547 | 60.2597 | 60.3185 | 60.34 | -61.1769 | 0.002163 | -0.043251 | 2.5961 | 0.065401 | 0.063238 | -0.38557 | -0.35808 | -0.037972 | -0.22007 | 0.082868 | -0.015739 | 0.022233 | -0.16126 | -0.13974 | 121.5754 | 121.2331 | 121.2606 | 61.1129 | -121.6165 | 121.3986 | 121.4574 | 121.4789 | 61.1347 | -121.6566
19.1719 | 121.9254 | -61.0886 | 60.5164 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064812 | -0.0026366 | 0.060956 | -0.0022889 | 0.00077334 | 0.00015807 | 0.065126 | 0.0047542 | 0.064196 | -58.5565 | -0.030644 | -61.0827 | 60.4365 | 60.085 | 60.1217 | -61.1505 | -61.0652 | 0.004938 | -61.1684 | 60.2551 | 60.3322 | 60.3537 | -61.1769 | -0.061928 | -0.079872 | 2.532 | 0.00589 | 0.067818 | -0.43135 | -0.3947 | -0.088326 | -0.26127 | 0.023356 | -0.07983 | 0.008496 | -0.18414 | -0.16262 | 121.525 | 121.1736 | 121.2102 | 61.0579 | -121.6668 | 121.3437 | 121.4208 | 121.4423 | 61.0935 | -121.6932
20.9219 | 121.9025 | -61.1481 | 60.4706 | 1.4211e-13 | -0.010338 | -0.00052352 | 0.064599 | -0.002423 | 0.06117 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064699 | 0.0049678 | 0.065051 | -58.5657 | -0.026065 | -61.0689 | 60.4365 | 60.0896 | 60.1217 | -61.1368 | -61.0606 | -0.008798 | -61.1592 | 60.2505 | 60.3185 | 60.3583 | -61.1769 | 0.011318 | -0.034096 | 2.5824 | 0.079134 | 0.067816 | -0.381 | -0.34892 | -0.028817 | -0.22007 | 0.087444 | -0.011163 | 0.017654 | -0.1521 | -0.11227 | 121.5846 | 121.2377 | 121.2697 | 61.122 | -121.6073 | 121.3986 | 121.4666 | 121.5064 | 61.1393 | -121.6475
22.6094 | 121.8842 | -61.1298 | 60.4385 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064812 | -0.0026366 | 0.060956 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.065126 | 0.0049678 | 0.06441 | -58.5291 | -0.026065 | -61.0735 | 60.4273 | 60.085 | 60.1171 | -61.1322 | -61.056 | 0.000359 | -61.1592 | 60.2551 | 60.3231 | 60.3537 | -61.1815 | -0.002413 | -0.01121 | 2.6007 | 0.056246 | 0.058659 | -0.35353 | -0.32146 | -0.051706 | -0.18345 | 0.073713 | -0.029473 | 0.022233 | -0.11548 | -0.084806 | 121.5571 | 121.2148 | 121.2468 | 61.1037 | -121.5707 | 121.3849 | 121.4528 | 121.4835 | 61.1301 | -121.62
24.3594 | 121.8613 | -61.0886 | 60.5392 | 1.4211e-13 | -0.010124 | -0.00073712 | 0.064812 | -0.002423 | 0.06117 | 0.0053411 | 0.00055974 | 0.00015807 | 0.065126 | 0.0049678 | 0.064624 | -58.5336 | -0.030644 | -61.0781 | 60.4365 | 60.0758 | 60.1171 | -61.1459 | -61.0606 | 0.000359 | -61.1592 | 60.2551 | 60.3231 | 60.3583 | -61.1815 | -0.057349 | -0.10276 | 2.5549 | 0.010468 | 0.067817 | -0.4634 | -0.42217 | -0.092905 | -0.28415 | 0.027935 | -0.070672 | 0.022233 | -0.21619 | -0.18094 | 121.525 | 121.1644 | 121.2056 | 61.0579 | -121.6852 | 121.3437 | 121.4116 | 121.4469 | 61.0889 | -121.7207
26.0312 | 121.9391 | -61.1435 | 60.4294 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064812 | -0.0028504 | 0.06117 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064913 | 0.0051816 | 0.064624 | -58.5016 | -0.030644 | -61.0781 | 60.4319 | 60.085 | 60.1171 | -61.1322 | -61.056 | 0.000359 | -61.1547 | 60.2551 | 60.3322 | 60.3537 | -61.1769 | 0.01132 | 0.002525 | 2.6419 | 0.0654 | 0.05408 | -0.34437 | -0.3123 | -0.033394 | -0.17429 | 0.087446 | -0.011161 | 0.022233 | -0.097166 | -0.07565 | 121.5754 | 121.2285 | 121.2606 | 61.1128 | -121.5616 | 121.3986 | 121.4757 | 121.4972 | 61.1439 | -121.6063
27.7188 | 121.9116 | -61.1252 | 60.4706 | 1.4211e-13 | -0.010338 | -9.6116e-05 | 0.065026 | -0.0026366 | 0.060956 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.065126 | 0.0053952 | 0.06441 | -58.5565 | -0.026065 | -61.0781 | 60.4365 | 60.0804 | 60.1125 | -61.1276 | -61.0515 | 0.014095 | -61.1592 | 60.2551 | 60.3231 | 60.3492 | -61.1769 | -0.002412 | -0.034096 | 2.5686 | 0.047089 | 0.049501 | -0.39015 | -0.35808 | -0.051705 | -0.21549 | 0.073713 | -0.034051 | 0.017654 | -0.14752 | -0.12143 | 121.5617 | 121.2056 | 121.2377 | 61.0991 | -121.5982 | 121.3803 | 121.4482 | 121.4743 | 61.1393 | -121.6475
29.4688 | 121.8475 | -61.116 | 60.5118 | 1.4211e-13 | -0.0099101 | -0.00073712 | 0.065026 | -0.0026366 | 0.061383 | 0.0053411 | 0.00013254 | 0.00037167 | 0.064913 | 0.0051816 | 0.06441 | -58.4833 | -0.030644 | -61.0781 | 60.4365 | 60.0896 | 60.1217 | -61.1322 | -61.0606 | 0.000359 | -61.1592 | 60.2459 | 60.3276 | 60.3492 | -61.1769 | -0.016146 | -0.075295 | 2.6327 | 0.037934 | 0.05408 | -0.42219 | -0.39012 | -0.06086 | -0.26584 | 0.055401 | -0.043206 | 0.017654 | -0.18414 | -0.16263 | 121.5525 | 121.2056 | 121.2377 | 61.0854 | -121.644 | 121.362 | 121.4437 | 121.4652 | 61.1164 | -121.6887
31.1562 | 121.9482 | -61.1389 | 60.3836 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064812 | -0.0026366 | 0.06117 | 0.0053411 | 0.00034614 | 0.00037167 | 0.065126 | 0.0053952 | 0.064196 | -58.497 | -0.021486 | -61.0781 | 60.4319 | 60.085 | 60.1125 | -61.1322 | -61.0423 | 0.004938 | -61.1638 | 60.2505 | 60.3185 | 60.3492 | -61.1769 | 0.006742 | 0.048301 | 2.6419 | 0.060822 | 0.05408 | -0.2986 | -0.2711 | -0.037972 | -0.13309 | 0.096604 | -0.024897 | 0.013075 | -0.065126 | -0.034453 | 121.5708 | 121.2239 | 121.2514 | 61.1174 | -121.5158 | 121.3894 | 121.4574 | 121.4881 | 61.1439 | -121.5605
32.8438 | 121.788 | -61.1664 | 60.4843 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.065026 | -0.0026366 | 0.060956 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064913 | 0.0049678 | 0.06441 | -58.465 | -0.030644 | -61.0918 | 60.4319 | 60.0896 | 60.1262 | -61.123 | -61.0515 | 0.000359 | -61.1592 | 60.2551 | 60.3185 | 60.3171 | -61.1769 | 0.043366 | -0.052407 | 2.7014 | 0.074554 | 0.031188 | -0.39473 | -0.35808 | -0.010506 | -0.22922 | 0.11491 | 0.007148 | 0.017654 | -0.16583 | -0.16721 | 121.5983 | 121.256 | 121.2926 | 61.1357 | -121.6073 | 121.4215 | 121.4849 | 121.4835 | 61.1667 | -121.6612
34.5312 | 121.788 | -61.1664 | 60.4752 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064812 | -0.0028504 | 0.060956 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0053952 | 0.064624 | -58.4604 | -0.026065 | -61.0781 | 60.4319 | 60.0896 | 60.1171 | -61.1368 | -61.0469 | 0.000359 | -61.1547 | 60.2505 | 60.3231 | 60.3537 | -61.1723 | 0.029629 | -0.043252 | 2.706 | 0.088288 | 0.058659 | -0.38557 | -0.35808 | -0.005927 | -0.22465 | 0.11949 | 0.011727 | 0.017654 | -0.1521 | -0.12143 | 121.5983 | 121.256 | 121.2835 | 61.1403 | -121.6119 | 121.4169 | 121.4894 | 121.5201 | 61.1667 | -121.6475
36.2188 | 121.7789 | -61.1114 | 60.5759 | 1.4211e-13 | -0.010338 | -0.00052352 | 0.065026 | -0.002423 | 0.060956 | -0.0022889 | 0.00034614 | -0.00026913 | 0.065126 | 0.0053952 | 0.064624 | -58.4558 | -0.026065 | -61.0781 | 60.4273 | 60.085 | 60.1262 | -61.1276 | -61.056 | -0.00422 | -61.1547 | 60.2551 | 60.3139 | 60.3492 | -61.1815 | -0.016145 | -0.14854 | 2.6556 | 0.033356 | 0.049501 | -0.49086 | -0.44963 | -0.070017 | -0.32078 | 0.055402 | -0.043205 | 0.026812 | -0.26197 | -0.22671 | 121.5388 | 121.1965 | 121.2377 | 61.0854 | -121.7035 | 121.3665 | 121.4254 | 121.4606 | 61.1072 | -121.7573
37.9844 | 121.8613 | -61.1114 | 60.4889 | 1.4211e-13 | -0.010338 | -0.00052352 | 0.064599 | -0.002423 | 0.060956 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064913 | 0.0049678 | 0.06441 | -58.4054 | -0.021486 | -61.0872 | 60.4273 | 60.085 | 60.1217 | -61.1368 | -61.0515 | -0.008798 | -61.1547 | 60.2551 | 60.3231 | 60.3537 | -61.1677 | -0.025303 | -0.061564 | 2.706 | 0.0242 | 0.049503 | -0.40389 | -0.36723 | -0.05628 | -0.2338 | 0.05998 | -0.043205 | 0.013075 | -0.16583 | -0.13516 | 121.5388 | 121.1965 | 121.2331 | 61.09 | -121.6256 | 121.3665 | 121.4345 | 121.4652 | 61.1027 | -121.6566
39.7344 | 121.9299 | -61.0886 | 60.5072 | 1.4211e-13 | -0.010124 | -0.00052352 | 0.064385 | -0.002423 | 0.060742 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064699 | 0.0056088 | 0.06441 | -58.5199 | -0.026065 | -61.0781 | 60.4273 | 60.0758 | 60.1262 | -61.1368 | -61.056 | 0.000359 | -61.1547 | 60.2505 | 60.3368 | 60.3492 | -61.1723 | -0.048191 | -0.079874 | 2.5687 | 0.010468 | 0.058659 | -0.43135 | -0.38096 | -0.083747 | -0.25669 | 0.032514 | -0.066093 | 0.017654 | -0.17041 | -0.15805 | 121.5159 | 121.1644 | 121.2148 | 61.0625 | -121.644 | 121.3391 | 121.4254 | 121.4377 | 61.0889 | -121.6795
41.4062 | 121.843 | -61.1343 | 60.4935 | 1.4211e-13 | -0.010124 | -0.00030992 | 0.064812 | -0.003064 | 0.06117 | 0.012972 | 0.00034614 | 0.00037167 | 0.064913 | 0.0051816 | 0.064837 | -58.4054 | -0.030644 | -61.0827 | 60.4319 | 60.0896 | 60.1125 | -61.1322 | -61.0469 | -0.00422 | -61.1547 | 60.2459 | 60.3368 | 60.3492 | -61.1769 | 0.002164 | -0.061562 | 2.7289 | 0.051666 | 0.049502 | -0.40388 | -0.38097 | -0.04255 | -0.24753 | 0.087447 | -0.020317 | 0.022233 | -0.15667 | -0.14432 | 121.5662 | 121.2239 | 121.2468 | 61.1037 | -121.6256 | 121.3803 | 121.4711 | 121.4835 | 61.1301 | -121.6704
43.1719 | 121.9482 | -61.0474 | 60.498 | 1.4211e-13 | -0.010765 | -0.00052352 | 0.064812 | -0.002423 | 0.060742 | -0.0022889 | 0.00055974 | 0.00037167 | 0.065126 | 0.0049678 | 0.06441 | -58.5199 | -0.035222 | -61.0827 | 60.4365 | 60.0804 | 60.1217 | -61.1322 | -61.0515 | -0.00422 | -61.1501 | 60.2459 | 60.3231 | 60.3492 | -61.1723 | -0.084811 | -0.061562 | 2.5275 | -0.035309 | 0.049502 | -0.41762 | -0.37639 | -0.12495 | -0.25211 | -0.004107 | -0.10271 | 0.022232 | -0.17499 | -0.14889 | 121.4838 | 121.1278 | 121.169 | 61.0121 | -121.6302 | 121.2933 | 121.3704 | 121.3965 | 61.0431 | -121.6704
44.9375 | 121.843 | -61.1343 | 60.4889 | 1.4211e-13 | -0.010124 | -0.00030992 | 0.064171 | -0.0026366 | 0.060956 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0051816 | 0.06441 | -58.41 | -0.030644 | -61.0827 | 60.4365 | 60.085 | 60.1171 | -61.1322 | -61.0515 | 0.000359 | -61.1547 | 60.2414 | 60.3276 | 60.3537 | -61.1723 | 0.002164 | -0.052407 | 2.7243 | 0.051666 | 0.049502 | -0.40389 | -0.37181 | -0.037971 | -0.24754 | 0.082868 | -0.020317 | 0.017654 | -0.16125 | -0.13516 | 121.5708 | 121.2193 | 121.2514 | 61.1037 | -121.6211 | 121.3757 | 121.462 | 121.4881 | 61.1347 | -121.6612
46.625 | 121.8109 | -61.1389 | 60.4706 | 1.4211e-13 | -0.010551 | -0.00030992 | 0.064812 | -0.0028504 | 0.060742 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064485 | 0.0053952 | 0.06441 | -58.4009 | -0.026065 | -61.0781 | 60.4273 | 60.0804 | 60.1171 | -61.1322 | -61.0469 | 0.000359 | -61.1547 | 60.2459 | 60.3231 | 60.3537 | -61.1723 | 0.006742 | -0.043253 | 2.738 | 0.060822 | 0.05408 | -0.39015 | -0.3535 | -0.033393 | -0.22465 | 0.092025 | -0.015739 | 0.017654 | -0.14752 | -0.11685 | 121.5662 | 121.2193 | 121.256 | 61.1129 | -121.6028 | 121.3849 | 121.462 | 121.4926 | 61.1393 | -121.6429
48.3594 | 121.9254 | -61.084 | 60.5026 | 1.4211e-13 | -0.010551 | -0.00030992 | 0.064812 | -0.0028504 | 0.060956 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064913 | 0.0049678 | 0.06441 | -58.5062 | -0.026065 | -61.0872 | 60.4319 | 60.0804 | 60.1125 | -61.1322 | -61.0606 | -0.00422 | -61.1501 | 60.2459 | 60.3276 | 60.3537 | -61.1677 | -0.04819 | -0.070718 | 2.5778 | -0.003266 | 0.044924 | -0.4222 | -0.39012 | -0.083746 | -0.25669 | 0.023357 | -0.066093 | 0.017653 | -0.17499 | -0.14889 | 121.5159 | 121.1644 | 121.1965 | 61.0579 | -121.6348 | 121.3299 | 121.4116 | 121.4377 | 61.0798 | -121.6704
50.0625 | 121.7697 | -61.1664 | 60.4843 | 1.4211e-13 | -0.010551 | -0.00030992 | 0.064385 | -0.002423 | 0.060956 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064699 | 0.0053952 | 0.06441 | -58.41 | -0.030644 | -61.0781 | 60.4365 | 60.0804 | 60.1171 | -61.1322 | -61.0469 | -0.008798 | -61.1501 | 60.2459 | 60.3231 | 60.3492 | -61.1632 | 0.034208 | -0.047829 | 2.7564 | 0.088288 | 0.05408 | -0.40389 | -0.36723 | 0.003231 | -0.23838 | 0.11949 | 0.016305 | 0.013074 | -0.16125 | -0.13516 | 121.6029 | 121.2468 | 121.2835 | 61.1357 | -121.6165 | 121.4123 | 121.4894 | 121.5155 | 61.1576 | -121.6475
51.7969 | 121.8796 | -61.1343 | 60.4385 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064812 | -0.0026366 | 0.060742 | -0.0022889 | 0.00034614 | 0.00015807 | 0.065126 | 0.0056088 | 0.06441 | -58.4787 | -0.026065 | -61.0827 | 60.4273 | 60.0804 | 60.1217 | -61.1368 | -61.0515 | 0.000359 | -61.1501 | 60.2505 | 60.3322 | 60.3492 | -61.1677 | -0.002415 | -0.01121 | 2.6556 | 0.051666 | 0.054081 | -0.35811 | -0.31688 | -0.033392 | -0.18803 | 0.082868 | -0.015739 | 0.017653 | -0.10632 | -0.089385 | 121.5617 | 121.2148 | 121.256 | 61.1083 | -121.5753 | 121.3849 | 121.4666 | 121.4835 | 61.1347 | -121.6063
53.4688 | 121.8063 | -61.1755 | 60.4752 | 1.4211e-13 | -0.010765 | -0.00030992 | 0.064812 | -0.002423 | 0.060956 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0051816 | 0.064624 | -58.4146 | -0.026065 | -61.0827 | 60.4319 | 60.085 | 60.1217 | -61.1368 | -61.0423 | -0.00422 | -61.1501 | 60.2505 | 60.3276 | 60.3492 | -61.1723 | 0.038784 | -0.043252 | 2.7609 | 0.092865 | 0.054081 | -0.39015 | -0.3535 | 0.003228 | -0.22465 | 0.13322 | 0.02546 | 0.022232 | -0.14752 | -0.12601 | 121.6074 | 121.2605 | 121.2972 | 61.1495 | -121.6119 | 121.4261 | 121.5032 | 121.5247 | 61.1713 | -121.6475
55.25 | 121.9162 | -61.1069 | 60.4752 | 1.4211e-13 | -0.010979 | -0.00030992 | 0.064599 | -0.0028504 | 0.060956 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0056088 | 0.06441 | -58.5062 | -0.026065 | -61.0827 | 60.4228 | 60.0758 | 60.1171 | -61.1368 | -61.0515 | 0.000359 | -61.1547 | 60.2551 | 60.3322 | 60.3492 | -61.1677 | -0.02988 | -0.052409 | 2.6007 | 0.024201 | 0.054081 | -0.39931 | -0.35808 | -0.060857 | -0.22007 | 0.055403 | -0.047782 | 0.013075 | -0.14294 | -0.12601 | 121.5296 | 121.1827 | 121.224 | 61.0808 | -121.6119 | 121.362 | 121.4391 | 121.456 | 61.1072 | -121.6429
57 | 121.9162 | -61.1618 | 60.4156 | 1.4211e-13 | -0.010551 | -9.6116e-05 | 0.064385 | -0.0028504 | 0.060529 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.064913 | 0.0053952 | 0.064624 | -58.4283 | -0.021486 | -61.0918 | 60.4273 | 60.0758 | 60.1217 | -61.1368 | -61.0515 | -0.008798 | -61.1455 | 60.2459 | 60.3322 | 60.3492 | -61.1632 | 0.025051 | 0.011679 | 2.7335 | 0.069976 | 0.044925 | -0.3398 | -0.29399 | -0.001347 | -0.16971 | 0.11033 | 0.016306 | 0.017653 | -0.083433 | -0.066496 | 121.5891 | 121.2377 | 121.2835 | 61.1403 | -121.5524 | 121.4077 | 121.494 | 121.511 | 61.153 | -121.5788
58.6875 | 121.8887 | -61.1389 | 60.4156 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064812 | -0.0028504 | 0.060742 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064485 | 0.0051816 | 0.06441 | -58.4238 | -0.026065 | -61.0781 | 60.4273 | 60.0758 | 60.1171 | -61.1368 | -61.056 | 0.004938 | -61.1547 | 60.2459 | 60.3322 | 60.3537 | -61.1586 | 0.002163 | 0.011679 | 2.7152 | 0.060822 | 0.058659 | -0.3398 | -0.29857 | -0.019657 | -0.16971 | 0.082868 | -0.015739 | 0.003918 | -0.083433 | -0.061917 | 121.5662 | 121.2148 | 121.256 | 61.1129 | -121.5524 | 121.3849 | 121.4711 | 121.4926 | 61.1439 | -121.5742
60.4375 | 121.8292 | -61.0931 | 60.5347 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064599 | -0.0026366 | 0.060742 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.065126 | 0.0053952 | 0.063983 | -58.4741 | -0.026065 | -61.0781 | 60.409 | 60.0804 | 60.1217 | -61.1276 | -61.0515 | 0.000359 | -61.1501 | 60.2459 | 60.3276 | 60.3492 | -61.1677 | -0.034455 | -0.12565 | 2.619 | 0.015046 | 0.049501 | -0.45424 | -0.41301 | -0.07459 | -0.28873 | 0.04167 | -0.056937 | 0.017653 | -0.20703 | -0.18552 | 121.5022 | 121.1736 | 121.2148 | 61.0671 | -121.6623 | 121.3391 | 121.4208 | 121.4423 | 61.0935 | -121.7024
62.1875 | 121.9208 | -61.0657 | 60.4706 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064599 | -0.0026366 | 0.060956 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064913 | 0.0053952 | 0.064196 | -58.5199 | -0.026065 | -61.0781 | 60.4228 | 60.0758 | 60.1171 | -61.1276 | -61.0423 | -0.00422 | -61.1501 | 60.2505 | 60.3185 | 60.3446 | -61.1677 | -0.061921 | -0.047831 | 2.5458 | -0.01242 | 0.049501 | -0.39473 | -0.3535 | -0.10206 | -0.22007 | 0.023362 | -0.084403 | 0.017653 | -0.1521 | -0.12601 | 121.4884 | 121.1415 | 121.1828 | 61.0396 | -121.5982 | 121.3162 | 121.3842 | 121.4102 | 61.0615 | -121.6383
63.875 | 121.9208 | -61.1481 | 60.3928 | 1.4211e-13 | -0.010338 | -9.6116e-05 | 0.064171 | -0.002423 | 0.060742 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064699 | 0.0053952 | 0.06441 | -58.4421 | -0.026065 | -61.0781 | 60.4228 | 60.0804 | 60.1217 | -61.1322 | -61.0423 | 0.000359 | -61.1455 | 60.2414 | 60.3231 | 60.3537 | -61.1632 | 0.015897 | 0.029989 | 2.706 | 0.069977 | 0.05408 | -0.31233 | -0.2711 | -0.01508 | -0.1514 | 0.10576 | 0.002573 | 0.017653 | -0.069702 | -0.039029 | 121.5708 | 121.2285 | 121.2697 | 61.122 | -121.5249 | 121.3894 | 121.4711 | 121.5018 | 61.1484 | -121.5559
65.5625 | 121.8979 | -61.1572 | 60.4156 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064599 | -0.003064 | 0.060742 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064913 | 0.0053952 | 0.063983 | -58.4283 | -0.026065 | -61.0872 | 60.4228 | 60.085 | 60.1217 | -61.1322 | -61.0423 | 0.004938 | -61.1409 | 60.2414 | 60.3276 | 60.3446 | -61.1677 | 0.025053 | 0.007101 | 2.7289 | 0.069977 | 0.044924 | -0.33064 | -0.29399 | -0.010503 | -0.17429 | 0.11491 | 0.016308 | 0.026811 | -0.088012 | -0.071074 | 121.58 | 121.2422 | 121.2789 | 61.1312 | -121.5478 | 121.3986 | 121.4849 | 121.5018 | 61.1622 | -121.5834
67.2344 | 121.9254 | -61.0703 | 60.4706 | 1.4211e-13 | -0.010765 | -0.00030992 | 0.064599 | -0.0026366 | 0.060315 | 0.012972 | 0.00013254 | 0.00015807 | 0.065126 | 0.0053952 | 0.063983 | -58.5199 | -0.026065 | -61.0735 | 60.4228 | 60.0713 | 60.1171 | -61.1276 | -61.0423 | 0.000359 | -61.1363 | 60.2322 | 60.3231 | 60.3446 | -61.1677 | -0.057344 | -0.047831 | 2.5503 | -0.003264 | 0.05408 | -0.39931 | -0.3535 | -0.097479 | -0.23838 | 0.027939 | -0.06609 | 0.031389 | -0.14752 | -0.12601 | 121.493 | 121.1415 | 121.1873 | 61.0442 | -121.5982 | 121.3024 | 121.3933 | 121.4148 | 61.0706 | -121.6383
68.9219 | 121.9299 | -61.0703 | 60.4752 | 1.4211e-13 | -0.010765 | -0.00052352 | 0.064812 | -0.002423 | 0.060315 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064913 | 0.0058226 | 0.06441 | -58.5199 | -0.030644 | -61.0689 | 60.4228 | 60.0758 | 60.1217 | -61.1276 | -61.0423 | 0.000359 | -61.1455 | 60.2368 | 60.3185 | 60.3492 | -61.1632 | -0.057344 | -0.052409 | 2.5503 | 0.001314 | 0.058658 | -0.39931 | -0.3535 | -0.0929 | -0.23838 | 0.027939 | -0.075247 | 0.017653 | -0.15668 | -0.12601 | 121.493 | 121.1461 | 121.1919 | 61.0396 | -121.6028 | 121.307 | 121.3887 | 121.4194 | 61.0706 | -121.6383
70.6719 | 121.9116 | -61.0519 | 60.4843 | 1.4211e-13 | -0.010551 | -0.00052352 | 0.064599 | -0.0026366 | 0.060742 | 0.012972 | 0.00013254 | 0.00037167 | 0.064913 | 0.0056088 | 0.06441 | -58.5153 | -0.030644 | -61.0735 | 60.4273 | 60.0804 | 60.1171 | -61.1276 | -61.0377 | 0.004938 | -61.1455 | 60.2414 | 60.3276 | 60.3492 | -61.1723 | -0.075654 | -0.056986 | 2.5366 | -0.021574 | 0.05408 | -0.40389 | -0.36723 | -0.12037 | -0.24296 | 0.014208 | -0.093557 | 0.026811 | -0.15668 | -0.13516 | 121.4793 | 121.1324 | 121.169 | 61.0213 | -121.6119 | 121.2933 | 121.3796 | 121.4011 | 61.0569 | -121.6566
72.3438 | 121.8292 | -61.1435 | 60.498 | 1.4211e-13 | -0.010551 | -0.00073712 | 0.064599 | -0.0026366 | 0.060742 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064913 | 0.0053952 | 0.064196 | -58.4009 | -0.030644 | -61.0781 | 60.4228 | 60.0713 | 60.1171 | -61.123 | -61.0423 | 0.000359 | -61.1409 | 60.2459 | 60.3276 | 60.34 | -61.1632 | 0.020478 | -0.075297 | 2.7426 | 0.0654 | 0.044922 | -0.42678 | -0.38097 | -0.019657 | -0.25211 | 0.10118 | 0.002575 | 0.022232 | -0.17041 | -0.15805 | 121.5662 | 121.2148 | 121.2606 | 61.1128 | -121.6211 | 121.3894 | 121.4711 | 121.4835 | 61.1439 | -121.6612
74.0938 | 121.7834 | -61.1023 | 60.5484 | 1.4211e-13 | -0.010979 | -0.00095092 | 0.064599 | -0.0026366 | 0.060529 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0056088 | 0.06441 | -58.4329 | -0.026065 | -61.0781 | 60.4182 | 60.0758 | 60.1033 | -61.1276 | -61.0423 | 0.004938 | -61.1501 | 60.2322 | 60.3231 | 60.3492 | -61.1677 | -0.0253 | -0.13023 | 2.6694 | 0.024201 | 0.049501 | -0.47255 | -0.44506 | -0.065435 | -0.3162 | 0.059983 | -0.047782 | 0.017653 | -0.22534 | -0.19925 | 121.5205 | 121.1781 | 121.2056 | 61.0762 | -121.676 | 121.3345 | 121.4254 | 121.4514 | 61.1072 | -121.7161
75.7812 | 121.9299 | -61.0611 | 60.4797 | 1.4211e-13 | -0.010979 | -0.00052352 | 0.064812 | -0.0028504 | 0.060529 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.064699 | 0.0053952 | 0.064196 | -58.5199 | -0.026065 | -61.0781 | 60.4273 | 60.0713 | 60.1217 | -61.1276 | -61.0423 | 0.000359 | -61.1409 | 60.2459 | 60.3276 | 60.3446 | -61.1677 | -0.066499 | -0.052408 | 2.5412 | -0.016998 | 0.049501 | -0.40847 | -0.35808 | -0.10663 | -0.2338 | 0.018784 | -0.079823 | 0.026811 | -0.1521 | -0.13516 | 121.4884 | 121.1324 | 121.1828 | 61.035 | -121.6073 | 121.307 | 121.3887 | 121.4057 | 61.0615 | -121.6475
77.4688 | 121.7972 | -61.0703 | 60.5576 | 1.4211e-13 | -0.010979 | -0.00052352 | 0.065026 | -0.0028504 | 0.060742 | 0.012972 | 0.00055974 | 0.00037167 | 0.064699 | 0.0053952 | 0.06441 | -58.4604 | -0.021486 | -61.0735 | 60.4182 | 60.0758 | 60.1171 | -61.1322 | -61.0377 | 0.000359 | -61.1409 | 60.2459 | 60.3231 | 60.34 | -61.1586 | -0.061923 | -0.13938 | 2.6099 | -0.003264 | 0.058659 | -0.48171 | -0.44048 | -0.088322 | -0.31162 | 0.032518 | -0.070668 | 0.017654 | -0.2345 | -0.21756 | 121.4884 | 121.1461 | 121.1873 | 61.0488 | -121.6897 | 121.3162 | 121.3933 | 121.4102 | 61.0706 | -121.7161
79.2344 | 121.7972 | -61.1206 | 60.5484 | 1.4211e-13 | -0.010765 | -0.00073712 | 0.064385 | -0.0026366 | 0.060742 | 0.0053411 | 0.00013254 | -0.00026913 | 0.064699 | 0.0051816 | 0.064196 | -58.4238 | -0.026065 | -61.0781 | 60.4228 | 60.0804 | 60.1079 | -61.1276 | -61.0423 | -0.00422 | -61.1409 | 60.2414 | 60.3093 | 60.3354 | -61.1632 | -0.00699 | -0.12565 | 2.6968 | 0.042511 | 0.049501 | -0.46797 | -0.44048 | -0.042546 | -0.30704 | 0.078293 | -0.020314 | 0.022232 | -0.23908 | -0.21298 | 121.5434 | 121.201 | 121.2285 | 61.0945 | -121.676 | 121.362 | 121.4299 | 121.456 | 61.1164 | -121.7116
80.9375 | 121.7789 | -61.1938 | 60.4614 | 1.4211e-13 | -0.010765 | -0.00030992 | 0.064599 | -0.0026366 | 0.060956 | -0.0022889 | 0.00055974 | -0.00026913 | 0.064699 | 0.0056088 | 0.06441 | -58.4054 | -0.021486 | -61.0735 | 60.4182 | 60.0804 | 60.1125 | -61.1322 | -61.0469 | 0.004938 | -61.1409 | 60.2414 | 60.3276 | 60.3354 | -61.1632 | 0.061674 | -0.043254 | 2.7884 | 0.12033 | 0.058659 | -0.381 | -0.34892 | 0.030697 | -0.22007 | 0.14696 | 0.052929 | 0.022232 | -0.13379 | -0.12601 | 121.612 | 121.2743 | 121.3064 | 61.1724 | -121.5936 | 121.4352 | 121.5215 | 121.5293 | 61.1988 | -121.6246
82.6875 | 121.7743 | -61.1755 | 60.4385 | 1.4211e-13 | -0.010979 | -0.00030992 | 0.064385 | -0.0028504 | 0.060956 | 0.012972 | 0.00034614 | -0.00026913 | 0.064913 | 0.0056088 | 0.06441 | -58.4009 | -0.030644 | -61.0689 | 60.4182 | 60.0713 | 60.1171 | -61.1139 | -61.0423 | 0.004938 | -61.1455 | 60.2368 | 60.3139 | 60.3446 | -61.1632 | 0.061679 | -0.020366 | 2.7747 | 0.1066 | 0.044921 | -0.36727 | -0.32146 | 0.012386 | -0.20176 | 0.13322 | 0.030039 | 0.017653 | -0.12464 | -0.093963 | 121.5937 | 121.2468 | 121.2926 | 61.1449 | -121.5524 | 121.4123 | 121.4894 | 121.5201 | 61.1805 | -121.6017
84.3594 | 121.7926 | -61.1664 | 60.4202 | 1.4211e-13 | -0.010979 | -0.00073712 | 0.064599 | -0.002423 | 0.060529 | -0.0022889 | 0.00013254 | 0.00015807 | 0.065126 | 0.0051816 | 0.063983 | -58.41 | -0.016908 | -61.0735 | 60.4136 | 60.0758 | 60.1171 | -61.1184 | -61.0423 | 0.004938 | -61.1455 | 60.2368 | 60.3276 | 60.3492 | -61.1586 | 0.047945 | -0.006634 | 2.7564 | 0.092867 | 0.044922 | -0.34438 | -0.30315 | 0.007809 | -0.18345 | 0.12407 | 0.020884 | 0.013075 | -0.09259 | -0.071074 | 121.58 | 121.2422 | 121.2835 | 61.1495 | -121.5387 | 121.4032 | 121.494 | 121.5155 | 61.1713 | -121.5788
86.0469 | 121.8567 | -61.116 | 60.4431 | 1.4211e-13 | -0.010979 | -9.6116e-05 | 0.064599 | -0.0028504 | 0.060742 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0053952 | 0.06441 | -58.4833 | -0.030644 | -61.0644 | 60.4182 | 60.0758 | 60.1125 | -61.1184 | -61.0423 | -0.00422 | -61.1455 | 60.2459 | 60.3139 | 60.34 | -61.1586 | -0.002409 | -0.024943 | 2.6327 | 0.051669 | 0.054078 | -0.36727 | -0.33061 | -0.042545 | -0.19718 | 0.073716 | -0.02947 | 0.013075 | -0.12921 | -0.10312 | 121.5342 | 121.1919 | 121.2285 | 61.0854 | -121.5616 | 121.362 | 121.4299 | 121.456 | 61.1118 | -121.6017
87.7344 | 121.9254 | -61.0977 | 60.4843 | 1.4211e-13 | -0.010979 | -0.00073712 | 0.064599 | -0.0026366 | 0.060956 | 0.0053411 | 0.00013254 | -0.00026913 | 0.064913 | 0.0053952 | 0.06441 | -58.5199 | -0.021486 | -61.0735 | 60.4182 | 60.0804 | 60.1171 | -61.1276 | -61.0423 | -0.00422 | -61.1455 | 60.2459 | 60.3139 | 60.34 | -61.1586 | -0.029878 | -0.066142 | 2.5778 | 0.024202 | 0.05408 | -0.40389 | -0.36723 | -0.060856 | -0.23838 | 0.055405 | -0.047781 | 0.013075 | -0.17041 | -0.14432 | 121.5159 | 121.1781 | 121.2148 | 61.0762 | -121.6119 | 121.3437 | 121.4116 | 121.4377 | 61.0935 | -121.6429
89.4688 | 121.8567 | -61.1618 | 60.4111 | 1.4211e-13 | -0.011406 | -0.00052352 | 0.064599 | -0.002423 | 0.060529 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064485 | 0.0058226 | 0.063769 | -58.4192 | -0.026065 | -61.0735 | 60.4136 | 60.0713 | 60.1079 | -61.123 | -61.0332 | 0.000359 | -61.1363 | 60.2368 | 60.3185 | 60.3492 | -61.1632 | 0.038788 | 0.002521 | 2.7426 | 0.088289 | 0.049501 | -0.3398 | -0.30315 | -0.001347 | -0.17429 | 0.12865 | 0.025463 | 0.02681 | -0.092592 | -0.061919 | 121.5754 | 121.2331 | 121.2697 | 61.1357 | -121.5341 | 121.3986 | 121.4803 | 121.511 | 61.1622 | -121.5742
91.25 | 121.8246 | -61.1298 | 60.4248 | 1.4211e-13 | -0.010765 | -0.00052352 | 0.064599 | -0.002423 | 0.060742 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064913 | 0.0053952 | 0.064196 | -58.4054 | -0.021486 | -61.0689 | 60.4228 | 60.0758 | 60.1079 | -61.123 | -61.0377 | -0.00422 | -61.1409 | 60.2322 | 60.3139 | 60.3446 | -61.1586 | 0.006745 | -0.002055 | 2.7243 | 0.060824 | 0.054079 | -0.34896 | -0.31688 | -0.028812 | -0.19261 | 0.092028 | -0.011158 | 0.017654 | -0.1109 | -0.08023 | 121.5525 | 121.2056 | 121.2377 | 61.1083 | -121.5478 | 121.362 | 121.4437 | 121.4743 | 61.1255 | -121.5834
93.0156 | 121.8018 | -61.1114 | 60.466 | 1.4211e-13 | -0.010979 | -0.00052352 | 0.065026 | -0.0026366 | 0.060742 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0056088 | 0.06441 | -58.4054 | -0.021486 | -61.0689 | 60.4182 | 60.0758 | 60.1079 | -61.1184 | -61.0332 | -0.00422 | -61.1409 | 60.2368 | 60.3185 | 60.34 | -61.1632 | -0.006987 | -0.047831 | 2.706 | 0.042513 | 0.0495 | -0.39015 | -0.35808 | -0.051701 | -0.22922 | 0.078295 | -0.029469 | 0.022232 | -0.14752 | -0.12601 | 121.5296 | 121.1873 | 121.2194 | 61.09 | -121.5844 | 121.3482 | 121.4299 | 121.4514 | 61.1072 | -121.6292
94.7188 | 121.7651 | -61.1801 | 60.4568 | 1.4211e-13 | -0.011192 | -0.00052352 | 0.064812 | -0.0028504 | 0.060529 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0056088 | 0.063983 | -58.4009 | -0.026065 | -61.0735 | 60.4182 | 60.0758 | 60.1125 | -61.1276 | -61.0332 | 0.000359 | -61.1363 | 60.2368 | 60.3185 | 60.34 | -61.1632 | 0.05252 | -0.038676 | 2.7792 | 0.1066 | 0.05408 | -0.381 | -0.34435 | 0.016964 | -0.22007 | 0.14696 | 0.043774 | 0.02681 | -0.13837 | -0.11685 | 121.5983 | 121.256 | 121.2926 | 61.154 | -121.5844 | 121.4169 | 121.4986 | 121.5201 | 61.1805 | -121.62
96.4688 | 121.8155 | -61.1526 | 60.4202 | 1.4211e-13 | -0.010979 | -0.00030992 | 0.064599 | -0.0028504 | 0.060956 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064699 | 0.0058226 | 0.06441 | -58.4054 | -0.030644 | -61.0644 | 60.4136 | 60.0758 | 60.1125 | -61.1139 | -61.0377 | 0.004938 | -61.1409 | 60.2322 | 60.3139 | 60.3354 | -61.1632 | 0.038791 | -0.006634 | 2.7472 | 0.08829 | 0.049499 | -0.34438 | -0.30772 | -0.010502 | -0.18803 | 0.11492 | 0.01173 | 0.022232 | -0.10632 | -0.08481 | 121.5662 | 121.2285 | 121.2652 | 61.122 | -121.5341 | 121.3848 | 121.4666 | 121.4881 | 61.1576 | -121.5834
98.25 | 121.9162 | -61.116 | 60.3928 | 1.4211e-13 | -0.011192 | -0.00052352 | 0.064171 | -0.0026366 | 0.060742 | -0.0099194 | 0.00013254 | 0.00037167 | 0.065126 | 0.0056088 | 0.06441 | -58.4329 | -0.026065 | -61.0598 | 60.4182 | 60.0713 | 60.1079 | -61.123 | -61.0423 | 0.004938 | -61.1363 | 60.2276 | 60.3139 | 60.3446 | -61.1586 | -0.006988 | 0.025411 | 2.6831 | 0.056248 | 0.063236 | -0.32149 | -0.28484 | -0.042545 | -0.16514 | 0.073716 | -0.020313 | 0.022232 | -0.078859 | -0.048186 | 121.5342 | 121.1873 | 121.224 | 61.09 | -121.5158 | 121.3436 | 121.4299 | 121.4606 | 61.121 | -121.5513
99.9844 | 121.8475 | -61.0657 | 60.5118 | 1.4211e-13 | -0.010979 | -0.00030992 | 0.064599 | -0.002423 | 0.060529 | 0.0053411 | 0.00055974 | 0.00037167 | 0.065126 | 0.0058226 | 0.064196 | -58.4741 | -0.035222 | -61.0735 | 60.4182 | 60.0713 | 60.1033 | -61.123 | -61.0332 | 0.000359 | -61.1363 | 60.2322 | 60.3185 | 60.3354 | -61.1677 | -0.057342 | -0.093608 | 2.5916 | -0.007841 | 0.049501 | -0.44051 | -0.40844 | -0.10206 | -0.27958 | 0.032519 | -0.070667 | 0.031389 | -0.1933 | -0.17636 | 121.4838 | 121.1369 | 121.169 | 61.0305 | -121.6348 | 121.2979 | 121.3842 | 121.4011 | 61.066 | -121.6795
101.7344 | 121.756 | -61.0748 | 60.5392 | 1.4211e-13 | -0.011406 | -0.00030992 | 0.064599 | -0.002423 | 0.060742 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064699 | 0.0056088 | 0.064196 | -58.4283 | -0.021486 | -61.0689 | 60.4136 | 60.0804 | 60.1079 | -61.1276 | -61.0377 | 0.004938 | -61.1363 | 60.2368 | 60.3047 | 60.3263 | -61.1632 | -0.052766 | -0.12565 | 2.6465 | 0.005892 | 0.058658 | -0.45882 | -0.43132 | -0.088322 | -0.30247 | 0.037096 | -0.061512 | 0.02681 | -0.2345 | -0.21299 | 121.4884 | 121.1553 | 121.1828 | 61.0533 | -121.6668 | 121.3116 | 121.3796 | 121.4011 | 61.0798 | -121.7024
103.4062 | 121.9025 | -61.1343 | 60.379 | 1.4211e-13 | -0.011192 | -9.6116e-05 | 0.064812 | -0.002423 | 0.060315 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.064699 | 0.0058226 | 0.064196 | -58.4238 | -0.035222 | -61.0689 | 60.4182 | 60.0667 | 60.0988 | -61.1184 | -61.0286 | 0.004938 | -61.1409 | 60.2414 | 60.3139 | 60.34 | -61.154 | 0.015901 | 0.039144 | 2.7106 | 0.065401 | 0.0495 | -0.31234 | -0.28026 | -0.019656 | -0.13767 | 0.10576 | -0.006581 | 0.013075 | -0.065126 | -0.039032 | 121.5525 | 121.201 | 121.2331 | 61.0991 | -121.4975 | 121.3757 | 121.4482 | 121.4743 | 61.1393 | -121.533
105.1875 | 121.8109 | -61.1206 | 60.4614 | 1.4211e-13 | -0.010979 | -0.00073712 | 0.064599 | -0.0026366 | 0.060529 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0056088 | 0.064196 | -58.3963 | -0.026065 | -61.0598 | 60.409 | 60.0758 | 60.0942 | -61.123 | -61.0286 | 0.000359 | -61.1363 | 60.2368 | 60.3139 | 60.3125 | -61.1586 | -0.002411 | -0.052411 | 2.7243 | 0.060825 | 0.063236 | -0.38558 | -0.36724 | -0.037968 | -0.22465 | 0.092029 | -0.015736 | 0.022232 | -0.14752 | -0.1489 | 121.5296 | 121.1965 | 121.2148 | 61.0945 | -121.5844 | 121.3574 | 121.4345 | 121.4331 | 61.121 | -121.62
107.0469 | 121.8155 | -61.1298 | 60.4752 | 1.4211e-13 | -0.011192 | -0.00052352 | 0.064385 | -0.0026366 | 0.060529 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0056088 | 0.06441 | -58.3917 | -0.026065 | -61.0644 | 60.4136 | 60.0758 | 60.0988 | -61.1139 | -61.0332 | 0.000359 | -61.1363 | 60.2368 | 60.3139 | 60.3354 | -61.154 | 0.015903 | -0.061566 | 2.7381 | 0.065402 | 0.049499 | -0.39931 | -0.37639 | -0.024233 | -0.23838 | 0.096606 | -0.00658 | 0.017653 | -0.16126 | -0.13974 | 121.5434 | 121.2056 | 121.2285 | 61.1037 | -121.589 | 121.3665 | 121.4437 | 121.4652 | 61.1301 | -121.6292
109.0156 | 121.843 | -61.0565 | 60.4889 | 1.4211e-13 | -0.011192 | -0.00073712 | 0.064599 | -0.0026366 | 0.060742 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.064699 | 0.0056088 | 0.063983 | -58.4741 | -0.021486 | -61.0598 | 60.4182 | 60.0713 | 60.0988 | -61.1139 | -61.0332 | -0.00422 | -61.1363 | 60.2414 | 60.3139 | 60.34 | -61.154 | -0.057339 | -0.07072 | 2.5824 | -0.003261 | 0.054078 | -0.41762 | -0.39013 | -0.097475 | -0.24754 | 0.023364 | -0.079822 | 0.017653 | -0.17499 | -0.1489 | 121.4747 | 121.1278 | 121.1553 | 61.035 | -121.6028 | 121.2979 | 121.3704 | 121.3965 | 61.0523 | -121.6429
110.7031 | 121.8887 | -61.1206 | 60.4065 | 1.4211e-13 | -0.011406 | -0.00052352 | 0.064385 | -0.0028504 | 0.060529 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0056088 | 0.063983 | -58.4329 | -0.026065 | -61.0598 | 60.4136 | 60.0758 | 60.0942 | -61.1139 | -61.0286 | 0.000359 | -61.1363 | 60.2368 | 60.3093 | 60.3308 | -61.1586 | 0.006747 | 0.007099 | 2.6877 | 0.060825 | 0.054078 | -0.33065 | -0.31231 | -0.037968 | -0.16972 | 0.092029 | -0.015736 | 0.022232 | -0.097171 | -0.075655 | 121.5342 | 121.1965 | 121.2148 | 61.0945 | -121.5204 | 121.3574 | 121.4299 | 121.4514 | 61.121 | -121.5651
112.4062 | 121.8567 | -61.1023 | 60.4385 | 1.4211e-13 | -0.011192 | -0.00073712 | 0.064599 | -0.002423 | 0.060315 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.064699 | 0.0056088 | 0.064196 | -58.4512 | -0.026065 | -61.0598 | 60.409 | 60.0667 | 60.0942 | -61.1184 | -61.0286 | 0.004938 | -61.1318 | 60.2322 | 60.3093 | 60.3354 | -61.1586 | -0.016142 | -0.029523 | 2.6511 | 0.042515 | 0.058657 | -0.37185 | -0.34435 | -0.056278 | -0.20634 | 0.073719 | -0.029467 | 0.026811 | -0.12922 | -0.10312 | 121.5113 | 121.169 | 121.1965 | 61.0762 | -121.557 | 121.3345 | 121.4116 | 121.4377 | 61.1072 | -121.5971
114.1094 | 121.8796 | -61.0428 | 60.4843 | 1.4211e-13 | -0.011192 | -0.00073712 | 0.064812 | -0.0026366 | 0.060529 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0058226 | 0.064196 | -58.4879 | -0.026065 | -61.0598 | 60.409 | 60.0758 | 60.0942 | -61.1184 | -61.0286 | 0.000359 | -61.1318 | 60.2368 | 60.3093 | 60.3308 | -61.1586 | -0.075651 | -0.075299 | 2.5549 | -0.016994 | 0.058657 | -0.40846 | -0.39013 | -0.11579 | -0.24754 | 0.01421 | -0.088976 | 0.026811 | -0.17499 | -0.15348 | 121.4518 | 121.1186 | 121.137 | 61.0167 | -121.6028 | 121.2796 | 121.3521 | 121.3736 | 61.0431 | -121.6429
115.7812 | 121.8796 | -61.1114 | 60.3882 | 1.4211e-13 | -0.011833 | -0.00073712 | 0.064599 | -0.0028504 | 0.060742 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064699 | 0.0056088 | 0.064196 | -58.4329 | -0.026065 | -61.0598 | 60.4136 | 60.0713 | 60.0942 | -61.1184 | -61.0286 | -0.00422 | -61.1318 | 60.2276 | 60.3139 | 60.3263 | -61.1586 | -0.006987 | 0.025409 | 2.6785 | 0.05167 | 0.058657 | -0.31691 | -0.294 | -0.047123 | -0.16056 | 0.082874 | -0.020312 | 0.026811 | -0.074282 | -0.061924 | 121.525 | 121.1827 | 121.2056 | 61.0854 | -121.5066 | 121.3391 | 121.4254 | 121.4377 | 61.1072 | -121.5468
117.4688 | 121.7926 | -61.1206 | 60.4294 | 1.4211e-13 | -0.01162 | -0.00052352 | 0.064385 | -0.0028504 | 0.060315 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064913 | 0.0056088 | 0.063983 | -58.3871 | -0.030644 | -61.0552 | 60.4136 | 60.0758 | 60.0942 | -61.1184 | -61.0286 | 0.004938 | -61.1272 | 60.2368 | 60.3047 | 60.3354 | -61.154 | 0.002168 | -0.015789 | 2.7335 | 0.065403 | 0.063235 | -0.35353 | -0.33519 | -0.033389 | -0.1926 | 0.092029 | -0.006578 | 0.026811 | -0.12464 | -0.093965 | 121.5342 | 121.1965 | 121.2148 | 61.09 | -121.5478 | 121.3574 | 121.4253 | 121.456 | 61.1255 | -121.5834
119.1406 | 121.788 | -61.1298 | 60.4706 | 1.4211e-13 | -0.011406 | -0.00073712 | 0.064599 | -0.0026366 | 0.060529 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.064913 | 0.0056088 | 0.064196 | -58.3917 | -0.021486 | -61.0598 | 60.4136 | 60.0713 | 60.0942 | -61.123 | -61.0286 | 0.000359 | -61.1318 | 60.2368 | 60.3139 | 60.3263 | -61.154 | 0.006745 | -0.056988 | 2.7381 | 0.069981 | 0.063236 | -0.39931 | -0.37639 | -0.024233 | -0.2338 | 0.10119 | -0.002001 | 0.022232 | -0.15668 | -0.14432 | 121.5434 | 121.201 | 121.2239 | 61.1083 | -121.5936 | 121.3665 | 121.4437 | 121.456 | 61.1301 | -121.6246
120.8281 | 121.7972 | -61.0977 | 60.4752 | 1.4211e-13 | -0.011192 | -0.00052352 | 0.064385 | -0.0026366 | 0.060742 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.064485 | 0.0058226 | 0.064196 | -58.4009 | -0.021486 | -61.0598 | 60.4136 | 60.0758 | 60.0942 | -61.1184 | -61.0286 | 0.000359 | -61.1363 | 60.2368 | 60.3185 | 60.3354 | -61.1586 | -0.02072 | -0.061566 | 2.6968 | 0.037937 | 0.058657 | -0.39931 | -0.38097 | -0.060856 | -0.23838 | 0.069141 | -0.038624 | 0.022232 | -0.15668 | -0.13974 | 121.5113 | 121.1736 | 121.1919 | 61.0762 | -121.5936 | 121.3345 | 121.4162 | 121.4331 | 61.0981 | -121.6337
122.5 | 121.907 | -61.0565 | 60.4752 | 1.4211e-13 | -0.011406 | -0.00030992 | 0.064385 | -0.0026366 | 0.060315 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0058226 | 0.064196 | -58.5107 | -0.026065 | -61.0598 | 60.4136 | 60.0667 | 60.0896 | -61.1139 | -61.0332 | 0.000359 | -61.1318 | 60.2322 | 60.3139 | 60.3308 | -61.1586 | -0.057339 | -0.061566 | 2.5458 | -0.003261 | 0.054078 | -0.40847 | -0.38555 | -0.10205 | -0.24296 | 0.023364 | -0.075243 | 0.026811 | -0.16126 | -0.14432 | 121.4701 | 121.1232 | 121.1461 | 61.0305 | -121.589 | 121.2887 | 121.3704 | 121.3874 | 61.0569 | -121.6337
124.1875 | 121.7606 | -61.1618 | 60.4477 | 1.4211e-13 | -0.011192 | -0.00052352 | 0.064385 | -0.0028504 | 0.060315 | -0.0022889 | 0.00055974 | -0.00026913 | 0.064699 | 0.0058226 | 0.063983 | -58.3871 | -0.030644 | -61.0552 | 60.409 | 60.0758 | 60.0942 | -61.1184 | -61.024 | 0.000359 | -61.1318 | 60.2322 | 60.3093 | 60.3263 | -61.154 | 0.043367 | -0.038678 | 2.7747 | 0.1066 | 0.063235 | -0.37184 | -0.35351 | 0.00781 | -0.21549 | 0.13781 | 0.030042 | 0.022232 | -0.13837 | -0.12143 | 121.5708 | 121.2377 | 121.256 | 61.1312 | -121.5661 | 121.394 | 121.4711 | 121.4881 | 61.1622 | -121.6017
125.8438 | 121.7743 | -61.0886 | 60.5164 | 1.4211e-13 | -0.011406 | -0.00030992 | 0.064599 | -0.0026366 | 0.060529 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0060362 | 0.064196 | -58.4146 | -0.021486 | -61.0644 | 60.409 | 60.0713 | 60.0896 | -61.1139 | -61.0286 | 0.000359 | -61.1318 | 60.2322 | 60.3185 | 60.3308 | -61.1586 | -0.025296 | -0.10734 | 2.674 | 0.024203 | 0.049499 | -0.44509 | -0.42675 | -0.070011 | -0.28416 | 0.059986 | -0.0432 | 0.026811 | -0.19788 | -0.18552 | 121.4976 | 121.1598 | 121.1782 | 61.0671 | -121.6302 | 121.3208 | 121.407 | 121.4194 | 61.0889 | -121.6749
127.5312 | 121.8704 | -61.1252 | 60.4202 | 1.4211e-13 | -0.011833 | -0.00052352 | 0.064599 | -0.0026366 | 0.060529 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0056088 | 0.063983 | -58.4283 | -0.026065 | -61.0598 | 60.4136 | 60.0621 | 60.0896 | -61.1184 | -61.0286 | 0.000359 | -61.1318 | 60.2322 | 60.3185 | 60.3308 | -61.154 | 0.006746 | -0.006634 | 2.6968 | 0.065403 | 0.058657 | -0.35811 | -0.33062 | -0.028811 | -0.18803 | 0.096607 | -0.006579 | 0.022232 | -0.10175 | -0.089388 | 121.5388 | 121.1873 | 121.2148 | 61.0991 | -121.5387 | 121.3574 | 121.4437 | 121.456 | 61.1255 | -121.5742
129.2812 | 121.7606 | -61.1343 | 60.4706 | 1.4211e-13 | -0.011406 | -0.00073712 | 0.064599 | -0.003064 | 0.060529 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064699 | 0.0056088 | 0.063769 | -58.3871 | -0.026065 | -61.0552 | 60.4136 | 60.0713 | 60.0942 | -61.1093 | -61.024 | -0.00422 | -61.1409 | 60.2322 | 60.3139 | 60.34 | -61.1586 | 0.025059 | -0.056988 | 2.7472 | 0.079136 | 0.054077 | -0.39931 | -0.37639 | -0.024235 | -0.23838 | 0.11034 | -0.006581 | 0.017654 | -0.15668 | -0.13059 | 121.5479 | 121.2056 | 121.2285 | 61.1083 | -121.5799 | 121.3665 | 121.4482 | 121.4743 | 61.1301 | -121.6292
130.9531 | 121.8155 | -61.1206 | 60.4294 | 1.4211e-13 | -0.01162 | -0.00073712 | 0.064385 | -0.0028504 | 0.060529 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064699 | 0.0056088 | 0.063555 | -58.4009 | -0.021486 | -61.0598 | 60.4044 | 60.0667 | 60.0896 | -61.1139 | -61.0286 | -0.008798 | -61.1272 | 60.2276 | 60.3047 | 60.3217 | -61.1494 | 0.006747 | -0.024946 | 2.7197 | 0.060825 | 0.054078 | -0.36269 | -0.33977 | -0.02881 | -0.20176 | 0.092029 | -0.006578 | 0.022232 | -0.12464 | -0.1077 | 121.525 | 121.1873 | 121.2102 | 61.0991 | -121.5432 | 121.3482 | 121.4253 | 121.4423 | 61.1118 | -121.5788
132.6406 | 121.8796 | -61.0794 | 60.4614 | 1.4211e-13 | -0.012047 | -0.00073712 | 0.064385 | -0.0028504 | 0.060529 | 0.0053411 | 0.00013254 | 0.00037167 | 0.064485 | 0.0058226 | 0.063769 | -58.4879 | -0.021486 | -61.0598 | 60.409 | 60.0758 | 60.0988 | -61.1184 | -61.0286 | 0.004938 | -61.1318 | 60.2322 | 60.3047 | 60.3263 | -61.154 | -0.03903 | -0.052411 | 2.5916 | 0.019627 | 0.058657 | -0.38558 | -0.36266 | -0.074587 | -0.22923 | 0.050831 | -0.052355 | 0.022232 | -0.15668 | -0.13517 | 121.4884 | 121.1553 | 121.1782 | 61.0579 | -121.5799 | 121.3116 | 121.3842 | 121.4057 | 61.0843 | -121.6154
134.3125 | 121.7972 | -61.1069 | 60.4156 | 1.4211e-13 | -0.01162 | -0.00073712 | 0.064599 | -0.0028504 | 0.060529 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0060362 | 0.064196 | -58.3963 | -0.026065 | -61.0598 | 60.409 | 60.0667 | 60.0896 | -61.1139 | -61.0286 | 0.000359 | -61.1318 | 60.2276 | 60.3047 | 60.3308 | -61.1586 | -0.006985 | -0.006634 | 2.7106 | 0.047093 | 0.054078 | -0.34896 | -0.32604 | -0.0517 | -0.18803 | 0.078297 | -0.024889 | 0.026811 | -0.11091 | -0.08481 | 121.5159 | 121.1736 | 121.1965 | 61.0808 | -121.5295 | 121.3345 | 121.4116 | 121.4377 | 61.1072 | -121.5742
135.9844 | 121.7514 | -61.1298 | 60.466 | 1.4211e-13 | -0.01162 | -0.00030992 | 0.064599 | -0.003064 | 0.060529 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0060362 | 0.063769 | -58.3871 | -0.021486 | -61.0552 | 60.4136 | 60.0758 | 60.0942 | -61.1184 | -61.024 | 0.000359 | -61.1318 | 60.2276 | 60.3185 | 60.3308 | -61.1586 | 0.011324 | -0.05241 | 2.7426 | 0.074559 | 0.063235 | -0.39015 | -0.37182 | -0.028812 | -0.23838 | 0.10576 | -0.002001 | 0.026811 | -0.14752 | -0.13516 | 121.5434 | 121.2056 | 121.2239 | 61.1083 | -121.5844 | 121.3574 | 121.4482 | 121.4606 | 61.1301 | -121.6246
137.6719 | 121.8246 | -61.0794 | 60.4431 | 1.4211e-13 | -0.012047 | -0.00073712 | 0.064812 | -0.0028504 | 0.060529 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064699 | 0.0056088 | 0.063769 | -58.4695 | -0.026065 | -61.0552 | 60.4136 | 60.0621 | 60.0942 | -61.1093 | -61.0286 | -0.00422 | -61.1318 | 60.2322 | 60.3093 | 60.3354 | -61.1494 | -0.029872 | -0.029522 | 2.6099 | 0.024205 | 0.054077 | -0.381 | -0.34893 | -0.070008 | -0.21092 | 0.050831 | -0.052355 | 0.017653 | -0.13379 | -0.1077 | 121.493 | 121.1415 | 121.1736 | 61.0533 | -121.5524 | 121.3116 | 121.3887 | 121.4148 | 61.0752 | -121.5925
139.3438 | 121.7468 | -61.1618 | 60.4385 | 1.4211e-13 | -0.012047 | -0.00052352 | 0.064599 | -0.0032776 | 0.060742 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0058226 | 0.063983 | -58.378 | -0.021486 | -61.0552 | 60.4136 | 60.0667 | 60.0896 | -61.1047 | -61.0286 | 0.004938 | -61.1226 | 60.2276 | 60.3093 | 60.3308 | -61.154 | 0.057104 | -0.024945 | 2.7838 | 0.1066 | 0.049498 | -0.37185 | -0.34893 | 0.00781 | -0.21092 | 0.13323 | 0.0392 | 0.03139 | -0.12922 | -0.1077 | 121.5754 | 121.2285 | 121.2514 | 61.1403 | -121.5432 | 121.3894 | 121.4711 | 121.4926 | 61.1667 | -121.5925
141.0156 | 121.7514 | -61.171 | 60.4523 | 1.4211e-13 | -0.011833 | -0.00052352 | 0.064599 | -0.0028504 | 0.060742 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0058226 | 0.063983 | -58.3826 | -0.026065 | -61.0598 | 60.4136 | 60.0713 | 60.0896 | -61.1093 | -61.0332 | 0.000359 | -61.1363 | 60.2322 | 60.3047 | 60.3263 | -61.1586 | 0.06168 | -0.038678 | 2.7884 | 0.11118 | 0.049499 | -0.381 | -0.36266 | 0.012386 | -0.22007 | 0.1378 | 0.034618 | 0.022232 | -0.14753 | -0.12601 | 121.5846 | 121.2422 | 121.2606 | 61.1449 | -121.5616 | 121.4032 | 121.4757 | 121.4972 | 61.1713 | -121.6108
142.6875 | 121.7606 | -61.1389 | 60.4111 | 1.4211e-13 | -0.012047 | -0.00030992 | 0.064385 | -0.0028504 | 0.060529 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0058226 | 0.064196 | -58.3963 | -0.016908 | -61.0552 | 60.4182 | 60.0713 | 60.0942 | -61.1093 | -61.0286 | 0.004938 | -61.1318 | 60.2276 | 60.3093 | 60.3446 | -61.1632 | 0.029637 | 0.0071 | 2.7426 | 0.083714 | 0.054077 | -0.3398 | -0.31688 | -0.024235 | -0.18345 | 0.11034 | 0.007154 | 0.031389 | -0.10175 | -0.066497 | 121.5571 | 121.2102 | 121.2331 | 61.122 | -121.5204 | 121.3665 | 121.4482 | 121.4835 | 61.1439 | -121.5742
144.375 | 121.8979 | -61.1023 | 60.3836 | 1.4211e-13 | -0.011406 | -0.00052352 | 0.064599 | -0.003064 | 0.060529 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064699 | 0.0060362 | 0.063983 | -58.4146 | -0.016908 | -61.0552 | 60.4136 | 60.0713 | 60.0942 | -61.1184 | -61.024 | 0.004938 | -61.1226 | 60.223 | 60.3047 | 60.3263 | -61.1586 | -0.016142 | 0.029987 | 2.6877 | 0.047093 | 0.063235 | -0.31234 | -0.28942 | -0.056278 | -0.16056 | 0.078298 | -0.020309 | 0.035969 | -0.078862 | -0.057346 | 121.5159 | 121.1736 | 121.1965 | 61.0854 | -121.502 | 121.3253 | 121.407 | 121.4286 | 61.1072 | -121.5422
146.0781 | 121.756 | -61.0931 | 60.5484 | 1.4211e-13 | -0.011833 | -0.00073712 | 0.064812 | -0.003064 | 0.060101 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064699 | 0.0060362 | 0.063983 | -58.4238 | -0.026065 | -61.0552 | 60.409 | 60.0713 | 60.0942 | -61.1139 | -61.0332 | -0.00422 | -61.1272 | 60.2276 | 60.3093 | 60.3308 | -61.154 | -0.020718 | -0.13939 | 2.6694 | 0.037938 | 0.058656 | -0.47713 | -0.45421 | -0.060854 | -0.32078 | 0.059985 | -0.034043 | 0.026811 | -0.23908 | -0.21756 | 121.5022 | 121.1644 | 121.1873 | 61.0671 | -121.6623 | 121.3208 | 121.4025 | 121.424 | 61.0889 | -121.7024
147.75 | 121.7697 | -61.0886 | 60.5026 | 1.4211e-13 | -0.011833 | -0.00052352 | 0.064599 | -0.003064 | 0.060529 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.064699 | 0.0060362 | 0.063983 | -58.4421 | -0.021486 | -61.0552 | 60.409 | 60.0667 | 60.0896 | -61.1093 | -61.0286 | 0.000359 | -61.1272 | 60.2276 | 60.3002 | 60.3217 | -61.154 | -0.020717 | -0.09361 | 2.6465 | 0.03336 | 0.054077 | -0.43593 | -0.41302 | -0.065432 | -0.275 | 0.059986 | -0.038621 | 0.026811 | -0.20246 | -0.18094 | 121.4976 | 121.1553 | 121.1782 | 61.0671 | -121.6119 | 121.3162 | 121.3887 | 121.4102 | 61.0889 | -121.6566
149.4219 | 121.8613 | -61.0519 | 60.4431 | 1.4211e-13 | -0.011833 | -0.00073712 | 0.064171 | -0.003064 | 0.060742 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064699 | 0.0058226 | 0.064196 | -58.4879 | -0.026065 | -61.0552 | 60.4044 | 60.0621 | 60.085 | -61.1093 | -61.0286 | -0.00422 | -61.1272 | 60.2276 | 60.3047 | 60.3217 | -61.1494 | -0.057338 | -0.038679 | 2.5641 | -0.003261 | 0.054077 | -0.381 | -0.35808 | -0.097474 | -0.21549 | 0.023365 | -0.075242 | 0.022232 | -0.13837 | -0.12143 | 121.4564 | 121.1141 | 121.137 | 61.0259 | -121.5524 | 121.2796 | 121.3567 | 121.3736 | 61.0477 | -121.5925
151.0938 | 121.8887 | -61.0519 | 60.4477 | 1.4211e-13 | -0.012047 | -0.00052352 | 0.064385 | -0.0028504 | 0.060315 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0060362 | 0.063983 | -58.4924 | -0.021486 | -61.0552 | 60.4136 | 60.0667 | 60.0896 | -61.1047 | -61.024 | 0.004938 | -61.1272 | 60.2368 | 60.3002 | 60.3354 | -61.1494 | -0.052759 | -0.0341 | 2.5595 | -0.003261 | 0.049498 | -0.381 | -0.35808 | -0.097474 | -0.21091 | 0.027944 | -0.075242 | 0.022232 | -0.14753 | -0.11228 | 121.4655 | 121.1186 | 121.1415 | 61.0305 | -121.5524 | 121.2887 | 121.3521 | 121.3874 | 61.0569 | -121.5971
152.7969 | 121.8109 | -61.0931 | 60.4111 | 1.4211e-13 | -0.012047 | -0.00073712 | 0.064812 | -0.003064 | 0.060529 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064699 | 0.0062498 | 0.063983 | -58.4467 | -0.016908 | -61.0506 | 60.4044 | 60.0621 | 60.085 | -61.1139 | -61.0194 | -0.00422 | -61.1226 | 60.223 | 60.3047 | 60.3308 | -61.154 | -0.020718 | -0.006636 | 2.6465 | 0.042516 | 0.063234 | -0.34896 | -0.32604 | -0.060854 | -0.18803 | 0.073721 | -0.029464 | 0.03139 | -0.10633 | -0.080233 | 121.4976 | 121.1553 | 121.1782 | 61.0762 | -121.5249 | 121.3162 | 121.3979 | 121.424 | 61.0889 | -121.5651
154.4688 | 121.8796 | -61.0977 | 60.3607 | 1.4211e-13 | -0.012047 | -0.00030992 | 0.064171 | -0.003064 | 0.060529 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064699 | 0.0056088 | 0.063983 | -58.4146 | -0.021486 | -61.0506 | 60.4044 | 60.0575 | 60.0896 | -61.1139 | -61.0194 | 0.000359 | -61.1226 | 60.2276 | 60.3047 | 60.3263 | -61.1586 | -0.016141 | 0.043718 | 2.6831 | 0.047093 | 0.063234 | -0.30318 | -0.27111 | -0.060856 | -0.1331 | 0.078298 | -0.024887 | 0.035969 | -0.055974 | -0.034458 | 121.5022 | 121.1552 | 121.1873 | 61.0762 | -121.4746 | 121.3253 | 121.4025 | 121.424 | 61.0981 | -121.5193
156.1719 | 121.7834 | -61.1069 | 60.498 | 1.4211e-13 | -0.012261 | -0.00052352 | 0.064599 | -0.003064 | 0.060529 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064699 | 0.0058226 | 0.063555 | -58.3963 | -0.021486 | -61.0506 | 60.409 | 60.0667 | 60.085 | -61.1093 | -61.0194 | 0.004938 | -61.1272 | 60.2276 | 60.3002 | 60.3308 | -61.154 | -0.002406 | -0.089032 | 2.7106 | 0.056249 | 0.058655 | -0.43136 | -0.41302 | -0.047121 | -0.27043 | 0.087454 | -0.02031 | 0.026811 | -0.19788 | -0.16721 | 121.5159 | 121.1736 | 121.1919 | 61.0854 | -121.6073 | 121.3345 | 121.407 | 121.4377 | 61.1118 | -121.652
157.8438 | 121.7468 | -61.0703 | 60.498 | 1.4211e-13 | -0.012261 | -0.00073712 | 0.064599 | -0.003064 | 0.060315 | -0.0022889 | -0.00029486 | 0.00015807 | 0.065126 | 0.0060362 | 0.063983 | -58.4192 | -0.016908 | -61.0598 | 60.4136 | 60.0667 | 60.0805 | -61.1047 | -61.024 | 0.004938 | -61.1272 | 60.2322 | 60.3047 | 60.3308 | -61.1586 | -0.034449 | -0.084454 | 2.6511 | 0.010471 | 0.04492 | -0.43136 | -0.41759 | -0.088322 | -0.26585 | 0.046254 | -0.056932 | 0.03139 | -0.1933 | -0.16721 | 121.4838 | 121.1369 | 121.1507 | 61.0533 | -121.6027 | 121.3024 | 121.375 | 121.4011 | 61.0752 | -121.6566
159.5156 | 121.7422 | -61.1526 | 60.4523 | 1.4211e-13 | -0.01162 | -0.00052352 | 0.064171 | -0.0028504 | 0.060101 | -0.0099194 | 0.00013254 | 0.00037167 | 0.064485 | 0.0058226 | 0.063555 | -58.378 | -0.016908 | -61.046 | 60.4044 | 60.0621 | 60.0942 | -61.1093 | -61.0148 | 0.004938 | -61.1226 | 60.2276 | 60.3002 | 60.3263 | -61.154 | 0.04337 | -0.047835 | 2.7747 | 0.1066 | 0.063233 | -0.39016 | -0.35808 | -0.001345 | -0.22465 | 0.13781 | 0.030045 | 0.03139 | -0.15211 | -0.12601 | 121.5571 | 121.2148 | 121.2468 | 61.1357 | -121.5616 | 121.3803 | 121.4528 | 121.4789 | 61.1576 | -121.6063
161.1875 | 121.7651 | -61.116 | 60.4614 | 1.4211e-13 | -0.012261 | -0.00073712 | 0.064385 | -0.0032776 | 0.060315 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064485 | 0.0060362 | 0.063555 | -58.378 | -0.012329 | -61.0506 | 60.4044 | 60.0621 | 60.0896 | -61.1139 | -61.0194 | 0.004938 | -61.1272 | 60.223 | 60.3047 | 60.3263 | -61.1586 | 0.00217 | -0.05699 | 2.7381 | 0.065404 | 0.063234 | -0.39931 | -0.37182 | -0.042545 | -0.23838 | 0.096609 | -0.011155 | 0.03139 | -0.15668 | -0.13517 | 121.5205 | 121.1781 | 121.2056 | 61.1037 | -121.5753 | 121.3391 | 121.4208 | 121.4423 | 61.121 | -121.62
162.8594 | 121.7377 | -61.0886 | 60.5164 | 1.4211e-13 | -0.012474 | -0.00052352 | 0.063957 | -0.003064 | 0.060529 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064699 | 0.0060362 | 0.063769 | -58.4192 | -0.016908 | -61.0506 | 60.4044 | 60.0621 | 60.085 | -61.1047 | -61.024 | 0.004938 | -61.1226 | 60.223 | 60.2956 | 60.3308 | -61.154 | -0.016138 | -0.11192 | 2.6694 | 0.037938 | 0.054076 | -0.45425 | -0.43133 | -0.065432 | -0.29331 | 0.064565 | -0.034042 | 0.03139 | -0.22077 | -0.18552 | 121.493 | 121.1507 | 121.1736 | 61.0717 | -121.6211 | 121.3116 | 121.3841 | 121.4194 | 61.0935 | -121.6704
164.5312 | 121.8338 | -61.0703 | 60.4889 | 1.4211e-13 | -0.012261 | -0.00073712 | 0.064385 | -0.0032776 | 0.060101 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064485 | 0.0058226 | 0.063769 | -58.4695 | -0.021486 | -61.046 | 60.4136 | 60.0667 | 60.085 | -61.1139 | -61.0148 | 0.000359 | -61.1226 | 60.2276 | 60.3047 | 60.3308 | -61.1494 | -0.043607 | -0.075299 | 2.6007 | 0.024205 | 0.067812 | -0.4222 | -0.40386 | -0.079164 | -0.26127 | 0.055411 | -0.052353 | 0.026811 | -0.18415 | -0.15805 | 121.4838 | 121.1369 | 121.1553 | 61.0488 | -121.6028 | 121.2979 | 121.375 | 121.4011 | 61.0706 | -121.6383
166.2344 | 121.8704 | -61.0977 | 60.3836 | 1.4211e-13 | -0.012261 | -0.00030992 | 0.064385 | -0.0032776 | 0.060101 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064485 | 0.0058226 | 0.063769 | -58.4054 | -0.016908 | -61.046 | 60.4044 | 60.0621 | 60.0896 | -61.1047 | -61.0194 | 0.000359 | -61.1226 | 60.2276 | 60.291 | 60.3217 | -61.154 | -0.006983 | 0.02083 | 2.6923 | 0.051671 | 0.058654 | -0.32149 | -0.294 | -0.056277 | -0.15599 | 0.078298 | -0.024887 | 0.03139 | -0.092597 | -0.061924 | 121.5022 | 121.1598 | 121.1873 | 61.0808 | -121.4883 | 121.3253 | 121.3887 | 121.4194 | 61.0981 | -121.5376
167.9688 | 121.8201 | -61.0931 | 60.4385 | 1.4211e-13 | -0.012261 | -0.00095092 | 0.064171 | -0.0028504 | 0.060742 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0060362 | 0.064196 | -58.4512 | -0.016908 | -61.0415 | 60.4044 | 60.0667 | 60.085 | -61.1093 | -61.024 | 0.000359 | -61.1226 | 60.2276 | 60.3047 | 60.3217 | -61.1586 | -0.016139 | -0.034102 | 2.6419 | 0.051673 | 0.067812 | -0.37185 | -0.35351 | -0.065433 | -0.21092 | 0.069143 | -0.029464 | 0.035969 | -0.13379 | -0.11686 | 121.4976 | 121.1598 | 121.1782 | 61.0762 | -121.5478 | 121.3208 | 121.3979 | 121.4148 | 61.0935 | -121.5971
169.6562 | 121.843 | -61.084 | 60.4477 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.064171 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0060362 | 0.063769 | -58.4741 | -0.016908 | -61.0506 | 60.4044 | 60.0621 | 60.085 | -61.1093 | -61.0103 | 0.000359 | -61.1134 | 60.2322 | 60.3002 | 60.3217 | -61.1586 | -0.025295 | -0.043257 | 2.6099 | 0.03336 | 0.058655 | -0.38558 | -0.36266 | -0.074589 | -0.21549 | 0.073723 | -0.029463 | 0.045126 | -0.14753 | -0.12601 | 121.4884 | 121.1461 | 121.169 | 61.0671 | -121.557 | 121.3162 | 121.3842 | 121.4057 | 61.0843 | -121.6063
171.3281 | 121.8155 | -61.0336 | 60.5026 | 1.4211e-13 | -0.012047 | -0.00073712 | 0.064171 | -0.0032776 | 0.060742 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.065126 | 0.0053952 | 0.063983 | -58.4558 | -0.026065 | -61.0552 | 60.409 | 60.0575 | 60.0759 | -61.1093 | -61.0148 | 0.000359 | -61.1226 | 60.2322 | 60.3002 | 60.3263 | -61.154 | -0.075649 | -0.09361 | 2.5778 | -0.021572 | 0.054077 | -0.44509 | -0.42675 | -0.12036 | -0.27043 | 0.01879 | -0.088974 | 0.03139 | -0.20246 | -0.17637 | 121.4426 | 121.0912 | 121.1095 | 61.0076 | -121.6119 | 121.2658 | 121.3338 | 121.3599 | 61.034 | -121.6566
173 | 121.8704 | -61.0474 | 60.4431 | 1.4211e-13 | -0.012261 | -0.00052352 | 0.064599 | -0.0028504 | 0.060315 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0060362 | 0.063769 | -58.4879 | -0.021486 | -61.0506 | 60.3999 | 60.0575 | 60.085 | -61.1139 | -61.0103 | 0.004938 | -61.1226 | 60.223 | 60.3047 | 60.3263 | -61.1586 | -0.066495 | -0.043257 | 2.5595 | -0.003261 | 0.063234 | -0.38558 | -0.35808 | -0.11121 | -0.22007 | 0.037102 | -0.075241 | 0.035969 | -0.13837 | -0.11686 | 121.4472 | 121.1049 | 121.1324 | 61.0259 | -121.557 | 121.2704 | 121.3521 | 121.3736 | 61.0523 | -121.6017
174.6719 | 121.8842 | -61.0336 | 60.4431 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.063957 | -0.003064 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064699 | 0.0062498 | 0.063769 | -58.4879 | -0.016908 | -61.0369 | 60.3999 | 60.053 | 60.0896 | -61.1047 | -61.0148 | 0.009516 | -61.1226 | 60.2185 | 60.3047 | 60.3171 | -61.1586 | -0.07107 | -0.043257 | 2.5458 | -0.003259 | 0.067811 | -0.39016 | -0.35351 | -0.12494 | -0.22465 | 0.01879 | -0.088974 | 0.035969 | -0.13837 | -0.12601 | 121.4335 | 121.0866 | 121.1232 | 61.0167 | -121.5478 | 121.2521 | 121.3384 | 121.3507 | 61.0431 | -121.6017
176.375 | 121.7422 | -61.084 | 60.5164 | 1.4211e-13 | -0.012474 | -0.00095092 | 0.063957 | -0.0034912 | 0.060101 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064699 | 0.0060362 | 0.063769 | -58.4329 | -0.021486 | -61.0506 | 60.3999 | 60.0575 | 60.085 | -61.1139 | -61.0103 | 0.004938 | -61.1134 | 60.2185 | 60.3047 | 60.3217 | -61.154 | -0.029874 | -0.1165 | 2.6511 | 0.03336 | 0.063234 | -0.45882 | -0.43133 | -0.07001 | -0.29789 | 0.073723 | -0.029463 | 0.040547 | -0.21161 | -0.19467 | 121.4838 | 121.1415 | 121.169 | 61.0625 | -121.6302 | 121.3024 | 121.3887 | 121.4057 | 61.0889 | -121.6704
178.1094 | 121.756 | -61.0794 | 60.4889 | 1.4211e-13 | -0.012261 | -0.00030992 | 0.06353 | -0.0032776 | 0.060315 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064913 | 0.0062498 | 0.063769 | -58.3963 | -0.026065 | -61.046 | 60.4044 | 60.053 | 60.085 | -61.1047 | -61.0148 | 0.000359 | -61.1226 | 60.2322 | 60.3047 | 60.3354 | -61.1586 | -0.025293 | -0.084456 | 2.6831 | 0.033361 | 0.058654 | -0.43594 | -0.40386 | -0.079166 | -0.25669 | 0.064567 | -0.043197 | 0.035969 | -0.18415 | -0.15348 | 121.4838 | 121.1324 | 121.1644 | 61.0533 | -121.5936 | 121.3116 | 121.3842 | 121.4148 | 61.0798 | -121.6475
179.8438 | 121.8155 | -61.0931 | 60.4431 | 1.4211e-13 | -0.012474 | -0.00052352 | 0.064171 | -0.003064 | 0.060101 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064485 | 0.0062498 | 0.063128 | -58.4558 | -0.012329 | -61.0552 | 60.4044 | 60.0621 | 60.085 | -61.1184 | -61.0103 | 0.004938 | -61.1272 | 60.2276 | 60.2956 | 60.3217 | -61.1586 | -0.025297 | -0.038679 | 2.6373 | 0.037938 | 0.063235 | -0.381 | -0.35808 | -0.065433 | -0.21549 | 0.082879 | -0.034043 | 0.03139 | -0.14753 | -0.12143 | 121.4976 | 121.1553 | 121.1782 | 61.0808 | -121.5616 | 121.3208 | 121.3887 | 121.4148 | 61.0981 | -121.6017
181.5156 | 121.7422 | -61.0657 | 60.4935 | 1.4211e-13 | -0.012261 | -0.00052352 | 0.063957 | -0.003064 | 0.060101 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064913 | 0.0064636 | 0.063555 | -58.3963 | -0.021486 | -61.0506 | 60.3999 | 60.0621 | 60.0805 | -61.1093 | -61.0103 | 0.000359 | -61.1226 | 60.223 | 60.3047 | 60.3171 | -61.1494 | -0.043605 | -0.093611 | 2.6694 | 0.01505 | 0.058655 | -0.43136 | -0.41302 | -0.083741 | -0.27043 | 0.055413 | -0.05693 | 0.026811 | -0.18872 | -0.17637 | 121.4655 | 121.1278 | 121.1461 | 61.0442 | -121.6027 | 121.2887 | 121.3704 | 121.3828 | 61.066 | -121.6429
183.1875 | 121.8246 | -61.0703 | 60.4431 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063957 | -0.003064 | 0.060529 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064699 | 0.0064636 | 0.063769 | -58.4695 | -0.021486 | -61.046 | 60.409 | 60.053 | 60.085 | -61.1047 | -61.0103 | 0.004938 | -61.118 | 60.2185 | 60.3047 | 60.3263 | -61.154 | -0.034449 | -0.0341 | 2.6007 | 0.024205 | 0.058654 | -0.39016 | -0.35808 | -0.083743 | -0.22465 | 0.05999 | -0.047775 | 0.035968 | -0.13837 | -0.11686 | 121.4793 | 121.1232 | 121.1553 | 61.0488 | -121.5478 | 121.2887 | 121.375 | 121.3965 | 61.0752 | -121.5971
184.8906 | 121.8613 | -61.0474 | 60.4523 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.064385 | -0.003064 | 0.060315 | 0.012972 | 0.00034614 | -0.00026913 | 0.064485 | 0.0062498 | 0.063769 | -58.4787 | -0.021486 | -61.0506 | 60.3999 | 60.0575 | 60.0805 | -61.1047 | -61.0148 | 0.004938 | -61.118 | 60.2185 | 60.3047 | 60.3125 | -61.1632 | -0.057337 | -0.052413 | 2.5687 | -0.003261 | 0.054076 | -0.39474 | -0.37182 | -0.11579 | -0.23381 | 0.032523 | -0.070663 | 0.045125 | -0.14753 | -0.13975 | 121.4472 | 121.1049 | 121.1278 | 61.0259 | -121.557 | 121.2658 | 121.3521 | 121.3599 | 61.0523 | -121.6154
186.5781 | 121.875 | -61.0611 | 60.4385 | 1.4211e-13 | -0.012261 | -0.00095092 | 0.064171 | -0.0032776 | 0.060315 | 0.0053411 | -0.00029486 | 0.00015807 | 0.064485 | 0.0062498 | 0.063769 | -58.4833 | -0.016908 | -61.0506 | 60.4044 | 60.0621 | 60.0759 | -61.1047 | -61.0194 | 0.000359 | -61.1226 | 60.2185 | 60.3047 | 60.3125 | -61.1632 | -0.043604 | -0.034102 | 2.5778 | 0.010472 | 0.054076 | -0.37643 | -0.36266 | -0.10206 | -0.22007 | 0.041677 | -0.061508 | 0.040547 | -0.13379 | -0.12601 | 121.4655 | 121.1232 | 121.137 | 61.0442 | -121.5432 | 121.2796 | 121.3658 | 121.3736 | 61.0615 | -121.6017
188.3281 | 121.8613 | -61.0474 | 60.4431 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.063957 | -0.0032776 | 0.060315 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064699 | 0.0062498 | 0.063555 | -58.4741 | -0.021486 | -61.0506 | 60.3953 | 60.053 | 60.085 | -61.1093 | -61.0103 | 0.000359 | -61.1226 | 60.2139 | 60.3002 | 60.3125 | -61.154 | -0.061916 | -0.047835 | 2.5732 | -0.003261 | 0.058655 | -0.39016 | -0.35808 | -0.10663 | -0.22923 | 0.037102 | -0.075241 | 0.03139 | -0.14295 | -0.13059 | 121.4426 | 121.1003 | 121.1324 | 61.0259 | -121.5524 | 121.2612 | 121.3475 | 121.3599 | 61.0477 | -121.5971
190.0312 | 121.8155 | -61.0977 | 60.4111 | 1.4211e-13 | -0.012474 | -0.00095092 | 0.064171 | -0.003064 | 0.060315 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0062498 | 0.063555 | -58.4283 | -0.016908 | -61.046 | 60.4044 | 60.053 | 60.0805 | -61.1093 | -61.0194 | -0.00422 | -61.1089 | 60.2185 | 60.3047 | 60.3171 | -61.154 | -0.011562 | -0.006636 | 2.6694 | 0.051671 | 0.063233 | -0.35812 | -0.33062 | -0.056277 | -0.19261 | 0.078298 | -0.011151 | 0.045126 | -0.10633 | -0.093969 | 121.5022 | 121.1507 | 121.1782 | 61.0808 | -121.5204 | 121.3162 | 121.4025 | 121.4148 | 61.0935 | -121.5651
191.7344 | 121.8201 | -61.1023 | 60.3973 | 1.4211e-13 | -0.012474 | -0.00052352 | 0.064171 | -0.0032776 | 0.060315 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064699 | 0.0062498 | 0.063555 | -58.4238 | -0.007751 | -61.0415 | 60.3999 | 60.0621 | 60.085 | -61.1001 | -61.0057 | 0.000359 | -61.1134 | 60.223 | 60.3002 | 60.3171 | -61.1586 | 0.002174 | 0.002519 | 2.6785 | 0.060828 | 0.058654 | -0.33523 | -0.31231 | -0.056278 | -0.1743 | 0.096613 | -0.011152 | 0.045126 | -0.097173 | -0.080236 | 121.5022 | 121.1644 | 121.1873 | 61.0945 | -121.4975 | 121.3253 | 121.4025 | 121.4194 | 61.1027 | -121.5559
193.4531 | 121.8613 | -61.1023 | 60.379 | 1.4211e-13 | -0.012261 | -0.00073712 | 0.063957 | -0.003064 | 0.060529 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.064699 | 0.0062498 | 0.063555 | -58.3963 | -0.016908 | -61.0506 | 60.3953 | 60.053 | 60.0896 | -61.1047 | -61.0148 | 0.000359 | -61.118 | 60.2185 | 60.3002 | 60.3171 | -61.154 | -0.002405 | 0.016252 | 2.706 | 0.051671 | 0.054076 | -0.32607 | -0.28942 | -0.051699 | -0.16056 | 0.087455 | -0.015731 | 0.035968 | -0.078862 | -0.061925 | 121.4976 | 121.1552 | 121.1919 | 61.0854 | -121.4837 | 121.3208 | 121.4025 | 121.4194 | 61.1027 | -121.533
195.1562 | 121.7285 | -61.0428 | 60.5118 | 1.4211e-13 | -0.012474 | -0.00095092 | 0.063957 | -0.003064 | 0.060529 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.064699 | 0.0064636 | 0.063769 | -58.41 | -0.016908 | -61.046 | 60.3999 | 60.0575 | 60.0805 | -61.1093 | -61.0148 | -0.00422 | -61.118 | 60.223 | 60.2956 | 60.3217 | -61.1586 | -0.066493 | -0.11192 | 2.6328 | -0.00326 | 0.063233 | -0.45425 | -0.43133 | -0.11579 | -0.28874 | 0.027946 | -0.07524 | 0.040547 | -0.21619 | -0.1901 | 121.4426 | 121.1003 | 121.1232 | 61.0259 | -121.6211 | 121.2658 | 121.3384 | 121.3645 | 61.0386 | -121.6704
196.8438 | 121.7789 | -61.1023 | 60.4523 | 1.4211e-13 | -0.012047 | -0.00052352 | 0.064171 | -0.0034912 | 0.060101 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064485 | 0.0066772 | 0.063342 | -58.3826 | -0.021486 | -61.0506 | 60.3953 | 60.0575 | 60.0805 | -61.1093 | -61.0103 | 0.004938 | -61.1134 | 60.2185 | 60.3002 | 60.3171 | -61.1586 | -0.006984 | -0.056991 | 2.7197 | 0.051671 | 0.058655 | -0.39474 | -0.37182 | -0.056278 | -0.23381 | 0.092034 | -0.011152 | 0.045126 | -0.15211 | -0.13517 | 121.4976 | 121.1598 | 121.1827 | 61.0808 | -121.5616 | 121.3208 | 121.4025 | 121.4194 | 61.1072 | -121.6108
198.5156 | 121.8292 | -61.1069 | 60.3653 | 1.4211e-13 | -0.012261 | -0.00052352 | 0.064171 | -0.0034912 | 0.059888 | -0.0022889 | -0.00050846 | -5.5534e-05 | 0.064913 | 0.0064636 | 0.063342 | -58.3917 | -0.021486 | -61.0369 | 60.3999 | 60.0575 | 60.0896 | -61.1001 | -61.0057 | 0.000359 | -61.1134 | 60.2139 | 60.3002 | 60.3217 | -61.154 | 0.006752 | 0.034563 | 2.7152 | 0.069984 | 0.063232 | -0.30776 | -0.27569 | -0.047121 | -0.15141 | 0.10119 | -0.006574 | 0.040547 | -0.065129 | -0.043613 | 121.5067 | 121.1644 | 121.1965 | 61.0854 | -121.4654 | 121.3208 | 121.407 | 121.4286 | 61.1072 | -121.5193
200.2656 | 121.8109 | -61.0794 | 60.4156 | 1.4211e-13 | -0.012474 | -0.00095092 | 0.064171 | -0.0028504 | 0.060315 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0062498 | 0.063555 | -58.4421 | -0.021486 | -61.0415 | 60.3907 | 60.0621 | 60.0942 | -61.0955 | -61.0011 | 0.004938 | -61.1226 | 60.223 | 60.2956 | 60.3217 | -61.154 | -0.016135 | -0.024948 | 2.6373 | 0.03794 | 0.054075 | -0.35354 | -0.32146 | -0.074587 | -0.19261 | 0.078303 | -0.043197 | 0.03139 | -0.12006 | -0.093967 | 121.4701 | 121.1415 | 121.1736 | 61.0579 | -121.5112 | 121.3024 | 121.375 | 121.4011 | 61.0843 | -121.5696
201.9531 | 121.8063 | -61.0977 | 60.4248 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.063957 | -0.0032776 | 0.060315 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.064485 | 0.0062498 | 0.063555 | -58.4512 | -0.012329 | -61.0415 | 60.3999 | 60.053 | 60.0896 | -61.1047 | -61.0057 | 0.000359 | -61.118 | 60.223 | 60.3002 | 60.3125 | -61.1586 | -0.006983 | -0.024947 | 2.6465 | 0.05625 | 0.063233 | -0.37185 | -0.3352 | -0.060856 | -0.20176 | 0.092035 | -0.020309 | 0.040547 | -0.12464 | -0.11228 | 121.4976 | 121.1507 | 121.1873 | 61.0854 | -121.5295 | 121.3208 | 121.3979 | 121.4102 | 61.0981 | -121.5834
203.625 | 121.8109 | -61.1023 | 60.3973 | 1.4211e-13 | -0.012047 | -0.00052352 | 0.063957 | -0.0032776 | 0.060529 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064699 | 0.0066772 | 0.063555 | -58.4329 | -0.016908 | -61.0506 | 60.3999 | 60.053 | 60.085 | -61.1047 | -61.0057 | 0.000359 | -61.1089 | 60.2185 | 60.3002 | 60.3217 | -61.1586 | -0.002405 | 0.002519 | 2.6694 | 0.051671 | 0.054076 | -0.34439 | -0.31231 | -0.056278 | -0.17888 | 0.096613 | -0.006573 | 0.049705 | -0.097173 | -0.075657 | 121.5022 | 121.1552 | 121.1873 | 61.0854 | -121.502 | 121.3208 | 121.4025 | 121.424 | 61.1027 | -121.5559
205.375 | 121.7697 | -61.084 | 60.4477 | 1.4211e-13 | -0.012261 | -0.00095092 | 0.064171 | -0.003064 | 0.060101 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064913 | 0.0062498 | 0.063983 | -58.4283 | -0.012329 | -61.0506 | 60.3953 | 60.0575 | 60.0896 | -61.1047 | -61.0011 | 0.009516 | -61.1043 | 60.2185 | 60.3002 | 60.3217 | -61.1632 | -0.020716 | -0.052413 | 2.6556 | 0.03336 | 0.054076 | -0.39016 | -0.35808 | -0.079167 | -0.22923 | 0.08288 | -0.020306 | 0.058861 | -0.14753 | -0.12601 | 121.4793 | 121.1415 | 121.1736 | 61.0717 | -121.5524 | 121.3024 | 121.3842 | 121.4057 | 61.0935 | -121.6108
207.0625 | 121.8521 | -61.1069 | 60.3928 | 1.4211e-13 | -0.012261 | -0.00095092 | 0.064385 | -0.0032776 | 0.060315 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.065126 | 0.0060362 | 0.063555 | -58.465 | -0.016908 | -61.046 | 60.3953 | 60.0575 | 60.085 | -61.1001 | -61.0148 | -0.00422 | -61.1134 | 60.223 | 60.3047 | 60.3125 | -61.1632 | 0.006752 | 0.002519 | 2.6419 | 0.060827 | 0.054075 | -0.33523 | -0.30773 | -0.056278 | -0.16972 | 0.092033 | -0.006574 | 0.049704 | -0.088017 | -0.080237 | 121.5022 | 121.1644 | 121.1919 | 61.09 | -121.4929 | 121.3299 | 121.4116 | 121.4194 | 61.1027 | -121.5559
208.7344 | 121.8246 | -61.0886 | 60.3836 | 1.4211e-13 | -0.012688 | -0.00052352 | 0.064171 | -0.003064 | 0.060101 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064485 | 0.0064636 | 0.063769 | -58.4695 | -0.012329 | -61.046 | 60.3907 | 60.053 | 60.085 | -61.1047 | -61.0057 | 0.004938 | -61.1043 | 60.2185 | 60.3047 | 60.3171 | -61.1494 | -0.016138 | 0.007095 | 2.619 | 0.042516 | 0.058654 | -0.33065 | -0.29858 | -0.060853 | -0.16514 | 0.08288 | -0.015728 | 0.045125 | -0.078862 | -0.066503 | 121.4793 | 121.1415 | 121.1736 | 61.0762 | -121.4883 | 121.307 | 121.3933 | 121.4057 | 61.0935 | -121.533
210.4219 | 121.8567 | -61.0291 | 60.4614 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063744 | -0.0032776 | 0.060315 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.064485 | 0.0066772 | 0.063555 | -58.5336 | -0.021486 | -61.0415 | 60.3953 | 60.053 | 60.085 | -61.1047 | -61.0057 | -0.00422 | -61.1134 | 60.223 | 60.3002 | 60.3125 | -61.154 | -0.075647 | -0.066146 | 2.4954 | -0.012414 | 0.063233 | -0.40847 | -0.3764 | -0.12494 | -0.23838 | 0.023371 | -0.084394 | 0.040547 | -0.16126 | -0.1489 | 121.4243 | 121.082 | 121.1141 | 61.0076 | -121.5661 | 121.2521 | 121.3292 | 121.3416 | 61.0248 | -121.6154
212.1094 | 121.8018 | -61.0703 | 60.4202 | 1.4211e-13 | -0.012902 | -0.00030992 | 0.063957 | -0.0032776 | 0.060529 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064913 | 0.0062498 | 0.063769 | -58.5062 | -0.016908 | -61.046 | 60.3907 | 60.0484 | 60.0942 | -61.1047 | -61.0057 | 0.000359 | -61.1043 | 60.2185 | 60.2956 | 60.3171 | -61.1586 | -0.034449 | -0.029526 | 2.5641 | 0.024205 | 0.058654 | -0.37185 | -0.32604 | -0.088322 | -0.20176 | 0.064569 | -0.034039 | 0.054283 | -0.12464 | -0.10312 | 121.461 | 121.1186 | 121.1644 | 61.0533 | -121.5249 | 121.2887 | 121.3658 | 121.3874 | 61.0706 | -121.5788
213.9062 | 121.7651 | -61.0886 | 60.4523 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063744 | -0.0034912 | 0.060315 | -0.0099194 | 0.00013254 | 0.00015807 | 0.064699 | 0.0064636 | 0.063769 | -58.41 | -0.016908 | -61.046 | 60.3953 | 60.0575 | 60.0896 | -61.1001 | -61.0103 | 0.000359 | -61.118 | 60.2185 | 60.3002 | 60.3217 | -61.1586 | -0.011559 | -0.056991 | 2.6785 | 0.042516 | 0.054075 | -0.39474 | -0.36266 | -0.070011 | -0.23381 | 0.078301 | -0.029464 | 0.040547 | -0.15211 | -0.13059 | 121.4838 | 121.1461 | 121.1782 | 61.0717 | -121.5524 | 121.307 | 121.3887 | 121.4102 | 61.0889 | -121.6108
215.5938 | 121.7651 | -61.084 | 60.4568 | 1.4211e-13 | -0.012688 | -0.00030992 | 0.064171 | -0.003064 | 0.060101 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064699 | 0.0064636 | 0.063769 | -58.4283 | -0.021486 | -61.0506 | 60.3953 | 60.0575 | 60.085 | -61.0955 | -61.0057 | 0.000359 | -61.1089 | 60.2139 | 60.3002 | 60.3263 | -61.1586 | -0.011558 | -0.061568 | 2.6556 | 0.03336 | 0.044918 | -0.39932 | -0.37182 | -0.074589 | -0.24296 | 0.078302 | -0.024884 | 0.049705 | -0.15668 | -0.13059 | 121.4793 | 121.1415 | 121.169 | 61.0625 | -121.5524 | 121.2979 | 121.3842 | 121.4102 | 61.0843 | -121.6154
217.3438 | 121.788 | -61.1069 | 60.4111 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063957 | -0.0032776 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0062498 | 0.063555 | -58.4833 | -0.021486 | -61.0415 | 60.3907 | 60.053 | 60.085 | -61.1047 | -61.0057 | 0.000359 | -61.1043 | 60.223 | 60.3002 | 60.3171 | -61.154 | 0.002173 | -0.020371 | 2.6236 | 0.065406 | 0.063233 | -0.35812 | -0.32604 | -0.047121 | -0.18803 | 0.10119 | 0.002583 | 0.049704 | -0.11091 | -0.093969 | 121.4976 | 121.1598 | 121.1919 | 61.0854 | -121.5158 | 121.3299 | 121.407 | 121.424 | 61.1072 | -121.5651
219.0469 | 121.7056 | -61.0565 | 60.5164 | 1.4211e-13 | -0.012902 | -0.00052352 | 0.063957 | -0.003064 | 0.059888 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064699 | 0.0066772 | 0.063342 | -58.465 | -0.021486 | -61.0323 | 60.3999 | 60.053 | 60.085 | -61.1001 | -61.0057 | 0.004938 | -61.1043 | 60.2139 | 60.3002 | 60.3217 | -61.1586 | -0.043602 | -0.1165 | 2.5916 | 0.024208 | 0.06781 | -0.4634 | -0.43133 | -0.10205 | -0.30247 | 0.050837 | -0.047771 | 0.054283 | -0.21619 | -0.19467 | 121.4564 | 121.1095 | 121.1415 | 61.035 | -121.6165 | 121.2704 | 121.3567 | 121.3782 | 61.0615 | -121.6749
220.7344 | 121.8063 | -61.0703 | 60.4156 | 1.4211e-13 | -0.013115 | -0.00052352 | 0.064171 | -0.0034912 | 0.060101 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063769 | -58.5153 | -0.016908 | -61.046 | 60.3907 | 60.053 | 60.085 | -61.1001 | -61.0011 | 0.000359 | -61.1134 | 60.223 | 60.3047 | 60.3125 | -61.1494 | -0.02987 | -0.024948 | 2.5549 | 0.024205 | 0.054075 | -0.3627 | -0.33062 | -0.079164 | -0.19261 | 0.069147 | -0.043196 | 0.035968 | -0.11091 | -0.10312 | 121.461 | 121.1232 | 121.1553 | 61.0533 | -121.5158 | 121.2933 | 121.375 | 121.3828 | 61.0706 | -121.5651
222.4375 | 121.8704 | -61.0291 | 60.4706 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0064636 | 0.063769 | -58.5336 | -0.016908 | -61.0415 | 60.3953 | 60.0484 | 60.085 | -61.1047 | -61.0011 | 0.000359 | -61.118 | 60.2139 | 60.3002 | 60.3217 | -61.1494 | -0.075647 | -0.075301 | 2.4954 | -0.012414 | 0.063233 | -0.42221 | -0.38555 | -0.12036 | -0.2567 | 0.027949 | -0.088973 | 0.031389 | -0.17042 | -0.1489 | 121.4243 | 121.0774 | 121.1141 | 61.0121 | -121.5753 | 121.2429 | 121.3292 | 121.3507 | 61.0294 | -121.62
224.25 | 121.7422 | -61.1343 | 60.3836 | 1.4211e-13 | -0.012474 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0066772 | 0.063342 | -58.4283 | -0.021486 | -61.0415 | 60.3907 | 60.053 | 60.0896 | -61.0955 | -61.0011 | 0.000359 | -61.0997 | 60.2139 | 60.3047 | 60.3171 | -61.154 | 0.038796 | 0.007095 | 2.706 | 0.092871 | 0.054075 | -0.33065 | -0.294 | -0.019656 | -0.16972 | 0.13323 | 0.034627 | 0.054283 | -0.078862 | -0.066503 | 121.525 | 121.1873 | 121.2239 | 61.1129 | -121.4791 | 121.3482 | 121.4391 | 121.4514 | 61.1347 | -121.5376
226.0156 | 121.8475 | -61.0886 | 60.379 | 1.4211e-13 | -0.013115 | -0.00052352 | 0.063957 | -0.0032776 | 0.059888 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064699 | 0.0066772 | 0.063555 | -58.4604 | -0.016908 | -61.046 | 60.3999 | 60.053 | 60.0896 | -61.1001 | -61.0057 | 0.000359 | -61.1089 | 60.2185 | 60.3002 | 60.3171 | -61.1494 | -0.011559 | 0.02083 | 2.6282 | 0.042516 | 0.054075 | -0.32607 | -0.28942 | -0.060853 | -0.16056 | 0.08288 | -0.020306 | 0.040547 | -0.078862 | -0.061925 | 121.4884 | 121.1415 | 121.1782 | 61.0717 | -121.4791 | 121.307 | 121.3887 | 121.4057 | 61.0889 | -121.5284
227.7969 | 121.7377 | -61.1206 | 60.4568 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063744 | -0.0032776 | 0.060742 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063342 | -58.4192 | -0.016908 | -61.0506 | 60.3953 | 60.053 | 60.085 | -61.1093 | -61.0057 | 0.009516 | -61.1089 | 60.2093 | 60.3047 | 60.3217 | -61.154 | 0.011326 | -0.061568 | 2.7014 | 0.069981 | 0.058655 | -0.40389 | -0.37182 | -0.033389 | -0.24754 | 0.11492 | 0.011737 | 0.045126 | -0.1521 | -0.13517 | 121.5159 | 121.1736 | 121.2056 | 61.1037 | -121.5661 | 121.3299 | 121.4253 | 121.4423 | 61.1301 | -121.6108
229.4844 | 121.7468 | -61.0794 | 60.4614 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.064171 | -0.003064 | 0.059888 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063555 | -58.4329 | -0.016908 | -61.046 | 60.3953 | 60.053 | 60.085 | -61.0955 | -61.0057 | -0.00422 | -61.1089 | 60.2139 | 60.3047 | 60.3125 | -61.154 | -0.016135 | -0.066146 | 2.6465 | 0.033361 | 0.049496 | -0.40847 | -0.3764 | -0.074587 | -0.24754 | 0.073725 | -0.029461 | 0.045126 | -0.15668 | -0.1489 | 121.4747 | 121.1324 | 121.1644 | 61.0625 | -121.557 | 121.2933 | 121.3842 | 121.3919 | 61.0752 | -121.6154
231.25 | 121.7789 | -61.0748 | 60.4111 | 1.4211e-13 | -0.012688 | -0.00073712 | 0.063957 | -0.0028504 | 0.060315 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064485 | 0.0066772 | 0.063555 | -58.4833 | -0.016908 | -61.046 | 60.3861 | 60.0484 | 60.085 | -61.1047 | -61.0011 | 0.000359 | -61.1134 | 60.2139 | 60.3002 | 60.3171 | -61.1586 | -0.029871 | -0.024949 | 2.5915 | 0.028783 | 0.058654 | -0.3627 | -0.32604 | -0.083744 | -0.19719 | 0.073725 | -0.038618 | 0.045126 | -0.11091 | -0.093969 | 121.461 | 121.1232 | 121.1599 | 61.0579 | -121.5158 | 121.2887 | 121.375 | 121.3919 | 61.0752 | -121.5696
233.0156 | 121.7972 | -61.0977 | 60.3973 | 1.4211e-13 | -0.012688 | -0.00052352 | 0.064171 | -0.0028504 | 0.060101 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0066772 | 0.063128 | -58.4421 | -0.021486 | -61.0415 | 60.3999 | 60.0484 | 60.085 | -61.1001 | -61.0011 | 0.004938 | -61.1043 | 60.223 | 60.2956 | 60.3171 | -61.154 | -0.002404 | 0.002519 | 2.6556 | 0.05625 | 0.058654 | -0.34896 | -0.31231 | -0.056277 | -0.1743 | 0.096613 | -0.006573 | 0.049704 | -0.10175 | -0.080236 | 121.4976 | 121.1461 | 121.1827 | 61.0762 | -121.4975 | 121.3208 | 121.3933 | 121.4148 | 61.1027 | -121.5513
234.7031 | 121.8201 | -61.0977 | 60.3745 | 1.4211e-13 | -0.012902 | -0.00095092 | 0.063744 | -0.0032776 | 0.060315 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064272 | 0.0066772 | 0.063555 | -58.4787 | -0.026065 | -61.0369 | 60.3953 | 60.0484 | 60.0896 | -61.1001 | -60.9965 | -0.00422 | -61.1043 | 60.2093 | 60.3002 | 60.3217 | -61.1494 | -0.002404 | 0.020829 | 2.619 | 0.060828 | 0.063232 | -0.32608 | -0.28484 | -0.051698 | -0.16514 | 0.10119 | -0.006573 | 0.045125 | -0.074285 | -0.052769 | 121.493 | 121.1461 | 121.1873 | 61.0717 | -121.4746 | 121.307 | 121.3979 | 121.4194 | 61.0935 | -121.5239
236.4531 | 121.7972 | -61.0291 | 60.4706 | 1.4211e-13 | -0.012902 | -0.00095092 | 0.064385 | -0.0032776 | 0.060101 | 0.0053411 | 0.00013254 | -0.00026913 | 0.064485 | 0.0066772 | 0.063983 | -58.4924 | -0.021486 | -61.0369 | 60.3953 | 60.0484 | 60.0805 | -61.0955 | -61.0057 | 0.004938 | -61.1043 | 60.2093 | 60.3002 | 60.3217 | -61.154 | -0.066489 | -0.075301 | 2.5366 | -0.007836 | 0.058653 | -0.42221 | -0.39013 | -0.12494 | -0.26127 | 0.023371 | -0.075237 | 0.049704 | -0.17042 | -0.1489 | 121.4243 | 121.0774 | 121.1095 | 61.0076 | -121.5661 | 121.2384 | 121.3292 | 121.3507 | 61.034 | -121.6246
238.2344 | 121.8018 | -61.0703 | 60.4202 | 1.4211e-13 | -0.013115 | -0.00052352 | 0.06353 | -0.003064 | 0.059888 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064485 | 0.0064636 | 0.063128 | -58.5199 | -0.016908 | -61.0415 | 60.3861 | 60.0484 | 60.0805 | -61.091 | -61.0011 | -0.00422 | -61.1089 | 60.2185 | 60.3002 | 60.3217 | -61.154 | -0.020713 | -0.034104 | 2.5503 | 0.028784 | 0.049497 | -0.37185 | -0.33977 | -0.083743 | -0.20176 | 0.069147 | -0.038617 | 0.045126 | -0.12006 | -0.098545 | 121.4564 | 121.1186 | 121.1507 | 61.0533 | -121.5112 | 121.2887 | 121.3704 | 121.3919 | 61.066 | -121.5742
239.9844 | 121.7972 | -61.0794 | 60.4111 | 1.4211e-13 | -0.012902 | -0.00030992 | 0.063957 | -0.0032776 | 0.060101 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.0066772 | 0.063555 | -58.5107 | -0.016908 | -61.0415 | 60.3953 | 60.053 | 60.085 | -61.0955 | -61.0011 | 0.000359 | -61.1089 | 60.2139 | 60.3002 | 60.3171 | -61.1494 | -0.016135 | -0.015792 | 2.5687 | 0.03794 | 0.054075 | -0.35812 | -0.32604 | -0.070008 | -0.19719 | 0.078303 | -0.029461 | 0.040547 | -0.11091 | -0.093969 | 121.4747 | 121.1324 | 121.1644 | 61.0625 | -121.5066 | 121.2933 | 121.3796 | 121.3965 | 61.0798 | -121.5605
241.6719 | 121.8475 | -61.0382 | 60.4477 | 1.4211e-13 | -0.012902 | -0.00073712 | 0.063744 | -0.0032776 | 0.060101 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0066772 | 0.063555 | -58.5245 | -0.021486 | -61.0369 | 60.3907 | 60.0438 | 60.085 | -61.0955 | -61.0057 | 0.000359 | -61.1089 | 60.2139 | 60.3002 | 60.3217 | -61.1494 | -0.057334 | -0.056992 | 2.5137 | 0.001319 | 0.058653 | -0.4039 | -0.36266 | -0.11121 | -0.23381 | 0.032526 | -0.07066 | 0.040547 | -0.14753 | -0.12601 | 121.4289 | 121.082 | 121.1232 | 61.0167 | -121.5432 | 121.2521 | 121.3384 | 121.3599 | 61.0386 | -121.5971
243.4375 | 121.7514 | -61.1206 | 60.3882 | 1.4211e-13 | -0.012902 | -0.00073712 | 0.063957 | -0.0032776 | 0.060315 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0066772 | 0.063555 | -58.4283 | -0.021486 | -61.0415 | 60.3907 | 60.0484 | 60.085 | -61.091 | -61.0011 | 0.000359 | -61.1089 | 60.2093 | 60.2956 | 60.3171 | -61.154 | 0.029641 | 0.002517 | 2.6923 | 0.079138 | 0.049497 | -0.33981 | -0.30315 | -0.033389 | -0.17888 | 0.1195 | 0.011737 | 0.045126 | -0.092597 | -0.071081 | 121.5113 | 121.169 | 121.2056 | 61.0991 | -121.4791 | 121.3299 | 121.4162 | 121.4377 | 61.121 | -121.5422
245.1875 | 121.788 | -61.0977 | 60.4248 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064058 | 0.0064636 | 0.063555 | -58.4879 | -0.021486 | -61.0369 | 60.3953 | 60.0438 | 60.0896 | -61.1001 | -61.0057 | -0.00422 | -61.1089 | 60.2093 | 60.2956 | 60.3171 | -61.154 | -0.002404 | -0.029525 | 2.6099 | 0.060828 | 0.063232 | -0.38101 | -0.3352 | -0.056277 | -0.2155 | 0.092035 | -0.011151 | 0.045126 | -0.12922 | -0.1077 | 121.493 | 121.1415 | 121.1873 | 61.0762 | -121.5249 | 121.307 | 121.3933 | 121.4148 | 61.0935 | -121.5788
246.8906 | 121.7468 | -61.0519 | 60.4797 | 1.4211e-13 | -0.012902 | -0.00073712 | 0.063957 | -0.0032776 | 0.059888 | 0.0053411 | -0.00029486 | 0.00015807 | 0.064913 | 0.0066772 | 0.063769 | -58.4924 | -0.016908 | -61.0415 | 60.3953 | 60.053 | 60.0805 | -61.0955 | -60.9965 | 0.000359 | -61.1043 | 60.2093 | 60.3002 | 60.3217 | -61.1494 | -0.043601 | -0.084456 | 2.5595 | 0.010474 | 0.054075 | -0.42678 | -0.39928 | -0.097474 | -0.27043 | 0.055416 | -0.052349 | 0.045125 | -0.17957 | -0.15805 | 121.4472 | 121.1049 | 121.1324 | 61.035 | -121.5753 | 121.2612 | 121.3521 | 121.3736 | 61.0523 | -121.6292
248.6406 | 121.8613 | -61.0245 | 60.466 | 1.4211e-13 | -0.012902 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | 0.012972 | 0.00013254 | 0.00037167 | 0.064485 | 0.0064636 | 0.063128 | -58.5336 | -0.026065 | -61.0369 | 60.3999 | 60.0484 | 60.085 | -61.0955 | -61.0011 | 0.004938 | -61.1043 | 60.2139 | 60.3002 | 60.3125 | -61.1494 | -0.071067 | -0.066145 | 2.4908 | -0.012414 | 0.058653 | -0.41763 | -0.38097 | -0.12494 | -0.25212 | 0.023371 | -0.079815 | 0.045125 | -0.16584 | -0.15348 | 121.4243 | 121.0729 | 121.1095 | 60.9984 | -121.5615 | 121.2384 | 121.3246 | 121.337 | 61.0294 | -121.6154
250.3438 | 121.6965 | -61.0931 | 60.4385 | 1.4211e-13 | -0.013115 | -0.00095092 | 0.063957 | -0.003064 | 0.060101 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064485 | 0.006891 | 0.063555 | -58.4238 | -0.016908 | -61.0369 | 60.3907 | 60.0484 | 60.085 | -61.1001 | -61.0057 | -0.00422 | -61.0997 | 60.2185 | 60.3047 | 60.3171 | -61.1494 | -0.006981 | -0.047837 | 2.6694 | 0.056251 | 0.063232 | -0.39016 | -0.35351 | -0.056275 | -0.22007 | 0.087458 | -0.006571 | 0.049704 | -0.13379 | -0.12143 | 121.4838 | 121.1415 | 121.1782 | 61.0762 | -121.5387 | 121.3116 | 121.3979 | 121.4102 | 61.0889 | -121.588
252.1094 | 121.701 | -61.0657 | 60.5072 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.06353 | -0.0032776 | 0.059888 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064699 | 0.0066772 | 0.063769 | -58.465 | -0.021486 | -61.0369 | 60.3907 | 60.0484 | 60.0759 | -61.0955 | -60.9965 | -0.008798 | -61.0997 | 60.2139 | 60.291 | 60.3171 | -61.1494 | -0.029868 | -0.1165 | 2.6007 | 0.028785 | 0.058653 | -0.45883 | -0.43133 | -0.083741 | -0.29332 | 0.069149 | -0.034037 | 0.049704 | -0.21619 | -0.1901 | 121.4564 | 121.114 | 121.1415 | 61.0442 | -121.6027 | 121.2796 | 121.3567 | 121.3828 | 61.0569 | -121.6566
253.8594 | 121.7239 | -61.1114 | 60.4385 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.063957 | -0.003064 | 0.060315 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0060362 | 0.063555 | -58.4146 | -0.012329 | -61.0369 | 60.3953 | 60.053 | 60.085 | -61.1001 | -60.9965 | 0.000359 | -61.1043 | 60.2185 | 60.291 | 60.3125 | -61.1494 | 0.011329 | -0.043258 | 2.6968 | 0.074561 | 0.063232 | -0.38558 | -0.35351 | -0.037965 | -0.22007 | 0.11492 | 0.00716 | 0.045125 | -0.14753 | -0.12601 | 121.5067 | 121.1644 | 121.1965 | 61.0991 | -121.5387 | 121.3299 | 121.4025 | 121.424 | 61.1118 | -121.588
255.5469 | 121.7102 | -61.1389 | 60.4156 | 1.4211e-13 | -0.013329 | -0.00073712 | 0.063744 | -0.0032776 | 0.059888 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.064485 | 0.0064636 | 0.063769 | -58.4192 | -0.026065 | -61.0415 | 60.3907 | 60.0484 | 60.0805 | -61.1001 | -60.9965 | -0.00422 | -61.0997 | 60.2093 | 60.291 | 60.3217 | -61.1494 | 0.038795 | -0.024948 | 2.7197 | 0.097449 | 0.058654 | -0.36727 | -0.3352 | -0.010499 | -0.20634 | 0.14239 | 0.039205 | 0.049704 | -0.12464 | -0.093967 | 121.5296 | 121.1873 | 121.2194 | 61.1129 | -121.5158 | 121.3482 | 121.4299 | 121.4606 | 61.1347 | -121.5651
257.2969 | 121.7285 | -61.1343 | 60.4248 | 1.4211e-13 | -0.013329 | -0.00073712 | 0.063744 | -0.0034912 | 0.060315 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0064636 | 0.063555 | -58.4238 | -0.016908 | -61.0415 | 60.3907 | 60.0392 | 60.0805 | -61.1001 | -60.9965 | -0.00422 | -61.1043 | 60.2093 | 60.2956 | 60.3079 | -61.1494 | 0.034217 | -0.034104 | 2.7106 | 0.092871 | 0.058654 | -0.38559 | -0.34435 | -0.015077 | -0.2155 | 0.13781 | 0.030048 | 0.045125 | -0.12922 | -0.11686 | 121.525 | 121.1736 | 121.2148 | 61.1174 | -121.5249 | 121.3436 | 121.4299 | 121.4423 | 61.1301 | -121.5742
259 | 121.756 | -61.0565 | 60.4568 | 1.4211e-13 | -0.013115 | -0.0011645 | 0.063957 | -0.003064 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063555 | -58.4283 | -0.021486 | -61.0415 | 60.3907 | 60.053 | 60.0896 | -61.0864 | -61.0011 | 0.000359 | -61.1089 | 60.2093 | 60.2956 | 60.3125 | -61.154 | -0.029866 | -0.066147 | 2.6282 | 0.015052 | 0.044918 | -0.40389 | -0.36724 | -0.097475 | -0.24754 | 0.055415 | -0.052349 | 0.045126 | -0.16126 | -0.14432 | 121.4472 | 121.1095 | 121.1461 | 61.035 | -121.5432 | 121.2658 | 121.3521 | 121.369 | 61.0569 | -121.6108
260.7031 | 121.701 | -61.1252 | 60.4248 | 1.4211e-13 | -0.013329 | -0.00052352 | 0.063957 | -0.0032776 | 0.060101 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063555 | -58.4375 | -0.021486 | -61.0415 | 60.3953 | 60.0484 | 60.0896 | -61.0955 | -60.9919 | 0.000359 | -61.0997 | 60.2139 | 60.2956 | 60.3171 | -61.1494 | 0.029641 | -0.029525 | 2.6877 | 0.083716 | 0.054075 | -0.37643 | -0.3352 | -0.024232 | -0.21092 | 0.13324 | 0.025472 | 0.049704 | -0.12922 | -0.1077 | 121.5205 | 121.1736 | 121.2148 | 61.1037 | -121.5203 | 121.3391 | 121.4208 | 121.4423 | 61.1255 | -121.5742
262.4688 | 121.7789 | -61.084 | 60.3882 | 1.4211e-13 | -0.013329 | -0.00073712 | 0.063957 | -0.003064 | 0.060315 | -0.0022889 | 0.00013254 | -0.00026913 | 0.064485 | 0.0066772 | 0.063342 | -58.4833 | -0.016908 | -61.0369 | 60.3953 | 60.0484 | 60.085 | -61.0955 | -60.9919 | 0.000359 | -61.1043 | 60.2047 | 60.2956 | 60.3034 | -61.1494 | -0.011558 | 0.007096 | 2.6007 | 0.047095 | 0.058653 | -0.33981 | -0.30315 | -0.065431 | -0.18346 | 0.092038 | -0.020306 | 0.045125 | -0.092597 | -0.084817 | 121.4793 | 121.1324 | 121.169 | 61.0671 | -121.4837 | 121.2887 | 121.3796 | 121.3874 | 61.0843 | -121.5376
264.1719 | 121.7606 | -61.0931 | 60.4477 | 1.4211e-13 | -0.013329 | -0.00052352 | 0.063957 | -0.0032776 | 0.060315 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0066772 | 0.063555 | -58.4283 | -0.016908 | -61.0415 | 60.3861 | 60.0575 | 60.0805 | -61.0955 | -60.9965 | 0.004938 | -61.0997 | 60.2093 | 60.291 | 60.3125 | -61.1448 | -0.002402 | -0.06157 | 2.6648 | 0.051673 | 0.054075 | -0.39016 | -0.36724 | -0.051696 | -0.23839 | 0.096615 | -0.006571 | 0.045125 | -0.15668 | -0.13517 | 121.4793 | 121.1507 | 121.1736 | 61.0762 | -121.5432 | 121.3024 | 121.3841 | 121.4057 | 61.0981 | -121.5925
265.875 | 121.8201 | -61.084 | 60.3561 | 1.4211e-13 | -0.012902 | -0.0011645 | 0.063957 | -0.003064 | 0.059888 | 0.012972 | 0.00013254 | -0.00026913 | 0.064699 | 0.0066772 | 0.063555 | -58.4467 | -0.026065 | -61.0323 | 60.3907 | 60.0438 | 60.085 | -61.091 | -60.9919 | 0.004938 | -61.1089 | 60.2093 | 60.3047 | 60.3125 | -61.1494 | -0.00698 | 0.034561 | 2.6373 | 0.051673 | 0.058653 | -0.31234 | -0.27111 | -0.065431 | -0.14683 | 0.092038 | -0.024884 | 0.040547 | -0.051396 | -0.043616 | 121.4747 | 121.1278 | 121.169 | 61.0579 | -121.4471 | 121.2933 | 121.3887 | 121.3965 | 61.0889 | -121.5056
267.5781 | 121.7468 | -61.0794 | 60.466 | 1.4211e-13 | -0.012902 | -0.00095092 | 0.063957 | -0.0032776 | 0.060315 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064699 | 0.0066772 | 0.063342 | -58.4238 | -0.021486 | -61.0323 | 60.3953 | 60.0621 | 60.085 | -61.0955 | -60.9965 | -0.00422 | -61.0951 | 60.2093 | 60.2956 | 60.3171 | -61.1494 | -0.016135 | -0.070723 | 2.6556 | 0.047096 | 0.063231 | -0.40389 | -0.38097 | -0.070008 | -0.2567 | 0.082882 | -0.015725 | 0.054283 | -0.17042 | -0.1489 | 121.4747 | 121.1415 | 121.1644 | 61.0579 | -121.5615 | 121.2887 | 121.375 | 121.3965 | 61.0752 | -121.6154
269.3281 | 121.8292 | -61.0611 | 60.379 | 1.4211e-13 | -0.013115 | -0.00052352 | 0.063957 | -0.003064 | 0.060101 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064699 | 0.0066772 | 0.063342 | -58.4467 | -0.016908 | -61.0323 | 60.3999 | 60.0438 | 60.0896 | -61.091 | -60.9919 | 0.004938 | -61.0997 | 60.2047 | 60.291 | 60.3125 | -61.1494 | -0.029868 | 0.02083 | 2.6144 | 0.028785 | 0.058653 | -0.33523 | -0.28942 | -0.088319 | -0.1743 | 0.06915 | -0.038615 | 0.049704 | -0.088019 | -0.066504 | 121.461 | 121.1049 | 121.1507 | 61.0442 | -121.47 | 121.2658 | 121.3521 | 121.3736 | 61.066 | -121.5284
271.0938 | 121.8155 | -61.084 | 60.4019 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.063744 | -0.0032776 | 0.059674 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0066772 | 0.063555 | -58.465 | -0.021486 | -61.0277 | 60.3815 | 60.053 | 60.0805 | -61.0955 | -60.9965 | 0.004938 | -61.0951 | 60.2047 | 60.3002 | 60.3171 | -61.1494 | -0.011558 | -0.020372 | 2.619 | 0.056252 | 0.06781 | -0.34896 | -0.32146 | -0.065431 | -0.19719 | 0.087459 | -0.011148 | 0.054283 | -0.10175 | -0.084814 | 121.4655 | 121.1369 | 121.1644 | 61.0625 | -121.4975 | 121.2887 | 121.3842 | 121.4011 | 61.0889 | -121.5513
272.7969 | 121.7743 | -61.1069 | 60.4019 | 1.4211e-13 | -0.013543 | -0.00095092 | 0.063744 | -0.0034912 | 0.059888 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063769 | -58.4375 | -0.021486 | -61.0323 | 60.3861 | 60.053 | 60.085 | -61.0955 | -60.9828 | 0.000359 | -61.0906 | 60.2093 | 60.291 | 60.3171 | -61.1448 | 0.011331 | -0.015794 | 2.6694 | 0.074562 | 0.063231 | -0.34896 | -0.31689 | -0.037963 | -0.19261 | 0.12408 | 0.01632 | 0.054283 | -0.11091 | -0.084814 | 121.493 | 121.1598 | 121.1919 | 61.0854 | -121.4975 | 121.3162 | 121.3979 | 121.424 | 61.1072 | -121.5468
274.4844 | 121.6782 | -61.116 | 60.434 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.064171 | -0.003064 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.006891 | 0.063555 | -58.4146 | -0.021486 | -61.0369 | 60.3953 | 60.0484 | 60.085 | -61.091 | -60.9965 | -0.00422 | -61.0951 | 60.2139 | 60.2956 | 60.3171 | -61.1448 | 0.025064 | -0.03868 | 2.7014 | 0.079139 | 0.054075 | -0.38558 | -0.34893 | -0.028808 | -0.22008 | 0.1195 | 0.020896 | 0.049704 | -0.13837 | -0.11686 | 121.5113 | 121.1644 | 121.2011 | 61.0945 | -121.5249 | 121.3299 | 121.4116 | 121.4331 | 61.1118 | -121.5788
276.2656 | 121.8063 | -61.0199 | 60.4706 | 1.4211e-13 | -0.013329 | -0.00095092 | 0.063957 | -0.0032776 | 0.060315 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064699 | 0.006891 | 0.063555 | -58.497 | -0.016908 | -61.0369 | 60.3953 | 60.0438 | 60.0805 | -61.0955 | -60.9919 | -0.008798 | -61.1043 | 60.2093 | 60.291 | 60.3079 | -61.1494 | -0.075645 | -0.075301 | 2.5229 | -0.016992 | 0.058653 | -0.42679 | -0.39013 | -0.12952 | -0.26127 | 0.027951 | -0.084393 | 0.045125 | -0.17957 | -0.16264 | 121.4152 | 121.0637 | 121.1003 | 61.003 | -121.5661 | 121.2292 | 121.3109 | 121.3278 | 61.0111 | -121.62
278.0469 | 121.7972 | -61.0703 | 60.4065 | 1.4211e-13 | -0.013115 | -0.00073712 | 0.063957 | -0.003064 | 0.059888 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.064485 | 0.006891 | 0.063555 | -58.5107 | -0.016908 | -61.0369 | 60.3861 | 60.0392 | 60.0896 | -61.0955 | -60.9965 | -0.00422 | -61.0997 | 60.2185 | 60.3002 | 60.3079 | -61.1448 | -0.025291 | -0.020371 | 2.5595 | 0.033362 | 0.058653 | -0.36728 | -0.31688 | -0.074585 | -0.18803 | 0.073726 | -0.02946 | 0.045125 | -0.10633 | -0.098548 | 121.4564 | 121.1095 | 121.1599 | 61.0533 | -121.502 | 121.2887 | 121.3704 | 121.3782 | 61.066 | -121.5513
279.75 | 121.6873 | -61.116 | 60.4431 | 1.4211e-13 | -0.013329 | -0.00073712 | 0.063744 | -0.0034912 | 0.059888 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.006891 | 0.062914 | -58.4192 | -0.016908 | -61.0369 | 60.3861 | 60.0484 | 60.0896 | -61.1001 | -60.9919 | 0.000359 | -61.0997 | 60.2139 | 60.291 | 60.3171 | -61.1448 | 0.015907 | -0.056992 | 2.6968 | 0.079139 | 0.063232 | -0.39474 | -0.35351 | -0.028808 | -0.22923 | 0.12408 | 0.016317 | 0.045125 | -0.15211 | -0.12601 | 121.5022 | 121.1644 | 121.2056 | 61.0991 | -121.5432 | 121.3299 | 121.407 | 121.4331 | 61.1164 | -121.588
281.5 | 121.6873 | -61.116 | 60.4202 | 1.4211e-13 | -0.013756 | -0.00052352 | 0.06353 | -0.0032776 | 0.060101 | -0.0022889 | -0.00050846 | -5.5534e-05 | 0.064485 | 0.006891 | 0.063342 | -58.4192 | -0.026065 | -61.0369 | 60.3907 | 60.0484 | 60.085 | -61.091 | -60.9965 | 0.004938 | -61.0997 | 60.2093 | 60.2956 | 60.3171 | -61.1448 | 0.025064 | -0.029526 | 2.6968 | 0.079139 | 0.054075 | -0.37185 | -0.3352 | -0.028808 | -0.21092 | 0.1195 | 0.016317 | 0.045125 | -0.12464 | -0.10312 | 121.5067 | 121.1644 | 121.2011 | 61.09 | -121.5112 | 121.3253 | 121.4116 | 121.4331 | 61.121 | -121.5651
283.2812 | 121.8246 | -61.0062 | 60.4477 | 1.4211e-13 | -0.013329 | -0.00052352 | 0.064171 | -0.003064 | 0.059888 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064485 | 0.006891 | 0.062914 | -58.5153 | -0.021486 | -61.0415 | 60.3907 | 60.0484 | 60.0805 | -61.091 | -60.9965 | 0.000359 | -61.0906 | 60.2002 | 60.2956 | 60.3079 | -61.1494 | -0.084799 | -0.056992 | 2.4908 | -0.035302 | 0.049497 | -0.39932 | -0.36724 | -0.14325 | -0.24754 | 0.00964 | -0.084388 | 0.058862 | -0.15211 | -0.13975 | 121.3969 | 121.0545 | 121.0866 | 60.9847 | -121.5387 | 121.2063 | 121.3018 | 121.3141 | 61.0065 | -121.5971
285.0469 | 121.7331 | -61.0657 | 60.5026 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063744 | -0.003064 | 0.060101 | 0.0053411 | -0.00029486 | 0.00015807 | 0.064699 | 0.0066772 | 0.063128 | -58.4375 | -0.021486 | -61.0369 | 60.3815 | 60.0438 | 60.085 | -61.0955 | -60.9919 | -0.00422 | -61.0906 | 60.2047 | 60.2956 | 60.3125 | -61.1448 | -0.029868 | -0.12108 | 2.6282 | 0.028785 | 0.058653 | -0.45883 | -0.41759 | -0.079162 | -0.2979 | 0.073728 | -0.024879 | 0.054283 | -0.20704 | -0.1901 | 121.4472 | 121.1095 | 121.1507 | 61.0442 | -121.5982 | 121.2704 | 121.3613 | 121.3782 | 61.0615 | -121.6475
286.75 | 121.7972 | -61.0748 | 60.434 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063744 | -0.0032776 | 0.060101 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.064699 | 0.0071046 | 0.063128 | -58.5107 | -0.021486 | -61.0415 | 60.3815 | 60.0392 | 60.0713 | -61.0955 | -60.9874 | 0.000359 | -61.0997 | 60.2047 | 60.291 | 60.3125 | -61.1448 | -0.020713 | -0.052415 | 2.5641 | 0.033362 | 0.054075 | -0.39474 | -0.36267 | -0.070007 | -0.22923 | 0.087461 | -0.024882 | 0.045125 | -0.14295 | -0.12144 | 121.4564 | 121.114 | 121.1461 | 61.0533 | -121.5295 | 121.2796 | 121.3658 | 121.3874 | 61.0752 | -121.5788
288.5 | 121.7102 | -61.0977 | 60.4065 | 1.4211e-13 | -0.013329 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.006891 | 0.063128 | -58.4283 | -0.012329 | -61.0369 | 60.3907 | 60.0438 | 60.0805 | -61.0864 | -60.9919 | 0.000359 | -61.0951 | 60.2047 | 60.291 | 60.3171 | -61.1448 | 0.011332 | -0.015793 | 2.6694 | 0.060828 | 0.049496 | -0.3627 | -0.32604 | -0.047119 | -0.20177 | 0.10577 | 0.002585 | 0.049704 | -0.11548 | -0.089391 | 121.4884 | 121.1415 | 121.1782 | 61.0854 | -121.4929 | 121.3024 | 121.3887 | 121.4148 | 61.0981 | -121.5513
290.2969 | 121.7468 | -61.0886 | 60.4431 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063744 | -0.0034912 | 0.060101 | 0.0053411 | -8.1262e-05 | -0.00048293 | 0.064485 | 0.006891 | 0.063128 | -58.4238 | -0.021486 | -61.0323 | 60.3953 | 60.0484 | 60.0713 | -61.091 | -60.9874 | -0.00422 | -61.1043 | 60.1956 | 60.2956 | 60.3125 | -61.1403 | -0.002402 | -0.047835 | 2.6648 | 0.056251 | 0.058653 | -0.39474 | -0.37182 | -0.051695 | -0.24754 | 0.10119 | -0.015728 | 0.035967 | -0.14753 | -0.13059 | 121.4838 | 121.1369 | 121.1599 | 61.0671 | -121.5341 | 121.2841 | 121.3841 | 121.4011 | 61.0843 | -121.5834
292.0625 | 121.8155 | -61.0977 | 60.3561 | 1.4211e-13 | -0.013756 | -0.00052352 | 0.063957 | -0.0032776 | 0.060101 | 0.012972 | -8.1262e-05 | 0.00015807 | 0.064272 | 0.006891 | 0.063128 | -58.4329 | -0.016908 | -61.0369 | 60.3907 | 60.0484 | 60.085 | -61.091 | -60.9828 | -0.00422 | -61.0951 | 60.2047 | 60.2819 | 60.3125 | -61.1494 | 0.006753 | 0.034561 | 2.6648 | 0.060828 | 0.054075 | -0.30777 | -0.27111 | -0.051698 | -0.15141 | 0.11493 | 0.002585 | 0.054283 | -0.074289 | -0.043616 | 121.4884 | 121.1461 | 121.1827 | 61.0808 | -121.4471 | 121.3024 | 121.3796 | 121.4102 | 61.0935 | -121.5056
293.8281 | 121.7194 | -61.0931 | 60.434 | 1.4211e-13 | -0.013543 | -0.00030992 | 0.063957 | -0.0034912 | 0.060101 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064485 | 0.0073182 | 0.063342 | -58.4238 | -0.021486 | -61.0323 | 60.3861 | 60.0392 | 60.085 | -61.0864 | -60.9874 | 0.000359 | -61.0906 | 60.2002 | 60.2956 | 60.3125 | -61.1403 | 0.006755 | -0.047837 | 2.6694 | 0.060829 | 0.054074 | -0.39474 | -0.34893 | -0.047117 | -0.23381 | 0.10577 | 0.002587 | 0.049704 | -0.13837 | -0.12144 | 121.4793 | 121.1324 | 121.1782 | 61.0717 | -121.5203 | 121.2933 | 121.3887 | 121.4057 | 61.0935 | -121.5742
295.5156 | 121.7697 | -61.0931 | 60.3699 | 1.4211e-13 | -0.013543 | -0.00052352 | 0.063957 | -0.0034912 | 0.059888 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.006891 | 0.063128 | -58.4283 | -0.016908 | -61.0232 | 60.3907 | 60.0484 | 60.085 | -61.0864 | -60.9874 | -0.00422 | -61.0906 | 60.2093 | 60.291 | 60.3079 | -61.1448 | 0.006755 | 0.020828 | 2.6648 | 0.069986 | 0.063231 | -0.3215 | -0.28484 | -0.051696 | -0.16057 | 0.10577 | 0.002587 | 0.054283 | -0.078864 | -0.061927 | 121.4838 | 121.1415 | 121.1782 | 61.0762 | -121.4563 | 121.3024 | 121.3841 | 121.4011 | 61.0889 | -121.5147
297.2812 | 121.8613 | -61.0245 | 60.4294 | 1.4211e-13 | -0.01397 | -0.00030992 | 0.063957 | -0.0032776 | 0.059888 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.0073182 | 0.063342 | -58.5245 | -0.026065 | -61.0232 | 60.3815 | 60.0438 | 60.0805 | -61.091 | -60.9919 | -0.008798 | -61.0906 | 60.2047 | 60.2864 | 60.3125 | -61.1494 | -0.066489 | -0.047837 | 2.5 | 0.001321 | 0.06781 | -0.38559 | -0.34893 | -0.12494 | -0.22465 | 0.032529 | -0.066078 | 0.058862 | -0.14295 | -0.11686 | 121.406 | 121.0683 | 121.1049 | 60.9984 | -121.5203 | 121.2292 | 121.3109 | 121.337 | 61.0157 | -121.5788
299.0469 | 121.669 | -61.116 | 60.4111 | 1.4211e-13 | -0.013543 | -0.00052352 | 0.063957 | -0.0034912 | 0.059888 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064699 | 0.006891 | 0.063128 | -58.4192 | -0.016908 | -61.0277 | 60.3907 | 60.053 | 60.0805 | -61.091 | -60.9874 | 0.004938 | -61.0951 | 60.2047 | 60.3002 | 60.3079 | -61.1357 | 0.025064 | -0.020371 | 2.6968 | 0.088296 | 0.063232 | -0.35812 | -0.33062 | -0.019651 | -0.20634 | 0.12866 | 0.020896 | 0.040547 | -0.11091 | -0.10313 | 121.5067 | 121.169 | 121.1965 | 61.0991 | -121.502 | 121.3208 | 121.4162 | 121.424 | 61.121 | -121.5468
300.75 | 121.8201 | -61.0153 | 60.4202 | 1.4211e-13 | -0.013329 | -0.00095092 | 0.063957 | -0.0032776 | 0.060101 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.064485 | 0.006891 | 0.062914 | -58.5245 | -0.021486 | -61.0369 | 60.3861 | 60.0484 | 60.085 | -61.091 | -60.9828 | 0.000359 | -61.086 | 60.2047 | 60.2956 | 60.3171 | -61.1494 | -0.075644 | -0.034104 | 2.4908 | -0.021569 | 0.054075 | -0.37185 | -0.3352 | -0.13409 | -0.2155 | 0.032531 | -0.070655 | 0.06344 | -0.12464 | -0.10312 | 121.4014 | 121.0637 | 121.1004 | 60.9938 | -121.5112 | 121.22 | 121.3109 | 121.3324 | 61.0157 | -121.5696
302.4531 | 121.6919 | -61.1114 | 60.4202 | 1.4211e-13 | -0.013543 | -0.00052352 | 0.06353 | -0.003064 | 0.060101 | -0.0022889 | -0.00050846 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.063128 | -58.41 | -0.016908 | -61.0277 | 60.3861 | 60.0484 | 60.085 | -61.0864 | -60.9828 | -0.008798 | -61.0951 | 60.2047 | 60.2864 | 60.3125 | -61.1311 | 0.025065 | -0.034104 | 2.7014 | 0.083718 | 0.058653 | -0.37185 | -0.3352 | -0.01965 | -0.2155 | 0.12866 | 0.016318 | 0.035968 | -0.1338 | -0.1077 | 121.4976 | 121.1598 | 121.1965 | 61.0945 | -121.5066 | 121.3162 | 121.3979 | 121.424 | 61.1027 | -121.5513
304.1562 | 121.8109 | -61.0886 | 60.379 | 1.4211e-13 | -0.01397 | -0.0011645 | 0.063957 | -0.003064 | 0.060101 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.064485 | 0.006891 | 0.062701 | -58.465 | -0.021486 | -61.0277 | 60.3861 | 60.053 | 60.085 | -61.0864 | -60.9828 | 0.004938 | -61.086 | 60.2093 | 60.291 | 60.3125 | -61.1357 | 0.002177 | 0.007095 | 2.6236 | 0.06083 | 0.058653 | -0.32607 | -0.294 | -0.047117 | -0.16972 | 0.10577 | 0.002587 | 0.049704 | -0.088019 | -0.066504 | 121.4747 | 121.1415 | 121.1736 | 61.0671 | -121.4654 | 121.2979 | 121.3796 | 121.4011 | 61.0935 | -121.5147
305.9062 | 121.8155 | -61.0886 | 60.3561 | 1.4211e-13 | -0.013756 | -0.00095092 | 0.063957 | -0.0034912 | 0.05946 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.006891 | 0.063128 | -58.4421 | -0.021486 | -61.0415 | 60.3907 | 60.0484 | 60.0896 | -61.091 | -60.9828 | -0.00422 | -61.0906 | 60.2047 | 60.2864 | 60.3125 | -61.1494 | -0.002402 | 0.034561 | 2.6465 | 0.047095 | 0.049497 | -0.30777 | -0.26653 | -0.060853 | -0.15141 | 0.10577 | -0.001991 | 0.058862 | -0.06971 | -0.043616 | 121.4793 | 121.1369 | 121.1782 | 61.0671 | -121.4471 | 121.2933 | 121.375 | 121.4011 | 61.0843 | -121.5056
307.6094 | 121.6873 | -61.0428 | 60.4477 | 1.4211e-13 | -0.013756 | -0.00095092 | 0.063957 | -0.0034912 | 0.060101 | -0.0099194 | -0.00029486 | -0.00026913 | 0.064485 | 0.0066772 | 0.062487 | -58.465 | -0.016908 | -61.0277 | 60.3907 | 60.0438 | 60.085 | -61.0818 | -60.9874 | 0.000359 | -61.0906 | 60.2047 | 60.291 | 60.3125 | -61.1357 | -0.03902 | -0.056992 | 2.5778 | 0.015054 | 0.054074 | -0.4039 | -0.36266 | -0.092893 | -0.24296 | 0.055418 | -0.047767 | 0.045126 | -0.15668 | -0.13517 | 121.4335 | 121.0866 | 121.1278 | 61.0259 | -121.5295 | 121.2475 | 121.3338 | 121.3553 | 61.0431 | -121.5834
309.375 | 121.6827 | -61.0336 | 60.4614 | 1.4211e-13 | -0.01397 | -0.00073712 | 0.06353 | -0.0032776 | 0.059888 | 0.0053411 | -0.00029486 | -0.00026913 | 0.064272 | 0.0066772 | 0.062914 | -58.4695 | -0.026065 | -61.0232 | 60.3907 | 60.0438 | 60.085 | -61.091 | -60.9828 | -0.00422 | -61.0951 | 60.2047 | 60.291 | 60.3125 | -61.1403 | -0.057334 | -0.070725 | 2.5641 | 0.010476 | 0.06781 | -0.41763 | -0.3764 | -0.10663 | -0.2567 | 0.050841 | -0.061502 | 0.045125 | -0.17042 | -0.1489 | 121.4243 | 121.0774 | 121.1187 | 61.0076 | -121.5524 | 121.2384 | 121.3246 | 121.3462 | 61.0294 | -121.6017
311.1406 | 121.8155 | -61.0748 | 60.3607 | 1.4211e-13 | -0.013756 | -0.00095092 | 0.06353 | -0.0034912 | 0.060101 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064272 | 0.006891 | 0.062701 | -58.4467 | -0.026065 | -61.0369 | 60.3861 | 60.0484 | 60.0896 | -61.0818 | -60.9828 | 0.000359 | -61.086 | 60.2047 | 60.291 | 60.3125 | -61.1357 | -0.006977 | 0.025405 | 2.6282 | 0.03794 | 0.044917 | -0.31234 | -0.27111 | -0.06085 | -0.15599 | 0.09204 | -0.011146 | 0.049704 | -0.069709 | -0.048194 | 121.461 | 121.1232 | 121.1644 | 61.0488 | -121.4425 | 121.2796 | 121.3658 | 121.3874 | 61.0752 | -121.4964
312.9062 | 121.7926 | -61.0794 | 60.3561 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063744 | -0.0034912 | 0.059888 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.006891 | 0.062914 | -58.4329 | -0.012329 | -61.0369 | 60.3861 | 60.0438 | 60.085 | -61.0864 | -60.9736 | 0.000359 | -61.0906 | 60.2093 | 60.2956 | 60.3171 | -61.1311 | -0.006978 | 0.029983 | 2.6465 | 0.042518 | 0.049496 | -0.31234 | -0.27111 | -0.051693 | -0.14683 | 0.10578 | -0.011146 | 0.040547 | -0.060553 | -0.039037 | 121.4655 | 121.1232 | 121.1644 | 61.0671 | -121.4425 | 121.2887 | 121.375 | 121.3965 | 61.0798 | -121.4872
314.5938 | 121.7743 | -61.0748 | 60.4065 | 1.4211e-13 | -0.01397 | -0.00073712 | 0.063744 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0071046 | 0.063128 | -58.4879 | -0.012329 | -61.0232 | 60.3861 | 60.0392 | 60.0896 | -61.0864 | -60.9828 | 0.004938 | -61.086 | 60.2093 | 60.3002 | 60.3171 | -61.1357 | -0.011556 | -0.020371 | 2.587 | 0.051675 | 0.063231 | -0.36728 | -0.31688 | -0.06085 | -0.19719 | 0.09204 | -0.011146 | 0.049704 | -0.10633 | -0.089391 | 121.461 | 121.114 | 121.1644 | 61.0625 | -121.4929 | 121.2841 | 121.375 | 121.3919 | 61.0798 | -121.5422
316.3438 | 121.8338 | -61.0016 | 60.4477 | 1.4211e-13 | -0.013756 | -0.00052352 | 0.063744 | -0.0032776 | 0.059674 | 0.0053411 | 0.00077334 | -5.5534e-05 | 0.064913 | 0.0066772 | 0.062487 | -58.5245 | -0.016908 | -61.0323 | 60.3907 | 60.0484 | 60.0805 | -61.0864 | -60.9874 | -0.00422 | -61.0951 | 60.2093 | 60.2956 | 60.3079 | -61.1357 | -0.084798 | -0.056992 | 2.4771 | -0.030724 | 0.054074 | -0.39932 | -0.36724 | -0.13409 | -0.23839 | 0.014219 | -0.093545 | 0.040547 | -0.15211 | -0.13975 | 121.3923 | 121.05 | 121.082 | 60.9847 | -121.5341 | 121.2109 | 121.2972 | 121.3095 | 60.9974 | -121.5834
318.1094 | 121.8155 | -61.0336 | 60.4523 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063744 | -0.0032776 | 0.05946 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064272 | 0.0071046 | 0.062487 | -58.5153 | -0.016908 | -61.0277 | 60.3907 | 60.0438 | 60.085 | -61.091 | -60.9874 | 0.000359 | -61.0951 | 60.2047 | 60.3002 | 60.3171 | -61.1403 | -0.057334 | -0.06157 | 2.5183 | 0.005898 | 0.063232 | -0.40848 | -0.36724 | -0.10663 | -0.24754 | 0.046262 | -0.061502 | 0.045125 | -0.15211 | -0.13517 | 121.4243 | 121.0774 | 121.1187 | 61.0167 | -121.5432 | 121.2384 | 121.3338 | 121.3507 | 61.034 | -121.5925
319.875 | 121.7194 | -61.0657 | 60.4523 | 1.4211e-13 | -0.01397 | -0.00073712 | 0.06353 | -0.003705 | 0.059888 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064485 | 0.006891 | 0.062701 | -58.41 | -0.012329 | -61.0277 | 60.3861 | 60.053 | 60.0896 | -61.0864 | -60.9874 | 0.009516 | -61.086 | 60.2185 | 60.3047 | 60.3125 | -61.1311 | -0.020711 | -0.066148 | 2.6556 | 0.037942 | 0.058653 | -0.39932 | -0.36266 | -0.065426 | -0.23381 | 0.078306 | -0.020301 | 0.045125 | -0.14753 | -0.13975 | 121.4518 | 121.1186 | 121.1553 | 61.0533 | -121.5387 | 121.2841 | 121.3704 | 121.3782 | 61.0752 | -121.5834
321.5781 | 121.7331 | -61.0291 | 60.4523 | 1.4211e-13 | -0.013756 | -0.00095092 | 0.063957 | -0.0034912 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0071046 | 0.063128 | -58.4054 | -0.012329 | -61.0232 | 60.3907 | 60.0575 | 60.0896 | -61.0818 | -60.9782 | 0.000359 | -61.086 | 60.2002 | 60.3002 | 60.3171 | -61.1219 | -0.052753 | -0.06157 | 2.6236 | 0.005899 | 0.058652 | -0.39474 | -0.36266 | -0.092889 | -0.25212 | 0.050843 | -0.056922 | 0.035967 | -0.15211 | -0.13517 | 121.4198 | 121.0866 | 121.1187 | 61.0167 | -121.5341 | 121.2292 | 121.3292 | 121.3462 | 61.0294 | -121.5742
323.3594 | 121.6736 | -61.0291 | 60.4843 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063957 | -0.0032776 | 0.059674 | -0.01755 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.006891 | 0.062914 | -58.4512 | -0.016908 | -61.0323 | 60.3861 | 60.0484 | 60.085 | -61.0864 | -60.9736 | 0.004938 | -61.0814 | 60.2047 | 60.2956 | 60.3125 | -61.1403 | -0.057332 | -0.098191 | 2.5778 | -0.003258 | 0.054074 | -0.43594 | -0.39928 | -0.1112 | -0.27959 | 0.055421 | -0.052343 | 0.058861 | -0.18873 | -0.17179 | 121.4152 | 121.0774 | 121.1141 | 61.0121 | -121.5707 | 121.2338 | 121.3246 | 121.3416 | 61.034 | -121.6246
325.1406 | 121.7743 | -61.0291 | 60.4614 | 1.4211e-13 | -0.01397 | -0.00073712 | 0.063957 | -0.003705 | 0.059674 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064699 | 0.0071046 | 0.062487 | -58.4879 | -0.026065 | -61.0323 | 60.3907 | 60.0484 | 60.085 | -61.091 | -60.9782 | 0.000359 | -61.0951 | 60.2093 | 60.3047 | 60.3171 | -61.1357 | -0.061911 | -0.070725 | 2.5412 | -0.003258 | 0.058653 | -0.41305 | -0.3764 | -0.10663 | -0.25212 | 0.050843 | -0.066079 | 0.040547 | -0.15668 | -0.14432 | 121.4198 | 121.0774 | 121.1141 | 61.003 | -121.5524 | 121.2384 | 121.3338 | 121.3462 | 61.0294 | -121.5971
326.8438 | 121.8018 | -61.0748 | 60.3836 | 1.4211e-13 | -0.01397 | -0.00095092 | 0.063957 | -0.003064 | 0.059888 | 0.012972 | 0.00055974 | 0.00015807 | 0.064272 | 0.0071046 | 0.062914 | -58.4283 | -0.012329 | -61.0232 | 60.3907 | 60.0484 | 60.085 | -61.0772 | -60.9736 | -0.00422 | -61.086 | 60.2185 | 60.3002 | 60.3125 | -61.1403 | -0.002398 | 0.007095 | 2.6465 | 0.051675 | 0.054073 | -0.33523 | -0.29858 | -0.065428 | -0.16514 | 0.1012 | -0.011146 | 0.054282 | -0.08344 | -0.071082 | 121.4655 | 121.1232 | 121.1599 | 61.0625 | -121.4608 | 121.2933 | 121.375 | 121.3874 | 61.0706 | -121.5239
328.6094 | 121.7926 | -61.0062 | 60.4568 | 1.4211e-13 | -0.014184 | -0.00095092 | 0.063744 | -0.003705 | 0.059888 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064699 | 0.0073182 | 0.062701 | -58.5016 | -0.016908 | -61.0277 | 60.3861 | 60.053 | 60.0805 | -61.0818 | -60.9736 | -0.00422 | -61.0814 | 60.2047 | 60.3002 | 60.3171 | -61.1357 | -0.075641 | -0.070725 | 2.5046 | -0.021567 | 0.054074 | -0.40389 | -0.3764 | -0.12951 | -0.25212 | 0.032533 | -0.075231 | 0.054283 | -0.15668 | -0.13974 | 121.3923 | 121.0591 | 121.0866 | 60.9893 | -121.5387 | 121.2109 | 121.3063 | 121.3233 | 61.0019 | -121.5925
330.375 | 121.6919 | -61.0931 | 60.4248 | 1.4211e-13 | -0.01397 | -0.00073712 | 0.063744 | -0.0032776 | 0.059674 | 0.0053411 | 0.00055974 | -0.00026913 | 0.064272 | 0.0073182 | 0.062914 | -58.4054 | -0.016908 | -61.0323 | 60.3907 | 60.0484 | 60.0896 | -61.0864 | -60.9691 | 0.000359 | -61.086 | 60.2047 | 60.3047 | 60.3171 | -61.1265 | 0.006755 | -0.034104 | 2.6877 | 0.060829 | 0.054074 | -0.37643 | -0.3352 | -0.033381 | -0.22008 | 0.12409 | 0.007165 | 0.040546 | -0.12006 | -0.1077 | 121.4838 | 121.1415 | 121.1827 | 61.0762 | -121.5112 | 121.2979 | 121.3979 | 121.4102 | 61.0935 | -121.5513
332.125 | 121.701 | -61.0977 | 60.434 | 1.4211e-13 | -0.013756 | -0.00073712 | 0.063957 | -0.003705 | 0.060315 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064485 | 0.0073182 | 0.062487 | -58.41 | -0.012329 | -61.0277 | 60.3861 | 60.053 | 60.0942 | -61.0772 | -60.9736 | 0.000359 | -61.0722 | 60.2093 | 60.2956 | 60.3125 | -61.1311 | 0.02049 | -0.047837 | 2.6877 | 0.069985 | 0.049495 | -0.38101 | -0.33977 | -0.033383 | -0.22465 | 0.12409 | 0.025478 | 0.058861 | -0.13837 | -0.12144 | 121.4838 | 121.1507 | 121.1919 | 61.0854 | -121.5112 | 121.307 | 121.3933 | 121.4102 | 61.0981 | -121.5651
333.8281 | 121.7422 | -61.0474 | 60.4477 | 1.4211e-13 | -0.014397 | -0.00052352 | 0.063316 | -0.0034912 | 0.060101 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0066772 | 0.062914 | -58.41 | -0.016908 | -61.0232 | 60.3907 | 60.053 | 60.085 | -61.091 | -60.9691 | 0.009516 | -61.0814 | 60.2047 | 60.2956 | 60.3171 | -61.1311 | -0.043601 | -0.056992 | 2.6373 | 0.024209 | 0.06781 | -0.39474 | -0.36266 | -0.083737 | -0.24296 | 0.07831 | -0.034033 | 0.049704 | -0.15211 | -0.13059 | 121.4381 | 121.1003 | 121.1324 | 61.0305 | -121.5387 | 121.2521 | 121.343 | 121.3645 | 61.0569 | -121.5788
335.5938 | 121.6873 | -61.0886 | 60.4111 | 1.4211e-13 | -0.01397 | -0.00095092 | 0.063744 | -0.0034912 | 0.059674 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064272 | 0.0071046 | 0.063128 | -58.4009 | -0.021486 | -61.0323 | 60.3953 | 60.053 | 60.0942 | -61.0772 | -60.9736 | 0.000359 | -61.086 | 60.2093 | 60.3047 | 60.3171 | -61.1311 | 0.011335 | -0.015792 | 2.6877 | 0.056251 | 0.044916 | -0.35812 | -0.31688 | -0.042538 | -0.20176 | 0.11493 | 0.002587 | 0.045125 | -0.10633 | -0.093969 | 121.4838 | 121.1415 | 121.1827 | 61.0671 | -121.4883 | 121.2979 | 121.3933 | 121.4057 | 61.0889 | -121.5422
337.3594 | 121.7285 | -61.0474 | 60.466 | 1.4211e-13 | -0.014184 | -0.00052352 | 0.06353 | -0.0032776 | 0.060101 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064485 | 0.0071046 | 0.062701 | -58.4238 | -0.016908 | -61.0277 | 60.3907 | 60.053 | 60.0896 | -61.0818 | -60.9691 | -0.00422 | -61.0722 | 60.2093 | 60.2956 | 60.3125 | -61.1311 | -0.034443 | -0.075302 | 2.6236 | 0.019631 | 0.054074 | -0.41305 | -0.37639 | -0.083737 | -0.2567 | 0.07831 | -0.024876 | 0.058861 | -0.17042 | -0.15348 | 121.4381 | 121.1003 | 121.137 | 61.0305 | -121.5478 | 121.2567 | 121.343 | 121.3599 | 61.0431 | -121.5971
339.0781 | 121.8246 | -61.0199 | 60.4706 | 1.4211e-13 | -0.01397 | -0.0011645 | 0.06353 | -0.0032776 | 0.059674 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.0071046 | 0.062914 | -58.5153 | -0.012329 | -61.0232 | 60.3953 | 60.0575 | 60.0942 | -61.0726 | -60.9691 | -0.008798 | -61.0814 | 60.2047 | 60.2956 | 60.3171 | -61.1265 | -0.052751 | -0.075301 | 2.5046 | -0.003257 | 0.049494 | -0.41305 | -0.37639 | -0.10662 | -0.26585 | 0.050844 | -0.061499 | 0.045125 | -0.17499 | -0.15348 | 121.4152 | 121.0774 | 121.1141 | 61.0076 | -121.5432 | 121.2246 | 121.3155 | 121.337 | 61.0111 | -121.5971
340.8438 | 121.7972 | -61.0611 | 60.3745 | 1.4211e-13 | -0.014184 | -0.00073712 | 0.06353 | -0.0034912 | 0.059888 | 0.012972 | 0.00055974 | 0.00015807 | 0.063631 | 0.0071046 | 0.063128 | -58.4512 | -0.012329 | -61.0232 | 60.3953 | 60.0575 | 60.0896 | -61.0772 | -60.9645 | 0.000359 | -61.086 | 60.2047 | 60.3002 | 60.3125 | -61.1265 | -0.016131 | 0.020829 | 2.6099 | 0.037942 | 0.054073 | -0.31692 | -0.28484 | -0.065425 | -0.16972 | 0.096622 | -0.024879 | 0.040546 | -0.074285 | -0.061927 | 121.4564 | 121.1186 | 121.1507 | 61.0488 | -121.4517 | 121.2658 | 121.3613 | 121.3736 | 61.0615 | -121.501
342.5312 | 121.7697 | -61.0519 | 60.4065 | 1.4211e-13 | -0.014184 | -0.00073712 | 0.063957 | -0.0032776 | 0.059888 | -0.0099194 | 0.00098694 | -5.5534e-05 | 0.064272 | 0.0073182 | 0.062914 | -58.4787 | -0.021486 | -61.0232 | 60.3999 | 60.053 | 60.0942 | -61.0818 | -60.9691 | 0.004938 | -61.0814 | 60.2093 | 60.3002 | 60.3171 | -61.1311 | -0.029865 | -0.006636 | 2.5732 | 0.028787 | 0.058652 | -0.35354 | -0.31231 | -0.079159 | -0.19719 | 0.082888 | -0.029455 | 0.049704 | -0.10633 | -0.089391 | 121.4518 | 121.1049 | 121.1461 | 61.0305 | -121.4883 | 121.2612 | 121.3521 | 121.369 | 61.0569 | -121.5376
344.2969 | 121.7972 | -61.0474 | 60.3745 | 1.4211e-13 | -0.01397 | -0.00052352 | 0.063316 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.007532 | 0.062914 | -58.4421 | -0.012329 | -61.0186 | 60.3861 | 60.0438 | 60.0896 | -61.0726 | -60.9782 | 0.004938 | -61.0814 | 60.2185 | 60.2956 | 60.3171 | -61.1311 | -0.025285 | 0.011672 | 2.6053 | 0.028787 | 0.054072 | -0.33066 | -0.28484 | -0.083737 | -0.15599 | 0.069153 | -0.034033 | 0.049704 | -0.078864 | -0.057348 | 121.4335 | 121.0912 | 121.137 | 61.035 | -121.4471 | 121.2658 | 121.343 | 121.3645 | 61.0523 | -121.5056
346.0469 | 121.7606 | -61.0519 | 60.3836 | 1.4211e-13 | -0.014397 | -0.00073712 | 0.063957 | -0.0034912 | 0.060315 | 0.0053411 | 0.00055974 | -0.00026913 | 0.064485 | 0.0073182 | 0.062487 | -58.4467 | -0.016908 | -61.0186 | 60.3815 | 60.053 | 60.085 | -61.0726 | -60.9736 | 0.004938 | -61.0814 | 60.2093 | 60.3002 | 60.3125 | -61.1219 | -0.020707 | -0.002061 | 2.6053 | 0.033365 | 0.054072 | -0.33065 | -0.29858 | -0.070001 | -0.1743 | 0.078309 | -0.029455 | 0.040546 | -0.08344 | -0.071082 | 121.4335 | 121.1049 | 121.137 | 61.035 | -121.4563 | 121.2612 | 121.3521 | 121.3645 | 61.0569 | -121.5055
347.7344 | 121.8292 | -61.0016 | 60.4431 | 1.4211e-13 | -0.014397 | -0.00073712 | 0.063744 | -0.0034912 | 0.059674 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064272 | 0.007532 | 0.062701 | -58.5062 | -0.016908 | -61.0186 | 60.3953 | 60.0484 | 60.0988 | -61.0681 | -60.9599 | 0.009516 | -61.0722 | 60.2093 | 60.291 | 60.3034 | -61.1311 | -0.066482 | -0.047835 | 2.4954 | -0.016989 | 0.049493 | -0.39474 | -0.34435 | -0.12951 | -0.23381 | 0.041692 | -0.070652 | 0.058861 | -0.15211 | -0.13975 | 121.3969 | 121.05 | 121.1004 | 60.9847 | -121.5112 | 121.2109 | 121.2926 | 121.305 | 61.0111 | -121.5742
349.5 | 121.7194 | -61.0657 | 60.4523 | 1.4211e-13 | -0.014184 | -0.00073712 | 0.063957 | -0.0032776 | 0.060101 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0071046 | 0.062914 | -58.4009 | -0.016908 | -61.0186 | 60.3953 | 60.053 | 60.0896 | -61.0726 | -60.9691 | 0.004938 | -61.0768 | 60.2139 | 60.3002 | 60.3217 | -61.1219 | -0.006974 | -0.056991 | 2.6648 | 0.047098 | 0.054072 | -0.39932 | -0.36266 | -0.056268 | -0.23839 | 0.096621 | -0.011143 | 0.045125 | -0.15211 | -0.13059 | 121.461 | 121.1186 | 121.1553 | 61.0488 | -121.5249 | 121.2796 | 121.3658 | 121.3874 | 61.0706 | -121.5742
351.2656 | 121.8155 | -60.9924 | 60.4614 | 1.4211e-13 | -0.014611 | -0.00052352 | 0.06353 | -0.0034912 | 0.059888 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064485 | 0.0073182 | 0.062487 | -58.497 | -0.012329 | -61.0232 | 60.3861 | 60.0575 | 60.0942 | -61.0726 | -60.9599 | 0.004938 | -61.086 | 60.2185 | 60.3002 | 60.3217 | -61.1265 | -0.080216 | -0.075303 | 2.4954 | -0.030722 | 0.049494 | -0.40389 | -0.36724 | -0.13409 | -0.24296 | 0.032537 | -0.093543 | 0.040546 | -0.16126 | -0.13974 | 121.3786 | 121.05 | 121.0866 | 60.9801 | -121.5341 | 121.2109 | 121.2926 | 121.3141 | 60.9974 | -121.5879
353.0312 | 121.701 | -61.0794 | 60.4385 | 1.4211e-13 | -0.014184 | -0.00030992 | 0.063744 | -0.003705 | 0.060315 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064485 | 0.0071046 | 0.062914 | -58.3871 | -0.012329 | -61.0186 | 60.3907 | 60.0575 | 60.0942 | -61.0635 | -60.9599 | 0.004938 | -61.0768 | 60.2185 | 60.3002 | 60.3263 | -61.1311 | 0.015917 | -0.047837 | 2.6923 | 0.060831 | 0.044914 | -0.38101 | -0.34435 | -0.051693 | -0.22007 | 0.11951 | 0.00259 | 0.054283 | -0.13837 | -0.11228 | 121.4701 | 121.1369 | 121.1736 | 61.0671 | -121.502 | 121.2979 | 121.3796 | 121.4057 | 61.0843 | -121.5696
354.7344 | 121.7056 | -61.0245 | 60.4797 | 1.4211e-13 | -0.014611 | -0.00095092 | 0.063744 | -0.003705 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0073182 | 0.062487 | -58.41 | -0.012329 | -61.0186 | 60.3907 | 60.0575 | 60.0988 | -61.0726 | -60.9645 | 0.004938 | -61.0722 | 60.2093 | 60.2956 | 60.3263 | -61.1219 | -0.048173 | -0.089035 | 2.6145 | 0.005899 | 0.054072 | -0.4222 | -0.38097 | -0.097467 | -0.27043 | 0.060001 | -0.047764 | 0.049703 | -0.18415 | -0.15348 | 121.4152 | 121.082 | 121.1232 | 61.0121 | -121.5524 | 121.2338 | 121.3201 | 121.3507 | 61.0294 | -121.6017
356.4844 | 121.701 | -61.0245 | 60.4889 | 1.4211e-13 | -0.014184 | -0.00095092 | 0.063957 | -0.0032776 | 0.059888 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.007532 | 0.062701 | -58.41 | -0.012329 | -61.0186 | 60.3953 | 60.0667 | 60.0942 | -61.0726 | -60.9553 | -0.00422 | -61.0677 | 60.2139 | 60.3002 | 60.3263 | -61.1174 | -0.048173 | -0.093612 | 2.6145 | 0.005899 | 0.054072 | -0.4222 | -0.39471 | -0.092888 | -0.27501 | 0.069158 | -0.043185 | 0.049703 | -0.18873 | -0.16263 | 121.4198 | 121.0912 | 121.1187 | 61.0121 | -121.5615 | 121.2384 | 121.3246 | 121.3507 | 61.0203 | -121.6063
358.1875 | 121.8155 | -61.0016 | 60.4523 | 1.4211e-13 | -0.014611 | -0.00073712 | 0.06353 | -0.0032776 | 0.059888 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064272 | 0.0073182 | 0.062701 | -58.497 | -0.012329 | -61.0186 | 60.3907 | 60.0575 | 60.0988 | -61.0589 | -60.9691 | 0.000359 | -61.0677 | 60.2185 | 60.3002 | 60.3263 | -61.1219 | -0.057324 | -0.06157 | 2.5046 | -0.016989 | 0.040335 | -0.39474 | -0.35351 | -0.12035 | -0.23381 | 0.032534 | -0.066073 | 0.054282 | -0.15211 | -0.12601 | 121.3923 | 121.0591 | 121.1004 | 60.9893 | -121.5112 | 121.2201 | 121.3018 | 121.3278 | 61.0019 | -121.5742
359.9531 | 121.7194 | -61.0565 | 60.4385 | 1.4211e-13 | -0.014397 | -0.00030992 | 0.06353 | -0.0032776 | 0.059888 | 0.012972 | 0.00055974 | -5.5534e-05 | 0.064485 | 0.007532 | 0.062487 | -58.378 | -0.003172 | -61.0048 | 60.3999 | 60.0621 | 60.0988 | -61.0635 | -60.9553 | 0.009516 | -61.0677 | 60.2185 | 60.3047 | 60.3263 | -61.1082 | -0.006971 | -0.03868 | 2.6785 | 0.051678 | 0.058649 | -0.37643 | -0.33977 | -0.051687 | -0.22007 | 0.1012 | -0.011141 | 0.040546 | -0.13379 | -0.11228 | 121.4564 | 121.1186 | 121.1553 | 61.0533 | -121.502 | 121.275 | 121.3613 | 121.3828 | 61.066 | -121.5467
361.6562 | 121.756 | -61.0519 | 60.4294 | 1.4211e-13 | -0.014397 | -0.00095092 | 0.063957 | -0.0034912 | 0.059888 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0071046 | 0.062914 | -58.4558 | -0.007751 | -61.014 | 60.3999 | 60.0575 | 60.1033 | -61.0543 | -60.9599 | 0.004938 | -61.0631 | 60.2276 | 60.3002 | 60.3308 | -61.1174 | -0.002391 | -0.029524 | 2.5961 | 0.037943 | 0.040334 | -0.37185 | -0.32604 | -0.065422 | -0.20176 | 0.092046 | -0.01114 | 0.054282 | -0.12922 | -0.098543 | 121.4518 | 121.1095 | 121.1553 | 61.0442 | -121.4837 | 121.2796 | 121.3521 | 121.3828 | 61.0569 | -121.5467
363.4219 | 121.7926 | -61.0428 | 60.3653 | 1.4211e-13 | -0.014184 | -0.00073712 | 0.06353 | -0.003705 | 0.059674 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.007532 | 0.062914 | -58.4146 | -0.012329 | -61.0048 | 60.4044 | 60.0667 | 60.1033 | -61.0543 | -60.9553 | 0.000359 | -61.0631 | 60.2185 | 60.3047 | 60.3354 | -61.1082 | -0.011546 | 0.039141 | 2.6282 | 0.037945 | 0.049491 | -0.2986 | -0.26195 | -0.06542 | -0.14683 | 0.087469 | -0.020295 | 0.045125 | -0.060551 | -0.029878 | 121.4472 | 121.1095 | 121.1461 | 61.0305 | -121.4196 | 121.2612 | 121.3475 | 121.3782 | 61.0431 | -121.4735
365.125 | 121.7377 | -61.0382 | 60.466 | 1.4211e-13 | -0.014611 | -0.0013783 | 0.06353 | -0.0032776 | 0.060101 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.062914 | -58.3871 | -0.012329 | -61.014 | 60.3999 | 60.0621 | 60.1033 | -61.0681 | -60.9599 | 0.009516 | -61.0722 | 60.223 | 60.3047 | 60.3263 | -61.1128 | -0.029861 | -0.066145 | 2.6511 | 0.02421 | 0.054071 | -0.40389 | -0.36266 | -0.074576 | -0.24296 | 0.078313 | -0.034031 | 0.040545 | -0.16126 | -0.13974 | 121.4381 | 121.1003 | 121.1416 | 61.0259 | -121.5341 | 121.2612 | 121.343 | 121.3645 | 61.0477 | -121.5788
366.9062 | 121.6644 | -61.0428 | 60.5255 | 1.4211e-13 | -0.014611 | -0.00052352 | 0.063744 | -0.003064 | 0.059674 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.062701 | -58.41 | -0.021486 | -61.0094 | 60.409 | 60.0758 | 60.1079 | -61.0589 | -60.9462 | 0.000359 | -61.0539 | 60.2322 | 60.3047 | 60.3354 | -61.1036 | -0.016125 | -0.1165 | 2.6328 | 0.033367 | 0.049492 | -0.44966 | -0.41759 | -0.060841 | -0.29331 | 0.096627 | -0.011138 | 0.049703 | -0.22077 | -0.1901 | 121.4518 | 121.1186 | 121.1507 | 61.0213 | -121.5844 | 121.275 | 121.3475 | 121.3782 | 61.0431 | -121.6291
368.6094 | 121.7468 | -61.0336 | 60.4568 | 1.4211e-13 | -0.014397 | -0.0011645 | 0.063957 | -0.003064 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0077456 | 0.062914 | -58.4695 | -0.021486 | -61.014 | 60.3953 | 60.0667 | 60.1079 | -61.0543 | -60.9553 | 0.004938 | -61.0677 | 60.2185 | 60.3047 | 60.3217 | -61.1128 | -0.020702 | -0.061568 | 2.5641 | 0.019632 | 0.040334 | -0.39016 | -0.34893 | -0.079154 | -0.23838 | 0.078313 | -0.03403 | 0.045124 | -0.1521 | -0.13517 | 121.4289 | 121.1003 | 121.1416 | 61.0121 | -121.5112 | 121.2521 | 121.3384 | 121.3553 | 61.0386 | -121.5696
370.3594 | 121.7468 | -61.0016 | 60.4843 | 1.4211e-13 | -0.014611 | -0.00095092 | 0.063744 | -0.0034912 | 0.059888 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063844 | 0.007532 | 0.062701 | -58.4512 | -0.016908 | -61.0003 | 60.4182 | 60.0667 | 60.1125 | -61.0498 | -60.937 | 0.004938 | -61.0585 | 60.2322 | 60.3185 | 60.34 | -61.099 | -0.048166 | -0.066142 | 2.5504 | 0.001324 | 0.04949 | -0.41762 | -0.37181 | -0.097461 | -0.25211 | 0.064585 | -0.056915 | 0.040546 | -0.16583 | -0.14432 | 121.4198 | 121.0683 | 121.1141 | 60.9847 | -121.5341 | 121.2338 | 121.3201 | 121.3416 | 61.0065 | -121.5834
372.125 | 121.7331 | -61.0519 | 60.4477 | 1.4211e-13 | -0.014611 | -0.00095092 | 0.063744 | -0.003064 | 0.059888 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0073182 | 0.062701 | -58.3871 | -0.007751 | -61.0094 | 60.4136 | 60.0713 | 60.1033 | -61.0589 | -60.9462 | 0.000359 | -61.0585 | 60.223 | 60.3093 | 60.3263 | -61.1174 | -0.00697 | -0.0341 | 2.6648 | 0.042522 | 0.049492 | -0.37642 | -0.34435 | -0.065422 | -0.22465 | 0.10578 | -0.006561 | 0.058861 | -0.13837 | -0.12143 | 121.4655 | 121.1232 | 121.1553 | 61.0442 | -121.5066 | 121.275 | 121.3613 | 121.3782 | 61.0523 | -121.5651
373.8906 | 121.7972 | -60.965 | 60.4568 | 1.4211e-13 | -0.014611 | -0.00095092 | 0.063744 | -0.0032776 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.007532 | 0.062487 | -58.4833 | -0.016908 | -61.014 | 60.3999 | 60.0667 | 60.1125 | -61.0589 | -60.9416 | 0.000359 | -61.0585 | 60.223 | 60.3093 | 60.3263 | -61.1128 | -0.093945 | -0.05699 | 2.4817 | -0.049032 | 0.044913 | -0.39016 | -0.34435 | -0.14782 | -0.23381 | 0.023385 | -0.093536 | 0.054282 | -0.14753 | -0.13059 | 121.3648 | 121.0317 | 121.0775 | 60.9481 | -121.5158 | 121.188 | 121.2743 | 121.2912 | 60.9653 | -121.5696
375.5781 | 121.7194 | -61.0199 | 60.4797 | 1.4211e-13 | -0.015038 | -0.00073712 | 0.06353 | -0.0032776 | 0.060101 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.007532 | 0.062701 | -58.3963 | -0.016908 | -61.0048 | 60.409 | 60.085 | 60.1125 | -61.0543 | -60.9462 | 0.004938 | -61.0539 | 60.2276 | 60.3093 | 60.3308 | -61.1082 | -0.034435 | -0.070721 | 2.6236 | 0.015056 | 0.049491 | -0.39473 | -0.36723 | -0.088309 | -0.25212 | 0.073738 | -0.034027 | 0.054282 | -0.17041 | -0.1489 | 121.4289 | 121.1049 | 121.1324 | 61.003 | -121.5341 | 121.2475 | 121.3292 | 121.3507 | 61.0248 | -121.5879
377.3438 | 121.7514 | -61.0153 | 60.4797 | 1.4211e-13 | -0.014825 | -0.00095092 | 0.06353 | -0.0032776 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.007532 | 0.062914 | -58.3734 | -0.016908 | -60.9957 | 60.409 | 60.0804 | 60.1125 | -61.0589 | -60.9416 | 0.004938 | -61.0493 | 60.2276 | 60.3276 | 60.3354 | -61.1036 | -0.043591 | -0.070721 | 2.6419 | 0.019636 | 0.063227 | -0.39931 | -0.36723 | -0.088307 | -0.25212 | 0.073739 | -0.034025 | 0.054282 | -0.1521 | -0.14432 | 121.4243 | 121.0957 | 121.1278 | 60.9984 | -121.5386 | 121.2429 | 121.343 | 121.3507 | 61.0203 | -121.5834
379.1094 | 121.7651 | -61.0153 | 60.4706 | 1.4211e-13 | -0.014825 | -0.00073712 | 0.063744 | -0.003064 | 0.059888 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.007532 | 0.062914 | -58.4695 | -0.012329 | -60.9957 | 60.4136 | 60.0713 | 60.1125 | -61.0498 | -60.9416 | 0.000359 | -61.0493 | 60.2322 | 60.3185 | 60.3446 | -61.0945 | -0.034433 | -0.056988 | 2.5458 | 0.019636 | 0.054069 | -0.39931 | -0.35808 | -0.079149 | -0.23838 | 0.073739 | -0.034025 | 0.045124 | -0.1521 | -0.12601 | 121.4289 | 121.0866 | 121.1278 | 61.003 | -121.5203 | 121.2475 | 121.3338 | 121.3599 | 61.0157 | -121.565
380.7969 | 121.7148 | -61.0016 | 60.5026 | 1.4211e-13 | -0.014825 | -0.00095092 | 0.063744 | -0.0034912 | 0.059674 | -0.0099194 | 0.00055974 | -0.00026913 | 0.064272 | 0.007532 | 0.062914 | -58.4421 | -0.012329 | -60.9957 | 60.4044 | 60.0758 | 60.1033 | -61.0543 | -60.9462 | -0.00422 | -61.0402 | 60.2322 | 60.3231 | 60.34 | -61.099 | -0.052745 | -0.098189 | 2.5595 | 0.005903 | 0.058648 | -0.42678 | -0.39928 | -0.097461 | -0.27043 | 0.055428 | -0.038601 | 0.05886 | -0.17957 | -0.16263 | 121.406 | 121.0774 | 121.1049 | 60.9893 | -121.557 | 121.2338 | 121.3246 | 121.3416 | 60.9974 | -121.6017
382.5 | 121.6599 | -61.084 | 60.4431 | 1.4211e-13 | -0.014825 | -0.00073712 | 0.063957 | -0.003064 | 0.059674 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0073182 | 0.062701 | -58.3688 | -0.007751 | -60.9957 | 60.4182 | 60.085 | 60.1171 | -61.0498 | -60.9416 | 0.004938 | -61.0493 | 60.2322 | 60.3231 | 60.34 | -61.099 | 0.034231 | -0.024943 | 2.7152 | 0.0883 | 0.054069 | -0.35811 | -0.32603 | -0.015064 | -0.21092 | 0.1424 | 0.034639 | 0.049703 | -0.12006 | -0.10312 | 121.5022 | 121.169 | 121.2011 | 61.0762 | -121.4929 | 121.3162 | 121.407 | 121.424 | 61.0889 | -121.5422
384.2031 | 121.8063 | -61.0428 | 60.3745 | 1.4211e-13 | -0.014825 | -0.00095092 | 0.06353 | -0.003064 | 0.05946 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.007532 | 0.062701 | -58.4009 | -0.012329 | -61.0003 | 60.4136 | 60.0667 | 60.1079 | -61.0543 | -60.9462 | 0.009516 | -61.0539 | 60.223 | 60.3185 | 60.3308 | -61.1082 | -0.011546 | 0.039142 | 2.6419 | 0.042523 | 0.054069 | -0.30776 | -0.26653 | -0.06542 | -0.15141 | 0.096627 | -0.011138 | 0.054282 | -0.055971 | -0.043612 | 121.4564 | 121.1095 | 121.1507 | 61.0305 | -121.4288 | 121.2658 | 121.3613 | 121.3736 | 61.0523 | -121.4827
385.8906 | 121.788 | -60.9558 | 60.4706 | 1.4211e-13 | -0.015038 | -0.00073712 | 0.06353 | -0.0032776 | 0.060101 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064485 | 0.007532 | 0.062701 | -58.4512 | -0.016908 | -60.9911 | 60.4136 | 60.0713 | 60.1171 | -61.0452 | -60.9416 | 0.009516 | -61.0356 | 60.2368 | 60.3185 | 60.3446 | -61.099 | -0.089363 | -0.056988 | 2.5046 | -0.035295 | 0.054068 | -0.39931 | -0.3535 | -0.14324 | -0.2338 | 0.01423 | -0.079798 | 0.063439 | -0.1521 | -0.12601 | 121.3694 | 121.0271 | 121.0729 | 60.9389 | -121.5158 | 121.1926 | 121.2743 | 121.3004 | 60.9653 | -121.5696
387.5938 | 121.7468 | -61.0565 | 60.4019 | 1.4211e-13 | -0.014825 | -0.00073712 | 0.063957 | -0.003064 | 0.059888 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064272 | 0.0077456 | 0.063128 | -58.378 | -0.016908 | -60.9957 | 60.4136 | 60.0758 | 60.1171 | -61.0406 | -60.9324 | -0.00422 | -61.0402 | 60.2368 | 60.3276 | 60.3446 | -61.1036 | 0.015924 | 0.011676 | 2.6785 | 0.060835 | 0.044911 | -0.32607 | -0.28484 | -0.047108 | -0.16514 | 0.1241 | 0.016331 | 0.063439 | -0.07428 | -0.057342 | 121.4701 | 121.1324 | 121.1736 | 61.0396 | -121.4425 | 121.2933 | 121.3842 | 121.4011 | 61.0523 | -121.5055
389.2969 | 121.6873 | -61.0062 | 60.4935 | 1.4211e-13 | -0.014611 | -0.0011645 | 0.06353 | -0.0034912 | 0.060101 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.007532 | 0.062914 | -58.3871 | -0.021486 | -61.0048 | 60.3999 | 60.085 | 60.1125 | -61.0498 | -60.937 | 0.009516 | -61.0448 | 60.2276 | 60.3139 | 60.34 | -61.099 | -0.043588 | -0.093611 | 2.619 | 0.001324 | 0.044912 | -0.40846 | -0.38097 | -0.092883 | -0.26585 | 0.069163 | -0.038601 | 0.054282 | -0.17957 | -0.15347 | 121.406 | 121.0912 | 121.1187 | 60.9847 | -121.5432 | 121.2338 | 121.3201 | 121.3462 | 61.0157 | -121.5925
391.0469 | 121.6644 | -61.0565 | 60.4614 | 1.4211e-13 | -0.014825 | -0.00052352 | 0.063957 | -0.0032776 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.007532 | 0.062701 | -58.3551 | -0.012329 | -60.9865 | 60.4273 | 60.085 | 60.1217 | -61.036 | -60.9278 | 0.004938 | -61.0448 | 60.2414 | 60.3276 | 60.34 | -61.0945 | 0.020503 | -0.034098 | 2.7014 | 0.069991 | 0.049488 | -0.37642 | -0.33977 | -0.03795 | -0.22007 | 0.12868 | 0.011753 | 0.049703 | -0.13379 | -0.12143 | 121.4838 | 121.1415 | 121.1782 | 61.0442 | -121.4974 | 121.2979 | 121.3842 | 121.3965 | 61.0615 | -121.5559
392.7969 | 121.7102 | -61.0428 | 60.4523 | 1.4211e-13 | -0.014397 | -0.00095092 | 0.064171 | -0.0032776 | 0.059674 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064485 | 0.0073182 | 0.063128 | -58.3642 | -0.016908 | -60.9957 | 60.4136 | 60.0804 | 60.1217 | -61.0498 | -60.9416 | 0.000359 | -61.0402 | 60.2368 | 60.3276 | 60.34 | -61.099 | -0.006967 | -0.038678 | 2.6785 | 0.047102 | 0.054069 | -0.37184 | -0.33061 | -0.056262 | -0.21549 | 0.10121 | 0.002598 | 0.05886 | -0.12463 | -0.11228 | 121.4564 | 121.1232 | 121.1644 | 61.0259 | -121.502 | 121.2796 | 121.3704 | 121.3828 | 61.0431 | -121.5513
394.5 | 121.6644 | -61.1069 | 60.434 | 1.4211e-13 | -0.015038 | -0.00073712 | 0.063744 | -0.003064 | 0.059674 | 0.0053411 | -8.1262e-05 | -0.00048293 | 0.064485 | 0.007532 | 0.063555 | -58.3688 | -0.016908 | -60.9957 | 60.4182 | 60.0758 | 60.1217 | -61.036 | -60.9324 | 0.000359 | -61.0493 | 60.2414 | 60.3276 | 60.3537 | -61.0945 | 0.070857 | -0.015788 | 2.7381 | 0.11119 | 0.040332 | -0.35811 | -0.3123 | 0.012404 | -0.1926 | 0.17445 | 0.057528 | 0.045124 | -0.10632 | -0.080228 | 121.525 | 121.1827 | 121.2285 | 61.09 | -121.47 | 121.3482 | 121.4345 | 121.4606 | 61.1072 | -121.5284
396.25 | 121.7972 | -61.0245 | 60.3928 | 1.4211e-13 | -0.015038 | -0.00073712 | 0.063957 | -0.003064 | 0.059674 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.0077456 | 0.063342 | -58.4192 | -0.016908 | -60.9865 | 60.4182 | 60.0758 | 60.1308 | -61.0314 | -60.9278 | 0.000359 | -61.0402 | 60.2368 | 60.3276 | 60.3492 | -61.0899 | -0.006963 | 0.025411 | 2.6053 | 0.037947 | 0.04491 | -0.31691 | -0.26194 | -0.065415 | -0.15598 | 0.096631 | -0.015713 | 0.049702 | -0.065124 | -0.043608 | 121.4426 | 121.1003 | 121.1553 | 61.0076 | -121.4242 | 121.2613 | 121.3521 | 121.3736 | 61.0248 | -121.4827
398.0156 | 121.7056 | -60.9924 | 60.498 | 1.4211e-13 | -0.014611 | -0.00073712 | 0.063957 | -0.0034912 | 0.060101 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064272 | 0.007532 | 0.063342 | -58.4283 | -0.007751 | -60.9957 | 60.4228 | 60.0804 | 60.1262 | -61.0452 | -60.9324 | 0.000359 | -61.0402 | 60.2322 | 60.3185 | 60.3354 | -61.0945 | -0.052742 | -0.075297 | 2.5641 | -0.003252 | 0.04949 | -0.41762 | -0.37181 | -0.10204 | -0.26585 | 0.060009 | -0.047756 | 0.054281 | -0.17957 | -0.16263 | 121.4152 | 121.0729 | 121.1187 | 60.9847 | -121.5432 | 121.2246 | 121.3109 | 121.3278 | 60.9928 | -121.5925
399.7344 | 121.8018 | -60.965 | 60.434 | 1.4211e-13 | -0.015038 | -0.00052352 | 0.063744 | -0.003064 | 0.059888 | -0.0022889 | 0.00055974 | -0.00026913 | 0.064272 | 0.0079592 | 0.063342 | -58.4741 | -0.021486 | -60.9865 | 60.4182 | 60.0758 | 60.1262 | -61.0452 | -60.9278 | 0.009516 | -61.0402 | 60.2368 | 60.3231 | 60.3446 | -61.0945 | -0.080208 | -0.015788 | 2.4908 | -0.021562 | 0.058646 | -0.35811 | -0.30772 | -0.1295 | -0.19718 | 0.037122 | -0.075222 | 0.054281 | -0.1109 | -0.089385 | 121.3831 | 121.0408 | 121.0912 | 60.9435 | -121.4791 | 121.2017 | 121.288 | 121.3095 | 60.9745 | -121.5284
401.5 | 121.8018 | -60.9512 | 60.498 | 1.4211e-13 | -0.015038 | -0.00073712 | 0.064171 | -0.0034912 | 0.059888 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.063128 | -58.4512 | -0.016908 | -60.9682 | 60.4319 | 60.0987 | 60.14 | -61.0269 | -60.9187 | 0.004938 | -61.031 | 60.2505 | 60.3322 | 60.3537 | -61.0807 | -0.075626 | -0.06614 | 2.5 | -0.016982 | 0.058644 | -0.3993 | -0.35807 | -0.1295 | -0.24753 | 0.032546 | -0.079797 | 0.049703 | -0.16583 | -0.14431 | 121.3831 | 121.05 | 121.0912 | 60.9343 | -121.5249 | 121.2017 | 121.2834 | 121.305 | 60.9562 | -121.5788
403.2031 | 121.7514 | -61.0107 | 60.4385 | 1.4211e-13 | -0.014825 | -0.00073712 | 0.064385 | -0.0034912 | 0.059888 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0077456 | 0.063128 | -58.4054 | -0.016908 | -60.9774 | 60.4228 | 60.0804 | 60.1308 | -61.0269 | -60.9187 | 0.004938 | -61.0219 | 60.2551 | 60.3414 | 60.3583 | -61.0762 | -0.016117 | -0.015788 | 2.6053 | 0.033371 | 0.049488 | -0.35811 | -0.30772 | -0.065412 | -0.18345 | 0.092055 | -0.011131 | 0.054281 | -0.097165 | -0.080228 | 121.4335 | 121.0912 | 121.1416 | 60.9938 | -121.4654 | 121.2658 | 121.3521 | 121.3691 | 61.0157 | -121.5147
404.9688 | 121.8018 | -61.0062 | 60.3882 | 1.4211e-13 | -0.015038 | -0.00052352 | 0.063744 | -0.0032776 | 0.059674 | 0.012972 | 0.00055974 | -0.00026913 | 0.064272 | 0.007532 | 0.063342 | -58.3826 | -0.007751 | -60.9774 | 60.4228 | 60.0896 | 60.1354 | -61.0314 | -60.9187 | 0.009516 | -61.0173 | 60.2505 | 60.3368 | 60.3583 | -61.0807 | -0.025273 | 0.034566 | 2.6236 | 0.028794 | 0.054067 | -0.2986 | -0.25279 | -0.074568 | -0.13767 | 0.087478 | -0.011129 | 0.063439 | -0.051389 | -0.029874 | 121.4289 | 121.0958 | 121.1416 | 60.9984 | -121.4196 | 121.2567 | 121.343 | 121.3645 | 61.0157 | -121.4689
406.6562 | 121.6599 | -60.9741 | 60.5347 | 1.4211e-13 | -0.014397 | -0.00073712 | 0.06353 | -0.0032776 | 0.059674 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0077456 | 0.063128 | -58.4009 | -0.016908 | -60.9728 | 60.4273 | 60.0942 | 60.1354 | -61.0223 | -60.9187 | 0.009516 | -61.0265 | 60.2505 | 60.3414 | 60.3583 | -61.0807 | -0.048159 | -0.10734 | 2.5733 | 0.001328 | 0.049487 | -0.4405 | -0.39927 | -0.10661 | -0.28416 | 0.055434 | -0.052331 | 0.054281 | -0.1933 | -0.17636 | 121.4014 | 121.0683 | 121.1095 | 60.9572 | -121.5569 | 121.2246 | 121.3155 | 121.3324 | 60.9836 | -121.6154
408.4219 | 121.6553 | -60.9833 | 60.5072 | 1.4211e-13 | -0.015038 | -0.00095092 | 0.063744 | -0.0032776 | 0.059674 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064485 | 0.0077456 | 0.063128 | -58.378 | -0.003172 | -60.9774 | 60.4365 | 60.0942 | 60.14 | -61.0131 | -60.9141 | 0.009516 | -61.0219 | 60.2551 | 60.3414 | 60.3675 | -61.0762 | -0.029846 | -0.070717 | 2.6053 | 0.005905 | 0.035751 | -0.41304 | -0.36723 | -0.092878 | -0.25211 | 0.069168 | -0.038597 | 0.054281 | -0.16583 | -0.13973 | 121.4198 | 121.0774 | 121.1232 | 60.9801 | -121.5203 | 121.2384 | 121.3246 | 121.3507 | 60.9928 | -121.5834
410.125 | 121.6827 | -61.0062 | 60.5164 | 1.4211e-13 | -0.014825 | -0.00095092 | 0.063957 | -0.003064 | 0.059888 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064272 | 0.0077456 | 0.063342 | -58.41 | -0.016908 | -60.9728 | 60.4319 | 60.0942 | 60.14 | -61.0269 | -60.9095 | 0.000359 | -61.0173 | 60.2551 | 60.3322 | 60.3583 | -61.0716 | -0.020694 | -0.08445 | 2.5961 | 0.033372 | 0.054066 | -0.42219 | -0.37638 | -0.06541 | -0.26127 | 0.096635 | -0.011129 | 0.054281 | -0.18414 | -0.15805 | 121.4381 | 121.1003 | 121.1461 | 60.9893 | -121.5432 | 121.2613 | 121.3384 | 121.3645 | 61.0065 | -121.5879
411.875 | 121.6736 | -61.0199 | 60.4568 | 1.4211e-13 | -0.014825 | -0.00095092 | 0.06353 | -0.0034912 | 0.059674 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064485 | 0.0077456 | 0.063555 | -58.3551 | -0.012329 | -60.9774 | 60.4319 | 60.0942 | 60.14 | -61.0269 | -60.9141 | 0.018674 | -61.031 | 60.2551 | 60.3368 | 60.3675 | -61.0762 | -0.006962 | -0.024941 | 2.6648 | 0.042526 | 0.049488 | -0.36268 | -0.31688 | -0.056257 | -0.20176 | 0.10579 | -0.011133 | 0.045124 | -0.12005 | -0.08938 | 121.4518 | 121.1141 | 121.1599 | 61.0076 | -121.4837 | 121.275 | 121.3567 | 121.3874 | 61.0386 | -121.533
413.5781 | 121.6827 | -60.9879 | 60.4843 | 1.4211e-13 | -0.015038 | -0.0011645 | 0.063744 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.0073182 | 0.063342 | -58.3276 | -0.016908 | -60.9636 | 60.4456 | 60.1125 | 60.1583 | -61.0131 | -60.8958 | 0.009516 | -61.0127 | 60.2688 | 60.3505 | 60.372 | -61.0624 | -0.025268 | -0.038672 | 2.6602 | 0.024218 | 0.049486 | -0.37183 | -0.32603 | -0.074563 | -0.21549 | 0.092061 | -0.024861 | 0.049702 | -0.13378 | -0.11227 | 121.4335 | 121.1003 | 121.1461 | 60.9709 | -121.4974 | 121.2567 | 121.3384 | 121.3599 | 60.9974 | -121.5467
415.3438 | 121.6553 | -61.0611 | 60.4752 | 1.4211e-13 | -0.015038 | -0.00095092 | 0.06353 | -0.0032776 | 0.059888 | 0.012972 | 0.00055974 | 0.00015807 | 0.063844 | 0.0077456 | 0.063128 | -58.3413 | -0.012329 | -60.9682 | 60.4456 | 60.1171 | 60.1537 | -61.0085 | -60.9095 | 0.014095 | -61.0127 | 60.2688 | 60.3597 | 60.3766 | -61.0578 | 0.052553 | -0.029517 | 2.7197 | 0.092881 | 0.040328 | -0.3581 | -0.32145 | 0.003257 | -0.20633 | 0.15157 | 0.048381 | 0.045124 | -0.11547 | -0.098534 | 121.5067 | 121.1782 | 121.2148 | 61.0488 | -121.4837 | 121.3299 | 121.4208 | 121.4377 | 61.0752 | -121.533
417.1094 | 121.6644 | -60.9787 | 60.5804 | 1.4211e-13 | -0.015252 | -0.00052352 | 0.063744 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.007532 | 0.062914 | -58.3871 | -0.016908 | -60.9682 | 60.4319 | 60.0987 | 60.1446 | -61.0223 | -60.9095 | 0.004938 | -61.0219 | 60.2551 | 60.3414 | 60.372 | -61.067 | -0.043581 | -0.14854 | 2.5916 | 0.010484 | 0.054065 | -0.4817 | -0.43589 | -0.088297 | -0.32535 | 0.069169 | -0.043174 | 0.045123 | -0.23907 | -0.2084 | 121.4106 | 121.0774 | 121.1233 | 60.9618 | -121.6027 | 121.2338 | 121.3201 | 121.3507 | 60.9836 | -121.6474
418.8594 | 121.7926 | -60.9924 | 60.3973 | 1.4211e-13 | -0.015252 | -0.00095092 | 0.06353 | -0.0034912 | 0.060101 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.007532 | 0.062701 | -58.3734 | -0.007751 | -60.9728 | 60.4365 | 60.0896 | 60.1446 | -61.0223 | -60.905 | 0.018674 | -61.0219 | 60.2505 | 60.3414 | 60.3629 | -61.0762 | -0.029848 | 0.039146 | 2.619 | 0.019639 | 0.049487 | -0.30775 | -0.25279 | -0.083722 | -0.14683 | 0.087481 | -0.029441 | 0.054281 | -0.055966 | -0.03445 | 121.4289 | 121.082 | 121.137 | 60.9847 | -121.4196 | 121.2429 | 121.3338 | 121.3553 | 61.0111 | -121.4735
420.5625 | 121.6644 | -60.9329 | 60.553 | 1.4211e-13 | -0.015252 | -0.00095092 | 0.063744 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.063342 | -58.3551 | -0.012329 | -60.9499 | 60.4502 | 60.1216 | 60.1629 | -61.004 | -60.8866 | 0.014095 | -61.0036 | 60.278 | 60.3597 | 60.3766 | -61.0487 | -0.071042 | -0.10276 | 2.5778 | -0.01698 | 0.054062 | -0.43134 | -0.39011 | -0.11576 | -0.275 | 0.046286 | -0.070636 | 0.045123 | -0.19329 | -0.17635 | 121.3831 | 121.0546 | 121.0958 | 60.9206 | -121.5569 | 121.2109 | 121.2926 | 121.3095 | 60.947 | -121.6017
422.3125 | 121.6965 | -60.9833 | 60.5164 | 1.4211e-13 | -0.015252 | -0.00073712 | 0.06353 | -0.0034912 | 0.060101 | -0.0022889 | 0.00013254 | -0.00048293 | 0.064272 | 0.0077456 | 0.063128 | -58.3505 | -0.012329 | -60.9591 | 60.4365 | 60.1125 | 60.1446 | -61.0131 | -60.9004 | 0.014095 | -61.0127 | 60.2597 | 60.3505 | 60.3675 | -61.067 | -0.029846 | -0.079872 | 2.6328 | 0.024218 | 0.054064 | -0.40388 | -0.37181 | -0.08372 | -0.25669 | 0.082904 | -0.029439 | 0.054281 | -0.16583 | -0.14889 | 121.4198 | 121.0958 | 121.1278 | 60.9709 | -121.5295 | 121.2429 | 121.3338 | 121.3507 | 60.9974 | -121.5834
424.0781 | 121.6599 | -61.0382 | 60.5026 | 1.4211e-13 | -0.015252 | -0.00073712 | 0.063744 | -0.0034912 | 0.059674 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0077456 | 0.063128 | -58.3276 | -0.016908 | -60.9591 | 60.4456 | 60.1079 | 60.1537 | -61.0085 | -60.9004 | 0.014095 | -61.0127 | 60.2642 | 60.3505 | 60.3766 | -61.067 | 0.029665 | -0.056983 | 2.7106 | 0.07915 | 0.049485 | -0.39472 | -0.34892 | -0.028788 | -0.23838 | 0.13784 | 0.025493 | 0.054281 | -0.1521 | -0.126 | 121.4838 | 121.1461 | 121.1919 | 61.0213 | -121.5112 | 121.3025 | 121.3887 | 121.4148 | 61.0523 | -121.5696
425.7656 | 121.8018 | -60.997 | 60.4385 | 1.4211e-13 | -0.015252 | -0.00073712 | 0.063316 | -0.0032776 | 0.059888 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.008173 | 0.062914 | -58.3459 | -0.016908 | -60.9591 | 60.4548 | 60.1216 | 60.1583 | -60.9994 | -60.8912 | 0.014095 | -60.9944 | 60.278 | 60.3643 | 60.3812 | -61.0533 | -0.002376 | 0.016261 | 2.6511 | 0.037951 | 0.040327 | -0.3169 | -0.28025 | -0.056251 | -0.16055 | 0.10579 | 0.002608 | 0.058859 | -0.074272 | -0.057335 | 121.4518 | 121.1186 | 121.1553 | 60.9801 | -121.4379 | 121.275 | 121.3613 | 121.3782 | 61.0111 | -121.4918
427.4688 | 121.8246 | -60.9512 | 60.498 | 1.4211e-13 | -0.015252 | -0.00073712 | 0.06353 | -0.0032776 | 0.059674 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064272 | 0.0077456 | 0.063342 | -58.4238 | -0.016908 | -60.9407 | 60.464 | 60.1216 | 60.1674 | -60.9994 | -60.8866 | 0.009516 | -60.9944 | 60.2734 | 60.3643 | 60.3858 | -61.0487 | -0.048152 | -0.034091 | 2.5275 | 0.010488 | 0.05864 | -0.37641 | -0.3306 | -0.097448 | -0.22464 | 0.064597 | -0.043168 | 0.05428 | -0.13378 | -0.11227 | 121.4152 | 121.0729 | 121.1187 | 60.9343 | -121.4974 | 121.2246 | 121.3155 | 121.337 | 60.9607 | -121.5467
429.25 | 121.7651 | -60.9787 | 60.4935 | 1.4211e-13 | -0.015466 | -0.00073712 | 0.063744 | -0.0032776 | 0.060101 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064058 | 0.0077456 | 0.062914 | -58.4238 | -0.012329 | -60.9636 | 60.4411 | 60.1033 | 60.1674 | -61.0085 | -60.8912 | 0.014095 | -60.999 | 60.2734 | 60.3597 | 60.372 | -61.0578 | -0.029844 | -0.052405 | 2.5549 | 0.015063 | 0.044907 | -0.39015 | -0.32602 | -0.07914 | -0.22006 | 0.087484 | -0.02028 | 0.05886 | -0.13378 | -0.12142 | 121.4198 | 121.082 | 121.1461 | 60.9664 | -121.502 | 121.2521 | 121.3384 | 121.3507 | 60.9928 | -121.5513
430.9531 | 121.7102 | -60.9558 | 60.5164 | 1.4211e-13 | -0.015466 | -0.00095092 | 0.063744 | -0.0032776 | 0.05946 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0079592 | 0.063128 | -58.3276 | -0.016908 | -60.9591 | 60.4456 | 60.1216 | 60.1537 | -61.004 | -60.8912 | 0.014095 | -60.9944 | 60.278 | 60.3597 | 60.3766 | -61.0533 | -0.048153 | -0.070715 | 2.6282 | -0.003247 | 0.044906 | -0.39472 | -0.36265 | -0.097449 | -0.23837 | 0.064596 | -0.03859 | 0.058859 | -0.15667 | -0.13973 | 121.4015 | 121.0774 | 121.1095 | 60.9389 | -121.5203 | 121.2338 | 121.3155 | 121.3324 | 60.9699 | -121.5696
432.6562 | 121.6736 | -61.0474 | 60.4889 | 1.4211e-13 | -0.015679 | -0.00095092 | 0.06353 | -0.0034912 | 0.05946 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0077456 | 0.062914 | -58.323 | -0.016908 | -60.9591 | 60.4594 | 60.1171 | 60.1583 | -60.9994 | -60.8821 | 0.018674 | -60.999 | 60.2734 | 60.3688 | 60.3812 | -61.0487 | 0.047978 | -0.029515 | 2.7243 | 0.088305 | 0.040327 | -0.37183 | -0.3306 | -0.001318 | -0.21549 | 0.16531 | 0.048384 | 0.049702 | -0.12005 | -0.10769 | 121.5067 | 121.1644 | 121.2057 | 61.0305 | -121.4883 | 121.3208 | 121.4162 | 121.4286 | 61.066 | -121.5376
434.4375 | 121.6827 | -60.9467 | 60.5896 | 1.4211e-13 | -0.015679 | -0.00052352 | 0.06353 | -0.0032776 | 0.059674 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.063128 | -58.3734 | -0.012329 | -60.9591 | 60.4548 | 60.1171 | 60.1629 | -60.9994 | -60.8866 | 0.009516 | -60.999 | 60.2688 | 60.3643 | 60.3858 | -61.0487 | -0.05273 | -0.1348 | 2.5733 | -0.012403 | 0.040327 | -0.47254 | -0.42673 | -0.10203 | -0.32077 | 0.060019 | -0.052324 | 0.049702 | -0.22533 | -0.20382 | 121.4015 | 121.0637 | 121.1095 | 60.9343 | -121.589 | 121.2155 | 121.3109 | 121.3324 | 60.9562 | -121.6383
436.2031 | 121.6873 | -61.0245 | 60.498 | 1.4211e-13 | -0.015252 | -0.0013783 | 0.063744 | -0.0034912 | 0.059888 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064485 | 0.0077456 | 0.062914 | -58.3368 | -0.021486 | -60.9636 | 60.4411 | 60.1079 | 60.1629 | -61.004 | -60.8958 | 0.014095 | -61.0036 | 60.2642 | 60.3551 | 60.372 | -61.0533 | 0.020511 | -0.056983 | 2.6877 | 0.060839 | 0.040328 | -0.39015 | -0.33518 | -0.028785 | -0.2338 | 0.12868 | 0.020917 | 0.049702 | -0.14294 | -0.126 | 121.4655 | 121.1324 | 121.1873 | 61.003 | -121.502 | 121.2887 | 121.3796 | 121.3965 | 61.0386 | -121.5513
437.8906 | 121.8063 | -60.9421 | 60.4843 | 1.4211e-13 | -0.015466 | -0.0011645 | 0.063316 | -0.0032776 | 0.05946 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064485 | 0.0077456 | 0.063342 | -58.4467 | -0.016908 | -60.9636 | 60.4456 | 60.1033 | 60.1446 | -61.0085 | -60.8958 | 0.018674 | -61.0081 | 60.2597 | 60.346 | 60.3766 | -61.0533 | -0.066465 | -0.038672 | 2.4954 | -0.021558 | 0.044907 | -0.38099 | -0.33976 | -0.11118 | -0.22464 | 0.046285 | -0.066059 | 0.045123 | -0.13836 | -0.10769 | 121.3877 | 121.0454 | 121.0866 | 60.9252 | -121.4929 | 121.2017 | 121.288 | 121.3187 | 60.9608 | -121.5376
439.5938 | 121.8018 | -60.9421 | 60.498 | 1.4211e-13 | -0.015466 | -0.00052352 | 0.063744 | -0.0032776 | 0.059888 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0077456 | 0.063128 | -58.4558 | -0.021486 | -60.9636 | 60.4411 | 60.1033 | 60.1491 | -61.0177 | -60.9095 | 0.014095 | -61.0081 | 60.2597 | 60.3505 | 60.3629 | -61.0716 | -0.075623 | -0.056983 | 2.4863 | -0.021558 | 0.054065 | -0.39472 | -0.34892 | -0.1295 | -0.23838 | 0.032548 | -0.066059 | 0.063438 | -0.14752 | -0.13516 | 121.3831 | 121.0454 | 121.0912 | 60.9206 | -121.5157 | 121.2017 | 121.2926 | 121.305 | 60.9562 | -121.5696
441.3438 | 121.7834 | -61.0016 | 60.4385 | 1.4211e-13 | -0.015679 | -0.00052352 | 0.06353 | -0.003705 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064485 | 0.0077456 | 0.062914 | -58.3368 | -0.012329 | -60.9407 | 60.4594 | 60.1216 | 60.172 | -60.9902 | -60.8775 | 0.018674 | -60.999 | 60.2826 | 60.3688 | 60.3904 | -61.0441 | 0.01136 | 0.020839 | 2.6648 | 0.060842 | 0.049482 | -0.3169 | -0.26651 | -0.042515 | -0.15597 | 0.12411 | 0.002608 | 0.045123 | -0.069693 | -0.048177 | 121.461 | 121.1232 | 121.1736 | 60.9893 | -121.4288 | 121.2842 | 121.3704 | 121.3919 | 61.0203 | -121.4826
443.1094 | 121.7743 | -60.9375 | 60.5026 | 1.4211e-13 | -0.015893 | -0.00073712 | 0.06353 | -0.003064 | 0.05946 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063844 | 0.0077456 | 0.062701 | -58.4192 | -0.021486 | -60.9453 | 60.464 | 60.1262 | 60.1629 | -60.9948 | -60.8775 | 0.023253 | -60.9944 | 60.2734 | 60.3643 | 60.3904 | -61.0441 | -0.057306 | -0.038669 | 2.5183 | -0.007823 | 0.049483 | -0.37641 | -0.33976 | -0.1066 | -0.22922 | 0.060021 | -0.056901 | 0.049701 | -0.13836 | -0.11226 | 121.4015 | 121.0637 | 121.1004 | 60.916 | -121.4974 | 121.2109 | 121.3018 | 121.3279 | 60.9608 | -121.5467
444.8125 | 121.756 | -60.9283 | 60.5072 | 1.4211e-13 | -0.015679 | -0.00095092 | 0.063744 | -0.0032776 | 0.059674 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0079592 | 0.062914 | -58.3734 | -0.021486 | -60.9316 | 60.4685 | 60.1354 | 60.1812 | -60.9765 | -60.8729 | 0.018674 | -60.9852 | 60.2871 | 60.3688 | 60.3995 | -61.0395 | -0.048145 | -0.038668 | 2.5549 | -0.003244 | 0.044901 | -0.37183 | -0.32602 | -0.11118 | -0.22006 | 0.055445 | -0.056898 | 0.05428 | -0.13836 | -0.10768 | 121.3969 | 121.0637 | 121.1095 | 60.9069 | -121.4837 | 121.2155 | 121.2972 | 121.3279 | 60.947 | -121.5467
446.5781 | 121.8292 | -60.9146 | 60.5072 | 1.4211e-13 | -0.015466 | -0.00052352 | 0.06353 | -0.0034912 | 0.05946 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.0077456 | 0.062914 | -58.4146 | -0.030644 | -60.9407 | 60.4685 | 60.1308 | 60.172 | -60.9811 | -60.8729 | 0.018674 | -60.9852 | 60.2826 | 60.378 | 60.3949 | -61.0395 | -0.066457 | -0.038668 | 2.5 | -0.026133 | 0.040324 | -0.37641 | -0.33518 | -0.12491 | -0.22464 | 0.041712 | -0.070631 | 0.05428 | -0.1292 | -0.11226 | 121.3831 | 121.0454 | 121.0866 | 60.884 | -121.4883 | 121.1972 | 121.2926 | 121.3096 | 60.9333 | -121.5467
448.3438 | 121.7056 | -60.9558 | 60.5438 | 1.4211e-13 | -0.015466 | -0.00073712 | 0.06353 | -0.0032776 | 0.059674 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0079592 | 0.062914 | -58.3047 | -0.021486 | -60.9224 | 60.4777 | 60.1491 | 60.1949 | -60.9719 | -60.8592 | 0.018674 | -60.9669 | 60.2917 | 60.3872 | 60.4133 | -61.0304 | -0.016101 | -0.066132 | 2.6511 | 0.033379 | 0.04948 | -0.39471 | -0.34891 | -0.074555 | -0.2521 | 0.096647 | -0.011117 | 0.063438 | -0.15666 | -0.13057 | 121.4335 | 121.1049 | 121.1507 | 60.9343 | -121.5157 | 121.2475 | 121.343 | 121.3691 | 60.9745 | -121.5742
450.1094 | 121.788 | -60.8734 | 60.5804 | 1.4211e-13 | -0.015679 | -0.0011645 | 0.063316 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064058 | 0.008173 | 0.063128 | -58.3826 | -0.016908 | -60.9133 | 60.4914 | 60.1583 | 60.1995 | -60.9582 | -60.8454 | 0.023253 | -60.9532 | 60.31 | 60.4055 | 60.4224 | -61.0121 | -0.084762 | -0.089018 | 2.4909 | -0.039862 | 0.0449 | -0.42217 | -0.38095 | -0.13864 | -0.27041 | 0.027985 | -0.079779 | 0.058858 | -0.17497 | -0.15803 | 121.3648 | 121.0317 | 121.0729 | 60.8565 | -121.5386 | 121.1834 | 121.2789 | 121.2958 | 60.8967 | -121.5925
451.8594 | 121.8201 | -60.8505 | 60.5988 | 1.4211e-13 | -0.015893 | -0.0011645 | 0.063744 | -0.0034912 | 0.059888 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064699 | 0.0079592 | 0.062701 | -58.3505 | -0.016908 | -60.8812 | 60.5281 | 60.1903 | 60.2499 | -60.917 | -60.8088 | 0.03241 | -60.9257 | 60.3558 | 60.4375 | 60.4499 | -60.9754 | -0.066439 | -0.070702 | 2.5 | -0.030702 | 0.035737 | -0.40843 | -0.34889 | -0.1249 | -0.24294 | 0.041727 | -0.075195 | 0.0497 | -0.16123 | -0.14887 | 121.3786 | 121.0408 | 121.1004 | 60.8336 | -121.5157 | 121.2063 | 121.288 | 121.3004 | 60.8829 | -121.5742
453.5625 | 121.8018 | -60.7956 | 60.6079 | 1.4211e-13 | -0.016107 | -0.00073712 | 0.06353 | -0.003064 | 0.059888 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0079592 | 0.062701 | -58.323 | -0.003172 | -60.8446 | 60.5555 | 60.2178 | 60.2728 | -60.8849 | -60.7722 | 0.023253 | -60.8937 | 60.3787 | 60.465 | 60.4865 | -60.9479 | -0.089319 | -0.052387 | 2.4726 | -0.049008 | 0.040311 | -0.39011 | -0.33516 | -0.15235 | -0.2292 | 0.023425 | -0.098076 | 0.054278 | -0.14291 | -0.1214 | 121.3511 | 121.0134 | 121.0683 | 60.7924 | -121.4928 | 121.1743 | 121.2606 | 121.2821 | 60.8188 | -121.5559
455.3125 | 121.8109 | -60.7498 | 60.6949 | 1.4211e-13 | -0.015893 | -0.00030992 | 0.063316 | -0.003064 | 0.059674 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.008173 | 0.062701 | -58.2635 | -0.012329 | -60.7897 | 60.6196 | 60.2911 | 60.3323 | -60.8254 | -60.7126 | 0.018674 | -60.8296 | 60.452 | 60.5337 | 60.5506 | -60.8793 | -0.075569 | -0.075264 | 2.4863 | -0.039845 | 0.035724 | -0.40383 | -0.36261 | -0.12945 | -0.24292 | 0.037172 | -0.07975 | 0.049698 | -0.16121 | -0.14427 | 121.3694 | 121.0409 | 121.0821 | 60.7375 | -121.5203 | 121.2018 | 121.2835 | 121.3004 | 60.7685 | -121.5742
457.0625 | 121.7926 | -60.6583 | 60.7681 | 1.4211e-13 | -0.015679 | -0.0011645 | 0.063744 | -0.0032776 | 0.059674 | -0.0022889 | 0.00013254 | -0.00026913 | 0.064058 | 0.0079592 | 0.062701 | -58.1491 | -0.016908 | -60.6752 | 60.7295 | 60.3964 | 60.4422 | -60.7246 | -60.6073 | 0.018674 | -60.7243 | 60.5573 | 60.6344 | 60.6559 | -60.7785 | -0.066386 | -0.038625 | 2.5092 | -0.016941 | 0.049445 | -0.37175 | -0.32597 | -0.12027 | -0.21086 | 0.050929 | -0.065993 | 0.054274 | -0.13372 | -0.11221 | 121.3878 | 121.0546 | 121.1004 | 60.6414 | -121.4928 | 121.2155 | 121.2927 | 121.3142 | 60.6769 | -121.5467
458.75 | 121.6644 | -60.6079 | 60.8826 | 1.4211e-13 | -0.015893 | -0.00052352 | 0.06353 | -0.003064 | 0.059674 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064272 | 0.0083866 | 0.062914 | -58.0163 | -0.016908 | -60.6157 | 60.789 | 60.4605 | 60.4925 | -60.6605 | -60.5478 | 0.023253 | -60.6647 | 60.6122 | 60.6985 | 60.72 | -60.719 | -0.052635 | -0.093547 | 2.5916 | -0.007777 | 0.044858 | -0.42209 | -0.39004 | -0.1111 | -0.27035 | 0.060099 | -0.056823 | 0.054273 | -0.18406 | -0.16255 | 121.3969 | 121.0684 | 121.1004 | 60.591 | -121.5431 | 121.2201 | 121.3064 | 121.3279 | 60.6312 | -121.6016
460.5 | 121.6736 | -60.6125 | 60.8826 | 1.4211e-13 | -0.015679 | -0.00095092 | 0.063744 | -0.0032776 | 0.059674 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064699 | 0.0077456 | 0.062914 | -57.998 | -0.021486 | -60.6157 | 60.7982 | 60.4651 | 60.5017 | -60.656 | -60.5432 | 0.027831 | -60.6556 | 60.6122 | 60.7031 | 60.7246 | -60.7098 | -0.043478 | -0.08439 | 2.6145 | -0.003199 | 0.040279 | -0.41751 | -0.38088 | -0.097361 | -0.27035 | 0.069255 | -0.043088 | 0.054273 | -0.17948 | -0.15797 | 121.4107 | 121.0775 | 121.1142 | 60.591 | -121.5385 | 121.2247 | 121.3156 | 121.3371 | 60.6403 | -121.5924
462.2656 | 121.6736 | -60.5667 | 60.9787 | 1.4211e-13 | -0.015893 | -0.00095092 | 0.063744 | -0.0032776 | 0.059674 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064058 | 0.008173 | 0.062914 | -57.943 | -0.016908 | -60.5562 | 60.8531 | 60.52 | 60.5658 | -60.5964 | -60.4837 | 0.027831 | -60.5961 | 60.6763 | 60.7672 | 60.7795 | -60.6549 | -0.029729 | -0.12558 | 2.6237 | 0.010541 | 0.04027 | -0.45869 | -0.41292 | -0.088192 | -0.30239 | 0.083001 | -0.029342 | 0.05885 | -0.21152 | -0.19916 | 121.4198 | 121.0867 | 121.1325 | 60.5498 | -121.5751 | 121.243 | 121.3339 | 121.3463 | 60.5945 | -121.6336
464.0156 | 121.6644 | -60.5438 | 60.9787 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.063957 | -0.0034912 | 0.059888 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064485 | 0.008173 | 0.062914 | -57.9476 | -0.016908 | -60.5379 | 60.8623 | 60.5383 | 60.5704 | -60.5827 | -60.4791 | 0.027831 | -60.5823 | 60.6809 | 60.7809 | 60.7979 | -60.6366 | -0.03888 | -0.11642 | 2.5962 | 0.005967 | 0.044847 | -0.44038 | -0.40834 | -0.092764 | -0.29781 | 0.064692 | -0.038494 | 0.05427 | -0.19778 | -0.18084 | 121.4061 | 121.0821 | 121.1142 | 60.5269 | -121.5614 | 121.2247 | 121.3247 | 121.3417 | 60.5717 | -121.6153
465.7031 | 121.6736 | -60.553 | 60.9238 | 1.4211e-13 | -0.015893 | -0.0011645 | 0.063957 | -0.0032776 | 0.059674 | 0.0053411 | 0.00013254 | -0.00026913 | 0.064485 | 0.0079592 | 0.063342 | -57.8652 | -0.012329 | -60.4967 | 60.9126 | 60.575 | 60.6207 | -60.5415 | -60.4196 | 0.023253 | -60.5457 | 60.7267 | 60.8175 | 60.8345 | -60.5862 | 0.011486 | -0.011129 | 2.6878 | 0.056327 | 0.044841 | -0.34881 | -0.30304 | -0.033241 | -0.19709 | 0.13337 | 0.007292 | 0.040533 | -0.10622 | -0.089282 | 121.4656 | 121.1279 | 121.1737 | 60.5406 | -121.4653 | 121.2797 | 121.3705 | 121.3875 | 60.5762 | -121.51
467.4531 | 121.6782 | -60.5164 | 61.0062 | 1.4211e-13 | -0.015466 | -0.00095092 | 0.063744 | -0.0032776 | 0.059888 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.008173 | 0.062487 | -57.8011 | -0.016908 | -60.4417 | 60.9584 | 60.6345 | 60.6802 | -60.482 | -60.3692 | 0.027831 | -60.4816 | 60.7954 | 60.8816 | 60.8986 | -60.5313 | 0.03439 | -0.047744 | 2.7153 | 0.074644 | 0.040254 | -0.37169 | -0.32592 | -0.014918 | -0.21081 | 0.14711 | 0.034772 | 0.04969 | -0.12452 | -0.10758 | 121.4748 | 121.1508 | 121.1966 | 60.4994 | -121.4881 | 121.3117 | 121.398 | 121.4149 | 60.5442 | -121.5374
469.2031 | 121.7056 | -60.4202 | 61.084 | 1.4211e-13 | -0.015893 | -0.00073712 | 0.06353 | -0.0034912 | 0.059674 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0079592 | 0.063128 | -57.7828 | -0.012329 | -60.4051 | 61.0042 | 60.6711 | 60.7169 | -60.4499 | -60.3372 | 0.027831 | -60.4495 | 60.8274 | 60.9137 | 60.9352 | -60.5038 | -0.029687 | -0.079779 | 2.6374 | 0.015141 | 0.044828 | -0.41287 | -0.36711 | -0.083575 | -0.25658 | 0.083036 | -0.029307 | 0.054268 | -0.17028 | -0.14877 | 121.4244 | 121.0913 | 121.1371 | 60.4079 | -121.5339 | 121.2476 | 121.3339 | 121.3554 | 60.4481 | -121.5878
470.9062 | 121.8018 | -60.4019 | 61.0382 | 1.4211e-13 | -0.01632 | -0.00073712 | 0.063103 | -0.003064 | 0.059888 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064058 | 0.0077456 | 0.062914 | -57.8972 | -0.016908 | -60.4326 | 60.9722 | 60.6436 | 60.6848 | -60.4774 | -60.3601 | 0.027831 | -60.477 | 60.7954 | 60.8816 | 60.8986 | -60.5221 | -0.075471 | -0.066051 | 2.5047 | -0.030639 | 0.044832 | -0.39457 | -0.35338 | -0.1202 | -0.24285 | 0.041833 | -0.075089 | 0.045111 | -0.15656 | -0.13962 | 121.3741 | 121.0456 | 121.0867 | 60.385 | -121.5156 | 121.1973 | 121.2836 | 121.3005 | 60.4297 | -121.5603
472.6719 | 121.7239 | -60.6766 | 60.7544 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.06353 | -0.0034912 | 0.059674 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063844 | 0.0079592 | 0.062701 | -58.0346 | -0.021486 | -60.6569 | 60.757 | 60.433 | 60.4696 | -60.6926 | -60.5799 | 0.03241 | -60.6876 | 60.5893 | 60.6665 | 60.6925 | -60.7465 | -0.016022 | 0.002577 | 2.642 | 0.019683 | 0.035705 | -0.32139 | -0.28476 | -0.069904 | -0.16507 | 0.096713 | -0.011052 | 0.058852 | -0.087941 | -0.061847 | 121.4335 | 121.1096 | 121.1462 | 60.6551 | -121.447 | 121.2659 | 121.343 | 121.3691 | 60.709 | -121.5009
474.4219 | 121.669 | -60.672 | 60.8093 | 1.4211e-13 | -0.015893 | -0.00095092 | 0.063744 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | -0.00026913 | 0.064058 | 0.008173 | 0.062487 | -57.9797 | -0.012329 | -60.6157 | 60.7936 | 60.4651 | 60.5017 | -60.6605 | -60.5432 | 0.027831 | -60.6602 | 60.6122 | 60.7031 | 60.7246 | -60.7098 | 0.011452 | -0.015727 | 2.6923 | 0.05631 | 0.044858 | -0.34427 | -0.30764 | -0.037852 | -0.19711 | 0.12876 | 0.011842 | 0.049694 | -0.10624 | -0.084727 | 121.4656 | 121.1371 | 121.1737 | 60.6597 | -121.4699 | 121.2842 | 121.3751 | 121.3966 | 60.6998 | -121.5192
476.125 | 121.701 | -60.5896 | 60.8963 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.063316 | -0.0032776 | 0.059674 | -0.0099194 | 0.00013254 | 0.00037167 | 0.064272 | 0.0079592 | 0.062914 | -57.9568 | -0.026065 | -60.5836 | 60.8211 | 60.4971 | 60.5429 | -60.6239 | -60.5112 | 0.027831 | -60.6235 | 60.6534 | 60.7397 | 60.7612 | -60.6824 | -0.034313 | -0.075231 | 2.6328 | 0.005961 | 0.040274 | -0.39919 | -0.35341 | -0.092776 | -0.24288 | 0.078418 | -0.033925 | 0.058851 | -0.15659 | -0.13507 | 121.4107 | 121.0867 | 121.1325 | 60.5635 | -121.5202 | 121.243 | 121.3293 | 121.3508 | 60.6174 | -121.5787
477.8281 | 121.6461 | -60.5759 | 60.9146 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.06353 | -0.0032776 | 0.059888 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064272 | 0.008173 | 0.063128 | -57.8881 | -0.012329 | -60.5241 | 60.8806 | 60.5475 | 60.5933 | -60.5644 | -60.4517 | 0.03241 | -60.564 | 60.7038 | 60.7901 | 60.8162 | -60.6229 | 0.01148 | -0.034023 | 2.6878 | 0.051745 | 0.040265 | -0.36713 | -0.32136 | -0.046984 | -0.21083 | 0.12421 | 0.011865 | 0.058849 | -0.12454 | -0.098441 | 121.4565 | 121.1233 | 121.1691 | 60.5635 | -121.479 | 121.2797 | 121.3659 | 121.392 | 60.6083 | -121.5375
479.5938 | 121.7514 | -60.3516 | 61.0794 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.06353 | -0.003705 | 0.059888 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064272 | 0.008173 | 0.062487 | -57.824 | -0.021486 | -60.373 | 61.0408 | 60.7032 | 60.7535 | -60.4133 | -60.296 | 0.03241 | -60.4129 | 60.8595 | 60.9549 | 60.9627 | -60.458 | -0.061721 | -0.038575 | 2.5276 | -0.021476 | 0.040245 | -0.37625 | -0.3259 | -0.10645 | -0.21995 | 0.05558 | -0.061342 | 0.04511 | -0.1245 | -0.11672 | 121.3924 | 121.0547 | 121.1051 | 60.3301 | -121.4927 | 121.211 | 121.3065 | 121.3142 | 60.384 | -121.5374
481.3594 | 121.7102 | -60.2966 | 61.1755 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.06353 | -0.003705 | 0.059888 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.0079592 | 0.062914 | -57.6729 | -0.016908 | -60.2998 | 61.1141 | 60.781 | 60.8268 | -60.3354 | -60.2227 | 0.03241 | -60.3442 | 60.9327 | 61.0236 | 61.0451 | -60.3939 | -0.03881 | -0.06145 | 2.6237 | -0.003155 | 0.035655 | -0.39453 | -0.34877 | -0.097279 | -0.24283 | 0.073908 | -0.047593 | 0.049686 | -0.15195 | -0.13044 | 121.4107 | 121.0776 | 121.1234 | 60.2797 | -121.511 | 121.2293 | 121.3202 | 121.3417 | 60.329 | -121.5694
483.0625 | 121.8063 | -60.26 | 61.1572 | 1.4211e-13 | -0.016107 | -0.00073712 | 0.063316 | -0.003705 | 0.059674 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.008173 | 0.062701 | -57.7691 | -0.021486 | -60.2769 | 61.1141 | 60.7947 | 60.8313 | -60.3171 | -60.2136 | 0.03241 | -60.3305 | 60.9464 | 61.0373 | 61.0497 | -60.3802 | -0.057115 | -0.04314 | 2.491 | -0.016884 | 0.040231 | -0.36249 | -0.32588 | -0.12016 | -0.21078 | 0.046444 | -0.070478 | 0.049686 | -0.11991 | -0.10755 | 121.3741 | 121.0547 | 121.0914 | 60.2385 | -121.4744 | 121.2065 | 121.2973 | 121.3097 | 60.2924 | -121.5374
484.8125 | 121.6507 | -60.4889 | 61.0245 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.063744 | -0.003064 | 0.059674 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0079592 | 0.062701 | -57.911 | -0.016908 | -60.5104 | 60.9035 | 60.5658 | 60.6024 | -60.5506 | -60.4333 | 0.027831 | -60.5411 | 60.7221 | 60.8084 | 60.8253 | -60.6045 | -0.061758 | -0.12099 | 2.5779 | -0.021495 | 0.040263 | -0.45868 | -0.42206 | -0.11564 | -0.30238 | 0.055548 | -0.052216 | 0.063428 | -0.21608 | -0.19915 | 121.3924 | 121.0547 | 121.0913 | 60.472 | -121.5751 | 121.211 | 121.2973 | 121.3142 | 60.5167 | -121.629
486.5 | 121.6599 | -60.5621 | 60.9787 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.063744 | -0.0034912 | 0.05946 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.0083866 | 0.062914 | -57.8469 | -0.016908 | -60.4921 | 60.9172 | 60.5887 | 60.6345 | -60.5232 | -60.4104 | 0.03241 | -60.5274 | 60.7404 | 60.8313 | 60.8482 | -60.5816 | 0.038957 | -0.061483 | 2.7153 | 0.07006 | 0.031103 | -0.39001 | -0.34424 | -0.019508 | -0.23829 | 0.15168 | 0.034762 | 0.05427 | -0.14742 | -0.13048 | 121.4794 | 121.1508 | 121.1966 | 60.5452 | -121.5019 | 121.3025 | 121.3934 | 121.4104 | 60.5945 | -121.5603
488.25 | 121.6736 | -60.5392 | 60.9421 | 1.4211e-13 | -0.016107 | -0.0011645 | 0.063316 | -0.003705 | 0.059674 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0079592 | 0.062914 | -57.8606 | -0.016908 | -60.4829 | 60.9264 | 60.5887 | 60.639 | -60.5278 | -60.415 | 0.03241 | -60.5274 | 60.7496 | 60.8267 | 60.8528 | -60.5816 | 0.01149 | -0.015705 | 2.6786 | 0.056329 | 0.044839 | -0.35339 | -0.30304 | -0.042396 | -0.19251 | 0.12422 | 0.011874 | 0.05427 | -0.11537 | -0.089278 | 121.4656 | 121.1279 | 121.1783 | 60.5223 | -121.4698 | 121.2888 | 121.366 | 121.392 | 60.5717 | -121.5237
490.0156 | 121.7285 | -60.5026 | 60.9421 | 1.4211e-13 | -0.016534 | -0.00073712 | 0.063316 | -0.0032776 | 0.059674 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.008173 | 0.062914 | -57.8423 | -0.012329 | -60.46 | 60.9355 | 60.6116 | 60.6482 | -60.5049 | -60.3967 | 0.03241 | -60.5045 | 60.7496 | 60.8496 | 60.8665 | -60.5633 | -0.002236 | -0.006549 | 2.6603 | 0.042599 | 0.044835 | -0.33049 | -0.29388 | -0.060701 | -0.19251 | 0.10591 | -0.001854 | 0.058847 | -0.09248 | -0.075543 | 121.4382 | 121.1142 | 121.1508 | 60.4903 | -121.4469 | 121.2522 | 121.3522 | 121.3692 | 60.535 | -121.5054
491.7188 | 121.701 | -60.4477 | 61.0748 | 1.4211e-13 | -0.01632 | -0.00095092 | 0.063316 | -0.0034912 | 0.059674 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064058 | 0.0083866 | 0.062487 | -57.7736 | -0.021486 | -60.4463 | 60.9584 | 60.6345 | 60.6757 | -60.4865 | -60.3692 | 0.036989 | -60.4816 | 60.7908 | 60.8725 | 60.8894 | -60.5404 | -0.038853 | -0.11641 | 2.6741 | 0.001402 | 0.040255 | -0.44035 | -0.39916 | -0.092739 | -0.28405 | 0.078451 | -0.033892 | 0.058847 | -0.20234 | -0.1854 | 121.4061 | 121.0822 | 121.1234 | 60.4262 | -121.5614 | 121.2385 | 121.3202 | 121.3371 | 60.4847 | -121.6153
493.4688 | 121.6782 | -60.4477 | 61.0382 | 1.4211e-13 | -0.01632 | -0.0011645 | 0.063316 | -0.003705 | 0.059888 | -0.0022889 | 0.00034614 | -0.00069653 | 0.064058 | 0.0079592 | 0.062487 | -57.7919 | -0.016908 | -60.4554 | 60.9538 | 60.6253 | 60.6665 | -60.4911 | -60.3876 | 0.03241 | -60.4999 | 60.7725 | 60.8633 | 60.8757 | -60.5633 | -0.043431 | -0.084365 | 2.6558 | -0.007754 | 0.035677 | -0.41289 | -0.37169 | -0.11563 | -0.26575 | 0.060136 | -0.052207 | 0.063426 | -0.17487 | -0.16251 | 121.4015 | 121.073 | 121.1142 | 60.4308 | -121.5293 | 121.2202 | 121.311 | 121.3234 | 60.4801 | -121.6015
495.25 | 121.7834 | -60.4202 | 61.0016 | 1.4211e-13 | -0.015893 | -0.00095092 | 0.06353 | -0.0034912 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0079592 | 0.062487 | -57.8652 | -0.016908 | -60.4463 | 60.9493 | 60.6162 | 60.6711 | -60.482 | -60.3784 | 0.027831 | -60.4907 | 60.7816 | 60.8633 | 60.8803 | -60.5496 | -0.06174 | -0.052322 | 2.555 | -0.026064 | 0.035676 | -0.38542 | -0.3305 | -0.12936 | -0.21997 | 0.041828 | -0.070515 | 0.058848 | -0.13825 | -0.12132 | 121.3695 | 121.0364 | 121.0913 | 60.4033 | -121.4836 | 121.2018 | 121.2836 | 121.3005 | 60.4481 | -121.5512
497.0156 | 121.6553 | -60.4294 | 61.0474 | 1.4211e-13 | -0.016107 | -0.00095092 | 0.06353 | -0.003705 | 0.059888 | -0.0099194 | 0.00013254 | -0.00026913 | 0.064058 | 0.0079592 | 0.062914 | -57.7965 | -0.021486 | -60.4371 | 60.963 | 60.6391 | 60.6848 | -60.4774 | -60.3647 | 0.03241 | -60.4816 | 60.7999 | 60.8725 | 60.894 | -60.5359 | -0.048006 | -0.084363 | 2.6329 | -0.007752 | 0.040254 | -0.40831 | -0.36254 | -0.10647 | -0.24743 | 0.064719 | -0.052203 | 0.054268 | -0.17487 | -0.15336 | 121.3924 | 121.0684 | 121.1142 | 60.4079 | -121.5248 | 121.2293 | 121.3019 | 121.3234 | 60.4618 | -121.5832
498.7031 | 121.6599 | -60.4477 | 61.0474 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.063316 | -0.003705 | 0.059888 | 0.0053411 | 0.00013254 | 0.00037167 | 0.064058 | 0.008173 | 0.062914 | -57.7278 | -0.021486 | -60.4005 | 60.9996 | 60.6711 | 60.7169 | -60.3904 | -60.3326 | 0.036989 | -60.4404 | 60.8228 | 60.9183 | 60.9261 | -60.4946 | 0.057305 | -0.047736 | 2.7198 | 0.047185 | -0.01012 | -0.37625 | -0.33049 | -0.046951 | -0.22454 | 0.11508 | 0.007316 | 0.054267 | -0.12909 | -0.12131 | 121.4473 | 121.1188 | 121.1646 | 60.4262 | -121.4378 | 121.2705 | 121.366 | 121.3738 | 60.4847 | -121.542
500.4531 | 121.7377 | -60.4065 | 61.0336 | 1.4211e-13 | -0.01632 | -0.0011645 | 0.063316 | -0.003064 | 0.059674 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.064058 | 0.008173 | 0.062701 | -57.705 | -0.012329 | -60.373 | 61.0408 | 60.6986 | 60.7535 | -60.3583 | -60.2914 | 0.03241 | -60.3992 | 60.864 | 60.9503 | 60.9764 | -60.4626 | 0.048158 | 0.007202 | 2.7015 | 0.033456 | -0.014702 | -0.33505 | -0.28012 | -0.056098 | -0.1696 | 0.11509 | 0.007326 | 0.063424 | -0.083303 | -0.057208 | 121.4473 | 121.1051 | 121.16 | 60.3942 | -121.392 | 121.2705 | 121.3568 | 121.3829 | 60.4389 | -121.4962
502.2188 | 121.8109 | -60.3607 | 61.0611 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.063316 | -0.003705 | 0.059888 | -0.0022889 | 0.00013254 | -0.00026913 | 0.064058 | 0.0086004 | 0.062487 | -57.8103 | -0.016908 | -60.3868 | 61.0225 | 60.6848 | 60.726 | -60.3767 | -60.3189 | 0.018674 | -60.4221 | 60.8411 | 60.9274 | 60.9444 | -60.4855 | -0.015933 | -0.038577 | 2.5505 | -0.026055 | -0.010122 | -0.37625 | -0.33506 | -0.12477 | -0.21996 | 0.041842 | -0.061344 | 0.063424 | -0.13366 | -0.11672 | 121.3832 | 121.0456 | 121.0868 | 60.3438 | -121.4377 | 121.2019 | 121.2882 | 121.3051 | 60.3794 | -121.5466
503.9219 | 121.7194 | -60.3928 | 61.0565 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.06353 | -0.0032776 | 0.059888 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.0083866 | 0.062914 | -57.8057 | -0.012329 | -60.4188 | 60.9813 | 60.6482 | 60.7031 | -60.4087 | -60.3418 | 0.03241 | -60.4633 | 60.8091 | 60.9 | 60.9169 | -60.513 | -0.015943 | -0.075206 | 2.5871 | -0.02606 | -0.010117 | -0.4083 | -0.35338 | -0.1202 | -0.24743 | 0.050991 | -0.070509 | 0.049689 | -0.15656 | -0.13962 | 121.3741 | 121.041 | 121.0959 | 60.3804 | -121.4652 | 121.2019 | 121.2927 | 121.3097 | 60.4252 | -121.5695
505.6875 | 121.7377 | -60.3653 | 61.0611 | 1.4211e-13 | -0.016534 | -0.00073712 | 0.06353 | -0.0034912 | 0.059888 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.008173 | 0.062914 | -57.7599 | -0.016908 | -60.3822 | 61.0317 | 60.694 | 60.7398 | -60.3583 | -60.3051 | 0.03241 | -60.4175 | 60.8549 | 60.9457 | 60.9581 | -60.4763 | 0.006959 | -0.02942 | 2.6054 | -0.0169 | -0.023859 | -0.36709 | -0.32133 | -0.11103 | -0.20622 | 0.060155 | -0.052188 | 0.058846 | -0.11535 | -0.10299 | 121.397 | 121.0593 | 121.1051 | 60.3484 | -121.4194 | 121.2202 | 121.311 | 121.3234 | 60.3977 | -121.5374
507.4531 | 121.7606 | -60.3745 | 61.0519 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.063744 | -0.0034912 | 0.059888 | -0.0022889 | 0.00013254 | 0.00037167 | 0.064058 | 0.0086004 | 0.062487 | -57.8103 | -0.026065 | -60.4051 | 60.9905 | 60.6711 | 60.7123 | -60.3995 | -60.3372 | 0.036989 | -60.4495 | 60.8228 | 60.9091 | 60.9306 | -60.5038 | -0.025095 | -0.061471 | 2.5642 | -0.030635 | -0.00554 | -0.38083 | -0.33964 | -0.12935 | -0.22912 | 0.03726 | -0.075083 | 0.054268 | -0.14282 | -0.1213 | 121.3649 | 121.0456 | 121.0867 | 60.3484 | -121.4515 | 121.1973 | 121.2836 | 121.3051 | 60.4114 | -121.5557
509.1719 | 121.669 | -60.3882 | 61.0931 | 1.4211e-13 | -0.01632 | -0.00095092 | 0.06353 | -0.0034912 | 0.059888 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064058 | 0.0083866 | 0.062701 | -57.7782 | -0.035222 | -60.4097 | 60.9996 | 60.6665 | 60.7169 | -60.395 | -60.328 | 0.027831 | -60.4495 | 60.8182 | 60.9091 | 60.9352 | -60.5084 | -0.006783 | -0.093513 | 2.61 | -0.021481 | -0.014698 | -0.42661 | -0.37626 | -0.1202 | -0.27489 | 0.060151 | -0.06135 | 0.058847 | -0.18402 | -0.15793 | 121.3878 | 121.0547 | 121.1051 | 60.353 | -121.4881 | 121.2064 | 121.2973 | 121.3234 | 60.416 | -121.6015
510.9375 | 121.7239 | -60.3882 | 61.0291 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.062889 | -0.0034912 | 0.059888 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064272 | 0.008173 | 0.062701 | -57.7645 | -0.021486 | -60.3776 | 61.0271 | 60.7032 | 60.7489 | -60.3629 | -60.296 | 0.036989 | -60.4129 | 60.8549 | 60.9412 | 60.9627 | -60.4718 | 0.025269 | -0.001956 | 2.6237 | 0.010567 | -0.014702 | -0.32589 | -0.28012 | -0.083566 | -0.17418 | 0.092202 | -0.02472 | 0.058846 | -0.087883 | -0.066367 | 121.4153 | 121.0913 | 121.1371 | 60.3667 | -121.392 | 121.2431 | 121.3294 | 121.3509 | 60.4252 | -121.5008
512.6562 | 121.6736 | -60.3928 | 61.0794 | 1.4211e-13 | -0.01632 | -0.00052352 | 0.063316 | -0.0039186 | 0.060101 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.008173 | 0.062487 | -57.6683 | -0.021486 | -60.3685 | 61.0408 | 60.7215 | 60.7627 | -60.3538 | -60.2868 | 0.036989 | -60.3992 | 60.8686 | 60.9549 | 60.9764 | -60.4672 | 0.039004 | -0.038575 | 2.7244 | 0.024301 | -0.014703 | -0.35793 | -0.31674 | -0.07441 | -0.2108 | 0.10594 | -0.006407 | 0.068003 | -0.1245 | -0.10299 | 121.4336 | 121.1142 | 121.1554 | 60.3713 | -121.4332 | 121.2614 | 121.3477 | 121.3692 | 60.4297 | -121.5466
514.4219 | 121.6965 | -60.3287 | 61.1435 | 1.4211e-13 | -0.01632 | -0.0011645 | 0.063744 | -0.0034912 | 0.059888 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064058 | 0.008173 | 0.062487 | -57.6409 | -0.021486 | -60.3181 | 61.0775 | 60.7535 | 60.8039 | -60.308 | -60.2365 | 0.036989 | -60.3671 | 60.9052 | 60.987 | 61.0039 | -60.4168 | 0.020707 | -0.066035 | 2.6878 | 0.010575 | -0.010132 | -0.38996 | -0.33962 | -0.08813 | -0.23826 | 0.092215 | -0.038443 | 0.049687 | -0.15654 | -0.1396 | 121.4061 | 121.0822 | 121.1325 | 60.3072 | -121.4515 | 121.2339 | 121.3156 | 121.3326 | 60.3657 | -121.5603
516.1406 | 121.6919 | -60.2966 | 61.2076 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.063316 | -0.0034912 | 0.059674 | 0.012972 | 0.00013254 | -0.00026913 | 0.064058 | 0.0083866 | 0.062487 | -57.6821 | -0.021486 | -60.2998 | 61.1049 | 60.7764 | 60.8176 | -60.2897 | -60.2227 | 0.036989 | -60.3442 | 60.9236 | 61.0236 | 61.0359 | -60.3985 | 0.006979 | -0.10265 | 2.6146 | -0.003155 | -0.010134 | -0.43116 | -0.38997 | -0.10186 | -0.28403 | 0.073908 | -0.047593 | 0.054265 | -0.184 | -0.17164 | 121.4016 | 121.0731 | 121.1142 | 60.2751 | -121.4972 | 121.2202 | 121.3202 | 121.3326 | 60.3336 | -121.6061
517.8438 | 121.6232 | -60.2829 | 61.1984 | 1.4211e-13 | -0.01632 | -0.00095092 | 0.063316 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.008173 | 0.062701 | -57.5859 | -0.021486 | -60.2815 | 61.1324 | 60.7993 | 60.8359 | -60.2668 | -60.2044 | 0.036989 | -60.3168 | 60.9464 | 61.0373 | 61.0588 | -60.3802 | 0.016141 | -0.066025 | 2.697 | 0.001425 | -0.014716 | -0.39911 | -0.3625 | -0.097276 | -0.25198 | 0.07849 | -0.033853 | 0.063423 | -0.1611 | -0.13959 | 121.4153 | 121.0822 | 121.1188 | 60.2614 | -121.4652 | 121.2293 | 121.3202 | 121.3417 | 60.3199 | -121.5786
519.6094 | 121.7148 | -60.2783 | 61.1801 | 1.4211e-13 | -0.016534 | -0.00073712 | 0.06353 | -0.0034912 | 0.059674 | 0.012972 | 0.00034614 | 0.00015807 | 0.064272 | 0.0083866 | 0.062487 | -57.6821 | -0.026065 | -60.2952 | 61.1049 | 60.7718 | 60.8222 | -60.2897 | -60.2227 | 0.036989 | -60.3351 | 60.9281 | 61.0144 | 61.0359 | -60.3985 | -0.011332 | -0.075185 | 2.5963 | -0.016888 | -0.005556 | -0.40827 | -0.35793 | -0.12017 | -0.25198 | 0.055597 | -0.056746 | 0.063423 | -0.16569 | -0.14417 | 121.3833 | 121.0502 | 121.1005 | 60.2523 | -121.4698 | 121.2065 | 121.2927 | 121.3143 | 60.3153 | -121.5786
521.375 | 121.7422 | -60.3333 | 61.0611 | 1.4211e-13 | -0.01632 | -0.00095092 | 0.063316 | -0.0039186 | 0.059888 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.064058 | 0.0083866 | 0.062487 | -57.6775 | -0.016908 | -60.3089 | 61.0912 | 60.7627 | 60.813 | -60.3034 | -60.2319 | 0.036989 | -60.3488 | 60.9236 | 61.019 | 61.0222 | -60.4122 | 0.029863 | 0.030099 | 2.6558 | 0.02431 | -0.005553 | -0.29841 | -0.24807 | -0.078973 | -0.13754 | 0.10137 | -0.01555 | 0.063423 | -0.04209 | -0.038888 | 121.4244 | 121.0959 | 121.1463 | 60.3163 | -121.3645 | 121.2568 | 121.3523 | 121.3555 | 60.3702 | -121.4733
523.0625 | 121.7377 | -60.26 | 61.171 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.06353 | -0.0034912 | 0.059674 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0083866 | 0.062487 | -57.6225 | -0.021486 | -60.254 | 61.1599 | 60.8314 | 60.8817 | -60.2347 | -60.1769 | 0.03241 | -60.2893 | 60.9831 | 61.0648 | 61.0909 | -60.3435 | 0.025305 | -0.011089 | 2.6375 | 0.006007 | -0.019298 | -0.33959 | -0.28925 | -0.083533 | -0.18789 | 0.083074 | -0.029269 | 0.054264 | -0.10617 | -0.080072 | 121.4199 | 121.0914 | 121.1417 | 60.2385 | -121.4057 | 121.2431 | 121.3248 | 121.3509 | 60.2924 | -121.5145
524.8281 | 121.7377 | -60.1868 | 61.2671 | 1.4211e-13 | -0.01632 | -0.00095092 | 0.063103 | -0.0034912 | 0.059888 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0083866 | 0.062273 | -57.5951 | -0.026065 | -60.1945 | 61.2057 | 60.8772 | 60.9138 | -60.1935 | -60.122 | 0.036989 | -60.2435 | 61.0289 | 61.1152 | 61.1321 | -60.3023 | -0.006726 | -0.061436 | 2.5917 | -0.007717 | -0.000991 | -0.38993 | -0.35333 | -0.11557 | -0.23823 | 0.064777 | -0.056724 | 0.058842 | -0.15193 | -0.135 | 121.3924 | 121.0639 | 121.1005 | 60.1607 | -121.4606 | 121.2156 | 121.3019 | 121.3189 | 60.2238 | -121.5694
526.5312 | 121.6644 | -60.1868 | 61.3403 | 1.4211e-13 | -0.016534 | -0.00095092 | 0.063316 | -0.0034912 | 0.05946 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063844 | 0.0083866 | 0.062273 | -57.5218 | -0.016908 | -60.1441 | 61.2514 | 60.9184 | 60.9733 | -60.134 | -60.0808 | 0.03241 | -60.1885 | 61.0746 | 61.1655 | 61.1825 | -60.2474 | 0.0528 | -0.088894 | 2.6649 | 0.042644 | -0.010156 | -0.42196 | -0.36705 | -0.06062 | -0.26569 | 0.10599 | -0.00178 | 0.05884 | -0.17481 | -0.15787 | 121.4382 | 121.1051 | 121.16 | 60.1699 | -121.4743 | 121.2614 | 121.3523 | 121.3692 | 60.2192 | -121.5877
528.2812 | 121.7514 | -60.1273 | 61.2625 | 1.4211e-13 | -0.016961 | -0.00095092 | 0.06353 | -0.003705 | 0.059888 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.064272 | 0.0086004 | 0.062487 | -57.5035 | -0.026065 | -60.1304 | 61.2835 | 60.9458 | 60.9916 | -60.1111 | -60.0487 | 0.03241 | -60.1657 | 61.093 | 61.193 | 61.2054 | -60.2291 | 0.016184 | 0.020975 | 2.6238 | -0.003131 | -0.019315 | -0.31667 | -0.27092 | -0.10182 | -0.16956 | 0.078526 | -0.038396 | 0.063419 | -0.069519 | -0.05716 | 121.4107 | 121.0731 | 121.1189 | 60.1012 | -121.3736 | 121.2202 | 121.3203 | 121.3326 | 60.1597 | -121.4916
529.9844 | 121.7285 | -60.0815 | 61.3541 | 1.4211e-13 | -0.016748 | -0.0011645 | 0.063316 | -0.003705 | 0.060101 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.0086004 | 0.062273 | -57.4623 | -0.021486 | -60.0754 | 61.3293 | 60.9962 | 61.0465 | -60.0607 | -59.9892 | 0.036989 | -60.1153 | 61.1433 | 61.2479 | 61.2649 | -60.165 | 0.020776 | -0.024794 | 2.6192 | 0.006032 | -0.014744 | -0.35785 | -0.30753 | -0.083487 | -0.21074 | 0.092273 | -0.033806 | 0.049681 | -0.10613 | -0.089191 | 121.4108 | 121.0777 | 121.128 | 60.06 | -121.4148 | 121.2248 | 121.3294 | 121.3464 | 60.1185 | -121.519
531.75 | 121.6873 | -60.0632 | 61.4136 | 1.4211e-13 | -0.016961 | -0.0011645 | 0.063316 | -0.003705 | 0.05946 | -0.0022889 | 0.00034614 | -0.00048293 | 0.064272 | 0.0086004 | 0.062487 | -57.3662 | -0.021486 | -60.0342 | 61.3659 | 61.0283 | 61.0832 | -60.0378 | -59.9709 | 0.036989 | -60.0832 | 61.1799 | 61.2754 | 61.2923 | -60.1467 | 0.02536 | -0.047676 | 2.697 | 0.028925 | 0.003565 | -0.38531 | -0.33041 | -0.083483 | -0.23363 | 0.092277 | -0.020066 | 0.063417 | -0.13817 | -0.12123 | 121.4291 | 121.0914 | 121.1463 | 60.0417 | -121.4514 | 121.2431 | 121.3386 | 121.3555 | 60.1002 | -121.5602
533.4375 | 121.7743 | -60.0403 | 61.3632 | 1.4211e-13 | -0.016748 | -0.00073712 | 0.063316 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064058 | 0.0086004 | 0.062273 | -57.3662 | -0.016908 | -60.0159 | 61.3888 | 61.0512 | 61.0969 | -60.0012 | -59.948 | 0.041567 | -60.0512 | 61.2028 | 61.3075 | 61.3107 | -60.11 | 0.039103 | 0.02557 | 2.6741 | 0.024351 | -0.014752 | -0.31206 | -0.26632 | -0.06974 | -0.16038 | 0.092282 | -0.010903 | 0.058837 | -0.055762 | -0.05256 | 121.4291 | 121.0914 | 121.1372 | 60.0234 | -121.3644 | 121.2431 | 121.3477 | 121.3509 | 60.0819 | -121.4732
535.2031 | 121.7377 | -59.9762 | 61.441 | 1.4211e-13 | -0.017175 | -0.0011645 | 0.063316 | -0.0034912 | 0.05946 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0083866 | 0.062273 | -57.3249 | -0.016908 | -59.9564 | 61.4437 | 61.1107 | 61.1656 | -59.9462 | -59.8885 | 0.036989 | -60.0054 | 61.2624 | 61.3624 | 61.361 | -60.0551 | 0.029964 | 0.002691 | 2.6512 | 0.019781 | -0.010183 | -0.33035 | -0.27546 | -0.078882 | -0.17868 | 0.087719 | -0.029203 | 0.049679 | -0.078638 | -0.080016 | 121.4199 | 121.0869 | 121.1418 | 59.9593 | -121.3873 | 121.2386 | 121.3386 | 121.3372 | 60.0132 | -121.4961
536.9062 | 121.6461 | -59.9167 | 61.5921 | 1.4211e-13 | -0.016961 | -0.00052352 | 0.063103 | -0.0039186 | 0.059674 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.064272 | 0.0083866 | 0.062701 | -57.2975 | -0.021486 | -59.9427 | 61.4712 | 61.1382 | 61.1839 | -59.9279 | -59.8656 | 0.027831 | -59.9779 | 61.2853 | 61.3807 | 61.3931 | -60.0368 | -0.01123 | -0.1209 | 2.6192 | -0.025993 | -0.014763 | -0.45394 | -0.40821 | -0.12007 | -0.30685 | 0.051103 | -0.06124 | 0.058835 | -0.21139 | -0.19903 | 121.3879 | 121.0548 | 121.1006 | 59.8952 | -121.52 | 121.2019 | 121.2974 | 121.3098 | 59.9445 | -121.6289
538.6094 | 121.7743 | -59.9625 | 61.4548 | 1.4211e-13 | -0.016961 | -0.00073712 | 0.063316 | -0.0039186 | 0.059674 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063844 | 0.008814 | 0.062273 | -57.3021 | -0.016908 | -59.9473 | 61.462 | 61.1244 | 61.1747 | -59.9279 | -59.8702 | 0.03241 | -59.9825 | 61.2853 | 61.3761 | 61.3931 | -60.0413 | 0.034546 | 0.007271 | 2.6604 | 0.015205 | -0.019341 | -0.33035 | -0.28004 | -0.078878 | -0.16952 | 0.092301 | -0.020043 | 0.058835 | -0.078636 | -0.061698 | 121.4245 | 121.0869 | 121.1372 | 59.9456 | -121.3827 | 121.2477 | 121.3386 | 121.3555 | 59.9949 | -121.4961
540.3906 | 121.7697 | -59.8572 | 61.5509 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.063316 | -0.0039186 | 0.059888 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.064058 | 0.0083866 | 0.062487 | -57.3478 | -0.021486 | -59.9335 | 61.4758 | 61.1473 | 61.1885 | -59.905 | -59.8473 | 0.041567 | -59.9688 | 61.299 | 61.399 | 61.4068 | -60.023 | -0.047844 | -0.075124 | 2.5093 | -0.076345 | -0.028501 | -0.40359 | -0.36243 | -0.16585 | -0.25191 | 0.009909 | -0.11159 | 0.054256 | -0.15187 | -0.14409 | 121.333 | 121.0045 | 121.0457 | 59.8357 | -121.4559 | 121.1562 | 121.2562 | 121.264 | 59.8987 | -121.5739
542.1719 | 121.669 | -59.7977 | 61.6974 | 1.4211e-13 | -0.016961 | -0.00073712 | 0.063316 | -0.0034912 | 0.05946 | -0.0022889 | 0.00034614 | -0.00048293 | 0.064272 | 0.0086004 | 0.062273 | -57.2105 | -0.012329 | -59.8694 | 61.5353 | 61.2023 | 61.2434 | -59.8547 | -59.7969 | 0.036989 | -59.9047 | 61.3539 | 61.4494 | 61.4709 | -59.9681 | -0.056986 | -0.16209 | 2.5872 | -0.071759 | -0.014773 | -0.49512 | -0.45397 | -0.17041 | -0.34346 | 0.000765 | -0.107 | 0.063412 | -0.24799 | -0.22648 | 121.333 | 120.9999 | 121.0411 | 59.7853 | -121.552 | 121.1516 | 121.2471 | 121.2686 | 59.8347 | -121.6655
543.875 | 121.7697 | -59.935 | 61.5051 | 1.4211e-13 | -0.016748 | -0.0011645 | 0.063316 | -0.0034912 | 0.059888 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063844 | 0.0086004 | 0.062487 | -57.357 | -0.021486 | -59.9473 | 61.4575 | 61.1244 | 61.1793 | -59.9371 | -59.8656 | 0.041567 | -59.9871 | 61.2761 | 61.367 | 61.3931 | -60.0368 | -0.002077 | -0.047661 | 2.578 | -0.01226 | -0.010183 | -0.3807 | -0.32581 | -0.10176 | -0.22903 | 0.069414 | -0.052086 | 0.049678 | -0.13815 | -0.11205 | 121.3925 | 121.0594 | 121.1143 | 59.9135 | -121.4422 | 121.2111 | 121.302 | 121.3281 | 59.9766 | -121.5419
545.5781 | 121.6919 | -60.0082 | 61.4639 | 1.4211e-13 | -0.016961 | -0.00095092 | 0.063316 | -0.003705 | 0.059674 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.064058 | 0.0086004 | 0.062487 | -57.3249 | -0.016908 | -60.0068 | 61.4025 | 61.0695 | 61.1152 | -59.992 | -59.9251 | 0.036989 | -60.042 | 61.2257 | 61.312 | 61.3381 | -60.0963 | 0.016218 | -0.061403 | 2.6833 | 0.001464 | -0.014754 | -0.39445 | -0.34871 | -0.088047 | -0.2382 | 0.083133 | -0.033789 | 0.054258 | -0.15189 | -0.1258 | 121.4108 | 121.0777 | 121.1235 | 59.9913 | -121.456 | 121.234 | 121.3203 | 121.3464 | 60.0452 | -121.5602
547.3438 | 121.7789 | -59.9579 | 61.4365 | 1.4211e-13 | -0.016961 | -0.00095092 | 0.063103 | -0.0039186 | 0.059888 | -0.0099194 | 0.00013254 | 0.00015807 | 0.064058 | 0.0083866 | 0.062273 | -57.2654 | -0.021486 | -59.9198 | 61.4804 | 61.1473 | 61.1931 | -59.9142 | -59.8473 | 0.036989 | -59.9596 | 61.3081 | 61.3945 | 61.4114 | -60.0093 | 0.043706 | 0.043896 | 2.6925 | 0.038097 | -0.005609 | -0.28914 | -0.24341 | -0.051404 | -0.12832 | 0.11062 | -0.001726 | 0.049678 | -0.04201 | -0.025073 | 121.4382 | 121.1052 | 121.1509 | 59.9364 | -121.3506 | 121.266 | 121.3523 | 121.3693 | 59.9949 | -121.4458
549.125 | 121.637 | -59.9625 | 61.5326 | 1.4211e-13 | -0.016961 | -0.0013783 | 0.06353 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | -0.00048293 | 0.064058 | 0.0086004 | 0.062487 | -57.2288 | -0.021486 | -59.9152 | 61.4941 | 61.1656 | 61.2114 | -59.9004 | -59.829 | 0.046146 | -59.9459 | 61.3127 | 61.399 | 61.4297 | -60.0047 | 0.06202 | -0.0385 | 2.7337 | 0.047253 | -0.014767 | -0.36696 | -0.32123 | -0.042248 | -0.21987 | 0.13351 | 0.016587 | 0.058835 | -0.13356 | -0.10289 | 121.4566 | 121.1281 | 121.1738 | 59.941 | -121.433 | 121.2752 | 121.3615 | 121.3922 | 60.0086 | -121.5373
550.8906 | 121.7743 | -60.0952 | 61.3083 | 1.4211e-13 | -0.016961 | -0.0013783 | 0.063103 | -0.003705 | 0.05946 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063844 | 0.008814 | 0.062273 | -57.5356 | -0.021486 | -60.1121 | 61.2835 | 60.9504 | 61.0008 | -60.1157 | -60.0442 | 0.036989 | -60.1657 | 61.0975 | 61.1884 | 61.2099 | -60.2199 | -0.020438 | -0.024802 | 2.5597 | -0.016861 | 0.003577 | -0.35787 | -0.30754 | -0.1247 | -0.21075 | 0.051062 | -0.070439 | 0.054261 | -0.11987 | -0.098358 | 121.3787 | 121.0456 | 121.096 | 60.0737 | -121.4239 | 121.1928 | 121.2836 | 121.3051 | 60.1322 | -121.5282
552.5938 | 121.7789 | -59.9854 | 61.3953 | 1.4211e-13 | -0.017175 | -0.00073712 | 0.06353 | -0.003705 | 0.05946 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.008173 | 0.062273 | -57.4852 | -0.021486 | -60.0663 | 61.3384 | 61.01 | 61.0603 | -60.0515 | -59.9801 | 0.036989 | -60.1061 | 61.1662 | 61.2479 | 61.274 | -60.1558 | -0.066196 | -0.056836 | 2.5002 | -0.080942 | -0.014746 | -0.38531 | -0.33499 | -0.17046 | -0.22905 | 0.005301 | -0.12078 | 0.049681 | -0.14733 | -0.12123 | 121.3238 | 120.9953 | 121.0456 | 59.9639 | -121.4468 | 121.1516 | 121.2333 | 121.2594 | 60.0223 | -121.5511
554.3438 | 121.756 | -60.0128 | 61.4136 | 1.4211e-13 | -0.016748 | -0.00095092 | 0.063316 | -0.003705 | 0.059247 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063631 | 0.0086004 | 0.06206 | -57.3387 | -0.021486 | -59.9747 | 61.4163 | 61.0924 | 61.1427 | -59.9645 | -59.8976 | 0.03241 | -60.0191 | 61.244 | 61.3395 | 61.3519 | -60.0826 | 0.048269 | 0.002686 | 2.6741 | 0.038089 | -0.01018 | -0.3212 | -0.27089 | -0.069734 | -0.16953 | 0.11518 | -0.006318 | 0.063416 | -0.074065 | -0.061707 | 121.4291 | 121.1052 | 121.1555 | 59.9913 | -121.3781 | 121.2569 | 121.3523 | 121.3647 | 60.0452 | -121.4961
556.0625 | 121.7239 | -59.9075 | 61.5051 | 1.4211e-13 | -0.016961 | -0.0011645 | 0.062889 | -0.003705 | 0.059674 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064058 | 0.0086004 | 0.062487 | -57.3066 | -0.021486 | -59.9335 | 61.4666 | 61.1336 | 61.1885 | -59.9142 | -59.8564 | 0.036989 | -59.9733 | 61.2944 | 61.3853 | 61.3977 | -60.0322 | -0.006648 | -0.038505 | 2.6009 | -0.025991 | -0.019343 | -0.37155 | -0.31665 | -0.12465 | -0.21072 | 0.051106 | -0.065816 | 0.058836 | -0.11983 | -0.10747 | 121.3742 | 121.0411 | 121.096 | 59.886 | -121.4193 | 121.2019 | 121.2928 | 121.3052 | 59.9445 | -121.5373
557.8281 | 121.6415 | -59.9396 | 61.5097 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.06353 | -0.003705 | 0.059674 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.064058 | 0.0086004 | 0.062487 | -57.1876 | -0.026065 | -59.8877 | 61.5216 | 61.1839 | 61.2343 | -59.8684 | -59.8106 | 0.041567 | -59.9184 | 61.3448 | 61.4357 | 61.4434 | -59.9864 | 0.071184 | 0.011858 | 2.752 | 0.051834 | -0.01935 | -0.32576 | -0.27545 | -0.04682 | -0.16493 | 0.12894 | 0.021171 | 0.067991 | -0.074046 | -0.066266 | 121.4611 | 121.1235 | 121.1738 | 59.9135 | -121.3781 | 121.2843 | 121.3752 | 121.383 | 59.9811 | -121.4961
559.5312 | 121.6782 | -59.8938 | 61.5509 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.063316 | -0.003705 | 0.05946 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0086004 | 0.062487 | -57.2196 | -0.026065 | -59.8877 | 61.5078 | 61.1748 | 61.2297 | -59.8775 | -59.8152 | 0.036989 | -59.923 | 61.331 | 61.4219 | 61.4389 | -59.9864 | 0.01625 | -0.043075 | 2.6742 | 0.006058 | -0.010192 | -0.37611 | -0.32122 | -0.092596 | -0.21986 | 0.078581 | -0.029183 | 0.063413 | -0.12898 | -0.11204 | 121.4016 | 121.0686 | 121.1235 | 59.8677 | -121.4285 | 121.2248 | 121.3157 | 121.3327 | 59.9308 | -121.5373
561.2969 | 121.7606 | -59.8114 | 61.5967 | 1.4211e-13 | -0.016961 | -0.00073712 | 0.06353 | -0.0039186 | 0.05946 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0086004 | 0.062273 | -57.2608 | -0.021486 | -59.8374 | 61.5673 | 61.2343 | 61.2846 | -59.8226 | -59.7649 | 0.03241 | -59.8726 | 61.386 | 61.4723 | 61.4892 | -59.936 | -0.0112 | -0.029333 | 2.5506 | -0.025978 | -0.014778 | -0.36236 | -0.31206 | -0.12463 | -0.2107 | 0.046549 | -0.061216 | 0.063411 | -0.12439 | -0.10746 | 121.3787 | 121.0457 | 121.096 | 59.7899 | -121.4193 | 121.1974 | 121.2837 | 121.3006 | 59.8438 | -121.5327
563 | 121.6965 | -59.7931 | 61.6745 | 1.4211e-13 | -0.016748 | -0.0011645 | 0.063316 | -0.003705 | 0.059247 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0086004 | 0.062273 | -57.2242 | -0.026065 | -59.8282 | 61.5765 | 61.2435 | 61.2846 | -59.8134 | -59.7511 | 0.036989 | -59.8635 | 61.3997 | 61.4906 | 61.5075 | -59.9223 | -0.020353 | -0.097996 | 2.5689 | -0.035132 | -0.014779 | -0.43103 | -0.38988 | -0.1292 | -0.27478 | 0.041975 | -0.070368 | 0.058833 | -0.1839 | -0.16696 | 121.3696 | 121.0366 | 121.0777 | 59.767 | -121.4879 | 121.1928 | 121.2837 | 121.3006 | 59.8301 | -121.5968
564.7969 | 121.6461 | -60.1868 | 61.3358 | 1.4211e-13 | -0.016961 | -0.00095092 | 0.06353 | -0.0034912 | 0.05946 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064058 | 0.0086004 | 0.062487 | -57.5401 | -0.021486 | -60.1899 | 61.2011 | 60.8772 | 60.9321 | -60.1889 | -60.1174 | 0.027831 | -60.2252 | 61.0334 | 61.1243 | 61.1458 | -60.2886 | -0.002147 | -0.13468 | 2.6466 | -0.003139 | -0.000992 | -0.45859 | -0.40368 | -0.10183 | -0.30232 | 0.069355 | -0.038409 | 0.06342 | -0.21144 | -0.18992 | 121.3878 | 121.0639 | 121.1188 | 60.1653 | -121.5247 | 121.2202 | 121.3111 | 121.3326 | 60.2146 | -121.6244
566.4844 | 121.7194 | -60.2188 | 61.2167 | 1.4211e-13 | -0.017175 | -0.0011645 | 0.063103 | -0.003705 | 0.05946 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.0083866 | 0.062273 | -57.6866 | -0.021486 | -60.2906 | 61.1095 | 60.7764 | 60.8313 | -60.2851 | -60.2136 | 0.03241 | -60.3351 | 60.9281 | 61.019 | 61.0405 | -60.3939 | -0.066262 | -0.10723 | 2.5322 | -0.071818 | -0.005556 | -0.44031 | -0.38539 | -0.1751 | -0.2886 | 0.005245 | -0.11625 | 0.058844 | -0.19773 | -0.17621 | 121.3283 | 120.9952 | 121.0502 | 60.1973 | -121.5018 | 121.1469 | 121.2378 | 121.2593 | 60.2512 | -121.6106
568.25 | 121.6415 | -60.1547 | 61.3495 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.063316 | -0.0039186 | 0.05946 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064058 | 0.0086004 | 0.062487 | -57.4577 | -0.026065 | -60.1304 | 61.2606 | 60.9367 | 60.9824 | -60.1248 | -60.0533 | 0.046146 | -60.1748 | 61.0838 | 61.1747 | 61.1962 | -60.2428 | 0.029914 | -0.088892 | 2.697 | 0.024335 | -0.005579 | -0.4128 | -0.36705 | -0.088085 | -0.26569 | 0.10141 | -0.020087 | 0.067998 | -0.17481 | -0.15329 | 121.4153 | 121.0914 | 121.1372 | 60.1287 | -121.4743 | 121.2385 | 121.3294 | 121.3509 | 60.2009 | -121.5923
569.9375 | 121.756 | -60.1685 | 61.2396 | 1.4211e-13 | -0.017175 | -0.00073712 | 0.063316 | -0.0039186 | 0.059247 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.008814 | 0.062273 | -57.5356 | -0.016908 | -60.1762 | 61.2194 | 60.8863 | 60.9275 | -60.166 | -60.0991 | 0.036989 | -60.216 | 61.0426 | 61.1335 | 61.1367 | -60.284 | 0.002436 | -0.020234 | 2.6329 | -0.007715 | -0.010151 | -0.3533 | -0.31213 | -0.11556 | -0.19703 | 0.069359 | -0.047563 | 0.067999 | -0.10615 | -0.10295 | 121.3878 | 121.0548 | 121.0959 | 60.1515 | -121.4056 | 121.2111 | 121.3019 | 121.3051 | 60.2054 | -121.5236
571.6406 | 121.7148 | -60.2051 | 61.2122 | 1.4211e-13 | -0.017175 | -0.0011645 | 0.06353 | -0.003705 | 0.059247 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064058 | 0.008814 | 0.062273 | -57.6088 | -0.021486 | -60.167 | 61.2331 | 60.8955 | 60.955 | -60.1569 | -60.0854 | 0.036989 | -60.2069 | 61.0563 | 61.1472 | 61.155 | -60.2657 | 0.048215 | 0.020967 | 2.5963 | 0.038062 | -0.010153 | -0.31668 | -0.25719 | -0.060625 | -0.15583 | 0.11972 | -0.001784 | 0.058841 | -0.064951 | -0.057171 | 121.4382 | 121.1006 | 121.16 | 60.1836 | -121.369 | 121.2614 | 121.3523 | 121.3601 | 60.2421 | -121.4779
573.3906 | 121.756 | -59.9213 | 61.4685 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.063316 | -0.0034912 | 0.059247 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.008814 | 0.062273 | -57.3341 | -0.016908 | -59.9335 | 61.4529 | 61.1244 | 61.1839 | -59.9279 | -59.8518 | 0.036989 | -59.9733 | 61.2853 | 61.3716 | 61.3931 | -60.0322 | -0.006652 | -0.015619 | 2.5872 | -0.012258 | -0.005606 | -0.34408 | -0.28461 | -0.11092 | -0.18325 | 0.069417 | -0.052083 | 0.058836 | -0.096947 | -0.075431 | 121.3742 | 121.0457 | 121.1052 | 59.9044 | -121.3964 | 121.2065 | 121.2928 | 121.3143 | 59.9583 | -121.5007
575.1719 | 121.6461 | -59.8846 | 61.5921 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.063316 | -0.003705 | 0.059674 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.008814 | 0.062273 | -57.3295 | -0.021486 | -59.9335 | 61.4666 | 61.1336 | 61.1885 | -59.9233 | -59.8473 | 0.041567 | -59.9688 | 61.2898 | 61.3899 | 61.3977 | -60.0276 | -0.038694 | -0.12548 | 2.5551 | -0.048879 | -0.010185 | -0.45852 | -0.40363 | -0.14296 | -0.30227 | 0.037375 | -0.084126 | 0.058835 | -0.20223 | -0.19445 | 121.3513 | 121.0182 | 121.0731 | 59.8632 | -121.5154 | 121.1745 | 121.2745 | 121.2823 | 59.9262 | -121.6197
576.9375 | 121.7056 | -60.1318 | 61.2991 | 1.4211e-13 | -0.017602 | -0.00073712 | 0.063103 | -0.0039186 | 0.059247 | 0.012972 | -8.1262e-05 | 0.00015807 | 0.064485 | 0.0086004 | 0.062273 | -57.5905 | -0.021486 | -60.1395 | 61.2652 | 60.9275 | 60.9779 | -60.1248 | -60.067 | 0.046146 | -60.184 | 61.0792 | 61.1701 | 61.187 | -60.2428 | 0.007026 | -0.03396 | 2.5413 | -0.00771 | -0.014736 | -0.3716 | -0.32127 | -0.11097 | -0.21991 | 0.064789 | -0.052133 | 0.05884 | -0.12903 | -0.11209 | 121.397 | 121.0594 | 121.1097 | 60.1103 | -121.4239 | 121.2111 | 121.3019 | 121.3189 | 60.178 | -121.5419
578.6406 | 121.7102 | -60.0815 | 61.3358 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.063316 | -0.0039186 | 0.05946 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064058 | 0.0083866 | 0.06206 | -57.5447 | -0.021486 | -60.0846 | 61.311 | 60.9825 | 61.0374 | -60.0836 | -60.0121 | 0.041567 | -60.1244 | 61.1296 | 61.225 | 61.2374 | -60.1879 | -0.002118 | -0.024797 | 2.5368 | -0.003125 | -0.001007 | -0.35328 | -0.29838 | -0.10638 | -0.20617 | 0.06938 | -0.042964 | 0.063417 | -0.11071 | -0.098352 | 121.3924 | 121.064 | 121.1189 | 60.06 | -121.4194 | 121.2111 | 121.3065 | 121.3189 | 60.123 | -121.5236
580.3906 | 121.637 | -60.26 | 61.2167 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.063103 | -0.0034912 | 0.05946 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0086004 | 0.062487 | -57.7141 | -0.021486 | -60.2906 | 61.1095 | 60.7902 | 60.8359 | -60.2713 | -60.1998 | 0.027831 | -60.3168 | 60.9419 | 61.0282 | 61.0451 | -60.3939 | -0.011326 | -0.10723 | 2.5459 | -0.030619 | -0.019293 | -0.42657 | -0.38081 | -0.1339 | -0.27487 | 0.06018 | -0.056741 | 0.077159 | -0.18857 | -0.17163 | 121.3695 | 121.0502 | 121.0959 | 60.2385 | -121.4881 | 121.2019 | 121.2882 | 121.3051 | 60.2878 | -121.6106
582.0781 | 121.7148 | -60.5759 | 60.8368 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.063744 | -0.0039186 | 0.059247 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0086004 | 0.06206 | -57.998 | -0.030644 | -60.5653 | 60.8394 | 60.4925 | 60.5566 | -60.5598 | -60.4883 | 0.036989 | -60.6006 | 60.6534 | 60.7534 | 60.7612 | -60.6641 | 0.016059 | 0.002591 | 2.5779 | 0.010541 | -0.005518 | -0.34426 | -0.28017 | -0.088193 | -0.18337 | 0.087579 | -0.024764 | 0.063429 | -0.083344 | -0.075565 | 121.4153 | 121.0684 | 121.1325 | 60.5452 | -121.3966 | 121.2293 | 121.3293 | 121.3371 | 60.6129 | -121.5009
583.8438 | 121.6782 | -60.6491 | 60.8139 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.06353 | -0.0032776 | 0.059033 | -0.0099194 | 0.00013254 | -0.00026913 | 0.063844 | 0.0086004 | 0.062487 | -58.0209 | -0.026065 | -60.6477 | 60.7524 | 60.4193 | 60.4742 | -60.6468 | -60.5753 | 0.036989 | -60.6876 | 60.5756 | 60.6619 | 60.6834 | -60.7511 | 0.002301 | -0.06151 | 2.6282 | 0.001374 | -0.000927 | -0.39464 | -0.33969 | -0.10195 | -0.23832 | 0.073825 | -0.038518 | 0.063431 | -0.15203 | -0.13051 | 121.4015 | 121.0684 | 121.1233 | 60.623 | -121.4607 | 121.2247 | 121.311 | 121.3325 | 60.6861 | -121.565
585.5469 | 121.7514 | -61.4319 | 59.9533 | 1.4211e-13 | -0.017389 | -0.0011645 | 0.063316 | -0.003705 | 0.05946 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.008814 | 0.062487 | -58.8633 | -0.030644 | -61.3986 | 59.9832 | 59.6592 | 59.7187 | -61.3978 | -61.3216 | 0.018674 | -61.4431 | 59.8156 | 59.9018 | 59.9142 | -61.5111 | 0.034133 | 0.029917 | 2.5686 | 0.033312 | -0.000821 | -0.29414 | -0.23457 | -0.079257 | -0.13775 | 0.11027 | -0.011229 | 0.068028 | -0.051481 | -0.039122 | 121.4151 | 121.0911 | 121.1506 | 61.4012 | -121.3511 | 121.2474 | 121.3337 | 121.3461 | 61.4506 | -121.4644
587.3281 | 121.7651 | -60.7773 | 60.6171 | 1.4211e-13 | -0.017175 | -0.00095092 | 0.063103 | -0.0039186 | 0.05946 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.063844 | 0.008814 | 0.062273 | -58.3139 | -0.021486 | -60.895 | 60.4914 | 60.1766 | 60.2178 | -60.8849 | -60.818 | 0.046146 | -60.9303 | 60.3283 | 60.4101 | 60.4361 | -60.9937 | -0.10763 | -0.12564 | 2.4634 | -0.11768 | -0.01005 | -0.44048 | -0.39925 | -0.21645 | -0.28872 | -0.040672 | -0.15302 | 0.063436 | -0.20701 | -0.18092 | 121.2687 | 120.9539 | 120.9951 | 60.7558 | -121.502 | 121.1056 | 121.1873 | 121.2134 | 60.8234 | -121.6108
589.0312 | 121.7789 | -60.4843 | 60.9009 | 1.4211e-13 | -0.017602 | -0.00073712 | 0.062889 | -0.0034912 | 0.059247 | -0.0022889 | 0.00013254 | -0.00026913 | 0.064058 | 0.008814 | 0.062273 | -58.0575 | -0.021486 | -60.5562 | 60.8714 | 60.6711 | 60.5887 | -60.5506 | -60.4837 | 0.041567 | -60.5869 | 60.6672 | 60.7626 | 60.807 | -60.6641 | -0.066336 | -0.029447 | 2.4268 | -0.071856 | -0.00552 | -0.22977 | -0.3122 | -0.17975 | -0.23372 | 0.000604 | -0.10258 | 0.077165 | -0.13827 | -0.093866 | 121.3557 | 121.1554 | 121.073 | 60.4628 | -121.4515 | 121.1515 | 121.2469 | 121.2913 | 60.5259 | -121.5649
590.7969 | 121.6599 | -62.4481 | 59.0332 | 1.4211e-13 | -0.017602 | -0.0011645 | 0.063316 | -0.0039186 | 0.05946 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0092414 | 0.06206 | -59.8614 | -0.026065 | -62.4836 | 58.9394 | 58.7571 | 58.6794 | -62.4921 | -62.4342 | 0.023253 | -62.51 | 58.7259 | 58.8167 | 58.8794 | -62.6055 | -0.043994 | -0.093851 | 2.5867 | -0.035506 | 0.008488 | -0.27608 | -0.3538 | -0.15736 | -0.30733 | 0.01388 | -0.061834 | 0.095525 | -0.2165 | -0.15378 | 121.3875 | 121.2052 | 121.1275 | 62.4221 | -121.5253 | 121.174 | 121.2648 | 121.3275 | 62.4714 | -121.6387
592.5781 | 121.7285 | -62.6266 | 58.754 | 1.4211e-13 | -0.017389 | -0.00073712 | 0.063316 | -0.0041322 | 0.05946 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0086004 | 0.061846 | -59.898 | -0.035222 | -62.5477 | 58.8798 | 58.6884 | 58.6153 | -62.5562 | -62.5029 | 0.009516 | -62.5832 | 58.6709 | 58.7572 | 58.8245 | -62.6604 | 0.070429 | 0.12587 | 2.7286 | 0.078926 | 0.008497 | -0.065532 | -0.13867 | -0.033777 | -0.083035 | 0.12373 | 0.043435 | 0.077212 | 0.00321 | 0.070512 | 121.5065 | 121.3151 | 121.2419 | 62.5914 | -121.3102 | 121.2976 | 121.3838 | 121.4511 | 62.6362 | -121.4144
594.3438 | 121.6461 | -63.4964 | 57.9483 | 1.4211e-13 | -0.017602 | -0.00073712 | 0.063103 | -0.0039186 | 0.05946 | -0.0022889 | -8.1262e-05 | -0.00048293 | 0.064058 | 0.0090276 | 0.062273 | -60.6855 | -0.039801 | -63.3764 | 58.0374 | 57.8551 | 57.7728 | -63.3896 | -63.3408 | 0.018674 | -63.4074 | 57.8239 | 57.9147 | 57.9866 | -63.5029 | 0.10681 | 0.089107 | 2.8109 | 0.12001 | 0.013194 | -0.093232 | -0.17547 | -0.006528 | -0.12439 | 0.15557 | 0.089018 | 0.095546 | -0.033589 | 0.038291 | 121.5338 | 121.3515 | 121.2692 | 63.4566 | -121.3379 | 121.3203 | 121.4111 | 121.483 | 63.5151 | -121.4512
596.0938 | 121.7926 | -64.2883 | 57.1381 | 1.4211e-13 | -0.017389 | -0.00073712 | 0.063316 | -0.0039186 | 0.059674 | -0.0099194 | 0.00034614 | -0.00048293 | 0.063631 | 0.008814 | 0.062487 | -61.6744 | -0.030644 | -64.2646 | 57.108 | 56.9713 | 56.8937 | -64.2733 | -64.2154 | 0.009516 | -64.2911 | 56.9403 | 57.0219 | 57.0983 | -64.3912 | 0.015014 | -0.030065 | 2.6139 | 0.023753 | 0.008739 | -0.16672 | -0.24432 | -0.10289 | -0.1978 | 0.072972 | -0.002742 | 0.10015 | -0.11618 | -0.039717 | 121.3963 | 121.2597 | 121.1821 | 64.2577 | -121.4114 | 121.2286 | 121.3102 | 121.3867 | 64.2978 | -121.5293
597.8594 | 121.6461 | -63.0432 | 58.4427 | 1.4211e-13 | -0.017602 | -0.00073712 | 0.063316 | -0.0039186 | 0.059247 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.008814 | 0.06206 | -60.3879 | -0.035222 | -63.0513 | 58.3121 | 58.1756 | 58.1025 | -63.0645 | -63.0157 | 0.027831 | -63.0915 | 58.1444 | 58.2306 | 58.3117 | -63.1824 | -0.021267 | -0.13058 | 2.6553 | -0.008119 | 0.013148 | -0.26709 | -0.34019 | -0.1392 | -0.29828 | 0.027477 | -0.048237 | 0.09096 | -0.21205 | -0.13101 | 121.3553 | 121.2188 | 121.1457 | 63.008 | -121.5072 | 121.1876 | 121.2739 | 121.3549 | 63.071 | -121.6251
599.5625 | 121.6782 | -63.7848 | 57.6691 | 1.4211e-13 | -0.017389 | -0.0013783 | 0.06353 | -0.0039186 | 0.059247 | -0.0022889 | 0.00034614 | -0.00048293 | 0.064058 | 0.0090276 | 0.06206 | -61.1067 | -0.030644 | -63.793 | 57.5842 | 57.443 | 57.3653 | -63.7971 | -63.7438 | 0.023253 | -63.824 | 57.4073 | 57.4935 | 57.5699 | -63.9104 | -0.012318 | -0.084917 | 2.6781 | -0.008224 | 0.004094 | -0.2261 | -0.30373 | -0.12565 | -0.2618 | 0.041039 | -0.039253 | 0.086399 | -0.17558 | -0.099125 | 121.3689 | 121.2278 | 121.1501 | 63.7541 | -121.4662 | 121.1921 | 121.2783 | 121.3547 | 63.808 | -121.5795
601.3125 | 121.7606 | -64.325 | 57.1106 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.063316 | -0.003705 | 0.059247 | -0.0022889 | -0.00029486 | -0.00048293 | 0.064272 | 0.0090276 | 0.062487 | -61.4547 | -0.026065 | -64.1181 | 57.2499 | 57.1224 | 57.0403 | -64.1268 | -64.0688 | 0.023253 | -64.1491 | 57.0868 | 57.1776 | 57.2449 | -64.2493 | 0.19816 | 0.13933 | 2.8703 | 0.20688 | 0.008719 | 0.011847 | -0.070337 | 0.075677 | -0.023823 | 0.25611 | 0.17582 | 0.10014 | 0.066963 | 0.13426 | 121.5749 | 121.4474 | 121.3652 | 64.2989 | -121.2374 | 121.4117 | 121.5025 | 121.5698 | 64.3482 | -121.3599
603.0781 | 121.7651 | -64.769 | 56.6437 | 1.4211e-13 | -0.017602 | -0.0011645 | 0.062889 | -0.003705 | 0.059247 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.008814 | 0.062273 | -62.1597 | -0.039801 | -64.7499 | 56.6044 | 56.4585 | 56.3947 | -64.7816 | -64.7236 | 0.004938 | -64.7947 | 56.4366 | 56.5228 | 56.5993 | -64.8949 | -0.012595 | -0.039302 | 2.6093 | 0.019108 | 0.031703 | -0.18518 | -0.249 | -0.12591 | -0.20705 | 0.045387 | -0.025748 | 0.10016 | -0.12086 | -0.044399 | 121.3734 | 121.2275 | 121.1637 | 64.7292 | -121.4253 | 121.2056 | 121.2918 | 121.3683 | 64.7739 | -121.5386
604.8594 | 121.6873 | -63.8351 | 57.6141 | 1.4211e-13 | -0.017816 | -0.00095092 | 0.062889 | -0.0034912 | 0.059247 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063631 | 0.0090276 | 0.06206 | -61.1799 | -0.021486 | -63.8571 | 57.5063 | 57.3697 | 57.2875 | -63.8749 | -63.817 | 0.023253 | -63.8836 | 57.3477 | 57.4294 | 57.5058 | -63.9837 | -0.039806 | -0.10782 | 2.6552 | -0.021966 | 0.01784 | -0.24443 | -0.32663 | -0.14856 | -0.26639 | 0.018134 | -0.048422 | 0.10014 | -0.18475 | -0.1083 | 121.3415 | 121.2048 | 121.1226 | 63.8137 | -121.4891 | 121.1829 | 121.2645 | 121.341 | 63.8584 | -121.5978
606.5625 | 121.7239 | -65.3 | 56.0898 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.063103 | -0.003705 | 0.059247 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.063844 | 0.008814 | 0.06206 | -62.5123 | -0.030644 | -65.1299 | 56.2656 | 56.0876 | 56.0147 | -65.2028 | -65.0945 | 0.018674 | -65.1748 | 56.0612 | 56.1474 | 56.2238 | -65.2703 | 0.09715 | 0.17579 | 2.7877 | 0.17012 | 0.072966 | -0.002177 | -0.07513 | 0.029638 | -0.028593 | 0.20552 | 0.12523 | 0.095587 | 0.05759 | 0.13405 | 121.5656 | 121.3876 | 121.3146 | 65.2693 | -121.2926 | 121.3612 | 121.4474 | 121.5238 | 65.3187 | -121.3601
608.3438 | 121.7285 | -66.9388 | 54.4785 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.063103 | -0.0039186 | 0.059674 | -0.0022889 | 0.00034614 | -0.00048293 | 0.064058 | 0.0090276 | 0.06206 | -64.22 | -0.035222 | -66.8513 | 54.5258 | 54.3522 | 54.2885 | -66.8833 | -66.8069 | -0.00422 | -66.8872 | 54.3351 | 54.4167 | 54.4885 | -67.0011 | 0.055479 | 0.047331 | 2.7188 | 0.087477 | 0.031998 | -0.12626 | -0.18994 | -0.062361 | -0.14336 | 0.13187 | 0.051582 | 0.11394 | -0.061793 | 0.010087 | 121.4646 | 121.291 | 121.2273 | 66.9036 | -121.3618 | 121.2739 | 121.3554 | 121.4273 | 66.9346 | -121.4796
610.1094 | 121.7468 | -67.3737 | 54.0756 | 1.4211e-13 | -0.017816 | -0.00073712 | 0.063316 | -0.0039186 | 0.05946 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.0090276 | 0.062273 | -64.7557 | -0.035222 | -67.3595 | 54.013 | 53.8531 | 53.7757 | -67.3916 | -67.3243 | 0.000359 | -67.4 | 53.8269 | 53.8947 | 53.9757 | -67.5186 | -0.017907 | -0.062616 | 2.618 | 0.014163 | 0.03207 | -0.22253 | -0.29991 | -0.14489 | -0.24874 | 0.049355 | -0.026359 | 0.11853 | -0.18092 | -0.099884 | 121.3867 | 121.2267 | 121.1494 | 67.3384 | -121.4672 | 121.2005 | 121.2684 | 121.3494 | 67.374 | -121.5942
611.8125 | 121.7102 | -68.7469 | 52.6428 | 1.4211e-13 | -0.017816 | -0.0011645 | 0.062889 | -0.0039186 | 0.05946 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.0090276 | 0.06206 | -66.0468 | -0.044379 | -68.6277 | 52.7356 | 52.5756 | 52.5029 | -68.6691 | -68.5926 | -0.008798 | -68.6592 | 52.5357 | 52.6218 | 52.6983 | -68.7915 | 0.077864 | 0.092815 | 2.7002 | 0.11927 | 0.041406 | -0.067251 | -0.13996 | -0.044513 | -0.10707 | 0.15434 | 0.087787 | 0.1323 | -0.020973 | 0.055486 | 121.4826 | 121.3225 | 121.2498 | 68.7026 | -121.3119 | 121.2827 | 121.3688 | 121.4453 | 68.7382 | -121.4343
613.5312 | 121.6324 | -69.6899 | 51.7319 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.063316 | -0.0039186 | 0.059674 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063844 | 0.0090276 | 0.062701 | -66.8114 | -0.053537 | -69.4426 | 51.9161 | 51.7559 | 51.6879 | -69.4887 | -69.403 | -0.017956 | -69.4696 | 51.7299 | 51.8023 | 51.8833 | -69.6111 | 0.20123 | 0.18423 | 2.8786 | 0.24733 | 0.046099 | 0.02407 | -0.044 | 0.078872 | -0.001939 | 0.28691 | 0.22035 | 0.14148 | 0.070407 | 0.15144 | 121.606 | 121.4459 | 121.3778 | 69.6364 | -121.2206 | 121.4199 | 121.4922 | 121.5733 | 69.672 | -121.3429
615.2969 | 121.6278 | -69.3878 | 52.0981 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.062889 | -0.0034912 | 0.059674 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.008814 | 0.06206 | -66.4817 | -0.035222 | -69.1313 | 52.2457 | 52.0765 | 51.9992 | -69.1682 | -69.0825 | -0.008798 | -69.1582 | 52.0459 | 52.1182 | 52.2038 | -69.2951 | 0.21963 | 0.14767 | 2.9061 | 0.25653 | 0.036897 | -0.021615 | -0.098865 | 0.092686 | -0.052233 | 0.30529 | 0.22958 | 0.13689 | 0.02012 | 0.10574 | 121.6336 | 121.4643 | 121.387 | 69.3526 | -121.2663 | 121.4337 | 121.506 | 121.5916 | 69.379 | -121.3932
617.0625 | 121.7056 | -69.6075 | 51.8097 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.063316 | -0.0034912 | 0.05946 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.008814 | 0.062273 | -66.8617 | -0.048958 | -69.438 | 51.8841 | 51.7559 | 51.6925 | -69.4887 | -69.3939 | -0.031692 | -69.4742 | 51.7437 | 51.8114 | 51.8833 | -69.6065 | 0.11883 | 0.074365 | 2.7458 | 0.16951 | 0.050677 | -0.053749 | -0.11724 | 0.001054 | -0.066023 | 0.21367 | 0.13337 | 0.13232 | 0.001745 | 0.073625 | 121.4916 | 121.3635 | 121.3 | 69.5586 | -121.2984 | 121.3512 | 121.419 | 121.4909 | 69.5759 | -121.4162
618.8438 | 121.7194 | -69.0445 | 52.3636 | 1.4211e-13 | -0.017816 | -0.00095092 | 0.063316 | -0.003705 | 0.05946 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.008814 | 0.061846 | -66.3444 | -0.039801 | -68.8978 | 52.4335 | 52.31 | 52.2465 | -68.9392 | -68.8536 | -0.022535 | -68.9247 | 52.2931 | 52.37 | 52.4327 | -69.057 | 0.10525 | 0.069877 | 2.7001 | 0.1467 | 0.041443 | -0.053593 | -0.11712 | -0.012537 | -0.070497 | 0.1909 | 0.11977 | 0.13231 | 0.00644 | 0.069163 | 121.478 | 121.3545 | 121.291 | 69.0047 | -121.3028 | 121.3376 | 121.4145 | 121.4772 | 69.022 | -121.4206
620.5469 | 121.7194 | -70.1431 | 51.2741 | 1.4211e-13 | -0.017816 | -0.0011645 | 0.06353 | -0.003705 | 0.05946 | -0.0022889 | 0.00013254 | -0.00048293 | 0.064058 | 0.0090276 | 0.062273 | -67.2738 | -0.044379 | -69.8409 | 51.472 | 51.353 | 51.2895 | -69.8917 | -69.806 | -0.027113 | -69.8771 | 51.3224 | 51.4085 | 51.4758 | -70.014 | 0.25147 | 0.19789 | 2.8693 | 0.30221 | 0.050735 | 0.078889 | 0.015426 | 0.12912 | 0.048339 | 0.33716 | 0.26603 | 0.13691 | 0.13441 | 0.20171 | 121.6151 | 121.4961 | 121.4327 | 70.0987 | -121.1658 | 121.4656 | 121.5516 | 121.6189 | 70.116 | -121.2881
622.2812 | 121.6461 | -69.5389 | 51.915 | 1.4211e-13 | -0.017602 | -0.0011645 | 0.062889 | -0.003705 | 0.05946 | 0.0053411 | 0.00034614 | -0.00026913 | 0.063631 | 0.009455 | 0.062487 | -67.0403 | -0.039801 | -69.6166 | 51.7101 | 51.5819 | 51.5139 | -69.6581 | -69.5724 | -0.008798 | -69.6436 | 51.556 | 51.642 | 51.7002 | -69.7805 | -0.11925 | -0.2049 | 2.4986 | -0.077708 | 0.041544 | -0.33303 | -0.40109 | -0.24161 | -0.35903 | -0.03357 | -0.1047 | 0.1369 | -0.27295 | -0.2148 | 121.249 | 121.1208 | 121.0528 | 69.4991 | -121.5731 | 121.0948 | 121.1809 | 121.2391 | 69.5301 | -121.6955
624.0469 | 121.6278 | -67.9047 | 53.5629 | 1.4211e-13 | -0.017389 | -0.00095092 | 0.062889 | -0.004346 | 0.059247 | 0.012972 | 0.00013254 | -0.00026913 | 0.063631 | 0.0090276 | 0.06206 | -65.241 | -0.021486 | -67.8585 | 53.4682 | 53.3448 | 53.2766 | -67.9044 | -67.8142 | -0.00422 | -67.8899 | 53.3233 | 53.4048 | 53.4767 | -68.0131 | 0.00026 | -0.094748 | 2.6637 | 0.046136 | 0.045876 | -0.2181 | -0.28628 | -0.1084 | -0.23968 | 0.090439 | 0.014725 | 0.12312 | -0.15814 | -0.086256 | 121.3728 | 121.2495 | 121.1813 | 67.8832 | -121.4673 | 121.2279 | 121.3095 | 121.3813 | 67.9004 | -121.576
625.75 | 121.6415 | -75.0275 | 46.4539 | 1.4211e-13 | -0.01803 | -0.0011645 | 0.063103 | -0.0039186 | 0.05946 | 0.0053411 | 0.00013254 | -0.00048293 | 0.063631 | 0.0092414 | 0.062273 | -71.0967 | -0.10848 | -73.7737 | 47.5575 | 47.3876 | 47.3474 | -73.9074 | -73.7437 | -0.15074 | -73.8056 | 47.3666 | 47.4526 | 47.497 | -73.9747 | 1.1201 | 1.1036 | 3.9307 | 1.2538 | 0.13371 | 0.93379 | 0.8935 | 1.0528 | 0.91277 | 1.2838 | 1.2218 | 0.16905 | 0.99875 | 1.0432 | 122.5849 | 122.4151 | 122.3748 | 74.919 | -120.3612 | 122.3941 | 122.4801 | 122.5245 | 74.8767 | -120.4285
627.5312 | 121.7606 | -79.1428 | 42.1967 | 1.4211e-13 | -0.017602 | -0.0015919 | 0.062889 | -0.0039186 | 0.05946 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.0090276 | 0.06206 | -76.3527 | -0.16342 | -79.0616 | 42.2511 | 42.0761 | 42.0591 | -79.2052 | -79.0137 | -0.28352 | -79.0895 | 42.0556 | 42.1369 | 42.1904 | -79.2815 | -0.062428 | 0.054474 | 2.79 | 0.081182 | 0.14361 | -0.12056 | -0.13758 | -0.13877 | -0.14108 | 0.12901 | 0.053299 | 0.19207 | -0.059805 | -0.006239 | 121.3939 | 121.2189 | 121.2018 | 78.9793 | -121.4018 | 121.1983 | 121.2796 | 121.3332 | 78.8592 | -121.4782
629.2969 | 121.6827 | -74.4278 | 47.0306 | 1.4211e-13 | -0.017816 | -0.0013783 | 0.062889 | -0.0039186 | 0.05946 | -0.0099194 | 0.00034614 | -0.00026913 | 0.064058 | 0.0090276 | 0.062273 | -71.582 | -0.048958 | -74.2407 | 47.0859 | 46.8061 | 46.9353 | -74.2691 | -74.1466 | -0.13242 | -74.2131 | 46.9683 | 47.036 | 47.0529 | -74.3914 | 0.15869 | 0.055266 | 2.8457 | 0.18715 | 0.028458 | -0.22451 | -0.095356 | 0.036441 | -0.062341 | 0.28122 | 0.21466 | 0.17822 | 0.005314 | 0.022252 | 121.5137 | 121.2339 | 121.3631 | 74.3788 | -121.2997 | 121.3961 | 121.4637 | 121.4807 | 74.2954 | -121.422
631.0625 | 121.6644 | -81.0287 | 40.3976 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.062889 | -0.003705 | 0.05946 | 0.0053411 | 0.00013254 | -0.00069653 | 0.063844 | 0.0090276 | 0.06206 | -78.1749 | -0.081008 | -80.8196 | 40.4793 | 40.3407 | 40.2872 | -80.9131 | -80.772 | -0.27894 | -80.8294 | 40.3157 | 40.3787 | 40.4551 | -81.0444 | 0.11562 | 0.081649 | 2.8538 | 0.20911 | 0.093489 | -0.05696 | -0.11049 | -0.015628 | -0.081899 | 0.25677 | 0.19938 | 0.215 | -0.018978 | 0.057481 | 121.508 | 121.3694 | 121.3159 | 80.9477 | -121.3108 | 121.3445 | 121.4074 | 121.4839 | 80.7498 | -121.442
632.7969 | 121.6782 | -79.3488 | 42.1005 | 1.4211e-13 | -0.018243 | -0.00095092 | 0.063103 | -0.0034912 | 0.059247 | 0.0053411 | 0.00013254 | -0.00026913 | 0.063203 | 0.0086004 | 0.061846 | -76.4809 | -0.062694 | -79.1577 | 42.1046 | 42.0028 | 41.9446 | -79.2464 | -79.1099 | -0.26063 | -79.1765 | 41.9869 | 42.0499 | 42.1172 | -79.3823 | 0.10236 | 0.004095 | 2.8678 | 0.19103 | 0.088676 | -0.097691 | -0.15592 | -0.03351 | -0.11363 | 0.23885 | 0.1723 | 0.20581 | -0.050669 | 0.016633 | 121.4534 | 121.3516 | 121.2934 | 79.2861 | -121.3469 | 121.3357 | 121.3986 | 121.4659 | 79.0881 | -121.4828
634.5781 | 121.7789 | -86.5585 | 34.758 | 1.4211e-13 | -0.018457 | -0.0013783 | 0.063103 | -0.003705 | 0.05946 | -0.0022889 | 0.00034614 | -0.00026913 | 0.064058 | 0.0092414 | 0.062487 | -81.2653 | -0.2321 | -84.0336 | 37.2241 | 37.0713 | 37.0776 | -84.21 | -84.0183 | -0.61319 | -84.0848 | 37.0559 | 37.1324 | 37.1723 | -84.3182 | 2.3486 | 2.4661 | 5.2932 | 2.5249 | 0.17636 | 2.3133 | 2.3196 | 2.2403 | 2.2979 | 2.5403 | 2.4737 | 0.2334 | 2.3744 | 2.4143 | 123.7826 | 123.6299 | 123.6361 | 86.3264 | -118.968 | 123.6144 | 123.691 | 123.7308 | 85.9453 | -119.0762
636.3594 | 121.7285 | -87.6663 | 33.7234 | 1.4211e-13 | -0.01803 | -0.0013783 | 0.063103 | -0.003705 | 0.059674 | -0.0022889 | -0.00029486 | -0.00026913 | 0.063631 | 0.0090276 | 0.062487 | -84.9647 | -0.11764 | -87.5589 | 33.6438 | 33.5685 | 33.5337 | -87.6854 | -87.4935 | -0.6544 | -87.5601 | 33.567 | 33.6023 | 33.6834 | -87.821 | -0.019036 | -0.079691 | 2.7016 | 0.10745 | 0.12649 | -0.15499 | -0.18974 | -0.1547 | -0.15641 | 0.1728 | 0.10625 | 0.26095 | -0.12112 | -0.040078 | 121.3101 | 121.2348 | 121.2 | 87.5487 | -121.4088 | 121.2334 | 121.2687 | 121.3497 | 87.0119 | -121.5445
638.125 | 121.6141 | -81.1066 | 40.3519 | 1.4211e-13 | -0.017816 | -0.0013783 | 0.062675 | -0.003705 | 0.05946 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063631 | 0.008814 | 0.062487 | -80.954 | -0.062694 | -83.237 | 38.0619 | 37.9734 | 37.8834 | -83.2804 | -83.1025 | -0.49414 | -83.1645 | 37.967 | 37.9932 | 38.0926 | -83.4162 | -2.1739 | -2.29 | 0.15256 | -2.1304 | 0.043461 | -2.3785 | -2.4685 | -2.3096 | -2.3849 | -1.996 | -2.0579 | 0.25169 | -2.3587 | -2.2593 | 119.1685 | 119.0799 | 118.99 | 81.0439 | -123.6323 | 119.0735 | 119.0998 | 119.1991 | 80.6124 | -123.7681
639.8281 | 121.756 | -82.7133 | 38.6673 | 1.4211e-13 | -0.017816 | -0.0015919 | 0.062889 | -0.0039186 | 0.05946 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.0090276 | 0.062273 | -79.7499 | -0.10848 | -82.4358 | 38.8311 | 38.5549 | 38.648 | -82.5158 | -82.3516 | -0.55366 | -82.4228 | 38.7224 | 38.7807 | 38.7702 | -82.647 | 0.19757 | 0.16378 | 2.9634 | 0.27755 | 0.07998 | -0.11239 | -0.019284 | 0.066356 | 0.055132 | 0.36169 | 0.29055 | 0.2242 | 0.11344 | 0.1029 | 121.5444 | 121.2682 | 121.3613 | 82.6048 | -121.183 | 121.4357 | 121.4941 | 121.4835 | 82.1597 | -121.3143
641.5312 | 121.6782 | -84.8282 | 37.2299 | 1.4211e-13 | -0.018243 | -0.0011645 | 0.063103 | -0.0039186 | 0.059674 | -0.0022889 | 0.00013254 | -0.00048293 | 0.063417 | 0.0092414 | 0.062487 | -86.21 | -0.081008 | -88.7813 | 32.4534 | 32.3459 | 32.3066 | -88.9125 | -88.7206 | -0.7826 | -88.7689 | 32.3492 | 32.3798 | 32.47 | -89.039 | -4.0843 | -4.7765 | -1.3818 | -3.9531 | 0.13124 | -4.884 | -4.9233 | -4.2108 | -4.8808 | -3.8924 | -3.9407 | 0.27014 | -4.8501 | -4.7599 | 117.2816 | 117.1741 | 117.1348 | 84.7472 | -126.1424 | 117.1774 | 117.208 | 117.2982 | 84.0456 | -126.2689
643.3125 | 121.7743 | -89.0854 | 32.2678 | 1.4211e-13 | -0.018243 | -0.0013783 | 0.062675 | -0.003705 | 0.059247 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.064058 | 0.0092414 | 0.062273 | -86.3016 | -0.14511 | -88.9369 | 32.3343 | 32.2039 | 32.1876 | -89.0453 | -88.8626 | -0.91996 | -88.9245 | 32.2027 | 32.2562 | 32.3235 | -89.1901 | 0.04009 | 0.066579 | 2.7838 | 0.14846 | 0.10837 | -0.063826 | -0.080156 | -0.1047 | -0.065109 | 0.22283 | 0.16086 | 0.26556 | -0.011536 | 0.055766 | 121.4197 | 121.2893 | 121.273 | 88.9403 | -121.3131 | 121.288 | 121.3416 | 121.4089 | 88.1654 | -121.4579
645.0781 | 121.7651 | -89.5111 | 31.8375 | 1.4211e-13 | -0.01803 | -0.0011645 | 0.062675 | -0.0039186 | 0.059674 | 0.0053411 | 0.00013254 | -0.00048293 | 0.063844 | 0.0090276 | 0.062487 | -86.7594 | -0.14511 | -89.3948 | 31.8857 | 31.7735 | 31.7343 | -89.4895 | -89.2975 | -0.97491 | -89.3549 | 31.7677 | 31.8075 | 31.8886 | -89.6251 | 0.021654 | 0.048195 | 2.7517 | 0.11635 | 0.094695 | -0.063947 | -0.10314 | -0.11397 | -0.069768 | 0.21358 | 0.15618 | 0.27015 | -0.029941 | 0.051097 | 121.3968 | 121.2846 | 121.2454 | 89.366 | -121.3269 | 121.2788 | 121.3186 | 121.3997 | 88.5362 | -121.4625
646.7969 | 121.6278 | -90.9256 | 30.5008 | 1.4211e-13 | -0.017816 | -0.0015919 | 0.062675 | -0.0034912 | 0.05946 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063631 | 0.0092414 | 0.062273 | -88.252 | -0.14053 | -90.9239 | 30.3061 | 30.2029 | 30.1593 | -91.06 | -90.8589 | -1.126 | -90.9208 | 30.1973 | 30.2325 | 30.3089 | -91.2002 | -0.13443 | -0.19468 | 2.6736 | 0.001694 | 0.13612 | -0.29785 | -0.34151 | -0.27459 | -0.30352 | 0.066727 | 0.00475 | 0.27934 | -0.26831 | -0.19185 | 121.2317 | 121.1285 | 121.0849 | 90.7851 | -121.5608 | 121.1229 | 121.1581 | 121.2345 | 89.7996 | -121.701
648.5156 | 121.7606 | -87.5702 | 33.8242 | 1.4211e-13 | -0.017816 | -0.0013783 | 0.062889 | -0.0039186 | 0.059674 | -0.0022889 | 0.00034614 | -0.00048293 | 0.063417 | 0.0090276 | 0.062487 | -87.3363 | -0.021486 | -89.7793 | 31.4507 | 31.3889 | 31.3039 | -89.8924 | -89.6592 | -0.95201 | -89.7212 | 31.3923 | 31.4046 | 31.4399 | -90.0051 | -2.3222 | -2.3734 | 0.23391 | -2.2091 | 0.11306 | -2.4353 | -2.5202 | -2.4349 | -2.4319 | -2.0891 | -2.151 | 0.2839 | -2.4196 | -2.3843 | 119.0209 | 118.9591 | 118.8741 | 87.5487 | -123.7166 | 118.9624 | 118.9748 | 119.01 | 86.6182 | -123.8293
650.2969 | 121.7239 | -97.6044 | 23.7488 | 1.4211e-13 | -0.018243 | -0.0013783 | 0.062675 | -0.003705 | 0.059674 | -0.0022889 | -8.1262e-05 | -0.00048293 | 0.063417 | 0.0092414 | 0.062487 | -95.2248 | -0.22752 | -97.8051 | 23.3653 | 23.2979 | 23.2685 | -97.9696 | -97.6903 | -1.7762 | -97.7981 | 23.3066 | 23.3188 | 23.4044 | -98.1234 | -0.36525 | -0.3835 | 2.3795 | -0.20069 | 0.16456 | -0.45085 | -0.48029 | -0.51899 | -0.44214 | -0.085936 | -0.1937 | 0.32529 | -0.42999 | -0.34437 | 120.9696 | 120.9023 | 120.8729 | 97.3768 | -121.7184 | 120.911 | 120.9232 | 121.0088 | 95.8282 | -121.8721
652.0625 | 121.6599 | -90.4449 | 30.9769 | 1.4211e-13 | -0.018243 | -0.0013783 | 0.062889 | -0.0034912 | 0.059888 | 0.0053411 | 0.00013254 | -0.00048293 | 0.063417 | 0.0090276 | 0.062487 | -87.7209 | -0.18174 | -90.4157 | 30.8235 | 30.7158 | 30.6721 | -90.5838 | -90.3506 | -1.3229 | -90.4035 | 30.7101 | 30.7361 | 30.8217 | -90.6828 | -0.13887 | -0.15339 | 2.7241 | 0.029231 | 0.1681 | -0.26108 | -0.30478 | -0.23784 | -0.26681 | 0.094312 | 0.041492 | 0.27933 | -0.24074 | -0.15512 | 121.2684 | 121.1607 | 121.117 | 90.2632 | -121.5607 | 121.155 | 121.1811 | 121.2667 | 89.1221 | -121.6597
653.8281 | 121.6278 | -91.8594 | 29.5807 | 1.4211e-13 | -0.01803 | -0.0015919 | 0.062675 | -0.0039186 | 0.059888 | -0.0022889 | -0.00029486 | -0.00026913 | 0.063631 | 0.0092414 | 0.062487 | -89.4881 | -0.20005 | -92.1371 | 29.0745 | 28.9758 | 28.9368 | -92.2826 | -92.0768 | -1.4557 | -92.1342 | 28.9794 | 29.0054 | 29.0956 | -92.4273 | -0.42316 | -0.50616 | 2.3713 | -0.27771 | 0.14545 | -0.60489 | -0.64389 | -0.56788 | -0.6013 | -0.21737 | -0.27477 | 0.29311 | -0.57527 | -0.48508 | 120.934 | 120.8352 | 120.7962 | 91.6594 | -121.8633 | 120.8388 | 120.8649 | 120.955 | 90.4038 | -122.008
655.5312 | 121.5546 | -92.926 | 28.5004 | 1.4211e-13 | -0.018457 | -0.0013783 | 0.062675 | -0.0039186 | 0.059674 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063417 | 0.0092414 | 0.06206 | -90.1795 | -0.20463 | -92.9109 | 28.3008 | 28.2386 | 28.1996 | -93.0244 | -92.814 | -1.5427 | -92.876 | 28.2331 | 28.2637 | 28.3493 | -93.1645 | -0.098358 | -0.19958 | 2.7466 | 0.015147 | 0.11351 | -0.26178 | -0.30072 | -0.23848 | -0.26727 | 0.11204 | 0.050068 | 0.28855 | -0.23668 | -0.15107 | 121.2268 | 121.1646 | 121.1257 | 92.7214 | -121.5247 | 121.1591 | 121.1897 | 121.2753 | 91.3834 | -121.6649
657.2812 | 121.6827 | -43.5699 | 77.8702 | 1.4211e-13 | -0.017816 | -0.00073712 | 0.063316 | -0.003064 | 0.059033 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0090276 | 0.061846 | -43.5303 | 0.13876 | -43.5982 | 77.9397 | 77.691 | 77.5936 | -43.4438 | -43.4967 | 0.56354 | -43.6136 | 77.6992 | 77.8271 | 77.844 | -43.4981 | 0.12616 | 0.069484 | 0.039682 | -0.028272 | -0.15443 | -0.17921 | -0.27657 | 0.071871 | -0.17102 | 0.07325 | -0.043672 | -0.11554 | -0.043122 | -0.026185 | 121.5096 | 121.2609 | 121.1636 | 43.7087 | -121.314 | 121.2691 | 121.397 | 121.4139 | 44.1335 | -121.3683
659.0469 | 121.6415 | -43.6798 | 77.7466 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.063316 | -0.003064 | 0.059247 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063631 | 0.0090276 | 0.061633 | -43.7546 | 0.12045 | -43.8271 | 77.7062 | 77.4666 | 77.3738 | -43.6819 | -43.7348 | 0.51317 | -43.8426 | 77.4748 | 77.6073 | 77.6105 | -43.7408 | -0.002082 | -0.040418 | -0.074795 | -0.14732 | -0.14524 | -0.27998 | -0.37275 | -0.060942 | -0.27177 | -0.054979 | -0.16274 | -0.1018 | -0.1393 | -0.1361 | 121.386 | 121.1464 | 121.0536 | 43.8003 | -121.4285 | 121.1546 | 121.2871 | 121.2903 | 44.193 | -121.4873
660.75 | 121.5729 | -43.4784 | 78.0304 | 1.4211e-13 | -0.017816 | -0.00073712 | 0.063103 | -0.0028504 | 0.059247 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063844 | 0.009455 | 0.061633 | -43.5211 | 0.11587 | -43.5936 | 77.9534 | 77.7093 | 77.6028 | -43.4484 | -43.4967 | 0.49028 | -43.6136 | 77.7221 | 77.8454 | 77.8532 | -43.5027 | 0.030027 | -0.076999 | -0.042713 | -0.11525 | -0.14527 | -0.32111 | -0.42763 | -0.02426 | -0.30835 | -0.018302 | -0.13522 | -0.11096 | -0.18502 | -0.17724 | 121.4318 | 121.1877 | 121.0812 | 43.5943 | -121.4788 | 121.2004 | 121.3238 | 121.3315 | 43.9687 | -121.5331
662.5156 | 121.6644 | -41.5924 | 79.834 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.06353 | -0.003064 | 0.059033 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.0090276 | 0.06206 | -41.6714 | 0.12503 | -41.7532 | 79.826 | 79.5729 | 79.4754 | -41.5802 | -41.6515 | 0.55438 | -41.7592 | 79.5809 | 79.7089 | 79.7212 | -41.6391 | 0.012241 | -0.008026 | -0.079032 | -0.16076 | -0.17301 | -0.26107 | -0.35857 | -0.046668 | -0.25306 | -0.059069 | -0.16683 | -0.12017 | -0.12512 | -0.11276 | 121.4184 | 121.1653 | 121.0678 | 41.7174 | -121.4142 | 121.1733 | 121.3013 | 121.3136 | 42.1468 | -121.4731
664.2969 | 121.7102 | -41.4276 | 79.9713 | 1.4211e-13 | -0.018243 | -0.00095092 | 0.063316 | -0.0032776 | 0.059247 | 0.0053411 | 0.00013254 | -0.00026913 | 0.063631 | 0.0092414 | 0.061846 | -41.3555 | 0.12045 | -41.4235 | 80.1556 | 79.9301 | 79.8005 | -41.2688 | -41.3401 | 0.55438 | -41.4479 | 79.906 | 80.0385 | 80.0371 | -41.3689 | 0.15881 | 0.18429 | 0.072082 | 0.004077 | -0.15474 | -0.041247 | -0.17082 | 0.058687 | -0.06532 | 0.087488 | -0.020276 | -0.078963 | 0.067208 | 0.065831 | 121.5832 | 121.3577 | 121.2281 | 41.5481 | -121.2401 | 121.3336 | 121.4661 | 121.4648 | 41.982 | -121.3402
666 | 121.7239 | -42.2699 | 79.1336 | 1.4211e-13 | -0.017602 | -0.00073712 | 0.063316 | -0.0032776 | 0.059033 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.0090276 | 0.061846 | -42.2987 | 0.12045 | -42.3575 | 79.2033 | 79.0143 | 78.8573 | -42.2121 | -42.265 | 0.51317 | -42.3774 | 78.9537 | 79.0908 | 79.1031 | -42.3167 | 0.057839 | 0.069691 | -0.028781 | -0.087607 | -0.14545 | -0.11933 | -0.27631 | -0.046843 | -0.17994 | 0.004874 | -0.10747 | -0.060626 | -0.042855 | -0.030497 | 121.4732 | 121.2842 | 121.1272 | 42.3903 | -121.3457 | 121.2236 | 121.3606 | 121.373 | 42.7831 | -121.4503
667.7812 | 121.6599 | -37.7884 | 83.6517 | 1.4211e-13 | -0.017816 | -0.00073712 | 0.063316 | -0.003064 | 0.059247 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.0092414 | 0.061846 | -37.5372 | 0.15708 | -37.6052 | 84.0014 | 83.7443 | 83.6374 | -37.4179 | -37.5077 | 0.73753 | -37.6201 | 83.7382 | 83.8754 | 83.8877 | -37.5319 | 0.37047 | 0.34972 | 0.25124 | 0.18314 | -0.18733 | 0.092577 | -0.014372 | 0.25652 | 0.086461 | 0.28065 | 0.1683 | -0.088211 | 0.22366 | 0.23602 | 121.7898 | 121.5327 | 121.4258 | 37.9455 | -121.0697 | 121.5266 | 121.6638 | 121.6761 | 38.5259 | -121.1836
669.4688 | 121.6919 | -44.1376 | 77.2705 | 1.4211e-13 | -0.017816 | -0.0011645 | 0.062889 | -0.0032776 | 0.058819 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.0092414 | 0.061633 | -44.5787 | 0.0884 | -44.6054 | 76.9141 | 76.7157 | 76.6138 | -44.5244 | -44.5681 | 0.41244 | -44.6713 | 76.669 | 76.7969 | 76.855 | -44.6245 | -0.38684 | -0.35641 | -0.44114 | -0.46787 | -0.081025 | -0.55485 | -0.65672 | -0.48689 | -0.60151 | -0.43054 | -0.53373 | -0.046836 | -0.47364 | -0.41549 | 121.0517 | 120.8532 | 120.7514 | 44.226 | -121.7949 | 120.8066 | 120.9344 | 120.9926 | 44.55 | -121.895
671.2344 | 121.6553 | -45.4102 | 76.0437 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.063103 | -0.003064 | 0.059033 | 0.012972 | 0.00013254 | -0.00026913 | 0.064058 | 0.009455 | 0.061633 | -45.4898 | 0.074664 | -45.5165 | 75.9755 | 75.7999 | 75.6935 | -45.4219 | -45.4747 | 0.36208 | -45.5733 | 75.7487 | 75.8812 | 75.9485 | -45.5311 | -0.011728 | -0.068167 | -0.079658 | -0.10636 | -0.094634 | -0.24383 | -0.35022 | -0.12091 | -0.29498 | -0.064543 | -0.16315 | -0.042236 | -0.16255 | -0.095249 | 121.3857 | 121.21 | 121.1036 | 45.4848 | -121.4656 | 121.1589 | 121.2913 | 121.3586 | 45.7722 | -121.5748
672.9375 | 121.7422 | -42.2379 | 79.1565 | 1.4211e-13 | -0.017816 | -0.00095092 | 0.063316 | -0.003064 | 0.058819 | -0.0099194 | 0.00013254 | 0.00015807 | 0.064058 | 0.0090276 | 0.061633 | -41.6852 | 0.074664 | -41.7349 | 79.8305 | 79.5912 | 79.4891 | -41.5847 | -41.6606 | 0.46281 | -41.7638 | 79.5855 | 79.718 | 79.7258 | -41.6986 | 0.65311 | 0.67404 | 0.55268 | 0.503 | -0.15011 | 0.43473 | 0.33265 | 0.53925 | 0.429 | 0.57722 | 0.47404 | -0.065219 | 0.56153 | 0.5693 | 122.0684 | 121.8291 | 121.727 | 42.3125 | -120.7412 | 121.8234 | 121.9559 | 121.9637 | 42.7007 | -120.8551
674.7031 | 121.7239 | -42.7368 | 78.6438 | 1.4211e-13 | -0.018243 | -0.00095092 | 0.063103 | -0.0032776 | 0.059033 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.009455 | 0.061633 | -42.8435 | 0.10214 | -42.9069 | 78.6539 | 78.419 | 78.3079 | -42.757 | -42.8236 | 0.44907 | -42.9222 | 78.418 | 78.5551 | 78.5674 | -42.857 | -0.020134 | 0.010091 | -0.10669 | -0.17008 | -0.14995 | -0.22478 | -0.33593 | -0.12022 | -0.22582 | -0.08681 | -0.18542 | -0.065193 | -0.088745 | -0.076386 | 121.3907 | 121.1558 | 121.0447 | 42.839 | -121.4007 | 121.1548 | 121.2919 | 121.3042 | 43.1859 | -121.5008
676.3906 | 121.7194 | -42.3294 | 79.0787 | 1.4211e-13 | -0.018243 | -0.00095092 | 0.063316 | -0.003064 | 0.059033 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0090276 | 0.061419 | -42.4452 | 0.097557 | -42.4994 | 79.0659 | 78.822 | 78.7245 | -42.3494 | -42.4161 | 0.46739 | -42.5193 | 78.83 | 78.958 | 78.9658 | -42.4495 | -0.020018 | -0.012729 | -0.11578 | -0.17002 | -0.15001 | -0.25671 | -0.35415 | -0.12012 | -0.24863 | -0.086713 | -0.1899 | -0.06978 | -0.1207 | -0.11292 | 121.3954 | 121.1514 | 121.0539 | 42.427 | -121.4281 | 121.1595 | 121.2874 | 121.2952 | 42.7968 | -121.5282
678.1562 | 121.6461 | -42.2836 | 79.1977 | 1.4211e-13 | -0.01803 | -0.00052352 | 0.062889 | -0.003064 | 0.059033 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064058 | 0.0090276 | 0.061633 | -42.2941 | 0.11129 | -42.3621 | 79.2033 | 78.9685 | 78.871 | -42.2121 | -42.2696 | 0.47197 | -42.3819 | 78.972 | 79.0999 | 79.1031 | -42.3167 | 0.071572 | 0.005604 | -0.01047 | -0.078453 | -0.15002 | -0.2292 | -0.32666 | -0.03311 | -0.22571 | 0.014028 | -0.098315 | -0.065205 | -0.097785 | -0.094584 | 121.4869 | 121.2521 | 121.1547 | 42.3949 | -121.4098 | 121.2556 | 121.3835 | 121.3867 | 42.7556 | -121.5144
679.9531 | 121.669 | -41.5466 | 79.9164 | 1.4211e-13 | -0.018243 | -0.00095092 | 0.063103 | -0.0028504 | 0.058819 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.009455 | 0.061633 | -41.7355 | 0.11587 | -41.799 | 79.7756 | 79.5271 | 79.4342 | -41.6443 | -41.7202 | 0.5086 | -41.8188 | 79.5351 | 79.6631 | 79.68 | -41.7535 | -0.09764 | -0.14079 | -0.18891 | -0.25232 | -0.15468 | -0.38926 | -0.48218 | -0.20691 | -0.38125 | -0.17353 | -0.27213 | -0.065219 | -0.25331 | -0.23637 | 121.3222 | 121.0738 | 120.9808 | 41.6625 | -121.5607 | 121.0818 | 121.2097 | 121.2266 | 42.0552 | -121.6699
681.6562 | 121.7285 | -41.4642 | 79.9576 | 1.4211e-13 | -0.018243 | -0.00073712 | 0.063316 | -0.003064 | 0.058819 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.009455 | 0.061846 | -41.5249 | 0.11129 | -41.5884 | 80.0228 | 79.7973 | 79.6952 | -41.4336 | -41.4958 | 0.49486 | -41.6081 | 79.7457 | 79.8828 | 79.8906 | -41.5383 | 0.030592 | 0.065247 | -0.060697 | -0.12412 | -0.15471 | -0.1603 | -0.2624 | -0.074108 | -0.21184 | -0.031567 | -0.14391 | -0.069802 | -0.074732 | -0.066952 | 121.4871 | 121.2615 | 121.1594 | 41.5755 | -121.3912 | 121.21 | 121.3471 | 121.3549 | 41.9591 | -121.4959
683.4219 | 121.6415 | -40.3427 | 81.1478 | 1.4211e-13 | -0.018243 | -0.00030992 | 0.063103 | -0.0028504 | 0.059033 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.0092414 | 0.061419 | -40.4399 | 0.13419 | -40.4987 | 81.1171 | 80.8916 | 80.7803 | -40.3393 | -40.4061 | 0.55438 | -40.5276 | 80.8354 | 80.968 | 80.9803 | -40.444 | 0.003434 | -0.030703 | -0.09714 | -0.15601 | -0.15944 | -0.25613 | -0.36745 | -0.10129 | -0.31234 | -0.063355 | -0.18485 | -0.083563 | -0.17979 | -0.16743 | 121.4598 | 121.2344 | 121.123 | 40.4769 | -121.487 | 121.1781 | 121.3107 | 121.323 | 40.8971 | -121.5918
685.1875 | 121.756 | -47.0764 | 74.2676 | 1.4211e-13 | -0.018457 | -0.0011645 | 0.063316 | -0.0032776 | 0.059247 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.0090276 | 0.061846 | -47.1518 | 0.060928 | -47.1784 | 74.3594 | 74.1331 | 74.0406 | -47.1527 | -47.1322 | 0.2934 | -47.2308 | 74.0821 | 74.2145 | 74.2773 | -47.2161 | -0.076301 | 0.091785 | -0.075353 | -0.10202 | -0.025717 | -0.13443 | -0.22697 | -0.13966 | -0.18543 | -0.055776 | -0.15438 | -0.014725 | -0.053039 | 0.009684 | 121.4358 | 121.2096 | 121.117 | 47.1373 | -121.4203 | 121.1586 | 121.291 | 121.3537 | 47.3698 | -121.4837
686.9531 | 121.6278 | -46.6095 | 74.8672 | 1.4211e-13 | -0.018457 | -0.00073712 | 0.063103 | -0.0028504 | 0.058819 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0092414 | 0.061633 | -46.5978 | 0.065507 | -46.6199 | 74.9225 | 74.7009 | 74.5992 | -46.5346 | -46.5644 | 0.2934 | -46.6814 | 74.6499 | 74.7686 | 74.8404 | -46.6437 | 0.074935 | 0.055255 | 0.011713 | -0.010387 | -0.085322 | -0.16631 | -0.26805 | -0.034225 | -0.21737 | 0.045065 | -0.071857 | -0.037632 | -0.098699 | -0.026819 | 121.532 | 121.3104 | 121.2087 | 46.675 | -121.4018 | 121.2594 | 121.378 | 121.4499 | 46.9029 | -121.511
688.6719 | 121.6644 | -46.7056 | 74.762 | 1.4211e-13 | -0.018671 | -0.0011645 | 0.063316 | -0.0028504 | 0.059033 | -0.0022889 | 0.00055974 | -0.00026913 | 0.063844 | 0.0096686 | 0.061419 | -46.9549 | 0.074664 | -46.9724 | 74.5562 | 74.3438 | 74.2375 | -46.8917 | -46.9307 | 0.2934 | -47.0339 | 74.2928 | 74.4068 | 74.4925 | -47.0009 | -0.18609 | -0.20573 | -0.24927 | -0.26678 | -0.080692 | -0.41818 | -0.52447 | -0.29524 | -0.4692 | -0.2251 | -0.32829 | -0.033044 | -0.35512 | -0.26951 | 121.2619 | 121.0494 | 120.9431 | 46.7803 | -121.6537 | 120.9984 | 121.1125 | 121.1981 | 46.999 | -121.7628
690.4375 | 121.6141 | -45.5795 | 75.8972 | 1.4211e-13 | -0.017602 | -0.00095092 | 0.063103 | -0.0032776 | 0.05946 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0090276 | 0.061846 | -45.7279 | 0.0884 | -45.7592 | 75.7878 | 75.5664 | 75.4646 | -45.6737 | -45.7082 | 0.3346 | -45.8068 | 75.5152 | 75.6339 | 75.7104 | -45.7692 | -0.094196 | -0.1094 | -0.14836 | -0.17964 | -0.085442 | -0.33087 | -0.43266 | -0.18964 | -0.382 | -0.12868 | -0.22729 | -0.037652 | -0.26331 | -0.18685 | 121.3673 | 121.1459 | 121.0441 | 45.6679 | -121.5709 | 121.0947 | 121.2134 | 121.2899 | 45.9141 | -121.6664
692.1875 | 121.6003 | -44.1696 | 77.3254 | 1.4211e-13 | -0.018457 | -0.0011645 | 0.06353 | -0.0032776 | 0.059033 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.009455 | 0.061633 | -44.2674 | 0.083821 | -44.3033 | 77.2575 | 77.0316 | 76.9297 | -44.1993 | -44.2522 | 0.37581 | -44.3645 | 76.9803 | 77.1082 | 77.1755 | -44.3131 | -0.029694 | -0.067957 | -0.097768 | -0.13366 | -0.10396 | -0.29383 | -0.39573 | -0.14349 | -0.3451 | -0.082566 | -0.19491 | -0.051422 | -0.21722 | -0.14992 | 121.4271 | 121.2012 | 121.0993 | 44.2534 | -121.5248 | 121.15 | 121.2778 | 121.3451 | 44.5454 | -121.6385
693.8906 | 121.756 | -42.9199 | 78.5019 | 1.4211e-13 | -0.018243 | -0.0011645 | 0.063103 | -0.0032776 | 0.058819 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0090276 | 0.061633 | -42.9992 | 0.097557 | -43.0305 | 78.4982 | 78.3229 | 78.2163 | -42.9081 | -42.9793 | 0.42618 | -43.0871 | 78.2532 | 78.3948 | 78.4621 | -43.0265 | 0.011868 | -0.003667 | -0.079249 | -0.11059 | -0.12246 | -0.17903 | -0.2856 | -0.10654 | -0.24874 | -0.05938 | -0.16714 | -0.060609 | -0.10709 | -0.039787 | 121.4181 | 121.2428 | 121.1362 | 43.0175 | -121.4099 | 121.1731 | 121.3147 | 121.382 | 43.3461 | -121.5283
695.6562 | 121.6187 | -41.2354 | 80.278 | 1.4211e-13 | -0.018457 | -0.0011645 | 0.06353 | -0.0032776 | 0.059033 | -0.0099194 | 0.00055974 | -0.00026913 | 0.064058 | 0.009455 | 0.061419 | -41.1541 | 0.10671 | -41.1809 | 80.3662 | 80.1727 | 80.0706 | -41.0582 | -41.1341 | 0.4857 | -41.2464 | 80.1166 | 80.2491 | 80.3164 | -41.1675 | 0.17718 | 0.088193 | 0.081271 | 0.054466 | -0.12272 | -0.10527 | -0.20739 | 0.067895 | -0.16141 | 0.10127 | -0.011073 | -0.078968 | -0.028878 | 0.038424 | 121.6016 | 121.4081 | 121.306 | 41.3421 | -121.3362 | 121.352 | 121.4845 | 121.5518 | 41.7211 | -121.4455
697.4219 | 121.6873 | -38.4979 | 82.9834 | 1.4211e-13 | -0.01803 | -0.0011645 | 0.063103 | -0.003064 | 0.058819 | -0.0022889 | 0.00077334 | 0.00037167 | 0.064058 | 0.009455 | 0.061419 | -38.636 | 0.15708 | -38.6628 | 82.9118 | 82.7141 | 82.6026 | -38.5169 | -38.6021 | 0.62306 | -38.719 | 82.6622 | 82.7994 | 82.8621 | -38.6262 | -0.018941 | -0.071607 | -0.13804 | -0.16491 | -0.14597 | -0.26935 | -0.3808 | -0.12829 | -0.32115 | -0.10413 | -0.22105 | -0.092764 | -0.18398 | -0.12126 | 121.4097 | 121.212 | 121.1005 | 38.655 | -121.5003 | 121.1602 | 121.2973 | 121.3601 | 39.121 | -121.6096
699.1875 | 121.6827 | -35.5728 | 85.8948 | 1.4211e-13 | -0.01803 | -0.0011645 | 0.06353 | -0.0032776 | 0.058819 | -0.01755 | 0.00013254 | 0.00037167 | 0.063844 | 0.0092414 | 0.061419 | -35.9897 | 0.20286 | -36.0212 | 85.5627 | 85.3652 | 85.2445 | -35.8657 | -35.9601 | 0.80163 | -36.0816 | 85.3086 | 85.455 | 85.5223 | -35.9659 | -0.29285 | -0.3321 | -0.41684 | -0.44835 | -0.1555 | -0.52953 | -0.65032 | -0.3931 | -0.58616 | -0.38733 | -0.50883 | -0.11572 | -0.43977 | -0.37246 | 121.1355 | 120.9381 | 120.8173 | 35.7757 | -121.7604 | 120.8814 | 121.0278 | 121.0951 | 36.3744 | -121.8607
700.9531 | 121.7056 | -33.7692 | 87.7075 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.062675 | -0.0028504 | 0.058819 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.0096686 | 0.061205 | -34.0667 | 0.21202 | -34.0983 | 87.5085 | 87.3021 | 87.1858 | -33.9242 | -34.0279 | 0.9161 | -34.1448 | 87.2407 | 87.3826 | 87.4545 | -34.0291 | -0.15498 | -0.19903 | -0.29751 | -0.32906 | -0.17408 | -0.40539 | -0.52174 | -0.25985 | -0.46678 | -0.2587 | -0.37562 | -0.11577 | -0.32492 | -0.25304 | 121.2777 | 121.0714 | 120.955 | 33.9812 | -121.6317 | 121.01 | 121.1518 | 121.2237 | 34.6853 | -121.7366
702.6562 | 121.6141 | -32.4783 | 89.0396 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.063316 | -0.0034912 | 0.059033 | -0.0022889 | 0.00055974 | -0.00026913 | 0.063844 | 0.0090276 | 0.061846 | -32.3727 | 0.22576 | -32.3997 | 89.2254 | 89.0009 | 88.8982 | -32.2392 | -32.3384 | 1.0443 | -32.4645 | 88.9394 | 89.095 | 89.1531 | -32.3395 | 0.23917 | 0.18578 | 0.1056 | 0.078589 | -0.16058 | -0.038697 | -0.14144 | 0.13884 | -0.10025 | 0.13995 | 0.013874 | -0.12496 | 0.055385 | 0.11353 | 121.7037 | 121.4792 | 121.3765 | 32.7041 | -121.2788 | 121.4177 | 121.5733 | 121.6315 | 33.5226 | -121.3791
704.4219 | 121.7285 | -32.4005 | 89.0533 | 1.4211e-13 | -0.018457 | -0.00052352 | 0.063316 | -0.003064 | 0.059033 | 0.012972 | 0.00034614 | 0.00037167 | 0.063631 | 0.0090276 | 0.061633 | -32.5147 | 0.23949 | -32.5417 | 89.0743 | 88.8773 | 88.7517 | -32.3674 | -32.4803 | 1.0626 | -32.6201 | 88.8066 | 88.9576 | 88.9654 | -32.4723 | 0.033143 | 0.020956 | -0.11415 | -0.14116 | -0.1743 | -0.17606 | -0.30168 | -0.07177 | -0.24676 | -0.079807 | -0.21962 | -0.14785 | -0.095706 | -0.087926 | 121.4748 | 121.2778 | 121.1522 | 32.64 | -121.4207 | 121.2071 | 121.3582 | 121.3659 | 33.4631 | -121.5256
706.125 | 121.6553 | -31.7322 | 89.7995 | 1.4211e-13 | -0.018457 | -0.00073712 | 0.063103 | -0.0034912 | 0.058819 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.0092414 | 0.061633 | -31.718 | 0.24407 | -31.7496 | 89.8709 | 89.6694 | 89.5438 | -31.5798 | -31.679 | 1.1176 | -31.8143 | 89.5987 | 89.7497 | 89.7575 | -31.6756 | 0.15238 | 0.071441 | 0.014154 | -0.01745 | -0.16983 | -0.13006 | -0.25574 | 0.056609 | -0.20083 | 0.053132 | -0.082105 | -0.13871 | -0.049763 | -0.041983 | 121.6031 | 121.4016 | 121.2759 | 31.9763 | -121.3793 | 121.3308 | 121.4819 | 121.4897 | 32.8497 | -121.4751
707.8906 | 121.6782 | -30.8716 | 90.5914 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.063316 | -0.0032776 | 0.058819 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.0092414 | 0.061419 | -30.9031 | 0.26239 | -30.9393 | 90.6951 | 90.4799 | 90.3725 | -30.7602 | -30.8732 | 1.1954 | -30.9947 | 90.4228 | 90.5693 | 90.5771 | -30.8514 | 0.11142 | 0.10362 | -0.031489 | -0.067691 | -0.17911 | -0.11152 | -0.21895 | 0.0202 | -0.16863 | -0.001611 | -0.12311 | -0.14331 | -0.022124 | -0.014344 | 121.5666 | 121.3515 | 121.2441 | 31.134 | -121.3516 | 121.2944 | 121.4409 | 121.4487 | 32.067 | -121.4428
709.6562 | 121.637 | -28.9444 | 92.5827 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.063316 | -0.003705 | 0.058819 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0096686 | 0.061633 | -29.1953 | 0.31275 | -29.2362 | 92.4119 | 92.2016 | 92.0757 | -29.0385 | -29.1562 | 1.3511 | -29.2914 | 92.1352 | 92.2817 | 92.2941 | -29.1343 | -0.094095 | -0.17076 | -0.25094 | -0.29176 | -0.19766 | -0.38112 | -0.50698 | -0.18993 | -0.44755 | -0.21178 | -0.34702 | -0.15709 | -0.301 | -0.28864 | 121.3563 | 121.146 | 121.0201 | 29.2571 | -121.6212 | 121.0796 | 121.2261 | 121.2385 | 30.2955 | -121.717
711.3594 | 121.6507 | -28.0014 | 93.4982 | 1.4211e-13 | -0.018457 | -0.0011645 | 0.06353 | -0.0032776 | 0.058606 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.0092414 | 0.061633 | -28.2613 | 0.33565 | -28.2976 | 93.3459 | 93.1311 | 93.0098 | -28.1044 | -28.2175 | 1.4747 | -28.3574 | 93.0646 | 93.2203 | 93.2327 | -28.2002 | -0.10299 | -0.15229 | -0.25994 | -0.2962 | -0.19321 | -0.36713 | -0.48847 | -0.19884 | -0.43364 | -0.21614 | -0.35595 | -0.15711 | -0.27791 | -0.26555 | 121.3473 | 121.1325 | 121.0112 | 28.337 | -121.6026 | 121.066 | 121.2217 | 121.2341 | 29.4761 | -121.6985
713.125 | 121.6232 | -27.1408 | 94.3726 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.063316 | -0.003064 | 0.059033 | 0.012972 | 0.00034614 | 0.00015807 | 0.064058 | 0.009455 | 0.061419 | -27.1259 | 0.3448 | -27.1713 | 94.4905 | 94.2758 | 94.1453 | -26.978 | -27.0866 | 1.5663 | -27.2264 | 94.2001 | 94.3512 | 94.3727 | -27.0693 | 0.16283 | 0.11798 | 0.014907 | -0.03054 | -0.19337 | -0.096723 | -0.22731 | 0.071529 | -0.1725 | 0.054208 | -0.085607 | -0.15714 | -0.021326 | 0.00019 | 121.6313 | 121.4166 | 121.2861 | 27.4856 | -121.3505 | 121.3409 | 121.492 | 121.5136 | 28.7071 | -121.4418
714.9062 | 121.6827 | -25.8591 | 95.6131 | 1.4211e-13 | -0.01803 | -0.00095092 | 0.063103 | -0.0032776 | 0.058392 | 0.012972 | 0.00055974 | 0.00015807 | 0.063631 | 0.009455 | 0.061419 | -25.9538 | 0.38601 | -25.9993 | 95.6672 | 95.4389 | 95.322 | -25.8058 | -25.919 | 1.6945 | -26.068 | 95.3676 | 95.5234 | 95.5357 | -25.8925 | 0.053299 | 0.054082 | -0.094763 | -0.14024 | -0.19354 | -0.17421 | -0.29114 | -0.033453 | -0.24553 | -0.059959 | -0.20893 | -0.17548 | -0.089743 | -0.077384 | 121.5263 | 121.298 | 121.181 | 26.2451 | -121.4189 | 121.2266 | 121.3824 | 121.3948 | 27.5536 | -121.5056
716.5938 | 121.7422 | -24.646 | 96.7987 | 1.4211e-13 | -0.018457 | -0.0011645 | 0.062889 | -0.0034912 | 0.058392 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.009455 | 0.061633 | -24.736 | 0.41348 | -24.7952 | 96.8759 | 96.6477 | 96.5215 | -24.5924 | -24.7057 | 1.8227 | -24.8592 | 96.5855 | 96.7413 | 96.7536 | -24.6791 | 0.05364 | 0.077168 | -0.089986 | -0.14922 | -0.20286 | -0.15099 | -0.27716 | -0.03314 | -0.21325 | -0.059675 | -0.21323 | -0.18009 | -0.057443 | -0.045084 | 121.5219 | 121.2937 | 121.1675 | 25.0595 | -121.3911 | 121.2314 | 121.3873 | 121.3996 | 26.4687 | -121.4778
718.3438 | 121.669 | -25.1633 | 96.3364 | 1.4211e-13 | -0.018671 | -0.00095092 | 0.063103 | -0.0034912 | 0.058819 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.0096686 | 0.061419 | -25.1526 | 0.41348 | -25.1981 | 96.4776 | 96.2448 | 96.1186 | -25.009 | -25.1132 | 1.8318 | -25.2667 | 96.1734 | 96.3383 | 96.3461 | -25.0821 | 0.15423 | 0.14119 | 0.010654 | -0.03484 | -0.18907 | -0.091591 | -0.21773 | 0.081197 | -0.16298 | 0.050093 | -0.10346 | -0.18466 | 0.001981 | 0.009761 | 121.6408 | 121.408 | 121.2819 | 25.5768 | -121.3454 | 121.3367 | 121.5016 | 121.5094 | 26.9951 | -121.4184
720.0938 | 121.6049 | -24.614 | 96.936 | 1.4211e-13 | -0.018671 | -0.00095092 | 0.06353 | -0.0032776 | 0.058392 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063844 | 0.009455 | 0.061419 | -24.8275 | 0.42722 | -24.8731 | 96.8026 | 96.5699 | 96.4529 | -24.6656 | -24.7835 | 1.8959 | -24.9325 | 96.503 | 96.6726 | 96.6758 | -24.7616 | -0.051666 | -0.13341 | -0.2136 | -0.2591 | -0.20743 | -0.36616 | -0.48316 | -0.1476 | -0.433 | -0.16956 | -0.31853 | -0.17093 | -0.26345 | -0.26025 | 121.4166 | 121.1838 | 121.0668 | 25.0412 | -121.6017 | 121.117 | 121.2865 | 121.2897 | 26.5099 | -121.6976
721.7969 | 121.701 | -24.1013 | 97.3892 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.063103 | -0.0028504 | 0.059033 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.009455 | 0.061419 | -24.4613 | 0.45469 | -24.5022 | 97.1643 | 96.9545 | 96.8146 | -24.2993 | -24.4081 | 1.9646 | -24.5662 | 96.8693 | 97.0435 | 97.0375 | -24.3861 | -0.19805 | -0.22491 | -0.36002 | -0.40095 | -0.20291 | -0.43471 | -0.57464 | -0.28484 | -0.5199 | -0.3068 | -0.46493 | -0.18009 | -0.34577 | -0.35173 | 121.2656 | 121.0558 | 120.9158 | 24.5559 | -121.6885 | 120.9706 | 121.1447 | 121.1388 | 26.0659 | -121.7753
723.5625 | 121.6827 | -29.1504 | 92.3767 | 1.4211e-13 | -0.018885 | -0.0011645 | 0.06353 | -0.0034912 | 0.058392 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.009455 | 0.061419 | -28.9527 | 0.33565 | -28.9752 | 92.7324 | 92.4443 | 92.3733 | -28.8645 | -28.9181 | 1.5938 | -29.0579 | 92.387 | 92.5564 | 92.5871 | -28.9008 | 0.2859 | 0.35572 | 0.19771 | 0.1752 | -0.1107 | 0.067558 | -0.003374 | 0.24959 | 0.010262 | 0.23231 | 0.092492 | -0.15709 | 0.17971 | 0.21038 | 121.8828 | 121.5947 | 121.5237 | 29.486 | -121.2412 | 121.5374 | 121.7068 | 121.7375 | 30.7441 | -121.2775
725.25 | 121.7194 | -27.5665 | 93.8828 | 1.4211e-13 | -0.018457 | -0.00073712 | 0.063316 | -0.0032776 | 0.058606 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0096686 | 0.061633 | -27.8493 | 0.39517 | -27.881 | 93.7717 | 93.5615 | 93.431 | -27.6831 | -27.8009 | 1.7128 | -27.9407 | 93.4858 | 93.6461 | 93.718 | -27.7698 | -0.1166 | -0.11102 | -0.28276 | -0.31445 | -0.19785 | -0.32123 | -0.45176 | -0.20331 | -0.39694 | -0.23435 | -0.37417 | -0.17086 | -0.23662 | -0.16474 | 121.3383 | 121.1281 | 120.9975 | 27.9617 | -121.5659 | 121.0523 | 121.2127 | 121.2845 | 29.2793 | -121.6526
727 | 121.6278 | -28.9124 | 92.6147 | 1.4211e-13 | -0.018671 | -0.00030992 | 0.063316 | -0.003064 | 0.058819 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0096686 | 0.061633 | -28.1927 | 0.33107 | -28.2106 | 93.5016 | 93.2181 | 93.138 | -28.0952 | -28.1718 | 1.6258 | -28.3024 | 93.147 | 93.321 | 93.3471 | -28.1316 | 0.81712 | 0.88686 | 0.71969 | 0.70174 | -0.11538 | 0.60336 | 0.52322 | 0.78079 | 0.53226 | 0.7406 | 0.60994 | -0.17085 | 0.7063 | 0.7324 | 122.414 | 122.1305 | 122.0503 | 29.2434 | -120.71 | 122.0594 | 122.2334 | 122.2595 | 30.5382 | -120.7463
728.7656 | 121.6873 | -24.0692 | 97.4304 | 1.4211e-13 | -0.018885 | -0.0013783 | 0.063744 | -0.0034912 | 0.058819 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0092414 | 0.061419 | -24.7406 | 0.47758 | -24.7998 | 96.8621 | 96.6569 | 96.5124 | -24.5786 | -24.6919 | 2.0013 | -24.8409 | 96.5855 | 96.7458 | 96.8223 | -24.6654 | -0.50941 | -0.56828 | -0.67135 | -0.73059 | -0.22118 | -0.77354 | -0.91803 | -0.59619 | -0.84497 | -0.62272 | -0.77169 | -0.17551 | -0.68458 | -0.60812 | 120.9314 | 120.7261 | 120.5816 | 24.5468 | -122.009 | 120.6547 | 120.8151 | 120.8915 | 26.0705 | -122.0958
730.4688 | 121.7377 | -18.837 | 102.6627 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.06353 | -0.0032776 | 0.058606 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0096686 | 0.061419 | -19.1458 | 0.59662 | -19.2189 | 102.4752 | 102.234 | 102.1029 | -19.0152 | -19.1105 | 2.569 | -19.264 | 102.1529 | 102.3317 | 102.3395 | -19.0976 | -0.17825 | -0.18742 | -0.30879 | -0.3819 | -0.20365 | -0.42865 | -0.55979 | -0.26058 | -0.50976 | -0.27351 | -0.42706 | -0.16648 | -0.33092 | -0.32314 | 121.3122 | 121.071 | 120.9398 | 19.4336 | -121.6779 | 120.9899 | 121.1687 | 121.1765 | 21.406 | -121.7602
732.25 | 121.6827 | -17.0975 | 104.4205 | 1.4211e-13 | -0.018457 | -0.00073712 | 0.06353 | -0.0032776 | 0.059033 | 0.0053411 | 0.00077334 | 0.00015807 | 0.063844 | 0.0096686 | 0.061205 | -17.1267 | 0.65157 | -17.2136 | 104.4852 | 104.2442 | 104.1129 | -17.0097 | -17.0959 | 2.8575 | -17.2677 | 104.1629 | 104.3463 | 104.3449 | -17.1012 | 0.087816 | 0.064684 | -0.029228 | -0.11612 | -0.20393 | -0.17632 | -0.3076 | -0.003721 | -0.25761 | 0.001618 | -0.17025 | -0.16653 | -0.074149 | -0.075526 | 121.5826 | 121.3416 | 121.2103 | 17.749 | -121.4301 | 121.2603 | 121.4438 | 121.4424 | 19.9549 | -121.5217
733.9531 | 121.6553 | -17.9626 | 103.5919 | 1.4211e-13 | -0.018243 | -0.0011645 | 0.06353 | -0.0032776 | 0.058606 | 0.0053411 | 0.00077334 | 0.00015807 | 0.064058 | 0.009455 | 0.061633 | -18.0058 | 0.64699 | -18.1338 | 103.6153 | 103.3742 | 103.2384 | -17.8888 | -17.9704 | 2.8483 | -18.1377 | 103.2929 | 103.4627 | 103.5345 | -17.962 | 0.073835 | 0.023342 | -0.043106 | -0.17118 | -0.24501 | -0.21776 | -0.35356 | 0.000635 | -0.29897 | -0.007743 | -0.17503 | -0.17566 | -0.12927 | -0.057387 | 121.5779 | 121.3368 | 121.201 | 18.6096 | -121.4807 | 121.2556 | 121.4253 | 121.4972 | 20.811 | -121.5539
735.7188 | 121.7102 | -24.7787 | 96.698 | 1.4211e-13 | -0.018885 | -0.00073712 | 0.063316 | -0.0034912 | 0.058606 | 0.0053411 | 0.00077334 | -0.00026913 | 0.063631 | 0.009455 | 0.061419 | -24.7131 | 0.50963 | -24.754 | 96.9812 | 96.6981 | 96.5994 | -24.6198 | -24.6782 | 2.2989 | -24.8272 | 96.6221 | 96.8008 | 96.8406 | -24.6517 | 0.15892 | 0.28318 | 0.065658 | 0.024732 | -0.13419 | 8.9e-05 | -0.098613 | 0.12709 | -0.075919 | 0.10055 | -0.048423 | -0.17551 | 0.10279 | 0.14262 | 121.7599 | 121.4768 | 121.3781 | 25.2884 | -121.3178 | 121.4008 | 121.5795 | 121.6194 | 27.0776 | -121.3497
737.4062 | 121.6507 | -23.2727 | 98.259 | 1.4211e-13 | -0.018671 | -0.0011645 | 0.06353 | -0.0032776 | 0.058819 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.064058 | 0.0096686 | 0.061419 | -23.5548 | 0.55084 | -23.6186 | 98.0708 | 97.8428 | 97.7166 | -23.411 | -23.5152 | 2.3767 | -23.6596 | 97.7667 | 97.9409 | 97.999 | -23.4886 | -0.13829 | -0.18814 | -0.28205 | -0.3459 | -0.20761 | -0.41615 | -0.54241 | -0.21594 | -0.49227 | -0.2425 | -0.3869 | -0.17096 | -0.31812 | -0.25997 | 121.3435 | 121.1155 | 120.9893 | 23.8235 | -121.67 | 121.0394 | 121.2136 | 121.2717 | 25.6494 | -121.7476
739.1719 | 121.701 | -18.7042 | 102.7954 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.062889 | -0.0034912 | 0.058606 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064058 | 0.009455 | 0.061419 | -18.7429 | 0.64699 | -18.8572 | 102.9285 | 102.6461 | 102.5195 | -18.6626 | -18.703 | 2.8941 | -18.8657 | 102.5741 | 102.7484 | 102.8065 | -18.6946 | 0.041575 | 0.13309 | -0.038648 | -0.15297 | -0.19454 | -0.1493 | -0.27589 | 0.009602 | -0.22129 | 0.001242 | -0.16147 | -0.17107 | -0.04702 | 0.011124 | 121.6327 | 121.3503 | 121.2237 | 19.3512 | -121.4581 | 121.2783 | 121.4526 | 121.5108 | 21.5983 | -121.49
740.9375 | 121.7331 | -17.6147 | 103.8712 | 1.4211e-13 | -0.018671 | -0.0011645 | 0.063316 | -0.0034912 | 0.058606 | 0.012972 | 0.00077334 | -5.5534e-05 | 0.064058 | 0.0092414 | 0.061205 | -17.7082 | 0.68362 | -17.8179 | 103.9174 | 103.6764 | 103.5543 | -17.5866 | -17.6728 | 3.0315 | -17.8263 | 103.5905 | 103.7694 | 103.8413 | -17.6644 | 0.028144 | 0.04628 | -0.093411 | -0.20317 | -0.23132 | -0.19479 | -0.31687 | -0.049642 | -0.28061 | -0.058026 | -0.21158 | -0.16194 | -0.10174 | -0.029856 | 121.5322 | 121.2911 | 121.169 | 18.2984 | -121.4578 | 121.2053 | 121.3842 | 121.456 | 20.6462 | -121.5355
742.6406 | 121.7514 | -16.2506 | 105.2399 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.063316 | -0.0032776 | 0.058606 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064485 | 0.0098824 | 0.060992 | -16.5452 | 0.72025 | -16.6642 | 105.0758 | 104.8303 | 104.6989 | -16.4236 | -16.5006 | 3.2055 | -16.6633 | 104.7535 | 104.9415 | 105.0088 | -16.5014 | -0.17294 | -0.1641 | -0.29464 | -0.41358 | -0.24064 | -0.40961 | -0.54094 | -0.25076 | -0.48638 | -0.25001 | -0.41272 | -0.16196 | -0.29833 | -0.23103 | 121.3264 | 121.0809 | 120.9495 | 16.9709 | -121.6634 | 121.0041 | 121.1921 | 121.2595 | 19.4561 | -121.7412
744.4062 | 121.6736 | -16.5894 | 104.9469 | 1.4211e-13 | -0.018885 | -0.00052352 | 0.063316 | -0.0032776 | 0.058392 | 0.012972 | 0.00055974 | 0.00037167 | 0.064272 | 0.009455 | 0.061205 | -16.765 | 0.72483 | -16.8931 | 104.8423 | 104.5418 | 104.4242 | -16.6479 | -16.7296 | 3.1871 | -16.906 | 104.5246 | 104.708 | 104.7021 | -16.744 | -0.058567 | -0.10463 | -0.17565 | -0.30375 | -0.24519 | -0.40511 | -0.52268 | -0.15469 | -0.42234 | -0.1402 | -0.31665 | -0.16196 | -0.23887 | -0.24482 | 121.4316 | 121.1311 | 121.0136 | 17.3142 | -121.5948 | 121.1139 | 121.2974 | 121.2914 | 19.7765 | -121.6909
746.1562 | 121.6736 | -14.7354 | 106.7825 | 1.4211e-13 | -0.018671 | -0.00052352 | 0.063103 | -0.0032776 | 0.058392 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064058 | 0.009455 | 0.061419 | -16.939 | 0.77061 | -17.0579 | 104.7049 | 104.4182 | 104.2869 | -16.8494 | -16.8898 | 3.3062 | -17.0571 | 104.3597 | 104.5569 | 104.5922 | -16.8906 | -2.114 | -2.0776 | -2.2036 | -2.3225 | -0.20853 | -2.3644 | -2.4957 | -2.1552 | -2.4228 | -2.1544 | -2.3217 | -0.16653 | -2.2256 | -2.1903 | 119.4403 | 119.1536 | 119.0223 | 15.506 | -123.6319 | 119.0951 | 119.2924 | 119.3276 | 18.0416 | -123.6731
747.8594 | 121.6461 | -13.3759 | 108.2291 | 1.4211e-13 | -0.018885 | -0.00095092 | 0.06353 | -0.0034912 | 0.058819 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.0096686 | 0.060992 | -13.5556 | 0.83013 | -13.6883 | 108.0517 | 107.7379 | 107.6109 | -13.4701 | -13.5107 | 3.7091 | -13.6872 | 107.7066 | 107.9039 | 107.9071 | -13.548 | -0.094294 | -0.17735 | -0.17971 | -0.31246 | -0.21816 | -0.49119 | -0.61814 | -0.17218 | -0.52245 | -0.13487 | -0.31132 | -0.13914 | -0.32517 | -0.32197 | 121.4276 | 121.1137 | 120.9868 | 14.206 | -121.6992 | 121.0825 | 121.2798 | 121.283 | 17.085 | -121.7771
749.625 | 121.7331 | -12.204 | 109.2865 | 1.4211e-13 | -0.018457 | -0.00095092 | 0.06353 | -0.0032776 | 0.058392 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.0092414 | 0.061205 | -12.3148 | 0.86218 | -12.4476 | 109.2741 | 108.9742 | 108.8471 | -12.2476 | -12.2745 | 3.9426 | -12.4418 | 108.9245 | 109.131 | 109.1296 | -12.3163 | -0.043596 | -0.012351 | -0.11084 | -0.24362 | -0.20002 | -0.31232 | -0.43935 | -0.11235 | -0.362 | -0.070495 | -0.23778 | -0.12543 | -0.15554 | -0.15692 | 121.4781 | 121.1782 | 121.0511 | 13.0662 | -121.5341 | 121.1285 | 121.3349 | 121.3336 | 16.1466 | -121.6028
751.3906 | 121.6461 | -10.1578 | 111.4426 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.063316 | -0.003705 | 0.058819 | -0.0099194 | 0.00055974 | 0.00037167 | 0.064058 | 0.009455 | 0.061205 | -10.0439 | 0.94002 | -10.1859 | 111.5176 | 111.2133 | 111.0678 | -10.0176 | -10.008 | 4.3227 | -10.1799 | 111.1725 | 111.3745 | 111.3731 | -10.091 | 0.14014 | 0.074993 | 0.11384 | -0.028151 | -0.16829 | -0.22929 | -0.3748 | 0.066752 | -0.27003 | 0.14976 | -0.022103 | -0.088855 | -0.068089 | -0.069466 | 121.6753 | 121.3711 | 121.2255 | 11.0978 | -121.4602 | 121.3303 | 121.5323 | 121.5309 | 14.4804 | -121.5336
753.1562 | 121.7056 | -10.3821 | 111.1267 | 1.4211e-13 | -0.019098 | -0.00095092 | 0.063744 | -0.003705 | 0.058392 | -0.0099194 | 0.00077334 | 0.00037167 | 0.064058 | 0.0096686 | 0.061205 | -10.337 | 0.95376 | -10.4698 | 111.2337 | 110.9202 | 110.7976 | -10.2924 | -10.3011 | 4.3913 | -10.4683 | 110.8932 | 111.0906 | 111.0892 | -10.3703 | 0.089705 | 0.10699 | 0.045128 | -0.0877 | -0.17741 | -0.20648 | -0.32908 | 0.011748 | -0.23346 | 0.08103 | -0.086257 | -0.098005 | -0.036105 | -0.037483 | 121.6158 | 121.3023 | 121.1797 | 11.3358 | -121.4191 | 121.2753 | 121.4727 | 121.4713 | 14.7734 | -121.497
754.8906 | 121.5912 | -10.0937 | 111.4929 | 1.4211e-13 | -0.018885 | -0.00052352 | 0.063316 | -0.003705 | 0.058392 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064272 | 0.0096686 | 0.060992 | -10.0348 | 0.97665 | -10.1768 | 111.5359 | 111.2224 | 111.0998 | -10.0085 | -9.9943 | 4.515 | -10.1753 | 111.1817 | 111.3882 | 111.3868 | -10.0727 | 0.085208 | 0.042952 | 0.05891 | -0.083081 | -0.16829 | -0.27048 | -0.3931 | 0.02098 | -0.31123 | 0.099413 | -0.081611 | -0.10259 | -0.10471 | -0.10608 | 121.6296 | 121.3161 | 121.1935 | 11.0703 | -121.5014 | 121.2754 | 121.4819 | 121.4805 | 14.6087 | -121.5656
756.6562 | 121.7377 | -9.3384 | 112.1933 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.063744 | -0.0039186 | 0.058178 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.0098824 | 0.060992 | -9.3434 | 1.0087 | -9.4809 | 112.2181 | 111.9093 | 111.7729 | -9.3125 | -9.2983 | 4.634 | -9.4702 | 111.873 | 112.0704 | 112.0736 | -9.3859 | 0.025894 | 0.024754 | -0.005063 | -0.14249 | -0.16839 | -0.28402 | -0.42042 | -0.047508 | -0.32025 | 0.040067 | -0.1318 | -0.084292 | -0.12287 | -0.11967 | 121.5564 | 121.2477 | 121.1113 | 10.3471 | -121.5058 | 121.2114 | 121.4088 | 121.412 | 13.9724 | -121.5792
758.4219 | 121.6599 | -8.4778 | 113.0905 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.06353 | -0.0034912 | 0.057965 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064272 | 0.009455 | 0.061205 | -8.3911 | 1.0499 | -8.5149 | 113.1704 | 112.848 | 112.7252 | -8.3784 | -8.3368 | 4.8584 | -8.5086 | 112.8116 | 113.0182 | 113.0214 | -8.4427 | 0.099399 | 0.079842 | 0.086646 | -0.037072 | -0.13647 | -0.24256 | -0.36529 | 0.035133 | -0.27888 | 0.141 | -0.030866 | -0.065999 | -0.07232 | -0.069118 | 121.6481 | 121.3257 | 121.203 | 9.5277 | -121.4689 | 121.2894 | 121.496 | 121.4992 | 13.3362 | -121.5332
760.125 | 121.7239 | -8.107 | 113.4064 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.063316 | -0.0032776 | 0.058392 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.0096686 | 0.060992 | -8.0432 | 1.0728 | -8.1761 | 113.5046 | 113.1914 | 113.064 | -8.035 | -8.0071 | 4.9912 | -8.1744 | 113.155 | 113.3524 | 113.3511 | -8.1038 | 0.07203 | 0.098207 | 0.063815 | -0.069067 | -0.1411 | -0.215 | -0.34233 | 0.003177 | -0.25135 | 0.099879 | -0.067409 | -0.070586 | -0.053939 | -0.055316 | 121.6116 | 121.2984 | 121.171 | 9.1798 | -121.4413 | 121.262 | 121.4594 | 121.4581 | 13.0981 | -121.5102
761.8906 | 121.6827 | -7.8964 | 113.6993 | 1.4211e-13 | -0.018885 | -0.0011645 | 0.063103 | -0.0034912 | 0.058178 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.0096686 | 0.061419 | -7.8234 | 1.0911 | -7.9563 | 113.7289 | 113.4112 | 113.2792 | -7.8152 | -7.7782 | 5.0781 | -7.9455 | 113.3748 | 113.5768 | 113.5846 | -7.884 | 0.081246 | 0.029579 | 0.073006 | -0.059881 | -0.14113 | -0.28818 | -0.42011 | 0.012388 | -0.32455 | 0.11824 | -0.049045 | -0.061433 | -0.12256 | -0.11478 | 121.6253 | 121.3076 | 121.1757 | 8.9875 | -121.5145 | 121.2712 | 121.4732 | 121.481 | 12.9746 | -121.5834
763.6406 | 121.6049 | -7.6492 | 113.9465 | 1.4211e-13 | -0.019312 | -0.00052352 | 0.06353 | -0.0034912 | 0.057965 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064272 | 0.009455 | 0.060992 | -7.5258 | 1.114 | -7.6587 | 114.0128 | 113.7042 | 113.5768 | -7.5221 | -7.4851 | 5.1697 | -7.657 | 113.6587 | 113.8652 | 113.8684 | -7.6001 | 0.12711 | 0.066247 | 0.12341 | -0.009485 | -0.13659 | -0.24232 | -0.36969 | 0.049083 | -0.28787 | 0.16409 | -0.007778 | -0.056861 | -0.081296 | -0.078095 | 121.662 | 121.3534 | 121.2261 | 8.7632 | -121.4687 | 121.3079 | 121.5145 | 121.5177 | 12.819 | -121.5467
765.3906 | 121.6095 | -7.2372 | 114.386 | 1.4211e-13 | -0.019098 | -0.00073712 | 0.06353 | -0.0034912 | 0.058178 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.0096686 | 0.060992 | -7.0817 | 1.1461 | -7.2192 | 114.4523 | 114.1438 | 114.0118 | -7.0917 | -7.0456 | 5.2842 | -7.2129 | 114.0936 | 114.291 | 114.3034 | -7.1652 | 0.14554 | 0.066319 | 0.15553 | 0.018043 | -0.12749 | -0.2422 | -0.37418 | 0.072084 | -0.29237 | 0.19166 | 0.024369 | -0.047715 | -0.094939 | -0.082581 | 121.6895 | 121.381 | 121.2491 | 8.3833 | -121.4777 | 121.3309 | 121.5283 | 121.5406 | 12.5214 | -121.5511
767.0938 | 121.7056 | -7.0129 | 114.5416 | 1.4211e-13 | -0.019098 | -0.00073712 | 0.063103 | -0.003705 | 0.058178 | 0.0053411 | 0.00077334 | -5.5534e-05 | 0.064058 | 0.009455 | 0.060992 | -6.9077 | 1.1689 | -7.0406 | 114.64 | 114.3269 | 114.195 | -6.9085 | -6.8624 | 5.3529 | -7.0206 | 114.2813 | 114.4925 | 114.4865 | -6.982 | 0.10439 | 0.098393 | 0.1052 | -0.027709 | -0.1321 | -0.21468 | -0.34667 | 0.030931 | -0.26029 | 0.1505 | -0.00763 | -0.038561 | -0.049121 | -0.055077 | 121.653 | 121.3399 | 121.2079 | 8.1819 | -121.4502 | 121.2943 | 121.5054 | 121.4995 | 12.3658 | -121.5236
768.875 | 121.6324 | -6.4133 | 115.2054 | 1.4211e-13 | -0.018885 | -0.00073712 | 0.063316 | -0.0032776 | 0.058606 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.0096686 | 0.061205 | -6.3217 | 1.2056 | -6.4546 | 115.2261 | 114.8993 | 114.7719 | -6.327 | -6.2718 | 5.5314 | -6.4391 | 114.8674 | 115.0648 | 115.068 | -6.4005 | 0.086243 | 0.02067 | 0.091563 | -0.041359 | -0.1276 | -0.30607 | -0.43352 | 0.012771 | -0.338 | 0.14148 | -0.025804 | -0.038575 | -0.14055 | -0.13735 | 121.6393 | 121.3126 | 121.1851 | 7.6188 | -121.5324 | 121.2807 | 121.4781 | 121.4813 | 11.9447 | -121.6059
770.6406 | 121.701 | -6.0928 | 115.4617 | 1.4211e-13 | -0.018671 | -0.00073712 | 0.06353 | -0.0034912 | 0.058392 | -0.01755 | 0.00055974 | 0.00015807 | 0.064272 | 0.0098824 | 0.060992 | -6.0104 | 1.2193 | -6.1525 | 115.5236 | 115.2107 | 115.0786 | -6.0294 | -5.965 | 5.623 | -6.1323 | 115.1696 | 115.3762 | 115.3748 | -6.0891 | 0.063438 | 0.061917 | 0.082458 | -0.059628 | -0.12307 | -0.25105 | -0.38311 | 0.003696 | -0.29217 | 0.12782 | -0.039465 | -0.043161 | -0.085555 | -0.086933 | 121.6165 | 121.3035 | 121.1715 | 7.3121 | -121.4911 | 121.2624 | 121.469 | 121.4676 | 11.7158 | -121.5509
772.3906 | 121.6049 | -5.8914 | 115.7089 | 1.4211e-13 | -0.018885 | -0.00052352 | 0.063316 | -0.003705 | 0.058178 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.0098824 | 0.061205 | -5.7631 | 1.2331 | -5.8915 | 115.7663 | 115.4488 | 115.3121 | -5.7913 | -5.7223 | 5.6825 | -5.885 | 115.4076 | 115.6234 | 115.6175 | -5.8602 | 0.10013 | 0.057379 | 0.12827 | -8.2e-05 | -0.10021 | -0.26014 | -0.39679 | 0.031221 | -0.30128 | 0.16908 | 0.006369 | -0.024852 | -0.085503 | -0.091459 | 121.6577 | 121.3402 | 121.2036 | 7.1245 | -121.5002 | 121.2991 | 121.5148 | 121.5089 | 11.574 | -121.5691
774.0938 | 121.6324 | -5.6076 | 116.011 | 1.4211e-13 | -0.018671 | -0.00095092 | 0.063316 | -0.003705 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064272 | 0.009455 | 0.060992 | -5.4884 | 1.2559 | -5.626 | 116.0318 | 115.7235 | 115.5731 | -5.512 | -5.4522 | 5.8016 | -5.6103 | 115.6732 | 115.889 | 115.883 | -5.59 | 0.095628 | 0.020802 | 0.11917 | -0.018355 | -0.11398 | -0.28753 | -0.43793 | 0.017558 | -0.33785 | 0.15541 | -0.002721 | -0.020279 | -0.12207 | -0.12802 | 121.6395 | 121.3311 | 121.1807 | 6.8635 | -121.523 | 121.2808 | 121.4966 | 121.4906 | 11.4092 | -121.6011
775.8438 | 121.669 | -5.4016 | 116.1758 | 1.4211e-13 | -0.018885 | -0.00073712 | 0.06353 | -0.0034912 | 0.058178 | 0.0053411 | 0.00055974 | 0.00058547 | 0.064272 | 0.0098824 | 0.061205 | -5.3099 | 1.2651 | -5.4383 | 116.215 | 115.9067 | 115.7563 | -5.3426 | -5.269 | 5.8611 | -5.4272 | 115.8609 | 116.063 | 116.0707 | -5.4023 | 0.059054 | 0.039142 | 0.091729 | -0.036639 | -0.095693 | -0.26917 | -0.41958 | -0.000705 | -0.31493 | 0.13256 | -0.025567 | -0.024862 | -0.11288 | -0.1051 | 121.6166 | 121.3083 | 121.1579 | 6.6667 | -121.5184 | 121.2625 | 121.4646 | 121.4724 | 11.2627 | -121.5782
777.5312 | 121.6507 | -5.2551 | 116.3361 | 1.4211e-13 | -0.019098 | -0.00073712 | 0.06353 | -0.0034912 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.0098824 | 0.060992 | -5.1359 | 1.2972 | -5.2597 | 116.3981 | 116.0807 | 115.9348 | -5.1594 | -5.0859 | 5.9115 | -5.2532 | 116.0395 | 116.2415 | 116.2447 | -5.2283 | 0.095727 | 0.06206 | 0.11922 | -0.00457 | -0.1003 | -0.25539 | -0.40124 | 0.026806 | -0.29658 | 0.16923 | 0.00194 | -0.024866 | -0.094529 | -0.091327 | 121.6532 | 121.3358 | 121.19 | 6.5523 | -121.4955 | 121.2946 | 121.4967 | 121.4999 | 11.1666 | -121.5644
779.2969 | 121.5912 | -5.0262 | 116.5787 | 1.4211e-13 | -0.019098 | -0.00095092 | 0.063744 | -0.0034912 | 0.058178 | 0.0053411 | 0.00034614 | -0.00026913 | 0.064058 | 0.0098824 | 0.060778 | -4.8978 | 1.32 | -5.017 | 116.6362 | 116.3234 | 116.1683 | -4.9259 | -4.857 | 6.0168 | -5.0105 | 116.273 | 116.4842 | 116.4782 | -4.9902 | 0.10037 | 0.057522 | 0.12842 | 0.009197 | -0.091173 | -0.25532 | -0.41034 | 0.036023 | -0.30569 | 0.16928 | 0.01573 | -0.020293 | -0.094477 | -0.10043 | 121.6624 | 121.3496 | 121.1946 | 6.3463 | -121.5045 | 121.2992 | 121.5104 | 121.5045 | 11.043 | -121.5689
781.0625 | 121.6827 | -4.7836 | 116.7664 | 1.4211e-13 | -0.019098 | -0.00073712 | 0.063316 | -0.0034912 | 0.058606 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064058 | 0.0098824 | 0.060992 | -4.6826 | 1.3475 | -4.811 | 116.8468 | 116.5294 | 116.3789 | -4.7061 | -4.6418 | 6.1221 | -4.7999 | 116.4836 | 116.6948 | 116.6889 | -4.7796 | 0.077543 | 0.080445 | 0.10099 | -0.027396 | -0.10494 | -0.23695 | -0.38741 | 0.004034 | -0.28277 | 0.14187 | -0.016265 | -0.020299 | -0.071544 | -0.0775 | 121.6304 | 121.313 | 121.1626 | 6.1311 | -121.4724 | 121.2672 | 121.4784 | 121.4725 | 10.9057 | -121.546
782.8281 | 121.6553 | -4.541 | 117.0776 | 1.4211e-13 | -0.019312 | -0.00073712 | 0.06353 | -0.0034912 | 0.058178 | -0.01755 | 0.00034614 | 0.00037167 | 0.064272 | 0.0098824 | 0.060778 | -4.4308 | 1.3613 | -4.5638 | 117.094 | 116.7812 | 116.617 | -4.4726 | -4.3899 | 6.2137 | -4.5435 | 116.7308 | 116.9421 | 116.9315 | -4.5369 | 0.068454 | 0.016398 | 0.11018 | -0.022783 | -0.091237 | -0.29639 | -0.4606 | 0.004097 | -0.34681 | 0.15108 | -0.002471 | -0.006568 | -0.13558 | -0.14611 | 121.6351 | 121.3223 | 121.1581 | 5.9023 | -121.5502 | 121.2718 | 121.4831 | 121.4725 | 10.7547 | -121.6146
784.6094 | 121.6782 | -4.5776 | 116.9907 | 1.4211e-13 | -0.019312 | -0.0011645 | 0.06353 | -0.003705 | 0.058392 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.0096686 | 0.060564 | -4.4446 | 1.375 | -4.573 | 117.0849 | 116.7538 | 116.6033 | -4.4771 | -4.4037 | 6.264 | -4.5618 | 116.7217 | 116.9283 | 116.9224 | -4.5552 | 0.1005 | 0.094216 | 0.13307 | 0.004682 | -0.095814 | -0.23689 | -0.38736 | 0.022403 | -0.26899 | 0.17397 | 0.015835 | -0.006568 | -0.06234 | -0.068296 | 121.6625 | 121.3314 | 121.1809 | 5.9526 | -121.4678 | 121.2993 | 121.506 | 121.5 | 10.8417 | -121.5459
786.3125 | 121.7377 | -4.303 | 117.2607 | 1.4211e-13 | -0.019312 | -0.0011645 | 0.063744 | -0.0034912 | 0.058178 | 0.012972 | 0.00077334 | 0.00037167 | 0.063844 | 0.0096686 | 0.060564 | -4.2156 | 1.3704 | -4.3395 | 117.3184 | 117.0056 | 116.8322 | -4.2436 | -4.1656 | 6.3739 | -4.3237 | 116.9552 | 117.171 | 117.1605 | -4.3126 | 0.059364 | 0.057634 | 0.087331 | -0.036484 | -0.095848 | -0.25512 | -0.42851 | -0.009578 | -0.30557 | 0.1374 | -0.02073 | -0.011152 | -0.089754 | -0.10029 | 121.6214 | 121.3086 | 121.1352 | 5.6734 | -121.5044 | 121.2582 | 121.474 | 121.4634 | 10.6769 | -121.5733
788.0781 | 121.6003 | -4.0924 | 117.5629 | 1.4211e-13 | -0.018885 | -0.00073712 | 0.06353 | -0.003705 | 0.058392 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0098824 | 0.060992 | -3.9501 | 1.3887 | -4.0785 | 117.5793 | 117.2483 | 117.0978 | -3.9872 | -3.9046 | 6.4563 | -4.0627 | 117.2116 | 117.432 | 117.4214 | -4.0516 | 0.10521 | 0.016478 | 0.14231 | 0.013906 | -0.091305 | -0.31457 | -0.46508 | 0.040842 | -0.35129 | 0.18781 | 0.029685 | -0.011157 | -0.1309 | -0.14143 | 121.6718 | 121.3407 | 121.1902 | 5.4811 | -121.5501 | 121.304 | 121.5244 | 121.5138 | 10.5487 | -121.6144
789.7812 | 121.6736 | -3.7811 | 117.778 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063316 | -0.003064 | 0.057751 | -0.0099194 | 0.00055974 | 0.00037167 | 0.063844 | 0.0096686 | 0.061205 | -3.6983 | 1.4116 | -3.8221 | 117.822 | 117.5047 | 117.3496 | -3.7262 | -3.6528 | 6.5388 | -3.8109 | 117.4634 | 117.6792 | 117.6641 | -3.8043 | 0.054931 | 0.043984 | 0.082838 | -0.040989 | -0.09592 | -0.27329 | -0.4284 | -0.02318 | -0.31463 | 0.12836 | -0.029765 | -0.006585 | -0.098802 | -0.11391 | 121.6031 | 121.2858 | 121.1307 | 5.1927 | -121.5042 | 121.2445 | 121.4603 | 121.4452 | 10.3199 | -121.5823
791.4844 | 121.5958 | -3.5019 | 118.1213 | 1.4211e-13 | -0.019312 | -0.00073712 | 0.063103 | -0.0032776 | 0.058178 | -0.0022889 | 0.00098694 | 0.00015807 | 0.064058 | 0.0098824 | 0.060564 | -3.3412 | 1.4345 | -3.4604 | 118.1837 | 117.8665 | 117.7159 | -3.3874 | -3.2865 | 6.6303 | -3.4492 | 117.8205 | 118.0318 | 118.035 | -3.4426 | 0.11453 | 0.062353 | 0.16072 | 0.041459 | -0.073076 | -0.25488 | -0.40544 | 0.05931 | -0.30083 | 0.21543 | 0.052717 | -0.006593 | -0.089573 | -0.086372 | 121.6856 | 121.3683 | 121.2178 | 4.9364 | -121.5087 | 121.3224 | 121.5337 | 121.5369 | 10.1322 | -121.5639
793.25 | 121.6049 | -3.3646 | 118.2404 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063316 | -0.0032776 | 0.058178 | 0.0053411 | 0.00077334 | 0.00015807 | 0.064485 | 0.0098824 | 0.060992 | -3.2038 | 1.4482 | -3.3322 | 118.321 | 117.9947 | 117.8349 | -3.25 | -3.1674 | 6.6853 | -3.3164 | 117.9487 | 118.1554 | 118.154 | -3.319 | 0.11457 | 0.080687 | 0.16074 | 0.032322 | -0.082252 | -0.24569 | -0.40541 | 0.045609 | -0.29165 | 0.19714 | 0.04817 | 0.002561 | -0.084969 | -0.086346 | 121.6856 | 121.3592 | 121.1995 | 4.8128 | -121.4903 | 121.3133 | 121.52 | 121.5186 | 10.0498 | -121.5593
795.0156 | 121.701 | -3.1586 | 118.4418 | 1.4211e-13 | -0.018885 | -0.00095092 | 0.063744 | -0.0032776 | 0.057751 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064272 | 0.010096 | 0.061205 | -3.039 | 1.4711 | -3.1445 | 118.4996 | 118.1687 | 118.0135 | -3.076 | -2.9843 | 6.7631 | -3.147 | 118.1181 | 118.3385 | 118.3326 | -3.1495 | 0.082579 | 0.057828 | 0.11957 | 0.014037 | -0.068542 | -0.27311 | -0.42826 | 0.009031 | -0.32366 | 0.1743 | 0.011589 | 0.002558 | -0.10324 | -0.1092 | 121.6582 | 121.3272 | 121.1721 | 4.6297 | -121.5178 | 121.2767 | 121.4971 | 121.4911 | 9.9217 | -121.5913
796.7812 | 121.6415 | -3.0808 | 118.5196 | 1.4211e-13 | -0.018885 | -0.00073712 | 0.06353 | -0.0032776 | 0.058178 | -0.0022889 | 0.00055974 | 0.00058547 | 0.064058 | 0.0098824 | 0.060992 | -2.9383 | 1.4666 | -3.0621 | 118.582 | 118.2648 | 118.1051 | -2.9844 | -2.8927 | 6.8181 | -3.0417 | 118.2143 | 118.4347 | 118.4241 | -3.0488 | 0.096339 | 0.062419 | 0.14247 | 0.018627 | -0.077712 | -0.25477 | -0.41451 | 0.031946 | -0.30533 | 0.18805 | 0.03908 | 0.007134 | -0.08491 | -0.095444 | 121.6628 | 121.3456 | 121.1858 | 4.5473 | -121.504 | 121.295 | 121.5154 | 121.5049 | 9.8988 | -121.5684
798.5312 | 121.7239 | -2.9984 | 118.5654 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.06353 | -0.0034912 | 0.058392 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064272 | 0.0096686 | 0.061205 | -2.8696 | 1.4895 | -2.9797 | 118.669 | 118.3427 | 118.1829 | -2.9066 | -2.8057 | 6.8684 | -2.973 | 118.3013 | 118.5125 | 118.4974 | -2.9755 | 0.091783 | 0.10363 | 0.12875 | 0.018639 | -0.073144 | -0.22271 | -0.38245 | 0.022809 | -0.26412 | 0.19265 | 0.025363 | 0.002554 | -0.052851 | -0.067964 | 121.6674 | 121.341 | 121.1813 | 4.4878 | -121.4719 | 121.2996 | 121.5109 | 121.4958 | 9.8668 | -121.5409
800.2969 | 121.6141 | -2.9572 | 118.6661 | 1.4211e-13 | -0.019312 | -0.00073712 | 0.063316 | -0.003064 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.0098824 | 0.060992 | -2.8238 | 1.4986 | -2.9385 | 118.7148 | 118.3885 | 118.2287 | -2.8608 | -2.7737 | 6.8913 | -2.9135 | 118.3379 | 118.5537 | 118.5523 | -2.9252 | 0.096373 | 0.048707 | 0.13333 | 0.018644 | -0.077729 | -0.27762 | -0.43737 | 0.031977 | -0.3282 | 0.1835 | 0.043687 | 0.01171 | -0.11235 | -0.11373 | 121.6719 | 121.3456 | 121.1859 | 4.4558 | -121.5269 | 121.295 | 121.5109 | 121.5095 | 9.8485 | -121.5913
802 | 121.7331 | -2.7878 | 118.7531 | 1.4211e-13 | -0.019526 | -0.00073712 | 0.063103 | -0.003705 | 0.058178 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064272 | 0.0098824 | 0.060778 | -2.6819 | 1.5032 | -2.8012 | 118.843 | 118.5212 | 118.3661 | -2.7143 | -2.6363 | 6.9737 | -2.7853 | 118.4661 | 118.6911 | 118.6851 | -2.7878 | 0.073526 | 0.089927 | 0.10589 | -0.01338 | -0.086906 | -0.23181 | -0.38699 | -3e-05 | -0.28697 | 0.15149 | 0.002519 | 0.002549 | -0.061968 | -0.067924 | 121.6308 | 121.309 | 121.1538 | 4.291 | -121.4673 | 121.2539 | 121.4789 | 121.4729 | 9.7615 | -121.5409
803.7656 | 121.5866 | -2.7466 | 118.8858 | 1.4211e-13 | -0.018885 | -0.00052352 | 0.06353 | -0.0034912 | 0.057965 | -0.0099194 | 0.00055974 | 0.00037167 | 0.064058 | 0.010096 | 0.060778 | -2.5629 | 1.5307 | -2.6775 | 118.962 | 118.6357 | 118.4851 | -2.6135 | -2.5172 | 7.0241 | -2.6708 | 118.5943 | 118.8055 | 118.7996 | -2.6733 | 0.13306 | 0.076214 | 0.18373 | 0.069035 | -0.064029 | -0.25009 | -0.4007 | 0.073241 | -0.29153 | 0.22934 | 0.075788 | 0.002547 | -0.080254 | -0.08621 | 121.7086 | 121.3823 | 121.2317 | 4.2772 | -121.4993 | 121.3409 | 121.5521 | 121.5462 | 9.7707 | -121.5591
805.5469 | 121.6919 | -2.623 | 118.895 | 1.4211e-13 | -0.019098 | -0.00073712 | 0.063316 | -0.0034912 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.0098824 | 0.060564 | -2.5125 | 1.5352 | -2.6318 | 119.0215 | 118.6952 | 118.54 | -2.5494 | -2.4577 | 7.0378 | -2.6113 | 118.6492 | 118.8605 | 118.8591 | -2.6184 | 0.073573 | 0.12658 | 0.1105 | -0.008778 | -0.082351 | -0.19972 | -0.35491 | 0.004591 | -0.24574 | 0.16527 | 0.011715 | 0.007124 | -0.034466 | -0.035843 | 121.6445 | 121.3182 | 121.163 | 4.1582 | -121.4444 | 121.2722 | 121.4835 | 121.4821 | 9.6608 | -121.5134
807.3125 | 121.7239 | -2.5772 | 118.9774 | 1.4211e-13 | -0.019312 | -0.00073712 | 0.06353 | -0.0034912 | 0.058392 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.0096686 | 0.060778 | -2.4575 | 1.549 | -2.5768 | 119.0673 | 118.7456 | 118.5904 | -2.499 | -2.4074 | 7.0607 | -2.5609 | 118.7087 | 118.9154 | 118.9141 | -2.5634 | 0.078164 | 0.089964 | 0.11966 | 0.000384 | -0.07778 | -0.23175 | -0.38694 | 0.01376 | -0.26862 | 0.16985 | 0.016304 | 0.002544 | -0.061921 | -0.063298 | 121.6445 | 121.3228 | 121.1676 | 4.1262 | -121.4764 | 121.2859 | 121.4926 | 121.4913 | 9.6379 | -121.5408
809.0156 | 121.5912 | -2.4811 | 119.1147 | 1.4211e-13 | -0.019312 | -0.00095092 | 0.063957 | -0.003705 | 0.057965 | -0.0022889 | 0.00098694 | 0.00015807 | 0.064485 | 0.0098824 | 0.060992 | -2.3477 | 1.5673 | -2.4669 | 119.1772 | 118.8601 | 118.7003 | -2.3892 | -2.2975 | 7.1157 | -2.4602 | 118.8049 | 119.0253 | 119.0194 | -2.4581 | 0.091928 | 0.062516 | 0.13341 | 0.014133 | -0.077795 | -0.2546 | -0.41438 | 0.022943 | -0.3098 | 0.18361 | 0.020905 | -0.002038 | -0.089363 | -0.095319 | 121.6583 | 121.3412 | 121.1814 | 4.0484 | -121.5038 | 121.286 | 121.5064 | 121.5004 | 9.5968 | -121.5728
810.7812 | 121.6095 | -2.4033 | 119.2154 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063316 | -0.003705 | 0.057965 | 0.0053411 | 0.00077334 | -5.5534e-05 | 0.064272 | 0.0098824 | 0.060564 | -2.2607 | 1.581 | -2.3754 | 119.2642 | 118.9425 | 118.7964 | -2.3113 | -2.2105 | 7.1935 | -2.3594 | 118.8965 | 119.1123 | 119.1064 | -2.3711 | 0.09195 | 0.048798 | 0.14258 | 0.027879 | -0.064071 | -0.27289 | -0.41894 | 0.03212 | -0.31894 | 0.19279 | 0.043817 | 0.011697 | -0.10308 | -0.10903 | 121.6675 | 121.3458 | 121.1997 | 3.9843 | -121.5267 | 121.2997 | 121.5156 | 121.5096 | 9.5968 | -121.5865
812.5469 | 121.6187 | -2.2202 | 119.4168 | 1.4211e-13 | -0.019312 | -0.00095092 | 0.063744 | -0.0032776 | 0.057965 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064058 | 0.01031 | 0.060992 | -2.0684 | 1.5993 | -2.1831 | 119.4656 | 119.1394 | 118.975 | -2.1098 | -2.0182 | 7.2713 | -2.1671 | 119.0842 | 119.3229 | 119.3032 | -2.1742 | 0.11032 | 0.048831 | 0.15177 | 0.037061 | -0.073256 | -0.27741 | -0.44179 | 0.045904 | -0.33263 | 0.20199 | 0.053018 | 0.007114 | -0.093878 | -0.11357 | 121.6858 | 121.3596 | 121.1952 | 3.8195 | -121.5266 | 121.3043 | 121.5431 | 121.5234 | 9.4915 | -121.5911
814.3125 | 121.5912 | -2.1744 | 119.4305 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.06353 | -0.003705 | 0.057965 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064058 | 0.010096 | 0.060564 | -2.0318 | 1.6085 | -2.151 | 119.4885 | 119.176 | 119.0116 | -2.0778 | -1.9815 | 7.3492 | -2.1305 | 119.1162 | 119.3412 | 119.3307 | -2.1376 | 0.096593 | 0.05799 | 0.14262 | 0.023332 | -0.073261 | -0.25451 | -0.4189 | 0.036758 | -0.31432 | 0.19284 | 0.04387 | 0.007112 | -0.089297 | -0.099831 | 121.6629 | 121.3504 | 121.186 | 3.7829 | -121.5083 | 121.2906 | 121.5156 | 121.5051 | 9.5236 | -121.5682
816.0156 | 121.7239 | -2.1149 | 119.4626 | 1.4211e-13 | -0.019526 | -0.00073712 | 0.06353 | -0.0032776 | 0.057751 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064272 | 0.0098824 | 0.060778 | -1.9906 | 1.6131 | -2.0961 | 119.5389 | 119.2218 | 119.0529 | -2.0228 | -1.9403 | 7.3629 | -2.0847 | 119.1666 | 119.3916 | 119.3765 | -2.0918 | 0.092031 | 0.076309 | 0.12432 | 0.018763 | -0.073268 | -0.24077 | -0.40973 | 0.023037 | -0.296 | 0.17454 | 0.030148 | 0.007111 | -0.070975 | -0.086088 | 121.6538 | 121.3367 | 121.1677 | 3.7279 | -121.4854 | 121.2815 | 121.5065 | 121.4914 | 9.4778 | -121.5544
817.7812 | 121.6187 | -2.1881 | 119.4031 | 1.4211e-13 | -0.019312 | -0.00095092 | 0.063316 | -0.003064 | 0.057965 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064058 | 0.010096 | 0.060992 | -2.0318 | 1.6177 | -2.1465 | 119.4656 | 119.144 | 118.9842 | -2.0732 | -1.977 | 7.3812 | -2.1305 | 119.0979 | 119.3138 | 119.3078 | -2.1376 | 0.1149 | 0.062564 | 0.15635 | 0.041644 | -0.073261 | -0.2591 | -0.4189 | 0.050491 | -0.30516 | 0.21115 | 0.057603 | 0.007112 | -0.089302 | -0.095258 | 121.6537 | 121.3321 | 121.1723 | 3.8058 | -121.4763 | 121.286 | 121.5019 | 121.4959 | 9.5693 | -121.5407
819.5 | 121.6324 | -2.2018 | 119.2291 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063316 | -0.0034912 | 0.057965 | -0.0022889 | 0.00034614 | 0.00015807 | 0.064485 | 0.0098824 | 0.060992 | -2.0821 | 1.6177 | -2.2014 | 119.3329 | 119.0066 | 118.8468 | -2.1282 | -2.0273 | 7.4179 | -2.1809 | 118.9514 | 119.181 | 119.1659 | -2.1971 | 0.073691 | 0.10374 | 0.11972 | 0.000437 | -0.073254 | -0.22252 | -0.38231 | 0.004699 | -0.27773 | 0.17452 | 0.020971 | 0.016272 | -0.048132 | -0.063245 | 121.5347 | 121.2085 | 121.0487 | 3.8195 | -121.3573 | 121.1532 | 121.3828 | 121.3677 | 9.6197 | -121.4263
821.25 | 121.5225 | -2.2751 | 119.0918 | 1.4211e-13 | -0.019312 | -0.00095092 | 0.063103 | -0.003705 | 0.057751 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.0098824 | 0.060564 | -2.1279 | 1.6131 | -2.2472 | 119.1818 | 118.8692 | 118.7049 | -2.1785 | -2.0868 | 7.4499 | -2.2358 | 118.814 | 119.0391 | 119.0239 | -2.2475 | 0.096565 | 0.089983 | 0.14718 | 0.027896 | -0.068669 | -0.22256 | -0.38692 | 0.027574 | -0.27775 | 0.18824 | 0.039268 | 0.011694 | -0.052739 | -0.067852 | 121.4569 | 121.1443 | 120.98 | 3.8882 | -121.2703 | 121.0891 | 121.3141 | 121.299 | 9.725 | -121.3393
823.0156 | 121.3394 | -1.9226 | 119.3436 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063103 | -0.003705 | 0.057537 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064058 | 0.0098824 | 0.060778 | -1.7662 | 1.6405 | -1.8809 | 119.4061 | 119.0845 | 118.9247 | -1.8076 | -1.7114 | 7.5003 | -1.8604 | 119.0384 | 119.2588 | 119.2437 | -1.8766 | 0.11498 | 0.062554 | 0.1564 | 0.041681 | -0.073298 | -0.25912 | -0.41892 | 0.045981 | -0.30518 | 0.21122 | 0.062244 | 0.016263 | -0.084737 | -0.09985 | 121.3287 | 121.0071 | 120.8473 | 3.5632 | -121.1512 | 120.961 | 121.1814 | 121.1663 | 9.4229 | -121.2202
824.7812 | 121.5546 | -1.7487 | 119.5908 | 1.4211e-13 | -0.019312 | -0.0011645 | 0.06353 | -0.0034912 | 0.057751 | 0.0053411 | 0.00077334 | 0.00037167 | 0.064058 | 0.010096 | 0.060564 | -1.6518 | 1.6589 | -1.771 | 119.6946 | 119.3683 | 119.2131 | -1.7023 | -1.6015 | 7.5964 | -1.7505 | 119.3223 | 119.5427 | 119.5276 | -1.7713 | 0.046345 | 0.1038 | 0.096907 | -0.02239 | -0.068735 | -0.22242 | -0.37766 | -0.022657 | -0.2685 | 0.14716 | -0.001817 | 0.02084 | -0.048055 | -0.063168 | 121.4432 | 121.117 | 120.9618 | 3.4075 | -121.2931 | 121.0709 | 121.2914 | 121.2762 | 9.3451 | -121.3621
826.5312 | 121.6049 | -1.767 | 119.6457 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.063316 | -0.0039186 | 0.057965 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.0096686 | 0.060564 | -1.6609 | 1.6589 | -1.7756 | 119.7358 | 119.4141 | 119.2589 | -1.7023 | -1.5969 | 7.6148 | -1.7505 | 119.368 | 119.5885 | 119.5825 | -1.7667 | 0.064656 | 0.090074 | 0.10606 | -0.008658 | -0.073314 | -0.23156 | -0.3868 | 0.000233 | -0.27765 | 0.17005 | 0.016494 | 0.016261 | -0.057201 | -0.063157 | 121.5027 | 121.1811 | 121.0259 | 3.4258 | -121.348 | 121.135 | 121.3555 | 121.3495 | 9.3817 | -121.4124
828.2969 | 121.6232 | -1.7853 | 119.6686 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00098694 | 0.00015807 | 0.063844 | 0.0098824 | 0.060778 | -1.6518 | 1.6726 | -1.7756 | 119.7678 | 119.4462 | 119.2864 | -1.7023 | -1.6107 | 7.6285 | -1.7459 | 119.3909 | 119.616 | 119.6008 | -1.7667 | 0.082966 | 0.099234 | 0.13353 | 0.009652 | -0.073314 | -0.22239 | -0.38222 | 0.018543 | -0.27764 | 0.17462 | 0.039383 | 0.02084 | -0.052618 | -0.067731 | 121.5531 | 121.2315 | 121.0716 | 3.4579 | -121.3709 | 121.1762 | 121.4012 | 121.3861 | 9.4138 | -121.4353
830.0156 | 121.5912 | -1.799 | 119.7006 | 1.4211e-13 | -0.019526 | -0.00095092 | 0.063103 | -0.0034912 | 0.057751 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.010096 | 0.060564 | -1.6563 | 1.6818 | -1.7756 | 119.7815 | 119.4599 | 119.3001 | -1.7023 | -1.6107 | 7.6239 | -1.7596 | 119.4093 | 119.6343 | 119.6146 | -1.7713 | 0.096699 | 0.080926 | 0.14268 | 0.023385 | -0.073314 | -0.2407 | -0.40053 | 0.027697 | -0.29137 | 0.18835 | 0.03938 | 0.011683 | -0.066347 | -0.086039 | 121.5806 | 121.2589 | 121.0991 | 3.4808 | -121.4029 | 121.2083 | 121.4333 | 121.4136 | 9.4229 | -121.4719
831.7969 | 121.5729 | -1.8402 | 119.6594 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.063316 | -0.003705 | 0.057537 | -0.0099194 | 0.00077334 | 0.00015807 | 0.064058 | 0.010096 | 0.060992 | -1.6975 | 1.6818 | -1.8168 | 119.7541 | 119.4324 | 119.2726 | -1.7435 | -1.6473 | 7.6651 | -1.7963 | 119.3864 | 119.6022 | 119.5917 | -1.7988 | 0.096687 | 0.094654 | 0.14268 | 0.02338 | -0.073307 | -0.22698 | -0.3868 | 0.041423 | -0.27307 | 0.19292 | 0.043949 | 0.002526 | -0.057198 | -0.067733 | 121.5943 | 121.2727 | 121.1128 | 3.522 | -121.4029 | 121.2266 | 121.4424 | 121.4319 | 9.5053 | -121.4582
833.5 | 121.5958 | -1.8539 | 119.6777 | 1.4211e-13 | -0.019526 | -0.00052352 | 0.063316 | -0.0034912 | 0.057751 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064058 | 0.010096 | 0.060778 | -1.6838 | 1.7001 | -1.8031 | 119.777 | 119.4553 | 119.2955 | -1.7344 | -1.629 | 7.7063 | -1.7825 | 119.4138 | 119.6297 | 119.6192 | -1.7942 | 0.11958 | 0.099236 | 0.17014 | 0.050848 | -0.06873 | -0.22239 | -0.38222 | 0.059735 | -0.26391 | 0.22497 | 0.071418 | 0.011683 | -0.048037 | -0.058571 | 121.6309 | 121.3093 | 121.1495 | 3.554 | -121.4121 | 121.2678 | 121.4836 | 121.4731 | 9.5603 | -121.4719
835.2656 | 121.6324 | -1.8265 | 119.7189 | 1.4211e-13 | -0.019953 | -0.00073712 | 0.063316 | -0.003705 | 0.057751 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064058 | 0.01031 | 0.060992 | -1.6746 | 1.7001 | -1.7894 | 119.7999 | 119.4737 | 119.323 | -1.7206 | -1.629 | 7.7201 | -1.7734 | 119.4276 | 119.6434 | 119.6375 | -1.7896 | 0.10585 | 0.080929 | 0.15183 | 0.037116 | -0.068733 | -0.24528 | -0.39594 | 0.036848 | -0.29137 | 0.1975 | 0.05311 | 0.016262 | -0.0755 | -0.081456 | 121.6263 | 121.3001 | 121.1495 | 3.5265 | -121.4396 | 121.254 | 121.4699 | 121.464 | 9.5465 | -121.5086
837.0312 | 121.582 | -1.7899 | 119.8242 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.063316 | -0.0034912 | 0.057751 | -0.0099194 | 0.00077334 | 0.00058547 | 0.064058 | 0.0096686 | 0.060778 | -1.6197 | 1.7001 | -1.7344 | 119.8594 | 119.5332 | 119.3871 | -1.6657 | -1.5695 | 7.7659 | -1.7138 | 119.4871 | 119.7121 | 119.697 | -1.7347 | 0.12417 | 0.035162 | 0.17015 | 0.055435 | -0.06874 | -0.29103 | -0.43713 | 0.055173 | -0.33714 | 0.22041 | 0.076012 | 0.020839 | -0.11211 | -0.12722 | 121.6492 | 121.323 | 121.1769 | 3.4899 | -121.4899 | 121.2769 | 121.502 | 121.4869 | 9.5557 | -121.5589
838.7969 | 121.55 | -1.7349 | 119.8608 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.063103 | -0.0032776 | 0.057965 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064272 | 0.0096686 | 0.060778 | -1.5693 | 1.7184 | -1.6886 | 119.9052 | 119.5927 | 119.4329 | -1.6153 | -1.5145 | 7.83 | -1.6772 | 119.5374 | 119.7579 | 119.7519 | -1.6843 | 0.11961 | 0.044325 | 0.16558 | 0.046286 | -0.073325 | -0.26813 | -0.42796 | 0.050608 | -0.32339 | 0.22042 | 0.05771 | 0.007102 | -0.10294 | -0.1089 | 121.6401 | 121.3276 | 121.1678 | 3.4533 | -121.4762 | 121.2724 | 121.4928 | 121.4869 | 9.5649 | -121.5452
840.5625 | 121.7102 | -1.6891 | 119.8151 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00077334 | -5.5534e-05 | 0.063844 | 0.0098824 | 0.060992 | -1.5602 | 1.7184 | -1.6795 | 119.9235 | 119.611 | 119.4466 | -1.6062 | -1.5145 | 7.8528 | -1.6635 | 119.5558 | 119.7762 | 119.7657 | -1.6706 | 0.082993 | 0.10842 | 0.12896 | 0.009666 | -0.073327 | -0.20404 | -0.36845 | 0.018568 | -0.2593 | 0.17464 | 0.02567 | 0.007102 | -0.03885 | -0.049385 | 121.6126 | 121.3002 | 121.1358 | 3.4075 | -121.4212 | 121.2449 | 121.4654 | 121.4548 | 9.542 | -121.4856
842.3281 | 121.6782 | -1.6067 | 119.9066 | 1.4211e-13 | -0.019526 | -0.0011645 | 0.063316 | -0.0032776 | 0.057751 | -0.0099194 | 0.00077334 | 0.00015807 | 0.064058 | 0.010096 | 0.060564 | -1.4961 | 1.7275 | -1.6062 | 120.0013 | 119.6843 | 119.529 | -1.5329 | -1.4504 | 7.8666 | -1.5856 | 119.6244 | 119.854 | 119.8344 | -1.6065 | 0.073858 | 0.094695 | 0.11066 | 0.000521 | -0.073337 | -0.22233 | -0.37759 | 0.000274 | -0.28218 | 0.15635 | 0.02111 | 0.020836 | -0.052567 | -0.072259 | 121.6081 | 121.291 | 121.1358 | 3.3343 | -121.4395 | 121.2312 | 121.4608 | 121.4411 | 9.4733 | -121.5131
844.0938 | 121.6232 | -1.6251 | 119.9707 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.06353 | -0.0034912 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.010096 | 0.060778 | -1.464 | 1.7413 | -1.5742 | 120.0379 | 119.7118 | 119.5565 | -1.5146 | -1.4092 | 7.9124 | -1.5627 | 119.6702 | 119.8861 | 119.8756 | -1.5744 | 0.11049 | 0.067235 | 0.16102 | 0.05088 | -0.059605 | -0.25894 | -0.4142 | 0.050637 | -0.30048 | 0.21587 | 0.062314 | 0.011677 | -0.084604 | -0.095138 | 121.663 | 121.3368 | 121.1816 | 3.3663 | -121.4853 | 121.2953 | 121.5112 | 121.5006 | 9.5374 | -121.5451
845.8125 | 121.6965 | -1.5427 | 119.9799 | 1.4211e-13 | -0.020167 | -0.00095092 | 0.063316 | -0.0034912 | 0.057751 | -0.01755 | 0.00077334 | 0.00037167 | 0.064058 | 0.0098824 | 0.060564 | -1.4137 | 1.7459 | -1.533 | 120.0837 | 119.7713 | 119.6114 | -1.4688 | -1.368 | 7.9673 | -1.517 | 119.716 | 119.9319 | 119.9214 | -1.5286 | 0.073877 | 0.10386 | 0.12899 | 0.009687 | -0.06419 | -0.20857 | -0.36842 | 0.014028 | -0.26385 | 0.17468 | 0.025704 | 0.011676 | -0.047973 | -0.058507 | 121.6264 | 121.314 | 121.1541 | 3.2885 | -121.4486 | 121.2587 | 121.4745 | 121.464 | 9.51 | -121.5085
847.5781 | 121.5683 | -1.5747 | 120.0577 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.063316 | -0.003705 | 0.057537 | 0.0053411 | 0.00077334 | 0.00037167 | 0.064058 | 0.0098824 | 0.060778 | -1.3954 | 1.7459 | -1.5238 | 120.102 | 119.7896 | 119.616 | -1.4459 | -1.3497 | 7.9719 | -1.4986 | 119.7297 | 119.9456 | 119.9397 | -1.5103 | 0.12882 | 0.044358 | 0.17935 | 0.050887 | -0.077928 | -0.26807 | -0.44166 | 0.064386 | -0.32793 | 0.22504 | 0.076062 | 0.011676 | -0.11206 | -0.11801 | 121.6767 | 121.3643 | 121.1907 | 3.3206 | -121.5036 | 121.3045 | 121.5203 | 121.5144 | 9.5466 | -121.568
849.3438 | 121.5546 | -1.4236 | 120.2179 | 1.4211e-13 | -0.019953 | -0.00052352 | 0.063316 | -0.0034912 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.010096 | 0.060778 | -1.2534 | 1.7642 | -1.3682 | 120.244 | 119.9316 | 119.7763 | -1.2994 | -1.2032 | 8.0452 | -1.3521 | 119.8763 | 120.0967 | 120.0862 | -1.3684 | 0.12428 | 0.02607 | 0.17021 | 0.055486 | -0.068792 | -0.28634 | -0.44163 | 0.055267 | -0.34164 | 0.22049 | 0.071519 | 0.016252 | -0.12118 | -0.13172 | 121.6676 | 121.3552 | 121.1999 | 3.1878 | -121.5173 | 121.2999 | 121.5204 | 121.5098 | 9.4688 | -121.5863
851.0469 | 121.701 | -1.2863 | 120.2545 | 1.4211e-13 | -0.020167 | -0.00095092 | 0.063103 | -0.0041322 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.010096 | 0.060778 | -1.1527 | 1.7779 | -1.2674 | 120.3493 | 120.0323 | 119.8724 | -1.2032 | -1.107 | 8.0497 | -1.2514 | 119.9724 | 120.202 | 120.1915 | -1.2676 | 0.083107 | 0.094752 | 0.13361 | 0.018879 | -0.064228 | -0.22223 | -0.3821 | 0.018672 | -0.28211 | 0.17932 | 0.034922 | 0.01625 | -0.052494 | -0.063029 | 121.6356 | 121.3186 | 121.1587 | 3.0642 | -121.4577 | 121.2587 | 121.4883 | 121.4778 | 9.336 | -121.5222
852.8125 | 121.6599 | -1.2726 | 120.3049 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.063316 | -0.0034912 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.010096 | 0.060778 | -1.1344 | 1.7871 | -1.2491 | 120.3813 | 120.0598 | 119.8999 | -1.1803 | -1.0887 | 8.0772 | -1.2331 | 119.9999 | 120.2249 | 120.2144 | -1.2493 | 0.092268 | 0.076446 | 0.13819 | 0.02346 | -0.068808 | -0.24511 | -0.40498 | 0.023255 | -0.305 | 0.1839 | 0.039503 | 0.016248 | -0.079955 | -0.09049 | 121.6539 | 121.3323 | 121.1725 | 3.0596 | -121.4852 | 121.2725 | 121.4975 | 121.487 | 9.3498 | -121.5542
854.5781 | 121.6553 | -1.2589 | 120.3278 | 1.4211e-13 | -0.019739 | -0.00095092 | 0.063316 | -0.003705 | 0.057751 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.0096686 | 0.061205 | -1.1115 | 1.7916 | -1.2262 | 120.3905 | 120.0735 | 119.9228 | -1.162 | -1.0612 | 8.1093 | -1.2102 | 120.0273 | 120.2524 | 120.2373 | -1.2356 | 0.096851 | 0.062715 | 0.14735 | 0.032618 | -0.064233 | -0.25426 | -0.40497 | 0.023258 | -0.30041 | 0.19764 | 0.048664 | 0.025406 | -0.075372 | -0.090485 | 121.6493 | 121.3323 | 121.1816 | 3.0505 | -121.4898 | 121.2862 | 121.5112 | 121.4961 | 9.3681 | -121.5634
856.2656 | 121.6278 | -1.2543 | 120.3598 | 1.4211e-13 | -0.019953 | -0.0011645 | 0.063316 | -0.0039186 | 0.057537 | -0.0099194 | 0.00055974 | 0.00015807 | 0.064058 | 0.01031 | 0.060992 | -1.0886 | 1.8008 | -1.2033 | 120.4179 | 120.101 | 119.9548 | -1.1391 | -1.0429 | 8.123 | -1.1827 | 120.0502 | 120.2799 | 120.2602 | -1.1944 | 0.11517 | 0.058143 | 0.16566 | 0.050931 | -0.064236 | -0.25883 | -0.40497 | 0.059889 | -0.30956 | 0.21137 | 0.071558 | 0.011669 | -0.079943 | -0.099635 | 121.6722 | 121.3552 | 121.2091 | 3.0551 | -121.4989 | 121.3045 | 121.5341 | 121.5144 | 9.3773 | -121.5542
858.0312 | 121.6507 | -1.2268 | 120.369 | 1.4211e-13 | -0.019953 | -0.0011645 | 0.063103 | -0.0034912 | 0.057751 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064058 | 0.010096 | 0.060778 | -1.0795 | 1.81 | -1.1896 | 120.4363 | 120.1147 | 119.964 | -1.1254 | -1.02 | 8.1734 | -1.169 | 120.0594 | 120.289 | 120.2693 | -1.1852 | 0.10144 | 0.0673 | 0.14735 | 0.037201 | -0.064238 | -0.25425 | -0.40496 | 0.041582 | -0.30956 | 0.2068 | 0.057829 | 0.016247 | -0.079942 | -0.099634 | 121.6631 | 121.3415 | 121.1908 | 3.0368 | -121.4943 | 121.2862 | 121.5158 | 121.4961 | 9.4002 | -121.5542
859.7969 | 121.7056 | -1.1856 | 120.3506 | 1.4211e-13 | -0.019953 | -0.00095092 | 0.063316 | -0.0034912 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.01031 | 0.060778 | -1.0611 | 1.8145 | -1.1759 | 120.45 | 120.1422 | 119.9777 | -1.1071 | -1.0017 | 8.2237 | -1.1507 | 120.0914 | 120.3073 | 120.2922 | -1.1715 | 0.078556 | 0.099346 | 0.12447 | 0.009737 | -0.068819 | -0.20847 | -0.37292 | 0.014119 | -0.2592 | 0.18392 | 0.034945 | 0.020826 | -0.043317 | -0.05843 | 121.6356 | 121.3278 | 121.1633 | 3.0001 | -121.4577 | 121.2771 | 121.4929 | 121.4778 | 9.4093 | -121.5221
861.5469 | 121.6919 | -1.1536 | 120.4102 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.06353 | -0.0034912 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064272 | 0.010096 | 0.060778 | -1.0337 | 1.8191 | -1.1438 | 120.4775 | 120.1697 | 120.0098 | -1.0796 | -0.98337 | 8.2237 | -1.1323 | 120.1143 | 120.3394 | 120.3243 | -1.144 | 0.073985 | 0.067308 | 0.1199 | 0.009741 | -0.064244 | -0.2405 | -0.40038 | 0.009548 | -0.29582 | 0.17019 | 0.021216 | 0.011668 | -0.070775 | -0.085888 | 121.631 | 121.3232 | 121.1633 | 2.9727 | -121.4897 | 121.2679 | 121.4929 | 121.4778 | 9.3773 | -121.5542
863.2969 | 121.5912 | -1.181 | 120.4514 | 1.4211e-13 | -0.019739 | -0.0011645 | 0.063316 | -0.0032776 | 0.058178 | -0.01755 | 0.00055974 | 0.00015807 | 0.064272 | 0.01031 | 0.060778 | -1.0154 | 1.8283 | -1.1255 | 120.5004 | 120.1925 | 120.0281 | -1.0521 | -0.96048 | 8.2466 | -1.1003 | 120.1327 | 120.3485 | 120.3426 | -1.1257 | 0.12892 | 0.049001 | 0.16568 | 0.05552 | -0.073405 | -0.25881 | -0.42326 | 0.05533 | -0.3187 | 0.22055 | 0.080733 | 0.025403 | -0.10282 | -0.10877 | 121.6814 | 121.3736 | 121.2091 | 3.0093 | -121.5035 | 121.3137 | 121.5296 | 121.5236 | 9.4276 | -121.5771
865.0156 | 121.6278 | -1.1581 | 120.4651 | 1.4211e-13 | -0.019953 | -0.00073712 | 0.06353 | -0.0034912 | 0.057751 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.0098824 | 0.060564 | -0.99246 | 1.8374 | -1.1026 | 120.5187 | 120.2154 | 120.0556 | -1.0384 | -0.94674 | 8.2832 | -1.0866 | 120.151 | 120.376 | 120.3655 | -1.0982 | 0.11977 | 0.053581 | 0.16568 | 0.055524 | -0.06425 | -0.24964 | -0.40952 | 0.059915 | -0.31412 | 0.2114 | 0.071581 | 0.011666 | -0.089079 | -0.099613 | 121.6768 | 121.3736 | 121.2137 | 2.9956 | -121.5035 | 121.3091 | 121.5342 | 121.5236 | 9.4414 | -121.5633
866.7812 | 121.5775 | -1.1673 | 120.4788 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.06353 | -0.0039186 | 0.057751 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.010096 | 0.060564 | -0.99246 | 1.842 | -1.1026 | 120.5232 | 120.22 | 120.0647 | -1.0338 | -0.93759 | 8.3153 | -1.0774 | 120.1601 | 120.3806 | 120.3701 | -1.0982 | 0.13351 | 0.044426 | 0.17483 | 0.064679 | -0.068829 | -0.2588 | -0.4141 | 0.06907 | -0.3187 | 0.22971 | 0.089894 | 0.020824 | -0.098233 | -0.10877 | 121.6905 | 121.3873 | 121.232 | 3.0093 | -121.5126 | 121.3274 | 121.5479 | 121.5374 | 9.4826 | -121.577
868.5469 | 121.6873 | -1.0666 | 120.5109 | 1.4211e-13 | -0.019953 | -0.00073712 | 0.06353 | -0.003705 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.064272 | 0.01031 | 0.060778 | -0.91921 | 1.8557 | -1.0431 | 120.5873 | 120.2841 | 120.1242 | -0.96968 | -0.87349 | 8.3245 | -1.0133 | 120.2196 | 120.4401 | 120.4387 | -1.0433 | 0.096905 | 0.076481 | 0.14738 | 0.023488 | -0.073417 | -0.22674 | -0.38662 | 0.023307 | -0.29122 | 0.1931 | 0.053288 | 0.029981 | -0.070754 | -0.072131 | 121.6539 | 121.3507 | 121.1908 | 2.9223 | -121.4805 | 121.2862 | 121.5067 | 121.5053 | 9.391 | -121.5541
870.2969 | 121.6003 | -1.0529 | 120.5612 | 1.4211e-13 | -0.019953 | -0.00073712 | 0.06353 | -0.0034912 | 0.057751 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064058 | 0.010523 | 0.060992 | -0.89632 | 1.8695 | -1.0019 | 120.6194 | 120.3208 | 120.1609 | -0.93763 | -0.83686 | 8.3428 | -0.98583 | 120.2609 | 120.4813 | 120.4662 | -0.99749 | 0.11522 | 0.058176 | 0.15654 | 0.05096 | -0.064264 | -0.24046 | -0.40034 | 0.055363 | -0.30037 | 0.216 | 0.067027 | 0.011664 | -0.079901 | -0.095014 | 121.6723 | 121.3736 | 121.2137 | 2.9223 | -121.4988 | 121.3137 | 121.5342 | 121.5191 | 9.3956 | -121.5587
872 | 121.6141 | -1.0712 | 120.5795 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.063316 | -0.0034912 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.01031 | 0.060564 | -0.89174 | 1.8832 | -0.99732 | 120.6286 | 120.3253 | 120.1609 | -0.93763 | -0.83228 | 8.3519 | -0.98583 | 120.2609 | 120.4813 | 120.4799 | -0.99749 | 0.13353 | 0.049021 | 0.17943 | 0.073849 | -0.059686 | -0.25419 | -0.41865 | 0.073674 | -0.31868 | 0.23889 | 0.085338 | 0.011664 | -0.098212 | -0.099589 | 121.6997 | 121.3965 | 121.232 | 2.9544 | -121.5172 | 121.332 | 121.5525 | 121.5511 | 9.4231 | -121.577
873.7656 | 121.7056 | -0.96588 | 120.6024 | 1.4211e-13 | -0.019739 | -0.00073712 | 0.063316 | -0.0032776 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064058 | 0.01031 | 0.060778 | -0.84595 | 1.8832 | -0.94696 | 120.6835 | 120.3711 | 120.2158 | -0.88269 | -0.78191 | 8.384 | -0.93088 | 120.3158 | 120.5363 | 120.5303 | -0.94255 | 0.083196 | 0.081074 | 0.11993 | 0.018924 | -0.064272 | -0.23129 | -0.3866 | 0.023333 | -0.28663 | 0.18397 | 0.034996 | 0.011663 | -0.066156 | -0.072112 | 121.6494 | 121.337 | 121.1817 | 2.8491 | -121.4851 | 121.2817 | 121.5021 | 121.4962 | 9.3499 | -121.545
875.4844 | 121.6461 | -0.94299 | 120.6757 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.063316 | -0.0041322 | 0.058392 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.010523 | 0.060992 | -0.80017 | 1.8924 | -0.91949 | 120.7201 | 120.4169 | 120.257 | -0.85063 | -0.7407 | 8.4252 | -0.8851 | 120.3616 | 120.5683 | 120.5624 | -0.89676 | 0.092361 | 0.044459 | 0.14282 | 0.023506 | -0.068855 | -0.25874 | -0.41863 | 0.046233 | -0.31408 | 0.20229 | 0.057895 | 0.011662 | -0.10735 | -0.1133 | 121.6631 | 121.3599 | 121.2 | 2.8354 | -121.5263 | 121.3046 | 121.5113 | 121.5053 | 9.3682 | -121.5724
877.25 | 121.669 | -0.91095 | 120.6757 | 1.4211e-13 | -0.02038 | -0.00073712 | 0.063316 | -0.0039186 | 0.057751 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064272 | 0.01031 | 0.060778 | -0.7727 | 1.8969 | -0.88286 | 120.743 | 120.4444 | 120.2845 | -0.80942 | -0.71323 | 8.4801 | -0.8622 | 120.389 | 120.5958 | 120.5944 | -0.88302 | 0.10153 | 0.067351 | 0.13825 | 0.028089 | -0.073439 | -0.23127 | -0.39116 | 0.027927 | -0.28661 | 0.19772 | 0.048746 | 0.020819 | -0.079877 | -0.081254 | 121.654 | 121.3553 | 121.1954 | 2.8079 | -121.4851 | 121.3 | 121.5067 | 121.5054 | 9.3911 | -121.5587
879.0312 | 121.6003 | -0.89722 | 120.7031 | 1.4211e-13 | -0.02038 | -0.00073712 | 0.063103 | -0.003705 | 0.058392 | -0.0022889 | 0.00077334 | -5.5534e-05 | 0.063844 | 0.01031 | 0.060564 | -0.7315 | 1.9153 | -0.85539 | 120.7796 | 120.4764 | 120.3074 | -0.79111 | -0.69034 | 8.5259 | -0.83015 | 120.4211 | 120.6324 | 120.6265 | -0.84639 | 0.10611 | 0.076512 | 0.16572 | 0.041826 | -0.064285 | -0.22668 | -0.39574 | 0.050824 | -0.28203 | 0.20688 | 0.067064 | 0.01624 | -0.070714 | -0.07667 | 121.6769 | 121.3737 | 121.2046 | 2.8125 | -121.4942 | 121.3183 | 121.5296 | 121.5237 | 9.4231 | -121.5495
880.8125 | 121.6324 | -0.89722 | 120.7214 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.063316 | -0.003705 | 0.058178 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063844 | 0.01031 | 0.060564 | -0.73607 | 1.9015 | -0.85539 | 120.7751 | 120.4764 | 120.3165 | -0.79111 | -0.68576 | 8.5168 | -0.83015 | 120.4165 | 120.6416 | 120.6219 | -0.85097 | 0.10611 | 0.053623 | 0.16114 | 0.041826 | -0.064285 | -0.24499 | -0.40489 | 0.046246 | -0.30492 | 0.21146 | 0.067064 | 0.020818 | -0.079868 | -0.099559 | 121.6723 | 121.3737 | 121.2138 | 2.7987 | -121.5125 | 121.3137 | 121.5388 | 121.5191 | 9.414 | -121.5724
882.5156 | 121.7239 | -0.82398 | 120.694 | 1.4211e-13 | -0.02038 | -0.00095092 | 0.063103 | -0.0034912 | 0.057537 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063844 | 0.010523 | 0.060778 | -0.72692 | 1.9153 | -0.82792 | 120.7934 | 120.4902 | 120.3349 | -0.77279 | -0.67202 | 8.5625 | -0.81184 | 120.4303 | 120.6461 | 120.6448 | -0.83723 | 0.051184 | 0.099402 | 0.097059 | -0.003947 | -0.055131 | -0.20379 | -0.35911 | -0.01326 | -0.26372 | 0.15195 | 0.012137 | 0.025397 | -0.047823 | -0.0492 | 121.6173 | 121.3142 | 121.1588 | 2.7392 | -121.4668 | 121.2542 | 121.4701 | 121.4687 | 9.3865 | -121.5312
884.2812 | 121.6141 | -0.87433 | 120.726 | 1.4211e-13 | -0.020167 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00077334 | 0.00037167 | 0.064058 | 0.010523 | 0.061205 | -0.71318 | 1.9198 | -0.82792 | 120.8025 | 120.4948 | 120.344 | -0.76821 | -0.66744 | 8.5259 | -0.80726 | 120.4394 | 120.6599 | 120.6585 | -0.8235 | 0.10612 | 0.076516 | 0.16115 | 0.046407 | -0.05971 | -0.23125 | -0.38199 | 0.050831 | -0.2866 | 0.20688 | 0.067069 | 0.016238 | -0.06613 | -0.067507 | 121.6769 | 121.3691 | 121.2183 | 2.7942 | -121.4942 | 121.3137 | 121.5342 | 121.5328 | 9.4002 | -121.5495
886.0469 | 121.6736 | -0.84228 | 120.7443 | 1.4211e-13 | -0.020594 | -0.0011645 | 0.06353 | -0.0039186 | 0.057751 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063844 | 0.01031 | 0.061205 | -0.70402 | 1.9198 | -0.80961 | 120.8208 | 120.5085 | 120.3623 | -0.7499 | -0.64913 | 8.5946 | -0.78895 | 120.4623 | 120.6736 | 120.6722 | -0.81434 | 0.092389 | 0.076519 | 0.13826 | 0.032677 | -0.059712 | -0.23583 | -0.38199 | 0.027944 | -0.28202 | 0.19316 | 0.05334 | 0.025396 | -0.070705 | -0.072083 | 121.6631 | 121.3508 | 121.2046 | 2.7621 | -121.4942 | 121.3046 | 121.5159 | 121.5145 | 9.4369 | -121.5587
887.75 | 121.6827 | -0.81482 | 120.7352 | 1.4211e-13 | -0.020594 | -0.0011645 | 0.063103 | -0.0039186 | 0.057965 | -0.0099194 | 0.00034614 | 0.00058547 | 0.064272 | 0.010523 | 0.061205 | -0.69029 | 1.9244 | -0.80503 | 120.83 | 120.536 | 120.3806 | -0.73616 | -0.63081 | 8.5763 | -0.77979 | 120.476 | 120.6874 | 120.6768 | -0.79603 | 0.07866 | 0.094831 | 0.12453 | 0.009789 | -0.068871 | -0.1992 | -0.35452 | 0.018793 | -0.25913 | 0.184 | 0.035032 | 0.016239 | -0.047814 | -0.058348 | 121.6448 | 121.3508 | 121.1955 | 2.7392 | -121.4713 | 121.2909 | 121.5022 | 121.4916 | 9.3911 | -121.5312
889.5 | 121.6278 | -0.80566 | 120.8221 | 1.4211e-13 | -0.020167 | -0.0011645 | 0.063103 | -0.0034912 | 0.057751 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.01031 | 0.060778 | -0.6674 | 1.9336 | -0.77756 | 120.8575 | 120.5589 | 120.3898 | -0.71327 | -0.60792 | 8.5854 | -0.76147 | 120.4944 | 120.7102 | 120.7043 | -0.77771 | 0.092399 | 0.035326 | 0.13827 | 0.028103 | -0.064296 | -0.26328 | -0.43234 | 0.027954 | -0.32779 | 0.19774 | 0.044192 | 0.016238 | -0.1119 | -0.11785 | 121.6631 | 121.3645 | 121.1955 | 2.7392 | -121.5354 | 121.3 | 121.5159 | 121.51 | 9.3911 | -121.5999
891.2812 | 121.582 | -0.82398 | 120.8176 | 1.4211e-13 | -0.019953 | -0.0011645 | 0.063744 | -0.0041322 | 0.057537 | -0.0022889 | 0.00077334 | 0.00015807 | 0.064272 | 0.01031 | 0.060992 | -0.65366 | 1.9473 | -0.76383 | 120.862 | 120.568 | 120.4173 | -0.69953 | -0.60334 | 8.6312 | -0.73858 | 120.5035 | 120.7194 | 120.718 | -0.76397 | 0.12445 | 0.044482 | 0.17031 | 0.060149 | -0.064298 | -0.24954 | -0.40029 | 0.060001 | -0.31406 | 0.22063 | 0.085396 | 0.025395 | -0.098161 | -0.099539 | 121.686 | 121.392 | 121.2413 | 2.7713 | -121.5171 | 121.3275 | 121.5434 | 121.542 | 9.4552 | -121.5815
893.0469 | 121.7239 | -0.76446 | 120.8038 | 1.4211e-13 | -0.02038 | -0.0013783 | 0.063316 | -0.0039186 | 0.057751 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063844 | 0.010523 | 0.060992 | -0.63535 | 1.9565 | -0.74551 | 120.8895 | 120.5863 | 120.4264 | -0.68121 | -0.58503 | 8.6862 | -0.72026 | 120.5264 | 120.7423 | 120.7318 | -0.74108 | 0.083253 | 0.085685 | 0.12912 | 0.018952 | -0.064301 | -0.2175 | -0.3774 | 0.023385 | -0.27743 | 0.17944 | 0.044201 | 0.020816 | -0.061535 | -0.07207 | 121.654 | 121.3508 | 121.1909 | 2.7209 | -121.485 | 121.2909 | 121.5068 | 121.4962 | 9.4506 | -121.5449
894.7656 | 121.7422 | -0.75531 | 120.8176 | 1.4211e-13 | -0.020167 | -0.0011645 | 0.06353 | -0.003705 | 0.057965 | -0.01755 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.01031 | 0.060992 | -0.61704 | 1.9427 | -0.7272 | 120.8987 | 120.6047 | 120.4493 | -0.6629 | -0.56213 | 8.7091 | -0.71569 | 120.5401 | 120.7606 | 120.7547 | -0.73192 | 0.092414 | 0.081109 | 0.13828 | 0.028111 | -0.064303 | -0.21291 | -0.36824 | 0.023388 | -0.27743 | 0.19318 | 0.039625 | 0.016237 | -0.056954 | -0.06291 | 121.654 | 121.36 | 121.2046 | 2.698 | -121.4805 | 121.2954 | 121.5159 | 121.51 | 9.4644 | -121.5495
896.5156 | 121.7377 | -0.73242 | 120.8359 | 1.4211e-13 | -0.020594 | -0.0011645 | 0.06353 | -0.003705 | 0.058178 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064058 | 0.010523 | 0.060992 | -0.59872 | 1.9565 | -0.72262 | 120.917 | 120.6184 | 120.4631 | -0.64458 | -0.55298 | 8.6999 | -0.69279 | 120.5722 | 120.7698 | 120.7638 | -0.71361 | 0.087841 | 0.081113 | 0.1337 | 0.009801 | -0.07804 | -0.21749 | -0.37281 | 0.018815 | -0.26369 | 0.17945 | 0.03963 | 0.020815 | -0.066107 | -0.072063 | 121.6494 | 121.3508 | 121.1955 | 2.6889 | -121.4805 | 121.3046 | 121.5022 | 121.4962 | 9.4323 | -121.5495
898.2812 | 121.7148 | -0.71411 | 120.8359 | 1.4211e-13 | -0.020594 | -0.00073712 | 0.06353 | -0.0039186 | 0.057965 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063844 | 0.01031 | 0.060992 | -0.61246 | 1.9656 | -0.71804 | 120.9124 | 120.6047 | 120.4493 | -0.6629 | -0.57129 | 8.7182 | -0.69737 | 120.563 | 120.7652 | 120.7592 | -0.72276 | 0.051215 | 0.076534 | 0.10166 | -0.003932 | -0.055147 | -0.23122 | -0.38655 | -0.008653 | -0.27285 | 0.14282 | 0.016741 | 0.025394 | -0.070685 | -0.076641 | 121.6265 | 121.3188 | 121.1634 | 2.6797 | -121.4988 | 121.2771 | 121.4793 | 121.4733 | 9.4323 | -121.5586
899.9844 | 121.6415 | -0.7782 | 120.8221 | 1.4211e-13 | -0.02038 | -0.00073712 | 0.06353 | -0.0039186 | 0.057965 | -0.0099194 | 0.00077334 | 0.00015807 | 0.064058 | 0.010523 | 0.061419 | -0.6033 | 1.9748 | -0.71804 | 120.917 | 120.6184 | 120.4631 | -0.64916 | -0.5484 | 8.7045 | -0.69279 | 120.5722 | 120.7698 | 120.7638 | -0.70903 | 0.12904 | 0.094845 | 0.1749 | 0.060155 | -0.068883 | -0.20376 | -0.35908 | 0.06917 | -0.24996 | 0.2298 | 0.085406 | 0.016236 | -0.052375 | -0.058331 | 121.6952 | 121.3966 | 121.2413 | 2.753 | -121.4713 | 121.3504 | 121.548 | 121.542 | 9.4827 | -121.5312
901.7656 | 121.6599 | -0.74158 | 120.8405 | 1.4211e-13 | -0.02038 | -0.00095092 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064058 | 0.01031 | 0.060778 | -0.58956 | 1.9702 | -0.70431 | 120.9353 | 120.6367 | 120.4768 | -0.63084 | -0.53466 | 8.7182 | -0.68363 | 120.5859 | 120.7881 | 120.7821 | -0.70445 | 0.11073 | 0.094848 | 0.15201 | 0.037269 | -0.073464 | -0.20375 | -0.36366 | 0.037128 | -0.25453 | 0.20692 | 0.057943 | 0.020815 | -0.05237 | -0.058326 | 121.6769 | 121.3783 | 121.2184 | 2.7118 | -121.4713 | 121.3275 | 121.5297 | 121.5237 | 9.4598 | -121.5449
903.5156 | 121.6919 | -0.73242 | 120.8405 | 1.4211e-13 | -0.020167 | -0.0011645 | 0.063316 | -0.003705 | 0.057537 | -0.0022889 | 0.00055974 | 0.00058547 | 0.064058 | 0.01031 | 0.061205 | -0.58956 | 1.9794 | -0.70431 | 120.9261 | 120.6367 | 120.4722 | -0.64 | -0.53466 | 8.7274 | -0.67448 | 120.5859 | 120.7835 | 120.7821 | -0.69529 | 0.09242 | 0.085692 | 0.14286 | 0.028114 | -0.064306 | -0.20375 | -0.36823 | 0.03713 | -0.25453 | 0.19776 | 0.057945 | 0.020815 | -0.056949 | -0.058326 | 121.6586 | 121.3691 | 121.2046 | 2.7118 | -121.4805 | 121.3183 | 121.5159 | 121.5145 | 9.4598 | -121.5357
905.2188 | 121.6049 | -0.74158 | 120.8771 | 1.4211e-13 | -0.020167 | -0.00073712 | 0.062889 | -0.0041322 | 0.057751 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063844 | 0.01031 | 0.060992 | -0.58956 | 1.9839 | -0.70431 | 120.9353 | 120.6459 | 120.486 | -0.63084 | -0.53008 | 8.7777 | -0.68363 | 120.5859 | 120.7881 | 120.7867 | -0.69987 | 0.11073 | 0.058227 | 0.15201 | 0.037269 | -0.073464 | -0.23121 | -0.39112 | 0.041707 | -0.29115 | 0.21149 | 0.057943 | 0.016236 | -0.088991 | -0.090369 | 121.6769 | 121.3874 | 121.2275 | 2.7255 | -121.5079 | 121.3275 | 121.5297 | 121.5283 | 9.5193 | -121.5769
906.9844 | 121.5958 | -0.75989 | 120.8862 | 1.4211e-13 | -0.02038 | -0.00073712 | 0.06353 | -0.003705 | 0.057751 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063844 | 0.01031 | 0.060992 | -0.59414 | 1.9931 | -0.69057 | 120.9399 | 120.655 | 120.4951 | -0.62626 | -0.5255 | 8.8144 | -0.66532 | 120.5951 | 120.7927 | 120.7959 | -0.69071 | 0.13362 | 0.053651 | 0.16575 | 0.069315 | -0.064308 | -0.23121 | -0.39112 | 0.069175 | -0.29115 | 0.23438 | 0.094568 | 0.025393 | -0.093568 | -0.090366 | 121.6998 | 121.4149 | 121.255 | 2.753 | -121.5125 | 121.355 | 121.5526 | 121.5558 | 9.5743 | -121.5769
908.7656 | 121.6965 | -0.70953 | 120.8313 | 1.4211e-13 | -0.02038 | -0.00095092 | 0.06353 | -0.003705 | 0.057324 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064272 | 0.01031 | 0.060778 | -0.58041 | 1.9977 | -0.69515 | 120.9445 | 120.6413 | 120.4951 | -0.62626 | -0.5255 | 8.8235 | -0.66532 | 120.5951 | 120.7972 | 120.7913 | -0.68613 | 0.083269 | 0.11316 | 0.12913 | 0.014383 | -0.068886 | -0.19002 | -0.33619 | 0.0234 | -0.23622 | 0.18403 | 0.044214 | 0.020814 | -0.034058 | -0.040014 | 121.654 | 121.3508 | 121.2046 | 2.7072 | -121.4576 | 121.3046 | 121.5068 | 121.5008 | 9.5331 | -121.5174
910.4844 | 121.7102 | -0.70953 | 120.8817 | 1.4211e-13 | -0.02038 | -0.00073712 | 0.063316 | -0.0039186 | 0.057537 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064272 | 0.010523 | 0.060564 | -0.57125 | 2.0114 | -0.68142 | 120.9536 | 120.6596 | 120.5043 | -0.61253 | -0.51635 | 8.8556 | -0.65616 | 120.5997 | 120.811 | 120.8096 | -0.68156 | 0.097006 | 0.071963 | 0.13828 | 0.028117 | -0.068889 | -0.22205 | -0.37738 | 0.027979 | -0.28199 | 0.19319 | 0.053372 | 0.025393 | -0.070676 | -0.072054 | 121.6632 | 121.3691 | 121.2138 | 2.7209 | -121.4942 | 121.3092 | 121.5205 | 121.5191 | 9.5651 | -121.5632
912.2344 | 121.7377 | -0.70038 | 120.845 | 1.4211e-13 | -0.020594 | -0.00073712 | 0.063103 | -0.003705 | 0.057537 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.01031 | 0.060778 | -0.56667 | 2.0114 | -0.67684 | 120.9536 | 120.6596 | 120.5043 | -0.61711 | -0.51177 | 8.851 | -0.65158 | 120.6134 | 120.8156 | 120.805 | -0.67698 | 0.083271 | 0.10858 | 0.1337 | 0.02354 | -0.059731 | -0.18543 | -0.34076 | 0.023402 | -0.23164 | 0.18861 | 0.048795 | 0.025393 | -0.029477 | -0.040011 | 121.654 | 121.36 | 121.2046 | 2.7118 | -121.4621 | 121.3138 | 121.5159 | 121.5054 | 9.5514 | -121.522
914 | 121.7377 | -0.69122 | 120.8588 | 1.4211e-13 | -0.020594 | -0.00095092 | 0.063316 | -0.0039186 | 0.058178 | 0.0053411 | 0.00077334 | -5.5534e-05 | 0.064272 | 0.010523 | 0.060778 | -0.57125 | 2.0251 | -0.67684 | 120.9628 | 120.6688 | 120.5043 | -0.60795 | -0.51177 | 8.8647 | -0.65158 | 120.6134 | 120.8201 | 120.8096 | -0.6724 | 0.083274 | 0.10401 | 0.11997 | 0.014385 | -0.068889 | -0.19001 | -0.3545 | 0.018826 | -0.24537 | 0.17946 | 0.03964 | 0.020814 | -0.038631 | -0.049166 | 121.654 | 121.36 | 121.1955 | 2.7164 | -121.4667 | 121.3046 | 121.5114 | 121.5008 | 9.556 | -121.5312
915.7031 | 121.7239 | -0.69122 | 120.8771 | 1.4211e-13 | -0.02038 | -0.00095092 | 0.063744 | -0.0034912 | 0.057965 | -0.0099194 | 0.00034614 | 0.00037167 | 0.064058 | 0.01031 | 0.060778 | -0.56209 | 2.0206 | -0.68142 | 120.9674 | 120.6733 | 120.518 | -0.61253 | -0.49803 | 8.8602 | -0.64701 | 120.618 | 120.8201 | 120.8096 | -0.67698 | 0.078695 | 0.090276 | 0.12913 | 0.009806 | -0.068889 | -0.20374 | -0.35907 | 0.014247 | -0.2591 | 0.19319 | 0.044218 | 0.029971 | -0.056941 | -0.067476 | 121.6586 | 121.3646 | 121.2092 | 2.7118 | -121.4896 | 121.3092 | 121.5114 | 121.5008 | 9.5514 | -121.5541
917.4531 | 121.5912 | -0.70953 | 120.9229 | 1.4211e-13 | -0.020808 | -0.00095092 | 0.063103 | -0.003705 | 0.057537 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010737 | 0.060778 | -0.54836 | 2.0206 | -0.65395 | 120.9857 | 120.6871 | 120.5363 | -0.58963 | -0.47972 | 8.8922 | -0.63785 | 120.6317 | 120.8339 | 120.8371 | -0.6495 | 0.1199 | 0.062813 | 0.16117 | 0.055587 | -0.064313 | -0.23578 | -0.38653 | 0.060031 | -0.29114 | 0.22982 | 0.071687 | 0.011656 | -0.088982 | -0.085781 | 121.6952 | 121.3966 | 121.2459 | 2.7301 | -121.5125 | 121.3412 | 121.5434 | 121.5466 | 9.6017 | -121.5724
919.2188 | 121.7422 | -0.68207 | 120.845 | 1.4211e-13 | -0.020594 | -0.0013783 | 0.063316 | -0.003705 | 0.058178 | -0.0022889 | 0.00098694 | 0.00058547 | 0.064058 | 0.010737 | 0.060778 | -0.54836 | 2.0114 | -0.65853 | 120.9765 | 120.6779 | 120.5226 | -0.60337 | -0.50261 | 8.8922 | -0.63785 | 120.6271 | 120.8293 | 120.8188 | -0.6724 | 0.078698 | 0.13148 | 0.13371 | 0.023543 | -0.055155 | -0.16712 | -0.32245 | 0.009671 | -0.2179 | 0.17946 | 0.044221 | 0.03455 | -0.015741 | -0.026275 | 121.6586 | 121.36 | 121.2047 | 2.6935 | -121.4484 | 121.3092 | 121.5114 | 121.5008 | 9.5743 | -121.5174
920.9375 | 121.6461 | -0.68665 | 120.9274 | 1.4211e-13 | -0.020808 | -0.00073712 | 0.063103 | -0.0039186 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.064272 | 0.01031 | 0.060992 | -0.5392 | 2.016 | -0.64021 | 120.9857 | 120.6917 | 120.5363 | -0.58963 | -0.4843 | 8.906 | -0.63327 | 120.6409 | 120.843 | 120.8417 | -0.64492 | 0.097012 | 0.058236 | 0.14744 | 0.046434 | -0.050578 | -0.23578 | -0.39111 | 0.041721 | -0.28656 | 0.20235 | 0.053377 | 0.011656 | -0.084402 | -0.085779 | 121.6723 | 121.3783 | 121.223 | 2.7026 | -121.5171 | 121.3275 | 121.5297 | 121.5283 | 9.5926 | -121.5724
922.7031 | 121.5912 | -0.6958 | 120.9732 | 1.4211e-13 | -0.021021 | -0.0011645 | 0.063316 | -0.003705 | 0.057751 | -0.0022889 | 0.00077334 | -5.5534e-05 | 0.063844 | 0.010737 | 0.060778 | -0.52089 | 2.0068 | -0.63106 | 121.004 | 120.71 | 120.5546 | -0.57132 | -0.46598 | 8.9288 | -0.61495 | 120.6592 | 120.8613 | 120.86 | -0.63119 | 0.12448 | 0.030772 | 0.17491 | 0.064745 | -0.059738 | -0.26324 | -0.41857 | 0.064613 | -0.31403 | 0.22982 | 0.080847 | 0.016234 | -0.11187 | -0.11324 | 121.6998 | 121.4058 | 121.2504 | 2.7026 | -121.5445 | 121.355 | 121.5571 | 121.5558 | 9.6246 | -121.6044
924.3906 | 121.5912 | -0.68665 | 120.9641 | 1.4211e-13 | -0.020594 | -0.00095092 | 0.063316 | -0.003705 | 0.057751 | -0.0099194 | 0.00098694 | 0.00058547 | 0.063844 | 0.010523 | 0.061205 | -0.50257 | 2.0251 | -0.62648 | 121.0086 | 120.7191 | 120.5638 | -0.553 | -0.45682 | 8.9472 | -0.61038 | 120.6729 | 120.8751 | 120.8645 | -0.62661 | 0.13364 | 0.044507 | 0.18407 | 0.060169 | -0.073475 | -0.24492 | -0.40026 | 0.060037 | -0.29114 | 0.22982 | 0.076271 | 0.016234 | -0.088973 | -0.099507 | 121.6952 | 121.4058 | 121.2504 | 2.7118 | -121.5171 | 121.3596 | 121.5617 | 121.5512 | 9.6338 | -121.5907
926.1562 | 121.7377 | -0.61798 | 120.9366 | 1.4211e-13 | -0.02038 | -0.00095092 | 0.063316 | -0.0041322 | 0.057965 | -0.0022889 | 0.00077334 | 0.00015807 | 0.063844 | 0.01031 | 0.060992 | -0.50257 | 2.0389 | -0.6219 | 121.0177 | 120.7329 | 120.5684 | -0.55758 | -0.45682 | 8.9792 | -0.59664 | 120.6775 | 120.8751 | 120.8645 | -0.61745 | 0.0604 | 0.081129 | 0.11541 | -0.003918 | -0.064318 | -0.20372 | -0.36821 | 0.000529 | -0.25909 | 0.16116 | 0.021342 | 0.020813 | -0.061507 | -0.072041 | 121.6357 | 121.3508 | 121.1864 | 2.6569 | -121.4942 | 121.2955 | 121.4931 | 121.4825 | 9.5972 | -121.554
927.9062 | 121.5958 | -0.66376 | 120.9732 | 1.4211e-13 | -0.020594 | -0.00073712 | 0.063316 | -0.003705 | 0.057537 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.010523 | 0.060992 | -0.498 | 2.0389 | -0.60359 | 121.0223 | 120.7374 | 120.5775 | -0.54842 | -0.44309 | 9.0158 | -0.59206 | 120.6821 | 120.8842 | 120.8783 | -0.60829 | 0.11533 | 0.049086 | 0.16576 | 0.060171 | -0.055163 | -0.23577 | -0.39568 | 0.055463 | -0.29114 | 0.22067 | 0.071697 | 0.016234 | -0.088972 | -0.094927 | 121.686 | 121.4012 | 121.2413 | 2.7026 | -121.5216 | 121.3458 | 121.548 | 121.542 | 9.6796 | -121.5815
929.6094 | 121.5912 | -0.66376 | 120.9641 | 1.4211e-13 | -0.020594 | -0.00095092 | 0.063316 | -0.0041322 | 0.057965 | 0.0053411 | 0.00034614 | 0.00015807 | 0.064058 | 0.010737 | 0.060992 | -0.49342 | 2.0526 | -0.60816 | 121.0269 | 120.7329 | 120.5729 | -0.54842 | -0.44767 | 9.0342 | -0.59206 | 120.6775 | 120.8842 | 120.8737 | -0.61287 | 0.11533 | 0.06282 | 0.17034 | 0.055593 | -0.059741 | -0.23119 | -0.3911 | 0.050884 | -0.28656 | 0.21609 | 0.071697 | 0.020813 | -0.079816 | -0.09035 | 121.6906 | 121.3966 | 121.2367 | 2.7164 | -121.5125 | 121.3413 | 121.548 | 121.5375 | 9.6979 | -121.5769
931.375 | 121.6644 | -0.65918 | 120.9641 | 1.4211e-13 | -0.020594 | -0.00073712 | 0.06353 | -0.0041322 | 0.057965 | 0.0053411 | 0.00034614 | 0.00058547 | 0.063844 | 0.010523 | 0.060992 | -0.49342 | 2.048 | -0.61274 | 121.036 | 120.7374 | 120.5867 | -0.53926 | -0.43393 | 9.057 | -0.58748 | 120.6775 | 120.898 | 120.8874 | -0.60372 | 0.11991 | 0.071977 | 0.16576 | 0.046438 | -0.073477 | -0.22661 | -0.37737 | 0.055465 | -0.28656 | 0.22525 | 0.071699 | 0.016234 | -0.06608 | -0.076614 | 121.6952 | 121.3966 | 121.2459 | 2.7072 | -121.5033 | 121.3367 | 121.5572 | 121.5466 | 9.7162 | -121.5678
933.0938 | 121.6919 | -0.63171 | 120.9595 | 1.4211e-13 | -0.020594 | -0.00073712 | 0.063316 | -0.003705 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.010523 | 0.060564 | -0.48426 | 2.0618 | -0.59901 | 121.0452 | 120.7466 | 120.5913 | -0.53926 | -0.42477 | 9.0708 | -0.57832 | 120.6912 | 120.9025 | 120.8874 | -0.59914 | 0.092449 | 0.085711 | 0.14745 | 0.032706 | -0.059743 | -0.21287 | -0.36821 | 0.032578 | -0.26825 | 0.20694 | 0.05339 | 0.020812 | -0.056924 | -0.072037 | 121.6769 | 121.3783 | 121.223 | 2.6935 | -121.4987 | 121.3229 | 121.5343 | 121.5191 | 9.7025 | -121.5586
934.8594 | 121.6415 | -0.64545 | 120.9732 | 1.4211e-13 | -0.020808 | -0.00095092 | 0.063316 | -0.003705 | 0.057965 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.010951 | 0.060778 | -0.47968 | 2.0618 | -0.59443 | 121.0406 | 120.7466 | 120.5867 | -0.53926 | -0.43393 | 9.0342 | -0.57832 | 120.6958 | 120.9025 | 120.8966 | -0.59914 | 0.10618 | 0.067399 | 0.16576 | 0.051018 | -0.055164 | -0.22661 | -0.38652 | 0.046311 | -0.2774 | 0.21152 | 0.067123 | 0.020812 | -0.070657 | -0.076613 | 121.6861 | 121.392 | 121.2321 | 2.7072 | -121.5125 | 121.3413 | 121.548 | 121.542 | 9.6796 | -121.5723
936.625 | 121.6782 | -0.60883 | 120.9732 | 1.4211e-13 | -0.021021 | -0.00073712 | 0.06353 | -0.0039186 | 0.057751 | -0.0099194 | 0.00055974 | 0.00037167 | 0.064058 | 0.010737 | 0.060564 | -0.48426 | 2.0709 | -0.59901 | 121.0406 | 120.7512 | 120.5958 | -0.53469 | -0.42477 | 9.0754 | -0.57374 | 120.6912 | 120.8934 | 120.8874 | -0.58998 | 0.074139 | 0.067399 | 0.12456 | 0.009818 | -0.064321 | -0.22203 | -0.37737 | 0.018847 | -0.28198 | 0.18405 | 0.035081 | 0.016234 | -0.079814 | -0.08577 | 121.6494 | 121.36 | 121.2047 | 2.6798 | -121.5079 | 121.3001 | 121.5022 | 121.4963 | 9.6842 | -121.5632
938.3906 | 121.6736 | -0.60425 | 121.0007 | 1.4211e-13 | -0.020808 | -0.00095092 | 0.063316 | -0.0041322 | 0.057751 | -0.0022889 | 0.00055974 | 0.00058547 | 0.063844 | 0.010737 | 0.060351 | -0.4751 | 2.0755 | -0.58527 | 121.0498 | 120.7695 | 120.6096 | -0.51637 | -0.42019 | 9.1486 | -0.56001 | 120.7141 | 120.9163 | 120.9149 | -0.56708 | 0.087877 | 0.049091 | 0.12914 | 0.018975 | -0.068902 | -0.23118 | -0.39109 | 0.037163 | -0.28655 | 0.18405 | 0.044239 | 0.007076 | -0.084386 | -0.085764 | 121.654 | 121.3737 | 121.2138 | 2.6798 | -121.517 | 121.3184 | 121.5205 | 121.5192 | 9.7529 | -121.5678
940.1094 | 121.6095 | -0.63629 | 121.0007 | 1.4211e-13 | -0.020808 | -0.00073712 | 0.063316 | -0.0039186 | 0.057751 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.010737 | 0.060992 | -0.45679 | 2.0664 | -0.57154 | 121.0635 | 120.7787 | 120.6233 | -0.51637 | -0.41104 | 9.1486 | -0.55085 | 120.7187 | 120.9254 | 120.9103 | -0.58082 | 0.11992 | 0.062826 | 0.1795 | 0.064754 | -0.055167 | -0.22202 | -0.37736 | 0.055471 | -0.28197 | 0.22526 | 0.08544 | 0.029969 | -0.075229 | -0.090342 | 121.6998 | 121.4149 | 121.2596 | 2.7026 | -121.517 | 121.355 | 121.5617 | 121.5466 | 9.7849 | -121.5815
941.8906 | 121.6644 | -0.59967 | 120.9686 | 1.4211e-13 | -0.021021 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010737 | 0.060992 | -0.4751 | 2.0755 | -0.57612 | 121.0589 | 120.7695 | 120.6142 | -0.51637 | -0.41562 | 9.1761 | -0.56001 | 120.7095 | 120.93 | 120.9103 | -0.56708 | 0.083299 | 0.090291 | 0.12457 | 0.023554 | -0.059745 | -0.19913 | -0.35447 | 0.032585 | -0.25909 | 0.18406 | 0.039661 | 0.007076 | -0.038608 | -0.058299 | 121.6586 | 121.3692 | 121.2138 | 2.6752 | -121.485 | 121.3092 | 121.5297 | 121.51 | 9.7758 | -121.5357
943.6562 | 121.6278 | -0.62256 | 121.0007 | 1.4211e-13 | -0.021021 | -0.0013783 | 0.063316 | -0.0039186 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.010523 | 0.060778 | -0.45221 | 2.0847 | -0.56696 | 121.0681 | 120.7832 | 120.6233 | -0.51179 | -0.3973 | 9.1898 | -0.54169 | 120.7324 | 120.9346 | 120.9241 | -0.56251 | 0.11077 | 0.067405 | 0.17035 | 0.055599 | -0.055168 | -0.21744 | -0.37736 | 0.060053 | -0.26824 | 0.22526 | 0.080865 | 0.020812 | -0.066072 | -0.076606 | 121.6906 | 121.4058 | 121.2459 | 2.7072 | -121.5125 | 121.355 | 121.5572 | 121.5466 | 9.8124 | -121.5632
945.3594 | 121.6919 | -0.59052 | 120.9732 | 1.4211e-13 | -0.020808 | -0.00073712 | 0.06353 | -0.0039186 | 0.058178 | -0.0099194 | 0.00077334 | 0.00037167 | 0.064058 | 0.010737 | 0.060778 | -0.44306 | 2.0892 | -0.55322 | 121.0772 | 120.7832 | 120.637 | -0.49348 | -0.39272 | 9.1898 | -0.53712 | 120.7324 | 120.9392 | 120.9286 | -0.55793 | 0.097039 | 0.10403 | 0.14746 | 0.03729 | -0.059749 | -0.18998 | -0.33616 | 0.032588 | -0.24077 | 0.19779 | 0.053399 | 0.020811 | -0.034028 | -0.044563 | 121.6677 | 121.3737 | 121.2276 | 2.6798 | -121.4667 | 121.3229 | 121.5297 | 121.5192 | 9.7803 | -121.5311
947.1406 | 121.6782 | -0.57678 | 121.0327 | 1.4211e-13 | -0.021021 | -0.0011645 | 0.063103 | -0.003705 | 0.057751 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.064272 | 0.011164 | 0.060778 | -0.4339 | 2.103 | -0.54407 | 121.091 | 120.8015 | 120.6462 | -0.49348 | -0.38356 | 9.2036 | -0.52338 | 120.7507 | 120.9575 | 120.9378 | -0.54877 | 0.083306 | 0.058253 | 0.14288 | 0.032714 | -0.050592 | -0.23117 | -0.38651 | 0.028013 | -0.28197 | 0.19322 | 0.053402 | 0.025389 | -0.075223 | -0.094915 | 121.6677 | 121.3783 | 121.223 | 2.6798 | -121.5262 | 121.3275 | 121.5343 | 121.5146 | 9.7803 | -121.5815
948.8438 | 121.5775 | -0.59967 | 121.0373 | 1.4211e-13 | -0.021021 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | 0.012972 | 0.00077334 | -5.5534e-05 | 0.063844 | 0.010737 | 0.060564 | -0.4339 | 2.0984 | -0.54865 | 121.091 | 120.8061 | 120.6462 | -0.4889 | -0.38356 | 9.2494 | -0.52796 | 120.7462 | 120.9575 | 120.9515 | -0.53961 | 0.11077 | 0.053676 | 0.16577 | 0.051024 | -0.059749 | -0.23117 | -0.39109 | 0.060058 | -0.29112 | 0.21611 | 0.071712 | 0.011654 | -0.0798 | -0.085756 | 121.6906 | 121.4058 | 121.2459 | 2.6981 | -121.5262 | 121.3458 | 121.5572 | 121.5512 | 9.849 | -121.5769
950.5938 | 121.7239 | -0.55847 | 120.9961 | 1.4211e-13 | -0.020808 | -0.00095092 | 0.06353 | -0.0041322 | 0.057965 | 0.0053411 | 0.00055974 | 0.00037167 | 0.063631 | 0.010737 | 0.060564 | -0.42474 | 2.0984 | -0.53491 | 121.1001 | 120.8107 | 120.6599 | -0.47974 | -0.36983 | 9.2585 | -0.50964 | 120.7507 | 120.9666 | 120.9515 | -0.54419 | 0.078733 | 0.10403 | 0.13373 | 0.02356 | -0.055173 | -0.18539 | -0.33615 | 0.014281 | -0.24535 | 0.18864 | 0.048829 | 0.034548 | -0.029445 | -0.044558 | 121.6586 | 121.3692 | 121.2184 | 2.6569 | -121.4758 | 121.3092 | 121.5251 | 121.51 | 9.817 | -121.5403
952.3594 | 121.6095 | -0.58136 | 121.0556 | 1.4211e-13 | -0.020808 | -0.0011645 | 0.063316 | -0.0039186 | 0.058178 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064272 | 0.011378 | 0.060778 | -0.41559 | 2.1213 | -0.52118 | 121.1139 | 120.8199 | 120.6783 | -0.47058 | -0.35609 | 9.2448 | -0.50506 | 120.7691 | 120.9758 | 120.9699 | -0.52587 | 0.11078 | 0.058257 | 0.16577 | 0.060183 | -0.050595 | -0.23574 | -0.37735 | 0.055485 | -0.28654 | 0.22527 | 0.076295 | 0.02081 | -0.079797 | -0.085752 | 121.6952 | 121.4012 | 121.2596 | 2.7027 | -121.5262 | 121.3504 | 121.5572 | 121.5512 | 9.8261 | -121.5815
954.0625 | 121.6415 | -0.56305 | 121.051 | 1.4211e-13 | -0.021021 | -0.00073712 | 0.06353 | -0.0039186 | 0.057537 | -0.0022889 | 0.00077334 | -5.5534e-05 | 0.063844 | 0.010737 | 0.060778 | -0.41101 | 2.1213 | -0.52118 | 121.1139 | 120.8336 | 120.6783 | -0.46142 | -0.35609 | 9.2677 | -0.50049 | 120.7828 | 120.9804 | 120.9699 | -0.51214 | 0.10163 | 0.062835 | 0.15204 | 0.041872 | -0.059753 | -0.21743 | -0.37277 | 0.05091 | -0.26823 | 0.20696 | 0.062563 | 0.011653 | -0.07064 | -0.081174 | 121.6769 | 121.3966 | 121.2413 | 2.6843 | -121.5124 | 121.3458 | 121.5434 | 121.5329 | 9.8307 | -121.5632
955.8438 | 121.7194 | -0.53101 | 121.0373 | 1.4211e-13 | -0.021021 | -0.00095092 | 0.063103 | -0.0039186 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063631 | 0.010951 | 0.060778 | -0.39727 | 2.1167 | -0.5166 | 121.1184 | 120.8428 | 120.6828 | -0.46142 | -0.34693 | 9.286 | -0.49591 | 120.7828 | 120.9895 | 120.9744 | -0.51214 | 0.069582 | 0.081146 | 0.13373 | 0.014407 | -0.055175 | -0.19453 | -0.35446 | 0.018867 | -0.25449 | 0.18407 | 0.035099 | 0.016232 | -0.04775 | -0.062863 | 121.6494 | 121.3738 | 121.2138 | 2.6477 | -121.4987 | 121.3138 | 121.5205 | 121.5054 | 9.817 | -121.5494
957.6094 | 121.6873 | -0.52185 | 121.051 | 1.4211e-13 | -0.020808 | -0.00073712 | 0.063316 | -0.003705 | 0.057965 | 0.012972 | 0.00034614 | 0.00037167 | 0.063844 | 0.010951 | 0.060564 | -0.40185 | 2.1305 | -0.50744 | 121.1322 | 120.8473 | 120.6966 | -0.45227 | -0.33778 | 9.2997 | -0.48217 | 120.7874 | 120.9987 | 120.9882 | -0.50756 | 0.069585 | 0.081148 | 0.12 | 0.014409 | -0.055176 | -0.20369 | -0.35446 | 0.014291 | -0.26365 | 0.18407 | 0.03968 | 0.025389 | -0.052326 | -0.06286 | 121.654 | 121.3692 | 121.2184 | 2.6523 | -121.5033 | 121.3092 | 121.5206 | 121.51 | 9.8216 | -121.5586
959.375 | 121.6827 | -0.53558 | 121.0464 | 1.4211e-13 | -0.021235 | -0.00095092 | 0.063744 | -0.0034912 | 0.057751 | 0.012972 | 0.00077334 | 0.00015807 | 0.063844 | 0.011378 | 0.060564 | -0.38811 | 2.135 | -0.50286 | 121.1413 | 120.8519 | 120.7011 | -0.43853 | -0.3332 | 9.3272 | -0.47759 | 120.7965 | 120.9987 | 120.9927 | -0.4984 | 0.097054 | 0.094882 | 0.14747 | 0.032719 | -0.064335 | -0.19453 | -0.3453 | 0.037181 | -0.24991 | 0.20239 | 0.057991 | 0.02081 | -0.047749 | -0.053704 | 121.6769 | 121.3875 | 121.2367 | 2.6706 | -121.485 | 121.3321 | 121.5343 | 121.5283 | 9.8628 | -121.5448
961.0938 | 121.6782 | -0.52643 | 121.0602 | 1.4211e-13 | -0.021235 | -0.00052352 | 0.06353 | -0.0041322 | 0.057965 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063844 | 0.011164 | 0.060351 | -0.38354 | 2.1305 | -0.50286 | 121.1459 | 120.8565 | 120.7011 | -0.43853 | -0.32862 | 9.2539 | -0.47301 | 120.8057 | 121.0079 | 121.0019 | -0.4984 | 0.087899 | 0.085727 | 0.14289 | 0.023564 | -0.064335 | -0.20369 | -0.35903 | 0.028026 | -0.25449 | 0.19781 | 0.053414 | 0.025388 | -0.052324 | -0.05828 | 121.6723 | 121.3829 | 121.2276 | 2.6569 | -121.4987 | 121.3321 | 121.5343 | 121.5283 | 9.7804 | -121.5586
962.875 | 121.6736 | -0.5127 | 121.0419 | 1.4211e-13 | -0.020808 | -0.00095092 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010951 | 0.060778 | -0.37896 | 2.1396 | -0.48913 | 121.1459 | 120.8611 | 120.7103 | -0.43395 | -0.32404 | 9.2768 | -0.47301 | 120.8011 | 121.0079 | 121.0111 | -0.48924 | 0.078745 | 0.10404 | 0.13374 | 0.023566 | -0.055179 | -0.1808 | -0.33156 | 0.02345 | -0.24076 | 0.18865 | 0.039681 | 0.016231 | -0.034013 | -0.030812 | 121.6586 | 121.3738 | 121.223 | 2.6523 | -121.4758 | 121.3138 | 121.5206 | 121.5238 | 9.7895 | -121.5311
964.5781 | 121.6736 | -0.52185 | 121.0831 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.003705 | 0.057751 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.011164 | 0.060351 | -0.3698 | 2.1488 | -0.47997 | 121.1505 | 120.8611 | 120.7149 | -0.43853 | -0.31946 | 9.2997 | -0.46843 | 120.8103 | 121.017 | 121.0065 | -0.48467 | 0.083322 | 0.067418 | 0.15205 | 0.041879 | -0.041443 | -0.222 | -0.36818 | 0.037185 | -0.2728 | 0.20239 | 0.053416 | 0.016231 | -0.066055 | -0.07659 | 121.6723 | 121.3829 | 121.2367 | 2.6706 | -121.5216 | 121.3321 | 121.5389 | 121.5283 | 9.8216 | -121.5677
966.3438 | 121.7148 | -0.50812 | 121.0693 | 1.4211e-13 | -0.021235 | -0.00073712 | 0.063316 | -0.0041322 | 0.057965 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063844 | 0.010951 | 0.060564 | -0.37438 | 2.1488 | -0.48455 | 121.1551 | 120.8702 | 120.7195 | -0.42479 | -0.3103 | 9.3043 | -0.46386 | 120.8103 | 121.0216 | 121.0065 | -0.48009 | 0.083326 | 0.085729 | 0.13374 | 0.023567 | -0.059759 | -0.19911 | -0.34987 | 0.028031 | -0.25907 | 0.19781 | 0.044262 | 0.016231 | -0.047744 | -0.062857 | 121.6632 | 121.3783 | 121.2276 | 2.6569 | -121.4941 | 121.3184 | 121.5297 | 121.5146 | 9.8124 | -121.5494
968.0469 | 121.7377 | -0.49896 | 121.0785 | 1.4211e-13 | -0.021021 | -0.0013783 | 0.06353 | -0.0039186 | 0.057751 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.010951 | 0.060778 | -0.37438 | 2.1579 | -0.47539 | 121.1596 | 120.8794 | 120.7195 | -0.42479 | -0.3103 | 9.3272 | -0.45928 | 120.8194 | 121.017 | 121.0156 | -0.48009 | 0.07417 | 0.081152 | 0.12458 | 0.023568 | -0.050602 | -0.1991 | -0.35903 | 0.018875 | -0.25906 | 0.18866 | 0.039684 | 0.020809 | -0.061477 | -0.062854 | 121.6586 | 121.3784 | 121.2184 | 2.6569 | -121.5033 | 121.3184 | 121.516 | 121.5146 | 9.8262 | -121.5586
969.8125 | 121.6873 | -0.5127 | 121.0922 | 1.4211e-13 | -0.021449 | -0.00052352 | 0.062889 | -0.003705 | 0.057751 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010951 | 0.060778 | -0.3698 | 2.1534 | -0.47539 | 121.1596 | 120.8794 | 120.7286 | -0.42937 | -0.30573 | 9.3501 | -0.4547 | 120.8194 | 121.0353 | 121.0156 | -0.47551 | 0.083324 | 0.067419 | 0.14289 | 0.037301 | -0.046023 | -0.21284 | -0.3636 | 0.037187 | -0.2728 | 0.20697 | 0.057996 | 0.020809 | -0.056896 | -0.076587 | 121.6723 | 121.3921 | 121.2413 | 2.666 | -121.5216 | 121.3321 | 121.548 | 121.5283 | 9.8628 | -121.5677
971.5 | 121.6873 | -0.52185 | 121.0693 | 1.4211e-13 | -0.021021 | -0.0011645 | 0.06353 | -0.0041322 | 0.057751 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.010737 | 0.060564 | -0.36064 | 2.1671 | -0.47082 | 121.1734 | 120.8794 | 120.7286 | -0.42021 | -0.30573 | 9.3272 | -0.44554 | 120.8194 | 121.0353 | 121.0248 | -0.47093 | 0.10164 | 0.10404 | 0.16121 | 0.051035 | -0.050603 | -0.18995 | -0.34072 | 0.050921 | -0.24991 | 0.21612 | 0.07631 | 0.025389 | -0.034008 | -0.044542 | 121.6952 | 121.4012 | 121.2505 | 2.6889 | -121.4895 | 121.3413 | 121.5572 | 121.5466 | 9.849 | -121.5403
973.2656 | 121.7102 | -0.48981 | 121.0693 | 1.4211e-13 | -0.021449 | -0.0011645 | 0.063103 | -0.0039186 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.064058 | 0.011164 | 0.060778 | -0.35149 | 2.1671 | -0.46624 | 121.1734 | 120.8885 | 120.7332 | -0.41106 | -0.30115 | 9.3776 | -0.44554 | 120.8377 | 121.0399 | 121.0294 | -0.47093 | 0.078751 | 0.10404 | 0.13832 | 0.02357 | -0.055181 | -0.18079 | -0.33614 | 0.018877 | -0.2316 | 0.18866 | 0.044266 | 0.025389 | -0.029429 | -0.039964 | 121.6632 | 121.3784 | 121.223 | 2.6569 | -121.4804 | 121.3275 | 121.5297 | 121.5192 | 9.8674 | -121.5403
975.0469 | 121.6324 | -0.52185 | 121.0876 | 1.4211e-13 | -0.021449 | -0.00052352 | 0.06353 | -0.0039186 | 0.057751 | 0.012972 | 0.00055974 | 0.00015807 | 0.063844 | 0.010737 | 0.060778 | -0.34233 | 2.1671 | -0.4525 | 121.1825 | 120.9023 | 120.7561 | -0.39732 | -0.29199 | 9.3455 | -0.4318 | 120.8469 | 121.0445 | 121.0431 | -0.46177 | 0.12453 | 0.094889 | 0.17952 | 0.069348 | -0.055184 | -0.18536 | -0.33155 | 0.060079 | -0.24075 | 0.22986 | 0.090046 | 0.029967 | -0.043161 | -0.044538 | 121.7044 | 121.4241 | 121.2779 | 2.6889 | -121.485 | 121.3687 | 121.5663 | 121.565 | 9.8674 | -121.5494
976.7656 | 121.7377 | -0.4715 | 121.0785 | 1.4211e-13 | -0.021449 | -0.00052352 | 0.06353 | -0.003705 | 0.057537 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.011164 | 0.060778 | -0.33775 | 2.1671 | -0.44335 | 121.1917 | 120.9023 | 120.7515 | -0.39732 | -0.28283 | 9.3821 | -0.4318 | 120.8423 | 121.0491 | 121.0431 | -0.45719 | 0.074178 | 0.1132 | 0.13374 | 0.028151 | -0.046027 | -0.17621 | -0.32698 | 0.014304 | -0.23617 | 0.18867 | 0.039692 | 0.025388 | -0.029427 | -0.035383 | 121.6632 | 121.3738 | 121.223 | 2.6386 | -121.4758 | 121.3138 | 121.5206 | 121.5146 | 9.8536 | -121.5357
978.5156 | 121.6095 | -0.49896 | 121.1426 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.063316 | -0.0034912 | 0.057751 | -0.0099194 | 0.00034614 | -0.00026913 | 0.063631 | 0.010737 | 0.060564 | -0.33775 | 2.1717 | -0.4525 | 121.2008 | 120.9069 | 120.7469 | -0.39732 | -0.28283 | 9.4004 | -0.4318 | 120.8515 | 121.0536 | 121.0523 | -0.45261 | 0.10164 | 0.058271 | 0.16121 | 0.046459 | -0.055184 | -0.23572 | -0.39564 | 0.046348 | -0.2911 | 0.21613 | 0.067157 | 0.020809 | -0.088935 | -0.090313 | 121.6998 | 121.4058 | 121.2459 | 2.6706 | -121.5399 | 121.3504 | 121.5526 | 121.5512 | 9.8994 | -121.5952
980.2969 | 121.6873 | -0.48981 | 121.0968 | 1.4211e-13 | -0.021662 | -0.00095092 | 0.06353 | -0.003705 | 0.057537 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063631 | 0.011164 | 0.060778 | -0.34233 | 2.1625 | -0.44335 | 121.2008 | 120.9069 | 120.7561 | -0.4019 | -0.28283 | 9.4279 | -0.42723 | 120.8561 | 121.0536 | 121.0523 | -0.45261 | 0.087909 | 0.10405 | 0.14747 | 0.046461 | -0.041448 | -0.18994 | -0.34071 | 0.037193 | -0.24075 | 0.20698 | 0.06258 | 0.025387 | -0.043159 | -0.044537 | 121.6907 | 121.3967 | 121.2459 | 2.6523 | -121.4987 | 121.3459 | 121.5434 | 121.5421 | 9.9177 | -121.5494
982 | 121.7102 | -0.48065 | 121.0831 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.063957 | -0.003705 | 0.057965 | 0.0053411 | 0.00077334 | 0.00015807 | 0.063844 | 0.011164 | 0.060564 | -0.33775 | 2.19 | -0.44335 | 121.1963 | 120.9114 | 120.7515 | -0.39274 | -0.27825 | 9.4188 | -0.42723 | 120.8561 | 121.0536 | 121.0477 | -0.44346 | 0.087912 | 0.1132 | 0.1429 | 0.037306 | -0.050606 | -0.17163 | -0.33155 | 0.037195 | -0.22701 | 0.2024 | 0.053425 | 0.01623 | -0.029426 | -0.035382 | 121.6769 | 121.3921 | 121.2322 | 2.6706 | -121.4758 | 121.3367 | 121.5343 | 121.5283 | 9.8994 | -121.5265
983.7656 | 121.6095 | -0.50354 | 121.1288 | 1.4211e-13 | -0.021235 | -0.00073712 | 0.063744 | -0.0039186 | 0.057751 | -0.0099194 | 0.00055974 | 0.00058547 | 0.063844 | 0.011164 | 0.060564 | -0.3286 | 2.19 | -0.44792 | 121.2008 | 120.9206 | 120.7607 | -0.39274 | -0.27825 | 9.4371 | -0.41807 | 120.8561 | 121.0582 | 121.0614 | -0.44346 | 0.1108 | 0.072004 | 0.17494 | 0.055616 | -0.055184 | -0.20825 | -0.36817 | 0.060083 | -0.27279 | 0.22529 | 0.085471 | 0.025388 | -0.070624 | -0.067422 | 121.7044 | 121.4241 | 121.2642 | 2.6935 | -121.5216 | 121.3596 | 121.5618 | 121.565 | 9.9406 | -121.5723
985.4688 | 121.7422 | -0.46234 | 121.1105 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.0039186 | 0.057965 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063844 | 0.010951 | 0.060564 | -0.31944 | 2.1946 | -0.43877 | 121.21 | 120.9114 | 120.7652 | -0.38816 | -0.2691 | 9.4325 | -0.41807 | 120.8515 | 121.0491 | 121.0568 | -0.43888 | 0.07418 | 0.099471 | 0.1429 | 0.023573 | -0.050607 | -0.19909 | -0.34529 | 0.023463 | -0.25906 | 0.19325 | 0.044272 | 0.020809 | -0.061471 | -0.053691 | 121.6723 | 121.3738 | 121.2276 | 2.6569 | -121.4987 | 121.3138 | 121.5114 | 121.5192 | 9.8948 | -121.5494
987.25 | 121.7148 | -0.45319 | 121.1105 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.0039186 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010951 | 0.060351 | -0.33317 | 2.2037 | -0.43419 | 121.2054 | 120.916 | 120.7652 | -0.38816 | -0.26452 | 9.4966 | -0.41349 | 120.8698 | 121.0628 | 121.066 | -0.43888 | 0.065025 | 0.094892 | 0.12001 | 0.018997 | -0.046028 | -0.19452 | -0.34529 | 0.014308 | -0.24075 | 0.18867 | 0.039696 | 0.025388 | -0.047735 | -0.044534 | 121.6586 | 121.3692 | 121.2184 | 2.6569 | -121.4987 | 121.323 | 121.516 | 121.5192 | 9.9498 | -121.5494
989.0156 | 121.7422 | -0.46234 | 121.0922 | 1.4211e-13 | -0.021662 | -0.00095092 | 0.063957 | -0.0034912 | 0.057324 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064272 | 0.010951 | 0.060778 | -0.33317 | 2.2037 | -0.43877 | 121.2054 | 120.9298 | 120.7698 | -0.379 | -0.26452 | 9.4829 | -0.40891 | 120.8652 | 121.0765 | 121.0614 | -0.42514 | 0.083338 | 0.1132 | 0.12917 | 0.023573 | -0.059765 | -0.16247 | -0.3224 | 0.0372 | -0.22701 | 0.19782 | 0.053429 | 0.016229 | -0.015688 | -0.030801 | 121.6678 | 121.3921 | 121.2322 | 2.6661 | -121.4712 | 121.3276 | 121.5389 | 121.5238 | 9.9452 | -121.5174
990.7969 | 121.7148 | -0.44861 | 121.1472 | 1.4211e-13 | -0.021449 | -0.0013783 | 0.063744 | -0.0039186 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.010951 | 0.060137 | -0.32402 | 2.2083 | -0.42503 | 121.2146 | 120.9298 | 120.7744 | -0.37442 | -0.25994 | 9.492 | -0.41349 | 120.8698 | 121.0674 | 121.0706 | -0.42514 | 0.074184 | 0.067428 | 0.12459 | 0.023575 | -0.050609 | -0.2174 | -0.37275 | 0.023467 | -0.27737 | 0.18867 | 0.035118 | 0.011651 | -0.079778 | -0.076576 | 121.6632 | 121.3784 | 121.223 | 2.6569 | -121.5216 | 121.3184 | 121.516 | 121.5192 | 9.9406 | -121.5723
992.5 | 121.669 | -0.44403 | 121.1334 | 1.4211e-13 | -0.021662 | -0.00073712 | 0.06353 | -0.0041322 | 0.057751 | -0.0099194 | 0.00077334 | 0.00015807 | 0.063844 | 0.010737 | 0.060564 | -0.31028 | 2.222 | -0.42046 | 121.2237 | 120.9343 | 120.7836 | -0.36984 | -0.25536 | 9.5699 | -0.39975 | 120.8744 | 121.0765 | 121.0706 | -0.41598 | 0.074186 | 0.090318 | 0.13375 | 0.023576 | -0.05061 | -0.19909 | -0.34986 | 0.028047 | -0.25905 | 0.18867 | 0.044277 | 0.01623 | -0.056887 | -0.062843 | 121.6678 | 121.3784 | 121.2276 | 2.6661 | -121.5033 | 121.3184 | 121.5206 | 121.5146 | 10.0139 | -121.5494
994.2656 | 121.6003 | -0.47607 | 121.1655 | 1.4211e-13 | -0.021662 | -0.0013783 | 0.063744 | -0.0039186 | 0.057537 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.011164 | 0.060564 | -0.31028 | 2.222 | -0.41588 | 121.2237 | 120.9343 | 120.7881 | -0.36984 | -0.25078 | 9.5287 | -0.39518 | 120.8881 | 121.0811 | 121.0889 | -0.42056 | 0.10623 | 0.058275 | 0.16579 | 0.060198 | -0.046031 | -0.23113 | -0.37732 | 0.055511 | -0.27736 | 0.22529 | 0.080898 | 0.025387 | -0.084352 | -0.076572 | 121.6998 | 121.4104 | 121.2642 | 2.6981 | -121.5353 | 121.3642 | 121.5572 | 121.565 | 10.0047 | -121.586
996.0469 | 121.6232 | -0.48523 | 121.1517 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.003705 | 0.057537 | 0.0053411 | 0.00034614 | 0.00037167 | 0.064058 | 0.011164 | 0.060564 | -0.31486 | 2.222 | -0.41588 | 121.2283 | 120.9435 | 120.7973 | -0.379 | -0.25078 | 9.5515 | -0.39975 | 120.8789 | 121.0811 | 121.0797 | -0.41598 | 0.10623 | 0.076586 | 0.17037 | 0.069353 | -0.036873 | -0.20824 | -0.35443 | 0.069245 | -0.27279 | 0.23445 | 0.085475 | 0.01623 | -0.070619 | -0.071996 | 121.7135 | 121.4287 | 121.2825 | 2.7073 | -121.5307 | 121.3642 | 121.5663 | 121.565 | 10.0368 | -121.5677
997.8281 | 121.637 | -0.46234 | 121.1609 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.003705 | 0.057965 | -0.0022889 | 0.00055974 | 0.00037167 | 0.063844 | 0.011164 | 0.060351 | -0.3057 | 2.222 | -0.41588 | 121.2329 | 120.9527 | 120.8019 | -0.36069 | -0.2462 | 9.5882 | -0.3906 | 120.8927 | 121.0903 | 121.0843 | -0.41141 | 0.10165 | 0.072009 | 0.15664 | 0.046465 | -0.055189 | -0.20824 | -0.35901 | 0.050936 | -0.26821 | 0.21614 | 0.071744 | 0.020808 | -0.070618 | -0.076573 | 121.6952 | 121.415 | 121.2642 | 2.6844 | -121.5216 | 121.355 | 121.5526 | 121.5467 | 10.0505 | -121.5723
999.5312 | 121.6644 | -0.43945 | 121.1472 | 1.4211e-13 | -0.021449 | -0.0011645 | 0.06353 | -0.003705 | 0.057537 | 0.0053411 | 0.00013254 | 0.00015807 | 0.064058 | 0.011164 | 0.060351 | -0.3057 | 2.2358 | -0.41588 | 121.2375 | 120.9389 | 120.8019 | -0.36069 | -0.2462 | 9.6019 | -0.38602 | 120.8881 | 121.0948 | 121.0889 | -0.41141 | 0.078766 | 0.09032 | 0.13375 | 0.023577 | -0.055189 | -0.20824 | -0.34528 | 0.028048 | -0.25905 | 0.19325 | 0.053435 | 0.025387 | -0.052306 | -0.058262 | 121.6769 | 121.3784 | 121.2413 | 2.6752 | -121.5078 | 121.3276 | 121.5343 | 121.5283 | 10.0414 | -121.5586
1001.2969 | 121.7377 | -0.41657 | 121.1426 | 1.4211e-13 | -0.021449 | -0.00095092 | 0.06353 | -0.0041322 | 0.057751 | -0.01755 | 0.00055974 | -5.5534e-05 | 0.064058 | 0.010951 | 0.060564 | -0.29655 | 2.2403 | -0.40214 | 121.2329 | 120.9527 | 120.7973 | -0.35611 | -0.24162 | 9.6157 | -0.38144 | 120.8927 | 121.0948 | 121.0935 | -0.41141 | 0.060457 | 0.09032 | 0.12002 | 0.014423 | -0.046034 | -0.18993 | -0.34528 | 0.00516 | -0.2499 | 0.17494 | 0.035126 | 0.029966 | -0.047728 | -0.049105 | 121.6495 | 121.3692 | 121.2139 | 2.6569 | -121.4987 | 121.3092 | 121.5114 | 121.51 | 10.0322 | -121.554
1003.0781 | 121.6782 | -0.4303 | 121.1563 | 1.4211e-13 | -0.021876 | -0.00095092 | 0.063316 | -0.0039186 | 0.058178 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.064058 | 0.010737 | 0.060778 | -0.29655 | 2.2449 | -0.39756 | 121.2421 | 120.9572 | 120.8065 | -0.35611 | -0.23705 | 9.6248 | -0.38144 | 120.8973 | 121.104 | 121.0981 | -0.40683 | 0.07419 | 0.085743 | 0.13375 | 0.032735 | -0.041455 | -0.19908 | -0.34985 | 0.023472 | -0.25905 | 0.19325 | 0.048859 | 0.025387 | -0.052304 | -0.05826 | 121.6724 | 121.3875 | 121.2368 | 2.6752 | -121.5124 | 121.3276 | 121.5343 | 121.5283 | 10.0551 | -121.5631
1004.7812 | 121.7102 | -0.4303 | 121.1426 | 1.4211e-13 | -0.021235 | -0.00095092 | 0.06353 | -0.0039186 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.010951 | 0.060564 | -0.29197 | 2.2541 | -0.39298 | 121.2466 | 120.9572 | 120.811 | -0.35153 | -0.23705 | 9.6294 | -0.38144 | 120.8973 | 121.104 | 121.0935 | -0.41141 | 0.078768 | 0.10406 | 0.13833 | 0.037313 | -0.041455 | -0.18535 | -0.33154 | 0.018893 | -0.24532 | 0.19325 | 0.048859 | 0.029966 | -0.038571 | -0.049105 | 121.6769 | 121.3875 | 121.2413 | 2.6844 | -121.4941 | 121.3276 | 121.5343 | 121.5238 | 10.0597 | -121.554
1006.5469 | 121.6599 | -0.46234 | 121.1609 | 1.4211e-13 | -0.021449 | -0.0013783 | 0.06353 | -0.0039186 | 0.057965 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064058 | 0.011164 | 0.060778 | -0.29655 | 2.2587 | -0.39756 | 121.2421 | 120.9618 | 120.8065 | -0.36069 | -0.24162 | 9.6294 | -0.38144 | 120.9018 | 121.0948 | 121.0935 | -0.40683 | 0.10165 | 0.081165 | 0.16579 | 0.064778 | -0.036876 | -0.19908 | -0.35443 | 0.055515 | -0.25905 | 0.22072 | 0.080902 | 0.025387 | -0.066039 | -0.067416 | 121.7044 | 121.4241 | 121.2688 | 2.721 | -121.5216 | 121.3642 | 121.5572 | 121.5558 | 10.0917 | -121.5677
1008.3125 | 121.6049 | -0.46692 | 121.1929 | 1.4211e-13 | -0.021235 | -0.00073712 | 0.06353 | -0.0034912 | 0.057965 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.010737 | 0.060351 | -0.30113 | 2.2724 | -0.40214 | 121.2421 | 120.9527 | 120.811 | -0.35153 | -0.24162 | 9.6111 | -0.38602 | 120.9018 | 121.104 | 121.0935 | -0.40225 | 0.11539 | 0.049122 | 0.16579 | 0.064777 | -0.050612 | -0.24028 | -0.3819 | 0.064672 | -0.29109 | 0.22529 | 0.080901 | 0.016229 | -0.088925 | -0.099459 | 121.709 | 121.4196 | 121.278 | 2.7393 | -121.5445 | 121.3688 | 121.5709 | 121.5604 | 10.078 | -121.5952
1010.0781 | 121.6553 | -0.45776 | 121.1746 | 1.4211e-13 | -0.021876 | -0.00095092 | 0.063744 | -0.003705 | 0.057965 | -0.01755 | 0.00013254 | 0.00037167 | 0.063844 | 0.011164 | 0.060564 | -0.29197 | 2.2678 | -0.39756 | 121.2466 | 120.971 | 120.8156 | -0.35153 | -0.23705 | 9.5515 | -0.3677 | 120.9018 | 121.0994 | 121.0981 | -0.40225 | 0.10623 | 0.072011 | 0.1658 | 0.060201 | -0.046033 | -0.20366 | -0.35901 | 0.055517 | -0.27278 | 0.22072 | 0.090061 | 0.034544 | -0.075193 | -0.076571 | 121.7044 | 121.4287 | 121.2734 | 2.7256 | -121.5262 | 121.3596 | 121.5572 | 121.5558 | 10.0093 | -121.5769
1011.7969 | 121.6782 | -0.41657 | 121.138 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.06353 | -0.0041322 | 0.057965 | -0.01755 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.010951 | 0.060137 | -0.29655 | 2.2861 | -0.40214 | 121.2466 | 120.9572 | 120.811 | -0.34237 | -0.22789 | 9.6111 | -0.3906 | 120.9018 | 121.1086 | 121.1026 | -0.39767 | 0.074193 | 0.10863 | 0.12002 | 0.014423 | -0.05977 | -0.18077 | -0.32697 | 0.018897 | -0.23616 | 0.18868 | 0.025968 | 0.007071 | -0.029414 | -0.03537 | 121.6632 | 121.3738 | 121.2276 | 2.7027 | -121.4804 | 121.3184 | 121.5252 | 121.5192 | 10.0276 | -121.5357
1013.4844 | 121.6827 | -0.41657 | 121.1792 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.064171 | -0.0039186 | 0.057751 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.010951 | 0.060564 | -0.29197 | 2.2816 | -0.39298 | 121.2466 | 120.9664 | 120.8156 | -0.34695 | -0.22789 | 9.6385 | -0.38144 | 120.9018 | 121.1086 | 121.1118 | -0.39767 | 0.069614 | 0.067434 | 0.1246 | 0.02358 | -0.046034 | -0.21281 | -0.36359 | 0.018897 | -0.27736 | 0.18868 | 0.035126 | 0.016229 | -0.070613 | -0.067412 | 121.6632 | 121.383 | 121.2322 | 2.6981 | -121.5262 | 121.3184 | 121.5252 | 121.5284 | 10.0551 | -121.5769
1015.25 | 121.6324 | -0.45319 | 121.1975 | 1.4211e-13 | -0.021449 | -0.0011645 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063631 | 0.011164 | 0.060564 | -0.28739 | 2.2907 | -0.39298 | 121.2604 | 120.971 | 120.8202 | -0.34695 | -0.22789 | 9.6431 | -0.37228 | 120.9064 | 121.1132 | 121.1072 | -0.39767 | 0.10623 | 0.062858 | 0.16579 | 0.060201 | -0.046034 | -0.22654 | -0.37732 | 0.055518 | -0.29109 | 0.2253 | 0.080904 | 0.025386 | -0.084346 | -0.090301 | 121.7136 | 121.4242 | 121.2734 | 2.7439 | -121.5445 | 121.3596 | 121.5663 | 121.5604 | 10.0963 | -121.5952
1016.9688 | 121.7422 | -0.42114 | 121.1517 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063631 | 0.011164 | 0.060564 | -0.28739 | 2.2953 | -0.39298 | 121.2512 | 120.9664 | 120.8294 | -0.35153 | -0.22331 | 9.6477 | -0.38144 | 120.911 | 121.1132 | 121.1026 | -0.39309 | 0.069613 | 0.099478 | 0.13375 | 0.028158 | -0.041455 | -0.18534 | -0.32238 | 0.028053 | -0.24074 | 0.19783 | 0.039704 | 0.011651 | -0.038569 | -0.049103 | 121.6724 | 121.3875 | 121.2505 | 2.7164 | -121.5033 | 121.3321 | 121.5343 | 121.5238 | 10.0688 | -121.5448
1018.6719 | 121.6873 | -0.41199 | 121.1746 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | 0.012972 | 0.00034614 | 0.00058547 | 0.064272 | 0.011164 | 0.060564 | -0.28281 | 2.2953 | -0.38841 | 121.2466 | 120.9755 | 120.811 | -0.34695 | -0.21873 | 9.6981 | -0.36312 | 120.9156 | 121.1223 | 121.1072 | -0.39309 | 0.065036 | 0.072011 | 0.12917 | 0.02358 | -0.041456 | -0.19908 | -0.36359 | 0.018897 | -0.25905 | 0.19326 | 0.048862 | 0.029965 | -0.0523 | -0.067413 | 121.6586 | 121.3875 | 121.223 | 2.7073 | -121.5216 | 121.3276 | 121.5343 | 121.5192 | 10.1101 | -121.5677
1020.4219 | 121.6415 | -0.4303 | 121.1975 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.063744 | -0.0041322 | 0.057965 | 0.0053411 | 0.00013254 | 0.00037167 | 0.063631 | 0.011164 | 0.060351 | -0.28281 | 2.2999 | -0.38841 | 121.2604 | 120.971 | 120.8202 | -0.34237 | -0.21873 | 9.6843 | -0.36312 | 120.911 | 121.1177 | 121.1164 | -0.38393 | 0.087926 | 0.062858 | 0.14749 | 0.041891 | -0.046035 | -0.22654 | -0.37732 | 0.046366 | -0.28651 | 0.21157 | 0.067173 | 0.020807 | -0.079767 | -0.081144 | 121.6907 | 121.4013 | 121.2505 | 2.7302 | -121.5399 | 121.3413 | 121.548 | 121.5467 | 10.1146 | -121.5814
1022.2188 | 121.6553 | -0.43488 | 121.2158 | 1.4211e-13 | -0.02209 | -0.00073712 | 0.06353 | -0.0039186 | 0.058178 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.011378 | 0.060778 | -0.27366 | 2.2999 | -0.38841 | 121.2604 | 120.9801 | 120.8294 | -0.33779 | -0.21415 | 9.6706 | -0.36312 | 120.9202 | 121.1223 | 121.1164 | -0.38851 | 0.097082 | 0.044548 | 0.16122 | 0.046468 | -0.050614 | -0.2357 | -0.38647 | 0.046364 | -0.29567 | 0.22072 | 0.07175 | 0.025386 | -0.093498 | -0.099454 | 121.6952 | 121.415 | 121.2642 | 2.7347 | -121.5536 | 121.355 | 121.5572 | 121.5512 | 10.1055 | -121.6043
1023.9219 | 121.7422 | -0.38452 | 121.1655 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.063744 | -0.0041322 | 0.057537 | 0.0053411 | 0.00077334 | 0.00015807 | 0.063844 | 0.011164 | 0.060564 | -0.27366 | 2.3044 | -0.37467 | 121.2649 | 120.9801 | 120.8294 | -0.33321 | -0.21415 | 9.6752 | -0.35397 | 120.9247 | 121.1269 | 121.1209 | -0.37935 | 0.051307 | 0.09948 | 0.11086 | 0.009849 | -0.041458 | -0.18534 | -0.33612 | 0.005168 | -0.24074 | 0.17037 | 0.030554 | 0.025386 | -0.038566 | -0.044522 | 121.6495 | 121.3646 | 121.2139 | 2.689 | -121.4987 | 121.3093 | 121.5114 | 121.5055 | 10.0597 | -121.5448
1025.625 | 121.7239 | -0.38452 | 121.1884 | 1.4211e-13 | -0.021662 | -0.0011645 | 0.063744 | -0.003705 | 0.057965 | -0.0099194 | 0.00055974 | 0.00037167 | 0.064058 | 0.010951 | 0.060351 | -0.26908 | 2.3044 | -0.37925 | 121.2649 | 120.9847 | 120.8385 | -0.33321 | -0.21415 | 9.7484 | -0.35397 | 120.9247 | 121.1269 | 121.1209 | -0.37935 | 0.051307 | 0.076592 | 0.11544 | 0.005271 | -0.046036 | -0.20365 | -0.34985 | 0.005168 | -0.26362 | 0.17037 | 0.030554 | 0.025386 | -0.061454 | -0.06741 | 121.6495 | 121.3692 | 121.223 | 2.689 | -121.5216 | 121.3093 | 121.5114 | 121.5055 | 10.133 | -121.5677
1027.3906 | 121.6965 | -0.41657 | 121.1975 | 1.4211e-13 | -0.021876 | -0.0011645 | 0.06353 | -0.0039186 | 0.057751 | -0.0022889 | 0.00013254 | 0.00058547 | 0.063631 | 0.010951 | 0.060778 | -0.25992 | 2.2999 | -0.37467 | 121.2833 | 120.9939 | 120.8431 | -0.32864 | -0.20957 | 9.7439 | -0.34939 | 120.9339 | 121.1315 | 121.1347 | -0.38393 | 0.08793 | 0.08575 | 0.15664 | 0.041893 | -0.046037 | -0.20365 | -0.35442 | 0.032633 | -0.26362 | 0.20699 | 0.067176 | 0.034543 | -0.066031 | -0.06283 | 121.6998 | 121.4104 | 121.2597 | 2.7164 | -121.5261 | 121.3505 | 121.548 | 121.5512 | 10.1604 | -121.5814
1029.1719 | 121.6553 | -0.42572 | 121.225 | 1.4211e-13 | -0.021876 | -0.00073712 | 0.063744 | -0.0039186 | 0.057537 | 0.0053411 | 0.00055974 | 0.00037167 | 0.064058 | 0.010737 | 0.060564 | -0.2645 | 2.3044 | -0.37467 | 121.2649 | 120.9984 | 120.8477 | -0.32406 | -0.20499 | 9.7255 | -0.34023 | 120.9339 | 121.1361 | 121.1393 | -0.3702 | 0.10166 | 0.03997 | 0.16122 | 0.051048 | -0.050616 | -0.22654 | -0.37731 | 0.055524 | -0.29109 | 0.22073 | 0.085489 | 0.029965 | -0.088918 | -0.085717 | 121.6907 | 121.4242 | 121.2734 | 2.7302 | -121.549 | 121.3596 | 121.5618 | 121.565 | 10.1513 | -121.5952
1030.8906 | 121.6599 | -0.4303 | 121.225 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.063103 | -0.0039186 | 0.057751 | -0.0099194 | 0.00077334 | 0.00015807 | 0.064058 | 0.010951 | 0.060137 | -0.25992 | 2.3228 | -0.36094 | 121.2833 | 120.9939 | 120.8568 | -0.32406 | -0.20042 | 9.7942 | -0.34481 | 120.9385 | 121.1406 | 121.1347 | -0.36562 | 0.10624 | 0.058284 | 0.17038 | 0.069361 | -0.036881 | -0.23112 | -0.36816 | 0.064681 | -0.28651 | 0.22988 | 0.085488 | 0.020807 | -0.08434 | -0.090296 | 121.7136 | 121.4242 | 121.2871 | 2.7531 | -121.549 | 121.3688 | 121.5709 | 121.565 | 10.2245 | -121.5906
1032.6094 | 121.7194 | -0.38452 | 121.17 | 1.4211e-13 | -0.021876 | -0.0011645 | 0.06353 | -0.0041322 | 0.057965 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063844 | 0.011592 | 0.060778 | -0.25076 | 2.3273 | -0.35178 | 121.2787 | 121.003 | 120.8614 | -0.3149 | -0.20042 | 9.7988 | -0.33565 | 120.9522 | 121.1544 | 121.1484 | -0.36562 | 0.069623 | 0.10864 | 0.13376 | 0.032741 | -0.036882 | -0.16703 | -0.30864 | 0.018904 | -0.21784 | 0.1841 | 0.048869 | 0.029965 | -0.015672 | -0.021628 | 121.6632 | 121.3875 | 121.2459 | 2.7119 | -121.4849 | 121.3367 | 121.5389 | 121.5329 | 10.1833 | -121.5357
1034.3594 | 121.7194 | -0.37994 | 121.1655 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.06353 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.011164 | 0.060351 | -0.24618 | 2.3411 | -0.3472 | 121.2924 | 121.0122 | 120.8614 | -0.30574 | -0.18668 | 9.7851 | -0.33565 | 120.9522 | 121.1452 | 121.1484 | -0.35188 | 0.074204 | 0.12695 | 0.13376 | 0.032742 | -0.041462 | -0.15329 | -0.30407 | 0.028064 | -0.21326 | 0.19326 | 0.044292 | 0.016228 | -0.020251 | -0.01705 | 121.6724 | 121.3921 | 121.2413 | 2.721 | -121.4712 | 121.3321 | 121.5252 | 121.5284 | 10.165 | -121.5173
1036.0625 | 121.6415 | -0.41657 | 121.2067 | 1.4211e-13 | -0.021876 | -0.0011645 | 0.06353 | -0.0039186 | 0.057965 | -0.0022889 | 0.00013254 | 0.00015807 | 0.064058 | 0.011378 | 0.060564 | -0.23703 | 2.3502 | -0.3472 | 121.297 | 121.0168 | 120.866 | -0.3149 | -0.18668 | 9.7759 | -0.32649 | 120.9522 | 121.159 | 121.1484 | -0.35188 | 0.10167 | 0.09033 | 0.17954 | 0.069363 | -0.032304 | -0.18991 | -0.34069 | 0.064685 | -0.25446 | 0.22989 | 0.09007 | 0.025385 | -0.047714 | -0.058249 | 121.7136 | 121.4333 | 121.2825 | 2.7668 | -121.5216 | 121.3688 | 121.5755 | 121.565 | 10.1925 | -121.5585
1037.8281 | 121.6187 | -0.39825 | 121.2112 | 1.4211e-13 | -0.021876 | -0.00073712 | 0.063316 | -0.0039186 | 0.057965 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.011378 | 0.060351 | -0.24161 | 2.3502 | -0.3472 | 121.3016 | 121.0213 | 120.8706 | -0.31032 | -0.17752 | 9.8492 | -0.32649 | 120.9522 | 121.1635 | 121.1576 | -0.35188 | 0.087935 | 0.09033 | 0.15665 | 0.051052 | -0.036883 | -0.18991 | -0.34069 | 0.046374 | -0.25904 | 0.22073 | 0.071759 | 0.025385 | -0.047714 | -0.05367 | 121.6998 | 121.4196 | 121.2688 | 2.7485 | -121.5216 | 121.3505 | 121.5618 | 121.5558 | 10.2474 | -121.5631
1039.5156 | 121.582 | -0.41199 | 121.257 | 1.4211e-13 | -0.021876 | -0.0013783 | 0.063744 | -0.0041322 | 0.057965 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.011378 | 0.060351 | -0.23703 | 2.3365 | -0.34262 | 121.3062 | 121.0213 | 120.8843 | -0.30116 | -0.17752 | 9.8263 | -0.32192 | 120.9614 | 121.159 | 121.1622 | -0.35646 | 0.11083 | 0.049133 | 0.17496 | 0.069363 | -0.041463 | -0.23568 | -0.37273 | 0.055528 | -0.29566 | 0.23446 | 0.090071 | 0.034543 | -0.098068 | -0.094867 | 121.7181 | 121.4333 | 121.2963 | 2.7485 | -121.5582 | 121.3733 | 121.5709 | 121.5741 | 10.2383 | -121.6135
1041.2656 | 121.6827 | -0.35706 | 121.2204 | 1.4211e-13 | -0.022517 | -0.00095092 | 0.063103 | -0.0039186 | 0.057537 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.011378 | 0.060137 | -0.22787 | 2.3365 | -0.33805 | 121.3062 | 121.0305 | 120.8797 | -0.29658 | -0.17294 | 9.8125 | -0.32192 | 120.9614 | 121.1681 | 121.1667 | -0.34272 | 0.060474 | 0.085754 | 0.12918 | 0.01901 | -0.041464 | -0.18991 | -0.34068 | 0.014333 | -0.25904 | 0.18411 | 0.03514 | 0.020807 | -0.05229 | -0.053668 | 121.6632 | 121.3875 | 121.2368 | 2.6936 | -121.517 | 121.3184 | 121.5252 | 121.5238 | 10.1696 | -121.5631
1042.9844 | 121.6141 | -0.3891 | 121.2616 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.06353 | -0.0039186 | 0.058178 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.063631 | 0.011378 | 0.060351 | -0.22329 | 2.3365 | -0.33347 | 121.3153 | 121.0351 | 120.8843 | -0.29658 | -0.17294 | 9.84 | -0.32192 | 120.9659 | 121.1727 | 121.1713 | -0.33357 | 0.092517 | 0.053712 | 0.16581 | 0.055632 | -0.036885 | -0.22653 | -0.3773 | 0.055534 | -0.29566 | 0.21616 | 0.067183 | 0.011649 | -0.088911 | -0.090288 | 121.7044 | 121.4242 | 121.2734 | 2.7256 | -121.5582 | 121.355 | 121.5618 | 121.5604 | 10.2291 | -121.5952
1044.7344 | 121.7194 | -0.34332 | 121.2296 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.063316 | -0.003705 | 0.058178 | -0.0099194 | 0.00034614 | 0.00058547 | 0.063631 | 0.011164 | 0.060137 | -0.22329 | 2.3365 | -0.32889 | 121.3245 | 121.0351 | 120.8889 | -0.292 | -0.16836 | 9.8537 | -0.31734 | 120.9705 | 121.1773 | 121.1759 | -0.32441 | 0.051319 | 0.094912 | 0.12003 | 0.014434 | -0.036885 | -0.19448 | -0.34068 | 0.018916 | -0.25904 | 0.17496 | 0.025985 | 0.007069 | -0.052288 | -0.053665 | 121.6678 | 121.3784 | 121.2322 | 2.6798 | -121.5216 | 121.3138 | 121.5206 | 121.5192 | 10.1971 | -121.554
1046.4844 | 121.7331 | -0.33417 | 121.2341 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.06353 | -0.0041322 | 0.057751 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.064058 | 0.011805 | 0.060564 | -0.21871 | 2.3228 | -0.32431 | 121.3153 | 121.0305 | 120.898 | -0.28742 | -0.15921 | 9.8904 | -0.3036 | 120.9797 | 121.1818 | 121.1713 | -0.32899 | 0.046742 | 0.081178 | 0.11545 | 0.009856 | -0.036886 | -0.20364 | -0.3361 | 0.005181 | -0.25446 | 0.17496 | 0.030566 | 0.025385 | -0.052287 | -0.062822 | 121.6495 | 121.3647 | 121.2322 | 2.6569 | -121.5216 | 121.3138 | 121.516 | 121.5055 | 10.2245 | -121.5631
1048.25 | 121.6827 | -0.35248 | 121.2158 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.06353 | -0.0039186 | 0.058178 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.011164 | 0.060351 | -0.21414 | 2.3319 | -0.32889 | 121.3245 | 121.0396 | 120.8889 | -0.292 | -0.15921 | 9.8858 | -0.29902 | 120.9705 | 121.1818 | 121.1805 | -0.32899 | 0.060474 | 0.10865 | 0.13834 | 0.023589 | -0.036885 | -0.17617 | -0.32695 | 0.023492 | -0.2453 | 0.19327 | 0.053455 | 0.029963 | -0.033976 | -0.035354 | 121.6769 | 121.3921 | 121.2414 | 2.6844 | -121.5078 | 121.323 | 121.5343 | 121.5329 | 10.2383 | -121.5448
1050.0156 | 121.637 | -0.3891 | 121.2524 | 1.4211e-13 | -0.021876 | -0.0011645 | 0.06353 | -0.0039186 | 0.057965 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.011378 | 0.060564 | -0.21871 | 2.3457 | -0.32889 | 121.3245 | 121.0488 | 120.9026 | -0.28285 | -0.15921 | 9.895 | -0.30818 | 120.9797 | 121.1818 | 121.1805 | -0.32441 | 0.10625 | 0.072024 | 0.17038 | 0.06021 | -0.046043 | -0.20363 | -0.34983 | 0.064692 | -0.27277 | 0.22989 | 0.080919 | 0.016227 | -0.070597 | -0.071975 | 121.7136 | 121.4379 | 121.2917 | 2.7348 | -121.5353 | 121.3688 | 121.5709 | 121.5696 | 10.2841 | -121.5768
1051.7656 | 121.7422 | -0.34332 | 121.2341 | 1.4211e-13 | -0.022303 | -0.0013783 | 0.063744 | -0.0041322 | 0.057751 | 0.012972 | 0.00034614 | 0.00037167 | 0.063631 | 0.011805 | 0.059923 | -0.21414 | 2.3548 | -0.32889 | 121.329 | 121.0442 | 120.9026 | -0.292 | -0.15463 | 9.8812 | -0.3036 | 120.9797 | 121.191 | 121.185 | -0.31983 | 0.051319 | 0.094913 | 0.12919 | 0.014434 | -0.036885 | -0.1899 | -0.33152 | 0.023494 | -0.25446 | 0.18869 | 0.039722 | 0.016228 | -0.04313 | -0.049086 | 121.6724 | 121.3876 | 121.2459 | 2.6981 | -121.5261 | 121.323 | 121.5343 | 121.5284 | 10.2245 | -121.554
1053.4531 | 121.6736 | -0.36163 | 121.2387 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.063316 | -0.0039186 | 0.057537 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.011805 | 0.060351 | -0.21871 | 2.3502 | -0.32431 | 121.329 | 121.0442 | 120.8935 | -0.28285 | -0.15463 | 9.8995 | -0.3036 | 120.9797 | 121.1956 | 121.1896 | -0.32441 | 0.078787 | 0.090336 | 0.14292 | 0.037322 | -0.041465 | -0.19448 | -0.34526 | 0.037226 | -0.25903 | 0.207 | 0.058032 | 0.020806 | -0.043129 | -0.049085 | 121.6907 | 121.4059 | 121.2551 | 2.7119 | -121.5216 | 121.3413 | 121.5572 | 121.5513 | 10.2612 | -121.5631
1055.2344 | 121.6507 | -0.37079 | 121.2662 | 1.4211e-13 | -0.021876 | -0.0011645 | 0.06353 | -0.0039186 | 0.057965 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.011378 | 0.060137 | -0.20956 | 2.3685 | -0.31058 | 121.3474 | 121.0488 | 120.9072 | -0.27369 | -0.14547 | 9.9041 | -0.30818 | 120.9888 | 121.2002 | 121.1896 | -0.31983 | 0.097101 | 0.081183 | 0.16123 | 0.060213 | -0.036888 | -0.21737 | -0.35899 | 0.05096 | -0.27734 | 0.22532 | 0.062609 | 0.011649 | -0.066016 | -0.076551 | 121.7181 | 121.4196 | 121.278 | 2.7393 | -121.5399 | 121.3596 | 121.5709 | 121.5604 | 10.2749 | -121.586
1057.0156 | 121.6095 | -0.39368 | 121.2753 | 1.4211e-13 | -0.02209 | -0.0011645 | 0.06353 | -0.003705 | 0.057965 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063844 | 0.011592 | 0.060351 | -0.2004 | 2.3731 | -0.31515 | 121.3382 | 121.0534 | 120.9026 | -0.27369 | -0.15463 | 9.9178 | -0.29902 | 120.9934 | 121.2047 | 121.1942 | -0.32441 | 0.11999 | 0.062871 | 0.19328 | 0.078523 | -0.041466 | -0.22194 | -0.37272 | 0.06927 | -0.28192 | 0.23905 | 0.094654 | 0.025384 | -0.070593 | -0.081128 | 121.7319 | 121.4471 | 121.2963 | 2.7668 | -121.549 | 121.3871 | 121.5984 | 121.5879 | 10.3115 | -121.5997
1058.7969 | 121.6553 | -0.37079 | 121.2799 | 1.4211e-13 | -0.022517 | -0.00073712 | 0.063744 | -0.0041322 | 0.057965 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.010951 | 0.060351 | -0.2004 | 2.3777 | -0.306 | 121.3382 | 121.058 | 120.9209 | -0.27369 | -0.14547 | 9.9178 | -0.28986 | 120.9934 | 121.2002 | 121.1988 | -0.31525 | 0.097101 | 0.058294 | 0.17039 | 0.064791 | -0.03231 | -0.22194 | -0.35898 | 0.055539 | -0.2865 | 0.22532 | 0.080924 | 0.025385 | -0.079749 | -0.081126 | 121.709 | 121.4288 | 121.2917 | 2.7485 | -121.5536 | 121.3642 | 121.5709 | 121.5696 | 10.2886 | -121.5952
1060.4844 | 121.6095 | -0.38452 | 121.2891 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.06353 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063631 | 0.011164 | 0.060137 | -0.20498 | 2.3823 | -0.31058 | 121.3382 | 121.058 | 120.9163 | -0.26911 | -0.14547 | 9.9545 | -0.29444 | 120.9934 | 121.2047 | 121.1942 | -0.31983 | 0.11541 | 0.049139 | 0.17954 | 0.073945 | -0.041467 | -0.2311 | -0.37272 | 0.064692 | -0.29565 | 0.23905 | 0.090077 | 0.025385 | -0.084325 | -0.09486 | 121.7227 | 121.4425 | 121.3009 | 2.7668 | -121.5582 | 121.3779 | 121.5893 | 121.5787 | 10.339 | -121.6089
1062.2812 | 121.7697 | -0.34332 | 121.2433 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.063744 | -0.004346 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063844 | 0.011378 | 0.060137 | -0.21414 | 2.3777 | -0.31515 | 121.329 | 121.0534 | 120.9026 | -0.27827 | -0.15005 | 9.9453 | -0.28986 | 120.998 | 121.2002 | 121.1988 | -0.31525 | 0.065056 | 0.085758 | 0.12919 | 0.028169 | -0.036887 | -0.1899 | -0.34068 | 0.028073 | -0.2453 | 0.19327 | 0.053458 | 0.025385 | -0.043128 | -0.044505 | 121.6724 | 121.3967 | 121.2459 | 2.721 | -121.5216 | 121.3413 | 121.5435 | 121.5421 | 10.2886 | -121.5585
1064.0625 | 121.6919 | -0.33875 | 121.2616 | 1.4211e-13 | -0.022303 | -0.00095092 | 0.063744 | -0.0039186 | 0.057324 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063844 | 0.011805 | 0.060351 | -0.20498 | 2.3914 | -0.30142 | 121.3382 | 121.058 | 120.9163 | -0.27369 | -0.14547 | 9.9728 | -0.28986 | 121.0026 | 121.2093 | 121.1942 | -0.31525 | 0.065057 | 0.076604 | 0.13377 | 0.037326 | -0.027731 | -0.20363 | -0.34525 | 0.023495 | -0.25903 | 0.19327 | 0.04888 | 0.025385 | -0.052282 | -0.067395 | 121.6769 | 121.3967 | 121.2551 | 2.7302 | -121.5353 | 121.3413 | 121.5481 | 121.5329 | 10.3115 | -121.5768
1065.8438 | 121.6095 | -0.39368 | 121.3028 | 1.4211e-13 | -0.02209 | -0.00095092 | 0.063957 | -0.0041322 | 0.057324 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063631 | 0.011592 | 0.060137 | -0.20498 | 2.3869 | -0.31058 | 121.3474 | 121.058 | 120.9209 | -0.26911 | -0.14089 | 9.9407 | -0.28529 | 121.0071 | 121.2002 | 121.1988 | -0.31525 | 0.12457 | 0.044562 | 0.1887 | 0.083101 | -0.041467 | -0.24483 | -0.38187 | 0.078427 | -0.29565 | 0.25279 | 0.10839 | 0.029963 | -0.10264 | -0.10401 | 121.741 | 121.4516 | 121.3146 | 2.7805 | -121.5719 | 121.4008 | 121.5938 | 121.5925 | 10.3344 | -121.618
1067.5312 | 121.6141 | -0.37994 | 121.2936 | 1.4211e-13 | -0.022517 | -0.0013783 | 0.063744 | -0.0041322 | 0.057751 | 0.0053411 | 0.00077334 | 0.00037167 | 0.063844 | 0.011592 | 0.060351 | -0.2004 | 2.3823 | -0.31058 | 121.3336 | 121.0625 | 120.9163 | -0.26911 | -0.13631 | 9.9819 | -0.28529 | 121.0117 | 121.2093 | 121.1988 | -0.30609 | 0.11084 | 0.039982 | 0.17954 | 0.069368 | -0.041467 | -0.23109 | -0.3773 | 0.073852 | -0.28192 | 0.24363 | 0.094657 | 0.020805 | -0.084325 | -0.094859 | 121.7136 | 121.4425 | 121.2963 | 2.7622 | -121.5627 | 121.3917 | 121.5893 | 121.5787 | 10.3619 | -121.5997
1069.2969 | 121.7468 | -0.3067 | 121.2479 | 1.4211e-13 | -0.022517 | -0.0013783 | 0.063744 | -0.0039186 | 0.057751 | -0.0099194 | 0.00055974 | 0.00037167 | 0.063844 | 0.011378 | 0.060564 | -0.2004 | 2.3914 | -0.30142 | 121.3428 | 121.0671 | 120.9255 | -0.26453 | -0.13631 | 9.9819 | -0.28071 | 121.0071 | 121.2139 | 121.1988 | -0.31525 | 0.042172 | 0.094915 | 0.1063 | 0.005283 | -0.036889 | -0.18074 | -0.32236 | -0.008548 | -0.24072 | 0.17039 | 0.025994 | 0.034542 | -0.03397 | -0.049083 | 121.6495 | 121.3738 | 121.2322 | 2.6981 | -121.5124 | 121.3138 | 121.5206 | 121.5055 | 10.2886 | -121.5631
1071.0781 | 121.7606 | -0.33417 | 121.257 | 1.4211e-13 | -0.022731 | -0.00073712 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.011592 | 0.060351 | -0.19582 | 2.3914 | -0.29684 | 121.3519 | 121.0717 | 120.9347 | -0.25995 | -0.14547 | 9.9636 | -0.28529 | 121.0117 | 121.2139 | 121.2125 | -0.30609 | 0.074216 | 0.094917 | 0.13834 | 0.037326 | -0.03689 | -0.18532 | -0.32236 | 0.028075 | -0.2453 | 0.1887 | 0.04888 | 0.020805 | -0.043125 | -0.044502 | 121.6861 | 121.4059 | 121.2688 | 2.7256 | -121.517 | 121.3459 | 121.5481 | 121.5467 | 10.2978 | -121.5631
1072.7969 | 121.7514 | -0.31586 | 121.2524 | 1.4211e-13 | -0.022517 | -0.00030992 | 0.063744 | -0.004346 | 0.057537 | -0.0099194 | 0.00034614 | 0.00037167 | 0.064058 | 0.011378 | 0.060137 | -0.19582 | 2.3914 | -0.29684 | 121.3474 | 121.0625 | 120.9255 | -0.26453 | -0.13173 | 9.9957 | -0.27613 | 121.0026 | 121.2185 | 121.2079 | -0.30609 | 0.051327 | 0.094916 | 0.12003 | 0.019016 | -0.032311 | -0.1899 | -0.32694 | 0.009765 | -0.24988 | 0.18412 | 0.039728 | 0.029963 | -0.033969 | -0.044503 | 121.6632 | 121.3784 | 121.2414 | 2.7073 | -121.517 | 121.3184 | 121.5343 | 121.5238 | 10.3115 | -121.5585
1074.5 | 121.6461 | -0.35706 | 121.2662 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.06353 | -0.004346 | 0.058178 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063417 | 0.011592 | 0.060564 | -0.19124 | 2.4143 | -0.29226 | 121.3519 | 121.0763 | 120.9347 | -0.25995 | -0.13631 | 10.014 | -0.27613 | 121.0163 | 121.2185 | 121.2034 | -0.30151 | 0.097105 | 0.085762 | 0.16581 | 0.064793 | -0.032312 | -0.18989 | -0.33152 | 0.055543 | -0.24987 | 0.22074 | 0.080927 | 0.025384 | -0.047702 | -0.062815 | 121.709 | 121.4333 | 121.2917 | 2.7714 | -121.5261 | 121.3734 | 121.5755 | 121.5604 | 10.3711 | -121.5677
1076.2812 | 121.7148 | -0.33417 | 121.2616 | 1.4211e-13 | -0.022517 | -0.00095092 | 0.06353 | -0.0039186 | 0.057965 | -0.0022889 | 0.00034614 | 0.00037167 | 0.064058 | 0.012019 | 0.060137 | -0.19124 | 2.4143 | -0.29684 | 121.3565 | 121.0763 | 120.9301 | -0.26453 | -0.12716 | 9.9911 | -0.27613 | 121.0209 | 121.2276 | 121.2171 | -0.29693 | 0.069637 | 0.094917 | 0.14292 | 0.037326 | -0.032311 | -0.18531 | -0.33152 | 0.037233 | -0.24072 | 0.20701 | 0.058038 | 0.020805 | -0.033967 | -0.044502 | 121.6907 | 121.4104 | 121.2642 | 2.7485 | -121.5261 | 121.355 | 121.5618 | 121.5513 | 10.3253 | -121.5585
1078.0469 | 121.7285 | -0.31128 | 121.2479 | 1.4211e-13 | -0.022731 | -0.00073712 | 0.063744 | -0.0039186 | 0.057751 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.011805 | 0.060564 | -0.18667 | 2.4372 | -0.29684 | 121.3611 | 121.0763 | 120.9392 | -0.25995 | -0.13631 | 10.0369 | -0.27155 | 121.0209 | 121.2231 | 121.2125 | -0.29693 | 0.051328 | 0.11323 | 0.12461 | 0.014438 | -0.03689 | -0.17158 | -0.30863 | 0.014345 | -0.22698 | 0.17496 | 0.039729 | 0.025384 | -0.024813 | -0.035347 | 121.6724 | 121.3876 | 121.2505 | 2.7485 | -121.5078 | 121.3322 | 121.5343 | 121.5238 | 10.3482 | -121.5448
1079.8281 | 121.6919 | -0.32501 | 121.2708 | 1.4211e-13 | -0.022517 | -0.00095092 | 0.063744 | -0.004346 | 0.057537 | -0.01755 | 0.00077334 | 0.00015807 | 0.063844 | 0.011805 | 0.060351 | -0.18667 | 2.4235 | -0.29684 | 121.3565 | 121.0809 | 120.9392 | -0.25079 | -0.12258 | 10.0735 | -0.28071 | 121.0255 | 121.2322 | 121.2217 | -0.30151 | 0.074219 | 0.085762 | 0.13835 | 0.028171 | -0.046048 | -0.18989 | -0.33152 | 0.023499 | -0.24529 | 0.20243 | 0.044304 | 0.020805 | -0.038544 | -0.049078 | 121.6815 | 121.4059 | 121.2642 | 2.7485 | -121.5215 | 121.3505 | 121.5572 | 121.5467 | 10.3985 | -121.5723
1081.5156 | 121.7239 | -0.32044 | 121.2616 | 1.4211e-13 | -0.022517 | -0.00095092 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.011805 | 0.060564 | -0.18667 | 2.4189 | -0.28768 | 121.3657 | 121.0717 | 120.9438 | -0.25537 | -0.12258 | 10.0689 | -0.26697 | 121.0209 | 121.2231 | 121.2263 | -0.30151 | 0.065063 | 0.10407 | 0.13377 | 0.032751 | -0.032312 | -0.18989 | -0.31778 | 0.018922 | -0.24072 | 0.19786 | 0.053463 | 0.034541 | -0.038546 | -0.035345 | 121.6861 | 121.3921 | 121.2643 | 2.7393 | -121.517 | 121.3413 | 121.5435 | 121.5467 | 10.3894 | -121.5631
1083.2969 | 121.6324 | -0.36621 | 121.2936 | 1.4211e-13 | -0.022517 | -0.00095092 | 0.063957 | -0.0041322 | 0.057965 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.011592 | 0.060351 | -0.18667 | 2.4326 | -0.29226 | 121.3611 | 121.0809 | 120.9392 | -0.25537 | -0.13173 | 10.0323 | -0.27155 | 121.0209 | 121.2276 | 121.2217 | -0.29693 | 0.11084 | 0.067452 | 0.17955 | 0.073948 | -0.036891 | -0.21278 | -0.3544 | 0.069277 | -0.27276 | 0.23448 | 0.094661 | 0.025384 | -0.06601 | -0.071966 | 121.7273 | 121.4471 | 121.3054 | 2.7989 | -121.549 | 121.3871 | 121.5938 | 121.5879 | 10.3985 | -121.5906
1085.0781 | 121.6965 | -0.31586 | 121.2799 | 1.4211e-13 | -0.022944 | -0.00073712 | 0.063744 | -0.004346 | 0.057751 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.011592 | 0.060137 | -0.19124 | 2.4326 | -0.29226 | 121.3702 | 121.0854 | 120.9392 | -0.24621 | -0.12258 | 10.0369 | -0.27155 | 121.0209 | 121.2276 | 121.2308 | -0.29236 | 0.069643 | 0.090342 | 0.12461 | 0.023594 | -0.046049 | -0.19447 | -0.34067 | 0.023501 | -0.25903 | 0.19328 | 0.044307 | 0.020806 | -0.052277 | -0.049076 | 121.6861 | 121.4013 | 121.2551 | 2.7485 | -121.5261 | 121.3367 | 121.5435 | 121.5467 | 10.3527 | -121.5723
1086.8594 | 121.7285 | -0.31128 | 121.2799 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.063744 | -0.0041322 | 0.057537 | -0.0022889 | 0.00034614 | 0.00058547 | 0.063844 | 0.011378 | 0.060137 | -0.18667 | 2.4326 | -0.28768 | 121.3657 | 121.0809 | 120.9392 | -0.25079 | -0.12258 | 10.0552 | -0.26239 | 121.0209 | 121.2414 | 121.2171 | -0.29693 | 0.060486 | 0.085764 | 0.12461 | 0.023595 | -0.036891 | -0.19905 | -0.34067 | 0.014345 | -0.25903 | 0.1887 | 0.048886 | 0.034541 | -0.038542 | -0.062812 | 121.677 | 121.3921 | 121.2505 | 2.7439 | -121.5307 | 121.3322 | 121.5526 | 121.5284 | 10.3665 | -121.5768
1088.5625 | 121.7285 | -0.30212 | 121.2799 | 1.4211e-13 | -0.022731 | -0.0013783 | 0.063957 | -0.0041322 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063631 | 0.011592 | 0.060137 | -0.17751 | 2.4235 | -0.28311 | 121.3611 | 121.0854 | 120.9484 | -0.25079 | -0.12258 | 10.0552 | -0.26697 | 121.0346 | 121.2368 | 121.2263 | -0.28778 | 0.051331 | 0.081185 | 0.12461 | 0.019018 | -0.032313 | -0.19447 | -0.33151 | 0.014347 | -0.24529 | 0.17955 | 0.035152 | 0.020805 | -0.04312 | -0.053655 | 121.6632 | 121.3876 | 121.2505 | 2.7256 | -121.5307 | 121.3367 | 121.5389 | 121.5284 | 10.3573 | -121.5677
1090.3438 | 121.7148 | -0.31128 | 121.2845 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.06353 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.011805 | 0.060564 | -0.18209 | 2.4372 | -0.28768 | 121.3702 | 121.09 | 120.9484 | -0.24621 | -0.118 | 10.0827 | -0.25781 | 121.0255 | 121.2414 | 121.2308 | -0.28778 | 0.065065 | 0.085764 | 0.12919 | 0.023595 | -0.04147 | -0.19447 | -0.33609 | 0.023502 | -0.25903 | 0.19328 | 0.053465 | 0.029963 | -0.04312 | -0.053654 | 121.6815 | 121.4013 | 121.2597 | 2.7485 | -121.5307 | 121.3367 | 121.5526 | 121.5421 | 10.394 | -121.5723
1092.0469 | 121.7377 | -0.32044 | 121.2708 | 1.4211e-13 | -0.022944 | -0.00095092 | 0.063316 | -0.0041322 | 0.057324 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063631 | 0.012019 | 0.060351 | -0.17751 | 2.4464 | -0.28768 | 121.3611 | 121.09 | 120.953 | -0.25079 | -0.12258 | 10.0689 | -0.26697 | 121.03 | 121.2368 | 121.2308 | -0.28778 | 0.069642 | 0.09034 | 0.14293 | 0.032751 | -0.036891 | -0.18073 | -0.31778 | 0.032658 | -0.24072 | 0.19786 | 0.053463 | 0.020805 | -0.033965 | -0.039921 | 121.6815 | 121.4105 | 121.2734 | 2.7668 | -121.5215 | 121.3505 | 121.5572 | 121.5513 | 10.3894 | -121.5585
1093.8281 | 121.7331 | -0.28381 | 121.2524 | 1.4211e-13 | -0.022944 | -0.00095092 | 0.06353 | -0.0041322 | 0.057537 | -0.0099194 | 0.00034614 | 0.00037167 | 0.064058 | 0.011592 | 0.060137 | -0.17751 | 2.4555 | -0.28311 | 121.3702 | 121.0854 | 120.953 | -0.24163 | -0.11342 | 10.0827 | -0.26239 | 121.03 | 121.2368 | 121.2217 | -0.27862 | 0.042178 | 0.11781 | 0.1063 | 0.000707 | -0.041471 | -0.167 | -0.29947 | 0.005194 | -0.2224 | 0.17039 | 0.02142 | 0.016226 | -0.015654 | -0.030767 | 121.6541 | 121.3693 | 121.2368 | 2.7393 | -121.4941 | 121.3138 | 121.5206 | 121.5055 | 10.3665 | -121.5311
1095.5938 | 121.6049 | -0.34332 | 121.3303 | 1.4211e-13 | -0.022944 | -0.0013783 | 0.06353 | -0.0039186 | 0.057537 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063844 | 0.011592 | 0.060351 | -0.16835 | 2.451 | -0.28311 | 121.3702 | 121.0992 | 120.9667 | -0.24163 | -0.12258 | 10.046 | -0.26239 | 121.0346 | 121.2459 | 121.24 | -0.2832 | 0.10169 | 0.039988 | 0.17497 | 0.060217 | -0.041471 | -0.23108 | -0.36355 | 0.060125 | -0.29565 | 0.22074 | 0.08093 | 0.020805 | -0.084317 | -0.090273 | 121.7136 | 121.4425 | 121.31 | 2.7943 | -121.5719 | 121.3779 | 121.5893 | 121.5833 | 10.3894 | -121.6135
1097.3125 | 121.7377 | -0.29297 | 121.2799 | 1.4211e-13 | -0.022731 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.011592 | 0.060137 | -0.17293 | 2.451 | -0.27395 | 121.3794 | 121.0992 | 120.9576 | -0.24163 | -0.11342 | 10.0964 | -0.25324 | 121.03 | 121.2459 | 121.2308 | -0.27862 | 0.051334 | 0.099499 | 0.12004 | 0.019019 | -0.032315 | -0.18073 | -0.32236 | 0.01435 | -0.24987 | 0.17955 | 0.039733 | 0.025383 | -0.033963 | -0.049076 | 121.6724 | 121.3921 | 121.2505 | 2.7439 | -121.5215 | 121.323 | 121.5389 | 121.5238 | 10.3894 | -121.5585
1099.0938 | 121.6003 | -0.33875 | 121.3074 | 1.4211e-13 | -0.022731 | -0.00095092 | 0.063744 | -0.0045596 | 0.057537 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.011592 | 0.060351 | -0.17751 | 2.4601 | -0.27853 | 121.3794 | 121.0992 | 120.9576 | -0.24621 | -0.118 | 10.0918 | -0.26239 | 121.03 | 121.2368 | 121.2354 | -0.2832 | 0.092531 | 0.072033 | 0.16124 | 0.060217 | -0.032314 | -0.2082 | -0.34982 | 0.055547 | -0.27734 | 0.22075 | 0.076352 | 0.020805 | -0.070586 | -0.071963 | 121.7182 | 121.4379 | 121.2963 | 2.7989 | -121.5536 | 121.3688 | 121.5755 | 121.5742 | 10.4306 | -121.5906
1100.8594 | 121.7285 | -0.31128 | 121.2982 | 1.4211e-13 | -0.022517 | -0.0011645 | 0.063744 | -0.0041322 | 0.057751 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063844 | 0.011805 | 0.060351 | -0.17293 | 2.4601 | -0.27395 | 121.3748 | 121.1083 | 120.9576 | -0.24163 | -0.11342 | 10.1697 | -0.25324 | 121.0392 | 121.2459 | 121.2354 | -0.27862 | 0.069644 | 0.07661 | 0.13835 | 0.037329 | -0.032315 | -0.18988 | -0.34067 | 0.03266 | -0.25902 | 0.19786 | 0.058043 | 0.025383 | -0.052274 | -0.062808 | 121.6861 | 121.4196 | 121.2688 | 2.7714 | -121.5399 | 121.3505 | 121.5572 | 121.5467 | 10.481 | -121.5768
1102.5781 | 121.6873 | -0.31586 | 121.312 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.06353 | -0.0041322 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063631 | 0.012233 | 0.060351 | -0.16835 | 2.4693 | -0.27853 | 121.3794 | 121.1083 | 120.953 | -0.24163 | -0.11342 | 10.2063 | -0.25781 | 121.0438 | 121.2459 | 121.2354 | -0.28778 | 0.074222 | 0.067455 | 0.1475 | 0.037329 | -0.036893 | -0.20362 | -0.35898 | 0.02808 | -0.26818 | 0.20244 | 0.058043 | 0.029963 | -0.066007 | -0.076541 | 121.6953 | 121.4242 | 121.2688 | 2.7851 | -121.5536 | 121.3596 | 121.5618 | 121.5513 | 10.5222 | -121.5997
1104.3594 | 121.7239 | -0.28381 | 121.2799 | 1.4211e-13 | -0.022731 | -0.0011645 | 0.063316 | -0.0041322 | 0.057537 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063844 | 0.011592 | 0.060137 | -0.16377 | 2.4784 | -0.27853 | 121.384 | 121.1038 | 120.9667 | -0.24621 | -0.11342 | 10.1743 | -0.26239 | 121.0438 | 121.2459 | 121.2446 | -0.2832 | 0.037599 | 0.10408 | 0.12004 | 0.005285 | -0.032314 | -0.17615 | -0.3132 | 0.000615 | -0.23613 | 0.17039 | 0.02142 | 0.020805 | -0.033963 | -0.03534 | 121.6678 | 121.3876 | 121.2505 | 2.7622 | -121.5261 | 121.3276 | 121.5298 | 121.5284 | 10.4581 | -121.5631
1106.125 | 121.6141 | -0.32959 | 121.3074 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.063744 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063844 | 0.011805 | 0.060137 | -0.16377 | 2.4647 | -0.26937 | 121.3886 | 121.1038 | 120.9713 | -0.23706 | -0.10426 | 10.1834 | -0.24866 | 121.0438 | 121.2551 | 121.24 | -0.26488 | 0.092534 | 0.08119 | 0.16582 | 0.060219 | -0.032315 | -0.20362 | -0.33609 | 0.064707 | -0.2636 | 0.22533 | 0.080933 | 0.016226 | -0.052272 | -0.067385 | 121.7182 | 121.4333 | 121.3009 | 2.7943 | -121.5444 | 121.3734 | 121.5847 | 121.5696 | 10.513 | -121.5723
1107.8281 | 121.6003 | -0.33875 | 121.2982 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.06353 | -0.0041322 | 0.057965 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.011592 | 0.060351 | -0.1592 | 2.4555 | -0.26479 | 121.384 | 121.1129 | 120.9713 | -0.23706 | -0.099684 | 10.1971 | -0.25324 | 121.0438 | 121.2505 | 121.2446 | -0.26946 | 0.10169 | 0.085766 | 0.17955 | 0.073952 | -0.027737 | -0.1853 | -0.32693 | 0.069283 | -0.25445 | 0.23906 | 0.085509 | 0.016226 | -0.047695 | -0.053651 | 121.7227 | 121.4517 | 121.31 | 2.7943 | -121.5353 | 121.3825 | 121.5893 | 121.5833 | 10.5359 | -121.5677
1109.5781 | 121.6507 | -0.32501 | 121.2753 | 1.4211e-13 | -0.022944 | -0.0013783 | 0.06353 | -0.004346 | 0.057751 | -0.0099194 | 0.00034614 | 0.00015807 | 0.064058 | 0.012233 | 0.060351 | -0.16377 | 2.4693 | -0.27395 | 121.3794 | 121.1038 | 120.9713 | -0.23706 | -0.10884 | 10.188 | -0.24866 | 121.0438 | 121.2597 | 121.2446 | -0.27404 | 0.087956 | 0.10408 | 0.16124 | 0.051062 | -0.036894 | -0.17157 | -0.30404 | 0.050972 | -0.23156 | 0.21617 | 0.076355 | 0.025383 | -0.01565 | -0.030763 | 121.7044 | 121.4288 | 121.2963 | 2.7943 | -121.5124 | 121.3688 | 121.5847 | 121.5696 | 10.513 | -121.5494
1111.3594 | 121.6919 | -0.32044 | 121.2845 | 1.4211e-13 | -0.023158 | -0.00095092 | 0.06353 | -0.0039186 | 0.057537 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063631 | 0.011805 | 0.059923 | -0.16835 | 2.483 | -0.26937 | 121.3886 | 121.1083 | 120.9759 | -0.24163 | -0.10426 | 10.1926 | -0.25781 | 121.0392 | 121.2505 | 121.2446 | -0.2832 | 0.0788 | 0.10408 | 0.15208 | 0.051064 | -0.027736 | -0.17615 | -0.30862 | 0.037237 | -0.24529 | 0.21617 | 0.062621 | 0.025384 | -0.033962 | -0.039918 | 121.709 | 121.4288 | 121.2963 | 2.8034 | -121.5261 | 121.3596 | 121.571 | 121.565 | 10.513 | -121.5677
1113.0781 | 121.7102 | -0.3067 | 121.2982 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.063316 | -0.0039186 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063844 | 0.012233 | 0.059923 | -0.1592 | 2.4784 | -0.27395 | 121.384 | 121.1175 | 120.9667 | -0.23248 | -0.10426 | 10.1697 | -0.24866 | 121.0438 | 121.2551 | 121.2446 | -0.26946 | 0.074225 | 0.085766 | 0.14751 | 0.032752 | -0.041473 | -0.18073 | -0.33151 | 0.03724 | -0.25445 | 0.20244 | 0.058045 | 0.020805 | -0.043117 | -0.053651 | 121.6907 | 121.4242 | 121.2734 | 2.7851 | -121.5307 | 121.3505 | 121.5618 | 121.5513 | 10.4764 | -121.5677
1114.8594 | 121.6461 | -0.31586 | 121.3165 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.06353 | -0.0041322 | 0.057537 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063417 | 0.012019 | 0.060137 | -0.16377 | 2.4739 | -0.26937 | 121.3931 | 121.1083 | 120.9713 | -0.23706 | -0.10884 | 10.22 | -0.25324 | 121.0484 | 121.2551 | 121.2354 | -0.27404 | 0.078801 | 0.076613 | 0.15208 | 0.046486 | -0.032315 | -0.20819 | -0.34524 | 0.041817 | -0.26818 | 0.20702 | 0.062621 | 0.020804 | -0.061427 | -0.081118 | 121.709 | 121.4242 | 121.2871 | 2.7897 | -121.5536 | 121.3642 | 121.571 | 121.5513 | 10.5359 | -121.5906
1116.5469 | 121.5866 | -0.34332 | 121.3531 | 1.4211e-13 | -0.022731 | -0.0013783 | 0.063316 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.011805 | 0.060137 | -0.1592 | 2.4876 | -0.27395 | 121.384 | 121.1175 | 120.9759 | -0.23706 | -0.10884 | 10.1971 | -0.24408 | 121.0484 | 121.2597 | 121.2583 | -0.26946 | 0.10627 | 0.030835 | 0.18413 | 0.069373 | -0.036894 | -0.23566 | -0.37728 | 0.073861 | -0.3048 | 0.23448 | 0.099245 | 0.025384 | -0.093469 | -0.094846 | 121.7273 | 121.4608 | 121.3192 | 2.8309 | -121.5902 | 121.3917 | 121.603 | 121.6016 | 10.5405 | -121.6226
1118.3125 | 121.701 | -0.31586 | 121.312 | 1.4211e-13 | -0.022731 | -0.0013783 | 0.06353 | -0.0039186 | 0.057751 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.011592 | 0.059923 | -0.16377 | 2.4876 | -0.27395 | 121.3886 | 121.1129 | 120.9713 | -0.2279 | -0.10884 | 10.1834 | -0.25781 | 121.0575 | 121.2551 | 121.24 | -0.26946 | 0.087958 | 0.076612 | 0.15208 | 0.041907 | -0.046051 | -0.19904 | -0.34066 | 0.046395 | -0.25444 | 0.20702 | 0.058043 | 0.011648 | -0.05685 | -0.071963 | 121.7044 | 121.4288 | 121.2871 | 2.8034 | -121.5398 | 121.3734 | 121.571 | 121.5558 | 10.4993 | -121.5814
1120.0938 | 121.7377 | -0.27466 | 121.3028 | 1.4211e-13 | -0.022944 | -0.0013783 | 0.063316 | -0.0039186 | 0.057965 | -0.0099194 | 0.00034614 | 0.00058547 | 0.063844 | 0.011805 | 0.060137 | -0.16377 | 2.483 | -0.26937 | 121.3931 | 121.1175 | 120.9713 | -0.23248 | -0.095105 | 10.2384 | -0.24408 | 121.0438 | 121.2597 | 121.2491 | -0.27862 | 0.042181 | 0.090346 | 0.11088 | 0.005287 | -0.036894 | -0.1853 | -0.33151 | -0.003961 | -0.25902 | 0.17955 | 0.03058 | 0.034541 | -0.043115 | -0.05365 | 121.6678 | 121.3922 | 121.2459 | 2.7577 | -121.5353 | 121.3184 | 121.5343 | 121.5238 | 10.513 | -121.5814
1121.7969 | 121.6095 | -0.3479 | 121.3165 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.063744 | -0.0041322 | 0.057537 | -0.01755 | 0.00034614 | 0.00037167 | 0.063844 | 0.011592 | 0.060137 | -0.1592 | 2.4922 | -0.26479 | 121.3886 | 121.1221 | 120.9759 | -0.22332 | -0.090527 | 10.188 | -0.23492 | 121.0575 | 121.2597 | 121.2446 | -0.26488 | 0.12458 | 0.072035 | 0.1887 | 0.083107 | -0.041473 | -0.19446 | -0.34066 | 0.083017 | -0.25902 | 0.25737 | 0.11298 | 0.029962 | -0.056848 | -0.071961 | 121.7365 | 121.47 | 121.3238 | 2.8401 | -121.5398 | 121.4054 | 121.6076 | 121.5925 | 10.5359 | -121.5814
1123.5625 | 121.6141 | -0.32044 | 121.3531 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.063103 | -0.0039186 | 0.057751 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063631 | 0.012019 | 0.060137 | -0.1592 | 2.5059 | -0.26021 | 121.4023 | 121.1266 | 120.985 | -0.21874 | -0.095105 | 10.2429 | -0.2395 | 121.0621 | 121.2688 | 121.2537 | -0.26488 | 0.10169 | 0.049149 | 0.16124 | 0.06022 | -0.041474 | -0.2265 | -0.36813 | 0.055552 | -0.29106 | 0.22533 | 0.080936 | 0.025384 | -0.084312 | -0.099425 | 121.7227 | 121.4471 | 121.3055 | 2.8263 | -121.5719 | 121.3825 | 121.5893 | 121.5742 | 10.5634 | -121.618
1125.3438 | 121.7056 | -0.29297 | 121.3028 | 1.4211e-13 | -0.023158 | -0.0013783 | 0.06353 | -0.0039186 | 0.057324 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063417 | 0.011805 | 0.060137 | -0.15462 | 2.4967 | -0.26021 | 121.3977 | 121.1312 | 120.985 | -0.22332 | -0.095105 | 10.22 | -0.2395 | 121.0575 | 121.2688 | 121.2537 | -0.26946 | 0.069649 | 0.094925 | 0.13835 | 0.032754 | -0.036895 | -0.17157 | -0.31777 | 0.023507 | -0.24529 | 0.19786 | 0.05347 | 0.029963 | -0.033958 | -0.049071 | 121.6907 | 121.4242 | 121.278 | 2.7897 | -121.5261 | 121.3505 | 121.5618 | 121.5467 | 10.513 | -121.5723
1127.0469 | 121.6873 | -0.29297 | 121.3028 | 1.4211e-13 | -0.023585 | -0.0013783 | 0.063744 | -0.0041322 | 0.057751 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.011592 | 0.060351 | -0.15004 | 2.5151 | -0.26021 | 121.4023 | 121.1312 | 120.985 | -0.2279 | -0.095105 | 10.2017 | -0.24408 | 121.0667 | 121.2643 | 121.2583 | -0.26488 | 0.06507 | 0.099503 | 0.14293 | 0.032754 | -0.032316 | -0.17157 | -0.31777 | 0.028086 | -0.23613 | 0.19786 | 0.048891 | 0.020805 | -0.038537 | -0.044492 | 121.6953 | 121.4242 | 121.278 | 2.808 | -121.5307 | 121.3596 | 121.5572 | 121.5513 | 10.4947 | -121.5677
1128.8281 | 121.7239 | -0.28381 | 121.3165 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.06353 | -0.0039186 | 0.057537 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.011378 | 0.060137 | -0.15004 | 2.5242 | -0.25106 | 121.3977 | 121.1312 | 120.9896 | -0.22332 | -0.090527 | 10.188 | -0.24408 | 121.0667 | 121.2688 | 121.2583 | -0.2603 | 0.060493 | 0.081192 | 0.13377 | 0.032755 | -0.027738 | -0.1853 | -0.32693 | 0.023509 | -0.24986 | 0.19329 | 0.039735 | 0.016226 | -0.047691 | -0.058225 | 121.6815 | 121.415 | 121.2734 | 2.808 | -121.5398 | 121.3505 | 121.5526 | 121.5421 | 10.4718 | -121.5768
1130.5938 | 121.6324 | -0.31586 | 121.3394 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.06353 | -0.0041322 | 0.057751 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.012019 | 0.060351 | -0.14546 | 2.5288 | -0.25106 | 121.4069 | 121.1404 | 120.9896 | -0.22332 | -0.090527 | 10.2704 | -0.23492 | 121.0621 | 121.2734 | 121.2629 | -0.25572 | 0.092537 | 0.067459 | 0.1704 | 0.064799 | -0.027738 | -0.19903 | -0.34982 | 0.060132 | -0.27733 | 0.22533 | 0.080936 | 0.020804 | -0.066001 | -0.076536 | 121.7227 | 121.4562 | 121.3055 | 2.8447 | -121.5627 | 121.3779 | 121.5893 | 121.5787 | 10.5863 | -121.5951
1132.375 | 121.6324 | -0.34332 | 121.3303 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.06353 | -0.004346 | 0.057537 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.012019 | 0.059923 | -0.15004 | 2.5242 | -0.25106 | 121.4115 | 121.1312 | 120.9988 | -0.22332 | -0.095105 | 10.2841 | -0.23034 | 121.0667 | 121.2734 | 121.2629 | -0.25572 | 0.12 | 0.081194 | 0.19328 | 0.092265 | -0.027738 | -0.19903 | -0.3315 | 0.087598 | -0.2636 | 0.24822 | 0.11298 | 0.025383 | -0.056845 | -0.06738 | 121.7548 | 121.4746 | 121.3421 | 2.8675 | -121.5536 | 121.41 | 121.6167 | 121.6062 | 10.6275 | -121.586
1134.0781 | 121.7102 | -0.27924 | 121.2936 | 1.4211e-13 | -0.023372 | -0.0011645 | 0.06353 | -0.003705 | 0.057751 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063631 | 0.011592 | 0.059496 | -0.15004 | 2.538 | -0.24648 | 121.4115 | 121.1358 | 120.9896 | -0.22332 | -0.081369 | 10.2429 | -0.2395 | 121.0712 | 121.2826 | 121.2675 | -0.25572 | 0.055916 | 0.11782 | 0.1292 | 0.032756 | -0.02316 | -0.15783 | -0.30404 | 0.023511 | -0.2224 | 0.19787 | 0.039737 | 0.016226 | -0.011067 | -0.02618 | 121.6907 | 121.415 | 121.2688 | 2.8172 | -121.517 | 121.3505 | 121.5618 | 121.5467 | 10.5222 | -121.5494
1135.8438 | 121.6187 | -0.33417 | 121.3348 | 1.4211e-13 | -0.023372 | -0.0011645 | 0.06353 | -0.0041322 | 0.057965 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.011805 | 0.060137 | -0.14546 | 2.538 | -0.24648 | 121.416 | 121.1404 | 121.0033 | -0.21416 | -0.07679 | 10.2933 | -0.23034 | 121.0758 | 121.2826 | 121.272 | -0.25572 | 0.12001 | 0.081194 | 0.18871 | 0.087687 | -0.032318 | -0.19445 | -0.3315 | 0.078442 | -0.25902 | 0.25738 | 0.10383 | 0.025383 | -0.052266 | -0.062801 | 121.7502 | 121.4746 | 121.3375 | 2.8721 | -121.549 | 121.41 | 121.6167 | 121.6062 | 10.6275 | -121.5906
1137.6094 | 121.7422 | -0.27924 | 121.3165 | 1.4211e-13 | -0.023372 | -0.00095092 | 0.06353 | -0.004346 | 0.057537 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.012019 | 0.060137 | -0.14088 | 2.5288 | -0.25106 | 121.4115 | 121.145 | 120.9942 | -0.22332 | -0.081369 | 10.2704 | -0.23034 | 121.0712 | 121.2826 | 121.2675 | -0.25115 | 0.055916 | 0.094927 | 0.13835 | 0.028178 | -0.027738 | -0.17156 | -0.32235 | 0.02809 | -0.24529 | 0.19787 | 0.048894 | 0.020804 | -0.033955 | -0.049068 | 121.6907 | 121.4242 | 121.2734 | 2.808 | -121.5398 | 121.3505 | 121.5618 | 121.5467 | 10.5496 | -121.5677
1139.3906 | 121.6873 | -0.29297 | 121.3348 | 1.4211e-13 | -0.023372 | -0.0011645 | 0.06353 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.012019 | 0.059923 | -0.14546 | 2.5425 | -0.24648 | 121.4206 | 121.1358 | 121.0033 | -0.21416 | -0.085948 | 10.2979 | -0.22576 | 121.0758 | 121.278 | 121.272 | -0.24657 | 0.078807 | 0.085772 | 0.14751 | 0.046489 | -0.032318 | -0.19903 | -0.3315 | 0.046402 | -0.25902 | 0.20702 | 0.067206 | 0.020804 | -0.056845 | -0.062801 | 121.7136 | 121.4288 | 121.2963 | 2.8355 | -121.549 | 121.3688 | 121.571 | 121.565 | 10.5908 | -121.5814
1141.1719 | 121.7377 | -0.2655 | 121.3165 | 1.4211e-13 | -0.022944 | -0.0011645 | 0.063316 | -0.004346 | 0.057751 | -0.0099194 | 0.00034614 | -0.00026913 | 0.063631 | 0.012019 | 0.060137 | -0.14088 | 2.5425 | -0.2419 | 121.4115 | 121.1495 | 121.0033 | -0.21874 | -0.081369 | 10.3116 | -0.23034 | 121.0758 | 121.2826 | 121.2766 | -0.25572 | 0.046762 | 0.094927 | 0.12462 | 0.023601 | -0.023161 | -0.16698 | -0.31319 | 0.009778 | -0.24071 | 0.18413 | 0.035161 | 0.025383 | -0.033955 | -0.039911 | 121.677 | 121.415 | 121.2688 | 2.808 | -121.5353 | 121.3413 | 121.5481 | 121.5421 | 10.5771 | -121.5723
1142.9531 | 121.6507 | -0.31128 | 121.3577 | 1.4211e-13 | -0.023372 | -0.0013783 | 0.063744 | -0.004346 | 0.057537 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063844 | 0.011805 | 0.059923 | -0.13173 | 2.538 | -0.2419 | 121.4206 | 121.1404 | 121.0033 | -0.21416 | -0.081369 | 10.3391 | -0.22576 | 121.0804 | 121.2917 | 121.272 | -0.24657 | 0.097117 | 0.062884 | 0.17955 | 0.069377 | -0.02774 | -0.21734 | -0.35439 | 0.064712 | -0.27733 | 0.22991 | 0.085516 | 0.020804 | -0.065997 | -0.085689 | 121.7319 | 121.4517 | 121.3146 | 2.8492 | -121.5719 | 121.3917 | 121.603 | 121.5833 | 10.6504 | -121.6043
1144.6562 | 121.6644 | -0.30212 | 121.3394 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.06353 | -0.0041322 | 0.057537 | -0.0022889 | 0.00013254 | 0.00037167 | 0.063417 | 0.011805 | 0.059923 | -0.14088 | 2.5471 | -0.24648 | 121.4206 | 121.145 | 121.0125 | -0.205 | -0.072212 | 10.3254 | -0.22576 | 121.0758 | 121.2872 | 121.2766 | -0.25115 | 0.09712 | 0.081194 | 0.16124 | 0.055644 | -0.041476 | -0.19445 | -0.32692 | 0.050978 | -0.26359 | 0.22991 | 0.076361 | 0.025383 | -0.052266 | -0.0628 | 121.7227 | 121.4471 | 121.3146 | 2.8492 | -121.5444 | 121.3779 | 121.5893 | 121.5787 | 10.6275 | -121.5906
1146.4219 | 121.7148 | -0.29755 | 121.3165 | 1.4211e-13 | -0.023585 | -0.0013783 | 0.06353 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063417 | 0.012446 | 0.060137 | -0.13173 | 2.5425 | -0.2419 | 121.416 | 121.145 | 121.0125 | -0.205 | -0.07679 | 10.3528 | -0.22118 | 121.085 | 121.278 | 121.2766 | -0.24657 | 0.092542 | 0.099505 | 0.16582 | 0.055644 | -0.036898 | -0.17156 | -0.30403 | 0.050979 | -0.23155 | 0.22076 | 0.076361 | 0.025382 | -0.038534 | -0.039911 | 121.7136 | 121.4425 | 121.31 | 2.8401 | -121.5215 | 121.3825 | 121.5755 | 121.5742 | 10.6504 | -121.5631
1148.2031 | 121.6049 | -0.31128 | 121.3303 | 1.4211e-13 | -0.023799 | -0.00095092 | 0.063744 | -0.0045596 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.011805 | 0.05971 | -0.14088 | 2.5563 | -0.2419 | 121.4115 | 121.1495 | 121.0079 | -0.20042 | -0.085948 | 10.3162 | -0.22118 | 121.0804 | 121.2917 | 121.2766 | -0.25115 | 0.11085 | 0.081194 | 0.1704 | 0.069377 | -0.041477 | -0.18072 | -0.32235 | 0.060133 | -0.24986 | 0.22533 | 0.090094 | 0.029961 | -0.038531 | -0.053644 | 121.7227 | 121.4608 | 121.3192 | 2.8675 | -121.5307 | 121.3917 | 121.603 | 121.5879 | 10.6275 | -121.5814
1149.9688 | 121.7422 | -0.27008 | 121.344 | 1.4211e-13 | -0.023158 | -0.0011645 | 0.063316 | -0.004346 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.012233 | 0.060137 | -0.1363 | 2.5608 | -0.23732 | 121.4206 | 121.1541 | 121.0125 | -0.20958 | -0.072212 | 10.3574 | -0.21661 | 121.0804 | 121.2872 | 121.272 | -0.24199 | 0.060498 | 0.076617 | 0.13378 | 0.032758 | -0.02774 | -0.18987 | -0.3315 | 0.028092 | -0.26359 | 0.19787 | 0.053475 | 0.025383 | -0.056843 | -0.071956 | 121.6907 | 121.4242 | 121.2826 | 2.8309 | -121.5536 | 121.3505 | 121.5572 | 121.5421 | 10.6275 | -121.586
1151.6719 | 121.6919 | -0.27466 | 121.3348 | 1.4211e-13 | -0.023585 | -0.00095092 | 0.06353 | -0.004346 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.012019 | 0.060137 | -0.1363 | 2.5746 | -0.2419 | 121.4252 | 121.1587 | 121.0125 | -0.205 | -0.07679 | 10.3254 | -0.22118 | 121.085 | 121.2963 | 121.2812 | -0.24199 | 0.069654 | 0.090351 | 0.13835 | 0.032756 | -0.036898 | -0.17614 | -0.32234 | 0.032669 | -0.24986 | 0.19787 | 0.053473 | 0.020804 | -0.03853 | -0.053643 | 121.6998 | 121.4334 | 121.2872 | 2.8492 | -121.5398 | 121.3596 | 121.571 | 121.5559 | 10.6 | -121.5768
1153.4375 | 121.6919 | -0.25177 | 121.3028 | 1.4211e-13 | -0.023372 | -0.0015919 | 0.063103 | -0.0039186 | 0.057965 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063844 | 0.011805 | 0.060137 | -0.1363 | 2.5654 | -0.22817 | 121.4298 | 121.1541 | 121.0125 | -0.20042 | -0.067633 | 10.3528 | -0.22118 | 121.0896 | 121.2963 | 121.2766 | -0.24199 | 0.051345 | 0.12697 | 0.11547 | 0.023603 | -0.027742 | -0.14867 | -0.2903 | 0.009781 | -0.21324 | 0.18414 | 0.030585 | 0.020804 | -0.006486 | -0.026178 | 121.6815 | 121.4059 | 121.2643 | 2.8172 | -121.5032 | 121.3413 | 121.5481 | 121.5284 | 10.6046 | -121.5448
1155.1719 | 121.756 | -0.27008 | 121.3211 | 1.4211e-13 | -0.023799 | -0.0013783 | 0.06353 | -0.0039186 | 0.057537 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.012233 | 0.060137 | -0.1363 | 2.57 | -0.23275 | 121.4206 | 121.1541 | 121.0079 | -0.20042 | -0.067633 | 10.3437 | -0.22576 | 121.085 | 121.2917 | 121.2812 | -0.24657 | 0.069656 | 0.099505 | 0.13378 | 0.037336 | -0.03232 | -0.16698 | -0.31319 | 0.023514 | -0.23613 | 0.20245 | 0.044318 | 0.020804 | -0.029376 | -0.03991 | 121.6907 | 121.4242 | 121.278 | 2.8401 | -121.5215 | 121.3551 | 121.5618 | 121.5513 | 10.6137 | -121.5677
1156.9531 | 121.6919 | -0.27008 | 121.3348 | 1.4211e-13 | -0.023585 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.012019 | 0.05971 | -0.1363 | 2.5654 | -0.23275 | 121.4252 | 121.1541 | 121.0171 | -0.205 | -0.072212 | 10.3391 | -0.20745 | 121.0804 | 121.3009 | 121.2812 | -0.24199 | 0.065077 | 0.090351 | 0.13378 | 0.037336 | -0.027741 | -0.18072 | -0.31777 | 0.028092 | -0.25444 | 0.19787 | 0.062632 | 0.03454 | -0.033952 | -0.053643 | 121.6953 | 121.4242 | 121.2872 | 2.8355 | -121.5398 | 121.3505 | 121.571 | 121.5513 | 10.6092 | -121.5768
1158.7188 | 121.7331 | -0.23346 | 121.312 | 1.4211e-13 | -0.023585 | -0.0013783 | 0.06353 | -0.0041322 | 0.057751 | 0.012972 | 0.00055974 | 0.00015807 | 0.063844 | 0.011805 | 0.05971 | -0.13173 | 2.5792 | -0.23732 | 121.4298 | 121.1541 | 121.0171 | -0.205 | -0.07679 | 10.3666 | -0.21661 | 121.0896 | 121.2963 | 121.2858 | -0.24199 | 0.028455 | 0.11782 | 0.10173 | -0.003864 | -0.032319 | -0.15783 | -0.29488 | -0.00853 | -0.22239 | 0.15667 | 0.016853 | 0.025383 | -0.015642 | -0.026177 | 121.6632 | 121.3876 | 121.2505 | 2.8126 | -121.517 | 121.323 | 121.5298 | 121.5192 | 10.6 | -121.5539
1160.4219 | 121.7239 | -0.25177 | 121.3165 | 1.4211e-13 | -0.023585 | -0.0011645 | 0.063316 | -0.0039186 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.012019 | 0.059923 | -0.13173 | 2.5746 | -0.23732 | 121.4343 | 121.1587 | 121.0171 | -0.19585 | -0.067633 | 10.3757 | -0.21661 | 121.085 | 121.2963 | 121.2812 | -0.24199 | 0.055924 | 0.11782 | 0.12004 | 0.014447 | -0.041477 | -0.15783 | -0.29946 | 0.009781 | -0.23155 | 0.18414 | 0.035164 | 0.025383 | -0.020219 | -0.035332 | 121.6861 | 121.4105 | 121.2688 | 2.8264 | -121.5124 | 121.3367 | 121.5481 | 121.533 | 10.6275 | -121.5585
1162.2031 | 121.7422 | -0.26093 | 121.344 | 1.4211e-13 | -0.023372 | -0.0011645 | 0.063744 | -0.0039186 | 0.057751 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063631 | 0.012233 | 0.060137 | -0.1363 | 2.5837 | -0.22817 | 121.4298 | 121.1633 | 121.0217 | -0.20042 | -0.072212 | 10.3711 | -0.21661 | 121.0896 | 121.3009 | 121.2949 | -0.23741 | 0.0605 | 0.085774 | 0.12462 | 0.032758 | -0.027742 | -0.18071 | -0.32234 | 0.023515 | -0.25444 | 0.18871 | 0.044319 | 0.020804 | -0.043107 | -0.049063 | 121.6907 | 121.4242 | 121.2826 | 2.8447 | -121.5444 | 121.3505 | 121.5618 | 121.5559 | 10.6321 | -121.5814
1163.9688 | 121.6049 | -0.30212 | 121.3806 | 1.4211e-13 | -0.023585 | -0.0011645 | 0.063316 | -0.0041322 | 0.057324 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063844 | 0.012019 | 0.059923 | -0.13173 | 2.5837 | -0.22817 | 121.4343 | 121.1633 | 121.0308 | -0.19585 | -0.063054 | 10.3895 | -0.21661 | 121.085 | 121.2963 | 121.2812 | -0.23741 | 0.10628 | 0.053732 | 0.1704 | 0.073957 | -0.032321 | -0.21733 | -0.34981 | 0.064714 | -0.29564 | 0.23907 | 0.085518 | 0.020804 | -0.084306 | -0.099419 | 121.7365 | 121.4654 | 121.3329 | 2.8859 | -121.5765 | 121.3871 | 121.5984 | 121.5833 | 10.6916 | -121.618
1165.7344 | 121.7239 | -0.25635 | 121.3211 | 1.4211e-13 | -0.023799 | -0.00073712 | 0.063316 | -0.004346 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.012019 | 0.059923 | -0.13173 | 2.5975 | -0.23732 | 121.4343 | 121.1679 | 121.0217 | -0.19127 | -0.067633 | 10.394 | -0.21661 | 121.0896 | 121.3055 | 121.2766 | -0.23741 | 0.065081 | 0.11324 | 0.12462 | 0.019025 | -0.046056 | -0.15325 | -0.29945 | 0.018938 | -0.23155 | 0.18872 | 0.039742 | 0.020804 | -0.01564 | -0.044489 | 121.6907 | 121.4242 | 121.278 | 2.8538 | -121.5124 | 121.3459 | 121.5618 | 121.533 | 10.6504 | -121.5585
1167.4844 | 121.637 | -0.28381 | 121.3715 | 1.4211e-13 | -0.024013 | -0.0011645 | 0.063316 | -0.0041322 | 0.057751 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.063844 | 0.012019 | 0.059923 | -0.12257 | 2.6021 | -0.23732 | 121.4343 | 121.1633 | 121.0262 | -0.20042 | -0.058476 | 10.3528 | -0.21203 | 121.0896 | 121.2872 | 121.2858 | -0.24199 | 0.083388 | 0.062887 | 0.16124 | 0.04649 | -0.036898 | -0.20818 | -0.34523 | 0.041824 | -0.2819 | 0.22534 | 0.071786 | 0.029962 | -0.084309 | -0.085686 | 121.7182 | 121.4471 | 121.31 | 2.8859 | -121.5719 | 121.3734 | 121.571 | 121.5696 | 10.6366 | -121.6134
1169.1875 | 121.6232 | -0.30212 | 121.3669 | 1.4211e-13 | -0.023585 | -0.0015919 | 0.06353 | -0.0041322 | 0.057537 | 0.0053411 | 0.00077334 | 0.00037167 | 0.063844 | 0.011805 | 0.059496 | -0.12257 | 2.6158 | -0.22817 | 121.4389 | 121.1679 | 121.0354 | -0.19585 | -0.067633 | 10.2979 | -0.20287 | 121.0941 | 121.3055 | 121.2995 | -0.23283 | 0.10628 | 0.072043 | 0.17956 | 0.073957 | -0.032321 | -0.19902 | -0.3315 | 0.069293 | -0.27275 | 0.23449 | 0.099254 | 0.029961 | -0.061416 | -0.067372 | 121.741 | 121.47 | 121.3375 | 2.9179 | -121.5627 | 121.3963 | 121.6076 | 121.6016 | 10.6 | -121.5997
1170.9531 | 121.701 | -0.2655 | 121.3577 | 1.4211e-13 | -0.023585 | -0.00073712 | 0.06353 | -0.004346 | 0.057751 | 0.0053411 | 0.00055974 | 0.00058547 | 0.063417 | 0.012019 | 0.05971 | -0.12715 | 2.6204 | -0.23275 | 121.4389 | 121.1679 | 121.0308 | -0.19585 | -0.063054 | 10.3208 | -0.20745 | 121.0941 | 121.3055 | 121.2904 | -0.23741 | 0.069657 | 0.081198 | 0.13836 | 0.032758 | -0.036899 | -0.18987 | -0.32692 | 0.028093 | -0.26359 | 0.20245 | 0.058054 | 0.029961 | -0.052261 | -0.067374 | 121.7044 | 121.4334 | 121.2963 | 2.8859 | -121.5536 | 121.3596 | 121.571 | 121.5559 | 10.5863 | -121.5951
1172.7188 | 121.7285 | -0.25177 | 121.3257 | 1.4211e-13 | -0.023799 | -0.00095092 | 0.06353 | -0.0039186 | 0.057537 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063844 | 0.012233 | 0.059923 | -0.12257 | 2.6295 | -0.22817 | 121.4343 | 121.1633 | 121.0308 | -0.19585 | -0.053897 | 10.4032 | -0.20287 | 121.0987 | 121.3055 | 121.2949 | -0.23283 | 0.055924 | 0.10866 | 0.1292 | 0.023603 | -0.032321 | -0.1624 | -0.29488 | 0.018939 | -0.22697 | 0.19787 | 0.0489 | 0.029961 | -0.020218 | -0.030753 | 121.6861 | 121.4151 | 121.2826 | 2.8813 | -121.5215 | 121.3505 | 121.5572 | 121.5467 | 10.655 | -121.5585
1174.4688 | 121.756 | -0.25635 | 121.3394 | 1.4211e-13 | -0.023799 | -0.00095092 | 0.063316 | -0.0041322 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.012233 | 0.05971 | -0.12715 | 2.6158 | -0.22817 | 121.4389 | 121.1679 | 121.0354 | -0.20042 | -0.058476 | 10.4123 | -0.20745 | 121.0941 | 121.3055 | 121.2904 | -0.23283 | 0.055923 | 0.099508 | 0.1292 | 0.028181 | -0.027742 | -0.17156 | -0.30403 | 0.023517 | -0.24528 | 0.19787 | 0.048899 | 0.025382 | -0.033951 | -0.049064 | 121.6953 | 121.4242 | 121.2917 | 2.8721 | -121.5398 | 121.3505 | 121.5618 | 121.5467 | 10.6687 | -121.5722
1176.1719 | 121.6415 | -0.29755 | 121.3623 | 1.4211e-13 | -0.023585 | -0.00073712 | 0.06353 | -0.004346 | 0.057965 | 0.0053411 | 0.00013254 | 0.00037167 | 0.063631 | 0.012446 | 0.059923 | -0.11799 | 2.6204 | -0.22817 | 121.4389 | 121.1724 | 121.0262 | -0.19585 | -0.063054 | 10.4032 | -0.20745 | 121.0987 | 121.31 | 121.2995 | -0.22367 | 0.1017 | 0.07662 | 0.17955 | 0.069379 | -0.032321 | -0.18987 | -0.33608 | 0.073873 | -0.26359 | 0.23449 | 0.090097 | 0.016224 | -0.052261 | -0.062795 | 121.7365 | 121.47 | 121.3238 | 2.9179 | -121.5582 | 121.3963 | 121.6076 | 121.5971 | 10.7007 | -121.586
1177.9375 | 121.6461 | -0.28839 | 121.3531 | 1.4211e-13 | -0.023799 | -0.0011645 | 0.06353 | -0.0039186 | 0.057965 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.012233 | 0.059923 | -0.12715 | 2.6158 | -0.22817 | 121.4481 | 121.1724 | 121.0354 | -0.20042 | -0.063054 | 10.4078 | -0.21203 | 121.0941 | 121.3146 | 121.2995 | -0.22825 | 0.087966 | 0.094933 | 0.16124 | 0.060224 | -0.027742 | -0.18071 | -0.31776 | 0.060139 | -0.25901 | 0.22534 | 0.076364 | 0.016225 | -0.038526 | -0.053639 | 121.7365 | 121.4608 | 121.3238 | 2.9042 | -121.5536 | 121.3825 | 121.603 | 121.5879 | 10.6962 | -121.5814
1179.7188 | 121.6461 | -0.28839 | 121.3577 | 1.4211e-13 | -0.024013 | -0.00095092 | 0.063744 | -0.0039186 | 0.057965 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063631 | 0.012233 | 0.059923 | -0.11799 | 2.6204 | -0.22359 | 121.4343 | 121.177 | 121.0308 | -0.20042 | -0.058476 | 10.3803 | -0.20287 | 121.1033 | 121.3055 | 121.2949 | -0.23283 | 0.087966 | 0.07662 | 0.1704 | 0.064802 | -0.023164 | -0.18071 | -0.32692 | 0.05556 | -0.25443 | 0.22992 | 0.085521 | 0.029961 | -0.052261 | -0.062796 | 121.7227 | 121.4654 | 121.3192 | 2.9088 | -121.5582 | 121.3917 | 121.5939 | 121.5833 | 10.6687 | -121.5906
1181.4062 | 121.6782 | -0.29755 | 121.3486 | 1.4211e-13 | -0.023799 | -0.0011645 | 0.063316 | -0.0039186 | 0.057751 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063844 | 0.012233 | 0.05971 | -0.11341 | 2.6341 | -0.22359 | 121.4435 | 121.1679 | 121.0308 | -0.19585 | -0.058476 | 10.3803 | -0.20287 | 121.0987 | 121.3146 | 121.3041 | -0.22825 | 0.1017 | 0.094931 | 0.18413 | 0.073957 | -0.027743 | -0.18071 | -0.31776 | 0.069294 | -0.24986 | 0.23907 | 0.094676 | 0.025382 | -0.033949 | -0.044483 | 121.741 | 121.4654 | 121.3284 | 2.9316 | -121.5444 | 121.3963 | 121.6122 | 121.6016 | 10.6778 | -121.5768
1183.1875 | 121.6507 | -0.27466 | 121.3989 | 1.4211e-13 | -0.024013 | -0.00095092 | 0.06353 | -0.004346 | 0.057751 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063417 | 0.012233 | 0.060351 | -0.12257 | 2.6387 | -0.22359 | 121.4481 | 121.177 | 121.04 | -0.19127 | -0.053897 | 10.3757 | -0.20287 | 121.1033 | 121.3146 | 121.3041 | -0.23283 | 0.083391 | 0.049156 | 0.15209 | 0.051069 | -0.032322 | -0.22191 | -0.35896 | 0.041827 | -0.29563 | 0.22076 | 0.071788 | 0.029961 | -0.084303 | -0.094837 | 121.7227 | 121.4517 | 121.3146 | 2.9133 | -121.5902 | 121.378 | 121.5893 | 121.5787 | 10.6504 | -121.6318
1184.9531 | 121.5912 | -0.28381 | 121.4035 | 1.4211e-13 | -0.023799 | -0.0011645 | 0.06353 | -0.0039186 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.012233 | 0.059923 | -0.11341 | 2.6433 | -0.22359 | 121.4527 | 121.1816 | 121.04 | -0.18669 | -0.049318 | 10.3895 | -0.20287 | 121.1033 | 121.3146 | 121.2995 | -0.22825 | 0.097125 | 0.049157 | 0.1704 | 0.060224 | -0.036901 | -0.22191 | -0.36354 | 0.055561 | -0.30021 | 0.23449 | 0.080943 | 0.025382 | -0.08888 | -0.10399 | 121.7365 | 121.4654 | 121.3238 | 2.9271 | -121.5902 | 121.3871 | 121.5984 | 121.5833 | 10.6733 | -121.6318
1186.6562 | 121.7377 | -0.2655 | 121.344 | 1.4211e-13 | -0.024013 | -0.0013783 | 0.063744 | -0.0041322 | 0.05711 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063844 | 0.012446 | 0.059923 | -0.11341 | 2.6433 | -0.22817 | 121.4481 | 121.1816 | 121.0354 | -0.18211 | -0.053897 | 10.4032 | -0.20287 | 121.0987 | 121.3238 | 121.2995 | -0.22367 | 0.083394 | 0.10409 | 0.15209 | 0.037336 | -0.046058 | -0.1624 | -0.30861 | 0.04183 | -0.24528 | 0.21161 | 0.062633 | 0.020803 | -0.020214 | -0.044484 | 121.7136 | 121.4471 | 121.3009 | 2.9088 | -121.5261 | 121.3642 | 121.5893 | 121.565 | 10.6687 | -121.5677
1188.4219 | 121.7468 | -0.25635 | 121.3577 | 1.4211e-13 | -0.024013 | -0.0015919 | 0.06353 | -0.004346 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063844 | 0.012233 | 0.059923 | -0.12257 | 2.6433 | -0.22817 | 121.4481 | 121.177 | 121.04 | -0.19585 | -0.058476 | 10.3711 | -0.20287 | 121.1079 | 121.31 | 121.2949 | -0.22825 | 0.060502 | 0.090355 | 0.13378 | 0.028181 | -0.032321 | -0.18071 | -0.31776 | 0.028096 | -0.24986 | 0.19787 | 0.053478 | 0.025382 | -0.047683 | -0.062796 | 121.7044 | 121.4334 | 121.2963 | 2.8996 | -121.5536 | 121.3642 | 121.5664 | 121.5513 | 10.6275 | -121.586
1190.125 | 121.6827 | -0.2655 | 121.3806 | 1.4211e-13 | -0.024013 | -0.0011645 | 0.063316 | -0.004346 | 0.057751 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.012233 | 0.05971 | -0.12257 | 2.6433 | -0.21901 | 121.4435 | 121.177 | 121.04 | -0.19127 | -0.067633 | 10.3986 | -0.19829 | 121.1033 | 121.3192 | 121.3041 | -0.23741 | 0.074236 | 0.062888 | 0.14293 | 0.046493 | -0.027743 | -0.2036 | -0.34065 | 0.028093 | -0.27732 | 0.19787 | 0.067212 | 0.039119 | -0.061413 | -0.076526 | 121.709 | 121.4425 | 121.3055 | 2.9088 | -121.5719 | 121.3688 | 121.5847 | 121.5696 | 10.6641 | -121.618
1191.8906 | 121.6187 | -0.29297 | 121.3852 | 1.4211e-13 | -0.024226 | -0.0013783 | 0.063316 | -0.0045596 | 0.057537 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.01266 | 0.059923 | -0.11799 | 2.657 | -0.22359 | 121.4481 | 121.1816 | 121.0491 | -0.20042 | -0.053897 | 10.3711 | -0.19829 | 121.1079 | 121.3192 | 121.2949 | -0.22825 | 0.092544 | 0.062889 | 0.17498 | 0.06938 | -0.023164 | -0.2036 | -0.33607 | 0.064717 | -0.27732 | 0.23907 | 0.094678 | 0.029961 | -0.065991 | -0.090262 | 121.7411 | 121.4746 | 121.3421 | 2.95 | -121.5856 | 121.4008 | 121.6122 | 121.5879 | 10.6641 | -121.6134
1193.6562 | 121.6278 | -0.27924 | 121.3531 | 1.4211e-13 | -0.023585 | -0.00095092 | 0.06353 | -0.004346 | 0.057537 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.012233 | 0.05971 | -0.11341 | 2.6707 | -0.22359 | 121.4481 | 121.1816 | 121.0445 | -0.19127 | -0.049318 | 10.4215 | -0.20287 | 121.1079 | 121.3238 | 121.3087 | -0.22367 | 0.087969 | 0.094933 | 0.16582 | 0.055647 | -0.032322 | -0.17155 | -0.30861 | 0.055563 | -0.24528 | 0.22992 | 0.076366 | 0.020803 | -0.029369 | -0.044482 | 121.7273 | 121.4608 | 121.3238 | 2.95 | -121.5444 | 121.3871 | 121.603 | 121.5879 | 10.7007 | -121.5768
1195.3594 | 121.6461 | -0.27466 | 121.3669 | 1.4211e-13 | -0.023799 | -0.0011645 | 0.06353 | -0.004346 | 0.057751 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.011805 | 0.05971 | -0.11799 | 2.6753 | -0.23275 | 121.4481 | 121.1862 | 121.0491 | -0.19127 | -0.058476 | 10.4444 | -0.19371 | 121.1124 | 121.3284 | 121.3041 | -0.22367 | 0.083391 | 0.0812 | 0.15667 | 0.041913 | -0.041478 | -0.18071 | -0.31776 | 0.050985 | -0.25443 | 0.21618 | 0.080946 | 0.029961 | -0.038523 | -0.062793 | 121.7227 | 121.4608 | 121.3238 | 2.95 | -121.5581 | 121.3871 | 121.603 | 121.5787 | 10.7191 | -121.5906
1197.125 | 121.7194 | -0.24719 | 121.3348 | 1.4211e-13 | -0.024013 | -0.0011645 | 0.06353 | -0.0041322 | 0.057537 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.063631 | 0.012446 | 0.05971 | -0.11799 | 2.6707 | -0.22359 | 121.4527 | 121.1816 | 121.0537 | -0.18211 | -0.044739 | 10.4673 | -0.19371 | 121.1033 | 121.3238 | 121.3041 | -0.22825 | 0.065083 | 0.11782 | 0.1292 | 0.023603 | -0.04148 | -0.15324 | -0.28114 | 0.01894 | -0.23155 | 0.20245 | 0.05348 | 0.03454 | -0.011059 | -0.03075 | 121.6999 | 121.4288 | 121.3009 | 2.9179 | -121.5169 | 121.3505 | 121.571 | 121.5513 | 10.7145 | -121.5631
1198.8438 | 121.7285 | -0.23346 | 121.3394 | 1.4211e-13 | -0.024013 | -0.0013783 | 0.06353 | -0.004346 | 0.057537 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.063631 | 0.012233 | 0.05971 | -0.12257 | 2.6845 | -0.21901 | 121.4481 | 121.1816 | 121.0445 | -0.19127 | -0.063054 | 10.394 | -0.19829 | 121.1124 | 121.3238 | 121.3041 | -0.22825 | 0.042192 | 0.10867 | 0.11089 | 0.014449 | -0.027743 | -0.15782 | -0.29487 | 0.005207 | -0.22697 | 0.17041 | 0.035168 | 0.029961 | -0.015637 | -0.035328 | 121.6815 | 121.4151 | 121.278 | 2.9179 | -121.5307 | 121.3459 | 121.5572 | 121.5375 | 10.6275 | -121.5677
1200.5625 | 121.7239 | -0.2243 | 121.3348 | 1.4211e-13 | -0.024013 | -0.0013783 | 0.06353 | -0.004346 | 0.057324 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.01266 | 0.059923 | -0.11341 | 2.6799 | -0.21901 | 121.4527 | 121.1816 | 121.0491 | -0.18669 | -0.058476 | 10.4536 | -0.19829 | 121.1124 | 121.3284 | 121.3087 | -0.22825 | 0.037616 | 0.11782 | 0.11089 | 0.005294 | -0.032322 | -0.15324 | -0.28572 | -0.003948 | -0.22239 | 0.16583 | 0.026013 | 0.029961 | -0.00648 | -0.026172 | 121.677 | 121.4059 | 121.2734 | 2.9042 | -121.5215 | 121.3368 | 121.5527 | 121.533 | 10.6779 | -121.5631
1202.3281 | 121.7239 | -0.25177 | 121.376 | 1.4211e-13 | -0.023799 | -0.00073712 | 0.06353 | -0.004346 | 0.057537 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063631 | 0.012446 | 0.059923 | -0.10883 | 2.6799 | -0.21443 | 121.4618 | 121.1816 | 121.0491 | -0.18669 | -0.049318 | 10.4536 | -0.19829 | 121.117 | 121.3284 | 121.3041 | -0.2191 | 0.065082 | 0.085779 | 0.14294 | 0.037338 | -0.027744 | -0.19444 | -0.32691 | 0.032675 | -0.25901 | 0.20245 | 0.053479 | 0.020804 | -0.047679 | -0.071949 | 121.7136 | 121.4334 | 121.3009 | 2.9317 | -121.5627 | 121.3688 | 121.5801 | 121.5559 | 10.7053 | -121.5951
1204.0938 | 121.6919 | -0.23804 | 121.3623 | 1.4211e-13 | -0.024226 | -0.00095092 | 0.063103 | -0.004346 | 0.057537 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063844 | 0.012019 | 0.059923 | -0.10883 | 2.6753 | -0.21901 | 121.4572 | 121.1862 | 121.0491 | -0.18669 | -0.049318 | 10.4032 | -0.18913 | 121.1124 | 121.3284 | 121.3087 | -0.2191 | 0.051349 | 0.094934 | 0.1292 | 0.019027 | -0.032322 | -0.17613 | -0.31318 | 0.018942 | -0.24986 | 0.18872 | 0.048903 | 0.029961 | -0.033946 | -0.053638 | 121.6953 | 121.4242 | 121.2872 | 2.9133 | -121.549 | 121.3505 | 121.5664 | 121.5467 | 10.6412 | -121.5814
1205.7969 | 121.6049 | -0.27924 | 121.3852 | 1.4211e-13 | -0.024013 | -0.0011645 | 0.06353 | -0.004346 | 0.057537 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.012233 | 0.05971 | -0.10426 | 2.6799 | -0.21443 | 121.4618 | 121.1953 | 121.0629 | -0.18669 | -0.049318 | 10.3803 | -0.19371 | 121.1124 | 121.3375 | 121.3132 | -0.2191 | 0.092548 | 0.076624 | 0.17498 | 0.064804 | -0.027744 | -0.18986 | -0.32233 | 0.060141 | -0.27274 | 0.22992 | 0.085524 | 0.025383 | -0.047677 | -0.071947 | 121.7411 | 121.4746 | 121.3421 | 2.9591 | -121.5719 | 121.3917 | 121.6168 | 121.5925 | 10.6595 | -121.6043
1207.5469 | 121.669 | -0.27008 | 121.3989 | 1.4211e-13 | -0.024226 | -0.0015919 | 0.06353 | -0.004346 | 0.057751 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.012233 | 0.059923 | -0.10883 | 2.6936 | -0.21443 | 121.4618 | 121.1999 | 121.0537 | -0.17753 | -0.049318 | 10.4398 | -0.19829 | 121.117 | 121.3238 | 121.3087 | -0.22825 | 0.092551 | 0.062891 | 0.16125 | 0.055649 | -0.036902 | -0.19901 | -0.34522 | 0.041829 | -0.2819 | 0.22076 | 0.07179 | 0.029961 | -0.075146 | -0.090259 | 121.7319 | 121.47 | 121.3238 | 2.9637 | -121.5765 | 121.3871 | 121.5939 | 121.5787 | 10.7099 | -121.6272
1209.3281 | 121.7789 | -0.2243 | 121.3486 | 1.4211e-13 | -0.024226 | -0.00073712 | 0.06353 | -0.0041322 | 0.057324 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063417 | 0.012233 | 0.059923 | -0.11341 | 2.689 | -0.21901 | 121.4618 | 121.1908 | 121.0537 | -0.18669 | -0.053897 | 10.4169 | -0.18913 | 121.117 | 121.3284 | 121.3132 | -0.22367 | 0.037616 | 0.11324 | 0.11089 | 0.005294 | -0.032322 | -0.15782 | -0.29487 | 0.000631 | -0.23154 | 0.17041 | 0.03517 | 0.034539 | -0.020213 | -0.035326 | 121.6861 | 121.4151 | 121.278 | 2.9133 | -121.5353 | 121.3413 | 121.5527 | 121.5376 | 10.6412 | -121.5722
1211.0312 | 121.6782 | -0.24719 | 121.3715 | 1.4211e-13 | -0.024013 | -0.0013783 | 0.063316 | -0.004346 | 0.057324 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.012233 | 0.060137 | -0.10426 | 2.6982 | -0.20985 | 121.4618 | 121.1908 | 121.0583 | -0.18211 | -0.049318 | 10.4719 | -0.19371 | 121.1216 | 121.3284 | 121.3132 | -0.21452 | 0.065083 | 0.090357 | 0.14294 | 0.037338 | -0.027745 | -0.18071 | -0.31318 | 0.032676 | -0.24985 | 0.19787 | 0.05348 | 0.020804 | -0.043101 | -0.058214 | 121.709 | 121.4379 | 121.3055 | 2.9454 | -121.5536 | 121.3688 | 121.5756 | 121.5604 | 10.7191 | -121.586
1212.7969 | 121.7285 | -0.2243 | 121.344 | 1.4211e-13 | -0.024013 | -0.0011645 | 0.06353 | -0.004346 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.01266 | 0.059923 | -0.11341 | 2.7119 | -0.20528 | 121.4664 | 121.1908 | 121.0583 | -0.17753 | -0.044739 | 10.4169 | -0.19371 | 121.1216 | 121.3284 | 121.3132 | -0.2191 | 0.046774 | 0.1224 | 0.11089 | 0.019029 | -0.027745 | -0.15324 | -0.28571 | 0.005209 | -0.22239 | 0.17957 | 0.030592 | 0.025383 | -0.015635 | -0.030748 | 121.6907 | 121.4151 | 121.2826 | 2.9362 | -121.5215 | 121.3459 | 121.5527 | 121.5376 | 10.6412 | -121.5631
1214.5 | 121.7422 | -0.21973 | 121.3623 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.063316 | -0.0041322 | 0.057537 | -0.01755 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.012446 | 0.059923 | -0.10883 | 2.7074 | -0.21443 | 121.4618 | 121.1862 | 121.0583 | -0.18669 | -0.053897 | 10.4444 | -0.17998 | 121.1216 | 121.3329 | 121.3178 | -0.22367 | 0.033039 | 0.099512 | 0.11089 | 0.005295 | -0.027744 | -0.17613 | -0.30403 | -0.003946 | -0.2407 | 0.16583 | 0.039751 | 0.043697 | -0.029368 | -0.044481 | 121.6815 | 121.4059 | 121.278 | 2.9271 | -121.549 | 121.3413 | 121.5527 | 121.5376 | 10.6641 | -121.586
1216.2656 | 121.6736 | -0.27924 | 121.3669 | 1.4211e-13 | -0.024226 | -0.00095092 | 0.06353 | -0.0045596 | 0.057751 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.012446 | 0.05971 | -0.10883 | 2.7119 | -0.21443 | 121.4572 | 121.1953 | 121.0629 | -0.17753 | -0.053897 | 10.4444 | -0.18913 | 121.117 | 121.3284 | 121.3087 | -0.22367 | 0.10171 | 0.090357 | 0.1704 | 0.064804 | -0.036902 | -0.17155 | -0.30402 | 0.055563 | -0.24985 | 0.22534 | 0.090102 | 0.034539 | -0.038523 | -0.058215 | 121.7365 | 121.4746 | 121.3421 | 2.9912 | -121.5444 | 121.3963 | 121.6076 | 121.5879 | 10.7236 | -121.5906
1217.9688 | 121.7056 | -0.26093 | 121.3623 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.063316 | -0.004346 | 0.057537 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.012446 | 0.059923 | -0.10883 | 2.7119 | -0.21443 | 121.4572 | 121.1953 | 121.0629 | -0.18669 | -0.040161 | 10.4444 | -0.18913 | 121.1216 | 121.3284 | 121.3178 | -0.20994 | 0.074237 | 0.094934 | 0.15209 | 0.046493 | -0.027744 | -0.16697 | -0.29945 | 0.050988 | -0.2407 | 0.22076 | 0.071791 | 0.020803 | -0.033946 | -0.044481 | 121.7182 | 121.4563 | 121.3238 | 2.9729 | -121.549 | 121.3825 | 121.5893 | 121.5787 | 10.7053 | -121.5722
1219.7344 | 121.7056 | -0.2655 | 121.3623 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.06353 | -0.0039186 | 0.057537 | -0.0099194 | -8.1262e-05 | 0.00037167 | 0.063844 | 0.012446 | 0.059923 | -0.099677 | 2.7303 | -0.21443 | 121.4572 | 121.1953 | 121.0629 | -0.18669 | -0.044739 | 10.4398 | -0.19829 | 121.117 | 121.3284 | 121.3087 | -0.21452 | 0.078815 | 0.094934 | 0.16583 | 0.051071 | -0.027744 | -0.16697 | -0.29945 | 0.050987 | -0.24528 | 0.22076 | 0.067212 | 0.016225 | -0.033946 | -0.053638 | 121.7227 | 121.4608 | 121.3284 | 2.9958 | -121.549 | 121.3825 | 121.5939 | 121.5742 | 10.7053 | -121.5768
1221.4844 | 121.701 | -0.25635 | 121.3394 | 1.4211e-13 | -0.024013 | -0.0013783 | 0.063103 | -0.0045596 | 0.057324 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.012446 | 0.05971 | -0.10883 | 2.7303 | -0.21443 | 121.4664 | 121.1908 | 121.0629 | -0.18669 | -0.049318 | 10.4398 | -0.18913 | 121.1262 | 121.3284 | 121.3087 | -0.21452 | 0.06966 | 0.12698 | 0.14751 | 0.041916 | -0.027744 | -0.14866 | -0.27656 | 0.041832 | -0.21323 | 0.20703 | 0.067214 | 0.025382 | -0.011058 | -0.03075 | 121.7227 | 121.4471 | 121.3192 | 2.9866 | -121.5261 | 121.3825 | 121.5847 | 121.565 | 10.6962 | -121.5539
1223.1875 | 121.6827 | -0.24719 | 121.3623 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.063103 | -0.0045596 | 0.057324 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.012446 | 0.059923 | -0.10426 | 2.7303 | -0.20528 | 121.4572 | 121.1953 | 121.0629 | -0.18211 | -0.040161 | 10.4902 | -0.18913 | 121.1216 | 121.3329 | 121.3178 | -0.21452 | 0.065083 | 0.094934 | 0.14294 | 0.041917 | -0.023166 | -0.16697 | -0.29945 | 0.032676 | -0.2407 | 0.20703 | 0.058058 | 0.025382 | -0.029368 | -0.044481 | 121.7044 | 121.4425 | 121.3101 | 2.9774 | -121.5444 | 121.3688 | 121.5801 | 121.565 | 10.7374 | -121.5768
1224.9688 | 121.6736 | -0.25177 | 121.3531 | 1.4211e-13 | -0.02444 | -0.0011645 | 0.063103 | -0.0045596 | 0.057537 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.012233 | 0.059496 | -0.10883 | 2.744 | -0.21443 | 121.4664 | 121.1999 | 121.0583 | -0.18211 | -0.049318 | 10.3986 | -0.18913 | 121.1216 | 121.3375 | 121.3132 | -0.21452 | 0.069661 | 0.11325 | 0.14294 | 0.037338 | -0.032323 | -0.15324 | -0.29487 | 0.037254 | -0.23154 | 0.20245 | 0.062636 | 0.025382 | -0.015633 | -0.039903 | 121.7182 | 121.4517 | 121.31 | 2.9958 | -121.5353 | 121.3734 | 121.5893 | 121.565 | 10.6504 | -121.5677
1226.7188 | 121.7606 | -0.24719 | 121.3303 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.06353 | -0.004346 | 0.057324 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063844 | 0.012233 | 0.05971 | -0.10883 | 2.7348 | -0.20528 | 121.4618 | 121.2045 | 121.0674 | -0.18669 | -0.049318 | 10.4215 | -0.18913 | 121.1308 | 121.3375 | 121.3132 | -0.22367 | 0.060504 | 0.13156 | 0.13836 | 0.041917 | -0.018587 | -0.12577 | -0.26282 | 0.023519 | -0.1995 | 0.19787 | 0.058058 | 0.034539 | 0.007255 | -0.017015 | 121.709 | 121.4517 | 121.3146 | 2.982 | -121.5169 | 121.378 | 121.5847 | 121.5604 | 10.6687 | -121.5539
1228.4688 | 121.701 | -0.24719 | 121.3623 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.063103 | -0.0045596 | 0.057537 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063417 | 0.012233 | 0.059496 | -0.10426 | 2.744 | -0.20985 | 121.4618 | 121.1953 | 121.0674 | -0.17753 | -0.049318 | 10.4261 | -0.19371 | 121.1262 | 121.3421 | 121.3178 | -0.20994 | 0.069662 | 0.099512 | 0.14294 | 0.037338 | -0.032324 | -0.16697 | -0.29487 | 0.037255 | -0.23612 | 0.19787 | 0.05348 | 0.016225 | -0.02021 | -0.044481 | 121.709 | 121.4425 | 121.3146 | 2.9912 | -121.5398 | 121.3734 | 121.5893 | 121.565 | 10.6733 | -121.5722
1230.25 | 121.6965 | -0.2243 | 121.3394 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.063316 | -0.0041322 | 0.057324 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.01266 | 0.05971 | -0.10426 | 2.7486 | -0.20528 | 121.471 | 121.2045 | 121.0674 | -0.16837 | -0.044739 | 10.4398 | -0.18913 | 121.1262 | 121.3421 | 121.3178 | -0.21452 | 0.055931 | 0.13156 | 0.12005 | 0.019029 | -0.036902 | -0.13492 | -0.27198 | 0.009788 | -0.21323 | 0.17957 | 0.03517 | 0.025382 | 0.002678 | -0.021593 | 121.6953 | 121.4288 | 121.2917 | 2.9729 | -121.5078 | 121.3505 | 121.5664 | 121.5421 | 10.6641 | -121.5539
1232 | 121.6049 | -0.28839 | 121.3898 | 1.4211e-13 | -0.02444 | -0.00095092 | 0.06353 | -0.0045596 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.012446 | 0.05971 | -0.10426 | 2.744 | -0.20528 | 121.4572 | 121.2045 | 121.0674 | -0.18211 | -0.044739 | 10.4398 | -0.19371 | 121.1262 | 121.3375 | 121.3178 | -0.2191 | 0.10628 | 0.067468 | 0.18414 | 0.083116 | -0.023166 | -0.18528 | -0.32233 | 0.069296 | -0.26359 | 0.24365 | 0.094679 | 0.025383 | -0.052255 | -0.071947 | 121.7456 | 121.4929 | 121.3558 | 3.0324 | -121.5719 | 121.4146 | 121.6259 | 121.6062 | 10.7282 | -121.6089
1233.7031 | 121.7743 | -0.24261 | 121.3303 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.06353 | -0.004346 | 0.057324 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.012874 | 0.059923 | -0.099677 | 2.744 | -0.21901 | 121.4618 | 121.1953 | 121.0674 | -0.17753 | -0.049318 | 10.4581 | -0.19371 | 121.1216 | 121.3375 | 121.3178 | -0.20994 | 0.065085 | 0.13156 | 0.14294 | 0.023605 | -0.04148 | -0.13493 | -0.26282 | 0.032678 | -0.20865 | 0.1933 | 0.048903 | 0.016225 | 0.007255 | -0.012437 | 121.7044 | 121.4379 | 121.3101 | 2.9866 | -121.5078 | 121.3642 | 121.5801 | 121.5604 | 10.7007 | -121.5402
1235.4688 | 121.7606 | -0.22888 | 121.3531 | 1.4211e-13 | -0.024226 | -0.0011645 | 0.06353 | -0.004346 | 0.057324 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063631 | 0.012019 | 0.060137 | -0.10883 | 2.7531 | -0.20985 | 121.4664 | 121.1953 | 121.0629 | -0.17753 | -0.044739 | 10.4719 | -0.18913 | 121.1262 | 121.3375 | 121.3224 | -0.21452 | 0.051352 | 0.11325 | 0.12005 | 0.019028 | -0.032324 | -0.15781 | -0.29029 | 0.014366 | -0.22696 | 0.18414 | 0.039748 | 0.025382 | -0.015633 | -0.030746 | 121.6953 | 121.4242 | 121.2917 | 2.982 | -121.5307 | 121.3551 | 121.5664 | 121.5513 | 10.7008 | -121.5677
1237.1719 | 121.6095 | -0.27008 | 121.4172 | 1.4211e-13 | -0.02444 | -0.00095092 | 0.063103 | -0.004346 | 0.057537 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063631 | 0.012446 | 0.059923 | -0.10883 | 2.7348 | -0.20985 | 121.4664 | 121.2091 | 121.072 | -0.17753 | -0.049318 | 10.4993 | -0.18913 | 121.1262 | 121.3375 | 121.3178 | -0.20536 | 0.092551 | 0.049159 | 0.16125 | 0.060227 | -0.032324 | -0.20817 | -0.34522 | 0.064723 | -0.29105 | 0.22076 | 0.080947 | 0.016224 | -0.07972 | -0.099412 | 121.7365 | 121.4792 | 121.3421 | 3.0049 | -121.5948 | 121.3963 | 121.6076 | 121.5879 | 10.7694 | -121.6226
1238.9375 | 121.701 | -0.24261 | 121.3623 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.063316 | -0.0041322 | 0.057324 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063417 | 0.01266 | 0.05971 | -0.10426 | 2.744 | -0.21901 | 121.471 | 121.1999 | 121.0766 | -0.17753 | -0.040161 | 10.5177 | -0.18913 | 121.1262 | 121.3238 | 121.327 | -0.21452 | 0.065085 | 0.10867 | 0.13836 | 0.023605 | -0.04148 | -0.16239 | -0.28571 | 0.028099 | -0.23612 | 0.20245 | 0.053481 | 0.025382 | -0.038525 | -0.035323 | 121.7136 | 121.4425 | 121.3192 | 2.9866 | -121.5398 | 121.3688 | 121.5664 | 121.5696 | 10.7603 | -121.5768
1240.7188 | 121.5958 | -0.28839 | 121.3943 | 1.4211e-13 | -0.02444 | -0.0011645 | 0.06353 | -0.0041322 | 0.057324 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063631 | 0.012446 | 0.059496 | -0.10426 | 2.7303 | -0.20985 | 121.4664 | 121.2045 | 121.0674 | -0.17753 | -0.044739 | 10.5314 | -0.18913 | 121.1216 | 121.3375 | 121.3178 | -0.2191 | 0.11086 | 0.072047 | 0.18414 | 0.078537 | -0.032324 | -0.18986 | -0.32691 | 0.069296 | -0.27274 | 0.24365 | 0.099257 | 0.029961 | -0.056832 | -0.076524 | 121.7548 | 121.4929 | 121.3558 | 3.0186 | -121.5719 | 121.41 | 121.6259 | 121.6062 | 10.8198 | -121.6134
1242.4375 | 121.7239 | -0.25177 | 121.3531 | 1.4211e-13 | -0.024654 | -0.00095092 | 0.063316 | -0.004346 | 0.056896 | -0.0099194 | 0.00055974 | -0.00026913 | 0.063844 | 0.012446 | 0.05971 | -0.10426 | 2.7394 | -0.21901 | 121.4572 | 121.2045 | 121.072 | -0.17753 | -0.049318 | 10.5634 | -0.18913 | 121.1308 | 121.3284 | 121.3132 | -0.2191 | 0.07424 | 0.10409 | 0.14752 | 0.03276 | -0.04148 | -0.14866 | -0.28113 | 0.032675 | -0.22239 | 0.20245 | 0.062636 | 0.029961 | -0.02479 | -0.039903 | 121.709 | 121.4563 | 121.3238 | 2.9912 | -121.5307 | 121.3825 | 121.5801 | 121.565 | 10.8152 | -121.5722
1244.2031 | 121.6507 | -0.27008 | 121.3943 | 1.4211e-13 | -0.02444 | -0.00095092 | 0.063316 | -0.0045596 | 0.057324 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.01266 | 0.060137 | -0.099677 | 2.744 | -0.2007 | 121.471 | 121.2045 | 121.0766 | -0.17753 | -0.040161 | 10.5085 | -0.18913 | 121.1308 | 121.3284 | 121.327 | -0.21452 | 0.092551 | 0.076626 | 0.1704 | 0.069384 | -0.023167 | -0.18986 | -0.31775 | 0.055565 | -0.26358 | 0.22992 | 0.080947 | 0.025382 | -0.065989 | -0.067366 | 121.7411 | 121.4746 | 121.3467 | 3.0141 | -121.5719 | 121.4008 | 121.5984 | 121.5971 | 10.7786 | -121.6089
1245.9688 | 121.5912 | -0.25635 | 121.4081 | 1.4211e-13 | -0.02444 | -0.0011645 | 0.063103 | -0.0045596 | 0.057324 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063203 | 0.012446 | 0.059923 | -0.10883 | 2.744 | -0.20985 | 121.4664 | 121.1999 | 121.072 | -0.17295 | -0.044739 | 10.5314 | -0.18913 | 121.1262 | 121.3284 | 121.3224 | -0.20994 | 0.083397 | 0.058314 | 0.14751 | 0.046494 | -0.036903 | -0.20817 | -0.33606 | 0.046411 | -0.2819 | 0.21161 | 0.067214 | 0.020803 | -0.079722 | -0.085678 | 121.7227 | 121.4563 | 121.3284 | 3.0003 | -121.581 | 121.3825 | 121.5847 | 121.5788 | 10.7877 | -121.618
1247.7188 | 121.6232 | -0.2655 | 121.4035 | 1.4211e-13 | -0.024654 | -0.0011645 | 0.063316 | -0.0041322 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.012446 | 0.059496 | -0.099677 | 2.7623 | -0.21443 | 121.4664 | 121.2091 | 121.072 | -0.17295 | -0.040161 | 10.4856 | -0.18913 | 121.1308 | 121.3284 | 121.327 | -0.21452 | 0.092552 | 0.062892 | 0.16583 | 0.051071 | -0.041481 | -0.19443 | -0.33149 | 0.050987 | -0.27274 | 0.22534 | 0.076369 | 0.025382 | -0.075144 | -0.076521 | 121.7319 | 121.4746 | 121.3375 | 3.0278 | -121.5765 | 121.3963 | 121.5939 | 121.5925 | 10.7511 | -121.618
1249.4219 | 121.7697 | -0.22888 | 121.3531 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.06353 | -0.0045596 | 0.05711 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063417 | 0.01266 | 0.059496 | -0.10883 | 2.7715 | -0.20528 | 121.471 | 121.2045 | 121.072 | -0.18211 | -0.049318 | 10.5222 | -0.18913 | 121.1399 | 121.3329 | 121.3224 | -0.20994 | 0.046773 | 0.11782 | 0.12005 | 0.023607 | -0.023166 | -0.14866 | -0.28113 | 0.018945 | -0.21323 | 0.17956 | 0.039748 | 0.020803 | -0.020212 | -0.030746 | 121.6999 | 121.4334 | 121.3009 | 3.0003 | -121.5353 | 121.3688 | 121.5618 | 121.5513 | 10.7511 | -121.5631
1251.2031 | 121.6736 | -0.2655 | 121.4081 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.063316 | -0.0045596 | 0.057537 | 0.0053411 | 0.00055974 | 0.00037167 | 0.063631 | 0.01266 | 0.060137 | -0.099677 | 2.7852 | -0.21443 | 121.471 | 121.2045 | 121.0858 | -0.17295 | -0.044739 | 10.5314 | -0.18913 | 121.1262 | 121.3284 | 121.3224 | -0.20994 | 0.092552 | 0.062893 | 0.16583 | 0.051071 | -0.041481 | -0.20359 | -0.32233 | 0.055566 | -0.2819 | 0.22076 | 0.076369 | 0.020803 | -0.079722 | -0.085678 | 121.7365 | 121.47 | 121.3513 | 3.0507 | -121.581 | 121.3917 | 121.5939 | 121.5879 | 10.7969 | -121.618
1252.9688 | 121.7285 | -0.23346 | 121.3806 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.06353 | -0.0045596 | 0.057537 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063844 | 0.01266 | 0.05971 | -0.10883 | 2.7944 | -0.20528 | 121.4572 | 121.1999 | 121.0812 | -0.17753 | -0.049318 | 10.5314 | -0.18455 | 121.1308 | 121.3421 | 121.327 | -0.2191 | 0.055929 | 0.076624 | 0.12462 | 0.028184 | -0.027745 | -0.1807 | -0.29944 | 0.014364 | -0.24985 | 0.18414 | 0.048904 | 0.03454 | -0.03852 | -0.053633 | 121.6907 | 121.4334 | 121.3146 | 3.0278 | -121.5581 | 121.3642 | 121.5756 | 121.5604 | 10.7649 | -121.5997
1254.75 | 121.5912 | -0.27466 | 121.4172 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.06353 | -0.004346 | 0.057537 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063631 | 0.01266 | 0.059923 | -0.095099 | 2.7944 | -0.2007 | 121.4664 | 121.2182 | 121.0812 | -0.17753 | -0.044739 | 10.5177 | -0.18913 | 121.1399 | 121.3421 | 121.327 | -0.20994 | 0.097128 | 0.049159 | 0.17956 | 0.073961 | -0.023167 | -0.19901 | -0.33606 | 0.064721 | -0.27732 | 0.22992 | 0.085524 | 0.020803 | -0.075141 | -0.090254 | 121.7411 | 121.4929 | 121.3558 | 3.069 | -121.5948 | 121.4146 | 121.6168 | 121.6016 | 10.7923 | -121.6272
1256.5156 | 121.7194 | -0.25177 | 121.376 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.063316 | -0.004346 | 0.057537 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063631 | 0.012446 | 0.05971 | -0.10883 | 2.7989 | -0.21443 | 121.471 | 121.2091 | 121.0766 | -0.18211 | -0.040161 | 10.5405 | -0.18455 | 121.1399 | 121.3375 | 121.3178 | -0.21452 | 0.069661 | 0.094936 | 0.14294 | 0.037338 | -0.032323 | -0.16697 | -0.29944 | 0.037254 | -0.23612 | 0.21161 | 0.067215 | 0.029961 | -0.038522 | -0.058214 | 121.7227 | 121.4608 | 121.3284 | 3.0507 | -121.5581 | 121.3917 | 121.5893 | 121.5696 | 10.7923 | -121.5906
1258.2188 | 121.6919 | -0.25177 | 121.376 | 1.4211e-13 | -0.02444 | -0.00095092 | 0.063316 | -0.0047732 | 0.056896 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.063844 | 0.012446 | 0.059923 | -0.099677 | 2.7898 | -0.2007 | 121.4756 | 121.2091 | 121.0812 | -0.17753 | -0.044739 | 10.4856 | -0.18913 | 121.1308 | 121.3375 | 121.3316 | -0.20994 | 0.07424 | 0.099514 | 0.15209 | 0.051073 | -0.023167 | -0.16697 | -0.29486 | 0.041833 | -0.24527 | 0.20703 | 0.062636 | 0.020803 | -0.038522 | -0.044478 | 121.7273 | 121.4608 | 121.3329 | 3.0415 | -121.5536 | 121.3825 | 121.5893 | 121.5833 | 10.7374 | -121.586
1259.9844 | 121.6644 | -0.25177 | 121.4081 | 1.4211e-13 | -0.024654 | -0.00073712 | 0.063316 | -0.0045596 | 0.057751 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.012874 | 0.059923 | -0.099677 | 2.7989 | -0.20985 | 121.4618 | 121.2136 | 121.0812 | -0.17753 | -0.044739 | 10.536 | -0.17998 | 121.1445 | 121.3329 | 121.3361 | -0.21452 | 0.07424 | 0.053736 | 0.15209 | 0.041916 | -0.032324 | -0.19443 | -0.32691 | 0.037254 | -0.26358 | 0.20703 | 0.071794 | 0.03454 | -0.075144 | -0.071942 | 121.7136 | 121.4654 | 121.3329 | 3.0507 | -121.5856 | 121.3963 | 121.5847 | 121.5879 | 10.7877 | -121.6226
1261.6719 | 121.7056 | -0.23804 | 121.3806 | 1.4211e-13 | -0.024867 | -0.00095092 | 0.063316 | -0.0045596 | 0.057324 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063417 | 0.01266 | 0.05971 | -0.099677 | 2.7898 | -0.20985 | 121.4801 | 121.2091 | 121.0858 | -0.16837 | -0.035582 | 10.5543 | -0.17998 | 121.1353 | 121.3375 | 121.327 | -0.20536 | 0.069664 | 0.099516 | 0.13836 | 0.028183 | -0.041481 | -0.17154 | -0.29486 | 0.032679 | -0.24527 | 0.20245 | 0.058061 | 0.025382 | -0.043099 | -0.053633 | 121.7182 | 121.4471 | 121.3238 | 3.0278 | -121.549 | 121.3734 | 121.5756 | 121.565 | 10.7923 | -121.586
1263.4375 | 121.6965 | -0.22888 | 121.3898 | 1.4211e-13 | -0.02444 | -0.0011645 | 0.063316 | -0.004346 | 0.05711 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063203 | 0.01266 | 0.059923 | -0.099677 | 2.7852 | -0.2007 | 121.4756 | 121.2136 | 121.0858 | -0.18211 | -0.040161 | 10.5177 | -0.18455 | 121.1353 | 121.3375 | 121.3224 | -0.20536 | 0.046773 | 0.085781 | 0.12921 | 0.028185 | -0.018588 | -0.17612 | -0.30402 | 0.023524 | -0.25443 | 0.18872 | 0.044327 | 0.020803 | -0.052255 | -0.067368 | 121.7044 | 121.4425 | 121.3146 | 3.0141 | -121.5719 | 121.3642 | 121.5664 | 121.5513 | 10.7465 | -121.5951
1265.2188 | 121.6415 | -0.27008 | 121.4035 | 1.4211e-13 | -0.02444 | -0.00095092 | 0.063316 | -0.0045596 | 0.057537 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063203 | 0.01266 | 0.059923 | -0.09052 | 2.7989 | -0.20528 | 121.471 | 121.2091 | 121.0949 | -0.17295 | -0.031003 | 10.5955 | -0.17998 | 121.1399 | 121.3375 | 121.3316 | -0.20994 | 0.09713 | 0.067471 | 0.17956 | 0.064806 | -0.032324 | -0.19443 | -0.30859 | 0.060144 | -0.26358 | 0.23908 | 0.090105 | 0.029961 | -0.065987 | -0.071943 | 121.7411 | 121.4792 | 121.365 | 3.069 | -121.5765 | 121.41 | 121.6076 | 121.6016 | 10.8656 | -121.6134
1266.9844 | 121.7377 | -0.23804 | 121.3898 | 1.4211e-13 | -0.024226 | -0.00095092 | 0.063316 | -0.0045596 | 0.057537 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063631 | 0.012233 | 0.059923 | -0.099677 | 2.7989 | -0.19612 | 121.4756 | 121.2091 | 121.0903 | -0.18211 | -0.035582 | 10.5222 | -0.18455 | 121.1399 | 121.3467 | 121.3224 | -0.21452 | 0.055928 | 0.085781 | 0.13836 | 0.041918 | -0.01401 | -0.1807 | -0.29944 | 0.023521 | -0.24985 | 0.20245 | 0.053482 | 0.029961 | -0.043098 | -0.067368 | 121.7136 | 121.4471 | 121.3284 | 3.037 | -121.5719 | 121.378 | 121.5847 | 121.5604 | 10.7603 | -121.6043
1268.6875 | 121.7514 | -0.24719 | 121.3486 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.06353 | -0.004346 | 0.05711 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063631 | 0.012446 | 0.059496 | -0.099677 | 2.8218 | -0.2007 | 121.4618 | 121.2136 | 121.0903 | -0.16837 | -0.040161 | 10.5222 | -0.17998 | 121.1353 | 121.3513 | 121.3224 | -0.20536 | 0.078819 | 0.11324 | 0.14752 | 0.046495 | -0.032324 | -0.13492 | -0.25824 | 0.041834 | -0.21323 | 0.20703 | 0.067216 | 0.025382 | 0.00268 | -0.026169 | 121.709 | 121.4608 | 121.3375 | 3.069 | -121.5169 | 121.3825 | 121.5984 | 121.5696 | 10.7694 | -121.5539
1270.4688 | 121.7285 | -0.22888 | 121.3577 | 1.4211e-13 | -0.024654 | -0.0011645 | 0.062889 | -0.0045596 | 0.057537 | -0.0022889 | 0.00013254 | 0.00037167 | 0.063417 | 0.012874 | 0.059923 | -0.099677 | 2.7944 | -0.20528 | 121.4664 | 121.2182 | 121.0858 | -0.18211 | -0.044739 | 10.5405 | -0.18913 | 121.1353 | 121.3467 | 121.327 | -0.20536 | 0.046773 | 0.10867 | 0.12921 | 0.023607 | -0.023166 | -0.1395 | -0.27198 | 0.023524 | -0.22239 | 0.18414 | 0.039748 | 0.016224 | -0.011054 | -0.030745 | 121.6953 | 121.4471 | 121.3146 | 3.0232 | -121.5398 | 121.3642 | 121.5756 | 121.5559 | 10.7694 | -121.5631
1272.1719 | 121.7239 | -0.23804 | 121.376 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.063316 | -0.0045596 | 0.056896 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063203 | 0.012446 | 0.05971 | -0.09052 | 2.8035 | -0.20528 | 121.4756 | 121.2182 | 121.0903 | -0.17753 | -0.044739 | 10.4948 | -0.1754 | 121.1399 | 121.3421 | 121.3224 | -0.21452 | 0.060507 | 0.099514 | 0.14752 | 0.032762 | -0.027745 | -0.15781 | -0.28571 | 0.023521 | -0.23612 | 0.1933 | 0.062639 | 0.039118 | -0.033943 | -0.053635 | 121.7136 | 121.4563 | 121.3284 | 3.0415 | -121.5536 | 121.378 | 121.5801 | 121.5604 | 10.7328 | -121.5906
1273.9375 | 121.6553 | -0.27466 | 121.3989 | 1.4211e-13 | -0.024654 | -0.0013783 | 0.063103 | -0.0045596 | 0.05711 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063844 | 0.01266 | 0.060137 | -0.10426 | 2.7989 | -0.2007 | 121.4756 | 121.2136 | 121.0949 | -0.17753 | -0.044739 | 10.5177 | -0.17082 | 121.1353 | 121.3467 | 121.327 | -0.20994 | 0.097128 | 0.076626 | 0.1704 | 0.073961 | -0.023167 | -0.18528 | -0.30402 | 0.064721 | -0.26358 | 0.22992 | 0.10384 | 0.039118 | -0.052253 | -0.071944 | 121.7502 | 121.4883 | 121.3696 | 3.0736 | -121.5765 | 121.41 | 121.6213 | 121.6016 | 10.7923 | -121.6089
1275.7031 | 121.6873 | -0.2243 | 121.344 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.062889 | -0.0045596 | 0.05711 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.012874 | 0.05971 | -0.099677 | 2.8264 | -0.2007 | 121.471 | 121.2091 | 121.0858 | -0.17295 | -0.040161 | 10.5039 | -0.17998 | 121.1445 | 121.3513 | 121.327 | -0.21452 | 0.051353 | 0.12698 | 0.12463 | 0.023607 | -0.027746 | -0.13492 | -0.25824 | 0.009788 | -0.19949 | 0.18414 | 0.044328 | 0.03454 | 0.007258 | -0.017012 | 121.6953 | 121.4334 | 121.3101 | 3.0507 | -121.5169 | 121.3688 | 121.5756 | 121.5513 | 10.7282 | -121.5585
1277.4062 | 121.7194 | -0.21057 | 121.3577 | 1.4211e-13 | -0.024867 | -0.0015919 | 0.063103 | -0.0047732 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.012446 | 0.059923 | -0.099677 | 2.8264 | -0.19612 | 121.4801 | 121.2136 | 121.0903 | -0.17295 | -0.044739 | 10.4948 | -0.1754 | 121.1491 | 121.3467 | 121.3178 | -0.20994 | 0.03762 | 0.1224 | 0.11089 | 0.014452 | -0.023168 | -0.14408 | -0.2674 | 0.000634 | -0.20865 | 0.16583 | 0.035173 | 0.034539 | -0.011054 | -0.039903 | 121.6907 | 121.4242 | 121.3009 | 3.037 | -121.5307 | 121.3596 | 121.5572 | 121.5284 | 10.7053 | -121.5677
1279.1719 | 121.6049 | -0.27008 | 121.3989 | 1.4211e-13 | -0.024654 | -0.0011645 | 0.063316 | -0.0041322 | 0.05711 | -0.0099194 | 0.00034614 | 0.00037167 | 0.063631 | 0.013087 | 0.05971 | -0.09052 | 2.831 | -0.2007 | 121.4847 | 121.2136 | 121.0995 | -0.17753 | -0.035582 | 10.4902 | -0.1754 | 121.1445 | 121.3558 | 121.327 | -0.20994 | 0.092551 | 0.085783 | 0.17956 | 0.069384 | -0.023167 | -0.18528 | -0.29944 | 0.060144 | -0.25443 | 0.2345 | 0.094683 | 0.034539 | -0.043096 | -0.071944 | 121.7548 | 121.4837 | 121.3696 | 3.1011 | -121.5765 | 121.4146 | 121.6259 | 121.5971 | 10.7603 | -121.6089
1280.875 | 121.6644 | -0.27466 | 121.3715 | 1.4211e-13 | -0.025081 | -0.0013783 | 0.06353 | -0.0041322 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.01266 | 0.059923 | -0.09052 | 2.8356 | -0.2007 | 121.4801 | 121.2182 | 121.0949 | -0.17295 | -0.035582 | 10.5726 | -0.17082 | 121.1491 | 121.3467 | 121.327 | -0.21452 | 0.10171 | 0.10867 | 0.18414 | 0.073961 | -0.027746 | -0.15323 | -0.27655 | 0.060142 | -0.22238 | 0.23908 | 0.10384 | 0.043697 | -0.024787 | -0.044478 | 121.7548 | 121.4929 | 121.3696 | 3.1102 | -121.5444 | 121.4237 | 121.6213 | 121.6016 | 10.8473 | -121.586
1282.6406 | 121.7514 | -0.21973 | 121.3669 | 1.4211e-13 | -0.024867 | -0.0013783 | 0.06353 | -0.0045596 | 0.057324 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063631 | 0.012874 | 0.059923 | -0.099677 | 2.8356 | -0.19612 | 121.4801 | 121.2182 | 121.0903 | -0.17753 | -0.035582 | 10.5589 | -0.1754 | 121.1491 | 121.3513 | 121.3361 | -0.20536 | 0.042197 | 0.11325 | 0.12005 | 0.023608 | -0.018589 | -0.14865 | -0.27655 | 0.014369 | -0.2178 | 0.18415 | 0.044329 | 0.02996 | -0.01563 | -0.030743 | 121.6999 | 121.438 | 121.3101 | 3.0553 | -121.5444 | 121.3688 | 121.571 | 121.5559 | 10.7786 | -121.5722
1284.3906 | 121.7834 | -0.24261 | 121.3715 | 1.4211e-13 | -0.024867 | -0.00095092 | 0.063316 | -0.004346 | 0.056896 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.012446 | 0.059923 | -0.099677 | 2.831 | -0.20985 | 121.4801 | 121.2136 | 121.0949 | -0.16837 | -0.044739 | 10.5405 | -0.17998 | 121.1491 | 121.3467 | 121.3224 | -0.20994 | 0.074242 | 0.10867 | 0.14294 | 0.032761 | -0.041481 | -0.15781 | -0.27655 | 0.032678 | -0.22238 | 0.19788 | 0.062639 | 0.029961 | -0.024787 | -0.049057 | 121.7227 | 121.4563 | 121.3375 | 3.0736 | -121.5398 | 121.3917 | 121.5893 | 121.565 | 10.7832 | -121.5814
1286.0938 | 121.6232 | -0.25635 | 121.4218 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.063316 | -0.0041322 | 0.05711 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063417 | 0.012874 | 0.05971 | -0.095099 | 2.8264 | -0.19612 | 121.4801 | 121.2228 | 121.0949 | -0.17753 | -0.040161 | 10.536 | -0.17082 | 121.1445 | 121.3421 | 121.3316 | -0.20994 | 0.078818 | 0.058317 | 0.16125 | 0.060229 | -0.018589 | -0.19901 | -0.3269 | 0.046411 | -0.27732 | 0.21619 | 0.085529 | 0.039118 | -0.079719 | -0.090254 | 121.7365 | 121.4792 | 121.3513 | 3.0828 | -121.5993 | 121.4008 | 121.5984 | 121.5879 | 10.7923 | -121.6318
1287.8594 | 121.7422 | -0.21057 | 121.376 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.063103 | -0.004346 | 0.05711 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.012874 | 0.05971 | -0.09052 | 2.8127 | -0.2007 | 121.471 | 121.2182 | 121.1041 | -0.17753 | -0.040161 | 10.536 | -0.1754 | 121.1353 | 121.3421 | 121.327 | -0.20994 | 0.033041 | 0.094936 | 0.12005 | 0.009874 | -0.023167 | -0.15781 | -0.27197 | 0.000634 | -0.2407 | 0.17041 | 0.035173 | 0.034539 | -0.033943 | -0.049056 | 121.6815 | 121.4288 | 121.3146 | 3.0232 | -121.5536 | 121.3459 | 121.5527 | 121.5376 | 10.7465 | -121.586
1289.6094 | 121.6324 | -0.27008 | 121.4127 | 1.4211e-13 | -0.024867 | -0.0013783 | 0.06353 | -0.0041322 | 0.057324 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.01266 | 0.05971 | -0.099677 | 2.8264 | -0.2007 | 121.4756 | 121.2136 | 121.0949 | -0.17753 | -0.035582 | 10.5634 | -0.1754 | 121.1445 | 121.3467 | 121.327 | -0.20994 | 0.092551 | 0.062893 | 0.1704 | 0.069384 | -0.023167 | -0.19901 | -0.31775 | 0.060144 | -0.26816 | 0.2345 | 0.094683 | 0.034539 | -0.065986 | -0.085677 | 121.7456 | 121.4837 | 121.365 | 3.0965 | -121.5902 | 121.4146 | 121.6168 | 121.5971 | 10.8335 | -121.6226
1291.3125 | 121.7377 | -0.23804 | 121.3852 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063103 | -0.004346 | 0.05711 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063844 | 0.012874 | 0.060137 | -0.099677 | 2.8447 | -0.19612 | 121.4847 | 121.2228 | 121.0995 | -0.16837 | -0.035582 | 10.5726 | -0.1754 | 121.1399 | 121.3421 | 121.3224 | -0.20536 | 0.069664 | 0.099516 | 0.13836 | 0.041918 | -0.027746 | -0.16239 | -0.28571 | 0.032679 | -0.24527 | 0.20245 | 0.062639 | 0.02996 | -0.043098 | -0.06279 | 121.7227 | 121.4608 | 121.3375 | 3.0828 | -121.5536 | 121.378 | 121.5801 | 121.5604 | 10.8106 | -121.5906
1293.0781 | 121.6644 | -0.25635 | 121.4127 | 1.4211e-13 | -0.025081 | -0.0015919 | 0.06353 | -0.0047732 | 0.05711 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.01266 | 0.05971 | -0.095099 | 2.8493 | -0.19612 | 121.4801 | 121.2136 | 121.0949 | -0.17295 | -0.031003 | 10.623 | -0.1754 | 121.1491 | 121.3421 | 121.3361 | -0.20536 | 0.083397 | 0.067472 | 0.16125 | 0.060229 | -0.023168 | -0.19901 | -0.31775 | 0.05099 | -0.26358 | 0.22535 | 0.08095 | 0.02996 | -0.070564 | -0.07652 | 121.7365 | 121.47 | 121.3513 | 3.1056 | -121.5856 | 121.4054 | 121.5984 | 121.5925 | 10.8793 | -121.618
1294.8281 | 121.6644 | -0.2655 | 121.4035 | 1.4211e-13 | -0.025081 | -0.00095092 | 0.063103 | -0.0045596 | 0.056896 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.01266 | 0.059923 | -0.09052 | 2.8585 | -0.2007 | 121.4893 | 121.2228 | 121.1041 | -0.17295 | -0.031003 | 10.5818 | -0.18455 | 121.1445 | 121.3467 | 121.3407 | -0.21452 | 0.092552 | 0.085784 | 0.17498 | 0.064806 | -0.027746 | -0.1807 | -0.29944 | 0.050987 | -0.259 | 0.2345 | 0.080948 | 0.029961 | -0.05683 | -0.062786 | 121.7548 | 121.4883 | 121.3696 | 3.124 | -121.5765 | 121.41 | 121.6122 | 121.6062 | 10.8473 | -121.618
1296.5938 | 121.6919 | -0.23346 | 121.3989 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063316 | -0.004987 | 0.057324 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.012874 | 0.059923 | -0.095099 | 2.8447 | -0.20528 | 121.4801 | 121.2274 | 121.1041 | -0.17753 | -0.035582 | 10.6504 | -0.17998 | 121.1491 | 121.3421 | 121.327 | -0.20536 | 0.055929 | 0.081205 | 0.13836 | 0.028184 | -0.027745 | -0.17154 | -0.29486 | 0.028101 | -0.24985 | 0.19788 | 0.053483 | 0.025382 | -0.056831 | -0.071944 | 121.7136 | 121.4608 | 121.3375 | 3.0782 | -121.5765 | 121.3825 | 121.5756 | 121.5604 | 10.8839 | -121.6043
1298.375 | 121.6278 | -0.2655 | 121.3943 | 1.4211e-13 | -0.024867 | -0.0013783 | 0.06353 | -0.004346 | 0.057324 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063631 | 0.01266 | 0.059923 | -0.09052 | 2.8447 | -0.19612 | 121.4801 | 121.2274 | 121.1132 | -0.17295 | -0.040161 | 10.5863 | -0.17082 | 121.1537 | 121.3513 | 121.3361 | -0.2191 | 0.092552 | 0.085783 | 0.17498 | 0.069384 | -0.023168 | -0.16696 | -0.28112 | 0.046408 | -0.24069 | 0.22534 | 0.094684 | 0.048276 | -0.043096 | -0.058209 | 121.7456 | 121.4929 | 121.3787 | 3.1102 | -121.5673 | 121.4192 | 121.6168 | 121.6016 | 10.8518 | -121.6134
1300.0781 | 121.7377 | -0.23804 | 121.3806 | 1.4211e-13 | -0.025081 | -0.0013783 | 0.063316 | -0.0047732 | 0.05711 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.013087 | 0.059923 | -0.095099 | 2.8676 | -0.19154 | 121.4801 | 121.2182 | 121.1041 | -0.17295 | -0.035582 | 10.6047 | -0.1754 | 121.1582 | 121.3558 | 121.3361 | -0.20078 | 0.065086 | 0.099516 | 0.14294 | 0.046496 | -0.01859 | -0.16239 | -0.27655 | 0.037258 | -0.22238 | 0.20245 | 0.062639 | 0.025381 | -0.024785 | -0.044476 | 121.7182 | 121.4563 | 121.3421 | 3.1056 | -121.5536 | 121.3963 | 121.5939 | 121.5742 | 10.8427 | -121.5814
1301.8438 | 121.637 | -0.27008 | 121.3989 | 1.4211e-13 | -0.024654 | -0.0011645 | 0.063316 | -0.004346 | 0.057324 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063631 | 0.012874 | 0.05971 | -0.095099 | 2.8585 | -0.19154 | 121.4847 | 121.232 | 121.1178 | -0.16837 | -0.035582 | 10.6459 | -0.17998 | 121.1491 | 121.3558 | 121.3361 | -0.20536 | 0.10171 | 0.085783 | 0.17498 | 0.07854 | -0.023168 | -0.16696 | -0.28112 | 0.064723 | -0.24985 | 0.2345 | 0.090105 | 0.025382 | -0.043096 | -0.062787 | 121.7548 | 121.502 | 121.3879 | 3.1285 | -121.5673 | 121.4192 | 121.6259 | 121.6062 | 10.9159 | -121.6043
1303.6094 | 121.6232 | -0.25635 | 121.4172 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063316 | -0.0041322 | 0.05711 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.012446 | 0.059496 | -0.09052 | 2.8585 | -0.2007 | 121.4893 | 121.2274 | 121.1086 | -0.16837 | -0.035582 | 10.6321 | -0.17998 | 121.1537 | 121.3558 | 121.3407 | -0.21452 | 0.087975 | 0.072051 | 0.16583 | 0.055651 | -0.032324 | -0.18985 | -0.30859 | 0.041832 | -0.26358 | 0.22077 | 0.076372 | 0.03454 | -0.061406 | -0.076519 | 121.7456 | 121.4837 | 121.365 | 3.1148 | -121.5856 | 121.41 | 121.6122 | 121.5971 | 10.8885 | -121.6318
1305.3125 | 121.7834 | -0.23346 | 121.3669 | 1.4211e-13 | -0.025081 | -0.0013783 | 0.063103 | -0.004346 | 0.056896 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.01266 | 0.060351 | -0.085942 | 2.8539 | -0.19154 | 121.4847 | 121.2274 | 121.1086 | -0.16837 | -0.035582 | 10.6275 | -0.1754 | 121.1491 | 121.3558 | 121.3361 | -0.20078 | 0.065086 | 0.11783 | 0.14752 | 0.041918 | -0.023168 | -0.1395 | -0.25824 | 0.03268 | -0.2178 | 0.19788 | 0.058061 | 0.025381 | -0.011052 | -0.030743 | 121.7182 | 121.4608 | 121.3421 | 3.0873 | -121.5353 | 121.3825 | 121.5893 | 121.5696 | 10.861 | -121.5677
1307.0781 | 121.7377 | -0.21515 | 121.3806 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063103 | -0.0045596 | 0.056896 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.012874 | 0.05971 | -0.085942 | 2.8493 | -0.18696 | 121.4893 | 121.232 | 121.1086 | -0.17753 | -0.031003 | 10.6459 | -0.17082 | 121.1628 | 121.3558 | 121.3453 | -0.20078 | 0.037619 | 0.10867 | 0.12921 | 0.028187 | -0.009432 | -0.14865 | -0.27197 | 0.01437 | -0.2178 | 0.18415 | 0.04433 | 0.02996 | -0.024785 | -0.035319 | 121.7044 | 121.4471 | 121.3238 | 3.0644 | -121.5581 | 121.378 | 121.571 | 121.5604 | 10.861 | -121.5814
1308.8438 | 121.756 | -0.22888 | 121.3669 | 1.4211e-13 | -0.024867 | -0.0013783 | 0.063103 | -0.004346 | 0.056896 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.012874 | 0.059923 | -0.095099 | 2.8676 | -0.19612 | 121.4893 | 121.2274 | 121.1178 | -0.16837 | -0.035582 | 10.5955 | -0.16624 | 121.1537 | 121.3513 | 121.3316 | -0.20078 | 0.060509 | 0.12241 | 0.13378 | 0.032763 | -0.027746 | -0.1395 | -0.24908 | 0.028103 | -0.21323 | 0.1933 | 0.062642 | 0.034539 | -0.01563 | -0.035322 | 121.7182 | 121.4563 | 121.3467 | 3.0965 | -121.5353 | 121.3825 | 121.5801 | 121.5604 | 10.8244 | -121.5677
1310.6094 | 121.6232 | -0.25177 | 121.4218 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.06353 | -0.004346 | 0.05711 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063631 | 0.012874 | 0.059923 | -0.085942 | 2.8676 | -0.19612 | 121.4893 | 121.232 | 121.1132 | -0.16837 | -0.031003 | 10.6092 | -0.1754 | 121.1537 | 121.3558 | 121.3453 | -0.1962 | 0.083397 | 0.067473 | 0.16583 | 0.055651 | -0.027746 | -0.18985 | -0.30859 | 0.05557 | -0.26816 | 0.22077 | 0.076372 | 0.020802 | -0.065984 | -0.076518 | 121.7411 | 121.4837 | 121.365 | 3.1194 | -121.5902 | 121.4054 | 121.6076 | 121.5971 | 10.861 | -121.618
1312.375 | 121.6324 | -0.2655 | 121.4127 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063103 | -0.0047732 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063844 | 0.01266 | 0.060137 | -0.095099 | 2.8539 | -0.19612 | 121.4847 | 121.2274 | 121.1086 | -0.16837 | -0.026425 | 10.6275 | -0.16624 | 121.1582 | 121.3696 | 121.3361 | -0.19162 | 0.09713 | 0.07205 | 0.1704 | 0.069384 | -0.027746 | -0.18527 | -0.30402 | 0.073881 | -0.25442 | 0.23908 | 0.099263 | 0.025382 | -0.043093 | -0.07652 | 121.7502 | 121.4929 | 121.3741 | 3.1194 | -121.581 | 121.4237 | 121.6351 | 121.6016 | 10.893 | -121.6043
1314.1406 | 121.669 | -0.25177 | 121.3989 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.063103 | -0.0041322 | 0.056896 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063631 | 0.01266 | 0.060137 | -0.09052 | 2.8722 | -0.2007 | 121.4801 | 121.232 | 121.1178 | -0.16837 | -0.035582 | 10.6459 | -0.1754 | 121.1537 | 121.3513 | 121.3407 | -0.20994 | 0.083397 | 0.081205 | 0.16125 | 0.051073 | -0.032324 | -0.16696 | -0.28112 | 0.041833 | -0.24527 | 0.21619 | 0.076372 | 0.034539 | -0.047674 | -0.058209 | 121.7319 | 121.4837 | 121.3696 | 3.124 | -121.5673 | 121.4054 | 121.603 | 121.5925 | 10.8976 | -121.6089
1315.8438 | 121.6507 | -0.26093 | 121.4355 | 1.4211e-13 | -0.024867 | -0.0013783 | 0.063316 | -0.004346 | 0.056896 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.01266 | 0.05971 | -0.099677 | 2.8813 | -0.19612 | 121.4847 | 121.232 | 121.1178 | -0.16837 | -0.035582 | 10.5955 | -0.17082 | 121.1537 | 121.3604 | 121.3407 | -0.20078 | 0.092552 | 0.049162 | 0.16125 | 0.064806 | -0.027746 | -0.20358 | -0.31775 | 0.060146 | -0.28189 | 0.22534 | 0.090106 | 0.02996 | -0.075138 | -0.09483 | 121.7456 | 121.4929 | 121.3787 | 3.1423 | -121.6039 | 121.4146 | 121.6213 | 121.6016 | 10.8564 | -121.6363
1317.6094 | 121.6415 | -0.25177 | 121.431 | 1.4211e-13 | -0.025508 | -0.0011645 | 0.063316 | -0.0045596 | 0.057324 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063631 | 0.013087 | 0.05971 | -0.09052 | 2.8813 | -0.19154 | 121.4847 | 121.232 | 121.1224 | -0.17295 | -0.021846 | 10.6138 | -0.1754 | 121.1537 | 121.365 | 121.3407 | -0.20994 | 0.078819 | 0.05374 | 0.16125 | 0.060229 | -0.01859 | -0.199 | -0.30859 | 0.041833 | -0.27731 | 0.22992 | 0.076372 | 0.034539 | -0.065981 | -0.090252 | 121.7365 | 121.4837 | 121.3742 | 3.1331 | -121.6039 | 121.4054 | 121.6168 | 121.5925 | 10.8656 | -121.6409
1319.375 | 121.6324 | -0.26093 | 121.4355 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.06353 | -0.004987 | 0.05711 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.01266 | 0.05971 | -0.09052 | 2.8859 | -0.19612 | 121.4939 | 121.232 | 121.1132 | -0.17295 | -0.026425 | 10.6047 | -0.16624 | 121.1582 | 121.3558 | 121.3407 | -0.20536 | 0.087974 | 0.058319 | 0.17041 | 0.064806 | -0.023168 | -0.20358 | -0.32232 | 0.055567 | -0.27731 | 0.2345 | 0.094685 | 0.039118 | -0.079717 | -0.09483 | 121.7548 | 121.4929 | 121.3741 | 3.1469 | -121.6085 | 121.4192 | 121.6168 | 121.6016 | 10.8656 | -121.6409
1321.0781 | 121.7377 | -0.22888 | 121.4035 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.06353 | -0.0041322 | 0.056896 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063417 | 0.012874 | 0.05971 | -0.09052 | 2.8859 | -0.18696 | 121.4893 | 121.2365 | 121.1224 | -0.16379 | -0.040161 | 10.5726 | -0.17082 | 121.1628 | 121.3604 | 121.3407 | -0.20536 | 0.065088 | 0.085784 | 0.13836 | 0.04192 | -0.023168 | -0.16696 | -0.28112 | 0.023524 | -0.24069 | 0.18872 | 0.058063 | 0.034539 | -0.043094 | -0.062786 | 121.7182 | 121.4654 | 121.3513 | 3.1148 | -121.5673 | 121.3917 | 121.5893 | 121.5696 | 10.8015 | -121.6089
1322.8438 | 121.7102 | -0.23804 | 121.3989 | 1.4211e-13 | -0.025081 | -0.00095092 | 0.063103 | -0.0045596 | 0.05711 | -0.0022889 | 0.00055974 | 0.00015807 | 0.063203 | 0.013087 | 0.059923 | -0.09052 | 2.8859 | -0.19612 | 121.4984 | 121.2274 | 121.1224 | -0.16837 | -0.026425 | 10.6001 | -0.16624 | 121.1537 | 121.3604 | 121.3453 | -0.20536 | 0.069664 | 0.099518 | 0.14752 | 0.041918 | -0.027746 | -0.17154 | -0.27655 | 0.032679 | -0.24527 | 0.21161 | 0.071797 | 0.039118 | -0.038517 | -0.05363 | 121.7365 | 121.4654 | 121.3604 | 3.124 | -121.5673 | 121.3917 | 121.5984 | 121.5833 | 10.8381 | -121.6043
1324.6094 | 121.6187 | -0.25635 | 121.4035 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063316 | -0.004346 | 0.056896 | 0.012972 | 0.00034614 | 0.00015807 | 0.063631 | 0.01266 | 0.060137 | -0.09052 | 2.9042 | -0.19154 | 121.4893 | 121.2411 | 121.1224 | -0.16837 | -0.031003 | 10.6001 | -0.17082 | 121.1582 | 121.365 | 121.3407 | -0.20078 | 0.087975 | 0.085784 | 0.16583 | 0.064807 | -0.023168 | -0.16238 | -0.28112 | 0.055569 | -0.24527 | 0.22535 | 0.085529 | 0.02996 | -0.038515 | -0.062786 | 121.7456 | 121.4975 | 121.3787 | 3.1606 | -121.5719 | 121.4146 | 121.6213 | 121.5971 | 10.8564 | -121.6043
1326.3125 | 121.6095 | -0.2655 | 121.4127 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063316 | -0.004346 | 0.056896 | 0.0053411 | 0.00055974 | -5.5534e-05 | 0.063417 | 0.01266 | 0.060137 | -0.085942 | 2.9042 | -0.19154 | 121.4893 | 121.2365 | 121.1224 | -0.15921 | -0.026425 | 10.6138 | -0.17082 | 121.1582 | 121.365 | 121.3453 | -0.20536 | 0.10629 | 0.076628 | 0.17956 | 0.073962 | -0.032326 | -0.17612 | -0.29028 | 0.060145 | -0.25442 | 0.23908 | 0.094684 | 0.034539 | -0.047671 | -0.067363 | 121.7548 | 121.502 | 121.3879 | 3.1697 | -121.5719 | 121.4237 | 121.6305 | 121.6108 | 10.8793 | -121.618
1328.0625 | 121.7056 | -0.23346 | 121.3852 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063316 | -0.004346 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.013087 | 0.059496 | -0.095099 | 2.9042 | -0.18696 | 121.4893 | 121.2365 | 121.1224 | -0.16837 | -0.026425 | 10.6825 | -0.17082 | 121.1582 | 121.365 | 121.3453 | -0.20536 | 0.065086 | 0.10409 | 0.13836 | 0.046497 | -0.018589 | -0.14865 | -0.26281 | 0.028101 | -0.22696 | 0.20703 | 0.06264 | 0.034539 | -0.020205 | -0.039897 | 121.7227 | 121.47 | 121.3558 | 3.1377 | -121.5536 | 121.3917 | 121.5984 | 121.5788 | 10.9159 | -121.5906
1329.7656 | 121.6141 | -0.27924 | 121.4447 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063316 | -0.0045596 | 0.057324 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063844 | 0.012874 | 0.059923 | -0.085942 | 2.8997 | -0.18696 | 121.4939 | 121.2411 | 121.127 | -0.16837 | -0.026425 | 10.6413 | -0.16166 | 121.1674 | 121.3696 | 121.3453 | -0.20078 | 0.11086 | 0.049164 | 0.19329 | 0.092274 | -0.018589 | -0.20358 | -0.31774 | 0.078457 | -0.27731 | 0.25281 | 0.11757 | 0.039118 | -0.075136 | -0.099406 | 121.7731 | 121.5204 | 121.4062 | 3.1789 | -121.6131 | 121.4466 | 121.6488 | 121.6245 | 10.9205 | -121.6455
1331.5469 | 121.7514 | -0.22888 | 121.3715 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063103 | -0.004346 | 0.056896 | -0.0099194 | 0.00034614 | -0.00026913 | 0.063631 | 0.012874 | 0.059923 | -0.09052 | 2.918 | -0.19612 | 121.4984 | 121.2365 | 121.127 | -0.16379 | -0.031003 | 10.6367 | -0.16624 | 121.1628 | 121.365 | 121.3453 | -0.20078 | 0.065088 | 0.12698 | 0.13836 | 0.032763 | -0.032325 | -0.13492 | -0.2445 | 0.028103 | -0.20865 | 0.19788 | 0.062642 | 0.034539 | -0.006472 | -0.026164 | 121.7273 | 121.4654 | 121.3558 | 3.1469 | -121.5353 | 121.3917 | 121.5939 | 121.5742 | 10.8656 | -121.5722
1333.25 | 121.7697 | -0.20599 | 121.3806 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063103 | -0.004346 | 0.05711 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.01266 | 0.060137 | -0.09052 | 2.9088 | -0.19154 | 121.4939 | 121.2411 | 121.127 | -0.16837 | -0.031003 | 10.6275 | -0.1754 | 121.1628 | 121.365 | 121.3453 | -0.1962 | 0.037621 | 0.11325 | 0.11547 | 0.014453 | -0.023168 | -0.13949 | -0.25366 | 0.009794 | -0.2178 | 0.17499 | 0.030596 | 0.020802 | -0.015627 | -0.035319 | 121.6999 | 121.4471 | 121.333 | 3.1148 | -121.549 | 121.3688 | 121.571 | 121.5513 | 10.8335 | -121.5768
1335.0156 | 121.7148 | -0.24261 | 121.4035 | 1.4211e-13 | -0.025295 | -0.0015919 | 0.063103 | -0.004346 | 0.05711 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063631 | 0.013087 | 0.05971 | -0.09052 | 2.918 | -0.19154 | 121.4893 | 121.2365 | 121.1315 | -0.15921 | -0.026425 | 10.6688 | -0.1754 | 121.1582 | 121.3696 | 121.3453 | -0.20078 | 0.0834 | 0.085784 | 0.15209 | 0.051074 | -0.032326 | -0.16696 | -0.27196 | 0.041836 | -0.24527 | 0.21619 | 0.067217 | 0.025381 | -0.033937 | -0.058207 | 121.7319 | 121.4792 | 121.3742 | 3.1606 | -121.5627 | 121.4009 | 121.6122 | 121.5879 | 10.9114 | -121.6043
1336.9531 | 121.5958 | -0.27008 | 121.4355 | 1.4211e-13 | -0.025081 | -0.0013783 | 0.063744 | -0.0041322 | 0.05711 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.01266 | 0.059496 | -0.085942 | 2.9134 | -0.19612 | 121.4893 | 121.2411 | 121.127 | -0.16379 | -0.031003 | 10.6596 | -0.1754 | 121.1628 | 121.365 | 121.3499 | -0.1962 | 0.10629 | 0.05374 | 0.18414 | 0.073962 | -0.032325 | -0.19442 | -0.30859 | 0.073881 | -0.27273 | 0.23908 | 0.094683 | 0.020802 | -0.070559 | -0.085672 | 121.7594 | 121.5112 | 121.397 | 3.1835 | -121.5993 | 121.4329 | 121.6351 | 121.62 | 10.9297 | -121.6317
1338.7188 | 121.7651 | -0.21057 | 121.3943 | 1.4211e-13 | -0.025508 | -0.0011645 | 0.063316 | -0.0041322 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063631 | 0.01266 | 0.059496 | -0.095099 | 2.918 | -0.19612 | 121.4893 | 121.2365 | 121.1224 | -0.16837 | -0.026425 | 10.6459 | -0.18455 | 121.1582 | 121.365 | 121.3361 | -0.20536 | 0.042198 | 0.094939 | 0.11547 | 0.014452 | -0.027746 | -0.1578 | -0.27197 | 0.005213 | -0.23611 | 0.18415 | 0.026016 | 0.020803 | -0.02936 | -0.058209 | 121.6999 | 121.4471 | 121.333 | 3.1285 | -121.5627 | 121.3688 | 121.5756 | 121.5467 | 10.8564 | -121.5997
1340.4844 | 121.7651 | -0.22888 | 121.3577 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063316 | -0.0045596 | 0.057324 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.012446 | 0.05971 | -0.095099 | 2.9271 | -0.19612 | 121.4984 | 121.2365 | 121.127 | -0.15921 | -0.031003 | 10.6916 | -0.1754 | 121.1628 | 121.365 | 121.3361 | -0.20078 | 0.069667 | 0.14072 | 0.13378 | 0.032763 | -0.036904 | -0.12118 | -0.23077 | 0.028103 | -0.19491 | 0.19788 | 0.053484 | 0.025381 | 0.007261 | -0.021588 | 121.7273 | 121.4654 | 121.3558 | 3.156 | -121.5169 | 121.3917 | 121.5939 | 121.565 | 10.9205 | -121.5585
1342.2031 | 121.6873 | -0.23804 | 121.4264 | 1.4211e-13 | -0.025295 | -0.0011645 | 0.06353 | -0.0041322 | 0.05711 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.012874 | 0.059496 | -0.085942 | 2.9226 | -0.19154 | 121.4893 | 121.2411 | 121.127 | -0.16379 | -0.026425 | 10.7054 | -0.17082 | 121.1491 | 121.3604 | 121.3453 | -0.20536 | 0.074243 | 0.062895 | 0.15209 | 0.046496 | -0.027747 | -0.18527 | -0.29943 | 0.032679 | -0.27731 | 0.21161 | 0.067218 | 0.034539 | -0.065983 | -0.081096 | 121.7273 | 121.4792 | 121.365 | 3.1606 | -121.5902 | 121.3871 | 121.5984 | 121.5833 | 10.9434 | -121.6318
1343.9688 | 121.7148 | -0.2243 | 121.4081 | 1.4211e-13 | -0.025295 | -0.00095092 | 0.063316 | -0.0045596 | 0.057324 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.01266 | 0.060351 | -0.09052 | 2.918 | -0.19612 | 121.4893 | 121.2365 | 121.1315 | -0.16379 | -0.021846 | 10.6779 | -0.1754 | 121.1628 | 121.3741 | 121.3407 | -0.20536 | 0.06051 | 0.081206 | 0.13378 | 0.028185 | -0.032325 | -0.17154 | -0.27654 | 0.018946 | -0.24527 | 0.20246 | 0.048906 | 0.02996 | -0.033936 | -0.067364 | 121.7136 | 121.4608 | 121.3558 | 3.1423 | -121.5719 | 121.3871 | 121.5984 | 121.565 | 10.9022 | -121.6134
1345.6719 | 121.6278 | -0.27466 | 121.4447 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.063316 | -0.0045596 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.01266 | 0.059923 | -0.095099 | 2.9409 | -0.18238 | 121.4939 | 121.2365 | 121.1315 | -0.16837 | -0.021846 | 10.6642 | -0.16624 | 121.1582 | 121.365 | 121.3453 | -0.20078 | 0.10629 | 0.049164 | 0.17956 | 0.092274 | -0.014011 | -0.20816 | -0.31316 | 0.073879 | -0.28647 | 0.25281 | 0.10842 | 0.034539 | -0.079714 | -0.099406 | 121.7685 | 121.5112 | 121.4062 | 3.2155 | -121.6131 | 121.4329 | 121.6396 | 121.62 | 10.9388 | -121.6455
1347.4375 | 121.637 | -0.28381 | 121.4493 | 1.4211e-13 | -0.024867 | -0.0011645 | 0.06353 | -0.0045596 | 0.05711 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.012874 | 0.059923 | -0.076785 | 2.9454 | -0.2007 | 121.4984 | 121.2411 | 121.127 | -0.16379 | -0.031003 | 10.6688 | -0.17082 | 121.1628 | 121.3696 | 121.3453 | -0.20078 | 0.12002 | 0.049164 | 0.20703 | 0.083116 | -0.036903 | -0.20816 | -0.32232 | 0.083034 | -0.28647 | 0.25281 | 0.11299 | 0.02996 | -0.079714 | -0.10398 | 121.7823 | 121.5249 | 121.4108 | 3.2293 | -121.6131 | 121.4466 | 121.6534 | 121.6291 | 10.9526 | -121.6501
1349.1406 | 121.7697 | -0.21515 | 121.3989 | 1.4211e-13 | -0.025295 | -0.0013783 | 0.063103 | -0.0047732 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.012446 | 0.060137 | -0.081363 | 2.9409 | -0.19154 | 121.4984 | 121.232 | 121.1315 | -0.16379 | -0.021846 | 10.655 | -0.17082 | 121.1582 | 121.3696 | 121.3453 | -0.20078 | 0.051355 | 0.099518 | 0.13379 | 0.023608 | -0.027747 | -0.16696 | -0.26739 | 0.01437 | -0.24069 | 0.1933 | 0.04433 | 0.02996 | -0.02936 | -0.05363 | 121.7136 | 121.4471 | 121.3467 | 3.156 | -121.5627 | 121.3734 | 121.5847 | 121.5604 | 10.8702 | -121.5997
1350.9062 | 121.7468 | -0.21515 | 121.4035 | 1.4211e-13 | -0.025295 | -0.0015919 | 0.063103 | -0.004346 | 0.057324 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.01266 | 0.05971 | -0.085942 | 2.9271 | -0.2007 | 121.503 | 121.2411 | 121.1315 | -0.16837 | -0.026425 | 10.6825 | -0.16624 | 121.1582 | 121.3696 | 121.3361 | -0.20078 | 0.046776 | 0.099519 | 0.12921 | 0.014452 | -0.032324 | -0.16238 | -0.27196 | 0.01437 | -0.24527 | 0.18872 | 0.048909 | 0.034539 | -0.033937 | -0.067364 | 121.7182 | 121.4563 | 121.3467 | 3.1423 | -121.5719 | 121.3734 | 121.5847 | 121.5513 | 10.8976 | -121.6043
1352.6719 | 121.7468 | -0.20599 | 121.3852 | 1.4211e-13 | -0.025936 | -0.0013783 | 0.06353 | -0.004346 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.013087 | 0.059923 | -0.081363 | 2.9363 | -0.19612 | 121.4939 | 121.2365 | 121.1407 | -0.15921 | -0.026425 | 10.7054 | -0.17082 | 121.172 | 121.3696 | 121.3499 | -0.20536 | 0.046779 | 0.10867 | 0.12463 | 0.009875 | -0.036904 | -0.14865 | -0.2445 | 0.000636 | -0.21322 | 0.17957 | 0.035175 | 0.034539 | -0.015627 | -0.035318 | 121.6999 | 121.4425 | 121.3467 | 3.1423 | -121.5444 | 121.378 | 121.5756 | 121.5559 | 10.9114 | -121.5906
1354.375 | 121.6461 | -0.27466 | 121.4172 | 1.4211e-13 | -0.025081 | -0.00095092 | 0.063103 | -0.0047732 | 0.057324 | -0.0022889 | -8.1262e-05 | -0.00048293 | 0.063631 | 0.01266 | 0.05971 | -0.09052 | 2.9226 | -0.19612 | 121.4984 | 121.2457 | 121.1453 | -0.15921 | -0.026425 | 10.6825 | -0.17082 | 121.1674 | 121.365 | 121.3453 | -0.19162 | 0.11544 | 0.081208 | 0.18414 | 0.078539 | -0.036904 | -0.17153 | -0.27196 | 0.083036 | -0.24984 | 0.24823 | 0.10384 | 0.020803 | -0.052248 | -0.07194 | 121.7731 | 121.5204 | 121.4199 | 3.1972 | -121.5765 | 121.4421 | 121.6396 | 121.62 | 10.9571 | -121.6089
1356.1406 | 121.6232 | -0.2655 | 121.4447 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.063103 | -0.0045596 | 0.057324 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013087 | 0.060137 | -0.09052 | 2.9226 | -0.18696 | 121.4984 | 121.2457 | 121.1315 | -0.16379 | -0.021846 | 10.7283 | -0.16166 | 121.1628 | 121.365 | 121.3407 | -0.19162 | 0.10171 | 0.053742 | 0.17498 | 0.078541 | -0.023168 | -0.199 | -0.31316 | 0.073881 | -0.28189 | 0.24366 | 0.10384 | 0.029961 | -0.079714 | -0.10399 | 121.7639 | 121.5112 | 121.397 | 3.1881 | -121.6085 | 121.4283 | 121.6305 | 121.6062 | 10.9938 | -121.6363
1357.8438 | 121.7789 | -0.2243 | 121.3943 | 1.4211e-13 | -0.025081 | -0.0011645 | 0.06353 | -0.004346 | 0.05711 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.063631 | 0.012874 | 0.059923 | -0.081363 | 2.918 | -0.19154 | 121.4984 | 121.2411 | 121.1361 | -0.16379 | -0.021846 | 10.6779 | -0.17082 | 121.1674 | 121.3604 | 121.3453 | -0.1962 | 0.06051 | 0.1041 | 0.14294 | 0.032763 | -0.027747 | -0.15322 | -0.25823 | 0.028104 | -0.22696 | 0.20246 | 0.053485 | 0.025381 | -0.033939 | -0.049052 | 121.7227 | 121.4654 | 121.3604 | 3.1423 | -121.5581 | 121.3917 | 121.5847 | 121.5696 | 10.9022 | -121.5905
1359.5469 | 121.6599 | -0.24261 | 121.4172 | 1.4211e-13 | -0.025295 | -0.0015919 | 0.06353 | -0.0045596 | 0.057324 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013087 | 0.060137 | -0.081363 | 2.918 | -0.19612 | 121.4939 | 121.2365 | 121.1407 | -0.15464 | -0.021846 | 10.6688 | -0.16624 | 121.1582 | 121.365 | 121.3453 | -0.20078 | 0.087979 | 0.07663 | 0.16125 | 0.046496 | -0.041483 | -0.18069 | -0.27654 | 0.041836 | -0.259 | 0.22077 | 0.076375 | 0.034539 | -0.052248 | -0.07194 | 121.7365 | 121.4792 | 121.3833 | 3.1606 | -121.5719 | 121.4009 | 121.6076 | 121.5879 | 10.9114 | -121.618
1361.3125 | 121.6965 | -0.25177 | 121.4081 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.063103 | -0.0045596 | 0.057324 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.013087 | 0.060137 | -0.081363 | 2.9409 | -0.19612 | 121.4984 | 121.2457 | 121.1499 | -0.15921 | -0.026425 | 10.6962 | -0.15708 | 121.172 | 121.365 | 121.3545 | -0.20078 | 0.092555 | 0.090363 | 0.17041 | 0.055651 | -0.036904 | -0.16238 | -0.25823 | 0.050991 | -0.23611 | 0.22534 | 0.094687 | 0.043696 | -0.043093 | -0.053628 | 121.7502 | 121.4975 | 121.4016 | 3.1926 | -121.5673 | 121.4237 | 121.6168 | 121.6062 | 10.948 | -121.6089
1363.0938 | 121.6461 | -0.2655 | 121.4355 | 1.4211e-13 | -0.025508 | -0.0011645 | 0.063744 | -0.0041322 | 0.056896 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.012874 | 0.059923 | -0.076785 | 2.9226 | -0.19154 | 121.4984 | 121.2457 | 121.1407 | -0.16379 | -0.026425 | 10.5726 | -0.16624 | 121.172 | 121.3696 | 121.3499 | -0.1962 | 0.10171 | 0.062897 | 0.18872 | 0.073962 | -0.027747 | -0.18985 | -0.29485 | 0.069303 | -0.26358 | 0.23908 | 0.099263 | 0.02996 | -0.065981 | -0.085672 | 121.7639 | 121.5112 | 121.4062 | 3.1881 | -121.5993 | 121.4375 | 121.6351 | 121.6154 | 10.8381 | -121.6317
1364.8594 | 121.6187 | -0.25635 | 121.431 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.06353 | -0.0047732 | 0.057324 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.012874 | 0.05971 | -0.085942 | 2.9409 | -0.18696 | 121.503 | 121.2411 | 121.1453 | -0.15921 | -0.026425 | 10.6367 | -0.17082 | 121.1674 | 121.3696 | 121.3545 | -0.19162 | 0.097133 | 0.072053 | 0.17041 | 0.069386 | -0.027747 | -0.18985 | -0.2857 | 0.064726 | -0.26358 | 0.22992 | 0.085529 | 0.020803 | -0.061403 | -0.076516 | 121.7594 | 121.4975 | 121.4016 | 3.1972 | -121.5902 | 121.4237 | 121.6259 | 121.6108 | 10.893 | -121.6226
1366.5781 | 121.6873 | -0.23804 | 121.4081 | 1.4211e-13 | -0.025295 | -0.00095092 | 0.063316 | -0.0045596 | 0.057537 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063203 | 0.013301 | 0.059923 | -0.081363 | 2.9363 | -0.18238 | 121.4893 | 121.2411 | 121.1499 | -0.16379 | -0.026425 | 10.6504 | -0.16624 | 121.172 | 121.3696 | 121.3499 | -0.20078 | 0.074243 | 0.081206 | 0.15667 | 0.055653 | -0.01859 | -0.16696 | -0.25823 | 0.037258 | -0.23611 | 0.21161 | 0.071797 | 0.034539 | -0.038515 | -0.058206 | 121.7273 | 121.4792 | 121.3879 | 3.1743 | -121.5719 | 121.41 | 121.6076 | 121.5879 | 10.8885 | -121.6089
1368.3438 | 121.7422 | -0.20599 | 121.3898 | 1.4211e-13 | -0.025936 | -0.0013783 | 0.063316 | -0.004346 | 0.057324 | 0.0053411 | 0.00034614 | 0.00015807 | 0.063417 | 0.013087 | 0.060351 | -0.076785 | 2.9683 | -0.18696 | 121.4984 | 121.2457 | 121.1499 | -0.15921 | -0.026425 | 10.6733 | -0.16624 | 121.1628 | 121.365 | 121.3499 | -0.20078 | 0.046779 | 0.10867 | 0.12921 | 0.019032 | -0.027747 | -0.14407 | -0.23992 | 0.005215 | -0.22696 | 0.17957 | 0.039754 | 0.034539 | -0.024783 | -0.039896 | 121.7044 | 121.4517 | 121.3558 | 3.1743 | -121.549 | 121.3688 | 121.571 | 121.5559 | 10.8793 | -121.5905
1370.1094 | 121.6736 | -0.24261 | 121.4401 | 1.4211e-13 | -0.025508 | -0.0011645 | 0.063103 | -0.0047732 | 0.05711 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063417 | 0.013301 | 0.059923 | -0.081363 | 2.9454 | -0.18696 | 121.4984 | 121.2503 | 121.159 | -0.15921 | -0.017267 | 10.7283 | -0.16624 | 121.172 | 121.3696 | 121.3499 | -0.1962 | 0.0834 | 0.058319 | 0.16125 | 0.055653 | -0.027747 | -0.18984 | -0.28112 | 0.046415 | -0.26815 | 0.22535 | 0.076375 | 0.02996 | -0.070559 | -0.09025 | 121.7411 | 121.4929 | 121.4016 | 3.1881 | -121.5993 | 121.4146 | 121.6122 | 121.5925 | 10.9709 | -121.6363
1371.875 | 121.7148 | -0.23804 | 121.3989 | 1.4211e-13 | -0.025722 | -0.0013783 | 0.063103 | -0.0045596 | 0.05711 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.013515 | 0.059923 | -0.081363 | 2.9409 | -0.18696 | 121.503 | 121.2503 | 121.1499 | -0.16379 | -0.021846 | 10.6871 | -0.16624 | 121.1674 | 121.3833 | 121.3545 | -0.1962 | 0.074243 | 0.1041 | 0.15667 | 0.051075 | -0.023168 | -0.14865 | -0.24907 | 0.041837 | -0.23153 | 0.21619 | 0.071797 | 0.02996 | -0.015624 | -0.044473 | 121.7411 | 121.4883 | 121.3879 | 3.1789 | -121.5627 | 121.4054 | 121.6213 | 121.5925 | 10.9251 | -121.5951
1373.5781 | 121.7514 | -0.21515 | 121.3989 | 1.4211e-13 | -0.025295 | -0.0015919 | 0.063103 | -0.004346 | 0.057324 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063417 | 0.013087 | 0.060137 | -0.076785 | 2.9271 | -0.19154 | 121.4984 | 121.2503 | 121.159 | -0.15464 | -0.017267 | 10.7054 | -0.15708 | 121.172 | 121.3741 | 121.3545 | -0.19162 | 0.060513 | 0.099518 | 0.13836 | 0.023608 | -0.036905 | -0.14865 | -0.23992 | 0.023527 | -0.22696 | 0.19788 | 0.058066 | 0.034539 | -0.024781 | -0.044473 | 121.7136 | 121.4654 | 121.3742 | 3.1423 | -121.5536 | 121.3871 | 121.5893 | 121.5696 | 10.9205 | -121.5905
1375.2812 | 121.6873 | -0.24719 | 121.4264 | 1.4211e-13 | -0.025295 | -0.0011645 | 0.063316 | -0.0047732 | 0.05711 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063203 | 0.012874 | 0.060137 | -0.081363 | 2.9409 | -0.17781 | 121.503 | 121.2503 | 121.1636 | -0.15921 | -0.017267 | 10.7329 | -0.16166 | 121.1628 | 121.3741 | 121.3545 | -0.19162 | 0.087977 | 0.07663 | 0.16583 | 0.069386 | -0.018591 | -0.17611 | -0.2628 | 0.05557 | -0.26358 | 0.22992 | 0.085531 | 0.029961 | -0.052247 | -0.071939 | 121.7502 | 121.4975 | 121.4108 | 3.1881 | -121.5856 | 121.41 | 121.6213 | 121.6016 | 10.98 | -121.618
1377 | 121.7056 | -0.20142 | 121.431 | 1.4211e-13 | -0.025508 | -0.0015919 | 0.063103 | -0.0045596 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.012874 | 0.059923 | -0.081363 | 2.9363 | -0.18696 | 121.503 | 121.2503 | 121.1499 | -0.15921 | -0.012689 | 10.7466 | -0.16166 | 121.1674 | 121.3696 | 121.3545 | -0.19162 | 0.042201 | 0.072053 | 0.12005 | 0.014454 | -0.027747 | -0.18069 | -0.28112 | 0.009794 | -0.26358 | 0.18873 | 0.039755 | 0.029961 | -0.061403 | -0.076516 | 121.7044 | 121.4517 | 121.3513 | 3.1377 | -121.5902 | 121.3688 | 121.571 | 121.5559 | 10.948 | -121.6226
1378.7656 | 121.7239 | -0.2243 | 121.4218 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.063103 | -0.004346 | 0.057537 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013087 | 0.060137 | -0.072207 | 2.9638 | -0.18696 | 121.503 | 121.2549 | 121.159 | -0.15921 | -0.017267 | 10.7145 | -0.16166 | 121.1582 | 121.3787 | 121.3499 | -0.19162 | 0.065089 | 0.081208 | 0.1521 | 0.037342 | -0.027747 | -0.16695 | -0.26281 | 0.032682 | -0.26358 | 0.20704 | 0.062643 | 0.029961 | -0.043091 | -0.071939 | 121.7273 | 121.4792 | 121.3833 | 3.1881 | -121.581 | 121.3825 | 121.603 | 121.5742 | 10.9388 | -121.6134
1380.4688 | 121.6095 | -0.25635 | 121.4539 | 1.4211e-13 | -0.025936 | -0.0013783 | 0.063316 | -0.0047732 | 0.05711 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.063417 | 0.013087 | 0.059923 | -0.09052 | 2.9409 | -0.18238 | 121.5076 | 121.2503 | 121.1636 | -0.15464 | -0.017267 | 10.7054 | -0.16624 | 121.1674 | 121.3787 | 121.3545 | -0.19162 | 0.10171 | 0.053744 | 0.16583 | 0.073964 | -0.027748 | -0.20358 | -0.29027 | 0.064726 | -0.28646 | 0.23908 | 0.090108 | 0.025382 | -0.075134 | -0.099404 | 121.7639 | 121.5066 | 121.4199 | 3.1972 | -121.6085 | 121.4237 | 121.6351 | 121.6108 | 10.9617 | -121.6455
1382.2344 | 121.6324 | -0.24719 | 121.4081 | 1.4211e-13 | -0.025722 | -0.0011645 | 0.063316 | -0.0045596 | 0.057324 | -0.0099194 | 0.00013254 | 0.00037167 | 0.063417 | 0.013087 | 0.060351 | -0.081363 | 2.9546 | -0.17781 | 121.503 | 121.264 | 121.159 | -0.15921 | -0.021846 | 10.7191 | -0.16166 | 121.1628 | 121.365 | 121.3499 | -0.18704 | 0.087977 | 0.094941 | 0.16583 | 0.069386 | -0.018591 | -0.14406 | -0.24907 | 0.060149 | -0.24527 | 0.22535 | 0.085531 | 0.025382 | -0.043093 | -0.058206 | 121.7502 | 121.5112 | 121.4062 | 3.2018 | -121.5673 | 121.41 | 121.6122 | 121.5971 | 10.9663 | -121.5951
1383.9844 | 121.637 | -0.2655 | 121.4401 | 1.4211e-13 | -0.025722 | -0.0013783 | 0.06353 | -0.0047732 | 0.057537 | -0.01755 | -8.1262e-05 | 0.00015807 | 0.063844 | 0.012874 | 0.060137 | -0.085942 | 2.95 | -0.18238 | 121.5076 | 121.2594 | 121.1544 | -0.15464 | -0.017267 | 10.71 | -0.16166 | 121.1674 | 121.3833 | 121.3545 | -0.19162 | 0.11087 | 0.067476 | 0.17956 | 0.083119 | -0.027748 | -0.18069 | -0.28569 | 0.073881 | -0.27273 | 0.24824 | 0.10384 | 0.029961 | -0.056823 | -0.085672 | 121.7731 | 121.5249 | 121.4199 | 3.2155 | -121.5948 | 121.4329 | 121.6488 | 121.62 | 10.9755 | -121.6317
1385.75 | 121.6644 | -0.25635 | 121.4401 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.06353 | -0.0047732 | 0.05711 | -0.01755 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.012874 | 0.059496 | -0.076785 | 2.9638 | -0.18238 | 121.5168 | 121.2549 | 121.1636 | -0.15464 | -0.012689 | 10.6733 | -0.15708 | 121.1674 | 121.3741 | 121.359 | -0.19162 | 0.10171 | 0.076633 | 0.17956 | 0.073964 | -0.027748 | -0.18527 | -0.27654 | 0.064726 | -0.27273 | 0.24366 | 0.099265 | 0.034539 | -0.06598 | -0.081093 | 121.7731 | 121.5112 | 121.4199 | 3.2201 | -121.5948 | 121.4237 | 121.6305 | 121.6154 | 10.9297 | -121.6317
1387.5156 | 121.7651 | -0.19684 | 121.3852 | 1.4211e-13 | -0.025722 | -0.0011645 | 0.063316 | -0.0047732 | 0.057324 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.013301 | 0.060137 | -0.081363 | 2.95 | -0.17781 | 121.5076 | 121.2503 | 121.1636 | -0.15921 | -0.012689 | 10.7466 | -0.16166 | 121.1628 | 121.3741 | 121.359 | -0.19162 | 0.037623 | 0.12241 | 0.11548 | 0.019032 | -0.018591 | -0.13491 | -0.2216 | 0.005216 | -0.22238 | 0.18415 | 0.035177 | 0.029961 | -0.011048 | -0.026161 | 121.7044 | 121.4471 | 121.3604 | 3.1469 | -121.5444 | 121.3597 | 121.571 | 121.5559 | 10.9434 | -121.5768
1389.2812 | 121.6644 | -0.22888 | 121.4447 | 1.4211e-13 | -0.025508 | -0.0013783 | 0.063316 | -0.004987 | 0.057537 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.013087 | 0.059923 | -0.076785 | 2.9546 | -0.18696 | 121.5076 | 121.2594 | 121.1544 | -0.15921 | -0.017267 | 10.71 | -0.16166 | 121.1628 | 121.3787 | 121.3636 | -0.18704 | 0.069667 | 0.062899 | 0.1521 | 0.04192 | -0.027747 | -0.18526 | -0.29027 | 0.041839 | -0.28189 | 0.21161 | 0.067221 | 0.025382 | -0.065979 | -0.081092 | 121.7365 | 121.4883 | 121.3833 | 3.1835 | -121.6039 | 121.3917 | 121.6076 | 121.5925 | 10.9388 | -121.6317
1391.0625 | 121.701 | -0.23346 | 121.4172 | 1.4211e-13 | -0.025722 | -0.0011645 | 0.063316 | -0.004346 | 0.056896 | -0.01755 | -0.00050846 | 0.00037167 | 0.063417 | 0.012874 | 0.060137 | -0.081363 | 2.9592 | -0.18238 | 121.5122 | 121.2503 | 121.1727 | -0.15921 | -0.017267 | 10.6688 | -0.16624 | 121.1674 | 121.3741 | 121.359 | -0.19162 | 0.074244 | 0.094943 | 0.1521 | 0.051075 | -0.023169 | -0.16696 | -0.24449 | 0.041837 | -0.24984 | 0.21619 | 0.067219 | 0.025382 | -0.043091 | -0.058204 | 121.7456 | 121.4837 | 121.4062 | 3.1926 | -121.5765 | 121.4009 | 121.6076 | 121.5925 | 10.9022 | -121.6089
1392.8438 | 121.6324 | -0.24261 | 121.431 | 1.4211e-13 | -0.025722 | -0.0011645 | 0.06353 | -0.0047732 | 0.057324 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.013301 | 0.060137 | -0.081363 | 2.9775 | -0.18696 | 121.5076 | 121.2594 | 121.1682 | -0.15006 | -0.026425 | 10.7329 | -0.15708 | 121.1628 | 121.3787 | 121.3636 | -0.1962 | 0.092558 | 0.076632 | 0.16125 | 0.055653 | -0.036905 | -0.17153 | -0.2628 | 0.046415 | -0.26816 | 0.21619 | 0.085532 | 0.039117 | -0.052246 | -0.067359 | 121.7502 | 121.5021 | 121.4108 | 3.2201 | -121.581 | 121.4054 | 121.6213 | 121.6062 | 10.9755 | -121.6272
1394.5469 | 121.6415 | -0.2655 | 121.4539 | 1.4211e-13 | -0.025508 | -0.0011645 | 0.063316 | -0.0045596 | 0.05711 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.013301 | 0.060137 | -0.076785 | 2.9729 | -0.18238 | 121.5122 | 121.2594 | 121.159 | -0.15921 | -0.021846 | 10.7008 | -0.16166 | 121.1765 | 121.3741 | 121.3636 | -0.19162 | 0.10629 | 0.058322 | 0.18872 | 0.083119 | -0.023169 | -0.19442 | -0.29485 | 0.073881 | -0.27731 | 0.24366 | 0.10384 | 0.029961 | -0.079712 | -0.090247 | 121.7777 | 121.5249 | 121.4245 | 3.2384 | -121.6131 | 121.4421 | 121.6396 | 121.6291 | 10.9663 | -121.6455
1396.3125 | 121.7606 | -0.19684 | 121.3989 | 1.4211e-13 | -0.025936 | -0.0011645 | 0.063103 | -0.004346 | 0.056896 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013301 | 0.059923 | -0.081363 | 2.9821 | -0.19154 | 121.5076 | 121.2549 | 121.159 | -0.15006 | -0.021846 | 10.7191 | -0.16624 | 121.172 | 121.3787 | 121.3636 | -0.19162 | 0.046781 | 0.10867 | 0.11548 | 0.005297 | -0.041484 | -0.14407 | -0.23992 | 0.005216 | -0.22696 | 0.17499 | 0.030598 | 0.025382 | -0.020203 | -0.035316 | 121.7044 | 121.4517 | 121.3558 | 3.1789 | -121.549 | 121.3688 | 121.5756 | 121.5604 | 10.916 | -121.5905
1398.0781 | 121.6965 | -0.23804 | 121.431 | 1.4211e-13 | -0.025722 | -0.0013783 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013087 | 0.060137 | -0.081363 | 2.9592 | -0.17781 | 121.5076 | 121.2549 | 121.1636 | -0.15464 | -0.012689 | 10.7145 | -0.16166 | 121.1674 | 121.3741 | 121.3545 | -0.20078 | 0.083401 | 0.076632 | 0.15667 | 0.060231 | -0.02317 | -0.17611 | -0.26738 | 0.037258 | -0.26358 | 0.22535 | 0.076376 | 0.039118 | -0.056824 | -0.076516 | 121.7456 | 121.4929 | 121.4016 | 3.1972 | -121.5856 | 121.4054 | 121.6122 | 121.5925 | 10.9526 | -121.6317
1399.8438 | 121.7422 | -0.20142 | 121.4035 | 1.4211e-13 | -0.025722 | -0.0011645 | 0.06353 | -0.004346 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.013087 | 0.060137 | -0.081363 | 2.9958 | -0.18238 | 121.5122 | 121.264 | 121.1636 | -0.15464 | -0.021846 | 10.7237 | -0.15708 | 121.172 | 121.3696 | 121.359 | -0.19162 | 0.04678 | 0.10868 | 0.12005 | 0.019032 | -0.027748 | -0.13949 | -0.23991 | 0.009794 | -0.23153 | 0.17957 | 0.044333 | 0.034539 | -0.033937 | -0.044471 | 121.7136 | 121.4654 | 121.365 | 3.1972 | -121.5581 | 121.3734 | 121.571 | 121.5604 | 10.9251 | -121.5951
1401.5469 | 121.6736 | -0.24261 | 121.4127 | 1.4211e-13 | -0.025722 | -0.0015919 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063631 | 0.01266 | 0.059923 | -0.076785 | 2.9958 | -0.18696 | 121.5076 | 121.2549 | 121.1636 | -0.15006 | -0.021846 | 10.7329 | -0.16166 | 121.172 | 121.3741 | 121.3682 | -0.19162 | 0.092558 | 0.094942 | 0.16583 | 0.055653 | -0.036905 | -0.1578 | -0.24907 | 0.050993 | -0.24069 | 0.22077 | 0.080954 | 0.029961 | -0.038514 | -0.04447 | 121.7502 | 121.4975 | 121.4062 | 3.2384 | -121.5627 | 121.4146 | 121.6168 | 121.6108 | 10.9755 | -121.6043
1403.3125 | 121.6324 | -0.25177 | 121.4127 | 1.4211e-13 | -0.025508 | -0.0015919 | 0.063316 | -0.004346 | 0.056896 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063631 | 0.013301 | 0.060137 | -0.081363 | 2.9958 | -0.18696 | 121.503 | 121.2594 | 121.1682 | -0.15921 | -0.017267 | 10.7466 | -0.16624 | 121.172 | 121.3787 | 121.359 | -0.18704 | 0.092555 | 0.090363 | 0.17041 | 0.064808 | -0.027747 | -0.15322 | -0.24449 | 0.064727 | -0.24069 | 0.2345 | 0.08553 | 0.020803 | -0.033936 | -0.053627 | 121.7548 | 121.5112 | 121.4199 | 3.2476 | -121.5719 | 121.4237 | 121.6305 | 121.6108 | 10.9984 | -121.5997
1405.0156 | 121.6873 | -0.24261 | 121.4584 | 1.4211e-13 | -0.025722 | -0.00095092 | 0.063103 | -0.0047732 | 0.056896 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013087 | 0.060351 | -0.081363 | 2.9958 | -0.17781 | 121.5076 | 121.2594 | 121.1682 | -0.15921 | -0.021846 | 10.742 | -0.16166 | 121.172 | 121.3787 | 121.359 | -0.18704 | 0.0834 | 0.049166 | 0.16125 | 0.064809 | -0.018591 | -0.199 | -0.29027 | 0.055572 | -0.28646 | 0.22077 | 0.080954 | 0.025382 | -0.079712 | -0.099403 | 121.7502 | 121.5021 | 121.4108 | 3.2384 | -121.6176 | 121.4146 | 121.6213 | 121.6016 | 10.9846 | -121.6455
1406.7812 | 121.6232 | -0.2655 | 121.4539 | 1.4211e-13 | -0.025936 | -0.0015919 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.013515 | 0.059923 | -0.081363 | 3.0187 | -0.17781 | 121.5122 | 121.2594 | 121.1682 | -0.15921 | -0.021846 | 10.7512 | -0.16166 | 121.1765 | 121.3741 | 121.3636 | -0.19162 | 0.10629 | 0.058322 | 0.18414 | 0.087697 | -0.018591 | -0.19442 | -0.28569 | 0.073881 | -0.27731 | 0.24366 | 0.10384 | 0.029961 | -0.079712 | -0.090247 | 121.7777 | 121.5249 | 121.4337 | 3.2842 | -121.6131 | 121.4421 | 121.6396 | 121.6291 | 11.0167 | -121.6455
1408.5469 | 121.7148 | -0.21973 | 121.4127 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063103 | -0.0045596 | 0.056896 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063417 | 0.013087 | 0.059923 | -0.081363 | 2.9958 | -0.18238 | 121.5168 | 121.2549 | 121.1636 | -0.15006 | -0.012689 | 10.7329 | -0.17082 | 121.172 | 121.3741 | 121.359 | -0.19162 | 0.06967 | 0.1041 | 0.13836 | 0.037343 | -0.032327 | -0.1578 | -0.24907 | 0.028105 | -0.24069 | 0.20704 | 0.048908 | 0.020803 | -0.038514 | -0.053627 | 121.7365 | 121.4746 | 121.3833 | 3.2155 | -121.5627 | 121.3917 | 121.5939 | 121.5788 | 10.9526 | -121.6043
1410.2656 | 121.7651 | -0.21973 | 121.4218 | 1.4211e-13 | -0.025936 | -0.0011645 | 0.062889 | -0.0047732 | 0.056896 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.013301 | 0.060137 | -0.076785 | 3.0095 | -0.18238 | 121.5076 | 121.2549 | 121.1682 | -0.15464 | -0.031003 | 10.7145 | -0.16166 | 121.1811 | 121.3787 | 121.3636 | -0.19162 | 0.065091 | 0.085787 | 0.14294 | 0.037343 | -0.027748 | -0.16695 | -0.25365 | 0.028105 | -0.24069 | 0.18872 | 0.058066 | 0.029961 | -0.043091 | -0.058204 | 121.7273 | 121.4746 | 121.3879 | 3.2293 | -121.5764 | 121.4009 | 121.5984 | 121.5833 | 10.9343 | -121.6134
1412.0312 | 121.7697 | -0.19684 | 121.3852 | 1.4211e-13 | -0.026149 | -0.0011645 | 0.063316 | -0.0047732 | 0.056896 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063631 | 0.013087 | 0.05971 | -0.076785 | 3.0095 | -0.17781 | 121.503 | 121.2594 | 121.1636 | -0.15464 | -0.031003 | 10.6871 | -0.1525 | 121.172 | 121.3741 | 121.3636 | -0.18704 | 0.042202 | 0.11783 | 0.12005 | 0.019032 | -0.02317 | -0.12575 | -0.2216 | 0.009795 | -0.21322 | 0.16584 | 0.044334 | 0.034539 | -0.011048 | -0.021583 | 121.6999 | 121.4563 | 121.3604 | 3.2064 | -121.5398 | 121.3688 | 121.571 | 121.5604 | 10.8839 | -121.5722
1413.7344 | 121.6736 | -0.26093 | 121.4081 | 1.4211e-13 | -0.025722 | -0.00095092 | 0.063316 | -0.004987 | 0.05711 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.012874 | 0.060137 | -0.081363 | 3.0095 | -0.19154 | 121.5122 | 121.264 | 121.1727 | -0.15006 | -0.021846 | 10.6459 | -0.15708 | 121.1765 | 121.3833 | 121.359 | -0.1962 | 0.11087 | 0.1041 | 0.17956 | 0.069384 | -0.041484 | -0.14406 | -0.23534 | 0.064725 | -0.23153 | 0.23908 | 0.10384 | 0.039117 | -0.024779 | -0.049049 | 121.7731 | 121.5249 | 121.4337 | 3.2705 | -121.5581 | 121.4375 | 121.6442 | 121.62 | 10.9068 | -121.6043
1415.5 | 121.7697 | -0.20142 | 121.376 | 1.4211e-13 | -0.025936 | -0.0015919 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.013087 | 0.059923 | -0.085942 | 3.0095 | -0.18696 | 121.5076 | 121.2549 | 121.1682 | -0.15921 | -0.017267 | 10.7145 | -0.16624 | 121.1765 | 121.3787 | 121.3636 | -0.20536 | 0.042201 | 0.13156 | 0.11547 | 0.014454 | -0.027747 | -0.12118 | -0.20787 | -0.003942 | -0.19949 | 0.18415 | 0.035176 | 0.039118 | 0.002685 | -0.012428 | 121.709 | 121.4563 | 121.3696 | 3.211 | -121.5353 | 121.378 | 121.5801 | 121.565 | 10.916 | -121.5814
1417.2188 | 121.7514 | -0.21515 | 121.4035 | 1.4211e-13 | -0.025936 | -0.0018055 | 0.063316 | -0.0045596 | 0.05711 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063203 | 0.01266 | 0.05971 | -0.076785 | 3.0095 | -0.18238 | 121.5122 | 121.2594 | 121.1636 | -0.15464 | -0.021846 | 10.6962 | -0.16166 | 121.1765 | 121.3696 | 121.359 | -0.19162 | 0.060513 | 0.10868 | 0.13836 | 0.032765 | -0.027748 | -0.14406 | -0.23991 | 0.023527 | -0.22695 | 0.1933 | 0.053488 | 0.029961 | -0.033937 | -0.044471 | 121.7273 | 121.4746 | 121.3787 | 3.2247 | -121.5581 | 121.3917 | 121.5847 | 121.5742 | 10.9114 | -121.5951
1418.9844 | 121.7285 | -0.21973 | 121.4355 | 1.4211e-13 | -0.025936 | -0.0011645 | 0.063103 | -0.0047732 | 0.05711 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.012874 | 0.05971 | -0.072207 | 3.0095 | -0.18696 | 121.5076 | 121.2594 | 121.1682 | -0.15921 | -0.017267 | 10.6733 | -0.16166 | 121.1674 | 121.3741 | 121.359 | -0.18704 | 0.060512 | 0.072054 | 0.14752 | 0.032765 | -0.027747 | -0.17611 | -0.26738 | 0.032684 | -0.26815 | 0.20246 | 0.058066 | 0.025382 | -0.061402 | -0.076515 | 121.7273 | 121.4792 | 121.3879 | 3.2293 | -121.5948 | 121.3871 | 121.5939 | 121.5788 | 10.8931 | -121.6226
1420.6875 | 121.6553 | -0.24719 | 121.4172 | 1.4211e-13 | -0.025936 | -0.0013783 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063631 | 0.013515 | 0.060351 | -0.081363 | 3.0141 | -0.18696 | 121.5076 | 121.2503 | 121.1682 | -0.15006 | -0.017267 | 10.6779 | -0.16166 | 121.172 | 121.3787 | 121.3636 | -0.20078 | 0.097135 | 0.090365 | 0.16583 | 0.06023 | -0.036905 | -0.16696 | -0.24907 | 0.046413 | -0.24527 | 0.22992 | 0.085531 | 0.039118 | -0.038513 | -0.053626 | 121.7548 | 121.4975 | 121.4154 | 3.2613 | -121.5673 | 121.4192 | 121.6259 | 121.6108 | 10.9251 | -121.618
1422.7344 | 121.7926 | -0.19684 | 121.3852 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.063417 | 0.013301 | 0.060137 | -0.081363 | 3.005 | -0.18238 | 121.5122 | 121.2549 | 121.1682 | -0.15921 | -0.00811 | 10.6138 | -0.16624 | 121.172 | 121.3787 | 121.359 | -0.18704 | 0.037623 | 0.12699 | 0.11548 | 0.014454 | -0.023169 | -0.13033 | -0.21703 | 0.009795 | -0.21322 | 0.18873 | 0.030598 | 0.020803 | -0.00647 | -0.026161 | 121.709 | 121.4517 | 121.365 | 3.2018 | -121.5444 | 121.3688 | 121.5756 | 121.5559 | 10.8106 | -121.5722
1426.4531 | 121.6736 | -0.23804 | 121.431 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063103 | -0.0047732 | 0.05711 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013087 | 0.05971 | -0.076785 | 3.0233 | -0.17781 | 121.5168 | 121.264 | 121.1682 | -0.15921 | -0.012689 | 10.6642 | -0.15708 | 121.172 | 121.3741 | 121.3636 | -0.19162 | 0.078822 | 0.085789 | 0.16125 | 0.060231 | -0.018591 | -0.16695 | -0.2628 | 0.046415 | -0.259 | 0.22535 | 0.080954 | 0.034539 | -0.056824 | -0.067359 | 121.7548 | 121.5021 | 121.4062 | 3.2613 | -121.5902 | 121.41 | 121.6122 | 121.6016 | 10.9022 | -121.6226
1430.0938 | 121.7194 | -0.21515 | 121.3989 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063316 | -0.0045596 | 0.056896 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063417 | 0.013301 | 0.060137 | -0.081363 | 3.0233 | -0.17781 | 121.5213 | 121.264 | 121.1727 | -0.15921 | -0.021846 | 10.6504 | -0.16624 | 121.1765 | 121.3833 | 121.359 | -0.19162 | 0.055934 | 0.12241 | 0.13379 | 0.037343 | -0.018591 | -0.13491 | -0.22618 | 0.023527 | -0.22238 | 0.1933 | 0.048909 | 0.025382 | -0.015624 | -0.039894 | 121.7365 | 121.4792 | 121.3879 | 3.2384 | -121.5581 | 121.3917 | 121.5985 | 121.5742 | 10.8656 | -121.5905
1435.9375 | 121.7697 | -0.21515 | 121.4081 | 1.4211e-13 | -0.026363 | -0.0013783 | 0.063103 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.013301 | 0.059923 | -0.081363 | 3.0279 | -0.18696 | 121.5168 | 121.264 | 121.1773 | -0.15464 | -0.003531 | 10.6688 | -0.15708 | 121.1765 | 121.3879 | 121.3636 | -0.17788 | 0.060513 | 0.10868 | 0.13379 | 0.028187 | -0.032326 | -0.14406 | -0.23076 | 0.037264 | -0.23153 | 0.21162 | 0.058066 | 0.020802 | -0.0202 | -0.044471 | 121.7319 | 121.4792 | 121.3925 | 3.243 | -121.5627 | 121.3917 | 121.603 | 121.5788 | 10.8839 | -121.586
1437.7031 | 121.6736 | -0.23346 | 121.4355 | 1.4211e-13 | -0.026149 | -0.0011645 | 0.063316 | -0.0047732 | 0.056896 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013087 | 0.060137 | -0.076785 | 3.0324 | -0.18238 | 121.5213 | 121.264 | 121.1819 | -0.15006 | -0.012689 | 10.6642 | -0.16166 | 121.1765 | 121.3787 | 121.3682 | -0.18704 | 0.083402 | 0.085789 | 0.15667 | 0.051075 | -0.032327 | -0.17153 | -0.25365 | 0.046416 | -0.259 | 0.22077 | 0.071798 | 0.025382 | -0.056824 | -0.067358 | 121.7548 | 121.4975 | 121.4154 | 3.2659 | -121.5856 | 121.41 | 121.6122 | 121.6016 | 10.8976 | -121.6226
1439.4688 | 121.6644 | -0.24719 | 121.4355 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063316 | -0.0045596 | 0.05711 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063203 | 0.013087 | 0.05971 | -0.076785 | 3.0462 | -0.18238 | 121.5122 | 121.2686 | 121.1727 | -0.15006 | -0.012689 | 10.6779 | -0.15708 | 121.1765 | 121.3879 | 121.3682 | -0.19162 | 0.097135 | 0.076632 | 0.17041 | 0.064808 | -0.032327 | -0.16695 | -0.2628 | 0.05557 | -0.259 | 0.2345 | 0.090109 | 0.034539 | -0.047666 | -0.067358 | 121.7594 | 121.5158 | 121.4199 | 3.2934 | -121.5856 | 121.4237 | 121.6351 | 121.6154 | 10.9251 | -121.6272
1441.1719 | 121.637 | -0.25177 | 121.4722 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063103 | -0.0045596 | 0.05711 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.013087 | 0.059923 | -0.076785 | 3.0508 | -0.17781 | 121.5168 | 121.2686 | 121.1773 | -0.14548 | -0.012689 | 10.6825 | -0.1525 | 121.1765 | 121.3833 | 121.359 | -0.18704 | 0.10629 | 0.04459 | 0.17499 | 0.073964 | -0.032328 | -0.20357 | -0.29484 | 0.064727 | -0.29562 | 0.23908 | 0.099266 | 0.034539 | -0.088866 | -0.11314 | 121.7685 | 121.5204 | 121.4291 | 3.3025 | -121.6176 | 121.4283 | 121.6351 | 121.6108 | 10.9343 | -121.6592
1442.9375 | 121.7651 | -0.2243 | 121.4218 | 1.4211e-13 | -0.025722 | -0.0015919 | 0.063316 | -0.0052006 | 0.056896 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063631 | 0.013515 | 0.059923 | -0.081363 | 3.0416 | -0.18696 | 121.5168 | 121.2686 | 121.1727 | -0.15464 | -0.012689 | 10.7283 | -0.15708 | 121.1765 | 121.3833 | 121.3636 | -0.18704 | 0.069668 | 0.094944 | 0.14294 | 0.037342 | -0.032326 | -0.15322 | -0.24907 | 0.037261 | -0.24527 | 0.21161 | 0.067221 | 0.02996 | -0.038512 | -0.058204 | 121.7411 | 121.4929 | 121.397 | 3.2659 | -121.5764 | 121.4009 | 121.6076 | 121.5879 | 10.9526 | -121.6089
1444.6562 | 121.7514 | -0.20142 | 121.4127 | 1.4211e-13 | -0.025936 | -0.0011645 | 0.063316 | -0.0047732 | 0.056896 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063203 | 0.013301 | 0.059923 | -0.085942 | 3.0508 | -0.17781 | 121.5168 | 121.2686 | 121.1636 | -0.15464 | -0.00811 | 10.7603 | -0.15708 | 121.1765 | 121.3879 | 121.3682 | -0.18704 | 0.04678 | 0.1041 | 0.11547 | 0.02361 | -0.02317 | -0.14406 | -0.24907 | 0.014373 | -0.23611 | 0.19331 | 0.044333 | 0.02996 | -0.024778 | -0.04447 | 121.7182 | 121.47 | 121.365 | 3.2522 | -121.5673 | 121.378 | 121.5893 | 121.5696 | 10.9617 | -121.5997
1446.4062 | 121.7285 | -0.21515 | 121.431 | 1.4211e-13 | -0.026149 | -0.0011645 | 0.063103 | -0.004987 | 0.05711 | -0.02518 | 0.00013254 | -0.00026913 | 0.06299 | 0.013515 | 0.05971 | -0.081363 | 3.0462 | -0.17781 | 121.5168 | 121.2778 | 121.1773 | -0.15006 | -0.017267 | 10.7283 | -0.16166 | 121.1765 | 121.3879 | 121.3682 | -0.1962 | 0.065092 | 0.085789 | 0.13379 | 0.037343 | -0.027749 | -0.15322 | -0.25365 | 0.018949 | -0.25442 | 0.19788 | 0.053488 | 0.034539 | -0.043088 | -0.06278 | 121.7319 | 121.4929 | 121.3925 | 3.2613 | -121.581 | 121.3917 | 121.603 | 121.5833 | 10.9434 | -121.6272
1448.1719 | 121.7697 | -0.18768 | 121.4035 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063316 | -0.0045596 | 0.056683 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063203 | 0.013087 | 0.059923 | -0.076785 | 3.0553 | -0.18238 | 121.5168 | 121.2686 | 121.1727 | -0.15464 | -0.00811 | 10.742 | -0.16166 | 121.1765 | 121.3787 | 121.3682 | -0.1962 | 0.033047 | 0.11325 | 0.1109 | 0.005299 | -0.027748 | -0.13491 | -0.23076 | -0.008517 | -0.22695 | 0.17957 | 0.026022 | 0.034539 | -0.02478 | -0.035314 | 121.7044 | 121.4563 | 121.3604 | 3.243 | -121.5581 | 121.3642 | 121.5664 | 121.5559 | 10.9297 | -121.5997
1449.875 | 121.7697 | -0.20142 | 121.4493 | 1.4211e-13 | -0.026149 | -0.00095092 | 0.06353 | -0.0045596 | 0.056896 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063631 | 0.013728 | 0.059923 | -0.072207 | 3.0599 | -0.18238 | 121.5259 | 121.2686 | 121.1819 | -0.14548 | -0.026425 | 10.7832 | -0.15708 | 121.1811 | 121.3879 | 121.3682 | -0.18704 | 0.055938 | 0.076634 | 0.12921 | 0.019032 | -0.036906 | -0.18068 | -0.26738 | 0.014373 | -0.26815 | 0.17499 | 0.044333 | 0.02996 | -0.061399 | -0.081091 | 121.7273 | 121.47 | 121.3833 | 3.2613 | -121.5948 | 121.3825 | 121.5893 | 121.5696 | 10.9846 | -121.6363
1451.5781 | 121.7148 | -0.2243 | 121.3943 | 1.4211e-13 | -0.026577 | -0.0011645 | 0.06353 | -0.0045596 | 0.056683 | -0.0099194 | -8.1262e-05 | 0.00037167 | 0.063203 | 0.013087 | 0.05971 | -0.076785 | 3.0691 | -0.17781 | 121.5122 | 121.2686 | 121.1819 | -0.15464 | -0.00811 | 10.7649 | -0.15708 | 121.1765 | 121.3925 | 121.3682 | -0.18246 | 0.069668 | 0.11783 | 0.14752 | 0.046498 | -0.02317 | -0.12575 | -0.21245 | 0.04184 | -0.2178 | 0.21619 | 0.067221 | 0.025381 | -0.001889 | -0.026159 | 121.7365 | 121.4929 | 121.4062 | 3.2934 | -121.549 | 121.4009 | 121.6168 | 121.5925 | 10.9892 | -121.5768
1453.3281 | 121.6507 | -0.26093 | 121.4401 | 1.4211e-13 | -0.026149 | -0.0015919 | 0.063103 | -0.0047732 | 0.05711 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.013301 | 0.05971 | -0.072207 | 3.0691 | -0.18696 | 121.5168 | 121.2732 | 121.1819 | -0.15464 | -0.00811 | 10.7557 | -0.15708 | 121.1765 | 121.3925 | 121.3682 | -0.19162 | 0.10629 | 0.076633 | 0.18872 | 0.073963 | -0.032326 | -0.16695 | -0.25822 | 0.069303 | -0.26358 | 0.25282 | 0.10384 | 0.034539 | -0.047666 | -0.071936 | 121.7777 | 121.5341 | 121.4428 | 3.33 | -121.5948 | 121.4375 | 121.6534 | 121.6291 | 11.0167 | -121.6317
1455.0469 | 121.7926 | -0.19226 | 121.3989 | 1.4211e-13 | -0.026363 | -0.0018055 | 0.063316 | -0.0047732 | 0.057324 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013087 | 0.060137 | -0.076785 | 3.0691 | -0.17781 | 121.5213 | 121.2823 | 121.1819 | -0.15006 | -0.012689 | 10.7008 | -0.16166 | 121.1857 | 121.3833 | 121.3636 | -0.19162 | 0.042204 | 0.12241 | 0.11548 | 0.014455 | -0.027749 | -0.11659 | -0.21702 | 0.000639 | -0.21322 | 0.17957 | 0.0306 | 0.029961 | -0.015624 | -0.035316 | 121.7136 | 121.4746 | 121.3742 | 3.2613 | -121.549 | 121.378 | 121.5756 | 121.5559 | 10.8931 | -121.5905
1456.8125 | 121.6415 | -0.27008 | 121.431 | 1.4211e-13 | -0.025936 | -0.0011645 | 0.062889 | -0.0047732 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.013087 | 0.05971 | -0.072207 | 3.0553 | -0.17781 | 121.5213 | 121.2732 | 121.1819 | -0.15921 | -0.017267 | 10.742 | -0.15708 | 121.1765 | 121.3925 | 121.3682 | -0.18246 | 0.11087 | 0.090367 | 0.19787 | 0.092275 | -0.018591 | -0.15779 | -0.24907 | 0.087617 | -0.25442 | 0.25281 | 0.113 | 0.025381 | -0.03851 | -0.06278 | 121.7914 | 121.5433 | 121.452 | 3.3254 | -121.5902 | 121.4466 | 121.6625 | 121.6383 | 11.0121 | -121.6134
1458.5781 | 121.756 | -0.19684 | 121.4081 | 1.4211e-13 | -0.026149 | -0.0015919 | 0.063103 | -0.0045596 | 0.05711 | -0.0022889 | 0.00013254 | 0.00037167 | 0.063631 | 0.013515 | 0.060137 | -0.072207 | 3.0462 | -0.17781 | 121.5305 | 121.2778 | 121.1865 | -0.15006 | -0.00811 | 10.7191 | -0.15708 | 121.1811 | 121.3879 | 121.3682 | -0.18704 | 0.046781 | 0.12241 | 0.12463 | 0.019032 | -0.027749 | -0.13033 | -0.2216 | 0.009795 | -0.22695 | 0.18873 | 0.039755 | 0.02996 | -0.0202 | -0.039892 | 121.7273 | 121.4746 | 121.3833 | 3.243 | -121.5581 | 121.378 | 121.5847 | 121.565 | 10.916 | -121.5951
1460.2656 | 121.6324 | -0.24261 | 121.4493 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063103 | -0.0052006 | 0.056896 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.013301 | 0.059923 | -0.076785 | 3.0462 | -0.18238 | 121.5213 | 121.2732 | 121.1819 | -0.14548 | -0.021846 | 10.7329 | -0.15708 | 121.1811 | 121.3879 | 121.3728 | -0.19162 | 0.097137 | 0.072056 | 0.16583 | 0.060231 | -0.036906 | -0.17611 | -0.26738 | 0.050993 | -0.26815 | 0.22077 | 0.085532 | 0.034539 | -0.061399 | -0.076512 | 121.764 | 121.5158 | 121.4245 | 3.2888 | -121.5948 | 121.4237 | 121.6305 | 121.6154 | 10.9755 | -121.6409
1462.0312 | 121.7834 | -0.20142 | 121.4081 | 1.4211e-13 | -0.026149 | -0.0015919 | 0.06353 | -0.0047732 | 0.056896 | -0.0099194 | 0.00055974 | 0.00015807 | 0.063417 | 0.013728 | 0.059923 | -0.076785 | 3.0553 | -0.18696 | 121.5213 | 121.2732 | 121.1819 | -0.15921 | -0.017267 | 10.7512 | -0.15708 | 121.1811 | 121.3925 | 121.3682 | -0.19162 | 0.042201 | 0.11326 | 0.12463 | 0.014454 | -0.027747 | -0.13491 | -0.22618 | 0.009794 | -0.22695 | 0.18415 | 0.044333 | 0.034539 | -0.015622 | -0.039892 | 121.7228 | 121.4746 | 121.3833 | 3.2568 | -121.5673 | 121.3825 | 121.5939 | 121.5696 | 10.9526 | -121.5997
1463.7344 | 121.701 | -0.21973 | 121.4081 | 1.4211e-13 | -0.026577 | -0.0015919 | 0.063316 | -0.0045596 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.013087 | 0.059923 | -0.076785 | 3.0599 | -0.18238 | 121.5122 | 121.2732 | 121.1865 | -0.15006 | -0.017267 | 10.7924 | -0.16166 | 121.1811 | 121.3879 | 121.3636 | -0.20078 | 0.06967 | 0.1041 | 0.14294 | 0.037343 | -0.032327 | -0.13491 | -0.2216 | 0.018948 | -0.22695 | 0.20246 | 0.058066 | 0.039118 | -0.0202 | -0.044471 | 121.7319 | 121.4929 | 121.4062 | 3.2796 | -121.5581 | 121.4009 | 121.6076 | 121.5833 | 11.0121 | -121.6089
1465.5 | 121.6782 | -0.25177 | 121.4493 | 1.4211e-13 | -0.026363 | -0.0011645 | 0.063103 | -0.0045596 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013301 | 0.05971 | -0.081363 | 3.0599 | -0.17781 | 121.5168 | 121.2778 | 121.1819 | -0.15464 | -0.012689 | 10.8061 | -0.1525 | 121.1811 | 121.3879 | 121.3728 | -0.1962 | 0.097134 | 0.067478 | 0.17041 | 0.073964 | -0.02317 | -0.17153 | -0.26738 | 0.05557 | -0.26815 | 0.23908 | 0.099266 | 0.043696 | -0.061399 | -0.076512 | 121.7685 | 121.5295 | 121.4337 | 3.3117 | -121.6039 | 121.4329 | 121.6397 | 121.6245 | 11.0579 | -121.6455
1467.2812 | 121.6278 | -0.25635 | 121.4584 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063103 | -0.0047732 | 0.056469 | -0.0022889 | 0.00013254 | 0.00037167 | 0.062776 | 0.013515 | 0.059923 | -0.072207 | 3.0508 | -0.18238 | 121.5213 | 121.2686 | 121.1773 | -0.15464 | -0.012689 | 10.7557 | -0.16166 | 121.1811 | 121.3925 | 121.3682 | -0.18246 | 0.10171 | 0.062901 | 0.18414 | 0.073964 | -0.027748 | -0.18984 | -0.28111 | 0.073884 | -0.27731 | 0.24366 | 0.094687 | 0.020803 | -0.065976 | -0.090246 | 121.7777 | 121.5249 | 121.4337 | 3.3071 | -121.6131 | 121.4375 | 121.6488 | 121.6245 | 11.0121 | -121.6409
1468.9844 | 121.7239 | -0.2243 | 121.4172 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.062675 | -0.0047732 | 0.05711 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063631 | 0.013728 | 0.05971 | -0.076785 | 3.0553 | -0.19154 | 121.5259 | 121.2732 | 121.1865 | -0.15006 | -0.012689 | 10.7374 | -0.1525 | 121.1811 | 121.3925 | 121.3636 | -0.1962 | 0.074247 | 0.10868 | 0.14752 | 0.032763 | -0.041484 | -0.14406 | -0.23076 | 0.028104 | -0.23611 | 0.21161 | 0.0718 | 0.043696 | -0.024777 | -0.053626 | 121.7502 | 121.4975 | 121.4108 | 3.2796 | -121.5673 | 121.4054 | 121.6168 | 121.5879 | 10.9617 | -121.6134
1470.7656 | 121.6324 | -0.24719 | 121.463 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.062889 | -0.0047732 | 0.056896 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063417 | 0.013515 | 0.05971 | -0.076785 | 3.0645 | -0.18238 | 121.5259 | 121.2778 | 121.1865 | -0.15464 | -0.012689 | 10.7329 | -0.15708 | 121.1903 | 121.397 | 121.3728 | -0.18704 | 0.092556 | 0.062901 | 0.17041 | 0.064808 | -0.027748 | -0.18526 | -0.27653 | 0.060149 | -0.27273 | 0.2345 | 0.090109 | 0.02996 | -0.065975 | -0.090245 | 121.7731 | 121.5249 | 121.4337 | 3.3117 | -121.6176 | 121.4375 | 121.6442 | 121.62 | 10.98 | -121.6501
1472.4531 | 121.7697 | -0.1831 | 121.4127 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063103 | -0.0045596 | 0.056683 | -0.01755 | -0.00029486 | 0.00015807 | 0.063417 | 0.013515 | 0.05971 | -0.072207 | 3.0828 | -0.18238 | 121.5213 | 121.2778 | 121.1865 | -0.15464 | -0.012689 | 10.6962 | -0.1525 | 121.1811 | 121.4016 | 121.3636 | -0.19162 | 0.028469 | 0.10868 | 0.1109 | 0.000721 | -0.027748 | -0.13491 | -0.22618 | -0.008517 | -0.23153 | 0.17042 | 0.030601 | 0.039118 | -0.011043 | -0.049049 | 121.7044 | 121.4609 | 121.3696 | 3.2659 | -121.5673 | 121.3642 | 121.5847 | 121.5467 | 10.8793 | -121.6043
1474.2344 | 121.756 | -0.21973 | 121.4127 | 1.4211e-13 | -0.02679 | -0.0018055 | 0.062889 | -0.0045596 | 0.056683 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.013515 | 0.05971 | -0.072207 | 3.0736 | -0.18238 | 121.5213 | 121.2732 | 121.1865 | -0.15921 | -0.017267 | 10.7603 | -0.1525 | 121.1857 | 121.397 | 121.3728 | -0.18246 | 0.060512 | 0.10868 | 0.14752 | 0.037343 | -0.023169 | -0.13948 | -0.22618 | 0.037263 | -0.22695 | 0.20246 | 0.067223 | 0.02996 | -0.015621 | -0.039891 | 121.7411 | 121.4929 | 121.4062 | 3.2934 | -121.5719 | 121.4054 | 121.6168 | 121.5925 | 10.9801 | -121.5951
1476 | 121.756 | -0.19226 | 121.4081 | 1.4211e-13 | -0.026577 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | 0.0053411 | 0.00034614 | -0.00026913 | 0.062776 | 0.013515 | 0.060137 | -0.076785 | 3.0828 | -0.17781 | 121.5259 | 121.2869 | 121.1865 | -0.15464 | -0.00811 | 10.7329 | -0.14793 | 121.1857 | 121.397 | 121.3728 | -0.18704 | 0.037625 | 0.11783 | 0.11548 | 0.014455 | -0.02317 | -0.12117 | -0.2216 | 0.005218 | -0.22237 | 0.18415 | 0.044336 | 0.039118 | -0.011043 | -0.035313 | 121.7182 | 121.4792 | 121.3787 | 3.2751 | -121.5627 | 121.378 | 121.5893 | 121.565 | 10.9251 | -121.5951
1477.7031 | 121.7789 | -0.19226 | 121.4127 | 1.4211e-13 | -0.026577 | -0.0011645 | 0.063316 | -0.0045596 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.013301 | 0.05971 | -0.076785 | 3.0874 | -0.17323 | 121.5351 | 121.2778 | 121.1865 | -0.15921 | -0.017267 | 10.7512 | -0.15708 | 121.1857 | 121.4016 | 121.3728 | -0.18704 | 0.033046 | 0.12241 | 0.11548 | 0.019034 | -0.014012 | -0.13491 | -0.22618 | 0.005218 | -0.22695 | 0.17499 | 0.035178 | 0.02996 | -0.011043 | -0.039891 | 121.7273 | 121.47 | 121.3787 | 3.2796 | -121.5719 | 121.378 | 121.5939 | 121.565 | 10.9434 | -121.5997
1479.4688 | 121.7606 | -0.18768 | 121.4035 | 1.4211e-13 | -0.025936 | -0.0013783 | 0.063103 | -0.0045596 | 0.05711 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013301 | 0.059496 | -0.076785 | 3.0736 | -0.18238 | 121.5305 | 121.2869 | 121.1819 | -0.15006 | -0.00811 | 10.7145 | -0.1525 | 121.1949 | 121.397 | 121.3819 | -0.18704 | 0.037626 | 0.12699 | 0.1109 | 0.005299 | -0.032327 | -0.11659 | -0.2216 | 0.00064 | -0.20864 | 0.17957 | 0.035179 | 0.034539 | -0.006465 | -0.021578 | 121.7182 | 121.4746 | 121.3696 | 3.2613 | -121.5536 | 121.3825 | 121.5847 | 121.5696 | 10.9022 | -121.5905
1481.1719 | 121.6873 | -0.20142 | 121.4172 | 1.4211e-13 | -0.026149 | -0.0013783 | 0.063316 | -0.004987 | 0.05711 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013087 | 0.059923 | -0.076785 | 3.0736 | -0.17781 | 121.5259 | 121.2823 | 121.1865 | -0.15464 | -0.017267 | 10.7557 | -0.1525 | 121.1857 | 121.3925 | 121.3773 | -0.18704 | 0.04678 | 0.10868 | 0.12463 | 0.02361 | -0.02317 | -0.1349 | -0.23076 | 0.014373 | -0.23153 | 0.18415 | 0.048912 | 0.034539 | -0.024777 | -0.03989 | 121.7273 | 121.4837 | 121.3879 | 3.2751 | -121.5719 | 121.3871 | 121.5939 | 121.5788 | 10.9572 | -121.6043
1482.9375 | 121.7194 | -0.21057 | 121.4355 | 1.4211e-13 | -0.026363 | -0.0013783 | 0.063316 | -0.0047732 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.013728 | 0.05971 | -0.072207 | 3.0691 | -0.18238 | 121.5168 | 121.2823 | 121.1865 | -0.15006 | -0.00811 | 10.7512 | -0.1525 | 121.1903 | 121.4016 | 121.3682 | -0.18704 | 0.060514 | 0.081211 | 0.13836 | 0.028187 | -0.032327 | -0.15321 | -0.24907 | 0.023528 | -0.24526 | 0.20246 | 0.058067 | 0.034539 | -0.033931 | -0.067358 | 121.7273 | 121.4929 | 121.3971 | 3.2796 | -121.5856 | 121.4009 | 121.6122 | 121.5788 | 10.9617 | -121.6226
1484.6719 | 121.6827 | -0.23804 | 121.463 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063103 | -0.0045596 | 0.056896 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.063631 | 0.013515 | 0.05971 | -0.072207 | 3.1011 | -0.17781 | 121.5351 | 121.2778 | 121.1956 | -0.15464 | -0.012689 | 10.7054 | -0.15708 | 121.1903 | 121.397 | 121.3682 | -0.1962 | 0.083401 | 0.072058 | 0.16583 | 0.060231 | -0.02317 | -0.18526 | -0.26738 | 0.041837 | -0.27273 | 0.22535 | 0.080954 | 0.039117 | -0.065975 | -0.094824 | 121.7731 | 121.5158 | 121.4337 | 3.3392 | -121.6176 | 121.4283 | 121.6351 | 121.6062 | 10.9434 | -121.6592
1486.4375 | 121.6232 | -0.25635 | 121.463 | 1.4211e-13 | -0.026577 | -0.0015919 | 0.062889 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.013515 | 0.05971 | -0.072207 | 3.1011 | -0.17781 | 121.5305 | 121.2869 | 121.1865 | -0.15006 | -0.003531 | 10.6733 | -0.1525 | 121.1857 | 121.4062 | 121.3773 | -0.18246 | 0.10629 | 0.06748 | 0.18414 | 0.078542 | -0.027749 | -0.1761 | -0.27653 | 0.073884 | -0.27731 | 0.25282 | 0.10384 | 0.02996 | -0.056818 | -0.085667 | 121.7868 | 121.5433 | 121.4428 | 3.3575 | -121.6131 | 121.4421 | 121.6625 | 121.6337 | 10.9297 | -121.6455
1488.1406 | 121.6461 | -0.23804 | 121.4584 | 1.4211e-13 | -0.026577 | -0.0018055 | 0.063103 | -0.0045596 | 0.057324 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.013515 | 0.060137 | -0.085942 | 3.1149 | -0.18238 | 121.5351 | 121.2823 | 121.1865 | -0.15006 | -0.00811 | 10.8061 | -0.1525 | 121.1857 | 121.4016 | 121.3819 | -0.18704 | 0.08798 | 0.076636 | 0.15209 | 0.055653 | -0.032327 | -0.1761 | -0.27195 | 0.050994 | -0.27273 | 0.22993 | 0.085533 | 0.034539 | -0.056819 | -0.07651 | 121.7731 | 121.5204 | 121.4245 | 3.3529 | -121.6085 | 121.4237 | 121.6397 | 121.62 | 11.0442 | -121.6455
1489.9062 | 121.7285 | -0.20599 | 121.4081 | 1.4211e-13 | -0.026577 | -0.0015919 | 0.062675 | -0.0047732 | 0.057324 | 0.0053411 | 0.00013254 | -0.00026913 | 0.063203 | 0.013942 | 0.059496 | -0.072207 | 3.1286 | -0.17781 | 121.5259 | 121.2823 | 121.1911 | -0.15006 | -0.00811 | 10.7557 | -0.15708 | 121.1857 | 121.397 | 121.3636 | -0.18704 | 0.055937 | 0.11783 | 0.13379 | 0.028188 | -0.027749 | -0.12575 | -0.21702 | 0.018951 | -0.22237 | 0.19788 | 0.048911 | 0.02996 | -0.011043 | -0.044471 | 121.7319 | 121.4883 | 121.3971 | 3.3346 | -121.5581 | 121.3917 | 121.603 | 121.5696 | 10.9617 | -121.5951
1491.6094 | 121.7651 | -0.20599 | 121.4447 | 1.4211e-13 | -0.026577 | -0.0018055 | 0.063316 | -0.004987 | 0.056896 | -0.0099194 | 0.00034614 | 0.00015807 | 0.06299 | 0.013301 | 0.059496 | -0.076785 | 3.1194 | -0.16865 | 121.5259 | 121.2823 | 121.1911 | -0.15006 | -0.003531 | 10.7832 | -0.1525 | 121.1949 | 121.397 | 121.3728 | -0.18704 | 0.055937 | 0.081212 | 0.12921 | 0.037345 | -0.018592 | -0.16237 | -0.25364 | 0.018951 | -0.24984 | 0.20246 | 0.05349 | 0.034539 | -0.047664 | -0.071934 | 121.7319 | 121.4883 | 121.3971 | 3.3254 | -121.5948 | 121.4009 | 121.603 | 121.5788 | 10.9892 | -121.6317
1493.375 | 121.756 | -0.19226 | 121.4081 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063316 | -0.0045596 | 0.056896 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062776 | 0.013942 | 0.05971 | -0.076785 | 3.1332 | -0.17781 | 121.5259 | 121.2961 | 121.1865 | -0.15464 | 0.001048 | 10.7832 | -0.14793 | 121.1903 | 121.4016 | 121.3773 | -0.18246 | 0.037625 | 0.11783 | 0.11548 | 0.014455 | -0.02317 | -0.11201 | -0.2216 | 0.009797 | -0.2178 | 0.19331 | 0.044336 | 0.034539 | -0.006465 | -0.030735 | 121.7182 | 121.4883 | 121.3787 | 3.3254 | -121.5627 | 121.3825 | 121.5939 | 121.5696 | 10.9755 | -121.5905
1495.0781 | 121.6782 | -0.24261 | 121.4218 | 1.4211e-13 | -0.02679 | -0.0011645 | 0.063103 | -0.0047732 | 0.05711 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.013728 | 0.05971 | -0.072207 | 3.1332 | -0.16865 | 121.5305 | 121.2869 | 121.1911 | -0.15006 | -0.012689 | 10.7374 | -0.15708 | 121.1857 | 121.397 | 121.3865 | -0.18704 | 0.092558 | 0.10868 | 0.17041 | 0.073966 | -0.018592 | -0.1349 | -0.23076 | 0.055572 | -0.23611 | 0.22993 | 0.085532 | 0.02996 | -0.024776 | -0.035311 | 121.7731 | 121.5295 | 121.4337 | 3.3758 | -121.5719 | 121.4283 | 121.6397 | 121.6291 | 10.98 | -121.6089
1496.8438 | 121.6782 | -0.24261 | 121.463 | 1.4211e-13 | -0.026363 | -0.0013783 | 0.063103 | -0.004987 | 0.056896 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.013515 | 0.059923 | -0.067628 | 3.124 | -0.17781 | 121.5259 | 121.2778 | 121.1956 | -0.15006 | -0.00811 | 10.7054 | -0.16166 | 121.1903 | 121.397 | 121.3819 | -0.18704 | 0.092558 | 0.062901 | 0.17499 | 0.064809 | -0.027749 | -0.18526 | -0.26738 | 0.055572 | -0.27273 | 0.2345 | 0.080954 | 0.025382 | -0.065975 | -0.081088 | 121.7685 | 121.5204 | 121.4383 | 3.3666 | -121.6131 | 121.4329 | 121.6397 | 121.6245 | 10.948 | -121.6501
1498.5469 | 121.7056 | -0.2243 | 121.4539 | 1.4211e-13 | -0.026577 | -0.0013783 | 0.062889 | -0.0052006 | 0.05711 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.013728 | 0.059923 | -0.081363 | 3.1103 | -0.18238 | 121.5305 | 121.2869 | 121.2002 | -0.15921 | -0.00811 | 10.7557 | -0.14793 | 121.1949 | 121.4016 | 121.3819 | -0.18704 | 0.065089 | 0.076636 | 0.14294 | 0.04192 | -0.023169 | -0.16694 | -0.25364 | 0.037261 | -0.25899 | 0.21619 | 0.076379 | 0.039118 | -0.052241 | -0.071932 | 121.7548 | 121.5112 | 121.4245 | 3.3346 | -121.6131 | 121.4192 | 121.6259 | 121.6062 | 10.9801 | -121.6409
1500.3125 | 121.669 | -0.23346 | 121.4447 | 1.4211e-13 | -0.026363 | -0.0018055 | 0.062889 | -0.004987 | 0.056896 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063203 | 0.013942 | 0.05971 | -0.072207 | 3.1194 | -0.18238 | 121.5351 | 121.2915 | 121.2002 | -0.15006 | -0.00811 | 10.7237 | -0.14793 | 121.1903 | 121.4016 | 121.3773 | -0.18246 | 0.083402 | 0.090369 | 0.16125 | 0.051075 | -0.032327 | -0.15321 | -0.24449 | 0.050995 | -0.25442 | 0.22535 | 0.085534 | 0.034539 | -0.043086 | -0.067356 | 121.7685 | 121.5249 | 121.4337 | 3.3529 | -121.5948 | 121.4237 | 121.6351 | 121.6108 | 10.9572 | -121.6272
1502.0781 | 121.6919 | -0.23804 | 121.431 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063316 | -0.0047732 | 0.056683 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063203 | 0.013301 | 0.059496 | -0.072207 | 3.1286 | -0.17781 | 121.5305 | 121.2961 | 121.1911 | -0.14548 | -0.00811 | 10.7191 | -0.15708 | 121.1857 | 121.397 | 121.3865 | -0.1962 | 0.092559 | 0.099524 | 0.16583 | 0.060231 | -0.032328 | -0.1349 | -0.23991 | 0.041837 | -0.24526 | 0.22993 | 0.080954 | 0.039117 | -0.033931 | -0.044466 | 121.7685 | 121.5341 | 121.4291 | 3.3666 | -121.5764 | 121.4237 | 121.6351 | 121.6245 | 10.9572 | -121.6272
1503.7812 | 121.7239 | -0.21057 | 121.4127 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063316 | -0.0047732 | 0.056896 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063417 | 0.013515 | 0.05971 | -0.072207 | 3.1194 | -0.17781 | 121.5305 | 121.2915 | 121.1865 | -0.15464 | -0.012689 | 10.742 | -0.1525 | 121.1903 | 121.4016 | 121.3728 | -0.19162 | 0.055935 | 0.11783 | 0.13836 | 0.032765 | -0.02317 | -0.12117 | -0.22618 | 0.018949 | -0.22237 | 0.19788 | 0.058067 | 0.039118 | -0.011043 | -0.039891 | 121.7411 | 121.5021 | 121.3971 | 3.33 | -121.5673 | 121.4009 | 121.6122 | 121.5833 | 10.9526 | -121.6043
1505.5625 | 121.756 | -0.20142 | 121.4172 | 1.4211e-13 | -0.02679 | -0.0011645 | 0.062889 | -0.004987 | 0.05711 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013728 | 0.05971 | -0.076785 | 3.124 | -0.17323 | 121.5351 | 121.2869 | 121.2048 | -0.14548 | -0.017267 | 10.7557 | -0.14793 | 121.1994 | 121.4016 | 121.3773 | -0.18704 | 0.055938 | 0.11783 | 0.12463 | 0.028189 | -0.027749 | -0.13032 | -0.21244 | 0.014373 | -0.2178 | 0.18415 | 0.053491 | 0.039118 | -0.01562 | -0.03989 | 121.7365 | 121.4883 | 121.4062 | 3.3254 | -121.5627 | 121.4009 | 121.603 | 121.5788 | 10.9572 | -121.6043
1507.3281 | 121.6599 | -0.25177 | 121.4539 | 1.4211e-13 | -0.026577 | -0.0013783 | 0.063316 | -0.0052006 | 0.056683 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013301 | 0.05971 | -0.067628 | 3.124 | -0.16865 | 121.5351 | 121.2869 | 121.1956 | -0.15006 | -0.00811 | 10.8015 | -0.15708 | 121.1903 | 121.4016 | 121.3773 | -0.18246 | 0.10171 | 0.081214 | 0.18414 | 0.083121 | -0.018592 | -0.16694 | -0.25822 | 0.069306 | -0.26357 | 0.24366 | 0.094687 | 0.025381 | -0.052241 | -0.076511 | 121.7868 | 121.5387 | 121.4474 | 3.3758 | -121.6039 | 121.4421 | 121.6534 | 121.6291 | 11.0533 | -121.6363
1509.0156 | 121.7651 | -0.20142 | 121.431 | 1.4211e-13 | -0.026577 | -0.0015919 | 0.063103 | -0.0052006 | 0.056683 | 0.012972 | -8.1262e-05 | -5.5534e-05 | 0.063417 | 0.013087 | 0.059496 | -0.072207 | 3.1423 | -0.16865 | 121.5305 | 121.2823 | 121.2002 | -0.15006 | -0.00811 | 10.7695 | -0.15708 | 121.1903 | 121.3925 | 121.3773 | -0.17788 | 0.051359 | 0.099524 | 0.12921 | 0.032767 | -0.018592 | -0.14864 | -0.23075 | 0.023531 | -0.24068 | 0.19331 | 0.044333 | 0.020802 | -0.03851 | -0.053623 | 121.7319 | 121.4837 | 121.4016 | 3.3437 | -121.581 | 121.3917 | 121.5939 | 121.5788 | 10.9709 | -121.6089
1510.7969 | 121.7239 | -0.23346 | 121.4493 | 1.4211e-13 | -0.026577 | -0.0011645 | 0.063316 | -0.004346 | 0.056896 | 0.0053411 | 0.00055974 | 0.00015807 | 0.063203 | 0.013728 | 0.05971 | -0.076785 | 3.1377 | -0.18238 | 121.5305 | 121.2869 | 121.1956 | -0.15464 | -0.00811 | 10.7832 | -0.14793 | 121.1949 | 121.4016 | 121.3773 | -0.18704 | 0.078823 | 0.081213 | 0.15667 | 0.051075 | -0.027748 | -0.16237 | -0.25364 | 0.046416 | -0.25442 | 0.22535 | 0.085534 | 0.039118 | -0.047664 | -0.071934 | 121.764 | 121.5204 | 121.4291 | 3.3712 | -121.6039 | 121.4283 | 121.6351 | 121.6108 | 11.0167 | -121.6363
1512.5 | 121.6599 | -0.22888 | 121.4539 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.062889 | -0.0052006 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.013515 | 0.05971 | -0.072207 | 3.1286 | -0.17323 | 121.5396 | 121.2869 | 121.1956 | -0.15006 | -0.003531 | 10.7832 | -0.14793 | 121.1903 | 121.397 | 121.3865 | -0.18704 | 0.078825 | 0.085793 | 0.15668 | 0.055655 | -0.02317 | -0.16694 | -0.25822 | 0.041839 | -0.26357 | 0.22535 | 0.080957 | 0.039118 | -0.056819 | -0.067354 | 121.7685 | 121.5158 | 121.4245 | 3.3575 | -121.6039 | 121.4192 | 121.6259 | 121.6154 | 11.0121 | -121.6409
1514.2656 | 121.6461 | -0.23804 | 121.4539 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.06353 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.013515 | 0.05971 | -0.072207 | 3.1194 | -0.17781 | 121.5396 | 121.2961 | 121.2002 | -0.15464 | -0.012689 | 10.7008 | -0.1525 | 121.1949 | 121.4016 | 121.3773 | -0.18246 | 0.083401 | 0.085793 | 0.16583 | 0.060231 | -0.02317 | -0.15779 | -0.25364 | 0.055573 | -0.25899 | 0.22535 | 0.085533 | 0.02996 | -0.052241 | -0.076511 | 121.7777 | 121.5341 | 121.4383 | 3.3575 | -121.6085 | 121.4329 | 121.6397 | 121.6154 | 10.9388 | -121.6363
1516.0156 | 121.637 | -0.23804 | 121.463 | 1.4211e-13 | -0.026363 | -0.0013783 | 0.063316 | -0.0047732 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.013515 | 0.059923 | -0.072207 | 3.1423 | -0.16865 | 121.5351 | 121.2961 | 121.2002 | -0.15006 | -0.012689 | 10.7603 | -0.16166 | 121.1949 | 121.4016 | 121.3819 | -0.18704 | 0.08798 | 0.072058 | 0.16583 | 0.069388 | -0.018592 | -0.16694 | -0.2628 | 0.050994 | -0.26815 | 0.22535 | 0.076376 | 0.025382 | -0.061397 | -0.081088 | 121.7731 | 121.5341 | 121.4383 | 3.3804 | -121.6131 | 121.4329 | 121.6397 | 121.62 | 10.9984 | -121.6501
1517.7188 | 121.7697 | -0.18768 | 121.4035 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063103 | -0.0045596 | 0.056896 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.013942 | 0.059282 | -0.072207 | 3.1606 | -0.16865 | 121.5351 | 121.2915 | 121.2002 | -0.14548 | -0.012689 | 10.8015 | -0.14793 | 121.1994 | 121.4016 | 121.3728 | -0.18704 | 0.042205 | 0.13157 | 0.11548 | 0.019034 | -0.023171 | -0.11201 | -0.20329 | 0.00064 | -0.20406 | 0.17499 | 0.039758 | 0.039118 | -0.001887 | -0.030735 | 121.7228 | 121.4792 | 121.3879 | 3.3483 | -121.549 | 121.3871 | 121.5893 | 121.5605 | 10.9892 | -121.5905
1519.4844 | 121.6278 | -0.25635 | 121.463 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063316 | -0.004987 | 0.056896 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.063631 | 0.013515 | 0.059496 | -0.076785 | 3.1606 | -0.17781 | 121.5396 | 121.2915 | 121.2048 | -0.15006 | -0.00811 | 10.7237 | -0.14335 | 121.1949 | 121.4016 | 121.3819 | -0.18704 | 0.10629 | 0.076637 | 0.17956 | 0.078542 | -0.027749 | -0.17152 | -0.25822 | 0.069305 | -0.26815 | 0.24824 | 0.113 | 0.043696 | -0.061397 | -0.081088 | 121.796 | 121.5478 | 121.4611 | 3.417 | -121.6131 | 121.4512 | 121.658 | 121.6383 | 10.98 | -121.6501
1521.25 | 121.7789 | -0.18768 | 121.4218 | 1.4211e-13 | -0.026363 | -0.0015919 | 0.063103 | -0.0052006 | 0.05711 | -0.0099194 | 0.00013254 | -0.00026913 | 0.063203 | 0.013301 | 0.05971 | -0.067628 | 3.1652 | -0.18238 | 121.5396 | 121.3006 | 121.2002 | -0.15464 | -0.00811 | 10.7008 | -0.15708 | 121.1949 | 121.4062 | 121.3911 | -0.17788 | 0.033047 | 0.11784 | 0.12005 | 0.005299 | -0.027748 | -0.12116 | -0.2216 | 0.009798 | -0.22695 | 0.17957 | 0.0306 | 0.020802 | -0.015619 | -0.030732 | 121.7273 | 121.4883 | 121.3879 | 3.3529 | -121.5764 | 121.3825 | 121.5939 | 121.5788 | 10.8885 | -121.5997
1522.9531 | 121.6461 | -0.22888 | 121.4493 | 1.4211e-13 | -0.02679 | -0.0011645 | 0.063103 | -0.004987 | 0.056896 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.013515 | 0.059923 | -0.072207 | 3.1561 | -0.17323 | 121.5396 | 121.3006 | 121.1956 | -0.15006 | -0.003531 | 10.7786 | -0.1525 | 121.204 | 121.4016 | 121.3819 | -0.18704 | 0.078825 | 0.09037 | 0.15668 | 0.055655 | -0.02317 | -0.14863 | -0.25364 | 0.041839 | -0.24526 | 0.22535 | 0.076378 | 0.034539 | -0.047664 | -0.067355 | 121.7685 | 121.5295 | 121.4245 | 3.3849 | -121.5993 | 121.4329 | 121.6305 | 121.6108 | 11.0075 | -121.6363
1524.7344 | 121.6461 | -0.24261 | 121.4813 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.062889 | -0.0047732 | 0.056896 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.013942 | 0.05971 | -0.06305 | 3.1744 | -0.17323 | 121.5442 | 121.3052 | 121.2002 | -0.14548 | -0.012689 | 10.7786 | -0.14793 | 121.2086 | 121.4016 | 121.3819 | -0.18246 | 0.097137 | 0.062905 | 0.17957 | 0.069388 | -0.027749 | -0.1761 | -0.28111 | 0.060151 | -0.27273 | 0.22993 | 0.09469 | 0.034539 | -0.079707 | -0.099398 | 121.7868 | 121.5478 | 121.4428 | 3.417 | -121.6268 | 121.4512 | 121.6442 | 121.6245 | 11.0213 | -121.6638
1526.4844 | 121.669 | -0.22888 | 121.4584 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.062889 | -0.0047732 | 0.056896 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013515 | 0.059496 | -0.076785 | 3.1561 | -0.17781 | 121.5396 | 121.3052 | 121.2048 | -0.14548 | -0.00811 | 10.7695 | -0.1525 | 121.1949 | 121.4016 | 121.3819 | -0.17788 | 0.083404 | 0.081215 | 0.1521 | 0.051076 | -0.032328 | -0.15321 | -0.25364 | 0.050997 | -0.26357 | 0.22077 | 0.076378 | 0.025381 | -0.056819 | -0.07651 | 121.7685 | 121.5341 | 121.4337 | 3.3849 | -121.6039 | 121.4237 | 121.6305 | 121.6108 | 10.9984 | -121.6363
1528.1875 | 121.7194 | -0.21515 | 121.4218 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.063103 | -0.004987 | 0.056683 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.013515 | 0.05971 | -0.067628 | 3.1698 | -0.17323 | 121.5396 | 121.3006 | 121.2002 | -0.1409 | -0.00811 | 10.7786 | -0.15708 | 121.1949 | 121.4062 | 121.3865 | -0.18246 | 0.07425 | 0.11784 | 0.14752 | 0.041922 | -0.032328 | -0.12116 | -0.2216 | 0.032685 | -0.22695 | 0.20704 | 0.058066 | 0.025381 | -0.015619 | -0.035311 | 121.7548 | 121.5158 | 121.4154 | 3.3849 | -121.5627 | 121.41 | 121.6213 | 121.6017 | 10.9938 | -121.6043
1529.9531 | 121.6599 | -0.25635 | 121.4584 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063103 | -0.0047732 | 0.056896 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.013942 | 0.059496 | -0.067628 | 3.1606 | -0.17323 | 121.5351 | 121.3052 | 121.2002 | -0.15006 | -0.012689 | 10.7283 | -0.1525 | 121.1994 | 121.4062 | 121.3773 | -0.18704 | 0.10629 | 0.076636 | 0.18872 | 0.083121 | -0.02317 | -0.15321 | -0.25822 | 0.069305 | -0.25899 | 0.24366 | 0.10384 | 0.034539 | -0.05224 | -0.081089 | 121.7914 | 121.5616 | 121.4566 | 3.417 | -121.6085 | 121.4558 | 121.6625 | 121.6337 | 10.9846 | -121.6455
1531.7188 | 121.7606 | -0.17853 | 121.4172 | 1.4211e-13 | -0.026577 | -0.0015919 | 0.06353 | -0.004987 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013515 | 0.05971 | -0.067628 | 3.1698 | -0.17323 | 121.5351 | 121.2915 | 121.2048 | -0.1409 | -0.017267 | 10.6459 | -0.14793 | 121.1949 | 121.4108 | 121.3911 | -0.18246 | 0.037629 | 0.11783 | 0.1109 | 0.005301 | -0.032328 | -0.12575 | -0.21244 | -0.003936 | -0.22237 | 0.16126 | 0.030603 | 0.034539 | -0.006462 | -0.026154 | 121.7136 | 121.47 | 121.3833 | 3.3483 | -121.5581 | 121.3734 | 121.5893 | 121.5696 | 10.8244 | -121.5997
1533.4688 | 121.7926 | -0.19226 | 121.4035 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063103 | -0.0047732 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.013515 | 0.059496 | -0.067628 | 3.1698 | -0.16865 | 121.5396 | 121.2961 | 121.1956 | -0.15464 | -0.00811 | 10.6733 | -0.13877 | 121.1949 | 121.4016 | 121.3819 | -0.18246 | 0.037625 | 0.13615 | 0.12463 | 0.023612 | -0.014013 | -0.10743 | -0.20786 | 0.009797 | -0.20864 | 0.18415 | 0.053493 | 0.043696 | -0.001887 | -0.021578 | 121.7319 | 121.4883 | 121.3879 | 3.3621 | -121.5581 | 121.3871 | 121.5939 | 121.5742 | 10.8656 | -121.586
1535.25 | 121.7056 | -0.19684 | 121.4447 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.06353 | -0.0047732 | 0.056683 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059282 | -0.076785 | 3.1835 | -0.16407 | 121.5442 | 121.3098 | 121.2048 | -0.15006 | -0.003531 | 10.7008 | -0.14335 | 121.204 | 121.4062 | 121.3865 | -0.17788 | 0.046781 | 0.099526 | 0.12005 | 0.032767 | -0.014014 | -0.1349 | -0.23991 | 0.018953 | -0.24068 | 0.19331 | 0.053491 | 0.034538 | -0.038507 | -0.058199 | 121.7411 | 121.5066 | 121.4016 | 3.3804 | -121.5948 | 121.4009 | 121.603 | 121.5833 | 10.8976 | -121.6226
1536.9375 | 121.6324 | -0.25177 | 121.4539 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063103 | -0.0045596 | 0.056683 | -0.0022889 | 0.00034614 | 0.00037167 | 0.063417 | 0.013942 | 0.059496 | -0.067628 | 3.1881 | -0.16407 | 121.5351 | 121.3052 | 121.2048 | -0.15006 | 0.005626 | 10.7237 | -0.14793 | 121.1994 | 121.4062 | 121.3957 | -0.18246 | 0.10171 | 0.081214 | 0.18414 | 0.087699 | -0.014014 | -0.14863 | -0.24906 | 0.069306 | -0.25442 | 0.2574 | 0.10384 | 0.034539 | -0.047662 | -0.058196 | 121.7868 | 121.557 | 121.4566 | 3.4399 | -121.6039 | 121.4512 | 121.658 | 121.6474 | 10.9755 | -121.6363
1538.7031 | 121.7789 | -0.19226 | 121.4172 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063316 | -0.0047732 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.013515 | 0.05971 | -0.072207 | 3.179 | -0.17323 | 121.5442 | 121.3052 | 121.2048 | -0.15464 | -0.00811 | 10.7283 | -0.14335 | 121.204 | 121.4062 | 121.3911 | -0.17788 | 0.037625 | 0.12699 | 0.12005 | 0.019034 | -0.018591 | -0.11201 | -0.21244 | 0.014376 | -0.21322 | 0.18415 | 0.048914 | 0.034538 | -0.011041 | -0.026154 | 121.7365 | 121.4975 | 121.3971 | 3.3712 | -121.5719 | 121.3963 | 121.5985 | 121.5833 | 10.9205 | -121.5951
1540.4688 | 121.6324 | -0.25635 | 121.4584 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063103 | -0.0047732 | 0.056683 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063417 | 0.013515 | 0.05971 | -0.067628 | 3.179 | -0.16407 | 121.5442 | 121.3052 | 121.214 | -0.13632 | -0.003531 | 10.742 | -0.1525 | 121.1994 | 121.4062 | 121.3865 | -0.18704 | 0.12003 | 0.085793 | 0.18872 | 0.092277 | -0.027751 | -0.15321 | -0.24448 | 0.069305 | -0.25899 | 0.25282 | 0.10384 | 0.034539 | -0.05224 | -0.071932 | 121.8006 | 121.5616 | 121.4703 | 3.4353 | -121.5948 | 121.4558 | 121.6625 | 121.6429 | 10.9984 | -121.6455
1542.1875 | 121.756 | -0.17853 | 121.431 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.062889 | -0.004987 | 0.056683 | -0.01755 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.013728 | 0.05971 | -0.067628 | 3.2064 | -0.15949 | 121.5396 | 121.2961 | 121.2094 | -0.14548 | -0.003531 | 10.7374 | -0.14793 | 121.2086 | 121.4062 | 121.3865 | -0.18704 | 0.03305 | 0.10868 | 0.1109 | 0.019035 | -0.014015 | -0.1349 | -0.2216 | -0.008515 | -0.22237 | 0.175 | 0.030603 | 0.039118 | -0.024774 | -0.044466 | 121.7182 | 121.4746 | 121.3879 | 3.385 | -121.5764 | 121.3871 | 121.5847 | 121.565 | 10.916 | -121.618
1543.9375 | 121.6415 | -0.22888 | 121.4401 | 1.4211e-13 | -0.02679 | -0.0018055 | 0.063103 | -0.0047732 | 0.056896 | -0.0099194 | 0.00077334 | -5.5534e-05 | 0.063203 | 0.013728 | 0.05971 | -0.06305 | 3.2018 | -0.15949 | 121.5396 | 121.3052 | 121.2048 | -0.14548 | -0.00811 | 10.7008 | -0.14793 | 121.1949 | 121.4062 | 121.3773 | -0.18246 | 0.083404 | 0.099525 | 0.16583 | 0.069389 | -0.014015 | -0.1349 | -0.23533 | 0.046418 | -0.24526 | 0.22077 | 0.080957 | 0.034539 | -0.03393 | -0.062779 | 121.7685 | 121.5341 | 121.4337 | 3.4307 | -121.5856 | 121.4237 | 121.6351 | 121.6062 | 10.9297 | -121.6226
1545.6562 | 121.7148 | -0.21973 | 121.4218 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.063103 | -0.0052006 | 0.056896 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063203 | 0.013942 | 0.05971 | -0.072207 | 3.1927 | -0.16865 | 121.5396 | 121.3052 | 121.2048 | -0.15006 | -0.003531 | 10.7329 | -0.14335 | 121.2086 | 121.4062 | 121.3865 | -0.17788 | 0.06967 | 0.11784 | 0.14752 | 0.051078 | -0.018592 | -0.11659 | -0.21702 | 0.041842 | -0.21322 | 0.2162 | 0.07638 | 0.034538 | -0.015619 | -0.035311 | 121.7594 | 121.525 | 121.4245 | 3.4124 | -121.5719 | 121.4283 | 121.6259 | 121.6062 | 10.9526 | -121.5997
1547.4219 | 121.7468 | -0.17853 | 121.431 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063316 | -0.0047732 | 0.056683 | -0.0022889 | 0.00013254 | 0.00037167 | 0.06299 | 0.013301 | 0.059496 | -0.067628 | 3.2018 | -0.15949 | 121.5442 | 121.3098 | 121.2048 | -0.13632 | -0.012689 | 10.7191 | -0.1525 | 121.1994 | 121.4108 | 121.3865 | -0.17331 | 0.042208 | 0.11326 | 0.1109 | 0.019035 | -0.023173 | -0.12116 | -0.22617 | 0.005222 | -0.23153 | 0.16584 | 0.026024 | 0.020802 | -0.020195 | -0.044466 | 121.7228 | 121.4883 | 121.3833 | 3.3804 | -121.5673 | 121.378 | 121.5893 | 121.565 | 10.8976 | -121.6043
1549.125 | 121.7834 | -0.19226 | 121.4264 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.062889 | -0.0047732 | 0.056683 | 0.0053411 | -0.00029486 | 0.00015807 | 0.06299 | 0.013515 | 0.05971 | -0.067628 | 3.1973 | -0.16407 | 121.5488 | 121.3052 | 121.2048 | -0.14548 | -0.012689 | 10.71 | -0.14335 | 121.204 | 121.4016 | 121.3865 | -0.18246 | 0.046783 | 0.12241 | 0.12463 | 0.02819 | -0.018593 | -0.12116 | -0.2216 | 0.009797 | -0.22237 | 0.17957 | 0.048914 | 0.039117 | -0.024776 | -0.039889 | 121.7411 | 121.4975 | 121.3971 | 3.3895 | -121.5719 | 121.3963 | 121.5939 | 121.5788 | 10.9022 | -121.6089
1550.8906 | 121.6873 | -0.20599 | 121.4676 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.063103 | -0.004987 | 0.05711 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.013942 | 0.059496 | -0.067628 | 3.2064 | -0.16865 | 121.5488 | 121.3144 | 121.2094 | -0.1409 | -0.003531 | 10.7145 | -0.14335 | 121.2086 | 121.4154 | 121.3911 | -0.17788 | 0.065095 | 0.081216 | 0.13837 | 0.037345 | -0.02775 | -0.1532 | -0.25822 | 0.028109 | -0.25899 | 0.20246 | 0.062647 | 0.034538 | -0.052238 | -0.076508 | 121.7548 | 121.5204 | 121.4154 | 3.4124 | -121.6085 | 121.4146 | 121.6213 | 121.5971 | 10.9205 | -121.6455
1552.5938 | 121.7834 | -0.19226 | 121.4447 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.062889 | -0.0047732 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059496 | -0.067628 | 3.2018 | -0.16407 | 121.5396 | 121.3052 | 121.2094 | -0.13632 | -0.003531 | 10.7649 | -0.14793 | 121.2132 | 121.4062 | 121.3865 | -0.18246 | 0.055941 | 0.094948 | 0.12463 | 0.02819 | -0.027751 | -0.13947 | -0.23533 | 0.009797 | -0.23153 | 0.18873 | 0.044336 | 0.034539 | -0.038507 | -0.058199 | 121.7319 | 121.4975 | 121.4016 | 3.3941 | -121.581 | 121.4054 | 121.5985 | 121.5788 | 10.9572 | -121.6272
1554.3594 | 121.7697 | -0.1831 | 121.431 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.062889 | -0.0045596 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.013942 | 0.059496 | -0.067628 | 3.2293 | -0.16865 | 121.5442 | 121.3098 | 121.2094 | -0.14548 | -0.00811 | 10.7832 | -0.1525 | 121.2086 | 121.4108 | 121.3865 | -0.18246 | 0.037627 | 0.11326 | 0.11548 | 0.014456 | -0.023171 | -0.12116 | -0.2216 | 0.000641 | -0.22237 | 0.17499 | 0.030601 | 0.02996 | -0.020195 | -0.044466 | 121.7273 | 121.4929 | 121.3925 | 3.4124 | -121.5764 | 121.3917 | 121.5939 | 121.5696 | 10.9663 | -121.6134
1556.125 | 121.6507 | -0.24719 | 121.4676 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.063103 | -0.004987 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.013515 | 0.059496 | -0.072207 | 3.2202 | -0.15949 | 121.5534 | 121.3098 | 121.2048 | -0.14548 | -0.003531 | 10.7695 | -0.14793 | 121.1994 | 121.4108 | 121.3957 | -0.18704 | 0.10171 | 0.085795 | 0.17499 | 0.087699 | -0.014015 | -0.15778 | -0.26279 | 0.060149 | -0.26815 | 0.24366 | 0.099267 | 0.039118 | -0.056816 | -0.071929 | 121.8006 | 121.557 | 121.452 | 3.4674 | -121.6131 | 121.4466 | 121.658 | 121.6429 | 11.0167 | -121.6546
1557.875 | 121.6507 | -0.24261 | 121.463 | 1.4211e-13 | -0.02679 | -0.0011645 | 0.062889 | -0.004987 | 0.056683 | -0.0099194 | 0.00034614 | 0.00058547 | 0.063417 | 0.013942 | 0.05971 | -0.072207 | 3.2339 | -0.15949 | 121.5488 | 121.3144 | 121.214 | -0.15006 | -0.003531 | 10.797 | -0.14793 | 121.2086 | 121.4108 | 121.3865 | -0.18246 | 0.092558 | 0.085793 | 0.17041 | 0.083122 | -0.009436 | -0.14863 | -0.24906 | 0.060151 | -0.25442 | 0.23908 | 0.09469 | 0.034539 | -0.052239 | -0.07651 | 121.7914 | 121.557 | 121.4566 | 3.4765 | -121.6131 | 121.4512 | 121.6534 | 121.6291 | 11.0396 | -121.6455
1559.5781 | 121.7606 | -0.17395 | 121.4264 | 1.4211e-13 | -0.02679 | -0.0018055 | 0.063103 | -0.0052006 | 0.056469 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014156 | 0.059496 | -0.067628 | 3.2202 | -0.16407 | 121.5442 | 121.3052 | 121.214 | -0.15464 | -0.00811 | 10.7191 | -0.1525 | 121.204 | 121.4062 | 121.3911 | -0.18246 | 0.019314 | 0.11784 | 0.10632 | 0.009879 | -0.009435 | -0.12116 | -0.21244 | -0.008514 | -0.22237 | 0.16584 | 0.021446 | 0.02996 | -0.020197 | -0.03531 | 121.7182 | 121.4792 | 121.3879 | 3.3941 | -121.581 | 121.378 | 121.5801 | 121.565 | 10.8931 | -121.6089
1561.3438 | 121.7056 | -0.21515 | 121.4493 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063103 | -0.0052006 | 0.056896 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063203 | 0.013728 | 0.05971 | -0.06305 | 3.2202 | -0.16865 | 121.5442 | 121.3144 | 121.2002 | -0.1409 | -0.003531 | 10.7054 | -0.13419 | 121.2086 | 121.4108 | 121.3957 | -0.18246 | 0.07425 | 0.094948 | 0.1521 | 0.0465 | -0.02775 | -0.13489 | -0.24906 | 0.032685 | -0.24068 | 0.21162 | 0.08096 | 0.048275 | -0.038506 | -0.053619 | 121.7594 | 121.5295 | 121.4154 | 3.4353 | -121.5902 | 121.4237 | 121.6259 | 121.6108 | 10.9205 | -121.6317
1563.1094 | 121.7285 | -0.21057 | 121.4172 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.062889 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063417 | 0.013728 | 0.059496 | -0.06305 | 3.2156 | -0.15949 | 121.5442 | 121.3144 | 121.2048 | -0.14548 | -0.00811 | 10.6962 | -0.14793 | 121.2086 | 121.4108 | 121.3865 | -0.18704 | 0.065093 | 0.12699 | 0.14752 | 0.051078 | -0.014015 | -0.10285 | -0.21244 | 0.023528 | -0.20864 | 0.20246 | 0.062646 | 0.039118 | -0.006462 | -0.030733 | 121.7548 | 121.525 | 121.4154 | 3.4262 | -121.5627 | 121.4192 | 121.6213 | 121.5971 | 10.9068 | -121.6043
1564.8906 | 121.6827 | -0.2243 | 121.4584 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.063103 | -0.0052006 | 0.056896 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059069 | -0.06305 | 3.2247 | -0.16407 | 121.5442 | 121.3052 | 121.214 | -0.14548 | 0.001048 | 10.7329 | -0.14793 | 121.204 | 121.4062 | 121.3911 | -0.17788 | 0.078826 | 0.085793 | 0.16125 | 0.060233 | -0.018593 | -0.15321 | -0.24448 | 0.046419 | -0.25441 | 0.22535 | 0.076379 | 0.02996 | -0.05224 | -0.067353 | 121.7685 | 121.5295 | 121.4383 | 3.449 | -121.6039 | 121.4283 | 121.6305 | 121.6154 | 10.9572 | -121.6363
1566.6562 | 121.6553 | -0.24719 | 121.463 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.063103 | -0.004987 | 0.05711 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.013728 | 0.05971 | -0.06305 | 3.2156 | -0.16407 | 121.5488 | 121.3144 | 121.2231 | -0.14548 | -0.00811 | 10.7695 | -0.13877 | 121.204 | 121.4154 | 121.3957 | -0.17788 | 0.10171 | 0.085793 | 0.18414 | 0.083121 | -0.018593 | -0.14863 | -0.2399 | 0.069307 | -0.25899 | 0.23908 | 0.10842 | 0.039117 | -0.047661 | -0.067352 | 121.796 | 121.5616 | 121.4703 | 3.4628 | -121.6085 | 121.4512 | 121.6625 | 121.6429 | 11.0167 | -121.6409
1568.3594 | 121.7743 | -0.1831 | 121.3989 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | 0.0053411 | -0.00029486 | 0.00015807 | 0.063631 | 0.013728 | 0.05971 | -0.06305 | 3.2202 | -0.16407 | 121.5488 | 121.3098 | 121.214 | -0.15006 | -0.003531 | 10.7145 | -0.14335 | 121.2086 | 121.4154 | 121.3865 | -0.18246 | 0.033048 | 0.14988 | 0.12005 | 0.019034 | -0.014014 | -0.089119 | -0.18497 | 0.000641 | -0.19033 | 0.17957 | 0.039758 | 0.039117 | 0.016426 | -0.012423 | 121.7319 | 121.4929 | 121.3971 | 3.4033 | -121.549 | 121.3917 | 121.5985 | 121.5696 | 10.8976 | -121.5814
1570.1406 | 121.6782 | -0.23804 | 121.4401 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.062889 | -0.0047732 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.013728 | 0.059496 | -0.067628 | 3.2385 | -0.16865 | 121.5534 | 121.3052 | 121.2231 | -0.14548 | 0.001048 | 10.6779 | -0.13877 | 121.204 | 121.4154 | 121.3865 | -0.17788 | 0.092559 | 0.11326 | 0.17041 | 0.069388 | -0.023171 | -0.1349 | -0.21701 | 0.060152 | -0.2361 | 0.23908 | 0.099269 | 0.039117 | -0.024773 | -0.053622 | 121.7914 | 121.5433 | 121.4611 | 3.4765 | -121.5856 | 121.4421 | 121.6534 | 121.6245 | 10.9159 | -121.618
1571.9062 | 121.7789 | -0.19684 | 121.4355 | 1.4211e-13 | -0.027004 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013728 | 0.060137 | -0.072207 | 3.2385 | -0.16407 | 121.5534 | 121.3144 | 121.214 | -0.14548 | -0.00811 | 10.6962 | -0.14793 | 121.2132 | 121.4245 | 121.3865 | -0.17788 | 0.05136 | 0.11784 | 0.12463 | 0.032767 | -0.018593 | -0.12116 | -0.22159 | 0.018953 | -0.22237 | 0.18873 | 0.048913 | 0.02996 | -0.011038 | -0.049044 | 121.7502 | 121.5112 | 121.4108 | 3.4353 | -121.581 | 121.41 | 121.6213 | 121.5833 | 10.8931 | -121.6134
1573.6094 | 121.7194 | -0.21057 | 121.463 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.063316 | -0.0052006 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059282 | -0.072207 | 3.2293 | -0.16407 | 121.5396 | 121.319 | 121.214 | -0.1409 | -0.00811 | 10.6916 | -0.1525 | 121.204 | 121.4199 | 121.3911 | -0.18246 | 0.069672 | 0.076637 | 0.13836 | 0.0465 | -0.023172 | -0.14405 | -0.24906 | 0.028107 | -0.25899 | 0.20246 | 0.058067 | 0.02996 | -0.043082 | -0.071931 | 121.7502 | 121.5295 | 121.4245 | 3.4399 | -121.6039 | 121.4146 | 121.6305 | 121.6017 | 10.9022 | -121.6455
1575.3906 | 121.7468 | -0.17853 | 121.4447 | 1.4211e-13 | -0.02679 | -0.0013783 | 0.062675 | -0.004987 | 0.056683 | -0.01755 | 0.00013254 | 0.00015807 | 0.062776 | 0.014156 | 0.05971 | -0.067628 | 3.2202 | -0.15949 | 121.5442 | 121.3098 | 121.214 | -0.1409 | -0.00811 | 10.6642 | -0.1525 | 121.2086 | 121.4199 | 121.3865 | -0.17788 | 0.037629 | 0.099526 | 0.1109 | 0.019035 | -0.018594 | -0.1349 | -0.23075 | 0.000643 | -0.2361 | 0.17042 | 0.026024 | 0.025381 | -0.024771 | -0.058199 | 121.7228 | 121.4883 | 121.3925 | 3.3987 | -121.5856 | 121.3871 | 121.5985 | 121.565 | 10.8427 | -121.6226
1577.0938 | 121.7239 | -0.20142 | 121.4722 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.063103 | -0.004987 | 0.056896 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059496 | -0.06305 | 3.2156 | -0.15491 | 121.5488 | 121.3144 | 121.2185 | -0.14548 | -0.00811 | 10.71 | -0.14793 | 121.2132 | 121.4245 | 121.3911 | -0.17331 | 0.055938 | 0.076638 | 0.13837 | 0.046502 | -0.009436 | -0.15778 | -0.25364 | 0.02811 | -0.25899 | 0.19331 | 0.053491 | 0.025381 | -0.047659 | -0.081086 | 121.7502 | 121.5158 | 121.4199 | 3.417 | -121.6176 | 121.4146 | 121.6259 | 121.5925 | 10.9114 | -121.6455
1578.8594 | 121.7239 | -0.21973 | 121.4722 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.063103 | -0.0045596 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.013942 | 0.05971 | -0.067628 | 3.2247 | -0.15491 | 121.558 | 121.3144 | 121.2185 | -0.1409 | -0.00811 | 10.6688 | -0.14793 | 121.2132 | 121.4154 | 121.3957 | -0.17331 | 0.078828 | 0.085795 | 0.1521 | 0.064813 | -0.014015 | -0.15778 | -0.25364 | 0.046421 | -0.25899 | 0.21162 | 0.071802 | 0.025381 | -0.056816 | -0.076507 | 121.7777 | 121.5341 | 121.4383 | 3.4445 | -121.6131 | 121.4329 | 121.6351 | 121.6154 | 10.8885 | -121.6455
1580.5781 | 121.7834 | -0.1831 | 121.4355 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.062889 | -0.0045596 | 0.056896 | -0.0022889 | 0.00034614 | -0.00026913 | 0.063417 | 0.013942 | 0.059496 | -0.06305 | 3.2156 | -0.16407 | 121.5488 | 121.3144 | 121.2185 | -0.15006 | -0.00811 | 10.655 | -0.13419 | 121.2132 | 121.4199 | 121.3911 | -0.18246 | 0.033048 | 0.11326 | 0.12005 | 0.019034 | -0.014014 | -0.12116 | -0.21702 | 0.000641 | -0.22237 | 0.17499 | 0.048916 | 0.048275 | -0.015616 | -0.044465 | 121.7319 | 121.4975 | 121.4016 | 3.3987 | -121.5856 | 121.3963 | 121.603 | 121.5742 | 10.8381 | -121.618
1582.3438 | 121.7514 | -0.19226 | 121.4447 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.063103 | -0.004987 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063417 | 0.013942 | 0.05971 | -0.058472 | 3.2476 | -0.15949 | 121.558 | 121.3144 | 121.2185 | -0.14548 | -0.00811 | 10.6367 | -0.14793 | 121.2223 | 121.4154 | 121.3957 | -0.17788 | 0.046783 | 0.11326 | 0.13379 | 0.032768 | -0.014015 | -0.13032 | -0.22617 | 0.014376 | -0.22237 | 0.18415 | 0.044336 | 0.02996 | -0.02935 | -0.049041 | 121.7502 | 121.5066 | 121.4108 | 3.4399 | -121.5902 | 121.4146 | 121.6076 | 121.5879 | 10.829 | -121.6226
1584.0938 | 121.7926 | -0.20142 | 121.4401 | 1.4211e-13 | -0.02679 | -0.0015919 | 0.062675 | -0.0047732 | 0.056683 | -0.0099194 | -0.00029486 | -0.00026913 | 0.06299 | 0.013942 | 0.059496 | -0.058472 | 3.2431 | -0.15949 | 121.5534 | 121.3144 | 121.2185 | -0.13632 | -0.012689 | 10.623 | -0.14335 | 121.2132 | 121.4154 | 121.3911 | -0.17788 | 0.065096 | 0.11326 | 0.14294 | 0.041923 | -0.023173 | -0.12574 | -0.22159 | 0.023531 | -0.22695 | 0.18873 | 0.058069 | 0.034538 | -0.024773 | -0.049043 | 121.7548 | 121.5158 | 121.4199 | 3.4445 | -121.5764 | 121.4146 | 121.6168 | 121.5925 | 10.8244 | -121.618
1585.875 | 121.7194 | -0.20599 | 121.4264 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.062889 | -0.004987 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059496 | -0.06305 | 3.2293 | -0.16407 | 121.558 | 121.3098 | 121.214 | -0.1409 | 0.001048 | 10.5818 | -0.14335 | 121.2132 | 121.4154 | 121.3957 | -0.17788 | 0.065095 | 0.13157 | 0.14294 | 0.041923 | -0.023172 | -0.11659 | -0.21244 | 0.028109 | -0.21322 | 0.20704 | 0.062647 | 0.034538 | -0.01104 | -0.030731 | 121.764 | 121.5158 | 121.4199 | 3.4353 | -121.5673 | 121.4192 | 121.6213 | 121.6017 | 10.7878 | -121.6043
1587.5781 | 121.6507 | -0.24719 | 121.4905 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.063316 | -0.004987 | 0.056896 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.063631 | 0.013728 | 0.059282 | -0.067628 | 3.2385 | -0.15491 | 121.5534 | 121.3235 | 121.2323 | -0.15006 | -0.003531 | 10.5909 | -0.14335 | 121.2132 | 121.4199 | 121.4002 | -0.17331 | 0.097135 | 0.062906 | 0.17956 | 0.092278 | -0.004857 | -0.16693 | -0.25821 | 0.073886 | -0.2773 | 0.24366 | 0.10384 | 0.029959 | -0.070548 | -0.09024 | 121.8006 | 121.5707 | 121.4795 | 3.4857 | -121.6405 | 121.4604 | 121.6671 | 121.6474 | 10.8381 | -121.6638
1589.3438 | 121.6644 | -0.23804 | 121.4813 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.063316 | -0.0047732 | 0.056469 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.014369 | 0.059923 | -0.06305 | 3.2247 | -0.15949 | 121.5534 | 121.319 | 121.2277 | -0.14548 | -0.003531 | 10.6413 | -0.14793 | 121.2178 | 121.4245 | 121.4002 | -0.18246 | 0.092559 | 0.072062 | 0.17499 | 0.078544 | -0.014015 | -0.16236 | -0.25364 | 0.055573 | -0.26357 | 0.23451 | 0.090112 | 0.034539 | -0.056814 | -0.081084 | 121.7914 | 121.557 | 121.4657 | 3.4628 | -121.6268 | 121.4558 | 121.6625 | 121.6383 | 10.8793 | -121.6638
1591.1094 | 121.637 | -0.22888 | 121.463 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059496 | -0.053893 | 3.2202 | -0.16407 | 121.558 | 121.319 | 121.2231 | -0.14548 | -0.00811 | 10.6596 | -0.14335 | 121.2223 | 121.4245 | 121.4002 | -0.17788 | 0.083404 | 0.09495 | 0.17499 | 0.064811 | -0.018593 | -0.14405 | -0.2399 | 0.050997 | -0.24068 | 0.22077 | 0.085535 | 0.034538 | -0.038504 | -0.062774 | 121.7868 | 121.5478 | 121.452 | 3.449 | -121.6085 | 121.4512 | 121.6534 | 121.6291 | 10.8885 | -121.6409
1592.875 | 121.6507 | -0.23804 | 121.4722 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.063316 | -0.004987 | 0.056683 | -0.0099194 | -8.1262e-05 | -0.00048293 | 0.063631 | 0.013942 | 0.059496 | -0.06305 | 3.2293 | -0.15949 | 121.5534 | 121.319 | 121.2185 | -0.14548 | -0.003531 | 10.6138 | -0.13877 | 121.2086 | 121.4199 | 121.4002 | -0.18246 | 0.092559 | 0.081217 | 0.17499 | 0.078544 | -0.014015 | -0.1532 | -0.25364 | 0.055573 | -0.26357 | 0.23451 | 0.099269 | 0.043696 | -0.052237 | -0.071929 | 121.7914 | 121.557 | 121.4566 | 3.4674 | -121.6176 | 121.4466 | 121.658 | 121.6383 | 10.8518 | -121.6546
1594.6406 | 121.6507 | -0.24719 | 121.4767 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.063103 | -0.004987 | 0.056683 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059496 | -0.06305 | 3.2339 | -0.15491 | 121.5488 | 121.3235 | 121.2277 | -0.15464 | -0.003531 | 10.6688 | -0.14335 | 121.2132 | 121.4245 | 121.3957 | -0.17788 | 0.092556 | 0.07206 | 0.18414 | 0.092278 | -0.000278 | -0.1532 | -0.24906 | 0.069307 | -0.26357 | 0.24366 | 0.10384 | 0.034538 | -0.052237 | -0.081085 | 121.796 | 121.5707 | 121.4749 | 3.4811 | -121.6314 | 121.4604 | 121.6717 | 121.6429 | 10.9159 | -121.6546
1596.4062 | 121.637 | -0.23346 | 121.5134 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.063103 | -0.004987 | 0.056683 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013942 | 0.059282 | -0.067628 | 3.2522 | -0.16407 | 121.558 | 121.319 | 121.2277 | -0.14548 | -0.003531 | 10.6642 | -0.13877 | 121.2132 | 121.4382 | 121.4048 | -0.18246 | 0.087981 | 0.044596 | 0.16583 | 0.069388 | -0.018593 | -0.1944 | -0.28568 | 0.050995 | -0.30019 | 0.22993 | 0.094691 | 0.043696 | -0.075122 | -0.10855 | 121.7914 | 121.5524 | 121.4611 | 3.4857 | -121.6588 | 121.4466 | 121.6717 | 121.6383 | 10.8976 | -121.6958
1598.1094 | 121.669 | -0.23346 | 121.4905 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.063103 | -0.0052006 | 0.056896 | -0.0099194 | 0.00013254 | -0.00026913 | 0.063203 | 0.013728 | 0.059069 | -0.06305 | 3.2293 | -0.15949 | 121.5625 | 121.319 | 121.2277 | -0.1409 | 0.005626 | 10.6504 | -0.13877 | 121.2178 | 121.4291 | 121.4094 | -0.18246 | 0.09256 | 0.072063 | 0.17041 | 0.073966 | -0.018594 | -0.17151 | -0.26279 | 0.050995 | -0.27272 | 0.23908 | 0.094691 | 0.043696 | -0.061391 | -0.081083 | 121.796 | 121.5524 | 121.4611 | 3.4628 | -121.6314 | 121.4512 | 121.6625 | 121.6429 | 10.8839 | -121.6729
1599.875 | 121.669 | -0.24719 | 121.4767 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.063103 | -0.0052006 | 0.056683 | -0.0099194 | 0.00013254 | 0.00015807 | 0.063631 | 0.014369 | 0.059496 | -0.06305 | 3.2476 | -0.16407 | 121.558 | 121.3235 | 121.2231 | -0.14548 | 0.001048 | 10.6413 | -0.14335 | 121.2086 | 121.4245 | 121.4048 | -0.18246 | 0.10171 | 0.081217 | 0.18414 | 0.083121 | -0.018593 | -0.1532 | -0.25364 | 0.064728 | -0.26815 | 0.24824 | 0.10384 | 0.039117 | -0.052237 | -0.071928 | 121.8052 | 121.5707 | 121.4703 | 3.4948 | -121.6222 | 121.4558 | 121.6717 | 121.652 | 10.8885 | -121.6592
1601.6406 | 121.7285 | -0.21057 | 121.431 | 1.4211e-13 | -0.027218 | -0.0020193 | 0.062889 | -0.0045596 | 0.056469 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.013728 | 0.05971 | -0.072207 | 3.2568 | -0.15949 | 121.5625 | 121.3235 | 121.2231 | -0.14548 | 0.001048 | 10.6504 | -0.14335 | 121.2178 | 121.4199 | 121.4048 | -0.17331 | 0.065093 | 0.13157 | 0.13836 | 0.051078 | -0.014015 | -0.10743 | -0.20786 | 0.037265 | -0.21321 | 0.21162 | 0.067224 | 0.029959 | -0.011038 | -0.026151 | 121.7731 | 121.5341 | 121.4337 | 3.4674 | -121.5764 | 121.4283 | 121.6305 | 121.6154 | 10.861 | -121.6043
1603.3594 | 121.669 | -0.23346 | 121.4584 | 1.4211e-13 | -0.027431 | -0.0011645 | 0.063103 | -0.0047732 | 0.056683 | -0.0099194 | 0.00034614 | 0.00015807 | 0.063417 | 0.013728 | 0.059282 | -0.06305 | 3.2568 | -0.15949 | 121.5671 | 121.3235 | 121.2277 | -0.1409 | 0.001048 | 10.6275 | -0.13877 | 121.2132 | 121.4245 | 121.4094 | -0.17331 | 0.09256 | 0.10869 | 0.17041 | 0.073966 | -0.018594 | -0.13489 | -0.23075 | 0.060153 | -0.24526 | 0.23451 | 0.094691 | 0.034538 | -0.033926 | -0.049039 | 121.8006 | 121.557 | 121.4611 | 3.4903 | -121.5993 | 121.4466 | 121.658 | 121.6429 | 10.861 | -121.6317
1605.125 | 121.7285 | -0.21057 | 121.4447 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.062889 | -0.0052006 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013728 | 0.059282 | -0.058472 | 3.2431 | -0.15949 | 121.558 | 121.3281 | 121.2231 | -0.1409 | -0.00811 | 10.623 | -0.14335 | 121.2223 | 121.4199 | 121.4048 | -0.18246 | 0.069672 | 0.11326 | 0.1521 | 0.051078 | -0.018594 | -0.11658 | -0.22159 | 0.028107 | -0.22237 | 0.20246 | 0.067224 | 0.039117 | -0.024771 | -0.039884 | 121.7685 | 121.5387 | 121.4337 | 3.4536 | -121.5856 | 121.4329 | 121.6305 | 121.6154 | 10.8335 | -121.6272
1606.9062 | 121.7651 | -0.18768 | 121.4264 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.062889 | -0.0045596 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.014156 | 0.059282 | -0.058472 | 3.2522 | -0.15949 | 121.5534 | 121.3235 | 121.2231 | -0.13632 | -0.003531 | 10.6596 | -0.13877 | 121.2223 | 121.4199 | 121.4048 | -0.16873 | 0.051363 | 0.12699 | 0.12921 | 0.02819 | -0.023173 | -0.10285 | -0.20328 | 0.018955 | -0.20406 | 0.18415 | 0.048915 | 0.02996 | -0.006461 | -0.021574 | 121.7411 | 121.5112 | 121.4108 | 3.4399 | -121.5627 | 121.41 | 121.6076 | 121.5925 | 10.8473 | -121.5951
1608.6719 | 121.6965 | -0.2243 | 121.4813 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062889 | -0.004987 | 0.056469 | 0.012972 | 0.00034614 | 0.00015807 | 0.063417 | 0.013942 | 0.059496 | -0.058472 | 3.2385 | -0.15491 | 121.5534 | 121.3235 | 121.2277 | -0.1409 | 0.005626 | 10.6504 | -0.13419 | 121.2086 | 121.4245 | 121.4048 | -0.17788 | 0.083405 | 0.072062 | 0.16583 | 0.06939 | -0.014015 | -0.15778 | -0.25364 | 0.046419 | -0.27273 | 0.22993 | 0.090115 | 0.043696 | -0.056814 | -0.076505 | 121.7777 | 121.5478 | 121.452 | 3.4628 | -121.6222 | 121.4329 | 121.6488 | 121.6291 | 10.8747 | -121.6592
1610.4375 | 121.6873 | -0.21057 | 121.4676 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.062889 | -0.004987 | 0.056896 | -0.0022889 | 0.00034614 | -0.00026913 | 0.06299 | 0.013728 | 0.059496 | -0.06305 | 3.266 | -0.16407 | 121.5534 | 121.3281 | 121.2323 | -0.13632 | -0.003531 | 10.6459 | -0.13877 | 121.2223 | 121.4199 | 121.4048 | -0.17788 | 0.074251 | 0.085795 | 0.14752 | 0.0465 | -0.027751 | -0.13947 | -0.23532 | 0.032686 | -0.24526 | 0.20704 | 0.071803 | 0.039117 | -0.047659 | -0.062772 | 121.764 | 121.5387 | 121.4428 | 3.4765 | -121.6039 | 121.4329 | 121.6305 | 121.6154 | 10.8564 | -121.6455
1612.2188 | 121.7422 | -0.21973 | 121.4539 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.062889 | -0.0047732 | 0.056683 | -0.0099194 | 0.00013254 | 0.00015807 | 0.06299 | 0.013728 | 0.059496 | -0.06305 | 3.2614 | -0.15034 | 121.5534 | 121.3235 | 121.2323 | -0.14548 | -0.00811 | 10.6504 | -0.13419 | 121.2223 | 121.4245 | 121.4048 | -0.17788 | 0.074249 | 0.099528 | 0.15668 | 0.069391 | -0.004858 | -0.13031 | -0.22159 | 0.041842 | -0.23152 | 0.21162 | 0.085538 | 0.043696 | -0.029348 | -0.049039 | 121.7731 | 121.5433 | 121.452 | 3.4811 | -121.5993 | 121.4421 | 121.6442 | 121.6245 | 10.8702 | -121.6317
1613.9844 | 121.6919 | -0.21057 | 121.4722 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.062889 | -0.0045596 | 0.056896 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.013728 | 0.059496 | -0.058472 | 3.2797 | -0.16407 | 121.5671 | 121.3281 | 121.2368 | -0.14548 | -0.003531 | 10.6733 | -0.14335 | 121.2178 | 121.4245 | 121.3911 | -0.17788 | 0.065093 | 0.094952 | 0.1521 | 0.0465 | -0.018593 | -0.14404 | -0.23532 | 0.032686 | -0.25441 | 0.20704 | 0.067224 | 0.034538 | -0.047659 | -0.081086 | 121.7777 | 121.5387 | 121.4474 | 3.4903 | -121.6176 | 121.4283 | 121.6351 | 121.6017 | 10.8839 | -121.6501
1615.7031 | 121.6507 | -0.23346 | 121.4676 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.063103 | -0.004987 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.013942 | 0.059282 | -0.06305 | 3.2888 | -0.15949 | 121.5534 | 121.3235 | 121.2368 | -0.15006 | 0.005626 | 10.6688 | -0.12961 | 121.2178 | 121.4245 | 121.4048 | -0.17331 | 0.083402 | 0.085795 | 0.17041 | 0.073966 | -0.009436 | -0.14405 | -0.23074 | 0.060153 | -0.24984 | 0.23908 | 0.10385 | 0.043696 | -0.043081 | -0.062772 | 121.7868 | 121.557 | 121.4703 | 3.5223 | -121.6176 | 121.4512 | 121.658 | 121.6383 | 10.9022 | -121.6409
1617.4688 | 121.7377 | -0.1831 | 121.4493 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.062889 | -0.004987 | 0.056683 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059282 | -0.06305 | 3.2888 | -0.15949 | 121.558 | 121.319 | 121.2414 | -0.13632 | -0.003531 | 10.623 | -0.13419 | 121.2315 | 121.4337 | 121.4094 | -0.16873 | 0.046785 | 0.10868 | 0.12005 | 0.023612 | -0.023173 | -0.13031 | -0.20786 | 0.014377 | -0.21779 | 0.17957 | 0.048916 | 0.034539 | -0.015613 | -0.039884 | 121.7411 | 121.5021 | 121.4245 | 3.4719 | -121.5856 | 121.4146 | 121.6168 | 121.5925 | 10.8061 | -121.618
1619.1719 | 121.7834 | -0.17853 | 121.4447 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062889 | -0.004987 | 0.056896 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014369 | 0.059496 | -0.067628 | 3.2797 | -0.15949 | 121.5625 | 121.3281 | 121.2323 | -0.14548 | 0.001048 | 10.6642 | -0.13419 | 121.2223 | 121.4245 | 121.4002 | -0.17331 | 0.03305 | 0.11784 | 0.1109 | 0.019035 | -0.014015 | -0.11658 | -0.21244 | 0.005222 | -0.22237 | 0.17958 | 0.044339 | 0.039117 | -0.020193 | -0.044463 | 121.7411 | 121.5067 | 121.4108 | 3.4582 | -121.5902 | 121.4009 | 121.603 | 121.5788 | 10.8427 | -121.618
1620.9375 | 121.7697 | -0.17395 | 121.4584 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.063103 | -0.0047732 | 0.056896 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.013942 | 0.059282 | -0.058472 | 3.2843 | -0.16407 | 121.5671 | 121.3235 | 121.2368 | -0.1409 | 0.001048 | 10.6184 | -0.13877 | 121.2223 | 121.4245 | 121.4002 | -0.17788 | 0.033051 | 0.10869 | 0.11548 | 0.009879 | -0.023172 | -0.13489 | -0.22159 | -0.003935 | -0.2361 | 0.175 | 0.035182 | 0.039117 | -0.033926 | -0.058196 | 121.7411 | 121.4975 | 121.4108 | 3.4582 | -121.5993 | 121.3963 | 121.5985 | 121.5742 | 10.7923 | -121.6363
1622.7031 | 121.7148 | -0.20599 | 121.4447 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.062889 | -0.0045596 | 0.056896 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014369 | 0.059282 | -0.058472 | 3.2751 | -0.15949 | 121.5625 | 121.3281 | 121.2277 | -0.13632 | -0.00811 | 10.6688 | -0.13419 | 121.2223 | 121.4291 | 121.4094 | -0.18246 | 0.069674 | 0.11784 | 0.14752 | 0.046501 | -0.023173 | -0.11658 | -0.21701 | 0.02353 | -0.22237 | 0.19788 | 0.071805 | 0.048275 | -0.015614 | -0.035306 | 121.7685 | 121.5341 | 121.4337 | 3.4811 | -121.581 | 121.4283 | 121.6351 | 121.6154 | 10.8747 | -121.6272
1624.4844 | 121.6919 | -0.21973 | 121.4584 | 1.4211e-13 | -0.027218 | -0.0018055 | 0.062889 | -0.004987 | 0.056469 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.013942 | 0.059496 | -0.072207 | 3.2843 | -0.15491 | 121.5717 | 121.3327 | 121.2368 | -0.15006 | 0.001048 | 10.6596 | -0.13877 | 121.2315 | 121.4291 | 121.4094 | -0.17788 | 0.06967 | 0.11326 | 0.14752 | 0.064813 | -0.004857 | -0.12573 | -0.22159 | 0.041842 | -0.22694 | 0.22077 | 0.080959 | 0.039117 | -0.029347 | -0.049039 | 121.7914 | 121.5524 | 121.4566 | 3.504 | -121.6085 | 121.4512 | 121.6488 | 121.6291 | 10.8793 | -121.6363
1626.2656 | 121.7331 | -0.18768 | 121.463 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.062889 | -0.0052006 | 0.056469 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.014156 | 0.059069 | -0.06305 | 3.2797 | -0.15949 | 121.558 | 121.3327 | 121.2368 | -0.1409 | 0.001048 | 10.6825 | -0.13419 | 121.2269 | 121.4291 | 121.4094 | -0.17788 | 0.046784 | 0.09495 | 0.12463 | 0.02819 | -0.018594 | -0.13031 | -0.22617 | 0.009798 | -0.2361 | 0.18873 | 0.053494 | 0.043696 | -0.033925 | -0.053617 | 121.7456 | 121.5204 | 121.4245 | 3.4674 | -121.6039 | 121.4146 | 121.6168 | 121.5971 | 10.8702 | -121.6409
1627.9531 | 121.7056 | -0.22888 | 121.4722 | 1.4211e-13 | -0.027431 | -0.0015919 | 0.063103 | -0.0052006 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059282 | -0.058472 | 3.298 | -0.15949 | 121.558 | 121.3373 | 121.2368 | -0.14548 | 0.001048 | 10.6138 | -0.13419 | 121.2269 | 121.4337 | 121.4048 | -0.17788 | 0.083404 | 0.085795 | 0.17041 | 0.069389 | -0.014015 | -0.13489 | -0.23532 | 0.050997 | -0.24526 | 0.22993 | 0.094693 | 0.043696 | -0.038501 | -0.06735 | 121.7868 | 121.5662 | 121.4657 | 3.5269 | -121.6176 | 121.4558 | 121.6625 | 121.6337 | 10.8427 | -121.6501
1629.7344 | 121.7834 | -0.18768 | 121.431 | 1.4211e-13 | -0.027431 | -0.0018055 | 0.063103 | -0.0047732 | 0.056469 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.014156 | 0.059282 | -0.053893 | 3.298 | -0.15034 | 121.5625 | 121.3327 | 121.2277 | -0.13632 | 0.010205 | 10.655 | -0.13419 | 121.2269 | 121.4291 | 121.4048 | -0.17331 | 0.051363 | 0.13157 | 0.13379 | 0.037347 | -0.014016 | -0.098268 | -0.20328 | 0.014377 | -0.20406 | 0.19789 | 0.053494 | 0.039117 | -0.001881 | -0.026151 | 121.7502 | 121.5204 | 121.4154 | 3.4857 | -121.5673 | 121.4146 | 121.6168 | 121.5925 | 10.8427 | -121.6043
1631.4375 | 121.7056 | -0.23346 | 121.4676 | 1.4211e-13 | -0.027645 | -0.0015919 | 0.063103 | -0.0047732 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.014156 | 0.05971 | -0.053893 | 3.3026 | -0.15949 | 121.558 | 121.3327 | 121.2323 | -0.14548 | -0.003531 | 10.6047 | -0.13877 | 121.2269 | 121.4382 | 121.4048 | -0.17788 | 0.087981 | 0.090373 | 0.17957 | 0.073966 | -0.014015 | -0.13489 | -0.23532 | 0.055574 | -0.24068 | 0.22993 | 0.094691 | 0.039117 | -0.029345 | -0.062772 | 121.7914 | 121.5662 | 121.4657 | 3.536 | -121.6131 | 121.4604 | 121.6717 | 121.6383 | 10.8381 | -121.6455
1633.2031 | 121.6461 | -0.21057 | 121.4813 | 1.4211e-13 | -0.027431 | -0.0018055 | 0.062889 | -0.0052006 | 0.056469 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059496 | -0.058472 | 3.3026 | -0.15491 | 121.5625 | 121.3373 | 121.2323 | -0.13632 | 0.001048 | 10.5772 | -0.13419 | 121.2269 | 121.4291 | 121.4094 | -0.16873 | 0.074251 | 0.081219 | 0.1521 | 0.055657 | -0.018594 | -0.14404 | -0.24906 | 0.041843 | -0.25441 | 0.21162 | 0.076382 | 0.034539 | -0.052235 | -0.071927 | 121.7731 | 121.5479 | 121.4428 | 3.5131 | -121.6176 | 121.4375 | 121.6397 | 121.62 | 10.7877 | -121.6501
1634.9844 | 121.6782 | -0.23346 | 121.4722 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.063103 | -0.004987 | 0.056469 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059282 | -0.067628 | 3.3117 | -0.15491 | 121.5625 | 121.3327 | 121.2414 | -0.1409 | 0.005626 | 10.5818 | -0.13877 | 121.2269 | 121.4245 | 121.4048 | -0.17331 | 0.09256 | 0.090374 | 0.16583 | 0.078545 | -0.014015 | -0.13947 | -0.23074 | 0.060153 | -0.24526 | 0.23908 | 0.094691 | 0.034538 | -0.047659 | -0.06735 | 121.796 | 121.5662 | 121.4749 | 3.5452 | -121.6131 | 121.4604 | 121.658 | 121.6383 | 10.8152 | -121.6455
1636.7031 | 121.6461 | -0.24261 | 121.463 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062889 | -0.0047732 | 0.056469 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063417 | 0.014369 | 0.059282 | -0.053893 | 3.3117 | -0.15949 | 121.5534 | 121.3419 | 121.2323 | -0.15006 | -0.003531 | 10.5863 | -0.13877 | 121.2223 | 121.4199 | 121.4048 | -0.17331 | 0.092558 | 0.090372 | 0.18872 | 0.083122 | -0.009436 | -0.12115 | -0.23075 | 0.069309 | -0.24068 | 0.23908 | 0.10385 | 0.034538 | -0.043082 | -0.058195 | 121.796 | 121.5845 | 121.4749 | 3.5544 | -121.6131 | 121.4649 | 121.6625 | 121.6474 | 10.829 | -121.6363
1638.4688 | 121.756 | -0.20599 | 121.4676 | 1.4211e-13 | -0.027645 | -0.0020193 | 0.063316 | -0.0052006 | 0.056683 | 0.0053411 | 0.00034614 | -0.00026913 | 0.063203 | 0.014583 | 0.059282 | -0.072207 | 3.2843 | -0.15949 | 121.5625 | 121.3327 | 121.2414 | -0.13632 | 0.001048 | 10.6275 | -0.13419 | 121.2269 | 121.4291 | 121.4094 | -0.16873 | 0.069674 | 0.094952 | 0.13379 | 0.046501 | -0.023173 | -0.13489 | -0.22617 | 0.037266 | -0.24068 | 0.20704 | 0.071805 | 0.034539 | -0.038502 | -0.058194 | 121.7685 | 121.5387 | 121.4474 | 3.4903 | -121.6039 | 121.4329 | 121.6351 | 121.6154 | 10.8335 | -121.6363
1640.1719 | 121.7148 | -0.20599 | 121.4539 | 1.4211e-13 | -0.027431 | -0.0018055 | 0.062675 | -0.004987 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.014156 | 0.05971 | -0.053893 | 3.298 | -0.15949 | 121.558 | 121.3373 | 121.2368 | -0.14548 | 0.001048 | 10.6321 | -0.12961 | 121.2223 | 121.4245 | 121.4048 | -0.17788 | 0.060516 | 0.10411 | 0.1521 | 0.046501 | -0.014015 | -0.11658 | -0.21701 | 0.028109 | -0.23152 | 0.20704 | 0.076384 | 0.048275 | -0.029348 | -0.049039 | 121.764 | 121.5433 | 121.4428 | 3.504 | -121.5993 | 121.4283 | 121.6305 | 121.6108 | 10.8381 | -121.6317
1641.9375 | 121.7743 | -0.19226 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.062889 | -0.004987 | 0.056683 | -0.0099194 | 0.00013254 | 0.00037167 | 0.06299 | 0.013942 | 0.059282 | -0.058472 | 3.298 | -0.15949 | 121.5671 | 121.3419 | 121.2368 | -0.13632 | 0.001048 | 10.623 | -0.13877 | 121.2269 | 121.4291 | 121.4094 | -0.17788 | 0.055941 | 0.127 | 0.13379 | 0.032768 | -0.023173 | -0.098266 | -0.20328 | 0.014376 | -0.21321 | 0.19331 | 0.053493 | 0.039117 | -0.011037 | -0.030729 | 121.7594 | 121.5341 | 121.4291 | 3.4903 | -121.5764 | 121.4192 | 121.6213 | 121.6017 | 10.8152 | -121.618
1643.7031 | 121.6965 | -0.21515 | 121.4722 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.06353 | -0.0052006 | 0.05711 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059282 | -0.053893 | 3.3072 | -0.15949 | 121.5625 | 121.3373 | 121.2323 | -0.1409 | 0.005626 | 10.6688 | -0.13419 | 121.2223 | 121.4291 | 121.4094 | -0.17788 | 0.07425 | 0.090374 | 0.16126 | 0.055656 | -0.018594 | -0.13489 | -0.2399 | 0.037264 | -0.24983 | 0.22077 | 0.08096 | 0.043696 | -0.04308 | -0.062772 | 121.7777 | 121.5524 | 121.4474 | 3.5223 | -121.6131 | 121.4375 | 121.6442 | 121.6245 | 10.8839 | -121.6501
1645.4688 | 121.7743 | -0.19226 | 121.4264 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.062675 | -0.004987 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014369 | 0.059282 | -0.06305 | 3.3117 | -0.15949 | 121.558 | 121.3327 | 121.2414 | -0.14548 | -0.003531 | 10.6504 | -0.12961 | 121.2223 | 121.4337 | 121.4048 | -0.16873 | 0.046783 | 0.13157 | 0.12921 | 0.032768 | -0.014015 | -0.093691 | -0.18497 | 0.023533 | -0.20406 | 0.18873 | 0.062651 | 0.039118 | 0.007275 | -0.021574 | 121.7502 | 121.525 | 121.4337 | 3.504 | -121.5719 | 121.4146 | 121.6259 | 121.5971 | 10.8427 | -121.5951
1647.1875 | 121.6644 | -0.23804 | 121.4951 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.063103 | -0.0047732 | 0.056683 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059496 | -0.058472 | 3.3117 | -0.15491 | 121.5671 | 121.3464 | 121.2323 | -0.14548 | 0.001048 | 10.6504 | -0.14335 | 121.2269 | 121.4291 | 121.414 | -0.16873 | 0.092559 | 0.072064 | 0.17957 | 0.083123 | -0.009436 | -0.14862 | -0.26279 | 0.069309 | -0.26814 | 0.23908 | 0.09469 | 0.025381 | -0.065968 | -0.081081 | 121.8052 | 121.5845 | 121.4703 | 3.5498 | -121.6405 | 121.4649 | 121.6671 | 121.652 | 10.8885 | -121.6638
1648.9531 | 121.6827 | -0.20142 | 121.463 | 1.4211e-13 | -0.027218 | -0.0015919 | 0.063103 | -0.004987 | 0.056683 | 0.0053411 | 0.00034614 | -0.00026913 | 0.063203 | 0.014156 | 0.059282 | -0.06305 | 3.3026 | -0.15491 | 121.5717 | 121.3464 | 121.2368 | -0.1409 | 0.001048 | 10.6367 | -0.12961 | 121.2315 | 121.4337 | 121.4094 | -0.18246 | 0.060517 | 0.10868 | 0.13837 | 0.046502 | -0.014015 | -0.11657 | -0.22617 | 0.018952 | -0.23152 | 0.20246 | 0.071806 | 0.052854 | -0.029346 | -0.053617 | 121.7731 | 121.5479 | 121.4383 | 3.504 | -121.6039 | 121.4329 | 121.6351 | 121.6108 | 10.8381 | -121.6455
1650.7188 | 121.7789 | -0.19684 | 121.4401 | 1.4211e-13 | -0.027431 | -0.0018055 | 0.063103 | -0.0047732 | 0.056683 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059282 | -0.058472 | 3.3026 | -0.15491 | 121.5625 | 121.3419 | 121.2323 | -0.14548 | -0.003531 | 10.6688 | -0.13419 | 121.2269 | 121.4291 | 121.4048 | -0.17788 | 0.05136 | 0.12242 | 0.13837 | 0.041924 | -0.009436 | -0.098266 | -0.20786 | 0.018953 | -0.21321 | 0.19331 | 0.062649 | 0.043696 | -0.011037 | -0.035307 | 121.7594 | 121.5387 | 121.4291 | 3.4994 | -121.5856 | 121.4237 | 121.6259 | 121.6017 | 10.8656 | -121.618
1652.4688 | 121.6599 | -0.21973 | 121.4722 | 1.4211e-13 | -0.027004 | -0.0015919 | 0.062675 | -0.004987 | 0.056683 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059496 | -0.053893 | 3.3072 | -0.15491 | 121.5671 | 121.351 | 121.2368 | -0.1409 | 0.005626 | 10.655 | -0.14335 | 121.2269 | 121.4291 | 121.414 | -0.18246 | 0.078828 | 0.094952 | 0.16583 | 0.064813 | -0.014015 | -0.12115 | -0.23532 | 0.037263 | -0.24526 | 0.22535 | 0.07638 | 0.039117 | -0.04308 | -0.058193 | 121.7868 | 121.5707 | 121.4566 | 3.5269 | -121.6131 | 121.4466 | 121.6488 | 121.6337 | 10.8747 | -121.6546
1654.25 | 121.6736 | -0.21515 | 121.4493 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.063316 | -0.0052006 | 0.056683 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063417 | 0.014156 | 0.059496 | -0.053893 | 3.3072 | -0.15949 | 121.5717 | 121.3464 | 121.2368 | -0.1409 | 0.001048 | 10.6779 | -0.13419 | 121.2315 | 121.4291 | 121.4094 | -0.16873 | 0.07425 | 0.12242 | 0.16126 | 0.055656 | -0.018594 | -0.10284 | -0.21243 | 0.046421 | -0.21779 | 0.2162 | 0.08096 | 0.034539 | -0.020192 | -0.039884 | 121.7868 | 121.5616 | 121.452 | 3.5223 | -121.5902 | 121.4466 | 121.6442 | 121.6245 | 10.8931 | -121.618
1655.9531 | 121.7377 | -0.21515 | 121.4584 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.063103 | -0.0047732 | 0.056896 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014369 | 0.059282 | -0.058472 | 3.3163 | -0.15949 | 121.5625 | 121.3419 | 121.246 | -0.14548 | 0.001048 | 10.6321 | -0.12961 | 121.2269 | 121.4337 | 121.4094 | -0.17331 | 0.069671 | 0.10411 | 0.15668 | 0.055656 | -0.014015 | -0.11658 | -0.21243 | 0.041843 | -0.23152 | 0.2162 | 0.085539 | 0.043696 | -0.024768 | -0.049039 | 121.7777 | 121.557 | 121.4612 | 3.5315 | -121.6039 | 121.4421 | 121.6488 | 121.6245 | 10.8473 | -121.6317
1657.6719 | 121.669 | -0.2243 | 121.4859 | 1.4211e-13 | -0.027431 | -0.0013783 | 0.063316 | -0.0052006 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059069 | -0.053893 | 3.3117 | -0.15491 | 121.5717 | 121.3419 | 121.2414 | -0.1409 | -0.00811 | 10.568 | -0.13419 | 121.2269 | 121.4291 | 121.414 | -0.18704 | 0.083405 | 0.085797 | 0.17041 | 0.06939 | -0.014015 | -0.14404 | -0.24448 | 0.037261 | -0.25899 | 0.21619 | 0.090115 | 0.052854 | -0.056813 | -0.071926 | 121.796 | 121.5662 | 121.4657 | 3.536 | -121.6268 | 121.4512 | 121.6534 | 121.6383 | 10.7923 | -121.6729
1659.4375 | 121.7148 | -0.23346 | 121.4722 | 1.4211e-13 | -0.027218 | -0.0018055 | 0.063103 | -0.0047732 | 0.056469 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.013942 | 0.059496 | -0.06305 | 3.3072 | -0.16407 | 121.5717 | 121.3419 | 121.246 | -0.1409 | -0.00811 | 10.568 | -0.13419 | 121.2269 | 121.4337 | 121.414 | -0.17331 | 0.09256 | 0.09953 | 0.17041 | 0.069388 | -0.023172 | -0.13031 | -0.22616 | 0.060153 | -0.24526 | 0.22535 | 0.09927 | 0.039117 | -0.038501 | -0.058193 | 121.8052 | 121.5753 | 121.4795 | 3.5406 | -121.6131 | 121.4604 | 121.6671 | 121.6474 | 10.8015 | -121.6455
1661.1406 | 121.7377 | -0.21515 | 121.4584 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.062462 | -0.004987 | 0.056896 | -0.0099194 | -8.1262e-05 | 0.00037167 | 0.063417 | 0.014369 | 0.059496 | -0.06305 | 3.3026 | -0.15491 | 121.558 | 121.3373 | 121.2414 | -0.14548 | -0.012689 | 10.623 | -0.13419 | 121.2269 | 121.4382 | 121.4094 | -0.17788 | 0.069671 | 0.099528 | 0.1521 | 0.060235 | -0.009436 | -0.12115 | -0.21701 | 0.037264 | -0.23152 | 0.20246 | 0.08096 | 0.043696 | -0.02019 | -0.049039 | 121.7731 | 121.5524 | 121.4566 | 3.5177 | -121.6039 | 121.4421 | 121.6534 | 121.6245 | 10.8381 | -121.6363
1662.9062 | 121.7697 | -0.17395 | 121.4355 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.062889 | -0.004987 | 0.056683 | -0.0099194 | 0.00013254 | -0.00048293 | 0.063417 | 0.014156 | 0.059496 | -0.058472 | 3.3072 | -0.16407 | 121.5625 | 121.351 | 121.2368 | -0.13632 | 0.001048 | 10.6047 | -0.13419 | 121.2269 | 121.4337 | 121.4048 | -0.16873 | 0.03763 | 0.12699 | 0.11548 | 0.009879 | -0.027751 | -0.08453 | -0.1987 | 0.005222 | -0.20864 | 0.175 | 0.039761 | 0.034539 | -0.00188 | -0.030729 | 121.7365 | 121.525 | 121.4108 | 3.4811 | -121.5719 | 121.4009 | 121.6076 | 121.5788 | 10.7786 | -121.6043
1664.6719 | 121.7651 | -0.1831 | 121.4401 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.063103 | -0.0052006 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014583 | 0.05971 | -0.06305 | 3.3438 | -0.15491 | 121.5625 | 121.351 | 121.2414 | -0.1409 | -0.003531 | 10.6047 | -0.14793 | 121.2269 | 121.4382 | 121.4048 | -0.18246 | 0.042206 | 0.12242 | 0.12005 | 0.028191 | -0.014015 | -0.089108 | -0.1987 | 0.000641 | -0.21321 | 0.17957 | 0.03518 | 0.034539 | -0.00188 | -0.035307 | 121.7456 | 121.5341 | 121.4245 | 3.5269 | -121.581 | 121.41 | 121.6213 | 121.5879 | 10.7878 | -121.6226
1666.4375 | 121.7697 | -0.17853 | 121.4493 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.063103 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063417 | 0.014369 | 0.059282 | -0.058472 | 3.3392 | -0.15034 | 121.5625 | 121.3419 | 121.2414 | -0.1409 | 0.010205 | 10.6275 | -0.13419 | 121.2269 | 121.4245 | 121.414 | -0.17331 | 0.037629 | 0.11326 | 0.12006 | 0.028192 | -0.009437 | -0.10742 | -0.20786 | 0.005222 | -0.22237 | 0.18873 | 0.044339 | 0.039117 | -0.024771 | -0.035305 | 121.7411 | 121.5204 | 121.42 | 3.5177 | -121.5902 | 121.4054 | 121.603 | 121.5925 | 10.8061 | -121.6226
1668.1406 | 121.8063 | -0.19226 | 121.4355 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.062889 | -0.004987 | 0.056896 | 0.0053411 | 0.00013254 | 0.00015807 | 0.06299 | 0.014583 | 0.059282 | -0.053893 | 3.3346 | -0.15949 | 121.5763 | 121.351 | 121.2414 | -0.14548 | -0.003531 | 10.5543 | -0.13877 | 121.2315 | 121.4337 | 121.4094 | -0.16873 | 0.046783 | 0.14073 | 0.13837 | 0.032768 | -0.014015 | -0.08453 | -0.19412 | 0.023533 | -0.20406 | 0.18873 | 0.053493 | 0.02996 | -0.00188 | -0.026151 | 121.7685 | 121.5433 | 121.4337 | 3.5269 | -121.581 | 121.4238 | 121.6259 | 121.6017 | 10.7465 | -121.6043
1669.9219 | 121.7056 | -0.20142 | 121.4539 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.063103 | -0.0052006 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062776 | 0.014369 | 0.059496 | -0.058472 | 3.3392 | -0.15949 | 121.5717 | 121.3373 | 121.246 | -0.14548 | -0.003531 | 10.5955 | -0.14793 | 121.2315 | 121.4337 | 121.4094 | -0.17788 | 0.055938 | 0.11784 | 0.14294 | 0.041923 | -0.014015 | -0.11658 | -0.20785 | 0.023531 | -0.22237 | 0.19789 | 0.053491 | 0.02996 | -0.02019 | -0.044461 | 121.7731 | 121.5387 | 121.4474 | 3.5406 | -121.5993 | 121.4329 | 121.6351 | 121.6108 | 10.7969 | -121.6317
1671.625 | 121.7102 | -0.22888 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.063103 | -0.004987 | 0.056469 | -0.0099194 | 0.00034614 | -0.00026913 | 0.063203 | 0.014369 | 0.059069 | -0.058472 | 3.3301 | -0.15949 | 121.558 | 121.3464 | 121.246 | -0.14548 | -0.003531 | 10.6459 | -0.13877 | 121.2269 | 121.4245 | 121.4094 | -0.17788 | 0.083404 | 0.11784 | 0.17041 | 0.069389 | -0.014015 | -0.093687 | -0.19412 | 0.050997 | -0.21321 | 0.22535 | 0.090114 | 0.039117 | -0.015616 | -0.030729 | 121.7868 | 121.5753 | 121.4749 | 3.5589 | -121.5856 | 121.4558 | 121.6534 | 121.6383 | 10.8747 | -121.618
1673.3906 | 121.701 | -0.21515 | 121.4676 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.062889 | -0.004987 | 0.056896 | -0.0022889 | 0.00034614 | 0.00015807 | 0.063417 | 0.014369 | 0.059496 | -0.058472 | 3.3346 | -0.15034 | 121.5717 | 121.3464 | 121.2368 | -0.15464 | -0.003531 | 10.6596 | -0.13877 | 121.2361 | 121.4337 | 121.414 | -0.18246 | 0.060513 | 0.10411 | 0.15668 | 0.064813 | 0.0043 | -0.12115 | -0.23074 | 0.032685 | -0.23152 | 0.21162 | 0.076381 | 0.043696 | -0.033923 | -0.053615 | 121.7868 | 121.5616 | 121.452 | 3.5498 | -121.6222 | 121.4512 | 121.6488 | 121.6291 | 10.8747 | -121.6501
1675.0938 | 121.6599 | -0.24261 | 121.4722 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.063103 | -0.004987 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.013942 | 0.059069 | -0.06305 | 3.3209 | -0.16407 | 121.5763 | 121.3464 | 121.2414 | -0.1409 | 0.001048 | 10.6092 | -0.13419 | 121.2361 | 121.4291 | 121.4094 | -0.17788 | 0.10172 | 0.10411 | 0.17957 | 0.078544 | -0.023172 | -0.12573 | -0.23074 | 0.06473 | -0.2361 | 0.24366 | 0.10843 | 0.043696 | -0.04308 | -0.062772 | 121.8189 | 121.5891 | 121.484 | 3.5635 | -121.6131 | 121.4787 | 121.6717 | 121.652 | 10.8518 | -121.6501
1676.875 | 121.7148 | -0.2243 | 121.4539 | 1.4211e-13 | -0.027645 | -0.0015919 | 0.062675 | -0.0052006 | 0.056896 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014156 | 0.059496 | -0.058472 | 3.3575 | -0.16407 | 121.5625 | 121.351 | 121.2414 | -0.14548 | -0.003531 | 10.5772 | -0.13419 | 121.2223 | 121.4291 | 121.4048 | -0.17331 | 0.078826 | 0.10868 | 0.16583 | 0.060233 | -0.018593 | -0.10284 | -0.21243 | 0.050998 | -0.23152 | 0.22077 | 0.090115 | 0.039117 | -0.024769 | -0.049039 | 121.7868 | 121.5753 | 121.4657 | 3.5818 | -121.5993 | 121.4466 | 121.6534 | 121.6291 | 10.8015 | -121.6272
1678.6406 | 121.7377 | -0.21515 | 121.4218 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.063103 | -0.0052006 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.014369 | 0.05971 | -0.06305 | 3.3575 | -0.15949 | 121.558 | 121.3419 | 121.2414 | -0.15006 | -0.00811 | 10.623 | -0.13419 | 121.2361 | 121.4428 | 121.4094 | -0.18704 | 0.065092 | 0.13615 | 0.1521 | 0.055656 | -0.009436 | -0.079955 | -0.18039 | 0.028106 | -0.18574 | 0.20704 | 0.08096 | 0.052854 | 0.02101 | -0.012418 | 121.7731 | 121.557 | 121.4566 | 3.5727 | -121.5719 | 121.4512 | 121.658 | 121.6245 | 10.8381 | -121.6089
1680.4062 | 121.7102 | -0.23346 | 121.4493 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062889 | -0.004987 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059069 | -0.06305 | 3.3529 | -0.15034 | 121.558 | 121.3464 | 121.246 | -0.15006 | 0.001048 | 10.6413 | -0.13877 | 121.2269 | 121.4337 | 121.4048 | -0.18704 | 0.083402 | 0.10868 | 0.17041 | 0.083123 | -0.000279 | -0.10284 | -0.20328 | 0.046416 | -0.22237 | 0.23451 | 0.094691 | 0.048275 | -0.015613 | -0.044462 | 121.7914 | 121.5799 | 121.4795 | 3.5864 | -121.5993 | 121.4604 | 121.6671 | 121.6383 | 10.8747 | -121.6363
1682.125 | 121.7789 | -0.20142 | 121.4539 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.063316 | -0.004987 | 0.056896 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063417 | 0.014369 | 0.059282 | -0.053893 | 3.3621 | -0.15949 | 121.5625 | 121.3464 | 121.2368 | -0.14548 | -0.003531 | 10.655 | -0.13419 | 121.2315 | 121.4337 | 121.4048 | -0.17788 | 0.055938 | 0.10868 | 0.14752 | 0.041923 | -0.014015 | -0.10742 | -0.21701 | 0.023531 | -0.22237 | 0.19789 | 0.067227 | 0.043696 | -0.02019 | -0.049039 | 121.764 | 121.5479 | 121.4383 | 3.5635 | -121.5993 | 121.4329 | 121.6351 | 121.6062 | 10.8564 | -121.6317
1683.8906 | 121.7194 | -0.21515 | 121.4355 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.063103 | -0.0052006 | 0.056469 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059069 | -0.06305 | 3.3621 | -0.16865 | 121.5625 | 121.351 | 121.2368 | -0.15006 | 0.010205 | 10.568 | -0.14335 | 121.2269 | 121.4337 | 121.4048 | -0.18246 | 0.065092 | 0.12699 | 0.1521 | 0.0465 | -0.018592 | -0.08453 | -0.1987 | 0.032685 | -0.20864 | 0.22535 | 0.071802 | 0.039117 | -0.00188 | -0.030729 | 121.7777 | 121.5662 | 121.452 | 3.5772 | -121.5856 | 121.4421 | 121.6488 | 121.62 | 10.7832 | -121.618
1685.6562 | 121.6736 | -0.23346 | 121.4905 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.063103 | -0.0054142 | 0.056683 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059282 | -0.067628 | 3.3575 | -0.15949 | 121.5763 | 121.3419 | 121.2414 | -0.15006 | -0.003531 | 10.6092 | -0.13877 | 121.2223 | 121.4337 | 121.414 | -0.18704 | 0.083402 | 0.085798 | 0.16583 | 0.073966 | -0.009436 | -0.14862 | -0.24905 | 0.046416 | -0.26814 | 0.22993 | 0.094691 | 0.048275 | -0.056812 | -0.076504 | 121.8097 | 121.5753 | 121.4749 | 3.591 | -121.6405 | 121.4558 | 121.6671 | 121.6474 | 10.8427 | -121.6775
1687.4219 | 121.6278 | -0.21515 | 121.4767 | 1.4211e-13 | -0.027645 | -0.0015919 | 0.063103 | -0.0052006 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014369 | 0.05971 | -0.058472 | 3.3667 | -0.15949 | 121.5717 | 121.351 | 121.2506 | -0.15006 | -0.00811 | 10.6047 | -0.13877 | 121.2269 | 121.4291 | 121.4094 | -0.17788 | 0.065092 | 0.094952 | 0.15668 | 0.055656 | -0.009436 | -0.12573 | -0.22617 | 0.037264 | -0.24983 | 0.20704 | 0.076381 | 0.039117 | -0.047658 | -0.06735 | 121.7868 | 121.5662 | 121.4657 | 3.5818 | -121.6268 | 121.4421 | 121.6442 | 121.6245 | 10.8198 | -121.6546
1689.125 | 121.7148 | -0.23346 | 121.4447 | 1.4211e-13 | -0.027218 | -0.0013783 | 0.063103 | -0.0054142 | 0.056255 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.059496 | -0.067628 | 3.3667 | -0.15949 | 121.5671 | 121.351 | 121.2506 | -0.15464 | -0.003531 | 10.536 | -0.13877 | 121.2269 | 121.4428 | 121.414 | -0.18246 | 0.078823 | 0.12242 | 0.16583 | 0.073966 | -0.004857 | -0.093685 | -0.19412 | 0.050995 | -0.21779 | 0.22993 | 0.094691 | 0.043696 | -0.001878 | -0.030727 | 121.8006 | 121.5845 | 121.484 | 3.6001 | -121.5993 | 121.4604 | 121.6763 | 121.6474 | 10.7694 | -121.6272
1690.9062 | 121.669 | -0.22888 | 121.4813 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062889 | -0.004987 | 0.056683 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.062776 | 0.014583 | 0.059282 | -0.058472 | 3.3758 | -0.16407 | 121.5671 | 121.3464 | 121.2414 | -0.14548 | -0.003531 | 10.4764 | -0.14335 | 121.2223 | 121.4337 | 121.4002 | -0.18246 | 0.083404 | 0.085797 | 0.17041 | 0.064811 | -0.018593 | -0.13488 | -0.2399 | 0.046418 | -0.25899 | 0.22535 | 0.085535 | 0.039117 | -0.047656 | -0.081084 | 121.796 | 121.5753 | 121.4703 | 3.6047 | -121.6268 | 121.4512 | 121.6625 | 121.6291 | 10.7053 | -121.6638
1692.6875 | 121.637 | -0.23804 | 121.4859 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.063103 | -0.0052006 | 0.056683 | -0.0022889 | -0.00029486 | -0.00026913 | 0.06299 | 0.014369 | 0.059282 | -0.053893 | 3.3896 | -0.16407 | 121.5671 | 121.3464 | 121.246 | -0.14548 | -0.003531 | 10.5314 | -0.14335 | 121.2269 | 121.4291 | 121.414 | -0.18246 | 0.092559 | 0.081219 | 0.18414 | 0.073966 | -0.018593 | -0.13946 | -0.2399 | 0.055573 | -0.25899 | 0.23451 | 0.09469 | 0.039117 | -0.056813 | -0.071926 | 121.8052 | 121.5845 | 121.484 | 3.6276 | -121.6314 | 121.4649 | 121.6671 | 121.652 | 10.7694 | -121.6684
1694.3906 | 121.6827 | -0.24261 | 121.4905 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062889 | -0.0047732 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014583 | 0.059282 | -0.067628 | 3.3804 | -0.15949 | 121.5625 | 121.351 | 121.246 | -0.14548 | 0.001048 | 10.5039 | -0.14335 | 121.2315 | 121.4428 | 121.4048 | -0.18704 | 0.097137 | 0.072063 | 0.17499 | 0.083122 | -0.014015 | -0.13946 | -0.24448 | 0.055572 | -0.25899 | 0.24366 | 0.099268 | 0.043696 | -0.047655 | -0.085661 | 121.8052 | 121.5936 | 121.4886 | 3.623 | -121.636 | 121.4741 | 121.6854 | 121.6474 | 10.7465 | -121.6775
1696.1562 | 121.7239 | -0.20599 | 121.4447 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.063316 | -0.0052006 | 0.056469 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014156 | 0.059282 | -0.058472 | 3.3667 | -0.15949 | 121.5671 | 121.351 | 121.2414 | -0.15464 | -0.00811 | 10.5451 | -0.13877 | 121.2223 | 121.4428 | 121.4048 | -0.17331 | 0.051358 | 0.12242 | 0.14752 | 0.046501 | -0.004857 | -0.093685 | -0.20328 | 0.032688 | -0.22237 | 0.19788 | 0.067226 | 0.034538 | -0.001878 | -0.039884 | 121.7731 | 121.557 | 121.4474 | 3.5727 | -121.5993 | 121.4283 | 121.6488 | 121.6108 | 10.7511 | -121.618
1697.8594 | 121.7102 | -0.19226 | 121.4859 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.063316 | -0.004987 | 0.056469 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063203 | 0.014156 | 0.05971 | -0.067628 | 3.3529 | -0.15034 | 121.5717 | 121.3419 | 121.2506 | -0.14548 | 0.001048 | 10.5772 | -0.13419 | 121.2269 | 121.4474 | 121.4094 | -0.18246 | 0.046783 | 0.085797 | 0.12463 | 0.041925 | -0.004858 | -0.14404 | -0.23532 | 0.009797 | -0.25899 | 0.19331 | 0.058072 | 0.048275 | -0.038499 | -0.076505 | 121.764 | 121.5341 | 121.4428 | 3.5452 | -121.6314 | 121.4192 | 121.6397 | 121.6017 | 10.7694 | -121.6684
1699.625 | 121.7194 | -0.22888 | 121.4767 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.062889 | -0.004987 | 0.056469 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.014797 | 0.059496 | -0.058472 | 3.3758 | -0.15034 | 121.5625 | 121.3464 | 121.2414 | -0.14548 | -0.003531 | 10.5589 | -0.13877 | 121.2315 | 121.4382 | 121.414 | -0.18246 | 0.083404 | 0.085796 | 0.17041 | 0.078546 | -0.004858 | -0.13031 | -0.23532 | 0.046418 | -0.24526 | 0.22535 | 0.090114 | 0.043696 | -0.038501 | -0.062771 | 121.7914 | 121.5753 | 121.4703 | 3.6047 | -121.6222 | 121.4604 | 121.6671 | 121.6429 | 10.7877 | -121.6592
1701.3281 | 121.7377 | -0.21057 | 121.4447 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062675 | -0.0047732 | 0.056469 | -0.0099194 | 0.00034614 | 0.00015807 | 0.06299 | 0.014369 | 0.059496 | -0.058472 | 3.3942 | -0.15949 | 121.558 | 121.3419 | 121.2414 | -0.14548 | -0.012689 | 10.5955 | -0.13877 | 121.2223 | 121.4337 | 121.4048 | -0.17788 | 0.065093 | 0.11326 | 0.1521 | 0.051078 | -0.014015 | -0.10284 | -0.20328 | 0.032686 | -0.22237 | 0.19788 | 0.071803 | 0.039117 | -0.011035 | -0.039884 | 121.7685 | 121.5524 | 121.452 | 3.6047 | -121.5902 | 121.4329 | 121.6442 | 121.6154 | 10.8061 | -121.6226
1703.1094 | 121.6736 | -0.23804 | 121.463 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062889 | -0.0052006 | 0.056255 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014369 | 0.059496 | -0.058472 | 3.3896 | -0.15491 | 121.5671 | 121.3419 | 121.2368 | -0.14548 | -0.003531 | 10.5772 | -0.14793 | 121.2269 | 121.4474 | 121.4048 | -0.18246 | 0.092559 | 0.10411 | 0.17957 | 0.083123 | -0.009436 | -0.12115 | -0.22617 | 0.055573 | -0.2361 | 0.23451 | 0.090112 | 0.034539 | -0.015611 | -0.058195 | 121.8052 | 121.5799 | 121.4749 | 3.6276 | -121.6085 | 121.4649 | 121.6854 | 121.6429 | 10.8152 | -121.6455
1704.8125 | 121.6644 | -0.21973 | 121.4905 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062675 | -0.0054142 | 0.056896 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.063203 | 0.014369 | 0.059496 | -0.058472 | 3.3942 | -0.16407 | 121.5625 | 121.351 | 121.2506 | -0.15006 | 0.001048 | 10.6138 | -0.14793 | 121.2223 | 121.4337 | 121.414 | -0.18246 | 0.06967 | 0.072063 | 0.16126 | 0.055656 | -0.014014 | -0.13946 | -0.2399 | 0.037263 | -0.26814 | 0.22077 | 0.071802 | 0.034539 | -0.056812 | -0.076504 | 121.7823 | 121.5707 | 121.4703 | 3.6139 | -121.6405 | 121.4421 | 121.6534 | 121.6337 | 10.8335 | -121.6729
1706.5781 | 121.6827 | -0.23346 | 121.4905 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062889 | -0.004987 | 0.056683 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014369 | 0.059282 | -0.06305 | 3.3804 | -0.16407 | 121.5625 | 121.3464 | 121.246 | -0.1409 | 0.001048 | 10.6047 | -0.14335 | 121.2269 | 121.4428 | 121.4048 | -0.18704 | 0.09256 | 0.072063 | 0.17041 | 0.069388 | -0.023172 | -0.14404 | -0.24448 | 0.046416 | -0.26357 | 0.23451 | 0.090112 | 0.043696 | -0.047655 | -0.085661 | 121.796 | 121.5799 | 121.4795 | 3.6139 | -121.6314 | 121.4604 | 121.6763 | 121.6383 | 10.8381 | -121.6775
1708.3438 | 121.7789 | -0.17853 | 121.4493 | 1.4211e-13 | -0.027645 | -0.0020193 | 0.062462 | -0.004987 | 0.056469 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014369 | 0.059282 | -0.053893 | 3.3804 | -0.16407 | 121.5717 | 121.351 | 121.2506 | -0.14548 | -0.003531 | 10.5818 | -0.13419 | 121.2361 | 121.4428 | 121.4048 | -0.17788 | 0.03305 | 0.12242 | 0.12463 | 0.014457 | -0.018593 | -0.098263 | -0.1987 | 0.000643 | -0.21321 | 0.175 | 0.044339 | 0.043696 | -0.006456 | -0.044462 | 121.7502 | 121.5295 | 121.4291 | 3.5589 | -121.5948 | 121.4146 | 121.6214 | 121.5833 | 10.7603 | -121.6272
1710.0469 | 121.6827 | -0.22888 | 121.4767 | 1.4211e-13 | -0.027645 | -0.0020193 | 0.062889 | -0.0052006 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.014156 | 0.059069 | -0.06305 | 3.3713 | -0.15034 | 121.5671 | 121.3556 | 121.2414 | -0.14548 | -0.003531 | 10.5222 | -0.13419 | 121.2223 | 121.4566 | 121.4048 | -0.18246 | 0.083404 | 0.090374 | 0.16583 | 0.078546 | -0.004858 | -0.12115 | -0.23532 | 0.046418 | -0.25441 | 0.22535 | 0.094693 | 0.048275 | -0.020186 | -0.071928 | 121.796 | 121.5845 | 121.4703 | 3.6001 | -121.6222 | 121.4512 | 121.6854 | 121.6337 | 10.7511 | -121.6592
1711.8125 | 121.6599 | -0.23346 | 121.463 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.063103 | -0.0052006 | 0.056255 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.014369 | 0.059496 | -0.06305 | 3.3713 | -0.15949 | 121.558 | 121.3419 | 121.2323 | -0.14548 | -0.003531 | 10.5451 | -0.13877 | 121.2269 | 121.4337 | 121.4048 | -0.18246 | 0.087981 | 0.09495 | 0.17041 | 0.073966 | -0.014015 | -0.12115 | -0.23075 | 0.050995 | -0.2361 | 0.22993 | 0.094691 | 0.043696 | -0.029346 | -0.058195 | 121.7914 | 121.5753 | 121.4657 | 3.6047 | -121.6085 | 121.4604 | 121.6671 | 121.6383 | 10.7786 | -121.6455
1713.5938 | 121.7239 | -0.21057 | 121.4584 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.063103 | -0.0052006 | 0.056683 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.014156 | 0.059282 | -0.06305 | 3.3667 | -0.16865 | 121.5625 | 121.3464 | 121.246 | -0.14548 | -0.003531 | 10.536 | -0.14335 | 121.2315 | 121.4382 | 121.4094 | -0.18704 | 0.065093 | 0.10411 | 0.14752 | 0.041922 | -0.023171 | -0.112 | -0.21243 | 0.023528 | -0.22694 | 0.20704 | 0.067224 | 0.043696 | -0.02019 | -0.049039 | 121.7731 | 121.557 | 121.4566 | 3.5772 | -121.6039 | 121.4421 | 121.6488 | 121.62 | 10.7465 | -121.6455
1715.2969 | 121.701 | -0.2243 | 121.463 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.062889 | -0.005628 | 0.056683 | -0.0022889 | 0.00055974 | 0.00015807 | 0.06299 | 0.014583 | 0.059496 | -0.067628 | 3.3529 | -0.15949 | 121.5717 | 121.3602 | 121.2414 | -0.15006 | -0.003531 | 10.5634 | -0.13877 | 121.2178 | 121.4382 | 121.414 | -0.18246 | 0.074247 | 0.10868 | 0.15668 | 0.064811 | -0.009436 | -0.10284 | -0.22159 | 0.04184 | -0.24526 | 0.22077 | 0.085536 | 0.043696 | -0.024768 | -0.049038 | 121.796 | 121.5845 | 121.4657 | 3.5772 | -121.6131 | 121.4421 | 121.6625 | 121.6383 | 10.7877 | -121.6455
1717.0625 | 121.6965 | -0.22888 | 121.4767 | 1.4211e-13 | -0.027859 | -0.0011645 | 0.063103 | -0.0054142 | 0.056255 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063203 | 0.014156 | 0.059496 | -0.06305 | 3.3896 | -0.15949 | 121.5671 | 121.351 | 121.2414 | -0.14548 | -0.00811 | 10.5863 | -0.13877 | 121.2269 | 121.4337 | 121.4094 | -0.18246 | 0.083404 | 0.090374 | 0.16583 | 0.069389 | -0.014015 | -0.12573 | -0.23532 | 0.046418 | -0.24983 | 0.22077 | 0.090114 | 0.043696 | -0.043079 | -0.06735 | 121.796 | 121.5799 | 121.4703 | 3.6185 | -121.6222 | 121.4558 | 121.6625 | 121.6383 | 10.8152 | -121.6592
1718.7656 | 121.701 | -0.22888 | 121.463 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062462 | -0.0052006 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014797 | 0.059282 | -0.067628 | 3.3575 | -0.16407 | 121.5671 | 121.3556 | 121.2368 | -0.15006 | -0.012689 | 10.4993 | -0.14335 | 121.2315 | 121.4428 | 121.4094 | -0.17788 | 0.078825 | 0.10411 | 0.16125 | 0.064811 | -0.014014 | -0.10742 | -0.22617 | 0.050997 | -0.23152 | 0.21619 | 0.085535 | 0.034538 | -0.020189 | -0.053617 | 121.796 | 121.5845 | 121.4657 | 3.5864 | -121.6131 | 121.4604 | 121.6717 | 121.6383 | 10.7282 | -121.6409
1720.5469 | 121.6599 | -0.24261 | 121.5042 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.063103 | -0.004987 | 0.056255 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.062776 | 0.014369 | 0.059496 | -0.06305 | 3.3575 | -0.15949 | 121.5671 | 121.351 | 121.2414 | -0.15006 | -0.00811 | 10.536 | -0.13877 | 121.2223 | 121.4382 | 121.4048 | -0.18246 | 0.092558 | 0.062909 | 0.17957 | 0.083122 | -0.009436 | -0.15319 | -0.26279 | 0.060151 | -0.28188 | 0.2345 | 0.10385 | 0.043696 | -0.065966 | -0.099393 | 121.8097 | 121.5936 | 121.484 | 3.6001 | -121.6543 | 121.4649 | 121.6809 | 121.6474 | 10.7786 | -121.6867
1722.3281 | 121.7468 | -0.21973 | 121.4767 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062889 | -0.004987 | 0.056255 | 0.0053411 | 0.00013254 | 0.00037167 | 0.06299 | 0.014797 | 0.059496 | -0.06305 | 3.3484 | -0.16407 | 121.5717 | 121.3464 | 121.2506 | -0.15006 | -0.00811 | 10.5085 | -0.13877 | 121.2269 | 121.4291 | 121.4002 | -0.18704 | 0.06967 | 0.094952 | 0.15668 | 0.055656 | -0.014014 | -0.13031 | -0.22617 | 0.032684 | -0.24983 | 0.21162 | 0.080959 | 0.048275 | -0.047658 | -0.076507 | 121.7914 | 121.5662 | 121.4703 | 3.5681 | -121.6268 | 121.4466 | 121.6488 | 121.62 | 10.7282 | -121.6638
1724.0938 | 121.669 | -0.26093 | 121.4767 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.062889 | -0.004987 | 0.056683 | 0.012972 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059282 | -0.053893 | 3.3667 | -0.16865 | 121.5671 | 121.3556 | 121.2414 | -0.14548 | -0.003531 | 10.5039 | -0.14335 | 121.2132 | 121.4382 | 121.4094 | -0.18246 | 0.11545 | 0.090374 | 0.20703 | 0.092276 | -0.023171 | -0.12115 | -0.23532 | 0.078461 | -0.26357 | 0.25739 | 0.11758 | 0.039117 | -0.038501 | -0.06735 | 121.828 | 121.6165 | 121.5023 | 3.6276 | -121.6222 | 121.4741 | 121.6992 | 121.6703 | 10.7648 | -121.6592
1725.7969 | 121.8201 | -0.19684 | 121.4539 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062889 | -0.0052006 | 0.056469 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014156 | 0.05971 | -0.06305 | 3.3804 | -0.15949 | 121.5625 | 121.3556 | 121.2368 | -0.15006 | -0.012689 | 10.5131 | -0.14335 | 121.2223 | 121.4428 | 121.4094 | -0.1962 | 0.046781 | 0.10868 | 0.13379 | 0.037345 | -0.009436 | -0.098261 | -0.21701 | 0.000638 | -0.23152 | 0.18415 | 0.053491 | 0.052853 | -0.011033 | -0.044461 | 121.7594 | 121.5524 | 121.4337 | 3.5773 | -121.6039 | 121.4192 | 121.6397 | 121.6062 | 10.7099 | -121.6501
1727.5781 | 121.7606 | -0.18768 | 121.4539 | 1.4211e-13 | -0.027859 | -0.0011645 | 0.062889 | -0.004987 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014797 | 0.059282 | -0.058472 | 3.3987 | -0.16407 | 121.5625 | 121.351 | 121.2506 | -0.15006 | -0.012689 | 10.5543 | -0.14335 | 121.2269 | 121.4382 | 121.4094 | -0.18704 | 0.037626 | 0.10868 | 0.12921 | 0.023612 | -0.014014 | -0.10284 | -0.20328 | 0.00064 | -0.22695 | 0.17499 | 0.044336 | 0.043696 | -0.015612 | -0.044461 | 121.7502 | 121.5387 | 121.4383 | 3.5864 | -121.6039 | 121.4146 | 121.6259 | 121.5971 | 10.742 | -121.6409
1729.3594 | 121.7422 | -0.21515 | 121.4767 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062889 | -0.0054142 | 0.056042 | 0.0053411 | 0.00013254 | -0.00026913 | 0.063203 | 0.014583 | 0.059282 | -0.067628 | 3.3987 | -0.15949 | 121.5625 | 121.3556 | 121.246 | -0.15006 | -0.00811 | 10.5772 | -0.14335 | 121.2223 | 121.4382 | 121.4048 | -0.19162 | 0.065092 | 0.085796 | 0.14752 | 0.055656 | -0.009436 | -0.12115 | -0.23074 | 0.023527 | -0.25441 | 0.20704 | 0.071802 | 0.048275 | -0.038501 | -0.071928 | 121.7777 | 121.5707 | 121.4612 | 3.6139 | -121.6268 | 121.4375 | 121.6534 | 121.62 | 10.7923 | -121.6684
1731.0469 | 121.7789 | -0.19226 | 121.4493 | 1.4211e-13 | -0.027645 | -0.0013783 | 0.062889 | -0.0052006 | 0.056683 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.06299 | 0.014583 | 0.059282 | -0.067628 | 3.385 | -0.16407 | 121.5717 | 121.3556 | 121.2506 | -0.14548 | -0.00811 | 10.5634 | -0.14335 | 121.2178 | 121.4291 | 121.4002 | -0.18246 | 0.046783 | 0.12242 | 0.12463 | 0.02819 | -0.018593 | -0.093684 | -0.1987 | 0.009797 | -0.23153 | 0.18415 | 0.048914 | 0.039117 | -0.020192 | -0.049041 | 121.764 | 121.5479 | 121.4428 | 3.5773 | -121.5948 | 121.41 | 121.6213 | 121.5925 | 10.7557 | -121.6317
1732.8281 | 121.7422 | -0.21515 | 121.4676 | 1.4211e-13 | -0.028286 | -0.0020193 | 0.062889 | -0.0052006 | 0.056255 | 0.0053411 | 0.00034614 | -0.00026913 | 0.062776 | 0.014583 | 0.059282 | -0.06305 | 3.3804 | -0.16407 | 121.5671 | 121.3464 | 121.2414 | -0.15921 | -0.00811 | 10.5955 | -0.14793 | 121.2269 | 121.4382 | 121.4094 | -0.19162 | 0.055934 | 0.09953 | 0.1521 | 0.051078 | -0.004856 | -0.12115 | -0.22617 | 0.023527 | -0.24068 | 0.20704 | 0.067224 | 0.043697 | -0.029345 | -0.058194 | 121.7823 | 121.5616 | 121.4566 | 3.5956 | -121.6268 | 121.4421 | 121.6534 | 121.6245 | 10.8106 | -121.6592
1734.5312 | 121.7697 | -0.19684 | 121.4447 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.063103 | -0.004987 | 0.056255 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014583 | 0.059496 | -0.072207 | 3.3896 | -0.16407 | 121.5671 | 121.3419 | 121.2414 | -0.15464 | -0.012689 | 10.5909 | -0.14335 | 121.2269 | 121.4382 | 121.3957 | -0.19162 | 0.042202 | 0.12242 | 0.12463 | 0.032767 | -0.009435 | -0.10284 | -0.20328 | 0.005216 | -0.21779 | 0.18415 | 0.053491 | 0.048275 | -0.006457 | -0.049041 | 121.764 | 121.5387 | 121.4383 | 3.5864 | -121.5993 | 121.4237 | 121.6351 | 121.5925 | 10.7878 | -121.6363
1736.2969 | 121.6553 | -0.24261 | 121.463 | 1.4211e-13 | -0.027431 | -0.0018055 | 0.062889 | -0.0054142 | 0.056469 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014369 | 0.059282 | -0.06305 | 3.3987 | -0.17323 | 121.5717 | 121.3464 | 121.246 | -0.14548 | -0.012689 | 10.5497 | -0.13877 | 121.2223 | 121.4382 | 121.4094 | -0.19162 | 0.097137 | 0.10868 | 0.17957 | 0.069388 | -0.027749 | -0.11657 | -0.21701 | 0.050993 | -0.24068 | 0.22993 | 0.10385 | 0.052854 | -0.024768 | -0.053617 | 121.8143 | 121.5891 | 121.4886 | 3.6413 | -121.6085 | 121.4649 | 121.6809 | 121.652 | 10.7923 | -121.6546
1738 | 121.6919 | -0.24261 | 121.4584 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.0047732 | 0.056469 | -0.01755 | 0.00013254 | 0.00015807 | 0.063203 | 0.014583 | 0.059282 | -0.06305 | 3.4079 | -0.16407 | 121.5717 | 121.3464 | 121.2414 | -0.15464 | -0.012689 | 10.623 | -0.14793 | 121.2223 | 121.4382 | 121.4002 | -0.18704 | 0.087979 | 0.11326 | 0.17957 | 0.078544 | -0.009435 | -0.112 | -0.21701 | 0.055572 | -0.2361 | 0.22993 | 0.09469 | 0.039118 | -0.02019 | -0.058196 | 121.8143 | 121.5891 | 121.484 | 3.6505 | -121.6131 | 121.4649 | 121.6809 | 121.6429 | 10.8656 | -121.6455
1739.7656 | 121.7148 | -0.22888 | 121.4813 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062675 | -0.004987 | 0.056255 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.06299 | 0.014156 | 0.059496 | -0.067628 | 3.3896 | -0.16865 | 121.5671 | 121.3464 | 121.246 | -0.15464 | -0.012689 | 10.5818 | -0.1525 | 121.2223 | 121.4474 | 121.4048 | -0.1962 | 0.074246 | 0.085797 | 0.16125 | 0.060233 | -0.014013 | -0.13488 | -0.23532 | 0.032682 | -0.25899 | 0.21619 | 0.076378 | 0.043696 | -0.033921 | -0.076505 | 121.796 | 121.5753 | 121.4749 | 3.6185 | -121.636 | 121.4512 | 121.6763 | 121.6337 | 10.8106 | -121.6775
1741.4688 | 121.756 | -0.21057 | 121.463 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.062675 | -0.004987 | 0.056042 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059282 | -0.06305 | 3.385 | -0.16865 | 121.558 | 121.3419 | 121.2414 | -0.15006 | -0.012689 | 10.5451 | -0.15708 | 121.2223 | 121.4337 | 121.4002 | -0.19162 | 0.060514 | 0.09495 | 0.14752 | 0.041922 | -0.018592 | -0.12115 | -0.22159 | 0.018949 | -0.24068 | 0.19788 | 0.053488 | 0.034539 | -0.029346 | -0.062774 | 121.7685 | 121.5524 | 121.452 | 3.5956 | -121.6131 | 121.4329 | 121.6442 | 121.6108 | 10.7557 | -121.6546
1743.2344 | 121.7102 | -0.22888 | 121.4951 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.062675 | -0.0054142 | 0.056042 | 0.0053411 | 0.00034614 | 0.00015807 | 0.06299 | 0.014583 | 0.059282 | -0.06305 | 3.3804 | -0.17781 | 121.558 | 121.3419 | 121.2323 | -0.15464 | -0.017267 | 10.5268 | -0.14793 | 121.2132 | 121.4428 | 121.4048 | -0.1962 | 0.074246 | 0.062907 | 0.16583 | 0.051076 | -0.02317 | -0.1532 | -0.26279 | 0.032682 | -0.28188 | 0.21161 | 0.080957 | 0.048275 | -0.052232 | -0.090238 | 121.7868 | 121.5707 | 121.4611 | 3.6093 | -121.6497 | 121.4421 | 121.6717 | 121.6337 | 10.7557 | -121.6913
1745.0156 | 121.7194 | -0.2243 | 121.4539 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.06299 | 0.014156 | 0.05971 | -0.067628 | 3.3942 | -0.17323 | 121.558 | 121.3419 | 121.2414 | -0.16379 | -0.021846 | 10.5589 | -0.1525 | 121.2086 | 121.4337 | 121.4002 | -0.19162 | 0.06051 | 0.10411 | 0.15668 | 0.051077 | -0.009433 | -0.112 | -0.21243 | 0.032682 | -0.24526 | 0.20246 | 0.0718 | 0.039118 | -0.02019 | -0.053618 | 121.7823 | 121.5662 | 121.4657 | 3.6185 | -121.6177 | 121.4329 | 121.658 | 121.6245 | 10.7832 | -121.6455
1746.7969 | 121.7834 | -0.19226 | 121.4355 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.0054142 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.014369 | 0.059282 | -0.081363 | 3.3987 | -0.16865 | 121.558 | 121.3419 | 121.2368 | -0.15464 | -0.012689 | 10.5222 | -0.15708 | 121.2178 | 121.4291 | 121.3957 | -0.20078 | 0.037625 | 0.12242 | 0.1109 | 0.023612 | -0.014013 | -0.093688 | -0.1987 | -0.008518 | -0.21779 | 0.17957 | 0.035178 | 0.043696 | -0.006459 | -0.039886 | 121.7502 | 121.5341 | 121.4291 | 3.591 | -121.5902 | 121.41 | 121.6213 | 121.5879 | 10.7145 | -121.6363
1748.5 | 121.6599 | -0.24719 | 121.4447 | 1.4211e-13 | -0.027645 | -0.0018055 | 0.062675 | -0.0052006 | 0.056469 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014583 | 0.059282 | -0.06305 | 3.4262 | -0.17323 | 121.558 | 121.3419 | 121.2414 | -0.16379 | -0.012689 | 10.5634 | -0.1525 | 121.2178 | 121.4291 | 121.3911 | -0.1962 | 0.083398 | 0.11326 | 0.18414 | 0.073965 | -0.009433 | -0.10284 | -0.20328 | 0.050992 | -0.22695 | 0.2345 | 0.094688 | 0.043696 | -0.015614 | -0.05362 | 121.8052 | 121.5891 | 121.4886 | 3.6734 | -121.6085 | 121.4649 | 121.6763 | 121.6383 | 10.8106 | -121.6409
1750.25 | 121.7422 | -0.23346 | 121.4447 | 1.4211e-13 | -0.028286 | -0.0013783 | 0.062248 | -0.0052006 | 0.056469 | -0.01755 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.059282 | -0.076785 | 3.4262 | -0.17323 | 121.558 | 121.3373 | 121.2414 | -0.16379 | -0.012689 | 10.5726 | -0.15708 | 121.2132 | 121.4245 | 121.3911 | -0.20078 | 0.069665 | 0.11326 | 0.15667 | 0.060232 | -0.009433 | -0.10742 | -0.20328 | 0.03268 | -0.23153 | 0.22077 | 0.076376 | 0.043696 | -0.020193 | -0.05362 | 121.7914 | 121.5707 | 121.4749 | 3.6597 | -121.6085 | 121.4466 | 121.658 | 121.6245 | 10.8061 | -121.6455
1752.0312 | 121.7972 | -0.17853 | 121.431 | 1.4211e-13 | -0.027859 | -0.0013783 | 0.062889 | -0.0047732 | 0.056469 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.014369 | 0.059282 | -0.076785 | 3.4262 | -0.16865 | 121.558 | 121.3419 | 121.2323 | -0.16379 | -0.021846 | 10.5405 | -0.1525 | 121.2132 | 121.4337 | 121.3957 | -0.20078 | 0.014734 | 0.12699 | 0.10174 | 0.009879 | -0.004855 | -0.08911 | -0.1987 | -0.022251 | -0.21779 | 0.15668 | 0.026024 | 0.048275 | 0.002698 | -0.035308 | 121.7365 | 121.5204 | 121.4108 | 3.6047 | -121.5948 | 121.3917 | 121.6122 | 121.5742 | 10.7191 | -121.6317
1753.75 | 121.6461 | -0.23804 | 121.4951 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.004987 | 0.056255 | 0.0053411 | 0.00013254 | -0.00026913 | 0.062776 | 0.014583 | 0.059282 | -0.076785 | 3.4399 | -0.17323 | 121.558 | 121.3373 | 121.2368 | -0.16379 | -0.017267 | 10.5085 | -0.1525 | 121.2178 | 121.4291 | 121.3957 | -0.1962 | 0.074243 | 0.062907 | 0.16125 | 0.06481 | -0.009433 | -0.15778 | -0.25821 | 0.041837 | -0.2773 | 0.22077 | 0.085533 | 0.043696 | -0.065968 | -0.099395 | 121.796 | 121.5753 | 121.4749 | 3.678 | -121.6589 | 121.4558 | 121.6671 | 121.6337 | 10.7465 | -121.6913
1755.5156 | 121.7606 | -0.21057 | 121.4355 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.062889 | -0.0054142 | 0.056683 | 0.0053411 | 0.00013254 | -0.00026913 | 0.06299 | 0.014369 | 0.059282 | -0.076785 | 3.4354 | -0.17781 | 121.558 | 121.3373 | 121.2368 | -0.15464 | -0.012689 | 10.4948 | -0.14793 | 121.2132 | 121.4245 | 121.3911 | -0.20078 | 0.055935 | 0.12242 | 0.13379 | 0.032765 | -0.02317 | -0.098267 | -0.1987 | 0.009792 | -0.22237 | 0.19788 | 0.062646 | 0.052854 | -0.011038 | -0.044465 | 121.7685 | 121.5479 | 121.4474 | 3.6459 | -121.5902 | 121.4237 | 121.6351 | 121.6017 | 10.7053 | -121.6363
1757.2969 | 121.7422 | -0.2243 | 121.431 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062675 | -0.0052006 | 0.056255 | -0.0099194 | 0.00034614 | 0.00037167 | 0.06299 | 0.014583 | 0.059282 | -0.085942 | 3.4399 | -0.17781 | 121.5534 | 121.3373 | 121.2414 | -0.15921 | -0.017267 | 10.481 | -0.15708 | 121.2178 | 121.4199 | 121.3911 | -0.20536 | 0.065089 | 0.12242 | 0.13836 | 0.046498 | -0.018591 | -0.093689 | -0.18955 | 0.018946 | -0.21321 | 0.20704 | 0.067221 | 0.048275 | -0.011038 | -0.039887 | 121.7777 | 121.5616 | 121.4657 | 3.6642 | -121.5902 | 121.4421 | 121.6442 | 121.6154 | 10.7053 | -121.6363
1759 | 121.7422 | -0.21057 | 121.4584 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062675 | -0.0052006 | 0.056469 | -0.01755 | -8.1262e-05 | -0.00026913 | 0.063203 | 0.014583 | 0.059282 | -0.081363 | 3.4399 | -0.17781 | 121.5534 | 121.3373 | 121.2368 | -0.16379 | -0.031003 | 10.4856 | -0.15708 | 121.2178 | 121.4291 | 121.3911 | -0.1962 | 0.046777 | 0.09495 | 0.12921 | 0.032765 | -0.014012 | -0.12115 | -0.22159 | 0.014371 | -0.24068 | 0.17957 | 0.053488 | 0.039117 | -0.029347 | -0.067353 | 121.764 | 121.5479 | 121.4474 | 3.6505 | -121.6222 | 121.4283 | 121.6397 | 121.6017 | 10.6962 | -121.6546
1760.7656 | 121.6553 | -0.27466 | 121.4813 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062889 | -0.0052006 | 0.056683 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014583 | 0.059069 | -0.081363 | 3.4399 | -0.17323 | 121.558 | 121.3373 | 121.2368 | -0.16837 | -0.017267 | 10.4856 | -0.15708 | 121.2178 | 121.4291 | 121.3911 | -0.1962 | 0.10629 | 0.07664 | 0.19329 | 0.10143 | -0.004854 | -0.14404 | -0.24448 | 0.078458 | -0.26357 | 0.25739 | 0.11758 | 0.039117 | -0.052235 | -0.090241 | 121.8326 | 121.6119 | 121.5115 | 3.7146 | -121.6497 | 121.4924 | 121.7037 | 121.6657 | 10.7603 | -121.6775
1762.5312 | 121.7422 | -0.2243 | 121.4447 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062675 | -0.0052006 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.014583 | 0.059069 | -0.076785 | 3.4399 | -0.17781 | 121.5534 | 121.3373 | 121.2323 | -0.16837 | -0.026425 | 10.449 | -0.15708 | 121.2132 | 121.4245 | 121.3957 | -0.20536 | 0.055931 | 0.10868 | 0.14752 | 0.046498 | -0.009433 | -0.10742 | -0.21244 | 0.018946 | -0.23153 | 0.19788 | 0.067221 | 0.048275 | -0.020193 | -0.049041 | 121.7777 | 121.5616 | 121.4566 | 3.6642 | -121.6131 | 121.4375 | 121.6488 | 121.62 | 10.6733 | -121.6501
1764.2969 | 121.7789 | -0.19684 | 121.4355 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062889 | -0.0054142 | 0.056255 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062776 | 0.014583 | 0.059282 | -0.072207 | 3.4537 | -0.17781 | 121.558 | 121.3419 | 121.2368 | -0.16379 | -0.017267 | 10.4993 | -0.1525 | 121.2086 | 121.4245 | 121.3911 | -0.20536 | 0.033044 | 0.12242 | 0.12463 | 0.019032 | -0.014012 | -0.093688 | -0.1987 | -0.00852 | -0.22695 | 0.17957 | 0.044334 | 0.052854 | -0.011038 | -0.044465 | 121.7548 | 121.5387 | 121.4337 | 3.6505 | -121.5993 | 121.4054 | 121.6213 | 121.5879 | 10.6962 | -121.6409
1766.0625 | 121.6553 | -0.27008 | 121.463 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062462 | -0.0052006 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.059496 | -0.081363 | 3.4399 | -0.17323 | 121.558 | 121.3373 | 121.2323 | -0.16837 | -0.021846 | 10.4536 | -0.15708 | 121.2132 | 121.4245 | 121.3957 | -0.20078 | 0.10171 | 0.09495 | 0.18872 | 0.096854 | -0.004854 | -0.12573 | -0.23075 | 0.069302 | -0.24984 | 0.24824 | 0.113 | 0.043696 | -0.038504 | -0.067352 | 121.828 | 121.6074 | 121.5023 | 3.71 | -121.6314 | 121.4833 | 121.6946 | 121.6657 | 10.7236 | -121.6638
1767.7812 | 121.7834 | -0.21973 | 121.4218 | 1.4211e-13 | -0.027859 | -0.0018055 | 0.062675 | -0.0052006 | 0.056683 | 0.0053411 | 0.00013254 | 0.00015807 | 0.063203 | 0.014583 | 0.059069 | -0.081363 | 3.4399 | -0.18238 | 121.5534 | 121.3327 | 121.2323 | -0.16379 | -0.026425 | 10.4398 | -0.15708 | 121.2132 | 121.4291 | 121.3911 | -0.20536 | 0.055933 | 0.13157 | 0.13836 | 0.037343 | -0.01859 | -0.089113 | -0.18955 | 0.014369 | -0.20864 | 0.1933 | 0.062644 | 0.048275 | 0.007274 | -0.030732 | 121.7731 | 121.5524 | 121.452 | 3.6597 | -121.5856 | 121.4329 | 121.6488 | 121.6108 | 10.6595 | -121.6272
1769.5312 | 121.7972 | -0.20142 | 121.4172 | 1.4211e-13 | -0.028286 | -0.0011645 | 0.062675 | -0.004987 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.059282 | -0.081363 | 3.4491 | -0.18238 | 121.5534 | 121.3419 | 121.2277 | -0.16379 | -0.026425 | 10.4627 | -0.15708 | 121.2132 | 121.4245 | 121.3911 | -0.20078 | 0.037622 | 0.13615 | 0.12005 | 0.019032 | -0.01859 | -0.075377 | -0.18955 | 0.000637 | -0.20406 | 0.17499 | 0.044333 | 0.043696 | 0.007273 | -0.026154 | 121.7548 | 121.5433 | 121.4291 | 3.6505 | -121.581 | 121.4146 | 121.6259 | 121.5925 | 10.6641 | -121.618
1771.3125 | 121.7148 | -0.23346 | 121.4355 | 1.4211e-13 | -0.028286 | -0.0013783 | 0.063103 | -0.0054142 | 0.056469 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.014797 | 0.059282 | -0.085942 | 3.4445 | -0.17781 | 121.5488 | 121.3464 | 121.2414 | -0.15921 | -0.031003 | 10.4536 | -0.15708 | 121.2086 | 121.4245 | 121.3911 | -0.20078 | 0.074244 | 0.11326 | 0.14752 | 0.055653 | -0.018591 | -0.089109 | -0.19412 | 0.03268 | -0.22695 | 0.20246 | 0.076376 | 0.043696 | -0.011038 | -0.044465 | 121.7823 | 121.5799 | 121.4749 | 3.678 | -121.5948 | 121.4421 | 121.658 | 121.6245 | 10.687 | -121.6363
1773.0938 | 121.7697 | -0.20599 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062675 | -0.004987 | 0.056469 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.014583 | 0.059282 | -0.085942 | 3.4445 | -0.16407 | 121.5534 | 121.3464 | 121.2323 | -0.16837 | -0.017267 | 10.4581 | -0.16166 | 121.2223 | 121.4291 | 121.3911 | -0.20536 | 0.037621 | 0.11326 | 0.12005 | 0.041923 | 0.004302 | -0.093687 | -0.20786 | 0.000636 | -0.21779 | 0.18873 | 0.044333 | 0.043697 | -0.011037 | -0.049043 | 121.7594 | 121.5524 | 121.4383 | 3.6505 | -121.6085 | 121.4283 | 121.6351 | 121.5971 | 10.6641 | -121.6455
1774.875 | 121.7056 | -0.24261 | 121.4676 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.062675 | -0.0052006 | 0.056683 | 0.0053411 | -0.00029486 | -0.00026913 | 0.06299 | 0.014583 | 0.05971 | -0.081363 | 3.4445 | -0.17781 | 121.558 | 121.3373 | 121.2323 | -0.17295 | -0.026425 | 10.4398 | -0.1525 | 121.2132 | 121.4291 | 121.3957 | -0.20078 | 0.069664 | 0.090373 | 0.16125 | 0.064809 | -0.004855 | -0.13031 | -0.23532 | 0.041836 | -0.25441 | 0.21619 | 0.090111 | 0.048275 | -0.038502 | -0.071929 | 121.8006 | 121.5799 | 121.4749 | 3.6871 | -121.6405 | 121.4558 | 121.6717 | 121.6383 | 10.6824 | -121.6684
1776.5625 | 121.6599 | -0.27008 | 121.4859 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062889 | -0.004987 | 0.056255 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.014797 | 0.059282 | -0.081363 | 3.4308 | -0.17323 | 121.5534 | 121.3373 | 121.2277 | -0.16379 | -0.026425 | 10.4215 | -0.16166 | 121.2132 | 121.4245 | 121.3911 | -0.20536 | 0.10629 | 0.067484 | 0.18872 | 0.096854 | -0.009433 | -0.14862 | -0.25821 | 0.064723 | -0.27272 | 0.24366 | 0.10842 | 0.043697 | -0.061392 | -0.094819 | 121.8235 | 121.6074 | 121.4978 | 3.7009 | -121.6497 | 121.4833 | 121.6946 | 121.6612 | 10.6916 | -121.6913
1778.3438 | 121.6553 | -0.26093 | 121.4996 | 1.4211e-13 | -0.027859 | -0.0015919 | 0.062889 | -0.0054142 | 0.056683 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014797 | 0.059069 | -0.081363 | 3.4399 | -0.17781 | 121.5534 | 121.3419 | 121.2414 | -0.15921 | -0.021846 | 10.4581 | -0.16166 | 121.2132 | 121.4291 | 121.4048 | -0.20078 | 0.10171 | 0.053751 | 0.17956 | 0.083119 | -0.018591 | -0.15778 | -0.25821 | 0.060146 | -0.28646 | 0.23908 | 0.099264 | 0.039118 | -0.070546 | -0.094816 | 121.8143 | 121.6028 | 121.5023 | 3.7009 | -121.6588 | 121.4741 | 121.69 | 121.6657 | 10.7191 | -121.7004
1780.0625 | 121.6827 | -0.2655 | 121.4676 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062675 | -0.0052006 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014583 | 0.059282 | -0.076785 | 3.4445 | -0.18696 | 121.5488 | 121.3327 | 121.2323 | -0.16379 | -0.021846 | 10.4444 | -0.1525 | 121.2086 | 121.4291 | 121.4002 | -0.20078 | 0.10171 | 0.081216 | 0.18872 | 0.078541 | -0.023168 | -0.13489 | -0.23532 | 0.064724 | -0.25899 | 0.24366 | 0.113 | 0.048275 | -0.038502 | -0.067351 | 121.8143 | 121.5982 | 121.4978 | 3.71 | -121.6314 | 121.4741 | 121.6946 | 121.6657 | 10.7099 | -121.6684
1781.8438 | 121.756 | -0.2243 | 121.4447 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062675 | -0.0054142 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014797 | 0.059282 | -0.076785 | 3.4583 | -0.17781 | 121.5534 | 121.3373 | 121.2323 | -0.16837 | -0.026425 | 10.4307 | -0.15708 | 121.2178 | 121.4199 | 121.3911 | -0.20536 | 0.055931 | 0.10868 | 0.14752 | 0.046498 | -0.009433 | -0.10742 | -0.21244 | 0.018946 | -0.22695 | 0.19788 | 0.067221 | 0.048275 | -0.024771 | -0.05362 | 121.7777 | 121.5616 | 121.4566 | 3.6826 | -121.6131 | 121.4421 | 121.6442 | 121.6154 | 10.655 | -121.6501
1783.6094 | 121.7651 | -0.2243 | 121.431 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.062776 | 0.01501 | 0.059069 | -0.081363 | 3.4628 | -0.18238 | 121.558 | 121.3327 | 121.2414 | -0.16379 | -0.021846 | 10.3666 | -0.16166 | 121.2132 | 121.4337 | 121.3911 | -0.20078 | 0.06051 | 0.12699 | 0.14294 | 0.04192 | -0.01859 | -0.098268 | -0.18955 | 0.023525 | -0.21779 | 0.20246 | 0.062643 | 0.039118 | 0.002698 | -0.039887 | 121.7823 | 121.557 | 121.4657 | 3.6871 | -121.5948 | 121.4375 | 121.658 | 121.6154 | 10.5909 | -121.6317
1785.375 | 121.7102 | -0.22888 | 121.4355 | 1.4211e-13 | -0.028286 | -0.0013783 | 0.062675 | -0.0054142 | 0.056469 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.014583 | 0.059496 | -0.09052 | 3.4674 | -0.17781 | 121.5534 | 121.3419 | 121.2323 | -0.16837 | -0.021846 | 10.4444 | -0.15708 | 121.2132 | 121.4291 | 121.3865 | -0.20536 | 0.060509 | 0.11784 | 0.13836 | 0.051076 | -0.009433 | -0.093688 | -0.20328 | 0.023524 | -0.22237 | 0.20704 | 0.071799 | 0.048275 | -0.006459 | -0.049044 | 121.7823 | 121.5707 | 121.4611 | 3.6963 | -121.6039 | 121.4421 | 121.658 | 121.6154 | 10.6733 | -121.6409
1787.0781 | 121.6507 | -0.27008 | 121.4539 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062675 | -0.0052006 | 0.056255 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014369 | 0.059282 | -0.085942 | 3.4537 | -0.18696 | 121.5488 | 121.3327 | 121.2368 | -0.17295 | -0.026425 | 10.4398 | -0.16624 | 121.2086 | 121.4199 | 121.4002 | -0.20078 | 0.09713 | 0.094949 | 0.18414 | 0.083119 | -0.014011 | -0.12116 | -0.21701 | 0.069302 | -0.24526 | 0.24366 | 0.10384 | 0.034539 | -0.033926 | -0.053618 | 121.8189 | 121.6028 | 121.5069 | 3.7238 | -121.6268 | 121.4787 | 121.69 | 121.6703 | 10.7099 | -121.6546
1788.8594 | 121.7239 | -0.21515 | 121.4447 | 1.4211e-13 | -0.0285 | -0.0018055 | 0.062675 | -0.004987 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.014797 | 0.059282 | -0.085942 | 3.4491 | -0.19154 | 121.5442 | 121.3373 | 121.2368 | -0.16837 | -0.021846 | 10.4261 | -0.17082 | 121.2132 | 121.4245 | 121.3865 | -0.20536 | 0.046776 | 0.099526 | 0.12921 | 0.023608 | -0.023168 | -0.10742 | -0.20786 | 0.009791 | -0.23153 | 0.1933 | 0.04433 | 0.034539 | -0.020193 | -0.058199 | 121.7594 | 121.5524 | 121.452 | 3.6642 | -121.6131 | 121.4283 | 121.6397 | 121.6017 | 10.6412 | -121.6501
1790.625 | 121.788 | -0.20142 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0013783 | 0.062889 | -0.004987 | 0.056255 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062776 | 0.014797 | 0.058855 | -0.076785 | 3.4674 | -0.18696 | 121.5442 | 121.3373 | 121.2368 | -0.17295 | -0.026425 | 10.4032 | -0.16624 | 121.2086 | 121.4199 | 121.3865 | -0.20994 | 0.028465 | 0.1041 | 0.12463 | 0.014454 | -0.014011 | -0.10284 | -0.20328 | -0.008521 | -0.23153 | 0.17499 | 0.035176 | 0.043697 | -0.020194 | -0.053622 | 121.7456 | 121.5387 | 121.4383 | 3.6688 | -121.6131 | 121.41 | 121.6213 | 121.5879 | 10.6046 | -121.6501
1792.3906 | 121.7606 | -0.21973 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062675 | -0.0052006 | 0.056469 | 0.0053411 | 0.00013254 | 0.00015807 | 0.06299 | 0.014583 | 0.059496 | -0.085942 | 3.472 | -0.18238 | 121.5534 | 121.3373 | 121.2414 | -0.16837 | -0.026425 | 10.394 | -0.16166 | 121.2132 | 121.4199 | 121.3865 | -0.20994 | 0.051354 | 0.11326 | 0.13378 | 0.037343 | -0.014011 | -0.10284 | -0.1987 | 0.00979 | -0.22695 | 0.1933 | 0.058066 | 0.048276 | -0.020194 | -0.053622 | 121.7731 | 121.557 | 121.4612 | 3.6917 | -121.6085 | 121.4329 | 121.6397 | 121.6062 | 10.6138 | -121.6501
1794.0938 | 121.6873 | -0.24261 | 121.4493 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062462 | -0.004987 | 0.056469 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.014583 | 0.059282 | -0.099677 | 3.472 | -0.20528 | 121.5305 | 121.319 | 121.214 | -0.19127 | -0.044739 | 10.3666 | -0.17998 | 121.1949 | 121.4108 | 121.3682 | -0.22367 | 0.051348 | 0.081213 | 0.14294 | 0.03734 | -0.014008 | -0.13031 | -0.23533 | 0.018942 | -0.25442 | 0.19788 | 0.062639 | 0.043697 | -0.038506 | -0.081091 | 121.7731 | 121.5616 | 121.4566 | 3.7146 | -121.6405 | 121.4375 | 121.6534 | 121.6108 | 10.6092 | -121.673
1795.875 | 121.7651 | -0.23346 | 121.4035 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062889 | -0.004987 | 0.056469 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.01501 | 0.059069 | -0.095099 | 3.4857 | -0.19154 | 121.5396 | 121.3235 | 121.2231 | -0.18669 | -0.035582 | 10.3574 | -0.16624 | 121.1949 | 121.4108 | 121.3773 | -0.2191 | 0.046771 | 0.13615 | 0.13836 | 0.041918 | -0.004853 | -0.079959 | -0.18039 | 0.014364 | -0.20864 | 0.19788 | 0.067219 | 0.052855 | 0.007271 | -0.026157 | 121.7731 | 121.557 | 121.4566 | 3.7192 | -121.5902 | 121.4283 | 121.6442 | 121.6108 | 10.5909 | -121.6226
1797.6562 | 121.6919 | -0.24261 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.0052006 | 0.056042 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.014797 | 0.059496 | -0.099677 | 3.4903 | -0.19154 | 121.5396 | 121.319 | 121.2277 | -0.19127 | -0.040161 | 10.3849 | -0.17998 | 121.1994 | 121.4154 | 121.3819 | -0.22367 | 0.051348 | 0.099525 | 0.14294 | 0.051074 | -0.000274 | -0.12116 | -0.21244 | 0.018942 | -0.24068 | 0.20245 | 0.062639 | 0.043697 | -0.024773 | -0.0582 | 121.7823 | 121.5616 | 121.4703 | 3.7329 | -121.6314 | 121.4421 | 121.658 | 121.6245 | 10.6275 | -121.6638
1799.3594 | 121.6827 | -0.26093 | 121.4401 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062462 | -0.0054142 | 0.056469 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.063417 | 0.014583 | 0.059282 | -0.09052 | 3.4903 | -0.19612 | 121.5442 | 121.3327 | 121.2277 | -0.18211 | -0.040161 | 10.3711 | -0.1754 | 121.1994 | 121.4199 | 121.3773 | -0.21452 | 0.078816 | 0.1041 | 0.17041 | 0.064806 | -0.01401 | -0.10742 | -0.21244 | 0.046409 | -0.24068 | 0.22076 | 0.085527 | 0.039118 | -0.020194 | -0.062779 | 121.8052 | 121.5936 | 121.4886 | 3.7512 | -121.6222 | 121.4604 | 121.6809 | 121.6383 | 10.6321 | -121.6546
1801.125 | 121.7422 | -0.23804 | 121.4264 | 1.4211e-13 | -0.028286 | -0.0013783 | 0.062675 | -0.0052006 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062776 | 0.014797 | 0.059069 | -0.099677 | 3.4857 | -0.18696 | 121.5351 | 121.3281 | 121.2277 | -0.18211 | -0.040161 | 10.3895 | -0.1754 | 121.1949 | 121.4199 | 121.3728 | -0.21452 | 0.055928 | 0.10868 | 0.13836 | 0.051075 | -0.004853 | -0.098269 | -0.1987 | 0.023521 | -0.23153 | 0.19788 | 0.062639 | 0.039118 | -0.006461 | -0.053624 | 121.7731 | 121.5662 | 121.4657 | 3.7238 | -121.6085 | 121.4329 | 121.658 | 121.6108 | 10.6275 | -121.6409
1802.8906 | 121.7926 | -0.21973 | 121.4081 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.0052006 | 0.056683 | -0.0022889 | 0.00055974 | -5.5534e-05 | 0.06299 | 0.01501 | 0.059069 | -0.09052 | 3.4766 | -0.19612 | 121.5396 | 121.319 | 121.2231 | -0.18211 | -0.040161 | 10.4398 | -0.1754 | 121.204 | 121.4199 | 121.3728 | -0.22367 | 0.037618 | 0.13157 | 0.12921 | 0.023608 | -0.01401 | -0.089116 | -0.18497 | -0.003946 | -0.20406 | 0.17957 | 0.044329 | 0.048275 | 0.01185 | -0.035313 | 121.7594 | 121.5387 | 121.4428 | 3.6963 | -121.5902 | 121.4237 | 121.6397 | 121.5925 | 10.6595 | -121.6318
1804.6562 | 121.7514 | -0.24261 | 121.4127 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062889 | -0.0054142 | 0.056255 | 0.0053411 | 0.00013254 | 0.00015807 | 0.06299 | 0.01501 | 0.059069 | -0.095099 | 3.4811 | -0.19612 | 121.5442 | 121.3281 | 121.2323 | -0.17753 | -0.035582 | 10.3849 | -0.17082 | 121.1903 | 121.4154 | 121.3865 | -0.2191 | 0.065085 | 0.13157 | 0.14752 | 0.046496 | -0.018589 | -0.084536 | -0.18039 | 0.02352 | -0.22237 | 0.20703 | 0.071796 | 0.048276 | 0.002693 | -0.026156 | 121.7868 | 121.5707 | 121.4749 | 3.7238 | -121.5902 | 121.4329 | 121.658 | 121.6291 | 10.6275 | -121.6318
1806.3594 | 121.7972 | -0.2243 | 121.3852 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062889 | -0.0054142 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.058855 | -0.09052 | 3.472 | -0.19612 | 121.5351 | 121.3235 | 121.2323 | -0.17753 | -0.035582 | 10.3666 | -0.17082 | 121.1994 | 121.4199 | 121.3728 | -0.2191 | 0.046774 | 0.14988 | 0.13378 | 0.028185 | -0.018589 | -0.061649 | -0.15293 | 0.005209 | -0.18575 | 0.18872 | 0.053485 | 0.048276 | 0.034738 | -0.012425 | 121.7594 | 121.5478 | 121.4566 | 3.6963 | -121.5627 | 121.4237 | 121.6442 | 121.5971 | 10.5909 | -121.6043
1808.1094 | 121.7239 | -0.23346 | 121.4355 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.063103 | -0.0054142 | 0.056469 | 0.012972 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.014797 | 0.059496 | -0.09052 | 3.4674 | -0.2007 | 121.5442 | 121.319 | 121.2323 | -0.17753 | -0.040161 | 10.3803 | -0.17082 | 121.204 | 121.4154 | 121.3773 | -0.2191 | 0.055929 | 0.10868 | 0.14294 | 0.032762 | -0.023167 | -0.11658 | -0.20328 | 0.014364 | -0.23153 | 0.1933 | 0.06264 | 0.048276 | -0.020195 | -0.058201 | 121.7777 | 121.5524 | 121.4657 | 3.7009 | -121.6131 | 121.4375 | 121.6488 | 121.6108 | 10.6138 | -121.6546
1809.8906 | 121.7239 | -0.25635 | 121.4539 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062675 | -0.0054142 | 0.056469 | 0.012972 | 0.00034614 | -0.00026913 | 0.06299 | 0.01501 | 0.059496 | -0.09052 | 3.4674 | -0.19154 | 121.5488 | 121.3327 | 121.2277 | -0.18211 | -0.044739 | 10.4169 | -0.17082 | 121.204 | 121.4154 | 121.3819 | -0.22367 | 0.074239 | 0.094949 | 0.16583 | 0.064807 | -0.009432 | -0.12116 | -0.22617 | 0.032675 | -0.24984 | 0.21161 | 0.085529 | 0.052854 | -0.038505 | -0.071932 | 121.8052 | 121.589 | 121.484 | 3.7238 | -121.636 | 121.4604 | 121.6717 | 121.6383 | 10.6733 | -121.6775
1811.5938 | 121.7926 | -0.22888 | 121.4401 | 1.4211e-13 | -0.0285 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.01501 | 0.058855 | -0.095099 | 3.4628 | -0.19612 | 121.5442 | 121.319 | 121.2231 | -0.18669 | -0.040161 | 10.3574 | -0.1754 | 121.204 | 121.4245 | 121.3728 | -0.2191 | 0.042194 | 0.1041 | 0.13378 | 0.032763 | -0.009431 | -0.12116 | -0.21701 | 0.009787 | -0.2361 | 0.18872 | 0.053484 | 0.043697 | -0.015616 | -0.067357 | 121.7731 | 121.5478 | 121.452 | 3.6917 | -121.6268 | 121.4329 | 121.6534 | 121.6016 | 10.5863 | -121.6592
1813.3594 | 121.7834 | -0.21973 | 121.3989 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | 0.00055974 | -5.5534e-05 | 0.063203 | 0.014583 | 0.058855 | -0.09052 | 3.472 | -0.19612 | 121.5396 | 121.3235 | 121.2277 | -0.17753 | -0.026425 | 10.3757 | -0.17082 | 121.1994 | 121.4245 | 121.3865 | -0.2191 | 0.042197 | 0.14072 | 0.12921 | 0.023608 | -0.018589 | -0.075382 | -0.17124 | 0.000632 | -0.19949 | 0.1933 | 0.048908 | 0.048276 | 0.025583 | -0.012423 | 121.7594 | 121.5433 | 121.4474 | 3.6917 | -121.5765 | 121.4192 | 121.6442 | 121.6062 | 10.5954 | -121.618
1815.125 | 121.7651 | -0.23346 | 121.4172 | 1.4211e-13 | -0.028072 | -0.0015919 | 0.062675 | -0.0052006 | 0.056042 | 0.0053411 | 0.00013254 | 0.00015807 | 0.06299 | 0.014797 | 0.059069 | -0.095099 | 3.4628 | -0.2007 | 121.5351 | 121.3281 | 121.2323 | -0.18669 | -0.040161 | 10.3803 | -0.1754 | 121.1994 | 121.4199 | 121.3773 | -0.22367 | 0.046771 | 0.11783 | 0.13836 | 0.032762 | -0.014009 | -0.089113 | -0.18497 | 0.009786 | -0.2178 | 0.1933 | 0.058061 | 0.048275 | 0.002695 | -0.03989 | 121.7685 | 121.5616 | 121.4657 | 3.6963 | -121.6039 | 121.4329 | 121.6534 | 121.6108 | 10.6138 | -121.6409
1816.8906 | 121.7606 | -0.2243 | 121.4401 | 1.4211e-13 | -0.0285 | -0.0013783 | 0.062675 | -0.0052006 | 0.056469 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.015224 | 0.059069 | -0.099677 | 3.4857 | -0.19612 | 121.5396 | 121.3235 | 121.2277 | -0.18211 | -0.044739 | 10.394 | -0.1754 | 121.204 | 121.4199 | 121.3819 | -0.2191 | 0.042195 | 0.099525 | 0.12463 | 0.028185 | -0.01401 | -0.11658 | -0.21244 | 0.005209 | -0.2361 | 0.17957 | 0.048906 | 0.043697 | -0.020194 | -0.0582 | 121.764 | 121.5478 | 121.452 | 3.71 | -121.6222 | 121.4283 | 121.6442 | 121.6062 | 10.6183 | -121.6592
1818.5938 | 121.7834 | -0.22888 | 121.4218 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062889 | -0.0054142 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.014583 | 0.058855 | -0.095099 | 3.472 | -0.2007 | 121.5351 | 121.3281 | 121.2231 | -0.19127 | -0.035582 | 10.4123 | -0.17082 | 121.1994 | 121.4199 | 121.3773 | -0.22367 | 0.037615 | 0.11326 | 0.13378 | 0.028185 | -0.00943 | -0.093691 | -0.1987 | 0.005209 | -0.22237 | 0.1933 | 0.058063 | 0.052854 | -0.001883 | -0.044468 | 121.764 | 121.557 | 121.452 | 3.7009 | -121.6131 | 121.4283 | 121.6488 | 121.6062 | 10.6412 | -121.6455
1820.3594 | 121.7377 | -0.25177 | 121.431 | 1.4211e-13 | -0.028286 | -0.0020193 | 0.062462 | -0.0052006 | 0.056255 | -0.0022889 | 0.00013254 | -0.00026913 | 0.06299 | 0.01501 | 0.059069 | -0.099677 | 3.4811 | -0.19612 | 121.5396 | 121.3281 | 121.2231 | -0.18669 | -0.044739 | 10.3162 | -0.17998 | 121.1949 | 121.4199 | 121.3728 | -0.2191 | 0.065082 | 0.10868 | 0.15209 | 0.055651 | -0.009431 | -0.10285 | -0.20786 | 0.032675 | -0.23611 | 0.20703 | 0.071794 | 0.039119 | -0.011038 | -0.058201 | 121.7914 | 121.5799 | 121.4749 | 3.7329 | -121.6177 | 121.4466 | 121.6717 | 121.6245 | 10.568 | -121.6501
1822.0625 | 121.7285 | -0.25635 | 121.4493 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.063103 | -0.005628 | 0.056042 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.063203 | 0.01501 | 0.058855 | -0.095099 | 3.4674 | -0.19154 | 121.5396 | 121.3281 | 121.2368 | -0.17753 | -0.035582 | 10.3025 | -0.16624 | 121.1994 | 121.4154 | 121.3682 | -0.2191 | 0.078818 | 0.09037 | 0.16125 | 0.064807 | -0.014011 | -0.12116 | -0.21243 | 0.037253 | -0.24984 | 0.22077 | 0.090108 | 0.052855 | -0.033928 | -0.081091 | 121.796 | 121.5845 | 121.4932 | 3.7238 | -121.6268 | 121.4558 | 121.6717 | 121.6245 | 10.5588 | -121.6684
1823.8438 | 121.7972 | -0.23346 | 121.3989 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062675 | -0.0054142 | 0.056469 | 0.0053411 | 0.00034614 | 0.00037167 | 0.063203 | 0.01501 | 0.058855 | -0.095099 | 3.5086 | -0.19612 | 121.5442 | 121.3235 | 121.2231 | -0.17753 | -0.040161 | 10.3254 | -0.1754 | 121.204 | 121.4154 | 121.3773 | -0.22367 | 0.055929 | 0.1453 | 0.13836 | 0.03734 | -0.018589 | -0.075382 | -0.17582 | 0.009786 | -0.19491 | 0.1933 | 0.058061 | 0.048275 | 0.016426 | -0.02158 | 121.7777 | 121.557 | 121.4566 | 3.7421 | -121.5765 | 121.4375 | 121.6488 | 121.6108 | 10.5588 | -121.6226
1825.5469 | 121.7697 | -0.22888 | 121.4264 | 1.4211e-13 | -0.028286 | -0.0013783 | 0.062889 | -0.005628 | 0.056042 | -0.0022889 | 0.00013254 | -0.00026913 | 0.06299 | 0.014797 | 0.058855 | -0.095099 | 3.5178 | -0.2007 | 121.5351 | 121.3235 | 121.2277 | -0.18211 | -0.044739 | 10.2841 | -0.17082 | 121.1949 | 121.4062 | 121.3819 | -0.2191 | 0.046773 | 0.10868 | 0.13378 | 0.028185 | -0.018588 | -0.10285 | -0.1987 | 0.009787 | -0.23153 | 0.18414 | 0.058063 | 0.048276 | -0.020197 | -0.044467 | 121.764 | 121.5524 | 121.4566 | 3.7467 | -121.6085 | 121.4237 | 121.6351 | 121.6108 | 10.513 | -121.6455
1827.3125 | 121.6919 | -0.26093 | 121.4401 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062889 | -0.0052006 | 0.056255 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.015224 | 0.058855 | -0.099677 | 3.5178 | -0.19612 | 121.5442 | 121.3281 | 121.2277 | -0.19127 | -0.044739 | 10.3299 | -0.1754 | 121.1903 | 121.4154 | 121.3773 | -0.2191 | 0.069658 | 0.1041 | 0.16125 | 0.064806 | -0.004852 | -0.112 | -0.21244 | 0.04183 | -0.24984 | 0.21619 | 0.085527 | 0.043697 | -0.024773 | -0.062779 | 121.8052 | 121.589 | 121.4886 | 3.7787 | -121.6314 | 121.4512 | 121.6763 | 121.6383 | 10.5909 | -121.6592
1829.0938 | 121.7468 | -0.23346 | 121.4264 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062675 | -0.004987 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.014583 | 0.058641 | -0.099677 | 3.5132 | -0.2007 | 121.5396 | 121.3235 | 121.2231 | -0.19127 | -0.040161 | 10.2704 | -0.1754 | 121.204 | 121.4154 | 121.3728 | -0.22367 | 0.042192 | 0.11326 | 0.13378 | 0.032762 | -0.00943 | -0.10285 | -0.20328 | 0.009786 | -0.22237 | 0.1933 | 0.058061 | 0.048275 | -0.01104 | -0.053624 | 121.7731 | 121.557 | 121.4566 | 3.7467 | -121.6177 | 121.4375 | 121.6488 | 121.6062 | 10.5039 | -121.6501
1830.8594 | 121.8063 | -0.23346 | 121.3898 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062889 | -0.0052006 | 0.056255 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014583 | 0.058855 | -0.099677 | 3.5224 | -0.2007 | 121.5396 | 121.319 | 121.2231 | -0.18669 | -0.040161 | 10.2475 | -0.17998 | 121.1903 | 121.4062 | 121.3728 | -0.22825 | 0.046771 | 0.14988 | 0.13378 | 0.032762 | -0.014009 | -0.070806 | -0.16666 | 0.005207 | -0.19949 | 0.1933 | 0.053483 | 0.048276 | 0.016424 | -0.017003 | 121.7731 | 121.5524 | 121.4566 | 3.7558 | -121.5765 | 121.4237 | 121.6397 | 121.6062 | 10.481 | -121.618
1832.5625 | 121.6782 | -0.27924 | 121.4447 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0054142 | 0.056683 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.014797 | 0.058641 | -0.10883 | 3.5315 | -0.20528 | 121.5396 | 121.3235 | 121.2231 | -0.18669 | -0.040161 | 10.3162 | -0.1754 | 121.1949 | 121.4108 | 121.3728 | -0.22825 | 0.092548 | 0.094948 | 0.1704 | 0.073961 | -0.018587 | -0.12116 | -0.22159 | 0.050984 | -0.24984 | 0.23907 | 0.10384 | 0.052854 | -0.033928 | -0.071934 | 121.8189 | 121.6028 | 121.5023 | 3.8107 | -121.6314 | 121.4741 | 121.69 | 121.652 | 10.5954 | -121.673
1834.3281 | 121.8018 | -0.23346 | 121.4081 | 1.4211e-13 | -0.028286 | -0.0020193 | 0.062675 | -0.0054142 | 0.056042 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062776 | 0.014797 | 0.059069 | -0.095099 | 3.5361 | -0.2007 | 121.5351 | 121.3281 | 121.2231 | -0.18669 | -0.049318 | 10.2292 | -0.17998 | 121.204 | 121.4108 | 121.3728 | -0.22367 | 0.046771 | 0.12699 | 0.13836 | 0.032762 | -0.014009 | -0.079958 | -0.18497 | 0.009786 | -0.20406 | 0.18414 | 0.053483 | 0.043697 | 0.002693 | -0.035313 | 121.7685 | 121.5616 | 121.4566 | 3.7695 | -121.5948 | 121.4375 | 121.6442 | 121.6062 | 10.4627 | -121.6318
1836.0938 | 121.7056 | -0.26093 | 121.4264 | 1.4211e-13 | -0.028072 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.06299 | 0.015224 | 0.058641 | -0.095099 | 3.5452 | -0.20528 | 121.5351 | 121.319 | 121.2277 | -0.19585 | -0.044739 | 10.2429 | -0.1754 | 121.1903 | 121.4154 | 121.3728 | -0.23283 | 0.065079 | 0.10868 | 0.16583 | 0.05565 | -0.009429 | -0.10743 | -0.1987 | 0.028094 | -0.23611 | 0.21619 | 0.085527 | 0.057433 | -0.01104 | -0.053624 | 121.796 | 121.5799 | 121.4886 | 3.8062 | -121.6222 | 121.4512 | 121.6763 | 121.6337 | 10.5039 | -121.6592
1837.8125 | 121.7056 | -0.27008 | 121.4264 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062462 | -0.0054142 | 0.056469 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.014797 | 0.058855 | -0.11341 | 3.5452 | -0.2007 | 121.5351 | 121.319 | 121.2277 | -0.19585 | -0.049318 | 10.2384 | -0.17998 | 121.1857 | 121.4154 | 121.3773 | -0.23741 | 0.074235 | 0.10868 | 0.15667 | 0.069384 | -0.004851 | -0.10743 | -0.1987 | 0.032671 | -0.24069 | 0.22076 | 0.090105 | 0.057434 | -0.01104 | -0.049046 | 121.8052 | 121.589 | 121.4978 | 3.8153 | -121.6222 | 121.4558 | 121.6854 | 121.6474 | 10.5084 | -121.6638
1839.5312 | 121.788 | -0.23346 | 121.3943 | 1.4211e-13 | -0.0285 | -0.0018055 | 0.062675 | -0.0054142 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.015438 | 0.058428 | -0.10883 | 3.5544 | -0.2007 | 121.5351 | 121.319 | 121.2277 | -0.19127 | -0.044739 | 10.2338 | -0.17998 | 121.1949 | 121.4108 | 121.3728 | -0.23283 | 0.042192 | 0.14072 | 0.12462 | 0.032762 | -0.00943 | -0.075383 | -0.16666 | 0.000628 | -0.19948 | 0.18872 | 0.053483 | 0.052855 | 0.016426 | -0.02158 | 121.7685 | 121.5524 | 121.4611 | 3.7879 | -121.5856 | 121.4283 | 121.6442 | 121.6062 | 10.4672 | -121.6272
1841.2969 | 121.701 | -0.30212 | 121.4081 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062675 | -0.0052006 | 0.056255 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.014583 | 0.058428 | -0.10426 | 3.5361 | -0.20528 | 121.5351 | 121.319 | 121.2277 | -0.19585 | -0.044739 | 10.2567 | -0.17998 | 121.1903 | 121.4062 | 121.3636 | -0.22825 | 0.10628 | 0.12699 | 0.19787 | 0.096849 | -0.009429 | -0.089116 | -0.18039 | 0.073872 | -0.2178 | 0.25738 | 0.12215 | 0.048276 | -0.001886 | -0.044471 | 121.8372 | 121.6211 | 121.5298 | 3.8382 | -121.6039 | 121.4924 | 121.7083 | 121.6657 | 10.5588 | -121.6363
1843.0625 | 121.7468 | -0.23804 | 121.3989 | 1.4211e-13 | -0.028286 | -0.0018055 | 0.062675 | -0.0052006 | 0.056042 | 0.0053411 | -0.00029486 | 0.00015807 | 0.06299 | 0.015224 | 0.058855 | -0.10883 | 3.5132 | -0.20985 | 121.5259 | 121.3144 | 121.2185 | -0.19585 | -0.049318 | 10.2429 | -0.18455 | 121.1903 | 121.4108 | 121.3682 | -0.23283 | 0.042191 | 0.12699 | 0.1292 | 0.028183 | -0.014008 | -0.08454 | -0.1804 | 0.005206 | -0.20864 | 0.18872 | 0.053482 | 0.048276 | 0.011848 | -0.030737 | 121.764 | 121.5524 | 121.4566 | 3.7512 | -121.5948 | 121.4283 | 121.6488 | 121.6062 | 10.481 | -121.6318
1844.8438 | 121.7834 | -0.25177 | 121.4218 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.063103 | -0.0054142 | 0.056042 | -0.0022889 | 0.00055974 | -0.00026913 | 0.06299 | 0.014583 | 0.058855 | -0.10426 | 3.5178 | -0.20528 | 121.5305 | 121.319 | 121.2185 | -0.19127 | -0.044739 | 10.2384 | -0.18913 | 121.1903 | 121.4108 | 121.3636 | -0.22825 | 0.060503 | 0.10868 | 0.14752 | 0.046495 | -0.014008 | -0.10285 | -0.20328 | 0.023518 | -0.23153 | 0.20703 | 0.062636 | 0.039118 | -0.01104 | -0.058204 | 121.7823 | 121.5707 | 121.4703 | 3.7695 | -121.6131 | 121.4421 | 121.6625 | 121.6154 | 10.4901 | -121.6501
1846.5469 | 121.7926 | -0.24719 | 121.4127 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062675 | -0.0054142 | 0.056042 | 0.0053411 | -0.00050846 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058855 | -0.11341 | 3.5178 | -0.21443 | 121.5259 | 121.319 | 121.2231 | -0.19127 | -0.049318 | 10.1788 | -0.18455 | 121.1903 | 121.4108 | 121.3636 | -0.23741 | 0.055925 | 0.11325 | 0.13378 | 0.03276 | -0.023165 | -0.093694 | -0.18955 | 0.009782 | -0.22237 | 0.19787 | 0.062637 | 0.052855 | -0.001885 | -0.049049 | 121.7731 | 121.5662 | 121.4703 | 3.765 | -121.6039 | 121.4375 | 121.658 | 121.6108 | 10.426 | -121.6501
1848.3125 | 121.6461 | -0.28381 | 121.4218 | 1.4211e-13 | -0.0285 | -0.0018055 | 0.062675 | -0.0054142 | 0.056255 | 0.012972 | -8.1262e-05 | 0.00015807 | 0.063203 | 0.014797 | 0.058641 | -0.10883 | 3.5132 | -0.20985 | 121.5396 | 121.319 | 121.2231 | -0.19585 | -0.049318 | 10.1926 | -0.17998 | 121.1765 | 121.4062 | 121.3636 | -0.23741 | 0.087967 | 0.11784 | 0.17498 | 0.073959 | -0.014008 | -0.10285 | -0.1987 | 0.046403 | -0.24527 | 0.23449 | 0.10384 | 0.057434 | -0.015619 | -0.058204 | 121.8235 | 121.6028 | 121.5069 | 3.797 | -121.6177 | 121.4604 | 121.69 | 121.6474 | 10.4764 | -121.6592
1850.0469 | 121.6415 | -0.29755 | 121.4264 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062889 | -0.0054142 | 0.056042 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.063203 | 0.01501 | 0.059282 | -0.10883 | 3.5086 | -0.20985 | 121.5259 | 121.3144 | 121.214 | -0.19127 | -0.053897 | 10.1834 | -0.17998 | 121.1903 | 121.4108 | 121.3636 | -0.23741 | 0.10628 | 0.099522 | 0.18871 | 0.087692 | -0.018587 | -0.11201 | -0.21244 | 0.060136 | -0.23611 | 0.24365 | 0.11757 | 0.057434 | -0.015618 | -0.062782 | 121.8235 | 121.6119 | 121.5115 | 3.8062 | -121.6177 | 121.4878 | 121.7083 | 121.6612 | 10.481 | -121.6638
1851.8281 | 121.7056 | -0.28381 | 121.4539 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.063103 | -0.0054142 | 0.056042 | -0.0022889 | -0.00050846 | 0.00015807 | 0.06299 | 0.01501 | 0.058855 | -0.11341 | 3.5132 | -0.20985 | 121.5259 | 121.3144 | 121.2094 | -0.20042 | -0.058476 | 10.1971 | -0.17998 | 121.1811 | 121.4108 | 121.3682 | -0.24199 | 0.083388 | 0.072057 | 0.1704 | 0.073959 | -0.009429 | -0.13947 | -0.24448 | 0.041824 | -0.27273 | 0.22534 | 0.10384 | 0.062013 | -0.043083 | -0.085668 | 121.8097 | 121.5982 | 121.4932 | 3.797 | -121.6543 | 121.4649 | 121.6946 | 121.652 | 10.481 | -121.6958
1853.5938 | 121.7697 | -0.24719 | 121.4172 | 1.4211e-13 | -0.0285 | -0.0013783 | 0.062675 | -0.0052006 | 0.056042 | -0.01755 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.01501 | 0.058855 | -0.10883 | 3.5132 | -0.20985 | 121.5259 | 121.3098 | 121.214 | -0.205 | -0.053897 | 10.1926 | -0.18455 | 121.1765 | 121.4108 | 121.3682 | -0.23741 | 0.042188 | 0.10868 | 0.13836 | 0.037338 | -0.00485 | -0.10743 | -0.20328 | 0.009782 | -0.24069 | 0.19329 | 0.062637 | 0.052855 | -0.006462 | -0.049047 | 121.7731 | 121.557 | 121.4611 | 3.7604 | -121.6222 | 121.4237 | 121.658 | 121.6154 | 10.4398 | -121.6546
1855.375 | 121.701 | -0.28381 | 121.4035 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062462 | -0.0054142 | 0.056469 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.015224 | 0.058855 | -0.11341 | 3.5132 | -0.20985 | 121.5213 | 121.319 | 121.2185 | -0.20042 | -0.058476 | 10.1743 | -0.18913 | 121.1765 | 121.4108 | 121.359 | -0.24199 | 0.083388 | 0.11783 | 0.1704 | 0.073959 | -0.009429 | -0.084538 | -0.18497 | 0.041824 | -0.22695 | 0.22534 | 0.094679 | 0.052855 | 0.007271 | -0.044471 | 121.8051 | 121.6028 | 121.5023 | 3.797 | -121.6039 | 121.4604 | 121.6946 | 121.6428 | 10.4581 | -121.6455
1857.0938 | 121.6599 | -0.3067 | 121.431 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062889 | -0.005628 | 0.056042 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.01501 | 0.059069 | -0.11799 | 3.5224 | -0.21443 | 121.5168 | 121.3098 | 121.2048 | -0.20042 | -0.063054 | 10.1926 | -0.19371 | 121.1765 | 121.4062 | 121.3545 | -0.23741 | 0.10628 | 0.085789 | 0.18871 | 0.09227 | -0.014007 | -0.12116 | -0.22617 | 0.069292 | -0.25442 | 0.24365 | 0.11299 | 0.043698 | -0.024774 | -0.076516 | 121.8235 | 121.6165 | 121.5115 | 3.8291 | -121.6314 | 121.4833 | 121.7129 | 121.6612 | 10.4993 | -121.6684
1858.875 | 121.756 | -0.22888 | 121.3852 | 1.4211e-13 | -0.028713 | -0.0022329 | 0.062889 | -0.0052006 | 0.056255 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.06299 | 0.01501 | 0.058641 | -0.10883 | 3.5224 | -0.21443 | 121.5213 | 121.3144 | 121.2231 | -0.20042 | -0.049318 | 10.1788 | -0.18913 | 121.1811 | 121.4154 | 121.359 | -0.23741 | 0.028457 | 0.13614 | 0.12005 | 0.01445 | -0.014007 | -0.070807 | -0.16208 | -0.008528 | -0.20407 | 0.17956 | 0.039748 | 0.048276 | 0.030159 | -0.026161 | 121.7502 | 121.5433 | 121.452 | 3.7512 | -121.5856 | 121.41 | 121.6442 | 121.5879 | 10.4077 | -121.6226
1860.5781 | 121.7606 | -0.25635 | 121.4401 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062462 | -0.0052006 | 0.056469 | -0.0022889 | 0.00013254 | -0.00026913 | 0.063203 | 0.01501 | 0.058855 | -0.12257 | 3.5315 | -0.21443 | 121.5259 | 121.3144 | 121.214 | -0.20042 | -0.058476 | 10.1102 | -0.18913 | 121.1857 | 121.4062 | 121.3682 | -0.23741 | 0.055923 | 0.085789 | 0.13378 | 0.041916 | -0.014007 | -0.12574 | -0.22617 | 0.018938 | -0.25442 | 0.19787 | 0.067214 | 0.048276 | -0.03393 | -0.071936 | 121.7823 | 121.5707 | 121.4703 | 3.7879 | -121.6405 | 121.4421 | 121.6625 | 121.6245 | 10.3665 | -121.6775
1862.3438 | 121.6599 | -0.28839 | 121.4584 | 1.4211e-13 | -0.028713 | -0.0013783 | 0.062675 | -0.005628 | 0.056042 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058641 | -0.11799 | 3.5452 | -0.20985 | 121.5259 | 121.3144 | 121.2094 | -0.20042 | -0.058476 | 10.1239 | -0.18913 | 121.1811 | 121.4108 | 121.3636 | -0.25115 | 0.087966 | 0.067479 | 0.1704 | 0.078537 | -0.009429 | -0.14405 | -0.24906 | 0.037245 | -0.27731 | 0.22992 | 0.099257 | 0.062012 | -0.047661 | -0.094825 | 121.8143 | 121.6028 | 121.4978 | 3.8336 | -121.6589 | 121.4695 | 121.6992 | 121.652 | 10.4123 | -121.7096
1864.125 | 121.7926 | -0.22888 | 121.4127 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0052006 | 0.056042 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.01501 | 0.059069 | -0.11341 | 3.5498 | -0.21443 | 121.5259 | 121.3052 | 121.2094 | -0.20042 | -0.053897 | 10.1422 | -0.18913 | 121.1765 | 121.4016 | 121.3545 | -0.24199 | 0.028457 | 0.11325 | 0.11547 | 0.01445 | -0.014007 | -0.10743 | -0.20329 | -0.013107 | -0.23611 | 0.17499 | 0.039748 | 0.052855 | -0.011043 | -0.058206 | 121.7548 | 121.5341 | 121.4383 | 3.7787 | -121.6131 | 121.4054 | 121.6305 | 121.5833 | 10.3711 | -121.6546
1865.8281 | 121.6736 | -0.3067 | 121.4035 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0052006 | 0.056469 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.06299 | 0.014797 | 0.058641 | -0.11341 | 3.5727 | -0.21443 | 121.5259 | 121.3098 | 121.214 | -0.20958 | -0.053897 | 10.1514 | -0.19371 | 121.1765 | 121.4016 | 121.3682 | -0.24657 | 0.097119 | 0.12241 | 0.19329 | 0.09227 | -0.004849 | -0.093696 | -0.18955 | 0.060135 | -0.22695 | 0.2528 | 0.11299 | 0.052855 | -0.001887 | -0.035314 | 121.8326 | 121.6165 | 121.5207 | 3.8794 | -121.6131 | 121.4833 | 121.7083 | 121.6749 | 10.4581 | -121.6501
1867.5938 | 121.8018 | -0.25177 | 121.3715 | 1.4211e-13 | -0.028286 | -0.0015919 | 0.062889 | -0.0054142 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.063203 | 0.01501 | 0.059069 | -0.12257 | 3.5498 | -0.22359 | 121.5122 | 121.3052 | 121.214 | -0.205 | -0.063054 | 10.1559 | -0.19829 | 121.172 | 121.4016 | 121.3545 | -0.25115 | 0.046766 | 0.14072 | 0.1292 | 0.028181 | -0.018585 | -0.066232 | -0.15751 | 0.000624 | -0.19949 | 0.18872 | 0.053479 | 0.052855 | 0.030156 | -0.017007 | 121.7639 | 121.557 | 121.4657 | 3.8016 | -121.5765 | 121.4237 | 121.6534 | 121.6062 | 10.4077 | -121.6226
1869.3594 | 121.7194 | -0.29755 | 121.4355 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062889 | -0.0054142 | 0.056469 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.015438 | 0.058641 | -0.12257 | 3.5773 | -0.21901 | 121.5213 | 121.3098 | 121.2094 | -0.205 | -0.053897 | 10.1743 | -0.19371 | 121.172 | 121.3925 | 121.3545 | -0.25115 | 0.092542 | 0.085789 | 0.17498 | 0.078536 | -0.014006 | -0.12574 | -0.22617 | 0.0464 | -0.26358 | 0.24365 | 0.10383 | 0.057434 | -0.043088 | -0.081094 | 121.8189 | 121.6074 | 121.5069 | 3.8748 | -121.6406 | 121.4695 | 121.69 | 121.652 | 10.4718 | -121.6867
1871.1406 | 121.7056 | -0.28839 | 121.4355 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0054142 | 0.056042 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.06299 | 0.01501 | 0.058428 | -0.12715 | 3.5819 | -0.22817 | 121.5168 | 121.3006 | 121.2048 | -0.21416 | -0.058476 | 10.2292 | -0.20287 | 121.172 | 121.3925 | 121.3499 | -0.24657 | 0.074229 | 0.081211 | 0.16124 | 0.060224 | -0.014005 | -0.1349 | -0.23075 | 0.041824 | -0.26358 | 0.22992 | 0.085521 | 0.043697 | -0.043088 | -0.085672 | 121.8051 | 121.589 | 121.4932 | 3.8703 | -121.6497 | 121.4604 | 121.6809 | 121.6383 | 10.5176 | -121.6821
1872.9062 | 121.7468 | -0.2655 | 121.3943 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062675 | -0.005628 | 0.056469 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.063203 | 0.015224 | 0.058428 | -0.13173 | 3.591 | -0.22817 | 121.5122 | 121.3006 | 121.1956 | -0.21874 | -0.067633 | 10.2429 | -0.20287 | 121.172 | 121.3833 | 121.3499 | -0.25115 | 0.046762 | 0.11783 | 0.13378 | 0.037336 | -0.009426 | -0.093699 | -0.19871 | 0.014357 | -0.22238 | 0.19787 | 0.062633 | 0.048276 | -0.011046 | -0.044473 | 121.7777 | 121.5662 | 121.4611 | 3.8565 | -121.6131 | 121.4375 | 121.6488 | 121.6154 | 10.5084 | -121.6455
1874.625 | 121.8613 | -0.29755 | 121.4035 | 1.4211e-13 | -0.028713 | -0.0011645 | 0.063103 | -0.005628 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.014797 | 0.058855 | -0.13173 | 3.6002 | -0.23275 | 121.5122 | 121.3006 | 121.2002 | -0.21874 | -0.072212 | 10.2109 | -0.21203 | 121.1582 | 121.3833 | 121.3453 | -0.2603 | 0.078805 | 0.10868 | 0.16582 | 0.064801 | -0.014004 | -0.10285 | -0.20329 | 0.037242 | -0.24527 | 0.22533 | 0.085519 | 0.048277 | -0.020201 | -0.058207 | 121.8097 | 121.5982 | 121.4978 | 3.8977 | -121.6222 | 121.4558 | 121.6808 | 121.6428 | 10.5084 | -121.6638
1876.3906 | 121.788 | -0.27466 | 121.3943 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062675 | -0.005628 | 0.056042 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062776 | 0.015224 | 0.058428 | -0.13173 | 3.5956 | -0.23732 | 121.5076 | 121.2915 | 121.1956 | -0.21874 | -0.07679 | 10.1605 | -0.20745 | 121.1628 | 121.3879 | 121.3407 | -0.25572 | 0.055917 | 0.11325 | 0.14293 | 0.037335 | -0.018582 | -0.10286 | -0.19871 | 0.018933 | -0.23153 | 0.19787 | 0.067209 | 0.048276 | -0.006467 | -0.053631 | 121.7823 | 121.5661 | 121.4703 | 3.8703 | -121.6131 | 121.4375 | 121.6625 | 121.6154 | 10.4352 | -121.6501
1878.1719 | 121.6782 | -0.28839 | 121.3852 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062889 | -0.0054142 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.015224 | 0.058641 | -0.14088 | 3.5865 | -0.23732 | 121.503 | 121.2915 | 121.1956 | -0.22332 | -0.081369 | 10.1697 | -0.21661 | 121.1491 | 121.3787 | 121.3407 | -0.26488 | 0.065071 | 0.11783 | 0.14751 | 0.051068 | -0.014003 | -0.093702 | -0.18955 | 0.023508 | -0.23611 | 0.20702 | 0.071785 | 0.048277 | -0.00647 | -0.044476 | 121.7914 | 121.5799 | 121.484 | 3.8748 | -121.6085 | 121.4375 | 121.6671 | 121.6291 | 10.4581 | -121.6501
1879.8906 | 121.6553 | -0.28381 | 121.4218 | 1.4211e-13 | -0.0285 | -0.0015919 | 0.062675 | -0.0054142 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058641 | -0.12715 | 3.5956 | -0.23275 | 121.503 | 121.2915 | 121.1956 | -0.21874 | -0.07679 | 10.1605 | -0.20745 | 121.1582 | 121.3833 | 121.3407 | -0.25572 | 0.065072 | 0.081208 | 0.15667 | 0.051068 | -0.014004 | -0.13032 | -0.22618 | 0.028088 | -0.26358 | 0.20702 | 0.076364 | 0.048276 | -0.038512 | -0.081097 | 121.7868 | 121.5753 | 121.4795 | 3.8794 | -121.6406 | 121.442 | 121.6671 | 121.6245 | 10.4443 | -121.6775
1881.6719 | 121.7056 | -0.31128 | 121.4172 | 1.4211e-13 | -0.028713 | -0.0020193 | 0.062675 | -0.005628 | 0.056042 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.015224 | 0.058428 | -0.1363 | 3.5865 | -0.23732 | 121.5076 | 121.2961 | 121.1911 | -0.21874 | -0.07679 | 10.188 | -0.20745 | 121.1628 | 121.3879 | 121.3407 | -0.26488 | 0.092538 | 0.090365 | 0.17497 | 0.073956 | -0.018582 | -0.12117 | -0.22618 | 0.046396 | -0.25442 | 0.23449 | 0.10383 | 0.057434 | -0.029355 | -0.076519 | 121.8189 | 121.6073 | 121.5023 | 3.8977 | -121.636 | 121.4741 | 121.6992 | 121.652 | 10.4993 | -121.6821
1883.375 | 121.7148 | -0.27924 | 121.3806 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062889 | -0.005628 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.01501 | 0.058428 | -0.1363 | 3.5773 | -0.23275 | 121.503 | 121.2961 | 121.1956 | -0.2279 | -0.081369 | 10.1743 | -0.20287 | 121.172 | 121.3833 | 121.3453 | -0.25572 | 0.051337 | 0.12241 | 0.14293 | 0.046491 | -0.004846 | -0.084545 | -0.18498 | 0.023511 | -0.20865 | 0.19787 | 0.076366 | 0.052855 | 0.002687 | -0.035319 | 121.7823 | 121.5753 | 121.4749 | 3.8565 | -121.6085 | 121.4512 | 121.6625 | 121.6245 | 10.4535 | -121.6363
1885.1719 | 121.7789 | -0.25635 | 121.3852 | 1.4211e-13 | -0.029354 | -0.0018055 | 0.062675 | -0.0054142 | 0.056469 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058641 | -0.14088 | 3.591 | -0.23732 | 121.5076 | 121.2869 | 121.1911 | -0.21874 | -0.081369 | 10.1285 | -0.21203 | 121.1674 | 121.3833 | 121.3407 | -0.26488 | 0.037607 | 0.12241 | 0.11547 | 0.019025 | -0.018582 | -0.098281 | -0.19413 | -0.008535 | -0.2178 | 0.17498 | 0.044321 | 0.052856 | -0.001891 | -0.044476 | 121.7639 | 121.5433 | 121.4474 | 3.8474 | -121.6039 | 121.4237 | 121.6397 | 121.5971 | 10.3848 | -121.6501
1886.9375 | 121.7926 | -0.25635 | 121.3577 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | 0.00013254 | -0.00026913 | 0.062776 | 0.015224 | 0.058641 | -0.1363 | 3.5727 | -0.23732 | 121.4984 | 121.2961 | 121.1911 | -0.22332 | -0.072212 | 10.1056 | -0.21661 | 121.1674 | 121.3833 | 121.3316 | -0.27404 | 0.033028 | 0.14072 | 0.12004 | 0.019025 | -0.014003 | -0.061657 | -0.16667 | -0.017692 | -0.19033 | 0.18414 | 0.039742 | 0.057434 | 0.025575 | -0.026167 | 121.7548 | 121.5524 | 121.4474 | 3.8291 | -121.581 | 121.4237 | 121.6397 | 121.5879 | 10.3619 | -121.6318
1888.6406 | 121.7743 | -0.27466 | 121.3669 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062675 | -0.0054142 | 0.055828 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.015224 | 0.058428 | -0.1363 | 3.5819 | -0.23732 | 121.4984 | 121.2869 | 121.1956 | -0.23248 | -0.07679 | 10.1102 | -0.21203 | 121.1628 | 121.3787 | 121.3361 | -0.27404 | 0.042181 | 0.13156 | 0.13835 | 0.037335 | -0.004846 | -0.07997 | -0.17124 | 0.000618 | -0.20407 | 0.19787 | 0.062631 | 0.062013 | 0.011841 | -0.030743 | 121.7731 | 121.5616 | 121.4703 | 3.8565 | -121.5994 | 121.4375 | 121.6534 | 121.6108 | 10.3848 | -121.6409
1890.4062 | 121.6873 | -0.31586 | 121.376 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062889 | -0.005628 | 0.056255 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.015224 | 0.058428 | -0.14088 | 3.5956 | -0.2419 | 121.4984 | 121.2869 | 121.1911 | -0.22332 | -0.085948 | 10.101 | -0.21661 | 121.1628 | 121.3741 | 121.3453 | -0.26946 | 0.092537 | 0.12241 | 0.17497 | 0.073955 | -0.018582 | -0.089126 | -0.18498 | 0.046395 | -0.21322 | 0.22991 | 0.099251 | 0.052856 | -0.001893 | -0.030742 | 121.8143 | 121.6028 | 121.5069 | 3.9115 | -121.5994 | 121.4787 | 121.69 | 121.6612 | 10.4169 | -121.6455
1892.1875 | 121.7331 | -0.29755 | 121.3669 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062462 | -0.0054142 | 0.056469 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.01501 | 0.058641 | -0.14546 | 3.5956 | -0.25106 | 121.4984 | 121.2915 | 121.1865 | -0.22332 | -0.090527 | 10.101 | -0.22118 | 121.1628 | 121.3787 | 121.3316 | -0.27404 | 0.074226 | 0.13156 | 0.15208 | 0.046488 | -0.027738 | -0.075391 | -0.1804 | 0.023506 | -0.20407 | 0.20702 | 0.076361 | 0.052855 | 0.011841 | -0.035322 | 121.796 | 121.589 | 121.484 | 3.8932 | -121.5902 | 121.4604 | 121.6763 | 121.6291 | 10.3985 | -121.6409
1893.9531 | 121.7926 | -0.28839 | 121.3577 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.063203 | 0.015438 | 0.058214 | -0.15462 | 3.5956 | -0.24648 | 121.4939 | 121.2732 | 121.1773 | -0.2279 | -0.085948 | 10.0689 | -0.22118 | 121.1491 | 121.3696 | 121.327 | -0.27862 | 0.060492 | 0.13614 | 0.13377 | 0.041911 | -0.018581 | -0.084552 | -0.1804 | 0.009772 | -0.20865 | 0.20244 | 0.067206 | 0.057434 | 0.011839 | -0.030745 | 121.7823 | 121.5616 | 121.4657 | 3.884 | -121.5856 | 121.4375 | 121.658 | 121.6154 | 10.3573 | -121.6363
1895.6719 | 121.669 | -0.32959 | 121.4127 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0099194 | -0.00029486 | -0.00026913 | 0.062563 | 0.01501 | 0.058641 | -0.15462 | 3.6139 | -0.26021 | 121.4801 | 121.2732 | 121.1819 | -0.2279 | -0.095105 | 10.0415 | -0.22576 | 121.1537 | 121.3787 | 121.327 | -0.2832 | 0.10169 | 0.067472 | 0.17497 | 0.069375 | -0.032316 | -0.13948 | -0.23076 | 0.046392 | -0.259 | 0.23448 | 0.10383 | 0.057435 | -0.033936 | -0.085677 | 121.8097 | 121.6028 | 121.5115 | 3.9435 | -121.6406 | 121.4832 | 121.7083 | 121.6566 | 10.3711 | -121.6959
1897.4375 | 121.6782 | -0.33417 | 121.4035 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0052006 | 0.056255 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.01501 | 0.058428 | -0.16377 | 3.6185 | -0.25564 | 121.4893 | 121.2778 | 121.1819 | -0.24621 | -0.090527 | 10.0644 | -0.22576 | 121.1537 | 121.3741 | 121.3178 | -0.2832 | 0.087953 | 0.085784 | 0.17039 | 0.07853 | -0.009423 | -0.12575 | -0.2216 | 0.050969 | -0.24985 | 0.24364 | 0.1084 | 0.057435 | -0.029358 | -0.085679 | 121.8235 | 121.6119 | 121.5161 | 3.9527 | -121.6497 | 121.4878 | 121.7083 | 121.652 | 10.3985 | -121.6867
1899.1406 | 121.7514 | -0.28381 | 121.3577 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062462 | -0.005628 | 0.056255 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.014797 | 0.058428 | -0.14088 | 3.6093 | -0.25106 | 121.4893 | 121.2732 | 121.1819 | -0.23706 | -0.099684 | 10.046 | -0.23034 | 121.1491 | 121.3696 | 121.3224 | -0.2832 | 0.046757 | 0.13156 | 0.14293 | 0.032755 | -0.014002 | -0.084552 | -0.17583 | 0.000615 | -0.20865 | 0.18413 | 0.053471 | 0.052856 | 0.011839 | -0.035324 | 121.7731 | 121.557 | 121.4657 | 3.8932 | -121.5948 | 121.4329 | 121.6534 | 121.6062 | 10.3299 | -121.6409
1900.9219 | 121.7651 | -0.29755 | 121.3852 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.01501 | 0.058855 | -0.16377 | 3.591 | -0.26479 | 121.4801 | 121.2732 | 121.1773 | -0.24621 | -0.095105 | 10.0094 | -0.23492 | 121.1491 | 121.3696 | 121.3224 | -0.28778 | 0.051332 | 0.094938 | 0.13377 | 0.032753 | -0.018579 | -0.11202 | -0.20787 | 0.009769 | -0.23611 | 0.20244 | 0.062625 | 0.052856 | -0.015627 | -0.06279 | 121.7777 | 121.5707 | 121.4749 | 3.8886 | -121.6314 | 121.4466 | 121.6671 | 121.6199 | 10.307 | -121.673
1902.6875 | 121.756 | -0.27466 | 121.376 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062462 | -0.0054142 | 0.056255 | -0.0099194 | 0.00013254 | 0.00015807 | 0.06299 | 0.015224 | 0.058428 | -0.15462 | 3.6139 | -0.25106 | 121.4847 | 121.2686 | 121.1773 | -0.24621 | -0.099684 | 9.9499 | -0.22576 | 121.1537 | 121.3741 | 121.3178 | -0.28778 | 0.028444 | 0.10867 | 0.12004 | 0.0236 | -0.004844 | -0.10744 | -0.19871 | -0.013119 | -0.22238 | 0.17497 | 0.048895 | 0.062014 | -0.001893 | -0.058214 | 121.7594 | 121.5433 | 121.452 | 3.8886 | -121.6223 | 121.4283 | 121.6488 | 121.5925 | 10.2246 | -121.6638
1904.4688 | 121.8063 | -0.29297 | 121.3531 | 1.4211e-13 | -0.029354 | -0.0015919 | 0.063103 | -0.005628 | 0.056042 | -0.01755 | -0.00029486 | 0.00058547 | 0.06299 | 0.015224 | 0.058214 | -0.1592 | 3.6231 | -0.26021 | 121.4756 | 121.2732 | 121.1773 | -0.24621 | -0.095105 | 9.9865 | -0.23492 | 121.1537 | 121.365 | 121.3178 | -0.28778 | 0.046755 | 0.1224 | 0.13377 | 0.032754 | -0.014001 | -0.079974 | -0.17583 | 0.005192 | -0.19949 | 0.19786 | 0.058048 | 0.052856 | 0.011839 | -0.035325 | 121.7685 | 121.5661 | 121.4703 | 3.916 | -121.5994 | 121.4466 | 121.658 | 121.6108 | 10.2795 | -121.6409
1906.1875 | 121.669 | -0.32959 | 121.376 | 1.4211e-13 | -0.028713 | -0.0018055 | 0.062889 | -0.0054142 | 0.056255 | 0.0053411 | 0.00013254 | -0.00026913 | 0.062563 | 0.01501 | 0.058641 | -0.16377 | 3.6322 | -0.26021 | 121.4801 | 121.2686 | 121.1727 | -0.24621 | -0.099684 | 9.9865 | -0.2395 | 121.1445 | 121.3604 | 121.3224 | -0.29236 | 0.083376 | 0.10409 | 0.16582 | 0.069375 | -0.014001 | -0.10744 | -0.20329 | 0.037234 | -0.23154 | 0.22991 | 0.090091 | 0.052857 | -0.015629 | -0.053635 | 121.8097 | 121.5982 | 121.5023 | 3.9618 | -121.6223 | 121.4741 | 121.69 | 121.652 | 10.3161 | -121.6684
1907.9688 | 121.7972 | -0.28381 | 121.3623 | 1.4211e-13 | -0.028927 | -0.0018055 | 0.062675 | -0.0052006 | 0.056255 | -0.0099194 | 0.00034614 | -0.00048293 | 0.062776 | 0.015438 | 0.058641 | -0.1592 | 3.6185 | -0.26021 | 121.4801 | 121.2594 | 121.1636 | -0.25079 | -0.099684 | 10.0048 | -0.23034 | 121.1491 | 121.365 | 121.3132 | -0.29236 | 0.03302 | 0.11783 | 0.12462 | 0.023598 | -0.009422 | -0.10287 | -0.19872 | -0.008543 | -0.21323 | 0.18413 | 0.053471 | 0.062014 | 0.002683 | -0.049059 | 121.7639 | 121.5433 | 121.4474 | 3.9023 | -121.6131 | 121.4329 | 121.6488 | 121.5971 | 10.2887 | -121.6547
1909.75 | 121.7468 | -0.30212 | 121.3715 | 1.4211e-13 | -0.028713 | -0.0015919 | 0.062462 | -0.0058416 | 0.055828 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.06299 | 0.01501 | 0.058641 | -0.16835 | 3.6185 | -0.26937 | 121.4801 | 121.2686 | 121.1682 | -0.25079 | -0.099684 | 9.9499 | -0.2395 | 121.1445 | 121.365 | 121.3087 | -0.29693 | 0.051331 | 0.10867 | 0.13377 | 0.032753 | -0.018578 | -0.10286 | -0.20329 | 0.00519 | -0.22696 | 0.20244 | 0.062625 | 0.057435 | -0.006472 | -0.062793 | 121.7823 | 121.5707 | 121.4703 | 3.9206 | -121.6223 | 121.4466 | 121.6671 | 121.6108 | 10.252 | -121.6684
1911.4531 | 121.8201 | -0.29755 | 121.3577 | 1.4211e-13 | -0.029354 | -0.0015919 | 0.062675 | -0.0052006 | 0.056255 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058641 | -0.16835 | 3.6139 | -0.26937 | 121.471 | 121.264 | 121.1682 | -0.25079 | -0.10426 | 9.9545 | -0.22576 | 121.1399 | 121.3604 | 121.3132 | -0.30151 | 0.046753 | 0.11325 | 0.12919 | 0.028175 | -0.018578 | -0.093709 | -0.18956 | -0.003967 | -0.21781 | 0.19328 | 0.071783 | 0.07575 | 0.002682 | -0.044481 | 121.7685 | 121.5616 | 121.4657 | 3.9115 | -121.6085 | 121.4375 | 121.658 | 121.6108 | 10.252 | -121.6592
1913.2188 | 121.6919 | -0.32501 | 121.3623 | 1.4211e-13 | -0.029141 | -0.0015919 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | 0.00013254 | -0.00048293 | 0.062776 | 0.014797 | 0.058428 | -0.16835 | 3.6139 | -0.26937 | 121.471 | 121.264 | 121.1636 | -0.25537 | -0.10426 | 9.895 | -0.2395 | 121.1308 | 121.3558 | 121.3132 | -0.29693 | 0.06964 | 0.10867 | 0.15666 | 0.055641 | -0.013999 | -0.098287 | -0.19872 | 0.028078 | -0.23154 | 0.22075 | 0.085513 | 0.057435 | -0.006475 | -0.049059 | 121.796 | 121.589 | 121.4886 | 3.9389 | -121.6177 | 121.4558 | 121.6808 | 121.6383 | 10.22 | -121.6592
1915 | 121.6415 | -0.34332 | 121.3623 | 1.4211e-13 | -0.029354 | -0.0013783 | 0.062889 | -0.005628 | 0.056469 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015224 | 0.058214 | -0.17293 | 3.6048 | -0.26937 | 121.4664 | 121.2594 | 121.1636 | -0.26453 | -0.10884 | 9.9316 | -0.24866 | 121.1353 | 121.3558 | 121.3087 | -0.30151 | 0.078793 | 0.10409 | 0.17039 | 0.073952 | -0.004841 | -0.10287 | -0.19872 | 0.04181 | -0.22696 | 0.23448 | 0.094666 | 0.052856 | -0.006475 | -0.053638 | 121.8097 | 121.6028 | 121.5069 | 3.9481 | -121.6268 | 121.4787 | 121.6992 | 121.652 | 10.2749 | -121.6638
1916.7031 | 121.788 | -0.30212 | 121.3394 | 1.4211e-13 | -0.029141 | -0.0015919 | 0.062034 | -0.0054142 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.015224 | 0.058214 | -0.17293 | 3.6048 | -0.26937 | 121.4756 | 121.2549 | 121.1636 | -0.25079 | -0.11342 | 9.9087 | -0.24866 | 121.1353 | 121.3467 | 121.3041 | -0.30151 | 0.051331 | 0.13613 | 0.12919 | 0.032753 | -0.018578 | -0.084557 | -0.17583 | 0.000611 | -0.20408 | 0.1887 | 0.053467 | 0.052856 | 0.007256 | -0.035328 | 121.7777 | 121.557 | 121.4657 | 3.9069 | -121.5902 | 121.4375 | 121.6488 | 121.6062 | 10.2108 | -121.6409
1918.4531 | 121.8109 | -0.31586 | 121.3303 | 1.4211e-13 | -0.028927 | -0.0015919 | 0.062462 | -0.005628 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.015224 | 0.058214 | -0.18667 | 3.6002 | -0.27853 | 121.4618 | 121.2411 | 121.1499 | -0.27369 | -0.12258 | 9.8812 | -0.25324 | 121.1262 | 121.3421 | 121.2949 | -0.31067 | 0.042169 | 0.13156 | 0.12919 | 0.037329 | -0.00484 | -0.089138 | -0.18041 | 0.005186 | -0.20408 | 0.19328 | 0.062621 | 0.057435 | 0.011834 | -0.03533 | 121.7777 | 121.557 | 121.4657 | 3.916 | -121.6039 | 121.442 | 121.658 | 121.6108 | 10.1971 | -121.6409
1920.25 | 121.7056 | -0.33875 | 121.3669 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062889 | -0.0058416 | 0.056469 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015224 | 0.058428 | -0.17293 | 3.6231 | -0.28311 | 121.4664 | 121.2549 | 121.159 | -0.26911 | -0.10884 | 9.8766 | -0.24408 | 121.1262 | 121.3467 | 121.2995 | -0.30609 | 0.069636 | 0.099513 | 0.16581 | 0.055639 | -0.013997 | -0.11202 | -0.20787 | 0.032653 | -0.2407 | 0.2299 | 0.094667 | 0.062014 | -0.020209 | -0.067372 | 121.8051 | 121.5936 | 121.4978 | 3.9618 | -121.636 | 121.4649 | 121.6854 | 121.6383 | 10.2154 | -121.673
1922.0312 | 121.7606 | -0.31586 | 121.3577 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.01501 | 0.058214 | -0.17751 | 3.6277 | -0.26937 | 121.4664 | 121.2457 | 121.159 | -0.26453 | -0.12258 | 9.8812 | -0.24866 | 121.1308 | 121.3558 | 121.2995 | -0.31067 | 0.051327 | 0.10867 | 0.13835 | 0.046486 | -0.004841 | -0.11203 | -0.19872 | 0.005186 | -0.22696 | 0.19328 | 0.0672 | 0.062014 | -0.001897 | -0.058217 | 121.7823 | 121.5616 | 121.4749 | 3.9435 | -121.6223 | 121.4466 | 121.6717 | 121.6154 | 10.1971 | -121.6684
1923.8125 | 121.7377 | -0.31586 | 121.3623 | 1.4211e-13 | -0.029354 | -0.0015919 | 0.062462 | -0.005628 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015438 | 0.058214 | -0.17751 | 3.6002 | -0.27395 | 121.4756 | 121.2594 | 121.1636 | -0.25537 | -0.10884 | 9.8583 | -0.24408 | 121.1262 | 121.3467 | 121.2995 | -0.30151 | 0.060485 | 0.11325 | 0.13835 | 0.041907 | -0.018578 | -0.10287 | -0.19872 | 0.014344 | -0.23612 | 0.20702 | 0.071779 | 0.057435 | -0.015632 | -0.062795 | 121.7914 | 121.5753 | 121.4794 | 3.916 | -121.6177 | 121.442 | 121.6625 | 121.6154 | 10.1742 | -121.6638
1925.5312 | 121.6507 | -0.35248 | 121.3989 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.01501 | 0.058214 | -0.16377 | 3.6185 | -0.26937 | 121.4756 | 121.2594 | 121.1682 | -0.26453 | -0.10884 | 9.808 | -0.2395 | 121.1308 | 121.3513 | 121.2995 | -0.29236 | 0.087948 | 0.076626 | 0.1887 | 0.083107 | -0.004841 | -0.13949 | -0.23076 | 0.060122 | -0.26816 | 0.24364 | 0.11298 | 0.052857 | -0.047674 | -0.099416 | 121.828 | 121.6119 | 121.5206 | 3.971 | -121.6635 | 121.4832 | 121.7037 | 121.652 | 10.1604 | -121.6913
1927.2812 | 121.7697 | -0.30212 | 121.3257 | 1.4211e-13 | -0.029354 | -0.0018055 | 0.062675 | -0.005628 | 0.056683 | -0.0022889 | -0.00050846 | 0.00015807 | 0.06299 | 0.015224 | 0.058214 | -0.16835 | 3.6414 | -0.26937 | 121.4801 | 121.2594 | 121.1636 | -0.25537 | -0.10426 | 9.8217 | -0.23492 | 121.1445 | 121.3558 | 121.3087 | -0.30609 | 0.046752 | 0.15445 | 0.13377 | 0.032753 | -0.013999 | -0.066245 | -0.1621 | -0.003968 | -0.18118 | 0.19786 | 0.067203 | 0.071171 | 0.030146 | -0.017017 | 121.7823 | 121.5616 | 121.4657 | 3.9435 | -121.5811 | 121.4466 | 121.658 | 121.6108 | 10.1238 | -121.6318
1929.0469 | 121.6736 | -0.3479 | 121.3852 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062776 | 0.015438 | 0.058214 | -0.17293 | 3.6322 | -0.27395 | 121.471 | 121.2549 | 121.1682 | -0.25537 | -0.10426 | 9.8263 | -0.2395 | 121.1308 | 121.3513 | 121.3087 | -0.29693 | 0.092528 | 0.085781 | 0.17497 | 0.07395 | -0.018578 | -0.13033 | -0.21703 | 0.050966 | -0.25443 | 0.24364 | 0.1084 | 0.057435 | -0.033941 | -0.076526 | 121.8189 | 121.6028 | 121.5161 | 3.9801 | -121.6406 | 121.4787 | 121.6992 | 121.6566 | 10.1742 | -121.6821
1930.7656 | 121.6782 | -0.34332 | 121.3989 | 1.4211e-13 | -0.029354 | -0.0013783 | 0.062462 | -0.0054142 | 0.056042 | -0.0099194 | -0.00029486 | 0.00015807 | 0.062776 | 0.015224 | 0.058428 | -0.16835 | 3.6506 | -0.27395 | 121.4756 | 121.264 | 121.1773 | -0.25537 | -0.10884 | 9.7805 | -0.2395 | 121.1308 | 121.3604 | 121.3041 | -0.29693 | 0.087951 | 0.076626 | 0.17497 | 0.069373 | -0.018578 | -0.13491 | -0.2216 | 0.046389 | -0.26816 | 0.23448 | 0.10382 | 0.057435 | -0.038517 | -0.094837 | 121.8189 | 121.6073 | 121.5206 | 3.9939 | -121.6543 | 121.4741 | 121.7037 | 121.6474 | 10.1238 | -121.6959
1932.5312 | 121.7789 | -0.29755 | 121.3577 | 1.4211e-13 | -0.029354 | -0.0018055 | 0.062462 | -0.0054142 | 0.056042 | -0.0022889 | -8.1262e-05 | -0.00048293 | 0.062563 | 0.015652 | 0.058214 | -0.16835 | 3.6231 | -0.26937 | 121.471 | 121.264 | 121.1727 | -0.24621 | -0.10426 | 9.7713 | -0.24408 | 121.1445 | 121.3558 | 121.3087 | -0.30151 | 0.051332 | 0.11325 | 0.12919 | 0.028175 | -0.023157 | -0.093709 | -0.18498 | -0.003967 | -0.21323 | 0.19328 | 0.053468 | 0.057435 | -0.001897 | -0.04906 | 121.7685 | 121.5616 | 121.4703 | 3.9206 | -121.6039 | 121.442 | 121.6534 | 121.6062 | 10.0689 | -121.6592
1934.2969 | 121.7606 | -0.31586 | 121.3211 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.015224 | 0.058641 | -0.16835 | 3.6322 | -0.26937 | 121.471 | 121.264 | 121.1682 | -0.25995 | -0.10426 | 9.8034 | -0.23492 | 121.1399 | 121.3604 | 121.3132 | -0.30151 | 0.055906 | 0.14987 | 0.1475 | 0.046486 | -0.00942 | -0.057088 | -0.15294 | 0.014344 | -0.18118 | 0.21159 | 0.080936 | 0.066592 | 0.039303 | -0.00786 | 121.7868 | 121.5799 | 121.484 | 3.9481 | -121.5811 | 121.4558 | 121.6763 | 121.6291 | 10.1192 | -121.6226
1936 | 121.7926 | -0.32959 | 121.3531 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062889 | -0.005628 | 0.056255 | 0.012972 | -8.1262e-05 | 0.00037167 | 0.062563 | 0.015438 | 0.058 | -0.17293 | 3.6368 | -0.26937 | 121.4801 | 121.2594 | 121.1682 | -0.25537 | -0.095105 | 9.753 | -0.23492 | 121.1308 | 121.3604 | 121.3087 | -0.29693 | 0.074218 | 0.12698 | 0.15666 | 0.060219 | -0.013999 | -0.09371 | -0.18498 | 0.032656 | -0.22239 | 0.23448 | 0.094669 | 0.062013 | 0.00726 | -0.044482 | 121.8097 | 121.589 | 121.4978 | 3.9664 | -121.6085 | 121.4604 | 121.69 | 121.6383 | 10.0826 | -121.6501
1937.7656 | 121.7697 | -0.29755 | 121.3577 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062889 | -0.0054142 | 0.056042 | -0.0022889 | -0.00029486 | 0.00015807 | 0.062563 | 0.015224 | 0.058641 | -0.17293 | 3.6368 | -0.26479 | 121.4756 | 121.2549 | 121.1682 | -0.25537 | -0.10426 | 9.7667 | -0.2395 | 121.1399 | 121.365 | 121.3087 | -0.30151 | 0.042174 | 0.11782 | 0.12461 | 0.032753 | -0.009421 | -0.10287 | -0.18956 | -0.003967 | -0.21781 | 0.19328 | 0.058047 | 0.062014 | 0.007261 | -0.04906 | 121.7731 | 121.5524 | 121.4657 | 3.9344 | -121.6131 | 121.4375 | 121.6625 | 121.6062 | 10.0643 | -121.6592
1939.4688 | 121.6553 | -0.34332 | 121.3989 | 1.4211e-13 | -0.029568 | -0.0015919 | 0.062889 | -0.0060552 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00037167 | 0.06299 | 0.015438 | 0.058214 | -0.17293 | 3.6551 | -0.26937 | 121.4801 | 121.2549 | 121.1682 | -0.25537 | -0.10426 | 9.7439 | -0.23034 | 121.1308 | 121.3604 | 121.3041 | -0.29693 | 0.087951 | 0.081205 | 0.17039 | 0.073952 | -0.013999 | -0.14407 | -0.23076 | 0.046389 | -0.26816 | 0.23906 | 0.11298 | 0.066592 | -0.038517 | -0.094837 | 121.8235 | 121.5982 | 121.5115 | 3.9985 | -121.6543 | 121.4741 | 121.7037 | 121.6474 | 10.0872 | -121.6959
1941.25 | 121.6873 | -0.32959 | 121.3852 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062675 | -0.0058416 | 0.056042 | 0.012972 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.015652 | 0.058214 | -0.17751 | 3.6734 | -0.26937 | 121.471 | 121.2594 | 121.1636 | -0.25995 | -0.10426 | 9.7713 | -0.23492 | 121.1399 | 121.3604 | 121.3087 | -0.30151 | 0.069639 | 0.085781 | 0.15208 | 0.060219 | -0.00942 | -0.12575 | -0.2216 | 0.028077 | -0.24527 | 0.22533 | 0.094669 | 0.066592 | -0.024784 | -0.076526 | 121.8006 | 121.589 | 121.4932 | 4.003 | -121.6451 | 121.4695 | 121.69 | 121.6383 | 10.1009 | -121.6867
1942.9688 | 121.7102 | -0.33417 | 121.3577 | 1.4211e-13 | -0.029354 | -0.0013783 | 0.062675 | -0.0052006 | 0.056042 | -0.0022889 | -8.1262e-05 | -0.00048293 | 0.062776 | 0.015652 | 0.058428 | -0.18209 | 3.646 | -0.27395 | 121.471 | 121.2594 | 121.1636 | -0.25537 | -0.099684 | 9.7759 | -0.23492 | 121.1353 | 121.3467 | 121.3087 | -0.29236 | 0.078795 | 0.11325 | 0.15208 | 0.060217 | -0.018578 | -0.098288 | -0.19414 | 0.041811 | -0.22239 | 0.23448 | 0.099246 | 0.057435 | -0.011054 | -0.04906 | 121.8051 | 121.5936 | 121.4978 | 3.9801 | -121.6131 | 121.4695 | 121.6808 | 121.6428 | 10.1101 | -121.6501
1944.6719 | 121.7239 | -0.33417 | 121.3806 | 1.4211e-13 | -0.029141 | -0.0018055 | 0.062462 | -0.005628 | 0.056042 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.062776 | 0.015224 | 0.058214 | -0.17293 | 3.6551 | -0.26937 | 121.471 | 121.264 | 121.1682 | -0.25537 | -0.10426 | 9.7759 | -0.23492 | 121.1353 | 121.3604 | 121.3041 | -0.29693 | 0.078795 | 0.090359 | 0.16124 | 0.064796 | -0.013999 | -0.1166 | -0.21245 | 0.037233 | -0.24527 | 0.2299 | 0.099246 | 0.062013 | -0.020206 | -0.076526 | 121.8051 | 121.5982 | 121.5023 | 3.9893 | -121.636 | 121.4695 | 121.6946 | 121.6383 | 10.1101 | -121.6775
1946.4375 | 121.7697 | -0.29755 | 121.3303 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062889 | -0.0054142 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062776 | 0.015652 | 0.058214 | -0.17293 | 3.6734 | -0.26937 | 121.471 | 121.2549 | 121.1727 | -0.26453 | -0.10426 | 9.8125 | -0.2395 | 121.1262 | 121.3604 | 121.3041 | -0.29693 | 0.033016 | 0.14071 | 0.12461 | 0.028175 | -0.004841 | -0.075401 | -0.15752 | 0.000612 | -0.20408 | 0.19328 | 0.058047 | 0.057435 | 0.030148 | -0.026172 | 121.7685 | 121.5524 | 121.4703 | 3.971 | -121.5948 | 121.4237 | 121.658 | 121.6016 | 10.1101 | -121.6272
1948.2188 | 121.7194 | -0.32044 | 121.3715 | 1.4211e-13 | -0.029141 | -0.0015919 | 0.063103 | -0.0058416 | 0.056683 | -0.01755 | -8.1262e-05 | 0.00015807 | 0.06299 | 0.015438 | 0.058641 | -0.17751 | 3.678 | -0.27853 | 121.4664 | 121.2549 | 121.1636 | -0.25995 | -0.10884 | 9.8171 | -0.2395 | 121.1308 | 121.3604 | 121.3041 | -0.29693 | 0.060484 | 0.094935 | 0.14293 | 0.041907 | -0.018577 | -0.1166 | -0.20787 | 0.023501 | -0.2407 | 0.21159 | 0.080936 | 0.057435 | -0.011051 | -0.067371 | 121.7868 | 121.5753 | 121.484 | 3.9985 | -121.6314 | 121.4512 | 121.6808 | 121.6245 | 10.1375 | -121.6684
1949.9219 | 121.7148 | -0.33417 | 121.344 | 1.4211e-13 | -0.029141 | -0.0020193 | 0.062889 | -0.005628 | 0.056469 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.015224 | 0.058641 | -0.17751 | 3.678 | -0.27395 | 121.4618 | 121.2594 | 121.1636 | -0.25995 | -0.10426 | 9.7805 | -0.23492 | 121.1353 | 121.3513 | 121.3132 | -0.29693 | 0.074216 | 0.11782 | 0.15666 | 0.060217 | -0.013999 | -0.084555 | -0.18041 | 0.037233 | -0.20865 | 0.2299 | 0.099246 | 0.062013 | 0.007258 | -0.030748 | 121.796 | 121.5936 | 121.4978 | 4.0122 | -121.6039 | 121.4695 | 121.6854 | 121.6474 | 10.1147 | -121.6409
1951.6406 | 121.788 | -0.32501 | 121.3303 | 1.4211e-13 | -0.029568 | -0.0015919 | 0.062889 | -0.005628 | 0.056042 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.06299 | 0.015652 | 0.058 | -0.18209 | 3.6826 | -0.27853 | 121.4664 | 121.2594 | 121.1636 | -0.26453 | -0.10884 | 9.7347 | -0.24408 | 121.1216 | 121.3513 | 121.3087 | -0.30609 | 0.060482 | 0.13613 | 0.14292 | 0.046484 | -0.013998 | -0.070822 | -0.16667 | 0.01892 | -0.20865 | 0.21617 | 0.080934 | 0.062014 | 0.020991 | -0.021594 | 121.7914 | 121.5845 | 121.4886 | 4.0076 | -121.5948 | 121.4466 | 121.6763 | 121.6337 | 10.0597 | -121.6364
1953.4062 | 121.8018 | -0.32501 | 121.344 | 1.4211e-13 | -0.029782 | -0.0018055 | 0.062462 | -0.0054142 | 0.056042 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062776 | 0.015438 | 0.058214 | -0.18667 | 3.6872 | -0.27853 | 121.4664 | 121.2503 | 121.1544 | -0.26453 | -0.10884 | 9.7347 | -0.24866 | 121.1308 | 121.3513 | 121.2995 | -0.31067 | 0.060482 | 0.1224 | 0.13835 | 0.046484 | -0.013998 | -0.093713 | -0.18956 | 0.014341 | -0.21323 | 0.21617 | 0.076355 | 0.062014 | 0.007258 | -0.044484 | 121.7914 | 121.5753 | 121.4794 | 4.0122 | -121.6085 | 121.4558 | 121.6763 | 121.6245 | 10.0597 | -121.6547
1955.1875 | 121.7743 | -0.30212 | 121.344 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062776 | 0.015438 | 0.058214 | -0.17751 | 3.7147 | -0.28311 | 121.4527 | 121.2594 | 121.1682 | -0.27369 | -0.10884 | 9.7072 | -0.24866 | 121.1216 | 121.3513 | 121.2995 | -0.31067 | 0.028436 | 0.10867 | 0.12461 | 0.019018 | -0.009418 | -0.084555 | -0.17583 | -0.008547 | -0.22239 | 0.19328 | 0.053467 | 0.062014 | 0.007258 | -0.044484 | 121.7548 | 121.5616 | 121.4703 | 4.0168 | -121.6177 | 121.4237 | 121.6534 | 121.6016 | 10.0093 | -121.6547
1956.9062 | 121.8018 | -0.31128 | 121.3348 | 1.4211e-13 | -0.029354 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | -8.1262e-05 | 0.00037167 | 0.062776 | 0.015438 | 0.058214 | -0.18667 | 3.6963 | -0.28768 | 121.4572 | 121.2411 | 121.159 | -0.26911 | -0.11342 | 9.7072 | -0.24866 | 121.1262 | 121.3421 | 121.2949 | -0.31525 | 0.04217 | 0.1224 | 0.12461 | 0.023595 | -0.018575 | -0.093716 | -0.17583 | -0.003971 | -0.20865 | 0.19786 | 0.062622 | 0.066593 | 0.007256 | -0.039908 | 121.7685 | 121.5524 | 121.4703 | 4.0076 | -121.6039 | 121.4375 | 121.6534 | 121.6062 | 10.0185 | -121.6501
1958.6875 | 121.6873 | -0.35248 | 121.3486 | 1.4211e-13 | -0.029568 | -0.0013783 | 0.062675 | -0.0052006 | 0.056255 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.015652 | 0.058428 | -0.18209 | 3.6963 | -0.28768 | 121.4527 | 121.2411 | 121.1544 | -0.27369 | -0.11342 | 9.6752 | -0.24408 | 121.1216 | 121.3467 | 121.2858 | -0.31067 | 0.07879 | 0.10409 | 0.17039 | 0.064794 | -0.013996 | -0.10745 | -0.19414 | 0.041807 | -0.22697 | 0.23906 | 0.1084 | 0.066593 | -0.001899 | -0.062798 | 121.8051 | 121.5936 | 121.5069 | 4.0488 | -121.6223 | 121.4741 | 121.6992 | 121.6383 | 10.0277 | -121.6592
1960.4531 | 121.7377 | -0.33875 | 121.3211 | 1.4211e-13 | -0.029782 | -0.0020193 | 0.062889 | -0.0054142 | 0.056042 | -0.0022889 | 0.00013254 | 0.00015807 | 0.06299 | 0.015438 | 0.058 | -0.18209 | 3.7009 | -0.29226 | 121.4572 | 121.2411 | 121.1499 | -0.27827 | -0.118 | 9.6614 | -0.24866 | 121.1216 | 121.3513 | 121.2949 | -0.31983 | 0.060478 | 0.13613 | 0.15666 | 0.046482 | -0.013996 | -0.079983 | -0.17125 | 0.018916 | -0.1995 | 0.22075 | 0.090088 | 0.071172 | 0.030146 | -0.026175 | 121.796 | 121.5799 | 121.4886 | 4.0397 | -121.5994 | 121.4604 | 121.69 | 121.6337 | 10.0002 | -121.6409
1962.25 | 121.6782 | -0.35706 | 121.3623 | 1.4211e-13 | -0.029782 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | -0.00029486 | 0.00015807 | 0.062776 | 0.015652 | 0.058214 | -0.18667 | 3.7192 | -0.29226 | 121.4527 | 121.2457 | 121.1544 | -0.27827 | -0.118 | 9.6752 | -0.24866 | 121.1262 | 121.3421 | 121.2858 | -0.31067 | 0.078789 | 0.090355 | 0.17039 | 0.064793 | -0.013996 | -0.1166 | -0.20787 | 0.046385 | -0.23612 | 0.23906 | 0.1084 | 0.062014 | -0.02021 | -0.076531 | 121.8097 | 121.6028 | 121.5115 | 4.0763 | -121.6406 | 121.4832 | 121.6992 | 121.6428 | 10.0322 | -121.673
1964.0156 | 121.7468 | -0.33875 | 121.3303 | 1.4211e-13 | -0.029782 | -0.0018055 | 0.062462 | -0.005628 | 0.056255 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.015438 | 0.058214 | -0.2004 | 3.7238 | -0.30142 | 121.4481 | 121.2365 | 121.1407 | -0.27369 | -0.12258 | 9.6935 | -0.24866 | 121.1124 | 121.3375 | 121.2904 | -0.31983 | 0.065057 | 0.11782 | 0.13834 | 0.037326 | -0.027731 | -0.093717 | -0.18957 | 0.018916 | -0.21781 | 0.21617 | 0.090088 | 0.071172 | 0.007255 | -0.039908 | 121.7868 | 121.5753 | 121.4794 | 4.0626 | -121.6039 | 121.4512 | 121.6763 | 121.6291 | 10.0322 | -121.6501
1965.7188 | 121.6507 | -0.37079 | 121.3623 | 1.4211e-13 | -0.029568 | -0.0018055 | 0.062462 | -0.0060552 | 0.056255 | -0.0099194 | 0.00034614 | -0.00026913 | 0.062776 | 0.015438 | 0.058214 | -0.19124 | 3.7147 | -0.30142 | 121.4481 | 121.232 | 121.1407 | -0.27827 | -0.12258 | 9.6477 | -0.25324 | 121.1079 | 121.3375 | 121.2904 | -0.32441 | 0.092522 | 0.085777 | 0.17954 | 0.06937 | -0.023152 | -0.13034 | -0.22161 | 0.046382 | -0.25443 | 0.24821 | 0.11755 | 0.071171 | -0.024789 | -0.071952 | 121.8189 | 121.6028 | 121.5115 | 4.0854 | -121.6406 | 121.4787 | 121.7083 | 121.6611 | 10.0185 | -121.6867
1967.4844 | 121.6919 | -0.38452 | 121.344 | 1.4211e-13 | -0.029568 | -0.0015919 | 0.062675 | -0.0058416 | 0.056255 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015652 | 0.058214 | -0.2004 | 3.7192 | -0.31058 | 121.4435 | 121.2274 | 121.1361 | -0.292 | -0.13173 | 9.6523 | -0.27155 | 121.1033 | 121.3284 | 121.2675 | -0.33357 | 0.092517 | 0.099509 | 0.18412 | 0.073945 | -0.018572 | -0.11661 | -0.20788 | 0.050956 | -0.2407 | 0.25279 | 0.11297 | 0.062015 | -0.015635 | -0.076534 | 121.828 | 121.6119 | 121.5206 | 4.1038 | -121.636 | 121.4878 | 121.7129 | 121.652 | 10.0368 | -121.6776
1969.2812 | 121.7606 | -0.33417 | 121.2936 | 1.4211e-13 | -0.029568 | -0.0015919 | 0.062675 | -0.0058416 | 0.056042 | -0.0099194 | -0.00050846 | -0.00048293 | 0.062349 | 0.015652 | 0.057573 | -0.20498 | 3.7101 | -0.306 | 121.4435 | 121.2228 | 121.1361 | -0.28285 | -0.12716 | 9.6523 | -0.26697 | 121.1079 | 121.3329 | 121.2766 | -0.32899 | 0.051321 | 0.14986 | 0.12919 | 0.028169 | -0.023152 | -0.070833 | -0.15752 | 0.005181 | -0.18577 | 0.20701 | 0.067195 | 0.062014 | 0.039297 | -0.017023 | 121.7777 | 121.557 | 121.4703 | 4.0442 | -121.5765 | 121.442 | 121.6671 | 121.6108 | 9.9864 | -121.6226
1971.0625 | 121.701 | -0.35706 | 121.3715 | 1.4211e-13 | -0.029354 | -0.0018055 | 0.062462 | -0.005628 | 0.056255 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.015224 | 0.058 | -0.20498 | 3.6826 | -0.306 | 121.4389 | 121.2274 | 121.1361 | -0.28285 | -0.12258 | 9.666 | -0.26239 | 121.1033 | 121.3284 | 121.2766 | -0.33814 | 0.07421 | 0.067465 | 0.15208 | 0.051058 | -0.023152 | -0.14407 | -0.23534 | 0.018912 | -0.26817 | 0.23448 | 0.094663 | 0.075751 | -0.043101 | -0.094843 | 121.796 | 121.5844 | 121.4932 | 4.0397 | -121.6543 | 121.4603 | 121.6854 | 121.6337 | 10.0231 | -121.7096
1972.7812 | 121.6873 | -0.35248 | 121.344 | 1.4211e-13 | -0.029568 | -0.0013783 | 0.062462 | -0.005628 | 0.056042 | -0.0022889 | -0.00029486 | -0.00026913 | 0.062776 | 0.015438 | 0.058428 | -0.2004 | 3.6963 | -0.30142 | 121.4343 | 121.2365 | 121.1453 | -0.28285 | -0.12258 | 9.6248 | -0.25781 | 121.1033 | 121.3284 | 121.2812 | -0.32899 | 0.069632 | 0.090353 | 0.15208 | 0.051059 | -0.018573 | -0.10745 | -0.19872 | 0.023492 | -0.2407 | 0.2299 | 0.094664 | 0.071172 | -0.015635 | -0.062798 | 121.7868 | 121.589 | 121.4978 | 4.0488 | -121.6268 | 121.4558 | 121.6808 | 121.6337 | 9.9773 | -121.673
1974.5469 | 121.6827 | -0.36163 | 121.3394 | 1.4211e-13 | -0.029782 | -0.0015919 | 0.062675 | -0.0054142 | 0.056042 | 0.012972 | -8.1262e-05 | -0.00048293 | 0.062776 | 0.015438 | 0.057787 | -0.20498 | 3.6963 | -0.30142 | 121.4481 | 121.232 | 121.1453 | -0.27827 | -0.118 | 9.5882 | -0.25781 | 121.1124 | 121.3375 | 121.272 | -0.32441 | 0.083366 | 0.10867 | 0.15665 | 0.060214 | -0.023152 | -0.10745 | -0.19414 | 0.037226 | -0.22697 | 0.24363 | 0.10382 | 0.066593 | -0.001901 | -0.067379 | 121.8097 | 121.5936 | 121.5069 | 4.058 | -121.6177 | 121.4741 | 121.6991 | 121.6337 | 9.9498 | -121.6638
1976.3281 | 121.7285 | -0.33875 | 121.3211 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062462 | -0.005628 | 0.056255 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.015652 | 0.058 | -0.19582 | 3.7009 | -0.29684 | 121.4343 | 121.2274 | 121.1361 | -0.28285 | -0.11342 | 9.5378 | -0.25781 | 121.117 | 121.3421 | 121.2812 | -0.31983 | 0.055899 | 0.11324 | 0.14292 | 0.041904 | -0.013995 | -0.09372 | -0.18499 | 0.018916 | -0.20408 | 0.22532 | 0.080931 | 0.062015 | 0.020989 | -0.03991 | 121.7731 | 121.5661 | 121.4749 | 4.0397 | -121.604 | 121.4558 | 121.6808 | 121.6199 | 9.8766 | -121.6409
1978.0938 | 121.6919 | -0.37994 | 121.3623 | 1.4211e-13 | -0.029782 | -0.0018055 | 0.062248 | -0.0058416 | 0.056042 | -0.0022889 | 0.00034614 | -0.00026913 | 0.062776 | 0.015865 | 0.058 | -0.19582 | 3.7009 | -0.30142 | 121.4481 | 121.2274 | 121.1499 | -0.292 | -0.11342 | 9.5241 | -0.25781 | 121.1124 | 121.3421 | 121.2858 | -0.33357 | 0.08794 | 0.085777 | 0.18412 | 0.078525 | -0.009415 | -0.13492 | -0.21245 | 0.046379 | -0.24986 | 0.26652 | 0.12213 | 0.075751 | -0.02021 | -0.076531 | 121.828 | 121.6073 | 121.5298 | 4.0809 | -121.6543 | 121.4924 | 121.722 | 121.6657 | 9.904 | -121.6959
1979.8125 | 121.6919 | -0.36621 | 121.3486 | 1.4211e-13 | -0.029782 | -0.0015919 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.063203 | 0.015652 | 0.057573 | -0.2004 | 3.7055 | -0.30142 | 121.4435 | 121.232 | 121.1453 | -0.28742 | -0.12258 | 9.5699 | -0.25781 | 121.1124 | 121.3375 | 121.2766 | -0.32441 | 0.078786 | 0.094931 | 0.16581 | 0.064792 | -0.013994 | -0.11661 | -0.2033 | 0.041804 | -0.23612 | 0.24363 | 0.1084 | 0.066593 | -0.011056 | -0.071955 | 121.8097 | 121.5982 | 121.5115 | 4.0717 | -121.636 | 121.4787 | 121.7037 | 121.6428 | 9.9361 | -121.673
1981.5312 | 121.7148 | -0.34332 | 121.3531 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062675 | -0.0058416 | 0.056255 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.015865 | 0.057787 | -0.19582 | 3.7101 | -0.30142 | 121.4435 | 121.2411 | 121.1453 | -0.28742 | -0.11342 | 9.5607 | -0.25781 | 121.1124 | 121.3375 | 121.2812 | -0.32441 | 0.055898 | 0.090354 | 0.1475 | 0.041904 | -0.013994 | -0.11203 | -0.20788 | 0.018916 | -0.2407 | 0.2299 | 0.085509 | 0.066593 | -0.015633 | -0.071953 | 121.7868 | 121.5844 | 121.4886 | 4.0534 | -121.6406 | 121.4558 | 121.6808 | 121.6245 | 9.904 | -121.6776
1983.2969 | 121.7194 | -0.35706 | 121.3394 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062248 | -0.005628 | 0.056255 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.015438 | 0.058 | -0.20498 | 3.7009 | -0.30142 | 121.4481 | 121.232 | 121.1453 | -0.28285 | -0.11342 | 9.5515 | -0.25324 | 121.1079 | 121.3329 | 121.2858 | -0.32441 | 0.07421 | 0.10867 | 0.15208 | 0.055637 | -0.018573 | -0.10745 | -0.19414 | 0.032649 | -0.23155 | 0.24364 | 0.10382 | 0.071171 | -0.00648 | -0.053643 | 121.8051 | 121.589 | 121.5023 | 4.058 | -121.6223 | 121.4649 | 121.69 | 121.6428 | 9.9086 | -121.6638
1985.0625 | 121.8018 | -0.32044 | 121.2982 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062675 | -0.005628 | 0.056469 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.015438 | 0.057787 | -0.19582 | 3.7147 | -0.30142 | 121.4389 | 121.232 | 121.1407 | -0.28285 | -0.118 | 9.5287 | -0.25781 | 121.1079 | 121.3329 | 121.2812 | -0.32441 | 0.037589 | 0.14071 | 0.12461 | 0.019016 | -0.018573 | -0.066253 | -0.15752 | -0.003972 | -0.19035 | 0.20244 | 0.062621 | 0.066593 | 0.034719 | -0.017022 | 121.7594 | 121.5524 | 121.4611 | 4.0351 | -121.5811 | 121.4283 | 121.6534 | 121.6016 | 9.8491 | -121.6226
1986.8438 | 121.8109 | -0.32044 | 121.3074 | 1.4211e-13 | -0.029782 | -0.0015919 | 0.062675 | -0.005628 | 0.056042 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.015652 | 0.058 | -0.2004 | 3.733 | -0.30142 | 121.4343 | 121.2274 | 121.1453 | -0.27369 | -0.118 | 9.5699 | -0.25781 | 121.117 | 121.3329 | 121.272 | -0.33357 | 0.046747 | 0.12697 | 0.12003 | 0.019016 | -0.027731 | -0.079987 | -0.1621 | -0.01313 | -0.19034 | 0.20244 | 0.062621 | 0.075751 | 0.025564 | -0.035335 | 121.7548 | 121.5478 | 121.4657 | 4.0534 | -121.5811 | 121.4375 | 121.6534 | 121.5925 | 9.8903 | -121.6409
1988.5312 | 121.6736 | -0.39368 | 121.312 | 1.4211e-13 | -0.029782 | -0.0015919 | 0.062462 | -0.0058416 | 0.055828 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.015438 | 0.057573 | -0.19582 | 3.7192 | -0.29684 | 121.4481 | 121.232 | 121.1361 | -0.28285 | -0.11342 | 9.5103 | -0.25781 | 121.1124 | 121.3329 | 121.2812 | -0.33357 | 0.11083 | 0.13613 | 0.19785 | 0.096836 | -0.013995 | -0.079986 | -0.17583 | 0.060112 | -0.1995 | 0.28026 | 0.13586 | 0.075751 | 0.020986 | -0.030755 | 121.8418 | 121.6256 | 121.5298 | 4.1129 | -121.5948 | 121.5061 | 121.7266 | 121.6749 | 9.904 | -121.6455
1990.3125 | 121.6827 | -0.36163 | 121.344 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062675 | -0.005628 | 0.056469 | 0.0053411 | 0.00013254 | 0.00015807 | 0.06299 | 0.015652 | 0.057787 | -0.2004 | 3.7101 | -0.29684 | 121.4435 | 121.2274 | 121.1407 | -0.28742 | -0.11342 | 9.5058 | -0.25781 | 121.1124 | 121.3329 | 121.2858 | -0.32899 | 0.074208 | 0.099509 | 0.16123 | 0.064792 | -0.009416 | -0.11661 | -0.2033 | 0.032647 | -0.23154 | 0.24821 | 0.10382 | 0.071172 | -0.011057 | -0.05822 | 121.8051 | 121.589 | 121.5023 | 4.0717 | -121.6314 | 121.4741 | 121.6946 | 121.6474 | 9.8674 | -121.673
1992.0312 | 121.7468 | -0.33875 | 121.3257 | 1.4211e-13 | -0.030209 | -0.0020193 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | 0.00013254 | -0.00026913 | 0.06299 | 0.016079 | 0.057573 | -0.19582 | 3.7284 | -0.306 | 121.4389 | 121.2228 | 121.1361 | -0.28285 | -0.11342 | 9.5195 | -0.25781 | 121.1033 | 121.3284 | 121.272 | -0.32899 | 0.055899 | 0.11324 | 0.14292 | 0.032747 | -0.023152 | -0.10288 | -0.18957 | 0.009759 | -0.22239 | 0.22532 | 0.080931 | 0.071172 | 0.002675 | -0.053646 | 121.7777 | 121.5616 | 121.4749 | 4.0671 | -121.6085 | 121.442 | 121.6671 | 121.6108 | 9.8582 | -121.6547
1993.8125 | 121.669 | -0.36621 | 121.3348 | 1.4211e-13 | -0.029782 | -0.0018055 | 0.062675 | -0.0060552 | 0.056469 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.015652 | 0.058214 | -0.2004 | 3.7284 | -0.29226 | 121.4435 | 121.2365 | 121.1499 | -0.28742 | -0.118 | 9.5103 | -0.26239 | 121.117 | 121.3375 | 121.2812 | -0.32899 | 0.078786 | 0.10866 | 0.16581 | 0.073948 | -0.004838 | -0.098295 | -0.18499 | 0.037225 | -0.21781 | 0.24821 | 0.10382 | 0.066593 | 0.002677 | -0.053643 | 121.8097 | 121.6028 | 121.5161 | 4.0946 | -121.6223 | 121.4832 | 121.7037 | 121.6474 | 9.8765 | -121.6638
1995.5156 | 121.7194 | -0.3479 | 121.3074 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062675 | -0.0058416 | 0.056255 | 0.0053411 | 0.00013254 | 0.00037167 | 0.062776 | 0.015865 | 0.058 | -0.19124 | 3.7238 | -0.29684 | 121.4527 | 121.2365 | 121.1453 | -0.28285 | -0.10884 | 9.4417 | -0.25781 | 121.117 | 121.3375 | 121.2766 | -0.32441 | 0.065054 | 0.14529 | 0.15665 | 0.051059 | -0.013995 | -0.070829 | -0.1621 | 0.023493 | -0.19034 | 0.23906 | 0.090086 | 0.066593 | 0.030143 | -0.030756 | 121.8006 | 121.5844 | 121.4932 | 4.0717 | -121.5902 | 121.4649 | 121.6854 | 121.6245 | 9.7896 | -121.6318
1997.2812 | 121.7743 | -0.33417 | 121.3028 | 1.4211e-13 | -0.029996 | -0.0020193 | 0.062248 | -0.0058416 | 0.056469 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062776 | 0.015438 | 0.057787 | -0.20498 | 3.733 | -0.29684 | 121.4435 | 121.2274 | 121.1361 | -0.28285 | -0.10884 | 9.4279 | -0.25781 | 121.117 | 121.3421 | 121.272 | -0.33357 | 0.051321 | 0.14071 | 0.12919 | 0.037326 | -0.013995 | -0.075409 | -0.16668 | 0.000602 | -0.18577 | 0.22533 | 0.076353 | 0.075751 | 0.0393 | -0.030757 | 121.7777 | 121.5616 | 121.4703 | 4.0671 | -121.5856 | 121.4512 | 121.6763 | 121.6062 | 9.7621 | -121.6364
1999.0625 | 121.7468 | -0.33417 | 121.2936 | 1.4211e-13 | -0.030423 | -0.0020193 | 0.062462 | -0.0058416 | 0.056255 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.015652 | 0.058 | -0.2004 | 3.7375 | -0.29684 | 121.4389 | 121.232 | 121.1361 | -0.28742 | -0.11342 | 9.4371 | -0.25324 | 121.117 | 121.3375 | 121.2675 | -0.33357 | 0.046742 | 0.14529 | 0.13376 | 0.037326 | -0.009416 | -0.061675 | -0.15752 | 0.000602 | -0.17661 | 0.22075 | 0.080931 | 0.080329 | 0.043876 | -0.02618 | 121.7731 | 121.5661 | 121.4703 | 4.0717 | -121.5811 | 121.4512 | 121.6717 | 121.6016 | 9.7712 | -121.6272
2000.8438 | 121.756 | -0.33875 | 121.3531 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062462 | -0.0054142 | 0.056255 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.016079 | 0.057787 | -0.19582 | 3.7192 | -0.31515 | 121.4435 | 121.2228 | 121.1407 | -0.28285 | -0.10426 | 9.4646 | -0.25324 | 121.1079 | 121.3375 | 121.2766 | -0.32899 | 0.055899 | 0.090354 | 0.14292 | 0.023591 | -0.032308 | -0.13034 | -0.21245 | 0.009759 | -0.24528 | 0.23448 | 0.085509 | 0.07575 | -0.015633 | -0.076532 | 121.7822 | 121.5616 | 121.4794 | 4.058 | -121.636 | 121.4466 | 121.6763 | 121.6154 | 9.8033 | -121.6821
2002.6094 | 121.7789 | -0.35248 | 121.3257 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062675 | -0.0058416 | 0.056255 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057787 | -0.2004 | 3.733 | -0.30142 | 121.4343 | 121.232 | 121.1499 | -0.28285 | -0.10884 | 9.4874 | -0.24866 | 121.1079 | 121.3329 | 121.2766 | -0.32441 | 0.069632 | 0.10866 | 0.15208 | 0.051059 | -0.018573 | -0.093719 | -0.17583 | 0.028071 | -0.21781 | 0.24364 | 0.10382 | 0.07575 | 0.007253 | -0.049067 | 121.7868 | 121.5844 | 121.5023 | 4.0854 | -121.6085 | 121.4603 | 121.6854 | 121.6291 | 9.8399 | -121.6501
2004.375 | 121.6644 | -0.36621 | 121.3303 | 1.4211e-13 | -0.030209 | -0.0018055 | 0.062462 | -0.0058416 | 0.056469 | -0.0099194 | 0.00013254 | -0.00048293 | 0.062776 | 0.015652 | 0.057573 | -0.2004 | 3.7284 | -0.31515 | 121.4481 | 121.232 | 121.1407 | -0.27827 | -0.10426 | 9.4325 | -0.25324 | 121.1124 | 121.3329 | 121.2812 | -0.32441 | 0.087944 | 0.11782 | 0.16581 | 0.051057 | -0.036887 | -0.098296 | -0.18957 | 0.041804 | -0.21781 | 0.26195 | 0.11297 | 0.071171 | 0.002676 | -0.049065 | 121.8143 | 121.5982 | 121.5069 | 4.0946 | -121.6085 | 121.4787 | 121.6991 | 121.6474 | 9.7987 | -121.6547
2006.1719 | 121.6644 | -0.37994 | 121.3394 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062675 | -0.0058416 | 0.056255 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.06299 | 0.015652 | 0.058 | -0.2004 | 3.7238 | -0.29684 | 121.4389 | 121.2274 | 121.1407 | -0.28742 | -0.10426 | 9.3455 | -0.25324 | 121.1124 | 121.3284 | 121.2766 | -0.32899 | 0.092519 | 0.099508 | 0.17954 | 0.083103 | -0.009416 | -0.11203 | -0.19872 | 0.050958 | -0.22697 | 0.27568 | 0.12671 | 0.07575 | -0.011058 | -0.0628 | 121.8189 | 121.6073 | 121.5206 | 4.1038 | -121.6268 | 121.4924 | 121.7083 | 121.6566 | 9.7255 | -121.6684
2007.8906 | 121.7789 | -0.33875 | 121.3211 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062248 | -0.0060552 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.015438 | 0.057573 | -0.2004 | 3.7421 | -0.29226 | 121.4343 | 121.2274 | 121.1453 | -0.28285 | -0.10426 | 9.373 | -0.25781 | 121.1033 | 121.3375 | 121.2766 | -0.32441 | 0.055899 | 0.11324 | 0.13834 | 0.046482 | -0.009417 | -0.09372 | -0.17583 | 0.014338 | -0.21781 | 0.23448 | 0.080931 | 0.066593 | 0.01641 | -0.044489 | 121.7731 | 121.5661 | 121.484 | 4.0809 | -121.604 | 121.442 | 121.6763 | 121.6154 | 9.7117 | -121.6455
2009.6562 | 121.7651 | -0.34332 | 121.312 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062462 | -0.0058416 | 0.056255 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057787 | -0.19582 | 3.7238 | -0.306 | 121.4298 | 121.2274 | 121.1315 | -0.28285 | -0.10426 | 9.373 | -0.25781 | 121.1033 | 121.3329 | 121.2766 | -0.33814 | 0.060477 | 0.11782 | 0.1475 | 0.037325 | -0.023152 | -0.084565 | -0.18041 | 0.005179 | -0.20866 | 0.23906 | 0.085509 | 0.08033 | 0.020986 | -0.035334 | 121.7731 | 121.5707 | 121.4749 | 4.0671 | -121.5948 | 121.4466 | 121.6763 | 121.6199 | 9.7163 | -121.6501
2011.4219 | 121.6644 | -0.38452 | 121.3257 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062462 | -0.0060552 | 0.056255 | -0.0099194 | -8.1262e-05 | -0.00026913 | 0.062776 | 0.015652 | 0.057787 | -0.20498 | 3.7284 | -0.31515 | 121.4298 | 121.2228 | 121.1361 | -0.29658 | -0.118 | 9.3409 | -0.26239 | 121.0987 | 121.3238 | 121.2675 | -0.33814 | 0.087939 | 0.10408 | 0.17954 | 0.069367 | -0.018572 | -0.10288 | -0.18957 | 0.046377 | -0.22697 | 0.26652 | 0.12213 | 0.075751 | -0.001904 | -0.058224 | 121.8143 | 121.6073 | 121.5206 | 4.1129 | -121.6223 | 121.4832 | 121.7083 | 121.652 | 9.7254 | -121.6638
2013.2188 | 121.7422 | -0.35248 | 121.2891 | 1.4211e-13 | -0.030637 | -0.0015919 | 0.062462 | -0.0054142 | 0.056042 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057787 | -0.20498 | 3.7147 | -0.306 | 121.4298 | 121.2136 | 121.1407 | -0.28285 | -0.10884 | 9.3409 | -0.25781 | 121.0987 | 121.3329 | 121.2675 | -0.33357 | 0.069632 | 0.14071 | 0.1475 | 0.04648 | -0.023152 | -0.075413 | -0.14837 | 0.018913 | -0.19035 | 0.24364 | 0.094664 | 0.075751 | 0.043875 | -0.021602 | 121.7822 | 121.5661 | 121.4932 | 4.0671 | -121.5719 | 121.4512 | 121.6854 | 121.6199 | 9.6934 | -121.6226
2014.9219 | 121.7331 | -0.32959 | 121.3165 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062675 | -0.0058416 | 0.056469 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015865 | 0.057573 | -0.20498 | 3.7284 | -0.306 | 121.4298 | 121.2228 | 121.1315 | -0.28742 | -0.10426 | 9.2814 | -0.25324 | 121.0987 | 121.3375 | 121.2675 | -0.34272 | 0.042165 | 0.11324 | 0.12461 | 0.023592 | -0.018573 | -0.093721 | -0.18499 | -0.013133 | -0.21781 | 0.22533 | 0.076354 | 0.089487 | 0.020988 | -0.049068 | 121.7594 | 121.5524 | 121.4611 | 4.058 | -121.604 | 121.4283 | 121.6671 | 121.597 | 9.611 | -121.6593
2016.6875 | 121.788 | -0.32501 | 121.2891 | 1.4211e-13 | -0.030423 | -0.0015919 | 0.062675 | -0.0054142 | 0.056255 | -0.0022889 | -0.00029486 | 0.00037167 | 0.062349 | 0.015865 | 0.057573 | -0.20498 | 3.7375 | -0.306 | 121.4343 | 121.2182 | 121.1178 | -0.29658 | -0.10884 | 9.2677 | -0.26239 | 121.0987 | 121.3329 | 121.2629 | -0.3473 | 0.02843 | 0.14529 | 0.12003 | 0.019014 | -0.009416 | -0.070834 | -0.17126 | -0.022289 | -0.19035 | 0.21617 | 0.062619 | 0.084908 | 0.043875 | -0.026181 | 121.7594 | 121.5432 | 121.4428 | 4.0626 | -121.5856 | 121.4237 | 121.6579 | 121.5879 | 9.5927 | -121.6364
2018.4531 | 121.6553 | -0.37537 | 121.3074 | 1.4211e-13 | -0.029782 | -0.0015919 | 0.062462 | -0.0060552 | 0.056255 | -0.01755 | -0.00050846 | 0.00015807 | 0.062776 | 0.016079 | 0.057573 | -0.2004 | 3.7467 | -0.29684 | 121.4343 | 121.2228 | 121.1315 | -0.28742 | -0.10884 | 9.286 | -0.25324 | 121.1033 | 121.3375 | 121.2675 | -0.33814 | 0.087941 | 0.12697 | 0.17496 | 0.078525 | -0.009416 | -0.084566 | -0.17583 | 0.037222 | -0.20408 | 0.26653 | 0.12213 | 0.084908 | 0.030143 | -0.039913 | 121.8097 | 121.5982 | 121.5069 | 4.1221 | -121.5948 | 121.4787 | 121.7129 | 121.6428 | 9.6613 | -121.6455
2020.2344 | 121.6324 | -0.37994 | 121.3074 | 1.4211e-13 | -0.029996 | -0.0015919 | 0.062675 | -0.0058416 | 0.056683 | -0.0099194 | 0.00013254 | -0.00026913 | 0.062776 | 0.015865 | 0.057787 | -0.2004 | 3.7559 | -0.306 | 121.4389 | 121.2182 | 121.1361 | -0.28742 | -0.10426 | 9.2722 | -0.25324 | 121.1033 | 121.3284 | 121.272 | -0.33357 | 0.092519 | 0.13155 | 0.17954 | 0.073946 | -0.018573 | -0.089145 | -0.17126 | 0.046379 | -0.20408 | 0.27568 | 0.12671 | 0.080329 | 0.020986 | -0.035335 | 121.8189 | 121.5982 | 121.5161 | 4.1358 | -121.5948 | 121.4832 | 121.7083 | 121.652 | 9.6522 | -121.6409
2021.9375 | 121.7194 | -0.33875 | 121.3303 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.015652 | 0.057787 | -0.20498 | 3.7467 | -0.31058 | 121.4298 | 121.2274 | 121.1361 | -0.28742 | -0.099684 | 9.2219 | -0.25324 | 121.1124 | 121.3375 | 121.2766 | -0.34272 | 0.05132 | 0.099507 | 0.13377 | 0.028169 | -0.023151 | -0.10287 | -0.19414 | -0.003978 | -0.21781 | 0.23906 | 0.085509 | 0.089487 | 0.007255 | -0.053644 | 121.7685 | 121.5661 | 121.4749 | 4.0854 | -121.6177 | 121.4512 | 121.6763 | 121.6154 | 9.5606 | -121.673
2023.7188 | 121.7743 | -0.32501 | 121.3303 | 1.4211e-13 | -0.030423 | -0.0020193 | 0.062675 | -0.005628 | 0.056469 | -0.0099194 | -0.00029486 | -0.00026913 | 0.062776 | 0.015865 | 0.058 | -0.20498 | 3.7513 | -0.306 | 121.4298 | 121.2228 | 121.1361 | -0.28285 | -0.095105 | 9.1395 | -0.24866 | 121.1079 | 121.3375 | 121.2629 | -0.32441 | 0.042166 | 0.099507 | 0.12003 | 0.019014 | -0.023152 | -0.10745 | -0.19414 | 0.000605 | -0.22239 | 0.22991 | 0.076355 | 0.07575 | 0.007255 | -0.06738 | 121.7548 | 121.5478 | 121.4611 | 4.0763 | -121.6131 | 121.4329 | 121.6625 | 121.5879 | 9.4645 | -121.6547
2025.4844 | 121.788 | -0.32501 | 121.2845 | 1.4211e-13 | -0.030209 | -0.0022329 | 0.062889 | -0.005628 | 0.056469 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.015652 | 0.057787 | -0.20498 | 3.7513 | -0.31058 | 121.4343 | 121.2274 | 121.1407 | -0.28285 | -0.090527 | 9.1669 | -0.24866 | 121.1079 | 121.3284 | 121.2675 | -0.33357 | 0.042166 | 0.14986 | 0.12003 | 0.014436 | -0.02773 | -0.057099 | -0.14379 | -0.008553 | -0.17661 | 0.23449 | 0.076355 | 0.084908 | 0.043874 | -0.017025 | 121.7594 | 121.5524 | 121.4657 | 4.0763 | -121.5673 | 121.4329 | 121.6534 | 121.5925 | 9.4919 | -121.618
2027.2812 | 121.7331 | -0.34332 | 121.3074 | 1.4211e-13 | -0.030423 | -0.0015919 | 0.062675 | -0.0060552 | 0.056255 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.016079 | 0.057787 | -0.2004 | 3.765 | -0.31058 | 121.4298 | 121.2182 | 121.1361 | -0.292 | -0.099684 | 9.1532 | -0.24866 | 121.1033 | 121.3329 | 121.2629 | -0.33814 | 0.051319 | 0.12239 | 0.14292 | 0.032747 | -0.018572 | -0.089145 | -0.17126 | 0.005179 | -0.20408 | 0.24364 | 0.094666 | 0.089487 | 0.025564 | -0.044492 | 121.7731 | 121.5616 | 121.4794 | 4.1083 | -121.5994 | 121.4466 | 121.6763 | 121.6062 | 9.4965 | -121.6455
2028.9844 | 121.7789 | -0.3479 | 121.2799 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062248 | -0.0058416 | 0.056469 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057787 | -0.21414 | 3.7604 | -0.31515 | 121.4252 | 121.2182 | 121.127 | -0.292 | -0.095105 | 9.1486 | -0.25781 | 121.0941 | 121.3284 | 121.2537 | -0.3473 | 0.055896 | 0.14528 | 0.13376 | 0.032746 | -0.02315 | -0.061679 | -0.15295 | 0.000599 | -0.18577 | 0.25279 | 0.090086 | 0.089487 | 0.048452 | -0.026183 | 121.7731 | 121.5661 | 121.4749 | 4.1083 | -121.5719 | 121.442 | 121.6763 | 121.6016 | 9.4965 | -121.6272
2030.7656 | 121.6415 | -0.40283 | 121.3257 | 1.4211e-13 | -0.030637 | -0.0013783 | 0.062462 | -0.0058416 | 0.056255 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.015865 | 0.057146 | -0.20956 | 3.7467 | -0.31973 | 121.4206 | 121.1999 | 121.1178 | -0.28742 | -0.10884 | 9.0891 | -0.25781 | 121.0941 | 121.3146 | 121.2583 | -0.3473 | 0.11541 | 0.094927 | 0.19327 | 0.0831 | -0.032307 | -0.12577 | -0.20788 | 0.055531 | -0.23155 | 0.29399 | 0.14502 | 0.089487 | -0.011061 | -0.067381 | 121.8234 | 121.6027 | 121.5206 | 4.1495 | -121.6131 | 121.497 | 121.7175 | 121.6611 | 9.4919 | -121.673
2032.4844 | 121.7651 | -0.33875 | 121.2753 | 1.4211e-13 | -0.030423 | -0.0020193 | 0.062462 | -0.006269 | 0.056042 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057787 | -0.21871 | 3.7513 | -0.31973 | 121.4069 | 121.2045 | 121.1178 | -0.30574 | -0.10884 | 9.0937 | -0.27155 | 121.0896 | 121.31 | 121.2537 | -0.35188 | 0.033005 | 0.13155 | 0.12003 | 0.019013 | -0.013992 | -0.070838 | -0.15753 | -0.013135 | -0.18577 | 0.2299 | 0.067195 | 0.08033 | 0.034714 | -0.021606 | 121.7456 | 121.5432 | 121.4565 | 4.09 | -121.5811 | 121.4283 | 121.6488 | 121.5925 | 9.4324 | -121.6272
2034.2656 | 121.6965 | -0.39825 | 121.3165 | 1.4211e-13 | -0.030209 | -0.0018055 | 0.062675 | -0.0058416 | 0.056255 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057573 | -0.22787 | 3.7788 | -0.32889 | 121.4069 | 121.1908 | 121.1178 | -0.31032 | -0.11342 | 9.1028 | -0.27155 | 121.0804 | 121.3055 | 121.2491 | -0.35646 | 0.087935 | 0.090348 | 0.17038 | 0.069365 | -0.01857 | -0.12577 | -0.19873 | 0.041795 | -0.23613 | 0.28483 | 0.1267 | 0.084909 | -0.011062 | -0.067383 | 121.8051 | 121.589 | 121.5161 | 4.177 | -121.6268 | 121.4787 | 121.7037 | 121.6474 | 9.5011 | -121.673
2036.0469 | 121.6324 | -0.43488 | 121.312 | 1.4211e-13 | -0.030423 | -0.0015919 | 0.062462 | -0.0060552 | 0.056683 | -0.0099194 | -0.00029486 | 0.00015807 | 0.062563 | 0.015865 | 0.057573 | -0.23703 | 3.7788 | -0.34262 | 121.3931 | 121.1862 | 121.1041 | -0.31948 | -0.12258 | 9.0937 | -0.28529 | 121.0667 | 121.2917 | 121.2354 | -0.36562 | 0.1154 | 0.08119 | 0.19785 | 0.092251 | -0.023147 | -0.12577 | -0.20788 | 0.069258 | -0.24529 | 0.3123 | 0.14959 | 0.08033 | -0.020221 | -0.076541 | 121.828 | 121.6211 | 121.5389 | 4.2136 | -121.6314 | 121.5015 | 121.7266 | 121.6703 | 9.5286 | -121.6776
2037.8281 | 121.7148 | -0.41199 | 121.2433 | 1.4211e-13 | -0.030209 | -0.0018055 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.016079 | 0.057787 | -0.25534 | 3.7925 | -0.36551 | 121.3702 | 121.1633 | 121.0812 | -0.33779 | -0.14089 | 9.0387 | -0.29902 | 121.0438 | 121.2734 | 121.2034 | -0.38851 | 0.074194 | 0.12696 | 0.15664 | 0.046472 | -0.027722 | -0.080005 | -0.16211 | 0.023476 | -0.19951 | 0.27109 | 0.11296 | 0.089488 | 0.03013 | -0.039927 | 121.7822 | 121.5753 | 121.4932 | 4.2045 | -121.5811 | 121.4558 | 121.6854 | 121.6153 | 9.4507 | -121.6318
2039.5312 | 121.7285 | -0.3891 | 121.2753 | 1.4211e-13 | -0.030209 | -0.0020193 | 0.062675 | -0.0058416 | 0.056255 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015865 | 0.058 | -0.23703 | 3.7696 | -0.34262 | 121.3977 | 121.1862 | 121.1086 | -0.31032 | -0.10884 | 9.0708 | -0.27613 | 121.0712 | 121.3055 | 121.2446 | -0.3702 | 0.07878 | 0.12239 | 0.15207 | 0.046475 | -0.032305 | -0.089154 | -0.16669 | 0.018903 | -0.20409 | 0.28026 | 0.11297 | 0.094067 | 0.030136 | -0.030763 | 121.7868 | 121.5753 | 121.4977 | 4.1587 | -121.5856 | 121.4603 | 121.6946 | 121.6337 | 9.4599 | -121.6455
2041.2969 | 121.7331 | -0.31128 | 121.3028 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062675 | -0.0060552 | 0.056042 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057359 | -0.19582 | 3.7833 | -0.29684 | 121.4389 | 121.2274 | 121.1407 | -0.28742 | -0.07679 | 9.0616 | -0.2395 | 121.1033 | 121.3329 | 121.272 | -0.33357 | 0.023854 | 0.13613 | 0.11546 | 0.014438 | -0.009416 | -0.075409 | -0.1621 | -0.022286 | -0.1995 | 0.23449 | 0.07178 | 0.094066 | 0.030142 | -0.030757 | 121.7502 | 121.5387 | 121.452 | 4.0946 | -121.5902 | 121.4146 | 121.6442 | 121.5833 | 9.3729 | -121.6364
2043.0938 | 121.6507 | -0.37537 | 121.3577 | 1.4211e-13 | -0.030423 | -0.0020193 | 0.062675 | -0.0058416 | 0.056255 | -0.0022889 | -0.00029486 | 0.00015807 | 0.062563 | 0.016293 | 0.057787 | -0.2004 | 3.7833 | -0.306 | 121.4298 | 121.2136 | 121.127 | -0.28742 | -0.07679 | 9.0342 | -0.24866 | 121.0987 | 121.3284 | 121.2583 | -0.33814 | 0.087941 | 0.072041 | 0.17496 | 0.069368 | -0.018573 | -0.14408 | -0.23077 | 0.037222 | -0.25901 | 0.29858 | 0.12671 | 0.089487 | -0.029368 | -0.099424 | 121.8051 | 121.589 | 121.5023 | 4.1587 | -121.6452 | 121.4741 | 121.7037 | 121.6337 | 9.4095 | -121.6959
2044.8594 | 121.6553 | -0.37537 | 121.3348 | 1.4211e-13 | -0.030423 | -0.0015919 | 0.062675 | -0.005628 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.015865 | 0.057787 | -0.20956 | 3.7559 | -0.29684 | 121.4252 | 121.2182 | 121.1361 | -0.28742 | -0.081369 | 8.9884 | -0.2395 | 121.1033 | 121.3192 | 121.2537 | -0.33814 | 0.087941 | 0.090351 | 0.16581 | 0.078525 | -0.009416 | -0.11661 | -0.19872 | 0.037222 | -0.23155 | 0.294 | 0.13587 | 0.098645 | -0.015637 | -0.081115 | 121.8006 | 121.5936 | 121.5115 | 4.1312 | -121.6223 | 121.4787 | 121.6946 | 121.6291 | 9.3637 | -121.673
2046.625 | 121.756 | -0.32501 | 121.3074 | 1.4211e-13 | -0.03085 | -0.0020193 | 0.062462 | -0.0054142 | 0.056042 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.015865 | 0.057787 | -0.20956 | 3.7925 | -0.31515 | 121.4206 | 121.2091 | 121.1224 | -0.292 | -0.085948 | 8.9655 | -0.25781 | 121.0941 | 121.3238 | 121.2537 | -0.33814 | 0.033008 | 0.11324 | 0.11545 | 0.009858 | -0.02315 | -0.098302 | -0.18499 | -0.013132 | -0.21324 | 0.23906 | 0.067198 | 0.08033 | 0.016407 | -0.053649 | 121.7456 | 121.5341 | 121.4474 | 4.1175 | -121.5994 | 121.4191 | 121.6488 | 121.5787 | 9.2905 | -121.6455
2048.3438 | 121.6507 | -0.38452 | 121.3074 | 1.4211e-13 | -0.030423 | -0.0015919 | 0.062675 | -0.0058416 | 0.056042 | 0.0053411 | 0.00013254 | -0.00026913 | 0.062563 | 0.016079 | 0.057787 | -0.20956 | 3.7971 | -0.31515 | 121.416 | 121.2045 | 121.1224 | -0.29658 | -0.085948 | 8.9655 | -0.24866 | 121.0941 | 121.3192 | 121.2537 | -0.3473 | 0.087939 | 0.10866 | 0.17496 | 0.069367 | -0.018572 | -0.10288 | -0.18499 | 0.03722 | -0.21324 | 0.29857 | 0.13586 | 0.098644 | 0.011829 | -0.053649 | 121.8006 | 121.589 | 121.5069 | 4.1816 | -121.604 | 121.4787 | 121.7037 | 121.6382 | 9.35 | -121.6547
2050.125 | 121.669 | -0.37994 | 121.312 | 1.4211e-13 | -0.030209 | -0.0020193 | 0.062675 | -0.005628 | 0.056255 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.016293 | 0.057573 | -0.21414 | 3.7971 | -0.31973 | 121.4115 | 121.1953 | 121.1178 | -0.30574 | -0.081369 | 8.9334 | -0.25781 | 121.0896 | 121.31 | 121.2537 | -0.3473 | 0.074204 | 0.099504 | 0.16581 | 0.060212 | -0.013992 | -0.11662 | -0.19415 | 0.032643 | -0.22239 | 0.29858 | 0.12213 | 0.089487 | -0.001907 | -0.058227 | 121.7914 | 121.5753 | 121.4977 | 4.177 | -121.6177 | 121.4695 | 121.69 | 121.6337 | 9.3134 | -121.6593
2051.9062 | 121.7468 | -0.37079 | 121.2982 | 1.4211e-13 | -0.030423 | -0.0018055 | 0.062462 | -0.0060552 | 0.056255 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.015865 | 0.057359 | -0.22329 | 3.7971 | -0.32889 | 121.4069 | 121.1953 | 121.1041 | -0.31032 | -0.10426 | 8.9243 | -0.25781 | 121.0712 | 121.3055 | 121.24 | -0.35646 | 0.06047 | 0.10866 | 0.1475 | 0.0419 | -0.01857 | -0.10288 | -0.19415 | 0.01433 | -0.22698 | 0.26653 | 0.11297 | 0.098645 | 0.007248 | -0.05823 | 121.7777 | 121.5661 | 121.4749 | 4.1679 | -121.6085 | 121.442 | 121.6763 | 121.6108 | 9.2951 | -121.6547
2053.6875 | 121.701 | -0.40283 | 121.2479 | 1.4211e-13 | -0.029996 | -0.0018055 | 0.062462 | -0.0058416 | 0.055828 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.062563 | 0.016293 | 0.057146 | -0.23245 | 3.7925 | -0.34262 | 121.3931 | 121.1862 | 121.0949 | -0.32406 | -0.10426 | 8.8739 | -0.27613 | 121.0621 | 121.2826 | 121.2308 | -0.36562 | 0.078776 | 0.14528 | 0.17038 | 0.060208 | -0.018568 | -0.061688 | -0.15296 | 0.037215 | -0.18578 | 0.29857 | 0.1267 | 0.089488 | 0.034709 | -0.017033 | 121.796 | 121.589 | 121.4977 | 4.1953 | -121.5719 | 121.4649 | 121.6854 | 121.6337 | 9.2767 | -121.6135
2055.4531 | 121.756 | -0.37537 | 121.2753 | 1.4211e-13 | -0.030209 | -0.0015919 | 0.062462 | -0.005628 | 0.056042 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.016079 | 0.057573 | -0.24161 | 3.7742 | -0.34262 | 121.384 | 121.1724 | 121.0903 | -0.31948 | -0.10884 | 8.8144 | -0.27155 | 121.0575 | 121.2963 | 121.2217 | -0.37477 | 0.055889 | 0.10865 | 0.13376 | 0.032742 | -0.023147 | -0.10289 | -0.185 | 0.000592 | -0.21782 | 0.26653 | 0.10382 | 0.10322 | 0.020979 | -0.053656 | 121.7593 | 121.5478 | 121.4657 | 4.1495 | -121.5948 | 121.4329 | 121.6717 | 121.597 | 9.1897 | -121.6501
2057.1719 | 121.7651 | -0.37994 | 121.2204 | 1.4211e-13 | -0.030637 | -0.0015919 | 0.062889 | -0.0060552 | 0.055828 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.015865 | 0.057787 | -0.25534 | 3.7696 | -0.35178 | 121.3702 | 121.1679 | 121.0766 | -0.32864 | -0.12258 | 8.8098 | -0.28986 | 121.0438 | 121.2643 | 121.2125 | -0.38393 | 0.051309 | 0.14985 | 0.1246 | 0.028164 | -0.023145 | -0.052538 | -0.1438 | -0.003988 | -0.17663 | 0.25737 | 0.090079 | 0.094067 | 0.04386 | -0.007881 | 121.7502 | 121.5478 | 121.4565 | 4.1495 | -121.549 | 121.4237 | 121.6442 | 121.5925 | 9.1897 | -121.6043
2058.9375 | 121.6278 | -0.44861 | 121.2845 | 1.4211e-13 | -0.030637 | -0.0013783 | 0.062248 | -0.0052006 | 0.056255 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062349 | 0.016293 | 0.057787 | -0.27366 | 3.7788 | -0.36094 | 121.3565 | 121.145 | 121.0766 | -0.34695 | -0.13173 | 8.7823 | -0.3036 | 121.0255 | 121.2551 | 121.2034 | -0.39767 | 0.10166 | 0.072029 | 0.17495 | 0.087671 | -0.013986 | -0.13952 | -0.20789 | 0.05094 | -0.25903 | 0.31687 | 0.14501 | 0.094067 | -0.029384 | -0.081126 | 121.8051 | 121.5936 | 121.5252 | 4.2274 | -121.6314 | 121.4741 | 121.7037 | 121.652 | 9.2309 | -121.6822
2060.6406 | 121.6736 | -0.4715 | 121.2479 | 1.4211e-13 | -0.03085 | -0.0013783 | 0.062675 | -0.005628 | 0.056469 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.016079 | 0.057359 | -0.28281 | 3.7742 | -0.39756 | 121.3336 | 121.1266 | 121.04 | -0.37442 | -0.15463 | 8.764 | -0.32649 | 121.0026 | 121.2368 | 121.1759 | -0.42056 | 0.097073 | 0.085758 | 0.18868 | 0.073934 | -0.023139 | -0.12121 | -0.2079 | 0.050934 | -0.2453 | 0.31687 | 0.145 | 0.094068 | -0.011077 | -0.071976 | 121.8051 | 121.5981 | 121.5115 | 4.2457 | -121.6223 | 121.4741 | 121.7083 | 121.6474 | 9.2355 | -121.6684
2062.4062 | 121.6324 | -0.4715 | 121.2296 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062462 | -0.0060552 | 0.056469 | -0.0099194 | 0.00034614 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057573 | -0.29197 | 3.7879 | -0.39756 | 121.3336 | 121.1221 | 121.0308 | -0.37442 | -0.15463 | 8.7686 | -0.33107 | 120.9934 | 121.2368 | 121.1622 | -0.42514 | 0.097073 | 0.10407 | 0.17953 | 0.073934 | -0.023139 | -0.10748 | -0.19875 | 0.046356 | -0.23614 | 0.31687 | 0.14042 | 0.094067 | 0.007234 | -0.067401 | 121.8051 | 121.5936 | 121.5023 | 4.2594 | -121.604 | 121.4649 | 121.7083 | 121.6336 | 9.2401 | -121.6547
2064.125 | 121.7697 | -0.42572 | 121.1838 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062462 | -0.0060552 | 0.056255 | 0.0053411 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.016293 | 0.057573 | -0.28739 | 3.7788 | -0.38841 | 121.3336 | 121.1175 | 121.04 | -0.37442 | -0.15005 | 8.6907 | -0.32649 | 120.998 | 121.2322 | 121.1713 | -0.42514 | 0.051296 | 0.14984 | 0.13833 | 0.037313 | -0.013983 | -0.066285 | -0.14381 | 0.000579 | -0.18579 | 0.27567 | 0.099225 | 0.098646 | 0.048431 | -0.012468 | 121.7593 | 121.5432 | 121.4657 | 4.2045 | -121.5582 | 121.4237 | 121.6579 | 121.597 | 9.1165 | -121.6089
2065.9062 | 121.7468 | -0.4303 | 121.1975 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062675 | -0.005628 | 0.055614 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057359 | -0.28281 | 3.7925 | -0.38841 | 121.3336 | 121.1175 | 121.0445 | -0.36984 | -0.15005 | 8.6679 | -0.31734 | 121.0071 | 121.2322 | 121.1759 | -0.42056 | 0.060453 | 0.13611 | 0.14749 | 0.041891 | -0.018562 | -0.080018 | -0.15297 | 0.009735 | -0.19037 | 0.28025 | 0.11296 | 0.10323 | 0.034698 | -0.021622 | 121.7639 | 121.5478 | 121.4748 | 4.2228 | -121.5674 | 121.4374 | 121.6625 | 121.6062 | 9.0982 | -121.6181
2067.6875 | 121.6599 | -0.4303 | 121.2112 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062889 | -0.0058416 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057573 | -0.29197 | 3.7879 | -0.39756 | 121.3245 | 121.1175 | 121.04 | -0.36527 | -0.15005 | 8.645 | -0.32649 | 120.9934 | 121.2322 | 121.1622 | -0.41141 | 0.065032 | 0.11322 | 0.13833 | 0.032735 | -0.032297 | -0.093751 | -0.17128 | 0.018893 | -0.21783 | 0.28025 | 0.1038 | 0.08491 | 0.020965 | -0.049091 | 121.7548 | 121.5478 | 121.4703 | 4.2182 | -121.5765 | 121.4237 | 121.6625 | 121.5924 | 9.0753 | -121.6226
2069.4531 | 121.7468 | -0.4303 | 121.1792 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062462 | -0.0058416 | 0.056255 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016079 | 0.057573 | -0.27823 | 3.8016 | -0.39756 | 121.3199 | 121.1175 | 121.0308 | -0.37442 | -0.14089 | 8.6221 | -0.33107 | 120.998 | 121.2185 | 121.1576 | -0.42056 | 0.055874 | 0.14069 | 0.15206 | 0.032735 | -0.023139 | -0.061707 | -0.14839 | 0.009735 | -0.18121 | 0.28941 | 0.099224 | 0.089489 | 0.039273 | -0.021626 | 121.7502 | 121.5478 | 121.4611 | 4.2319 | -121.5536 | 121.4283 | 121.6488 | 121.5879 | 9.0524 | -121.5998
2071.2344 | 121.7697 | -0.43488 | 121.1746 | 1.4211e-13 | -0.030637 | -0.0020193 | 0.062462 | -0.005628 | 0.056042 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.016293 | 0.057573 | -0.29655 | 3.8016 | -0.40214 | 121.3199 | 121.1129 | 121.0262 | -0.37442 | -0.14547 | 8.6038 | -0.33565 | 120.9888 | 121.2231 | 121.1576 | -0.4343 | 0.060451 | 0.14526 | 0.13833 | 0.032733 | -0.027718 | -0.061709 | -0.14839 | 0.000576 | -0.18579 | 0.2894 | 0.099223 | 0.098647 | 0.048429 | -0.017049 | 121.7548 | 121.5478 | 121.4611 | 4.2365 | -121.549 | 121.4237 | 121.6579 | 121.5924 | 9.0386 | -121.6089
2072.9375 | 121.6827 | -0.46692 | 121.2021 | 1.4211e-13 | -0.030637 | -0.0020193 | 0.062462 | -0.0060552 | 0.056469 | 0.0053411 | 0.00013254 | 0.00015807 | 0.062776 | 0.015865 | 0.057573 | -0.29655 | 3.7879 | -0.40672 | 121.3153 | 121.1083 | 121.0171 | -0.37442 | -0.15463 | 8.6083 | -0.33565 | 120.9843 | 121.2139 | 121.1576 | -0.4343 | 0.092495 | 0.11322 | 0.17037 | 0.060199 | -0.032296 | -0.093753 | -0.18502 | 0.03262 | -0.21784 | 0.31229 | 0.13127 | 0.098647 | 0.011807 | -0.044514 | 121.7822 | 121.5753 | 121.484 | 4.2548 | -121.5765 | 121.4512 | 121.6808 | 121.6245 | 9.0753 | -121.6364
2074.7188 | 121.6324 | -0.46692 | 121.2296 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062462 | -0.0058416 | 0.056896 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057359 | -0.31028 | 3.8016 | -0.4113 | 121.3107 | 121.1038 | 121.0217 | -0.38358 | -0.15921 | 8.6175 | -0.33107 | 120.9797 | 121.2093 | 121.153 | -0.4343 | 0.083337 | 0.081177 | 0.15664 | 0.055621 | -0.027716 | -0.1258 | -0.2079 | 0.03262 | -0.24988 | 0.30771 | 0.13584 | 0.10323 | -0.020238 | -0.076558 | 121.7776 | 121.5707 | 121.4886 | 4.2686 | -121.6131 | 121.4466 | 121.6762 | 121.6199 | 9.0844 | -121.6639
2076.4844 | 121.7972 | -0.43488 | 121.1929 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062462 | -0.0058416 | 0.056042 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.016293 | 0.057573 | -0.3057 | 3.7971 | -0.4113 | 121.3062 | 121.1083 | 121.0125 | -0.38358 | -0.15463 | 8.59 | -0.33565 | 120.9751 | 121.2139 | 121.1438 | -0.44804 | 0.051293 | 0.11322 | 0.12917 | 0.023577 | -0.027716 | -0.084598 | -0.18044 | -0.01316 | -0.21784 | 0.28025 | 0.099223 | 0.11238 | 0.020962 | -0.049095 | 121.741 | 121.5432 | 121.4474 | 4.2319 | -121.5765 | 121.41 | 121.6488 | 121.5787 | 9.0249 | -121.641
2078.2812 | 121.6782 | -0.4715 | 121.2296 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062675 | -0.0058416 | 0.056042 | 0.0053411 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.016293 | 0.057573 | -0.3057 | 3.7879 | -0.4113 | 121.3062 | 121.1038 | 121.0079 | -0.38816 | -0.15921 | 8.5305 | -0.34023 | 120.9751 | 121.2093 | 121.1438 | -0.43888 | 0.083336 | 0.076599 | 0.16579 | 0.060199 | -0.023137 | -0.1258 | -0.22164 | 0.032619 | -0.25446 | 0.31229 | 0.13127 | 0.098647 | -0.020238 | -0.085716 | 121.7776 | 121.5753 | 121.4794 | 4.2594 | -121.6177 | 121.4466 | 121.6808 | 121.6153 | 9.002 | -121.6684
2079.9844 | 121.7148 | -0.43488 | 121.2021 | 1.4211e-13 | -0.031064 | -0.0020193 | 0.062462 | -0.005628 | 0.056042 | -0.01755 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.016293 | 0.057787 | -0.28739 | 3.7971 | -0.39756 | 121.3245 | 121.1221 | 121.0262 | -0.37442 | -0.13631 | 8.4893 | -0.32192 | 120.9843 | 121.2231 | 121.1622 | -0.42056 | 0.060451 | 0.12238 | 0.14748 | 0.037312 | -0.023139 | -0.080016 | -0.17586 | 0.014312 | -0.21784 | 0.29856 | 0.11296 | 0.098647 | 0.020964 | -0.039935 | 121.7593 | 121.5569 | 121.4611 | 4.2319 | -121.5765 | 121.4191 | 121.6579 | 121.597 | 8.9242 | -121.6227
2081.7656 | 121.6919 | -0.45776 | 121.2158 | 1.4211e-13 | -0.030637 | -0.0024467 | 0.062248 | -0.005628 | 0.056255 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.015865 | 0.057573 | -0.29197 | 3.7833 | -0.40214 | 121.3062 | 121.1083 | 121.0262 | -0.36984 | -0.14089 | 8.4435 | -0.32649 | 120.9888 | 121.2139 | 121.153 | -0.42514 | 0.087919 | 0.090332 | 0.1658 | 0.055622 | -0.032297 | -0.10749 | -0.18959 | 0.032623 | -0.22699 | 0.31687 | 0.13127 | 0.098646 | -0.001926 | -0.062825 | 121.7639 | 121.5661 | 121.484 | 4.2411 | -121.5857 | 121.4466 | 121.6717 | 121.6108 | 8.9013 | -121.641
2083.5469 | 121.7239 | -0.43488 | 121.1746 | 1.4211e-13 | -0.031064 | -0.0020193 | 0.062675 | -0.0060552 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016079 | 0.057573 | -0.3057 | 3.765 | -0.4113 | 121.3107 | 121.1083 | 121.0125 | -0.379 | -0.14089 | 8.384 | -0.33565 | 120.9843 | 121.2002 | 121.1347 | -0.4343 | 0.055872 | 0.13611 | 0.12917 | 0.023577 | -0.032295 | -0.066288 | -0.16213 | 0.000576 | -0.19037 | 0.29398 | 0.099223 | 0.098647 | 0.025536 | -0.039942 | 121.7456 | 121.5432 | 121.4474 | 4.1999 | -121.5536 | 121.4191 | 121.635 | 121.5696 | 8.8189 | -121.6089
2085.25 | 121.6553 | -0.46234 | 121.1792 | 1.4211e-13 | -0.030637 | -0.0020193 | 0.062675 | -0.0060552 | 0.056255 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016079 | 0.057359 | -0.3057 | 3.7604 | -0.41588 | 121.3016 | 121.1038 | 121.0125 | -0.38358 | -0.15005 | 8.3702 | -0.34023 | 120.9659 | 121.2002 | 121.1393 | -0.43888 | 0.078759 | 0.12237 | 0.15664 | 0.046465 | -0.032294 | -0.075444 | -0.1667 | 0.023463 | -0.21326 | 0.31229 | 0.12211 | 0.098647 | 0.020959 | -0.03994 | 121.7639 | 121.5661 | 121.4748 | 4.2228 | -121.5628 | 121.4283 | 121.6625 | 121.6016 | 8.8326 | -121.6181
2087.0312 | 121.7422 | -0.4303 | 121.1517 | 1.4211e-13 | -0.030637 | -0.0020193 | 0.062248 | -0.0060552 | 0.056042 | -0.01755 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.016293 | 0.057573 | -0.31944 | 3.7879 | -0.41588 | 121.2924 | 121.0854 | 121.0033 | -0.39274 | -0.15463 | 8.3886 | -0.33565 | 120.9614 | 121.191 | 121.1301 | -0.44804 | 0.037558 | 0.14068 | 0.11086 | 0.014422 | -0.023136 | -0.066293 | -0.1484 | -0.017737 | -0.19037 | 0.27567 | 0.094646 | 0.11238 | 0.039268 | -0.021631 | 121.7227 | 121.5157 | 121.4336 | 4.2182 | -121.5445 | 121.3917 | 121.6213 | 121.5604 | 8.8189 | -121.5998
2088.7969 | 121.7422 | -0.43488 | 121.17 | 1.4211e-13 | -0.03085 | -0.0020193 | 0.062248 | -0.0058416 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.016506 | 0.057787 | -0.31944 | 3.8016 | -0.43877 | 121.2924 | 121.0763 | 120.9896 | -0.39732 | -0.15921 | 8.3199 | -0.34481 | 120.9568 | 121.1864 | 121.1255 | -0.46177 | 0.037556 | 0.12237 | 0.11544 | -0.003893 | -0.041449 | -0.093762 | -0.18044 | -0.026897 | -0.21326 | 0.27567 | 0.090065 | 0.11696 | 0.016378 | -0.044521 | 121.7273 | 121.5112 | 121.4245 | 4.2365 | -121.5674 | 121.3917 | 121.6213 | 121.5604 | 8.7547 | -121.6318
2090.5 | 121.756 | -0.45776 | 121.1884 | 1.4211e-13 | -0.03085 | -0.0020193 | 0.062462 | -0.005628 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016506 | 0.057146 | -0.32402 | 3.7879 | -0.42503 | 121.2787 | 121.0763 | 120.9988 | -0.40648 | -0.15921 | 8.3199 | -0.34939 | 120.9522 | 121.1818 | 121.1255 | -0.45719 | 0.051287 | 0.090327 | 0.13375 | 0.032731 | -0.018556 | -0.11207 | -0.1896 | 0.000571 | -0.23615 | 0.29856 | 0.10837 | 0.1078 | -0.00651 | -0.062831 | 121.7364 | 121.534 | 121.4565 | 4.2457 | -121.5948 | 121.41 | 121.6396 | 121.5833 | 8.7776 | -121.6455
2092.2812 | 121.7606 | -0.42572 | 121.17 | 1.4211e-13 | -0.031064 | -0.0020193 | 0.062462 | -0.0058416 | 0.056255 | 0.0053411 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.01672 | 0.057573 | -0.31028 | 3.7833 | -0.41588 | 121.2924 | 121.0854 | 121.0079 | -0.38816 | -0.13631 | 8.297 | -0.33565 | 120.9659 | 121.2047 | 121.1347 | -0.43888 | 0.037559 | 0.12237 | 0.11544 | 0.009844 | -0.027715 | -0.084604 | -0.16213 | -0.013158 | -0.20411 | 0.28941 | 0.090068 | 0.10323 | 0.034693 | -0.035364 | 121.7181 | 121.5112 | 121.4336 | 4.2091 | -121.5582 | 121.3917 | 121.6305 | 121.5604 | 8.7227 | -121.6089
2094.0625 | 121.6415 | -0.46234 | 121.1929 | 1.4211e-13 | -0.031064 | -0.0022329 | 0.062248 | -0.0060552 | 0.056469 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062349 | 0.016293 | 0.057359 | -0.31028 | 3.7833 | -0.4113 | 121.2924 | 121.09 | 120.9988 | -0.38816 | -0.13631 | 8.2237 | -0.32192 | 120.9614 | 121.1956 | 121.1301 | -0.43888 | 0.07418 | 0.099485 | 0.15206 | 0.051043 | -0.023137 | -0.10291 | -0.19417 | 0.023463 | -0.23157 | 0.32603 | 0.14043 | 0.11696 | 0.002647 | -0.06283 | 121.7548 | 121.5524 | 121.4611 | 4.2457 | -121.5811 | 121.4237 | 121.6579 | 121.5924 | 8.6861 | -121.6318
2095.8438 | 121.7056 | -0.45319 | 121.1563 | 1.4211e-13 | -0.03085 | -0.0018055 | 0.062462 | -0.0060552 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016506 | 0.057573 | -0.31944 | 3.7788 | -0.42503 | 121.2924 | 121.0854 | 120.9942 | -0.38816 | -0.14089 | 8.1962 | -0.33565 | 120.9522 | 121.191 | 121.1301 | -0.43888 | 0.065025 | 0.13611 | 0.13375 | 0.028153 | -0.036872 | -0.070871 | -0.16213 | 0.014308 | -0.20411 | 0.31229 | 0.11753 | 0.10323 | 0.03469 | -0.026209 | 121.7456 | 121.5386 | 121.4474 | 4.2319 | -121.5445 | 121.4054 | 121.6442 | 121.5833 | 8.6494 | -121.5952
2097.5469 | 121.6324 | -0.50354 | 121.2021 | 1.4211e-13 | -0.031064 | -0.0020193 | 0.062675 | -0.0058416 | 0.056042 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062776 | 0.016506 | 0.057359 | -0.31028 | 3.7971 | -0.41588 | 121.2878 | 121.0763 | 120.9942 | -0.4019 | -0.15005 | 8.1871 | -0.33565 | 120.9522 | 121.191 | 121.1164 | -0.44346 | 0.10164 | 0.085751 | 0.19326 | 0.087664 | -0.013978 | -0.1258 | -0.20791 | 0.060083 | -0.24989 | 0.35349 | 0.16789 | 0.1078 | -0.011086 | -0.085721 | 121.7914 | 121.5798 | 121.4977 | 4.3006 | -121.604 | 121.4557 | 121.6945 | 121.6199 | 8.6906 | -121.6455
2099.3281 | 121.6141 | -0.50812 | 121.1929 | 1.4211e-13 | -0.031064 | -0.0015919 | 0.062462 | -0.0060552 | 0.056255 | -0.0022889 | 0.00013254 | -0.00026913 | 0.06299 | 0.016293 | 0.057359 | -0.31944 | 3.7971 | -0.42961 | 121.2787 | 121.0717 | 120.985 | -0.4019 | -0.15463 | 8.1321 | -0.34481 | 120.943 | 121.1773 | 121.1118 | -0.45719 | 0.10622 | 0.085749 | 0.18868 | 0.078507 | -0.027713 | -0.12123 | -0.20791 | 0.050925 | -0.24989 | 0.35349 | 0.16331 | 0.11238 | -0.015667 | -0.081145 | 121.7868 | 121.5798 | 121.4931 | 4.3052 | -121.5948 | 121.4512 | 121.6854 | 121.6199 | 8.6403 | -121.6501
2101.1094 | 121.6461 | -0.48523 | 121.1929 | 1.4211e-13 | -0.030637 | -0.0018055 | 0.062462 | -0.006269 | 0.056255 | -0.0022889 | -8.1262e-05 | 0.00058547 | 0.062563 | 0.016506 | 0.057573 | -0.31944 | 3.8062 | -0.42503 | 121.2787 | 121.0671 | 120.985 | -0.40648 | -0.14547 | 8.123 | -0.34481 | 120.943 | 121.1727 | 121.1072 | -0.45261 | 0.078752 | 0.085749 | 0.16579 | 0.060196 | -0.018556 | -0.12581 | -0.20791 | 0.032615 | -0.24989 | 0.33976 | 0.14042 | 0.1078 | -0.020246 | -0.085723 | 121.7639 | 121.5524 | 121.4703 | 4.2915 | -121.5994 | 121.4283 | 121.6579 | 121.5924 | 8.6082 | -121.6455
2102.8906 | 121.6003 | -0.53558 | 121.1792 | 1.4211e-13 | -0.03085 | -0.0018055 | 0.062462 | -0.0060552 | 0.056255 | 0.0053411 | 0.00013254 | 0.00015807 | 0.062563 | 0.016079 | 0.057359 | -0.33317 | 3.8016 | -0.44335 | 121.2695 | 121.058 | 120.985 | -0.40648 | -0.15463 | 8.1505 | -0.35397 | 120.9293 | 121.1681 | 121.1072 | -0.47093 | 0.12911 | 0.090326 | 0.20241 | 0.092237 | -0.036869 | -0.12123 | -0.19418 | 0.064653 | -0.24989 | 0.38095 | 0.18162 | 0.11696 | -0.011091 | -0.07199 | 121.8051 | 121.5935 | 121.5206 | 4.3372 | -121.5857 | 121.4649 | 121.7037 | 121.6428 | 8.686 | -121.6501
2104.5938 | 121.637 | -0.50354 | 121.1563 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062675 | -0.0058416 | 0.056042 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.06299 | 0.016293 | 0.056932 | -0.34233 | 3.7971 | -0.44335 | 121.2604 | 121.0488 | 120.9713 | -0.42021 | -0.15921 | 8.0909 | -0.35397 | 120.9339 | 121.1544 | 121.0981 | -0.48009 | 0.083327 | 0.10406 | 0.16121 | 0.060194 | -0.023133 | -0.1075 | -0.18502 | 0.023453 | -0.22242 | 0.34433 | 0.14957 | 0.12612 | -0.001939 | -0.05826 | 121.7639 | 121.5523 | 121.4748 | 4.3006 | -121.5765 | 121.4374 | 121.6579 | 121.6016 | 8.5945 | -121.6364
2106.3125 | 121.7194 | -0.48065 | 121.1563 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062462 | -0.005628 | 0.056042 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016293 | 0.057573 | -0.33775 | 3.8108 | -0.44335 | 121.2558 | 121.0534 | 120.9667 | -0.42479 | -0.16379 | 8.036 | -0.35397 | 120.9202 | 121.1544 | 121.0935 | -0.47551 | 0.05586 | 0.099479 | 0.1429 | 0.037306 | -0.018554 | -0.10292 | -0.1896 | 0.005144 | -0.23616 | 0.31687 | 0.12669 | 0.12154 | -0.001939 | -0.062838 | 121.7364 | 121.534 | 121.4474 | 4.2915 | -121.5811 | 121.4008 | 121.635 | 121.5741 | 8.5166 | -121.6318
2108.0938 | 121.6644 | -0.46692 | 121.2158 | 1.4211e-13 | -0.030637 | -0.0022329 | 0.062675 | -0.0058416 | 0.056042 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016293 | 0.057787 | -0.31944 | 3.82 | -0.42046 | 121.2695 | 121.0717 | 120.985 | -0.4019 | -0.13631 | 8.0131 | -0.34481 | 120.9476 | 121.1773 | 121.1118 | -0.45719 | 0.065021 | 0.053705 | 0.14748 | 0.046464 | -0.018557 | -0.14412 | -0.2308 | 0.009726 | -0.2682 | 0.3306 | 0.12211 | 0.11238 | -0.038555 | -0.10403 | 121.7364 | 121.5386 | 121.4519 | 4.2869 | -121.6177 | 121.4145 | 121.6442 | 121.5787 | 8.48 | -121.673
2109.875 | 121.7514 | -0.4715 | 121.138 | 1.4211e-13 | -0.03085 | -0.0020193 | 0.062462 | -0.0054142 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016293 | 0.057146 | -0.34233 | 3.8337 | -0.44335 | 121.2649 | 121.0534 | 120.9759 | -0.40648 | -0.15005 | 8.0223 | -0.34481 | 120.9293 | 121.1635 | 121.0935 | -0.47093 | 0.06502 | 0.12695 | 0.12916 | 0.028151 | -0.036869 | -0.084613 | -0.16214 | 0.000567 | -0.20869 | 0.32145 | 0.12669 | 0.12612 | 0.025529 | -0.044527 | 121.7364 | 121.5249 | 121.4474 | 4.3052 | -121.5445 | 121.4008 | 121.635 | 121.565 | 8.4938 | -121.6089
2111.5781 | 121.7377 | -0.49439 | 121.1243 | 1.4211e-13 | -0.03085 | -0.0020193 | 0.062462 | -0.005628 | 0.056255 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062349 | 0.016506 | 0.057146 | -0.34691 | 3.8383 | -0.44335 | 121.2558 | 121.0488 | 120.9576 | -0.42021 | -0.15005 | 7.9994 | -0.35855 | 120.9202 | 121.1452 | 121.0843 | -0.48467 | 0.074172 | 0.13152 | 0.14748 | 0.051039 | -0.023133 | -0.07546 | -0.16672 | 0.009719 | -0.20412 | 0.34434 | 0.13584 | 0.12612 | 0.020947 | -0.039952 | 121.7502 | 121.5432 | 121.4519 | 4.3327 | -121.5445 | 121.4145 | 121.6396 | 121.5787 | 8.4938 | -121.6089
2113.3594 | 121.701 | -0.49439 | 121.1334 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062462 | -0.0058416 | 0.055828 | -0.01755 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.016506 | 0.057146 | -0.35149 | 3.8383 | -0.4525 | 121.2421 | 121.0396 | 120.9484 | -0.42479 | -0.15463 | 7.9627 | -0.37228 | 120.911 | 121.1498 | 121.0797 | -0.48467 | 0.069593 | 0.10863 | 0.1429 | 0.041882 | -0.027711 | -0.093773 | -0.18503 | 0.009719 | -0.22243 | 0.33976 | 0.1221 | 0.11238 | 0.01637 | -0.053686 | 121.7364 | 121.534 | 121.4428 | 4.3327 | -121.5582 | 121.4054 | 121.6442 | 121.5741 | 8.4571 | -121.6181
2115.125 | 121.7468 | -0.48065 | 121.1014 | 1.4211e-13 | -0.031064 | -0.0015919 | 0.062462 | -0.0058416 | 0.056255 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.016506 | 0.057573 | -0.36064 | 3.8429 | -0.45708 | 121.2375 | 121.0305 | 120.9438 | -0.42937 | -0.15921 | 7.9078 | -0.3677 | 120.9064 | 121.1361 | 121.0797 | -0.48924 | 0.051281 | 0.1361 | 0.12001 | 0.023571 | -0.02771 | -0.070887 | -0.15756 | -0.008593 | -0.19496 | 0.32145 | 0.11295 | 0.12154 | 0.034679 | -0.021642 | 121.7181 | 121.5111 | 121.4245 | 4.3235 | -121.5307 | 121.3871 | 121.6167 | 121.5604 | 8.3884 | -121.5906
2116.8906 | 121.6141 | -0.53101 | 121.1197 | 1.4211e-13 | -0.031064 | -0.0015919 | 0.062034 | -0.005628 | 0.056469 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062776 | 0.016506 | 0.057146 | -0.3698 | 3.8474 | -0.46624 | 121.2237 | 121.0213 | 120.9392 | -0.43853 | -0.16379 | 7.8895 | -0.38144 | 120.8973 | 121.1315 | 121.0706 | -0.48924 | 0.092477 | 0.10405 | 0.1612 | 0.064769 | -0.027708 | -0.098355 | -0.18045 | 0.041761 | -0.22243 | 0.36722 | 0.14957 | 0.10781 | 0.011789 | -0.04911 | 121.7547 | 121.5523 | 121.4702 | 4.3784 | -121.5582 | 121.4283 | 121.6625 | 121.6016 | 8.4205 | -121.6089
2118.6562 | 121.701 | -0.53101 | 121.0922 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062034 | -0.0060552 | 0.056042 | -0.0099194 | -0.00029486 | -5.5534e-05 | 0.062776 | 0.016934 | 0.057359 | -0.37896 | 3.8245 | -0.48455 | 121.2008 | 120.9984 | 120.9118 | -0.46142 | -0.19126 | 7.8803 | -0.39518 | 120.8744 | 121.1086 | 121.0385 | -0.5213 | 0.069582 | 0.10863 | 0.15205 | 0.046455 | -0.023127 | -0.093784 | -0.18046 | 0.009709 | -0.21786 | 0.33975 | 0.13583 | 0.12612 | 0.016362 | -0.053694 | 121.7319 | 121.5294 | 121.4428 | 4.3555 | -121.5536 | 121.4054 | 121.6396 | 121.5695 | 8.4113 | -121.6135
2120.4219 | 121.6919 | -0.54474 | 121.0739 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062462 | -0.0058416 | 0.055828 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016506 | 0.057359 | -0.39269 | 3.852 | -0.49828 | 121.2054 | 120.9939 | 120.9118 | -0.46142 | -0.1821 | 7.8803 | -0.39975 | 120.8606 | 121.104 | 121.0431 | -0.5213 | 0.083315 | 0.13151 | 0.15204 | 0.046454 | -0.036861 | -0.080053 | -0.16215 | 0.023442 | -0.21328 | 0.36264 | 0.14498 | 0.12154 | 0.030093 | -0.030806 | 121.7502 | 121.5386 | 121.4565 | 4.3967 | -121.5353 | 121.4054 | 121.6487 | 121.5878 | 8.4251 | -121.5952
2122.125 | 121.6827 | -0.50812 | 121.0922 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062248 | -0.0060552 | 0.056255 | -0.0022889 | 0.00034614 | 0.00015807 | 0.06299 | 0.016293 | 0.057359 | -0.37438 | 3.8657 | -0.47082 | 121.2237 | 121.003 | 120.9255 | -0.44311 | -0.16379 | 7.8574 | -0.38602 | 120.8789 | 121.1223 | 121.0523 | -0.4984 | 0.06501 | 0.13152 | 0.13374 | 0.037302 | -0.027708 | -0.089205 | -0.16672 | 0.009716 | -0.21328 | 0.34433 | 0.1221 | 0.11238 | 0.030098 | -0.039959 | 121.7319 | 121.5111 | 121.4336 | 4.3739 | -121.5353 | 121.3871 | 121.6304 | 121.5604 | 8.3655 | -121.5906
2123.8906 | 121.7331 | -0.4715 | 121.0968 | 1.4211e-13 | -0.03085 | -0.0015919 | 0.062462 | -0.0058416 | 0.056255 | -0.0022889 | 0.00034614 | -0.00026913 | 0.062776 | 0.016934 | 0.057146 | -0.36522 | 3.8612 | -0.46624 | 121.2329 | 121.0122 | 120.9392 | -0.43853 | -0.15463 | 7.8162 | -0.37228 | 120.8973 | 121.1269 | 121.0568 | -0.4984 | 0.032968 | 0.1361 | 0.10627 | 0.00526 | -0.027708 | -0.084625 | -0.15757 | -0.026905 | -0.19954 | 0.31687 | 0.099215 | 0.12612 | 0.030098 | -0.039958 | 121.7044 | 121.4837 | 121.4107 | 4.3327 | -121.5353 | 121.3688 | 121.5984 | 121.5283 | 8.2877 | -121.5952
2125.6562 | 121.6324 | -0.50812 | 121.1243 | 1.4211e-13 | -0.031064 | -0.0015919 | 0.062462 | -0.0058416 | 0.056255 | -0.0022889 | -8.1262e-05 | -0.00026913 | 0.062563 | 0.016293 | 0.057359 | -0.34691 | 3.8612 | -0.4525 | 121.2329 | 121.0259 | 120.9347 | -0.42937 | -0.14547 | 7.7933 | -0.35397 | 120.8973 | 121.1406 | 121.066 | -0.48467 | 0.078747 | 0.10863 | 0.16121 | 0.055615 | -0.023132 | -0.098354 | -0.18961 | 0.023452 | -0.22701 | 0.36265 | 0.15415 | 0.1307 | 0.016368 | -0.058267 | 121.741 | 121.534 | 121.4428 | 4.3693 | -121.5536 | 121.4054 | 121.6488 | 121.5741 | 8.3014 | -121.6089
2127.3594 | 121.7377 | -0.48981 | 121.0968 | 1.4211e-13 | -0.030637 | -0.0022329 | 0.062462 | -0.0058416 | 0.056042 | 0.012972 | -8.1262e-05 | -0.00026913 | 0.062349 | 0.016506 | 0.057359 | -0.35149 | 3.8612 | -0.4525 | 121.2375 | 121.0351 | 120.9392 | -0.42937 | -0.13173 | 7.7887 | -0.35397 | 120.9018 | 121.1361 | 121.0706 | -0.47551 | 0.060436 | 0.14067 | 0.13832 | 0.037304 | -0.023132 | -0.061731 | -0.15757 | 0.014299 | -0.19496 | 0.35807 | 0.13584 | 0.12154 | 0.039256 | -0.026222 | 121.7273 | 121.5249 | 121.429 | 4.351 | -121.5262 | 121.3916 | 121.6259 | 121.5604 | 8.2786 | -121.5723
2129.1406 | 121.637 | -0.48065 | 121.1609 | 1.4211e-13 | -0.031064 | -0.0020193 | 0.062248 | -0.0058416 | 0.056042 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.01672 | 0.057359 | -0.33317 | 3.8657 | -0.43877 | 121.2466 | 121.0442 | 120.9621 | -0.40648 | -0.118 | 7.7613 | -0.33565 | 120.9156 | 121.159 | 121.0843 | -0.46635 | 0.074175 | 0.085744 | 0.14748 | 0.041884 | -0.032291 | -0.11666 | -0.19876 | 0.014301 | -0.24531 | 0.36265 | 0.145 | 0.1307 | -0.001938 | -0.076573 | 121.7273 | 121.5249 | 121.4428 | 4.3464 | -121.5674 | 121.3962 | 121.6396 | 121.565 | 8.2419 | -121.6272
2130.9219 | 121.6827 | -0.46234 | 121.106 | 1.4211e-13 | -0.031064 | -0.0015919 | 0.062248 | -0.0060552 | 0.055828 | -0.0099194 | 0.00034614 | 0.00015807 | 0.062563 | 0.01672 | 0.057359 | -0.33317 | 3.8932 | -0.43419 | 121.2512 | 121.0442 | 120.9576 | -0.41106 | -0.10884 | 7.7384 | -0.33565 | 120.9202 | 121.159 | 121.0797 | -0.46635 | 0.051285 | 0.14525 | 0.12917 | 0.028152 | -0.023133 | -0.061728 | -0.14841 | -0.00401 | -0.1858 | 0.3535 | 0.12669 | 0.1307 | 0.052994 | -0.02622 | 121.7136 | 121.5066 | 121.4199 | 4.3556 | -121.517 | 121.3825 | 121.6213 | 121.5421 | 8.2007 | -121.5723
2132.7031 | 121.7148 | -0.45319 | 121.0922 | 1.4211e-13 | -0.03085 | -0.0018055 | 0.062462 | -0.0058416 | 0.056042 | 0.0053411 | -8.1262e-05 | 0.00015807 | 0.062776 | 0.01672 | 0.057573 | -0.3286 | 3.8795 | -0.43419 | 121.2466 | 121.0442 | 120.9576 | -0.41106 | -0.10884 | 7.688 | -0.33565 | 120.911 | 121.1498 | 121.0752 | -0.47551 | 0.04213 | 0.15441 | 0.12459 | 0.018997 | -0.023133 | -0.047995 | -0.13467 | -0.022322 | -0.18123 | 0.34435 | 0.11753 | 0.13986 | 0.057569 | -0.017066 | 121.6998 | 121.4974 | 121.4107 | 4.3327 | -121.5033 | 121.3642 | 121.603 | 121.5283 | 8.1412 | -121.5677
2134.4219 | 121.6965 | -0.46692 | 121.106 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062248 | -0.0054142 | 0.056042 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016293 | 0.057359 | -0.33317 | 3.8795 | -0.43419 | 121.2512 | 121.0442 | 120.9621 | -0.40648 | -0.10884 | 7.6926 | -0.32192 | 120.9156 | 121.1498 | 121.0889 | -0.46635 | 0.060442 | 0.14525 | 0.13374 | 0.03273 | -0.027712 | -0.061728 | -0.14383 | 0.000568 | -0.19038 | 0.35808 | 0.145 | 0.14444 | 0.043836 | -0.017063 | 121.7181 | 121.5111 | 121.429 | 4.3464 | -121.5124 | 121.3825 | 121.6167 | 121.5558 | 8.1595 | -121.5723
2136.2031 | 121.756 | -0.45319 | 121.1472 | 1.4211e-13 | -0.031278 | -0.0020193 | 0.062462 | -0.0060552 | 0.056042 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.016506 | 0.057359 | -0.31944 | 3.8795 | -0.42046 | 121.2604 | 121.0534 | 120.9667 | -0.4019 | -0.095105 | 7.6834 | -0.32192 | 120.9247 | 121.159 | 121.0889 | -0.45261 | 0.051288 | 0.11321 | 0.13375 | 0.032731 | -0.018557 | -0.093769 | -0.18045 | 0.000572 | -0.22243 | 0.35808 | 0.13127 | 0.1307 | 0.011795 | -0.058262 | 121.7136 | 121.5066 | 121.4199 | 4.3327 | -121.5491 | 121.3779 | 121.6121 | 121.5421 | 8.1366 | -121.5998
2138 | 121.5866 | -0.48523 | 121.17 | 1.4211e-13 | -0.031278 | -0.0020193 | 0.062675 | -0.006269 | 0.055828 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.01672 | 0.057359 | -0.3286 | 3.8841 | -0.43419 | 121.2604 | 121.0442 | 120.9621 | -0.41563 | -0.095105 | 7.6468 | -0.33107 | 120.9156 | 121.1498 | 121.0843 | -0.46177 | 0.069595 | 0.090324 | 0.15663 | 0.05104 | -0.018555 | -0.12582 | -0.20791 | 0.023457 | -0.25447 | 0.39012 | 0.15416 | 0.1307 | -0.020251 | -0.085728 | 121.7456 | 121.5295 | 121.4474 | 4.3693 | -121.5857 | 121.4008 | 121.635 | 121.5695 | 8.132 | -121.6318
2139.7656 | 121.5729 | -0.50354 | 121.1334 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062034 | -0.0060552 | 0.055828 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.01672 | 0.057146 | -0.33317 | 3.8749 | -0.43419 | 121.2466 | 121.0442 | 120.9576 | -0.41106 | -0.099684 | 7.6148 | -0.33565 | 120.911 | 121.1406 | 121.0797 | -0.46635 | 0.092484 | 0.11321 | 0.17036 | 0.069351 | -0.023133 | -0.089194 | -0.17587 | 0.037189 | -0.22243 | 0.40386 | 0.16789 | 0.1307 | 0.007213 | -0.053686 | 121.7502 | 121.5478 | 121.4611 | 4.3784 | -121.5445 | 121.4145 | 121.6442 | 121.5833 | 8.1183 | -121.5998
2141.4688 | 121.582 | -0.54016 | 121.1426 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062462 | -0.006269 | 0.056042 | -0.0022889 | 0.00013254 | -0.00048293 | 0.062563 | 0.016079 | 0.057573 | -0.33775 | 3.8795 | -0.44792 | 121.2283 | 121.0305 | 120.9438 | -0.42937 | -0.11342 | 7.5735 | -0.34481 | 120.9018 | 121.1223 | 121.066 | -0.47551 | 0.11079 | 0.085741 | 0.20241 | 0.092237 | -0.018553 | -0.11209 | -0.19876 | 0.064653 | -0.24074 | 0.42674 | 0.19535 | 0.1307 | -0.020256 | -0.076577 | 121.7685 | 121.5707 | 121.484 | 4.4196 | -121.5719 | 121.442 | 121.6625 | 121.6062 | 8.1137 | -121.6181
2143.25 | 121.5912 | -0.52185 | 121.106 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062248 | -0.006269 | 0.055828 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062349 | 0.01672 | 0.057146 | -0.35607 | 3.8886 | -0.46166 | 121.2192 | 121.0076 | 120.9301 | -0.44311 | -0.12258 | 7.5094 | -0.35397 | 120.8835 | 121.1177 | 121.0523 | -0.49382 | 0.078743 | 0.1132 | 0.16578 | 0.060192 | -0.018551 | -0.098359 | -0.17588 | 0.028027 | -0.22243 | 0.39927 | 0.16788 | 0.13986 | 0.011786 | -0.053692 | 121.741 | 121.5294 | 121.4519 | 4.4105 | -121.5491 | 121.4054 | 121.6396 | 121.5741 | 8.0313 | -121.5998
2145.0156 | 121.669 | -0.48065 | 121.1426 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062034 | -0.006269 | 0.056255 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062776 | 0.01672 | 0.057146 | -0.34233 | 3.9161 | -0.44335 | 121.2375 | 121.0213 | 120.9484 | -0.42021 | -0.095105 | 7.5323 | -0.33107 | 120.9064 | 121.1361 | 121.0706 | -0.47093 | 0.060439 | 0.094898 | 0.13832 | 0.037306 | -0.023133 | -0.12124 | -0.19419 | 0.009722 | -0.23616 | 0.38555 | 0.14958 | 0.13986 | -0.00652 | -0.071998 | 121.7181 | 121.502 | 121.429 | 4.3968 | -121.5628 | 121.3871 | 121.6167 | 121.5512 | 8.013 | -121.6135
2146.7969 | 121.582 | -0.48523 | 121.1426 | 1.4211e-13 | -0.031278 | -0.0015919 | 0.062462 | -0.0058416 | 0.056042 | -0.0022889 | 0.00055974 | -0.00026913 | 0.062776 | 0.016506 | 0.057573 | -0.3286 | 3.9161 | -0.42961 | 121.2375 | 121.0396 | 120.953 | -0.41106 | -0.090527 | 7.5232 | -0.32649 | 120.9018 | 121.1406 | 121.0797 | -0.46635 | 0.074173 | 0.094898 | 0.15663 | 0.055618 | -0.018555 | -0.10293 | -0.18961 | 0.018878 | -0.24074 | 0.3947 | 0.15873 | 0.13986 | -0.001942 | -0.062841 | 121.7227 | 121.5249 | 121.4382 | 4.4013 | -121.5536 | 121.3871 | 121.6259 | 121.565 | 8.0084 | -121.6089
2148.5625 | 121.637 | -0.48065 | 121.1151 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062462 | -0.0060552 | 0.055828 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062349 | 0.01672 | 0.057359 | -0.33317 | 3.939 | -0.44335 | 121.2375 | 121.0351 | 120.9438 | -0.42479 | -0.085948 | 7.4774 | -0.33107 | 120.9018 | 121.1361 | 121.0706 | -0.46635 | 0.05586 | 0.12236 | 0.14748 | 0.037306 | -0.018554 | -0.080041 | -0.1713 | 0.014301 | -0.21327 | 0.3947 | 0.14958 | 0.13528 | 0.020946 | -0.044532 | 121.7181 | 121.5157 | 121.4245 | 4.4197 | -121.5399 | 121.3825 | 121.6167 | 121.5512 | 7.958 | -121.5815
2150.3281 | 121.5958 | -0.51727 | 121.1426 | 1.4211e-13 | -0.031705 | -0.0022329 | 0.062248 | -0.006269 | 0.056042 | 0.012972 | -8.1262e-05 | 0.00037167 | 0.062563 | 0.01672 | 0.057146 | -0.35149 | 3.9344 | -0.44335 | 121.2329 | 121.0305 | 120.9438 | -0.41563 | -0.07679 | 7.4591 | -0.33107 | 120.8927 | 121.1315 | 121.066 | -0.48009 | 0.10164 | 0.09032 | 0.16578 | 0.073927 | -0.027712 | -0.11209 | -0.19876 | 0.037186 | -0.2499 | 0.44048 | 0.1862 | 0.14901 | -0.011099 | -0.076577 | 121.7502 | 121.5478 | 121.4611 | 4.4517 | -121.5582 | 121.41 | 121.6488 | 121.5833 | 7.9764 | -121.6227
2152.0938 | 121.6095 | -0.49896 | 121.1243 | 1.4211e-13 | -0.031491 | -0.0020193 | 0.062248 | -0.0058416 | 0.055828 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062349 | 0.01672 | 0.057146 | -0.34691 | 3.9527 | -0.4525 | 121.2283 | 121.0168 | 120.9347 | -0.42479 | -0.090527 | 7.4316 | -0.33107 | 120.8881 | 121.1132 | 121.0614 | -0.47551 | 0.07417 | 0.10405 | 0.15205 | 0.046459 | -0.027711 | -0.10751 | -0.18961 | 0.023454 | -0.23616 | 0.40843 | 0.16789 | 0.14443 | -0.011104 | -0.062845 | 121.7273 | 121.5157 | 121.4336 | 4.4517 | -121.5491 | 121.3871 | 121.6121 | 121.5604 | 7.9306 | -121.5998
2153.7969 | 121.582 | -0.52643 | 121.106 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062462 | -0.0060552 | 0.055614 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062563 | 0.016934 | 0.056932 | -0.35149 | 3.9527 | -0.4525 | 121.2192 | 121.0122 | 120.9255 | -0.42021 | -0.085948 | 7.4179 | -0.33107 | 120.8881 | 121.1177 | 121.0523 | -0.48009 | 0.10622 | 0.1132 | 0.17494 | 0.073925 | -0.03229 | -0.09378 | -0.18046 | 0.046341 | -0.21785 | 0.44048 | 0.19535 | 0.14901 | 0.011786 | -0.053692 | 121.7456 | 121.5386 | 121.4519 | 4.4792 | -121.5262 | 121.4145 | 121.6442 | 121.5787 | 7.9443 | -121.586
2155.5625 | 121.6278 | -0.53101 | 121.1014 | 1.4211e-13 | -0.031278 | -0.0020193 | 0.062248 | -0.0058416 | 0.055828 | 0.0053411 | -8.1262e-05 | -5.5534e-05 | 0.06299 | 0.016506 | 0.057573 | -0.35149 | 3.9619 | -0.46166 | 121.2146 | 121.0122 | 120.9209 | -0.42937 | -0.095105 | 7.3996 | -0.34481 | 120.8835 | 121.1086 | 121.0431 | -0.48467 | 0.10163 | 0.11321 | 0.17952 | 0.069347 | -0.032288 | -0.089202 | -0.18046 | 0.04634 | -0.21785 | 0.4359 | 0.1862 | 0.13986 | 0.007207 | -0.058271 | 121.7456 | 121.5432 | 121.4519 | 4.4929 | -121.5307 | 121.4145 | 121.6396 | 121.5741 | 7.9306 | -121.586
2157.2656 | 121.5958 | -0.48065 | 121.138 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062462 | -0.0060552 | 0.055828 | -0.0099194 | 0.00013254 | -0.00026913 | 0.062349 | 0.01672 | 0.057359 | -0.31944 | 3.939 | -0.42046 | 121.2421 | 121.0396 | 120.9484 | -0.41106 | -0.044739 | 7.395 | -0.3036 | 120.9064 | 121.1406 | 121.0752 | -0.46177 | 0.069596 | 0.10405 | 0.16121 | 0.060197 | -0.009399 | -0.09835 | -0.18961 | 0.01888 | -0.23158 | 0.43591 | 0.17705 | 0.15817 | 0.002636 | -0.062842 | 121.7227 | 121.5203 | 121.429 | 4.4197 | -121.5491 | 121.3871 | 121.6213 | 121.5558 | 7.8756 | -121.5998
2159.0469 | 121.6049 | -0.4715 | 121.138 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062462 | -0.0060552 | 0.056042 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.016934 | 0.057359 | -0.30113 | 3.9527 | -0.41588 | 121.2512 | 121.058 | 120.9667 | -0.39274 | -0.040161 | 7.3675 | -0.29444 | 120.9202 | 121.1544 | 121.0889 | -0.43888 | 0.078757 | 0.11321 | 0.17037 | 0.055621 | -0.023136 | -0.080034 | -0.17129 | 0.032619 | -0.21785 | 0.43134 | 0.17705 | 0.14443 | 0.016372 | -0.049106 | 121.7227 | 121.5295 | 121.4382 | 4.4242 | -121.5307 | 121.3916 | 121.6259 | 121.5604 | 7.839 | -121.5769
2160.8281 | 121.6965 | -0.4303 | 121.1151 | 1.4211e-13 | -0.031278 | -0.0018055 | 0.062248 | -0.0060552 | 0.055614 | 0.0053411 | 0.00013254 | -0.00026913 | 0.062776 | 0.016934 | 0.057359 | -0.31028 | 3.9573 | -0.41588 | 121.2558 | 121.0488 | 120.9667 | -0.38816 | -0.026425 | 7.3309 | -0.28529 | 120.9247 | 121.1544 | 121.0935 | -0.43888 | 0.042137 | 0.14068 | 0.12002 | 0.014422 | -0.027715 | -0.066304 | -0.1484 | -0.00858 | -0.19038 | 0.40387 | 0.14501 | 0.15359 | 0.03926 | -0.021639 | 121.6861 | 121.4791 | 121.397 | 4.3876 | -121.5033 | 121.355 | 121.5847 | 121.5238 | 7.7612 | -121.554
2162.5938 | 121.7148 | -0.4303 | 121.1243 | 1.4211e-13 | -0.031278 | -0.0020193 | 0.062248 | -0.0058416 | 0.055614 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.016506 | 0.057359 | -0.3057 | 3.9573 | -0.40214 | 121.2649 | 121.0488 | 120.9621 | -0.39274 | -0.026425 | 7.3171 | -0.28529 | 120.9156 | 121.1544 | 121.0843 | -0.43888 | 0.037558 | 0.14068 | 0.12459 | 0.028156 | -0.009402 | -0.07546 | -0.16214 | -0.00858 | -0.20869 | 0.40387 | 0.14501 | 0.15359 | 0.030104 | -0.039952 | 121.6952 | 121.4791 | 121.3924 | 4.3876 | -121.517 | 121.3459 | 121.5847 | 121.5146 | 7.7474 | -121.5631
2164.3906 | 121.6187 | -0.49896 | 121.1334 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062248 | -0.0058416 | 0.055614 | 0.0053411 | 0.00034614 | -0.00026913 | 0.062563 | 0.01672 | 0.056932 | -0.31028 | 3.939 | -0.40672 | 121.2512 | 121.0442 | 120.9621 | -0.39274 | -0.031003 | 7.2668 | -0.28529 | 120.911 | 121.1498 | 121.0797 | -0.44346 | 0.10622 | 0.11779 | 0.18868 | 0.092242 | -0.01398 | -0.089194 | -0.17129 | 0.055505 | -0.22243 | 0.46796 | 0.21368 | 0.15817 | 0.01637 | -0.053686 | 121.7502 | 121.5432 | 121.4611 | 4.438 | -121.5262 | 121.41 | 121.6488 | 121.5787 | 7.7657 | -121.5769
2166.1719 | 121.6827 | -0.42572 | 121.1609 | 1.4211e-13 | -0.031491 | -0.0020193 | 0.062248 | -0.0060552 | 0.055614 | 0.0053411 | 0.00013254 | -5.5534e-05 | 0.062563 | 0.01672 | 0.057146 | -0.28739 | 3.9711 | -0.38383 | 121.2649 | 121.0671 | 120.9804 | -0.36984 | -0.003531 | 7.2668 | -0.26697 | 120.9293 | 121.1681 | 121.1026 | -0.42056 | 0.055875 | 0.10406 | 0.13833 | 0.041892 | -0.013983 | -0.093765 | -0.18044 | 0.005157 | -0.23158 | 0.42219 | 0.15875 | 0.15359 | 0.007219 | -0.058259 | 121.6907 | 121.4928 | 121.4062 | 4.3968 | -121.5307 | 121.355 | 121.5938 | 121.5284 | 7.6925 | -121.5815
2167.9375 | 121.6873 | -0.43488 | 121.106 | 1.4211e-13 | -0.031064 | -0.0018055 | 0.062462 | -0.006269 | 0.055828 | -0.0099194 | 0.00055974 | 0.00015807 | 0.062563 | 0.01672 | 0.056932 | -0.31028 | 3.9711 | -0.41588 | 121.2421 | 121.0396 | 120.953 | -0.39274 | -0.021846 | 7.2393 | -0.28071 | 120.9156 | 121.159 | 121.0752 | -0.45261 | 0.042135 | 0.1361 | 0.12459 | 0.018999 | -0.023136 | -0.066307 | -0.15299 | -0.017739 | -0.19038 | 0.41303 | 0.15417 | 0.17191 | 0.052994 | -0.030799 | 121.6769 | 121.4745 | 121.3878 | 4.4059 | -121.4987 | 121.3505 | 121.5938 | 121.51 | 7.6742 | -121.5586
2169.7031 | 121.5912 | -0.50812 | 121.17 | 1.4211e-13 | -0.031491 | -0.0020193 | 0.062462 | -0.0060552 | 0.055828 | -0.0099194 | -8.1262e-05 | -5.5534e-05 | 0.062563 | 0.016934 | 0.057359 | -0.31944 | 3.9573 | -0.42503 | 121.2375 | 121.0351 | 120.9438 | -0.4019 | -0.026425 | 7.1935 | -0.28986 | 120.911 | 121.1406 | 121.066 | -0.46177 | 0.10622 | 0.067432 | 0.18868 | 0.083085 | -0.023135 | -0.13497 | -0.22623 | 0.046346 | -0.25905 | 0.48169 | 0.21825 | 0.17191 | -0.029408 | -0.10404 | 121.7456 | 121.5432 | 121.4519 | 4.4654 | -121.5719 | 121.4191 | 121.6488 | 121.5741 | 7.7016 | -121.6318
2171.4219 | 121.6599 | -0.44861 | 121.0739 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062248 | -0.0060552 | 0.056042 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062349 | 0.01672 | 0.057146 | -0.3286 | 3.9665 | -0.42503 | 121.2375 | 121.0213 | 120.9438 | -0.40648 | -0.021846 | 7.1569 | -0.29444 | 120.9018 | 121.1361 | 121.066 | -0.45719 | 0.042131 | 0.16356 | 0.12001 | 0.023575 | -0.018556 | -0.052579 | -0.1301 | -0.008585 | -0.17208 | 0.42676 | 0.15416 | 0.16275 | 0.062144 | -0.007913 | 121.6861 | 121.4699 | 121.3924 | 4.4151 | -121.4804 | 121.3504 | 121.5847 | 121.5146 | 7.6055 | -121.5311
2173.1875 | 121.7148 | -0.45319 | 121.0739 | 1.4211e-13 | -0.031705 | -0.0020193 | 0.062034 | -0.0058416 | 0.055828 | -0.0099194 | 0.00034614 | 0.00015807 | 0.062776 | 0.01672 | 0.056718 | -0.33317 | 3.9619 | -0.42961 | 121.2146 | 121.0076 | 120.9301 | -0.41106 | -0.021846 | 7.134 | -0.29444 | 120.8927 | 121.1223 | 121.0477 | -0.46635 | 0.04213 | 0.14067 | 0.12001 | 0.023575 | -0.018555 | -0.066316 | -0.14383 | -0.013165 | -0.18123 | 0.43134 | 0.15874 | 0.17191 | 0.048408 | -0.026227 | 121.6678 | 121.4608 | 121.3833 | 4.4151 | -121.485 | 121.3459 | 121.5755 | 121.5009 | 7.5872 | -121.5403
2174.9688 | 121.6827 | -0.45319 | 121.0831 | 1.4211e-13 | -0.031491 | -0.0015919 | 0.062248 | -0.0060552 | 0.055828 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.016506 | 0.057146 | -0.33317 | 3.9802 | -0.43877 | 121.2146 | 121.0076 | 120.9255 | -0.41563 | -0.031003 | 7.0974 | -0.29902 | 120.8835 | 121.1223 | 121.0431 | -0.47093 | 0.037552 | 0.13152 | 0.12001 | 0.014418 | -0.023134 | -0.075471 | -0.15757 | -0.017744 | -0.19954 | 0.42218 | 0.15416 | 0.17191 | 0.039253 | -0.039961 | 121.6678 | 121.4608 | 121.3787 | 4.4334 | -121.4987 | 121.3367 | 121.5755 | 121.4963 | 7.5505 | -121.554
2176.6719 | 121.6827 | -0.48065 | 121.0831 | 1.4211e-13 | -0.031278 | -0.0015919 | 0.062248 | -0.0060552 | 0.055614 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.017147 | 0.057359 | -0.33775 | 3.9711 | -0.4525 | 121.2054 | 120.9984 | 120.9118 | -0.42021 | -0.031003 | 7.0607 | -0.30818 | 120.8698 | 121.1086 | 121.034 | -0.47551 | 0.060439 | 0.12236 | 0.1429 | 0.028149 | -0.03229 | -0.084629 | -0.1713 | 0.005144 | -0.21328 | 0.44965 | 0.17247 | 0.16733 | 0.025517 | -0.049118 | 121.6861 | 121.4791 | 121.3924 | 4.4517 | -121.5033 | 121.3504 | 121.5892 | 121.5146 | 7.5414 | -121.5586
2178.4531 | 121.5958 | -0.52643 | 121.0785 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062248 | -0.0060552 | 0.055828 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.01672 | 0.057146 | -0.36522 | 3.9848 | -0.46166 | 121.1963 | 120.9801 | 120.9026 | -0.43853 | -0.044739 | 7.0562 | -0.32649 | 120.8561 | 121.0948 | 121.0202 | -0.48467 | 0.087899 | 0.11778 | 0.1612 | 0.064769 | -0.02313 | -0.098367 | -0.17588 | 0.041762 | -0.22244 | 0.48169 | 0.19993 | 0.15817 | 0.016359 | -0.058276 | 121.7227 | 121.5066 | 121.429 | 4.5112 | -121.517 | 121.3825 | 121.6213 | 121.5466 | 7.5826 | -121.5632
2180.2344 | 121.6599 | -0.50354 | 121.0556 | 1.4211e-13 | -0.031491 | -0.0022329 | 0.062034 | -0.0060552 | 0.055828 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.016934 | 0.057573 | -0.36522 | 3.9985 | -0.46166 | 121.1825 | 120.971 | 120.898 | -0.43853 | -0.035582 | 7.0195 | -0.33107 | 120.8469 | 121.0857 | 121.0156 | -0.49382 | 0.065011 | 0.12693 | 0.13832 | 0.041881 | -0.02313 | -0.084637 | -0.15757 | 0.009716 | -0.20871 | 0.46796 | 0.17247 | 0.16275 | 0.03009 | -0.039966 | 121.6861 | 121.4745 | 121.4016 | 4.5021 | -121.4941 | 121.3504 | 121.5892 | 121.5192 | 7.5231 | -121.5494
2182 | 121.669 | -0.50812 | 121.051 | 1.4211e-13 | -0.031491 | -0.0015919 | 0.062248 | -0.0058416 | 0.055614 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062776 | 0.016934 | 0.057573 | -0.37438 | 3.9802 | -0.47997 | 121.1734 | 120.9664 | 120.8751 | -0.45227 | -0.044739 | 6.9646 | -0.33107 | 120.8332 | 121.0811 | 121.0111 | -0.50756 | 0.055852 | 0.12235 | 0.13374 | 0.028146 | -0.027706 | -0.084637 | -0.17589 | 0.000558 | -0.21786 | 0.46338 | 0.17704 | 0.17649 | 0.030089 | -0.039967 | 121.6815 | 121.4745 | 121.3833 | 4.4883 | -121.5033 | 121.3413 | 121.5892 | 121.5192 | 7.4727 | -121.5586
2183.7188 | 121.6827 | -0.50812 | 121.019 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062462 | -0.0058416 | 0.055401 | -0.0022889 | 0.00013254 | -0.00026913 | 0.062776 | 0.01672 | 0.056932 | -0.37896 | 3.9848 | -0.47539 | 121.1688 | 120.9618 | 120.8751 | -0.44311 | -0.040161 | 6.9142 | -0.32192 | 120.8423 | 121.072 | 121.0065 | -0.4984 | 0.06501 | 0.14982 | 0.12916 | 0.032724 | -0.032286 | -0.057173 | -0.14385 | 0.009716 | -0.17666 | 0.46796 | 0.1862 | 0.17649 | 0.052975 | -0.012503 | 121.6769 | 121.4699 | 121.3833 | 4.4929 | -121.4621 | 121.3504 | 121.5801 | 121.5146 | 7.4223 | -121.5174
2185.4844 | 121.6782 | -0.50354 | 121.0007 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062248 | -0.006269 | 0.055614 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062349 | 0.016934 | 0.057359 | -0.38354 | 3.9665 | -0.48455 | 121.1505 | 120.9527 | 120.8706 | -0.46142 | -0.035582 | 6.8776 | -0.33565 | 120.8286 | 121.0628 | 120.979 | -0.51672 | 0.042116 | 0.14982 | 0.12 | 0.018989 | -0.023127 | -0.04802 | -0.13011 | -0.013178 | -0.17209 | 0.46796 | 0.16789 | 0.18107 | 0.062129 | -0.021663 | 121.654 | 121.4562 | 121.3741 | 4.47 | -121.4621 | 121.3321 | 121.5663 | 121.4825 | 7.3811 | -121.5174
2187.2656 | 121.6553 | -0.51727 | 121.0236 | 1.4211e-13 | -0.031705 | -0.0020193 | 0.062248 | -0.0058416 | 0.055828 | -0.0099194 | 0.00034614 | -0.00026913 | 0.062349 | 0.016934 | 0.057146 | -0.37438 | 4.0031 | -0.47997 | 121.1551 | 120.9527 | 120.8751 | -0.45227 | -0.035582 | 6.8364 | -0.33107 | 120.8332 | 121.0582 | 120.9927 | -0.5213 | 0.065007 | 0.1315 | 0.14289 | 0.037301 | -0.027706 | -0.070909 | -0.14842 | -0.004024 | -0.1904 | 0.48169 | 0.1862 | 0.19022 | 0.034661 | -0.030816 | 121.6723 | 121.4699 | 121.3924 | 4.5204 | -121.4758 | 121.3504 | 121.5755 | 121.51 | 7.3536 | -121.5449
2189.0469 | 121.637 | -0.52643 | 121.0373 | 1.4211e-13 | -0.031705 | -0.0015919 | 0.062248 | -0.0058416 | 0.055614 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062349 | 0.01672 | 0.057146 | -0.38811 | 3.9894 | -0.47997 | 121.1459 | 120.9481 | 120.8614 | -0.46142 | -0.044739 | 6.8043 | -0.33565 | 120.8103 | 121.0399 | 120.979 | -0.52587 | 0.065004 | 0.10862 | 0.13831 | 0.046456 | -0.018548 | -0.08922 | -0.17589 | 0.000553 | -0.22702 | 0.48169 | 0.19078 | 0.19022 | 0.002615 | -0.058284 | 121.6723 | 121.4745 | 121.3878 | 4.5158 | -121.4987 | 121.3367 | 121.5663 | 121.5054 | 7.3308 | -121.5632
2190.8125 | 121.5408 | -0.56763 | 121.0419 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062248 | -0.006269 | 0.055614 | -0.0099194 | -8.1262e-05 | 0.00015807 | 0.062135 | 0.016934 | 0.056718 | -0.39727 | 4.0123 | -0.50286 | 121.1368 | 120.9298 | 120.8568 | -0.47516 | -0.049318 | 6.7585 | -0.34481 | 120.8057 | 121.0353 | 120.9699 | -0.53045 | 0.092467 | 0.094881 | 0.17035 | 0.064763 | -0.027704 | -0.11211 | -0.18505 | 0.037173 | -0.23618 | 0.51831 | 0.22282 | 0.18564 | -0.006542 | -0.072019 | 121.7044 | 121.4974 | 121.4244 | 4.5799 | -121.517 | 121.3733 | 121.603 | 121.5375 | 7.3262 | -121.5723
2192.5156 | 121.6003 | -0.56305 | 121.0464 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062462 | -0.006269 | 0.055614 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062349 | 0.01672 | 0.057146 | -0.37896 | 4.0214 | -0.48913 | 121.1368 | 120.9435 | 120.8614 | -0.45685 | -0.031003 | 6.7265 | -0.34481 | 120.8148 | 121.0445 | 120.9744 | -0.5213 | 0.1062 | 0.090303 | 0.18409 | 0.07392 | -0.032284 | -0.10295 | -0.18505 | 0.041752 | -0.2316 | 0.53205 | 0.21824 | 0.17649 | -0.001963 | -0.072019 | 121.6998 | 121.5065 | 121.4244 | 4.5845 | -121.5033 | 121.3779 | 121.6075 | 121.5375 | 7.2895 | -121.5677
2194.2969 | 121.6644 | -0.52185 | 121.0464 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.062248 | -0.006269 | 0.055614 | -0.01755 | 0.00055974 | 0.00015807 | 0.062349 | 0.016934 | 0.057573 | -0.3698 | 4.0397 | -0.47539 | 121.1551 | 120.9572 | 120.8797 | -0.44311 | -0.003531 | 6.7082 | -0.31734 | 120.8286 | 121.0582 | 120.9973 | -0.50298 | 0.078743 | 0.10862 | 0.15205 | 0.046457 | -0.032286 | -0.089218 | -0.16673 | 0.01887 | -0.21787 | 0.51832 | 0.20451 | 0.18564 | 0.011773 | -0.049126 | 121.6769 | 121.4791 | 121.4016 | 4.5616 | -121.4896 | 121.3504 | 121.5801 | 121.5192 | 7.23 | -121.5494
2196.0625 | 121.669 | -0.48981 | 120.9824 | 1.4211e-13 | -0.031919 | -0.0018055 | 0.062248 | -0.006269 | 0.055401 | -0.0022889 | 0.00034614 | -5.5534e-05 | 0.062563 | 0.016934 | 0.057146 | -0.37438 | 4.0672 | -0.48455 | 121.1459 | 120.9435 | 120.866 | -0.45227 | -0.017267 | 6.6532 | -0.32649 | 120.8194 | 121.0491 | 120.979 | -0.51214 | 0.037541 | 0.16355 | 0.11543 | 0.005256 | -0.032285 | -0.038868 | -0.11638 | -0.022332 | -0.16293 | 0.47254 | 0.16331 | 0.18564 | 0.066703 | -0.003353 | 121.6357 | 121.4333 | 121.3558 | 4.557 | -121.4346 | 121.3092 | 121.5389 | 121.4688 | 7.143 | -121.4945
2197.8281 | 121.6507 | -0.53558 | 120.9778 | 1.4211e-13 | -0.031919 | -0.0013783 | 0.062034 | -0.0060552 | 0.055614 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062349 | 0.016934 | 0.057146 | -0.38811 | 4.0443 | -0.49371 | 121.1368 | 120.9389 | 120.8522 | -0.466 | -0.012689 | 6.6166 | -0.32192 | 120.8057 | 121.0491 | 120.9744 | -0.51672 | 0.06958 | 0.15897 | 0.14747 | 0.041876 | -0.027704 | -0.038869 | -0.12554 | 0.018865 | -0.17209 | 0.52289 | 0.21367 | 0.1948 | 0.071281 | -0.003354 | 121.6723 | 121.4745 | 121.3878 | 4.5799 | -121.4438 | 121.3413 | 121.5846 | 121.51 | 7.1522 | -121.4945
2199.5469 | 121.6553 | -0.51727 | 120.9915 | 1.4211e-13 | -0.031491 | -0.0015919 | 0.062034 | -0.006269 | 0.055614 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062135 | 0.017147 | 0.057146 | -0.39269 | 4.0535 | -0.48913 | 121.1368 | 120.9343 | 120.8522 | -0.45685 | -0.00811 | 6.5433 | -0.32192 | 120.8148 | 121.0445 | 120.9699 | -0.51672 | 0.060428 | 0.14523 | 0.12458 | 0.028144 | -0.032284 | -0.057181 | -0.13927 | 0.000555 | -0.17667 | 0.50916 | 0.19536 | 0.1948 | 0.052969 | -0.021665 | 121.654 | 121.4516 | 121.3695 | 4.5707 | -121.4484 | 121.3321 | 121.5618 | 121.4871 | 7.0606 | -121.5082
2201.3125 | 121.5454 | -0.58136 | 121.0419 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062248 | -0.005628 | 0.055401 | -0.01755 | -8.1262e-05 | 0.00015807 | 0.062563 | 0.016934 | 0.057359 | -0.39269 | 4.0535 | -0.49371 | 121.1276 | 120.9252 | 120.8477 | -0.47058 | -0.012689 | 6.4701 | -0.33107 | 120.8011 | 121.0262 | 120.9653 | -0.53503 | 0.11078 | 0.085725 | 0.18867 | 0.087653 | -0.023125 | -0.11669 | -0.19421 | 0.046327 | -0.24076 | 0.56867 | 0.25029 | 0.20396 | -0.015699 | -0.076598 | 121.709 | 121.5065 | 121.429 | 4.6348 | -121.5125 | 121.3825 | 121.6075 | 121.5466 | 7.0514 | -121.5769
2203.0938 | 121.5134 | -0.55847 | 121.0236 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062034 | -0.0058416 | 0.055614 | 0.0053411 | 0.00013254 | 0.00015807 | 0.062776 | 0.017147 | 0.057359 | -0.38811 | 4.0397 | -0.48913 | 121.1276 | 120.9252 | 120.8477 | -0.466 | 0.001048 | 6.4426 | -0.32192 | 120.7965 | 121.0262 | 120.9699 | -0.5213 | 0.092469 | 0.10403 | 0.17036 | 0.069343 | -0.023126 | -0.098383 | -0.1759 | 0.037175 | -0.22703 | 0.55952 | 0.23656 | 0.19938 | 0.002611 | -0.053709 | 121.6861 | 121.4836 | 121.4061 | 4.5982 | -121.4896 | 121.355 | 121.5846 | 121.5283 | 7.0011 | -121.5449
2204.875 | 121.669 | -0.52643 | 120.9824 | 1.4211e-13 | -0.031491 | -0.0020193 | 0.062034 | -0.0060552 | 0.055614 | -0.0022889 | -8.1262e-05 | -5.5534e-05 | 0.062349 | 0.016934 | 0.056932 | -0.39727 | 4.0306 | -0.50286 | 121.123 | 120.9206 | 120.8339 | -0.47516 | 0.005626 | 6.406 | -0.33107 | 120.792 | 121.0262 | 120.9515 | -0.53045 | 0.051268 | 0.14066 | 0.12916 | 0.023564 | -0.027704 | -0.061763 | -0.14843 | -0.004026 | -0.19041 | 0.53205 | 0.19535 | 0.19938 | 0.04381 | -0.030825 | 121.6494 | 121.447 | 121.3604 | 4.557 | -121.4575 | 121.3184 | 121.5526 | 121.478 | 6.9324 | -121.5128
2206.5781 | 121.637 | -0.53558 | 120.9595 | 1.4211e-13 | -0.031491 | -0.0015919 | 0.061821 | -0.0064826 | 0.055401 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062349 | 0.016934 | 0.057146 | -0.40185 | 4.0306 | -0.51202 | 121.1139 | 120.9206 | 120.8202 | -0.47058 | 0.001048 | 6.3236 | -0.32649 | 120.7874 | 121.0216 | 120.947 | -0.53503 | 0.065001 | 0.15439 | 0.13373 | 0.023563 | -0.041438 | -0.038875 | -0.13928 | 0.00055 | -0.1721 | 0.53663 | 0.20909 | 0.20854 | 0.062119 | -0.012515 | 121.6494 | 121.4562 | 121.3558 | 4.5662 | -121.4301 | 121.323 | 121.5572 | 121.4825 | 6.8591 | -121.4945
2208.3594 | 121.5683 | -0.58136 | 121.019 | 1.4211e-13 | -0.031705 | -0.0024467 | 0.062034 | -0.0060552 | 0.055828 | -0.0099194 | 0.00034614 | 0.00037167 | 0.062349 | 0.016934 | 0.057359 | -0.40643 | 4.0443 | -0.51202 | 121.1139 | 120.9114 | 120.8339 | -0.47974 | 0.001048 | 6.2961 | -0.33107 | 120.7874 | 121.017 | 120.9378 | -0.53961 | 0.10162 | 0.094878 | 0.17493 | 0.06934 | -0.032281 | -0.10754 | -0.18505 | 0.041748 | -0.2316 | 0.58241 | 0.25029 | 0.20854 | -0.001968 | -0.081182 | 121.6952 | 121.4928 | 121.4153 | 4.6257 | -121.4987 | 121.3687 | 121.5984 | 121.5192 | 6.8774 | -121.5586
2210.0625 | 121.6141 | -0.53558 | 120.9732 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.061821 | -0.0060552 | 0.055614 | -0.0099194 | 0.00034614 | -0.00026913 | 0.062563 | 0.017361 | 0.057146 | -0.40643 | 4.0626 | -0.5166 | 121.1139 | 120.9069 | 120.8248 | -0.47974 | 0.005626 | 6.2457 | -0.32192 | 120.7782 | 121.0079 | 120.9424 | -0.53503 | 0.055844 | 0.14065 | 0.12915 | 0.018984 | -0.03686 | -0.066344 | -0.14844 | 0.00055 | -0.19499 | 0.54121 | 0.21367 | 0.21312 | 0.034651 | -0.030827 | 121.6494 | 121.4424 | 121.3604 | 4.5982 | -121.4529 | 121.3138 | 121.5434 | 121.478 | 6.7813 | -121.5082
2211.8281 | 121.6507 | -0.50354 | 120.9869 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062034 | -0.0064826 | 0.055614 | -0.0099194 | -0.00029486 | -0.00026913 | 0.062563 | 0.017361 | 0.057146 | -0.38354 | 4.0489 | -0.48455 | 121.1413 | 120.9343 | 120.8477 | -0.46142 | 0.046835 | 6.2182 | -0.29902 | 120.8057 | 121.0399 | 120.9607 | -0.5213 | 0.042116 | 0.15439 | 0.12 | 0.018989 | -0.023127 | -0.052603 | -0.13927 | -0.017757 | -0.18125 | 0.55037 | 0.20452 | 0.22227 | 0.052969 | -0.026245 | 121.6449 | 121.4379 | 121.3512 | 4.5524 | -121.4484 | 121.3092 | 121.5434 | 121.4642 | 6.7218 | -121.5082
2213.5938 | 121.5225 | -0.5722 | 121.0098 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062034 | -0.006269 | 0.055401 | -0.0022889 | 0.00013254 | -5.5534e-05 | 0.062349 | 0.017147 | 0.057146 | -0.39269 | 4.0718 | -0.48913 | 121.1184 | 120.916 | 120.8431 | -0.466 | 0.037677 | 6.1587 | -0.3036 | 120.7874 | 121.0262 | 120.9561 | -0.52587 | 0.1062 | 0.10861 | 0.17951 | 0.083076 | -0.023126 | -0.093808 | -0.16674 | 0.04633 | -0.22245 | 0.60988 | 0.2686 | 0.22227 | 0.016344 | -0.053712 | 121.6906 | 121.4882 | 121.4153 | 4.644 | -121.4758 | 121.3596 | 121.5984 | 121.5283 | 6.7309 | -121.5357
2215.3594 | 121.6461 | -0.51727 | 120.9686 | 1.4211e-13 | -0.031491 | -0.0020193 | 0.062248 | -0.0060552 | 0.055187 | -0.0022889 | -0.00029486 | -5.5534e-05 | 0.062563 | 0.017147 | 0.056932 | -0.40185 | 4.0352 | -0.49828 | 121.1184 | 120.9114 | 120.8385 | -0.47516 | 0.046835 | 6.1084 | -0.30818 | 120.7828 | 121.017 | 120.947 | -0.53045 | 0.042113 | 0.14981 | 0.11542 | 0.018988 | -0.023125 | -0.057188 | -0.13012 | -0.013181 | -0.18583 | 0.56411 | 0.20909 | 0.22227 | 0.048386 | -0.02167 | 121.6357 | 121.4287 | 121.3558 | 4.5524 | -121.4438 | 121.3001 | 121.5343 | 121.4642 | 6.6256 | -121.4991
2217.0781 | 121.5729 | -0.55847 | 121.0144 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062462 | -0.0058416 | 0.055401 | 0.0053411 | 0.00013254 | -0.00026913 | 0.062135 | 0.017361 | 0.057359 | -0.39727 | 4.0397 | -0.50286 | 121.1047 | 120.9069 | 120.8202 | -0.47974 | 0.042256 | 6.0671 | -0.30818 | 120.7691 | 121.0124 | 120.9332 | -0.53045 | 0.078733 | 0.090299 | 0.1612 | 0.055608 | -0.023125 | -0.10754 | -0.19421 | 0.028018 | -0.24534 | 0.60073 | 0.25029 | 0.22227 | -0.001969 | -0.081182 | 121.6632 | 121.4653 | 121.3787 | 4.5982 | -121.4941 | 121.3275 | 121.5709 | 121.4917 | 6.6256 | -121.5449
2218.8594 | 121.637 | -0.52643 | 120.9686 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.062248 | -0.006269 | 0.055187 | -0.0099194 | -8.1262e-05 | 0.00037167 | 0.062135 | 0.017147 | 0.057146 | -0.41101 | 4.0489 | -0.51202 | 121.0955 | 120.8977 | 120.8156 | -0.466 | 0.055992 | 5.9664 | -0.30818 | 120.7782 | 121.0079 | 120.9332 | -0.53961 | 0.060425 | 0.12692 | 0.11542 | 0.014408 | -0.046017 | -0.070924 | -0.15301 | -0.013184 | -0.19041 | 0.58242 | 0.21825 | 0.23143 | 0.039229 | -0.035406 | 121.622 | 121.4241 | 121.342 | 4.5753 | -121.4346 | 121.3046 | 121.5343 | 121.4596 | 6.4928 | -121.5082
2220.5625 | 121.5683 | -0.56305 | 121.0052 | 1.4211e-13 | -0.032132 | -0.0018055 | 0.062034 | -0.0060552 | 0.055401 | -0.0022889 | -0.00029486 | 0.00015807 | 0.062349 | 0.017361 | 0.057146 | -0.40643 | 4.0718 | -0.5166 | 121.1001 | 120.9023 | 120.8202 | -0.48432 | 0.055992 | 5.9389 | -0.3036 | 120.7736 | 121.0079 | 120.9332 | -0.53961 | 0.078731 | 0.094875 | 0.15662 | 0.04645 | -0.032281 | -0.10297 | -0.18506 | 0.023437 | -0.23161 | 0.61904 | 0.25945 | 0.23601 | 0.002608 | -0.072027 | 121.6632 | 121.4653 | 121.3832 | 4.6348 | -121.4896 | 121.3367 | 121.5709 | 121.4963 | 6.502 | -121.5449
2222.3281 | 121.6003 | -0.55389 | 120.9549 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.062248 | -0.0060552 | 0.055401 | -0.0022889 | 0.00034614 | 0.00015807 | 0.062349 | 0.016934 | 0.057359 | -0.41101 | 4.058 | -0.5166 | 121.091 | 120.8931 | 120.8156 | -0.4889 | 0.06515 | 5.8977 | -0.30818 | 120.7599 | 120.9987 | 120.9195 | -0.54877 | 0.064997 | 0.13607 | 0.14289 | 0.037295 | -0.027702 | -0.06177 | -0.13928 | 0.005125 | -0.19499 | 0.61904 | 0.24571 | 0.24059 | 0.043804 | -0.035409 | 121.6449 | 121.447 | 121.3695 | 4.6119 | -121.4438 | 121.3138 | 121.5526 | 121.4734 | 6.4516 | -121.5037
2224.0938 | 121.5042 | -0.58594 | 121.0236 | 1.4211e-13 | -0.031491 | -0.0018055 | 0.061821 | -0.0060552 | 0.055401 | -0.0022889 | 0.00013254 | 0.00037167 | 0.062349 | 0.016934 | 0.056932 | -0.40643 | 4.0809 | -0.51202 | 121.0955 | 120.8931 | 120.8156 | -0.47974 | 0.078886 | 5.8657 | -0.29902 | 120.7645 | 121.0079 | 120.9195 | -0.54419 | 0.1062 | 0.071986 | 0.17951 | 0.073917 | -0.032281 | -0.13044 | -0.20795 | 0.041746 | -0.25908 | 0.66482 | 0.28691 | 0.24517 | -0.015703 | -0.10407 | 121.6815 | 121.4791 | 121.4016 | 4.6669 | -121.5033 | 121.3504 | 121.5938 | 121.5054 | 6.4516 | -121.5678
2225.8594 | 121.6049 | -0.54932 | 120.9595 | 1.4211e-13 | -0.031919 | -0.0018055 | 0.062034 | -0.006269 | 0.055187 | -0.0099194 | 0.00034614 | -0.00026913 | 0.062563 | 0.017147 | 0.057146 | -0.41559 | 4.0809 | -0.50744 | 121.091 | 120.8885 | 120.8065 | -0.47974 | 0.088043 | 5.8153 | -0.29444 | 120.7645 | 120.985 | 120.9195 | -0.54419 | 0.069577 | 0.1315 | 0.13373 | 0.041874 | -0.027703 | -0.070927 | -0.15302 | 0.005125 | -0.19499 | 0.63736 | 0.25487 | 0.24975 | 0.025491 | -0.039987 | 121.6403 | 121.4379 | 121.3558 | 4.6303 | -121.4392 | 121.3138 | 121.5343 | 121.4688 | 6.3646 | -121.5037
2227.625 | 121.5042 | -0.58594 | 120.9595 | 1.4211e-13 | -0.031705 | -0.0020193 | 0.062034 | -0.0060552 | 0.055401 | 0.0053411 | 0.00034614 | -0.00026913 | 0.062563 | 0.016934 | 0.057146 | -0.41101 | 4.0764 | -0.5166 | 121.0818 | 120.884 | 120.8019 | -0.49348 | 0.083464 | 5.7558 | -0.29444 | 120.7553 | 120.9895 | 120.9195 | -0.54877 | 0.092461 | 0.12234 | 0.17493 | 0.069338 | -0.023123 | -0.075506 | -0.1576 | 0.037168 | -0.20415 | 0.6694 | 0.29149 | 0.25432 | 0.030069 | -0.039987 | 121.6677 | 121.4699 | 121.3878 | 4.6623 | -121.4529 | 121.3413 | 121.5755 | 121.5054 | 6.3417 | -121.5082
2229.4062 | 121.582 | -0.55847 | 120.9686 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.061821 | -0.0060552 | 0.055401 | -0.0022889 | -8.1262e-05 | 0.00015807 | 0.062349 | 0.017147 | 0.057359 | -0.42016 | 4.0947 | -0.52118 | 121.0864 | 120.8794 | 120.7973 | -0.4889 | 0.097201 | 5.7054 | -0.29902 | 120.7553 | 120.985 | 120.9103 | -0.55335 | 0.069575 | 0.11776 | 0.13831 | 0.037295 | -0.03228 | -0.08924 | -0.17133 | 0.005124 | -0.2133 | 0.65567 | 0.25945 | 0.25432 | 0.016336 | -0.058299 | 121.6449 | 121.4379 | 121.3558 | 4.6531 | -121.4575 | 121.3138 | 121.5434 | 121.4688 | 6.2639 | -121.522
2231.1094 | 121.6507 | -0.54932 | 120.932 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.062034 | -0.0060552 | 0.055187 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062563 | 0.017361 | 0.057359 | -0.42016 | 4.1084 | -0.52118 | 121.0772 | 120.8702 | 120.7836 | -0.49806 | 0.10636 | 5.6642 | -0.28986 | 120.7553 | 120.9758 | 120.9103 | -0.54877 | 0.051261 | 0.14522 | 0.12915 | 0.028139 | -0.023122 | -0.061777 | -0.14844 | 0.000547 | -0.17668 | 0.65567 | 0.25945 | 0.2589 | 0.043799 | -0.021678 | 121.6265 | 121.4195 | 121.3329 | 4.6577 | -121.4301 | 121.3046 | 121.5251 | 121.4596 | 6.2135 | -121.4808
2232.875 | 121.5958 | -0.55847 | 120.9412 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.061607 | -0.006269 | 0.055401 | -0.0099194 | 0.00013254 | -5.5534e-05 | 0.062349 | 0.017147 | 0.057146 | -0.42474 | 4.1038 | -0.52575 | 121.0635 | 120.8748 | 120.7881 | -0.49806 | 0.11552 | 5.623 | -0.28529 | 120.7462 | 120.9758 | 120.9057 | -0.56251 | 0.060417 | 0.12233 | 0.13373 | 0.032717 | -0.0277 | -0.066353 | -0.15302 | -0.004034 | -0.19499 | 0.67399 | 0.27318 | 0.27722 | 0.034644 | -0.035412 | 121.622 | 121.4333 | 121.3466 | 4.6623 | -121.4392 | 121.3046 | 121.5343 | 121.4642 | 6.1815 | -121.5037
2234.5781 | 121.637 | -0.56763 | 120.9137 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.061821 | -0.006269 | 0.055187 | -0.0099194 | 0.00034614 | 0.00015807 | 0.062776 | 0.017147 | 0.056718 | -0.42474 | 4.1084 | -0.53033 | 121.0772 | 120.8657 | 120.7927 | -0.50263 | 0.12467 | 5.5955 | -0.29902 | 120.7416 | 120.9712 | 120.8966 | -0.55793 | 0.064993 | 0.16354 | 0.14288 | 0.037294 | -0.027699 | -0.048045 | -0.12098 | 0.0097 | -0.1721 | 0.6923 | 0.2686 | 0.2589 | 0.057532 | -0.017103 | 121.6449 | 121.4333 | 121.3603 | 4.676 | -121.4163 | 121.3092 | 121.5389 | 121.4642 | 6.1632 | -121.4716
2236.3438 | 121.5042 | -0.58594 | 120.9503 | 1.4211e-13 | -0.031705 | -0.0015919 | 0.061821 | -0.0060552 | 0.055401 | -0.0022889 | 0.00013254 | 0.00015807 | 0.062349 | 0.016934 | 0.057359 | -0.42932 | 4.1038 | -0.53491 | 121.0543 | 120.8611 | 120.7744 | -0.50721 | 0.12925 | 5.5498 | -0.28071 | 120.737 | 120.9575 | 120.892 | -0.57166 | 0.078724 | 0.10402 | 0.15662 | 0.051025 | -0.027699 | -0.089245 | -0.17591 | 0.014274 | -0.2133 | 0.71519 | 0.30523 | 0.29096 | 0.007175 | -0.058303 | 121.6403 | 121.447 | 121.3603 | 4.6898 | -121.4575 | 121.323 | 121.5434 | 121.478 | 6.1357 | -121.522
2238.125 | 121.5546 | -0.59052 | 120.9457 | 1.4211e-13 | -0.031705 | -0.0020193 | 0.062034 | -0.006269 | 0.055187 | -0.0022889 | 0.00034614 | 0.00037167 | 0.062563 | 0.016934 | 0.057359 | -0.42474 | 4.0993 | -0.54407 | 121.0498 | 120.8565 | 120.7698 | -0.51179 | 0.14299 | 5.4948 | -0.28529 | 120.7279 | 120.9529 | 120.8829 | -0.57166 | 0.078723 | 0.10402 | 0.16577 | 0.046447 | -0.032276 | -0.089247 | -0.17591 | 0.018852 | -0.21788 | 0.7335 | 0.30523 | 0.28638 | 0.007173 | -0.062883 | 121.6403 | 121.447 | 121.3603 | 4.6898 | -121.4575 | 121.3184 | 121.5434 | 121.4734 | 6.0853 | -121.5174
2239.9062 | 121.6278 | -0.5722 | 120.9137 | 1.4211e-13 | -0.031919 | -0.0018055 | 0.062034 | -0.0060552 | 0.055187 | 0.0053411 | -8.1262e-05 | 0.00058547 | 0.062563 | 0.01672 | 0.057359 | -0.44763 | 4.0993 | -0.54407 | 121.0452 | 120.8428 | 120.7652 | -0.51179 | 0.14299 | 5.4765 | -0.28071 | 120.7324 | 120.9483 | 120.8783 | -0.57624 | 0.060413 | 0.13149 | 0.12457 | 0.028137 | -0.032276 | -0.070939 | -0.14845 | -0.004037 | -0.18126 | 0.71519 | 0.2915 | 0.29553 | 0.034639 | -0.035417 | 121.6174 | 121.415 | 121.3375 | 4.6715 | -121.4255 | 121.3046 | 121.5205 | 121.4505 | 6.0487 | -121.4899
2241.6719 | 121.6232 | -0.57678 | 120.8954 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.062034 | -0.0060552 | 0.055401 | -0.0099194 | 0.00013254 | 0.00037167 | 0.062563 | 0.017147 | 0.057359 | -0.44306 | 4.1084 | -0.55322 | 121.0452 | 120.8473 | 120.7607 | -0.52095 | 0.15672 | 5.4399 | -0.27613 | 120.7095 | 120.9392 | 120.8783 | -0.58998 | 0.055832 | 0.1498 | 0.13373 | 0.023557 | -0.032275 | -0.048051 | -0.13471 | -0.013197 | -0.18584 | 0.73351 | 0.30065 | 0.31385 | 0.043792 | -0.017107 | 121.622 | 121.4241 | 121.3375 | 4.6852 | -121.4163 | 121.2863 | 121.516 | 121.4551 | 6.0166 | -121.4854
2243.4375 | 121.6278 | -0.55847 | 120.9 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.061821 | -0.0060552 | 0.054973 | -0.0022889 | 0.00034614 | -0.00026913 | 0.062349 | 0.017147 | 0.057146 | -0.44306 | 4.1038 | -0.53033 | 121.0543 | 120.8473 | 120.7698 | -0.50263 | 0.19335 | 5.4353 | -0.26239 | 120.7187 | 120.9529 | 120.8829 | -0.57624 | 0.055838 | 0.15438 | 0.11542 | 0.028139 | -0.027699 | -0.052628 | -0.13013 | -0.01777 | -0.18126 | 0.75182 | 0.29608 | 0.31385 | 0.05295 | -0.017106 | 121.6128 | 121.4058 | 121.3283 | 4.6623 | -121.4026 | 121.2772 | 121.5114 | 121.4413 | 5.9938 | -121.4762
2245.1562 | 121.5134 | -0.61798 | 120.9686 | 1.4211e-13 | -0.031919 | -0.0018055 | 0.062034 | -0.006269 | 0.055187 | -0.0022889 | 0.00013254 | 0.00037167 | 0.062349 | 0.017575 | 0.057573 | -0.44306 | 4.113 | -0.53949 | 121.0406 | 120.8382 | 120.7561 | -0.50721 | 0.19335 | 5.3666 | -0.26239 | 120.7141 | 120.9483 | 120.8783 | -0.56708 | 0.11077 | 0.071977 | 0.17492 | 0.078491 | -0.032277 | -0.13045 | -0.21254 | 0.050896 | -0.25451 | 0.81133 | 0.35559 | 0.30469 | -0.020293 | -0.090349 | 121.6586 | 121.4562 | 121.3741 | 4.731 | -121.4758 | 121.3321 | 121.5663 | 121.4963 | 5.9846 | -121.5357
2246.9219 | 121.5729 | -0.59052 | 120.9366 | 1.4211e-13 | -0.031705 | -0.0020193 | 0.061821 | -0.006269 | 0.054973 | -0.0099194 | 0.00034614 | 0.00037167 | 0.062349 | 0.017147 | 0.057359 | -0.44306 | 4.0809 | -0.55322 | 121.0314 | 120.8336 | 120.7561 | -0.52095 | 0.20251 | 5.3483 | -0.25781 | 120.7095 | 120.93 | 120.8737 | -0.58082 | 0.069565 | 0.094865 | 0.14746 | 0.03729 | -0.032275 | -0.10298 | -0.18049 | 0.009694 | -0.22704 | 0.79303 | 0.3327 | 0.32301 | -0.006564 | -0.062884 | 121.622 | 121.4241 | 121.3466 | 4.6715 | -121.4575 | 121.3001 | 121.5205 | 121.4642 | 5.9388 | -121.5174
2248.625 | 121.5042 | -0.61798 | 120.9412 | 1.4211e-13 | -0.032346 | -0.0018055 | 0.062034 | -0.0060552 | 0.055187 | -0.0022889 | 0.00013254 | 0.00037167 | 0.062349 | 0.017575 | 0.057573 | -0.45679 | 4.0855 | -0.5578 | 121.0269 | 120.8336 | 120.7469 | -0.52553 | 0.2254 | 5.3162 | -0.25324 | 120.705 | 120.9346 | 120.8645 | -0.5854 | 0.092452 | 0.085708 | 0.16119 | 0.060178 | -0.032274 | -0.10756 | -0.19423 | 0.032581 | -0.2362 | 0.84339 | 0.36474 | 0.33216 | -0.006563 | -0.076619 | 121.6449 | 121.4516 | 121.3649 | 4.7035 | -121.4667 | 121.3229 | 121.5526 | 121.4825 | 5.9342 | -121.5266
2250.4062 | 121.5271 | -0.61798 | 120.9366 | 1.4211e-13 | -0.032132 | -0.0018055 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | 0.00013254 | 0.00037167 | 0.062349 | 0.016934 | 0.057359 | -0.45679 | 4.0718 | -0.56238 | 121.0269 | 120.8244 | 120.7424 | -0.52553 | 0.23456 | 5.275 | -0.25324 | 120.6958 | 120.93 | 120.8554 | -0.59456 | 0.092452 | 0.090286 | 0.16119 | 0.0556 | -0.036852 | -0.11214 | -0.19423 | 0.023423 | -0.24078 | 0.85254 | 0.36474 | 0.34132 | -0.006564 | -0.081198 | 121.6449 | 121.4424 | 121.3603 | 4.6898 | -121.4621 | 121.3138 | 121.548 | 121.4734 | 5.893 | -121.5311
2252.125 | 121.4905 | -0.63171 | 120.9366 | 1.4211e-13 | -0.031919 | -0.0022329 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | 0.00013254 | 0.00079907 | 0.062563 | 0.017361 | 0.057359 | -0.45221 | 4.0626 | -0.55322 | 121.0269 | 120.829 | 120.7424 | -0.52095 | 0.25288 | 5.2567 | -0.24866 | 120.7004 | 120.93 | 120.8554 | -0.59456 | 0.11076 | 0.090286 | 0.1795 | 0.078489 | -0.032275 | -0.10756 | -0.19423 | 0.037156 | -0.2362 | 0.88459 | 0.38306 | 0.3459 | -0.006564 | -0.081198 | 121.6586 | 121.4607 | 121.3741 | 4.6943 | -121.4575 | 121.3321 | 121.5617 | 121.4871 | 5.8884 | -121.5311
2253.9062 | 121.5408 | -0.6134 | 120.8771 | 1.4211e-13 | -0.032132 | -0.0022329 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | 0.00034614 | 0.00037167 | 0.062563 | 0.017361 | 0.057359 | -0.45679 | 4.058 | -0.55322 | 121.0131 | 120.8153 | 120.7332 | -0.52553 | 0.28035 | 5.2064 | -0.23034 | 120.6958 | 120.9209 | 120.8417 | -0.59914 | 0.087874 | 0.13606 | 0.15661 | 0.060178 | -0.027696 | -0.061792 | -0.14388 | 0.014267 | -0.18127 | 0.89375 | 0.38306 | 0.36879 | 0.043788 | -0.035425 | 121.6265 | 121.4287 | 121.3466 | 4.6715 | -121.4026 | 121.3092 | 121.5343 | 121.4551 | 5.8198 | -121.4762
2255.625 | 121.4859 | -0.62714 | 120.9183 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.062034 | -0.0058416 | 0.055614 | -0.0099194 | 0.00034614 | 0.00058547 | 0.062776 | 0.017361 | 0.057359 | -0.45221 | 4.0718 | -0.5578 | 121.0131 | 120.8244 | 120.7424 | -0.53011 | 0.29866 | 5.2384 | -0.22576 | 120.6912 | 120.9209 | 120.8462 | -0.5854 | 0.097028 | 0.094861 | 0.17492 | 0.069333 | -0.027695 | -0.093833 | -0.17592 | 0.041736 | -0.22705 | 0.9258 | 0.40137 | 0.35964 | 0.002589 | -0.072046 | 121.6403 | 121.4516 | 121.3695 | 4.6989 | -121.4484 | 121.3184 | 121.548 | 121.4734 | 5.8655 | -121.5037
2257.3906 | 121.4996 | -0.63629 | 120.9091 | 1.4211e-13 | -0.032132 | -0.0018055 | 0.061821 | -0.006269 | 0.054973 | -0.0022889 | 0.00077334 | 0.00037167 | 0.062563 | 0.017147 | 0.056932 | -0.46137 | 4.1038 | -0.57154 | 121.0086 | 120.8153 | 120.7286 | -0.53926 | 0.32156 | 5.2979 | -0.22576 | 120.6867 | 120.9163 | 120.8508 | -0.59914 | 0.097027 | 0.099438 | 0.17492 | 0.064754 | -0.032273 | -0.093836 | -0.1805 | 0.037156 | -0.22247 | 0.95785 | 0.41053 | 0.37337 | 0.007166 | -0.058312 | 121.6448 | 121.4516 | 121.3649 | 4.7401 | -121.4484 | 121.3229 | 121.5526 | 121.4871 | 5.9342 | -121.5083
2259.1094 | 121.5271 | -0.63171 | 120.8862 | 1.4211e-13 | -0.031919 | -0.0015919 | 0.062034 | -0.0060552 | 0.055187 | -0.0022889 | -8.1262e-05 | 0.00037167 | 0.062135 | 0.017361 | 0.056932 | -0.46595 | 4.1221 | -0.57612 | 121.0086 | 120.8061 | 120.724 | -0.53926 | 0.33071 | 5.2567 | -0.21661 | 120.6821 | 120.9071 | 120.8325 | -0.60372 | 0.092449 | 0.12233 | 0.16577 | 0.055598 | -0.036851 | -0.080105 | -0.16219 | 0.027999 | -0.20416 | 0.96243 | 0.41511 | 0.38711 | 0.020897 | -0.053738 | 121.6403 | 121.4378 | 121.3558 | 4.7539 | -121.4255 | 121.3138 | 121.5388 | 121.4642 | 5.8884 | -121.4899
2260.8906 | 121.4951 | -0.65918 | 120.8725 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.061821 | -0.0058416 | 0.054973 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062563 | 0.017361 | 0.057359 | -0.4751 | 4.113 | -0.57154 | 120.9994 | 120.7924 | 120.7149 | -0.53926 | 0.35819 | 5.2292 | -0.21661 | 120.6775 | 120.898 | 120.8279 | -0.60829 | 0.11991 | 0.1269 | 0.18407 | 0.087642 | -0.032273 | -0.08011 | -0.15761 | 0.050886 | -0.195 | 1.0174 | 0.44257 | 0.39169 | 0.025472 | -0.044584 | 121.6586 | 121.4516 | 121.3741 | 4.7722 | -121.4118 | 121.3367 | 121.5572 | 121.4871 | 5.8884 | -121.4808
2262.6562 | 121.5454 | -0.62714 | 120.8954 | 1.4211e-13 | -0.031919 | -0.0022329 | 0.061821 | -0.0060552 | 0.055187 | -0.0099194 | 0.00013254 | 0.00015807 | 0.062563 | 0.017788 | 0.057573 | -0.48884 | 4.1267 | -0.58527 | 120.9857 | 120.7832 | 120.7057 | -0.55758 | 0.37192 | 5.2018 | -0.20287 | 120.6546 | 120.8888 | 120.8142 | -0.62203 | 0.069555 | 0.090279 | 0.1383 | 0.041863 | -0.027692 | -0.11216 | -0.18966 | 0.005106 | -0.24079 | 0.99906 | 0.42427 | 0.41916 | -0.006573 | -0.081208 | 121.6128 | 121.4104 | 121.3329 | 4.7539 | -121.453 | 121.2817 | 121.5159 | 121.4413 | 5.8289 | -121.5174
2264.4219 | 121.5775 | -0.63171 | 120.8359 | 1.4211e-13 | -0.032346 | -0.0018055 | 0.062034 | -0.0060552 | 0.054973 | -0.0022889 | 0.00034614 | 0.00015807 | 0.062349 | 0.017788 | 0.057359 | -0.48884 | 4.1084 | -0.60359 | 120.9765 | 120.7787 | 120.6874 | -0.55758 | 0.39024 | 5.1926 | -0.19829 | 120.6546 | 120.8797 | 120.805 | -0.62661 | 0.074133 | 0.14063 | 0.14287 | 0.028128 | -0.046005 | -0.057224 | -0.14846 | 0.005105 | -0.18128 | 1.022 | 0.43342 | 0.42832 | 0.04378 | -0.030855 | 121.6082 | 121.4104 | 121.3191 | 4.7401 | -121.3935 | 121.2863 | 121.5114 | 121.4367 | 5.8243 | -121.4625
2266.2031 | 121.4905 | -0.68207 | 120.8725 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.062034 | -0.0060552 | 0.055187 | -0.0099194 | 0.00013254 | 0.00037167 | 0.062349 | 0.017575 | 0.057573 | -0.498 | 4.1038 | -0.59901 | 120.9765 | 120.7741 | 120.692 | -0.56674 | 0.41771 | 5.2247 | -0.19371 | 120.65 | 120.8705 | 120.7959 | -0.62661 | 0.11533 | 0.10401 | 0.18407 | 0.08306 | -0.032269 | -0.098425 | -0.18051 | 0.055459 | -0.22248 | 1.0998 | 0.48836 | 0.4329 | -0.001999 | -0.076634 | 121.6586 | 121.4561 | 121.3741 | 4.7859 | -121.4392 | 121.3321 | 121.5526 | 121.4779 | 5.9067 | -121.4991
2267.9062 | 121.5271 | -0.6546 | 120.8496 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.062034 | -0.0060552 | 0.054973 | -0.0022889 | 0.00055974 | 0.00037167 | 0.062776 | 0.017575 | 0.057359 | -0.50257 | 4.0947 | -0.60359 | 120.9628 | 120.7649 | 120.6828 | -0.57132 | 0.43602 | 5.0598 | -0.18913 | 120.6409 | 120.8613 | 120.8004 | -0.63119 | 0.083284 | 0.11316 | 0.15203 | 0.051016 | -0.032268 | -0.084694 | -0.16678 | 0.023414 | -0.20874 | 1.0906 | 0.46547 | 0.44205 | 0.011732 | -0.049167 | 121.6174 | 121.4195 | 121.3374 | 4.7493 | -121.4209 | 121.2955 | 121.5159 | 121.455 | 5.7144 | -121.4808
2269.6875 | 121.4767 | -0.67291 | 120.9045 | 1.4211e-13 | -0.031919 | -0.0022329 | 0.061607 | -0.0060552 | 0.054973 | -0.0022889 | -8.1262e-05 | 0.00058547 | 0.062135 | 0.017361 | 0.057146 | -0.50257 | 4.1405 | -0.60359 | 120.9628 | 120.7603 | 120.6783 | -0.56674 | 0.47265 | 4.4921 | -0.16166 | 120.6317 | 120.8568 | 120.7913 | -0.63577 | 0.10617 | 0.058232 | 0.17034 | 0.069327 | -0.036847 | -0.1442 | -0.22628 | 0.037146 | -0.27283 | 1.1456 | 0.51125 | 0.47411 | -0.047778 | -0.11326 | 121.6357 | 121.4332 | 121.3512 | 4.8134 | -121.4713 | 121.3046 | 121.5297 | 121.4642 | 5.165 | -121.5403
2271.4531 | 121.5637 | -0.67749 | 120.8359 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.061607 | -0.0060552 | 0.055187 | -0.01755 | 0.00034614 | 0.00058547 | 0.062349 | 0.017361 | 0.057787 | -0.498 | 4.0993 | -0.61274 | 120.9582 | 120.7603 | 120.6691 | -0.5759 | 0.53218 | 4.2677 | -0.13877 | 120.6363 | 120.8659 | 120.7867 | -0.64035 | 0.10159 | 0.12232 | 0.17949 | 0.064748 | -0.036845 | -0.07554 | -0.16678 | 0.037144 | -0.19959 | 1.2097 | 0.53872 | 0.50158 | 0.030044 | -0.04917 | 121.6357 | 121.4378 | 121.3466 | 4.7767 | -121.4118 | 121.3138 | 121.5434 | 121.4642 | 4.9452 | -121.4762
2273.1562 | 121.6049 | -0.63629 | 120.7993 | 1.4211e-13 | -0.031919 | -0.0020193 | 0.062034 | -0.0060552 | 0.05476 | -0.0022889 | 0.00034614 | 0.00015807 | 0.062349 | 0.017788 | 0.057787 | -0.51173 | 4.1359 | -0.61732 | 120.9536 | 120.7603 | 120.6691 | -0.57132 | 0.55965 | 4.1075 | -0.12503 | 120.6317 | 120.8568 | 120.7821 | -0.64492 | 0.064974 | 0.15436 | 0.12456 | 0.018971 | -0.046003 | -0.038919 | -0.13016 | -0.008633 | -0.16755 | 1.1959 | 0.51126 | 0.51989 | 0.057508 | -0.017127 | 121.5899 | 121.3966 | 121.3054 | 4.7722 | -121.3706 | 121.268 | 121.4931 | 121.4184 | 4.7438 | -121.4442
2274.9219 | 121.6187 | -0.65002 | 120.7993 | 1.4211e-13 | -0.031919 | -0.0024467 | 0.061607 | -0.0064826 | 0.054973 | -0.0022889 | 0.00055974 | 0.00079907 | 0.062349 | 0.017361 | 0.057787 | -0.51173 | 4.1267 | -0.61274 | 120.9353 | 120.7512 | 120.6599 | -0.58048 | 0.6146 | 3.938 | -0.11587 | 120.6226 | 120.843 | 120.7775 | -0.64035 | 0.069548 | 0.13605 | 0.13829 | 0.037282 | -0.032266 | -0.048077 | -0.13931 | 0.009678 | -0.1767 | 1.2646 | 0.53415 | 0.52447 | 0.043772 | -0.021706 | 121.5853 | 121.4012 | 121.31 | 4.7768 | -121.3797 | 121.2726 | 121.4931 | 121.4276 | 4.5881 | -121.4396
2276.6875 | 121.4676 | -0.69122 | 120.8176 | 1.4211e-13 | -0.032346 | -0.0022329 | 0.062034 | -0.0060552 | 0.054973 | 0.0053411 | 0.00013254 | 0.00058547 | 0.062563 | 0.017575 | 0.057359 | -0.51173 | 4.1359 | -0.60359 | 120.9445 | 120.7558 | 120.6737 | -0.5759 | 0.6787 | 3.8098 | -0.079245 | 120.6226 | 120.8522 | 120.773 | -0.64492 | 0.11533 | 0.12689 | 0.17949 | 0.087637 | -0.027689 | -0.061809 | -0.14389 | 0.046298 | -0.19501 | 1.3699 | 0.61198 | 0.56568 | 0.034618 | -0.044595 | 121.6357 | 121.447 | 121.3649 | 4.8271 | -121.3935 | 121.3138 | 121.5434 | 121.4642 | 4.5011 | -121.4625
2278.4688 | 121.5134 | -0.68207 | 120.8542 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.061821 | -0.006269 | 0.055187 | -0.0099194 | 0.00077334 | 0.00058547 | 0.062349 | 0.017575 | 0.057573 | -0.50257 | 4.1267 | -0.61274 | 120.9445 | 120.7512 | 120.6599 | -0.58048 | 0.7428 | 3.645 | -0.047194 | 120.6226 | 120.8476 | 120.7867 | -0.64035 | 0.10159 | 0.090272 | 0.17949 | 0.069326 | -0.032266 | -0.10301 | -0.19425 | 0.041722 | -0.23164 | 1.4249 | 0.63487 | 0.59315 | -0.006581 | -0.067481 | 121.6265 | 121.4332 | 121.342 | 4.8088 | -121.4347 | 121.3046 | 121.5297 | 121.4688 | 4.3271 | -121.4945
2280.25 | 121.5912 | -0.62714 | 120.813 | 1.4211e-13 | -0.032346 | -0.0018055 | 0.061821 | -0.0064826 | 0.055187 | -0.0022889 | 0.00013254 | 0.00079907 | 0.062776 | 0.017788 | 0.057787 | -0.50715 | 4.145 | -0.61732 | 120.9536 | 120.742 | 120.6737 | -0.57132 | 0.80232 | 3.5122 | -0.010564 | 120.6226 | 120.8522 | 120.7775 | -0.6495 | 0.055818 | 0.14063 | 0.11998 | 0.009815 | -0.046003 | -0.070968 | -0.13931 | -0.022367 | -0.19044 | 1.4295 | 0.61657 | 0.63894 | 0.039196 | -0.035439 | 121.5808 | 121.3692 | 121.3008 | 4.7722 | -121.3843 | 121.2497 | 121.4793 | 121.4047 | 4.1394 | -121.4625
2281.9531 | 121.4584 | -0.67749 | 120.8633 | 1.4211e-13 | -0.032132 | -0.0018055 | 0.061821 | -0.0060552 | 0.055187 | -0.0099194 | 0.00055974 | 0.00079907 | 0.062349 | 0.017361 | 0.058214 | -0.51173 | 4.1405 | -0.60359 | 120.9399 | 120.742 | 120.6691 | -0.5759 | 0.871 | 3.3978 | -0.001407 | 120.6134 | 120.8476 | 120.7775 | -0.64035 | 0.10159 | 0.076539 | 0.16576 | 0.073904 | -0.027689 | -0.12132 | -0.19424 | 0.037144 | -0.24995 | 1.5485 | 0.67608 | 0.63894 | -0.015736 | -0.085793 | 121.6174 | 121.4195 | 121.3466 | 4.818 | -121.4392 | 121.2909 | 121.5251 | 121.455 | 4.0753 | -121.5037
2283.7344 | 121.463 | -0.69122 | 120.8588 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.061821 | -0.006269 | 0.05476 | -0.0022889 | 0.00055974 | 0.0010127 | 0.062349 | 0.018002 | 0.057787 | -0.51631 | 4.1496 | -0.6219 | 120.9307 | 120.742 | 120.6554 | -0.58505 | 1.0267 | 3.2696 | 0.016908 | 120.6042 | 120.8339 | 120.7592 | -0.65408 | 0.10617 | 0.071959 | 0.17491 | 0.069324 | -0.036844 | -0.11675 | -0.2034 | 0.037141 | -0.25453 | 1.7179 | 0.70813 | 0.67099 | -0.024895 | -0.09953 | 121.6219 | 121.4332 | 121.3466 | 4.8408 | -121.4438 | 121.2955 | 121.5251 | 121.4505 | 3.9608 | -121.5128
2285.5156 | 121.4401 | -0.68207 | 120.8267 | 1.4211e-13 | -0.032132 | -0.0020193 | 0.061607 | -0.0060552 | 0.055187 | -0.0099194 | 0.00034614 | 0.0010127 | 0.062776 | 0.017575 | 0.057787 | -0.50715 | 4.1817 | -0.6219 | 120.9353 | 120.7374 | 120.6508 | -0.59421 | 1.1366 | 3.1368 | 0.053538 | 120.6134 | 120.8339 | 120.7638 | -0.65408 | 0.087855 | 0.10858 | 0.17491 | 0.060169 | -0.027686 | -0.08928 | -0.17594 | 0.027986 | -0.21333 | 1.8186 | 0.73561 | 0.70762 | 0.007149 | -0.062908 | 121.6174 | 121.4195 | 121.3329 | 4.8637 | -121.4209 | 121.2955 | 121.5159 | 121.4459 | 3.8188 | -121.4808
2287.2969 | 121.5912 | -0.63629 | 120.7581 | 1.4211e-13 | -0.03256 | -0.0022329 | 0.061821 | -0.006269 | 0.054973 | -0.0099194 | 0.00034614 | 0.00079907 | 0.062563 | 0.017788 | 0.058214 | -0.51173 | 4.2 | -0.62648 | 120.9307 | 120.7374 | 120.6554 | -0.58048 | 1.2602 | 3.091 | 0.1039 | 120.6088 | 120.8384 | 120.7592 | -0.65408 | 0.055816 | 0.17267 | 0.12456 | 0.009815 | -0.046001 | -0.020616 | -0.10269 | -0.01779 | -0.14924 | 1.8965 | 0.7402 | 0.75799 | 0.080391 | 0.001178 | 121.567 | 121.3737 | 121.2917 | 4.8363 | -121.3385 | 121.2451 | 121.4747 | 121.3955 | 3.7273 | -121.4121
2289.0781 | 121.4813 | -0.68665 | 120.8313 | 1.4211e-13 | -0.032346 | -0.0020193 | 0.062034 | -0.0058416 | 0.055187 | -0.0022889 | 0.00055974 | 0.00079907 | 0.062563 | 0.018002 | 0.058 | -0.50715 | 4.2137 | -0.6219 | 120.9353 | 120.7329 | 120.6599 | -0.58048 | 1.3747 | 2.9719 | 0.14053 | 120.6088 | 120.8293 | 120.7592 | -0.6495 | 0.10617 | 0.104 | 0.17949 | 0.064747 | -0.041423 | -0.098437 | -0.17136 | 0.037143 | -0.22248 | 2.0613 | 0.82718 | 0.79004 | -0.002008 | -0.072064 | 121.6219 | 121.4195 | 121.3466 | 4.9004 | -121.4118 | 121.2955 | 121.5159 | 121.4459 | 3.6586 | -121.4808
2290.7969 | 121.5637 | -0.6546 | 120.7947 | 1.4211e-13 | -0.031705 | -0.0018055 | 0.062034 | -0.006269 | 0.054973 | -0.0022889 | 0.00034614 | 0.0010127 | 0.062563 | 0.017788 | 0.058214 | -0.52547 | 4.1771 | -0.62648 | 120.9078 | 120.7237 | 120.6416 | -0.59421 | 1.48 | 2.8758 | 0.16801 | 120.5905 | 120.8201 | 120.7455 | -0.66782 | 0.060389 | 0.11315 | 0.12913 | 0.028125 | -0.032264 | -0.070973 | -0.15305 | -0.013217 | -0.20418 | 2.1346 | 0.82261 | 0.83583 | 0.025456 | -0.049179 | 121.5624 | 121.3783 | 121.2962 | 4.8317 | -121.3889 | 121.2451 | 121.4747 | 121.4001 | 3.5304 | -121.4625
2292.5781 | 121.5454 | -0.67291 | 120.7764 | 1.4211e-13 | -0.032346 | -0.0015919 | 0.061607 | -0.0064826 | 0.05476 | -0.0099194 | 0.00077334 | 0.0014401 | 0.062349 | 0.018002 | 0.058214 | -0.52547 | 4.1725 | -0.63563 | 120.9124 | 120.7237 | 120.6416 | -0.59421 | 1.6402 | 2.798 | 0.20006 | 120.5859 | 120.8201 | 120.7455 | -0.66324 | 0.0787 | 0.13604 | 0.14745 | 0.037279 | -0.041421 | -0.052662 | -0.13474 | 0.009673 | -0.19044 | 2.3131 | 0.87297 | 0.8633 | 0.043767 | -0.030868 | 121.5853 | 121.3966 | 121.3145 | 4.8454 | -121.3706 | 121.2588 | 121.493 | 121.4184 | 3.4709 | -121.4396
2294.3594 | 121.6049 | -0.6546 | 120.7901 | 1.4211e-13 | -0.032346 | -0.0020193 | 0.062248 | -0.0060552 | 0.05476 | -0.0022889 | 0.00077334 | 0.0012265 | 0.062349 | 0.018216 | 0.058 | -0.53004 | 4.1679 | -0.63563 | 120.9124 | 120.7054 | 120.6279 | -0.60337 | 1.7959 | 2.6697 | 0.24584 | 120.5813 | 120.811 | 120.7363 | -0.65866 | 0.051232 | 0.12231 | 0.12456 | 0.018968 | -0.032264 | -0.084711 | -0.16221 | -0.004059 | -0.20876 | 2.4505 | 0.90045 | 0.90451 | 0.020877 | -0.053758 | 121.567 | 121.36 | 121.2825 | 4.8225 | -121.3935 | 121.2359 | 121.4656 | 121.3909 | 3.3243 | -121.4488
2296.1562 | 121.5729 | -0.66376 | 120.7489 | 1.4211e-13 | -0.032132 | -0.0022329 | 0.062034 | -0.006269 | 0.054973 | -0.0022889 | 0.00055974 | 0.0014401 | 0.06299 | 0.018002 | 0.058641 | -0.5392 | 4.1679 | -0.64479 | 120.8941 | 120.71 | 120.6233 | -0.60795 | 1.947 | 2.5828 | 0.26874 | 120.5859 | 120.7972 | 120.7272 | -0.67698 | 0.055808 | 0.1452 | 0.12456 | 0.018967 | -0.036841 | -0.038933 | -0.12559 | -0.013219 | -0.16298 | 2.6108 | 0.93249 | 0.94571 | 0.04834 | -0.021716 | 121.5579 | 121.3737 | 121.2871 | 4.8317 | -121.3569 | 121.2497 | 121.461 | 121.3909 | 3.2465 | -121.4259
2297.9375 | 121.4447 | -0.70953 | 120.7855 | 1.4211e-13 | -0.032132 | -0.0022329 | 0.061821 | -0.006269 | 0.05476 | -0.0022889 | 0.00055974 | 0.0018675 | 0.062776 | 0.018002 | 0.058214 | -0.5392 | 4.1908 | -0.64021 | 120.8941 | 120.6917 | 120.6187 | -0.60795 | 2.1347 | 2.5965 | 0.34658 | 120.5768 | 120.7972 | 120.7226 | -0.67698 | 0.10159 | 0.10858 | 0.17033 | 0.069322 | -0.032263 | -0.09387 | -0.16679 | 0.032558 | -0.20876 | 2.8443 | 1.0561 | 1.0236 | 0.011719 | -0.062916 | 121.6036 | 121.4012 | 121.3283 | 4.9004 | -121.3935 | 121.2863 | 121.5068 | 121.4321 | 3.306 | -121.4625
2299.6406 | 121.4767 | -0.71869 | 120.7855 | 1.4211e-13 | -0.032773 | -0.0022329 | 0.061821 | -0.0060552 | 0.054973 | -0.01755 | 0.00055974 | 0.0016537 | 0.062349 | 0.018216 | 0.058855 | -0.54378 | 4.1771 | -0.65395 | 120.8804 | 120.6917 | 120.6096 | -0.62169 | 2.327 | 2.5507 | 0.39236 | 120.5585 | 120.7789 | 120.718 | -0.68613 | 0.097003 | 0.09484 | 0.17491 | 0.064742 | -0.032261 | -0.09387 | -0.17594 | 0.032555 | -0.22707 | 3.0457 | 1.1111 | 1.0785 | -0.006595 | -0.067495 | 121.5991 | 121.4103 | 121.3283 | 4.8958 | -121.4072 | 121.2771 | 121.4976 | 121.4367 | 3.2694 | -121.4717
2301.3438 | 121.55 | -0.6546 | 120.7443 | 1.4211e-13 | -0.032346 | -0.0015919 | 0.061607 | -0.006269 | 0.05476 | -0.0022889 | 0.00077334 | 0.0018675 | 0.062563 | 0.018216 | 0.058855 | -0.53462 | 4.1862 | -0.64021 | 120.8987 | 120.6962 | 120.6187 | -0.60795 | 2.5422 | 2.4958 | 0.46104 | 120.5768 | 120.7972 | 120.7272 | -0.6724 | 0.046653 | 0.15435 | 0.11998 | 0.01439 | -0.032263 | -0.048093 | -0.12559 | -0.017795 | -0.16756 | 3.1968 | 1.1156 | 1.1334 | 0.052917 | -0.017139 | 121.5533 | 121.3508 | 121.2733 | 4.8409 | -121.3523 | 121.2314 | 121.4518 | 121.3818 | 3.1504 | -121.4167
2303.125 | 121.5729 | -0.66376 | 120.7901 | 1.4211e-13 | -0.032346 | -0.0022329 | 0.062034 | -0.006269 | 0.054973 | -0.0022889 | 0.00098694 | 0.0022947 | 0.062349 | 0.018216 | 0.059282 | -0.5392 | 4.1862 | -0.64479 | 120.8895 | 120.6962 | 120.605 | -0.60337 | 2.7757 | 2.4729 | 0.50683 | 120.5676 | 120.7927 | 120.7134 | -0.67698 | 0.060387 | 0.099418 | 0.12456 | 0.018967 | -0.04142 | -0.093869 | -0.1851 | -0.013219 | -0.22249 | 3.4395 | 1.1706 | 1.1838 | 0.002562 | -0.076651 | 121.5533 | 121.36 | 121.2688 | 4.85 | -121.3935 | 121.2314 | 121.4564 | 121.3772 | 3.1366 | -121.4671
2304.9062 | 121.5271 | -0.68665 | 120.7352 | 1.4211e-13 | -0.032346 | -0.0020193 | 0.061821 | -0.0058416 | 0.055187 | -0.0099194 | 0.00077334 | 0.0020811 | 0.062563 | 0.018643 | 0.059069 | -0.55294 | 4.2 | -0.65395 | 120.8804 | 120.6825 | 120.605 | -0.60795 | 3.0276 | 2.4225 | 0.58925 | 120.563 | 120.7835 | 120.718 | -0.68156 | 0.078697 | 0.14519 | 0.13371 | 0.032699 | -0.045998 | -0.052674 | -0.13017 | 0.005091 | -0.17214 | 3.7142 | 1.2759 | 1.2708 | 0.048337 | -0.017141 | 121.567 | 121.3691 | 121.2916 | 4.8866 | -121.3431 | 121.2497 | 121.4702 | 121.4047 | 3.1091 | -121.4167
2306.6875 | 121.4859 | -0.70496 | 120.7764 | 1.4211e-13 | -0.032132 | -0.0024467 | 0.061821 | -0.0060552 | 0.055187 | -0.0099194 | 0.00098694 | 0.0025083 | 0.062776 | 0.018429 | 0.059282 | -0.5392 | 4.2137 | -0.65395 | 120.8804 | 120.6871 | 120.605 | -0.61711 | 3.3023 | 2.4088 | 0.65793 | 120.5539 | 120.7789 | 120.718 | -0.68613 | 0.087849 | 0.104 | 0.16575 | 0.051009 | -0.03684 | -0.089294 | -0.17137 | 0.018822 | -0.22249 | 4.0073 | 1.3629 | 1.3441 | 0.00256 | -0.05834 | 121.5853 | 121.392 | 121.31 | 4.9187 | -121.3935 | 121.2588 | 121.4839 | 121.423 | 3.1137 | -121.4625
2308.4062 | 121.4447 | -0.71411 | 120.7855 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.0060552 | 0.054973 | 0.0053411 | 0.0012007 | 0.0027221 | 0.062563 | 0.018643 | 0.059496 | -0.54836 | 4.2229 | -0.64937 | 120.8804 | 120.6871 | 120.5958 | -0.62169 | 3.5908 | 2.4591 | 0.73577 | 120.563 | 120.7789 | 120.718 | -0.67698 | 0.092425 | 0.09484 | 0.16575 | 0.064742 | -0.027683 | -0.098449 | -0.18968 | 0.037135 | -0.22249 | 4.3049 | 1.4499 | 1.4127 | -0.006595 | -0.067495 | 121.5945 | 121.4012 | 121.31 | 4.937 | -121.4072 | 121.2771 | 121.493 | 121.4321 | 3.1732 | -121.4625
2310.1875 | 121.5225 | -0.67291 | 120.726 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.061393 | -0.0058416 | 0.05476 | -0.0022889 | 0.0012007 | 0.0027221 | 0.062776 | 0.018643 | 0.059496 | -0.5392 | 4.2412 | -0.64021 | 120.8712 | 120.6871 | 120.6004 | -0.61711 | 3.8838 | 2.4866 | 0.80902 | 120.5539 | 120.7789 | 120.7089 | -0.67698 | 0.055806 | 0.14519 | 0.13371 | 0.032701 | -0.023105 | -0.03894 | -0.12559 | -0.004063 | -0.17214 | 4.5567 | 1.4819 | 1.486 | 0.052914 | -0.017143 | 121.5441 | 121.36 | 121.2733 | 4.9141 | -121.3431 | 121.2268 | 121.4518 | 121.3818 | 3.1595 | -121.403
2311.9688 | 121.5637 | -0.67291 | 120.7169 | 1.4211e-13 | -0.032346 | -0.0020193 | 0.061821 | -0.0060552 | 0.054973 | -0.01755 | 0.0012007 | 0.0031493 | 0.062349 | 0.018643 | 0.05971 | -0.55294 | 4.1862 | -0.65395 | 120.8666 | 120.6779 | 120.5913 | -0.62626 | 4.1723 | 2.5553 | 0.89602 | 120.5447 | 120.7698 | 120.7043 | -0.69071 | 0.046648 | 0.14977 | 0.11998 | 0.018966 | -0.027682 | -0.038943 | -0.1256 | -0.0178 | -0.17214 | 4.8452 | 1.5689 | 1.5867 | 0.052911 | -0.012566 | 121.5395 | 121.3508 | 121.2642 | 4.8592 | -121.3431 | 121.2176 | 121.4427 | 121.3772 | 3.2282 | -121.4076
2313.6875 | 121.5134 | -0.70038 | 120.7535 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | 0.0014143 | 0.0033631 | 0.062563 | 0.018643 | 0.059923 | -0.55294 | 4.1862 | -0.65853 | 120.8666 | 120.6642 | 120.5913 | -0.63542 | 4.4561 | 2.5919 | 0.97386 | 120.5401 | 120.7698 | 120.6951 | -0.69071 | 0.064955 | 0.11315 | 0.14744 | 0.041853 | -0.023102 | -0.089301 | -0.16222 | 0.009665 | -0.21334 | 5.1565 | 1.6742 | 1.6646 | 0.01629 | -0.058345 | 121.567 | 121.3646 | 121.2916 | 4.8866 | -121.3889 | 121.2405 | 121.4701 | 121.3955 | 3.2923 | -121.4442
2315.4688 | 121.5546 | -0.68207 | 120.7123 | 1.4211e-13 | -0.03256 | -0.0015919 | 0.061607 | -0.0064826 | 0.055187 | -0.0022889 | 0.0016279 | 0.0033631 | 0.062563 | 0.018857 | 0.060137 | -0.54836 | 4.232 | -0.65853 | 120.862 | 120.6642 | 120.5867 | -0.62626 | 4.7492 | 2.6697 | 1.0837 | 120.5356 | 120.7606 | 120.6951 | -0.69071 | 0.055803 | 0.14977 | 0.13371 | 0.023543 | -0.03226 | -0.048102 | -0.1256 | -0.008645 | -0.17672 | 5.4312 | 1.7658 | 1.7745 | 0.048332 | -0.017146 | 121.5441 | 121.3462 | 121.2688 | 4.9141 | -121.3385 | 121.2176 | 121.4427 | 121.3772 | 3.3518 | -121.403
2317.1875 | 121.4905 | -0.71869 | 120.7443 | 1.4211e-13 | -0.032773 | -0.0020193 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | 0.0020551 | 0.0037903 | 0.062349 | 0.018857 | 0.060351 | -0.55294 | 4.2137 | -0.65853 | 120.8666 | 120.6733 | 120.5867 | -0.62169 | 5.0514 | 2.7705 | 1.1982 | 120.5401 | 120.7698 | 120.6997 | -0.69071 | 0.097003 | 0.1223 | 0.16575 | 0.060164 | -0.036839 | -0.070988 | -0.15764 | 0.027976 | -0.20419 | 5.7701 | 1.9169 | 1.8889 | 0.025445 | -0.044611 | 121.5853 | 121.392 | 121.3054 | 4.9324 | -121.366 | 121.2588 | 121.4885 | 121.4184 | 3.4892 | -121.435
2318.9531 | 121.5134 | -0.69122 | 120.7397 | 1.4211e-13 | -0.03256 | -0.0022329 | 0.062034 | -0.006269 | 0.054973 | 0.0053411 | 0.0020551 | 0.0037903 | 0.062349 | 0.018643 | 0.060564 | -0.55294 | 4.2229 | -0.65395 | 120.862 | 120.6642 | 120.5775 | -0.62169 | 5.3352 | 2.8666 | 1.3218 | 120.5401 | 120.7652 | 120.6906 | -0.68613 | 0.069537 | 0.1223 | 0.13829 | 0.037276 | -0.032261 | -0.075568 | -0.16222 | 0.005089 | -0.19961 | 6.0265 | 2.0131 | 2.008 | 0.025445 | -0.04919 | 121.5533 | 121.3554 | 121.2687 | 4.9141 | -121.3614 | 121.2314 | 121.4564 | 121.3818 | 3.5579 | -121.4259
2320.7344 | 121.5271 | -0.71869 | 120.7214 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.062034 | -0.0060552 | 0.054973 | -0.0022889 | 0.0022689 | 0.0042177 | 0.062776 | 0.019284 | 0.060564 | -0.55752 | 4.2183 | -0.65853 | 120.8575 | 120.6688 | 120.5775 | -0.61711 | 5.5504 | 2.9307 | 1.4455 | 120.5447 | 120.7606 | 120.686 | -0.69987 | 0.10158 | 0.13603 | 0.16117 | 0.060164 | -0.041418 | -0.052679 | -0.14391 | 0.018819 | -0.17672 | 6.2691 | 2.1642 | 2.1453 | 0.039176 | -0.035459 | 121.5762 | 121.3874 | 121.2962 | 4.937 | -121.3385 | 121.2634 | 121.4793 | 121.4047 | 3.6494 | -121.4213
2322.5 | 121.4905 | -0.72327 | 120.726 | 1.4211e-13 | -0.032346 | -0.0024467 | 0.062034 | -0.0064826 | 0.054973 | 0.012972 | 0.0024825 | 0.0046449 | 0.062563 | 0.019711 | 0.061205 | -0.55294 | 4.2229 | -0.65853 | 120.8483 | 120.6642 | 120.5638 | -0.63542 | 5.8481 | 3.0223 | 1.5828 | 120.5264 | 120.756 | 120.6814 | -0.69529 | 0.087844 | 0.1223 | 0.17033 | 0.064742 | -0.023102 | -0.061835 | -0.16222 | 0.027975 | -0.19961 | 6.5713 | 2.3061 | 2.2781 | 0.03002 | -0.044614 | 121.5716 | 121.3874 | 121.2871 | 4.9461 | -121.3614 | 121.2497 | 121.4793 | 121.4047 | 3.7456 | -121.4213
2324.2188 | 121.5271 | -0.63629 | 120.7718 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.062034 | -0.006269 | 0.054973 | 0.0053411 | 0.0024825 | 0.0044313 | 0.062563 | 0.019498 | 0.061205 | -0.52089 | 4.232 | -0.6219 | 120.8849 | 120.6962 | 120.6187 | -0.59421 | 6.0541 | 3.1276 | 1.7614 | 120.563 | 120.8018 | 120.718 | -0.65866 | 0.042079 | 0.11315 | 0.1154 | 0.014393 | -0.027686 | -0.075559 | -0.15306 | -0.022369 | -0.20876 | 6.6904 | 2.3977 | 2.4201 | 0.03003 | -0.053763 | 121.5212 | 121.3325 | 121.255 | 4.8683 | -121.366 | 121.1993 | 121.4381 | 121.3543 | 3.7639 | -121.4305
2326 | 121.55 | -0.51727 | 120.8542 | 1.4211e-13 | -0.03256 | -0.0015919 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | 0.0024825 | 0.0048587 | 0.062776 | 0.019711 | 0.061419 | -0.37896 | 4.2687 | -0.48913 | 121.0269 | 120.829 | 120.7424 | -0.466 | 6.4112 | 3.3291 | 2.0407 | 120.6958 | 120.9163 | 120.8462 | -0.52587 | 0.05127 | 0.17268 | 0.13831 | 0.028144 | -0.023126 | -0.025167 | -0.11183 | -0.008602 | -0.15838 | 6.9285 | 2.558 | 2.5666 | 0.062098 | -0.007959 | 121.5441 | 121.3463 | 121.2596 | 4.7859 | -121.3202 | 121.2131 | 121.4336 | 121.3635 | 3.8464 | -121.3801
2327.7656 | 121.4172 | -0.75531 | 120.7443 | 1.4211e-13 | -0.03256 | -0.0022329 | 0.061821 | -0.006269 | 0.054973 | -0.0022889 | 0.0029097 | 0.0050723 | 0.06299 | 0.019925 | 0.061419 | -0.57583 | 4.2687 | -0.67226 | 120.8254 | 120.6321 | 120.5546 | -0.64458 | 6.5898 | 3.3062 | 2.0224 | 120.4989 | 120.724 | 120.6539 | -0.71361 | 0.11073 | 0.081097 | 0.17948 | 0.08305 | -0.027679 | -0.1122 | -0.18969 | 0.041703 | -0.24539 | 7.3451 | 2.7777 | 2.736 | -0.020341 | -0.090397 | 121.5807 | 121.3874 | 121.3099 | 5.024 | -121.3889 | 121.2542 | 121.4793 | 121.4092 | 4.0615 | -121.4579
2329.5312 | 121.4172 | -0.75531 | 120.7352 | 1.4211e-13 | -0.032132 | -0.0015919 | 0.062034 | -0.0064826 | 0.05476 | -0.0099194 | 0.0033371 | 0.0057133 | 0.062776 | 0.019925 | 0.061846 | -0.57583 | 4.2961 | -0.67226 | 120.8254 | 120.6275 | 120.5455 | -0.64916 | 6.8462 | 3.4481 | 2.2055 | 120.5035 | 120.7286 | 120.6585 | -0.70903 | 0.10615 | 0.090253 | 0.17948 | 0.08305 | -0.0231 | -0.10762 | -0.18969 | 0.046282 | -0.23166 | 7.6015 | 2.9608 | 2.9146 | -0.006606 | -0.076662 | 121.5807 | 121.3829 | 121.3008 | 5.0514 | -121.3843 | 121.2588 | 121.4839 | 121.4138 | 4.2034 | -121.4442
2331.2656 | 121.5088 | -0.6958 | 120.7031 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.061821 | -0.0060552 | 0.054973 | -0.0099194 | 0.0033371 | 0.0061405 | 0.063203 | 0.020352 | 0.061846 | -0.57583 | 4.2916 | -0.66768 | 120.8254 | 120.6275 | 120.5455 | -0.64916 | 7.098 | 3.5763 | 2.3887 | 120.5081 | 120.724 | 120.6493 | -0.71361 | 0.046641 | 0.1223 | 0.11997 | 0.028119 | -0.018522 | -0.075578 | -0.15765 | -0.017806 | -0.19504 | 7.7938 | 3.0845 | 3.1023 | 0.020858 | -0.053777 | 121.5212 | 121.3233 | 121.2413 | 4.9874 | -121.3523 | 121.2039 | 121.4198 | 121.3451 | 4.2721 | -121.4167
2333.0469 | 121.5454 | -0.70496 | 120.6619 | 1.4211e-13 | -0.03256 | -0.0022329 | 0.062034 | -0.006269 | 0.054973 | -0.0022889 | 0.0037643 | 0.0057133 | 0.063203 | 0.020352 | 0.061846 | -0.56667 | 4.3236 | -0.66768 | 120.8163 | 120.6138 | 120.5409 | -0.64458 | 7.3361 | 3.7229 | 2.5856 | 120.4944 | 120.724 | 120.6448 | -0.70903 | 0.060375 | 0.15434 | 0.13828 | 0.037274 | -0.023101 | -0.048116 | -0.12103 | -0.004072 | -0.16757 | 8.0411 | 3.2905 | 3.2946 | 0.062057 | -0.017156 | 121.5212 | 121.3188 | 121.2459 | 5.0286 | -121.3065 | 121.1993 | 121.4289 | 121.3497 | 4.4278 | -121.371
2334.75 | 121.463 | -0.74158 | 120.6848 | 1.4211e-13 | -0.032773 | -0.0018055 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | 0.0035507 | 0.0063543 | 0.063203 | 0.020566 | 0.062273 | -0.57583 | 4.3144 | -0.67226 | 120.8117 | 120.6184 | 120.5363 | -0.65374 | 7.5605 | 3.8511 | 2.7504 | 120.4944 | 120.724 | 120.6448 | -0.71819 | 0.087838 | 0.12687 | 0.16575 | 0.069317 | -0.018521 | -0.066425 | -0.14849 | 0.023391 | -0.19046 | 8.3021 | 3.492 | 3.4686 | 0.039169 | -0.040044 | 121.5533 | 121.36 | 121.2779 | 5.056 | -121.3386 | 121.2359 | 121.4656 | 121.3863 | 4.5926 | -121.403
2336.5312 | 121.3943 | -0.75989 | 120.7077 | 1.4211e-13 | -0.032773 | -0.0022329 | 0.062034 | -0.0064826 | 0.05476 | -0.0099194 | 0.0044051 | 0.0063543 | 0.063417 | 0.020566 | 0.062701 | -0.57583 | 4.3328 | -0.67226 | 120.8163 | 120.6138 | 120.5317 | -0.64916 | 7.7665 | 4.0022 | 2.9198 | 120.4898 | 120.7148 | 120.6448 | -0.70903 | 0.11073 | 0.10856 | 0.18406 | 0.087628 | -0.0231 | -0.093893 | -0.17596 | 0.05086 | -0.21793 | 8.5264 | 3.6797 | 3.6288 | 0.007123 | -0.062933 | 121.5762 | 121.3737 | 121.2916 | 5.0927 | -121.3569 | 121.2497 | 121.4747 | 121.4047 | 4.762 | -121.4167
2338.3125 | 121.4539 | -0.76446 | 120.7031 | 1.4211e-13 | -0.032773 | -0.0013783 | 0.061821 | -0.006269 | 0.05476 | -0.0022889 | 0.0046189 | 0.0069951 | 0.063417 | 0.020566 | 0.06206 | -0.58041 | 4.3511 | -0.686 | 120.8071 | 120.6184 | 120.5272 | -0.65832 | 7.9634 | 4.1807 | 3.0892 | 120.4852 | 120.7102 | 120.631 | -0.72734 | 0.10615 | 0.10398 | 0.18406 | 0.07847 | -0.027678 | -0.084736 | -0.17596 | 0.037122 | -0.21793 | 8.7279 | 3.8537 | 3.8166 | 0.007122 | -0.072091 | 121.5716 | 121.3829 | 121.2916 | 5.1155 | -121.3614 | 121.2497 | 121.4747 | 121.3955 | 4.9452 | -121.4305
2340.0156 | 121.431 | -0.75531 | 120.7169 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.062034 | -0.0066962 | 0.05476 | 0.0053411 | 0.0046189 | 0.0074225 | 0.063631 | 0.020566 | 0.062701 | -0.57125 | 4.3419 | -0.66768 | 120.8025 | 120.6184 | 120.5409 | -0.65374 | 8.229 | 4.3776 | 3.2678 | 120.4898 | 120.724 | 120.6448 | -0.71361 | 0.10157 | 0.085671 | 0.18406 | 0.087628 | -0.013943 | -0.098469 | -0.17596 | 0.041703 | -0.22708 | 8.9843 | 4.0231 | 3.9814 | 0.007125 | -0.072088 | 121.5578 | 121.3737 | 121.2962 | 5.0972 | -121.3706 | 121.2451 | 121.4793 | 121.4001 | 5.1329 | -121.4305
2341.7812 | 121.4081 | -0.74158 | 120.7077 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.0022889 | 0.0052597 | 0.0076361 | 0.063844 | 0.02078 | 0.062914 | -0.56667 | 4.3465 | -0.65853 | 120.8208 | 120.623 | 120.5409 | -0.64916 | 8.4305 | 4.5974 | 3.4509 | 120.4989 | 120.7102 | 120.6493 | -0.71361 | 0.092417 | 0.11314 | 0.1749 | 0.083052 | -0.009365 | -0.084735 | -0.1668 | 0.02797 | -0.20877 | 9.172 | 4.1925 | 4.1645 | 0.002544 | -0.058355 | 121.5624 | 121.3645 | 121.2825 | 5.0881 | -121.3569 | 121.2405 | 121.4518 | 121.3909 | 5.339 | -121.4213
2343.5469 | 121.431 | -0.75073 | 120.726 | 1.4211e-13 | -0.03256 | -0.0020193 | 0.062034 | -0.0058416 | 0.054973 | 0.0053411 | 0.0054733 | 0.0076361 | 0.063844 | 0.021207 | 0.063128 | -0.57125 | 4.3877 | -0.67226 | 120.8117 | 120.623 | 120.5363 | -0.64458 | 8.6136 | 4.808 | 3.6112 | 120.4944 | 120.7148 | 120.6402 | -0.70903 | 0.10615 | 0.085673 | 0.17948 | 0.078472 | -0.027679 | -0.10304 | -0.18969 | 0.041704 | -0.23166 | 9.3643 | 4.3619 | 4.3202 | -0.011187 | -0.085822 | 121.5624 | 121.3737 | 121.2871 | 5.1384 | -121.3706 | 121.2451 | 121.4656 | 121.3909 | 5.5587 | -121.435
2345.3125 | 121.5363 | -0.70038 | 120.6573 | 1.4211e-13 | -0.032773 | -0.0020193 | 0.061821 | -0.0064826 | 0.05476 | -0.0022889 | 0.0056871 | 0.0078499 | 0.064058 | 0.021634 | 0.062914 | -0.56667 | 4.374 | -0.66768 | 120.8025 | 120.6184 | 120.5226 | -0.64458 | 8.7555 | 5.0507 | 3.776 | 120.4852 | 120.7102 | 120.6356 | -0.71819 | 0.055797 | 0.14518 | 0.1337 | 0.032696 | -0.023101 | -0.03896 | -0.13477 | -0.017808 | -0.17215 | 9.4559 | 4.4764 | 4.4942 | 0.052898 | -0.021736 | 121.5029 | 121.3188 | 121.223 | 5.0743 | -121.3019 | 121.1856 | 121.4106 | 121.336 | 5.7511 | -121.3755
2347.0781 | 121.4447 | -0.74158 | 120.6848 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.062034 | -0.006269 | 0.054546 | -0.0099194 | 0.0061143 | 0.0082771 | 0.064272 | 0.021421 | 0.063128 | -0.58041 | 4.3923 | -0.686 | 120.7934 | 120.5955 | 120.518 | -0.64916 | 8.9158 | 5.2476 | 3.8905 | 120.476 | 120.6965 | 120.6219 | -0.72734 | 0.092417 | 0.10856 | 0.16117 | 0.055582 | -0.036835 | -0.089319 | -0.16681 | 0.014234 | -0.20878 | 9.6574 | 4.6321 | 4.6178 | 0.011698 | -0.062937 | 121.5349 | 121.3371 | 121.2596 | 5.1339 | -121.334 | 121.2176 | 121.4381 | 121.3635 | 5.9891 | -121.4122
2348.7812 | 121.4584 | -0.737 | 120.6985 | 1.4211e-13 | -0.033201 | -0.0018055 | 0.061607 | -0.0058416 | 0.05476 | 0.0053411 | 0.0065415 | 0.0084909 | 0.064272 | 0.021207 | 0.063555 | -0.58041 | 4.3648 | -0.686 | 120.7888 | 120.5955 | 120.5134 | -0.65832 | 9.1127 | 5.504 | 4.0508 | 120.4669 | 120.6965 | 120.6219 | -0.72734 | 0.078683 | 0.090247 | 0.15659 | 0.051005 | -0.027678 | -0.10305 | -0.18512 | 0.009657 | -0.23167 | 9.8497 | 4.7878 | 4.7781 | -0.002035 | -0.07667 | 121.5258 | 121.3325 | 121.2504 | 5.1018 | -121.3569 | 121.2039 | 121.4335 | 121.3589 | 6.241 | -121.4259
2350.5469 | 121.4218 | -0.7782 | 120.6802 | 1.4211e-13 | -0.032346 | -0.0018055 | 0.061393 | -0.0060552 | 0.054332 | 0.0053411 | 0.0069689 | 0.0084909 | 0.064272 | 0.021634 | 0.063342 | -0.58499 | 4.4243 | -0.67684 | 120.7888 | 120.6001 | 120.5043 | -0.65374 | 9.2546 | 5.8291 | 4.2247 | 120.4623 | 120.6919 | 120.6219 | -0.72276 | 0.12446 | 0.10856 | 0.19321 | 0.10136 | -0.023099 | -0.080163 | -0.17597 | 0.055434 | -0.21793 | 10.0328 | 5.0029 | 4.9475 | 0.011696 | -0.05836 | 121.567 | 121.3783 | 121.2825 | 5.2025 | -121.334 | 121.2405 | 121.4701 | 121.4001 | 6.6073 | -121.403
2352.3281 | 121.4264 | -0.74616 | 120.6619 | 1.4211e-13 | -0.032773 | -0.0018055 | 0.061821 | -0.0064826 | 0.054973 | -0.0022889 | 0.0071825 | 0.0091317 | 0.064913 | 0.021848 | 0.063983 | -0.56667 | 4.406 | -0.66768 | 120.8025 | 120.6047 | 120.5226 | -0.64916 | 9.3966 | 6.1587 | 4.4079 | 120.4715 | 120.7057 | 120.6219 | -0.71819 | 0.096995 | 0.1406 | 0.17948 | 0.078473 | -0.018522 | -0.057274 | -0.13934 | 0.027969 | -0.19047 | 10.1427 | 5.154 | 5.1261 | 0.043743 | -0.040049 | 121.5487 | 121.3508 | 121.2687 | 5.1522 | -121.3111 | 121.2176 | 121.4518 | 121.368 | 6.9049 | -121.3801
2354.0469 | 121.5317 | -0.68665 | 120.639 | 1.4211e-13 | -0.032773 | -0.0018055 | 0.062034 | -0.0058416 | 0.054973 | -0.0022889 | 0.0076097 | 0.0093455 | 0.064913 | 0.022275 | 0.063983 | -0.57583 | 4.4152 | -0.66768 | 120.7934 | 120.6047 | 120.518 | -0.65374 | 9.6118 | 6.4701 | 4.5681 | 120.4715 | 120.6919 | 120.6219 | -0.71819 | 0.032907 | 0.15433 | 0.11082 | 0.018964 | -0.013943 | -0.034386 | -0.12103 | -0.03154 | -0.16758 | 10.2984 | 5.2548 | 5.2863 | 0.052895 | -0.017161 | 121.48 | 121.2913 | 121.2047 | 5.1018 | -121.2928 | 121.1581 | 121.3786 | 121.3085 | 7.1567 | -121.3572
2355.8281 | 121.4035 | -0.74158 | 120.694 | 1.4211e-13 | -0.033201 | -0.0018055 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | 0.0078235 | 0.0099865 | 0.064913 | 0.022275 | 0.06441 | -0.58041 | 4.4335 | -0.67684 | 120.7842 | 120.5955 | 120.5134 | -0.65374 | 9.8178 | 6.8593 | 4.7421 | 120.4623 | 120.6919 | 120.6173 | -0.72276 | 0.087838 | 0.090246 | 0.16117 | 0.064739 | -0.023099 | -0.098475 | -0.18054 | 0.018813 | -0.23167 | 10.5594 | 5.4837 | 5.4649 | -0.002037 | -0.076672 | 121.5258 | 121.3371 | 121.255 | 5.1751 | -121.3477 | 121.2039 | 121.4335 | 121.3589 | 7.6008 | -121.4167
2357.5469 | 121.4859 | -0.71411 | 120.6253 | 1.4211e-13 | -0.032773 | -0.0018055 | 0.062034 | -0.006269 | 0.05476 | -0.0022889 | 0.0082507 | 0.0099865 | 0.065126 | 0.022062 | 0.064196 | -0.56667 | 4.4335 | -0.6631 | 120.7842 | 120.6001 | 120.5134 | -0.64458 | 10.0925 | 7.2256 | 4.9299 | 120.4715 | 120.7011 | 120.6127 | -0.71361 | 0.06953 | 0.15891 | 0.14744 | 0.051007 | -0.018523 | -0.025231 | -0.11188 | 0.000504 | -0.15385 | 10.8066 | 5.644 | 5.6435 | 0.075785 | -0.012585 | 121.4983 | 121.3142 | 121.2275 | 5.1476 | -121.2699 | 121.1856 | 121.4152 | 121.3268 | 7.9397 | -121.3389
2359.3125 | 121.4401 | -0.71869 | 120.7077 | 1.4211e-13 | -0.032987 | -0.0015919 | 0.061607 | -0.006269 | 0.05476 | 0.0053411 | 0.0086779 | 0.010841 | 0.065554 | 0.022489 | 0.064837 | -0.56209 | 4.4655 | -0.66768 | 120.7934 | 120.6092 | 120.518 | -0.64 | 10.3901 | 7.6148 | 5.1634 | 120.4715 | 120.7011 | 120.6265 | -0.71361 | 0.078687 | 0.085669 | 0.1566 | 0.051007 | -0.02768 | -0.098472 | -0.1897 | 0.005082 | -0.23624 | 11.1088 | 5.8821 | 5.877 | -0.006613 | -0.081248 | 121.5121 | 121.3279 | 121.2367 | 5.1842 | -121.3477 | 121.1901 | 121.4198 | 121.3451 | 8.3334 | -121.4213
2361.0938 | 121.4722 | -0.74158 | 120.6116 | 1.4211e-13 | -0.033201 | -0.0018055 | 0.061821 | -0.0060552 | 0.054546 | -0.0099194 | 0.0088915 | 0.011055 | 0.066195 | 0.022275 | 0.065265 | -0.6033 | 4.4427 | -0.69973 | 120.7522 | 120.5726 | 120.4814 | -0.67205 | 10.6603 | 7.9124 | 5.3465 | 120.4303 | 120.6645 | 120.5852 | -0.74566 | 0.069523 | 0.1406 | 0.13828 | 0.041847 | -0.027676 | -0.038972 | -0.1302 | -0.004082 | -0.18132 | 11.4019 | 6.0881 | 6.0922 | 0.052889 | -0.026324 | 121.4937 | 121.3142 | 121.223 | 5.1842 | -121.2836 | 121.1718 | 121.406 | 121.3268 | 8.6539 | -121.3572
2362.8594 | 121.3989 | -0.7782 | 120.6665 | 1.4211e-13 | -0.033201 | -0.0024467 | 0.061821 | -0.006269 | 0.054973 | -0.0099194 | 0.0093189 | 0.011909 | 0.066195 | 0.022916 | 0.065478 | -0.59414 | 4.4518 | -0.686 | 120.7613 | 120.5726 | 120.4814 | -0.6629 | 10.9671 | 8.2741 | 5.5846 | 120.4348 | 120.6736 | 120.5898 | -0.7365 | 0.1153 | 0.09482 | 0.18405 | 0.092203 | -0.023099 | -0.093904 | -0.18513 | 0.041697 | -0.23167 | 11.7453 | 6.3628 | 6.3211 | 0.007115 | -0.076677 | 121.5395 | 121.3508 | 121.2596 | 5.23 | -121.3294 | 121.213 | 121.4518 | 121.368 | 9.0523 | -121.403
2364.5781 | 121.3898 | -0.75531 | 120.6573 | 1.4211e-13 | -0.032773 | -0.0018055 | 0.062034 | -0.006269 | 0.05476 | -0.0099194 | 0.0097461 | 0.012337 | 0.066622 | 0.022703 | 0.065906 | -0.59414 | 4.4655 | -0.69057 | 120.7659 | 120.568 | 120.4814 | -0.66748 | 11.2738 | 8.5809 | 5.809 | 120.444 | 120.6599 | 120.5852 | -0.7365 | 0.087835 | 0.10855 | 0.16117 | 0.064737 | -0.023098 | -0.089328 | -0.17597 | 0.018809 | -0.21336 | 12.0291 | 6.5643 | 6.5455 | 0.002534 | -0.072101 | 121.5212 | 121.3233 | 121.2367 | 5.2209 | -121.3248 | 121.1993 | 121.4152 | 121.3406 | 9.3362 | -121.3939
2366.3594 | 121.4722 | -0.737 | 120.607 | 1.4211e-13 | -0.032987 | -0.0018055 | 0.061607 | -0.0060552 | 0.055187 | -0.0022889 | 0.010387 | 0.012764 | 0.067049 | 0.02313 | 0.066119 | -0.6033 | 4.4747 | -0.69515 | 120.7522 | 120.5589 | 120.4768 | -0.66748 | 11.5898 | 8.8922 | 6.0288 | 120.4348 | 120.6645 | 120.5898 | -0.73192 | 0.069525 | 0.14517 | 0.1337 | 0.041849 | -0.027676 | -0.048132 | -0.1302 | 0.005078 | -0.17216 | 12.3268 | 6.7658 | 6.7607 | 0.057466 | -0.017168 | 121.4892 | 121.2959 | 121.2138 | 5.2117 | -121.2745 | 121.1718 | 121.4015 | 121.3268 | 9.6292 | -121.3389
2368.0625 | 121.4081 | -0.75989 | 120.6573 | 1.4211e-13 | -0.033201 | -0.0018055 | 0.062034 | -0.0064826 | 0.05476 | -0.0022889 | 0.010814 | 0.013405 | 0.067049 | 0.023344 | 0.066333 | -0.58499 | 4.493 | -0.69515 | 120.7567 | 120.5589 | 120.4768 | -0.67205 | 11.8874 | 9.1853 | 6.2256 | 120.4394 | 120.6645 | 120.5852 | -0.7365 | 0.087834 | 0.099396 | 0.1749 | 0.064737 | -0.023097 | -0.098486 | -0.18055 | 0.023387 | -0.21794 | 12.6473 | 6.9855 | 6.9621 | 0.007112 | -0.072101 | 121.5166 | 121.3188 | 121.2367 | 5.2529 | -121.3294 | 121.1993 | 121.4243 | 121.3451 | 9.9451 | -121.3939
2369.8281 | 121.431 | -0.76446 | 120.6528 | 1.4211e-13 | -0.032987 | -0.0022329 | 0.061607 | -0.0060552 | 0.05476 | -0.0099194 | 0.011028 | 0.013619 | 0.06769 | 0.023344 | 0.066974 | -0.59872 | 4.5159 | -0.69973 | 120.7567 | 120.5589 | 120.4722 | -0.67205 | 12.185 | 9.4646 | 6.4317 | 120.4303 | 120.6553 | 120.5761 | -0.74108 | 0.092411 | 0.10397 | 0.16574 | 0.064735 | -0.027676 | -0.093908 | -0.18055 | 0.023385 | -0.22252 | 12.9495 | 7.1961 | 7.1728 | 0.002533 | -0.07668 | 121.5212 | 121.3233 | 121.2367 | 5.2804 | -121.3248 | 121.1947 | 121.4198 | 121.3406 | 10.229 | -121.3939
2371.5469 | 121.4172 | -0.76446 | 120.6573 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.0022889 | 0.011455 | 0.014473 | 0.06769 | 0.023557 | 0.066974 | -0.59414 | 4.548 | -0.686 | 120.7567 | 120.568 | 120.4768 | -0.67205 | 12.5147 | 9.7255 | 6.6194 | 120.4303 | 120.6553 | 120.5852 | -0.7365 | 0.092411 | 0.099396 | 0.17032 | 0.07847 | -0.013941 | -0.089328 | -0.18055 | 0.027964 | -0.22709 | 13.2791 | 7.3839 | 7.3559 | -0.002045 | -0.072101 | 121.5212 | 121.3325 | 121.2413 | 5.3124 | -121.3294 | 121.1947 | 121.4198 | 121.3497 | 10.49 | -121.3939
2373.3125 | 121.3623 | -0.76904 | 120.6436 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.006269 | 0.05476 | -0.0022889 | 0.012096 | 0.0149 | 0.068331 | 0.023985 | 0.067187 | -0.59414 | 4.5525 | -0.686 | 120.7522 | 120.5543 | 120.4768 | -0.66748 | 12.8489 | 9.9545 | 6.8209 | 120.4211 | 120.6553 | 120.5807 | -0.74108 | 0.10157 | 0.10855 | 0.1749 | 0.083048 | -0.01852 | -0.089332 | -0.16682 | 0.027963 | -0.22252 | 13.618 | 7.5899 | 7.562 | 0.011688 | -0.062947 | 121.5212 | 121.3233 | 121.2458 | 5.3216 | -121.3111 | 121.1901 | 121.4243 | 121.3497 | 10.7235 | -121.3847
2375.0156 | 121.4996 | -0.72784 | 120.5887 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061821 | -0.0058416 | 0.054546 | -0.0022889 | 0.012096 | 0.015328 | 0.068331 | 0.023985 | 0.067828 | -0.59872 | 4.5663 | -0.69515 | 120.7384 | 120.5497 | 120.4631 | -0.67205 | 13.1648 | 10.1743 | 6.9811 | 120.4211 | 120.6461 | 120.5624 | -0.75024 | 0.05579 | 0.14975 | 0.12912 | 0.032693 | -0.023097 | -0.038979 | -0.12562 | -0.022393 | -0.16759 | 13.8927 | 7.709 | 7.7314 | 0.057463 | -0.026329 | 121.4663 | 121.2775 | 121.1909 | 5.2941 | -121.2607 | 121.1489 | 121.374 | 121.2902 | 10.9021 | -121.3389
2376.7969 | 121.4584 | -0.75073 | 120.6436 | 1.4211e-13 | -0.033201 | -0.0022329 | 0.062034 | -0.0064826 | 0.05476 | -0.0022889 | 0.013378 | 0.015755 | 0.068545 | 0.024626 | 0.068256 | -0.6033 | 4.5983 | -0.69515 | 120.743 | 120.5497 | 120.4631 | -0.66748 | 13.5037 | 10.4169 | 7.1872 | 120.4165 | 120.6507 | 120.5624 | -0.74108 | 0.083257 | 0.099394 | 0.14743 | 0.055581 | -0.027676 | -0.093911 | -0.18055 | 0.009652 | -0.2271 | 14.2544 | 7.9379 | 7.9282 | 0.00711 | -0.081261 | 121.4937 | 121.3004 | 121.2138 | 5.3491 | -121.3111 | 121.1673 | 121.4015 | 121.3131 | 11.1677 | -121.3847
2378.5781 | 121.4493 | -0.737 | 120.5933 | 1.4211e-13 | -0.03256 | -0.0024467 | 0.062034 | -0.0060552 | 0.054546 | -0.0022889 | 0.013378 | 0.016823 | 0.069186 | 0.024412 | 0.06911 | -0.59414 | 4.5754 | -0.69057 | 120.7384 | 120.5543 | 120.4585 | -0.66748 | 13.8745 | 10.6367 | 7.4069 | 120.4211 | 120.6461 | 120.5624 | -0.7365 | 0.069525 | 0.14517 | 0.14286 | 0.046427 | -0.023098 | -0.038978 | -0.13478 | 0.000499 | -0.17216 | 14.6115 | 8.1439 | 8.1434 | 0.052885 | -0.030907 | 121.4754 | 121.2913 | 121.1955 | 5.3124 | -121.2607 | 121.1581 | 121.3831 | 121.2994 | 11.3737 | -121.3298
2380.3594 | 121.3806 | -0.76904 | 120.6253 | 1.4211e-13 | -0.032987 | -0.0018055 | 0.061821 | -0.006269 | 0.054546 | -0.01755 | 0.013378 | 0.017464 | 0.069186 | 0.024839 | 0.069324 | -0.58956 | 4.5892 | -0.686 | 120.743 | 120.5543 | 120.4585 | -0.66748 | 14.2546 | 10.8382 | 7.613 | 120.4165 | 120.6416 | 120.5669 | -0.7365 | 0.10157 | 0.11771 | 0.17948 | 0.083048 | -0.01852 | -0.071021 | -0.16682 | 0.032542 | -0.20879 | 15.0236 | 8.382 | 8.3495 | 0.016263 | -0.058371 | 121.5121 | 121.3233 | 121.2275 | 5.3582 | -121.2928 | 121.1856 | 121.4106 | 121.336 | 11.6072 | -121.3618
2382.1406 | 121.4035 | -0.76904 | 120.6207 | 1.4211e-13 | -0.033201 | -0.0024467 | 0.061821 | -0.0060552 | 0.054332 | -0.0022889 | 0.014446 | 0.018533 | 0.069613 | 0.024626 | 0.069538 | -0.58956 | 4.6487 | -0.69057 | 120.743 | 120.5543 | 120.4631 | -0.6629 | 14.6483 | 11.0122 | 7.8145 | 120.4165 | 120.6461 | 120.5807 | -0.7365 | 0.10615 | 0.12228 | 0.17948 | 0.07847 | -0.027677 | -0.066444 | -0.15767 | 0.032542 | -0.20421 | 15.4174 | 8.5835 | 8.551 | 0.025419 | -0.040059 | 121.5121 | 121.3233 | 121.2321 | 5.4177 | -121.2836 | 121.1856 | 121.4152 | 121.3497 | 11.7812 | -121.3572
2383.9062 | 121.4355 | -0.74616 | 120.6162 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.061821 | -0.0064826 | 0.054546 | -0.0022889 | 0.01466 | 0.019387 | 0.070468 | 0.024839 | 0.070179 | -0.59872 | 4.6624 | -0.69973 | 120.7293 | 120.5405 | 120.4493 | -0.67205 | 15.0513 | 11.2228 | 8.0571 | 120.3982 | 120.6324 | 120.5532 | -0.7365 | 0.074101 | 0.11312 | 0.14743 | 0.046425 | -0.027676 | -0.075602 | -0.16682 | 0.009654 | -0.21795 | 15.7974 | 8.8033 | 8.7936 | 0.016261 | -0.062952 | 121.4754 | 121.2867 | 121.1955 | 5.4086 | -121.2882 | 121.1444 | 121.3786 | 121.2994 | 11.9689 | -121.3527
2385.6719 | 121.344 | -0.79193 | 120.6665 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061821 | -0.006269 | 0.054332 | -0.0099194 | 0.014874 | 0.020028 | 0.070681 | 0.025053 | 0.07082 | -0.59414 | 4.6487 | -0.69973 | 120.7247 | 120.536 | 120.4539 | -0.67663 | 15.4771 | 11.4609 | 8.2998 | 120.4074 | 120.6324 | 120.5486 | -0.74566 | 0.1153 | 0.058193 | 0.19779 | 0.092201 | -0.023097 | -0.13054 | -0.2126 | 0.046272 | -0.25914 | 16.269 | 9.0917 | 9.0455 | -0.034093 | -0.11789 | 121.5166 | 121.3279 | 121.2458 | 5.4406 | -121.3431 | 121.1993 | 121.4243 | 121.3406 | 12.2528 | -121.4122
2387.3906 | 121.3669 | -0.76446 | 120.6207 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.006269 | 0.054546 | -0.0099194 | 0.015514 | 0.020456 | 0.071108 | 0.025053 | 0.071033 | -0.6033 | 4.6533 | -0.69973 | 120.7247 | 120.5314 | 120.4493 | -0.68121 | 15.8983 | 11.6898 | 8.547 | 120.4028 | 120.6141 | 120.5486 | -0.75024 | 0.083253 | 0.10397 | 0.16117 | 0.064735 | -0.018518 | -0.089338 | -0.1714 | 0.014228 | -0.21795 | 16.6628 | 9.3115 | 9.2973 | -0.006631 | -0.072109 | 121.4892 | 121.2959 | 121.2138 | 5.4177 | -121.3019 | 121.1672 | 121.3786 | 121.3131 | 12.4543 | -121.371
2389.1719 | 121.4127 | -0.78735 | 120.607 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.061393 | -0.006269 | 0.05476 | 0.0053411 | 0.015728 | 0.02131 | 0.071963 | 0.025694 | 0.071461 | -0.6033 | 4.6853 | -0.69973 | 120.7201 | 120.5314 | 120.4493 | -0.67663 | 16.3287 | 11.9508 | 8.8035 | 120.3936 | 120.6141 | 120.544 | -0.75024 | 0.11072 | 0.11312 | 0.18405 | 0.087624 | -0.023097 | -0.075605 | -0.15767 | 0.037117 | -0.21337 | 17.1161 | 9.5908 | 9.5537 | 0.007102 | -0.062954 | 121.5075 | 121.3187 | 121.2367 | 5.4727 | -121.2836 | 121.181 | 121.4015 | 121.3314 | 12.7381 | -121.3572
2390.9375 | 121.431 | -0.75531 | 120.5933 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.061393 | -0.006269 | 0.054546 | -0.0022889 | 0.016583 | 0.022378 | 0.07239 | 0.025694 | 0.071674 | -0.60788 | 4.667 | -0.70431 | 120.7155 | 120.5314 | 120.4447 | -0.68121 | 16.7179 | 12.1935 | 9.0599 | 120.3936 | 120.6141 | 120.5349 | -0.75482 | 0.074098 | 0.12228 | 0.14743 | 0.051002 | -0.023096 | -0.061872 | -0.14851 | 0.000494 | -0.19964 | 17.4732 | 9.8152 | 9.8147 | 0.020835 | -0.058379 | 121.4708 | 121.2867 | 121.2001 | 5.4223 | -121.2745 | 121.1489 | 121.3694 | 121.2902 | 12.9488 | -121.3481
2392.7188 | 121.4539 | -0.72784 | 120.575 | 1.4211e-13 | -0.033628 | -0.0022329 | 0.061821 | -0.006269 | 0.05476 | 0.0053411 | 0.016583 | 0.023447 | 0.072604 | 0.025908 | 0.072529 | -0.61246 | 4.7036 | -0.71347 | 120.7155 | 120.5268 | 120.4402 | -0.68121 | 17.1117 | 12.4041 | 9.298 | 120.389 | 120.6187 | 120.5349 | -0.75482 | 0.046632 | 0.14059 | 0.11539 | 0.014379 | -0.032253 | -0.04814 | -0.13478 | -0.026972 | -0.1859 | 17.8395 | 10.0258 | 10.0528 | 0.043724 | -0.040068 | 121.4434 | 121.2547 | 121.168 | 5.4315 | -121.2562 | 121.1169 | 121.3465 | 121.2627 | 13.1319 | -121.3298
2394.4219 | 121.3531 | -0.79651 | 120.6253 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.0099194 | 0.017437 | 0.024515 | 0.073245 | 0.026121 | 0.072956 | -0.60788 | 4.7265 | -0.70889 | 120.7155 | 120.5177 | 120.4356 | -0.68579 | 17.478 | 12.7017 | 9.5727 | 120.3845 | 120.6095 | 120.5303 | -0.75024 | 0.11072 | 0.090235 | 0.18863 | 0.087623 | -0.023095 | -0.10765 | -0.18971 | 0.046272 | -0.24084 | 18.2745 | 10.3692 | 10.3229 | -0.015787 | -0.095 | 121.512 | 121.3142 | 121.2321 | 5.523 | -121.3111 | 121.181 | 121.406 | 121.3268 | 13.4982 | -121.3755
2396.2188 | 121.3486 | -0.80109 | 120.6162 | 1.4211e-13 | -0.033201 | -0.0022329 | 0.062034 | -0.0066962 | 0.05476 | -0.0022889 | 0.018292 | 0.025156 | 0.073886 | 0.026549 | 0.073597 | -0.61246 | 4.7448 | -0.70431 | 120.7064 | 120.5085 | 120.4219 | -0.69037 | 17.9084 | 12.9215 | 9.8428 | 120.3753 | 120.6095 | 120.5257 | -0.76397 | 0.11072 | 0.090233 | 0.18863 | 0.096778 | -0.013938 | -0.10766 | -0.1943 | 0.037112 | -0.24084 | 18.7095 | 10.6439 | 10.6068 | -0.006632 | -0.090424 | 121.5075 | 121.3096 | 121.2229 | 5.5459 | -121.3065 | 121.1764 | 121.4106 | 121.3268 | 13.7226 | -121.3801
2397.9844 | 121.4493 | -0.75073 | 120.575 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061821 | -0.0064826 | 0.054332 | -0.0099194 | 0.018933 | 0.026652 | 0.0741 | 0.026549 | 0.074024 | -0.61704 | 4.7494 | -0.71347 | 120.6972 | 120.5131 | 120.4356 | -0.68121 | 18.3891 | 13.1458 | 10.1313 | 120.3707 | 120.6049 | 120.5211 | -0.7594 | 0.06952 | 0.12228 | 0.1337 | 0.037267 | -0.032253 | -0.061877 | -0.13936 | -0.008663 | -0.20422 | 19.1399 | 10.882 | 10.8907 | 0.029989 | -0.053803 | 121.448 | 121.2638 | 121.1863 | 5.5001 | -121.2562 | 121.1215 | 121.3557 | 121.2719 | 13.8966 | -121.3343
2399.7031 | 121.4447 | -0.74616 | 120.5521 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.061607 | -0.0064826 | 0.054546 | -0.0022889 | 0.019787 | 0.027934 | 0.075168 | 0.026976 | 0.075093 | -0.61246 | 4.7677 | -0.71804 | 120.6926 | 120.5039 | 120.4173 | -0.69495 | 18.8516 | 13.3839 | 10.3877 | 120.3707 | 120.5912 | 120.5166 | -0.76397 | 0.051206 | 0.14059 | 0.1337 | 0.028112 | -0.023094 | -0.048147 | -0.13479 | -0.017819 | -0.18133 | 19.5978 | 11.1338 | 11.1517 | 0.039141 | -0.035494 | 121.4388 | 121.2501 | 121.1634 | 5.5139 | -121.247 | 121.1169 | 121.3374 | 121.2627 | 14.1301 | -121.316
2401.4844 | 121.3348 | -0.80109 | 120.607 | 1.4211e-13 | -0.033201 | -0.0015919 | 0.061607 | -0.006269 | 0.054546 | -0.0099194 | 0.020001 | 0.028788 | 0.075381 | 0.02719 | 0.075734 | -0.61246 | 4.7769 | -0.71347 | 120.6881 | 120.4902 | 120.4035 | -0.69953 | 19.369 | 13.6586 | 10.6899 | 120.3524 | 120.5912 | 120.5074 | -0.76855 | 0.10156 | 0.081074 | 0.18863 | 0.087621 | -0.013937 | -0.11682 | -0.20345 | 0.032533 | -0.25458 | 20.1701 | 11.491 | 11.4584 | -0.015791 | -0.099583 | 121.4892 | 121.2913 | 121.2046 | 5.578 | -121.3065 | 121.1535 | 121.3923 | 121.3085 | 14.4597 | -121.3755
2403.2656 | 121.4584 | -0.76446 | 120.5566 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.061607 | -0.006269 | 0.05476 | -0.0022889 | 0.020855 | 0.03007 | 0.076022 | 0.027404 | 0.076588 | -0.61704 | 4.7998 | -0.72262 | 120.6881 | 120.4993 | 120.4127 | -0.69953 | 19.8498 | 13.9242 | 10.9921 | 120.3616 | 120.582 | 120.5028 | -0.76855 | 0.064937 | 0.13143 | 0.14743 | 0.041844 | -0.023093 | -0.057304 | -0.14394 | -0.004088 | -0.19506 | 20.6142 | 11.7565 | 11.7606 | 0.025406 | -0.053808 | 121.4525 | 121.2638 | 121.1772 | 5.5642 | -121.2562 | 121.126 | 121.3465 | 121.2673 | 14.6887 | -121.3252
2404.9688 | 121.4355 | -0.77362 | 120.5566 | 1.4211e-13 | -0.033414 | -0.0018055 | 0.061607 | -0.006269 | 0.054973 | -0.0099194 | 0.02171 | 0.031138 | 0.076236 | 0.027831 | 0.077229 | -0.63077 | 4.8135 | -0.71804 | 120.6789 | 120.4856 | 120.4035 | -0.70411 | 20.4038 | 14.2264 | 11.3034 | 120.3478 | 120.5729 | 120.4845 | -0.77771 | 0.069514 | 0.12227 | 0.14285 | 0.055578 | -0.013936 | -0.071041 | -0.1531 | -0.004089 | -0.2088 | 21.1774 | 12.077 | 12.0811 | 0.016248 | -0.072122 | 121.4525 | 121.2592 | 121.1772 | 5.5871 | -121.2607 | 121.1215 | 121.3465 | 121.2581 | 15 | -121.3344
2406.7656 | 121.3806 | -0.80566 | 120.5566 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061607 | -0.006269 | 0.054973 | 0.0053411 | 0.022565 | 0.032634 | 0.076877 | 0.028045 | 0.078084 | -0.63535 | 4.8547 | -0.73178 | 120.6743 | 120.4764 | 120.3944 | -0.70869 | 21.0311 | 14.4553 | 11.5919 | 120.3433 | 120.5729 | 120.4937 | -0.77313 | 0.096978 | 0.11769 | 0.17032 | 0.073886 | -0.023092 | -0.080198 | -0.16226 | 0.032533 | -0.21338 | 21.8367 | 12.3976 | 12.365 | 0.016248 | -0.062965 | 121.48 | 121.2821 | 121.2 | 5.6604 | -121.2653 | 121.1489 | 121.3786 | 121.2993 | 15.261 | -121.3298
2408.4688 | 121.3394 | -0.80109 | 120.5612 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | 0.022992 | 0.033916 | 0.077732 | 0.028258 | 0.078725 | -0.63535 | 4.8456 | -0.73178 | 120.6652 | 120.4719 | 120.3806 | -0.70869 | 21.5988 | 14.7438 | 11.9124 | 120.3341 | 120.5637 | 120.4799 | -0.78229 | 0.0924 | 0.10396 | 0.16574 | 0.069308 | -0.023092 | -0.089354 | -0.18057 | 0.018797 | -0.22711 | 22.3999 | 12.7135 | 12.6947 | 0.002514 | -0.081278 | 121.4663 | 121.2729 | 121.1817 | 5.6467 | -121.2699 | 121.1352 | 121.3648 | 121.281 | 15.5449 | -121.3435
2410.2344 | 121.376 | -0.81024 | 120.5475 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061607 | -0.0064826 | 0.054546 | -0.0022889 | 0.023846 | 0.035625 | 0.078586 | 0.028472 | 0.080007 | -0.6445 | 4.8456 | -0.73178 | 120.656 | 120.4673 | 120.3806 | -0.71784 | 22.2856 | 15.0689 | 12.2924 | 120.3295 | 120.5592 | 120.4754 | -0.78229 | 0.092399 | 0.10854 | 0.16574 | 0.078464 | -0.013935 | -0.0802 | -0.16684 | 0.027953 | -0.21796 | 23.0959 | 13.1027 | 13.0747 | 0.011669 | -0.072123 | 121.4663 | 121.2775 | 121.1909 | 5.6558 | -121.2653 | 121.1398 | 121.3694 | 121.2856 | 15.8791 | -121.3298
2412.0156 | 121.3715 | -0.8194 | 120.5338 | 1.4211e-13 | -0.033201 | -0.0018055 | 0.061607 | -0.0058416 | 0.054546 | -0.0022889 | 0.024274 | 0.037548 | 0.078586 | 0.028899 | 0.080861 | -0.63535 | 4.8685 | -0.74093 | 120.6514 | 120.4627 | 120.3761 | -0.72242 | 22.89 | 15.1834 | 12.5626 | 120.3204 | 120.5546 | 120.4662 | -0.78687 | 0.096975 | 0.11769 | 0.18405 | 0.078463 | -0.018512 | -0.071046 | -0.15768 | 0.032529 | -0.21338 | 23.7094 | 13.382 | 13.3494 | 0.020823 | -0.067548 | 121.4708 | 121.2821 | 121.1955 | 5.6879 | -121.2562 | 121.1398 | 121.374 | 121.2856 | 16.0028 | -121.3206
2413.75 | 121.3165 | -0.8194 | 120.5612 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.061393 | -0.0060552 | 0.05476 | -0.0022889 | 0.025128 | 0.03883 | 0.079441 | 0.029113 | 0.08193 | -0.6445 | 4.9051 | -0.74093 | 120.6469 | 120.4627 | 120.3669 | -0.72242 | 23.4669 | 15.2978 | 12.819 | 120.3112 | 120.5454 | 120.4616 | -0.79145 | 0.096975 | 0.085646 | 0.17489 | 0.078463 | -0.018512 | -0.098512 | -0.19431 | 0.02795 | -0.25001 | 24.2863 | 13.6384 | 13.6104 | -0.0158 | -0.099592 | 121.4663 | 121.2821 | 121.1863 | 5.7245 | -121.2836 | 121.1306 | 121.3648 | 121.281 | 16.1172 | -121.3527
2415.5156 | 121.4401 | -0.78735 | 120.5063 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061821 | -0.0060552 | 0.054973 | -0.0022889 | 0.025769 | 0.04118 | 0.079227 | 0.028899 | 0.082784 | -0.64908 | 4.9097 | -0.74551 | 120.6423 | 120.449 | 120.3623 | -0.72242 | 24.0484 | 15.3802 | 13.0525 | 120.3158 | 120.5363 | 120.4525 | -0.79145 | 0.064932 | 0.136 | 0.13827 | 0.041841 | -0.023091 | -0.057318 | -0.14396 | -0.004093 | -0.19049 | 24.8358 | 13.8398 | 13.8439 | 0.029974 | -0.053819 | 121.4296 | 121.2363 | 121.1497 | 5.697 | -121.2287 | 121.1031 | 121.3236 | 121.2398 | 16.1676 | -121.2977
2417.25 | 121.3348 | -0.8194 | 120.5154 | 1.4211e-13 | -0.032987 | -0.0018055 | 0.061821 | -0.0060552 | 0.054546 | -0.0022889 | 0.026196 | 0.043103 | 0.080082 | 0.029113 | 0.083639 | -0.6445 | 4.9234 | -0.74551 | 120.6331 | 120.4444 | 120.3578 | -0.73158 | 24.6208 | 15.4169 | 13.2906 | 120.3021 | 120.5363 | 120.4525 | -0.8006 | 0.087817 | 0.11769 | 0.17489 | 0.073884 | -0.013933 | -0.071052 | -0.15769 | 0.018793 | -0.21339 | 25.4402 | 14.11 | 14.0912 | 0.020819 | -0.062974 | 121.4525 | 121.2638 | 121.1772 | 5.7428 | -121.247 | 121.1215 | 121.3557 | 121.2719 | 16.2363 | -121.316
2419.0156 | 121.3257 | -0.8194 | 120.5429 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061393 | -0.0064826 | 0.05476 | -0.0022889 | 0.027051 | 0.045026 | 0.080509 | 0.02954 | 0.084493 | -0.64908 | 4.96 | -0.75009 | 120.6331 | 120.4444 | 120.3578 | -0.73158 | 25.1885 | 15.4031 | 13.5058 | 120.3066 | 120.5271 | 120.4479 | -0.79145 | 0.087817 | 0.090221 | 0.17031 | 0.069306 | -0.018511 | -0.098518 | -0.18515 | 0.02795 | -0.23627 | 26.0079 | 14.3252 | 14.2972 | -0.015805 | -0.095018 | 121.4525 | 121.2638 | 121.1772 | 5.7794 | -121.2745 | 121.126 | 121.3465 | 121.2673 | 16.2225 | -121.3344
2420.7969 | 121.3531 | -0.81024 | 120.5338 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061607 | -0.006269 | 0.054973 | 0.0053411 | 0.027692 | 0.047163 | 0.081364 | 0.029968 | 0.085775 | -0.6445 | 5.0104 | -0.74093 | 120.6331 | 120.4352 | 120.3532 | -0.73158 | 25.8296 | 15.5542 | 13.808 | 120.3021 | 120.5271 | 120.4479 | -0.79145 | 0.078662 | 0.099377 | 0.16574 | 0.069308 | -0.009354 | -0.09852 | -0.18058 | 0.018795 | -0.2317 | 26.6398 | 14.6182 | 14.5994 | -0.006649 | -0.085862 | 121.4434 | 121.2455 | 121.1634 | 5.8206 | -121.2653 | 121.1123 | 121.3373 | 121.2581 | 16.3645 | -121.3252
2422.5156 | 121.4035 | -0.80109 | 120.488 | 1.4211e-13 | -0.033842 | -0.0024467 | 0.061607 | -0.006269 | 0.054546 | 0.0053411 | 0.028546 | 0.049299 | 0.082005 | 0.029968 | 0.087057 | -0.64908 | 4.9921 | -0.74551 | 120.624 | 120.4398 | 120.3532 | -0.727 | 26.4248 | 15.7603 | 14.156 | 120.2975 | 120.5271 | 120.4433 | -0.79603 | 0.074085 | 0.136 | 0.152 | 0.055573 | -0.018512 | -0.048165 | -0.1348 | 0.00506 | -0.1905 | 27.2259 | 14.9571 | 14.952 | 0.039127 | -0.044665 | 121.4251 | 121.2409 | 121.1543 | 5.7932 | -121.215 | 121.0986 | 121.3282 | 121.2444 | 16.5614 | -121.284
2424.3125 | 121.4218 | -0.79193 | 120.4697 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.062034 | -0.0064826 | 0.05476 | 0.0053411 | 0.029401 | 0.052077 | 0.082005 | 0.030181 | 0.088125 | -0.65824 | 5.0012 | -0.75925 | 120.6057 | 120.4261 | 120.3394 | -0.73158 | 26.9742 | 15.861 | 14.4398 | 120.2746 | 120.5088 | 120.4296 | -0.80518 | 0.060351 | 0.13599 | 0.13369 | 0.032684 | -0.027667 | -0.043592 | -0.13023 | -0.013252 | -0.19508 | 27.7662 | 15.2318 | 15.245 | 0.039123 | -0.040091 | 121.3976 | 121.218 | 121.1314 | 5.7932 | -121.2012 | 121.0665 | 121.3007 | 121.2215 | 16.6529 | -121.2748
2426.0938 | 121.2845 | -0.86517 | 120.5109 | 1.4211e-13 | -0.033201 | -0.0022329 | 0.062034 | -0.0060552 | 0.05476 | -0.01755 | 0.030256 | 0.054427 | 0.082859 | 0.030609 | 0.089407 | -0.67197 | 5.0287 | -0.76383 | 120.5919 | 120.4123 | 120.3165 | -0.74532 | 27.5328 | 15.9343 | 14.6917 | 120.2654 | 120.4996 | 120.4204 | -0.81892 | 0.11986 | 0.081059 | 0.1932 | 0.10135 | -0.018509 | -0.098526 | -0.19432 | 0.046253 | -0.24544 | 28.398 | 15.5568 | 15.5106 | -0.011232 | -0.090446 | 121.4571 | 121.2775 | 121.1817 | 5.8939 | -121.2562 | 121.1306 | 121.3648 | 121.2856 | 16.7994 | -121.3298
2427.875 | 121.3028 | -0.85602 | 120.4788 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061607 | -0.0060552 | 0.05476 | -0.0022889 | 0.030469 | 0.057418 | 0.0835 | 0.031036 | 0.090689 | -0.67655 | 5.0791 | -0.77756 | 120.5873 | 120.3986 | 120.3211 | -0.75448 | 28.0914 | 15.9526 | 14.9847 | 120.2563 | 120.4905 | 120.4113 | -0.82808 | 0.10154 | 0.10852 | 0.17946 | 0.078457 | -0.023086 | -0.08022 | -0.1577 | 0.027941 | -0.22255 | 28.9475 | 15.8407 | 15.8128 | 0.011654 | -0.06756 | 121.4434 | 121.2546 | 121.1771 | 5.9351 | -121.2333 | 121.1123 | 121.3465 | 121.2673 | 16.8086 | -121.3069
2429.5938 | 121.3943 | -0.83313 | 120.4376 | 1.4211e-13 | -0.033201 | -0.0020193 | 0.062034 | -0.006269 | 0.05476 | -0.0099194 | 0.031965 | 0.061051 | 0.084782 | 0.030822 | 0.091758 | -0.67655 | 5.1249 | -0.78214 | 120.5782 | 120.3894 | 120.3074 | -0.75905 | 28.7187 | 16.154 | 15.3602 | 120.2471 | 120.4859 | 120.3975 | -0.82808 | 0.074076 | 0.14057 | 0.15658 | 0.050991 | -0.023085 | -0.048179 | -0.13023 | 0.005053 | -0.19051 | 29.5518 | 16.1933 | 16.1882 | 0.048274 | -0.040097 | 121.4113 | 121.2226 | 121.1405 | 5.958 | -121.1967 | 121.0802 | 121.319 | 121.2307 | 16.9872 | -121.2657
2431.375 | 121.3715 | -0.82855 | 120.4468 | 1.4211e-13 | -0.033414 | -0.0022329 | 0.061821 | -0.0060552 | 0.05476 | -0.0099194 | 0.032819 | 0.064683 | 0.08585 | 0.031463 | 0.09368 | -0.68113 | 5.1386 | -0.79129 | 120.569 | 120.3803 | 120.2891 | -0.77279 | 29.4559 | 16.4654 | 15.8135 | 120.238 | 120.4676 | 120.3884 | -0.83266 | 0.055761 | 0.12225 | 0.14742 | 0.037257 | -0.018504 | -0.066492 | -0.1577 | -0.004104 | -0.20882 | 30.2844 | 16.642 | 16.6461 | 0.020805 | -0.058409 | 121.3976 | 121.2088 | 121.1176 | 5.9672 | -121.2196 | 121.0665 | 121.2961 | 121.2169 | 17.294 | -121.2794
2433.1094 | 121.4264 | -0.83771 | 120.4193 | 1.4211e-13 | -0.033414 | -0.0024467 | 0.061607 | -0.0060552 | 0.05476 | -0.0022889 | 0.033674 | 0.068529 | 0.086705 | 0.031463 | 0.094962 | -0.69487 | 5.1844 | -0.78672 | 120.5645 | 120.3803 | 120.2937 | -0.77279 | 30.0877 | 16.644 | 16.2026 | 120.2288 | 120.4584 | 120.3746 | -0.83723 | 0.064917 | 0.14514 | 0.14284 | 0.050991 | -0.013926 | -0.039027 | -0.12566 | 0.000473 | -0.19051 | 30.9255 | 17.0404 | 17.0399 | 0.039112 | -0.04468 | 121.4022 | 121.218 | 121.1314 | 6.0221 | -121.1921 | 121.0665 | 121.2961 | 121.2123 | 17.4817 | -121.2565
2434.875 | 121.2936 | -0.89264 | 120.4697 | 1.4211e-13 | -0.032987 | -0.0020193 | 0.062034 | -0.006269 | 0.054973 | -0.0022889 | 0.034742 | 0.074297 | 0.088414 | 0.031677 | 0.096672 | -0.70402 | 5.2302 | -0.80045 | 120.5461 | 120.3574 | 120.2662 | -0.78195 | 30.8799 | 17.0561 | 16.7521 | 120.2196 | 120.4401 | 120.3563 | -0.84639 | 0.11069 | 0.076473 | 0.18861 | 0.092187 | -0.018504 | -0.11227 | -0.20348 | 0.046246 | -0.25002 | 31.7725 | 17.6447 | 17.5985 | -0.029556 | -0.11335 | 121.4388 | 121.25 | 121.1588 | 6.1228 | -121.2516 | 121.1123 | 121.3327 | 121.249 | 17.9487 | -121.3161
2436.6562 | 121.2845 | -0.91095 | 120.4376 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061821 | -0.0064826 | 0.054332 | -0.0022889 | 0.035596 | 0.085621 | 0.089482 | 0.032532 | 0.099449 | -0.72692 | 5.2668 | -0.82334 | 120.5232 | 120.3345 | 120.2387 | -0.80942 | 31.7452 | 17.6375 | 17.3702 | 120.183 | 120.4081 | 120.338 | -0.87387 | 0.10153 | 0.085625 | 0.18403 | 0.087607 | -0.013921 | -0.10313 | -0.19891 | 0.037085 | -0.25461 | 32.6562 | 18.2812 | 18.2441 | -0.029562 | -0.099619 | 121.4342 | 121.2454 | 121.1497 | 6.1777 | -121.247 | 121.094 | 121.319 | 121.249 | 18.5485 | -121.3115
2438.4375 | 121.3211 | -1.4923 | 119.7144 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061607 | -0.0060552 | 0.055187 | 0.0053411 | 0.033033 | 0.41316 | 0.086277 | 0.035737 | 0.11248 | -1.3862 | 5.2164 | -1.4964 | 119.8182 | 119.6293 | 119.5473 | -1.4642 | 38.1966 | 23.045 | 20.525 | 119.455 | 119.6709 | 119.5963 | -1.5378 | 0.028102 | 0.10382 | 0.10611 | -0.004041 | -0.032143 | -0.085013 | -0.16701 | -0.045484 | -0.25932 | 39.689 | 22.0173 | 22.0627 | -0.04345 | -0.11808 | 121.3105 | 121.1217 | 121.0397 | 6.7087 | -121.1786 | 120.9473 | 121.1632 | 121.0886 | 24.5373 | -121.2521
2440.2188 | 121.3257 | -1.4603 | 119.7372 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061607 | -0.0060552 | 0.05476 | -0.0022889 | 0.033246 | 0.49114 | 0.086705 | 0.036805 | 0.11697 | -1.3175 | 5.2531 | -1.4231 | 119.8685 | 119.6843 | 119.5931 | -1.4001 | 39.9091 | 24.3087 | 21.6422 | 119.4917 | 119.7167 | 119.6375 | -1.46 | 0.060163 | 0.13129 | 0.14274 | 0.037168 | -0.022995 | -0.052955 | -0.14412 | 0.000312 | -0.24558 | 41.3693 | 23.1024 | 23.1021 | -0.020553 | -0.099767 | 121.3288 | 121.1446 | 121.0534 | 6.7133 | -121.1373 | 120.9519 | 121.177 | 121.0977 | 25.769 | -121.1972
2441.9219 | 121.1929 | -1.506 | 119.7189 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061821 | -0.0064826 | 0.054546 | -0.0022889 | 0.034528 | 0.56977 | 0.086918 | 0.037233 | 0.12039 | -1.3313 | 5.2668 | -1.4368 | 119.8319 | 119.6568 | 119.5611 | -1.4184 | 41.2827 | 25.2519 | 22.5121 | 119.4459 | 119.6663 | 119.5963 | -1.4737 | 0.087623 | 0.11298 | 0.17478 | 0.069209 | -0.018414 | -0.062118 | -0.15786 | 0.032352 | -0.27306 | 42.7887 | 24.0182 | 23.9858 | -0.052607 | -0.12266 | 121.338 | 121.1629 | 121.0671 | 6.7728 | -121.1374 | 120.9519 | 121.1724 | 121.1023 | 26.758 | -121.1926
2443.7031 | 121.2753 | -1.506 | 119.6411 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061607 | -0.0060552 | 0.05476 | -0.0099194 | 0.035169 | 0.65545 | 0.087559 | 0.03766 | 0.12381 | -1.3816 | 5.308 | -1.4826 | 119.777 | 119.5881 | 119.5016 | -1.455 | 42.583 | 26.1173 | 23.3637 | 119.3818 | 119.6022 | 119.5276 | -1.5241 | 0.050992 | 0.13586 | 0.12442 | 0.023426 | -0.027566 | -0.052982 | -0.13956 | -0.018015 | -0.25933 | 44.0891 | 24.8698 | 24.8878 | -0.038887 | -0.11352 | 121.283 | 121.0942 | 121.0076 | 6.814 | -121.0962 | 120.8878 | 121.1083 | 121.0336 | 27.6234 | -121.1652
2445.4688 | 121.2204 | -1.5976 | 119.5541 | 1.4211e-13 | -0.033842 | -0.0020193 | 0.061393 | -0.006269 | 0.05476 | -0.0022889 | 0.035383 | 0.73044 | 0.088841 | 0.038515 | 0.12786 | -1.4411 | 5.3172 | -1.5467 | 119.69 | 119.5057 | 119.4237 | -1.5192 | 43.833 | 26.8408 | 24.0826 | 119.3039 | 119.5107 | 119.4406 | -1.579 | 0.07844 | 0.13584 | 0.15645 | 0.050883 | -0.027557 | -0.048427 | -0.13042 | 0.018592 | -0.25019 | 45.4306 | 25.6802 | 25.6616 | -0.043484 | -0.11354 | 121.2876 | 121.1033 | 121.0213 | 6.9148 | -121.0733 | 120.9015 | 121.1082 | 121.0382 | 28.4384 | -121.1331
2447.1875 | 121.2479 | -1.6708 | 119.4717 | 1.4211e-13 | -0.033842 | -0.0020193 | 0.061607 | -0.0058416 | 0.054973 | -0.02518 | 0.036878 | 0.8095 | 0.090123 | 0.038942 | 0.13107 | -1.5007 | 5.3492 | -1.6154 | 119.6076 | 119.4279 | 119.3321 | -1.5924 | 44.996 | 27.4268 | 24.7923 | 119.2078 | 119.4282 | 119.3399 | -1.6477 | 0.078419 | 0.13583 | 0.17017 | 0.055451 | -0.022968 | -0.043872 | -0.13959 | 0.023151 | -0.26394 | 46.6669 | 26.4631 | 26.44 | -0.043502 | -0.13187 | 121.2784 | 121.0987 | 121.003 | 7.0201 | -121.0642 | 120.8786 | 121.0991 | 121.0107 | 29.0977 | -121.1194
2448.9531 | 121.2433 | -1.712 | 119.371 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061393 | -0.0058416 | 0.05476 | -0.0099194 | 0.038374 | 0.89154 | 0.090978 | 0.04001 | 0.13385 | -1.5785 | 5.3629 | -1.6886 | 119.5206 | 119.3271 | 119.2406 | -1.6657 | 45.9621 | 27.6191 | 25.2868 | 119.0933 | 119.3138 | 119.2483 | -1.7301 | 0.046355 | 0.14955 | 0.13354 | 0.023398 | -0.022957 | -0.0439 | -0.13046 | -0.018068 | -0.2777 | 47.6742 | 26.9988 | 27.0169 | -0.057259 | -0.12274 | 121.2326 | 121.0392 | 120.9526 | 7.075 | -121.0367 | 120.8054 | 121.0258 | 120.9603 | 29.3312 | -121.1011
2450.7188 | 121.2341 | -1.8494 | 119.252 | 1.4211e-13 | -0.033842 | -0.0024467 | 0.06118 | -0.0058416 | 0.05476 | 0.0053411 | 0.039656 | 0.98405 | 0.091619 | 0.040438 | 0.13727 | -1.693 | 5.3767 | -1.7939 | 119.3878 | 119.2081 | 119.117 | -1.7756 | 46.713 | 27.9259 | 25.8134 | 118.9606 | 119.1764 | 119.1018 | -1.8354 | 0.07379 | 0.13579 | 0.15641 | 0.055426 | -0.018364 | -0.043934 | -0.13506 | 0.013948 | -0.29146 | 48.5624 | 27.6627 | 27.6488 | -0.075598 | -0.15023 | 121.2372 | 121.0574 | 120.9663 | 7.2261 | -121.0276 | 120.8099 | 121.0258 | 120.9511 | 29.7753 | -121.0874
2452.4219 | 121.1151 | -1.973 | 119.1467 | 1.4211e-13 | -0.033628 | -0.0020193 | 0.061393 | -0.0060552 | 0.054332 | -0.0022889 | 0.041365 | 1.0631 | 0.093755 | 0.040438 | 0.14004 | -1.7891 | 5.3767 | -1.8992 | 119.2688 | 119.0845 | 118.9933 | -1.8809 | 47.3815 | 27.9763 | 26.0972 | 118.8369 | 119.0436 | 118.9782 | -1.9362 | 0.092071 | 0.12204 | 0.18386 | 0.073722 | -0.018349 | -0.062279 | -0.1534 | 0.03681 | -0.30979 | 49.3545 | 28.0702 | 28.0334 | -0.10309 | -0.16857 | 121.2417 | 121.0574 | 120.9663 | 7.3496 | -121.0276 | 120.8099 | 121.0166 | 120.9511 | 29.9492 | -121.0829
2454.1875 | 121.1563 | -2.3804 | 118.6752 | 1.4211e-13 | -0.033414 | -0.0020193 | 0.061393 | -0.006269 | 0.054546 | -0.0099194 | 0.043287 | 1.3789 | 0.09461 | 0.040438 | 0.14068 | -2.2561 | 5.3309 | -2.3616 | 118.7743 | 118.5945 | 118.5034 | -2.3205 | 47.4182 | 26.7812 | 25.589 | 118.3104 | 118.5308 | 118.4562 | -2.3895 | 0.059904 | 0.099071 | 0.12427 | 0.018725 | -0.041179 | -0.080727 | -0.17181 | -0.009083 | -0.36482 | 49.7985 | 27.9694 | 27.9785 | -0.1444 | -0.21903 | 121.1547 | 120.9749 | 120.8838 | 7.7113 | -120.9957 | 120.6908 | 120.9112 | 120.8366 | 29.1616 | -121.0647
2455.9688 | 121.0785 | -2.8427 | 118.2037 | 1.4211e-13 | -0.033628 | -0.0018055 | 0.06118 | -0.005628 | 0.054546 | -0.0022889 | 0.044783 | 1.6658 | 0.095892 | 0.041079 | 0.14538 | -2.6361 | 5.3034 | -2.7462 | 118.3577 | 118.1824 | 118.0959 | -2.7051 | 48.6086 | 27.4406 | 26.2071 | 117.8571 | 118.073 | 118.0075 | -2.7695 | 0.13762 | 0.15394 | 0.20661 | 0.096491 | -0.041124 | -0.021334 | -0.10781 | 0.073216 | -0.34659 | 51.4513 | 29.0498 | 28.9766 | -0.13076 | -0.19624 | 121.2004 | 121.0251 | 120.9386 | 8.1461 | -120.9088 | 120.6999 | 120.9157 | 120.8502 | 30.2833 | -120.9732
2457.6875 | 121.0602 | -4.8523 | 116.0294 | 1.4211e-13 | -0.033628 | -0.0018055 | 0.061821 | -0.005628 | 0.05476 | 0.0053411 | 0.043287 | 2.9585 | 0.093755 | 0.043643 | 0.20371 | -4.4446 | 5.0379 | -4.5684 | 116.4439 | 116.2638 | 116.1821 | -4.5138 | 104.6475 | 30.0275 | 27.3564 | 115.8106 | 116.0172 | 115.9563 | -4.5781 | 0.33852 | 0.41455 | 0.40773 | 0.28392 | -0.054605 | 0.23447 | 0.15271 | 0.27417 | -0.21881 | 109.4998 | 32.2087 | 31.9345 | -0.012178 | -0.073077 | 121.2962 | 121.1161 | 121.0344 | 9.8902 | -120.5431 | 120.6628 | 120.8695 | 120.8086 | 34.8798 | -120.6075
2459.4531 | 120.9274 | -4.4357 | 116.3589 | 1.4211e-13 | -0.033628 | -0.0022329 | 0.06118 | -0.0058416 | 0.054546 | -0.0022889 | 0.043715 | 3.4119 | 0.092901 | 0.045566 | 0.2176 | -4.2797 | 5.102 | -4.4036 | 116.508 | 116.3325 | 116.2462 | -4.4039 | 109.3452 | 34.7711 | 29.9937 | 115.838 | 116.0309 | 115.9838 | -4.395 | 0.031852 | 0.14905 | 0.15599 | 0.032171 | 0.000319 | -0.026432 | -0.11278 | 0.040754 | -0.52092 | 113.7809 | 34.4295 | 34.3887 | -0.32803 | -0.3752 | 120.9437 | 120.7682 | 120.6819 | 9.5377 | -120.7628 | 120.2738 | 120.4666 | 120.4195 | 39.2068 | -120.7539
2461.1719 | 120.7855 | -6.5048 | 114.1525 | 1.4211e-13 | -0.033628 | -0.0018055 | 0.06118 | -0.0058416 | 0.054119 | -0.01755 | 0.046065 | 6.2971 | 0.096533 | 0.045779 | 0.21739 | -6.9169 | 4.7219 | -7.0178 | 113.6465 | 113.489 | 113.3845 | -6.9818 | 103.5394 | 31.6072 | 27.274 | 112.6285 | 112.771 | 112.7696 | -6.9912 | -0.47699 | -0.50602 | -0.41207 | -0.51293 | -0.035945 | -0.66352 | -0.76799 | -0.48634 | -1.524 | 110.0442 | 33.7788 | 34.2651 | -1.3816 | -1.383 | 120.1513 | 119.9938 | 119.8894 | 11.2268 | -121.1343 | 119.1333 | 119.2758 | 119.2744 | 38.112 | -121.1437
2462.9375 | 120.694 | -7.9926 | 112.5092 | 1.4211e-13 | -0.033628 | -0.0022329 | 0.061607 | -0.005628 | 0.054546 | -0.0099194 | 0.046065 | 6.3257 | 0.095251 | 0.04813 | 0.23875 | -7.1229 | 4.6487 | -7.2467 | 113.4954 | 113.315 | 113.2472 | -7.2199 | 105.2564 | 36.6392 | 30.0029 | 112.4545 | 112.6199 | 112.591 | -7.2155 | 0.77264 | 0.98627 | 0.86963 | 0.74588 | -0.026755 | 0.80585 | 0.73803 | 0.77703 | -0.05464 | 113.249 | 37.9954 | 37.2184 | 0.1107 | 0.081853 | 121.488 | 121.3076 | 121.2397 | 12.6412 | -119.7291 | 120.4471 | 120.6124 | 120.5836 | 44.6317 | -119.7247
2464.7188 | 121.1014 | -0.40741 | 120.607 | 1.4211e-13 | -0.033842 | -0.0022329 | 0.061607 | -0.005628 | 0.054546 | -0.0099194 | -0.0013631 | 0.026652 | -0.0047366 | 0.018429 | 0.021252 | -0.24161 | 5.8712 | -0.3472 | 120.7384 | 120.5543 | 120.4585 | -0.35153 | -0.063054 | -0.19653 | -0.38144 | -0.075739 | -0.022922 | -0.005985 | -0.40683 | 0.05588 | 0.13144 | 0.1658 | 0.060208 | 0.004328 | -0.052711 | -0.14851 | 0.000584 | -120.6827 | 0.34436 | 0.025971 | 0.025387 | -120.6299 | -120.613 | 121.1458 | 120.9617 | 120.8659 | 6.2786 | -120.9585 | 0.33167 | 0.38449 | 0.40142 | 0.21088 | -121.0138
2466.4219 | 121.17 | -0.40741 | 120.6711 | 1.4211e-13 | -0.034055 | -0.0020193 | 0.061607 | -0.0058416 | 0.054546 | -0.0099194 | -0.0013631 | 0.025797 | -0.004523 | 0.018643 | 0.020611 | -0.24161 | 5.9399 | -0.36094 | 120.8025 | 120.6138 | 120.5226 | -0.35611 | -0.081369 | -0.19653 | -0.34481 | -0.089475 | -0.041237 | -0.033457 | -0.40225 | 0.051302 | 0.13145 | 0.1658 | 0.046473 | -0.004829 | -0.057272 | -0.1485 | 0.005163 | -120.7606 | 0.32604 | 0.0626 | 0.057437 | -120.7123 | -120.7045 | 121.2099 | 121.0212 | 120.93 | 6.3473 | -121.0272 | 0.31793 | 0.36617 | 0.37395 | 0.21088 | -121.0733
2468.2031 | 121.2341 | -0.39368 | 120.7169 | 1.4211e-13 | -0.033628 | -0.0024467 | 0.061607 | -0.0054142 | 0.05476 | -0.0022889 | -0.0011493 | 0.02537 | -0.0043092 | 0.018429 | 0.020825 | -0.25076 | 6.004 | -0.36094 | 120.83 | 120.6504 | 120.5592 | -0.36527 | -0.085948 | -0.20568 | -0.31734 | -0.10779 | -0.054973 | -0.047193 | -0.41598 | 0.028411 | 0.11314 | 0.14291 | 0.03274 | 0.004329 | -0.066416 | -0.15765 | -0.022307 | -120.8246 | 0.30773 | 0.076339 | 0.098646 | -120.7718 | -120.7641 | 121.2237 | 121.0441 | 120.9529 | 6.3976 | -121.0821 | 0.28589 | 0.3387 | 0.34648 | 0.18799 | -121.1328
2469.9688 | 121.1105 | -0.43488 | 120.7764 | 1.4211e-13 | -0.033842 | -0.0020193 | 0.061393 | -0.0058416 | 0.054973 | -0.0022889 | -0.0011493 | 0.025156 | -0.004523 | 0.018216 | 0.021038 | -0.24618 | 6.0726 | -0.36094 | 120.8575 | 120.6688 | 120.5729 | -0.35611 | -0.090527 | -0.21026 | -0.3036 | -0.11237 | -0.06413 | -0.05635 | -0.42514 | 0.078767 | 0.081103 | 0.18869 | 0.073938 | -0.004829 | -0.10761 | -0.20342 | 0.009734 | -120.8887 | 0.34435 | 0.13127 | 0.12154 | -120.8405 | -120.8327 | 121.2923 | 121.1036 | 121.0078 | 6.5075 | -121.1325 | 0.32251 | 0.37074 | 0.37853 | 0.22461 | -121.2015
2471.6875 | 121.2891 | -0.41199 | 120.7214 | 1.4211e-13 | -0.033842 | -0.0022329 | 0.061607 | -0.0054142 | 0.054546 | 0.0053411 | -0.0011493 | 0.024942 | -0.004523 | 0.018216 | 0.020611 | -0.25534 | 6.1093 | -0.35636 | 120.8575 | 120.6779 | 120.5913 | -0.35611 | -0.10426 | -0.21026 | -0.31276 | -0.1261 | -0.068708 | -0.05635 | -0.41598 | 0.055879 | 0.13603 | 0.15664 | 0.055628 | -0.000251 | -0.043521 | -0.13017 | -0.003997 | -120.8475 | 0.30772 | 0.099228 | 0.10323 | -120.7901 | -120.7778 | 121.2695 | 121.0899 | 121.0032 | 6.5212 | -121.0775 | 0.28588 | 0.34328 | 0.35564 | 0.20172 | -121.1374
2473.4531 | 121.2158 | -0.41657 | 120.7535 | 1.4211e-13 | -0.033628 | -0.0022329 | 0.062034 | -0.005628 | 0.054546 | -0.0022889 | -0.0011493 | 0.025156 | -0.004523 | 0.018429 | 0.020397 | -0.25992 | 6.1459 | -0.35636 | 120.8712 | 120.6871 | 120.605 | -0.36069 | -0.099684 | -0.21484 | -0.29902 | -0.1261 | -0.087023 | -0.065507 | -0.42056 | 0.055878 | 0.11773 | 0.15664 | 0.060206 | 0.004328 | -0.066406 | -0.14848 | -0.003998 | -120.8796 | 0.31688 | 0.11754 | 0.12154 | -120.8405 | -120.819 | 121.2878 | 121.1036 | 121.0216 | 6.5625 | -121.1142 | 0.29046 | 0.32954 | 0.35106 | 0.20173 | -121.174
2475.2344 | 121.1517 | -0.44861 | 120.7809 | 1.4211e-13 | -0.033414 | -0.0022329 | 0.061607 | -0.0058416 | 0.054332 | -0.0022889 | -0.0011493 | 0.024942 | -0.0043092 | 0.018429 | 0.020397 | -0.25992 | 6.155 | -0.35636 | 120.8804 | 120.6962 | 120.605 | -0.36527 | -0.10884 | -0.21026 | -0.29444 | -0.13068 | -0.082444 | -0.070086 | -0.42056 | 0.083342 | 0.099417 | 0.18869 | 0.092249 | 0.008907 | -0.084714 | -0.17595 | 0.028045 | -120.9116 | 0.33977 | 0.15416 | 0.12612 | -120.8634 | -120.851 | 121.329 | 121.1448 | 121.0536 | 6.6037 | -121.1462 | 0.31793 | 0.36616 | 0.37852 | 0.23835 | -121.2015
2476.9375 | 121.2021 | -0.43945 | 120.7672 | 1.4211e-13 | -0.033628 | -0.0022329 | 0.061607 | -0.0060552 | 0.054546 | -0.0099194 | -0.0011493 | 0.024942 | -0.0047366 | 0.018643 | 0.020397 | -0.26908 | 6.2054 | -0.37467 | 120.8804 | 120.6962 | 120.6004 | -0.36984 | -0.10884 | -0.20568 | -0.28986 | -0.13984 | -0.091601 | -0.070086 | -0.42972 | 0.069608 | 0.11315 | 0.17038 | 0.064781 | -0.004827 | -0.070981 | -0.16679 | 0.009733 | -120.907 | 0.33061 | 0.14959 | 0.13986 | -120.8588 | -120.8373 | 121.3198 | 121.1357 | 121.0399 | 6.6449 | -121.1371 | 0.29961 | 0.34785 | 0.36937 | 0.23377 | -121.1969
2478.7031 | 121.2296 | -0.42572 | 120.7581 | 1.4211e-13 | -0.033842 | -0.0020193 | 0.061607 | -0.0058416 | 0.05476 | -0.01755 | -0.00093566 | 0.025156 | -0.0043092 | 0.018216 | 0.020397 | -0.2645 | 6.2237 | -0.37467 | 120.8804 | 120.6962 | 120.605 | -0.36984 | -0.11342 | -0.21026 | -0.28529 | -0.13984 | -0.087023 | -0.065507 | -0.4343 | 0.055875 | 0.12231 | 0.16122 | 0.051048 | -0.004827 | -0.061826 | -0.15306 | -0.008579 | -120.8979 | 0.3123 | 0.14043 | 0.14901 | -120.8451 | -120.8236 | 121.3061 | 121.122 | 121.0307 | 6.6494 | -121.1279 | 0.28588 | 0.3387 | 0.36021 | 0.21546 | -121.1924
2480.4688 | 121.3028 | -0.41657 | 120.7672 | 1.4211e-13 | -0.033842 | -0.0022329 | 0.061393 | -0.0058416 | 0.054546 | -0.0022889 | -0.0013631 | 0.024729 | -0.004523 | 0.018429 | 0.020397 | -0.26908 | 6.2924 | -0.37009 | 120.8849 | 120.7054 | 120.6187 | -0.36984 | -0.099684 | -0.21026 | -0.28529 | -0.13068 | -0.091601 | -0.070086 | -0.42056 | 0.04672 | 0.11773 | 0.14749 | 0.046471 | -0.000249 | -0.061823 | -0.14848 | -0.003998 | -120.8979 | 0.31688 | 0.13128 | 0.13528 | -120.8588 | -120.8373 | 121.3015 | 121.122 | 121.0353 | 6.709 | -121.1371 | 0.28588 | 0.32496 | 0.34648 | 0.2063 | -121.1878
2482.1875 | 121.225 | -0.44403 | 120.7718 | 1.4211e-13 | -0.033842 | -0.0022329 | 0.06118 | -0.005628 | 0.054332 | 0.0053411 | -0.0013631 | 0.024942 | -0.0047366 | 0.018429 | 0.020184 | -0.27823 | 6.329 | -0.37925 | 120.8849 | 120.6962 | 120.605 | -0.38358 | -0.10884 | -0.21484 | -0.28986 | -0.13068 | -0.09618 | -0.074664 | -0.43888 | 0.060449 | 0.11315 | 0.1658 | 0.064781 | 0.004332 | -0.075559 | -0.16679 | 0.005153 | -120.9025 | 0.33519 | 0.15417 | 0.14901 | -120.868 | -120.8465 | 121.329 | 121.1403 | 121.049 | 6.7731 | -121.1554 | 0.31335 | 0.34785 | 0.36937 | 0.22919 | -121.2107
2483.9688 | 121.1975 | -8.876 | 112.2345 | 1.4211e-13 | -0.034055 | -0.0020193 | 0.06118 | -0.005628 | 0.05476 | -0.0022889 | -0.0011493 | 0.022378 | -0.0017456 | 0.02078 | 0.23918 | -8.794 | 4.8044 | -8.9361 | 112.3096 | 112.1886 | 112.1163 | -8.8683 | -3.6299 | -5.5261 | -5.8255 | -3.4867 | -3.4386 | -3.4262 | -8.8685 | 0.007709 | 0.075123 | 0.082002 | -0.060018 | -0.067727 | -0.045908 | -0.11823 | 0.007558 | -115.7212 | 5.2462 | 3.0505 | 3.043 | -115.6731 | -115.6607 | 121.1857 | 121.0646 | 120.9923 | 13.6804 | -121.1028 | 5.3893 | 5.4375 | 5.4498 | 3.3499 | -121.103
2485.6719 | 121.1288 | -8.9264 | 112.2391 | 1.4211e-13 | -0.033842 | -0.0022329 | 0.061393 | -0.0060552 | 0.05476 | -0.0099194 | -0.0011493 | 0.022378 | -0.0017456 | 0.02078 | 0.23939 | -8.8123 | 4.7952 | -8.9452 | 112.3142 | 112.1932 | 112.1208 | -8.8317 | -3.5887 | -5.4804 | -5.7797 | -3.4272 | -3.3882 | -3.3667 | -8.8868 | 0.094694 | 0.075123 | 0.11404 | -0.018821 | -0.11352 | -0.045907 | -0.11823 | 0.039596 | -115.6663 | 5.3377 | 3.1467 | 3.1071 | -115.6273 | -115.6058 | 121.2406 | 121.1196 | 121.0472 | 13.7216 | -121.0708 | 5.4992 | 5.5382 | 5.5597 | 3.446 | -121.1259
2487.4375 | 121.138 | -8.8257 | 112.3764 | 1.4211e-13 | -0.033842 | -0.0018055 | 0.061393 | -0.005628 | 0.05476 | -0.0099194 | -0.0011493 | 0.022592 | -0.0021728 | 0.020566 | 0.24153 | -8.7345 | 4.8547 | -8.8857 | 112.4058 | 112.2847 | 112.2124 | -8.763 | -3.6573 | -5.4712 | -5.7523 | -3.5005 | -3.4615 | -3.4354 | -8.8181 | 0.06267 | 0.029362 | 0.091167 | -0.060011 | -0.12268 | -0.091657 | -0.16398 | 0.007571 | -115.8769 | 5.1683 | 3.0734 | 3.0658 | -115.8379 | -115.8118 | 121.2314 | 121.1104 | 121.0381 | 13.6804 | -121.1394 | 5.3252 | 5.3642 | 5.3903 | 3.3545 | -121.1945
2489.1406 | 121.2341 | -10.0937 | 111.0626 | 1.4211e-13 | -0.034269 | -0.0020193 | 0.061607 | -0.005628 | 0.05476 | -0.0099194 | -0.0011493 | 0.022378 | -0.0019592 | 0.02078 | 0.24409 | -8.8902 | 4.8318 | -9.0414 | 112.2547 | 112.1474 | 112.0659 | -8.9233 | -3.7398 | -5.5628 | -5.8255 | -3.5829 | -3.5347 | -3.5224 | -8.9646 | 1.1704 | 1.1921 | 1.2035 | 1.0523 | -0.11808 | 1.0848 | 1.0033 | 1.1291 | -114.6455 | 6.3539 | 4.2682 | 3.1391 | -114.5973 | -114.585 | 122.3484 | 122.2411 | 122.1596 | 14.9255 | -119.9859 | 6.5108 | 6.559 | 6.5713 | 4.5309 | -120.0273
2490.9219 | 121.1838 | -18.4433 | 103.7384 | 1.4211e-13 | -0.034269 | -0.0026603 | 0.061393 | -0.0058416 | 0.05476 | -0.0099194 | -0.0017903 | 0.021524 | -0.00067718 | 0.02313 | 0.47911 | -17.0718 | 3.3942 | -17.1907 | 104.1784 | 104.0015 | 103.9847 | -17.0875 | -8.0346 | -10.9244 | -11.2925 | -7.1953 | -7.1793 | -7.0799 | -17.0783 | 1.3558 | 0.44 | 1.3715 | 1.2526 | -0.1032 | 0.26307 | 0.24627 | 1.365 | -110.9337 | 10.4087 | 7.1508 | 5.7858 | -110.9177 | -110.8183 | 122.6217 | 122.4448 | 122.428 | 21.8374 | -120.8259 | 11.248 | 11.264 | 11.3634 | 7.5189 | -120.8167
2492.7031 | 121.0236 | -70.9305 | 49.6674 | 1.4211e-13 | -0.034696 | -0.0024467 | 0.060752 | -0.0052006 | 0.055187 | -0.0099194 | -0.011404 | 0.031779 | -0.0013182 | 0.033814 | 3.1079 | -69.8423 | -5.0305 | -69.96 | 50.8036 | 50.7028 | 50.7584 | -70.0885 | -45.3236 | -50.6997 | -50.9899 | -8.8344 | -9.1435 | -8.7649 | -69.8125 | 0.84193 | 1.1362 | 1.0882 | 0.97052 | 0.12859 | 1.0354 | 1.0911 | 1.1179 | -58.5018 | 25.6069 | 19.9406 | 18.8226 | -58.8109 | -58.4322 | 121.734 | 121.6333 | 121.6889 | 65.9 | -119.7559 | 62.0961 | 61.787 | 62.1656 | 20.2308 | -119.4799
2494.4844 | 120.8542 | -80.8319 | 39.6194 | 1.4211e-13 | -0.034483 | -0.0026603 | 0.060325 | -0.0058416 | 0.054973 | -0.0099194 | -0.013754 | 0.03648 | -0.0034548 | 0.035096 | 5.3739 | -80.6564 | -6.6971 | -80.7555 | 39.7239 | 39.6172 | 39.7148 | -80.9818 | -54.8702 | -59.532 | -59.6574 | -8.8344 | -9.1527 | -8.774 | -80.4308 | -0.1499 | 0.10441 | 0.1755 | 0.076366 | 0.22627 | -0.002232 | 0.095382 | 0.40109 | -48.4538 | 25.9617 | 21.1745 | 20.7734 | -48.7721 | -48.3935 | 120.5558 | 120.4491 | 120.5467 | 74.1348 | -120.6013 | 71.9975 | 71.6793 | 72.0579 | 21.2999 | -120.0503
2496.2188 | 120.6894 | -86.2564 | 34.1721 | 1.4211e-13 | -0.034483 | -0.0028739 | 0.060539 | -0.005628 | 0.055187 | 0.0053411 | -0.028281 | 0.069811 | -0.022042 | 0.031677 | 4.7763 | -85.5095 | -7.5853 | -85.6314 | 34.7517 | 34.6582 | 34.7562 | -85.8675 | -75.1905 | -67.7966 | -68.6134 | -8.839 | -9.1527 | -8.774 | -85.3988 | 0.38889 | 0.57967 | 0.74691 | 0.625 | 0.23611 | 0.48618 | 0.58414 | 0.85758 | -43.011 | 11.0659 | 17.643 | 16.7855 | -43.3247 | -42.9461 | 121.0081 | 120.9146 | 121.0126 | 78.6711 | -120.0396 | 77.4174 | 77.1038 | 77.4824 | 18.4598 | -119.5709
2498 | 120.4514 | -85.4782 | 34.7763 | 1.4211e-13 | -0.034696 | -0.0026603 | 0.060325 | -0.005628 | 0.054973 | 0.0053411 | -0.027427 | 0.070024 | -0.022897 | 0.031036 | 6.9039 | -82.0711 | -6.9169 | -82.2893 | 37.9017 | 37.9139 | 37.8788 | -82.4013 | -71.7382 | -65.3607 | -65.3488 | -8.839 | -9.1527 | -8.7694 | -81.6121 | 3.0769 | 3.1254 | 3.4071 | 3.1889 | 0.11201 | 3.1375 | 3.1025 | 3.8661 | -43.6153 | 13.74 | 20.1295 | 16.2634 | -43.929 | -43.5457 | 123.3799 | 123.3921 | 123.357 | 78.5613 | -117.1776 | 76.6392 | 76.3256 | 76.7088 | 20.1175 | -116.3885
2499.7812 | 120.2316 | -87.7579 | 32.4142 | 1.4211e-13 | -0.034696 | -0.0030877 | 0.060325 | -0.005628 | 0.055401 | -0.0099194 | -0.027427 | 0.068315 | -0.022042 | 0.032318 | 7.0188 | -89.0623 | -8.4644 | -89.2116 | 30.6907 | 30.5922 | 30.7225 | -89.4528 | -73.7986 | -71.2535 | -69.433 | -8.8436 | -9.1618 | -8.7786 | -87.6287 | -1.6949 | -1.7235 | -1.3045 | -1.4538 | 0.2412 | -1.8221 | -1.6918 | 0.12916 | -41.2578 | 13.9593 | 18.3249 | 18.1958 | -41.5761 | -41.1928 | 118.4486 | 118.35 | 118.4803 | 79.2934 | -121.8671 | 78.9143 | 78.5961 | 78.9793 | 16.5044 | -120.043
2501.5 | 120.9183 | -119.5312 | 1.149 | 1.4211e-13 | -0.035124 | -0.0030877 | 0.060325 | -0.0058416 | 0.055828 | -0.0099194 | -0.00072206 | 0.02537 | -0.0043092 | 0.018429 | 0.015483 | -118.9913 | -13.9084 | -119.268 | 1.1601 | 1.1405 | 1.25 | -119.6142 | 0.097201 | 0.11025 | 0.021487 | 0.066194 | 0.1007 | 0.13595 | -0.040521 | -0.082948 | 0.011111 | 0.54 | 0.26321 | 0.34616 | -0.008476 | 0.101 | 119.4907 | -1.0828 | 119.6285 | 119.5527 | 0.062008 | -1.0483 | -1.013 | 120.6913 | 120.6718 | 120.7812 | 105.6229 | -120.7632 | 119.5974 | 119.632 | 119.6672 | 119.6415 | -1.1895
2503.2969 | 121.0648 | -119.014 | 1.7349 | 1.4211e-13 | -0.034696 | -0.0030877 | 0.060325 | -0.0054142 | 0.055401 | 0.0053411 | -0.0011493 | 0.025156 | -0.003882 | 0.018429 | 0.013988 | -118.4785 | -14.087 | -118.7553 | 1.7416 | 1.7312 | 1.836 | -119.0373 | 0.11094 | 0.11025 | 0.035223 | 0.070773 | 0.10986 | 0.14053 | -0.017627 | -0.023277 | 0.006629 | 0.5355 | 0.2587 | 0.28198 | -0.003732 | 0.10113 | 118.9963 | -1.6642 | 119.1249 | 119.0492 | 0.05285 | -1.6251 | -1.5944 | 120.7555 | 120.7452 | 120.85 | 104.927 | -120.7722 | 119.0847 | 119.1238 | 119.1545 | 119.1242 | -1.7526
2505 | 121.0052 | -118.5608 | 2.2202 | 1.4211e-13 | -0.034696 | -0.0028739 | 0.060539 | -0.005628 | 0.055828 | -0.0099194 | -0.0013631 | 0.025156 | -0.003882 | 0.018857 | 0.014202 | -118.0161 | -14.2152 | -118.2974 | 2.236 | 2.2166 | 2.326 | -118.5748 | 0.11094 | 0.11483 | 0.035223 | 0.066194 | 0.11444 | 0.13595 | -0.017627 | -0.013991 | 0.015865 | 0.54473 | 0.26335 | 0.27734 | -0.003596 | 0.10581 | 118.5432 | -2.154 | 118.6717 | 118.596 | 0.05285 | -2.1057 | -2.0842 | 120.7968 | 120.7773 | 120.8867 | 104.3456 | -120.7949 | 118.627 | 118.6752 | 118.6967 | 118.6756 | -2.2378
2506.7969 | 121.0876 | -117.9337 | 2.8519 | 1.4211e-13 | -0.03491 | -0.0030877 | 0.060325 | -0.005628 | 0.056255 | -0.0022889 | -0.0011493 | 0.02537 | -0.003882 | 0.018857 | 0.014202 | -117.485 | -14.2793 | -117.7709 | 2.79 | 2.7752 | 2.88 | -118.039 | 0.12009 | 0.11025 | 0.053538 | 0.075351 | 0.10986 | 0.14053 | -0.022205 | -0.10539 | -0.061864 | 0.44869 | 0.16271 | 0.26811 | -0.076681 | 0.028102 | 117.9115 | -2.7765 | 118.0537 | 117.9872 | 0.075743 | -2.742 | -2.7113 | 120.7237 | 120.7088 | 120.8136 | 103.6544 | -120.8909 | 118.009 | 118.0435 | 118.0742 | 118.0439 | -2.8741
2508.5156 | 121.0144 | -117.7826 | 3.0441 | 1.4211e-13 | -0.035124 | -0.0030877 | 0.060539 | -0.005628 | 0.056042 | 0.0053411 | -0.0011493 | 0.024942 | -0.003882 | 0.018002 | 0.013774 | -117.2332 | -14.412 | -117.5146 | 3.0647 | 3.0362 | 3.1455 | -117.7826 | 0.11552 | 0.10567 | 0.044381 | 0.075351 | 0.11444 | 0.13595 | -0.013048 | -3.5e-05 | 0.020579 | 0.54944 | 0.26804 | 0.26807 | -0.007942 | 0.1014 | 117.7695 | -2.9688 | 117.8981 | 117.827 | 0.057429 | -2.9297 | -2.9082 | 120.8473 | 120.8188 | 120.9281 | 103.3706 | -120.8268 | 117.8579 | 117.897 | 117.9185 | 117.8883 | -3.0572
2510.2812 | 121.0144 | -117.897 | 2.9892 | 1.4211e-13 | -0.03491 | -0.0033013 | 0.060325 | -0.0052006 | 0.055828 | -0.0022889 | -0.0013631 | 0.025156 | -0.0036684 | 0.018643 | 0.013774 | -117.343 | -14.6455 | -117.6244 | 2.9594 | 2.94 | 3.054 | -117.8879 | 0.11552 | 0.10567 | 0.058117 | 0.07993 | 0.10528 | 0.13595 | -0.008469 | 0.00909 | -0.029793 | 0.554 | 0.2726 | 0.26351 | -0.049168 | 0.06476 | 117.8886 | -2.9093 | 118.0125 | 117.9552 | 0.066586 | -2.8839 | -2.8532 | 120.8564 | 120.8371 | 120.951 | 103.2515 | -120.8771 | 117.977 | 118.0023 | 118.033 | 118.0027 | -2.9977
2512.0469 | 121.0007 | -117.9474 | 2.9663 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060325 | -0.0054142 | 0.055828 | 0.0053411 | -0.00093566 | 0.025156 | -0.0040956 | 0.018429 | 0.013774 | -117.3476 | -14.8058 | -117.629 | 2.9502 | 2.9309 | 3.0494 | -117.9063 | 0.12009 | 0.10109 | 0.053538 | 0.070773 | 0.10528 | 0.13595 | -0.00389 | 0.041129 | -0.016062 | 0.59978 | 0.31837 | 0.27724 | -0.035438 | 0.08307 | 117.9435 | -2.8955 | 118.0675 | 118.0009 | 0.057428 | -2.861 | -2.8304 | 120.8976 | 120.8783 | 120.9968 | 103.1416 | -120.8726 | 118.0182 | 118.0527 | 118.0833 | 118.0485 | -2.9702
2513.7656 | 120.9824 | -117.8833 | 3.0167 | 1.4211e-13 | -0.03491 | -0.0033013 | 0.060325 | -0.005628 | 0.055614 | -0.0099194 | -0.0011493 | 0.024942 | -0.0036684 | 0.018216 | 0.013988 | -117.3201 | -14.9889 | -117.6061 | 2.9823 | 2.9721 | 3.0768 | -117.8788 | 0.10636 | 0.091933 | 0.053538 | 0.084508 | 0.10986 | 0.13137 | -0.00389 | 0.004515 | -0.034367 | 0.56316 | 0.27718 | 0.27266 | -0.044582 | 0.060187 | 117.8794 | -2.9322 | 117.9897 | 117.9368 | 0.057428 | -2.9068 | -2.8853 | 120.8656 | 120.8554 | 120.9602 | 102.8944 | -120.8954 | 117.9678 | 117.9932 | 118.0147 | 117.9752 | -3.0206
2515.5312 | 121.1426 | -117.8146 | 3.0121 | 1.4211e-13 | -0.035124 | -0.0033013 | 0.060752 | -0.0058416 | 0.056042 | -0.0022889 | -0.0011493 | 0.02537 | -0.0040956 | 0.018643 | 0.014202 | -117.3064 | -15.2362 | -117.5924 | 3.0098 | 2.995 | 3.0952 | -117.8559 | 0.11552 | 0.10109 | 0.053538 | 0.075351 | 0.10528 | 0.13595 | -0.00389 | -0.041255 | -0.002319 | 0.50823 | 0.22225 | 0.2635 | -0.017109 | 0.08308 | 117.8107 | -2.9367 | 117.9302 | 117.8682 | 0.057428 | -2.9068 | -2.8761 | 120.8244 | 120.8096 | 120.9098 | 102.5785 | -120.868 | 117.89 | 117.9199 | 117.9506 | 117.9157 | -3.016
2517.25 | 121.0922 | -117.8513 | 3.0396 | 1.4211e-13 | -0.03491 | -0.0033013 | 0.060325 | -0.0052006 | 0.055828 | -0.0099194 | -0.0013631 | 0.025156 | -0.0040956 | 0.018857 | 0.013988 | -117.2972 | -15.4422 | -117.5832 | 3.0189 | 2.9996 | 3.1089 | -117.8559 | 0.12467 | 0.096512 | 0.062695 | 0.070773 | 0.10528 | 0.13595 | 0.005267 | -0.004634 | -0.020628 | 0.55401 | 0.26803 | 0.27266 | -0.039996 | 0.069349 | 117.8565 | -2.9688 | 117.9759 | 117.914 | 0.057428 | -2.9343 | -2.9036 | 120.8702 | 120.8508 | 120.9602 | 102.409 | -120.8954 | 117.922 | 117.9565 | 117.9872 | 117.9478 | -3.0343
2519.0312 | 121.0556 | -117.6636 | 3.1952 | 1.4211e-13 | -0.035124 | -0.0030877 | 0.060539 | -0.0054142 | 0.055828 | -0.02518 | -0.0011493 | 0.025156 | -0.0040956 | 0.018643 | 0.013774 | -117.1462 | -15.6025 | -117.4367 | 3.1746 | 3.1552 | 3.2646 | -117.7048 | 0.12009 | 0.10109 | 0.058117 | 0.075351 | 0.10986 | 0.13595 | 0.000689 | -0.041213 | -0.020602 | 0.51741 | 0.22685 | 0.26806 | -0.039952 | 0.069383 | 117.6643 | -3.1198 | 117.7837 | 117.7217 | 0.057428 | -3.0853 | -3.0592 | 120.8382 | 120.8188 | 120.9281 | 102.0611 | -120.9 | 117.7389 | 117.7734 | 117.7995 | 117.7647 | -3.1945
2520.7344 | 121.1472 | -117.7094 | 3.1219 | 1.4211e-13 | -0.035124 | -0.0035151 | 0.060752 | -0.0054142 | 0.055828 | -0.0022889 | -0.0013631 | 0.024942 | -0.0040956 | 0.018643 | 0.013774 | -117.1965 | -15.8222 | -117.4734 | 3.1425 | 3.1186 | 3.2234 | -117.7506 | 0.12009 | 0.096512 | 0.058117 | 0.075351 | 0.11444 | 0.13137 | -0.00389 | -0.041225 | 0.020591 | 0.51283 | 0.236 | 0.27722 | -0.003341 | 0.10142 | 117.7055 | -3.0466 | 117.8294 | 117.7675 | 0.062007 | -3.0075 | -2.9906 | 120.8519 | 120.828 | 120.9327 | 101.8871 | -120.8725 | 117.7847 | 117.8238 | 117.8407 | 117.8059 | -3.1258
2522.5 | 121.0693 | -117.7505 | 3.1357 | 1.4211e-13 | -0.035337 | -0.0033013 | 0.060539 | -0.0058416 | 0.055828 | -0.0099194 | -0.0011493 | 0.024729 | -0.0043092 | 0.018643 | 0.014202 | -117.2103 | -15.9642 | -117.4917 | 3.1105 | 3.082 | 3.1913 | -117.7735 | 0.11552 | 0.091933 | 0.058117 | 0.070773 | 0.10986 | 0.13595 | 0.005267 | -0.022921 | -0.02519 | 0.54029 | 0.25888 | 0.2818 | -0.053706 | 0.055634 | 117.7558 | -3.0649 | 117.8661 | 117.8087 | 0.05285 | -3.0258 | -2.9997 | 120.861 | 120.8325 | 120.9419 | 101.7864 | -120.9092 | 117.8213 | 117.8604 | 117.8865 | 117.8425 | -3.1304
2524.2188 | 121.0098 | -117.7505 | 3.154 | 1.4211e-13 | -0.035337 | -0.0028739 | 0.060111 | -0.0054142 | 0.055614 | -0.0099194 | -0.0011493 | 0.025156 | -0.0043092 | 0.018643 | 0.014202 | -117.1828 | -16.1199 | -117.455 | 3.1425 | 3.1186 | 3.2279 | -117.7414 | 0.12467 | 0.10109 | 0.062695 | 0.070773 | 0.10528 | 0.13137 | 0.000689 | 0.009131 | -0.011453 | 0.56776 | 0.29551 | 0.28638 | -0.035385 | 0.073952 | 117.7512 | -3.0832 | 117.8752 | 117.8132 | 0.062006 | -3.0487 | -3.0226 | 120.8931 | 120.8692 | 120.9785 | 101.6307 | -120.8954 | 117.8213 | 117.8558 | 117.8819 | 117.8516 | -3.1533
2525.9844 | 121.0373 | -117.8787 | 3.035 | 1.4211e-13 | -0.035124 | -0.0028739 | 0.060539 | -0.005628 | 0.055187 | -0.0022889 | -0.0013631 | 0.024942 | -0.0040956 | 0.018857 | 0.013774 | -117.2927 | -16.2984 | -117.6015 | 3.0235 | 3.0041 | 3.1135 | -117.8605 | 0.11552 | 0.091933 | 0.058117 | 0.075351 | 0.10986 | 0.13595 | 0.000689 | 0.018253 | -0.011472 | 0.58605 | 0.27718 | 0.25893 | -0.03084 | 0.078506 | 117.8794 | -2.9596 | 117.9942 | 117.9368 | 0.057428 | -2.9251 | -2.899 | 120.9022 | 120.8829 | 120.9922 | 101.5803 | -120.8954 | 117.9541 | 117.9886 | 118.0147 | 117.9707 | -3.0343
2527.7656 | 121.0922 | -117.7734 | 3.1036 | 1.4211e-13 | -0.035124 | -0.0028739 | 0.060111 | -0.004987 | 0.055614 | -0.0022889 | -0.0013631 | 0.025156 | -0.0043092 | 0.018429 | 0.013988 | -117.2377 | -16.5045 | -117.5283 | 3.0876 | 3.0591 | 3.1638 | -117.8009 | 0.11094 | 0.096512 | 0.053538 | 0.075351 | 0.10986 | 0.14053 | 0.000689 | -0.027507 | -0.016039 | 0.53571 | 0.24514 | 0.27265 | -0.044557 | 0.060206 | 117.7741 | -3.0283 | 117.8844 | 117.827 | 0.052849 | -2.9938 | -2.9631 | 120.861 | 120.8325 | 120.9373 | 101.269 | -120.9046 | 117.8488 | 117.8833 | 117.914 | 117.8699 | -3.1029
2529.5469 | 121.1105 | -117.8421 | 3.0075 | 1.4211e-13 | -0.035124 | -0.0028739 | 0.060325 | -0.0054142 | 0.055828 | -0.0022889 | -0.0015767 | 0.025156 | -0.0040956 | 0.018429 | 0.013988 | -117.311 | -16.7471 | -117.5878 | 3.0143 | 2.9996 | 3.0997 | -117.8742 | 0.11552 | 0.10109 | 0.062695 | 0.070773 | 0.10986 | 0.13595 | 0.005267 | -0.032105 | 0.006838 | 0.53112 | 0.25429 | 0.2864 | -0.007952 | 0.092236 | 117.8474 | -2.9367 | 117.9576 | 117.9048 | 0.057428 | -2.8977 | -2.8716 | 120.8564 | 120.8417 | 120.9418 | 101.095 | -120.8817 | 117.9129 | 117.952 | 117.9781 | 117.9432 | -3.0022
2531.3281 | 121.0236 | -117.9199 | 3.0167 | 1.4211e-13 | -0.035124 | -0.0028739 | 0.060325 | -0.0058416 | 0.055828 | -0.0022889 | -0.0011493 | 0.025156 | -0.0040956 | 0.018429 | 0.014202 | -117.3293 | -16.9852 | -117.6199 | 2.9915 | 2.9721 | 3.0723 | -117.9017 | 0.12009 | 0.091933 | 0.053538 | 0.070773 | 0.10528 | 0.13137 | -0.008469 | 0.018242 | -0.02521 | 0.59062 | 0.30006 | 0.28182 | -0.044582 | 0.055609 | 117.9115 | -2.9459 | 118.04 | 117.9735 | 0.062007 | -2.9114 | -2.8853 | 120.9114 | 120.892 | 120.9922 | 100.9347 | -120.9183 | 117.9907 | 118.0252 | 118.0513 | 118.0119 | -3.0251
2533.0312 | 121.0556 | -117.9153 | 2.9709 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060539 | -0.0052006 | 0.055828 | -0.0022889 | -0.0011493 | 0.025156 | -0.0040956 | 0.018857 | 0.013774 | -117.3568 | -17.1912 | -117.6428 | 2.9686 | 2.9492 | 3.0494 | -117.9292 | 0.11552 | 0.091933 | 0.062695 | 0.070773 | 0.10986 | 0.13137 | -0.013048 | -0.01381 | -0.002325 | 0.55858 | 0.27259 | 0.2864 | -0.0217 | 0.078493 | 117.9023 | -2.9001 | 118.0309 | 117.978 | 0.075743 | -2.861 | -2.8395 | 120.8839 | 120.8645 | 120.9647 | 100.7241 | -120.9 | 117.9861 | 118.0252 | 118.0467 | 118.0073 | -2.9839
2534.8281 | 121.1151 | -115.0085 | 5.7953 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060539 | -0.0054142 | 0.055614 | -0.01755 | -0.0013631 | 0.024942 | -0.0040956 | 0.018643 | 0.013774 | -114.5319 | -16.4953 | -114.8042 | 5.7614 | 5.7744 | 5.8698 | -115.0856 | 0.12009 | 0.091933 | 0.058117 | 0.066194 | 0.10986 | 0.12679 | 0.005267 | -0.077097 | -0.033911 | 0.47664 | 0.20433 | 0.28143 | -0.020905 | 0.07451 | 115.0138 | -5.7291 | 115.1286 | 115.0667 | 0.05285 | -5.6854 | -5.6685 | 120.7699 | 120.7829 | 120.8783 | 98.5132 | -120.8809 | 115.0747 | 115.1184 | 115.1353 | 115.1005 | -5.79
2536.6094 | 121.138 | -115.0589 | 5.7632 | 1.4211e-13 | -0.035337 | -0.0033013 | 0.060539 | -0.0054142 | 0.055828 | -0.0099194 | -0.0015767 | 0.024942 | -0.0047366 | 0.018857 | 0.013774 | -114.5411 | -16.7197 | -114.8179 | 5.7431 | 5.7606 | 5.8606 | -115.0948 | 0.11552 | 0.091933 | 0.062695 | 0.061616 | 0.10986 | 0.13595 | -0.00389 | -0.035901 | -0.020181 | 0.51784 | 0.24095 | 0.27685 | -0.002599 | 0.097396 | 115.055 | -5.7016 | 115.1744 | 115.1216 | 0.066585 | -5.6534 | -5.6273 | 120.802 | 120.8195 | 120.9195 | 98.3392 | -120.858 | 115.1205 | 115.1688 | 115.1949 | 115.1508 | -5.7671
2538.3906 | 121.1517 | -115.3336 | 5.4703 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060539 | -0.0054142 | 0.055401 | -0.01755 | -0.0011493 | 0.024729 | -0.0049502 | 0.018643 | 0.013988 | -114.8615 | -17.0173 | -115.143 | 5.418 | 5.4401 | 5.5264 | -115.4245 | 0.12009 | 0.10109 | 0.058117 | 0.070773 | 0.10986 | 0.12679 | -0.00389 | -0.090925 | -0.052278 | 0.47201 | 0.19055 | 0.28147 | -0.030155 | 0.056127 | 115.3297 | -5.3995 | 115.4537 | 115.3917 | 0.062007 | -5.3604 | -5.3435 | 120.7516 | 120.7737 | 120.86 | 98.3163 | -120.8948 | 115.4043 | 115.4434 | 115.4604 | 115.4346 | -5.4742
2540.0938 | 121.1792 | -115.6403 | 5.159 | 1.4211e-13 | -0.035337 | -0.0033013 | 0.060539 | -0.0054142 | 0.055401 | 0.0053411 | -0.0011493 | 0.025156 | -0.0049502 | 0.018643 | 0.013988 | -115.1179 | -17.237 | -115.3994 | 5.1662 | 5.1883 | 5.2837 | -115.6809 | 0.11552 | 0.091933 | 0.058117 | 0.070773 | 0.10528 | 0.13137 | -0.008469 | -0.040643 | 0.00719 | 0.52232 | 0.24087 | 0.28151 | 0.029283 | 0.12474 | 115.6318 | -5.0882 | 115.7558 | 115.6984 | 0.066586 | -5.0537 | -5.0276 | 120.8064 | 120.8285 | 120.924 | 98.4032 | -120.8399 | 115.711 | 115.7455 | 115.7716 | 115.7322 | -5.1675
2541.8594 | 121.138 | -115.4572 | 5.3833 | 1.4211e-13 | -0.035337 | -0.0028739 | 0.060325 | -0.005628 | 0.055828 | -0.0022889 | -0.0011493 | 0.025156 | -0.0049502 | 0.018643 | 0.013988 | -114.9394 | -17.4156 | -115.2163 | 5.3356 | 5.3531 | 5.4531 | -115.5161 | 0.11552 | 0.091933 | 0.062695 | 0.070773 | 0.10986 | 0.13137 | -0.00389 | -0.058908 | -0.047714 | 0.51777 | 0.24089 | 0.2998 | -0.030179 | 0.069844 | 115.4533 | -5.3125 | 115.5727 | 115.5198 | 0.066585 | -5.2734 | -5.2519 | 120.7927 | 120.8103 | 120.9103 | 98.0416 | -120.8994 | 115.5279 | 115.567 | 115.5885 | 115.5491 | -5.3872
2543.5781 | 121.0007 | -115.7272 | 5.1819 | 1.4211e-13 | -0.035124 | -0.0030877 | 0.060111 | -0.0054142 | 0.055614 | 0.0053411 | -0.0011493 | 0.025156 | -0.0047366 | 0.018429 | 0.013988 | -115.1454 | -17.6766 | -115.4269 | 5.1387 | 5.1516 | 5.2425 | -115.7175 | 0.11552 | 0.082776 | 0.062695 | 0.070773 | 0.096121 | 0.12679 | 0.000689 | 0.009701 | -0.043168 | 0.58183 | 0.30037 | 0.29067 | -0.030236 | 0.060644 | 115.7279 | -5.1111 | 115.8427 | 115.7899 | 0.062006 | -5.0858 | -5.0551 | 120.866 | 120.8789 | 120.9698 | 98.0507 | -120.8994 | 115.798 | 115.8234 | 115.854 | 115.81 | -5.1812
2545.3438 | 121.1655 | -116.1484 | 4.6783 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060325 | -0.005628 | 0.055828 | -0.0022889 | -0.00093566 | 0.02537 | -0.0047366 | 0.018857 | 0.013988 | -115.6216 | -18.0658 | -115.9076 | 4.658 | 4.6754 | 4.7709 | -116.1937 | 0.12009 | 0.082776 | 0.058117 | 0.070773 | 0.1007 | 0.13595 | -0.008469 | -0.045366 | -0.020359 | 0.52682 | 0.2408 | 0.28616 | -0.002904 | 0.092588 | 116.1399 | -4.6076 | 116.2685 | 116.2065 | 0.066586 | -4.5776 | -4.5424 | 120.8064 | 120.8238 | 120.9193 | 98.0826 | -120.8721 | 116.2191 | 116.2491 | 116.2843 | 116.2312 | -4.6868
2547.0938 | 121.0144 | -116.3132 | 4.6051 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060539 | -0.0054142 | 0.055614 | -0.0022889 | -0.0013631 | 0.02537 | -0.004523 | 0.01907 | 0.013988 | -115.7498 | -18.3908 | -116.0358 | 4.5252 | 4.5427 | 4.6427 | -116.3357 | 0.12009 | 0.082776 | 0.058117 | 0.070773 | 0.10986 | 0.13595 | 0.000689 | -0.022517 | -0.07989 | 0.56342 | 0.2774 | 0.29991 | -0.062451 | 0.037629 | 116.3139 | -4.5343 | 116.4333 | 116.3713 | 0.057428 | -4.4952 | -4.4692 | 120.8384 | 120.8558 | 120.9559 | 97.9223 | -120.9408 | 116.3839 | 116.423 | 116.4491 | 116.3959 | -4.6044
2548.8281 | 121.1517 | -116.7664 | 4.0878 | 1.4211e-13 | -0.035337 | -0.0033013 | 0.060111 | -0.0054142 | 0.055401 | -0.0099194 | -0.0011493 | 0.02537 | -0.0047366 | 0.018643 | 0.013988 | -115.9695 | -18.748 | -116.2464 | 4.3238 | 4.332 | 4.4275 | -116.5417 | 0.11552 | 0.087354 | 0.067274 | 0.070773 | 0.10986 | 0.13595 | 0.005267 | 0.22462 | 0.23593 | 0.79684 | 0.51998 | 0.29537 | 0.24419 | 0.33971 | 116.7716 | -4.0171 | 116.8819 | 116.8336 | 0.062007 | -3.978 | -3.9519 | 121.0901 | 121.0984 | 121.1939 | 98.0184 | -120.6296 | 116.8371 | 116.8762 | 116.9023 | 116.8537 | -4.0826
2550.5938 | 121.051 | -115.6082 | 5.3238 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060539 | -0.0054142 | 0.055828 | -0.01755 | -0.0011493 | 0.024942 | -0.0047366 | 0.018857 | 0.013988 | -115.063 | -18.7663 | -115.3445 | 5.2074 | 5.2386 | 5.3204 | -115.6397 | 0.12009 | 0.091933 | 0.062695 | 0.070773 | 0.10986 | 0.13137 | 0.000689 | -0.031477 | -0.1164 | 0.54522 | 0.26376 | 0.29524 | -0.085143 | -0.003427 | 115.6089 | -5.253 | 115.7283 | 115.6709 | 0.062006 | -5.2139 | -5.1924 | 120.8156 | 120.8469 | 120.9286 | 96.8419 | -120.9635 | 115.679 | 115.7181 | 115.7396 | 115.7001 | -5.3231
2552.2969 | 121.0739 | -115.8142 | 5.1086 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060539 | -0.005628 | 0.055828 | -0.0022889 | -0.0011493 | 0.024729 | -0.0047366 | 0.018429 | 0.013774 | -115.237 | -19.0227 | -115.5184 | 5.0426 | 5.0601 | 5.1601 | -115.8137 | 0.11552 | 0.087354 | 0.062695 | 0.066194 | 0.1007 | 0.13137 | 0.000689 | 0.000518 | -0.066073 | 0.57723 | 0.29578 | 0.29526 | -0.048572 | 0.051471 | 115.8149 | -5.0424 | 115.9297 | 115.8769 | 0.062006 | -5.0079 | -4.9773 | 120.8568 | 120.8743 | 120.9743 | 96.7915 | -120.9223 | 115.8804 | 115.9149 | 115.9456 | 115.9016 | -5.108
2554.0625 | 121.0464 | -116.0019 | 4.9255 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060325 | -0.0054142 | 0.055828 | -0.0099194 | -0.00093566 | 0.024729 | -0.0047366 | 0.018643 | 0.013988 | -115.3926 | -19.2745 | -115.6832 | 4.8915 | 4.9044 | 4.9953 | -115.9785 | 0.11552 | 0.096512 | 0.062695 | 0.066194 | 0.10528 | 0.13137 | 0.005267 | 0.02336 | -0.034053 | 0.60925 | 0.31865 | 0.29529 | -0.02115 | 0.069748 | 116.0072 | -4.8593 | 116.1174 | 116.0646 | 0.057428 | -4.8203 | -4.7942 | 120.8934 | 120.9063 | 120.9972 | 96.7274 | -120.9041 | 116.0681 | 116.1072 | 116.1333 | 116.0984 | -4.9203
2555.8438 | 121.0785 | -116.1484 | 4.7424 | 1.4211e-13 | -0.035765 | -0.0033013 | 0.060325 | -0.005628 | 0.055614 | -0.0022889 | -0.0013631 | 0.02537 | -0.0049502 | 0.018857 | 0.013774 | -115.5941 | -19.5675 | -115.8801 | 4.6946 | 4.7121 | 4.803 | -116.1708 | 0.11094 | 0.091933 | 0.067274 | 0.070773 | 0.1007 | 0.12679 | -0.008469 | -0.022471 | -0.047819 | 0.55429 | 0.26826 | 0.29073 | -0.03036 | 0.060551 | 116.1399 | -4.6717 | 116.2593 | 116.2156 | 0.075743 | -4.6417 | -4.6156 | 120.843 | 120.8604 | 120.9514 | 96.5808 | -120.9133 | 116.2191 | 116.2491 | 116.2752 | 116.2403 | -4.7509
2557.5469 | 121.051 | -116.3498 | 4.5685 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060325 | -0.005628 | 0.055614 | -0.0099194 | -0.00093566 | 0.024729 | -0.0047366 | 0.018643 | 0.013774 | -115.7681 | -19.9018 | -116.0495 | 4.5161 | 4.5243 | 4.629 | -116.3494 | 0.12009 | 0.087354 | 0.062695 | 0.070773 | 0.1007 | 0.12222 | -0.00389 | 0.000367 | -0.052425 | 0.58172 | 0.30028 | 0.29992 | -0.044145 | 0.060515 | 116.3459 | -4.4977 | 116.4699 | 116.4125 | 0.066585 | -4.4678 | -4.4463 | 120.8658 | 120.8741 | 120.9788 | 96.448 | -120.9179 | 116.4206 | 116.4505 | 116.472 | 116.4371 | -4.5724
2559.3125 | 121.0281 | -116.5009 | 4.39 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060752 | -0.0054142 | 0.055614 | -0.0099194 | -0.00093566 | 0.024942 | -0.0049502 | 0.018643 | 0.013988 | -115.9878 | -20.1948 | -116.2738 | 4.2871 | 4.3091 | 4.4046 | -116.5784 | 0.12009 | 0.091933 | 0.067274 | 0.061616 | 0.091543 | 0.12679 | -0.00389 | -0.077517 | -0.10282 | 0.51302 | 0.22701 | 0.30453 | -0.080827 | 0.014691 | 116.497 | -4.3283 | 116.6209 | 116.5681 | 0.071164 | -4.2984 | -4.2632 | 120.788 | 120.81 | 120.9055 | 96.306 | -120.9683 | 116.5625 | 116.5924 | 116.6276 | 116.5928 | -4.3938
2561.0312 | 121.0327 | -116.6702 | 4.2252 | 1.4211e-13 | -0.035337 | -0.0033013 | 0.060539 | -0.0058416 | 0.055614 | -0.0099194 | -0.0011493 | 0.025156 | -0.0047366 | 0.018857 | 0.013988 | -116.1252 | -20.4421 | -116.4066 | 4.1589 | 4.1626 | 4.2581 | -116.7157 | 0.12009 | 0.087354 | 0.062695 | 0.070773 | 0.10528 | 0.12679 | 0.005267 | -0.045512 | -0.066217 | 0.54505 | 0.26361 | 0.30912 | -0.062558 | 0.032971 | 116.6755 | -4.1544 | 116.7903 | 116.7329 | 0.057428 | -4.1199 | -4.0984 | 120.8292 | 120.8328 | 120.9284 | 96.2282 | -120.9409 | 116.741 | 116.7755 | 116.797 | 116.7576 | -4.2199
2562.7969 | 121.1288 | -116.272 | 4.5593 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060325 | -0.005628 | 0.055828 | -0.0099194 | -0.00093566 | 0.025156 | -0.004523 | 0.018857 | 0.013988 | -115.8367 | -20.7076 | -116.109 | 4.4245 | 4.4419 | 4.5374 | -116.4227 | 0.12009 | 0.091933 | 0.062695 | 0.070773 | 0.10986 | 0.12679 | 0.000689 | -0.15071 | -0.13484 | 0.43523 | 0.16295 | 0.31366 | -0.11741 | -0.021902 | 116.2727 | -4.4886 | 116.3921 | 116.3347 | 0.062006 | -4.4495 | -4.4325 | 120.6965 | 120.7139 | 120.8094 | 95.5644 | -120.982 | 116.3427 | 116.3818 | 116.3988 | 116.3639 | -4.5586
2564.5781 | 121.1746 | -117.1417 | 3.6987 | 1.4211e-13 | -0.035124 | -0.0035151 | 0.059898 | -0.0052006 | 0.055187 | -0.01755 | -0.0011493 | 0.024942 | -0.0049502 | 0.018643 | 0.013774 | -116.6609 | -21.2433 | -116.9377 | 3.605 | 3.6314 | 3.7224 | -117.2561 | 0.11552 | 0.091933 | 0.058117 | 0.057037 | 0.11901 | 0.12679 | -0.008469 | -0.11433 | -0.093773 | 0.48087 | 0.20403 | 0.31836 | -0.067284 | 0.023703 | 117.1333 | -3.6417 | 117.2572 | 117.1998 | 0.066586 | -3.5797 | -3.5719 | 120.7467 | 120.7732 | 120.8642 | 95.8984 | -120.9548 | 117.1988 | 117.2607 | 117.2685 | 117.2337 | -3.7072
2566.2969 | 121.0831 | -116.629 | 4.2755 | 1.4211e-13 | -0.035765 | -0.0035151 | 0.060325 | -0.0058416 | 0.055614 | -0.0099194 | -0.0011493 | 0.025156 | -0.0049502 | 0.01907 | 0.013988 | -116.084 | -21.3074 | -116.37 | 4.1956 | 4.2038 | 4.2993 | -116.67 | 0.12009 | 0.091933 | 0.058117 | 0.061616 | 0.11901 | 0.13137 | -0.00389 | -0.040922 | -0.079944 | 0.54505 | 0.25904 | 0.29996 | -0.071701 | 0.023824 | 116.6251 | -4.2139 | 116.7491 | 116.6871 | 0.062007 | -4.1565 | -4.1441 | 120.8246 | 120.8328 | 120.9284 | 95.3216 | -120.9455 | 116.6906 | 116.748 | 116.7604 | 116.721 | -4.2794
2568.0469 | 121.1609 | -116.2811 | 4.5364 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060539 | -0.005628 | 0.055614 | -0.0099194 | -0.0011493 | 0.024942 | -0.0051638 | 0.018643 | 0.013561 | -115.7681 | -21.3669 | -116.0541 | 4.5023 | 4.5198 | 4.6153 | -116.3632 | 0.11552 | 0.087354 | 0.062695 | 0.057037 | 0.1007 | 0.13595 | 0.000689 | -0.082034 | -0.034117 | 0.51306 | 0.22704 | 0.30908 | -0.01668 | 0.078823 | 116.2818 | -4.4794 | 116.3966 | 116.3438 | 0.062006 | -4.4357 | -4.4005 | 120.7834 | 120.8009 | 120.8964 | 94.9142 | -120.8996 | 116.3382 | 116.3818 | 116.4171 | 116.3685 | -4.5357
2569.8281 | 121.1243 | -116.2994 | 4.5547 | 1.4211e-13 | -0.036192 | -0.0033013 | 0.060325 | -0.0052006 | 0.055828 | -0.0022889 | -0.0011493 | 0.025156 | -0.0051638 | 0.018643 | 0.013988 | -115.7314 | -21.7882 | -116.0175 | 4.5298 | 4.5472 | 4.6473 | -116.3265 | 0.12009 | 0.087354 | 0.062695 | 0.061616 | 0.091543 | 0.13137 | -0.00389 | -0.027092 | -0.024958 | 0.568 | 0.28198 | 0.30907 | -0.007518 | 0.092562 | 116.2955 | -4.4931 | 116.4195 | 116.3621 | 0.066585 | -4.4632 | -4.4234 | 120.8292 | 120.8467 | 120.9467 | 94.5113 | -120.8813 | 116.3611 | 116.391 | 116.4308 | 116.3868 | -4.5586
2571.5938 | 121.019 | -116.185 | 4.7195 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060539 | -0.005628 | 0.055401 | -0.0022889 | -0.0013631 | 0.024942 | -0.0049502 | 0.018643 | 0.013774 | -115.6078 | -22.3742 | -115.8938 | 4.6626 | 4.6754 | 4.7664 | -116.2075 | 0.12009 | 0.082776 | 0.058117 | 0.066194 | 0.096121 | 0.12679 | -0.00389 | -0.02248 | -0.056979 | 0.57717 | 0.29115 | 0.31363 | -0.044102 | 0.046812 | 116.1811 | -4.6533 | 116.3051 | 116.2431 | 0.062007 | -4.6234 | -4.5927 | 120.8476 | 120.8604 | 120.9514 | 93.8108 | -120.927 | 116.2512 | 116.2811 | 116.3118 | 116.2678 | -4.7234
2573.3594 | 121.0739 | -116.4322 | 4.4861 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060325 | -0.005628 | 0.055828 | 0.0053411 | -0.0013631 | 0.024729 | -0.0047366 | 0.018643 | 0.013774 | -115.8459 | -23.2808 | -116.1273 | 4.4199 | 4.4328 | 4.5374 | -116.441 | 0.12467 | 0.087354 | 0.062695 | 0.066194 | 0.1007 | 0.13595 | -0.00389 | -0.008813 | -0.066174 | 0.58629 | 0.30485 | 0.31366 | -0.053326 | 0.05134 | 116.4283 | -4.4199 | 116.5569 | 116.4949 | 0.066585 | -4.3854 | -4.3501 | 120.8521 | 120.8649 | 120.9696 | 93.1514 | -120.9271 | 116.4984 | 116.5329 | 116.5681 | 116.5195 | -4.49
2575.1406 | 121.051 | -116.5375 | 4.3945 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060111 | -0.005628 | 0.055614 | -0.0022889 | -0.0015767 | 0.024942 | -0.0049502 | 0.01907 | 0.013988 | -115.9375 | -23.7432 | -116.2189 | 4.3283 | 4.3458 | 4.4367 | -116.5372 | 0.12467 | 0.091933 | 0.062695 | 0.066194 | 0.1007 | 0.12679 | 0.000689 | 0.000315 | -0.066189 | 0.60001 | 0.31857 | 0.31826 | -0.048773 | 0.042164 | 116.5382 | -4.3283 | 116.6621 | 116.6002 | 0.062006 | -4.2938 | -4.2677 | 120.8658 | 120.8832 | 120.9742 | 92.7943 | -120.9317 | 116.6037 | 116.6382 | 116.6643 | 116.6294 | -4.3938
2576.8594 | 121.0419 | -116.4368 | 4.5044 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060325 | -0.005628 | 0.055614 | -0.0022889 | -0.0011493 | 0.024729 | -0.0049502 | 0.01907 | 0.013988 | -115.8367 | -24.1278 | -116.1228 | 4.4245 | 4.4373 | 4.5374 | -116.4318 | 0.12009 | 0.091933 | 0.062695 | 0.066194 | 0.10528 | 0.13137 | 0.000689 | 0.004922 | -0.079907 | 0.60002 | 0.31401 | 0.30909 | -0.067058 | 0.033029 | 116.4375 | -4.4382 | 116.5569 | 116.4995 | 0.062006 | -4.3991 | -4.373 | 120.8613 | 120.8741 | 120.9742 | 92.3089 | -120.9362 | 116.503 | 116.542 | 116.5681 | 116.5287 | -4.5037
2578.625 | 121.0327 | -116.4093 | 4.4952 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060111 | -0.0054142 | 0.055614 | -0.0099194 | -0.0011493 | 0.024729 | -0.0051638 | 0.01907 | 0.013774 | -115.8139 | -24.4392 | -116.1044 | 4.4428 | 4.4511 | 4.5557 | -116.4273 | 0.12467 | 0.087354 | 0.062695 | 0.066194 | 0.091543 | 0.12222 | 0.000689 | -0.017965 | -0.052437 | 0.59545 | 0.30486 | 0.32282 | -0.044165 | 0.0605 | 116.41 | -4.429 | 116.534 | 116.472 | 0.062006 | -4.4037 | -4.373 | 120.8521 | 120.8604 | 120.965 | 91.9701 | -120.9225 | 116.4755 | 116.5008 | 116.5315 | 116.4967 | -4.4945
2580.4062 | 121.0693 | -116.3681 | 4.5456 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060111 | -0.0054142 | 0.055614 | 0.0053411 | -0.0011493 | 0.025156 | -0.0051638 | 0.018857 | 0.013988 | -115.7726 | -25.0115 | -116.0587 | 4.4886 | 4.5014 | 4.5924 | -116.3815 | 0.12009 | 0.087354 | 0.062695 | 0.061616 | 0.1007 | 0.12679 | -0.008469 | -0.013374 | -0.057007 | 0.59546 | 0.30944 | 0.32281 | -0.044151 | 0.046775 | 116.3596 | -4.484 | 116.4882 | 116.4308 | 0.071164 | -4.4449 | -4.4188 | 120.8567 | 120.8695 | 120.9605 | 91.3566 | -120.9271 | 116.4297 | 116.4688 | 116.4949 | 116.4555 | -4.5541
2582.1094 | 121.0693 | -116.3361 | 4.5639 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060325 | -0.005628 | 0.055187 | -0.0022889 | -0.00093566 | 0.024942 | -0.0047366 | 0.018857 | 0.013988 | -115.7635 | -25.3228 | -116.0541 | 4.4977 | 4.5106 | 4.6015 | -116.3723 | 0.12009 | 0.091933 | 0.053538 | 0.066194 | 0.091543 | 0.12679 | 0.005267 | -0.03626 | -0.066162 | 0.57257 | 0.28197 | 0.31823 | -0.053304 | 0.037621 | 116.3413 | -4.4977 | 116.4562 | 116.3896 | 0.048271 | -4.4724 | -4.4371 | 120.8338 | 120.8467 | 120.9376 | 91.0132 | -120.9362 | 116.4023 | 116.4276 | 116.4629 | 116.428 | -4.5586
2583.8906 | 121.0968 | -116.423 | 4.4724 | 1.4211e-13 | -0.035337 | -0.0028739 | 0.060325 | -0.005628 | 0.055828 | -0.01755 | -0.0013631 | 0.024942 | -0.0049502 | 0.018643 | 0.013774 | -115.8322 | -25.767 | -116.1228 | 4.4199 | 4.4328 | 4.5328 | -116.4364 | 0.12925 | 0.087354 | 0.058117 | 0.057037 | 0.10528 | 0.12679 | -0.008469 | -0.01339 | -0.052441 | 0.59087 | 0.30027 | 0.31367 | -0.039593 | 0.060495 | 116.4146 | -4.4153 | 116.5523 | 116.4812 | 0.066586 | -4.3671 | -4.3456 | 120.8429 | 120.8558 | 120.9559 | 90.6561 | -120.9088 | 116.4801 | 116.5283 | 116.5498 | 116.5104 | -4.4808
2585.6719 | 121.0922 | -116.4871 | 4.4128 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060325 | -0.0054142 | 0.055401 | -0.01755 | -0.0011493 | 0.024942 | -0.0049502 | 0.018429 | 0.013561 | -115.8963 | -25.973 | -116.1777 | 4.3558 | 4.3778 | 4.4687 | -116.5005 | 0.11552 | 0.091933 | 0.062695 | 0.061616 | 0.091543 | 0.12679 | -0.00389 | -0.013407 | -0.05703 | 0.59086 | 0.30942 | 0.32283 | -0.035031 | 0.055903 | 116.4832 | -4.3512 | 116.6026 | 116.5498 | 0.066585 | -4.3213 | -4.286 | 120.8429 | 120.8649 | 120.9559 | 90.5141 | -120.9134 | 116.5487 | 116.5787 | 116.6139 | 116.5791 | -4.4167
2587.4375 | 121.1563 | -116.3315 | 4.4815 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060111 | -0.0054142 | 0.055401 | -0.0022889 | -0.0011493 | 0.025156 | -0.0051638 | 0.018643 | 0.014202 | -115.791 | -26.321 | -116.0724 | 4.4565 | 4.4785 | 4.5649 | -116.4044 | 0.11552 | 0.096512 | 0.053538 | 0.070773 | 0.096121 | 0.12222 | -0.008469 | -0.07289 | -0.024969 | 0.54052 | 0.25908 | 0.33197 | -0.002959 | 0.08339 | 116.323 | -4.4107 | 116.447 | 116.385 | 0.062007 | -4.3854 | -4.3593 | 120.788 | 120.81 | 120.8964 | 90.0105 | -120.8859 | 116.4023 | 116.4276 | 116.4537 | 116.428 | -4.49
2589.1562 | 121.1197 | -116.4597 | 4.3762 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060325 | -0.0052006 | 0.055828 | -0.0022889 | -0.0013631 | 0.025156 | -0.0051638 | 0.018643 | 0.013561 | -115.8917 | -26.8017 | -116.1777 | 4.3467 | 4.3687 | 4.4642 | -116.5143 | 0.12009 | 0.087354 | 0.058117 | 0.061616 | 0.096121 | 0.13137 | 0.005267 | -0.05461 | -0.029565 | 0.56797 | 0.28196 | 0.33657 | -0.007568 | 0.087946 | 116.4649 | -4.3146 | 116.5797 | 116.5178 | 0.05285 | -4.2801 | -4.2448 | 120.8063 | 120.8283 | 120.9238 | 89.6579 | -120.8905 | 116.5213 | 116.5558 | 116.591 | 116.547 | -4.371
2590.9375 | 121.0144 | -116.1667 | 4.7379 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060111 | -0.0054142 | 0.055614 | -0.0022889 | -0.00072206 | 0.024942 | -0.0049502 | 0.01907 | 0.013774 | -115.649 | -27.2001 | -115.9396 | 4.5939 | 4.6022 | 4.6839 | -116.267 | 0.12009 | 0.091933 | 0.058117 | 0.057037 | 0.091543 | 0.12222 | 0.005267 | -0.10032 | -0.14397 | 0.51766 | 0.22706 | 0.32738 | -0.13568 | -0.053914 | 116.172 | -4.6808 | 116.2868 | 116.2248 | 0.05285 | -4.6463 | -4.6156 | 120.7606 | 120.7689 | 120.8506 | 88.9666 | -121.0049 | 116.2237 | 116.2582 | 116.2889 | 116.2586 | -4.7326
2592.7188 | 121.0098 | -116.3864 | 4.5181 | 1.4211e-13 | -0.035978 | -0.0033013 | 0.060539 | -0.005628 | 0.055401 | 0.0053411 | -0.0011493 | 0.025156 | -0.0047366 | 0.01907 | 0.013988 | -115.7726 | -27.7816 | -116.0587 | 4.4703 | 4.4831 | 4.5695 | -116.3952 | 0.11552 | 0.091933 | 0.053538 | 0.061616 | 0.096121 | 0.11764 | -0.00389 | -0.0088 | -0.047855 | 0.61377 | 0.32775 | 0.33655 | -0.035001 | 0.051348 | 116.3825 | -4.4565 | 116.5019 | 116.44 | 0.057428 | -4.422 | -4.4005 | 120.8567 | 120.8695 | 120.9559 | 88.6049 | -120.9133 | 116.448 | 116.4825 | 116.5041 | 116.4783 | -4.522
2594.5 | 121.0785 | -116.4368 | 4.454 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060325 | -0.005628 | 0.055614 | -0.0022889 | -0.0011493 | 0.024942 | -0.0049502 | 0.018857 | 0.013988 | -115.8184 | -28.418 | -116.0999 | 4.4153 | 4.4236 | 4.5237 | -116.4456 | 0.12467 | 0.087354 | 0.053538 | 0.066194 | 0.1007 | 0.12222 | 0.000689 | -0.008814 | -0.03871 | 0.61834 | 0.3369 | 0.34571 | -0.030441 | 0.069648 | 116.4375 | -4.3878 | 116.5614 | 116.4903 | 0.052849 | -4.3533 | -4.3318 | 120.8521 | 120.8604 | 120.9605 | 88.0188 | -120.8996 | 116.503 | 116.5375 | 116.559 | 116.5241 | -4.4534
2596.2344 | 121.0556 | -111.1816 | 9.7412 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060966 | -0.0058416 | 0.055614 | 0.0053411 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013774 | -110.3839 | -27.1497 | -110.6426 | 9.8728 | 9.7077 | 9.9264 | -110.9738 | 0.12009 | 0.087354 | 0.048959 | 0.052459 | 0.091543 | 0.11764 | -0.008469 | 0.20787 | 0.13156 | 0.79776 | 0.53908 | 0.33121 | -0.033532 | 0.18523 | 111.1732 | -9.6888 | 111.3017 | 111.2306 | 0.057428 | -9.6497 | -9.6236 | 121.0544 | 120.8893 | 121.1081 | 84.0319 | -120.715 | 111.2341 | 111.2732 | 111.2993 | 111.269 | -9.7497
2598 | 121.1334 | -112.6831 | 8.139 | 1.4211e-13 | -0.035551 | -0.0033013 | 0.060325 | -0.0058416 | 0.055614 | 0.012972 | -0.0013631 | 0.025156 | -0.0051638 | 0.018857 | 0.013561 | -112.1511 | -28.3997 | -112.4144 | 8.0918 | 7.9311 | 8.1499 | -112.755 | 0.11552 | 0.082776 | 0.058117 | 0.057037 | 0.091543 | 0.12679 | 0.000689 | -0.071864 | -0.047261 | 0.53196 | 0.26875 | 0.34062 | -0.20798 | 0.010904 | 112.6838 | -8.082 | 112.7986 | 112.7412 | 0.057428 | -8.0475 | -8.0122 | 120.7749 | 120.6142 | 120.833 | 84.2834 | -120.894 | 112.7401 | 112.7746 | 112.8099 | 112.7659 | -8.1383
2599.7812 | 121.0236 | -114.2029 | 6.6879 | 1.4211e-13 | -0.035978 | -0.0030877 | 0.060325 | -0.005628 | 0.055401 | -0.0022889 | -0.0011493 | 0.025156 | -0.0047366 | 0.018643 | 0.013774 | -113.5521 | -29.5809 | -113.8199 | 6.6908 | 6.5162 | 6.7397 | -114.1744 | 0.12009 | 0.096512 | 0.058117 | 0.061616 | 0.091543 | 0.12679 | 0.000689 | 0.028445 | 0.002863 | 0.65075 | 0.383 | 0.35455 | -0.17176 | 0.051805 | 114.2036 | -6.6263 | 114.323 | 114.261 | 0.057428 | -6.5964 | -6.5611 | 120.8937 | 120.7191 | 120.9426 | 84.6219 | -120.8624 | 114.2645 | 114.2944 | 114.3297 | 114.2994 | -6.6872
2601.5625 | 121.0464 | -114.8712 | 6.0516 | 1.4211e-13 | -0.035551 | -0.0035151 | 0.060752 | -0.0054142 | 0.055828 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013774 | -114.2572 | -30.5104 | -114.5295 | 5.9811 | 5.811 | 6.0392 | -114.875 | 0.12009 | 0.091933 | 0.058117 | 0.061616 | 0.086964 | 0.12222 | 0.005267 | -0.003795 | -0.070496 | 0.61402 | 0.3417 | 0.34549 | -0.24062 | -0.01243 | 114.8765 | -5.99 | 114.9913 | 114.9293 | 0.05285 | -5.9647 | -5.9294 | 120.8524 | 120.6822 | 120.9104 | 84.3608 | -120.9266 | 114.9328 | 114.9582 | 114.9934 | 114.9631 | -6.0464
2603.3438 | 121.0693 | -111.5204 | 9.343 | 1.4211e-13 | -0.035765 | -0.0033013 | 0.060539 | -0.005628 | 0.055828 | -0.0022889 | -0.0011493 | 0.025156 | -0.0049502 | 0.01907 | 0.013774 | -108.8043 | -29.3703 | -109.0676 | 11.4935 | 11.4477 | 11.5564 | -109.394 | 0.11552 | 0.082776 | 0.048959 | 0.057037 | 0.086964 | 0.11764 | -0.00389 | 2.1263 | 2.1506 | 2.716 | 2.4528 | 0.32641 | 2.1047 | 2.2135 | 111.5165 | -9.2859 | 111.6359 | 111.5693 | 0.052849 | -9.256 | -9.2253 | 123.0139 | 122.9681 | 123.0768 | 82.1501 | -118.737 | 111.5774 | 111.6073 | 111.638 | 111.6032 | -9.3468
2605.0469 | 121.1014 | -111.3968 | 9.4025 | 1.4211e-13 | -0.035765 | -0.0028739 | 0.060325 | -0.005628 | 0.055828 | -0.0099194 | -0.0013631 | 0.024942 | -0.0049502 | 0.01907 | 0.013774 | -110.7822 | -30.8721 | -111.0363 | 9.4561 | 9.4742 | 9.551 | -111.3859 | 0.12009 | 0.087354 | 0.048959 | 0.057037 | 0.091543 | 0.12222 | -0.008469 | 0.010919 | 0.05367 | 0.61459 | 0.3605 | 0.34958 | 0.071688 | 0.14853 | 111.3883 | -9.3454 | 111.5169 | 111.4457 | 0.057428 | -9.3109 | -9.2803 | 120.8529 | 120.8709 | 120.9478 | 80.5247 | -120.7883 | 111.4538 | 111.4883 | 111.519 | 111.4841 | -9.4109
2606.8125 | 121.1288 | -111.9324 | 8.8715 | 1.4211e-13 | -0.035765 | -0.0028739 | 0.060325 | -0.005628 | 0.055614 | -0.0099194 | -0.0011493 | 0.024729 | -0.0053776 | 0.018643 | 0.013774 | -111.4003 | -31.8474 | -111.6681 | 8.8243 | 8.8468 | 8.9237 | -112.0132 | 0.11094 | 0.087354 | 0.053538 | 0.057037 | 0.091543 | 0.11764 | -0.013048 | -0.08081 | -0.047141 | 0.53209 | 0.26428 | 0.34509 | -0.024619 | 0.052266 | 111.9193 | -8.8144 | 112.0433 | 111.9859 | 0.066586 | -8.7799 | -8.7538 | 120.7567 | 120.7792 | 120.8561 | 80.085 | -120.8846 | 111.9894 | 112.0239 | 112.05 | 112.0197 | -8.8845
2608.5781 | 121.1655 | -112.294 | 8.5007 | 1.4211e-13 | -0.035765 | -0.0033013 | 0.060325 | -0.005628 | 0.055614 | -0.0022889 | -0.0013631 | 0.025156 | -0.0049502 | 0.018857 | 0.013561 | -111.7528 | -32.7036 | -112.0069 | 8.4764 | 8.4805 | 8.562 | -112.3703 | 0.11094 | 0.082776 | 0.053538 | 0.057037 | 0.091543 | 0.11306 | -0.00389 | -0.076334 | -0.02431 | 0.54118 | 0.28712 | 0.36345 | -0.020144 | 0.061345 | 112.2901 | -8.4436 | 112.4049 | 112.3475 | 0.057428 | -8.4091 | -8.3876 | 120.7704 | 120.7745 | 120.856 | 79.5905 | -120.871 | 112.351 | 112.3855 | 112.4071 | 112.3768 | -8.5046
2610.3594 | 121.0739 | -112.532 | 8.3084 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060539 | -0.005628 | 0.055401 | -0.0022889 | -0.0011493 | 0.025156 | -0.0051638 | 0.01907 | 0.013774 | -111.9314 | -33.6101 | -112.1809 | 8.2978 | 8.3111 | 8.3926 | -112.5443 | 0.11094 | 0.082776 | 0.053538 | 0.052459 | 0.091543 | 0.11306 | -0.00389 | -0.012296 | -0.010607 | 0.60066 | 0.35118 | 0.36348 | 0.002696 | 0.084197 | 112.5282 | -8.256 | 112.643 | 112.5856 | 0.057428 | -8.2169 | -8.1954 | 120.8298 | 120.8432 | 120.9247 | 78.9219 | -120.8527 | 112.5845 | 112.6236 | 112.6451 | 112.6148 | -8.3123
2612.0469 | 121.0922 | -112.5229 | 8.2901 | 1.4211e-13 | -0.035765 | -0.0030877 | 0.060539 | -0.005628 | 0.055614 | -0.01755 | -0.00072206 | 0.025156 | -0.0051638 | 0.018857 | 0.013988 | -111.9588 | -34.361 | -112.2175 | 8.2612 | 8.2607 | 8.3514 | -112.5764 | 0.12009 | 0.082776 | 0.053538 | 0.057037 | 0.086964 | 0.11764 | -0.008469 | -0.053503 | -0.028923 | 0.56404 | 0.3054 | 0.3589 | -0.029361 | 0.0613 | 112.5144 | -8.2331 | 112.643 | 112.5764 | 0.062007 | -8.2031 | -8.1725 | 120.7841 | 120.7836 | 120.8743 | 78.1619 | -120.8665 | 112.5799 | 112.6099 | 112.6405 | 112.6057 | -8.2986
2613.8281 | 121.1517 | -111.232 | 9.5673 | 1.4211e-13 | -0.035765 | -0.0033013 | 0.060325 | -0.005628 | 0.056042 | -0.01755 | -0.00093566 | 0.024729 | -0.0049502 | 0.018857 | 0.013774 | -110.622 | -34.622 | -110.8623 | 9.6026 | 9.6115 | 9.6975 | -111.2302 | 0.10636 | 0.087354 | 0.062695 | 0.052459 | 0.096121 | 0.11764 | -0.00389 | 0.001808 | 0.035384 | 0.61003 | 0.36968 | 0.36787 | 0.044261 | 0.13025 | 111.2281 | -9.5148 | 111.3384 | 111.2947 | 0.066585 | -9.4711 | -9.4496 | 120.8346 | 120.8435 | 120.9295 | 76.61 | -120.7974 | 111.2845 | 111.3281 | 111.3496 | 111.3193 | -9.5712
2615.6094 | 121.0876 | -111.8408 | 8.9859 | 1.4211e-13 | -0.035978 | -0.0030877 | 0.060539 | -0.0054142 | 0.055614 | 0.0053411 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013774 | -111.2629 | -35.904 | -111.5124 | 8.9571 | 8.9659 | 9.0519 | -111.8804 | 0.11552 | 0.082776 | 0.053538 | 0.057037 | 0.086964 | 0.11764 | -0.00389 | -0.039575 | -0.028809 | 0.57789 | 0.32839 | 0.36796 | -0.020008 | 0.066025 | 111.8369 | -8.9289 | 111.9563 | 111.8944 | 0.057428 | -8.8989 | -8.8683 | 120.7979 | 120.8067 | 120.8927 | 75.9368 | -120.8663 | 111.8979 | 111.9278 | 111.9585 | 111.9236 | -8.9898
2617.3125 | 121.1334 | -112.0834 | 8.7112 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060325 | -0.0054142 | 0.055401 | -0.0099194 | -0.0011493 | 0.024515 | -0.0049502 | 0.018857 | 0.013988 | -111.5285 | -36.806 | -111.778 | 8.6732 | 8.6912 | 8.7726 | -112.1597 | 0.10636 | 0.078197 | 0.048959 | 0.061616 | 0.091543 | 0.11764 | -0.00389 | -0.076274 | -0.038011 | 0.55495 | 0.30546 | 0.38174 | -0.020085 | 0.061389 | 112.0795 | -8.6496 | 112.1898 | 112.1324 | 0.052849 | -8.6197 | -8.5936 | 120.7567 | 120.7746 | 120.8561 | 75.2775 | -120.871 | 112.1451 | 112.175 | 112.2011 | 112.1616 | -8.7151
2619.0781 | 121.0144 | -87.4832 | 33.4671 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060539 | -0.0054142 | 0.055401 | -0.0022889 | -0.00072206 | 0.025156 | -0.0047366 | 0.018643 | 0.013561 | -87.0982 | -27.4382 | -87.3071 | 33.2866 | 33.225 | 33.2544 | -87.5297 | 0.092622 | 0.059882 | 0.039802 | 0.034145 | 0.059493 | 0.099323 | -0.022205 | -0.046459 | -0.18046 | 0.38501 | 0.17615 | 0.22261 | -0.24207 | -0.21268 | 87.461 | -33.433 | 87.5758 | 87.523 | 0.062007 | -33.4076 | -33.3678 | 120.7699 | 120.7082 | 120.7376 | 60.0451 | -120.9968 | 87.5174 | 87.5427 | 87.5825 | 87.5431 | -33.4893
2620.8594 | 121.0144 | -89.4196 | 31.4941 | 1.4211e-13 | -0.035337 | -0.0028739 | 0.060752 | -0.005628 | 0.055614 | -0.0022889 | -0.0013631 | 0.024942 | -0.0047366 | 0.018643 | 0.013988 | -88.8609 | -28.8713 | -89.0285 | 31.5194 | 31.453 | 31.4917 | -89.3109 | 0.092622 | 0.064461 | 0.035223 | 0.029566 | 0.064071 | 0.099323 | -0.031363 | 0.10868 | 0.025246 | 0.55867 | 0.39106 | 0.28238 | -0.041149 | -0.002484 | 89.3882 | -31.4646 | 89.5122 | 89.4548 | 0.066586 | -31.4301 | -31.3948 | 120.9389 | 120.8725 | 120.9112 | 60.5483 | -120.805 | 89.4491 | 89.4836 | 89.5189 | 89.484 | -31.5255
2622.5781 | 121.1243 | -91.7404 | 29.0451 | 1.4211e-13 | -0.035337 | -0.0030877 | 0.060752 | -0.0058416 | 0.055187 | -0.0099194 | -0.0011493 | 0.024942 | -0.0049502 | 0.01907 | 0.013561 | -91.2554 | -30.4692 | -91.4229 | 29.1066 | 29.0491 | 29.0787 | -91.7331 | 0.097201 | 0.064461 | 0.035223 | 0.043302 | 0.073228 | 0.099323 | -0.022205 | 0.00729 | 0.061472 | 0.48504 | 0.31748 | 0.31019 | 0.003951 | 0.033629 | 91.7182 | -29.0018 | 91.8376 | 91.7756 | 0.057428 | -28.9719 | -28.9458 | 120.847 | 120.7895 | 120.8192 | 61.2712 | -120.7782 | 91.7837 | 91.8136 | 91.8397 | 91.8049 | -29.0673
2624.3594 | 121.0876 | -94.4275 | 26.3992 | 1.4211e-13 | -0.035765 | -0.0026603 | 0.060752 | -0.005628 | 0.055187 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013561 | -93.7414 | -32.0671 | -93.9181 | 26.5885 | 26.5306 | 26.5834 | -94.247 | 0.10178 | 0.06904 | 0.026066 | 0.043302 | 0.073228 | 0.099323 | -0.017627 | 0.18053 | 0.18923 | 0.68605 | 0.50939 | 0.32886 | 0.13142 | 0.18417 | 94.4099 | -26.3559 | 94.5293 | 94.4536 | 0.043693 | -26.326 | -26.2999 | 121.016 | 120.9581 | 121.0109 | 62.3604 | -120.6462 | 94.4708 | 94.5007 | 94.5268 | 94.4965 | -26.4169
2626.0781 | 121.106 | -92.0837 | 28.7338 | 1.4211e-13 | -0.035765 | -0.0035151 | 0.060752 | -0.0054142 | 0.055401 | 0.0053411 | -0.0013631 | 0.024729 | -0.0047366 | 0.01907 | 0.013774 | -91.6766 | -31.8565 | -91.8853 | 28.6625 | 28.6003 | 28.6438 | -92.1635 | 0.097201 | 0.06904 | 0.030644 | 0.034145 | 0.06865 | 0.099323 | -0.022205 | -0.079806 | -0.071353 | 0.40715 | 0.1984 | 0.2782 | -0.1335 | -0.090059 | 92.0615 | -28.6997 | 92.1809 | 92.1144 | 0.052849 | -28.6652 | -28.6345 | 120.7462 | 120.6841 | 120.7275 | 60.2272 | -120.8974 | 92.1179 | 92.1524 | 92.1831 | 92.1528 | -28.756
2627.8594 | 121.0464 | -89.7675 | 31.0776 | 1.4211e-13 | -0.035551 | -0.0026603 | 0.060325 | -0.0054142 | 0.055401 | -0.0099194 | -0.00093566 | 0.024729 | -0.004523 | 0.018857 | 0.013561 | -89.3553 | -31.6047 | -89.5458 | 31.0112 | 30.9493 | 30.9834 | -89.8146 | 0.097201 | 0.064461 | 0.030644 | 0.038723 | 0.064071 | 0.090166 | -0.022205 | -0.047101 | -0.06639 | 0.41211 | 0.22161 | 0.26872 | -0.12827 | -0.094143 | 89.7453 | -31.0389 | 89.8647 | 89.7981 | 0.052849 | -31.0135 | -30.9874 | 120.7786 | 120.7168 | 120.7509 | 58.1628 | -120.8921 | 89.8062 | 89.8315 | 89.8576 | 89.8319 | -31.0998
2629.5781 | 121.1426 | -87.8311 | 32.9773 | 1.4211e-13 | -0.035124 | -0.0028739 | 0.060325 | -0.005628 | 0.055401 | -0.0022889 | -0.00093566 | 0.025156 | -0.0049502 | 0.01907 | 0.013774 | -87.4095 | -31.4078 | -87.5909 | 32.9799 | 32.9045 | 32.9385 | -87.8548 | 0.092622 | 0.055303 | 0.026066 | 0.029566 | 0.06865 | 0.090166 | -0.035942 | -0.023662 | 0.002598 | 0.42158 | 0.2402 | 0.26386 | -0.072784 | -0.038799 | 87.7952 | -32.9477 | 87.9237 | 87.8572 | 0.062008 | -32.9086 | -32.8871 | 120.811 | 120.7356 | 120.7696 | 56.4233 | -120.8321 | 87.8607 | 87.8998 | 87.9213 | 87.8864 | -33.0132
2631.3594 | 121.1197 | -87.6755 | 33.1055 | 1.4211e-13 | -0.035765 | -0.0028739 | 0.060752 | -0.0054142 | 0.055614 | -0.0099194 | -0.0011493 | 0.024301 | -0.0049502 | 0.018429 | 0.013774 | -87.263 | -31.9527 | -87.4353 | 33.1218 | 33.051 | 33.0896 | -87.7083 | 0.10178 | 0.059882 | 0.026066 | 0.034145 | 0.064071 | 0.094744 | -0.026784 | -0.032776 | 0.016354 | 0.41245 | 0.24022 | 0.273 | -0.054433 | -0.015879 | 87.6487 | -33.0713 | 87.7773 | 87.7015 | 0.05285 | -33.0414 | -33.0107 | 120.7973 | 120.7265 | 120.7651 | 55.7228 | -120.8137 | 87.7096 | 87.7395 | 87.7702 | 87.7354 | -33.1323
2633.125 | 121.0007 | -87.7716 | 33.0963 | 1.4211e-13 | -0.035765 | -0.0033013 | 0.06118 | -0.005628 | 0.055401 | 0.0053411 | -0.0013631 | 0.024942 | -0.0047366 | 0.018857 | 0.013774 | -87.318 | -32.7173 | -87.5039 | 33.044 | 32.9824 | 33.0209 | -87.7815 | 0.092622 | 0.06904 | 0.026066 | 0.034145 | 0.059493 | 0.094744 | -0.022205 | -0.009909 | -0.052322 | 0.45364 | 0.26768 | 0.27759 | -0.11396 | -0.075402 | 87.7494 | -33.0622 | 87.8642 | 87.7977 | 0.048271 | -33.0368 | -33.0016 | 120.8156 | 120.754 | 120.7925 | 55.0543 | -120.8778 | 87.8058 | 87.8311 | 87.8664 | 87.8406 | -33.1185
2634.9062 | 121.019 | -92.0151 | 28.775 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060539 | -0.0058416 | 0.055401 | -0.0022889 | -0.0011493 | 0.024942 | -0.0047366 | 0.018857 | 0.013561 | -91.5484 | -35.3546 | -91.6885 | 28.8181 | 28.7514 | 28.804 | -92.0811 | 0.10178 | 0.064461 | 0.035223 | 0.034145 | 0.06865 | 0.099323 | -0.022205 | -0.066049 | 0.043115 | 0.46668 | 0.3266 | 0.39265 | -0.023598 | 0.028994 | 91.9929 | -28.7409 | 92.1169 | 92.0503 | 0.057428 | -28.7064 | -28.6757 | 120.8332 | 120.7665 | 120.8191 | 56.6605 | -120.8561 | 92.0492 | 92.0837 | 92.1144 | 92.0795 | -28.7972
2636.6875 | 120.9869 | -92.6102 | 28.1616 | 1.4211e-13 | -0.035551 | -0.0028739 | 0.060539 | -0.0052006 | 0.055187 | -0.0099194 | -0.0015767 | 0.024942 | -0.0049502 | 0.018429 | 0.013774 | -92.1573 | -36.3847 | -92.3111 | 28.0948 | 28.0875 | 28.1264 | -92.6535 | 0.097201 | 0.064461 | 0.039802 | 0.038723 | 0.064071 | 0.099323 | -0.022205 | -0.043322 | -0.066868 | 0.45285 | 0.29905 | 0.34237 | -0.074139 | -0.035236 | 92.588 | -28.1229 | 92.7074 | 92.65 | 0.062007 | -28.0976 | -28.0623 | 120.7049 | 120.6977 | 120.7366 | 56.2254 | -120.8151 | 92.6489 | 92.6742 | 92.7095 | 92.6746 | -28.1838
2638.4688 | 120.9412 | -91.8549 | 28.9215 | 1.4211e-13 | -0.035551 | -0.0026603 | 0.060325 | -0.005628 | 0.054973 | -0.0022889 | -0.00093566 | 0.024729 | -0.0051638 | 0.018857 | 0.013774 | -91.4202 | -36.8884 | -91.5694 | 28.8181 | 28.8018 | 28.8452 | -91.9254 | 0.092622 | 0.064461 | 0.026066 | 0.034145 | 0.06865 | 0.094744 | -0.026784 | -0.070583 | -0.10337 | 0.43466 | 0.28542 | 0.356 | -0.11971 | -0.076284 | 91.8281 | -28.8874 | 91.9475 | 91.8809 | 0.05285 | -28.8529 | -28.8268 | 120.673 | 120.6567 | 120.7001 | 54.9665 | -120.847 | 91.889 | 91.9235 | 91.9496 | 91.9193 | -28.9483
2640.1875 | 120.9366 | -91.8869 | 28.8986 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060966 | -0.0054142 | 0.054973 | 0.0053411 | -0.0013631 | 0.024942 | -0.0051638 | 0.018857 | 0.013561 | -91.3836 | -37.3188 | -91.5237 | 28.841 | 28.8293 | 28.8727 | -91.8751 | 0.10178 | 0.073618 | 0.021487 | 0.034145 | 0.064071 | 0.099323 | -0.022205 | 0.011829 | -0.05759 | 0.50333 | 0.36324 | 0.35141 | -0.069353 | -0.025924 | 91.8647 | -28.8645 | 91.9887 | 91.9084 | 0.043692 | -28.8346 | -28.7993 | 120.7279 | 120.7162 | 120.7596 | 54.5681 | -120.7737 | 91.921 | 91.951 | 91.9862 | 91.9605 | -28.9208
2641.9688 | 121.0327 | -91.6901 | 28.981 | 1.4211e-13 | -0.035337 | -0.0028739 | 0.060539 | -0.0054142 | 0.055187 | -0.0099194 | -0.0011493 | 0.024515 | -0.0047366 | 0.018643 | 0.013774 | -91.2142 | -37.9186 | -91.3634 | 28.9875 | 28.985 | 29.0146 | -91.7194 | 0.097201 | 0.06904 | 0.030644 | 0.038723 | 0.073228 | 0.1039 | -0.022205 | -0.029327 | 0.006521 | 0.47589 | 0.32664 | 0.35597 | 0.003933 | 0.033615 | 91.6679 | -28.9423 | 91.7873 | 91.7207 | 0.052849 | -28.9078 | -28.8771 | 120.6776 | 120.675 | 120.7047 | 53.7715 | -120.7004 | 91.7288 | 91.7633 | 91.794 | 91.7591 | -29.0032
2643.75 | 120.9045 | -91.9373 | 28.8162 | 1.4211e-13 | -0.035551 | -0.0030877 | 0.060539 | -0.0054142 | 0.055187 | -0.0099194 | -0.0011493 | 0.024729 | -0.0051638 | 0.01907 | 0.013774 | -91.4156 | -38.7885 | -91.5511 | 28.7815 | 28.7743 | 28.804 | -91.9254 | 0.097201 | 0.06904 | 0.035223 | 0.038723 | 0.073228 | 0.090166 | -0.026784 | 0.011815 | -0.034711 | 0.52163 | 0.38613 | 0.37431 | -0.041902 | -0.012205 | 91.9105 | -28.7775 | 92.0345 | 91.9725 | 0.062007 | -28.743 | -28.7261 | 120.7188 | 120.7116 | 120.7413 | 53.1487 | -120.7417 | 91.976 | 92.0105 | 92.0274 | 92.0063 | -28.843
2645.5312 | 120.9824 | -40.8417 | 80.0812 | 1.4211e-13 | -0.035551 | -0.0024467 | 0.06118 | -0.005628 | 0.054546 | -0.0099194 | -0.0011493 | 0.024729 | -0.0047366 | 0.019284 | 0.013561 | -40.7512 | -13.1895 | -40.8375 | 80.0137 | 79.8705 | 79.828 | -40.8338 | 0.051413 | 0.027831 | -0.019721 | -0.007062 | 0.027442 | 0.048958 | -0.063415 | 0.007874 | -0.067505 | 0.090492 | 0.00416 | -0.003714 | -0.21064 | -0.25321 | 40.7783 | -80.0882 | 40.8931 | 40.822 | 0.043694 | -80.0537 | -80.0322 | 120.8553 | 120.7122 | 120.6696 | 27.6521 | -120.915 | 40.8346 | 40.8691 | 40.8906 | 40.8695 | -80.1446
2647.25 | 121.1014 | -40.5945 | 80.3055 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.06118 | -0.005628 | 0.05476 | 0.0053411 | -0.0011493 | 0.024942 | -0.0047366 | 0.01907 | 0.013561 | -40.5177 | -13.4459 | -40.5994 | 80.3113 | 80.1727 | 80.1164 | -40.6003 | 0.046835 | 0.018674 | -0.010564 | -0.016219 | 0.027442 | 0.058115 | -0.067994 | -0.005794 | 0.005786 | 0.076797 | -0.004963 | 0.000831 | -0.13273 | -0.18906 | 40.5265 | -80.3217 | 40.6413 | 40.5839 | 0.05743 | -80.278 | -80.2474 | 120.9057 | 120.7672 | 120.7109 | 27.1485 | -120.9058 | 40.5783 | 40.6219 | 40.6526 | 40.6132 | -80.3735
2649.0469 | 121.0968 | -40.4434 | 80.4474 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061393 | -0.0058416 | 0.054546 | -0.0099194 | -0.0011493 | 0.024729 | -0.0047366 | 0.018857 | 0.013561 | -40.3895 | -13.7573 | -40.4758 | 80.4669 | 80.3284 | 80.2721 | -40.4812 | 0.051413 | 0.023253 | -0.010564 | -0.007062 | 0.022864 | 0.048958 | -0.058836 | -0.037804 | 0.019544 | 0.05393 | -0.032411 | 0.005393 | -0.11896 | -0.1753 | 40.3846 | -80.4545 | 40.4948 | 40.4329 | 0.048272 | -80.4245 | -80.3984 | 120.9104 | 120.7719 | 120.7155 | 26.6861 | -120.9286 | 40.4364 | 40.4663 | 40.4924 | 40.4667 | -80.5062
2650.7656 | 121.0556 | -40.3656 | 80.5801 | 1.4211e-13 | -0.035124 | -0.0024467 | 0.060966 | -0.005628 | 0.05476 | -0.0099194 | -0.0013631 | 0.025156 | -0.0051638 | 0.018857 | 0.013561 | -40.2979 | -14.0457 | -40.3705 | 80.5905 | 80.4383 | 80.3957 | -40.3805 | 0.051413 | 0.018674 | -0.010564 | -0.01164 | 0.022864 | 0.053537 | -0.058836 | -0.014887 | 0.01041 | 0.067679 | -0.00493 | 0.009957 | -0.14181 | -0.18443 | 40.3068 | -80.5918 | 40.417 | 40.355 | 0.048272 | -80.5573 | -80.5266 | 120.9561 | 120.8039 | 120.7613 | 26.3199 | -120.9606 | 40.354 | 40.3885 | 40.4191 | 40.3843 | -80.639
2652.5312 | 121.1609 | -40.2466 | 80.6717 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061393 | -0.0058416 | 0.05476 | -0.0022889 | -0.00093566 | 0.024942 | -0.0051638 | 0.018857 | 0.013561 | -40.1697 | -14.3113 | -40.2561 | 80.7096 | 80.5665 | 80.5285 | -40.2752 | 0.046835 | 0.018674 | -0.019721 | -0.01164 | 0.018285 | 0.053537 | -0.067994 | -0.028591 | 0.037895 | 0.076854 | -0.009492 | 0.019099 | -0.10516 | -0.1432 | 40.1786 | -80.6833 | 40.2934 | 40.2269 | 0.048273 | -80.6534 | -80.6182 | 120.9562 | 120.8131 | 120.7751 | 25.9353 | -120.9469 | 40.2349 | 40.2649 | 40.3001 | 40.2653 | -80.7397
2654.2969 | 121.1746 | -40.1184 | 80.8182 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.06118 | -0.005628 | 0.05476 | -0.0022889 | -0.0011493 | 0.024942 | -0.004523 | 0.01907 | 0.013347 | -40.0736 | -14.6135 | -40.1508 | 80.824 | 80.6856 | 80.6384 | -40.1744 | 0.046835 | 0.023253 | -0.015143 | -0.01164 | 0.022864 | 0.048958 | -0.063415 | -0.056028 | 0.00587 | 0.044827 | -0.032365 | 0.023663 | -0.13259 | -0.1798 | 40.055 | -80.8298 | 40.1652 | 40.1033 | 0.048272 | -80.7953 | -80.7692 | 120.9425 | 120.804 | 120.7568 | 25.5049 | -120.9926 | 40.1068 | 40.1413 | 40.1674 | 40.1417 | -80.8816
2656.0312 | 121.1655 | -40.0314 | 80.928 | 1.4211e-13 | -0.035124 | -0.0026603 | 0.061607 | -0.005628 | 0.054546 | -0.0022889 | -0.0013631 | 0.024729 | -0.0051638 | 0.018857 | 0.013561 | -39.9729 | -14.8653 | -40.0455 | 80.9477 | 80.8046 | 80.7528 | -40.0645 | 0.060571 | 0.023253 | -0.005985 | -0.01164 | 0.022864 | 0.048958 | -0.067994 | -0.033109 | 0.019623 | 0.058576 | -0.01404 | 0.019069 | -0.1234 | -0.1752 | 39.9634 | -80.9397 | 40.092 | 40.0254 | 0.062009 | -80.9052 | -80.8791 | 120.9791 | 120.8361 | 120.7843 | 25.1661 | -120.9926 | 40.0198 | 40.0543 | 40.0804 | 40.0547 | -80.996
2657.7969 | 121.1151 | -39.9536 | 81.0745 | 1.4211e-13 | -0.035124 | -0.0024467 | 0.061393 | -0.0058416 | 0.05476 | -0.0022889 | -0.0013631 | 0.024942 | -0.004523 | 0.019284 | 0.013347 | -39.8538 | -15.1446 | -39.9264 | 81.0759 | 80.9283 | 80.8902 | -39.9546 | 0.055992 | 0.027831 | -0.010564 | -0.01164 | 0.022864 | 0.053537 | -0.072572 | -0.001035 | 0.001334 | 0.099794 | 0.027176 | 0.028211 | -0.14625 | -0.18432 | 39.881 | -81.0862 | 40.0096 | 39.943 | 0.062008 | -81.0517 | -81.021 | 121.0295 | 120.8819 | 120.8438 | 24.809 | -121.0292 | 39.942 | 39.9765 | 40.0071 | 39.9814 | -81.1471
2659.5625 | 121.2708 | -39.7888 | 81.134 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.06118 | -0.0058416 | 0.05476 | -0.0022889 | -0.00093566 | 0.024942 | -0.0049502 | 0.019498 | 0.013561 | -39.7439 | -15.4285 | -39.8211 | 81.1857 | 81.0427 | 80.9864 | -39.8402 | 0.046835 | 0.027831 | -0.015143 | -0.01164 | 0.022864 | 0.053537 | -0.067994 | -0.051357 | 0.051706 | 0.044881 | -0.032319 | 0.019038 | -0.091289 | -0.14768 | 39.7208 | -81.1457 | 39.8357 | 39.7737 | 0.052851 | -81.1112 | -81.0805 | 120.9746 | 120.8316 | 120.7752 | 24.3603 | -120.9742 | 39.7772 | 39.8117 | 39.8424 | 39.8166 | -81.202
2661.2656 | 121.2067 | -39.7202 | 81.2439 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061607 | -0.0060552 | 0.054973 | -0.0022889 | -0.0011493 | 0.024301 | -0.0047366 | 0.01907 | 0.013561 | -39.6707 | -15.6986 | -39.7341 | 81.2682 | 81.1252 | 81.0825 | -39.7715 | 0.046835 | 0.023253 | -0.015143 | -0.020797 | 0.018285 | 0.053537 | -0.063415 | -0.051337 | 0.024254 | 0.049471 | -0.013996 | 0.037341 | -0.11873 | -0.1614 | 39.6567 | -81.2647 | 39.767 | 39.705 | 0.048272 | -81.2256 | -81.1904 | 120.9883 | 120.8453 | 120.8027 | 24.0215 | -121.0154 | 39.6994 | 39.7384 | 39.7737 | 39.7434 | -81.3073
2663.0469 | 121.2799 | -39.6057 | 81.3721 | 1.4211e-13 | -0.035124 | -0.0024467 | 0.06118 | -0.0058416 | 0.05476 | -0.0099194 | -0.00093566 | 0.024729 | -0.0051638 | 0.01907 | 0.013561 | -39.5425 | -15.923 | -39.6151 | 81.4009 | 81.2534 | 81.2153 | -39.6479 | 0.046835 | 0.027831 | -0.028879 | -0.016219 | 0.018285 | 0.044379 | -0.058836 | -0.042147 | 0.028853 | 0.063225 | -0.009401 | 0.032746 | -0.11869 | -0.15679 | 39.5469 | -81.3883 | 39.6525 | 39.5768 | 0.029957 | -81.3538 | -81.3277 | 121.0066 | 120.8591 | 120.821 | 23.6827 | -121.0199 | 39.5895 | 39.624 | 39.6501 | 39.6335 | -81.4309
2664.8281 | 121.225 | -39.5279 | 81.4865 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061393 | -0.005628 | 0.05476 | -0.01755 | -0.0013631 | 0.024729 | -0.0049502 | 0.019284 | 0.013774 | -39.428 | -16.1656 | -39.4961 | 81.5245 | 81.377 | 81.3343 | -39.5334 | 0.055992 | 0.018674 | -0.0243 | -0.007062 | 0.022864 | 0.058115 | -0.063415 | -0.005494 | 0.038029 | 0.099864 | 0.031814 | 0.037308 | -0.1095 | -0.15219 | 39.4645 | -81.4936 | 39.5839 | 39.5036 | 0.039115 | -81.4636 | -81.4284 | 121.0524 | 120.9049 | 120.8622 | 23.3623 | -121.0199 | 39.5208 | 39.5508 | 39.586 | 39.5466 | -81.5499
2666.6094 | 121.2204 | -39.2303 | 81.7657 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.06118 | -0.0054142 | 0.05476 | -0.0022889 | -0.0013631 | 0.024729 | -0.0049502 | 0.018643 | 0.013561 | -34.5429 | -13.5284 | -34.6065 | 86.4829 | 86.3039 | 86.2746 | -34.6568 | 0.046835 | 0.018674 | -0.015143 | -0.016219 | 0.018285 | 0.044379 | -0.072572 | 4.5735 | 4.7172 | 4.6875 | 4.6239 | 0.050357 | 4.5382 | 4.5089 | 39.1578 | -81.782 | 39.2772 | 39.2152 | 0.057429 | -81.7475 | -81.7214 | 125.7133 | 125.5343 | 125.505 | 25.702 | -116.4226 | 39.2141 | 39.2486 | 39.2747 | 39.249 | -81.8383
2668.3125 | 121.225 | -32.1213 | 88.9526 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061393 | -0.005628 | 0.055187 | -0.0099194 | -0.0011493 | 0.025156 | -0.0049502 | 0.018857 | 0.013561 | -32.8077 | -12.6859 | -32.8484 | 88.2777 | 88.0806 | 88.0923 | -32.926 | 0.055992 | 0.018674 | -0.019721 | -0.016219 | 0.013707 | 0.039801 | -0.063415 | -0.80472 | -0.67497 | -0.6864 | -0.72714 | 0.077583 | -0.87209 | -0.86029 | 32.0579 | -88.9689 | 32.1773 | 32.1016 | 0.043694 | -88.9389 | -88.9128 | 120.3989 | 120.2018 | 120.2136 | 19.4354 | -121.8786 | 32.1051 | 32.135 | 32.1611 | 32.14 | -89.0161
2670.0938 | 121.2982 | -31.929 | 89.0762 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061607 | -0.005628 | 0.05476 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.018643 | 0.013774 | -31.86 | -12.3517 | -31.9419 | 89.1613 | 89.0147 | 88.9531 | -31.9232 | 0.046835 | 0.014095 | -0.0243 | -0.016219 | 0.018285 | 0.058115 | -0.072572 | 0.005802 | 0.085058 | 0.069062 | -0.0129 | -0.018702 | -0.061581 | -0.12311 | 31.8564 | -89.0925 | 31.9759 | 31.9047 | 0.048272 | -89.0579 | -89.0181 | 121.0903 | 120.9437 | 120.8821 | 19.5774 | -120.9994 | 31.9128 | 31.9473 | 31.9871 | 31.9431 | -89.1488
2671.875 | 121.2753 | -35.9299 | 85.0891 | 1.4211e-13 | -0.035551 | -0.0024467 | 0.061393 | -0.0060552 | 0.054973 | -0.0099194 | -0.0011493 | 0.024942 | -0.0051638 | 0.018643 | 0.013774 | -33.8149 | -13.7985 | -33.8923 | 87.2155 | 87.0503 | 87.0072 | -33.9379 | 0.046835 | 0.023253 | -0.0243 | -0.020797 | 0.013707 | 0.044379 | -0.072572 | 1.9919 | 2.1264 | 2.1149 | 2.0376 | 0.045677 | 1.9612 | 1.9181 | 35.8573 | -85.1099 | 35.9767 | 35.9056 | 0.048272 | -85.0754 | -85.0447 | 123.1453 | 122.9802 | 122.9371 | 22.1314 | -119.0271 | 35.9091 | 35.9436 | 35.9742 | 35.9531 | -85.1617
2673.6719 | 121.2708 | -29.892 | 91.1499 | 1.4211e-13 | -0.035765 | -0.0024467 | 0.061607 | -0.0058416 | 0.054973 | -0.01755 | -0.0013631 | 0.024942 | -0.0051638 | 0.01907 | 0.013774 | -29.9141 | -11.5962 | -30.0145 | 91.1117 | 90.9699 | 90.9036 | -29.9818 | 0.037677 | 0.004938 | -0.019721 | -0.020797 | 0.013707 | 0.044379 | -0.067994 | -0.089782 | -0.038218 | -0.022171 | -0.12249 | -0.03271 | -0.18005 | -0.2463 | 29.824 | -91.1707 | 29.9296 | 29.8722 | 0.048273 | -91.1362 | -91.1055 | 121.0037 | 120.8618 | 120.7956 | 18.2958 | -121.1317 | 29.8712 | 29.9057 | 29.9363 | 29.8969 | -91.2179
2675.4375 | 121.2799 | -29.1275 | 91.9235 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061607 | -0.0058416 | 0.05476 | -0.0022889 | -0.0011493 | 0.024515 | -0.0047366 | 0.018643 | 0.013561 | -28.9893 | -11.2207 | -29.0851 | 92.0548 | 91.8994 | 91.8376 | -29.0568 | 0.046835 | 0.004938 | -0.0243 | -0.016219 | 0.013707 | 0.048958 | -0.077151 | 0.070695 | 0.13131 | 0.1382 | 0.042433 | -0.028262 | -0.024148 | -0.085884 | 29.0504 | -91.9397 | 29.1743 | 29.1032 | 0.052851 | -91.9098 | -91.8746 | 121.1823 | 121.0269 | 120.9651 | 17.9068 | -120.9803 | 29.1113 | 29.1412 | 29.1765 | 29.1324 | -92.0007
2677.1562 | 121.2021 | -29.0085 | 92.1295 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.061821 | -0.0060552 | 0.054973 | -0.0099194 | -0.0013631 | 0.024942 | -0.0049502 | 0.019284 | 0.013561 | -28.9206 | -11.3673 | -29.0164 | 92.1327 | 91.9726 | 91.9155 | -28.9973 | 0.037677 | 0.014095 | -0.0243 | -0.025376 | 0.009128 | 0.035222 | -0.067994 | 0.011203 | 0.003147 | 0.087855 | -0.007911 | -0.019114 | -0.15688 | -0.21404 | 28.9405 | -92.1549 | 29.0462 | 28.9842 | 0.043694 | -92.1204 | -92.0943 | 121.1411 | 120.9811 | 120.924 | 17.6412 | -121.1268 | 28.9831 | 29.0176 | 29.0437 | 29.0226 | -92.1975
2678.9375 | 121.2158 | -28.3905 | 92.7292 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.0060552 | 0.054546 | -0.0099194 | -0.0011493 | 0.024729 | -0.0051638 | 0.019284 | 0.013561 | -28.2339 | -11.088 | -28.3388 | 92.8103 | 92.6549 | 92.5931 | -28.315 | 0.051413 | 0.009516 | -0.0243 | -0.016219 | -2.9e-05 | 0.044379 | -0.067994 | 0.075481 | 0.081079 | 0.15663 | 0.051694 | -0.023787 | -0.07429 | -0.13608 | 28.3225 | -92.7454 | 28.4419 | 28.3662 | 0.043694 | -92.7292 | -92.6848 | 121.2008 | 121.0454 | 120.9836 | 17.3025 | -121.0442 | 28.3743 | 28.3905 | 28.4349 | 28.4 | -92.7972
2680.7188 | 121.2433 | -27.3331 | 93.7958 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061607 | -0.0058416 | 0.054546 | 0.0053411 | -0.0011493 | 0.024515 | -0.0047366 | 0.01907 | 0.013347 | -27.1351 | -10.5614 | -27.2538 | 93.9137 | 93.7584 | 93.6874 | -27.2161 | 0.042256 | 0.014095 | -0.028879 | -0.020797 | 0.013707 | 0.035222 | -0.090888 | 0.11699 | 0.11788 | 0.19801 | 0.079312 | -0.037677 | -0.037358 | -0.10838 | 27.2422 | -93.8166 | 27.3753 | 27.3042 | 0.062009 | -93.7821 | -93.7606 | 121.2467 | 121.0915 | 121.0205 | 16.7716 | -121.0119 | 27.3123 | 27.3468 | 27.3683 | 27.3472 | -93.8867
2682.4844 | 121.3394 | -28.1021 | 92.9443 | 1.4211e-13 | -0.035551 | -0.0026603 | 0.061607 | -0.0058416 | 0.054546 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013347 | -28.1103 | -11.3627 | -28.1786 | 92.9522 | 92.7785 | 92.735 | -28.1914 | 0.046835 | 0.009516 | -0.028879 | -0.020797 | 0.013707 | 0.044379 | -0.072572 | -0.089279 | 0.00786 | -0.008142 | -0.076458 | 0.012821 | -0.16581 | -0.20929 | 28.0295 | -92.9651 | 28.1489 | 28.0732 | 0.043693 | -92.9306 | -92.9 | 121.0543 | 120.8806 | 120.8372 | 16.7394 | -121.1357 | 28.0813 | 28.1158 | 28.1465 | 28.1116 | -93.0169
2684.2031 | 121.3531 | -27.7634 | 93.2785 | 1.4211e-13 | -0.035551 | -0.0024467 | 0.061607 | -0.0058416 | 0.05476 | -0.0022889 | -0.0013631 | 0.024729 | -0.0049502 | 0.019284 | 0.013347 | -27.7074 | -11.2711 | -27.7803 | 93.3368 | 93.1861 | 93.1151 | -27.7976 | 0.037677 | 0.014095 | -0.0243 | -0.025376 | 0.018285 | 0.039801 | -0.077151 | -0.034236 | 0.058277 | 0.056011 | -0.016892 | 0.017344 | -0.092451 | -0.16343 | 27.6862 | -93.3039 | 27.801 | 27.7391 | 0.052851 | -93.2602 | -93.2387 | 121.1001 | 120.9494 | 120.8784 | 16.4923 | -121.0761 | 27.738 | 27.7817 | 27.8032 | 27.7775 | -93.3557
2685.9844 | 121.3211 | -24.1425 | 96.9635 | 1.4211e-13 | -0.035551 | -0.0022329 | 0.061393 | -0.0058416 | 0.054546 | -0.0099194 | -0.00093566 | 0.024515 | -0.0051638 | 0.018857 | 0.013347 | -24.0675 | -9.0459 | -24.1863 | 96.9995 | 96.84 | 96.7642 | -24.1665 | 0.037677 | 0.009516 | -0.028879 | -0.016219 | 0.009128 | 0.026065 | -0.08173 | -0.02406 | 0.03599 | 0.074919 | -0.043853 | -0.019793 | -0.12347 | -0.19929 | 24.0607 | -96.9797 | 24.1801 | 24.1136 | 0.052851 | -96.9544 | -96.9374 | 121.1419 | 120.9825 | 120.9067 | 15.0965 | -121.13 | 24.1262 | 24.1516 | 24.1685 | 24.152 | -97.0452
2687.75 | 121.3257 | -24.3622 | 96.7667 | 1.4211e-13 | -0.035124 | -0.0026603 | 0.061607 | -0.0060552 | 0.05476 | -0.0099194 | -0.0013631 | 0.024942 | -0.0049502 | 0.018857 | 0.013774 | -24.2736 | -9.2886 | -24.3969 | 96.7935 | 96.6202 | 96.5536 | -24.3771 | 0.042256 | 0.009516 | -0.028879 | -0.025376 | 0.018285 | 0.035222 | -0.086309 | -0.014964 | 0.0268 | 0.088618 | -0.034727 | -0.019763 | -0.14642 | -0.21306 | 24.2759 | -96.792 | 24.4044 | 24.3333 | 0.05743 | -96.7484 | -96.7314 | 121.1556 | 120.9824 | 120.9158 | 15.0736 | -121.1438 | 24.3368 | 24.3805 | 24.3974 | 24.3717 | -96.853
2689.4531 | 121.3348 | -24.0875 | 96.9589 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.061607 | -0.005628 | 0.054546 | -0.0099194 | -0.00093566 | 0.024942 | -0.0051638 | 0.019284 | 0.013347 | -24.0126 | -9.2291 | -24.1588 | 97.0361 | 96.8675 | 96.8008 | -24.1299 | 0.046835 | 0.000359 | -0.028879 | -0.025376 | 0.009128 | 0.039801 | -0.067994 | -0.042361 | 0.077195 | 0.074927 | -0.071315 | -0.028954 | -0.091415 | -0.15808 | 24.0195 | -96.9843 | 24.1344 | 24.0586 | 0.039115 | -96.9498 | -96.9191 | 121.1236 | 120.955 | 120.8884 | 14.8585 | -121.0888 | 24.0621 | 24.0967 | 24.1273 | 24.0879 | -97.0269
2691.2969 | 121.2067 | -23.9868 | 97.1832 | 1.4211e-13 | -0.035124 | -0.0020193 | 0.06118 | -0.0060552 | 0.054973 | -0.0022889 | -0.00093566 | 0.024729 | -0.0053776 | 0.019284 | 0.013774 | -23.8478 | -9.2199 | -23.9711 | 97.2147 | 97.0461 | 96.9794 | -23.9605 | 0.046835 | 0.014095 | -0.028879 | -0.029954 | -2.9e-05 | 0.035222 | -0.067994 | 0.026352 | 0.031447 | 0.13904 | 0.015686 | -0.010666 | -0.13714 | -0.20382 | 23.9188 | -97.2132 | 24.0337 | 23.9579 | 0.039115 | -97.1833 | -97.148 | 121.2015 | 121.0329 | 120.9662 | 14.7669 | -121.1437 | 23.9569 | 23.9868 | 24.022 | 24.0009 | -97.2512
2693.0781 | 121.257 | -23.8724 | 97.261 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061607 | -0.0058416 | 0.054973 | -0.0099194 | -0.0011493 | 0.024942 | -0.0053776 | 0.01907 | 0.01292 | -23.7562 | -9.284 | -23.8887 | 97.3017 | 97.1331 | 97.0664 | -23.878 | 0.042256 | 0.004938 | -0.028879 | -0.029954 | 0.009128 | 0.039801 | -0.072572 | -0.005669 | 0.040617 | 0.11617 | -0.016346 | -0.010677 | -0.12796 | -0.19464 | 23.7998 | -97.291 | 23.9146 | 23.8435 | 0.043693 | -97.2519 | -97.2212 | 121.174 | 121.0055 | 120.9388 | 14.5884 | -121.1391 | 23.8424 | 23.8815 | 23.9122 | 23.8773 | -97.3336
2694.8594 | 121.3257 | -24.7101 | 96.3913 | 1.4211e-13 | -0.035551 | -0.0022329 | 0.061607 | -0.0060552 | 0.054546 | 0.0053411 | -0.0015767 | 0.024729 | -0.0049502 | 0.01907 | 0.013561 | -24.3148 | -9.7831 | -24.4381 | 96.7614 | 96.5882 | 96.5307 | -24.4413 | 0.042256 | 0.009516 | -0.033458 | -0.025376 | 0.013707 | 0.026065 | -0.072572 | 0.26883 | 0.37012 | 0.39531 | 0.27197 | 0.003138 | 0.1969 | 0.13941 | 24.6375 | -96.4167 | 24.7523 | 24.6766 | 0.039114 | -96.3776 | -96.3652 | 121.4715 | 121.2983 | 121.2408 | 14.927 | -120.8325 | 24.6847 | 24.7238 | 24.7361 | 24.7196 | -96.4639
2696.5781 | 121.3303 | -24.1287 | 97.0001 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.061607 | -0.0058416 | 0.054973 | -0.0099194 | -0.0011493 | 0.024729 | -0.0051638 | 0.01907 | 0.013561 | -23.9897 | -9.6915 | -24.1359 | 97.0544 | 96.895 | 96.8192 | -24.1207 | 0.042256 | 0.009516 | -0.038036 | -0.029954 | 0.018285 | 0.035222 | -0.08173 | 0.007996 | 0.054309 | 0.13902 | -0.007225 | -0.015221 | -0.10514 | -0.18096 | 24.047 | -97.0301 | 24.171 | 24.0907 | 0.043694 | -96.9818 | -96.9649 | 121.1832 | 121.0237 | 120.9479 | 14.4372 | -121.1208 | 24.0988 | 24.147 | 24.1639 | 24.1382 | -97.0819
2698.3438 | 121.344 | -24.3027 | 96.7575 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.0058416 | 0.054332 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.019284 | 0.013347 | -24.214 | -9.9708 | -24.3694 | 96.8255 | 96.6706 | 96.5948 | -24.3543 | 0.042256 | 0.009516 | -0.033458 | -0.025376 | 0.009128 | 0.030644 | -0.072572 | -0.051579 | 0.068005 | 0.088627 | -0.066767 | -0.015188 | -0.086893 | -0.1627 | 24.2301 | -96.7829 | 24.3449 | 24.2692 | 0.039114 | -96.7484 | -96.7269 | 121.1282 | 120.9733 | 120.8975 | 14.3319 | -121.1118 | 24.2773 | 24.3118 | 24.3333 | 24.3122 | -96.8301
2700.0469 | 121.2845 | -24.5453 | 96.611 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.0060552 | 0.054546 | -0.0022889 | -0.0017903 | 0.024942 | -0.0049502 | 0.019284 | 0.013133 | -24.4247 | -10.2272 | -24.5617 | 96.6195 | 96.46 | 96.3979 | -24.5649 | 0.046835 | 0.004938 | -0.038036 | -0.025376 | 0.018285 | 0.044379 | -0.077151 | -0.019595 | 0.008461 | 0.12064 | -0.01644 | 0.003155 | -0.15104 | -0.2131 | 24.4681 | -96.6364 | 24.5921 | 24.5073 | 0.039115 | -96.5927 | -96.5666 | 121.1648 | 121.0053 | 120.9432 | 14.3181 | -121.1759 | 24.5199 | 24.5636 | 24.5897 | 24.5502 | -96.6882
2701.8281 | 121.3303 | -23.2773 | 97.8653 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.061393 | -0.0060552 | 0.05476 | 0.0053411 | -0.0013631 | 0.024729 | -0.0051638 | 0.018643 | 0.013347 | -23.0054 | -9.3344 | -23.1241 | 98.0754 | 97.9252 | 97.8631 | -23.237 | 0.042256 | 0.004938 | -0.038036 | -0.029954 | -2.9e-05 | 0.035222 | -0.08173 | 0.040289 | 0.21012 | 0.27193 | 0.15313 | 0.11285 | 0.059944 | -0.002215 | 23.1956 | -97.8952 | 23.3195 | 23.2392 | 0.043694 | -97.8653 | -97.8301 | 121.3527 | 121.2025 | 121.1404 | 13.9429 | -121.1023 | 23.2473 | 23.2773 | 23.3125 | 23.2822 | -97.947
2703.5469 | 121.2936 | -24.0784 | 97.0779 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061393 | -0.0058416 | 0.054546 | -0.01755 | -0.0013631 | 0.025156 | -0.0053776 | 0.018857 | 0.013347 | -23.9439 | -10.0853 | -24.0673 | 97.0773 | 96.9362 | 96.9016 | -24.107 | 0.033099 | 0.000359 | -0.033458 | -0.025376 | 0.004549 | 0.035222 | -0.08173 | -0.028621 | -0.000619 | 0.13445 | 0.011095 | 0.039716 | -0.14175 | -0.17637 | 23.9966 | -97.1033 | 24.1115 | 24.0449 | 0.048272 | -97.0734 | -97.0427 | 121.1557 | 121.0146 | 120.9799 | 13.9931 | -121.1849 | 24.053 | 24.0829 | 24.1136 | 24.0787 | -97.1597
2705.3125 | 121.2662 | -24.0326 | 97.1512 | 1.4211e-13 | -0.03491 | -0.0022329 | 0.062034 | -0.005628 | 0.05476 | -0.0022889 | -0.0011493 | 0.024729 | -0.0049502 | 0.01907 | 0.013561 | -23.8295 | -10.131 | -23.9482 | 97.2009 | 97.0369 | 97.0206 | -24.0017 | 0.037677 | 0.014095 | -0.038036 | -0.029954 | 0.009128 | 0.035222 | -0.077151 | 0.030918 | 0.049756 | 0.20313 | 0.084355 | 0.053437 | -0.11426 | -0.13057 | 23.9554 | -97.1811 | 24.0703 | 23.9946 | 0.039115 | -97.1421 | -97.116 | 121.2335 | 121.0695 | 121.0532 | 13.9016 | -121.1529 | 24.0026 | 24.0417 | 24.0678 | 24.0467 | -97.2283
2707.0938 | 121.4081 | -23.7808 | 97.3251 | 1.4211e-13 | -0.035337 | -0.0024467 | 0.061821 | -0.0058416 | 0.054546 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.018857 | 0.013347 | -23.5868 | -10.0578 | -23.7147 | 97.4344 | 97.3254 | 97.2633 | -23.7773 | 0.037677 | 0.009516 | -0.033458 | -0.029954 | 0.004549 | 0.030644 | -0.08173 | 0.003516 | 0.1093 | 0.19402 | 0.066077 | 0.062561 | 0.000266 | -0.061851 | 23.6991 | -97.3551 | 23.8185 | 23.7474 | 0.048272 | -97.3206 | -97.2945 | 121.2153 | 121.1062 | 121.0441 | 13.723 | -121.1024 | 23.7509 | 23.7854 | 23.8115 | 23.7903 | -97.4069
2708.8125 | 121.3257 | -23.5519 | 97.6135 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061607 | -0.0058416 | 0.054546 | -0.0022889 | -0.0013631 | 0.024942 | -0.0051638 | 0.018643 | 0.013347 | -23.3442 | -9.9708 | -23.4721 | 97.6862 | 97.5727 | 97.5014 | -23.53 | 0.042256 | 0.000359 | -0.033458 | -0.016219 | -2.9e-05 | 0.035222 | -0.077151 | 0.021895 | 0.072724 | 0.20779 | 0.079844 | 0.057949 | -0.040863 | -0.11216 | 23.4748 | -97.6297 | 23.5942 | 23.5185 | 0.043693 | -97.6136 | -97.5783 | 121.2382 | 121.1246 | 121.0533 | 13.5812 | -121.1436 | 23.5357 | 23.5519 | 23.5872 | 23.5523 | -97.6907
2710.5938 | 121.3577 | -23.2864 | 97.847 | 1.4211e-13 | -0.035551 | -0.0022329 | 0.061821 | -0.0060552 | 0.05476 | -0.0099194 | -0.0013631 | 0.024729 | -0.0049502 | 0.018857 | 0.013561 | -23.042 | -9.838 | -23.1791 | 97.9701 | 97.8657 | 97.7944 | -23.2507 | 0.037677 | 0.004938 | -0.033458 | -0.025376 | -0.004608 | 0.039801 | -0.077151 | 0.035707 | 0.12312 | 0.24446 | 0.10735 | 0.071644 | 0.018728 | -0.052585 | 23.2093 | -97.8724 | 23.3241 | 23.253 | 0.043693 | -97.8516 | -97.8072 | 121.2565 | 121.1522 | 121.0808 | 13.4484 | -121.0977 | 23.2611 | 23.2818 | 23.3262 | 23.2914 | -97.9241
2712.375 | 121.4035 | -23.2452 | 97.8745 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.006269 | 0.054546 | -0.0099194 | -0.0017903 | 0.024729 | -0.0047366 | 0.019284 | 0.013347 | -22.9275 | -9.8197 | -23.0738 | 98.08 | 97.971 | 97.8951 | -23.1408 | 0.037677 | 0.004938 | -0.033458 | -0.025376 | 0.004549 | 0.030644 | -0.072572 | 0.1044 | 0.20554 | 0.31772 | 0.17145 | 0.06705 | 0.096577 | 0.020679 | 23.1727 | -97.8998 | 23.2829 | 23.2118 | 0.039114 | -97.8699 | -97.8438 | 121.3252 | 121.2163 | 121.1404 | 13.4255 | -121.0153 | 23.2199 | 23.2498 | 23.2759 | 23.2502 | -97.947
2714.0938 | 121.312 | -22.7783 | 98.4009 | 1.4211e-13 | -0.035124 | -0.0022329 | 0.061821 | -0.0060552 | 0.054973 | 0.0053411 | -0.0013631 | 0.024942 | -0.0053776 | 0.019284 | 0.013561 | -22.4834 | -9.5679 | -22.648 | 98.5012 | 98.3923 | 98.3255 | -22.7196 | 0.046835 | 0.009516 | -0.028879 | -0.034533 | -2.9e-05 | 0.030644 | -0.072572 | 0.058744 | 0.10032 | 0.2949 | 0.13031 | 0.071569 | -0.008589 | -0.075361 | 22.7057 | -98.4354 | 22.8252 | 22.7494 | 0.043693 | -98.4009 | -98.3702 | 121.2795 | 121.1706 | 121.1038 | 13.2104 | -121.1205 | 22.7438 | 22.7783 | 22.809 | 22.7878 | -98.4735
2715.875 | 121.3074 | -24.0234 | 97.1512 | 1.4211e-13 | -0.035765 | -0.0020193 | 0.06118 | -0.0060552 | 0.05476 | -0.0022889 | -0.00093566 | 0.024942 | -0.0051638 | 0.01907 | 0.013347 | -23.5914 | -10.3966 | -23.7514 | 97.4024 | 97.2842 | 97.2221 | -23.8414 | 0.046835 | 0.009516 | -0.033458 | -0.029954 | -2.9e-05 | 0.030644 | -0.077151 | 0.18203 | 0.2512 | 0.43205 | 0.27207 | 0.09004 | 0.13301 | 0.070891 | 23.9463 | -97.1811 | 24.0703 | 23.99 | 0.043693 | -97.1512 | -97.1205 | 121.4258 | 121.3076 | 121.2455 | 13.6268 | -120.9926 | 23.9935 | 24.0234 | 24.0541 | 24.033 | -97.2283
2717.6562 | 121.3806 | -22.7325 | 98.3871 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.0060552 | 0.054973 | -0.0022889 | -0.0013631 | 0.024301 | -0.0051638 | 0.01907 | 0.013561 | -22.2637 | -9.5679 | -22.4328 | 98.7347 | 98.5526 | 98.4949 | -22.5181 | 0.037677 | 0.009516 | -0.038036 | -0.025376 | 0.004549 | 0.026065 | -0.077151 | 0.21444 | 0.34755 | 0.46889 | 0.29972 | 0.085276 | 0.16541 | 0.10778 | 22.6554 | -98.4125 | 22.7702 | 22.6945 | 0.039115 | -98.3826 | -98.3611 | 121.4672 | 121.2851 | 121.2275 | 13.1647 | -120.9052 | 22.7072 | 22.7371 | 22.7586 | 22.7421 | -98.4643
2719.375 | 121.2936 | -21.8719 | 99.3942 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061607 | -0.005628 | 0.05476 | -0.0099194 | -0.0011493 | 0.024729 | -0.0049502 | 0.019284 | 0.013561 | -21.4716 | -9.1054 | -21.6637 | 99.5039 | 99.3355 | 99.2641 | -21.7397 | 0.042256 | 0.014095 | -0.038036 | -0.029954 | -2.9e-05 | 0.026065 | -0.086309 | 0.13226 | 0.10964 | 0.40036 | 0.20827 | 0.07601 | -0.058678 | -0.13009 | 21.7856 | -99.4242 | 21.9142 | 21.8339 | 0.048273 | -99.3943 | -99.3682 | 121.3758 | 121.2075 | 121.1361 | 12.7665 | -121.1339 | 21.842 | 21.8719 | 21.898 | 21.886 | -99.4805
2721.1562 | 121.344 | -21.2402 | 99.9664 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061607 | -0.0060552 | 0.05476 | -0.0022889 | -0.0013631 | 0.024942 | -0.0049502 | 0.019498 | 0.013347 | -21.0092 | -9.0322 | -21.2471 | 99.9571 | 99.7889 | 99.722 | -21.291 | 0.037677 | 0.004938 | -0.028879 | -0.025376 | 0.004549 | 0.030644 | -0.08173 | -0.050717 | -0.009302 | 0.23106 | -0.006819 | 0.043898 | -0.17757 | -0.24444 | 21.1585 | -99.9918 | 21.2779 | 21.2114 | 0.052851 | -99.9619 | -99.9358 | 121.1974 | 121.0291 | 120.9622 | 12.2081 | -121.2574 | 21.2149 | 21.2448 | 21.2709 | 21.2452 | -100.0482
2722.9375 | 121.3394 | -21.0205 | 100.1862 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061393 | -0.0058416 | 0.05476 | -0.0022889 | -0.0011493 | 0.024942 | -0.0051638 | 0.018857 | 0.013561 | -21.4441 | -9.403 | -21.6728 | 99.4901 | 99.3493 | 99.2596 | -21.7259 | 0.042256 | 0.000359 | -0.033458 | -0.029954 | -2.9e-05 | 0.030644 | -0.072572 | -0.70544 | -0.69602 | -0.42361 | -0.65233 | 0.053116 | -0.83687 | -0.9266 | 20.9479 | -100.2161 | 21.0628 | 20.987 | 0.039114 | -100.1862 | -100.1555 | 120.5106 | 120.3698 | 120.2801 | 11.6175 | -121.9121 | 20.9906 | 21.0205 | 21.0512 | 21.0209 | -100.2587
2724.6562 | 121.4172 | -21.904 | 99.2477 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061821 | -0.005628 | 0.054546 | -0.0099194 | -0.0013631 | 0.024515 | -0.0053776 | 0.018857 | 0.013347 | -21.6273 | -9.545 | -21.8422 | 99.3207 | 99.1661 | 99.1039 | -21.9183 | 0.042256 | 0.004938 | -0.028879 | -0.020797 | 0.004549 | 0.021486 | -0.067994 | -0.014272 | 0.072991 | 0.27673 | 0.061763 | 0.076035 | -0.081614 | -0.14386 | 21.836 | -99.2685 | 21.9462 | 21.8751 | 0.039115 | -99.2432 | -99.2263 | 121.2247 | 121.0701 | 121.0079 | 12.359 | -121.166 | 21.8832 | 21.9085 | 21.9255 | 21.9089 | -99.3157
2726.4375 | 121.3715 | -18.8049 | 102.42 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061821 | -0.0058416 | 0.05476 | 0.0053411 | -0.0013631 | 0.024942 | -0.0051638 | 0.01907 | 0.013133 | -18.4727 | -7.4709 | -18.7061 | 102.4707 | 102.3027 | 102.2219 | -18.7863 | 0.033099 | 0.004938 | -0.033458 | -0.034533 | -0.004608 | 0.030644 | -0.086309 | 0.018652 | 0.05062 | 0.33219 | 0.098825 | 0.080173 | -0.11735 | -0.19814 | 18.7186 | -102.4546 | 18.838 | 18.7715 | 0.052851 | -102.4247 | -102.3894 | 121.2756 | 121.1076 | 121.0268 | 11.3341 | -121.2063 | 18.7704 | 18.8003 | 18.8356 | 18.8099 | -102.5064
2728.1562 | 121.376 | -17.4728 | 103.7109 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061607 | -0.0058416 | 0.054973 | 0.0053411 | -0.0011493 | 0.024729 | -0.0051638 | 0.019284 | 0.013774 | -17.438 | -6.8619 | -17.7355 | 103.4916 | 103.3192 | 103.2429 | -17.7698 | 0.02852 | 0.000359 | -0.033458 | -0.029954 | -2.9e-05 | 0.026065 | -0.08173 | -0.29692 | -0.21929 | 0.034807 | -0.26267 | 0.034246 | -0.39173 | -0.468 | 17.3911 | -103.7409 | 17.5014 | 17.4394 | 0.048272 | -103.711 | -103.6849 | 120.9645 | 120.7921 | 120.7158 | 10.6109 | -121.4807 | 17.4429 | 17.4728 | 17.4989 | 17.4732 | -103.7927
2729.9375 | 121.4355 | -16.8365 | 104.3655 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.0060552 | 0.054546 | -0.01755 | -0.0011493 | 0.024729 | -0.0055912 | 0.019284 | 0.013774 | -16.4399 | -6.2484 | -16.7512 | 104.4714 | 104.2991 | 104.2273 | -16.7899 | 0.033099 | 0.000359 | -0.038036 | -0.034533 | -2.9e-05 | 0.021486 | -0.08173 | 0.046679 | 0.10588 | 0.39661 | 0.085367 | 0.038688 | -0.066438 | -0.1382 | 16.7548 | -104.4001 | 16.8696 | 16.7985 | 0.043694 | -104.3656 | -104.3441 | 121.308 | 121.1356 | 121.0639 | 10.5882 | -121.1554 | 16.802 | 16.8365 | 16.858 | 16.8369 | -104.4473
2731.6562 | 121.3531 | -16.6534 | 104.5761 | 1.4211e-13 | -0.035551 | -0.0022329 | 0.061821 | -0.006269 | 0.05476 | -0.0099194 | -0.0013631 | 0.024515 | -0.0051638 | 0.018643 | 0.013133 | -16.1652 | -6.0927 | -16.4856 | 104.7461 | 104.5738 | 104.5066 | -16.5334 | 0.037677 | 0.004938 | -0.033458 | -0.029954 | -0.009187 | 0.026065 | -0.086309 | 0.11999 | 0.17001 | 0.4882 | 0.1678 | 0.047808 | -0.002273 | -0.069479 | 16.5671 | -104.6061 | 16.6911 | 16.62 | 0.052851 | -104.5853 | -104.55 | 121.3996 | 121.2273 | 121.1601 | 10.5607 | -121.1096 | 16.6235 | 16.6443 | 16.6795 | 16.6584 | -104.6624
2733.4219 | 121.3211 | -14.7446 | 106.5353 | 1.4211e-13 | -0.035124 | -0.0018055 | 0.061821 | -0.0060552 | 0.05476 | -0.0099194 | -0.0013631 | 0.024515 | -0.0051638 | 0.01907 | 0.013347 | -14.2835 | -4.8336 | -14.6314 | 106.6004 | 106.4237 | 106.3472 | -14.6836 | 0.042256 | 0.000359 | -0.038036 | -0.029954 | -0.004608 | 0.026065 | -0.090888 | 0.061005 | 0.065031 | 0.46104 | 0.11313 | 0.052126 | -0.11162 | -0.18811 | 14.6537 | -106.5653 | 14.7868 | 14.7065 | 0.052852 | -106.5399 | -106.5093 | 121.3449 | 121.1683 | 121.0918 | 9.911 | -121.2189 | 14.7146 | 14.74 | 14.7706 | 14.7449 | -106.6262
2735.125 | 121.344 | -10.8627 | 110.4309 | 1.4211e-13 | -0.035337 | -0.0022329 | 0.061607 | -0.0060552 | 0.054546 | -0.0022889 | -0.0011493 | 0.024942 | -0.0051638 | 0.01907 | 0.013133 | -11.7608 | -3.1349 | -12.118 | 109.1047 | 108.9055 | 108.8517 | -12.2018 | 0.037677 | 0.000359 | -0.047194 | -0.039111 | -0.004608 | 0.030644 | -0.086309 | -1.3391 | -1.3262 | -0.8981 | -1.2552 | 0.083825 | -1.5254 | -1.5792 | 10.7764 | -110.47 | 10.9004 | 10.8155 | 0.039115 | -110.4355 | -110.4003 | 119.9675 | 119.7682 | 119.7145 | 7.7278 | -122.6327 | 10.8236 | 10.8581 | 10.8934 | 10.8631 | -110.5172
2736.9062 | 121.3257 | -12.5931 | 108.7372 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.01755 | -0.0013631 | 0.024942 | -0.0049502 | 0.019284 | 0.013133 | -12.1454 | -3.4738 | -12.5208 | 108.6973 | 108.53 | 108.4442 | -12.5956 | 0.033099 | 0.004938 | -0.042615 | -0.029954 | -2.9e-05 | 0.026065 | -0.086309 | -0.002495 | -0.039911 | 0.44766 | 0.072229 | 0.074724 | -0.20716 | -0.29295 | 12.5068 | -108.7671 | 12.6262 | 12.5505 | 0.043694 | -108.7372 | -108.7111 | 121.2904 | 121.1231 | 121.0373 | 9.1193 | -121.3328 | 12.5631 | 12.593 | 12.6191 | 12.598 | -108.8235
2738.6719 | 121.4218 | -11.3388 | 107.6431 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061393 | -0.006269 | 0.05476 | -0.0022889 | -0.0011493 | 0.024729 | -0.0053776 | 0.019284 | 0.013561 | -10.9505 | -2.7 | -11.3259 | 109.9105 | 109.748 | 109.6484 | -11.4829 | 0.033099 | 0.000359 | -0.038036 | -0.034533 | -0.004608 | 0.026065 | -0.090888 | -0.14409 | 2.2674 | 0.38835 | 0.012887 | 0.15698 | 2.1049 | 2.0053 | 11.2479 | -107.6777 | 11.3719 | 11.3008 | 0.052852 | -107.6477 | -107.6171 | 121.2494 | 121.0868 | 120.9872 | 8.6388 | -119.126 | 11.3043 | 11.3342 | 11.3649 | 11.3392 | -107.734
2740.375 | 121.3623 | -10.1028 | 111.1588 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.006269 | 0.05476 | -0.0099194 | -0.0013631 | 0.024942 | -0.0049502 | 0.018857 | 0.013347 | -10.3095 | -2.2879 | -10.7124 | 110.5195 | 110.3387 | 110.2482 | -10.8464 | 0.033099 | -0.008798 | -0.042615 | -0.034533 | -2.9e-05 | 0.021486 | -0.086309 | -0.74358 | -0.63928 | -0.20664 | -0.60959 | 0.134 | -0.82005 | -0.91055 | 10.0165 | -111.1933 | 10.1359 | 10.0602 | 0.043694 | -111.1588 | -111.1373 | 120.6223 | 120.4415 | 120.351 | 7.8149 | -122.0052 | 10.0683 | 10.1028 | 10.1243 | 10.094 | -111.2451
2742.1562 | 121.344 | -9.6634 | 111.6623 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061607 | -0.0064826 | 0.05476 | -0.0022889 | -0.0015767 | 0.024729 | -0.0049502 | 0.01907 | 0.013347 | -9.174 | -1.5187 | -9.5953 | 111.6091 | 111.488 | 111.3883 | -9.7612 | 0.033099 | -0.008798 | -0.047194 | -0.039111 | -0.009187 | 0.021486 | -0.090888 | -0.097828 | -0.053166 | 0.48935 | 0.068062 | 0.16589 | -0.17428 | -0.27402 | 9.5725 | -111.7014 | 9.6965 | 9.6162 | 0.043694 | -111.6715 | -111.6408 | 121.2725 | 121.1514 | 121.0517 | 8.1447 | -121.4235 | 9.6243 | 9.6542 | 9.6849 | 9.6546 | -111.7532
2743.875 | 121.3898 | -9.4116 | 111.8958 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.0099194 | -0.0011493 | 0.024942 | -0.0051638 | 0.01907 | 0.013133 | -8.8169 | -1.3401 | -9.2428 | 111.9662 | 111.8452 | 111.75 | -9.3629 | 0.02852 | -0.00422 | -0.042615 | -0.04369 | -0.004608 | 0.012329 | -0.090888 | 0.048768 | 0.070489 | 0.59469 | 0.16882 | 0.12005 | -0.050582 | -0.14577 | 9.3207 | -111.9394 | 9.4401 | 9.369 | 0.048273 | -111.9004 | -111.8834 | 121.3779 | 121.2568 | 121.1616 | 8.0715 | -121.2586 | 9.3679 | 9.407 | 9.4239 | 9.4074 | -111.9866
2745.6562 | 121.431 | -13.3301 | 107.8766 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.061393 | -0.0060552 | 0.054332 | 0.0053411 | -0.0011493 | 0.024515 | -0.0053776 | 0.01907 | 0.013133 | -10.3141 | -2.3703 | -10.7307 | 110.5103 | 110.3295 | 110.2894 | -10.8968 | 0.02852 | 0.000359 | -0.042615 | -0.039111 | -0.009187 | 0.021486 | -0.090888 | 2.4333 | 2.6337 | 3.016 | 2.5993 | 0.16605 | 2.453 | 2.4128 | 13.2392 | -107.9157 | 13.3586 | 13.2875 | 0.048273 | -107.8858 | -107.8551 | 123.8404 | 123.6596 | 123.6195 | 10.9598 | -118.7734 | 13.291 | 13.3209 | 13.3516 | 13.3304 | -107.9675
2747.4375 | 121.4081 | -11.9888 | 109.2133 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.0058416 | 0.054332 | -0.01755 | -0.0011493 | 0.025156 | -0.0049502 | 0.01907 | 0.013347 | -10.2454 | -2.3703 | -10.6895 | 110.5195 | 110.3387 | 110.2619 | -10.8098 | 0.02852 | -0.008798 | -0.038036 | -0.034533 | -0.009187 | 0.012329 | -0.090888 | 1.179 | 1.3062 | 1.7434 | 1.2993 | 0.12026 | 1.1254 | 1.0487 | 11.8979 | -109.2478 | 12.0174 | 11.9508 | 0.052852 | -109.2224 | -109.2009 | 122.5083 | 122.3275 | 122.2508 | 9.6185 | -120.023 | 11.9543 | 11.9796 | 12.0012 | 11.98 | -109.3041
2749.1562 | 121.3257 | -10.9726 | 110.3806 | 1.4211e-13 | -0.035551 | -0.0015919 | 0.061821 | -0.0060552 | 0.054973 | -0.0099194 | -0.0013631 | 0.024942 | -0.0053776 | 0.019284 | 0.013133 | -10.2179 | -2.3337 | -10.6987 | 110.524 | 110.3387 | 110.2574 | -10.8052 | 0.037677 | 0.004938 | -0.038036 | -0.04369 | -0.013765 | 0.016908 | -0.08173 | 0.16738 | 0.14349 | 0.75468 | 0.2739 | 0.10652 | -0.04185 | -0.1232 | 10.8909 | -110.4242 | 11.0103 | 10.9346 | 0.043694 | -110.3943 | -110.3636 | 121.4966 | 121.3113 | 121.23 | 8.6389 | -121.1858 | 10.9289 | 10.9588 | 10.9895 | 10.9775 | -110.4623
2750.9219 | 121.3531 | -11.6318 | 109.6802 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.061821 | -0.0060552 | 0.054546 | -0.0022889 | -0.0013631 | 0.024942 | -0.0049502 | 0.01907 | 0.013133 | -11.2297 | -3.0159 | -11.7059 | 109.526 | 109.3359 | 109.2638 | -11.8217 | 0.033099 | 0.004938 | -0.038036 | -0.034533 | -0.009187 | 0.021486 | -0.090888 | -0.18996 | -0.15422 | 0.40204 | -0.074141 | 0.11582 | -0.34426 | -0.41638 | 11.5409 | -109.7147 | 11.6649 | 11.5937 | 0.052852 | -109.6894 | -109.6587 | 121.1577 | 120.9677 | 120.8956 | 8.6159 | -121.5019 | 11.5972 | 11.6226 | 11.6533 | 11.6367 | -109.7711
2752.6406 | 121.4767 | -9.1782 | 112.0377 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.06118 | -0.0064826 | 0.05476 | -0.0022889 | -0.0011493 | 0.024515 | -0.0051638 | 0.01907 | 0.013347 | -10.456 | -2.526 | -10.9459 | 110.2997 | 110.1281 | 110.0651 | -11.1212 | 0.033099 | 0.004938 | -0.042615 | -0.04369 | -0.013765 | 0.021486 | -0.090888 | -1.943 | -1.738 | -1.2778 | -1.7678 | 0.17524 | -1.9096 | -1.9726 | 9.0873 | -112.0813 | 9.2113 | 9.1355 | 0.048273 | -112.0514 | -112.0162 | 119.4779 | 119.3062 | 119.2432 | 6.6522 | -123.1588 | 9.1345 | 9.1644 | 9.1996 | 9.1831 | -112.1285
2754.4219 | 121.4264 | -11.3937 | 109.8358 | 1.4211e-13 | -0.035337 | -0.0020193 | 0.062034 | -0.006269 | 0.054332 | -0.01755 | -0.0015767 | 0.024942 | -0.0051638 | 0.019284 | 0.013347 | -10.7627 | -2.7366 | -11.2847 | 109.9334 | 109.7618 | 109.6759 | -11.3913 | 0.02852 | -0.00422 | -0.047194 | -0.029954 | -0.004608 | 0.021486 | -0.086309 | 0.002421 | 0.097621 | 0.631 | 0.10902 | 0.1066 | -0.074056 | -0.15994 | 11.3074 | -109.8658 | 11.4223 | 11.3465 | 0.039115 | -109.8404 | -109.8143 | 121.3272 | 121.1555 | 121.0696 | 8.6571 | -121.2271 | 11.3638 | 11.3891 | 11.4152 | 11.3895 | -109.9221
2756.1406 | 121.4676 | -12.735 | 108.4534 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061607 | -0.0060552 | 0.054546 | -0.0099194 | -0.0011493 | 0.024515 | -0.0053776 | 0.019284 | 0.013347 | -12.0722 | -3.634 | -12.5941 | 108.6149 | 108.4385 | 108.3481 | -12.6963 | 0.037677 | 0.000359 | -0.038036 | -0.039111 | -0.009187 | 0.016908 | -0.10004 | 0.038675 | 0.16149 | 0.66282 | 0.14088 | 0.10221 | -0.014919 | -0.10529 | 12.6349 | -108.4925 | 12.7727 | 12.6969 | 0.062009 | -108.4626 | -108.4365 | 121.3498 | 121.1734 | 121.0831 | 9.101 | -121.1497 | 12.6959 | 12.7258 | 12.7519 | 12.7353 | -108.5534
2757.9375 | 121.3623 | -12.5885 | 108.6777 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.0060552 | 0.05476 | -0.0022889 | -0.0011493 | 0.024729 | -0.0053776 | 0.019498 | 0.013133 | -11.9898 | -3.5974 | -12.4888 | 108.6744 | 108.5117 | 108.4213 | -12.6185 | 0.033099 | -0.00422 | -0.042615 | -0.039111 | -0.009187 | 0.026065 | -0.086309 | -0.029967 | -0.003293 | 0.59875 | 0.099699 | 0.12967 | -0.16596 | -0.25634 | 12.5022 | -108.7168 | 12.6216 | 12.5459 | 0.043694 | -108.6869 | -108.6516 | 121.2629 | 121.1002 | 121.0098 | 8.9911 | -121.2961 | 12.5494 | 12.5793 | 12.6146 | 12.5843 | -108.764
2759.6562 | 121.4447 | -12.5015 | 108.6731 | 1.4211e-13 | -0.035124 | -0.0020193 | 0.061607 | -0.0060552 | 0.054119 | -0.0022889 | -0.0013631 | 0.024729 | -0.0051638 | 0.019498 | 0.013347 | -12.0493 | -3.6432 | -12.5804 | 108.5737 | 108.4018 | 108.3206 | -12.7192 | 0.02852 | 0.000359 | -0.042615 | -0.029954 | -0.004608 | 0.021486 | -0.086309 | -0.21768 | -0.099441 | 0.45226 | -0.078842 | 0.13884 | -0.27128 | -0.35249 | 12.4152 | -108.7031 | 12.53 | 12.4589 | 0.043694 | -108.6777 | -108.6516 | 121.0752 | 120.9033 | 120.8221 | 8.8584 | -121.3923 | 12.4716 | 12.4969 | 12.523 | 12.5019 | -108.7594
2761.4219 | 121.4767 | -8.9676 | 111.7813 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.006269 | 0.05476 | 0.0053411 | -0.00093566 | 0.024729 | -0.0051638 | 0.01907 | 0.013561 | -6.4728 | 0.047193 | -7.0498 | 114.1684 | 113.9927 | 113.8882 | -7.3435 | 0.02852 | 0.004938 | -0.042615 | -0.034533 | -0.009187 | 0.026065 | -0.095467 | 1.624 | 2.3871 | 2.4948 | 1.9178 | 0.29374 | 2.2114 | 2.1069 | 8.8721 | -111.8158 | 8.9961 | 8.925 | 0.052852 | -111.7905 | -111.7552 | 123.136 | 122.9603 | 122.8558 | 9.0148 | -119.1249 | 8.9331 | 8.9584 | 8.9937 | 8.9725 | -111.8768
2763.1875 | 121.3303 | -6.3171 | 115.1459 | 1.4211e-13 | -0.035765 | -0.0015919 | 0.061821 | -0.0064826 | 0.054332 | -0.0022889 | -0.0011493 | 0.024515 | -0.0049502 | 0.01907 | 0.01292 | -7.4114 | -0.63044 | -8.0158 | 113.1932 | 113.0128 | 112.9221 | -8.2181 | 0.02852 | -0.008798 | -0.047194 | -0.04369 | -0.013765 | 0.016908 | -0.090888 | -1.901 | -1.9526 | -1.0942 | -1.6987 | 0.2023 | -2.1331 | -2.2238 | 6.2263 | -115.1896 | 6.3457 | 6.2699 | 0.043694 | -115.1596 | -115.129 | 119.5104 | 119.3299 | 119.2392 | 5.6867 | -123.364 | 6.2734 | 6.3034 | 6.334 | 6.3083 | -115.2368
2764.8906 | 121.5225 | -4.8614 | 113.3881 | 1.4211e-13 | -0.035337 | -0.0015919 | 0.061821 | -0.006269 | 0.054546 | -0.0022889 | -0.0013631 | 0.024729 | -0.0053776 | 0.019284 | 0.013133 | -7.0634 | -0.45188 | -7.6725 | 113.5733 | 113.3791 | 113.3021 | -7.9159 | 0.023941 | -0.00422 | -0.042615 | -0.04369 | -2.9e-05 | 0.021486 | -0.090888 | -3.0545 | 0.18519 | -2.202 | -2.811 | 0.24346 | -0.008952 | -0.085935 | 4.7706 | -113.4318 | 4.8854 | 4.8188 | 0.048273 | -113.3881 | -113.3666 | 118.4347 | 118.2406 | 118.1636 | 4.4096 | -121.304 | 4.8178 | 4.8614 | 4.8829 | 4.8572 | -113.479
2766.6719 | 121.3806 | -18.1274 | 103.1525 | 1.4211e-13 | -0.035551 | -0.0018055 | 0.061607 | -0.006269 | 0.054546 | -0.0099194 | -0.0017903 | 0.024515 | -0.0053776 | 0.01907 | 0.013133 | -13.5372 | -4.7695 | -14.1416 | 107.0719 | 106.9091 | 106.8234 | -14.3127 | 0.033099 | 0.000359 | -0.038036 | -0.039111 | -0.004608 | 0.021486 | -0.086309 | 3.8148 | 3.9195 | 4.5902 | 3.9859 | 0.17111 | 3.7566 | 3.6709 | 18.0411 | -103.1916 | 18.1605 | 18.0894 | 0.048273 | -103.1571 | -103.131 | 125.1994 | 125.0365 | 124.9508 | 13.3579 | -117.4651 | 18.0883 | 18.1228 | 18.1489 | 18.1278 | -103.2388
2768.4375 | 121.3028 | -15.5228 | 105.8624 | 1.4211e-13 | -0.035124 | -0.0018055 | 0.061821 | -0.0058416 | 0.05476 | -0.0022889 | -0.0015767 | 0.024942 | -0.0051638 | 0.018857 | 0.013133 | -13.1252 | -4.5177 | -13.7616 | 107.4748 | 107.3075 | 107.2355 | -13.9326 | 0.033099 | 0.004938 | -0.038036 | -0.039111 | -2.9e-05 | 0.021486 | -0.090888 | 1.5901 | 1.6124 | 2.3976 | 1.7612 | 0.17106 | 1.445 | 1.3731 | 15.4319 | -105.9015 | 15.5559 | 15.4847 | 0.052852 | -105.8625 | -105.8409 | 122.9976 | 122.8302 | 122.7582 | 11.0051 | -119.795 | 15.4837 | 15.5227 | 15.5443 | 15.5277 | -105.9533
2770.1562 | 121.3898 | -9.6039 | 111.5662 | 1.4211e-13 | -0.035551 | -0.0018055 | 0.061607 | -0.0060552 | 0.054546 | -0.0022889 | -0.0013631 | 0.024942 | -0.0049502 | 0.018857 | 0.012706 | -14.1965 | -5.2823 | -14.8649 | 106.3302 | 106.1994 | 106.0496 | -14.9949 | 0.037677 | 0.000359 | -0.042615 | -0.039111 | -0.009187 | 0.026065 | -0.08173 | -5.391 | -5.2359 | -4.5927 | -5.261 | 0.13 | -5.3668 | -5.5165 | 9.5222 | -111.6053 | 9.6416 | 9.5613 | 0.039115 | -111.5753 | -111.5401 | 115.9341 | 115.8032 | 115.6535 | 4.3216 | -126.5611 | 9.5648 | 9.5947 | 9.6299 | 9.6042 | -111.6479
2771.9375 | 121.4081 | -20.5765 | 100.5615 | 1.4211e-13 | -0.035765 | -0.0018055 | 0.061821 | -0.0058416 | 0.054546 | -0.0099194 | -0.0013631 | 0.024515 | -0.0051638 | 0.01907 | 0.012706 | -22.1767 | -10.6438 | -22.8037 | 98.3089 | 98.2091 | 98.0966 | -22.976 | 0.033099 | 0.014095 | -0.038036 | -0.029954 | -0.004608 | 0.026065 | -0.08173 | -2.3995 | -2.2526 | -1.6002 | -2.2272 | 0.17233 | -2.3524 | -2.4649 | 20.4947 | -100.5915 | 20.6096 | 20.5384 | 0.043694 | -100.5661 | -100.5355 | 118.8854 | 118.7856 | 118.6731 | 9.9326 | -123.5375 | 20.5465 | 20.5719 | 20.6025 | 20.5906 | -100.6433
2773.6562 | 121.3394 | -25.4288 | 95.7504 | 1.4211e-13 | -0.035337 | -0.0018055 | 0.061821 | -0.0060552 | 0.054546 | -0.0099194 | -0.0011493 | 0.024515 | -0.0051638 | 0.019284 | 0.013133 | -23.0099 | -11.2848 | -23.5911 | 97.4802 | 97.3254 | 97.2816 | -23.8414 | 0.037677 | 0.000359 | -0.033458 | -0.029954 | -0.004608 | 0.030644 | -0.08173 | 1.5874 | 1.7298 | 2.4188 | 1.8376 | 0.25028 | 1.575 | 1.5312 | 25.347 | -95.7804 | 25.4664 | 25.3953 | 0.048272 | -95.755 | -95.7198 | 122.909 | 122.7542 | 122.7104 | 14.1439 | -119.5918 | 25.3988 | 25.4242 | 25.4594 | 25.4291 | -95.8322
2775.4062 | 121.3898 | -29.6631 | 91.2323 | 1.4211e-13 | -0.035765 | -0.0020193 | 0.061607 | -0.0060552 | 0.05476 | -0.0022889 | -0.0013631 | 0.024515 | -0.0053776 | 0.01907 | 0.013133 | -27.7302 | -14.5265 | -28.3434 | 92.6638 | 92.5267 | 92.4695 | -28.5852 | 0.042256 | 0.009516 | -0.028879 | -0.020797 | -2.9e-05 | 0.035222 | -0.08173 | 1.0779 | 1.4315 | 1.9328 | 1.3197 | 0.24179 | 1.2944 | 1.2372 | 29.5814 | -91.2531 | 29.7053 | 29.6342 | 0.052851 | -91.2323 | -91.1971 | 122.3268 | 122.1898 | 122.1326 | 15.1366 | -119.8175 | 29.6423 | 29.6631 | 29.6983 | 29.6726 | -91.314
2777.1406 | 121.3303 | -36.026 | 84.9792 | 1.4211e-13 | -0.035765 | -0.0020193 | 0.061607 | -0.0058416 | 0.05476 | -0.01755 | -0.0015767 | 0.024729 | -0.0053776 | 0.019284 | 0.013347 | -34.7398 | -19.2379 | -35.3344 | 85.5489 | 85.4202 | 85.3727 | -35.6688 | 0.046835 | 0.018674 | -0.0243 | -0.025376 | 0.009128 | 0.035222 | -0.067994 | 0.35723 | 0.56969 | 1.2862 | 0.69158 | 0.33435 | 0.44095 | 0.3934 | 35.958 | -85.0046 | 36.0728 | 36.0017 | 0.043694 | -84.9701 | -84.944 | 121.5749 | 121.4462 | 121.3987 | 16.7881 | -120.648 | 36.0006 | 36.0351 | 36.0612 | 36.0447 | -85.0472
2778.9062 | 121.3531 | -34.8907 | 86.1099 | 1.4211e-13 | -0.035551 | -0.0015919 | 0.061821 | -0.0060552 | 0.055187 | -0.0099194 | -0.00093566 | 0.024729 | -0.0051638 | 0.018857 | 0.013133 | -29.0717 | -15.4239 | -29.6528 | 91.3406 | 91.1118 | 91.1921 | -30.0459 | 0.042256 | 0.014095 | -0.028879 | -0.020797 | 0.004549 | 0.035222 | -0.072572 | 4.8449 | 5.2307 | 5.819 | 5.238 | 0.39308 | 5.0019 | 5.0821 | 34.8182 | -86.1307 | 34.933 | 34.8619 | 0.043693 | -86.1054 | -86.0747 | 126.2313 | 126.0025 | 126.0828 | 19.4668 | -116.1558 | 34.8699 | 34.8953 | 34.926 | 34.9048 | -86.1825
2780.6719 | 121.2341 | -32.515 | 88.5635 | 1.4211e-13 | -0.035765 | -0.0020193 | 0.061607 | -0.0054142 | 0.05476 | -0.0099194 | -0.0013631 | 0.024515 | -0.0053776 | 0.01907 | 0.013347 | -28.4216 | -15.0027 | -29.0622 | 91.9083 | 91.7208 | 91.7461 | -29.3956 | 0.042256 | 0.009516 | -0.0243 | -0.025376 | 0.009128 | 0.039801 | -0.077151 | 3.1193 | 3.3448 | 4.0934 | 3.4528 | 0.33347 | 3.1573 | 3.1825 | 32.4378 | -88.5889 | 32.5572 | 32.4907 | 0.052851 | -88.5544 | -88.5237 | 124.4233 | 124.2358 | 124.261 | 17.5123 | -117.9592 | 32.4896 | 32.5241 | 32.5548 | 32.5245 | -88.6407
2782.4375 | 121.1334 | -29.7913 | 91.3239 | 1.4211e-13 | -0.035978 | -0.0015919 | 0.061393 | -0.0058416 | 0.05476 | -0.0022889 | -0.0015767 | 0.024729 | -0.0051638 | 0.01907 | 0.013133 | -34.7031 | -19.2013 | -35.4123 | 85.3887 | 85.3011 | 85.1941 | -35.71 | 0.042256 | 0.014095 | -0.0243 | -0.020797 | -2.9e-05 | 0.035222 | -0.072572 | -5.9187 | -5.9352 | -4.9119 | -5.621 | 0.29773 | -6.0227 | -6.1298 | 29.7187 | -91.3447 | 29.8335 | 29.767 | 0.048272 | -91.3239 | -91.2886 | 115.18 | 115.0924 | 114.9853 | 10.59 | -127.0338 | 29.7705 | 29.7912 | 29.8265 | 29.8054 | -91.3964
2784.1562 | 121.2524 | -45.1538 | 75.769 | 1.4211e-13 | -0.035551 | -0.0020193 | 0.061393 | -0.0060552 | 0.055401 | -0.0022889 | -0.0015767 | 0.024515 | -0.0051638 | 0.01907 | 0.013347 | -43.631 | -25.0985 | -44.2392 | 76.3693 | 76.2349 | 76.2246 | -44.7717 | 0.060571 | 0.023253 | -0.019721 | -0.016219 | 0.013707 | 0.048958 | -0.072572 | 0.38213 | 0.60023 | 1.5228 | 0.91463 | 0.5325 | 0.46583 | 0.45556 | 45.0812 | -75.7853 | 45.2144 | 45.1341 | 0.052851 | -75.7553 | -75.7201 | 121.5231 | 121.3887 | 121.3784 | 20.0553 | -120.5407 | 45.1376 | 45.1675 | 45.2028 | 45.1771 | -75.8416
2785.9375 | 121.1334 | -45.3873 | 75.531 | 1.4211e-13 | -0.035978 | -0.0020193 | 0.061607 | -0.005628 | 0.054973 | -0.0099194 | -0.0011493 | 0.024515 | -0.0051638 | 0.019284 | 0.013133 | -43.2144 | -24.865 | -43.9095 | 76.7127 | 76.592 | 76.5588 | -44.3962 | 0.060571 | 0.014095 | -0.010564 | -0.016219 | 0.018285 | 0.044379 | -0.063415 | 0.99106 | 1.1816 | 2.1729 | 1.4777 | 0.48666 | 1.061 | 1.0278 | 45.3239 | -75.5472 | 45.4478 | 45.3767 | 0.052851 | -75.5127 | -75.4866 | 122.0999 | 121.9793 | 121.9461 | 20.5223 | -119.9272 | 45.371 | 45.4056 | 45.4316 | 45.4014 | -75.5944
2787.7188 | 120.8908 | -20.4941 | 102.0905 | 1.4211e-13 | -0.035551 | -0.0015919 | 0.061607 | -0.005628 | 0.05476 | -0.0099194 | -0.0013631 | 0.024942 | -0.0051638 | 0.019284 | 0.013133 | -24.8733 | -12.6264 | -25.6834 | 95.2139 | 95.0817 | 94.9923 | -25.9111 | 0.037677 | 0.009516 | -0.028879 | -0.034533 | -2.9e-05 | 0.030644 | -0.072572 | -5.417 | -6.8765 | -4.3793 | -5.1893 | 0.22768 | -7.0087 | -7.0982 | 20.4215 | -102.125 | 20.5318 | 20.4652 | 0.043693 | -102.0905 | -102.0598 | 115.708 | 115.5758 | 115.4864 | 7.8677 | -128.0015 | 20.4595 | 20.4941 | 20.5247 | 20.5036 | -102.163
2789.4844 | 121.2067 | -13.5086 | 108.2565 | 1.4211e-13 | -0.035124 | -0.0018055 | 0.062034 | -0.0058416 | 0.054546 | -0.0099194 | -0.0011493 | 0.024515 | -0.0049502 | 0.019284 | 0.012492 | -17.3007 | -7.5945 | -18.2117 | 102.7774 | 102.6507 | 102.5195 | -18.3788 | 0.033099 | 0.000359 | -0.038036 | -0.039111 | -0.004608 | 0.026065 | -0.086309 | -4.8701 | -5.4791 | -3.7921 | -4.703 | 0.1671 | -5.6058 | -5.737 | 13.4223 | -108.2956 | 13.5417 | 13.4706 | 0.048273 | -108.2611 | -108.2305 | 116.286 | 116.1593 | 116.0281 | 5.9141 | -126.6353 | 13.4695 | 13.504 | 13.5347 | 13.509 | -108.3428
2791.2031 | 121.1655 | -37.2757 | 83.7616 | 1.4211e-13 | -0.035765 | -0.0018055 | 0.061393 | -0.0058416 | 0.055187 | -0.0099194 | -0.00093566 | 0.024729 | -0.0053776 | 0.019284 | 0.013347 | -33.9294 | -18.661 | -34.7392 | 86.0251 | 85.8827 | 85.8351 | -35.1056 | 0.046835 | 0.023253 | -0.0243 | -0.016219 | 0.013707 | 0.035222 | -0.077151 | 2.1701 | 2.2635 | 3.3463 | 2.5365 | 0.36632 | 2.1211 | 2.0735 | 37.1985 | -83.7778 | 37.3225 | 37.2514 | 0.052851 | -83.7479 | -83.7264 | 123.3008 | 123.1584 | 123.1108 | 18.6147 | -118.8672 | 37.2595 | 37.2894 | 37.3109 | 37.2989 | -83.8387
2792.9844 | 121.1746 | -44.87 | 75.9384 | 1.4211e-13 | -0.035551 | -0.0018055 | 0.061393 | -0.006269 | 0.055187 | -0.0099194 | -0.0013631 | 0.024729 | -0.0051638 | 0.019498 | 0.013133 | -41.5616 | -23.7478 | -42.3209 | 78.283 | 78.1122 | 78.1659 | -42.8897 | 0.051413 | 0.027831 | -0.019721 | -0.01164 | 0.018285 | 0.044379 | -0.063415 | 1.9803 | 2.3446 | 3.3084 | 2.5491 | 0.56886 | 2.1738 | 2.2275 | 44.8066 | -75.9501 | 44.9214 | 44.8503 | 0.043694 | -75.9201 | -75.894 | 123.153 | 122.9822 | 123.0359 | 21.1222 | -118.8282 | 44.8584 | 44.8883 | 44.9144 | 44.8978 | -76.0018
2794.75 | 121.138 | -48.4955 | 72.2809 | 1.4211e-13 | -0.035765 | -0.0015919 | 0.06118 | -0.005628 | 0.055187 | -0.0099194 | -0.0015767 | 0.024729 | -0.0051638 | 0.018643 | 0.013347 | -46.6756 | -27.1131 | -47.444 | 72.9813 | 72.8648 | 72.8548 | -48.041 | 0.055992 | 0.023253 | -0.015143 | -0.01164 | 0.022864 | 0.044379 | -0.058836 | 0.45445 | 0.70038 | 1.8199 | 1.0515 | 0.59706 | 0.5839 | 0.57387 | 48.4366 | -72.2925 | 48.5515 | 48.4803 | 0.043693 | -72.258 | -72.2365 | 121.4768 | 121.3603 | 121.3502 | 21.3824 | -120.3219 | 48.4838 | 48.5183 | 48.5399 | 48.5187 | -72.3397
2796.5156 | 121.2112 | -110.1791 | 10.8124 | 1.4211e-13 | -0.036833 | -0.0024467 | 0.060966 | -0.0052006 | 0.056255 | -0.0022889 | -0.0013631 | 0.024301 | -0.0053776 | 0.01907 | 0.01292 | -108.3282 | -67.6246 | -109.1684 | 10.5595 | 10.5365 | 10.6178 | -110.5296 | 0.10636 | 0.06904 | 0.030644 | 0.038723 | 0.077807 | 0.094744 | -0.017627 | -0.35047 | -0.25285 | 1.8509 | 1.0108 | 1.3613 | -0.27591 | -0.19457 | 110.1615 | -10.7737 | 110.2855 | 110.2098 | 0.048271 | -10.7346 | -10.7176 | 120.7387 | 120.7156 | 120.7969 | 42.5546 | -121.342 | 110.2179 | 110.2569 | 110.2739 | 110.2482 | -10.83
2798.25 | 121.1655 | -91.7084 | 29.3243 | 1.4211e-13 | -0.036406 | -0.0022329 | 0.060966 | -0.0054142 | 0.056255 | -0.0099194 | -0.0011493 | 0.024515 | -0.0051638 | 0.019284 | 0.013347 | -89.9276 | -55.4729 | -90.7499 | 29.1295 | 29.1223 | 29.1703 | -91.8888 | 0.088043 | 0.059882 | 0.021487 | 0.020409 | 0.059493 | 0.07643 | -0.026784 | -0.18044 | -0.19487 | 1.7807 | 0.95844 | 1.1389 | -0.20202 | -0.15404 | 91.6816 | -29.3039 | 91.7964 | 91.7299 | 0.048271 | -29.2648 | -29.2479 | 120.8378 | 120.8307 | 120.8787 | 36.2354 | -121.2132 | 91.7288 | 91.7679 | 91.7848 | 91.7683 | -29.3511
2800.0312 | 121.1517 | -89.7217 | 31.3293 | 1.4211e-13 | -0.036619 | -0.0022329 | 0.060966 | -0.005628 | 0.056042 | -0.0022889 | -0.0013631 | 0.024515 | -0.0051638 | 0.01907 | 0.013133 | -87.9086 | -53.9941 | -88.7675 | 31.1165 | 31.1096 | 31.1528 | -89.8924 | 0.097201 | 0.046146 | 0.007751 | 0.020409 | 0.045757 | 0.081008 | -0.031363 | -0.17072 | -0.21286 | 1.8131 | 0.95415 | 1.1249 | -0.21977 | -0.17651 | 89.6903 | -31.3089 | 89.8189 | 89.7294 | 0.039114 | -31.2836 | -31.2483 | 120.8382 | 120.8313 | 120.8745 | 35.7276 | -121.2217 | 89.7421 | 89.7674 | 89.8027 | 89.7678 | -31.3607
2801.75 | 121.106 | -85.9085 | 35.1013 | 1.4211e-13 | -0.036406 | -0.0022329 | 0.06118 | -0.0054142 | 0.055828 | -0.0099194 | -0.0013631 | 0.024729 | -0.0053776 | 0.019498 | 0.013133 | -84.2413 | -51.572 | -85.1278 | 34.7884 | 34.7956 | 34.8203 | -86.2201 | 0.097201 | 0.050725 | 0.007751 | 0.015831 | 0.045757 | 0.07643 | -0.031363 | -0.31159 | -0.31296 | 1.6672 | 0.78071 | 1.0923 | -0.30571 | -0.28102 | 85.8771 | -35.0855 | 86.0057 | 85.9163 | 0.039114 | -35.0556 | -35.0249 | 120.6969 | 120.7041 | 120.7288 | 34.3365 | -121.3214 | 85.9243 | 85.9543 | 85.9849 | 85.9592 | -35.1327
2803.5156 | 121.138 | -98.6938 | 22.2336 | 1.4211e-13 | -0.036406 | -0.0024467 | 0.060966 | -0.0052006 | 0.056255 | -0.0022889 | -0.0013631 | 0.024729 | -0.0051638 | 0.018857 | 0.01292 | -97.3858 | -60.1294 | -98.3316 | 21.4195 | 21.416 | 21.437 | -99.5951 | 0.097201 | 0.059882 | 0.021487 | 0.024988 | 0.064071 | 0.07643 | -0.026784 | -0.90129 | -0.81412 | 1.308 | 0.36229 | 1.2636 | -0.81759 | -0.79654 | 98.6671 | -22.2086 | 98.791 | 98.7153 | 0.048271 | -22.1695 | -22.1572 | 120.1133 | 120.1098 | 120.1309 | 38.5645 | -121.8287 | 98.7188 | 98.7579 | 98.7703 | 98.7537 | -22.2604
2805.2344 | 121.1609 | -98.1216 | 22.8287 | 1.4211e-13 | -0.036619 | -0.0022329 | 0.060539 | -0.0054142 | 0.056255 | -0.0022889 | -0.0011493 | 0.024301 | -0.0053776 | 0.01907 | 0.01292 | -96.0993 | -59.1496 | -97.0542 | 22.6831 | 22.6752 | 22.7145 | -98.3497 | 0.10178 | 0.055303 | 0.021487 | 0.024988 | 0.050335 | 0.085587 | -0.017627 | -0.22803 | -0.14558 | 2.0223 | 1.0674 | 1.2955 | -0.15348 | -0.1142 | 98.104 | -22.8037 | 98.2234 | 98.1431 | 0.039114 | -22.7783 | -22.7431 | 120.8047 | 120.7968 | 120.8361 | 38.9721 | -121.1783 | 98.1466 | 98.172 | 98.2072 | 98.1769 | -22.8463
2807.0156 | 121.2433 | -96.0114 | 24.9252 | 1.4211e-13 | -0.036619 | -0.0022329 | 0.060966 | -0.0054142 | 0.056683 | -0.0099194 | -0.0011493 | 0.024515 | -0.0053776 | 0.019498 | 0.013133 | -92.3267 | -56.5489 | -93.3 | 26.4832 | 26.4574 | 26.4964 | -94.5629 | 0.092622 | 0.046146 | 0.016908 | 0.020409 | 0.050335 | 0.07643 | -0.026784 | 1.4485 | 1.5579 | 3.6846 | 2.7113 | 1.2629 | 1.5322 | 1.5712 | 95.9846 | -24.9048 | 96.104 | 96.0283 | 0.043692 | -24.8749 | -24.8488 | 122.4945 | 122.4687 | 122.5078 | 39.4624 | -119.4881 | 96.0318 | 96.0617 | 96.0878 | 96.0575 | -24.952
2808.7969 | 121.2524 | -99.9252 | 20.9427 | 1.4211e-13 | -0.036619 | -0.0024467 | 0.060539 | -0.005628 | 0.056683 | 0.0053411 | -0.0011493 | 0.024515 | -0.0055912 | 0.01907 | 0.013133 | -96.2779 | -59.0351 | -97.2694 | 22.4313 | 22.3867 | 22.4535 | -98.6107 | 0.097201 | 0.064461 | 0.016908 | 0.024988 | 0.054914 | 0.081008 | -0.022205 | 1.3146 | 1.4886 | 3.6474 | 2.6558 | 1.3413 | 1.444 | 1.5108 | 99.903 | -20.9177 | 100.0224 | 99.9421 | 0.039113 | -20.8878 | -20.8617 | 122.3565 | 122.312 | 122.3787 | 40.8901 | -119.5534 | 99.9502 | 99.9801 | 100.0062 | 99.9897 | -20.9649
2810.5625 | 121.1609 | -98.4558 | 22.5174 | 1.4211e-13 | -0.036406 | -0.0022329 | 0.060752 | -0.005628 | 0.056469 | -0.0099194 | -0.0011493 | 0.024515 | -0.0051638 | 0.019498 | 0.013133 | -95.9345 | -58.6413 | -96.9627 | 22.7014 | 22.6798 | 22.7419 | -98.313 | 0.092622 | 0.059882 | 0.016908 | 0.020409 | 0.050335 | 0.081008 | -0.013048 | 0.14277 | 0.18402 | 2.5213 | 1.4932 | 1.3504 | 0.16238 | 0.22455 | 98.4428 | -22.497 | 98.5484 | 98.4727 | 0.029956 | -22.4671 | -22.4364 | 121.1572 | 121.1356 | 121.1978 | 39.8145 | -120.8304 | 98.4762 | 98.5061 | 98.5368 | 98.5157 | -22.5304
2812.3438 | 121.2387 | -100.296 | 20.5627 | 1.4211e-13 | -0.036619 | -0.0024467 | 0.060539 | -0.0054142 | 0.056469 | -0.0022889 | -0.0011493 | 0.024301 | -0.0051638 | 0.01907 | 0.013133 | -97.9765 | -59.8364 | -99.0229 | 20.5496 | 20.5506 | 20.6175 | -100.3781 | 0.10636 | 0.059882 | 0.021487 | 0.029566 | 0.064071 | 0.085587 | -0.017627 | -0.082115 | -0.013174 | 2.3196 | 1.2731 | 1.3553 | -0.012172 | 0.054732 | 100.2784 | -20.5332 | 100.4024 | 100.3175 | 0.039114 | -20.4987 | -20.4772 | 120.8456 | 120.8466 | 120.9135 | 40.4597 | -120.9409 | 100.3256 | 100.3601 | 100.3816 | 100.3559 | -20.5804
2814.0625 | 121.1288 | -100.8545 | 20.0729 | 1.4211e-13 | -0.037047 | -0.0026603 | 0.060966 | -0.0054142 | 0.056896 | -0.0022889 | -0.0013631 | 0.024515 | -0.0053776 | 0.01907 | 0.013347 | -98.4801 | -60.1477 | -99.5448 | 20.0047 | 20.0103 | 20.0726 | -100.9184 | 0.097201 | 0.064461 | 0.016908 | 0.029566 | 0.059493 | 0.07643 | -0.017627 | -0.063957 | -0.068195 | 2.3744 | 1.3097 | 1.3736 | -0.062678 | -0.000314 | 100.8369 | -20.0434 | 100.9517 | 100.8714 | 0.034535 | -20.0134 | -19.9965 | 120.8592 | 120.8648 | 120.9271 | 40.7068 | -120.9914 | 100.8841 | 100.914 | 100.9309 | 100.919 | -20.0906
2815.8438 | 121.1563 | -86.6501 | 34.2773 | 1.4211e-13 | -0.036619 | -0.0020193 | 0.060539 | -0.0052006 | 0.056255 | -0.0099194 | -0.0013631 | 0.024515 | -0.0053776 | 0.01907 | 0.013347 | -83.8888 | -50.6471 | -84.9035 | 34.8021 | 34.7361 | 34.7837 | -86.1194 | 0.092622 | 0.050725 | 0.007751 | 0.020409 | 0.045757 | 0.071851 | -0.035942 | 0.53072 | 0.52475 | 2.7613 | 1.7466 | 1.2159 | 0.45874 | 0.50633 | 86.6141 | -34.2569 | 86.7427 | 86.6578 | 0.043693 | -34.2316 | -34.2055 | 121.4522 | 121.3862 | 121.4338 | 36.003 | -120.3967 | 86.6705 | 86.6958 | 86.7219 | 86.7008 | -34.3133
2817.625 | 121.1334 | -93.3426 | 27.5757 | 1.4211e-13 | -0.036619 | -0.0020193 | 0.060966 | -0.0054142 | 0.056469 | -0.0022889 | -0.0013631 | 0.024301 | -0.0051638 | 0.019284 | 0.013133 | -89.5293 | -54.2047 | -90.576 | 29.0791 | 28.9895 | 29.0833 | -91.9667 | 0.092622 | 0.055303 | 0.016908 | 0.020409 | 0.041178 | 0.07643 | -0.022205 | 1.3759 | 1.5034 | 3.8133 | 2.7666 | 1.3907 | 1.4138 | 1.5076 | 93.3204 | -27.5553 | 93.4352 | 93.3595 | 0.039113 | -27.5345 | -27.4993 | 122.4217 | 122.3321 | 122.4259 | 39.1379 | -119.5423 | 93.363 | 93.3838 | 93.419 | 93.3979 | -27.5979
2819.3281 | 121.1014 | -90.4266 | 30.5374 | 1.4211e-13 | -0.036619 | -0.0018055 | 0.060966 | -0.0054142 | 0.056683 | -0.01755 | -0.0015767 | 0.024729 | -0.0053776 | 0.019284 | 0.013133 | -88.6777 | -53.5453 | -89.7519 | 29.8529 | 29.8137 | 29.8479 | -91.0554 | 0.097201 | 0.059882 | 0.01233 | 0.015831 | 0.041178 | 0.081008 | -0.031363 | -0.62881 | -0.68456 | 1.7489 | 0.67477 | 1.3036 | -0.72368 | -0.68948 | 90.3953 | -30.5216 | 90.5238 | 90.439 | 0.043693 | -30.4962 | -30.4564 | 120.2795 | 120.2404 | 120.2746 | 36.8813 | -121.5929 | 90.4425 | 90.4678 | 90.5076 | 90.4865 | -30.5688
2821.1094 | 121.2112 | -88.8748 | 32.0114 | 1.4211e-13 | -0.036406 | -0.0020193 | 0.060966 | -0.004987 | 0.056255 | -0.01755 | -0.0013631 | 0.024515 | -0.0053776 | 0.019498 | 0.013133 | -86.2237 | -51.8925 | -87.3071 | 32.3206 | 32.2497 | 32.3066 | -88.6011 | 0.083464 | 0.050725 | 0.016908 | 0.015831 | 0.045757 | 0.07643 | -0.031363 | 0.27367 | 0.30919 | 2.6511 | 1.5678 | 1.2941 | 0.23831 | 0.29523 | 88.8435 | -31.9956 | 88.9583 | 88.8917 | 0.048271 | -31.9657 | -31.935 | 121.1954 | 121.1245 | 121.1815 | 36.9823 | -120.6126 | 88.8906 | 88.9206 | 88.9512 | 88.9255 | -32.0428
2822.9062 | 121.2387 | -101.1566 | 19.6747 | 1.4211e-13 | -0.036619 | -0.0020193 | 0.060539 | -0.004987 | 0.056683 | -0.0022889 | -0.0015767 | 0.024301 | -0.0051638 | 0.019284 | 0.01292 | -98.1504 | -59.3052 | -99.2747 | 20.1833 | 20.1339 | 20.2054 | -100.8269 | 0.10178 | 0.064461 | 0.01233 | 0.029566 | 0.059493 | 0.081008 | -0.026784 | 0.32975 | 0.50862 | 3.0062 | 1.8819 | 1.5522 | 0.45921 | 0.53072 | 101.1298 | -19.6451 | 101.2584 | 101.1689 | 0.039114 | -19.6152 | -19.5937 | 121.3399 | 121.2905 | 121.362 | 41.8514 | -120.5016 | 101.1862 | 101.2161 | 101.2376 | 101.2211 | -19.7015
2824.6719 | 121.106 | -103.2028 | 17.6697 | 1.4211e-13 | -0.036833 | -0.0020193 | 0.060752 | -0.0052006 | 0.056896 | -0.0099194 | -0.0013631 | 0.024729 | -0.0055912 | 0.019498 | 0.01292 | -100.5266 | -60.5643 | -101.692 | 17.656 | 17.6521 | 17.7284 | -103.2308 | 0.10178 | 0.064461 | 0.021487 | 0.029566 | 0.050335 | 0.081008 | -0.022205 | -0.027986 | -0.013649 | 2.6762 | 1.5108 | 1.5388 | -0.017565 | 0.0587 | 103.1806 | -17.6401 | 103.3046 | 103.2243 | 0.043692 | -17.6193 | -17.5887 | 120.8588 | 120.8549 | 120.9312 | 42.6385 | -120.9005 | 103.2324 | 103.2532 | 103.2838 | 103.2673 | -17.6919
2826.3906 | 121.138 | -98.1995 | 22.6959 | 1.4211e-13 | -0.036406 | -0.0020193 | 0.060539 | -0.004987 | 0.056896 | -0.0022889 | -0.0015767 | 0.024729 | -0.0053776 | 0.019498 | 0.013133 | -94.1306 | -56.4894 | -95.3328 | 24.1253 | 24.1267 | 24.1338 | -96.7745 | 0.10178 | 0.059882 | 0.01233 | 0.029566 | 0.050335 | 0.081008 | -0.026784 | 1.4249 | 1.4294 | 4.0689 | 2.8667 | 1.4417 | 1.4308 | 1.4379 | 98.1727 | -22.6664 | 98.3012 | 98.2118 | 0.039114 | -22.6456 | -22.6149 | 122.3248 | 122.3262 | 122.3333 | 41.7101 | -119.4704 | 98.229 | 98.2498 | 98.2805 | 98.2593 | -22.7227
2828.1719 | 121.1609 | -102.7405 | 18.1 | 1.4211e-13 | -0.036833 | -0.0020193 | 0.06118 | -0.0045596 | 0.056896 | -0.0022889 | -0.0013631 | 0.024515 | -0.0053776 | 0.01907 | 0.01292 | -100.0184 | -60.0012 | -101.2021 | 18.1139 | 18.0825 | 18.1496 | -102.8233 | 0.10636 | 0.059882 | 0.030644 | 0.029566 | 0.054914 | 0.085587 | -0.022205 | -0.082803 | 0.013892 | 2.7221 | 1.5383 | 1.6211 | -0.017444 | 0.049634 | 102.7183 | -18.0704 | 102.8468 | 102.7711 | 0.052849 | -18.0451 | -18.0144 | 120.8543 | 120.823 | 120.8901 | 42.7393 | -120.9233 | 102.77 | 102.7954 | 102.8261 | 102.8004 | -18.1222
2829.9531 | 121.225 | -101.1154 | 19.6701 | 1.4211e-13 | -0.036406 | -0.0022329 | 0.060752 | -0.0047732 | 0.057324 | -0.02518 | -0.0013631 | 0.024729 | -0.0053776 | 0.019284 | 0.01292 | -98.6541 | -59.003 | -99.8699 | 19.3821 | 19.3921 | 19.4454 | -101.5046 | 0.10178 | 0.064461 | 0.016908 | 0.024988 | 0.050335 | 0.085587 | -0.017627 | -0.38914 | -0.28802 | 2.4614 | 1.2456 | 1.6347 | -0.278 | -0.22475 | 101.0978 | -19.6451 | 101.2172 | 101.1323 | 0.034535 | -19.6198 | -19.5845 | 120.4975 | 120.5075 | 120.5608 | 42.1124 | -121.1747 | 101.1404 | 101.1658 | 101.201 | 101.1799 | -19.6877
2831.6719 | 121.1517 | -100.3601 | 20.3979 | 1.4211e-13 | -0.037047 | -0.0024467 | 0.060752 | -0.004987 | 0.05711 | -0.0099194 | -0.0015767 | 0.024301 | -0.0055912 | 0.019284 | 0.013133 | -97.6285 | -58.2567 | -98.8672 | 20.3847 | 20.3903 | 20.4526 | -100.5109 | 0.097201 | 0.055303 | 0.021487 | 0.020409 | 0.050335 | 0.081008 | -0.022205 | -0.15082 | -0.013201 | 2.7316 | 1.4929 | 1.6437 | -0.007639 | 0.054698 | 100.3379 | -20.3775 | 100.4573 | 100.3816 | 0.043692 | -20.3476 | -20.3169 | 120.7449 | 120.7504 | 120.8128 | 42.1034 | -120.9089 | 100.3805 | 100.4104 | 100.4411 | 100.4154 | -20.4202
2833.4375 | 121.1609 | -100.3098 | 20.4758 | 1.4211e-13 | -0.036619 | -0.0022329 | 0.060539 | -0.0052006 | 0.05711 | -0.0022889 | -0.0013631 | 0.024515 | -0.0053776 | 0.019498 | 0.01292 | -97.4042 | -58.0324 | -98.6612 | 20.5541 | 20.5552 | 20.6221 | -100.3369 | 0.097201 | 0.064461 | 0.016908 | 0.029566 | 0.054914 | 0.081008 | -0.022205 | -0.027173 | 0.07838 | 2.9056 | 1.6486 | 1.6757 | 0.079382 | 0.14629 | 100.2875 | -20.4462 | 100.407 | 100.3267 | 0.039113 | -20.4209 | -20.3948 | 120.8639 | 120.8649 | 120.9318 | 42.2774 | -120.8127 | 100.3393 | 100.3647 | 100.3908 | 100.3742 | -20.498
2835.1562 | 121.1472 | -98.5062 | 22.2977 | 1.4211e-13 | -0.036619 | -0.0020193 | 0.060752 | -0.0047732 | 0.056896 | -0.0022889 | -0.0011493 | 0.024515 | -0.0051638 | 0.019711 | 0.013133 | -95.2477 | -56.8374 | -96.5186 | 22.6877 | 22.7027 | 22.7557 | -98.1848 | 0.097201 | 0.059882 | 0.01233 | 0.024988 | 0.050335 | 0.07643 | -0.031363 | 0.32133 | 0.39001 | 3.2584 | 1.9876 | 1.6663 | 0.405 | 0.45802 | 98.4748 | -22.2727 | 98.6034 | 98.5185 | 0.043693 | -22.2473 | -22.2212 | 121.1938 | 121.2088 | 121.2618 | 41.6688 | -120.4825 | 98.5312 | 98.5565 | 98.5826 | 98.566 | -22.329
2836.9219 | 120.9595 | -29.4754 | 91.42 | 1.4211e-13 | -0.035551 | -0.0018055 | 0.061393 | -0.0060552 | 0.055187 | -0.0099194 | -0.0013631 | 0.024301 | -0.0053776 | 0.019284 | 0.012492 | -35.3075 | -19.1188 | -36.9322 | 83.214 | 83.3047 | 82.9002 | -37.2073 | 0.051413 | 0.014095 | -0.038036 | -0.020797 | -2.9e-05 | 0.030644 | -0.077151 | -7.7319 | -8.206 | -5.8321 | -7.4568 | 0.27505 | -8.1153 | -8.5198 | 29.3983 | -91.4408 | 29.5268 | 29.4374 | 0.039115 | -91.42 | -91.3893 | 112.6894 | 112.7801 | 112.3756 | 10.3566 | -128.6273 | 29.4546 | 29.4754 | 29.506 | 29.4895 | -91.4971
2838.7188 | 121.1609 | -5.4291 | 115.654 | 1.4211e-13 | -0.035337 | -0.0011645 | 0.061821 | -0.005628 | 0.05476 | 0.0053411 | -0.0013631 | 0.024515 | -0.0053776 | 0.019284 | 0.01292 | -6.8299 | -1.1845 | -8.4462 | 112.3829 | 112.2527 | 112.098 | -8.676 | 0.033099 | -0.00422 | -0.042615 | -0.039111 | -0.013765 | 0.021486 | -0.086309 | -3.2469 | -3.2711 | -1.4008 | -3.0171 | 0.22983 | -3.4013 | -3.556 | 5.3428 | -115.6931 | 5.4622 | 5.3865 | 0.043694 | -115.6678 | -115.6325 | 117.812 | 117.6818 | 117.527 | 4.2446 | -124.33 | 5.39 | 5.4153 | 5.4506 | 5.4249 | -115.7403
2840.4219 | 121.1884 | -5.3513 | 115.7639 | 1.4211e-13 | -0.035337 | -0.00095092 | 0.062034 | -0.0060552 | 0.054546 | -0.02518 | -0.0013631 | 0.024088 | -0.0055912 | 0.019498 | 0.01292 | -3.2588 | 0.97665 | -4.8614 | 116.0227 | 115.838 | 115.7334 | -5.1411 | 0.033099 | -0.008798 | -0.051772 | -0.039111 | -0.018344 | 0.021486 | -0.10004 | 0.21017 | 0.25884 | 2.0925 | 0.48987 | 0.2797 | 0.074137 | -0.03049 | 5.2512 | -115.803 | 5.3844 | 5.2995 | 0.048273 | -115.7822 | -115.7424 | 121.3739 | 121.1892 | 121.0846 | 6.3279 | -120.9049 | 5.3121 | 5.3329 | 5.3727 | 5.3425 | -115.8639
2842.2188 | 121.1563 | -5.1132 | 116.0934 | 1.4211e-13 | -0.035337 | -0.0011645 | 0.061607 | -0.0060552 | 0.054546 | -0.0022889 | -0.0015767 | 0.024515 | -0.0053776 | 0.019498 | 0.013347 | -3.2405 | 1.0087 | -4.8477 | 116.0593 | 115.8655 | 115.77 | -5.1457 | 0.02852 | -0.008798 | -0.051772 | -0.048268 | -0.013765 | 0.021486 | -0.090888 | -0.032444 | -0.034126 | 1.8728 | 0.26557 | 0.29801 | -0.22798 | -0.32345 | 5.0223 | -116.1417 | 5.1417 | 5.0614 | 0.039116 | -116.1072 | -116.072 | 121.1725 | 120.9787 | 120.8832 | 6.1219 | -121.2391 | 5.065 | 5.0995 | 5.1347 | 5.1044 | -116.1843
2844 | 121.1609 | -5.0858 | 116.1255 | 1.4211e-13 | -0.035124 | -0.00073712 | 0.061821 | -0.0064826 | 0.054973 | 0.0053411 | -0.0013631 | 0.024301 | -0.0053776 | 0.019284 | 0.013133 | -3.0527 | 1.0682 | -4.7011 | 116.2425 | 116.0532 | 115.9531 | -4.9808 | 0.02852 | -0.013377 | -0.047194 | -0.04369 | -0.013765 | 0.012329 | -0.086309 | 0.10493 | 0.11697 | 2.033 | 0.38461 | 0.27968 | -0.072287 | -0.17235 | 4.9994 | -116.1692 | 5.1143 | 5.0386 | 0.039115 | -116.1393 | -116.1132 | 121.3282 | 121.139 | 121.0389 | 6.154 | -121.1063 | 5.0421 | 5.072 | 5.0981 | 5.0724 | -116.2118
2845.7188 | 121.3348 | -5.1132 | 116.0339 | 1.4211e-13 | -0.035124 | -0.00095092 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | -0.0017903 | 0.024088 | -0.0053776 | 0.019711 | 0.01292 | -3.1809 | 0.9446 | -4.8477 | 116.1143 | 115.9296 | 115.8341 | -5.1411 | 0.033099 | -0.013377 | -0.047194 | -0.052847 | -0.018344 | 0.016908 | -0.090888 | -0.027865 | 0.080324 | 1.9323 | 0.26557 | 0.29343 | -0.10437 | -0.19984 | 5.0223 | -116.0868 | 5.1463 | 5.066 | 0.043694 | -116.0523 | -116.017 | 121.2275 | 121.0428 | 120.9473 | 6.0578 | -121.175 | 5.0604 | 5.0949 | 5.1301 | 5.0998 | -116.1248
2847.4844 | 121.2616 | -4.834 | 116.3727 | 1.4211e-13 | -0.035124 | -0.0011645 | 0.062034 | -0.0060552 | 0.055187 | -0.0022889 | -0.0013631 | 0.024301 | -0.0053776 | 0.019284 | 0.013133 | -2.8696 | 1.1369 | -4.5684 | 116.4164 | 116.2272 | 116.1317 | -4.8526 | 0.033099 | -0.00422 | -0.042615 | -0.057425 | -0.018344 | 0.016908 | -0.090888 | -0.018628 | 0.043753 | 1.9644 | 0.26561 | 0.28423 | -0.14548 | -0.24098 | 4.7431 | -116.4301 | 4.8671 | 4.7914 | 0.048273 | -116.391 | -116.3558 | 121.2504 | 121.0612 | 120.9657 | 5.9709 | -121.2253 | 4.7766 | 4.8156 | 4.8509 | 4.8298 | -116.4636
2849.2031 | 121.2982 | -4.8569 | 116.3132 | 1.4211e-13 | -0.035551 | -0.0011645 | 0.062034 | -0.0060552 | 0.054973 | -0.0022889 | -0.0015767 | 0.024729 | -0.0053776 | 0.019284 | 0.013133 | -2.7231 | 1.201 | -4.4356 | 116.5492 | 116.36 | 116.2645 | -4.729 | 0.033099 | -0.00422 | -0.051772 | -0.048268 | -0.013765 | 0.016908 | -0.095467 | 0.12789 | 0.23604 | 2.1338 | 0.42127 | 0.29337 | 0.046818 | -0.048688 | 4.7614 | -116.3614 | 4.89 | 4.8051 | 0.043695 | -116.3269 | -116.2963 | 121.4061 | 121.2169 | 121.1214 | 6.0579 | -121.0422 | 4.8086 | 4.8431 | 4.8738 | 4.8527 | -116.4086
2850.9844 | 121.2708 | -4.6051 | 116.6428 | 1.4211e-13 | -0.035124 | -0.0011645 | 0.061821 | -0.0060552 | 0.054973 | -0.0022889 | -0.0017903 | 0.024515 | -0.0051638 | 0.019284 | 0.01292 | -2.6773 | 1.2651 | -4.4264 | 116.5675 | 116.3829 | 116.2828 | -4.7107 | 0.037677 | -0.013377 | -0.047194 | -0.052847 | -0.022922 | 0.012329 | -0.090888 | -0.10556 | -0.075241 | 1.9278 | 0.17865 | 0.28422 | -0.25988 | -0.35996 | 4.5142 | -116.6956 | 4.6428 | 4.5579 | 0.043694 | -116.6657 | -116.6304 | 121.1726 | 120.988 | 120.8879 | 5.8702 | -121.3534 | 4.5523 | 4.5822 | 4.6174 | 4.5917 | -116.7336
2852.7812 | 121.3165 | -4.6875 | 116.5649 | 1.4211e-13 | -0.035337 | -0.00095092 | 0.062034 | -0.0060552 | 0.055401 | -0.0099194 | -0.0015767 | 0.024515 | -0.0051638 | 0.019498 | 0.01292 | -2.5674 | 1.2697 | -4.3715 | 116.6454 | 116.447 | 116.3606 | -4.6603 | 0.02852 | -0.013377 | -0.051772 | -0.057425 | -0.018344 | 0.012329 | -0.090888 | 0.027202 | 0.080412 | 2.1201 | 0.31599 | 0.28879 | -0.11795 | -0.20431 | 4.5966 | -116.6224 | 4.716 | 4.6357 | 0.039116 | -116.5833 | -116.5526 | 121.3329 | 121.1345 | 121.0481 | 5.9572 | -121.2252 | 4.6301 | 4.6692 | 4.6998 | 4.6741 | -116.6558
2854.5625 | 121.3715 | -5.04 | 116.1896 | 1.4211e-13 | -0.035337 | -0.00095092 | 0.062248 | -0.0058416 | 0.054973 | -0.0022889 | -0.0013631 | 0.024729 | -0.0053776 | 0.019284 | 0.013133 | -2.7323 | 1.1506 | -4.573 | 116.4393 | 116.2409 | 116.1592 | -4.8755 | 0.033099 | -0.008798 | -0.056351 | -0.057425 | -0.018344 | 0.012329 | -0.095467 | 0.16447 | 0.24975 | 2.3077 | 0.46702 | 0.30255 | 0.051362 | -0.0304 | 4.9445 | -116.247 | 5.0731 | 4.9836 | 0.039116 | -116.2079 | -116.1772 | 121.4793 | 121.2809 | 121.1992 | 6.1906 | -121.0651 | 4.9826 | 5.0216 | 5.0523 | 5.0312 | -116.285
2856.3438 | 121.3028 | -4.7607 | 116.5283 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.062034 | -0.0060552 | 0.055187 | -0.0099194 | -0.0011493 | 0.024729 | -0.0053776 | 0.019498 | 0.01292 | -2.5445 | 1.2743 | -4.4402 | 116.5858 | 116.4012 | 116.2965 | -4.729 | 0.023941 | -0.008798 | -0.047194 | -0.062004 | -0.009187 | 0.012329 | -0.095467 | 0.031761 | 0.057514 | 2.2162 | 0.32056 | 0.2888 | -0.12712 | -0.23179 | 4.6653 | -116.5903 | 4.7847 | 4.7135 | 0.048273 | -116.5375 | -116.516 | 121.3466 | 121.1619 | 121.0573 | 6.035 | -121.2573 | 4.6987 | 4.7516 | 4.7731 | 4.7519 | -116.6238
2858.0469 | 121.3074 | -4.7562 | 116.5466 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.061821 | -0.006269 | 0.055401 | -0.01755 | -0.0017903 | 0.024301 | -0.0053776 | 0.019284 | 0.012492 | -2.4713 | 1.3887 | -4.3898 | 116.6408 | 116.4516 | 116.3469 | -4.6969 | 0.033099 | -0.008798 | -0.051772 | -0.057425 | -0.022922 | 0.012329 | -0.090888 | 0.059236 | 0.094144 | 2.2849 | 0.36634 | 0.3071 | -0.095063 | -0.19973 | 4.6653 | -116.6041 | 4.7893 | 4.7044 | 0.039116 | -116.5696 | -116.5343 | 121.3969 | 121.2077 | 121.1031 | 6.1449 | -121.2436 | 4.6987 | 4.7332 | 4.7685 | 4.7474 | -116.6375
2859.8281 | 121.376 | -4.6509 | 116.5878 | 1.4211e-13 | -0.03491 | -0.00052352 | 0.062034 | -0.0064826 | 0.055401 | -0.0022889 | -0.0015767 | 0.024515 | -0.0053776 | 0.019711 | 0.013133 | -2.3751 | 1.4757 | -4.3303 | 116.6957 | 116.5157 | 116.4156 | -4.642 | 0.02852 | -0.00422 | -0.051772 | -0.052847 | -0.013765 | 0.016908 | -0.095467 | 0.008897 | 0.10789 | 2.2757 | 0.32057 | 0.31168 | -0.072157 | -0.17225 | 4.5554 | -116.6407 | 4.6794 | 4.5991 | 0.043695 | -116.6016 | -116.5709 | 121.3466 | 121.1666 | 121.0665 | 6.1266 | -121.2298 | 4.598 | 4.6371 | 4.6678 | 4.6467 | -116.6833
2861.6094 | 121.3989 | -4.866 | 116.3864 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.062248 | -0.006269 | 0.055401 | -0.0099194 | -0.0013631 | 0.024301 | -0.0055912 | 0.019284 | 0.01292 | -2.5125 | 1.4025 | -4.4722 | 116.5584 | 116.3691 | 116.2691 | -4.7885 | 0.037677 | -0.013377 | -0.056351 | -0.052847 | -0.009187 | 0.021486 | -0.095467 | 0.077521 | 0.17195 | 2.3535 | 0.39379 | 0.31627 | -0.017267 | -0.11735 | 4.7706 | -116.4393 | 4.9037 | 4.8097 | 0.039116 | -116.3956 | -116.3649 | 121.4244 | 121.2352 | 121.1351 | 6.2685 | -121.1749 | 4.8132 | 4.8568 | 4.8875 | 4.8527 | -116.4819
2863.3906 | 121.4218 | -5.0812 | 116.1438 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.062034 | -0.0060552 | 0.055401 | -0.0099194 | -0.0013631 | 0.024515 | -0.0051638 | 0.019498 | 0.01292 | -2.7597 | 1.2651 | -4.7378 | 116.2882 | 116.099 | 116.0127 | -5.0678 | 0.033099 | -0.00422 | -0.047194 | -0.052847 | -0.009187 | 0.016908 | -0.090888 | 0.013355 | 0.14444 | 2.3215 | 0.3434 | 0.33005 | -0.044808 | -0.13114 | 4.9903 | -116.1966 | 5.1143 | 5.034 | 0.043694 | -116.153 | -116.1269 | 121.3694 | 121.1802 | 121.0938 | 6.3463 | -121.2116 | 5.0283 | 5.072 | 5.0981 | 5.077 | -116.2347
2865.1094 | 121.3623 | -5.2597 | 116.066 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.061607 | -0.006269 | 0.055401 | -0.0099194 | -0.0015767 | 0.024515 | -0.0055912 | 0.019498 | 0.012706 | -2.8467 | 1.2926 | -4.8385 | 116.1829 | 115.9937 | 115.9074 | -5.1777 | 0.033099 | 0.004938 | -0.051772 | -0.057425 | -0.013765 | 0.007751 | -0.090888 | 0.081989 | 0.11696 | 2.413 | 0.42121 | 0.33922 | -0.072304 | -0.15863 | 5.1688 | -116.1234 | 5.2928 | 5.2079 | 0.039116 | -116.0797 | -116.0582 | 121.4426 | 121.2534 | 121.1671 | 6.5523 | -121.2437 | 5.2023 | 5.2459 | 5.2675 | 5.2646 | -116.1569
2866.8906 | 121.3943 | -5.1178 | 116.1987 | 1.4211e-13 | -0.035124 | -0.00073712 | 0.061821 | -0.0060552 | 0.055614 | -0.0099194 | -0.0013631 | 0.024301 | -0.0049502 | 0.01907 | 0.01292 | -2.746 | 1.4116 | -4.7378 | 116.2791 | 116.0898 | 115.9989 | -5.0724 | 0.033099 | -0.008798 | -0.051772 | -0.052847 | -0.018344 | 0.012329 | -0.095467 | 0.045397 | 0.080352 | 2.3718 | 0.38002 | 0.33463 | -0.1089 | -0.19981 | 5.0223 | -116.2516 | 5.1509 | 5.066 | 0.043695 | -116.2171 | -116.1864 | 121.3969 | 121.2076 | 121.1167 | 6.5294 | -121.2711 | 5.065 | 5.0995 | 5.1301 | 5.109 | -116.2942
2868.6875 | 121.3715 | -4.9576 | 116.4047 | 1.4211e-13 | -0.035124 | -0.00073712 | 0.062034 | -0.0060552 | 0.055614 | -0.0022889 | -0.0013631 | 0.024729 | -0.0055912 | 0.019711 | 0.013133 | -2.5537 | 1.5398 | -4.5546 | 116.4668 | 116.2821 | 116.1866 | -4.903 | 0.033099 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.012329 | -0.095467 | 0.0546 | 0.062072 | 2.4039 | 0.40294 | 0.34834 | -0.12258 | -0.21808 | 4.8621 | -116.4621 | 4.9907 | 4.915 | 0.052852 | -116.4185 | -116.3924 | 121.4244 | 121.2397 | 121.1442 | 6.4974 | -121.3077 | 4.9002 | 4.9438 | 4.9699 | 4.9579 | -116.5002
2870.4531 | 121.4264 | -5.3192 | 115.9836 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.062248 | -0.0058416 | 0.055187 | -0.01755 | -0.0013631 | 0.024301 | -0.0053776 | 0.019711 | 0.01292 | -2.8559 | 1.3979 | -4.8797 | 116.1463 | 115.9662 | 115.8707 | -5.2281 | 0.023941 | -0.00422 | -0.047194 | -0.052847 | -0.013765 | 0.012329 | -0.095467 | 0.09113 | 0.16273 | 2.4633 | 0.43951 | 0.34838 | -0.01738 | -0.11286 | 5.2237 | -116.0364 | 5.3432 | 5.272 | 0.048273 | -115.9973 | -115.9713 | 121.4655 | 121.2854 | 121.1899 | 6.7171 | -121.2117 | 5.2664 | 5.3054 | 5.3315 | 5.315 | -116.079
2872.2344 | 121.4996 | -5.9784 | 115.2924 | 1.4211e-13 | -0.035124 | -0.00052352 | 0.061821 | -0.0060552 | 0.055187 | -0.0022889 | -0.0013631 | 0.024088 | -0.0053776 | 0.019711 | 0.01292 | -3.3915 | 1.1506 | -5.4108 | 115.6152 | 115.4167 | 115.3396 | -5.773 | 0.02852 | -0.008798 | -0.047194 | -0.057425 | -0.013765 | 0.016908 | -0.090888 | 0.20542 | 0.32286 | 2.5869 | 0.56761 | 0.3622 | 0.12437 | 0.047247 | 5.8875 | -115.3498 | 6.0069 | 5.9312 | 0.043694 | -115.3061 | -115.2754 | 121.5936 | 121.3951 | 121.318 | 7.129 | -121.0653 | 5.921 | 5.9646 | 5.9953 | 5.9696 | -115.3832
2873.9531 | 121.431 | -6.221 | 115.1001 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.062248 | -0.0060552 | 0.055187 | -0.01755 | -0.0017903 | 0.024301 | -0.0053776 | 0.019498 | 0.013133 | -3.767 | 0.79351 | -5.7999 | 115.2169 | 115.0367 | 114.9413 | -6.153 | 0.033099 | -0.00422 | -0.051772 | -0.062004 | -0.018344 | 0.016908 | -0.095467 | 0.067981 | 0.1168 | 2.454 | 0.42107 | 0.35309 | -0.063418 | -0.15883 | 6.1255 | -115.1621 | 6.2541 | 6.1692 | 0.043695 | -115.1184 | -115.0832 | 121.4379 | 121.2577 | 121.1623 | 7.0145 | -121.2531 | 6.159 | 6.2027 | 6.2379 | 6.2168 | -115.1956
2875.7344 | 121.3623 | -6.2942 | 115.0772 | 1.4211e-13 | -0.035337 | -0.00073712 | 0.062034 | -0.0060552 | 0.055401 | -0.0099194 | -0.0015767 | 0.024515 | -0.0053776 | 0.019498 | 0.013133 | -3.8631 | 0.7523 | -5.8915 | 115.1299 | 114.9359 | 114.8451 | -6.2629 | 0.037677 | 0.000359 | -0.056351 | -0.057425 | -0.013765 | 0.012329 | -0.090888 | 0.031329 | 0.052698 | 2.4311 | 0.40275 | 0.37142 | -0.14126 | -0.23209 | 6.2034 | -115.1346 | 6.3319 | 6.2379 | 0.034537 | -115.091 | -115.0649 | 121.4242 | 121.2302 | 121.1394 | 7.0465 | -121.3401 | 6.2368 | 6.2805 | 6.3066 | 6.2946 | -115.1681
2877.5 | 121.5179 | -6.4133 | 114.8483 | 1.4211e-13 | -0.03491 | -0.00052352 | 0.061607 | -0.0060552 | 0.055614 | -0.01755 | -0.0013631 | 0.024088 | -0.0051638 | 0.019498 | 0.012706 | -4.0142 | 0.6653 | -6.0609 | 114.9559 | 114.7711 | 114.6803 | -6.4369 | 0.02852 | -0.008798 | -0.047194 | -0.062004 | -0.018344 | 0.016908 | -0.090888 | -0.023651 | 0.1076 | 2.3991 | 0.35237 | 0.37602 | -0.077225 | -0.16804 | 6.3224 | -114.9103 | 6.4418 | 6.3661 | 0.043694 | -114.8667 | -114.8314 | 121.3692 | 121.1844 | 121.0936 | 7.0786 | -121.2852 | 6.3513 | 6.3949 | 6.4302 | 6.4045 | -114.9392
2879.2188 | 121.3898 | -6.7612 | 114.6103 | 1.4211e-13 | -0.03491 | -0.00052352 | 0.061821 | -0.0058416 | 0.055401 | -0.01755 | -0.0015767 | 0.024515 | -0.0051638 | 0.019284 | 0.012706 | -4.2523 | 0.55084 | -6.3081 | 114.6995 | 114.5193 | 114.4285 | -6.6888 | 0.033099 | -0.00422 | -0.047194 | -0.057425 | -0.009187 | 0.012329 | -0.095467 | 0.072408 | 0.089247 | 2.5089 | 0.45305 | 0.38064 | -0.091029 | -0.18183 | 6.6657 | -114.6677 | 6.7943 | 6.714 | 0.048273 | -114.6195 | -114.598 | 121.4607 | 121.2804 | 121.1896 | 7.312 | -121.2991 | 6.7037 | 6.752 | 6.7735 | 6.7569 | -114.7058
2881.0156 | 121.4035 | -7.4432 | 113.9053 | 1.4211e-13 | -0.035337 | -0.0011645 | 0.061607 | -0.0060552 | 0.055401 | -0.0099194 | -0.0013631 | 0.024301 | -0.0051638 | 0.019498 | 0.01292 | -4.7422 | 0.28528 | -6.798 | 114.2234 | 114.0247 | 113.9386 | -7.1879 | 0.033099 | 0.000359 | -0.051772 | -0.052847 | -0.013765 | 0.016908 | -0.086309 | 0.25537 | 0.31805 | 2.7011 | 0.64524 | 0.38987 | 0.1194 | 0.033219 | 7.3569 | -113.9582 | 7.4763 | 7.3915 | 0.034537 | -113.9191 | -113.8884 | 121.6666 | 121.468 | 121.3818 | 7.7285 | -121.0932 | 7.3904 | 7.4295 | 7.4601 | 7.4436 | -113.9916
2882.7344 | 121.4218 | -7.489 | 113.8733 | 1.4211e-13 | -0.035124 | -0.0011645 | 0.062034 | -0.0060552 | 0.055187 | -0.0022889 | -0.0011493 | 0.024088 | -0.0051638 | 0.019284 | 0.013133 | -4.9024 | 0.22118 | -6.9537 | 114.0494 | 113.8599 | 113.7783 | -7.3344 | 0.023941 | -0.008798 | -0.047194 | -0.052847 | -0.018344 | 0.007751 | -0.086309 | 0.15463 | 0.17612 | 2.5866 | 0.53535 | 0.38073 | -0.013394 | -0.094989 | 7.4027 | -113.9261 | 7.513 | 7.4418 | 0.039115 | -113.8916 | -113.8655 | 121.5384 | 121.3489 | 121.2673 | 7.7102 | -121.2077 | 7.4362 | 7.4707 | 7.4968 | 7.4802 | -113.9596
2884.5 | 121.4264 | -6.9122 | 114.4455 | 1.4211e-13 | -0.035551 | -0.00052352 | 0.061821 | -0.006269 | 0.055401 | -0.0022889 | -0.0013631 | 0.024515 | -0.0055912 | 0.019284 | 0.01292 | -4.4171 | 0.58747 | -6.4638 | 114.5393 | 114.3636 | 114.2682 | -6.8628 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.013765 | 0.016908 | -0.095467 | 0.049471 | 0.093799 | 2.4951 | 0.44845 | 0.39898 | -0.081918 | -0.17728 | 6.8168 | -114.5029 | 6.9499 | 6.865 | 0.048273 | -114.4593 | -114.4286 | 121.4515 | 121.2758 | 121.1804 | 7.4997 | -121.3083 | 6.8548 | 6.8985 | 6.9291 | 6.9126 | -114.541
2886.2344 | 121.4401 | -7.0038 | 114.3036 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.061821 | -0.006269 | 0.055614 | -0.0022889 | -0.0015767 | 0.024088 | -0.0055912 | 0.019711 | 0.01292 | -4.6002 | 0.45011 | -6.6515 | 114.3424 | 114.1713 | 114.0759 | -7.0551 | 0.033099 | -0.00422 | -0.051772 | -0.057425 | -0.018344 | 0.021486 | -0.095467 | -0.051291 | 0.038835 | 2.4036 | 0.35229 | 0.40358 | -0.13233 | -0.22768 | 6.9083 | -114.361 | 7.0369 | 6.952 | 0.043695 | -114.3219 | -114.2821 | 121.3462 | 121.175 | 121.0797 | 7.4539 | -121.3587 | 6.9464 | 6.9854 | 7.0253 | 6.9996 | -114.3991
2888 | 121.4035 | -6.752 | 114.7202 | 1.4211e-13 | -0.034696 | -0.00052352 | 0.062034 | -0.006269 | 0.055401 | -0.0099194 | -0.0015767 | 0.024515 | -0.0053776 | 0.019498 | 0.012492 | -2.6132 | 1.6451 | -4.6325 | 116.389 | 116.2089 | 116.0997 | -5.077 | 0.02852 | -0.008798 | -0.051772 | -0.062004 | -0.013765 | 0.016908 | -0.090888 | 1.675 | 1.6688 | 4.1388 | 2.1195 | 0.44451 | 1.4887 | 1.3795 | 6.6611 | -114.7822 | 6.7805 | 6.7002 | 0.039116 | -114.7339 | -114.7032 | 123.141 | 122.9609 | 122.8517 | 8.3971 | -119.7971 | 6.69 | 6.7382 | 6.7689 | 6.7432 | -114.811
2889.7969 | 121.4767 | -43.9499 | 77.0966 | 1.4211e-13 | -0.035551 | -0.0011645 | 0.061393 | -0.0058416 | 0.056683 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.019711 | 0.013133 | -38.8786 | -20.1719 | -40.6406 | 79.4734 | 79.2524 | 79.393 | -41.9511 | 0.060571 | 0.018674 | -0.019721 | -0.029954 | 0.004549 | 0.044379 | -0.067994 | 1.9988 | 2.3769 | 5.0713 | 3.3092 | 1.3104 | 2.1558 | 2.2964 | 43.8819 | -77.1265 | 44.0105 | 43.9302 | 0.048273 | -77.092 | -77.0522 | 123.4233 | 123.2023 | 123.3429 | 23.778 | -119.0476 | 43.9199 | 43.9544 | 43.9943 | 43.9686 | -77.1646
2891.5312 | 121.463 | -44.1238 | 77.0554 | 1.4211e-13 | -0.036192 | -0.00073712 | 0.06118 | -0.0054142 | 0.056896 | 0.0053411 | -0.0015767 | 0.024515 | -0.0051638 | 0.019711 | 0.012492 | -41.1449 | -21.4768 | -42.9985 | 77.0927 | 77.027 | 76.9938 | -44.2359 | 0.060571 | 0.023253 | -0.019721 | -0.025376 | 0.009128 | 0.048958 | -0.067994 | -0.1121 | 0.037301 | 2.9789 | 1.1254 | 1.2375 | -0.028331 | -0.06155 | 44.0558 | -77.0807 | 44.1844 | 44.1041 | 0.048273 | -77.0462 | -77.0064 | 121.2165 | 121.1509 | 121.1176 | 22.647 | -121.2913 | 44.0985 | 44.133 | 44.1728 | 44.1471 | -77.1234
2893.2969 | 121.4539 | -44.1788 | 77.092 | 1.4211e-13 | -0.035978 | -0.0011645 | 0.061393 | -0.0052006 | 0.05711 | -0.0022889 | -0.0011493 | 0.024515 | -0.0051638 | 0.019284 | 0.013347 | -41.0991 | -21.4219 | -42.9481 | 77.1339 | 77.0728 | 77.035 | -44.1489 | 0.055992 | 0.027831 | -0.015143 | -0.034533 | 0.009128 | 0.039801 | -0.063415 | 0.029829 | 0.041886 | 3.0796 | 1.2307 | 1.2008 | -0.019163 | -0.056963 | 44.1154 | -77.1265 | 44.2348 | 44.1636 | 0.048272 | -77.0829 | -77.0522 | 121.3126 | 121.2516 | 121.2138 | 22.7569 | -121.2409 | 44.1442 | 44.1879 | 44.2186 | 44.2066 | -77.1554
2895.0781 | 121.5546 | -44.1101 | 77.1011 | 1.4211e-13 | -0.036192 | -0.00095092 | 0.06118 | -0.005628 | 0.056683 | 0.0053411 | -0.0015767 | 0.024301 | -0.0053776 | 0.019498 | 0.01292 | -41.1083 | -21.4081 | -42.9664 | 77.1156 | 77.0408 | 77.0075 | -44.1902 | 0.055992 | 0.018674 | -0.015143 | -0.034533 | 0.013707 | 0.044379 | -0.058836 | -0.080046 | 0.014417 | 3.0018 | 1.1437 | 1.2237 | -0.060371 | -0.09359 | 44.0513 | -77.1357 | 44.1661 | 44.095 | 0.043693 | -77.0874 | -77.0568 | 121.2257 | 121.1509 | 121.1177 | 22.702 | -121.2913 | 44.0756 | 44.1238 | 44.1545 | 44.1288 | -77.16
2896.8594 | 121.463 | -43.9957 | 77.2797 | 1.4211e-13 | -0.035765 | -0.00073712 | 0.061393 | -0.005628 | 0.056896 | -0.0099194 | -0.0015767 | 0.024729 | -0.0055912 | 0.019711 | 0.013133 | -40.9068 | -21.2891 | -42.7833 | 77.285 | 77.2239 | 77.1861 | -44.0162 | 0.060571 | 0.018674 | -0.019721 | -0.025376 | 0.009128 | 0.044379 | -0.067994 | -0.020487 | 0.00529 | 3.0888 | 1.2124 | 1.2329 | -0.055742 | -0.093552 | 43.9277 | -77.305 | 44.0562 | 43.9759 | 0.048273 | -77.2705 | -77.2353 | 121.2806 | 121.2196 | 121.1818 | 22.7066 | -121.2958 | 43.9703 | 44.0048 | 44.04 | 44.0143 | -77.3477
2898.6406 | 121.4355 | -43.9178 | 77.3849 | 1.4211e-13 | -0.035978 | -0.00095092 | 0.060966 | -0.0054142 | 0.056896 | -0.0099194 | -0.0013631 | 0.024301 | -0.0055912 | 0.019711 | 0.013347 | -40.7649 | -21.1243 | -42.6459 | 77.4223 | 77.3476 | 77.3189 | -43.8879 | 0.060571 | 0.018674 | -0.019721 | -0.034533 | 0.004549 | 0.035222 | -0.067994 | 0.029903 | 0.037355 | 3.1529 | 1.2719 | 1.242 | -0.037397 | -0.066059 | 43.8499 | -77.4195 | 43.9784 | 43.8981 | 0.048273 | -77.3804 | -77.3497 | 121.3402 | 121.2654 | 121.2367 | 22.7936 | -121.2729 | 43.8833 | 43.9224 | 43.9531 | 43.9365 | -77.4529
2900.3594 | 121.5225 | -43.7393 | 77.5131 | 1.4211e-13 | -0.035765 | -0.00095092 | 0.061393 | -0.0054142 | 0.056896 | -0.0022889 | -0.0013631 | 0.024301 | -0.0053776 | 0.019711 | 0.013347 | -40.5909 | -21.0419 | -42.4628 | 77.5734 | 77.5124 | 77.4837 | -43.7368 | 0.055992 | 0.014095 | -0.0243 | -0.029954 | 0.004549 | 0.039801 | -0.067994 | 0.002479 | 0.060268 | 3.1484 | 1.2765 | 1.274 | -0.000729 | -0.029403 | 43.6713 | -77.5431 | 43.7953 | 43.715 | 0.043694 | -77.5086 | -77.4733 | 121.3127 | 121.2517 | 121.223 | 22.6975 | -121.25 | 43.7094 | 43.7439 | 43.7791 | 43.7534 | -77.5811
2902.1406 | 121.4859 | -43.959 | 77.3209 | 1.4211e-13 | -0.035978 | -0.00095092 | 0.06118 | -0.004987 | 0.056896 | -0.0099194 | -0.0013631 | 0.024515 | -0.0055912 | 0.019498 | 0.01292 | -40.7741 | -21.1334 | -42.6597 | 77.3491 | 77.288 | 77.2548 | -43.9658 | 0.060571 | 0.018674 | -0.028879 | -0.025376 | 0.009128 | 0.044379 | -0.063415 | -0.006741 | 0.028188 | 3.185 | 1.2994 | 1.3061 | -0.032836 | -0.066072 | 43.8956 | -77.3462 | 44.0196 | 43.9302 | 0.034536 | -77.3117 | -77.2765 | 121.3081 | 121.2471 | 121.2138 | 22.8256 | -121.2866 | 43.9337 | 43.9682 | 44.0034 | 43.9777 | -77.3843
2903.9219 | 121.5134 | -43.8766 | 77.3804 | 1.4211e-13 | -0.035978 | -0.0011645 | 0.06118 | -0.005628 | 0.056896 | -0.01755 | -0.0015767 | 0.024729 | -0.0053776 | 0.019925 | 0.012706 | -40.5909 | -20.9503 | -42.4811 | 77.5276 | 77.4574 | 77.4242 | -43.7964 | 0.055992 | 0.014095 | -0.019721 | -0.034533 | 0.013707 | 0.035222 | -0.072572 | 0.080282 | 0.14724 | 3.2857 | 1.3955 | 1.3152 | 0.077076 | 0.043827 | 43.8041 | -77.4149 | 43.9326 | 43.8569 | 0.052851 | -77.3667 | -77.3451 | 121.4043 | 121.3341 | 121.3008 | 22.9264 | -121.1767 | 43.8421 | 43.8904 | 43.9119 | 43.8907 | -77.4529
2905.6406 | 121.5546 | -43.6203 | 77.6276 | 1.4211e-13 | -0.036192 | -0.00073712 | 0.061607 | -0.0052006 | 0.05711 | -0.0099194 | -0.0013631 | 0.024515 | -0.0058048 | 0.019711 | 0.01292 | -40.4353 | -20.758 | -42.3117 | 77.6741 | 77.6086 | 77.5799 | -43.6453 | 0.051413 | 0.018674 | -0.0243 | -0.034533 | 0.009128 | 0.044379 | -0.063415 | -0.024961 | 0.046552 | 3.185 | 1.3086 | 1.3335 | -0.019012 | -0.047693 | 43.5569 | -77.6621 | 43.6717 | 43.596 | 0.039115 | -77.6184 | -77.5832 | 121.2944 | 121.2289 | 121.2002 | 22.8623 | -121.2728 | 43.5858 | 43.6294 | 43.6647 | 43.639 | -77.691
2907.4062 | 121.5683 | -43.4921 | 77.774 | 1.4211e-13 | -0.035765 | -0.00073712 | 0.061607 | -0.004987 | 0.05711 | -0.0099194 | -0.0015767 | 0.024301 | -0.0053776 | 0.019498 | 0.01292 | -40.3117 | -20.6389 | -42.1973 | 77.7932 | 77.723 | 77.6852 | -43.5354 | 0.06515 | 0.018674 | -0.028879 | -0.029954 | 0.004549 | 0.039801 | -0.067994 | -0.043241 | 0.019106 | 3.1805 | 1.2949 | 1.3381 | -0.051024 | -0.08887 | 43.4241 | -77.804 | 43.5573 | 43.4632 | 0.039115 | -77.7695 | -77.7342 | 121.2853 | 121.2151 | 121.1773 | 22.8532 | -121.3094 | 43.4622 | 43.4967 | 43.5319 | 43.5108 | -77.842
2909.2031 | 121.4676 | -44.2886 | 77.0508 | 1.4211e-13 | -0.035765 | -0.0011645 | 0.061393 | -0.0052006 | 0.05711 | -0.0022889 | -0.0013631 | 0.024515 | -0.0053776 | 0.019711 | 0.013133 | -40.9481 | -20.9778 | -42.8291 | 77.111 | 77.0408 | 77.003 | -44.2314 | 0.060571 | 0.018674 | -0.019721 | -0.039111 | 0.004549 | 0.048958 | -0.077151 | 0.057272 | 0.060193 | 3.3406 | 1.4596 | 1.4023 | -0.010017 | -0.047815 | 44.2115 | -77.0899 | 44.3492 | 44.2689 | 0.05743 | -77.0462 | -77.0018 | 121.3996 | 121.3294 | 121.2916 | 23.3109 | -121.2821 | 44.2495 | 44.2932 | 44.3376 | 44.3073 | -77.1279
2910.9219 | 121.5546 | -44.1788 | 77.0828 | 1.4211e-13 | -0.035978 | -0.00095092 | 0.061607 | -0.0047732 | 0.05711 | 0.0053411 | -0.0013631 | 0.024515 | -0.0058048 | 0.019498 | 0.012706 | -40.884 | -20.8816 | -42.7924 | 77.1293 | 77.0637 | 77.0396 | -44.2039 | 0.055992 | 0.027831 | -0.028879 | -0.034533 | 0.004549 | 0.044379 | -0.063415 | -0.025118 | 0.046462 | 3.2948 | 1.3863 | 1.4114 | -0.019166 | -0.04323 | 44.1154 | -77.1174 | 44.2348 | 44.1499 | 0.034536 | -77.0783 | -77.0384 | 121.3081 | 121.2424 | 121.2184 | 23.2972 | -121.2867 | 44.1442 | 44.1833 | 44.2232 | 44.2066 | -77.1462
2912.7031 | 121.4767 | -44.1376 | 77.179 | 1.4211e-13 | -0.035765 | -0.00095092 | 0.061607 | -0.0052006 | 0.05711 | -0.0099194 | -0.0017903 | 0.024088 | -0.0053776 | 0.019711 | 0.01292 | -40.8015 | -20.7259 | -42.6963 | 77.198 | 77.1369 | 77.0945 | -44.1444 | 0.060571 | 0.023253 | -0.019721 | -0.025376 | 0.009128 | 0.035222 | -0.067994 | -0.006791 | 0.019008 | 3.336 | 1.4413 | 1.4481 | -0.042033 | -0.084417 | 44.0696 | -77.2043 | 44.1981 | 44.1179 | 0.048273 | -77.1698 | -77.1437 | 121.3355 | 121.2745 | 121.2321 | 23.4116 | -121.3233 | 44.1122 | 44.1467 | 44.1728 | 44.1608 | -77.2469
2914.4219 | 121.5363 | -44.0277 | 77.2476 | 1.4211e-13 | -0.035765 | -0.00095092 | 0.061393 | -0.0052006 | 0.057324 | -0.0022889 | -0.0013631 | 0.024301 | -0.0053776 | 0.019925 | 0.012492 | -40.6825 | -20.6115 | -42.5956 | 77.2987 | 77.2285 | 77.1953 | -44.0482 | 0.06515 | 0.014095 | -0.0243 | -0.025376 | 0.013707 | 0.044379 | -0.067994 | -0.020496 | 0.051068 | 3.3452 | 1.4321 | 1.4526 | -0.01912 | -0.052352 | 43.9597 | -77.273 | 44.0929 | 44.0034 | 0.043694 | -77.2339 | -77.2032 | 121.3264 | 121.2562 | 121.223 | 23.4162 | -121.2958 | 44.0023 | 44.0414 | 44.0721 | 44.0418 | -77.3156
2916.2031 | 121.6187 | -44.0094 | 77.2751 | 1.4211e-13 | -0.035551 | -0.00073712 | 0.061393 | -0.0054142 | 0.05711 | -0.0099194 | -0.0011493 | 0.024301 | -0.0053776 | 0.019498 | 0.012706 | -40.6321 | -20.4833 | -42.5544 | 77.3216 | 77.2606 | 77.2182 | -44.0207 | 0.06515 | 0.023253 | -0.0243 | -0.029954 | 0.009128 | 0.035222 | -0.067994 | -0.011334 | 0.046495 | 3.3773 | 1.455 | 1.4664 | -0.014532 | -0.056924 | 43.9414 | -77.305 | 44.0745 | 43.9851 | 0.043694 | -77.266 | -77.2399 | 121.331 | 121.27 | 121.2276 | 23.5261 | -121.2958 | 43.9794 | 44.0185 | 44.0446 | 44.0327 | -77.3431
2917.9688 | 121.6095 | -44.1559 | 77.0966 | 1.4211e-13 | -0.035765 | -0.0013783 | 0.06118 | -0.0052006 | 0.057324 | -0.0099194 | -0.0015767 | 0.024515 | -0.0053776 | 0.019711 | 0.01292 | -40.7603 | -20.4878 | -42.7009 | 77.1568 | 77.1003 | 77.0625 | -44.1856 | 0.060571 | 0.023253 | -0.019721 | -0.029954 | 0.009128 | 0.044379 | -0.067994 | -0.02969 | 0.0602 | 3.3955 | 1.455 | 1.4847 | 0.003732 | -0.03407 | 44.0879 | -77.1265 | 44.2165 | 44.1362 | 0.048273 | -77.0874 | -77.0522 | 121.3126 | 121.2562 | 121.2184 | 23.668 | -121.2821 | 44.1259 | 44.165 | 44.2003 | 44.1791 | -77.1646
2919.75 | 121.6049 | -44.0186 | 77.2476 | 1.4211e-13 | -0.035978 | -0.00095092 | 0.06118 | -0.0047732 | 0.057537 | -0.0099194 | -0.0015767 | 0.024515 | -0.0053776 | 0.019925 | 0.013133 | -40.568 | -20.3184 | -42.5177 | 77.3262 | 77.256 | 77.2319 | -44.0299 | 0.069728 | 0.027831 | -0.019721 | -0.029954 | 0.004549 | 0.039801 | -0.067994 | -0.011336 | 0.078538 | 3.4505 | 1.5008 | 1.5121 | 0.008354 | -0.015723 | 43.9506 | -77.2776 | 44.0883 | 43.9988 | 0.048273 | -77.2431 | -77.2078 | 121.3447 | 121.2745 | 121.2505 | 23.7001 | -121.2775 | 43.9886 | 44.0231 | 44.0584 | 44.0464 | -77.3156
2921.5312 | 121.4767 | -43.9224 | 77.4307 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.061393 | -0.004987 | 0.057324 | -0.0022889 | -0.0015767 | 0.024301 | -0.0055912 | 0.019711 | 0.01292 | -40.4307 | -20.2131 | -42.3621 | 77.4681 | 77.4071 | 77.3693 | -43.8971 | 0.060571 | 0.018674 | -0.0243 | -0.025376 | 0.009128 | 0.044379 | -0.067994 | 0.025322 | 0.037363 | 3.4917 | 1.5603 | 1.535 | -0.023647 | -0.06147 | 43.8544 | -77.4561 | 43.983 | 43.8981 | 0.043694 | -77.4216 | -77.3863 | 121.3905 | 121.3295 | 121.2917 | 23.7093 | -121.3278 | 43.897 | 43.9316 | 43.9668 | 43.9411 | -77.4987
2923.2344 | 121.6049 | -43.5928 | 77.7054 | 1.4211e-13 | -0.035978 | -0.0011645 | 0.06118 | -0.004987 | 0.057751 | -0.0099194 | -0.0013631 | 0.024088 | -0.0058048 | 0.019284 | 0.012706 | -40.1468 | -19.9934 | -42.0782 | 77.7428 | 77.6681 | 77.6348 | -43.6315 | 0.06515 | 0.018674 | -0.015143 | -0.034533 | 0.009128 | 0.035222 | -0.067994 | -0.03869 | 0.037408 | 3.446 | 1.5146 | 1.5533 | -0.037306 | -0.070569 | 43.5248 | -77.7399 | 43.658 | 43.5777 | 0.052851 | -77.6963 | -77.6702 | 121.3356 | 121.2609 | 121.2276 | 23.5995 | -121.3369 | 43.5583 | 43.602 | 43.6281 | 43.6115 | -77.7734
2925.0156 | 121.6049 | -43.5196 | 77.774 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.061607 | -0.004987 | 0.057537 | -0.0099194 | -0.0013631 | 0.024301 | -0.0053776 | 0.019711 | 0.01292 | -40.0553 | -19.9018 | -41.9958 | 77.7977 | 77.7322 | 77.6898 | -43.5674 | 0.060571 | 0.009516 | -0.019721 | -0.025376 | 0.009128 | 0.035222 | -0.063415 | -0.047827 | 0.023684 | 3.4643 | 1.5238 | 1.5716 | -0.041866 | -0.084291 | 43.4562 | -77.7994 | 43.5802 | 43.4999 | 0.043694 | -77.7649 | -77.7388 | 121.3173 | 121.2518 | 121.2093 | 23.6178 | -121.3415 | 43.4942 | 43.5287 | 43.5548 | 43.5291 | -77.8375
2926.7344 | 121.5454 | -43.4967 | 77.8427 | 1.4211e-13 | -0.035551 | -0.00052352 | 0.061393 | -0.004987 | 0.057324 | 0.0053411 | -0.0015767 | 0.024301 | -0.0055912 | 0.019925 | 0.012706 | -39.9591 | -19.8468 | -41.9134 | 77.871 | 77.8009 | 77.763 | -43.5033 | 0.060571 | 0.018674 | -0.015143 | -0.034533 | 0.009128 | 0.044379 | -0.067994 | -0.00661 | 0.028274 | 3.5376 | 1.5833 | 1.5899 | -0.041846 | -0.079698 | 43.4287 | -77.8772 | 43.5573 | 43.4816 | 0.052851 | -77.8336 | -77.7983 | 121.3677 | 121.2976 | 121.2597 | 23.6499 | -121.346 | 43.4622 | 43.5058 | 43.5411 | 43.5154 | -77.9107
2928.5156 | 121.6187 | -43.4738 | 77.7924 | 1.4211e-13 | -0.035765 | -0.00052352 | 0.061393 | -0.004987 | 0.057537 | -0.0099194 | -0.0015767 | 0.024301 | -0.0051638 | 0.019498 | 0.01292 | -39.9454 | -19.8743 | -41.9043 | 77.8435 | 77.778 | 77.7401 | -43.5308 | 0.051413 | 0.023253 | -0.015143 | -0.029954 | 0.004549 | 0.039801 | -0.067994 | -0.056972 | 0.051158 | 3.5284 | 1.5696 | 1.6265 | -0.014387 | -0.052237 | 43.4058 | -77.8223 | 43.5252 | 43.4587 | 0.052851 | -77.7878 | -77.7526 | 121.3173 | 121.2518 | 121.2139 | 23.5995 | -121.3231 | 43.4439 | 43.4784 | 43.5136 | 43.4971 | -77.8604
2930.25 | 121.55 | -43.5059 | 77.8473 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.061393 | -0.0052006 | 0.057537 | -0.0099194 | -0.0013631 | 0.024515 | -0.0051638 | 0.019711 | 0.013133 | -39.895 | -19.8148 | -41.8676 | 77.8618 | 77.7963 | 77.763 | -43.5216 | 0.060571 | 0.023253 | -0.0243 | -0.029954 | 0.004549 | 0.044379 | -0.067994 | -0.015771 | 0.014539 | 3.6108 | 1.6382 | 1.654 | -0.051003 | -0.084276 | 43.4379 | -77.8772 | 43.5664 | 43.4816 | 0.043694 | -77.8427 | -77.8029 | 121.3677 | 121.3021 | 121.2689 | 23.6911 | -121.3689 | 43.4759 | 43.5104 | 43.5502 | 43.5291 | -77.9153
2932.0312 | 121.5866 | -43.4509 | 77.8198 | 1.4211e-13 | -0.035765 | -0.00073712 | 0.061607 | -0.0052006 | 0.057537 | -0.0022889 | -0.0013631 | 0.024515 | -0.0055912 | 0.019925 | 0.012492 | -39.8126 | -19.7507 | -41.7944 | 77.8939 | 77.8283 | 77.7859 | -43.4804 | 0.051413 | 0.018674 | -0.019721 | -0.025376 | 0.004549 | 0.039801 | -0.067994 | -0.029492 | 0.074054 | 3.6383 | 1.6566 | 1.686 | 0.008515 | -0.033917 | 43.3829 | -77.8452 | 43.5023 | 43.4312 | 0.048273 | -77.8153 | -77.78 | 121.3448 | 121.2793 | 121.2368 | 23.7002 | -121.3002 | 43.4256 | 43.4555 | 43.4907 | 43.4696 | -77.8878
2933.75 | 121.5729 | -43.3456 | 77.9755 | 1.4211e-13 | -0.035551 | -0.00073712 | 0.06118 | -0.004987 | 0.057751 | -0.0022889 | -0.0015767 | 0.024088 | -0.0053776 | 0.020139 | 0.012492 | -39.6661 | -19.595 | -41.6433 | 78.0129 | 77.9428 | 77.905 | -43.3705 | 0.060571 | 0.018674 | -0.028879 | -0.029954 | 0.013707 | 0.039801 | -0.067994 | -0.024884 | 0.037452 | 3.6795 | 1.7023 | 1.7272 | -0.032651 | -0.070513 | 43.2776 | -78.0054 | 43.4062 | 43.3168 | 0.039115 | -77.9618 | -77.9357 | 121.3586 | 121.2885 | 121.2506 | 23.7506 | -121.346 | 43.3157 | 43.3593 | 43.3854 | 43.3643 | -78.0435
2935.5156 | 121.4813 | -43.3456 | 78.0121 | 1.4211e-13 | -0.035551 | -0.00095092 | 0.061607 | -0.0047732 | 0.057965 | 0.0053411 | -0.0013631 | 0.024301 | -0.0055912 | 0.019711 | 0.01292 | -39.6066 | -19.4897 | -41.5792 | 78.0587 | 77.9932 | 77.9507 | -43.3385 | 0.060571 | 0.027831 | -0.019721 | -0.029954 | 0.013707 | 0.039801 | -0.072572 | 0.007169 | 0.046615 | 3.7391 | 1.7664 | 1.7593 | -0.018904 | -0.061348 | 43.2731 | -78.042 | 43.4062 | 43.3259 | 0.052851 | -77.9984 | -77.9723 | 121.4043 | 121.3388 | 121.2964 | 23.8559 | -121.3506 | 43.3157 | 43.3593 | 43.3854 | 43.3735 | -78.0847
2937.2344 | 121.5454 | -43.1671 | 78.186 | 1.4211e-13 | -0.035765 | -0.00052352 | 0.060966 | -0.004987 | 0.057537 | -0.0099194 | -0.0013631 | 0.024301 | -0.0053776 | 0.020139 | 0.012706 | -39.4601 | -19.2882 | -41.4327 | 78.1869 | 78.1122 | 78.0744 | -43.2194 | 0.055992 | 0.014095 | -0.019721 | -0.025376 | 0.009128 | 0.044379 | -0.067994 | -0.052307 | 0.00086 | 3.707 | 1.7344 | 1.7867 | -0.073802 | -0.11168 | 43.0991 | -78.2114 | 43.2231 | 43.1474 | 0.048273 | -78.1769 | -78.1417 | 121.354 | 121.2793 | 121.2415 | 23.8789 | -121.4055 | 43.1417 | 43.1762 | 43.2115 | 43.1812 | -78.254
2939.0156 | 121.4767 | -43.1717 | 78.2181 | 1.4211e-13 | -0.035337 | -0.00030992 | 0.061821 | -0.004987 | 0.057751 | -0.0099194 | -0.0015767 | 0.024088 | -0.0053776 | 0.019711 | 0.012706 | -39.3548 | -19.2104 | -41.3457 | 78.2373 | 78.1855 | 78.143 | -43.1462 | 0.051413 | 0.018674 | -0.019721 | -0.029954 | 0.004549 | 0.035222 | -0.063415 | 0.025534 | 0.019178 | 3.8169 | 1.826 | 1.8005 | -0.032583 | -0.075041 | 43.1083 | -78.248 | 43.2231 | 43.152 | 0.043694 | -78.2135 | -78.1829 | 121.4089 | 121.3572 | 121.3147 | 23.9613 | -121.3642 | 43.1417 | 43.1762 | 43.2069 | 43.1904 | -78.2815
2940.7969 | 121.5775 | -43.0115 | 78.3646 | 1.4211e-13 | -0.035765 | -0.00073712 | 0.06118 | -0.004987 | 0.057537 | -0.0022889 | -0.0017903 | 0.024088 | -0.0053776 | 0.019925 | 0.012706 | -39.1808 | -19.0044 | -41.1855 | 78.3838 | 78.3137 | 78.2804 | -43.0134 | 0.060571 | 0.014095 | -0.0243 | -0.029954 | 0.004549 | 0.044379 | -0.067994 | -0.001894 | 0.019203 | 3.8307 | 1.826 | 1.8279 | -0.050858 | -0.084166 | 42.9435 | -78.3945 | 43.072 | 42.9872 | 0.043694 | -78.36 | -78.3202 | 121.3952 | 121.3252 | 121.2919 | 24.0071 | -121.3779 | 42.9815 | 43.016 | 43.0559 | 43.0256 | -78.4326
2942.5156 | 121.5042 | -42.9932 | 78.4378 | 1.4211e-13 | -0.035551 | -0.00052352 | 0.061393 | -0.0047732 | 0.057965 | -0.0022889 | -0.0013631 | 0.024088 | -0.0051638 | 0.019925 | 0.01292 | -39.0892 | -18.954 | -41.1168 | 78.4341 | 78.3641 | 78.3262 | -42.9767 | 0.055992 | 0.018674 | -0.0243 | -0.034533 | 0.009128 | 0.039801 | -0.067994 | 0.016426 | -0.003677 | 3.9039 | 1.8764 | 1.8599 | -0.073731 | -0.11162 | 42.9252 | -78.4723 | 43.0492 | 42.9689 | 0.043694 | -78.4287 | -78.398 | 121.4273 | 121.3572 | 121.3193 | 24.0392 | -121.4145 | 42.9586 | 43.0023 | 43.033 | 43.0118 | -78.5058
2944.2969 | 121.6232 | -43.0115 | 78.2547 | 1.4211e-13 | -0.035551 | -0.00030992 | 0.06118 | -0.0052006 | 0.058178 | -0.0099194 | -0.0013631 | 0.024301 | -0.0053776 | 0.019711 | 0.01292 | -39.1304 | -18.9586 | -41.1717 | 78.3471 | 78.2679 | 78.2392 | -43.0637 | 0.055992 | 0.014095 | -0.019721 | -0.029954 | 0.009128 | 0.048958 | -0.063415 | -0.052263 | 0.092438 | 3.881 | 1.8397 | 1.892 | 0.013216 | -0.015511 | 42.9481 | -78.2847 | 43.0675 | 42.9918 | 0.043694 | -78.2456 | -78.2057 | 121.3586 | 121.2794 | 121.2507 | 24.0529 | -121.3184 | 42.9815 | 43.0206 | 43.0604 | 43.0256 | -78.3181
2946.0781 | 121.6095 | -43.0527 | 78.2639 | 1.4211e-13 | -0.035551 | -0.00030992 | 0.061393 | -0.0052006 | 0.057751 | -0.0022889 | -0.0013631 | 0.024088 | -0.0055912 | 0.019925 | 0.01292 | -39.0892 | -18.867 | -41.1809 | 78.3151 | 78.2542 | 78.2163 | -43.0821 | 0.060571 | 0.009516 | -0.028879 | -0.034533 | 0.004549 | 0.039801 | -0.072572 | -0.02938 | 0.051235 | 3.9634 | 1.8718 | 1.9012 | -0.009676 | -0.047559 | 42.9801 | -78.2984 | 43.1132 | 43.0238 | 0.043693 | -78.2593 | -78.2241 | 121.3678 | 121.3069 | 121.269 | 24.1857 | -121.3459 | 43.0181 | 43.0572 | 43.0925 | 43.0622 | -78.3364
2947.8594 | 121.6187 | -43.0252 | 78.2593 | 1.4211e-13 | -0.035765 | -0.00052352 | 0.060966 | -0.0052006 | 0.057965 | -0.0099194 | -0.0013631 | 0.024088 | -0.0053776 | 0.019711 | 0.012706 | -39.0206 | -18.7892 | -41.1259 | 78.3426 | 78.2771 | 78.23 | -43.0683 | 0.060571 | 0.023253 | -0.0243 | -0.034533 | 0.009128 | 0.039801 | -0.067994 | -0.043109 | 0.083283 | 4.0047 | 1.8993 | 1.9424 | 0.017797 | -0.029245 | 42.9572 | -78.2938 | 43.0858 | 43.0009 | 0.043694 | -78.2501 | -78.2195 | 121.3678 | 121.3023 | 121.2552 | 24.236 | -121.3276 | 42.9907 | 43.0343 | 43.065 | 43.0485 | -78.3273
2949.5781 | 121.6599 | -43.1671 | 78.1311 | 1.4211e-13 | -0.035551 | -0.00030992 | 0.06118 | -0.004987 | 0.057751 | 0.0053411 | -0.0015767 | 0.024088 | -0.0055912 | 0.019711 | 0.01292 | -39.0801 | -18.7251 | -41.2038 | 78.2281 | 78.1672 | 78.1247 | -43.1828 | 0.060571 | 0.018674 | -0.019721 | -0.034533 | -2.9e-05 | 0.030644 | -0.067994 | -0.015676 | 0.096996 | 4.087 | 1.9633 | 1.979 | 0.036076 | -0.00638 | 43.0991 | -78.1656 | 43.2277 | 43.1474 | 0.048273 | -78.1311 | -78.1005 | 121.3952 | 121.3343 | 121.2918 | 24.442 | -121.3139 | 43.1326 | 43.1671 | 43.1978 | 43.1858 | -78.1991
2951.3906 | 121.55 | -43.2678 | 78.1265 | 1.4211e-13 | -0.035337 | -0.00052352 | 0.061393 | -0.004987 | 0.058606 | -0.0099194 | -0.0013631 | 0.024088 | -0.0051638 | 0.019711 | 0.012706 | -39.0663 | -18.5419 | -41.2404 | 78.1732 | 78.1168 | 78.0698 | -43.2423 | 0.060571 | 0.018674 | -0.019721 | -0.034533 | 0.009128 | 0.039801 | -0.067994 | 0.025506 | 0.046634 | 4.2015 | 2.0274 | 2.0019 | -0.009714 | -0.056745 | 43.1998 | -78.1611 | 43.3284 | 43.2481 | 0.048273 | -78.1174 | -78.0867 | 121.441 | 121.3846 | 121.3376 | 24.7259 | -121.3688 | 43.2333 | 43.2769 | 43.3076 | 43.2865 | -78.1945
2953.1094 | 121.6553 | -43.2678 | 78.0304 | 1.4211e-13 | -0.035551 | -0.00052352 | 0.061607 | -0.0047732 | 0.058606 | -0.0022889 | -0.0013631 | 0.024088 | -0.0055912 | 0.019711 | 0.013133 | -39.0526 | -18.4778 | -41.2679 | 78.1136 | 78.0527 | 78.0148 | -43.3018 | 0.051413 | 0.018674 | -0.019721 | -0.039111 | 0.004549 | 0.044379 | -0.067994 | -0.03402 | 0.083245 | 4.2152 | 1.9999 | 2.034 | 0.022311 | -0.015558 | 43.1998 | -78.0695 | 43.3192 | 43.2481 | 0.048273 | -78.0258 | -77.986 | 121.3815 | 121.3205 | 121.2827 | 24.79 | -121.3322 | 43.2287 | 43.2724 | 43.3122 | 43.2865 | -78.0984
2954.9062 | 121.5408 | -43.3411 | 78.0533 | 1.4211e-13 | -0.035337 | -0.00030992 | 0.061393 | -0.0045596 | 0.058392 | -0.0022889 | -0.0013631 | 0.024301 | -0.0053776 | 0.019925 | 0.012706 | -39.0343 | -18.4275 | -41.2725 | 78.0816 | 78.0115 | 77.9782 | -43.3385 | 0.055992 | 0.018674 | -0.019721 | -0.034533 | 0.009128 | 0.039801 | -0.067994 | 0.002591 | 0.028308 | 4.3068 | 2.0686 | 2.066 | -0.041788 | -0.075075 | 43.2731 | -78.0878 | 43.3971 | 43.3213 | 0.048273 | -78.0442 | -78.0135 | 121.4227 | 121.3526 | 121.3193 | 24.9136 | -121.3918 | 43.3065 | 43.3502 | 43.3809 | 43.3597 | -78.1213
2956.6875 | 121.5363 | -43.3548 | 78.0579 | 1.4211e-13 | -0.035551 | -0.00030992 | 0.061393 | -0.0045596 | 0.058606 | -0.0099194 | -0.0015767 | 0.023874 | -0.0055912 | 0.019711 | 0.012706 | -38.9656 | -18.3084 | -41.2358 | 78.077 | 78.0161 | 77.9782 | -43.3339 | 0.06515 | 0.018674 | -0.0243 | -0.025376 | 0.009128 | 0.035222 | -0.072572 | 0.020903 | 0.019153 | 4.3892 | 2.119 | 2.0981 | -0.041786 | -0.079652 | 43.2822 | -78.0832 | 43.4199 | 43.3305 | 0.048272 | -78.0487 | -78.0226 | 121.4318 | 121.3709 | 121.333 | 25.0464 | -121.3918 | 43.3294 | 43.3639 | 43.39 | 43.3735 | -78.1304
2958.4531 | 121.6507 | -43.2724 | 78.0807 | 1.4211e-13 | -0.035337 | -9.6116e-05 | 0.061821 | -0.0052006 | 0.059247 | -0.0022889 | -0.0011493 | 0.02366 | -0.0053776 | 0.019711 | 0.01292 | -38.874 | -18.1344 | -41.19 | 78.0999 | 78.0344 | 77.9965 | -43.3064 | 0.055992 | 0.018674 | -0.028879 | -0.04369 | -2.9e-05 | 0.039801 | -0.067994 | -0.034021 | 0.019156 | 4.3984 | 2.0824 | 2.1164 | -0.046359 | -0.084227 | 43.2044 | -78.1244 | 43.3284 | 43.2435 | 0.039115 | -78.0808 | -78.0409 | 121.3723 | 121.3068 | 121.2689 | 25.138 | -121.3872 | 43.2287 | 43.2724 | 43.3122 | 43.2911 | -78.1487
2960.1875 | 121.5454 | -43.3228 | 78.0899 | 1.4211e-13 | -0.035337 | -0.00030992 | 0.061821 | -0.0047732 | 0.058606 | -0.0022889 | -0.0011493 | 0.024088 | -0.0055912 | 0.019925 | 0.012492 | -38.8054 | -18.0795 | -41.1443 | 78.1136 | 78.0573 | 78.0148 | -43.311 | 0.060571 | 0.018674 | -0.015143 | -0.034533 | 0.004549 | 0.044379 | -0.067994 | 0.011754 | 0.023736 | 4.5174 | 2.1785 | 2.1667 | -0.032619 | -0.075067 | 43.2548 | -78.1244 | 43.3833 | 43.3076 | 0.052851 | -78.0854 | -78.0455 | 121.4364 | 121.38 | 121.3376 | 25.2433 | -121.4009 | 43.2882 | 43.3273 | 43.3671 | 43.3414 | -78.1579
2961.9688 | 121.5271 | -43.364 | 78.0029 | 1.4211e-13 | -0.035551 | -0.00030992 | 0.061393 | -0.004987 | 0.058819 | -0.0022889 | -0.0015767 | 0.024301 | -0.0053776 | 0.019711 | 0.01292 | -38.8054 | -18.0795 | -41.19 | 78.0495 | 77.9794 | 77.9416 | -43.3843 | 0.055992 | 0.014095 | -0.0243 | -0.025376 | 0.013707 | 0.035222 | -0.067994 | -0.020309 | 0.046613 | 4.5586 | 2.1739 | 2.1942 | -0.023486 | -0.06135 | 43.296 | -78.0283 | 43.4199 | 43.3397 | 0.043694 | -77.9892 | -77.9677 | 121.4135 | 121.3434 | 121.3055 | 25.2845 | -121.3872 | 43.3386 | 43.3777 | 43.3992 | 43.378 | -78.0709
2963.7656 | 121.669 | -43.2724 | 78.0029 | 1.4211e-13 | -0.035551 | -9.6116e-05 | 0.061607 | -0.004987 | 0.059247 | -0.0099194 | -0.0013631 | 0.024088 | -0.0053776 | 0.019925 | 0.01292 | -38.6909 | -17.965 | -41.1259 | 78.0679 | 78.0023 | 77.9599 | -43.3522 | 0.060571 | 0.018674 | -0.0243 | -0.029954 | 0.004549 | 0.039801 | -0.067994 | -0.07981 | 0.064927 | 4.5815 | 2.1465 | 2.2263 | -0.000591 | -0.043036 | 43.2044 | -78.0329 | 43.333 | 43.2481 | 0.043694 | -77.9984 | -77.9631 | 121.3403 | 121.2747 | 121.2323 | 25.3074 | -121.3551 | 43.2424 | 43.2769 | 43.3122 | 43.2911 | -78.0709
2965.4844 | 121.5591 | -43.4143 | 77.9984 | 1.4211e-13 | -0.035765 | -0.00030992 | 0.061393 | -0.0045596 | 0.059033 | -0.0022889 | -0.0015767 | 0.024301 | -0.0055912 | 0.019711 | 0.012706 | -38.6955 | -17.9467 | -41.1488 | 78.0083 | 77.9428 | 77.9095 | -43.4163 | 0.060571 | 0.014095 | -0.0243 | -0.034533 | 0.009128 | 0.030644 | -0.067994 | -0.002008 | 0.009986 | 4.7188 | 2.2655 | 2.2675 | -0.055539 | -0.088822 | 43.3463 | -78.0329 | 43.4749 | 43.39 | 0.043694 | -77.9892 | -77.9677 | 121.4226 | 121.3571 | 121.3238 | 25.4676 | -121.4147 | 43.3798 | 43.4234 | 43.445 | 43.4284 | -78.0663
2967.2812 | 121.5363 | -43.3548 | 78.0487 | 1.4211e-13 | -0.035124 | -9.6116e-05 | 0.061607 | -0.004346 | 0.059247 | -0.01755 | -0.0015767 | 0.023874 | -0.0053776 | 0.019925 | 0.013133 | -38.5764 | -17.8094 | -41.0527 | 78.0587 | 78.0023 | 77.9645 | -43.3614 | 0.06515 | 0.018674 | -0.028879 | -0.029954 | 0.004549 | 0.035222 | -0.072572 | -0.006571 | 0.009994 | 4.7783 | 2.3021 | 2.3087 | -0.046367 | -0.084233 | 43.2822 | -78.0787 | 43.4199 | 43.3259 | 0.043693 | -78.0442 | -78.0135 | 121.4135 | 121.3571 | 121.3193 | 25.5454 | -121.4101 | 43.3248 | 43.3593 | 43.39 | 43.3735 | -78.1213
2969.0625 | 121.669 | -43.2861 | 77.98 | 1.4211e-13 | -0.035337 | -0.00030992 | 0.06118 | -0.0047732 | 0.05946 | -0.0022889 | -0.0013631 | 0.023874 | -0.0055912 | 0.019925 | 0.013133 | -38.4528 | -17.6903 | -41.0069 | 78.0907 | 78.0252 | 77.9874 | -43.3476 | 0.060571 | 0.027831 | -0.0243 | -0.034533 | -2.9e-05 | 0.039801 | -0.058836 | -0.061498 | 0.11071 | 4.8333 | 2.2792 | 2.3407 | 0.045191 | 0.007324 | 43.2273 | -78.0146 | 43.3467 | 43.2618 | 0.034536 | -77.9801 | -77.9402 | 121.3769 | 121.3114 | 121.2735 | 25.5958 | -121.3277 | 43.2516 | 43.2861 | 43.3259 | 43.314 | -78.0389
2970.8594 | 121.5363 | -43.2632 | 78.1311 | 1.4211e-13 | -0.03491 | 0.00033128 | 0.061393 | -0.0047732 | 0.059888 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.020139 | 0.012706 | -38.2697 | -17.5804 | -40.8787 | 78.1777 | 78.1077 | 78.0744 | -43.2606 | 0.051413 | 0.023253 | -0.0243 | -0.029954 | -2.9e-05 | 0.030644 | -0.072572 | 0.002614 | 0.046634 | 4.9935 | 2.3845 | 2.3819 | -0.02345 | -0.056745 | 43.1907 | -78.1611 | 43.3147 | 43.2389 | 0.048272 | -78.1311 | -78.1005 | 121.441 | 121.3709 | 121.3376 | 25.6828 | -121.3917 | 43.2333 | 43.2632 | 43.2939 | 43.2865 | -78.2037
2972.5625 | 121.5363 | -43.309 | 78.1036 | 1.4211e-13 | -0.035337 | 0.00011748 | 0.061393 | -0.004346 | 0.059674 | 0.0053411 | -0.0013631 | 0.024088 | -0.0055912 | 0.019711 | 0.012706 | -38.2468 | -17.4705 | -40.8787 | 78.132 | 78.0573 | 78.0377 | -43.3064 | 0.051413 | 0.018674 | -0.0243 | -0.039111 | 0.009128 | 0.039801 | -0.072572 | 0.0026 | 0.028316 | 5.0622 | 2.4303 | 2.4277 | -0.046352 | -0.065907 | 43.2364 | -78.1427 | 43.3604 | 43.2847 | 0.048272 | -78.0945 | -78.0638 | 121.441 | 121.3663 | 121.3468 | 25.8385 | -121.4101 | 43.2699 | 43.3181 | 43.3488 | 43.3277 | -78.1762
2974.3438 | 121.637 | -43.2175 | 78.1494 | 1.4211e-13 | -0.035124 | -9.6116e-05 | 0.061821 | -0.0047732 | 0.059674 | 0.0053411 | -0.0011493 | 0.024515 | -0.0058048 | 0.019498 | 0.012706 | -38.0682 | -17.3057 | -40.7551 | 78.2189 | 78.1534 | 78.1201 | -43.224 | 0.055992 | 0.023253 | -0.028879 | -0.029954 | 0.009128 | 0.044379 | -0.067994 | -0.006532 | 0.06953 | 5.1492 | 2.4624 | 2.4689 | 0.004029 | -0.029269 | 43.1495 | -78.1794 | 43.2735 | 43.1886 | 0.039115 | -78.1403 | -78.105 | 121.4364 | 121.3709 | 121.3376 | 25.9118 | -121.3734 | 43.1875 | 43.2266 | 43.2618 | 43.2407 | -78.2174
2976.1406 | 121.6736 | -43.1946 | 78.1631 | 1.4211e-13 | -0.035124 | 0.00011748 | 0.061607 | -0.004346 | 0.059674 | -0.0099194 | -0.0013631 | 0.023874 | -0.0053776 | 0.020139 | 0.01292 | -37.9813 | -17.2141 | -40.6956 | 78.2327 | 78.1626 | 78.1293 | -43.2057 | 0.055992 | 0.023253 | -0.028879 | -0.029954 | 0.009128 | 0.039801 | -0.067994 | -0.011104 | 0.069532 | 5.2133 | 2.499 | 2.5101 | -0.000546 | -0.033844 | 43.1266 | -78.1931 | 43.2506 | 43.1657 | 0.039115 | -78.154 | -78.1233 | 121.4273 | 121.3572 | 121.3239 | 25.9804 | -121.3688 | 43.1646 | 43.2037 | 43.2344 | 43.2178 | -78.2311
2977.9219 | 121.5591 | -43.1717 | 78.2639 | 1.4211e-13 | -0.035124 | -9.6116e-05 | 0.061607 | -0.0045596 | 0.059674 | -0.0099194 | -0.0013631 | 0.024301 | -0.0055912 | 0.020139 | 0.012492 | -37.8485 | -17.1088 | -40.6223 | 78.2693 | 78.2038 | 78.1659 | -43.1691 | 0.055992 | 0.03241 | -0.0243 | -0.034533 | 0.013707 | 0.035222 | -0.067994 | 0.002639 | 0.005451 | 5.3232 | 2.5494 | 2.5467 | -0.060044 | -0.097924 | 43.1037 | -78.2984 | 43.2277 | 43.1474 | 0.043694 | -78.2501 | -78.2286 | 121.441 | 121.3755 | 121.3376 | 26.0629 | -121.4329 | 43.1372 | 43.1854 | 43.2069 | 43.2041 | -78.3318
2979.6875 | 121.5363 | -43.1763 | 78.2501 | 1.4211e-13 | -0.035551 | 0.00033128 | 0.061821 | -0.0045596 | 0.060101 | 0.0053411 | -0.0017903 | 0.023874 | -0.0055912 | 0.020139 | 0.012706 | -37.7569 | -17.0493 | -40.5766 | 78.2739 | 78.2084 | 78.1705 | -43.1691 | 0.051413 | 0.014095 | -0.019721 | -0.034533 | -2.9e-05 | 0.035222 | -0.072572 | 0.007217 | 0.023762 | 5.4194 | 2.5997 | 2.5925 | -0.041732 | -0.079612 | 43.1037 | -78.2847 | 43.2277 | 43.1565 | 0.052851 | -78.2502 | -78.2149 | 121.4502 | 121.3847 | 121.3468 | 26.127 | -121.4192 | 43.1417 | 43.1762 | 43.2115 | 43.1904 | -78.3227
2981.4219 | 121.6599 | -43.071 | 78.3279 | 1.4211e-13 | -0.035337 | 0.00011748 | 0.062034 | -0.004346 | 0.059888 | -0.0099194 | -0.0017903 | 0.024088 | -0.0053776 | 0.019711 | 0.012492 | -37.5921 | -16.8982 | -40.4529 | 78.3655 | 78.2954 | 78.2621 | -43.0775 | 0.060571 | 0.018674 | -0.028879 | -0.029954 | -0.004608 | 0.044379 | -0.067994 | -0.00649 | 0.03751 | 5.4789 | 2.618 | 2.6245 | -0.032552 | -0.06586 | 43.003 | -78.3579 | 43.1316 | 43.0421 | 0.039115 | -78.3325 | -78.2836 | 121.4364 | 121.3664 | 121.3331 | 26.1728 | -121.4054 | 43.041 | 43.0664 | 43.1154 | 43.0897 | -78.3959
2983.2031 | 121.6049 | -43.0252 | 78.3966 | 1.4211e-13 | -0.035337 | 0.00011748 | 0.061607 | -0.004346 | 0.060101 | 0.0053411 | -0.0015767 | 0.023874 | -0.0053776 | 0.020139 | 0.01292 | -37.4456 | -16.7883 | -40.3568 | 78.4295 | 78.3595 | 78.3308 | -43.0179 | 0.055992 | 0.023253 | -0.0243 | -0.034533 | 0.013707 | 0.035222 | -0.058836 | 0.00726 | 0.032943 | 5.5796 | 2.6684 | 2.6612 | -0.037111 | -0.065845 | 42.9664 | -78.4311 | 43.0812 | 43.0009 | 0.034536 | -78.3829 | -78.3614 | 121.4548 | 121.3847 | 121.356 | 26.2369 | -121.4146 | 42.9907 | 43.0389 | 43.0604 | 43.0485 | -78.4554
2984.9219 | 121.5546 | -43.1671 | 78.2867 | 1.4211e-13 | -0.035337 | 0.00054488 | 0.061821 | -0.0045596 | 0.060101 | -0.0099194 | -0.0017903 | 0.024088 | -0.0053776 | 0.020352 | 0.012706 | -37.4731 | -16.7517 | -40.43 | 78.3105 | 78.2404 | 78.2163 | -43.137 | 0.060571 | 0.023253 | -0.019721 | -0.025376 | 0.009128 | 0.039801 | -0.072572 | 0.030114 | 0.023768 | 5.6941 | 2.7371 | 2.707 | -0.0463 | -0.070447 | 43.0945 | -78.3121 | 43.2277 | 43.1474 | 0.052851 | -78.2776 | -78.2469 | 121.4776 | 121.4076 | 121.3834 | 26.4154 | -121.4237 | 43.1417 | 43.1762 | 43.2069 | 43.1904 | -78.3593
2986.7188 | 121.7148 | -43.0298 | 78.3325 | 1.4211e-13 | -0.035124 | 0.00033128 | 0.061821 | -0.004346 | 0.060529 | -0.0099194 | -0.0015767 | 0.024088 | -0.0055912 | 0.020139 | 0.012492 | -37.3769 | -16.683 | -40.3751 | 78.3288 | 78.2679 | 78.2346 | -43.1141 | 0.055992 | 0.023253 | -0.033458 | -0.029954 | -2.9e-05 | 0.044379 | -0.067994 | -0.084321 | -0.003695 | 5.6529 | 2.6547 | 2.739 | -0.064604 | -0.097909 | 42.9618 | -78.3625 | 43.0858 | 42.9963 | 0.034536 | -78.3325 | -78.2881 | 121.3586 | 121.2977 | 121.2644 | 26.3468 | -121.4466 | 42.9998 | 43.0298 | 43.0742 | 43.053 | -78.4005
2988.4219 | 121.6873 | -42.952 | 78.4012 | 1.4211e-13 | -0.035551 | 0.00054488 | 0.061821 | -0.004346 | 0.060315 | 0.0053411 | -0.0015767 | 0.023874 | -0.0053776 | 0.020139 | 0.01292 | -37.2029 | -16.6189 | -40.2378 | 78.4341 | 78.3824 | 78.3445 | -43.0042 | 0.060571 | 0.018674 | -0.019721 | -0.025376 | 0.004549 | 0.035222 | -0.067994 | -0.052247 | 0.032944 | 5.749 | 2.7142 | 2.7665 | -0.018795 | -0.056687 | 42.884 | -78.4266 | 43.0125 | 42.9322 | 0.048273 | -78.3966 | -78.366 | 121.3861 | 121.3344 | 121.2965 | 26.333 | -121.4054 | 42.9266 | 42.9565 | 42.9872 | 42.9706 | -78.4692
2990.2031 | 121.6873 | -42.9382 | 78.4058 | 1.4211e-13 | -0.035337 | 0.00054488 | 0.062034 | -0.0041322 | 0.060742 | -0.0099194 | -0.0013631 | 0.024088 | -0.0055912 | 0.019498 | 0.012706 | -37.0976 | -16.596 | -40.1828 | 78.457 | 78.3961 | 78.3628 | -42.9951 | 0.060571 | 0.018674 | -0.028879 | -0.029954 | 0.004549 | 0.039801 | -0.063415 | -0.056822 | 0.051258 | 5.8406 | 2.7554 | 2.8122 | -0.009636 | -0.042951 | 42.8748 | -78.4357 | 42.9988 | 42.9094 | 0.034536 | -78.4012 | -78.366 | 121.3953 | 121.3344 | 121.301 | 26.3422 | -121.4008 | 42.9083 | 42.9428 | 42.978 | 42.9569 | -78.4692
2991.9844 | 121.5591 | -42.9153 | 78.511 | 1.4211e-13 | -0.035124 | 0.00075848 | 0.061821 | -0.0039186 | 0.060956 | -0.0022889 | -0.0015767 | 0.024088 | -0.0055912 | 0.019925 | 0.012279 | -36.9374 | -16.4816 | -40.1004 | 78.5165 | 78.4511 | 78.4178 | -42.9401 | 0.055992 | 0.014095 | -0.019721 | -0.029954 | 0.013707 | 0.035222 | -0.067994 | -0.024763 | 0.005492 | 5.978 | 2.8149 | 2.8397 | -0.059974 | -0.093292 | 42.8473 | -78.541 | 42.9713 | 42.8956 | 0.048273 | -78.4973 | -78.4758 | 121.4319 | 121.3664 | 121.3331 | 26.4338 | -121.4512 | 42.8854 | 42.9291 | 42.9506 | 42.9294 | -78.579
2993.7031 | 121.6873 | -42.8925 | 78.4744 | 1.4211e-13 | -0.035337 | 0.00075848 | 0.061821 | -0.0039186 | 0.060742 | -0.0099194 | -0.0015767 | 0.024301 | -0.0053776 | 0.020139 | 0.01292 | -36.8641 | -16.3854 | -40.0638 | 78.512 | 78.4465 | 78.4132 | -42.9493 | 0.060571 | 0.018674 | -0.0243 | -0.029954 | -0.004608 | 0.035222 | -0.067994 | -0.056809 | 0.037534 | 6.0283 | 2.8287 | 2.8855 | -0.027932 | -0.06125 | 42.8245 | -78.5044 | 42.953 | 42.8682 | 0.043694 | -78.479 | -78.4392 | 121.4044 | 121.339 | 121.3056 | 26.507 | -121.4237 | 42.8625 | 42.8878 | 42.9277 | 42.9111 | -78.5424
2995.4688 | 121.6507 | -42.8421 | 78.5385 | 1.4211e-13 | -0.035337 | 0.00054488 | 0.061821 | -0.003705 | 0.060742 | -0.0099194 | -0.0017903 | 0.023874 | -0.0053776 | 0.019711 | 0.012706 | -36.6764 | -16.2938 | -39.9448 | 78.5898 | 78.5289 | 78.491 | -42.8577 | 0.060571 | 0.018674 | -0.028879 | -0.025376 | 0.004549 | 0.035222 | -0.077151 | -0.015584 | 0.05128 | 6.1657 | 2.8974 | 2.9129 | -0.009598 | -0.047501 | 42.765 | -78.5639 | 42.9027 | 42.8132 | 0.048272 | -78.534 | -78.5033 | 121.4319 | 121.371 | 121.3331 | 26.5483 | -121.3962 | 42.8167 | 42.8467 | 42.8773 | 42.8608 | -78.6157
2997.25 | 121.6599 | -42.8284 | 78.5385 | 1.4211e-13 | -0.035337 | 0.00075848 | 0.061821 | -0.003705 | 0.060742 | -0.0022889 | -0.0013631 | 0.024088 | -0.0055912 | 0.019925 | 0.012492 | -36.5803 | -16.2481 | -39.9081 | 78.5852 | 78.5198 | 78.491 | -42.8668 | 0.060571 | 0.014095 | -0.019721 | -0.039111 | 0.009128 | 0.035222 | -0.072572 | -0.038475 | 0.046702 | 6.2481 | 2.9202 | 2.9587 | -0.018756 | -0.047501 | 42.7558 | -78.5776 | 42.8889 | 42.8086 | 0.052851 | -78.5294 | -78.5033 | 121.4136 | 121.3481 | 121.3194 | 26.5803 | -121.4054 | 42.7893 | 42.8375 | 42.8636 | 42.8425 | -78.6111
2999.0312 | 121.5912 | -42.9062 | 78.4836 | 1.4211e-13 | -0.035337 | 0.00097228 | 0.061821 | -0.0039186 | 0.060742 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.019711 | 0.01292 | -36.5208 | -16.2023 | -39.9127 | 78.5532 | 78.474 | 78.4406 | -42.9126 | 0.055992 | 0.018674 | -0.0243 | -0.034533 | 0.004549 | 0.035222 | -0.067994 | -0.006444 | 0.069584 | 6.3854 | 2.9935 | 2.9999 | -0.009614 | -0.042934 | 42.8382 | -78.5181 | 42.9622 | 42.8819 | 0.043694 | -78.479 | -78.4484 | 121.4594 | 121.3802 | 121.3468 | 26.7039 | -121.3962 | 42.8717 | 42.9107 | 42.9414 | 42.9249 | -78.5516
3000.75 | 121.6919 | -42.9016 | 78.4424 | 1.4211e-13 | -0.035337 | 0.00097228 | 0.061821 | -0.0039186 | 0.060956 | -0.0099194 | -0.0015767 | 0.024088 | -0.0055912 | 0.019925 | 0.01292 | -36.4292 | -16.0878 | -39.8807 | 78.5349 | 78.4694 | 78.4361 | -42.9172 | 0.055992 | 0.018674 | -0.028879 | -0.029954 | -2.9e-05 | 0.039801 | -0.058836 | -0.015601 | 0.092469 | 6.4724 | 3.021 | 3.0366 | 0.027006 | -0.006314 | 42.8428 | -78.4723 | 42.9576 | 42.8727 | 0.029957 | -78.4424 | -78.4026 | 121.4365 | 121.371 | 121.3377 | 26.8138 | -121.3596 | 42.8717 | 42.9016 | 42.9414 | 42.9203 | -78.5012
3002.5312 | 121.5683 | -42.8558 | 78.5934 | 1.4211e-13 | -0.035124 | 0.00075848 | 0.062034 | -0.0041322 | 0.061383 | -0.0022889 | -0.0013631 | 0.024088 | -0.0058048 | 0.020352 | 0.012706 | -36.2918 | -15.9459 | -39.7937 | 78.5898 | 78.5289 | 78.4956 | -42.8623 | 0.055992 | 0.014095 | -0.028879 | -0.029954 | 0.013707 | 0.039801 | -0.067994 | -0.00643 | -0.003652 | 6.564 | 3.0622 | 3.0686 | -0.06453 | -0.097854 | 42.7878 | -78.6234 | 42.9118 | 42.827 | 0.039115 | -78.5797 | -78.5536 | 121.4456 | 121.3847 | 121.3514 | 26.91 | -121.4557 | 42.8259 | 42.8695 | 42.8956 | 42.8699 | -78.6614
3004.2656 | 121.7377 | -42.746 | 78.6026 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.061821 | -0.0041322 | 0.06117 | 0.0053411 | -0.0013631 | 0.024088 | -0.0053776 | 0.020139 | 0.01292 | -36.1728 | -15.8177 | -39.6563 | 78.6676 | 78.6022 | 78.5734 | -42.7798 | 0.055992 | 0.014095 | -0.0243 | -0.029954 | 0.009128 | 0.039801 | -0.072572 | -0.033872 | 0.065026 | 6.5732 | 3.0897 | 3.1235 | -0.000422 | -0.029173 | 42.6734 | -78.6326 | 42.802 | 42.7217 | 0.048272 | -78.5935 | -78.5628 | 121.4136 | 121.3482 | 121.3194 | 26.9283 | -121.3824 | 42.716 | 42.7551 | 42.7858 | 42.7601 | -78.6752
3006.0469 | 121.5866 | -42.8192 | 78.6346 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.061821 | -0.0039186 | 0.061597 | -0.0022889 | -0.0015767 | 0.023874 | -0.0053776 | 0.020139 | 0.012706 | -36.0721 | -15.781 | -39.638 | 78.6493 | 78.5884 | 78.5505 | -42.8073 | 0.055992 | 0.018674 | -0.019721 | -0.034533 | 0.004549 | 0.035222 | -0.063415 | 0.011896 | 0.014668 | 6.7471 | 3.1812 | 3.1693 | -0.046203 | -0.08411 | 42.7558 | -78.6692 | 42.8752 | 42.7995 | 0.043694 | -78.6301 | -78.5994 | 121.4685 | 121.4077 | 121.3697 | 27.0382 | -121.442 | 42.7847 | 42.8238 | 42.8544 | 42.8379 | -78.6981
3007.7656 | 121.7148 | -42.7414 | 78.5934 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.061607 | -0.0039186 | 0.061383 | -0.0099194 | -0.0015767 | 0.023874 | -0.0055912 | 0.020352 | 0.012492 | -35.9851 | -15.7444 | -39.5556 | 78.6859 | 78.6205 | 78.578 | -42.7844 | 0.055992 | 0.014095 | -0.0243 | -0.034533 | 0.004549 | 0.026065 | -0.077151 | -0.043029 | 0.092494 | 6.7563 | 3.1858 | 3.2288 | 0.027048 | -0.015439 | 42.6642 | -78.628 | 42.7974 | 42.7171 | 0.052851 | -78.5889 | -78.5674 | 121.4273 | 121.3619 | 121.3194 | 26.997 | -121.3779 | 42.7069 | 42.7459 | 42.7675 | 42.7555 | -78.6706
3009.5312 | 121.669 | -42.8467 | 78.5339 | 1.4211e-13 | -0.035124 | 0.00097228 | 0.061821 | -0.003705 | 0.061383 | -0.0022889 | -0.0015767 | 0.024088 | -0.0058048 | 0.019925 | 0.012492 | -35.9622 | -15.694 | -39.6105 | 78.5806 | 78.5243 | 78.491 | -42.876 | 0.060571 | 0.023253 | -0.028879 | -0.029954 | 0.004549 | 0.039801 | -0.072572 | -0.029322 | 0.0467 | 6.8845 | 3.2361 | 3.2655 | -0.0096 | -0.042924 | 42.7741 | -78.5639 | 42.9073 | 42.8178 | 0.043693 | -78.5294 | -78.4941 | 121.4273 | 121.371 | 121.3377 | 27.1526 | -121.4099 | 42.8167 | 42.8512 | 42.8865 | 42.8699 | -78.6065
3011.3281 | 121.6003 | -42.9291 | 78.511 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.061821 | -0.0039186 | 0.061597 | -0.0022889 | -0.0015767 | 0.024301 | -0.0053776 | 0.020352 | 0.012706 | -35.9347 | -15.5887 | -39.6197 | 78.5394 | 78.474 | 78.4269 | -42.9355 | 0.069728 | 0.014095 | -0.0243 | -0.029954 | 0.013707 | 0.039801 | -0.067994 | -0.006451 | 0.028384 | 6.9944 | 3.3094 | 3.3158 | -0.037079 | -0.084135 | 42.8611 | -78.541 | 42.9988 | 42.9048 | 0.043694 | -78.4973 | -78.4712 | 121.4685 | 121.403 | 121.356 | 27.3403 | -121.4466 | 42.8991 | 42.9428 | 42.9689 | 42.9432 | -78.579
3013.0625 | 121.5866 | -42.5354 | 78.8818 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.062248 | -0.0039186 | 0.062024 | -0.01755 | -0.0015767 | 0.023874 | -0.0055912 | 0.020352 | 0.012706 | -35.573 | -15.3049 | -39.2534 | 78.8737 | 78.8128 | 78.7749 | -42.583 | 0.069728 | 0.018674 | -0.019721 | -0.034533 | 0.009128 | 0.030644 | -0.067994 | -0.047551 | -0.008183 | 6.9624 | 3.282 | 3.3295 | -0.069028 | -0.10695 | 42.4674 | -78.9164 | 42.6051 | 42.5157 | 0.048273 | -78.8727 | -78.8512 | 121.4091 | 121.3482 | 121.3103 | 27.2305 | -121.4648 | 42.5009 | 42.5445 | 42.566 | 42.5541 | -78.9498
3014.8438 | 121.5683 | -42.3065 | 79.1245 | 1.4211e-13 | -0.03491 | 0.0011859 | 0.062034 | -0.003705 | 0.062451 | -0.0099194 | -0.0015767 | 0.024301 | -0.0053776 | 0.020139 | 0.012706 | -35.1701 | -15.0851 | -38.9467 | 79.1575 | 79.0921 | 79.0496 | -42.3082 | 0.055992 | 0.023253 | -0.028879 | -0.034533 | 0.004549 | 0.044379 | -0.072572 | -0.001696 | 0.033062 | 7.1364 | 3.3598 | 3.3615 | -0.032328 | -0.074849 | 42.2339 | -79.159 | 42.3625 | 42.2776 | 0.043693 | -79.1199 | -79.0801 | 121.464 | 121.3986 | 121.3561 | 27.2214 | -121.4327 | 42.272 | 42.3111 | 42.3509 | 42.3298 | -79.197
3016.625 | 121.6873 | -42.2699 | 79.1336 | 1.4211e-13 | -0.03491 | 0.0013995 | 0.062034 | -0.0039186 | 0.062024 | -0.0022889 | -0.0013631 | 0.02366 | -0.0053776 | 0.019925 | 0.012706 | -35.0877 | -15.0256 | -38.9192 | 79.1484 | 79.0692 | 79.0313 | -42.3174 | 0.060571 | 0.014095 | -0.0243 | -0.029954 | 0.004549 | 0.030644 | -0.067994 | -0.047476 | 0.01475 | 7.1822 | 3.3507 | 3.3982 | -0.064378 | -0.10232 | 42.2019 | -79.1636 | 42.3305 | 42.2456 | 0.043694 | -79.1291 | -79.103 | 121.4183 | 121.3391 | 121.3012 | 27.2443 | -121.451 | 42.2399 | 42.2744 | 42.3005 | 42.284 | -79.2016
3018.3281 | 121.6095 | -42.1921 | 79.2618 | 1.4211e-13 | -0.035124 | 0.0011859 | 0.062034 | -0.003705 | 0.06181 | 0.0053411 | -0.0015767 | 0.024088 | -0.0053776 | 0.019925 | 0.012706 | -34.8771 | -14.8607 | -38.7498 | 79.2811 | 79.2112 | 79.1732 | -42.1892 | 0.055992 | 0.014095 | -0.019721 | -0.034533 | -0.004608 | 0.030644 | -0.072572 | 0.002915 | 0.01935 | 7.315 | 3.4423 | 3.4393 | -0.050605 | -0.088556 | 42.1195 | -79.2963 | 42.2481 | 42.1724 | 0.052851 | -79.2664 | -79.2311 | 121.4732 | 121.4033 | 121.3653 | 27.3313 | -121.4509 | 42.1575 | 42.1875 | 42.2227 | 42.2062 | -79.3344
3020.0938 | 121.7056 | -42.1371 | 79.2114 | 1.4211e-13 | -0.03491 | 0.0016133 | 0.062248 | -0.003705 | 0.062024 | 0.0053411 | -0.0013631 | 0.02366 | -0.0058048 | 0.020139 | 0.012706 | -34.7627 | -14.7646 | -38.672 | 79.2949 | 79.2341 | 79.2007 | -42.1663 | 0.060571 | 0.018674 | -0.019721 | -0.029954 | 0.009128 | 0.035222 | -0.067994 | -0.029122 | 0.083439 | 7.3745 | 3.4652 | 3.4943 | 0.022643 | -0.01073 | 42.0692 | -79.2414 | 42.1977 | 42.1174 | 0.048273 | -79.2023 | -79.1762 | 121.432 | 121.3712 | 121.3378 | 27.3726 | -121.3777 | 42.1072 | 42.1463 | 42.1724 | 42.1558 | -79.2794
3021.875 | 121.5729 | -42.247 | 79.2206 | 1.4211e-13 | -0.035124 | 0.0016133 | 0.062248 | -0.003705 | 0.062238 | -0.0022889 | -0.0017903 | 0.024088 | -0.0055912 | 0.020139 | 0.012706 | -34.7443 | -14.847 | -38.7086 | 79.2125 | 79.1471 | 79.1137 | -42.2487 | 0.051413 | 0.018674 | -0.019721 | -0.04369 | 0.004549 | 0.039801 | -0.067994 | -0.00168 | -0.008127 | 7.5027 | 3.5384 | 3.5401 | -0.073511 | -0.10688 | 42.179 | -79.2643 | 42.2984 | 42.2273 | 0.048273 | -79.216 | -79.1808 | 121.4595 | 121.3941 | 121.3607 | 27.4 | -121.4693 | 42.2033 | 42.2516 | 42.2868 | 42.2657 | -79.2886
3023.5781 | 121.5683 | -42.2195 | 79.2435 | 1.4211e-13 | -0.03491 | 0.0013995 | 0.062248 | -0.003705 | 0.06181 | -0.0099194 | -0.0015767 | 0.024088 | -0.0055912 | 0.019711 | 0.012279 | -34.6253 | -14.8195 | -38.6308 | 79.2628 | 79.1883 | 79.1549 | -42.2121 | 0.060571 | 0.023253 | -0.019721 | -0.034533 | 0.004549 | 0.039801 | -0.067994 | 0.007485 | 0.019347 | 7.5942 | 3.5888 | 3.5813 | -0.055189 | -0.088559 | 42.1515 | -79.278 | 42.2801 | 42.1998 | 0.048273 | -79.2389 | -79.2037 | 121.4824 | 121.4078 | 121.3745 | 27.4 | -121.4555 | 42.185 | 42.2241 | 42.2593 | 42.2428 | -79.3115
3025.3594 | 121.582 | -42.0868 | 79.3716 | 1.4211e-13 | -0.035124 | 0.0018269 | 0.062248 | -0.0039186 | 0.062238 | -0.0022889 | -0.0015767 | 0.023874 | -0.0053776 | 0.020139 | 0.012279 | -34.4376 | -14.6959 | -38.5209 | 79.3361 | 79.2707 | 79.2236 | -42.1296 | 0.055992 | 0.023253 | -0.0243 | -0.039111 | 0.009128 | 0.035222 | -0.077151 | -0.042845 | -0.035573 | 7.6492 | 3.5659 | 3.6087 | -0.10094 | -0.14805 | 42.0096 | -79.4108 | 42.1428 | 42.0625 | 0.052851 | -79.3625 | -79.3364 | 121.4229 | 121.3575 | 121.3104 | 27.3909 | -121.5013 | 42.0477 | 42.0959 | 42.122 | 42.11 | -79.4488
3027.1406 | 121.5591 | -42.0273 | 79.4449 | 1.4211e-13 | -0.03491 | 0.0020407 | 0.062462 | -0.0034912 | 0.062665 | 0.0053411 | -0.0015767 | 0.023874 | -0.0051638 | 0.020139 | 0.012706 | -34.2316 | -14.5585 | -38.379 | 79.446 | 79.3714 | 79.3426 | -42.0197 | 0.055992 | 0.014095 | -0.019721 | -0.025376 | 0.009128 | 0.039801 | -0.072572 | 0.00754 | 0.001067 | 7.7957 | 3.6483 | 3.6408 | -0.073448 | -0.10225 | 41.9547 | -79.4703 | 42.0833 | 42.0076 | 0.052851 | -79.4358 | -79.4051 | 121.4732 | 121.3987 | 121.3699 | 27.4687 | -121.4646 | 42.0019 | 42.0364 | 42.0671 | 42.0414 | -79.5175
3028.9219 | 121.5591 | -41.8488 | 79.5822 | 1.4211e-13 | -0.034696 | 0.0018269 | 0.062034 | -0.0039186 | 0.062451 | -0.0099194 | -0.0015767 | 0.02366 | -0.0053776 | 0.020352 | 0.012492 | -34.0118 | -14.4441 | -38.1455 | 79.6382 | 79.5592 | 79.5258 | -41.832 | 0.051413 | 0.018674 | -0.028879 | -0.034533 | 0.009128 | 0.044379 | -0.067994 | 0.016748 | 0.05603 | 7.837 | 3.7033 | 3.6865 | -0.023041 | -0.056438 | 41.7808 | -79.6167 | 41.9002 | 41.8199 | 0.039115 | -79.5731 | -79.5378 | 121.487 | 121.4079 | 121.3745 | 27.4047 | -121.4142 | 41.8142 | 41.8579 | 41.8931 | 41.8674 | -79.6502
3030.6875 | 121.6278 | -41.9357 | 79.5044 | 1.4211e-13 | -0.03491 | 0.0020407 | 0.062248 | -0.0034912 | 0.062451 | -0.0099194 | -0.0020039 | 0.023874 | -0.0055912 | 0.020352 | 0.012492 | -33.9706 | -14.467 | -38.1821 | 79.5513 | 79.4813 | 79.4388 | -41.9144 | 0.055992 | 0.018674 | -0.019721 | -0.029954 | 0.009128 | 0.044379 | -0.067994 | 0.021302 | 0.04686 | 7.9651 | 3.7536 | 3.7323 | -0.023064 | -0.065612 | 41.8677 | -79.5343 | 41.9917 | 41.916 | 0.048273 | -79.4953 | -79.46 | 121.487 | 121.4171 | 121.3745 | 27.4688 | -121.4188 | 41.9058 | 41.9449 | 41.9801 | 41.9544 | -79.5724
3032.4062 | 121.5683 | -41.7572 | 79.7241 | 1.4211e-13 | -0.035124 | 0.0020407 | 0.062462 | -0.003705 | 0.062238 | -0.0099194 | -0.0015767 | 0.023874 | -0.0053776 | 0.019925 | 0.012706 | -33.7371 | -14.3662 | -37.9898 | 79.7115 | 79.6462 | 79.6128 | -41.7496 | 0.051413 | 0.023253 | -0.028879 | -0.029954 | 0.004549 | 0.035222 | -0.072572 | 0.007616 | -0.012623 | 8.0201 | 3.7674 | 3.7598 | -0.077949 | -0.11135 | 41.6846 | -79.7541 | 41.8086 | 41.7283 | 0.043693 | -79.7196 | -79.6889 | 121.4687 | 121.4034 | 121.37 | 27.391 | -121.4737 | 41.7272 | 41.7618 | 41.7924 | 41.7805 | -79.7967
3034.2031 | 121.6873 | -40.3931 | 80.983 | 1.4211e-13 | -0.034483 | 0.0022543 | 0.062675 | -0.003705 | 0.062879 | -0.0022889 | -0.0013631 | 0.023874 | -0.0058048 | 0.020139 | 0.01292 | -32.4872 | -13.7069 | -36.7583 | 81.0118 | 80.9374 | 80.8948 | -40.4629 | 0.055992 | 0.018674 | -0.028879 | -0.034533 | 0.009128 | 0.039801 | -0.067994 | -0.069843 | 0.028789 | 7.9059 | 3.6348 | 3.7046 | -0.045542 | -0.088192 | 40.3251 | -81.0175 | 40.4491 | 40.3642 | 0.039115 | -80.9738 | -80.9432 | 121.4048 | 121.3305 | 121.2878 | 26.6861 | -121.4459 | 40.3585 | 40.4022 | 40.4329 | 40.4117 | -81.051
3035.9844 | 121.6919 | -39.8026 | 81.5918 | 1.4211e-13 | -0.03491 | 0.0022543 | 0.062462 | -0.0032776 | 0.062665 | -0.0022889 | -0.0017903 | 0.024088 | -0.0055912 | 0.020352 | 0.012706 | -31.8371 | -13.3452 | -36.1585 | 81.6115 | 81.5464 | 81.5037 | -39.8539 | 0.055992 | 0.018674 | -0.019721 | -0.039111 | -2.9e-05 | 0.035222 | -0.067994 | -0.051361 | 0.019732 | 7.9655 | 3.644 | 3.6954 | -0.045371 | -0.088064 | 39.7346 | -81.6309 | 39.8585 | 39.7828 | 0.048273 | -81.5918 | -81.5566 | 121.4141 | 121.349 | 121.3063 | 26.4573 | -121.4457 | 39.7634 | 39.8025 | 39.8378 | 39.8212 | -81.6598
3037.7031 | 121.5637 | -39.8392 | 81.6284 | 1.4211e-13 | -0.03491 | 0.0024679 | 0.062462 | -0.0034912 | 0.062451 | -0.0099194 | -0.0015767 | 0.02366 | -0.0053776 | 0.020139 | 0.012706 | -31.7226 | -13.2811 | -36.0898 | 81.6482 | 81.5739 | 81.5266 | -39.8264 | 0.051413 | 0.023253 | -0.028879 | -0.039111 | -2.9e-05 | 0.026065 | -0.072572 | 0.012734 | 0.019738 | 8.1166 | 3.7493 | 3.7366 | -0.054518 | -0.10179 | 39.7666 | -81.6675 | 39.8906 | 39.8103 | 0.043693 | -81.6284 | -81.6024 | 121.4873 | 121.4131 | 121.3658 | 26.5581 | -121.4549 | 39.8001 | 39.8391 | 39.8652 | 39.8624 | -81.701
3039.4688 | 121.7102 | -39.1022 | 82.283 | 1.4211e-13 | -0.034483 | 0.0024679 | 0.062675 | -0.0034912 | 0.062665 | -0.0099194 | -0.0013631 | 0.02366 | -0.0055912 | 0.020352 | 0.012492 | -31.0496 | -13.0339 | -35.4397 | 82.2983 | 82.2241 | 82.1722 | -39.1808 | 0.055992 | 0.014095 | -0.028879 | -0.034533 | 0.004549 | 0.030644 | -0.077151 | -0.078637 | 0.015267 | 8.0526 | 3.6625 | 3.7411 | -0.058913 | -0.11081 | 39.025 | -82.3176 | 39.1582 | 39.0733 | 0.048272 | -82.2785 | -82.2524 | 121.4005 | 121.3263 | 121.2744 | 26.0683 | -121.4638 | 39.0676 | 39.1067 | 39.1328 | 39.1163 | -82.3602
3041.2656 | 121.5683 | -38.8458 | 82.6355 | 1.4211e-13 | -0.034696 | 0.0022543 | 0.062889 | -0.0034912 | 0.062665 | -0.0022889 | -0.0015767 | 0.024088 | -0.0055912 | 0.019925 | 0.012279 | -30.6787 | -12.8919 | -35.1055 | 82.6096 | 82.5355 | 82.4973 | -38.8603 | 0.060571 | 0.018674 | -0.0243 | -0.029954 | -2.9e-05 | 0.039801 | -0.072572 | -0.01446 | -0.02588 | 8.1671 | 3.7403 | 3.7548 | -0.10002 | -0.13821 | 38.7733 | -82.6655 | 38.9064 | 38.8215 | 0.048272 | -82.6355 | -82.5957 | 121.4554 | 121.3813 | 121.3431 | 25.9539 | -121.4958 | 38.8159 | 38.8458 | 38.8856 | 38.8645 | -82.7081
3042.9844 | 121.6873 | -38.0402 | 83.3496 | 1.4211e-13 | -0.03491 | 0.0024679 | 0.062889 | -0.0034912 | 0.062665 | -0.0022889 | -0.0013631 | 0.024301 | -0.0055912 | 0.019925 | 0.012492 | -29.8912 | -12.5119 | -34.3455 | 83.3879 | 83.3093 | 83.2711 | -38.0956 | 0.055992 | 0.018674 | -0.0243 | -0.039111 | 0.009128 | 0.026065 | -0.077151 | -0.055444 | 0.038335 | 8.1489 | 3.6946 | 3.7501 | -0.040297 | -0.078536 | 37.963 | -83.3887 | 38.0962 | 38.0159 | 0.052851 | -83.3405 | -83.3235 | 121.4281 | 121.3495 | 121.3112 | 25.5282 | -121.4452 | 38.001 | 38.0493 | 38.0662 | 38.0588 | -83.4268
3044.6875 | 121.6827 | -37.1658 | 84.1919 | 1.4211e-13 | -0.034696 | 0.0026817 | 0.062675 | -0.0034912 | 0.062665 | 0.0053411 | -0.0017903 | 0.023874 | -0.0055912 | 0.020352 | 0.012279 | -29.0305 | -12.0541 | -33.5306 | 84.2212 | 84.1473 | 84.109 | -37.2485 | 0.060571 | 0.009516 | -0.028879 | -0.039111 | 0.004549 | 0.039801 | -0.067994 | -0.08267 | 0.029315 | 8.1353 | 3.6353 | 3.7179 | -0.04464 | -0.082937 | 37.0978 | -84.231 | 37.2264 | 37.137 | 0.039115 | -84.1873 | -84.1521 | 121.387 | 121.3131 | 121.2748 | 25.1118 | -121.4404 | 37.1267 | 37.1704 | 37.2056 | 37.1753 | -84.2599
3046.4688 | 121.6553 | -36.7996 | 84.5856 | 1.4211e-13 | -0.034269 | 0.0026817 | 0.062675 | -0.003705 | 0.062451 | -0.0022889 | -0.0013631 | 0.02366 | -0.0055912 | 0.020352 | 0.012492 | -28.5727 | -11.8022 | -33.0636 | 84.6882 | 84.6189 | 84.5714 | -36.7815 | 0.060571 | 0.014095 | -0.0243 | -0.029954 | 0.004549 | 0.026065 | -0.072572 | 0.018169 | 0.10263 | 8.227 | 3.736 | 3.7179 | 0.033314 | -0.014175 | 36.727 | -84.6155 | 36.8602 | 36.7753 | 0.048272 | -84.581 | -84.5595 | 121.4878 | 121.4185 | 121.371 | 24.9974 | -121.367 | 36.7697 | 36.8042 | 36.8257 | 36.8137 | -84.6581
3048.25 | 121.5958 | -35.8154 | 85.6567 | 1.4211e-13 | -0.03491 | 0.0026817 | 0.062889 | -0.003705 | 0.062665 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.020566 | 0.012065 | -27.657 | -11.2894 | -32.1891 | 85.5901 | 85.5164 | 85.4596 | -35.884 | 0.060571 | 0.014095 | -0.028879 | -0.039111 | 0.004549 | 0.030644 | -0.072572 | -0.068554 | -0.06659 | 8.1584 | 3.6263 | 3.6948 | -0.14038 | -0.19709 | 35.7429 | -85.6958 | 35.876 | 35.7866 | 0.043693 | -85.6522 | -85.6261 | 121.4056 | 121.3318 | 121.2751 | 24.526 | -121.5407 | 35.7763 | 35.82 | 35.8461 | 35.8295 | -85.7293
3049.9688 | 121.637 | -35.8429 | 85.524 | 1.4211e-13 | -0.034483 | 0.0031091 | 0.062889 | -0.003705 | 0.062879 | -0.0099194 | -0.0015767 | 0.024088 | -0.0053776 | 0.020352 | 0.012492 | -27.6433 | -11.2894 | -32.1983 | 85.5261 | 85.4477 | 85.4047 | -35.9481 | 0.055992 | 0.014095 | -0.028879 | -0.04369 | -0.004608 | 0.030644 | -0.077151 | -0.10519 | 0.002064 | 8.1996 | 3.6446 | 3.7498 | -0.076317 | -0.11929 | 35.7657 | -85.5677 | 35.8989 | 35.814 | 0.048272 | -85.5286 | -85.4933 | 121.3689 | 121.2906 | 121.2476 | 24.5535 | -121.4721 | 35.7992 | 35.8383 | 35.8735 | 35.857 | -85.6011
3051.75 | 121.5637 | -35.4721 | 85.9726 | 1.4211e-13 | -0.034269 | 0.0028953 | 0.062675 | -0.0034912 | 0.063092 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.020139 | 0.012279 | -27.1122 | -10.9964 | -31.7313 | 85.9839 | 85.9101 | 85.8717 | -35.4856 | 0.051413 | 0.018674 | -0.028879 | -0.034533 | -2.9e-05 | 0.026065 | -0.072572 | -0.013511 | 0.011294 | 8.3599 | 3.7408 | 3.7543 | -0.062454 | -0.10088 | 35.3995 | -86.0071 | 35.5235 | 35.4432 | 0.043693 | -85.9726 | -85.9465 | 121.456 | 121.3822 | 121.3438 | 24.4757 | -121.4582 | 35.4376 | 35.4721 | 35.4982 | 35.4908 | -86.0452
3053.5 | 121.637 | -34.9823 | 86.3892 | 1.4211e-13 | -0.034483 | 0.0031091 | 0.063103 | -0.003705 | 0.063092 | -0.0099194 | -0.0013631 | 0.023874 | -0.0058048 | 0.020352 | 0.012279 | -26.6177 | -10.7308 | -31.2323 | 86.4829 | 86.4092 | 86.3571 | -34.9819 | 0.051413 | 0.009516 | -0.033458 | -0.034533 | -2.9e-05 | 0.026065 | -0.072572 | 0.000364 | 0.093774 | 8.3646 | 3.75 | 3.7497 | 0.020084 | -0.032109 | 34.9097 | -86.4237 | 35.0337 | 34.9488 | 0.039114 | -86.3892 | -86.3631 | 121.4652 | 121.3915 | 121.3394 | 24.2515 | -121.3711 | 34.9478 | 34.9823 | 35.0084 | 34.9918 | -86.4617
3055.2969 | 121.6782 | -34.5428 | 86.8469 | 1.4211e-13 | -0.034269 | 0.0033227 | 0.063103 | -0.0034912 | 0.062665 | -0.0099194 | -0.0015767 | 0.023874 | -0.0055912 | 0.020566 | 0.012279 | -26.1828 | -10.5294 | -30.8202 | 86.8996 | 86.8259 | 86.7783 | -34.5698 | 0.060571 | 0.014095 | -0.028879 | -0.039111 | -2.9e-05 | 0.030644 | -0.08173 | -0.026986 | 0.052643 | 8.3601 | 3.7226 | 3.7496 | -0.020998 | -0.068641 | 34.4611 | -86.886 | 34.6034 | 34.514 | 0.052851 | -86.847 | -86.8163 | 121.4424 | 121.3688 | 121.3211 | 24.0135 | -121.4168 | 34.5037 | 34.5428 | 34.5735 | 34.5569 | -86.9287
3057.0781 | 121.5591 | -34.5062 | 86.9568 | 1.4211e-13 | -0.034269 | 0.0033227 | 0.062889 | -0.003705 | 0.063092 | -0.01755 | -0.0013631 | 0.023447 | -0.0055912 | 0.019925 | 0.012492 | -26.0454 | -10.4378 | -30.7424 | 86.9545 | 86.8763 | 86.8195 | -34.524 | 0.055992 | 0.014095 | -0.028879 | -0.039111 | -2.9e-05 | 0.030644 | -0.072572 | -0.017817 | -0.002279 | 8.4608 | 3.7638 | 3.7816 | -0.080493 | -0.1373 | 34.4337 | -86.9959 | 34.5622 | 34.4773 | 0.043693 | -86.9568 | -86.9261 | 121.4607 | 121.3825 | 121.3257 | 24.0684 | -121.4808 | 34.4671 | 34.5062 | 34.5369 | 34.5203 | -87.0294
3058.8594 | 121.5683 | -34.3735 | 87.0895 | 1.4211e-13 | -0.034269 | 0.0031091 | 0.063316 | -0.003705 | 0.062879 | -0.0022889 | -0.0015767 | 0.02366 | -0.0058048 | 0.019925 | 0.012706 | -25.8302 | -10.3188 | -30.541 | 87.1148 | 87.0457 | 86.9935 | -34.3546 | 0.046835 | 0.004938 | -0.033458 | -0.034533 | -2.9e-05 | 0.030644 | -0.072572 | 0.018851 | 0.025212 | 8.5433 | 3.8325 | 3.8137 | -0.043824 | -0.096062 | 34.3009 | -87.1241 | 34.4203 | 34.34 | 0.039114 | -87.0896 | -87.0589 | 121.4882 | 121.4192 | 121.367 | 24.0547 | -121.4442 | 34.3389 | 34.3734 | 34.4041 | 34.3784 | -87.1621
3060.5625 | 121.5683 | -34.4604 | 86.9934 | 1.4211e-13 | -0.034269 | 0.0033227 | 0.063316 | -0.0032776 | 0.062879 | -0.0099194 | -0.0013631 | 0.023874 | -0.0058048 | 0.019925 | 0.012492 | -25.8668 | -10.3691 | -30.6234 | 86.982 | 86.9083 | 86.8515 | -34.4966 | 0.051413 | 0.018674 | -0.0243 | -0.034533 | -2.9e-05 | 0.026065 | -0.08173 | -0.036121 | -0.01143 | 8.5936 | 3.8371 | 3.8732 | -0.085061 | -0.14187 | 34.3787 | -87.0279 | 34.5119 | 34.4361 | 0.05743 | -86.9934 | -86.9673 | 121.4424 | 121.3688 | 121.312 | 24.0913 | -121.49 | 34.4259 | 34.4604 | 34.4865 | 34.4791 | -87.0751
3062.3438 | 121.6736 | -33.7784 | 87.5839 | 1.4211e-13 | -0.033842 | 0.0035363 | 0.06353 | -0.0034912 | 0.063092 | -0.0022889 | -0.0015767 | 0.02366 | -0.0058048 | 0.020139 | 0.012279 | -25.2076 | -10.0486 | -30.0099 | 87.6092 | 87.5357 | 87.4788 | -33.8601 | 0.060571 | 0.014095 | -0.0243 | -0.039111 | -2.9e-05 | 0.039801 | -0.077151 | -0.081718 | 0.025294 | 8.5708 | 3.7685 | 3.8502 | -0.048264 | -0.10511 | 33.7012 | -87.623 | 33.839 | 33.7541 | 0.052851 | -87.584 | -87.5441 | 121.3876 | 121.314 | 121.2572 | 23.7298 | -121.444 | 33.7393 | 33.7784 | 33.8182 | 33.7925 | -87.6611
3064.125 | 121.669 | -33.2611 | 88.0829 | 1.4211e-13 | -0.034055 | 0.0035363 | 0.06353 | -0.0039186 | 0.062879 | -0.0022889 | -0.0017903 | 0.02366 | -0.0053776 | 0.019925 | 0.012065 | -24.6994 | -9.7785 | -29.5154 | 88.1266 | 88.0439 | 88.0008 | -33.3473 | 0.051413 | 0.009516 | -0.028879 | -0.048268 | -2.9e-05 | 0.026065 | -0.077151 | -0.086152 | 0.043689 | 8.5618 | 3.7457 | 3.8318 | -0.038966 | -0.082116 | 33.184 | -88.1312 | 33.3125 | 33.2322 | 0.048272 | -88.0829 | -88.0568 | 121.3877 | 121.305 | 121.2619 | 23.4826 | -121.4301 | 33.2128 | 33.2611 | 33.2872 | 33.2706 | -88.16
3065.9062 | 121.5866 | -32.2632 | 89.1403 | 1.4211e-13 | -0.034055 | 0.0039637 | 0.063316 | -0.003705 | 0.062879 | -0.0022889 | -0.0015767 | 0.024088 | -0.0058048 | 0.020139 | 0.012492 | -23.7791 | -9.4168 | -28.586 | 89.1109 | 89.0238 | 88.9623 | -32.3674 | 0.051413 | 0.009516 | -0.028879 | -0.039111 | -2.9e-05 | 0.030644 | -0.086309 | -0.10419 | -0.029392 | 8.4841 | 3.6771 | 3.7813 | -0.11651 | -0.17804 | 32.1769 | -89.1794 | 32.3146 | 32.2343 | 0.05743 | -89.1403 | -89.1097 | 121.3741 | 121.287 | 121.2255 | 22.8464 | -121.5077 | 32.2241 | 32.2632 | 32.2938 | 32.2727 | -89.2266
3067.6719 | 121.5454 | -31.5399 | 89.9094 | 1.4211e-13 | -0.033842 | 0.0039637 | 0.063316 | -0.0034912 | 0.062879 | 0.0053411 | -0.0013631 | 0.023874 | -0.0053776 | 0.020139 | 0.012279 | -22.9962 | -8.904 | -27.794 | 89.9305 | 89.8434 | 89.7818 | -31.5523 | 0.046835 | 0.014095 | -0.028879 | -0.04369 | 0.004549 | 0.026065 | -0.072572 | -0.012404 | 0.021097 | 8.5437 | 3.7459 | 3.7583 | -0.065926 | -0.12752 | 31.4673 | -89.9531 | 31.5868 | 31.511 | 0.043693 | -89.9048 | -89.8833 | 121.4704 | 121.3834 | 121.3218 | 22.6359 | -121.4617 | 31.4962 | 31.5445 | 31.566 | 31.554 | -89.9819
3069.3906 | 121.6507 | -30.9769 | 90.3854 | 1.4211e-13 | -0.034055 | 0.0039637 | 0.063957 | -0.0039186 | 0.062879 | -0.0022889 | -0.0015767 | 0.02366 | -0.0058048 | 0.020352 | 0.012492 | -22.4376 | -8.7163 | -27.2354 | 90.4936 | 90.4112 | 90.3496 | -30.98 | 0.046835 | 0.009516 | -0.028879 | -0.039111 | 0.004549 | 0.021486 | -0.072572 | -0.003088 | 0.10816 | 8.5392 | 3.7414 | 3.7445 | 0.025787 | -0.035844 | 30.9043 | -90.4245 | 31.0237 | 30.948 | 0.043693 | -90.3809 | -90.364 | 121.4705 | 121.3881 | 121.3265 | 22.2606 | -121.3654 | 30.9378 | 30.9814 | 30.9984 | 30.9864 | -90.458
3071.1875 | 121.5225 | -30.5969 | 90.8478 | 1.4211e-13 | -0.034055 | 0.0041775 | 0.063316 | -0.0039186 | 0.062665 | -0.02518 | -0.0017903 | 0.024088 | -0.0058048 | 0.020352 | 0.012706 | -22.0118 | -8.4736 | -26.8554 | 90.8873 | 90.7959 | 90.7434 | -30.5816 | 0.051413 | 0.004938 | -0.028879 | -0.034533 | -0.009187 | 0.026065 | -0.072572 | 0.015335 | 0.039565 | 8.5851 | 3.7415 | 3.7261 | -0.051924 | -0.10443 | 30.5244 | -90.8823 | 30.6483 | 30.568 | 0.043693 | -90.857 | -90.8217 | 121.4843 | 121.3928 | 121.3403 | 22.1233 | -121.4294 | 30.5624 | 30.5877 | 30.623 | 30.6019 | -90.9203
3072.9219 | 121.6553 | -30.2216 | 91.1179 | 1.4211e-13 | -0.033842 | 0.0041775 | 0.06353 | -0.0039186 | 0.062665 | -0.01755 | -0.0017903 | 0.02366 | -0.0053776 | 0.020352 | 0.012279 | -21.7051 | -8.4186 | -26.5624 | 91.1529 | 91.0752 | 91.0181 | -30.3069 | 0.051413 | 0.009516 | -0.038036 | -0.04369 | -2.9e-05 | 0.026065 | -0.08173 | -0.085296 | 0.03503 | 8.5165 | 3.6591 | 3.7444 | -0.042691 | -0.09979 | 30.1398 | -91.1615 | 30.273 | 30.1835 | 0.043694 | -91.1179 | -91.0918 | 121.3744 | 121.2967 | 121.2396 | 21.8029 | -121.4247 | 30.1779 | 30.2215 | 30.2476 | 30.2311 | -91.1996
3074.6875 | 121.5317 | -30.1987 | 91.2781 | 1.4211e-13 | -0.033842 | 0.0041775 | 0.063957 | -0.003705 | 0.062879 | -0.0099194 | -0.0015767 | 0.02366 | -0.0055912 | 0.020352 | 0.012706 | -21.5815 | -8.3912 | -26.4342 | 91.2399 | 91.1622 | 91.1096 | -30.2244 | 0.046835 | 0.014095 | -0.038036 | -0.039111 | -0.004608 | 0.026065 | -0.077151 | -0.025764 | -0.038197 | 8.6172 | 3.7644 | 3.7902 | -0.11591 | -0.16844 | 30.1215 | -91.3172 | 30.2455 | 30.1606 | 0.039115 | -91.2827 | -91.252 | 121.4385 | 121.3608 | 121.3083 | 21.8075 | -121.5025 | 30.1596 | 30.1941 | 30.2247 | 30.2128 | -91.3552
3076.4219 | 121.5179 | -30.1437 | 91.2964 | 1.4211e-13 | -0.033414 | 0.0041775 | 0.06353 | -0.0034912 | 0.062665 | -0.0022889 | -0.0017903 | 0.02366 | -0.0058048 | 0.020352 | 0.012492 | -21.3754 | -8.2813 | -26.187 | 91.4596 | 91.3774 | 91.3157 | -30.023 | 0.046835 | 0.018674 | -0.038036 | -0.04369 | -0.009187 | 0.030644 | -0.077151 | 0.12078 | 0.16325 | 8.7683 | 3.9567 | 3.8359 | 0.08099 | 0.019291 | 30.0666 | -91.3401 | 30.1906 | 30.1057 | 0.039115 | -91.3056 | -91.2657 | 121.6034 | 121.5211 | 121.4594 | 21.8625 | -121.3193 | 30.1 | 30.1346 | 30.1744 | 30.1624 | -91.3735
3078.2188 | 121.5271 | -29.2877 | 92.1524 | 1.4211e-13 | -0.033414 | 0.0043911 | 0.063744 | -0.0034912 | 0.062879 | -0.0099194 | -0.0017903 | 0.023874 | -0.0055912 | 0.020139 | 0.012279 | -20.7848 | -7.915 | -25.5506 | 92.1372 | 92.0367 | 91.9796 | -29.3407 | 0.055992 | 0.009516 | -0.033458 | -0.04369 | -0.004608 | 0.030644 | -0.090888 | -0.052981 | -0.015162 | 8.5029 | 3.7371 | 3.7901 | -0.11566 | -0.17283 | 29.1968 | -92.1961 | 29.3437 | 29.2543 | 0.05743 | -92.157 | -92.1218 | 121.425 | 121.3245 | 121.2673 | 21.3727 | -121.4931 | 29.244 | 29.2831 | 29.3184 | 29.2972 | -92.2433
3080 | 121.6187 | -28.8437 | 92.5095 | 1.4211e-13 | -0.033628 | 0.0043911 | 0.064171 | -0.0039186 | 0.062879 | -0.0099194 | -0.0015767 | 0.024088 | -0.0058048 | 0.020566 | 0.012492 | -20.2629 | -7.6632 | -25.0882 | 92.5905 | 92.5084 | 92.4512 | -28.8691 | 0.051413 | 0.009516 | -0.038036 | -0.048268 | -2.9e-05 | 0.030644 | -0.08173 | -0.025383 | 0.081043 | 8.5808 | 3.7555 | 3.7808 | -0.001089 | -0.058289 | 28.762 | -92.5577 | 28.8951 | 28.8057 | 0.043694 | -92.5095 | -92.4788 | 121.4342 | 121.3521 | 121.2949 | 21.1805 | -121.3785 | 28.7954 | 28.8437 | 28.8743 | 28.8532 | -92.5912
3081.7812 | 121.5546 | -27.4612 | 93.956 | 1.4211e-13 | -0.033414 | 0.0046047 | 0.063957 | -0.0034912 | 0.062451 | 0.0053411 | -0.0015767 | 0.023874 | -0.0055912 | 0.020139 | 0.012279 | -19.0038 | -7.0039 | -23.8155 | 93.9869 | 93.8958 | 93.7973 | -27.4817 | 0.051413 | 0.014095 | -0.028879 | -0.052847 | -0.009187 | 0.021486 | -0.077151 | -0.020414 | 0.030917 | 8.4574 | 3.6458 | 3.6662 | -0.060208 | -0.15871 | 27.3841 | -94.0088 | 27.5127 | 27.4324 | 0.048272 | -93.9652 | -93.9345 | 121.4482 | 121.357 | 121.2585 | 20.4574 | -121.4377 | 27.4084 | 27.4521 | 27.4827 | 27.4753 | -94.0331
3083.4844 | 121.6415 | -27.0538 | 94.3588 | 1.4211e-13 | -0.033414 | 0.0050321 | 0.064171 | -0.0034912 | 0.062451 | -0.0099194 | -0.0013631 | 0.023874 | -0.0055912 | 0.020352 | 0.012492 | -18.665 | -6.7795 | -23.408 | 94.3807 | 94.2896 | 94.1819 | -27.0879 | 0.042256 | 0.014095 | -0.033458 | -0.04369 | -0.004608 | 0.026065 | -0.08173 | -0.034037 | 0.021827 | 8.3888 | 3.6458 | 3.6799 | -0.069253 | -0.17694 | 26.9721 | -94.4025 | 27.0961 | 27.0204 | 0.048272 | -94.3634 | -94.3328 | 121.4345 | 121.3434 | 121.2357 | 20.2743 | -121.4467 | 27.0101 | 27.0492 | 27.0799 | 27.0679 | -94.4406
3085.2656 | 121.5179 | -26.6556 | 94.812 | 1.4211e-13 | -0.033201 | 0.0048185 | 0.064171 | -0.003705 | 0.062238 | -0.0099194 | -0.0015767 | 0.023874 | -0.0053776 | 0.020352 | 0.012706 | -18.2301 | -6.5872 | -22.9868 | 94.811 | 94.72 | 94.6123 | -26.6483 | 0.046835 | 0.014095 | -0.038036 | -0.048268 | -0.004608 | 0.021486 | -0.077151 | 0.007286 | -0.000991 | 8.4255 | 3.6688 | 3.6615 | -0.09202 | -0.19974 | 26.5784 | -94.8603 | 26.7024 | 26.6175 | 0.039115 | -94.8166 | -94.7905 | 121.4666 | 121.3756 | 121.2679 | 20.0684 | -121.4603 | 26.6073 | 26.651 | 26.6771 | 26.6697 | -94.8892
3087.0469 | 121.6141 | -26.5686 | 94.7891 | 1.4211e-13 | -0.033628 | 0.0046047 | 0.064599 | -0.0034912 | 0.062238 | -0.0099194 | -0.0017903 | 0.02366 | -0.0055912 | 0.020352 | 0.012492 | -18.1797 | -6.5552 | -22.9456 | 94.8339 | 94.7429 | 94.6306 | -26.6346 | 0.051413 | 0.004938 | -0.038036 | -0.04369 | -0.009187 | 0.026065 | -0.08173 | -0.065952 | 0.044789 | 8.3889 | 3.623 | 3.689 | -0.046237 | -0.15854 | 26.4869 | -94.8328 | 26.62 | 26.5306 | 0.043694 | -94.7983 | -94.7631 | 121.4025 | 121.3115 | 121.1992 | 20.0135 | -121.4237 | 26.5249 | 26.5594 | 26.5947 | 26.5735 | -94.8709
3088.8281 | 121.6415 | -26.8982 | 94.455 | 1.4211e-13 | -0.033201 | 0.0048185 | 0.064385 | -0.0034912 | 0.062238 | -0.0022889 | -0.0015767 | 0.023447 | -0.0051638 | 0.020352 | 0.012065 | -18.1935 | -6.5735 | -22.9776 | 94.7561 | 94.6696 | 94.5619 | -26.7078 | 0.042256 | 0.014095 | -0.033458 | -0.04369 | -0.009187 | 0.026065 | -0.077151 | 0.19037 | 0.30112 | 8.7047 | 3.9205 | 3.7302 | 0.21467 | 0.10695 | 26.821 | -94.4986 | 26.9404 | 26.8647 | 0.043693 | -94.4641 | -94.4289 | 121.6543 | 121.5678 | 121.4601 | 20.3247 | -121.1628 | 26.8545 | 26.889 | 26.9243 | 26.9123 | -94.5321
3090.5312 | 121.5408 | -26.6052 | 94.812 | 1.4211e-13 | -0.033201 | 0.0054595 | 0.064599 | -0.003705 | 0.062451 | -0.0099194 | -0.0015767 | 0.02366 | -0.0055912 | 0.020566 | 0.012065 | -18.0012 | -6.578 | -22.8403 | 94.8889 | 94.7978 | 94.6901 | -26.5705 | 0.042256 | 0.009516 | -0.028879 | -0.04369 | -0.009187 | 0.021486 | -0.08173 | 0.034774 | 0.076842 | 8.6041 | 3.7649 | 3.7302 | -0.014178 | -0.1219 | 26.5235 | -94.8557 | 26.6475 | 26.5763 | 0.052851 | -94.8212 | -94.7905 | 121.4941 | 121.4031 | 121.2953 | 20.0272 | -121.3825 | 26.5615 | 26.596 | 26.6267 | 26.6147 | -94.8937
3092.3281 | 121.463 | -47.3465 | 73.8007 | 1.4211e-13 | -0.034055 | 0.0037501 | 0.063744 | -0.0022094 | 0.066297 | -0.0099194 | -0.0015767 | 0.023874 | -0.0055912 | 0.020352 | 0.012279 | -34.0072 | -15.4697 | -39.606 | 76.0442 | 75.8915 | 75.9362 | -45.5089 | 0.060571 | 0.023253 | -0.010564 | -0.025376 | 0.009128 | 0.044379 | -0.058836 | 1.8376 | 2.2435 | 13.3393 | 7.7405 | 5.9029 | 2.0908 | 2.1355 | 47.2877 | -73.826 | 47.4071 | 47.3359 | 0.048272 | -73.7915 | -73.7563 | 123.3907 | 123.238 | 123.2826 | 31.8768 | -119.3095 | 47.3211 | 47.3556 | 47.3909 | 47.3697 | -73.8595
3094.0938 | 121.257 | -45.7809 | 75.3204 | 1.4211e-13 | -0.034055 | 0.0039637 | 0.06353 | -0.0019956 | 0.066297 | 0.0053411 | -0.0013631 | 0.02366 | -0.0058048 | 0.020352 | 0.012279 | -33.2747 | -15.1171 | -38.9055 | 76.589 | 76.5005 | 76.4352 | -44.6343 | 0.055992 | 0.027831 | -0.019721 | -0.029954 | 0.009128 | 0.044379 | -0.063415 | 1.1466 | 1.2686 | 12.5063 | 6.8755 | 5.7288 | 1.18 | 1.1148 | 45.7175 | -75.3504 | 45.8369 | 45.7612 | 0.043694 | -75.3113 | -75.2761 | 122.37 | 122.2814 | 122.2162 | 30.6638 | -119.9547 | 45.751 | 45.7901 | 45.8253 | 45.8088 | -75.3839
3095.7969 | 121.1609 | -49.7726 | 71.2509 | 1.4211e-13 | -0.034483 | 0.0037501 | 0.063744 | -0.001782 | 0.067579 | -0.0022889 | -0.0013631 | 0.02366 | -0.0060184 | 0.020352 | 0.012492 | -36.4658 | -16.9669 | -42.2476 | 72.5875 | 72.4389 | 72.4793 | -48.5768 | 0.078886 | 0.03241 | -0.001407 | -0.01164 | 0.018285 | 0.053537 | -0.054257 | 1.1959 | 1.3366 | 13.3068 | 7.525 | 6.3291 | 1.188 | 1.2284 | 49.7184 | -71.2626 | 49.8515 | 49.7712 | 0.05285 | -71.2326 | -71.1974 | 122.3602 | 122.2116 | 122.252 | 32.8058 | -119.8277 | 49.761 | 49.7909 | 49.8262 | 49.8051 | -71.3052
3097.5781 | 121.2524 | -29.9789 | 91.9693 | 1.4211e-13 | -0.033842 | 0.0048185 | 0.064385 | -0.0028504 | 0.064161 | -0.0099194 | -0.0013631 | 0.023874 | -0.0058048 | 0.020352 | 0.011851 | -25.908 | -11.1887 | -31.3467 | 84.9721 | 84.8845 | 84.7957 | -36.177 | 0.060571 | 0.023253 | -0.0243 | -0.029954 | 0.004549 | 0.039801 | -0.063415 | -6.1981 | -6.9972 | 4.0709 | -1.3678 | 4.8303 | -7.0848 | -7.1736 | 29.9155 | -91.9993 | 30.0395 | 29.9546 | 0.039115 | -91.9648 | -91.9295 | 114.951 | 114.8634 | 114.7747 | 18.7902 | -128.1463 | 29.949 | 29.9835 | 30.0187 | 30.0022 | -92.0327
3099.3438 | 121.0693 | -53.7186 | 67.1951 | 1.4211e-13 | -0.034269 | 0.0035363 | 0.06353 | -0.0015684 | 0.067579 | 0.0053411 | -0.0015767 | 0.024088 | -0.0058048 | 0.020352 | 0.012279 | -38.288 | -18.1115 | -44.436 | 69.8817 | 69.8244 | 69.8008 | -51.0814 | 0.078886 | 0.041567 | -0.001407 | -0.007062 | 0.027442 | 0.058115 | -0.049678 | 2.6371 | 2.6866 | 15.4306 | 9.2825 | 6.6454 | 2.6292 | 2.6057 | 53.6689 | -67.2022 | 53.7975 | 53.7172 | 0.048271 | -67.1677 | -67.137 | 123.6003 | 123.5429 | 123.5194 | 35.607 | -118.2766 | 53.7115 | 53.746 | 53.7767 | 53.7601 | -67.2448
3101.0625 | 120.6299 | -79.6783 | 40.5991 | 1.4211e-13 | -0.036406 | 0.0020407 | 0.062034 | 0.00078203 | 0.072921 | -0.0022889 | -0.0013631 | 0.023874 | -0.0058048 | 0.020566 | 0.012492 | -60.8183 | -30.5928 | -68.4171 | 42.3015 | 42.1997 | 42.2972 | -78.2619 | 0.11094 | 0.059882 | 0.021487 | 0.015831 | 0.054914 | 0.085587 | -0.017627 | 1.4164 | 1.7024 | 18.8601 | 11.2613 | 9.8449 | 1.6007 | 1.6981 | 79.6607 | -40.5832 | 79.7893 | 79.6998 | 0.039114 | -40.5441 | -40.5135 | 121.9798 | 121.8781 | 121.9755 | 49.0855 | -118.861 | 79.6942 | 79.7333 | 79.7639 | 79.7382 | -40.6167
3102.8594 | 120.2774 | -73.2651 | 46.8338 | 1.4211e-13 | -0.035337 | 0.0022543 | 0.061607 | 0.00099563 | 0.072707 | -0.0099194 | -0.0013631 | 0.023874 | -0.0055912 | 0.020566 | 0.012279 | -58.9961 | -29.7412 | -66.659 | 43.9268 | 43.926 | 43.9042 | -76.1923 | 0.10636 | 0.064461 | 0.026066 | 0.015831 | 0.045757 | 0.085587 | -0.022205 | -2.9272 | -2.907 | 14.269 | 6.6061 | 9.5332 | -2.9078 | -2.9296 | 73.2429 | -46.818 | 73.3714 | 73.2911 | 0.048271 | -46.788 | -46.7482 | 117.1919 | 117.1911 | 117.1693 | 43.5239 | -123.0261 | 73.2809 | 73.3108 | 73.3507 | 73.3295 | -46.856
3104.5781 | 120.0531 | -63.0341 | 57.2159 | 1.4211e-13 | -0.035551 | 0.0033227 | 0.062248 | -7.2572e-05 | 0.069716 | -0.0022889 | -0.0015767 | 0.024088 | -0.0062322 | 0.020352 | 0.012279 | -46.4971 | -22.974 | -53.3866 | 58.5548 | 58.5007 | 58.4917 | -61.3657 | 0.12467 | 0.087354 | 0.044381 | 0.034145 | 0.077807 | 0.10848 | -0.008469 | 1.6684 | 1.3389 | 16.537 | 9.6475 | 7.9791 | 1.2848 | 1.2758 | 63.0256 | -57.1817 | 63.1587 | 63.0784 | 0.05285 | -57.1381 | -57.1074 | 121.5888 | 121.5348 | 121.5257 | 40.06 | -118.5816 | 63.0682 | 63.1119 | 63.1425 | 63.1214 | -57.2244
3106.375 | 119.1513 | -59.7702 | 59.3033 | 1.4211e-13 | -0.035124 | 0.0028953 | 0.061821 | -7.2572e-05 | 0.06993 | -0.0022889 | -0.0011493 | 0.024088 | -0.0062322 | 0.020566 | 0.012492 | -50.3383 | -25.0344 | -57.3743 | 53.3537 | 53.2945 | 53.3087 | -65.9584 | 0.14299 | 0.11025 | 0.062695 | 0.057037 | 0.10528 | 0.11764 | 0.009846 | -6.1882 | -5.9496 | 9.4319 | 2.3959 | 8.5841 | -6.0088 | -5.9946 | 59.78 | -59.2462 | 59.9132 | 59.8329 | 0.052849 | -59.198 | -59.1856 | 113.1239 | 113.0647 | 113.0789 | 34.7358 | -125.2616 | 59.8272 | 59.8755 | 59.8878 | 59.8805 | -59.2934
3108.0938 | 118.9041 | -68.7195 | 49.8825 | 1.4211e-13 | -0.035337 | 0.0026817 | 0.06118 | 0.00035463 | 0.070998 | -0.0022889 | -0.0015767 | 0.024088 | -0.0064458 | 0.02078 | 0.012279 | -53.154 | -26.6827 | -60.222 | 49.6498 | 49.5718 | 49.5955 | -69.3559 | 0.15672 | 0.1194 | 0.08101 | 0.075351 | 0.10986 | 0.14053 | 0.023583 | -0.63644 | -0.2327 | 15.5654 | 8.4975 | 9.134 | -0.31071 | -0.28705 | 68.7431 | -49.8072 | 68.8762 | 68.8005 | 0.057427 | -49.7726 | -49.742 | 118.3693 | 118.2913 | 118.3149 | 42.0368 | -119.2384 | 68.7948 | 68.8293 | 68.86 | 68.8389 | -49.8589
3109.875 | 119.0094 | -61.9583 | 56.7947 | 1.4211e-13 | -0.034696 | 0.0035363 | 0.061821 | -7.2572e-05 | 0.069502 | -0.0022889 | -0.0011493 | 0.024301 | -0.0066594 | 0.020352 | 0.012279 | -47.0739 | -23.3037 | -53.7849 | 56.6914 | 56.5913 | 56.619 | -62.135 | 0.20709 | 0.16061 | 0.12222 | 0.12114 | 0.16022 | 0.1909 | 0.051056 | -0.17665 | -0.10337 | 14.8844 | 8.1734 | 8.3501 | -0.20345 | -0.17571 | 62.0094 | -56.6736 | 62.1654 | 62.0805 | 0.071163 | -56.6345 | -56.6038 | 118.6497 | 118.5496 | 118.5773 | 38.6546 | -118.9297 | 62.0794 | 62.1185 | 62.1492 | 62.1189 | -56.7437
3111.5938 | 117.8879 | -48.4863 | 69.5206 | 1.4211e-13 | -0.034483 | 0.0039637 | 0.062034 | -0.001141 | 0.06587 | -0.01755 | -0.0011493 | 0.024729 | -0.0064458 | 0.020566 | 0.012279 | -37.2899 | -17.759 | -43.3968 | 67.4552 | 67.393 | 67.3284 | -50.2847 | 0.17962 | 0.1423 | 0.11306 | 0.093665 | 0.13733 | 0.168 | 0.041898 | -1.7984 | -2.0654 | 11.1964 | 5.0896 | 6.8879 | -2.1276 | -2.1922 | 48.5282 | -69.4269 | 48.6659 | 48.5994 | 0.071163 | -69.3832 | -69.3526 | 115.9415 | 115.8793 | 115.8147 | 30.7273 | -119.8053 | 48.58 | 48.6237 | 48.6543 | 48.6286 | -69.4787
3113.3906 | 118.4143 | -42.4713 | 75.7462 | 1.4211e-13 | -0.033628 | 0.0037501 | 0.062462 | -0.0015684 | 0.064802 | -0.01755 | -0.0013631 | 0.024088 | -0.0066594 | 0.02078 | 0.012492 | -32.1255 | -14.76 | -37.8021 | 74.2357 | 74.1331 | 74.1276 | -44.126 | 0.17504 | 0.13314 | 0.094746 | 0.084508 | 0.12817 | 0.15427 | 0.023583 | -1.6547 | -1.5104 | 10.3458 | 4.6692 | 6.3239 | -1.613 | -1.6186 | 42.4949 | -75.6616 | 42.6464 | 42.5661 | 0.071163 | -75.618 | -75.5919 | 116.7071 | 116.6045 | 116.5989 | 27.7113 | -119.8722 | 42.5558 | 42.5995 | 42.6256 | 42.6045 | -75.7226
3115.1094 | 117.4072 | -60.9375 | 56.0303 | 1.4211e-13 | -0.03491 | 0.0035363 | 0.060966 | -7.2572e-05 | 0.06822 | -0.0099194 | -0.0015767 | 0.023447 | -0.0058048 | 0.02078 | 0.012279 | -45.032 | -22.2323 | -51.7155 | 57.2591 | 57.2003 | 57.1868 | -59.9966 | 0.074307 | 0.03241 | -0.019721 | -0.029954 | 0.018285 | 0.048958 | -0.054257 | 0.9409 | 1.2288 | 15.9055 | 9.222 | 8.2811 | 1.17 | 1.1565 | 60.8832 | -56.0602 | 61.0118 | 60.9178 | 0.034536 | -56.012 | -55.9813 | 118.1966 | 118.1378 | 118.1243 | 38.7052 | -116.0269 | 60.9075 | 60.9558 | 60.9865 | 60.9699 | -56.0845
3116.8906 | 116.9952 | -60.6125 | 56.0852 | 1.4211e-13 | -0.035124 | 0.0028953 | 0.060752 | 0.00035463 | 0.068434 | -0.0099194 | -0.0020039 | 0.023447 | -0.0053776 | 0.020139 | 0.012279 | -46.4467 | -23.0931 | -53.208 | 55.034 | 54.9612 | 54.9616 | -61.7137 | 0.037677 | -0.008798 | -0.056351 | -0.062004 | -0.013765 | 0.016908 | -0.086309 | -1.1012 | -1.0512 | 14.1658 | 7.4045 | 8.5057 | -1.124 | -1.1236 | 60.5262 | -56.1472 | 60.6502 | 60.5561 | 0.029958 | -56.099 | -56.0683 | 115.6465 | 115.5737 | 115.5741 | 37.5194 | -117.7989 | 60.5505 | 60.5987 | 60.6294 | 60.6037 | -56.1715
3118.5938 | 118.6569 | -67.9047 | 50.2029 | 1.4211e-13 | -0.03491 | 0.0028953 | 0.06118 | 0.00035463 | 0.071212 | -0.0099194 | -0.0011493 | 0.023233 | -0.0053776 | 0.02078 | 0.012065 | -50.3337 | -25.3228 | -57.3514 | 51.6322 | 51.5362 | 51.5688 | -66.6315 | 0.055992 | 0.009516 | -0.033458 | -0.039111 | 0.009128 | 0.030644 | -0.072572 | 1.2732 | 1.4293 | 17.5709 | 10.5533 | 9.2801 | 1.3332 | 1.3659 | 67.8321 | -50.2421 | 67.9607 | 67.8712 | 0.039114 | -50.1938 | -50.1723 | 119.5369 | 119.4408 | 119.4735 | 42.5818 | -116.8344 | 67.8656 | 67.9138 | 67.9353 | 67.9142 | -50.2755
3120.375 | 117.778 | -64.7186 | 52.8122 | 1.4211e-13 | -0.035124 | 0.0026817 | 0.06118 | 0.00099563 | 0.071639 | -0.01755 | -0.0017903 | 0.023447 | -0.0055912 | 0.02078 | 0.012492 | -52.8381 | -26.7926 | -60.3318 | 47.9604 | 47.9921 | 47.8831 | -69.8184 | 0.055992 | 0.023253 | -0.033458 | -0.04369 | -0.004608 | 0.026065 | -0.072572 | -5.0998 | -4.8518 | 11.8805 | 4.3868 | 9.4866 | -4.8201 | -4.9291 | 64.6461 | -52.8559 | 64.7746 | 64.6852 | 0.039114 | -52.8168 | -52.7861 | 112.679 | 112.7107 | 112.6017 | 37.9261 | -122.6306 | 64.6749 | 64.714 | 64.7447 | 64.7419 | -52.8848
3122.1562 | 117.4255 | -41.5421 | 75.3296 | 1.4211e-13 | -0.033842 | 0.0050321 | 0.062248 | -0.001141 | 0.065015 | -0.0099194 | -0.0020039 | 0.023233 | -0.0053776 | 0.020352 | 0.012279 | -33.0366 | -15.4331 | -39.0749 | 71.4933 | 71.4728 | 71.3438 | -45.7104 | -0.012689 | -0.045428 | -0.097559 | -0.10321 | -0.06413 | -0.028878 | -0.12294 | -4.1683 | -3.8363 | 8.5055 | 2.4672 | 6.6355 | -3.8568 | -3.9858 | 41.4191 | -75.4328 | 41.5294 | 41.4445 | 0.02538 | -75.3937 | -75.3585 | 113.0353 | 113.0148 | 112.8859 | 26.109 | -121.0399 | 41.4388 | 41.4779 | 41.5132 | 41.4966 | -75.4525
3123.875 | 118.158 | -4.9072 | 113.3835 | 1.4211e-13 | -0.032346 | 0.0058869 | 0.063316 | -0.0028504 | 0.060956 | 0.0053411 | -0.0015767 | 0.023447 | -0.0053776 | 0.02078 | 0.012065 | -16.852 | -6.0698 | -21.8514 | 91.1071 | 91.0614 | 90.899 | -26.0027 | 0.023941 | -0.013377 | -0.051772 | -0.071161 | -0.027501 | -0.001407 | -0.10462 | -21.0954 | -22.2764 | -11.9448 | -16.9442 | 4.1513 | -22.3221 | -22.4845 | 4.8026 | -113.4546 | 4.9312 | 4.8555 | 0.052852 | -113.411 | -113.3849 | 96.0143 | 95.9687 | 95.8063 | -1.1626 | -139.3861 | 4.8361 | 4.8797 | 4.9058 | 4.8938 | -113.4881
3125.6406 | 118.634 | -9.3704 | 109.2453 | 1.4211e-13 | -0.031064 | 0.0071689 | 0.06524 | -0.0047732 | 0.058392 | -0.0099194 | -0.0015767 | 0.023447 | -0.0051638 | 0.020566 | 0.012279 | -3.4831 | 1.5215 | -7.4756 | 108.4684 | 108.2416 | 108.2382 | -10.21 | -0.003531 | -0.036271 | -0.079245 | -0.089475 | -0.045815 | -0.010564 | -0.12294 | -0.83953 | -0.77695 | 5.8873 | 1.8948 | 2.7344 | -1.0037 | -1.0071 | 9.2475 | -109.3348 | 9.3669 | 9.2912 | 0.043694 | -109.2911 | -109.2559 | 117.8388 | 117.612 | 117.6086 | 10.8919 | -119.4553 | 9.2809 | 9.3246 | 9.3599 | 9.3342 | -109.3682
3127.3438 | 117.3706 | -24.0189 | 93.1183 | 1.4211e-13 | -0.032346 | 0.0058869 | 0.06353 | -0.0026366 | 0.061383 | -0.0022889 | -0.0017903 | 0.023019 | -0.0053776 | 0.020566 | 0.012065 | -18.3033 | -6.7291 | -22.9548 | 89.7199 | 89.5046 | 89.5667 | -27.7976 | -0.017267 | -0.059164 | -0.10672 | -0.11237 | -0.077866 | -0.047193 | -0.14583 | -3.7787 | -3.3984 | 5.7155 | 1.0641 | 4.8429 | -3.6137 | -3.5516 | 23.873 | -93.2307 | 24.0016 | 23.9121 | 0.039116 | -93.1962 | -93.1655 | 113.7387 | 113.5235 | 113.5855 | 17.2897 | -120.9159 | 23.9065 | 23.941 | 23.9717 | 23.9597 | -93.2641
3129.1406 | 117.7185 | -20.8511 | 97.1924 | 1.4211e-13 | -0.031919 | 0.0065279 | 0.063957 | -0.0028504 | 0.060956 | -0.0022889 | -0.0022175 | 0.023233 | -0.0051638 | 0.02078 | 0.012706 | -14.4438 | -4.5131 | -19.0724 | 94.5134 | 94.3537 | 94.3192 | -23.2553 | -0.049318 | -0.086637 | -0.13877 | -0.14442 | -0.10076 | -0.074664 | -0.17331 | -2.4042 | -2.679 | 6.4074 | 1.7788 | 4.1829 | -2.8387 | -2.8731 | 20.6778 | -97.3368 | 20.8018 | 20.7124 | 0.034538 | -97.2931 | -97.267 | 115.3646 | 115.2048 | 115.1704 | 16.338 | -120.4477 | 20.7067 | 20.7504 | 20.7765 | 20.7645 | -97.3657
3130.9375 | 117.6361 | -12.973 | 104.3976 | 1.4211e-13 | -0.031278 | 0.0067415 | 0.064385 | -0.003705 | 0.059888 | -0.0022889 | -0.0017903 | 0.023019 | -0.0055912 | 0.020566 | 0.012706 | -10.4926 | -2.3337 | -14.9977 | 98.9865 | 98.8227 | 98.7788 | -18.6306 | -0.00811 | -0.040849 | -0.097559 | -0.10321 | -0.054973 | -0.033457 | -0.12752 | -5.6576 | -5.4111 | 2.4804 | -2.0247 | 3.6329 | -5.5749 | -5.6188 | 12.8455 | -104.5008 | 12.9649 | 12.8755 | 0.029959 | -104.4526 | -104.431 | 111.9595 | 111.7957 | 111.7518 | 10.6393 | -123.0282 | 12.8698 | 12.918 | 12.9396 | 12.9322 | -104.5251
3132.6562 | 116.7389 | -21.9818 | 94.4778 | 1.4211e-13 | -0.031919 | 0.0063141 | 0.063316 | -0.0032776 | 0.060315 | -0.0099194 | -0.0017903 | 0.023447 | -0.0051638 | 0.020352 | 0.012706 | -15.5243 | -5.2136 | -20.368 | 91.8809 | 91.7849 | 91.6591 | -24.6794 | 0.019362 | -0.022535 | -0.070087 | -0.075739 | -0.041237 | -0.005985 | -0.10462 | -2.6975 | -2.597 | 6.4575 | 1.6138 | 4.3113 | -2.6929 | -2.8188 | 21.8772 | -94.5536 | 22.0012 | 21.9117 | 0.034537 | -94.5191 | -94.4838 | 113.8627 | 113.7667 | 113.6409 | 16.7682 | -119.1572 | 21.9061 | 21.9406 | 21.9758 | 21.9593 | -94.5825
3134.4219 | 118.4326 | -6.4316 | 111.9965 | 1.4211e-13 | -0.030209 | 0.0078099 | 0.065881 | -0.004987 | 0.057751 | -0.0022889 | -0.0015767 | 0.02366 | -0.0053776 | 0.020566 | 0.011851 | -0.17293 | 3.4033 | -4.1197 | 112.0487 | 111.8955 | 111.782 | -6.3957 | 0.02852 | -0.008798 | -0.051772 | -0.062004 | -0.013765 | 0.003172 | -0.095467 | 0.03587 | 0.052192 | 6.2586 | 2.3119 | 2.276 | -0.10092 | -0.21443 | 6.3361 | -112.0585 | 6.4601 | 6.3798 | 0.043695 | -112.0102 | -111.9933 | 118.4802 | 118.3271 | 118.2136 | 9.8349 | -118.3922 | 6.3696 | 6.4178 | 6.4348 | 6.4228 | -112.0919
3136.2031 | 117.6636 | -13.3026 | 103.894 | 1.4211e-13 | -0.03085 | 0.0075963 | 0.065453 | -0.004346 | 0.058819 | -0.0022889 | -0.0013631 | 0.023874 | -0.0053776 | 0.020566 | 0.012492 | -5.4793 | 0.44095 | -9.7601 | 104.8285 | 104.7249 | 104.5616 | -12.8062 | 0.02852 | -0.013377 | -0.056351 | -0.071161 | -0.036658 | 0.007751 | -0.10462 | 0.49641 | 0.93449 | 7.8233 | 3.5425 | 3.0461 | 0.8309 | 0.66753 | 13.198 | -103.9652 | 13.3311 | 13.2463 | 0.048273 | -103.9307 | -103.8863 | 118.1311 | 118.0276 | 117.8642 | 13.7436 | -116.7002 | 13.2315 | 13.266 | 13.3104 | 13.2892 | -103.9987
3137.9844 | 118.5974 | -5.5252 | 112.8983 | 1.4211e-13 | -0.029996 | 0.0082373 | 0.066735 | -0.0052006 | 0.057537 | -0.01755 | -0.0015767 | 0.02366 | -0.0058048 | 0.020993 | 0.012065 | 1.2693 | 4.2229 | -2.6135 | 113.8113 | 113.6309 | 113.5494 | -4.8022 | 0.02852 | -0.00422 | -0.056351 | -0.057425 | -0.018344 | 0.012329 | -0.10004 | 0.72296 | 0.91308 | 6.7945 | 2.9118 | 2.1888 | 0.7327 | 0.65112 | 5.4252 | -112.9557 | 5.5537 | 5.4689 | 0.043694 | -112.9166 | -112.8859 | 119.3365 | 119.1562 | 119.0746 | 9.7481 | -117.7005 | 5.4678 | 5.5069 | 5.5375 | 5.521 | -112.9983
3139.7031 | 119.1834 | -0.58594 | 118.5791 | 1.4211e-13 | -0.029782 | 0.0088783 | 0.067376 | -0.005628 | 0.056683 | -0.0022889 | -0.0015767 | 0.02366 | -0.0053776 | 0.020352 | 0.012492 | 4.8175 | 6.2512 | 1.1224 | 118.6553 | 118.4755 | 118.3752 | -0.53926 | 0.033099 | -0.008798 | -0.056351 | -0.057425 | -0.022922 | 0.012329 | -0.10004 | 0.046672 | 0.076163 | 5.4034 | 1.7084 | 1.6617 | -0.10365 | -0.20388 | 0.48589 | -118.6365 | 0.61904 | 0.52959 | 0.043694 | -118.602 | -118.5668 | 119.2412 | 119.0614 | 118.9612 | 6.8371 | -119.1184 | 0.52851 | 0.56302 | 0.59827 | 0.57714 | -118.6791
3141.5 | 119.2383 | -0.54474 | 118.7988 | 1.4211e-13 | -0.029568 | 0.0086647 | 0.06759 | -0.005628 | 0.056896 | -0.0099194 | -0.0013631 | 0.02366 | -0.0055912 | 0.020352 | 0.012706 | 4.9228 | 6.3519 | 1.2048 | 118.8567 | 118.6815 | 118.595 | -0.47974 | 0.02852 | 0.000359 | -0.047194 | -0.062004 | -0.018344 | 0.007751 | -0.10004 | 0.065 | 0.057886 | 5.4676 | 1.7496 | 1.6846 | -0.11732 | -0.20384 | 0.44469 | -118.8608 | 0.57326 | 0.49754 | 0.052851 | -118.8172 | -118.7911 | 119.4015 | 119.2262 | 119.1397 | 6.8967 | -119.2786 | 0.48273 | 0.52639 | 0.55249 | 0.5451 | -118.8989
3143.2188 | 119.3619 | -0.73242 | 118.5104 | 1.4211e-13 | -0.029354 | 0.0090921 | 0.06759 | -0.005628 | 0.057324 | -0.0099194 | -0.0015767 | 0.023447 | -0.0055912 | 0.020993 | 0.012279 | 3.9247 | 5.8345 | 0.1381 | 117.5839 | 117.3994 | 117.3176 | -1.7435 | 0.023941 | -0.013377 | -0.06093 | -0.057425 | -0.022922 | -0.001407 | -0.10004 | -1.0111 | -0.92651 | 4.6571 | 0.87052 | 1.8816 | -1.111 | -1.1929 | 0.63238 | -118.5679 | 0.75636 | 0.67149 | 0.039115 | -118.5334 | -118.5118 | 118.3163 | 118.1318 | 118.05 | 6.567 | -120.254 | 0.675 | 0.7095 | 0.73101 | 0.71905 | -118.6105
3145 | 119.5129 | -0.48523 | 118.8995 | 1.4211e-13 | -0.028927 | 0.0088783 | 0.068017 | -0.0054142 | 0.05711 | -0.0099194 | -0.0015767 | 0.02366 | -0.0053776 | 0.020352 | 0.012492 | 5.0052 | 6.416 | 1.2369 | 118.9986 | 118.8143 | 118.7186 | -0.47974 | 0.037677 | -0.00422 | -0.047194 | -0.057425 | -0.022922 | -0.001407 | -0.10004 | 0.00549 | 0.099108 | 5.4905 | 1.7221 | 1.7166 | -0.085243 | -0.18092 | 0.38518 | -118.957 | 0.52291 | 0.43804 | 0.052851 | -118.9225 | -118.9009 | 119.4839 | 119.2995 | 119.2038 | 6.9013 | -119.3793 | 0.4278 | 0.46231 | 0.48382 | 0.48101 | -118.9996
3146.7812 | 119.5541 | -0.48981 | 118.9407 | 1.4211e-13 | -0.029354 | 0.0090921 | 0.068231 | -0.005628 | 0.057537 | 0.0053411 | -0.0015767 | 0.02366 | -0.0055912 | 0.020566 | 0.012279 | 5.0419 | 6.4435 | 1.2552 | 119.0536 | 118.8738 | 118.7827 | -0.47974 | 0.033099 | -0.00422 | -0.051772 | -0.057425 | -0.022922 | 0.012329 | -0.10004 | 0.010068 | 0.11285 | 5.5317 | 1.745 | 1.7349 | -0.066916 | -0.15802 | 0.38976 | -118.9982 | 0.52291 | 0.43804 | 0.048273 | -118.9637 | -118.9284 | 119.5434 | 119.3636 | 119.2725 | 6.9333 | -119.4205 | 0.43238 | 0.46688 | 0.50214 | 0.48559 | -119.0408
3148.5 | 119.2932 | -2.742 | 116.4688 | 1.4211e-13 | -0.029568 | 0.0086647 | 0.06759 | -0.0052006 | 0.057537 | -0.0022889 | -0.0013631 | 0.023447 | -0.0053776 | 0.02078 | 0.012492 | 2.5924 | 5.0562 | -1.3361 | 115.7984 | 115.6365 | 115.5319 | -3.456 | 0.033099 | -0.00422 | -0.056351 | -0.062004 | -0.027501 | 0.003172 | -0.10462 | -0.71404 | -0.67046 | 5.3344 | 1.4059 | 2.1199 | -0.83229 | -0.9369 | 2.6374 | -116.5308 | 2.7751 | 2.6857 | 0.048273 | -116.4963 | -116.4656 | 118.5404 | 118.3785 | 118.2739 | 7.7982 | -119.9249 | 2.68 | 2.7145 | 2.7452 | 2.7378 | -116.5734
3150.2812 | 119.5999 | -0.72784 | 118.8263 | 1.4211e-13 | -0.028927 | 0.0090921 | 0.068659 | -0.005628 | 0.057537 | 0.0053411 | -0.0017903 | 0.023447 | -0.0058048 | 0.020993 | 0.012492 | 4.9869 | 6.4252 | 1.1041 | 118.9208 | 118.7456 | 118.6545 | -0.68121 | 0.023941 | -0.00422 | -0.042615 | -0.052847 | -0.013765 | 0.007751 | -0.095467 | 0.046632 | 0.094518 | 5.7148 | 1.832 | 1.7853 | -0.080685 | -0.17178 | 0.63238 | -118.8791 | 0.75179 | 0.68523 | 0.052852 | -118.8401 | -118.8185 | 119.6487 | 119.4735 | 119.3824 | 7.153 | -119.5075 | 0.675 | 0.71408 | 0.73559 | 0.72362 | -118.9218
3152.0469 | 119.6365 | -0.5127 | 119.0552 | 1.4211e-13 | -0.028927 | 0.0090921 | 0.068445 | -0.0054142 | 0.057324 | -0.0022889 | -0.0015767 | 0.02366 | -0.0055912 | 0.020566 | 0.012279 | 5.17 | 6.558 | 1.2689 | 119.1543 | 118.9791 | 118.8789 | -0.4889 | 0.037677 | -0.00422 | -0.047194 | -0.057425 | -0.018344 | 0.012329 | -0.095467 | 0.023798 | 0.099133 | 5.6827 | 1.7816 | 1.7578 | -0.076042 | -0.17631 | 0.41723 | -119.1126 | 0.55037 | 0.4655 | 0.048273 | -119.0735 | -119.0428 | 119.667 | 119.4918 | 119.3916 | 7.0707 | -119.5441 | 0.45527 | 0.49435 | 0.52502 | 0.50848 | -119.1506
3153.8281 | 119.6136 | -0.59967 | 119.0826 | 1.4211e-13 | -0.0285 | 0.0093057 | 0.068445 | -0.0052006 | 0.057324 | -0.0099194 | -0.0013631 | 0.02366 | -0.0058048 | 0.02078 | 0.012065 | 5.1655 | 6.5992 | 1.2415 | 119.1497 | 118.97 | 118.8651 | -0.53469 | 0.033099 | -0.00422 | -0.051772 | -0.057425 | -0.022922 | 0.007751 | -0.095467 | 0.064983 | 0.067089 | 5.7651 | 1.8411 | 1.7761 | -0.11267 | -0.21751 | 0.5042 | -119.1401 | 0.63277 | 0.5479 | 0.043695 | -119.1056 | -119.0749 | 119.7494 | 119.5696 | 119.4648 | 7.1988 | -119.6173 | 0.54225 | 0.57675 | 0.60742 | 0.59545 | -119.1781
3155.6094 | 119.7739 | -0.60425 | 118.9957 | 1.4211e-13 | -0.028072 | 0.0093057 | 0.068659 | -0.0054142 | 0.05711 | -0.0022889 | -0.0013631 | 0.02366 | -0.0058048 | 0.02078 | 0.012065 | 5.2067 | 6.5809 | 1.2552 | 119.1955 | 119.0158 | 118.9384 | -0.54842 | 0.037677 | 0.000359 | -0.051772 | -0.057425 | -0.022922 | 0.012329 | -0.10004 | 0.055825 | 0.19985 | 5.8109 | 1.8594 | 1.8036 | 0.020099 | -0.05728 | 0.5042 | -119.0531 | 0.64192 | 0.55248 | 0.048273 | -119.0186 | -118.9833 | 119.7998 | 119.62 | 119.5426 | 7.1851 | -119.5441 | 0.54682 | 0.58133 | 0.61658 | 0.60461 | -119.0957
3157.3906 | 119.7876 | -0.64545 | 119.0277 | 1.4211e-13 | -0.028286 | 0.0093057 | 0.068445 | -0.0054142 | 0.057751 | -0.0022889 | -0.0013631 | 0.02366 | -0.0055912 | 0.020993 | 0.011638 | 5.2754 | 6.6495 | 1.2644 | 119.2321 | 119.0478 | 118.9521 | -0.54842 | 0.02852 | -0.00422 | -0.042615 | -0.062004 | -0.018344 | 0.012329 | -0.10004 | 0.097024 | 0.20443 | 5.9208 | 1.9098 | 1.8128 | 0.020108 | -0.075587 | 0.5454 | -119.0897 | 0.67397 | 0.60283 | 0.05743 | -119.0461 | -119.0154 | 119.8776 | 119.6933 | 119.5976 | 7.295 | -119.5761 | 0.58344 | 0.6271 | 0.65778 | 0.64123 | -119.1278
3159.125 | 119.8059 | -1.0757 | 118.5837 | 1.4211e-13 | -0.028286 | 0.0095193 | 0.068659 | -0.0052006 | 0.057965 | -0.0099194 | -0.0022175 | 0.023447 | -0.0058048 | 0.02078 | 0.012065 | 5.0968 | 6.5946 | 1.0766 | 118.9895 | 118.8097 | 118.714 | -0.814 | 0.023941 | -0.008798 | -0.056351 | -0.062004 | -0.018344 | 0.012329 | -0.090888 | 0.26174 | 0.40581 | 6.1725 | 2.1524 | 1.8906 | 0.22603 | 0.13036 | 0.98486 | -118.6457 | 1.0997 | 1.0194 | 0.034537 | -118.602 | -118.5714 | 120.0652 | 119.8855 | 119.7898 | 7.6703 | -119.3977 | 1.0137 | 1.0574 | 1.0881 | 1.0669 | -118.6746
3160.8906 | 119.6091 | -1.7807 | 117.9153 | 1.4211e-13 | -0.0285 | 0.0097331 | 0.068659 | -0.0052006 | 0.057751 | -0.01755 | -0.0015767 | 0.023447 | -0.0058048 | 0.02078 | 0.012492 | 4.4787 | 6.2146 | 0.37159 | 118.1104 | 117.9351 | 117.8441 | -1.6199 | 0.033099 | 0.000359 | -0.051772 | -0.062004 | -0.018344 | 0.003172 | -0.10004 | 0.16081 | 0.19509 | 6.2594 | 2.1523 | 1.9915 | 0.019795 | -0.071243 | 1.6807 | -117.9773 | 1.8138 | 1.7289 | 0.048273 | -117.9337 | -117.9122 | 119.8911 | 119.7158 | 119.6248 | 7.9953 | -119.5352 | 1.7187 | 1.7624 | 1.7839 | 1.7811 | -118.0154
3162.6094 | 119.7876 | -1.1627 | 118.5013 | 1.4211e-13 | -0.028072 | 0.0097331 | 0.068659 | -0.0054142 | 0.057537 | -0.01755 | -0.0017903 | 0.023233 | -0.0058048 | 0.020566 | 0.012279 | 4.7626 | 6.3657 | 0.66002 | 118.4767 | 118.3015 | 118.215 | -1.336 | 0.02852 | -0.013377 | -0.051772 | -0.062004 | -0.013765 | 0.007751 | -0.095467 | -0.17328 | -0.024574 | 5.9253 | 1.8227 | 1.996 | -0.19983 | -0.28631 | 1.0673 | -118.5633 | 1.1912 | 1.1109 | 0.043695 | -118.515 | -118.4935 | 119.6394 | 119.4642 | 119.3777 | 7.5284 | -119.8373 | 1.1007 | 1.149 | 1.1705 | 1.1493 | -118.5967
3164.3906 | 119.7464 | -0.70038 | 119.0414 | 1.4211e-13 | -0.027859 | 0.0099467 | 0.068872 | -0.0054142 | 0.057751 | -0.0022889 | -0.0015767 | 0.023233 | -0.0055912 | 0.02078 | 0.012065 | 4.7855 | 6.3565 | 0.64171 | 118.4492 | 118.274 | 118.1829 | -1.3268 | 0.037677 | -0.008798 | -0.051772 | -0.057425 | -0.022922 | 0.007751 | -0.10462 | -0.62646 | -0.59221 | 5.4858 | 1.3421 | 1.9685 | -0.76746 | -0.85853 | 0.59575 | -119.0989 | 0.73805 | 0.64861 | 0.052852 | -119.0644 | -119.0337 | 119.1496 | 118.9744 | 118.8833 | 7.0569 | -120.3683 | 0.64295 | 0.67746 | 0.70813 | 0.69158 | -119.1461
3166.1875 | 119.7281 | -2.4811 | 116.9907 | 1.4211e-13 | -0.028072 | 0.0095193 | 0.069086 | -0.005628 | 0.057751 | -0.01755 | -0.0013631 | 0.023447 | -0.0055912 | 0.020993 | 0.012065 | 4.085 | 5.9261 | -0.14576 | 117.4969 | 117.3032 | 117.226 | -2.2747 | 0.02852 | -0.00422 | -0.051772 | -0.052847 | -0.018344 | 0.003172 | -0.10004 | 0.2064 | 0.50627 | 6.566 | 2.3353 | 2.1289 | 0.31259 | 0.23533 | 2.381 | -117.0435 | 2.5096 | 2.4293 | 0.048273 | -117.009 | -116.9875 | 119.978 | 119.7843 | 119.7071 | 8.4072 | -119.2653 | 2.4282 | 2.4627 | 2.4843 | 2.4769 | -117.0907
3167.9062 | 119.5908 | -1.6846 | 117.9245 | 1.4211e-13 | -0.028072 | 0.0099467 | 0.0693 | -0.005628 | 0.057965 | -0.0099194 | -0.0015767 | 0.02366 | -0.0060184 | 0.020566 | 0.012492 | 3.8515 | 5.7933 | -0.47082 | 116.9201 | 116.7721 | 116.6354 | -2.5723 | 0.033099 | -0.008798 | -0.056351 | -0.071161 | -0.022922 | 0.007751 | -0.10462 | -0.88774 | -1.0044 | 5.536 | 1.2138 | 2.1015 | -1.1524 | -1.2891 | 1.5799 | -117.9957 | 1.7177 | 1.6282 | 0.048273 | -117.9474 | -117.9167 | 118.6046 | 118.4567 | 118.3199 | 7.4779 | -120.4968 | 1.6134 | 1.6616 | 1.6923 | 1.6758 | -118.0291
3169.6719 | 119.4809 | -4.4678 | 114.7842 | 1.4211e-13 | -0.028072 | 0.0099467 | 0.068872 | -0.004987 | 0.058178 | -0.0022889 | -0.0022175 | 0.02366 | -0.0055912 | 0.02078 | 0.012065 | 2.2719 | 4.8959 | -2.1327 | 114.901 | 114.7253 | 114.6437 | -4.5596 | 0.02852 | -0.008798 | -0.056351 | -0.062004 | -0.018344 | 0.007751 | -0.10004 | -0.091788 | 0.11675 | 6.7397 | 2.335 | 2.4268 | -0.058928 | -0.14058 | 4.3677 | -114.8462 | 4.4963 | 4.4114 | 0.043694 | -114.8026 | -114.7765 | 119.3688 | 119.1931 | 119.1114 | 9.3637 | -119.3438 | 4.4058 | 4.4494 | 4.4755 | 4.459 | -114.8843
3171.3906 | 119.3527 | -5.127 | 114.1937 | 1.4211e-13 | -0.027859 | 0.0099467 | 0.069086 | -0.004987 | 0.058392 | 0.012972 | -0.0013631 | 0.02366 | -0.0060184 | 0.020993 | 0.012279 | 2.1712 | 4.841 | -2.2563 | 114.6904 | 114.5055 | 114.433 | -4.7565 | 0.02852 | 0.000359 | -0.051772 | -0.066582 | -0.018344 | -0.001407 | -0.10004 | 0.3705 | 0.49666 | 7.2982 | 2.8706 | 2.5001 | 0.3118 | 0.23932 | 5.0269 | -114.2603 | 5.1555 | 5.0752 | 0.048273 | -114.2121 | -114.1951 | 119.8173 | 119.6325 | 119.56 | 9.9679 | -118.9502 | 5.0604 | 5.1086 | 5.1255 | 5.1273 | -114.2938
3173.1719 | 119.1879 | -6.2622 | 112.912 | 1.4211e-13 | -0.028072 | 0.01016 | 0.068659 | -0.0052006 | 0.058819 | -0.0022889 | -0.0015767 | 0.023447 | -0.0058048 | 0.02078 | 0.012065 | 1.1044 | 4.2778 | -3.4055 | 113.152 | 112.9716 | 112.8946 | -6.0569 | 0.033099 | -0.017956 | -0.056351 | -0.057425 | -0.022922 | -0.001407 | -0.10462 | 0.20534 | 0.24006 | 7.3666 | 2.8567 | 2.6514 | 0.059598 | -0.017355 | 6.1576 | -112.9694 | 6.2953 | 6.2059 | 0.048273 | -112.9349 | -112.9134 | 119.4143 | 119.2338 | 119.1568 | 10.54 | -118.9689 | 6.2048 | 6.2393 | 6.2608 | 6.2443 | -113.0166
3174.9375 | 118.7851 | -11.0275 | 107.5607 | 1.4211e-13 | -0.028286 | 0.0095193 | 0.068017 | -0.004346 | 0.059674 | -0.0099194 | -0.0017903 | 0.023233 | -0.0060184 | 0.02078 | 0.012492 | -2.7551 | 2.1167 | -7.6496 | 107.6763 | 107.5272 | 107.4278 | -10.9243 | 0.02852 | -0.008798 | -0.056351 | -0.071161 | -0.027501 | -0.001407 | -0.10462 | 0.10326 | 0.11556 | 8.2724 | 3.378 | 3.2747 | -0.033486 | -0.13295 | 10.9229 | -107.6319 | 11.056 | 10.9712 | 0.048273 | -107.5882 | -107.5621 | 118.7038 | 118.5548 | 118.4553 | 13.1442 | -118.485 | 10.9564 | 11 | 11.0261 | 11.0187 | -107.6654
3176.7188 | 118.8263 | -6.4957 | 112.4039 | 1.4211e-13 | -0.028286 | 0.0097331 | 0.068445 | -0.0047732 | 0.059033 | -0.0022889 | -0.0013631 | 0.023447 | -0.0055912 | 0.02078 | 0.012279 | -0.51631 | 3.3667 | -5.2917 | 110.4508 | 110.2792 | 110.2161 | -8.3005 | 0.033099 | -0.00422 | -0.056351 | -0.057425 | -0.013765 | 0.007751 | -0.10462 | -1.8049 | -1.9531 | 5.9794 | 1.2039 | 3.0088 | -2.1247 | -2.1877 | 6.391 | -112.4613 | 6.5288 | 6.4393 | 0.048273 | -112.4176 | -112.3961 | 116.9465 | 116.7748 | 116.7118 | 9.8623 | -120.7044 | 6.4382 | 6.4819 | 6.5034 | 6.4914 | -112.5085
3178.5 | 118.8538 | -5.9509 | 112.7838 | 1.4211e-13 | -0.027645 | 0.01016 | 0.068659 | -0.0045596 | 0.058819 | -0.0099194 | -0.0017903 | 0.023447 | -0.0060184 | 0.020993 | 0.012279 | 1.6493 | 4.6212 | -2.9843 | 113.1887 | 113.0174 | 112.9358 | -5.6814 | 0.023941 | -0.00422 | -0.051772 | -0.057425 | -0.018344 | 0.007751 | -0.10004 | 0.26953 | 0.40486 | 7.6002 | 2.9666 | 2.6971 | 0.23356 | 0.15203 | 5.8509 | -112.8412 | 5.9749 | 5.8992 | 0.048273 | -112.8022 | -112.7761 | 119.1396 | 118.9683 | 118.8868 | 10.5721 | -118.4652 | 5.8935 | 5.9326 | 5.9587 | 5.9467 | -112.8839
3180.2969 | 118.4555 | -8.0704 | 110.2432 | 1.4211e-13 | -0.027859 | 0.0097331 | 0.068231 | -0.0045596 | 0.059247 | -0.0022889 | -0.0017903 | 0.02366 | -0.0060184 | 0.020566 | 0.012065 | -0.53004 | 3.3804 | -5.333 | 109.9426 | 109.7984 | 109.6988 | -8.3738 | 0.033099 | 0.000359 | -0.051772 | -0.062004 | -0.013765 | 0.012329 | -0.10462 | -0.30343 | -0.30063 | 7.5403 | 2.7374 | 3.0409 | -0.44483 | -0.54446 | 7.9657 | -110.3052 | 8.1035 | 8.0186 | 0.052852 | -110.257 | -110.2309 | 118.013 | 117.8688 | 117.7691 | 11.4508 | -118.617 | 8.0084 | 8.0566 | 8.0827 | 8.0707 | -110.3478
3182.0781 | 118.2541 | -11.7966 | 106.2744 | 1.4211e-13 | -0.027859 | 0.0095193 | 0.068017 | -0.0041322 | 0.059888 | -0.0022889 | -0.0015767 | 0.023447 | -0.0055912 | 0.021207 | 0.012279 | -2.7643 | 2.0984 | -7.851 | 106.9666 | 106.7992 | 106.7501 | -11.3501 | 0.037677 | -0.00422 | -0.051772 | -0.057425 | -0.018344 | 0.007751 | -0.095467 | 0.44646 | 0.69223 | 9.0323 | 3.9456 | 3.4991 | 0.52478 | 0.47573 | 11.7011 | -106.3318 | 11.8342 | 11.7448 | 0.043695 | -106.2928 | -106.2667 | 118.7632 | 118.5958 | 118.5467 | 13.895 | -117.6245 | 11.7391 | 11.7782 | 11.8043 | 11.7923 | -106.3699
3183.8594 | 117.6865 | -16.1499 | 101.4038 | 1.4211e-13 | -0.0285 | 0.0093057 | 0.066949 | -0.003705 | 0.060956 | -0.0022889 | -0.0013631 | 0.02366 | -0.0058048 | 0.020993 | 0.011851 | -6.3812 | 0.0243 | -11.7609 | 101.9487 | 101.7899 | 101.7549 | -15.8741 | 0.033099 | -0.00422 | -0.047194 | -0.057425 | -0.022922 | 0.007751 | -0.090888 | 0.27582 | 0.54492 | 9.7687 | 4.389 | 4.1132 | 0.38604 | 0.35108 | 16.059 | -101.4612 | 16.183 | 16.1027 | 0.043694 | -101.4267 | -101.3961 | 118.0986 | 117.9398 | 117.9048 | 16.1742 | -117.2779 | 16.0925 | 16.127 | 16.1577 | 16.1457 | -101.4947
3185.5938 | 117.8192 | -12.2635 | 105.368 | 1.4211e-13 | -0.028286 | 0.0097331 | 0.067804 | -0.0034912 | 0.060742 | -0.0022889 | -0.0015767 | 0.02366 | -0.0060184 | 0.020993 | 0.012065 | -5.8181 | 0.33107 | -11.3488 | 102.0769 | 101.9776 | 101.8373 | -15.2971 | 0.02852 | -0.00422 | -0.051772 | -0.071161 | -0.022922 | 0.007751 | -0.090888 | -3.0336 | -3.2911 | 6.4454 | 0.91468 | 3.9483 | -3.3905 | -3.5307 | 12.1726 | -105.4392 | 12.292 | 12.2117 | 0.039116 | -105.391 | -105.3603 | 114.3404 | 114.2411 | 114.1008 | 12.5946 | -120.6652 | 12.1923 | 12.2406 | 12.2712 | 12.2593 | -105.4589
3187.3594 | 119.0094 | -0.55389 | 118.4052 | 1.4211e-13 | -0.02679 | 0.011229 | 0.0693 | -0.0054142 | 0.057537 | -0.0022889 | -0.0015767 | 0.023233 | -0.0058048 | 0.02078 | 0.012065 | 5.1059 | 6.4069 | 0.33496 | 116.8376 | 116.7034 | 116.5346 | -1.8488 | 0.02852 | 0.000359 | -0.042615 | -0.062004 | -0.022922 | 0.012329 | -0.095467 | -1.2949 | -1.5675 | 5.6598 | 0.88886 | 2.1838 | -1.7017 | -1.8705 | 0.45843 | -118.4672 | 0.58241 | 0.51128 | 0.052852 | -118.4281 | -118.3928 | 117.3915 | 117.2573 | 117.0885 | 6.9608 | -120.254 | 0.49189 | 0.53097 | 0.56622 | 0.55425 | -118.5006
3189.0781 | 119.3893 | -0.59967 | 118.8263 | 1.4211e-13 | -0.026149 | 0.011229 | 0.069941 | -0.0052006 | 0.058392 | -0.0099194 | -0.0015767 | 0.023233 | -0.0060184 | 0.021207 | 0.012065 | 6.2185 | 7.0341 | 1.5619 | 118.9208 | 118.7502 | 118.6545 | -0.52095 | 0.033099 | -0.008798 | -0.051772 | -0.052847 | -0.027501 | 0.003172 | -0.10004 | 0.07872 | 0.094518 | 6.8182 | 2.1616 | 2.0829 | -0.076106 | -0.17178 | 0.49963 | -118.8791 | 0.63277 | 0.5479 | 0.048273 | -118.8538 | -118.8231 | 119.5205 | 119.3499 | 119.2542 | 7.6338 | -119.3472 | 0.54682 | 0.57217 | 0.60284 | 0.59087 | -118.9263
3190.8594 | 119.5129 | -0.60425 | 118.9865 | 1.4211e-13 | -0.026149 | 0.011442 | 0.069941 | -0.0052006 | 0.058178 | -0.0099194 | -0.0015767 | 0.02366 | -0.0055912 | 0.02078 | 0.012279 | 6.2734 | 7.0982 | 1.5803 | 119.0353 | 118.8647 | 118.769 | -0.53469 | 0.037677 | -0.008798 | -0.047194 | -0.057425 | -0.027501 | 0.012329 | -0.10462 | 0.069561 | 0.04876 | 6.8777 | 2.1845 | 2.1149 | -0.12185 | -0.21753 | 0.49962 | -119.0439 | 0.64192 | 0.55705 | 0.05743 | -119.014 | -118.9742 | 119.6395 | 119.4689 | 119.3732 | 7.7025 | -119.5212 | 0.54682 | 0.57675 | 0.61658 | 0.59545 | -119.0911
3192.5781 | 119.5999 | -0.60883 | 118.9957 | 1.4211e-13 | -0.025722 | 0.011656 | 0.070154 | -0.0054142 | 0.058392 | -0.0099194 | -0.0013631 | 0.02366 | -0.0058048 | 0.020993 | 0.012279 | 6.3375 | 7.1898 | 1.6031 | 119.0856 | 118.9013 | 118.8193 | -0.55758 | 0.033099 | -0.008798 | -0.051772 | -0.052847 | -0.027501 | 0.007751 | -0.095467 | 0.051245 | 0.089967 | 6.9464 | 2.212 | 2.1607 | -0.094374 | -0.17632 | 0.51336 | -119.0485 | 0.64192 | 0.55705 | 0.043695 | -119.0232 | -118.9879 | 119.6945 | 119.5101 | 119.4282 | 7.7986 | -119.5532 | 0.55598 | 0.58132 | 0.61658 | 0.60003 | -119.0911
3194.3594 | 118.4784 | -5.5527 | 112.9578 | 1.4211e-13 | -0.026577 | 0.010801 | 0.068445 | -0.004346 | 0.05946 | -0.0022889 | -0.0015767 | 0.02366 | -0.0055912 | 0.02078 | 0.012279 | 0.66949 | 3.9985 | -4.4814 | 110.8308 | 110.6913 | 110.6145 | -7.6595 | 0.033099 | 0.000359 | -0.047194 | -0.062004 | -0.018344 | 0.012329 | -0.090888 | -2.1068 | -2.127 | 6.2222 | 1.0713 | 3.1781 | -2.2665 | -2.3433 | 5.4618 | -113.0198 | 5.5858 | 5.5055 | 0.043694 | -112.9761 | -112.9454 | 116.3835 | 116.244 | 116.1672 | 9.5512 | -120.6173 | 5.4907 | 5.5343 | 5.565 | 5.553 | -113.0487
3196.1406 | 119.6274 | -0.63171 | 118.9224 | 1.4211e-13 | -0.025722 | 0.01187 | 0.070368 | -0.0052006 | 0.058606 | -0.0022889 | -0.0013631 | 0.023233 | -0.0055912 | 0.020993 | 0.012065 | 6.4108 | 7.1669 | 1.5848 | 119.017 | 118.8372 | 118.7598 | -0.58505 | 0.02852 | -0.013377 | -0.047194 | -0.062004 | -0.03208 | 0.012329 | -0.10462 | 0.046659 | 0.094534 | 7.0425 | 2.2165 | 2.1699 | -0.085236 | -0.1626 | 0.52709 | -118.9844 | 0.66023 | 0.58452 | 0.05743 | -118.9545 | -118.9101 | 119.6487 | 119.4689 | 119.3915 | 7.7986 | -119.5075 | 0.56971 | 0.59963 | 0.64404 | 0.61834 | -119.027
3197.9062 | 119.5221 | -0.72327 | 118.7851 | 1.4211e-13 | -0.025508 | 0.012297 | 0.070368 | -0.0052006 | 0.058392 | -0.0099194 | -0.0017903 | 0.02366 | -0.0058048 | 0.020993 | 0.012065 | 5.985 | 6.883 | 1.0583 | 118.2203 | 118.0588 | 117.9357 | -1.1986 | 0.033099 | -0.008798 | -0.047194 | -0.062004 | -0.027501 | 0.012329 | -0.10004 | -0.47536 | -0.56478 | 6.7083 | 1.7816 | 2.257 | -0.72633 | -0.84942 | 0.62322 | -118.8471 | 0.75637 | 0.67607 | 0.052851 | -118.8126 | -118.7728 | 118.9436 | 118.782 | 118.6589 | 7.6063 | -119.9837 | 0.66126 | 0.69577 | 0.7356 | 0.71447 | -118.8851
3199.625 | 119.632 | -0.73242 | 118.9728 | 1.4211e-13 | -0.025295 | 0.01187 | 0.070795 | -0.0054142 | 0.058606 | -0.0099194 | -0.0015767 | 0.023447 | -0.0060184 | 0.021421 | 0.012279 | 6.4566 | 7.1349 | 1.5436 | 119.0307 | 118.8509 | 118.769 | -0.68579 | 0.02852 | -0.013377 | -0.051772 | -0.057425 | -0.027501 | 0.003172 | -0.10004 | 0.046631 | 0.057915 | 7.189 | 2.2761 | 2.2294 | -0.12185 | -0.2038 | 0.63238 | -119.0302 | 0.76094 | 0.68065 | 0.048273 | -119.0003 | -118.9696 | 119.7631 | 119.5833 | 119.5014 | 7.8673 | -119.6586 | 0.675 | 0.70492 | 0.73559 | 0.71905 | -119.0728
3201.4062 | 119.6228 | -0.71869 | 118.9911 | 1.4211e-13 | -0.025081 | 0.012511 | 0.070582 | -0.0052006 | 0.058606 | -0.0099194 | -0.0020039 | 0.023447 | -0.0055912 | 0.02078 | 0.012279 | 5.8385 | 6.8602 | 0.88893 | 118.2112 | 118.0267 | 117.9448 | -1.5008 | 0.033099 | -0.00422 | -0.051772 | -0.052847 | -0.018344 | 0.012329 | -0.10462 | -0.78215 | -0.77993 | 6.5572 | 1.6076 | 2.3898 | -0.96437 | -1.0463 | 0.61407 | -119.0439 | 0.75179 | 0.66692 | 0.052852 | -119.0094 | -118.9788 | 118.9299 | 118.7454 | 118.6635 | 7.5788 | -120.4919 | 0.66584 | 0.70034 | 0.73102 | 0.71447 | -119.0957
3203.125 | 119.8242 | -0.70496 | 119.0277 | 1.4211e-13 | -0.024867 | 0.012297 | 0.070795 | -0.0054142 | 0.058606 | -0.01755 | -0.0017903 | 0.023233 | -0.0060184 | 0.021207 | 0.012279 | 6.5481 | 7.2402 | 1.5894 | 119.1543 | 118.9791 | 118.8926 | -0.6629 | 0.023941 | -0.008798 | -0.056351 | -0.062004 | -0.018344 | -0.001407 | -0.10462 | 0.04206 | 0.1266 | 7.2531 | 2.2944 | 2.2523 | -0.048576 | -0.13511 | 0.60033 | -119.0897 | 0.7289 | 0.6486 | 0.048273 | -119.0461 | -119.0291 | 119.8593 | 119.6841 | 119.5976 | 7.9451 | -119.6906 | 0.64295 | 0.68661 | 0.70355 | 0.69616 | -119.1323
3204.9062 | 119.7784 | -0.72327 | 119.1376 | 1.4211e-13 | -0.02444 | 0.012297 | 0.071223 | -0.0052006 | 0.059033 | -0.0099194 | -0.0017903 | 0.023447 | -0.0058048 | 0.020993 | 0.012065 | 6.6306 | 7.2814 | 1.626 | 119.2092 | 119.0341 | 118.9384 | -0.6629 | 0.02852 | -0.008798 | -0.056351 | -0.062004 | -0.027501 | 0.012329 | -0.10462 | 0.060371 | 0.071677 | 7.3538 | 2.3493 | 2.2889 | -0.10349 | -0.19919 | 0.61864 | -119.1996 | 0.75179 | 0.66692 | 0.048273 | -119.1651 | -119.1252 | 119.9325 | 119.7573 | 119.6617 | 8.0047 | -119.8005 | 0.66126 | 0.69577 | 0.7356 | 0.71447 | -119.2422
3206.6875 | 119.9707 | -0.6958 | 119.1193 | 1.4211e-13 | -0.02444 | 0.012938 | 0.071009 | -0.0052006 | 0.059033 | -0.0022889 | -0.0020039 | 0.02366 | -0.0055912 | 0.021207 | 0.012279 | 6.658 | 7.286 | 1.6123 | 119.2367 | 119.0616 | 118.9704 | -0.66748 | 0.02852 | -0.008798 | -0.051772 | -0.057425 | -0.027501 | 0.012329 | -0.10004 | 0.028326 | 0.11746 | 7.3538 | 2.3081 | 2.2798 | -0.057708 | -0.14883 | 0.59576 | -119.1767 | 0.72432 | 0.64403 | 0.048273 | -119.1468 | -119.1069 | 119.9325 | 119.7574 | 119.6662 | 7.9818 | -119.7867 | 0.63838 | 0.6683 | 0.70813 | 0.687 | -119.2193
3208.3906 | 119.1147 | -7.6218 | 111.2457 | 1.4211e-13 | -0.024867 | 0.012511 | 0.070368 | -0.0052006 | 0.059247 | -0.0022889 | -0.0017903 | 0.023447 | -0.0055912 | 0.02078 | 0.012279 | 3.9888 | 5.7613 | -1.1484 | 115.4229 | 115.2473 | 115.1702 | -4.033 | 0.023941 | -0.008798 | -0.042615 | -0.062004 | -0.022922 | 0.012329 | -0.10462 | 3.5888 | 4.1772 | 11.6106 | 6.4734 | 2.8846 | 4.0016 | 3.9245 | 7.5171 | -111.3077 | 7.6457 | 7.5792 | 0.062009 | -111.2686 | -111.2334 | 123.0447 | 122.8691 | 122.792 | 13.3831 | -115.2787 | 7.5598 | 7.5988 | 7.6341 | 7.613 | -111.3504
3210.1719 | 119.0277 | -3.9825 | 114.9994 | 1.4211e-13 | -0.024867 | 0.012724 | 0.070368 | -0.0045596 | 0.059888 | -0.0099194 | -0.0017903 | 0.02366 | -0.0055912 | 0.021207 | 0.012065 | 2.7984 | 5.0333 | -2.5402 | 113.4039 | 113.2463 | 113.1465 | -5.6036 | 0.02852 | 0.000359 | -0.051772 | -0.066582 | -0.022922 | 0.012329 | -0.10004 | -1.621 | -1.5955 | 6.781 | 1.4423 | 3.0634 | -1.7531 | -1.8529 | 3.8825 | -115.066 | 4.0111 | 3.9308 | 0.048273 | -115.0223 | -114.9871 | 117.3864 | 117.2289 | 117.129 | 9.0158 | -120.6029 | 3.916 | 3.9596 | 3.9949 | 3.9829 | -115.0994
3211.9531 | 118.1946 | -10.936 | 107.1945 | 1.4211e-13 | -0.025508 | 0.01187 | 0.0693 | -0.0041322 | 0.060742 | -0.0022889 | -0.0017903 | 0.023447 | -0.0058048 | 0.020993 | 0.012065 | -0.69487 | 2.9683 | -6.2761 | 108.3402 | 108.1683 | 108.1146 | -10.0268 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.007751 | -0.10004 | 0.90918 | 1.1456 | 10.2411 | 4.6599 | 3.7507 | 0.97377 | 0.92005 | 10.8359 | -107.2474 | 10.9691 | 10.8934 | 0.05743 | -107.2129 | -107.1868 | 119.2761 | 119.1043 | 119.0505 | 13.9043 | -117.2213 | 10.8831 | 10.9176 | 10.9437 | 10.9363 | -107.2946
3213.7188 | 118.6752 | -5.4428 | 113.0585 | 1.4211e-13 | -0.024867 | 0.012511 | 0.069727 | -0.004346 | 0.060101 | -0.0099194 | -0.0017903 | 0.02366 | -0.0058048 | 0.02078 | 0.012065 | 1.0907 | 3.9665 | -4.4539 | 110.7072 | 110.5448 | 110.4726 | -7.8747 | 0.02852 | -0.00422 | -0.047194 | -0.062004 | -0.022922 | 0.007751 | -0.10004 | -2.4319 | -2.3513 | 6.5335 | 0.98889 | 3.4208 | -2.5137 | -2.5859 | 5.3428 | -113.1205 | 5.4713 | 5.3956 | 0.052851 | -113.0814 | -113.0507 | 116.15 | 115.9876 | 115.9154 | 9.4093 | -120.9332 | 5.3808 | 5.4199 | 5.4506 | 5.4386 | -113.1585
3215.4375 | 118.5287 | -6.3492 | 112.1017 | 1.4211e-13 | -0.025722 | 0.012297 | 0.069941 | -0.0039186 | 0.060315 | -0.01755 | -0.0020039 | 0.02366 | -0.0058048 | 0.021207 | 0.011851 | 1.0037 | 3.8566 | -4.605 | 110.3638 | 110.2151 | 110.1246 | -8.0716 | 0.023941 | -0.008798 | -0.051772 | -0.057425 | -0.036658 | 0.007751 | -0.10004 | -1.7224 | -1.7379 | 7.3529 | 1.7442 | 3.4666 | -1.8867 | -1.9772 | 6.2491 | -112.1592 | 6.3731 | 6.2974 | 0.048273 | -112.1384 | -112.094 | 116.713 | 116.5643 | 116.4738 | 10.2058 | -120.1733 | 6.2918 | 6.3125 | 6.3569 | 6.3404 | -112.2018
3217.2188 | 119.4901 | -0.67291 | 118.7897 | 1.4211e-13 | -0.023799 | 0.013579 | 0.071436 | -0.0052006 | 0.059247 | -0.0099194 | -0.0020039 | 0.02366 | -0.0055912 | 0.021207 | 0.012492 | 6.8549 | 7.1074 | 1.539 | 118.6553 | 118.48 | 118.3981 | -0.85521 | 0.037677 | -0.00422 | -0.051772 | -0.066582 | -0.022922 | 0.003172 | -0.090888 | -0.1823 | -0.13441 | 7.5278 | 2.212 | 2.3943 | -0.30964 | -0.39156 | 0.58203 | -118.8563 | 0.71059 | 0.62114 | 0.039116 | -118.8126 | -118.7865 | 119.3282 | 119.1529 | 119.071 | 7.7803 | -119.6449 | 0.60633 | 0.64999 | 0.67608 | 0.66869 | -118.8806
3219.0156 | 118.1076 | -11.2335 | 106.8604 | 1.4211e-13 | -0.025295 | 0.012511 | 0.069941 | -0.004346 | 0.060742 | -0.01755 | -0.0017903 | 0.023874 | -0.0058048 | 0.020993 | 0.012279 | -0.081363 | 3.2568 | -5.8182 | 108.711 | 108.5483 | 108.5266 | -9.6193 | 0.02852 | -0.008798 | -0.051772 | -0.062004 | -0.027501 | 0.003172 | -0.10462 | 1.6142 | 1.8507 | 11.1522 | 5.4153 | 3.801 | 1.688 | 1.6663 | 11.1289 | -106.9224 | 11.262 | 11.1817 | 0.052852 | -106.8879 | -106.8572 | 119.9445 | 119.7819 | 119.7602 | 14.4903 | -116.4796 | 11.1715 | 11.206 | 11.2367 | 11.2247 | -106.965
3220.7344 | 119.1055 | -2.4307 | 116.5878 | 1.4211e-13 | -0.024013 | 0.013365 | 0.071223 | -0.004987 | 0.059247 | -0.0022889 | -0.0015767 | 0.023874 | -0.0055912 | 0.021207 | 0.012065 | 4.5199 | 5.743 | -1.0523 | 115.0475 | 114.9085 | 114.7993 | -3.8956 | 0.019362 | -0.00422 | -0.051772 | -0.066582 | -0.022922 | 0.003172 | -0.1092 | -1.4649 | -1.5403 | 6.9506 | 1.3785 | 2.8434 | -1.6794 | -1.7885 | 2.3215 | -116.6544 | 2.4501 | 2.379 | 0.057431 | -116.6108 | -116.5847 | 117.4782 | 117.3392 | 117.2301 | 8.1737 | -120.4834 | 2.3641 | 2.4078 | 2.4339 | 2.4265 | -116.697
3222.5312 | 119.5404 | -1.355 | 118.0939 | 1.4211e-13 | -0.023372 | 0.013579 | 0.071436 | -0.0054142 | 0.05946 | -0.0099194 | -0.0015767 | 0.023447 | -0.0058048 | 0.020993 | 0.012492 | 6.8641 | 7.0158 | 1.388 | 118.4813 | 118.3106 | 118.2195 | -1.0796 | 0.02852 | -0.00422 | -0.056351 | -0.052847 | -0.022922 | 0.003172 | -0.10004 | 0.2754 | 0.38741 | 8.219 | 2.7429 | 2.4675 | 0.21674 | 0.12567 | 1.2549 | -118.1467 | 1.3835 | 1.2986 | 0.043694 | -118.1168 | -118.0907 | 119.8363 | 119.6656 | 119.5745 | 8.3708 | -119.1735 | 1.3021 | 1.3321 | 1.3582 | 1.3508 | -118.1939
3224.2656 | 118.9774 | -6.5872 | 112.3581 | 1.4211e-13 | -0.024013 | 0.013793 | 0.071223 | -0.0047732 | 0.060101 | -0.0099194 | -0.0017903 | 0.023447 | -0.0058048 | 0.021634 | 0.012065 | 3.8103 | 5.3309 | -1.8672 | 114.2188 | 114.0797 | 114.0164 | -5.0037 | 0.02852 | -0.00422 | -0.051772 | -0.066582 | -0.018344 | 0.007751 | -0.10004 | 1.5835 | 1.8607 | 10.3975 | 4.72 | 3.1365 | 1.7216 | 1.6583 | 6.4872 | -112.4247 | 6.6157 | 6.5354 | 0.048273 | -112.3764 | -112.3503 | 120.806 | 120.6669 | 120.6036 | 11.9181 | -117.3618 | 6.5206 | 6.5689 | 6.595 | 6.583 | -112.4581
3226.0312 | 118.8766 | -2.6413 | 116.1758 | 1.4211e-13 | -0.024226 | 0.013579 | 0.070582 | -0.0045596 | 0.060742 | -0.01755 | -0.0020039 | 0.023447 | -0.0055912 | 0.021207 | 0.012065 | 2.2948 | 4.4014 | -3.5108 | 111.7282 | 111.5659 | 111.5027 | -6.9864 | 0.033099 | -0.013377 | -0.051772 | -0.062004 | -0.03208 | 0.003172 | -0.10462 | -4.3451 | -4.4477 | 4.9361 | -0.8695 | 3.4756 | -4.61 | -4.6731 | 2.5367 | -116.2378 | 2.6744 | 2.5895 | 0.052852 | -116.2079 | -116.1727 | 114.3695 | 114.2072 | 114.144 | 7.0427 | -123.1622 | 2.5793 | 2.6092 | 2.6445 | 2.6279 | -116.2805
3227.8125 | 118.6523 | -7.3883 | 111.4105 | 1.4211e-13 | -0.02444 | 0.013579 | 0.070795 | -0.0039186 | 0.060742 | -0.0022889 | -0.0020039 | 0.02366 | -0.0058048 | 0.021207 | 0.012065 | 0.87094 | 3.5727 | -5.1498 | 109.6999 | 109.5282 | 109.4698 | -8.9187 | 0.023941 | -0.008798 | -0.056351 | -0.071161 | -0.03208 | 0.003172 | -0.1092 | -1.5304 | -1.7106 | 8.2592 | 2.2385 | 3.7689 | -1.8823 | -1.9407 | 7.2791 | -111.4817 | 7.4122 | 7.332 | 0.052852 | -111.4426 | -111.4073 | 117.0882 | 116.9165 | 116.8581 | 10.961 | -120.3292 | 7.3171 | 7.3562 | 7.3915 | 7.3795 | -111.5197
3229.5938 | 119.1422 | -4.5181 | 114.4363 | 1.4211e-13 | -0.023585 | 0.01422 | 0.07165 | -0.0045596 | 0.05946 | -0.0099194 | -0.0017903 | 0.02366 | -0.0060184 | 0.021421 | 0.011851 | 5.3486 | 6.1963 | -0.4113 | 115.8579 | 115.696 | 115.6052 | -3.3599 | 0.02852 | -0.013377 | -0.056351 | -0.071161 | -0.027501 | 0.003172 | -0.10004 | 1.1582 | 1.4215 | 9.8667 | 4.1068 | 2.9486 | 1.2597 | 1.1688 | 4.4181 | -114.5075 | 4.5466 | 4.4618 | 0.043694 | -114.4638 | -114.4332 | 120.376 | 120.2142 | 120.1233 | 10.7144 | -117.7962 | 4.447 | 4.4906 | 4.5213 | 4.5047 | -114.5364
3231.3594 | 119.0964 | -1.7212 | 117.0456 | 1.4211e-13 | -0.023799 | 0.014007 | 0.07165 | -0.0045596 | 0.059888 | -0.0022889 | -0.0013631 | 0.02366 | -0.0058048 | 0.021207 | 0.012279 | 4.1857 | 5.6285 | -1.7115 | 113.848 | 113.6951 | 113.5906 | -4.9579 | 0.02852 | -0.00422 | -0.051772 | -0.066582 | -0.03208 | 0.007751 | -0.1092 | -3.2367 | -3.1976 | 5.9069 | 0.009661 | 3.2464 | -3.3505 | -3.455 | 1.612 | -117.1122 | 1.7497 | 1.6694 | 0.057431 | -117.0777 | -117.0378 | 115.5691 | 115.4162 | 115.3118 | 7.3497 | -122.0035 | 1.6546 | 1.6891 | 1.7289 | 1.717 | -117.1548
3233.0781 | 119.1376 | -1.0208 | 118.0527 | 1.4211e-13 | -0.022303 | 0.014861 | 0.071864 | -0.004987 | 0.059247 | -0.0099194 | -0.0017903 | 0.023233 | -0.0058048 | 0.021207 | 0.012065 | 6.8961 | 7.0982 | 1.127 | 117.648 | 117.4772 | 117.3862 | -1.6153 | 0.033099 | -0.013377 | -0.051772 | -0.057425 | -0.03208 | 0.007751 | -0.10462 | -0.5945 | -0.40465 | 7.9169 | 2.1478 | 2.7423 | -0.57543 | -0.66643 | 0.91619 | -118.1101 | 1.0539 | 0.96904 | 0.052852 | -118.0848 | -118.0449 | 118.6688 | 118.4981 | 118.4071 | 8.1191 | -119.668 | 0.96339 | 0.98873 | 1.0286 | 1.0074 | -118.1573
3234.8438 | 118.3823 | -11.3205 | 107.3547 | 1.4211e-13 | -0.023799 | 0.014007 | 0.070795 | -0.0039186 | 0.060742 | -0.01755 | -0.0017903 | 0.024088 | -0.0060184 | 0.020993 | 0.011851 | 1.9469 | 4.2549 | -4.1426 | 110.5332 | 110.3341 | 110.3077 | -7.9205 | 0.02852 | -0.00422 | -0.056351 | -0.057425 | -0.027501 | 0.007751 | -0.10004 | 3.4 | 3.1785 | 13.2674 | 7.1779 | 3.7779 | 2.9794 | 2.953 | 11.2205 | -107.4122 | 11.349 | 11.2641 | 0.043694 | -107.3822 | -107.347 | 121.8537 | 121.6546 | 121.6282 | 15.5754 | -115.2752 | 11.2631 | 11.293 | 11.3282 | 11.3163 | -107.4548
3236.5625 | 119.3298 | -12.9089 | 106.5857 | 1.4211e-13 | -0.023585 | 0.014434 | 0.071436 | -0.0045596 | 0.060529 | -0.01755 | -0.0020039 | 0.02366 | -0.0058048 | 0.021207 | 0.011851 | 3.6409 | 5.2531 | -2.2335 | 113.2482 | 113.0265 | 113.0228 | -5.8691 | 0.02852 | -0.008798 | -0.047194 | -0.066582 | -0.022922 | 0.007751 | -0.10004 | 7.0398 | 6.6625 | 16.5498 | 10.6755 | 3.6357 | 6.4408 | 6.4371 | 12.8089 | -106.6523 | 12.9375 | 12.8617 | 0.052851 | -106.6086 | -106.5779 | 126.1571 | 125.9355 | 125.9318 | 18.162 | -112.4548 | 12.8424 | 12.886 | 12.9167 | 12.9001 | -106.6857
3238.3281 | 118.2587 | -14.328 | 103.5049 | 1.4211e-13 | -0.024226 | 0.013793 | 0.070795 | -0.0032776 | 0.06181 | -0.01755 | -0.0020039 | 0.023447 | -0.0060184 | 0.021421 | 0.012279 | -1.1069 | 2.5792 | -7.352 | 106.7011 | 106.4878 | 106.5075 | -11.8904 | 0.023941 | -0.008798 | -0.056351 | -0.057425 | -0.03208 | -0.001407 | -0.10462 | 2.4376 | 3.1962 | 13.2211 | 6.976 | 4.5384 | 2.9829 | 3.0025 | 14.2234 | -103.5624 | 14.3519 | 14.2717 | 0.048273 | -103.537 | -103.5064 | 121.0291 | 120.8158 | 120.8355 | 16.9072 | -115.3954 | 14.2706 | 14.2959 | 14.3266 | 14.3192 | -103.6096
3240.0469 | 119.0369 | -7.0496 | 111.9507 | 1.4211e-13 | -0.022731 | 0.015716 | 0.072291 | -0.0047732 | 0.060101 | -0.0022889 | -0.0017903 | 0.023874 | -0.0062322 | 0.02078 | 0.012065 | 5.2113 | 6.0452 | -0.65395 | 115.3588 | 115.1283 | 115.1244 | -3.9964 | 0.023941 | -0.00422 | -0.047194 | -0.066582 | -0.03208 | 0.003172 | -0.10462 | 3.0532 | 3.4081 | 12.2608 | 6.3956 | 3.3424 | 3.1776 | 3.1737 | 6.9449 | -112.0173 | 7.0735 | 7.0024 | 0.05743 | -111.9828 | -111.9475 | 122.4084 | 122.1778 | 122.174 | 13.0947 | -115.947 | 6.983 | 7.0175 | 7.0527 | 7.0453 | -112.0553
3241.7812 | 119.3115 | -2.3987 | 116.7572 | 1.4211e-13 | -0.021876 | 0.015289 | 0.072719 | -0.0045596 | 0.059674 | -0.0099194 | -0.0015767 | 0.02366 | -0.0060184 | 0.021421 | 0.012065 | 6.0949 | 6.5122 | 0.11063 | 116.2699 | 116.1127 | 116.0035 | -2.8425 | 0.033099 | -0.008798 | -0.06093 | -0.062004 | -0.027501 | 0.003172 | -0.10462 | -0.44378 | -0.48728 | 8.4936 | 2.5093 | 2.9531 | -0.64447 | -0.7537 | 2.2941 | -116.8192 | 2.4318 | 2.3378 | 0.043694 | -116.7847 | -116.754 | 118.6686 | 118.5114 | 118.4022 | 8.9109 | -119.5997 | 2.3367 | 2.3712 | 2.4019 | 2.3899 | -116.8618
3243.5 | 119.0598 | -2.5497 | 116.6107 | 1.4211e-13 | -0.022731 | 0.015502 | 0.072505 | -0.0047732 | 0.060101 | 0.0053411 | -0.0015767 | 0.02366 | -0.0060184 | 0.021421 | 0.012065 | 5.1151 | 5.9627 | -0.87828 | 115.107 | 114.913 | 114.868 | -4.1658 | 0.033099 | -0.008798 | -0.056351 | -0.057425 | -0.022922 | 0.012329 | -0.090888 | -1.616 | -1.5037 | 7.6649 | 1.6715 | 3.2875 | -1.6977 | -1.7427 | 2.4589 | -116.6681 | 2.5828 | 2.4934 | 0.034537 | -116.6336 | -116.5984 | 117.6568 | 117.4628 | 117.4178 | 8.5125 | -120.7765 | 2.4923 | 2.5268 | 2.5621 | 2.5409 | -116.7016
3245.2812 | 119.1376 | -4.509 | 114.4684 | 1.4211e-13 | -0.022303 | 0.015716 | 0.072505 | -0.0047732 | 0.060101 | -0.0022889 | -0.0017903 | 0.023447 | -0.0058048 | 0.021207 | 0.012279 | 4.6252 | 5.5553 | -1.478 | 114.2417 | 114.0797 | 113.9935 | -4.7793 | 0.033099 | -0.008798 | -0.047194 | -0.057425 | -0.027501 | 0.007751 | -0.10462 | -0.27038 | -0.22669 | 9.1342 | 3.0309 | 3.3013 | -0.3887 | -0.47489 | 4.4043 | -114.5258 | 4.5421 | 4.4618 | 0.05743 | -114.4959 | -114.4606 | 118.7507 | 118.5887 | 118.5025 | 10.0642 | -119.2477 | 4.4515 | 4.4815 | 4.5167 | 4.5002 | -114.573
3247.0625 | 118.959 | -3.5339 | 115.5075 | 1.4211e-13 | -0.022517 | 0.015502 | 0.072505 | -0.0041322 | 0.060956 | -0.01755 | -0.0015767 | 0.02366 | -0.0060184 | 0.021421 | 0.011851 | 3.8286 | 5.0745 | -2.4074 | 113.0696 | 112.9304 | 112.8305 | -5.8691 | 0.042256 | 0.000359 | -0.042615 | -0.062004 | -0.018344 | 0.003172 | -0.10004 | -2.3352 | -2.4379 | 7.3625 | 1.1265 | 3.4617 | -2.5771 | -2.677 | 3.4339 | -115.5695 | 3.5762 | 3.4913 | 0.05743 | -115.5259 | -115.5043 | 116.6036 | 116.4643 | 116.3645 | 8.6084 | -121.3766 | 3.4719 | 3.5156 | 3.5371 | 3.5343 | -115.6076
3248.7812 | 119.2108 | -2.8381 | 116.3361 | 1.4211e-13 | -0.02209 | 0.015716 | 0.072719 | -0.0045596 | 0.060101 | -0.0099194 | -0.0017903 | 0.023233 | -0.0060184 | 0.021207 | 0.012065 | 5.6325 | 6.1138 | -0.47082 | 115.6198 | 115.4625 | 115.3717 | -3.6117 | 0.037677 | -0.008798 | -0.047194 | -0.062004 | -0.022922 | 0.012329 | -0.10462 | -0.77359 | -0.71627 | 8.4706 | 2.3673 | 3.1409 | -0.87354 | -0.9644 | 2.7335 | -116.3981 | 2.8758 | 2.7909 | 0.05743 | -116.359 | -116.3237 | 118.4579 | 118.3007 | 118.2098 | 8.952 | -119.9478 | 2.7761 | 2.8152 | 2.8505 | 2.8293 | -116.4407
3250.5 | 119.0186 | -4.8157 | 114.0335 | 1.4211e-13 | -0.022303 | 0.016357 | 0.072719 | -0.0041322 | 0.060956 | -0.0022889 | -0.0020039 | 0.023447 | -0.0055912 | 0.021421 | 0.011851 | 4.0346 | 5.2805 | -2.1831 | 113.2207 | 113.0632 | 112.9816 | -5.7089 | 0.02852 | 0.000359 | -0.051772 | -0.071161 | -0.018344 | 0.003172 | -0.10004 | -0.8932 | -0.81279 | 8.8503 | 2.6326 | 3.5258 | -0.97034 | -1.0519 | 4.7156 | -114.1047 | 4.8442 | 4.7639 | 0.048273 | -114.0519 | -114.0303 | 118.0364 | 117.8788 | 117.7973 | 10.0962 | -119.7424 | 4.7445 | 4.7973 | 4.8188 | 4.816 | -114.1336
3252.2969 | 119.0186 | -4.454 | 114.6011 | 1.4211e-13 | -0.022303 | 0.016571 | 0.073146 | -0.004346 | 0.060529 | -0.0099194 | -0.0013631 | 0.024088 | -0.0055912 | 0.021421 | 0.011638 | 4.877 | 5.7613 | -1.3544 | 114.2509 | 114.0934 | 114.0072 | -4.7702 | 0.033099 | 0.000359 | -0.042615 | -0.066582 | -0.013765 | 0.003172 | -0.10004 | -0.31615 | -0.35028 | 9.3311 | 3.0996 | 3.4158 | -0.50771 | -0.5939 | 4.354 | -114.6677 | 4.4871 | 4.4114 | 0.05743 | -114.6149 | -114.598 | 118.7049 | 118.5475 | 118.4613 | 10.2153 | -119.3713 | 4.3875 | 4.4403 | 4.4572 | 4.4544 | -114.7012
3254.0781 | 118.8904 | -5.6534 | 113.3148 | 1.4211e-13 | -0.022303 | 0.016357 | 0.072719 | -0.004346 | 0.060529 | -0.0099194 | -0.0017903 | 0.02366 | -0.0062322 | 0.021421 | 0.012065 | 3.9659 | 5.2851 | -2.2884 | 112.8819 | 112.7197 | 112.652 | -5.9607 | 0.02852 | 0.004938 | -0.051772 | -0.057425 | -0.018344 | 0.012329 | -0.10004 | -0.30733 | -0.4329 | 9.6193 | 3.365 | 3.6723 | -0.59507 | -0.66285 | 5.5533 | -113.3722 | 5.6819 | 5.6016 | 0.048273 | -113.3332 | -113.3025 | 118.5353 | 118.3731 | 118.3053 | 10.9385 | -119.2755 | 5.596 | 5.635 | 5.6657 | 5.6583 | -113.4149
3255.8594 | 118.2358 | -9.8557 | 108.3069 | 1.4211e-13 | -0.022517 | 0.016357 | 0.072291 | -0.0039186 | 0.061597 | -0.0022889 | -0.0015767 | 0.023447 | -0.0064458 | 0.021421 | 0.012279 | 1.9881 | 4.1267 | -4.4402 | 109.8785 | 109.7526 | 109.6438 | -8.5524 | 0.037677 | -0.008798 | -0.042615 | -0.057425 | -0.009187 | 0.003172 | -0.095467 | 1.3033 | 1.5716 | 11.8437 | 5.4155 | 4.1122 | 1.4457 | 1.3369 | 9.7602 | -108.3643 | 9.8933 | 9.813 | 0.052852 | -108.3161 | -108.3037 | 119.7341 | 119.6083 | 119.4995 | 13.9824 | -116.8593 | 9.7982 | 9.8465 | 9.8588 | 9.8469 | -108.4024
3257.5781 | 118.2266 | -9.787 | 108.3252 | 1.4211e-13 | -0.022303 | 0.016357 | 0.072505 | -0.003705 | 0.061597 | 0.0053411 | -0.0015767 | 0.023233 | -0.0060184 | 0.021421 | 0.012492 | 1.8645 | 4.113 | -4.6004 | 109.5214 | 109.3726 | 109.2913 | -8.8134 | 0.033099 | 0.000359 | -0.047194 | -0.052847 | -0.013765 | 0.007751 | -0.10004 | 0.9736 | 1.1962 | 11.6514 | 5.1866 | 4.213 | 1.0474 | 0.96608 | 9.6869 | -108.378 | 9.8201 | 9.7398 | 0.052851 | -108.339 | -108.3174 | 119.3084 | 119.1595 | 119.0783 | 13.9 | -117.1386 | 9.7341 | 9.7732 | 9.7947 | 9.7873 | -108.4252
3259.375 | 117.5858 | -14.3646 | 102.9739 | 1.4211e-13 | -0.023158 | 0.015716 | 0.071864 | -0.003064 | 0.062238 | -0.0099194 | -0.0017903 | 0.02366 | -0.0055912 | 0.021207 | 0.011851 | -1.0932 | 2.3777 | -7.7091 | 105.2681 | 105.0867 | 105.0698 | -12.6459 | 0.037677 | 0.004938 | -0.042615 | -0.052847 | -0.013765 | 0.021486 | -0.095467 | 1.7187 | 2.2941 | 13.2714 | 6.6555 | 4.9369 | 2.1127 | 2.0959 | 14.2692 | -103.0268 | 14.4023 | 14.322 | 0.052852 | -102.9877 | -102.9525 | 119.6327 | 119.4513 | 119.4344 | 16.7423 | -115.6199 | 14.3118 | 14.3509 | 14.3861 | 14.3696 | -103.0694
3261.1562 | 117.7917 | -14.5569 | 103.1387 | 1.4211e-13 | -0.022517 | 0.016143 | 0.072077 | -0.003064 | 0.062238 | -0.0022889 | -0.0017903 | 0.023874 | -0.0058048 | 0.021634 | 0.012065 | 0.074302 | 3.0279 | -6.4317 | 106.8384 | 106.6893 | 106.6311 | -11.1028 | 0.033099 | 0.000359 | -0.047194 | -0.052847 | -0.018344 | 0.026065 | -0.090888 | 3.454 | 3.6997 | 14.6312 | 8.1251 | 4.6711 | 3.5506 | 3.4924 | 14.466 | -103.1916 | 14.59 | 14.5097 | 0.043694 | -103.1571 | -103.1127 | 121.3953 | 121.2462 | 121.188 | 17.5847 | -114.2416 | 14.504 | 14.5385 | 14.5829 | 14.5572 | -103.2296
3262.8594 | 117.7963 | -9.2422 | 108.7372 | 1.4211e-13 | -0.022944 | 0.016357 | 0.072077 | -0.0032776 | 0.062238 | -0.0022889 | -0.0015767 | 0.02366 | -0.0062322 | 0.021207 | 0.012279 | -0.25534 | 2.831 | -6.9491 | 105.9777 | 105.8285 | 105.7703 | -11.7576 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.10004 | -2.5154 | -2.7595 | 8.9869 | 2.2932 | 4.8085 | -2.9087 | -2.9669 | 9.1422 | -108.79 | 9.2753 | 9.1996 | 0.05743 | -108.7555 | -108.7249 | 115.22 | 115.0707 | 115.0126 | 12.0732 | -120.4948 | 9.1894 | 9.2239 | 9.2546 | 9.2426 | -108.8372
3264.6562 | 117.8833 | -10.6476 | 107.0938 | 1.4211e-13 | -0.021876 | 0.017212 | 0.073146 | -0.003705 | 0.061383 | -0.0022889 | -0.0017903 | 0.02366 | -0.0058048 | 0.021848 | 0.012279 | 3.1464 | 4.7448 | -3.1995 | 111.1284 | 110.9431 | 110.9029 | -7.3435 | 0.033099 | 0.004938 | -0.042615 | -0.052847 | -0.022922 | 0.012329 | -0.10004 | 3.304 | 4.0346 | 13.794 | 7.4481 | 4.1441 | 3.8493 | 3.8091 | 10.5475 | -107.1467 | 10.6807 | 10.605 | 0.05743 | -107.1167 | -107.0815 | 121.776 | 121.5907 | 121.5505 | 15.3924 | -114.4374 | 10.5947 | 10.6247 | 10.6599 | 10.6525 | -107.1939
3266.375 | 118.1076 | -8.8257 | 109.0118 | 1.4211e-13 | -0.021876 | 0.016784 | 0.07336 | -0.003705 | 0.06181 | -0.0022889 | -0.0020039 | 0.023447 | -0.0060184 | 0.021207 | 0.012492 | 2.2765 | 4.3236 | -4.2799 | 109.5489 | 109.4412 | 109.3599 | -8.6211 | 0.033099 | -0.00422 | -0.042615 | -0.052847 | -0.018344 | 0.016908 | -0.10004 | 0.20462 | 0.53701 | 11.1022 | 4.5457 | 4.3411 | 0.42939 | 0.34811 | 8.7256 | -109.0647 | 8.8588 | 8.7831 | 0.05743 | -109.0302 | -108.9949 | 118.3745 | 118.2669 | 118.1856 | 13.1493 | -117.6329 | 8.7728 | 8.8073 | 8.8426 | 8.8215 | -109.1119
3268.1562 | 117.1188 | -8.7799 | 108.2932 | 1.4211e-13 | -0.02209 | 0.016784 | 0.072932 | -0.0034912 | 0.062451 | -0.01755 | -0.0017903 | 0.023447 | -0.0060184 | 0.021848 | 0.012492 | 1.3791 | 3.7513 | -5.2826 | 108.1204 | 107.9714 | 107.904 | -9.8574 | 0.037677 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.016908 | -0.10004 | -1.0775 | -0.17276 | 10.159 | 3.4973 | 4.5748 | -0.32175 | -0.3892 | 8.6799 | -108.3506 | 8.8176 | 8.7373 | 0.05743 | -108.3069 | -108.2762 | 116.9003 | 116.7513 | 116.6839 | 12.5312 | -118.1505 | 8.7225 | 8.7661 | 8.7968 | 8.7803 | -108.3932
3269.875 | 118.5928 | -7.9514 | 111.0947 | 1.4211e-13 | -0.021876 | 0.017212 | 0.073146 | -0.003705 | 0.062665 | -0.0099194 | -0.0017903 | 0.023447 | -0.0058048 | 0.021421 | 0.012065 | 1.2922 | 3.559 | -5.4611 | 108.0151 | 107.889 | 107.8032 | -10.0085 | 0.042256 | 0.009516 | -0.038036 | -0.048268 | -0.013765 | 0.016908 | -0.090888 | -2.0571 | -3.0796 | 9.2435 | 2.4902 | 4.5473 | -3.2057 | -3.2914 | 7.8605 | -111.1429 | 7.9936 | 7.9133 | 0.052852 | -111.1084 | -111.0778 | 115.9664 | 115.8403 | 115.7546 | 11.5103 | -121.1031 | 7.9031 | 7.9376 | 7.9683 | 7.9609 | -111.1856
3271.6562 | 117.8101 | -10.3775 | 107.3639 | 1.4211e-13 | -0.021876 | 0.017212 | 0.072932 | -0.0032776 | 0.062451 | -0.0022889 | -0.0015767 | 0.023447 | -0.0060184 | 0.021848 | 0.011851 | 0.82058 | 3.3346 | -5.8732 | 107.2551 | 107.106 | 107.0386 | -10.6175 | 0.042256 | 0.000359 | -0.042615 | -0.057425 | -0.009187 | 0.007751 | -0.095467 | -0.23998 | -0.10881 | 11.1981 | 4.5043 | 4.7443 | -0.25791 | -0.32529 | 10.282 | -107.4213 | 10.4198 | 10.3349 | 0.052852 | -107.3731 | -107.3561 | 117.6326 | 117.4835 | 117.4161 | 13.7121 | -117.9814 | 10.3201 | 10.3683 | 10.3853 | 10.3779 | -107.4594
3273.375 | 117.8284 | -8.6197 | 109.0256 | 1.4211e-13 | -0.02209 | 0.016998 | 0.07336 | -0.003064 | 0.063092 | -0.01755 | -0.0020039 | 0.023019 | -0.0058048 | 0.021634 | 0.012279 | -0.16835 | 2.7165 | -7.0315 | 105.7213 | 105.572 | 105.5139 | -12.0369 | 0.042256 | 0.004938 | -0.038036 | -0.052847 | -0.009187 | 0.021486 | -0.090888 | -3.4173 | -3.3043 | 8.4513 | 1.5882 | 5.0055 | -3.4535 | -3.5117 | 8.5288 | -109.0784 | 8.6619 | 8.5817 | 0.052852 | -109.0348 | -109.0041 | 114.341 | 114.1917 | 114.1336 | 11.3362 | -121.0625 | 8.5668 | 8.6105 | 8.6412 | 8.6246 | -109.1165
3275.1562 | 117.2333 | -15.9897 | 101.0788 | 1.4211e-13 | -0.02209 | 0.017425 | 0.07336 | -0.0028504 | 0.06352 | -0.01755 | -0.0015767 | 0.023874 | -0.0058048 | 0.021421 | 0.012279 | -0.91921 | 2.2632 | -7.9197 | 104.4165 | 104.2808 | 104.1999 | -13.1267 | 0.02852 | 0.000359 | -0.047194 | -0.052847 | -0.009187 | 0.012329 | -0.10004 | 2.863 | 3.3377 | 15.0705 | 8.07 | 5.2071 | 3.202 | 3.1211 | 15.8896 | -101.1316 | 16.0182 | 15.9425 | 0.052851 | -101.088 | -101.0665 | 120.4062 | 120.2705 | 120.1895 | 18.2529 | -114.2055 | 15.9368 | 15.9805 | 16.002 | 15.99 | -101.1788
3276.9375 | 118.0115 | -11.3022 | 106.8832 | 1.4211e-13 | -0.021449 | 0.018066 | 0.074428 | -0.003705 | 0.062238 | -0.0099194 | -0.0013631 | 0.023233 | -0.0060184 | 0.021848 | 0.012065 | 1.9789 | 3.9619 | -4.7607 | 108.592 | 108.443 | 108.3801 | -9.3949 | 0.033099 | -0.00422 | -0.042615 | -0.057425 | -0.013765 | 0.016908 | -0.090888 | 1.9073 | 1.7087 | 13.2811 | 6.5415 | 4.6342 | 1.5598 | 1.4969 | 11.2113 | -106.9407 | 11.3353 | 11.2596 | 0.048273 | -106.897 | -106.8663 | 119.8942 | 119.7452 | 119.6823 | 15.2641 | -116.2781 | 11.2448 | 11.2884 | 11.3191 | 11.298 | -106.9741
3278.7188 | 117.5491 | -14.4424 | 102.8687 | 1.4211e-13 | -0.022517 | 0.017212 | 0.072719 | -0.002423 | 0.064161 | -0.0099194 | -0.0013631 | 0.024301 | -0.0064458 | 0.021421 | 0.012492 | -2.7826 | 1.3246 | -9.7556 | 101.7702 | 101.6708 | 101.6175 | -15.5673 | 0.033099 | 0.004938 | -0.033458 | -0.048268 | -0.013765 | 0.012329 | -0.095467 | -1.1249 | -1.0985 | 11.6598 | 4.6869 | 5.8117 | -1.1979 | -1.2511 | 14.347 | -102.9169 | 14.4755 | 14.409 | 0.062009 | -102.8824 | -102.8563 | 116.2126 | 116.1132 | 116.06 | 15.7671 | -118.4359 | 14.3942 | 14.4287 | 14.4548 | 14.4474 | -102.9641
3280.4375 | 116.7618 | -7.814 | 107.785 | 1.4211e-13 | -0.021021 | 0.01828 | 0.074855 | -0.0032776 | 0.062024 | -0.0022889 | -0.0017903 | 0.023447 | -0.0062322 | 0.021848 | 0.012065 | 2.945 | 4.5892 | -3.7718 | 109.8236 | 109.6885 | 109.5889 | -8.2456 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.090888 | -0.43157 | 2.0385 | 10.759 | 4.0423 | 4.4738 | 1.9035 | 1.8038 | 7.7231 | -107.8379 | 7.8471 | 7.7714 | 0.048273 | -107.8034 | -107.7727 | 117.6376 | 117.5025 | 117.4029 | 12.4032 | -116.0306 | 7.7612 | 7.7957 | 7.8264 | 7.8144 | -107.8759
3282.2188 | 118.0206 | -9.5718 | 108.2108 | 1.4211e-13 | -0.020808 | 0.018494 | 0.074642 | -0.0032776 | 0.062238 | -0.0022889 | -0.0013631 | 0.023447 | -0.0058048 | 0.021848 | 0.011851 | 2.4413 | 4.2183 | -4.2891 | 109.1231 | 108.9696 | 108.8975 | -8.9462 | 0.033099 | 0.000359 | -0.047194 | -0.057425 | -0.018344 | 0.012329 | -0.095467 | 0.62567 | 0.91231 | 12.0132 | 5.2827 | 4.6571 | 0.75885 | 0.68676 | 9.4764 | -108.2682 | 9.6049 | 9.5246 | 0.048273 | -108.2291 | -108.1984 | 118.6949 | 118.5414 | 118.4694 | 13.7901 | -117.1569 | 9.5144 | 9.5535 | 9.5842 | 9.5722 | -108.3062
3283.9844 | 118.5837 | -2.504 | 115.9653 | 1.4211e-13 | -0.02038 | 0.019348 | 0.075924 | -0.0039186 | 0.06181 | 0.0053411 | -0.0020039 | 0.023874 | -0.0060184 | 0.021634 | 0.012065 | 4.3139 | 5.2851 | -2.2701 | 111.806 | 111.6437 | 111.5668 | -6.5331 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.027501 | 0.007751 | -0.095467 | -4.0291 | -4.1593 | 6.8179 | 0.23389 | 4.263 | -4.3216 | -4.3984 | 2.4085 | -116.0181 | 2.5416 | 2.4568 | 0.048273 | -115.9928 | -115.9575 | 114.31 | 114.1477 | 114.0708 | 7.7891 | -122.4983 | 2.4511 | 2.4765 | 2.5117 | 2.5043 | -116.0607
3285.7656 | 118.7576 | -5.8319 | 112.9486 | 1.4211e-13 | -0.019312 | 0.019989 | 0.07742 | -0.004346 | 0.06117 | -0.0022889 | -0.0017903 | 0.023447 | -0.0062322 | 0.021421 | 0.011851 | 6.8457 | 6.8418 | 0.30291 | 115.7297 | 115.5312 | 115.5044 | -3.4423 | 0.02852 | -0.00422 | -0.047194 | -0.062004 | -0.018344 | 0.007751 | -0.10462 | 2.3896 | 2.7811 | 12.6776 | 6.1348 | 3.7452 | 2.5826 | 2.5558 | 5.7273 | -113.0106 | 5.8604 | 5.7847 | 0.05743 | -112.967 | -112.9409 | 121.5616 | 121.3631 | 121.3363 | 12.6737 | -116.3909 | 5.7699 | 5.8136 | 5.8397 | 5.8277 | -113.0532
3287.5469 | 119.371 | -0.90179 | 118.5287 | 1.4211e-13 | -0.018671 | 0.021058 | 0.077847 | -0.0047732 | 0.060742 | -0.0099194 | -0.0017903 | 0.02366 | -0.0060184 | 0.021421 | 0.012279 | 8.8969 | 7.9865 | 2.354 | 118.6644 | 118.4846 | 118.4118 | -0.80484 | 0.033099 | -0.008798 | -0.047194 | -0.062004 | -0.027501 | 0.003172 | -0.10004 | 0.096951 | 0.13567 | 9.7986 | 3.2558 | 3.1588 | -0.044138 | -0.1169 | 0.80175 | -118.5908 | 0.93489 | 0.8546 | 0.052851 | -118.5562 | -118.5256 | 119.5662 | 119.3864 | 119.3136 | 8.8883 | -119.3336 | 0.83979 | 0.87429 | 0.90497 | 0.893 | -118.6288
3289.2656 | 119.5679 | -0.76904 | 118.6615 | 1.4211e-13 | -0.018885 | 0.021058 | 0.078061 | -0.004987 | 0.060956 | -0.0022889 | -0.0020039 | 0.023233 | -0.0058048 | 0.021421 | 0.011851 | 8.8648 | 7.7988 | 2.2945 | 118.7331 | 118.5625 | 118.4759 | -0.80942 | 0.02852 | -0.008798 | -0.051772 | -0.066582 | -0.03208 | 0.007751 | -0.10004 | -0.040379 | 0.071599 | 9.6338 | 3.0635 | 3.1039 | -0.099047 | -0.18555 | 0.669 | -118.7281 | 0.79756 | 0.71727 | 0.048273 | -118.6936 | -118.6537 | 119.5021 | 119.3315 | 119.245 | 8.5678 | -119.4709 | 0.70246 | 0.73696 | 0.77679 | 0.76025 | -118.7615
3291.0469 | 119.3344 | -1.3275 | 118.0618 | 1.4211e-13 | -0.018671 | 0.021485 | 0.078274 | -0.0047732 | 0.060742 | -0.0099194 | -0.0015767 | 0.023233 | -0.0060184 | 0.021634 | 0.012065 | 8.3291 | 7.5378 | 1.7268 | 117.8907 | 117.7199 | 117.6472 | -1.6382 | 0.023941 | -0.008798 | -0.051772 | -0.066582 | -0.022922 | 0.012329 | -0.10004 | -0.31069 | -0.17115 | 9.6567 | 3.0543 | 3.365 | -0.3419 | -0.41461 | 1.2275 | -118.1284 | 1.3515 | 1.2757 | 0.048273 | -118.0848 | -118.0495 | 119.2182 | 119.0474 | 118.9747 | 8.8653 | -119.7 | 1.2609 | 1.3046 | 1.3398 | 1.3187 | -118.1619
3292.8281 | 119.6869 | -0.84686 | 118.7439 | 1.4211e-13 | -0.018243 | 0.021699 | 0.078915 | -0.0045596 | 0.060956 | -0.0099194 | -0.0015767 | 0.023447 | -0.0060184 | 0.021634 | 0.012065 | 8.9564 | 7.7759 | 2.3448 | 118.875 | 118.6998 | 118.6225 | -0.85063 | 0.019362 | -0.008798 | -0.056351 | -0.062004 | -0.013765 | 0.007751 | -0.10462 | -0.003769 | 0.13113 | 9.8032 | 3.1917 | 3.1955 | -0.044076 | -0.12143 | 0.74224 | -118.8059 | 0.86623 | 0.79051 | 0.048273 | -118.7577 | -118.7361 | 119.7219 | 119.5467 | 119.4693 | 8.6227 | -119.5945 | 0.78486 | 0.8331 | 0.85461 | 0.83807 | -118.8485
3294.6094 | 119.7647 | -0.99792 | 118.602 | 1.4211e-13 | -0.01803 | 0.022126 | 0.079129 | -0.004987 | 0.060956 | -0.01755 | -0.0015767 | 0.02366 | -0.0060184 | 0.021421 | 0.011638 | 8.8007 | 7.666 | 2.2121 | 118.7423 | 118.5716 | 118.4805 | -0.97426 | 0.02852 | -0.008798 | -0.056351 | -0.066582 | -0.018344 | 0.007751 | -0.11378 | 0.023662 | 0.14026 | 9.7986 | 3.21 | 3.1863 | -0.03038 | -0.12146 | 0.88414 | -118.6686 | 1.0264 | 0.94157 | 0.057431 | -118.6203 | -118.5942 | 119.7402 | 119.5695 | 119.4785 | 8.6639 | -119.5763 | 0.93134 | 0.97958 | 1.0057 | 0.98913 | -118.7158
3296.3906 | 119.8425 | -0.81024 | 118.9178 | 1.4211e-13 | -0.017602 | 0.022981 | 0.07977 | -0.0045596 | 0.060742 | 0.0053411 | -0.0017903 | 0.02366 | -0.0058048 | 0.021421 | 0.012065 | 9.0251 | 7.7392 | 2.3815 | 119.0307 | 118.8509 | 118.7827 | -0.76821 | 0.023941 | -0.008798 | -0.051772 | -0.062004 | -0.018344 | -0.001407 | -0.1092 | 0.04203 | 0.11285 | 9.8353 | 3.1917 | 3.1497 | -0.066923 | -0.13513 | 0.70104 | -118.9799 | 0.83418 | 0.75847 | 0.057431 | -118.9362 | -118.9193 | 119.8409 | 119.6612 | 119.593 | 8.5495 | -119.6861 | 0.74824 | 0.7919 | 0.80883 | 0.80144 | -119.027
3298.0938 | 119.9066 | -0.78735 | 118.9316 | 1.4211e-13 | -0.017816 | 0.022767 | 0.07977 | -0.004346 | 0.06117 | -0.01755 | -0.0017903 | 0.023233 | -0.0055912 | 0.021634 | 0.011851 | 9.0983 | 7.8674 | 2.4318 | 119.0856 | 118.915 | 118.8422 | -0.76363 | 0.02852 | -0.008798 | -0.056351 | -0.066582 | -0.022922 | 0.012329 | -0.1092 | 0.023721 | 0.15405 | 9.8857 | 3.2192 | 3.1954 | -0.016551 | -0.089344 | 0.67815 | -118.9982 | 0.81587 | 0.731 | 0.052852 | -118.9545 | -118.9193 | 119.873 | 119.7024 | 119.6296 | 8.6548 | -119.6952 | 0.72077 | 0.76443 | 0.79968 | 0.77856 | -119.0408
3299.875 | 119.8013 | -0.85602 | 119.0277 | 1.4211e-13 | -0.017389 | 0.023195 | 0.080197 | -0.004346 | 0.060956 | -0.0099194 | -0.0013631 | 0.023447 | -0.0058048 | 0.021421 | 0.011638 | 9.1807 | 7.9132 | 2.4639 | 119.136 | 118.9654 | 118.8789 | -0.77737 | 0.037677 | -0.013377 | -0.047194 | -0.062004 | -0.018344 | 0.003172 | -0.1092 | 0.078648 | 0.10829 | 10.0367 | 3.3199 | 3.2412 | -0.062313 | -0.14884 | 0.74682 | -119.0897 | 0.89369 | 0.80882 | 0.062009 | -119.0461 | -119.0245 | 119.992 | 119.8214 | 119.7349 | 8.7692 | -119.8051 | 0.79401 | 0.83767 | 0.85919 | 0.84264 | -119.1369
3301.6094 | 119.8563 | -0.86517 | 119.0781 | 1.4211e-13 | -0.017602 | 0.023408 | 0.080625 | -0.0047732 | 0.06117 | -0.0099194 | -0.0017903 | 0.023019 | -0.0062322 | 0.021207 | 0.011851 | 9.2494 | 7.9499 | 2.4913 | 119.168 | 119.0066 | 118.9155 | -0.78195 | 0.02852 | -0.008798 | -0.056351 | -0.066582 | -0.027501 | 0.007751 | -0.1092 | 0.083225 | 0.089981 | 10.1146 | 3.3565 | 3.2733 | -0.071456 | -0.16257 | 0.75597 | -119.1446 | 0.89369 | 0.80882 | 0.052852 | -119.1056 | -119.0703 | 120.0332 | 119.8718 | 119.7807 | 8.815 | -119.86 | 0.79859 | 0.83767 | 0.87292 | 0.85637 | -119.1873
3303.3906 | 119.9158 | -0.86975 | 119.1284 | 1.4211e-13 | -0.016748 | 0.023622 | 0.080625 | -0.0047732 | 0.061383 | -0.0022889 | -0.0017903 | 0.023447 | -0.0062322 | 0.021634 | 0.011851 | 9.3089 | 8.0048 | 2.5096 | 119.2001 | 119.0295 | 118.943 | -0.79568 | 0.023941 | -0.00422 | -0.056351 | -0.066582 | -0.018344 | -0.001407 | -0.1092 | 0.074066 | 0.071675 | 10.1787 | 3.3794 | 3.3053 | -0.098916 | -0.18545 | 0.76055 | -119.195 | 0.89369 | 0.8134 | 0.052852 | -119.1468 | -119.1298 | 120.0698 | 119.8993 | 119.8127 | 8.8746 | -119.9241 | 0.80317 | 0.85141 | 0.86834 | 0.86553 | -119.2376
3305.125 | 119.9707 | -0.90637 | 119.1147 | 1.4211e-13 | -0.017175 | 0.024049 | 0.080411 | -0.0045596 | 0.061383 | -0.01755 | -0.0017903 | 0.023233 | -0.0060184 | 0.021634 | 0.011851 | 9.2998 | 7.9499 | 2.4959 | 119.223 | 119.0524 | 118.9704 | -0.814 | 0.02852 | -0.013377 | -0.051772 | -0.066582 | -0.022922 | 0.003172 | -0.095467 | 0.092371 | 0.1083 | 10.2061 | 3.4023 | 3.3099 | -0.062288 | -0.14425 | 0.8109 | -119.1813 | 0.93489 | 0.8546 | 0.043695 | -119.1376 | -119.1115 | 120.1294 | 119.9588 | 119.8768 | 8.8562 | -119.9287 | 0.83979 | 0.88345 | 0.90954 | 0.89299 | -119.2102
3306.9062 | 120.0943 | -0.83771 | 119.1238 | 1.4211e-13 | -0.016534 | 0.024477 | 0.081693 | -0.0047732 | 0.061383 | -0.0099194 | -0.0015767 | 0.023233 | -0.0060184 | 0.021634 | 0.011851 | 9.3226 | 8.0231 | 2.5325 | 119.2642 | 119.0845 | 119.0071 | -0.814 | 0.02852 | -0.013377 | -0.06093 | -0.062004 | -0.027501 | 0.007751 | -0.10462 | 0.023707 | 0.14035 | 10.1604 | 3.3702 | 3.3465 | -0.03939 | -0.11677 | 0.73308 | -119.1858 | 0.86623 | 0.77678 | 0.043694 | -119.1513 | -119.1161 | 120.1019 | 119.9222 | 119.8448 | 8.8608 | -119.9378 | 0.7757 | 0.81021 | 0.84546 | 0.82433 | -119.2285
3308.625 | 120.0394 | -0.89264 | 119.1696 | 1.4211e-13 | -0.016534 | 0.024477 | 0.081907 | -0.0045596 | 0.062024 | -0.0099194 | -0.0017903 | 0.023019 | -0.0058048 | 0.021634 | 0.011851 | 9.3913 | 8.1147 | 2.5875 | 119.2917 | 119.1165 | 119.0345 | -0.82316 | 0.02852 | -0.008798 | -0.051772 | -0.066582 | -0.03208 | 0.003172 | -0.10462 | 0.06948 | 0.12204 | 10.284 | 3.4801 | 3.4106 | -0.053115 | -0.13508 | 0.78801 | -119.2362 | 0.92116 | 0.84087 | 0.052852 | -119.2017 | -119.1664 | 120.1843 | 120.0091 | 119.9272 | 9.0073 | -119.9928 | 0.82606 | 0.86056 | 0.89581 | 0.88384 | -119.2742
3310.4062 | 120.1859 | -0.86975 | 119.1925 | 1.4211e-13 | -0.016107 | 0.02469 | 0.082548 | -0.004346 | 0.06181 | -0.0022889 | -0.0017903 | 0.023447 | -0.0060184 | 0.021848 | 0.011638 | 9.4875 | 8.1834 | 2.6241 | 119.3237 | 119.1486 | 119.0712 | -0.81858 | 0.023941 | -0.013377 | -0.051772 | -0.062004 | -0.027501 | 0.003172 | -0.1092 | 0.051171 | 0.13121 | 10.3572 | 3.4939 | 3.4427 | -0.043951 | -0.12134 | 0.76055 | -119.2545 | 0.89369 | 0.81798 | 0.057431 | -119.22 | -119.1893 | 120.1935 | 120.0183 | 119.9409 | 9.0531 | -120.0111 | 0.80775 | 0.84225 | 0.87292 | 0.85637 | -119.3017
3312.125 | 120.1172 | -0.90179 | 119.2657 | 1.4211e-13 | -0.01632 | 0.024904 | 0.082762 | -0.0047732 | 0.06181 | -0.0099194 | -0.0020039 | 0.023447 | -0.0058048 | 0.021634 | 0.011851 | 9.5607 | 8.2063 | 2.6333 | 119.3512 | 119.1806 | 119.0986 | -0.8369 | 0.019362 | -0.017956 | -0.056351 | -0.071161 | -0.027501 | -0.001407 | -0.1092 | 0.064898 | 0.085433 | 10.4625 | 3.5351 | 3.4702 | -0.08514 | -0.16711 | 0.79259 | -119.3369 | 0.92116 | 0.84544 | 0.052852 | -119.2932 | -119.2672 | 120.253 | 120.0824 | 120.0004 | 9.1081 | -120.1026 | 0.83063 | 0.87429 | 0.90039 | 0.88384 | -119.3749
3313.9062 | 120.1813 | -0.92926 | 119.2657 | 1.4211e-13 | -0.016107 | 0.025331 | 0.082548 | -0.0041322 | 0.06181 | 0.0053411 | -0.0022175 | 0.023447 | -0.0060184 | 0.021634 | 0.011424 | 9.5882 | 8.1879 | 2.6287 | 119.3741 | 119.2035 | 119.1261 | -0.85063 | 0.019362 | -0.013377 | -0.06093 | -0.066582 | -0.022922 | 0.007751 | -0.1092 | 0.078628 | 0.10832 | 10.5175 | 3.5579 | 3.4793 | -0.062245 | -0.13964 | 0.82006 | -119.3323 | 0.94862 | 0.86833 | 0.048273 | -119.2887 | -119.258 | 120.3033 | 120.1328 | 120.0554 | 9.1172 | -120.1164 | 0.86268 | 0.90634 | 0.93701 | 0.91588 | -119.3749
3315.7031 | 120.3186 | -0.90637 | 119.2566 | 1.4211e-13 | -0.015893 | 0.0264 | 0.082762 | -0.0047732 | 0.062024 | -0.0099194 | -0.0017903 | 0.023447 | -0.0060184 | 0.021848 | 0.012065 | 9.6019 | 8.2017 | 2.6424 | 119.3924 | 119.2172 | 119.1353 | -0.86895 | 0.033099 | -0.013377 | -0.056351 | -0.066582 | -0.022922 | 0.007751 | -0.10462 | 0.037424 | 0.13579 | 10.5083 | 3.5488 | 3.5114 | -0.039354 | -0.12132 | 0.80175 | -119.3232 | 0.93947 | 0.85002 | 0.048273 | -119.2795 | -119.2488 | 120.2988 | 120.1236 | 120.0416 | 9.1081 | -120.1255 | 0.83979 | 0.88345 | 0.91412 | 0.89299 | -119.3612
3317.4688 | 120.3003 | -0.93384 | 119.2612 | 1.4211e-13 | -0.015038 | 0.025759 | 0.083189 | -0.0045596 | 0.062238 | 0.0053411 | -0.0015767 | 0.023233 | -0.0058048 | 0.021634 | 0.011851 | 9.6202 | 8.2017 | 2.6516 | 119.4015 | 119.2356 | 119.1536 | -0.87811 | 0.02852 | -0.008798 | -0.056351 | -0.066582 | -0.018344 | 0.007751 | -0.1092 | 0.055732 | 0.14037 | 10.5541 | 3.5854 | 3.5297 | -0.025615 | -0.10759 | 0.82464 | -119.3278 | 0.96236 | 0.87749 | 0.052852 | -119.2795 | -119.2534 | 120.3354 | 120.1694 | 120.0874 | 9.1355 | -120.1393 | 0.86726 | 0.91549 | 0.94159 | 0.92504 | -119.3704
3319.2031 | 120.3781 | -0.95673 | 119.2886 | 1.4211e-13 | -0.015038 | 0.026186 | 0.083616 | -0.004346 | 0.062238 | -0.0099194 | -0.0017903 | 0.023447 | -0.0060184 | 0.021421 | 0.011638 | 9.6889 | 8.3116 | 2.6836 | 119.3924 | 119.2264 | 119.1444 | -0.91932 | 0.02852 | -0.017956 | -0.06093 | -0.066582 | -0.022922 | -0.001407 | -0.11836 | 0.03741 | 0.10375 | 10.6456 | 3.6403 | 3.6029 | -0.062239 | -0.14421 | 0.83837 | -119.3552 | 0.98525 | 0.8958 | 0.057431 | -119.3116 | -119.29 | 120.3491 | 120.1831 | 120.1012 | 9.2683 | -120.208 | 0.89014 | 0.9338 | 0.95532 | 0.93877 | -119.407
3320.9844 | 120.2957 | -1.0071 | 119.339 | 1.4211e-13 | -0.014825 | 0.026827 | 0.08383 | -0.004346 | 0.062238 | -0.0022889 | -0.0015767 | 0.023233 | -0.0060184 | 0.022062 | 0.011851 | 9.7164 | 8.339 | 2.7111 | 119.4199 | 119.2539 | 119.1765 | -0.92847 | 0.023941 | -0.013377 | -0.06093 | -0.066582 | -0.022922 | 0.003172 | -0.1092 | 0.078606 | 0.080867 | 10.7235 | 3.7182 | 3.6396 | -0.085119 | -0.16251 | 0.89788 | -119.4056 | 1.031 | 0.94615 | 0.048273 | -119.3619 | -119.3358 | 120.4269 | 120.261 | 120.1836 | 9.3461 | -120.2675 | 0.9405 | 0.98416 | 1.0103 | 0.9937 | -119.4482
3322.7656 | 120.4605 | -0.97961 | 119.2932 | 1.4211e-13 | -0.014184 | 0.026827 | 0.084044 | -0.0045596 | 0.062238 | -0.0099194 | -0.0015767 | 0.02366 | -0.0062322 | 0.021421 | 0.011638 | 9.7988 | 8.4672 | 2.766 | 119.4427 | 119.2676 | 119.1948 | -0.93763 | 0.023941 | -0.017956 | -0.051772 | -0.071161 | -0.03208 | -0.001407 | -0.1092 | 0.041982 | 0.14954 | 10.7784 | 3.7456 | 3.7037 | -0.025606 | -0.098424 | 0.87041 | -119.3644 | 1.0036 | 0.92784 | 0.057431 | -119.3253 | -119.2946 | 120.4224 | 120.2472 | 120.1744 | 9.4469 | -120.2308 | 0.90845 | 0.94753 | 0.97821 | 0.96166 | -119.4024
3324.5469 | 120.4788 | -0.97961 | 119.3527 | 1.4211e-13 | -0.014397 | 0.027255 | 0.084471 | -0.004346 | 0.062451 | -0.0022889 | -0.0017903 | 0.023447 | -0.0060184 | 0.022062 | 0.011851 | 9.8308 | 8.4856 | 2.7843 | 119.4702 | 119.3042 | 119.2131 | -0.94221 | 0.023941 | -0.008798 | -0.056351 | -0.071161 | -0.03208 | 0.003172 | -0.10462 | 0.037403 | 0.1175 | 10.8105 | 3.764 | 3.7266 | -0.048484 | -0.13962 | 0.87499 | -119.4239 | 1.0036 | 0.92326 | 0.048273 | -119.3848 | -119.3495 | 120.4498 | 120.2839 | 120.1927 | 9.4652 | -120.2949 | 0.90845 | 0.94753 | 0.98279 | 0.97082 | -119.4573
3326.3438 | 120.369 | -1.0208 | 119.3939 | 1.4211e-13 | -0.014184 | 0.027468 | 0.084898 | -0.0045596 | 0.062238 | -0.01755 | -0.0015767 | 0.023447 | -0.0058048 | 0.021848 | 0.011638 | 9.7896 | 8.4764 | 2.8027 | 119.5023 | 119.3226 | 119.236 | -0.94679 | 0.023941 | -0.013377 | -0.056351 | -0.066582 | -0.03208 | 0.003172 | -0.10462 | 0.074023 | 0.10835 | 10.8105 | 3.8235 | 3.7494 | -0.071367 | -0.15793 | 0.91619 | -119.4605 | 1.0448 | 0.96446 | 0.048273 | -119.426 | -119.3907 | 120.5231 | 120.3434 | 120.2568 | 9.4972 | -120.3407 | 0.95423 | 0.98873 | 1.024 | 1.0074 | -119.4985
3328.0469 | 120.3918 | -1.0254 | 119.4077 | 1.4211e-13 | -0.013543 | 0.027896 | 0.085326 | -0.004346 | 0.062451 | -0.0099194 | -0.0022175 | 0.023233 | -0.0064458 | 0.021634 | 0.011424 | 9.9316 | 8.6824 | 2.9125 | 119.5297 | 119.3592 | 119.2589 | -0.94679 | 0.023941 | -0.013377 | -0.056351 | -0.071161 | -0.022922 | 0.003172 | -0.1092 | 0.078601 | 0.12208 | 10.957 | 3.9379 | 3.8593 | -0.048469 | -0.14876 | 0.91619 | -119.4788 | 1.0493 | 0.96904 | 0.052852 | -119.4306 | -119.4045 | 120.5551 | 120.3846 | 120.2843 | 9.7078 | -120.3544 | 0.95423 | 1.0025 | 1.0286 | 1.012 | -119.5169
3329.8281 | 120.4651 | -3.3463 | 117.0547 | 1.4211e-13 | -0.021662 | 0.019776 | 0.40713 | 0.0012092 | 0.077408 | -0.0022889 | -0.0022175 | 0.02366 | -0.0058048 | 0.021848 | 0.011638 | 18.7541 | 23.54 | 7.5641 | 117.1902 | 117.0239 | 116.9421 | -3.2317 | -0.003531 | -0.027113 | -0.065509 | -0.089475 | -0.045815 | -0.015142 | -0.1321 | 0.11458 | 0.13543 | 22.1004 | 10.9103 | 10.7957 | -0.030816 | -0.11263 | 3.2142 | -117.1442 | 3.3427 | 3.2807 | 0.066588 | -117.1006 | -117.0699 | 120.5364 | 120.3702 | 120.2884 | 26.8863 | -120.2864 | 3.2568 | 3.3004 | 3.3311 | 3.3191 | -117.1868
3331.5469 | 120.4056 | -5.2917 | 115.1093 | 1.4211e-13 | -0.024226 | 0.016784 | 0.67103 | 0.0031322 | 0.082749 | -0.0022889 | -0.0017903 | 0.02366 | -0.0058048 | 0.021848 | 0.011424 | 21.1303 | 26.7817 | 7.8525 | 115.2444 | 115.087 | 114.9916 | -5.1411 | -0.012689 | -0.045428 | -0.088402 | -0.10779 | -0.06413 | -0.033457 | -0.14583 | 0.15066 | 0.13511 | 26.4221 | 13.1442 | 12.9936 | -0.022205 | -0.11762 | 5.1459 | -115.217 | 5.2791 | 5.2033 | 0.057431 | -115.1734 | -115.1427 | 120.5361 | 120.3788 | 120.2834 | 32.0734 | -120.2503 | 5.184 | 5.2276 | 5.2583 | 5.2463 | -115.2551
3333.3125 | 120.433 | -6.459 | 113.9648 | 1.4211e-13 | -0.023799 | 0.016998 | 0.8298 | 0.0031322 | 0.082963 | -0.0099194 | -0.0022175 | 0.02366 | -0.0060184 | 0.022062 | 0.012065 | 20.1551 | 26.0124 | 6.9277 | 114.054 | 113.9011 | 113.8104 | -6.3133 | -0.026425 | -0.059164 | -0.10214 | -0.12152 | -0.077866 | -0.047193 | -0.15957 | 0.14576 | 0.089141 | 26.6142 | 13.3867 | 13.241 | -0.063737 | -0.15449 | 6.2995 | -114.0864 | 6.4326 | 6.3569 | 0.057432 | -114.0427 | -114.012 | 120.513 | 120.3602 | 120.2694 | 32.4715 | -120.2781 | 6.3375 | 6.3812 | 6.4119 | 6.3999 | -114.1244
3335.0156 | 120.5292 | -7.6355 | 112.7151 | 1.4211e-13 | -0.024226 | 0.016357 | 0.9516 | 0.003987 | 0.084459 | 0.0053411 | -0.0022175 | 0.02366 | -0.0058048 | 0.021848 | 0.011638 | 20.178 | 26.484 | 6.6942 | 113.1612 | 113.0036 | 112.9221 | -7.2062 | -0.031003 | -0.068322 | -0.1113 | -0.13526 | -0.087023 | -0.060928 | -0.16415 | 0.42932 | 0.44605 | 27.8135 | 14.3297 | 13.9004 | 0.28849 | 0.20695 | 7.4713 | -112.8504 | 7.6045 | 7.5242 | 0.052853 | -112.8022 | -112.7761 | 120.7967 | 120.6391 | 120.5576 | 34.1195 | -119.9213 | 7.5002 | 7.5485 | 7.5746 | 7.5672 | -112.8793
3336.8125 | 120.4285 | -6.9855 | 113.443 | 1.4211e-13 | -0.024654 | 0.015716 | 0.9922 | 0.0048416 | 0.086595 | -0.0099194 | -0.0020039 | 0.023233 | -0.0060184 | 0.021848 | 0.011851 | 21.9315 | 28.6223 | 7.6007 | 112.9964 | 112.848 | 112.7481 | -7.3848 | -0.040161 | -0.068322 | -0.1113 | -0.12152 | -0.082444 | -0.05635 | -0.16415 | -0.39928 | -0.44661 | 28.917 | 14.5862 | 14.9855 | -0.59504 | -0.69488 | 6.8213 | -113.5645 | 6.9453 | 6.8742 | 0.052853 | -113.5254 | -113.4993 | 119.9819 | 119.8334 | 119.7336 | 35.6077 | -120.8278 | 6.8639 | 6.903 | 6.9291 | 6.9172 | -113.6071
3338.5938 | 120.4788 | -6.5186 | 113.9648 | 1.4211e-13 | -0.025081 | 0.014648 | 0.87916 | 0.0048416 | 0.088946 | -0.0022889 | -0.0017903 | 0.023019 | -0.0055912 | 0.021848 | 0.011638 | 24.5412 | 31.113 | 9.1161 | 113.9258 | 113.7775 | 113.6776 | -6.4827 | -0.017267 | -0.054586 | -0.10214 | -0.11695 | -0.077866 | -0.047193 | -0.15041 | 0.035846 | -0.039053 | 31.0598 | 15.6347 | 15.5988 | -0.18737 | -0.28727 | 6.3681 | -114.0818 | 6.5013 | 6.4164 | 0.048274 | -114.0427 | -114.012 | 120.4443 | 120.296 | 120.1961 | 37.6316 | -120.4476 | 6.4016 | 6.4407 | 6.4714 | 6.464 | -114.1153
3340.375 | 120.4788 | -10.08 | 110.408 | 1.4211e-13 | -0.024226 | 0.016571 | 1.3228 | 0.003987 | 0.086595 | -0.0099194 | -0.0024313 | 0.023447 | -0.0055912 | 0.022275 | 0.011638 | 19.3081 | 25.7377 | 5.0689 | 110.6248 | 110.4761 | 110.3901 | -9.7292 | -0.058476 | -0.091215 | -0.13419 | -0.14899 | -0.10992 | -0.083821 | -0.19162 | 0.35079 | 0.21675 | 29.3881 | 15.1489 | 14.7981 | 0.068051 | -0.017884 | 9.8883 | -110.557 | 10.0215 | 9.9458 | 0.057433 | -110.5179 | -110.4918 | 120.7047 | 120.556 | 120.4701 | 35.8177 | -120.1372 | 9.931 | 9.97 | 9.9961 | 9.9887 | -110.5996
3342.1094 | 120.6116 | -11.618 | 108.6823 | 1.4211e-13 | -0.024226 | 0.017212 | 1.6003 | 0.0037732 | 0.085741 | -0.0099194 | -0.0026449 | 0.023874 | -0.0058048 | 0.022275 | 0.011424 | 16.9777 | 23.0318 | 3.0957 | 108.9628 | 108.8048 | 108.7281 | -11.3593 | -0.072212 | -0.10953 | -0.14335 | -0.16731 | -0.12823 | -0.092979 | -0.1962 | 0.25878 | 0.28057 | 28.5958 | 14.7137 | 14.4549 | 0.12251 | 0.045852 | 11.4218 | -108.8496 | 11.5458 | 11.4747 | 0.052853 | -108.8105 | -108.7752 | 120.5809 | 120.4228 | 120.3461 | 34.6498 | -120.0415 | 11.4507 | 11.4898 | 11.5251 | 11.5085 | -108.8785
3343.875 | 120.4468 | -16.4795 | 103.8757 | 1.4211e-13 | -0.024867 | 0.016357 | 2.3662 | 0.0052688 | 0.088732 | -0.01755 | -0.0032857 | 0.024088 | -0.0055912 | 0.021848 | 0.011851 | 14.5374 | 21.5758 | -0.031301 | 104.4302 | 104.2762 | 104.1907 | -15.7413 | -0.12258 | -0.15074 | -0.19829 | -0.21309 | -0.16944 | -0.14334 | -0.24199 | 0.7382 | 0.55448 | 31.0169 | 16.4482 | 15.71 | 0.40048 | 0.31498 | 16.2375 | -104.0888 | 16.3569 | 16.2812 | 0.043698 | -104.0452 | -104.0191 | 120.9097 | 120.7557 | 120.6702 | 38.0553 | -119.617 | 16.2664 | 16.3101 | 16.3361 | 16.3288 | -104.1177
3345.6562 | 120.5154 | -11.7828 | 108.5449 | 1.4211e-13 | -0.024867 | 0.014861 | 2.0696 | 0.0059098 | 0.092151 | -0.01755 | -0.0037131 | 0.024942 | -0.0062322 | 0.022062 | 0.011851 | 20.7411 | 26.8091 | 4.2723 | 107.8411 | 107.7058 | 107.5651 | -12.3071 | -0.085948 | -0.11411 | -0.15708 | -0.18105 | -0.14197 | -0.11129 | -0.20536 | -0.52426 | -0.70381 | 32.524 | 16.0551 | 16.5794 | -0.8391 | -0.97978 | 11.5775 | -108.726 | 11.6969 | 11.6258 | 0.048275 | -108.6869 | -108.6562 | 119.624 | 119.4887 | 119.348 | 38.592 | -120.852 | 11.6018 | 11.6409 | 11.6715 | 11.6687 | -108.7503
3347.3594 | 120.4697 | -16.0629 | 104.2282 | 1.4211e-13 | -0.024013 | 0.016998 | 2.56 | 0.0050552 | 0.088946 | -0.0022889 | -0.0037131 | 0.02537 | -0.0060184 | 0.021848 | 0.011851 | 15.9384 | 21.7681 | 1.0034 | 105.7717 | 105.5904 | 105.546 | -14.4226 | -0.11342 | -0.137 | -0.18455 | -0.20852 | -0.16486 | -0.14334 | -0.23283 | 1.6404 | 1.5435 | 32.0013 | 17.0663 | 15.426 | 1.3621 | 1.3178 | 15.8301 | -104.4367 | 15.9495 | 15.8784 | 0.048276 | -104.3931 | -104.3716 | 121.8346 | 121.6533 | 121.6089 | 37.831 | -118.6508 | 15.8544 | 15.8981 | 15.9196 | 15.9259 | -104.461
3349.1406 | 120.575 | -6.5048 | 113.9465 | 1.4211e-13 | -0.025295 | 0.014861 | 1.0715 | 0.0059098 | 0.093646 | -0.01755 | -0.0022175 | 0.023874 | -0.0062322 | 0.022062 | 0.012065 | 28.6297 | 33.0131 | 10.7551 | 114.4615 | 114.3041 | 114.1995 | -5.9653 | -0.017267 | -0.063743 | -0.10214 | -0.11695 | -0.082444 | -0.047193 | -0.15041 | 0.53953 | 0.51493 | 35.1345 | 17.2599 | 16.7204 | 0.35752 | 0.253 | 6.3544 | -114.0635 | 6.4876 | 6.4027 | 0.048274 | -114.029 | -113.9937 | 120.9663 | 120.8089 | 120.7044 | 39.518 | -119.9118 | 6.3879 | 6.4224 | 6.4576 | 6.4411 | -114.0969
3350.9062 | 120.5292 | -5.6946 | 114.8529 | 1.4211e-13 | -0.025722 | 0.013365 | 1.0012 | 0.0076192 | 0.099843 | -0.0022889 | -0.0026449 | 0.024301 | -0.0060184 | 0.022062 | 0.012065 | 32.5213 | 38.686 | 13.5296 | 114.9056 | 114.7482 | 114.6437 | -5.5761 | -0.021846 | -0.050007 | -0.097559 | -0.11695 | -0.077866 | -0.047193 | -0.15041 | 0.1185 | 0.052661 | 38.2159 | 19.2241 | 19.1056 | -0.1047 | -0.20925 | 5.5442 | -114.9699 | 5.6727 | 5.597 | 0.052853 | -114.9308 | -114.9001 | 120.6001 | 120.4428 | 120.3382 | 44.3806 | -120.429 | 5.5776 | 5.6167 | 5.6474 | 5.6446 | -115.0033
3352.625 | 120.5704 | -7.1503 | 113.3835 | 1.4211e-13 | -0.024654 | 0.014007 | 1.2544 | 0.0078328 | 0.099415 | 0.0053411 | -0.0022175 | 0.023874 | -0.0060184 | 0.021634 | 0.011638 | 31.656 | 37.0148 | 11.9958 | 113.381 | 113.2234 | 113.1236 | -7.078 | -0.035582 | -0.0729 | -0.12045 | -0.13068 | -0.091601 | -0.060928 | -0.16415 | 0.072299 | -0.002522 | 38.8063 | 19.1461 | 19.0738 | -0.16006 | -0.25992 | 6.9861 | -113.5142 | 7.1147 | 7.0298 | 0.043696 | -113.4751 | -113.4444 | 120.5312 | 120.3737 | 120.2738 | 44.1651 | -120.4615 | 7.0196 | 7.0587 | 7.0893 | 7.0774 | -113.5476
3354.4062 | 120.4926 | -15.3946 | 105.0613 | 1.4211e-13 | -0.025081 | 0.012297 | 2.694 | 0.0080466 | 0.13168 | -0.0022889 | -0.0037131 | 0.025156 | -0.0060184 | 0.021634 | 0.011638 | 77.6917 | 30.8978 | 4.8675 | 105.2955 | 105.192 | 105.1064 | -14.9675 | -0.12716 | -0.14616 | -0.19829 | -0.21309 | -0.17402 | -0.13876 | -0.23283 | 0.42713 | 0.23419 | 93.0863 | 20.2621 | 19.8349 | 0.13065 | 0.045089 | 15.1618 | -105.2744 | 15.2674 | 15.1963 | 0.03454 | -105.2354 | -105.2001 | 120.6901 | 120.5866 | 120.501 | 46.2924 | -120.0288 | 15.1815 | 15.2206 | 15.2558 | 15.2484 | -105.2942
3356.1406 | 120.5109 | -8.9172 | 111.5845 | 1.4211e-13 | -0.025936 | 0.011015 | 2.0952 | 0.0089012 | 0.13787 | -0.0022889 | -0.0030721 | 0.024942 | -0.0060184 | 0.021848 | 0.011638 | 89.275 | 35.6825 | 9.2672 | 109.0864 | 108.9513 | 108.8243 | -11.1532 | -0.07679 | -0.10495 | -0.1525 | -0.17647 | -0.13281 | -0.10214 | -0.20536 | -2.236 | -2.498 | 98.1923 | 18.1844 | 20.4204 | -2.6332 | -2.7602 | 8.7119 | -111.7609 | 8.8404 | 8.7647 | 0.052854 | -111.7173 | -111.6866 | 118.0037 | 117.8685 | 117.7415 | 44.5997 | -122.7377 | 8.7408 | 8.7844 | 8.8151 | 8.8123 | -111.7898
3357.9062 | 120.4468 | -28.1708 | 91.9235 | 1.4211e-13 | -0.026577 | 0.014648 | 5.5877 | 0.0089012 | 0.12612 | -0.0099194 | -0.0037131 | 0.025583 | -0.0058048 | 0.022275 | 0.011638 | 53.4995 | 19.4971 | -7.1276 | 91.6794 | 91.6109 | 91.508 | -27.9533 | -0.25994 | -0.26978 | -0.32649 | -0.35045 | -0.31595 | -0.2807 | -0.36562 | 0.21749 | -0.24412 | 81.6703 | 21.0431 | 20.8257 | -0.31262 | -0.41554 | 27.8052 | -92.274 | 27.9108 | 27.8443 | 0.039122 | -92.2395 | -92.2042 | 119.8502 | 119.7817 | 119.6788 | 47.6679 | -119.8768 | 27.8203 | 27.8548 | 27.8901 | 27.901 | -92.2891
3359.6875 | 120.3232 | -33.4671 | 86.5173 | 1.4211e-13 | -0.028072 | 0.052469 | 6.3304 | 0.010183 | 0.13125 | -0.0099194 | -0.0045677 | 0.02537 | -0.0053776 | 0.022062 | 0.012065 | 53.9757 | 17.3955 | -10.6621 | 86.6569 | 86.5695 | 86.5173 | -32.7795 | -0.32404 | -0.33847 | -0.38144 | -0.41913 | -0.38005 | -0.34938 | -0.42514 | 0.68763 | 0.13958 | 87.4428 | 22.805 | 22.1174 | 0.052172 | -3.2e-05 | 33.042 | -86.9365 | 33.1431 | 33.0857 | 0.043702 | -86.8974 | -86.8667 | 120.124 | 120.0366 | 119.9844 | 50.8626 | -119.2968 | 33.048 | 33.087 | 33.1177 | 33.1286 | -86.9425
3361.4688 | 120.4239 | -31.3477 | 88.6597 | 1.4211e-13 | -0.027218 | 1.082 | 3.5023 | 0.010824 | 0.14087 | -0.0022889 | -0.0043539 | 0.02537 | -0.0055912 | 0.022062 | 0.011638 | 70.7555 | 23.3111 | -5.6443 | 91.0476 | 90.9195 | 90.8532 | -28.7683 | -0.28741 | -0.31099 | -0.34939 | -0.37792 | -0.33885 | -0.31733 | -0.38851 | 2.5793 | 2.3879 | 102.1031 | 25.7034 | 23.1241 | 2.2598 | 2.1936 | 30.9591 | -89.0376 | 31.0602 | 30.9983 | 0.039122 | -88.9985 | -88.977 | 122.3952 | 122.2671 | 122.2009 | 54.6587 | -117.428 | 30.9697 | 31.0088 | 31.0303 | 31.0367 | -89.0482
3363.1875 | 120.4559 | -14.5981 | 105.5603 | 1.4211e-13 | -0.025508 | 0.78432 | 2.5273 | 0.0097558 | 0.14386 | 0.0053411 | -0.0028585 | 0.024088 | -0.0053776 | 0.021848 | 0.011638 | 91.0835 | 34.2539 | 7.0833 | 105.3001 | 105.1554 | 105.0561 | -14.7202 | -0.12258 | -0.15532 | -0.19829 | -0.20852 | -0.17402 | -0.14792 | -0.24199 | -0.12211 | -0.2602 | 105.6816 | 21.6814 | 21.8035 | -0.40494 | -0.50424 | 14.3561 | -105.7688 | 14.4755 | 14.3998 | 0.043698 | -105.7343 | -105.7082 | 119.8982 | 119.7534 | 119.6541 | 48.852 | -120.2805 | 14.3896 | 14.4241 | 14.4502 | 14.4428 | -105.8023
3364.9531 | 120.4147 | -21.2997 | 98.9365 | 1.4211e-13 | -0.025295 | 1.0021 | 3.2906 | 0.01061 | 0.14493 | -0.0099194 | -0.0032857 | 0.024729 | -0.0055912 | 0.021848 | 0.011851 | 83.7947 | 29.451 | 1.333 | 98.3776 | 98.2412 | 98.1607 | -21.4329 | -0.19584 | -0.21942 | -0.26239 | -0.29093 | -0.25643 | -0.2166 | -0.31525 | -0.13315 | -0.55888 | 105.0944 | 22.6328 | 22.7659 | -0.69528 | -0.77577 | 20.9845 | -99.2274 | 21.1039 | 21.0374 | 0.052857 | -99.1929 | -99.1531 | 119.6773 | 119.5409 | 119.4604 | 50.7507 | -120.3694 | 21.0088 | 21.0433 | 21.0831 | 21.0803 | -99.2517
3366.75 | 120.575 | -11.8103 | 108.5266 | 1.4211e-13 | -0.024867 | 0.60547 | 2.0775 | 0.0099694 | 0.14599 | 0.0053411 | -0.0028585 | 0.024088 | -0.0055912 | 0.022275 | 0.011424 | 95.9366 | 36.6531 | 10.0043 | 108.2806 | 108.1271 | 108.0322 | -11.8721 | -0.090527 | -0.12784 | -0.16166 | -0.18562 | -0.15112 | -0.11587 | -0.2191 | -0.061801 | -0.24597 | 107.7469 | 21.8146 | 21.8764 | -0.39953 | -0.49446 | 11.5912 | -108.7122 | 11.7198 | 11.6486 | 0.057434 | -108.6777 | -108.6425 | 120.0909 | 119.9374 | 119.8425 | 48.4634 | -120.3987 | 11.6247 | 11.6592 | 11.6944 | 11.6825 | -108.7457
3368.4688 | 120.3964 | -15.5731 | 104.8462 | 1.4211e-13 | -0.022944 | 0.99778 | 3.4357 | 0.01061 | 0.14535 | -0.0099194 | -0.0032857 | 0.024088 | -0.0058048 | 0.022275 | 0.011638 | 87.0133 | 31.2504 | 3.8236 | 100.9277 | 100.7916 | 100.6881 | -18.8916 | -0.15463 | -0.18279 | -0.22118 | -0.24972 | -0.20607 | -0.18455 | -0.27404 | -3.3185 | -3.9184 | 102.5864 | 19.3967 | 22.7152 | -4.0545 | -4.1581 | 15.2991 | -105.0959 | 15.4185 | 15.3519 | 0.052855 | -105.0523 | -105.0307 | 116.5009 | 116.3648 | 116.2612 | 46.8235 | -123.7378 | 15.3234 | 15.3671 | 15.3886 | 15.3903 | -105.1202
3370.25 | 120.0714 | -44.7372 | 75.0458 | 1.4211e-13 | 0.63987 | 3.4143 | 5.396 | 0.013174 | 0.14129 | -0.0099194 | -0.0047813 | 0.025156 | -0.0049502 | 0.022275 | 0.011638 | 50.986 | 12.2263 | -18.262 | 74.6753 | 74.5361 | 74.5214 | -44.126 | -0.47972 | -0.48498 | -0.54169 | -0.57022 | -0.53573 | -0.50963 | -0.58082 | 0.6112 | -0.37051 | 95.7232 | 26.4752 | 25.864 | -0.50968 | -0.52441 | 44.1564 | -75.616 | 44.2575 | 44.1955 | 0.039127 | -75.5815 | -75.5554 | 119.4125 | 119.2733 | 119.2586 | 56.9635 | -119.1718 | 44.167 | 44.2015 | 44.2276 | 44.2523 | -75.6266
3372.0312 | 120.5017 | -0.27466 | 120.2362 | 1.4211e-13 | -0.033842 | 0.023622 | 0.071223 | -0.00691 | -0.0091255 | 0.0053411 | -0.0024313 | 0.023233 | -0.0060184 | 0.022275 | 0.011424 | 0.33069 | 0.17081 | -0.27853 | 0.56491 | 0.5132 | 0.6914 | -0.42479 | 0.023941 | -0.008798 | -0.06093 | -0.066582 | -0.027501 | -0.010564 | -0.10462 | -0.15013 | -119.6713 | 0.60535 | -0.00387 | 0.14626 | -119.723 | -119.5448 | 0.17003 | -120.3028 | 0.2986 | 0.21373 | 0.043694 | -120.2637 | -120.2468 | 0.83957 | 0.78786 | 0.96606 | 0.44547 | -120.661 | 0.20808 | 0.24716 | 0.26409 | 0.26586 | -120.3408
3373.8125 | 120.607 | -0.28839 | 120.4285 | 1.4211e-13 | -0.038756 | 0.0080237 | 0.023999 | -0.0071236 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023447 | -0.0055912 | 0.021848 | 0.01121 | 0.069723 | 0.12045 | -0.11371 | 0.11165 | 0.096516 | 0.23354 | -0.23706 | 0.037677 | 0.004938 | -0.047194 | -0.057425 | -0.027501 | 0.016908 | -0.10462 | 0.051335 | -120.3168 | 0.35811 | 0.17468 | 0.12335 | -120.332 | -120.1949 | 0.18377 | -120.4859 | 0.32607 | 0.2412 | 0.05743 | -120.456 | -120.4116 | 0.40004 | 0.38491 | 0.52193 | 0.40884 | -120.6655 | 0.23097 | 0.26089 | 0.3053 | 0.29333 | -120.5331
3375.5312 | 120.7306 | -0.24719 | 120.433 | 1.4211e-13 | -0.03897 | 0.0078099 | 0.023571 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023233 | -0.0060184 | 0.021848 | 0.011638 | 0.065145 | 0.11587 | -0.095397 | 0.097912 | 0.08278 | 0.21522 | -0.23706 | 0.033099 | -0.00422 | -0.042615 | -0.057425 | -0.018344 | 0.007751 | -0.095467 | 0.010136 | -120.3351 | 0.31234 | 0.1518 | 0.14166 | -120.3503 | -120.2178 | 0.15172 | -120.4905 | 0.28029 | 0.20458 | 0.052852 | -120.4514 | -120.4253 | 0.3451 | 0.32997 | 0.46242 | 0.36306 | -120.6701 | 0.18977 | 0.22885 | 0.25494 | 0.24297 | -120.5285
3377.3281 | 120.6802 | -0.28381 | 120.5292 | 1.4211e-13 | -0.03897 | 0.0078099 | 0.023144 | -0.0071236 | -0.0097665 | -0.0022889 | -0.0020039 | 0.023447 | -0.0064458 | 0.022062 | 0.011851 | 0.060567 | 0.11129 | -0.090818 | 0.093333 | 0.091937 | 0.20607 | -0.23248 | 0.037677 | 0.000359 | -0.038036 | -0.062004 | -0.013765 | 0.016908 | -0.10462 | 0.051336 | -120.4358 | 0.34438 | 0.19299 | 0.14166 | -120.4372 | -120.3231 | 0.17919 | -120.5912 | 0.32149 | 0.24578 | 0.066588 | -120.5429 | -120.5123 | 0.37715 | 0.37575 | 0.48988 | 0.39511 | -120.7617 | 0.22181 | 0.27005 | 0.30072 | 0.28417 | -120.6338
3379.0938 | 120.7855 | -0.26093 | 120.5612 | 1.4211e-13 | -0.03897 | 0.0075963 | 0.02293 | -0.0071236 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023233 | -0.0060184 | 0.021848 | 0.011638 | 0.055988 | 0.11587 | -0.08624 | 0.079598 | 0.073622 | 0.19691 | -0.23706 | 0.037677 | -0.008798 | -0.038036 | -0.052847 | -0.013765 | 0.007751 | -0.090888 | 0.023869 | -120.4816 | 0.31691 | 0.17469 | 0.15082 | -120.4876 | -120.3643 | 0.17004 | -120.6141 | 0.2986 | 0.22289 | 0.052852 | -120.575 | -120.5535 | 0.34052 | 0.33455 | 0.45783 | 0.3768 | -120.7983 | 0.20808 | 0.24716 | 0.26868 | 0.25213 | -120.6521
3380.875 | 120.8954 | -0.23804 | 120.5154 | 1.4211e-13 | -0.039397 | 0.0080237 | 0.022717 | -0.00691 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023019 | -0.0060184 | 0.021848 | 0.011424 | 0.046831 | 0.11587 | -0.081662 | 0.07502 | 0.064464 | 0.18775 | -0.23706 | 0.037677 | 0.000359 | -0.042615 | -0.057425 | -0.009187 | 0.016908 | -0.10462 | 0.000981 | -120.4404 | 0.28487 | 0.15637 | 0.15539 | -120.451 | -120.3277 | 0.13341 | -120.5729 | 0.27571 | 0.19542 | 0.062009 | -120.5246 | -120.4985 | 0.31306 | 0.3025 | 0.42579 | 0.35391 | -120.7525 | 0.18061 | 0.22885 | 0.25494 | 0.2384 | -120.6201
3382.6562 | 120.8817 | -0.24719 | 120.5933 | 1.4211e-13 | -0.039611 | 0.0078099 | 0.022717 | -0.0071236 | -0.0097665 | -0.0022889 | -0.0017903 | 0.023019 | -0.0062322 | 0.022275 | 0.011638 | 0.037675 | 0.10671 | -0.081662 | 0.070441 | 0.059885 | 0.18775 | -0.23706 | 0.037677 | 0.000359 | -0.047194 | -0.048268 | -0.013765 | 0.012329 | -0.10004 | 0.010136 | -120.5228 | 0.28487 | 0.16553 | 0.15539 | -120.5334 | -120.4055 | 0.14715 | -120.6415 | 0.28487 | 0.2 | 0.052851 | -120.607 | -120.5809 | 0.31763 | 0.30708 | 0.43494 | 0.35391 | -120.8303 | 0.19892 | 0.23343 | 0.25952 | 0.24755 | -120.6933
3384.4375 | 120.8359 | -0.27466 | 120.5887 | 1.4211e-13 | -0.039183 | 0.0075963 | 0.023144 | -0.0071236 | -0.0093393 | 0.0053411 | -0.0013631 | 0.023019 | -0.0058048 | 0.022275 | 0.011424 | 0.037675 | 0.11129 | -0.08624 | 0.065863 | 0.055306 | 0.18317 | -0.24163 | 0.033099 | -0.00422 | -0.047194 | -0.057425 | -0.013765 | 0.012329 | -0.095467 | 0.033023 | -120.5228 | 0.31233 | 0.18842 | 0.1554 | -120.5334 | -120.4055 | 0.17919 | -120.6461 | 0.30776 | 0.22746 | 0.048273 | -120.6024 | -120.5764 | 0.34052 | 0.32996 | 0.45783 | 0.38595 | -120.8303 | 0.21723 | 0.26089 | 0.28699 | 0.27044 | -120.6842
3386.2344 | 120.9824 | -0.24719 | 120.5566 | 1.4211e-13 | -0.038756 | 0.0078099 | 0.02293 | -0.00691 | -0.0093393 | -0.0022889 | -0.0020039 | 0.023447 | -0.0058048 | 0.022489 | 0.011638 | 0.033096 | 0.12045 | -0.081662 | 0.065863 | 0.059885 | 0.17402 | -0.24621 | 0.033099 | 0.000359 | -0.038036 | -0.052847 | -0.022922 | 0.016908 | -0.090888 | 0.000978 | -120.4908 | 0.28029 | 0.16553 | 0.16455 | -120.4968 | -120.3826 | 0.1563 | -120.6095 | 0.28029 | 0.20916 | 0.052852 | -120.5796 | -120.5397 | 0.31305 | 0.30708 | 0.42121 | 0.36764 | -120.8029 | 0.19434 | 0.22427 | 0.2641 | 0.24755 | -120.6475
3387.9375 | 120.9366 | -0.24719 | 120.5978 | 1.4211e-13 | -0.039183 | 0.0075963 | 0.02293 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023233 | -0.0062322 | 0.021848 | 0.011638 | 0.037675 | 0.11129 | -0.081662 | 0.065863 | 0.055306 | 0.17402 | -0.24163 | 0.037677 | -0.00422 | -0.038036 | -0.052847 | -0.013765 | 0.012329 | -0.095467 | 0.005557 | -120.532 | 0.28487 | 0.16553 | 0.15997 | -120.5425 | -120.4238 | 0.15172 | -120.6507 | 0.28487 | 0.20916 | 0.057431 | -120.6116 | -120.5855 | 0.31305 | 0.3025 | 0.42121 | 0.35848 | -120.8395 | 0.19434 | 0.23343 | 0.25952 | 0.24297 | -120.6933
3389.7188 | 121.019 | -0.23346 | 120.5933 | 1.4211e-13 | -0.039611 | 0.0073825 | 0.023144 | -0.00691 | -0.0099803 | -0.0099194 | -0.0020039 | 0.023233 | -0.0058048 | 0.022489 | 0.011424 | 0.042253 | 0.12045 | -0.067927 | 0.056706 | 0.050727 | 0.1786 | -0.24621 | 0.033099 | -0.00422 | -0.042615 | -0.052847 | -0.018344 | 0.007751 | -0.10004 | -0.012755 | -120.5366 | 0.27571 | 0.16553 | 0.17829 | -120.5425 | -120.4147 | 0.13341 | -120.6461 | 0.26656 | 0.19084 | 0.05743 | -120.6116 | -120.5855 | 0.29017 | 0.28419 | 0.41205 | 0.35391 | -120.8395 | 0.18061 | 0.21512 | 0.24121 | 0.22924 | -120.6933
3391.4375 | 120.9686 | -0.25635 | 120.6436 | 1.4211e-13 | -0.039397 | 0.0071689 | 0.023144 | -0.0073372 | -0.0097665 | -0.0022889 | -0.0017903 | 0.023447 | -0.0062322 | 0.022275 | 0.011638 | 0.037675 | 0.12961 | -0.077084 | 0.061284 | 0.055306 | 0.17402 | -0.23248 | 0.046835 | -0.00422 | -0.042615 | -0.052847 | -0.009187 | 0.012329 | -0.090888 | 0.023871 | -120.5823 | 0.29402 | 0.17926 | 0.15539 | -120.5883 | -120.4696 | 0.16546 | -120.6965 | 0.30318 | 0.21373 | 0.048273 | -120.6528 | -120.6313 | 0.31763 | 0.31165 | 0.43036 | 0.38596 | -120.8761 | 0.2035 | 0.24716 | 0.26868 | 0.25213 | -120.7345
3393.2031 | 121.0098 | -0.24719 | 120.6619 | 1.4211e-13 | -0.039611 | 0.0069553 | 0.022717 | -0.0073372 | -0.0093393 | 0.0053411 | -0.0017903 | 0.023233 | -0.0062322 | 0.022275 | 0.011424 | 0.033096 | 0.13419 | -0.072505 | 0.065863 | 0.055306 | 0.17402 | -0.24621 | 0.02852 | 0.000359 | -0.051772 | -0.052847 | -0.009187 | 0.012329 | -0.10004 | 0.000978 | -120.5961 | 0.28029 | 0.17469 | 0.17371 | -120.6066 | -120.4879 | 0.14715 | -120.7148 | 0.27571 | 0.19542 | 0.048273 | -120.6711 | -120.6496 | 0.31305 | 0.3025 | 0.42121 | 0.38138 | -120.9081 | 0.19434 | 0.238 | 0.25952 | 0.24755 | -120.762
3394.9688 | 121.0419 | -0.23804 | 120.6619 | 1.4211e-13 | -0.039611 | 0.0073825 | 0.022503 | -0.0071236 | -0.0093393 | -0.0022889 | -0.0017903 | 0.023233 | -0.0060184 | 0.022275 | 0.011638 | 0.042253 | 0.13419 | -0.063349 | 0.061284 | 0.041569 | 0.17402 | -0.24163 | 0.033099 | 0.004938 | -0.047194 | -0.048268 | -0.013765 | 0.012329 | -0.10004 | -0.003598 | -120.6006 | 0.28029 | 0.17469 | 0.17829 | -120.6204 | -120.4879 | 0.13799 | -120.7102 | 0.27114 | 0.19084 | 0.052851 | -120.6757 | -120.6496 | 0.29932 | 0.27961 | 0.41205 | 0.37222 | -120.9036 | 0.18977 | 0.22427 | 0.25037 | 0.24297 | -120.762
3396.7656 | 121.019 | -0.27008 | 120.7169 | 1.4211e-13 | -0.039397 | 0.0073825 | 0.022717 | -0.0071236 | -0.0093393 | -0.0022889 | -0.0020039 | 0.02366 | -0.0060184 | 0.022062 | 0.011424 | 0.037675 | 0.13419 | -0.063349 | 0.052128 | 0.050727 | 0.16944 | -0.23706 | 0.042256 | 0.004938 | -0.042615 | -0.04369 | -0.009187 | 0.016908 | -0.10004 | 0.033025 | -120.6647 | 0.30776 | 0.20673 | 0.17371 | -120.6661 | -120.5474 | 0.17004 | -120.7605 | 0.31234 | 0.22747 | 0.05743 | -120.726 | -120.7 | 0.32221 | 0.32081 | 0.43952 | 0.40427 | -120.9539 | 0.22639 | 0.26089 | 0.28699 | 0.27502 | -120.8169
3398.5469 | 120.9778 | -0.28381 | 120.7214 | 1.4211e-13 | -0.039611 | 0.0075963 | 0.02293 | -0.00691 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023447 | -0.0060184 | 0.021848 | 0.011638 | 0.042253 | 0.13419 | -0.063349 | 0.061284 | 0.046148 | 0.16028 | -0.24621 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.10004 | 0.037599 | -120.6602 | 0.32607 | 0.22046 | 0.18286 | -120.6753 | -120.5612 | 0.18377 | -120.7743 | 0.31691 | 0.2412 | 0.05743 | -120.7398 | -120.7091 | 0.3451 | 0.32996 | 0.44409 | 0.418 | -120.9676 | 0.23097 | 0.26547 | 0.29614 | 0.28417 | -120.8215
3400.2656 | 121.0419 | -0.25177 | 120.7397 | 1.4211e-13 | -0.039397 | 0.0075963 | 0.022717 | -0.0071236 | -0.0095529 | -0.0099194 | -0.0017903 | 0.023233 | -0.0060184 | 0.022275 | 0.01121 | 0.028518 | 0.14334 | -0.05877 | 0.061284 | 0.050727 | 0.16486 | -0.24163 | 0.037677 | 0.004938 | -0.042615 | -0.057425 | -0.018344 | 0.016908 | -0.090888 | 0.010135 | -120.6785 | 0.28029 | 0.193 | 0.18286 | -120.689 | -120.5749 | 0.16088 | -120.7972 | 0.28945 | 0.20915 | 0.048273 | -120.7581 | -120.7228 | 0.31305 | 0.3025 | 0.41663 | 0.39511 | -120.9814 | 0.19434 | 0.23343 | 0.26868 | 0.25671 | -120.8306
3402.0469 | 121.0464 | -0.26093 | 120.7672 | 1.4211e-13 | -0.039183 | 0.0073825 | 0.02293 | -0.00691 | -0.0097665 | -0.0099194 | -0.0015767 | 0.023447 | -0.0060184 | 0.022062 | 0.011638 | 0.042253 | 0.13876 | -0.05877 | 0.056706 | 0.041569 | 0.16028 | -0.23248 | 0.037677 | 0.004938 | -0.038036 | -0.048268 | -0.013765 | 0.012329 | -0.095467 | 0.028448 | -120.7105 | 0.30318 | 0.20216 | 0.17371 | -120.7256 | -120.6069 | 0.16546 | -120.8155 | 0.2986 | 0.22289 | 0.057431 | -120.781 | -120.7549 | 0.31763 | 0.30249 | 0.42121 | 0.39969 | -120.9997 | 0.21266 | 0.24716 | 0.27325 | 0.26586 | -120.8627
3403.8281 | 121.0236 | -0.27466 | 120.7718 | 1.4211e-13 | -0.039397 | 0.0075963 | 0.022503 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023233 | -0.006873 | 0.022275 | 0.011424 | 0.042253 | 0.13876 | -0.05877 | 0.052128 | 0.046148 | 0.16486 | -0.24163 | 0.033099 | 0.004938 | -0.042615 | -0.062004 | -0.013765 | 0.016908 | -0.095467 | 0.033023 | -120.7197 | 0.31691 | 0.21589 | 0.18286 | -120.7256 | -120.6069 | 0.17919 | -120.8338 | 0.30776 | 0.23204 | 0.052852 | -120.7856 | -120.7549 | 0.32679 | 0.32081 | 0.43952 | 0.41342 | -121.0134 | 0.21265 | 0.26089 | 0.29157 | 0.2796 | -120.8673
3405.5469 | 121.0236 | -0.28381 | 120.8038 | 1.4211e-13 | -0.039397 | 0.0071689 | 0.02293 | -0.0071236 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023233 | -0.0064458 | 0.022062 | 0.01121 | 0.037675 | 0.14334 | -0.054192 | 0.052128 | 0.041569 | 0.16944 | -0.23706 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.090888 | 0.046757 | -120.7517 | 0.32149 | 0.22962 | 0.18286 | -120.7623 | -120.6344 | 0.19292 | -120.8567 | 0.31691 | 0.2412 | 0.048273 | -120.8222 | -120.7915 | 0.33594 | 0.32538 | 0.45325 | 0.42716 | -121.0409 | 0.23097 | 0.26547 | 0.29614 | 0.28417 | -120.8947
3407.3281 | 121.0648 | -0.27008 | 120.8405 | 1.4211e-13 | -0.039397 | 0.0073825 | 0.022717 | -0.0073372 | -0.0091255 | -0.0022889 | -0.0020039 | 0.023019 | -0.0058048 | 0.022275 | 0.011638 | 0.033096 | 0.14334 | -0.054192 | 0.061284 | 0.046148 | 0.16944 | -0.24163 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.013765 | 0.003172 | -0.090888 | 0.028446 | -120.7792 | 0.30318 | 0.21589 | 0.18744 | -120.7943 | -120.671 | 0.17919 | -120.8979 | 0.30776 | 0.22289 | 0.043694 | -120.8542 | -120.8373 | 0.33137 | 0.31623 | 0.43952 | 0.41342 | -121.0821 | 0.21266 | 0.25632 | 0.27325 | 0.27044 | -120.9313
3409.0469 | 121.1929 | -0.25177 | 120.7947 | 1.4211e-13 | -0.039611 | 0.0073825 | 0.02293 | -0.0071236 | -0.0095529 | -0.01755 | -0.0017903 | 0.023233 | -0.0060184 | 0.022489 | 0.011638 | 0.042253 | 0.14792 | -0.054192 | 0.047549 | 0.03699 | 0.16028 | -0.2279 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.013765 | 0.016908 | -0.10004 | 0.023871 | -120.7471 | 0.29402 | 0.19758 | 0.17371 | -120.7577 | -120.6344 | 0.15172 | -120.8521 | 0.28945 | 0.20458 | 0.052851 | -120.8084 | -120.7778 | 0.29932 | 0.28876 | 0.41205 | 0.39969 | -121.0226 | 0.19434 | 0.238 | 0.26868 | 0.25213 | -120.8947
3410.8281 | 121.2067 | -0.25177 | 120.8038 | 1.4211e-13 | -0.039611 | 0.0075963 | 0.022717 | -0.0073372 | -0.0099803 | -0.0022889 | -0.0017903 | 0.023233 | -0.0058048 | 0.022489 | 0.011424 | 0.028518 | 0.14792 | -0.054192 | 0.047549 | 0.03699 | 0.1557 | -0.2279 | 0.033099 | -0.00422 | -0.042615 | -0.052847 | -0.022922 | 0.012329 | -0.095467 | 0.023871 | -120.7563 | 0.28029 | 0.19758 | 0.17371 | -120.7668 | -120.6481 | 0.1563 | -120.8567 | 0.28487 | 0.20915 | 0.052852 | -120.8268 | -120.7915 | 0.29932 | 0.28876 | 0.40747 | 0.39969 | -121.0317 | 0.19892 | 0.22885 | 0.2641 | 0.24755 | -120.8993
3412.625 | 121.2021 | -0.25635 | 120.8221 | 1.4211e-13 | -0.039611 | 0.0073825 | 0.02293 | -0.0071236 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023233 | -0.0062322 | 0.022275 | 0.011424 | 0.042253 | 0.14792 | -0.049614 | 0.056706 | 0.041569 | 0.16028 | -0.23706 | 0.042256 | 0.000359 | -0.042615 | -0.057425 | -0.018344 | 0.016908 | -0.090888 | 0.019292 | -120.7654 | 0.2986 | 0.20673 | 0.18744 | -120.7806 | -120.6619 | 0.16546 | -120.8796 | 0.2986 | 0.21373 | 0.048273 | -120.8405 | -120.8052 | 0.31305 | 0.29792 | 0.41663 | 0.40427 | -121.0592 | 0.19892 | 0.238 | 0.27326 | 0.25671 | -120.913
3414.4062 | 121.1426 | -0.29755 | 120.8633 | 1.4211e-13 | -0.039611 | 0.0073825 | 0.023144 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0015767 | 0.023233 | -0.0062322 | 0.022489 | 0.01121 | 0.037675 | 0.13876 | -0.054192 | 0.061284 | 0.041569 | 0.16028 | -0.23248 | 0.037677 | 0.004938 | -0.042615 | -0.052847 | -0.013765 | 0.016908 | -0.10004 | 0.065069 | -120.8021 | 0.33522 | 0.24335 | 0.17828 | -120.8218 | -120.7031 | 0.1975 | -120.9162 | 0.33522 | 0.25493 | 0.05743 | -120.8771 | -120.8464 | 0.35883 | 0.33911 | 0.45783 | 0.43631 | -121.0958 | 0.2447 | 0.28378 | 0.31445 | 0.30248 | -120.9634
3416.125 | 121.106 | -0.28381 | 120.8954 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.022503 | -0.0071236 | -0.0095529 | -0.0099194 | -0.0015767 | 0.023233 | -0.0060184 | 0.022275 | 0.011424 | 0.037675 | 0.1525 | -0.049614 | 0.052128 | 0.032411 | 0.15112 | -0.23706 | 0.037677 | 0.000359 | -0.051772 | -0.052847 | -0.013765 | 0.021486 | -0.10462 | 0.046757 | -120.8433 | 0.32149 | 0.2342 | 0.18744 | -120.863 | -120.7443 | 0.17919 | -120.9482 | 0.32149 | 0.23204 | 0.052852 | -120.9092 | -120.8739 | 0.33594 | 0.31622 | 0.43494 | 0.43631 | -121.1324 | 0.23097 | 0.27005 | 0.3053 | 0.28417 | -121
3417.9219 | 121.1517 | -0.28839 | 120.9229 | 1.4211e-13 | -0.039824 | 0.0071689 | 0.022717 | -0.0071236 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023233 | -0.0064458 | 0.022062 | 0.011638 | 0.042253 | 0.1525 | -0.045036 | 0.056706 | 0.041569 | 0.1557 | -0.23706 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.018344 | 0.016908 | -0.095467 | 0.051335 | -120.8661 | 0.33064 | 0.24336 | 0.19202 | -120.8813 | -120.7672 | 0.19292 | -120.9757 | 0.32607 | 0.2412 | 0.048273 | -120.9412 | -120.9059 | 0.3451 | 0.32996 | 0.44409 | 0.44089 | -121.1599 | 0.23554 | 0.27005 | 0.3053 | 0.28875 | -121.0183
3419.7031 | 121.1517 | -0.28839 | 120.9137 | 1.4211e-13 | -0.039183 | 0.0071689 | 0.02293 | -0.0073372 | -0.0097665 | -0.0099194 | -0.0020039 | 0.023233 | -0.0060184 | 0.022275 | 0.010997 | 0.033096 | 0.1525 | -0.054192 | 0.052128 | 0.027833 | 0.16028 | -0.24163 | 0.033099 | 0.000359 | -0.047194 | -0.052847 | -0.018344 | 0.016908 | -0.095467 | 0.046756 | -120.8616 | 0.32149 | 0.2342 | 0.18744 | -120.8859 | -120.7534 | 0.19292 | -120.9665 | 0.32149 | 0.2412 | 0.048273 | -120.932 | -120.8968 | 0.34052 | 0.31622 | 0.44867 | 0.44089 | -121.1553 | 0.23554 | 0.27005 | 0.3053 | 0.28875 | -121.0092
3421.4688 | 121.2387 | -0.24261 | 120.8496 | 1.4211e-13 | -0.040038 | 0.0069553 | 0.02293 | -0.0071236 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023447 | -0.0060184 | 0.022703 | 0.01121 | 0.042253 | 0.14792 | -0.054192 | 0.042971 | 0.03699 | 0.15112 | -0.23706 | 0.046835 | 0.000359 | -0.047194 | -0.057425 | -0.013765 | 0.012329 | -0.10004 | 0.005559 | -120.8066 | 0.28487 | 0.18842 | 0.18286 | -120.8126 | -120.6985 | 0.14257 | -120.907 | 0.28945 | 0.19542 | 0.052851 | -120.8634 | -120.8373 | 0.28559 | 0.2796 | 0.39374 | 0.39054 | -121.0867 | 0.18519 | 0.22885 | 0.25494 | 0.24297 | -120.9497
3423.1875 | 121.1655 | -0.28381 | 120.9641 | 1.4211e-13 | -0.039611 | 0.0075963 | 0.02293 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0015767 | 0.023447 | -0.0064458 | 0.022275 | 0.011424 | 0.042253 | 0.1525 | -0.045036 | 0.047549 | 0.03699 | 0.14655 | -0.24621 | 0.042256 | 0.000359 | -0.047194 | -0.057425 | -0.022922 | 0.012329 | -0.095467 | 0.037599 | -120.9165 | 0.32607 | 0.23878 | 0.20118 | -120.9271 | -120.8175 | 0.18835 | -121.0215 | 0.32607 | 0.23662 | 0.048273 | -120.987 | -120.9517 | 0.33136 | 0.3208 | 0.43036 | 0.43631 | -121.2103 | 0.22639 | 0.26089 | 0.29614 | 0.28417 | -121.0595
3424.9531 | 121.2891 | -0.25635 | 120.9229 | 1.4211e-13 | -0.039824 | 0.0071689 | 0.02293 | -0.0073372 | -0.0097665 | -0.0022889 | -0.0015767 | 0.023019 | -0.0062322 | 0.022916 | 0.011851 | 0.037675 | 0.14792 | -0.045036 | 0.052128 | 0.041569 | 0.15112 | -0.24163 | 0.033099 | 0.000359 | -0.047194 | -0.048268 | -0.013765 | 0.016908 | -0.10004 | 0.014713 | -120.8707 | 0.29402 | 0.21131 | 0.1966 | -120.8813 | -120.7717 | 0.1563 | -120.9711 | 0.28945 | 0.20915 | 0.052851 | -120.9366 | -120.9059 | 0.30848 | 0.29792 | 0.40747 | 0.40427 | -121.1645 | 0.20808 | 0.24258 | 0.27326 | 0.25671 | -121.0229
3426.7344 | 121.2936 | -0.23346 | 120.9091 | 1.4211e-13 | -0.039611 | 0.0071689 | 0.02293 | -0.0071236 | -0.0091255 | -0.01755 | -0.0015767 | 0.023019 | -0.0062322 | 0.022489 | 0.011638 | 0.046831 | 0.1525 | -0.045036 | 0.052128 | 0.03699 | 0.15112 | -0.24163 | 0.037677 | 0.004938 | -0.042615 | -0.052847 | -0.013765 | 0.012329 | -0.095467 | -0.008176 | -120.857 | 0.28029 | 0.18842 | 0.1966 | -120.8721 | -120.758 | 0.13799 | -120.962 | 0.27114 | 0.19084 | 0.052852 | -120.9229 | -120.8968 | 0.28559 | 0.27045 | 0.38458 | 0.38596 | -121.1508 | 0.18061 | 0.21969 | 0.24579 | 0.2384 | -121.0046
3428.4531 | 121.2433 | -0.28381 | 120.9549 | 1.4211e-13 | -0.039824 | 0.0071689 | 0.02293 | -0.0073372 | -0.0093393 | -0.0022889 | -0.0015767 | 0.023019 | -0.0062322 | 0.022275 | 0.011424 | 0.037675 | 0.15708 | -0.049614 | 0.052128 | 0.032411 | 0.14655 | -0.24163 | 0.037677 | 0.000359 | -0.042615 | -0.052847 | -0.013765 | 0.016908 | -0.10004 | 0.042178 | -120.9028 | 0.32149 | 0.2342 | 0.19202 | -120.9225 | -120.8083 | 0.18377 | -121.0077 | 0.32149 | 0.2412 | 0.05743 | -120.9687 | -120.938 | 0.33594 | 0.31622 | 0.43036 | 0.44089 | -121.1965 | 0.23097 | 0.27005 | 0.30072 | 0.28417 | -121.0549
3430.25 | 121.2891 | -0.24719 | 120.9595 | 1.4211e-13 | -0.040038 | 0.0078099 | 0.022503 | -0.0073372 | -0.0097665 | -0.0022889 | -0.0017903 | 0.023233 | -0.0060184 | 0.022703 | 0.011638 | 0.037675 | 0.1525 | -0.054192 | 0.042971 | 0.032411 | 0.1557 | -0.24163 | 0.033099 | 0.004938 | -0.051772 | -0.052847 | -0.022922 | 0.016908 | -0.10004 | 0.005557 | -120.9165 | 0.28487 | 0.193 | 0.18744 | -120.9271 | -120.8038 | 0.14715 | -121.0123 | 0.28029 | 0.19542 | 0.048273 | -120.9824 | -120.9426 | 0.29016 | 0.2796 | 0.40289 | 0.39969 | -121.2011 | 0.19434 | 0.22427 | 0.2641 | 0.25213 | -121.0595
3432.0312 | 121.2433 | -0.27008 | 120.9732 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.02293 | -0.0075508 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023233 | -0.0064458 | 0.022489 | 0.011638 | 0.042253 | 0.14792 | -0.040457 | 0.047549 | 0.03699 | 0.14655 | -0.24163 | 0.033099 | 0.004938 | -0.042615 | -0.052847 | -0.013765 | 0.016908 | -0.090888 | 0.028446 | -120.9257 | 0.31233 | 0.22962 | 0.20118 | -120.9362 | -120.8267 | 0.17919 | -121.0261 | 0.30318 | 0.22747 | 0.048273 | -120.987 | -120.9563 | 0.31763 | 0.30707 | 0.41663 | 0.418 | -121.2148 | 0.21723 | 0.25632 | 0.28699 | 0.27502 | -121.0641
3433.8281 | 121.3486 | -0.25177 | 120.9595 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.022503 | -0.0071236 | -0.0097665 | -0.0099194 | -0.0015767 | 0.023233 | -0.0062322 | 0.022489 | 0.011424 | 0.037675 | 0.15708 | -0.049614 | 0.047549 | 0.03699 | 0.15112 | -0.24163 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.007751 | -0.095467 | 0.010135 | -120.9119 | 0.28945 | 0.20216 | 0.19202 | -120.9225 | -120.8084 | 0.1563 | -121.0123 | 0.29403 | 0.20915 | 0.052852 | -120.9778 | -120.9517 | 0.29932 | 0.28876 | 0.40289 | 0.40885 | -121.2011 | 0.19892 | 0.23343 | 0.25952 | 0.25213 | -121.0549
3435.6094 | 121.2479 | -0.29755 | 121.0052 | 1.4211e-13 | -0.040252 | 0.0073825 | 0.022289 | -0.0071236 | -0.0099803 | -0.0099194 | -0.0015767 | 0.023233 | -0.0064458 | 0.022489 | 0.01121 | 0.042253 | 0.1525 | -0.045036 | 0.052128 | 0.027833 | 0.14655 | -0.24621 | 0.037677 | 0.000359 | -0.047194 | -0.062004 | -0.009187 | 0.016908 | -0.10004 | 0.051332 | -120.9531 | 0.3398 | 0.25251 | 0.20118 | -120.9774 | -120.8587 | 0.1975 | -121.0673 | 0.33522 | 0.25035 | 0.052851 | -121.0144 | -120.9883 | 0.34967 | 0.32538 | 0.44409 | 0.45005 | -121.2515 | 0.23554 | 0.28836 | 0.31445 | 0.2979 | -121.1053
3437.3906 | 121.2616 | -0.29755 | 121.0281 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.022503 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0020039 | 0.022806 | -0.0062322 | 0.022703 | 0.011424 | 0.037675 | 0.1525 | -0.045036 | 0.042971 | 0.027833 | 0.14655 | -0.25079 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.013765 | 0.012329 | -0.10004 | 0.046753 | -120.9852 | 0.33522 | 0.25251 | 0.20576 | -121.0003 | -120.8816 | 0.1975 | -121.081 | 0.33522 | 0.25035 | 0.052851 | -121.0419 | -121.0158 | 0.34052 | 0.32538 | 0.44409 | 0.45005 | -121.2789 | 0.2447 | 0.28378 | 0.30987 | 0.2979 | -121.1282
3439.1094 | 121.2982 | -0.28381 | 121.0144 | 1.4211e-13 | -0.040038 | 0.0075963 | 0.02293 | -0.0071236 | -0.0095529 | -0.01755 | -0.0017903 | 0.023233 | -0.0060184 | 0.022489 | 0.011424 | 0.037675 | 0.14792 | -0.045036 | 0.042971 | 0.032411 | 0.15112 | -0.24621 | 0.037677 | 0.004938 | -0.051772 | -0.057425 | -0.013765 | 0.021486 | -0.090888 | 0.037599 | -120.9714 | 0.32149 | 0.23878 | 0.20118 | -120.982 | -120.8633 | 0.19292 | -121.0718 | 0.32149 | 0.23204 | 0.039116 | -121.0282 | -120.9929 | 0.32678 | 0.31622 | 0.43494 | 0.43173 | -121.2606 | 0.22639 | 0.27005 | 0.3053 | 0.28875 | -121.1053
3440.9062 | 121.2799 | -0.28839 | 121.0464 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022503 | -0.0073372 | -0.0097665 | -0.0022889 | -0.0020039 | 0.023019 | -0.0058048 | 0.022275 | 0.011851 | 0.042253 | 0.14334 | -0.049614 | 0.047549 | 0.032411 | 0.14197 | -0.24621 | 0.033099 | 0.004938 | -0.042615 | -0.062004 | -0.013765 | 0.016908 | -0.095467 | 0.042177 | -120.9989 | 0.33064 | 0.23878 | 0.1966 | -121.014 | -120.9045 | 0.19292 | -121.1085 | 0.32149 | 0.24578 | 0.052852 | -121.0602 | -121.0295 | 0.33594 | 0.3208 | 0.43036 | 0.43173 | -121.2927 | 0.22639 | 0.27463 | 0.3053 | 0.29333 | -121.1419
3442.6406 | 121.4264 | -0.24261 | 121.0236 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.02293 | -0.0075508 | -0.0095529 | -0.02518 | -0.0020039 | 0.023019 | -0.0058048 | 0.022489 | 0.011424 | 0.037675 | 0.1525 | -0.040457 | 0.047549 | 0.032411 | 0.14197 | -0.25079 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.013765 | 0.016908 | -0.10004 | -0.008178 | -120.976 | 0.28029 | 0.20216 | 0.21034 | -120.9911 | -120.8816 | 0.14257 | -121.081 | 0.28029 | 0.19542 | 0.052851 | -121.0373 | -121.0067 | 0.29016 | 0.27503 | 0.38458 | 0.39511 | -121.2744 | 0.18519 | 0.22885 | 0.25952 | 0.24297 | -121.1236
3444.4219 | 121.3211 | -0.28839 | 121.0373 | 1.4211e-13 | -0.039824 | 0.0069553 | 0.022717 | -0.0075508 | -0.0093393 | -0.0099194 | -0.0017903 | 0.023233 | -0.0064458 | 0.022275 | 0.011638 | 0.037675 | 0.15708 | -0.045036 | 0.047549 | 0.027833 | 0.15112 | -0.25079 | 0.037677 | 0.000359 | -0.047194 | -0.062004 | -0.013765 | 0.021486 | -0.10004 | 0.037598 | -120.9897 | 0.32607 | 0.24336 | 0.20576 | -121.0095 | -120.8862 | 0.18835 | -121.0993 | 0.32607 | 0.2412 | 0.052851 | -121.0511 | -121.0158 | 0.33594 | 0.31622 | 0.43951 | 0.44547 | -121.2881 | 0.22639 | 0.27463 | 0.30988 | 0.28875 | -121.1373
3446.1406 | 121.3165 | -0.32044 | 121.0464 | 1.4211e-13 | -0.040038 | 0.0073825 | 0.02293 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0020039 | 0.023447 | -0.0062322 | 0.022489 | 0.011424 | 0.033096 | 0.14792 | -0.049614 | 0.047549 | 0.03699 | 0.14655 | -0.25537 | 0.037677 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.10004 | 0.065063 | -120.9989 | 0.35353 | 0.27082 | 0.20576 | -121.0095 | -120.8999 | 0.22039 | -121.0993 | 0.35811 | 0.27782 | 0.05743 | -121.0648 | -121.0341 | 0.36798 | 0.35743 | 0.46698 | 0.46836 | -121.3018 | 0.26759 | 0.30209 | 0.33276 | 0.32079 | -121.1465
3447.9219 | 121.3348 | -0.30212 | 121.0648 | 1.4211e-13 | -0.039824 | 0.0073825 | 0.022717 | -0.0075508 | -0.0097665 | -0.0022889 | -0.0017903 | 0.023233 | -0.0060184 | 0.022489 | 0.011424 | 0.042253 | 0.14792 | -0.049614 | 0.047549 | 0.027833 | 0.14197 | -0.25079 | 0.037677 | -0.00422 | -0.038036 | -0.057425 | -0.013765 | 0.007751 | -0.095467 | 0.051331 | -121.0172 | 0.34438 | 0.25251 | 0.20118 | -121.0369 | -120.9228 | 0.20666 | -121.1222 | 0.3398 | 0.26409 | 0.057431 | -121.0785 | -121.057 | 0.34967 | 0.32996 | 0.44409 | 0.45005 | -121.3156 | 0.2447 | 0.28836 | 0.30988 | 0.2979 | -121.1602
3449.6875 | 121.4584 | -0.24261 | 121.0373 | 1.4211e-13 | -0.039824 | 0.0075963 | 0.02293 | -0.0071236 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023233 | -0.0060184 | 0.022703 | 0.011424 | 0.033096 | 0.1525 | -0.035879 | 0.056706 | 0.027833 | 0.14197 | -0.25537 | 0.037677 | -0.00422 | -0.047194 | -0.052847 | -0.022922 | 0.012329 | -0.10462 | -0.012757 | -120.9806 | 0.27571 | 0.20674 | 0.21949 | -121.0095 | -120.8953 | 0.13799 | -121.0901 | 0.28029 | 0.19542 | 0.05743 | -121.0602 | -121.025 | 0.29932 | 0.27045 | 0.38458 | 0.39511 | -121.2927 | 0.18977 | 0.21969 | 0.25494 | 0.23839 | -121.1419
3451.3906 | 121.344 | -0.29297 | 121.106 | 1.4211e-13 | -0.040252 | 0.0073825 | 0.022503 | -0.0073372 | -0.0095529 | -0.0099194 | -0.0017903 | 0.023233 | -0.0060184 | 0.022489 | 0.011424 | 0.042253 | 0.15708 | -0.045036 | 0.042971 | 0.032411 | 0.14197 | -0.25079 | 0.037677 | 0.004938 | -0.047194 | -0.04369 | -0.013765 | 0.012329 | -0.10004 | 0.042176 | -121.063 | 0.33522 | 0.24793 | 0.20576 | -121.0735 | -120.964 | 0.19292 | -121.1496 | 0.33065 | 0.24577 | 0.052851 | -121.1197 | -121.0936 | 0.33594 | 0.32538 | 0.43493 | 0.45005 | -121.3568 | 0.24928 | 0.2792 | 0.3053 | 0.29791 | -121.206
3453.1719 | 121.4401 | -0.27466 | 121.0739 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022717 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0020039 | 0.023447 | -0.0060184 | 0.022489 | 0.011424 | 0.046831 | 0.1525 | -0.049614 | 0.047549 | 0.027833 | 0.14655 | -0.25537 | 0.033099 | -0.00422 | -0.038036 | -0.052847 | -0.004608 | 0.012329 | -0.095467 | 0.019286 | -121.0264 | 0.32149 | 0.22504 | 0.20576 | -121.0461 | -120.9274 | 0.17919 | -121.1268 | 0.30776 | 0.23662 | 0.057431 | -121.0785 | -121.0616 | 0.32221 | 0.30249 | 0.4212 | 0.42716 | -121.3293 | 0.22181 | 0.27005 | 0.28699 | 0.27044 | -121.1694
3454.9531 | 121.4859 | -0.25177 | 121.051 | 1.4211e-13 | -0.040038 | 0.0069553 | 0.022289 | -0.0075508 | -0.0093393 | 0.0053411 | -0.0015767 | 0.023233 | -0.0064458 | 0.022489 | 0.011851 | 0.037675 | 0.1525 | -0.040457 | 0.042971 | 0.032411 | 0.14655 | -0.25079 | 0.033099 | -0.00422 | -0.047194 | -0.052847 | -2.9e-05 | 0.012329 | -0.095467 | 0.000977 | -121.0081 | 0.28945 | 0.21131 | 0.21034 | -121.0186 | -120.9045 | 0.1563 | -121.1039 | 0.28487 | 0.20458 | 0.048273 | -121.0511 | -121.0387 | 0.29474 | 0.28418 | 0.39831 | 0.40427 | -121.3018 | 0.19892 | 0.25174 | 0.2641 | 0.24755 | -121.1465
3456.6719 | 121.3806 | -0.31128 | 121.0968 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022717 | -0.0073372 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023019 | -0.0060184 | 0.022703 | 0.011638 | 0.042253 | 0.14792 | -0.040457 | 0.047549 | 0.032411 | 0.13739 | -0.24163 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.018344 | 0.007751 | -0.10462 | 0.069644 | -121.0493 | 0.35353 | 0.27082 | 0.20118 | -121.0644 | -120.9594 | 0.20665 | -121.1542 | 0.34896 | 0.26408 | 0.05743 | -121.1151 | -121.0891 | 0.35883 | 0.34369 | 0.44867 | 0.4592 | -121.3384 | 0.25385 | 0.29293 | 0.31903 | 0.31164 | -121.2014
3458.4531 | 121.5088 | -0.2655 | 121.0922 | 1.4211e-13 | -0.040252 | 0.0073825 | 0.022717 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0020039 | 0.023233 | -0.0060184 | 0.022275 | 0.011424 | 0.046831 | 0.1525 | -0.035879 | 0.042971 | 0.03699 | 0.15112 | -0.24621 | 0.037677 | -0.00422 | -0.042615 | -0.052847 | -0.009187 | 0.012329 | -0.095467 | 0.019289 | -121.0493 | 0.31233 | 0.22962 | 0.21033 | -121.0552 | -120.9411 | 0.17004 | -121.1451 | 0.30318 | 0.22289 | 0.052852 | -121.1014 | -121.0799 | 0.30847 | 0.30249 | 0.41663 | 0.418 | -121.3384 | 0.21266 | 0.25632 | 0.27783 | 0.26128 | -121.1877
3460.2344 | 121.5088 | -0.24719 | 121.106 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022717 | -0.0073372 | -0.0099803 | -0.0099194 | -0.0017903 | 0.023019 | -0.0062322 | 0.022489 | 0.01121 | 0.042253 | 0.1525 | -0.040457 | 0.038393 | 0.032411 | 0.14655 | -0.25537 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.004608 | 0.012329 | -0.10004 | -0.00818 | -121.0676 | 0.28945 | 0.20674 | 0.21491 | -121.0735 | -120.9594 | 0.14715 | -121.1588 | 0.28945 | 0.20458 | 0.05743 | -121.1106 | -121.0936 | 0.28558 | 0.2796 | 0.39374 | 0.39969 | -121.3613 | 0.19434 | 0.24258 | 0.25952 | 0.24755 | -121.206
3462.0156 | 121.4951 | -0.24719 | 121.1014 | 1.4211e-13 | -0.040038 | 0.0073825 | 0.022717 | -0.0073372 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023019 | -0.0064458 | 0.022275 | 0.010783 | 0.042253 | 0.1525 | -0.045036 | 0.042971 | 0.023254 | 0.14655 | -0.25079 | 0.037677 | -0.00422 | -0.047194 | -0.066582 | -0.004608 | 0.012329 | -0.10462 | -0.003601 | -121.0584 | 0.28945 | 0.20216 | 0.20576 | -121.0781 | -120.9548 | 0.14257 | -121.168 | 0.28487 | 0.2 | 0.05743 | -121.106 | -121.0891 | 0.29016 | 0.27045 | 0.39374 | 0.39969 | -121.3522 | 0.18061 | 0.24258 | 0.25952 | 0.24297 | -121.206
3463.75 | 121.5134 | -0.2655 | 121.1105 | 1.4211e-13 | -0.040252 | 0.0073825 | 0.022289 | -0.0071236 | -0.0095529 | -0.0099194 | -0.0015767 | 0.023233 | -0.0066594 | 0.022275 | 0.01121 | 0.05141 | 0.15708 | -0.040457 | 0.047549 | 0.032411 | 0.14197 | -0.25537 | 0.037677 | 0.000359 | -0.042615 | -0.048268 | -0.018344 | 0.007751 | -0.10004 | 0.010131 | -121.063 | 0.31691 | 0.22505 | 0.21491 | -121.0781 | -120.9686 | 0.16546 | -121.1588 | 0.30318 | 0.22289 | 0.05743 | -121.1289 | -121.1028 | 0.31305 | 0.29791 | 0.40747 | 0.42258 | -121.3659 | 0.21723 | 0.24716 | 0.27325 | 0.26586 | -121.2106
3465.5312 | 121.5179 | -0.26093 | 121.1243 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.02293 | -0.0071236 | -0.0095529 | -0.01755 | -0.0017903 | 0.023019 | -0.0062322 | 0.022703 | 0.011638 | 0.042253 | 0.1525 | -0.040457 | 0.047549 | 0.027833 | 0.14197 | -0.24621 | 0.046835 | -0.00422 | -0.042615 | -0.057425 | -0.013765 | 0.007751 | -0.10004 | 0.014711 | -121.0767 | 0.30318 | 0.22047 | 0.20576 | -121.0964 | -120.9823 | 0.16088 | -121.1817 | 0.30776 | 0.21831 | 0.05743 | -121.138 | -121.1165 | 0.30847 | 0.28876 | 0.40289 | 0.41343 | -121.3705 | 0.2035 | 0.24716 | 0.26868 | 0.25671 | -121.2243
3467.3125 | 121.5546 | -0.26093 | 121.138 | 1.4211e-13 | -0.040252 | 0.0069553 | 0.022717 | -0.0077646 | -0.0097665 | -0.0022889 | -0.0015767 | 0.022806 | -0.0060184 | 0.022489 | 0.011424 | 0.046831 | 0.1525 | -0.035879 | 0.052128 | 0.027833 | 0.14197 | -0.25537 | 0.033099 | -0.00422 | -0.047194 | -0.052847 | -0.009187 | 0.012329 | -0.1092 | 0.005553 | -121.0859 | 0.30776 | 0.22505 | 0.21949 | -121.1102 | -120.996 | 0.15172 | -121.1908 | 0.29402 | 0.21373 | 0.062009 | -121.1472 | -121.1257 | 0.31305 | 0.28876 | 0.40289 | 0.41343 | -121.3934 | 0.20808 | 0.25174 | 0.27325 | 0.25671 | -121.2472
3469.1094 | 121.4218 | -0.28381 | 121.1838 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022717 | -0.0075508 | -0.0099803 | -0.0099194 | -0.0022175 | 0.023019 | -0.0064458 | 0.022489 | 0.011424 | 0.046831 | 0.15708 | -0.031301 | 0.038393 | 0.032411 | 0.14197 | -0.26453 | 0.033099 | 0.009516 | -0.047194 | -0.052847 | -0.022922 | 0.016908 | -0.10004 | 0.019283 | -121.1454 | 0.33064 | 0.25251 | 0.23323 | -121.1514 | -121.0418 | 0.18377 | -121.2366 | 0.31691 | 0.23662 | 0.052851 | -121.2067 | -121.1669 | 0.32221 | 0.31622 | 0.42578 | 0.44089 | -121.4483 | 0.23097 | 0.26089 | 0.30072 | 0.29333 | -121.2838
3470.8281 | 121.4813 | -0.30212 | 121.1884 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022289 | -0.0075508 | -0.0097665 | -0.0022889 | -0.0015767 | 0.023233 | -0.0062322 | 0.022275 | 0.011424 | 0.046831 | 0.1525 | -0.035879 | 0.042971 | 0.027833 | 0.14197 | -0.25537 | 0.033099 | 0.004938 | -0.042615 | -0.057425 | -0.009187 | 0.007751 | -0.10004 | 0.046752 | -121.1454 | 0.34896 | 0.26625 | 0.21949 | -121.1605 | -121.0464 | 0.20208 | -121.2458 | 0.33522 | 0.25951 | 0.05743 | -121.1975 | -121.1806 | 0.34509 | 0.32996 | 0.44409 | 0.45462 | -121.4437 | 0.2447 | 0.29294 | 0.30988 | 0.30706 | -121.2884
3472.6094 | 121.55 | -0.25635 | 121.1472 | 1.4211e-13 | -0.040038 | 0.0073825 | 0.02293 | -0.0071236 | -0.0097665 | -0.0022889 | -0.0017903 | 0.023447 | -0.0058048 | 0.022489 | 0.011638 | 0.05141 | 0.14792 | -0.040457 | 0.047549 | 0.027833 | 0.12823 | -0.25995 | 0.033099 | -0.00422 | -0.038036 | -0.052847 | -0.013765 | 0.016908 | -0.10462 | -0.003603 | -121.0996 | 0.30776 | 0.21589 | 0.21949 | -121.1193 | -121.0189 | 0.15172 | -121.2 | 0.28945 | 0.21831 | 0.066588 | -121.1609 | -121.1302 | 0.3039 | 0.28418 | 0.38458 | 0.40427 | -121.4071 | 0.2035 | 0.24258 | 0.27326 | 0.25213 | -121.2518
3474.3906 | 121.4447 | -0.29755 | 121.2067 | 1.4211e-13 | -0.040252 | 0.0073825 | 0.022503 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023019 | -0.0062322 | 0.022489 | 0.01121 | 0.046831 | 0.14792 | -0.035879 | 0.042971 | 0.027833 | 0.14197 | -0.25537 | 0.042256 | -0.00422 | -0.042615 | -0.052847 | -0.004608 | 0.016908 | -0.10462 | 0.042174 | -121.1637 | 0.34438 | 0.26167 | 0.21949 | -121.1788 | -121.0647 | 0.19292 | -121.2595 | 0.3398 | 0.25493 | 0.062009 | -121.2113 | -121.1898 | 0.34052 | 0.32538 | 0.43951 | 0.44547 | -121.462 | 0.2447 | 0.29294 | 0.31445 | 0.29333 | -121.3113
3476.1094 | 121.5775 | -0.25177 | 121.1609 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.022503 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023019 | -0.0062322 | 0.022489 | 0.01121 | 0.046831 | 0.14792 | -0.035879 | 0.042971 | 0.027833 | 0.14197 | -0.25995 | 0.033099 | 0.000359 | -0.047194 | -0.062004 | -0.009187 | 0.012329 | -0.10462 | -0.008181 | -121.1179 | 0.2986 | 0.21589 | 0.22407 | -121.1331 | -121.0189 | 0.14715 | -121.2229 | 0.28487 | 0.20458 | 0.05743 | -121.1701 | -121.1486 | 0.29474 | 0.2796 | 0.39374 | 0.39969 | -121.4208 | 0.18977 | 0.24258 | 0.2641 | 0.25213 | -121.2655
3477.9062 | 121.5179 | -0.31128 | 121.2112 | 1.4211e-13 | -0.040038 | 0.0071689 | 0.022503 | -0.0071236 | -0.0097665 | -0.01755 | -0.0020039 | 0.023019 | -0.0062322 | 0.022275 | 0.010997 | 0.05141 | 0.14792 | -0.031301 | 0.042971 | 0.027833 | 0.13739 | -0.25079 | 0.033099 | 0.000359 | -0.042615 | -0.057425 | -0.018344 | 0.012329 | -0.10004 | 0.060486 | -121.1683 | 0.36269 | 0.27998 | 0.21949 | -121.1834 | -121.0739 | 0.21123 | -121.2687 | 0.34438 | 0.26866 | 0.05743 | -121.2296 | -121.1989 | 0.35425 | 0.33911 | 0.44867 | 0.4592 | -121.462 | 0.25385 | 0.29293 | 0.32361 | 0.31164 | -121.3113
3479.6875 | 121.5775 | -0.27466 | 121.2021 | 1.4211e-13 | -0.040252 | 0.0069553 | 0.022289 | -0.0073372 | -0.0097665 | -0.0099194 | -0.0015767 | 0.023019 | -0.0062322 | 0.022489 | 0.01121 | 0.05141 | 0.14792 | -0.035879 | 0.047549 | 0.023254 | 0.14655 | -0.25079 | 0.037677 | 0.000359 | -0.051772 | -0.057425 | -0.013765 | 0.021486 | -0.10462 | 0.023865 | -121.1545 | 0.32607 | 0.23878 | 0.21491 | -121.1788 | -121.0555 | 0.17003 | -121.2595 | 0.31234 | 0.22289 | 0.052852 | -121.2159 | -121.1806 | 0.32221 | 0.29791 | 0.4212 | 0.42258 | -121.4529 | 0.21723 | 0.26089 | 0.29614 | 0.27502 | -121.3067
3481.4688 | 121.5408 | -0.27466 | 121.1975 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.02293 | -0.0077646 | -0.0099803 | -0.0022889 | -0.0017903 | 0.023019 | -0.0066594 | 0.022703 | 0.01121 | 0.042253 | 0.15708 | -0.035879 | 0.042971 | 0.027833 | 0.13739 | -0.25995 | 0.02852 | 0.000359 | -0.042615 | -0.062004 | -0.018344 | 0.016908 | -0.095467 | 0.014707 | -121.1545 | 0.31691 | 0.23878 | 0.22407 | -121.1697 | -121.0601 | 0.17919 | -121.2595 | 0.30318 | 0.23204 | 0.052852 | -121.2159 | -121.1806 | 0.31763 | 0.30249 | 0.41204 | 0.43174 | -121.4575 | 0.21265 | 0.25631 | 0.29157 | 0.27502 | -121.293
3483.1875 | 121.582 | -0.26093 | 121.2112 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.022717 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0020039 | 0.023233 | -0.0064458 | 0.022489 | 0.011424 | 0.046831 | 0.1525 | -0.026723 | 0.047549 | 0.027833 | 0.14197 | -0.25537 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.018344 | 0.012329 | -0.095467 | 0.005553 | -121.1637 | 0.30776 | 0.2342 | 0.22865 | -121.1834 | -121.0693 | 0.16546 | -121.2641 | 0.2986 | 0.21373 | 0.048273 | -121.2296 | -121.1989 | 0.30847 | 0.28876 | 0.40289 | 0.41343 | -121.4666 | 0.20808 | 0.24258 | 0.27325 | 0.26128 | -121.3067
3484.9688 | 121.6095 | -0.26093 | 121.2112 | 1.4211e-13 | -0.040466 | 0.0073825 | 0.022717 | -0.0071236 | -0.0095529 | -0.0022889 | -0.0020039 | 0.023019 | -0.0060184 | 0.022703 | 0.011638 | 0.05141 | 0.1525 | -0.026723 | 0.042971 | 0.027833 | 0.13281 | -0.25537 | 0.033099 | 0.004938 | -0.047194 | -0.052847 | -0.018344 | 0.016908 | -0.095467 | 0.005553 | -121.1683 | 0.31234 | 0.2342 | 0.22865 | -121.1834 | -121.0784 | 0.16546 | -121.2641 | 0.29402 | 0.21373 | 0.048273 | -121.2296 | -121.1943 | 0.3039 | 0.28876 | 0.39373 | 0.41343 | -121.4666 | 0.20808 | 0.24258 | 0.27783 | 0.26586 | -121.3067
3486.75 | 121.5088 | -0.31128 | 121.2112 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.022717 | -0.0073372 | -0.0095529 | 0.0053411 | -0.0015767 | 0.023233 | -0.0064458 | 0.022916 | 0.011424 | 0.05141 | 0.1525 | -0.031301 | 0.042971 | 0.027833 | 0.13739 | -0.26453 | 0.033099 | 0.000359 | -0.042615 | -0.057425 | -0.009187 | 0.012329 | -0.10462 | 0.046749 | -121.1683 | 0.36269 | 0.27998 | 0.23323 | -121.1834 | -121.0739 | 0.20665 | -121.2687 | 0.34438 | 0.26866 | 0.062009 | -121.2204 | -121.1989 | 0.35425 | 0.33911 | 0.44867 | 0.46378 | -121.4758 | 0.25385 | 0.30209 | 0.32361 | 0.31164 | -121.3159
3488.4688 | 121.6278 | -0.29297 | 121.2204 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.02293 | -0.0073372 | -0.0097665 | -0.0022889 | -0.0020039 | 0.023233 | -0.0060184 | 0.022703 | 0.011638 | 0.05141 | 0.15708 | -0.031301 | 0.056706 | 0.032411 | 0.13739 | -0.26453 | 0.037677 | 0.000359 | -0.047194 | -0.062004 | -0.009187 | 0.012329 | -0.10004 | 0.028439 | -121.1637 | 0.34438 | 0.26167 | 0.23323 | -121.188 | -121.083 | 0.19292 | -121.2824 | 0.33065 | 0.24577 | 0.052851 | -121.2296 | -121.2081 | 0.34967 | 0.32538 | 0.43036 | 0.45005 | -121.4849 | 0.23096 | 0.28378 | 0.3053 | 0.29333 | -121.3204
3490.25 | 121.5729 | -0.29297 | 121.2753 | 1.4211e-13 | -0.040466 | 0.0069553 | 0.022503 | -0.0071236 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023233 | -0.0062322 | 0.022916 | 0.011424 | 0.046831 | 0.16166 | -0.031301 | 0.042971 | 0.023254 | 0.14197 | -0.26453 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.018344 | 0.016908 | -0.10004 | 0.028439 | -121.2324 | 0.3398 | 0.26167 | 0.23323 | -121.2521 | -121.1334 | 0.19292 | -121.3328 | 0.33065 | 0.24577 | 0.052851 | -121.2937 | -121.2584 | 0.33594 | 0.31622 | 0.43493 | 0.45463 | -121.5399 | 0.23554 | 0.27463 | 0.30988 | 0.29333 | -121.3754
3492.0312 | 121.637 | -0.2655 | 121.2158 | 1.4211e-13 | -0.040252 | 0.0069553 | 0.022503 | -0.0073372 | -0.0091255 | -0.0099194 | -0.0020039 | 0.023233 | -0.0062322 | 0.022916 | 0.011424 | 0.037675 | 0.1525 | -0.026723 | 0.042971 | 0.027833 | 0.14655 | -0.26911 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.013765 | 0.012329 | -0.10004 | -0.003606 | -121.1728 | 0.30318 | 0.23878 | 0.24239 | -121.188 | -121.0693 | 0.16546 | -121.2687 | 0.2986 | 0.22289 | 0.05743 | -121.2296 | -121.2035 | 0.30847 | 0.29334 | 0.41205 | 0.418 | -121.4849 | 0.21266 | 0.25174 | 0.27783 | 0.26586 | -121.3159
3493.8125 | 121.6049 | -0.29755 | 121.2387 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022503 | -0.0075508 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023233 | -0.0064458 | 0.022703 | 0.011424 | 0.05141 | 0.16166 | -0.031301 | 0.047549 | 0.032411 | 0.14197 | -0.26911 | 0.033099 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.021486 | -0.1092 | 0.028437 | -121.1912 | 0.34896 | 0.26624 | 0.23781 | -121.2063 | -121.0967 | 0.18834 | -121.2961 | 0.33064 | 0.25493 | 0.066588 | -121.2525 | -121.2172 | 0.34509 | 0.32996 | 0.43951 | 0.4592 | -121.5078 | 0.24012 | 0.28378 | 0.31903 | 0.2979 | -121.3479
3495.5938 | 121.4996 | -0.31586 | 121.2708 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.02293 | -0.0073372 | -0.0097665 | -0.0099194 | -0.0020039 | 0.023019 | -0.0062322 | 0.022703 | 0.01121 | 0.05141 | 0.15708 | -0.031301 | 0.047549 | 0.027833 | 0.13739 | -0.27369 | 0.02852 | -0.00422 | -0.047194 | -0.057425 | -0.013765 | 0.012329 | -0.10004 | 0.042169 | -121.2232 | 0.36727 | 0.28456 | 0.24239 | -121.2429 | -121.1334 | 0.21581 | -121.3282 | 0.34438 | 0.26866 | 0.052851 | -121.2845 | -121.2584 | 0.36341 | 0.34369 | 0.45324 | 0.47294 | -121.5444 | 0.25843 | 0.30209 | 0.32819 | 0.31164 | -121.3708
3497.3594 | 121.6187 | -0.27924 | 121.2387 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.02293 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0022175 | 0.023233 | -0.0064458 | 0.022489 | 0.011424 | 0.05141 | 0.16166 | -0.035879 | 0.047549 | 0.023254 | 0.14197 | -0.26911 | 0.02852 | 0.004938 | -0.038036 | -0.052847 | -0.018344 | 0.016908 | -0.095467 | 0.010127 | -121.1912 | 0.33065 | 0.24336 | 0.23323 | -121.2155 | -121.0967 | 0.18377 | -121.2916 | 0.30776 | 0.2412 | 0.057431 | -121.2571 | -121.2218 | 0.32678 | 0.30249 | 0.4212 | 0.44089 | -121.5078 | 0.22639 | 0.26089 | 0.29614 | 0.28417 | -121.3342
3499.0938 | 121.6278 | -0.29297 | 121.2479 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.02293 | -0.0073372 | -0.0095529 | -0.0022889 | -0.0015767 | 0.023233 | -0.0064458 | 0.022916 | 0.010997 | 0.046831 | 0.15708 | -0.031301 | 0.042971 | 0.032411 | 0.14655 | -0.27827 | 0.042256 | 0.000359 | -0.038036 | -0.057425 | -0.009187 | 0.012329 | -0.10004 | 0.014702 | -121.2049 | 0.3398 | 0.26167 | 0.24697 | -121.2155 | -121.1013 | 0.19292 | -121.3053 | 0.33522 | 0.25493 | 0.062009 | -121.2571 | -121.2355 | 0.33594 | 0.32538 | 0.43951 | 0.45005 | -121.5261 | 0.23554 | 0.28378 | 0.3053 | 0.29333 | -121.3479
3500.875 | 121.6003 | -0.30212 | 121.2708 | 1.4211e-13 | -0.040252 | 0.0071689 | 0.022289 | -0.0075508 | -0.0095529 | -0.0099194 | -0.0015767 | 0.023233 | -0.0064458 | 0.022703 | 0.011424 | 0.05141 | 0.15708 | -0.031301 | 0.038393 | 0.032411 | 0.13739 | -0.27369 | 0.033099 | -0.00422 | -0.042615 | -0.057425 | -0.018344 | 0.016908 | -0.095467 | 0.028436 | -121.2324 | 0.35353 | 0.27082 | 0.24239 | -121.2383 | -121.1334 | 0.20666 | -121.3282 | 0.33522 | 0.25951 | 0.052852 | -121.2891 | -121.2538 | 0.34052 | 0.33454 | 0.43951 | 0.4592 | -121.5444 | 0.2447 | 0.28378 | 0.31903 | 0.2979 | -121.3662
3502.6406 | 121.6003 | -0.32044 | 121.2662 | 1.4211e-13 | -0.040252 | 0.0069553 | 0.022717 | -0.0073372 | -0.0095529 | -0.0099194 | -0.0020039 | 0.023233 | -0.0062322 | 0.022916 | 0.011424 | 0.055988 | 0.16166 | -0.031301 | 0.052128 | 0.027833 | 0.14197 | -0.27369 | 0.033099 | -0.00422 | -0.042615 | -0.057425 | -0.018344 | 0.012329 | -0.10004 | 0.046747 | -121.214 | 0.37642 | 0.28913 | 0.24239 | -121.2383 | -121.1242 | 0.22039 | -121.3236 | 0.35353 | 0.27782 | 0.05743 | -121.2845 | -121.2538 | 0.37256 | 0.34827 | 0.4624 | 0.48209 | -121.5399 | 0.26301 | 0.30209 | 0.33276 | 0.31622 | -121.3662
3504.4219 | 121.5683 | -0.34332 | 121.2982 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.02293 | -0.0075508 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023233 | -0.0062322 | 0.022703 | 0.01121 | 0.060567 | 0.16624 | -0.026723 | 0.052128 | 0.03699 | 0.13281 | -0.27827 | 0.02852 | 0.000359 | -0.038036 | -0.052847 | -0.013765 | 0.016908 | -0.095467 | 0.065056 | -121.2461 | 0.40389 | 0.3166 | 0.25154 | -121.2612 | -121.1654 | 0.24786 | -121.3511 | 0.37184 | 0.30529 | 0.057431 | -121.312 | -121.2813 | 0.39545 | 0.38031 | 0.47613 | 0.50956 | -121.5765 | 0.29048 | 0.32956 | 0.36023 | 0.34368 | -121.3937
3506.1406 | 121.6461 | -0.29755 | 121.2753 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022717 | -0.0075508 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023233 | -0.0062322 | 0.022916 | 0.011424 | 0.042253 | 0.16166 | -0.035879 | 0.042971 | 0.023254 | 0.14197 | -0.27827 | 0.037677 | 0.000359 | -0.042615 | -0.048268 | -0.013765 | 0.012329 | -0.10004 | 0.019279 | -121.2324 | 0.3398 | 0.26167 | 0.24239 | -121.2521 | -121.1334 | 0.1975 | -121.3236 | 0.33522 | 0.25493 | 0.05743 | -121.2891 | -121.263 | 0.34052 | 0.3208 | 0.43951 | 0.4592 | -121.5536 | 0.24928 | 0.28378 | 0.30987 | 0.2979 | -121.3754
3507.9219 | 121.5912 | -0.31128 | 121.312 | 1.4211e-13 | -0.040466 | 0.0075963 | 0.022717 | -0.0071236 | -0.0093393 | 0.0053411 | -0.0017903 | 0.023019 | -0.0066594 | 0.022703 | 0.011638 | 0.05141 | 0.16166 | -0.022144 | 0.052128 | 0.027833 | 0.14197 | -0.27369 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.009187 | 0.007751 | -0.10462 | 0.037591 | -121.2598 | 0.36269 | 0.28913 | 0.25154 | -121.2841 | -121.17 | 0.20665 | -121.3648 | 0.34896 | 0.26408 | 0.05743 | -121.3211 | -121.3042 | 0.36341 | 0.33911 | 0.45325 | 0.47294 | -121.5856 | 0.25843 | 0.30209 | 0.31903 | 0.31164 | -121.4166
3509.7031 | 121.6095 | -0.32044 | 121.2845 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022503 | -0.0077646 | -0.0095529 | -0.0022889 | -0.0017903 | 0.023019 | -0.0062322 | 0.022489 | 0.011424 | 0.05141 | 0.17539 | -0.022144 | 0.052128 | 0.027833 | 0.14197 | -0.28285 | 0.033099 | 0.004938 | -0.047194 | -0.048268 | -0.018344 | 0.016908 | -0.10462 | 0.037589 | -121.2324 | 0.37185 | 0.29829 | 0.2607 | -121.2567 | -121.1425 | 0.21581 | -121.3328 | 0.35353 | 0.27324 | 0.05743 | -121.3028 | -121.2676 | 0.37256 | 0.34827 | 0.4624 | 0.49583 | -121.5673 | 0.27217 | 0.30209 | 0.33734 | 0.32537 | -121.3891
3511.4219 | 121.6782 | -0.29297 | 121.2753 | 1.4211e-13 | -0.040252 | 0.0069553 | 0.022503 | -0.0077646 | -0.0095529 | -0.0099194 | -0.0017903 | 0.023233 | -0.0066594 | 0.022489 | 0.011851 | 0.055988 | 0.17539 | -0.017566 | 0.047549 | 0.027833 | 0.13739 | -0.28285 | 0.033099 | 0.000359 | -0.042615 | -0.062004 | -0.018344 | 0.007751 | -0.10004 | 0.010123 | -121.2278 | 0.34896 | 0.2754 | 0.26528 | -121.2475 | -121.1379 | 0.19292 | -121.3373 | 0.32607 | 0.25035 | 0.05743 | -121.2937 | -121.2676 | 0.34052 | 0.3208 | 0.43036 | 0.46836 | -121.5582 | 0.23096 | 0.27463 | 0.30072 | 0.29333 | -121.3754
3513.2031 | 121.6507 | -0.33417 | 121.3348 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022717 | -0.0075508 | -0.0095529 | 0.0053411 | -0.0020039 | 0.023233 | -0.0064458 | 0.022916 | 0.011424 | 0.05141 | 0.17539 | -0.017566 | 0.052128 | 0.023254 | 0.14655 | -0.28285 | 0.033099 | -0.008798 | -0.047194 | -0.048268 | -0.009187 | 0.007751 | -0.10462 | 0.051321 | -121.2827 | 0.38558 | 0.3166 | 0.26528 | -121.3116 | -121.1883 | 0.22954 | -121.3831 | 0.36727 | 0.28697 | 0.05743 | -121.344 | -121.3271 | 0.38629 | 0.35742 | 0.48071 | 0.50956 | -121.6177 | 0.2859 | 0.32498 | 0.34192 | 0.32537 | -121.4395
3514.9844 | 121.6553 | -0.32044 | 121.3257 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022717 | -0.0073372 | -0.0095529 | -0.0099194 | -0.0022175 | 0.023233 | -0.0058048 | 0.022703 | 0.011424 | 0.055988 | 0.17539 | -0.022144 | 0.056706 | 0.032411 | 0.13281 | -0.28742 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | -0.018344 | 0.016908 | -0.10462 | 0.03301 | -121.269 | 0.37642 | 0.29829 | 0.26528 | -121.2933 | -121.1929 | 0.21581 | -121.3785 | 0.35353 | 0.27782 | 0.062009 | -121.344 | -121.3088 | 0.37714 | 0.35285 | 0.45324 | 0.49583 | -121.6131 | 0.26759 | 0.30209 | 0.33734 | 0.32079 | -121.4303
3516.7031 | 121.7422 | -0.29297 | 121.2982 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.022717 | -0.0073372 | -0.0093393 | -0.0099194 | -0.0017903 | 0.023233 | -0.0064458 | 0.022916 | 0.011638 | 0.05141 | 0.17539 | -0.012988 | 0.042971 | 0.032411 | 0.14197 | -0.27827 | 0.033099 | 0.000359 | -0.047194 | -0.057425 | -0.018344 | 0.021486 | -0.10004 | 0.014702 | -121.2552 | 0.34438 | 0.27998 | 0.26528 | -121.2658 | -121.1563 | 0.19292 | -121.3556 | 0.32607 | 0.24577 | 0.052851 | -121.3166 | -121.2767 | 0.33594 | 0.32538 | 0.43493 | 0.46836 | -121.5765 | 0.23554 | 0.27463 | 0.31445 | 0.29333 | -121.3983
3518.5 | 121.5958 | -0.34332 | 121.3394 | 1.4211e-13 | -0.040893 | 0.0067415 | 0.022717 | -0.0073372 | -0.0095529 | -0.02518 | -0.0022175 | 0.023019 | -0.0064458 | 0.022916 | 0.01121 | 0.055988 | 0.17997 | -0.022144 | 0.042971 | 0.032411 | 0.13281 | -0.29658 | 0.037677 | -0.008798 | -0.047194 | -0.057425 | -0.013765 | 0.012329 | -0.095467 | 0.046741 | -121.2964 | 0.39931 | 0.32118 | 0.27444 | -121.307 | -121.2066 | 0.24786 | -121.3968 | 0.381 | 0.29613 | 0.048273 | -121.3532 | -121.3271 | 0.38629 | 0.37573 | 0.47613 | 0.52329 | -121.636 | 0.2859 | 0.32956 | 0.35565 | 0.33452 | -121.4349
3520.2812 | 121.6278 | -0.33417 | 121.3394 | 1.4211e-13 | -0.041107 | 0.0075963 | 0.022503 | -0.0077646 | -0.0097665 | -0.0022889 | -0.0015767 | 0.023233 | -0.0060184 | 0.022916 | 0.01121 | 0.055988 | 0.18455 | -0.022144 | 0.052128 | 0.027833 | 0.13739 | -0.28742 | 0.037677 | 0.000359 | -0.047194 | -0.057425 | -0.009187 | 0.012329 | -0.086309 | 0.046742 | -121.2873 | 0.39015 | 0.31202 | 0.26528 | -121.3116 | -121.202 | 0.24786 | -121.3968 | 0.37184 | 0.28697 | 0.039115 | -121.3486 | -121.3271 | 0.38629 | 0.362 | 0.47155 | 0.51872 | -121.6268 | 0.27674 | 0.32498 | 0.3465 | 0.33453 | -121.4257
3522.0156 | 121.7422 | -0.31586 | 121.3348 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.022717 | -0.0075508 | -0.0093393 | -0.0022889 | -0.0017903 | 0.023447 | -0.0062322 | 0.022703 | 0.01121 | 0.060567 | 0.18455 | -0.026723 | 0.047549 | 0.027833 | 0.14197 | -0.28742 | 0.033099 | -0.008798 | -0.056351 | -0.057425 | -0.013765 | 0.012329 | -0.10462 | 0.028432 | -121.2873 | 0.37642 | 0.28913 | 0.2607 | -121.307 | -121.1929 | 0.21123 | -121.3923 | 0.34896 | 0.25951 | 0.048273 | -121.3486 | -121.3225 | 0.36341 | 0.34369 | 0.45782 | 0.50041 | -121.6223 | 0.25843 | 0.30209 | 0.32819 | 0.30706 | -121.4395
3523.7969 | 121.7606 | -0.31128 | 121.3211 | 1.4211e-13 | -0.040466 | 0.0071689 | 0.022717 | -0.0075508 | -0.0091255 | 0.0053411 | -0.0020039 | 0.023233 | -0.0064458 | 0.022916 | 0.011424 | 0.055988 | 0.18913 | -0.017566 | 0.052128 | 0.032411 | 0.13739 | -0.29658 | 0.033099 | 0.000359 | -0.051772 | -0.062004 | -0.013765 | 0.003172 | -0.10004 | 0.014697 | -121.269 | 0.36727 | 0.29371 | 0.27902 | -121.2887 | -121.1837 | 0.21123 | -121.3831 | 0.34438 | 0.25951 | 0.048273 | -121.3349 | -121.3179 | 0.36341 | 0.34369 | 0.44867 | 0.50041 | -121.6177 | 0.24927 | 0.29751 | 0.31445 | 0.31164 | -121.4212
3525.5781 | 121.7651 | -0.32044 | 121.2753 | 1.4211e-13 | -0.040466 | 0.0069553 | 0.022503 | -0.0075508 | -0.0093393 | -0.0099194 | -0.0015767 | 0.023233 | -0.0064458 | 0.022916 | 0.010997 | 0.05141 | 0.18913 | -0.017566 | 0.052128 | 0.032411 | 0.14197 | -0.29658 | 0.033099 | -0.00422 | -0.047194 | -0.052847 | -0.009187 | 0.007751 | -0.10004 | 0.023853 | -121.2232 | 0.37185 | 0.30287 | 0.27902 | -121.2429 | -121.1334 | 0.22039 | -121.3282 | 0.35353 | 0.27324 | 0.052851 | -121.2845 | -121.2676 | 0.37256 | 0.35285 | 0.4624 | 0.50956 | -121.5719 | 0.26759 | 0.31125 | 0.32819 | 0.31622 | -121.3754
3527.2812 | 121.6461 | -0.34332 | 121.3394 | 1.4211e-13 | -0.040679 | 0.0069553 | 0.023144 | -0.0077646 | -0.0095529 | -0.0022889 | -0.0022175 | 0.022806 | -0.0062322 | 0.02313 | 0.01121 | 0.055988 | 0.19371 | -0.017566 | 0.047549 | 0.027833 | 0.13281 | -0.30116 | 0.033099 | 0.000359 | -0.042615 | -0.062004 | -0.013765 | 0.016908 | -0.10004 | 0.042162 | -121.2919 | 0.39931 | 0.32576 | 0.2836 | -121.3116 | -121.2066 | 0.24328 | -121.4014 | 0.37642 | 0.30071 | 0.05743 | -121.3532 | -121.3225 | 0.39087 | 0.37116 | 0.47613 | 0.53703 | -121.6406 | 0.28132 | 0.32956 | 0.36023 | 0.34368 | -121.4395
3529.0781 | 121.6553 | -0.36163 | 121.3623 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.022503 | -0.0073372 | -0.0093393 | -0.0099194 | -0.0015767 | 0.023019 | -0.0066594 | 0.022489 | 0.011424 | 0.055988 | 0.19371 | -0.012988 | 0.047549 | 0.032411 | 0.14655 | -0.30116 | 0.037677 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.016908 | -0.10462 | 0.060472 | -121.3148 | 0.41762 | 0.34864 | 0.28817 | -121.3299 | -121.2158 | 0.25701 | -121.4197 | 0.39931 | 0.31902 | 0.062009 | -121.3761 | -121.3454 | 0.40918 | 0.39404 | 0.50818 | 0.55534 | -121.6635 | 0.30421 | 0.34787 | 0.37854 | 0.36199 | -121.4669
3530.8594 | 121.7926 | -0.31586 | 121.3348 | 1.4211e-13 | -0.040466 | 0.0065279 | 0.022717 | -0.0073372 | -0.0093393 | -0.0099194 | -0.0020039 | 0.023233 | -0.0062322 | 0.022489 | 0.011424 | 0.065145 | 0.19829 | -0.012988 | 0.047549 | 0.027833 | 0.13739 | -0.30574 | 0.033099 | 0.000359 | -0.047194 | -0.048268 | -0.013765 | 0.012329 | -0.10462 | 0.010117 | -121.2873 | 0.381 | 0.30287 | 0.29275 | -121.307 | -121.1975 | 0.21123 | -121.3831 | 0.34896 | 0.26866 | 0.05743 | -121.3486 | -121.3225 | 0.36341 | 0.34369 | 0.45324 | 0.51414 | -121.6406 | 0.26759 | 0.30209 | 0.32819 | 0.31622 | -121.4395
3532.5781 | 121.6736 | -0.35706 | 121.3348 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.022503 | -0.0073372 | -0.0095529 | 0.0053411 | -0.0020039 | 0.023233 | -0.0062322 | 0.02313 | 0.01121 | 0.055988 | 0.20286 | -0.008409 | 0.056706 | 0.03699 | 0.14655 | -0.30574 | 0.037677 | -0.00422 | -0.047194 | -0.062004 | -0.013765 | 0.007751 | -0.10004 | 0.051316 | -121.2781 | 0.41304 | 0.34865 | 0.29733 | -121.2978 | -121.1883 | 0.25701 | -121.3968 | 0.39473 | 0.30986 | 0.052851 | -121.3486 | -121.3271 | 0.41376 | 0.39405 | 0.5036 | 0.55992 | -121.6406 | 0.29505 | 0.34329 | 0.36481 | 0.35284 | -121.4349
3534.375 | 121.669 | -0.37079 | 121.3531 | 1.4211e-13 | -0.040679 | 0.0071689 | 0.02293 | -0.0075508 | -0.0097665 | -0.0099194 | -0.0017903 | 0.023233 | -0.0062322 | 0.02313 | 0.011424 | 0.069723 | 0.20286 | -0.017566 | 0.047549 | 0.03699 | 0.14197 | -0.3149 | 0.037677 | 0.004938 | -0.047194 | -0.052847 | -0.018344 | 0.012329 | -0.10462 | 0.055891 | -121.3056 | 0.44051 | 0.35322 | 0.29733 | -121.3162 | -121.2112 | 0.26616 | -121.406 | 0.40847 | 0.32359 | 0.05743 | -121.3715 | -121.3408 | 0.41834 | 0.40778 | 0.51275 | 0.57365 | -121.668 | 0.31794 | 0.35245 | 0.38312 | 0.37573 | -121.4578
3536.1406 | 121.7834 | -0.32501 | 121.3165 | 1.4211e-13 | -0.040679 | 0.0073825 | 0.022289 | -0.0077646 | -0.0095529 | -0.0022889 | -0.0020039 | 0.023233 | -0.0066594 | 0.02313 | 0.01121 | 0.060567 | 0.20744 | -0.008409 | 0.052128 | 0.03699 | 0.13739 | -0.31948 | 0.02852 | 0.000359 | -0.047194 | -0.052847 | -0.013765 | 0.016908 | -0.11378 | 0.005535 | -121.2644 | 0.38558 | 0.3166 | 0.31107 | -121.2795 | -121.1791 | 0.21123 | -121.3694 | 0.35353 | 0.27782 | 0.066588 | -121.3303 | -121.2996 | 0.37714 | 0.362 | 0.4624 | 0.53246 | -121.636 | 0.27217 | 0.31125 | 0.34192 | 0.32537 | -121.4303
3537.8594 | 121.7972 | -0.31128 | 121.312 | 1.4211e-13 | -0.040893 | 0.0073825 | 0.022503 | -0.0071236 | -0.0095529 | -0.0099194 | -0.0017903 | 0.023233 | -0.0064458 | 0.02313 | 0.010997 | 0.069723 | 0.22118 | -0.008409 | 0.056706 | 0.032411 | 0.14197 | -0.3149 | 0.033099 | -0.008798 | -0.042615 | -0.057425 | -0.018344 | 0.012329 | -0.095467 | -0.003619 | -121.2552 | 0.381 | 0.30287 | 0.30649 | -121.2795 | -121.17 | 0.21581 | -121.3694 | 0.34438 | 0.26866 | 0.052852 | -121.3303 | -121.2996 | 0.36798 | 0.34369 | 0.45325 | 0.53246 | -121.6268 | 0.25385 | 0.29293 | 0.32361 | 0.30248 | -121.4074
3539.6406 | 121.7239 | -0.37079 | 121.3394 | 1.4211e-13 | -0.040893 | 0.0071689 | 0.022503 | -0.0073372 | -0.0093393 | -0.0099194 | -0.0020039 | 0.023019 | -0.0064458 | 0.022916 | 0.011424 | 0.065145 | 0.2166 | -0.017566 | 0.056706 | 0.032411 | 0.14655 | -0.32864 | 0.037677 | -0.00422 | -0.047194 | -0.062004 | -0.013765 | 0.007751 | -0.10462 | 0.042154 | -121.2827 | 0.43593 | 0.35322 | 0.31107 | -121.307 | -121.1929 | 0.26616 | -121.4014 | 0.40847 | 0.32359 | 0.05743 | -121.3532 | -121.3317 | 0.42749 | 0.4032 | 0.51733 | 0.58739 | -121.6681 | 0.30878 | 0.35702 | 0.37854 | 0.36657 | -121.444
3541.4219 | 121.756 | -0.93842 | 120.726 | 1.4211e-13 | -0.041534 | 0.0073825 | 0.023358 | -0.0071236 | -0.0084845 | -0.01755 | -0.0024313 | 0.023447 | -0.0064458 | 0.022916 | 0.011424 | 0.10177 | 0.3448 | -0.15034 | 0.1208 | 0.1011 | 0.20607 | -0.88269 | 0.033099 | -0.017956 | -0.056351 | -0.066582 | -0.027501 | 0.007751 | -0.1092 | 0.055731 | -120.6052 | 1.0402 | 0.78808 | 0.73235 | -120.6249 | -120.5199 | 0.82921 | -120.7926 | 0.97152 | 0.88206 | 0.052852 | -120.7535 | -120.7183 | 1.0592 | 1.0395 | 1.1445 | 1.2832 | -121.6087 | 0.87183 | 0.91092 | 0.94617 | 0.92046 | -120.8352
3543.2031 | 121.8018 | -0.98419 | 120.6573 | 1.4211e-13 | -0.041748 | 0.0073825 | 0.023144 | -0.0073372 | -0.0080573 | -0.0099194 | -0.0022175 | 0.023233 | -0.0064458 | 0.022916 | 0.011424 | 0.10177 | 0.36769 | -0.16407 | 0.13454 | 0.10567 | 0.2198 | -0.95595 | 0.02852 | -0.008798 | -0.06093 | -0.066582 | -0.027501 | 0.003172 | -0.11378 | 0.028244 | -120.5228 | 1.086 | 0.82012 | 0.79188 | -120.5517 | -120.4375 | 0.87041 | -120.7239 | 1.0127 | 0.92326 | 0.052852 | -120.6848 | -120.6542 | 1.1187 | 1.0899 | 1.204 | 1.3519 | -121.6133 | 0.91761 | 0.95669 | 0.98736 | 0.97539 | -120.7711
3544.9219 | 121.7514 | -1.0574 | 120.5887 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.023144 | -0.00691 | -0.0080573 | -0.0022889 | -0.0022175 | 0.02366 | -0.0064458 | 0.022916 | 0.01121 | 0.092615 | 0.35854 | -0.19612 | 0.12538 | 0.11025 | 0.21522 | -1.0109 | 0.019362 | -0.013377 | -0.056351 | -0.071161 | -0.022922 | 0.003172 | -0.1092 | 0.046539 | -120.4633 | 1.15 | 0.86132 | 0.81478 | -120.4784 | -120.3735 | 0.94823 | -120.6598 | 1.0768 | 1.0011 | 0.052852 | -120.6116 | -120.5855 | 1.1828 | 1.1677 | 1.2727 | 1.416 | -121.5996 | 0.98627 | 1.0345 | 1.0606 | 1.0441 | -120.6979
3546.7031 | 121.8063 | -1.0895 | 120.52 | 1.4211e-13 | -0.041748 | 0.0073825 | 0.023785 | -0.0071236 | -0.0078435 | -0.0099194 | -0.0024313 | 0.02366 | -0.0066594 | 0.023344 | 0.01121 | 0.097194 | 0.3448 | -0.21443 | 0.12538 | 0.10567 | 0.21064 | -1.0658 | 0.02852 | -0.008798 | -0.056351 | -0.066582 | -0.03208 | -0.001407 | -0.11378 | 0.023636 | -120.3946 | 1.1867 | 0.87505 | 0.85141 | -120.4143 | -120.3094 | 0.9757 | -120.5866 | 1.118 | 1.0331 | 0.057431 | -120.5521 | -120.5214 | 1.2149 | 1.1952 | 1.3001 | 1.4343 | -121.5859 | 1.0229 | 1.0574 | 1.0881 | 1.0807 | -120.6338
3548.4688 | 121.7697 | -1.1765 | 120.5246 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.023785 | -0.00691 | -0.0074163 | -0.0022889 | -0.0024313 | 0.023874 | -0.0064458 | 0.02313 | 0.010997 | 0.074302 | 0.30817 | -0.306 | 0.12538 | 0.096516 | 0.20607 | -1.2536 | 0.023941 | -0.00422 | -0.06093 | -0.066582 | -0.022922 | 0.007751 | -0.11836 | -0.077125 | -120.3992 | 1.2508 | 0.87045 | 0.94758 | -120.4281 | -120.3185 | 1.0581 | -120.5912 | 1.2004 | 1.1155 | 0.057431 | -120.5475 | -120.5168 | 1.3018 | 1.273 | 1.3825 | 1.4846 | -121.7782 | 1.1099 | 1.1535 | 1.1842 | 1.1722 | -120.643
3550.1875 | 121.8109 | -0.94757 | 120.7123 | 1.4211e-13 | -0.041748 | 0.0073825 | 0.023358 | -0.0073372 | -0.0080573 | 0.0053411 | -0.0024313 | 0.02366 | -0.0064458 | 0.02313 | 0.01121 | 0.11551 | 0.39975 | -0.12745 | 0.13912 | 0.11483 | 0.22438 | -0.92847 | 0.023941 | -0.013377 | -0.051772 | -0.062004 | -0.03208 | 0.007751 | -0.11836 | 0.019097 | -120.5732 | 1.0631 | 0.82013 | 0.80103 | -120.5974 | -120.4879 | 0.82921 | -120.7743 | 0.97151 | 0.8958 | 0.066589 | -120.7444 | -120.7045 | 1.0867 | 1.0624 | 1.172 | 1.3473 | -121.6408 | 0.88557 | 0.91549 | 0.95532 | 0.93419 | -120.8306
3551.9688 | 121.7285 | -0.96588 | 120.7352 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.023571 | -0.00691 | -0.0078435 | -0.0099194 | -0.0020039 | 0.023874 | -0.0064458 | 0.022703 | 0.01121 | 0.11551 | 0.40432 | -0.13202 | 0.13912 | 0.11941 | 0.22896 | -0.94221 | 0.02852 | -0.00422 | -0.056351 | -0.062004 | -0.022922 | -0.001407 | -0.11836 | 0.02367 | -120.5961 | 1.0814 | 0.83386 | 0.81019 | -120.6158 | -120.5062 | 0.84752 | -120.7972 | 0.9944 | 0.90953 | 0.06201 | -120.7581 | -120.7366 | 1.105 | 1.0853 | 1.1948 | 1.3702 | -121.6774 | 0.90388 | 0.94296 | 0.96447 | 0.96166 | -120.8535
3553.75 | 121.8018 | -0.99335 | 120.6573 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.023785 | -0.00691 | -0.0080573 | -0.0022889 | -0.0024313 | 0.02366 | -0.0064458 | 0.022703 | 0.01121 | 0.12009 | 0.39059 | -0.15034 | 0.13454 | 0.11025 | 0.2198 | -0.9651 | 0.023941 | -0.008798 | -0.051772 | -0.066582 | -0.022922 | 0.003172 | -0.11378 | 0.028242 | -120.5228 | 1.1134 | 0.84301 | 0.81477 | -120.5471 | -120.4375 | 0.87956 | -120.7239 | 1.0173 | 0.94157 | 0.06201 | -120.6803 | -120.6542 | 1.1279 | 1.1036 | 1.2131 | 1.3839 | -121.6225 | 0.92676 | 0.97042 | 0.99652 | 0.98455 | -120.7711
3555.5312 | 121.6873 | -1.2085 | 120.52 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.023358 | -0.0066962 | -0.0074163 | -0.0022889 | -0.0020039 | 0.023447 | -0.0066594 | 0.022916 | 0.01121 | 0.092615 | 0.37227 | -0.22359 | 0.12996 | 0.11483 | 0.2198 | -1.1528 | 0.023941 | -0.008798 | -0.056351 | -0.071161 | -0.022922 | 0.003172 | -0.11378 | 0.055655 | -120.3901 | 1.3011 | 0.98491 | 0.92925 | -120.4052 | -120.3002 | 1.0947 | -120.5912 | 1.2324 | 1.1521 | 0.057431 | -120.5429 | -120.5168 | 1.3385 | 1.3233 | 1.4283 | 1.5808 | -121.6729 | 1.1373 | 1.1856 | 1.2117 | 1.1997 | -120.6338
3557.2344 | 121.7743 | -0.81482 | 120.8679 | 1.4211e-13 | -0.04132 | 0.0071689 | 0.023144 | -0.0073372 | -0.0082709 | -0.01755 | -0.0022175 | 0.023447 | -0.0066594 | 0.022916 | 0.011424 | 0.088037 | 0.31275 | -0.14118 | 0.084176 | 0.064464 | 0.18775 | -0.8369 | 0.02852 | -0.008798 | -0.051772 | -0.066582 | -0.018344 | 0.007751 | -0.11378 | -0.022077 | -120.7837 | 0.90286 | 0.67364 | 0.69572 | -120.8035 | -120.6802 | 0.70104 | -120.9345 | 0.84334 | 0.76305 | 0.06201 | -120.8863 | -120.8602 | 0.89899 | 0.87928 | 1.0026 | 1.1276 | -121.7048 | 0.74824 | 0.79647 | 0.82257 | 0.80602 | -120.9817
3559.0312 | 121.7102 | -1.1078 | 120.6436 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.023144 | -0.00691 | -0.0078435 | -0.0099194 | -0.0022175 | 0.023874 | -0.0064458 | 0.022916 | 0.01121 | 0.10177 | 0.37227 | -0.18238 | 0.11622 | 0.091937 | 0.21064 | -1.0155 | 0.019362 | -0.013377 | -0.056351 | -0.066582 | -0.027501 | 0.003172 | -0.11836 | 0.092314 | -120.5274 | 1.2096 | 0.9254 | 0.83309 | -120.5517 | -120.433 | 0.98943 | -120.7102 | 1.1272 | 1.0514 | 0.06201 | -120.6711 | -120.6404 | 1.224 | 1.1997 | 1.3184 | 1.4801 | -121.6591 | 1.0412 | 1.0803 | 1.111 | 1.0944 | -120.762
3560.8125 | 121.8201 | -1.1765 | 120.5109 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.023785 | -0.00691 | -0.0076299 | -0.0099194 | -0.0024313 | 0.02366 | -0.0066594 | 0.02313 | 0.01121 | 0.092615 | 0.36769 | -0.20985 | 0.1208 | 0.096516 | 0.21064 | -1.1208 | 0.023941 | -0.017956 | -0.056351 | -0.066582 | -0.027501 | 0.003172 | -0.11378 | 0.055664 | -120.3901 | 1.2691 | 0.9666 | 0.91094 | -120.4143 | -120.3002 | 1.0627 | -120.5774 | 1.2004 | 1.1201 | 0.057431 | -120.5384 | -120.5077 | 1.2973 | 1.273 | 1.3871 | 1.5441 | -121.6317 | 1.1099 | 1.149 | 1.1796 | 1.1585 | -120.6246
3562.5938 | 121.8338 | -1.7395 | 119.9295 | 1.4211e-13 | -0.041534 | 0.0073825 | 0.023358 | -0.00691 | -0.0065615 | -0.0099194 | -0.0026449 | 0.024515 | -0.0064458 | 0.022916 | 0.010997 | -0.012688 | 0.17997 | -0.50286 | 0.070441 | 0.050727 | 0.16028 | -1.6932 | 0.010205 | -0.022535 | -0.070087 | -0.071161 | -0.03208 | -0.010564 | -0.12294 | 0.046348 | -119.8591 | 1.7268 | 1.2366 | 1.1903 | -119.8788 | -119.7692 | 1.6166 | -120.0007 | 1.7497 | 1.6694 | 0.052852 | -119.9616 | -119.9401 | 1.8099 | 1.7902 | 1.8998 | 1.9195 | -121.6227 | 1.6683 | 1.7074 | 1.7289 | 1.717 | -120.0524
3564.375 | 121.7651 | -1.8585 | 119.8013 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.023571 | -0.0066962 | -0.0065615 | -0.0022889 | -0.0024313 | 0.024301 | -0.006873 | 0.02313 | 0.011638 | -0.06305 | 0.060928 | -0.65395 | 0.038393 | 0.023254 | 0.12823 | -1.89 | 0.014784 | -0.027113 | -0.070087 | -0.075739 | -0.041237 | -0.015142 | -0.1321 | -0.031527 | -119.7629 | 1.7955 | 1.2046 | 1.2361 | -119.7781 | -119.6731 | 1.7264 | -119.8771 | 1.8733 | 1.7884 | 0.06201 | -119.8426 | -119.8165 | 1.8969 | 1.8818 | 1.9868 | 1.9194 | -121.6914 | 1.7828 | 1.8173 | 1.8434 | 1.8314 | -119.9334
3566.1406 | 121.8155 | -1.8082 | 119.8288 | 1.4211e-13 | -0.041961 | 0.0073825 | 0.023144 | -0.00691 | -0.0065615 | -0.0099194 | -0.0024313 | 0.024301 | -0.0066594 | 0.02313 | 0.010997 | -0.06305 | 0.05635 | -0.61732 | 0.029236 | 0.014096 | 0.12823 | -1.7756 | 0.014784 | -0.031692 | -0.070087 | -0.075739 | -0.036658 | 0.003172 | -0.12294 | 0.032592 | -119.7996 | 1.7451 | 1.1908 | 1.1583 | -119.8147 | -119.7006 | 1.6852 | -119.9045 | 1.823 | 1.7381 | 0.052852 | -119.8655 | -119.8256 | 1.8374 | 1.8223 | 1.9364 | 1.8645 | -121.6044 | 1.7324 | 1.7715 | 1.8113 | 1.7765 | -119.9517
3567.9219 | 121.7606 | -1.8448 | 119.8471 | 1.4211e-13 | -0.041748 | 0.0073825 | 0.023358 | -0.0066962 | -0.0067753 | 0.012972 | -0.0030721 | 0.024088 | -0.0070868 | 0.02313 | 0.010997 | -0.072207 | 0.042614 | -0.65395 | 0.029236 | 0.009517 | 0.11907 | -1.8534 | 0.010205 | -0.027113 | -0.070087 | -0.080318 | -0.027501 | -0.015142 | -0.1321 | -0.008629 | -119.8179 | 1.7726 | 1.1908 | 1.1995 | -119.8376 | -119.728 | 1.7127 | -119.9274 | 1.855 | 1.7747 | 0.06201 | -119.8746 | -119.8622 | 1.874 | 1.8543 | 1.9639 | 1.8874 | -121.7005 | 1.7645 | 1.8173 | 1.8296 | 1.8177 | -119.9792
3569.6562 | 121.7651 | -2.2614 | 119.4168 | 1.4211e-13 | -0.042389 | 0.0073825 | 0.023571 | -0.0066962 | -0.0059207 | 0.0053411 | -0.0026449 | 0.024515 | -0.0066594 | 0.02313 | 0.010997 | -0.09052 | 0.015142 | -0.78214 | 0.033814 | 0.014096 | 0.12823 | -2.1923 | 0.010205 | -0.022535 | -0.074666 | -0.084896 | -0.041237 | -0.015142 | -0.13668 | 0.069096 | -119.383 | 2.1708 | 1.4792 | 1.4101 | -119.4027 | -119.2886 | 2.1247 | -119.5017 | 2.2716 | 2.1867 | 0.06201 | -119.458 | -119.432 | 2.2952 | 2.2754 | 2.3896 | 2.2765 | -121.6091 | 2.1765 | 2.2201 | 2.2462 | 2.2388 | -119.5535
3571.4375 | 121.7697 | -2.0325 | 119.6182 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.023358 | -0.0071236 | -0.0063479 | -0.0099194 | -0.0026449 | 0.024088 | -0.0064458 | 0.02313 | 0.010997 | -0.081363 | 0.0243 | -0.71804 | 0.033814 | 0.000359 | 0.11907 | -2.0549 | 0.019362 | -0.031692 | -0.079245 | -0.080318 | -0.041237 | -0.015142 | -0.12752 | -0.022418 | -119.5844 | 1.9511 | 1.3144 | 1.3368 | -119.6179 | -119.4992 | 1.905 | -119.6985 | 2.0518 | 1.9532 | 0.048273 | -119.6595 | -119.6334 | 2.0663 | 2.0328 | 2.1515 | 2.0568 | -121.6731 | 1.9522 | 1.9912 | 2.0173 | 2.0008 | -119.7457
3573.2188 | 121.7148 | -2.0462 | 119.6915 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.023358 | -0.0066962 | -0.0063479 | -0.01755 | -0.0028585 | 0.024515 | -0.0064458 | 0.02313 | 0.01121 | -0.081363 | 0.028878 | -0.70889 | 0.029236 | 0.009517 | 0.11907 | -2.0045 | 0.005626 | -0.027113 | -0.074666 | -0.080318 | -0.041237 | -0.005985 | -0.12294 | 0.041683 | -119.6622 | 1.9648 | 1.3373 | 1.2956 | -119.682 | -119.5724 | 1.9233 | -119.7718 | 2.0518 | 1.9715 | 0.048273 | -119.7327 | -119.6975 | 2.0754 | 2.0557 | 2.1653 | 2.0751 | -121.696 | 1.9659 | 2.005 | 2.0402 | 2.0191 | -119.8144
3574.9531 | 121.8201 | -2.2614 | 119.4214 | 1.4211e-13 | -0.041961 | 0.0075963 | 0.023358 | -0.0066962 | -0.0059207 | -0.0022889 | -0.0026449 | 0.024301 | -0.0066594 | 0.022916 | 0.010783 | -0.09052 | 0.015142 | -0.74551 | 0.024657 | 0.000359 | 0.11907 | -2.1282 | 0.010205 | -0.031692 | -0.079245 | -0.080318 | -0.045815 | -0.015142 | -0.12752 | 0.1332 | -119.3967 | 2.1708 | 1.5158 | 1.3826 | -119.421 | -119.3023 | 2.1338 | -119.5017 | 2.2716 | 2.1821 | 0.048273 | -119.4672 | -119.4365 | 2.286 | 2.2617 | 2.3804 | 2.2765 | -121.5495 | 2.181 | 2.2155 | 2.2462 | 2.2297 | -119.5489
3576.7344 | 121.7468 | -2.655 | 119.046 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.023785 | -0.006269 | -0.0050659 | -0.01755 | -0.0028585 | 0.024515 | -0.0070868 | 0.022916 | 0.011424 | -0.12715 | -0.026065 | -0.90117 | 0.015501 | 0.000359 | 0.10992 | -2.5723 | 0.010205 | -0.027113 | -0.074666 | -0.084896 | -0.050394 | -0.019721 | -0.13668 | 0.082721 | -119.0305 | 2.5279 | 1.7539 | 1.6711 | -119.0457 | -118.9361 | 2.5184 | -119.1309 | 2.6652 | 2.5804 | 0.06201 | -119.0964 | -119.0657 | 2.6705 | 2.6554 | 2.7649 | 2.629 | -121.6183 | 2.5701 | 2.6046 | 2.6353 | 2.6279 | -119.1827
3578.5 | 121.6873 | -2.6688 | 119.0186 | 1.4211e-13 | -0.042389 | 0.0071689 | 0.023785 | -0.00691 | -0.0057069 | -0.0022889 | -0.0024313 | 0.024729 | -0.0066594 | 0.022916 | 0.01121 | -0.085942 | 0.070086 | -0.70431 | 0.024657 | 0.004938 | 0.11907 | -2.238 | 0.005626 | -0.027113 | -0.074666 | -0.080318 | -0.045815 | -0.010564 | -0.14125 | 0.43072 | -118.9939 | 2.5828 | 1.9645 | 1.5337 | -119.0136 | -118.8995 | 2.5275 | -119.0989 | 2.6744 | 2.5941 | 0.066589 | -119.0644 | -119.0291 | 2.6934 | 2.6737 | 2.7878 | 2.7388 | -121.2566 | 2.5884 | 2.6229 | 2.6582 | 2.6416 | -119.1598
3580.2344 | 121.6827 | -2.7969 | 118.7988 | 1.4211e-13 | -0.042602 | 0.0071689 | 0.023785 | -0.0064826 | -0.0046387 | -0.0099194 | -0.0030721 | 0.024942 | -0.0073004 | 0.022916 | 0.011424 | -0.12257 | 0.033457 | -0.94696 | 0.029236 | 0.000359 | 0.10992 | -2.7417 | 0.001048 | -0.031692 | -0.079245 | -0.098632 | -0.054973 | -0.0243 | -0.14583 | 0.055208 | -118.7696 | 2.6744 | 1.85 | 1.7948 | -118.7985 | -118.6889 | 2.6511 | -118.8975 | 2.798 | 2.7177 | 0.066588 | -118.8538 | -118.8231 | 2.8262 | 2.7973 | 2.9069 | 2.8304 | -121.5406 | 2.6983 | 2.742 | 2.7726 | 2.7652 | -118.9447
3582.0469 | 121.6232 | -2.9114 | 118.7439 | 1.4211e-13 | -0.042602 | 0.0071689 | 0.023571 | -0.0064826 | -0.0046387 | -0.0099194 | -0.0030721 | 0.025156 | -0.0073004 | 0.022703 | 0.01121 | -0.1363 | 0.038035 | -0.96985 | 0.024657 | 0.004938 | 0.11449 | -2.8333 | -0.003531 | -0.045428 | -0.083823 | -0.084896 | -0.041237 | -0.019721 | -0.14583 | 0.07807 | -118.7192 | 2.7751 | 1.9415 | 1.8635 | -118.739 | -118.6294 | 2.7655 | -118.8288 | 2.9078 | 2.8276 | 0.06201 | -118.7851 | -118.7636 | 2.936 | 2.9163 | 3.0259 | 2.9494 | -121.5772 | 2.8265 | 2.8701 | 2.8917 | 2.8659 | -118.8897
3583.8281 | 121.6736 | -2.9572 | 118.6111 | 1.4211e-13 | -0.042389 | 0.0069553 | 0.023571 | -0.006269 | -0.0046387 | -0.0022889 | -0.0028585 | 0.024729 | -0.0073004 | 0.022916 | 0.011424 | -0.15004 | 0.0243 | -1.0019 | 0.024657 | -0.008799 | 0.10076 | -2.9111 | 0.001048 | -0.040849 | -0.083823 | -0.089475 | -0.050394 | -0.0243 | -0.14125 | 0.046005 | -118.5865 | 2.8071 | 1.9553 | 1.9093 | -118.6199 | -118.5104 | 2.8159 | -118.7006 | 2.9582 | 2.8733 | 0.057432 | -118.6615 | -118.6354 | 2.9818 | 2.9484 | 3.0579 | 2.9815 | -121.5223 | 2.8677 | 2.9068 | 2.9329 | 2.9163 | -118.7524
3585.5469 | 121.6644 | -3.0396 | 118.5196 | 1.4211e-13 | -0.042175 | 0.0067415 | 0.023571 | -0.0060552 | -0.0039977 | -0.0099194 | -0.0034995 | 0.025156 | -0.0073004 | 0.022916 | 0.010997 | -0.14088 | 0.019721 | -1.0248 | 0.020079 | -0.008799 | 0.10534 | -3.0027 | 0.001048 | -0.045428 | -0.083823 | -0.094053 | -0.050394 | -0.0243 | -0.1321 | 0.036824 | -118.4995 | 2.8987 | 2.0148 | 1.9779 | -118.5284 | -118.4143 | 2.9075 | -118.6136 | 3.0406 | 2.9557 | 0.048274 | -118.57 | -118.5439 | 3.0596 | 3.0308 | 3.1449 | 3.0593 | -121.5223 | 2.9455 | 2.9892 | 3.0153 | 2.9941 | -118.6517
3587.3125 | 121.7056 | -3.0808 | 118.428 | 1.4211e-13 | -0.041961 | 0.0071689 | 0.023785 | -0.0058416 | -0.0037839 | 0.0053411 | -0.0030721 | 0.024942 | -0.0073004 | 0.023557 | 0.010997 | -0.15462 | 0.005985 | -1.0477 | 0.020079 | -0.008799 | 0.10534 | -3.0577 | -0.003531 | -0.040849 | -0.083823 | -0.10321 | -0.054973 | -0.019721 | -0.14125 | 0.023076 | -118.408 | 2.9261 | 2.0331 | 2.01 | -118.4368 | -118.3227 | 2.9395 | -118.5312 | 3.0772 | 2.9969 | 0.057432 | -118.483 | -118.4478 | 3.1008 | 3.072 | 3.1861 | 3.0867 | -121.4857 | 2.9775 | 3.0258 | 3.061 | 3.0399 | -118.5693
3589.0781 | 121.6461 | -3.1586 | 118.3777 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.023785 | -0.0060552 | -0.0042113 | -0.01755 | -0.0028585 | 0.024942 | -0.0070868 | 0.023344 | 0.01121 | -0.16377 | 0.005985 | -1.0706 | 0.015501 | -0.00422 | 0.10076 | -3.1447 | -0.012689 | -0.040849 | -0.088402 | -0.094053 | -0.054973 | -0.019721 | -0.15041 | 0.013895 | -118.3622 | 2.9948 | 2.088 | 2.0741 | -118.3819 | -118.2769 | 3.0082 | -118.4717 | 3.1459 | 3.0702 | 0.06201 | -118.4327 | -118.3974 | 3.1741 | 3.1543 | 3.2593 | 3.1646 | -121.5224 | 3.0645 | 3.1036 | 3.1388 | 3.1177 | -118.5281
3590.875 | 121.6187 | -3.186 | 118.3868 | 1.4211e-13 | -0.042602 | 0.0073825 | 0.023785 | -0.006269 | -0.0035703 | -0.0022889 | -0.0032857 | 0.025156 | -0.007514 | 0.02313 | 0.011424 | -0.15462 | 0.005985 | -1.0477 | 0.020079 | 0.004938 | 0.10992 | -3.1264 | -0.003531 | -0.036271 | -0.088402 | -0.094053 | -0.054973 | -0.033457 | -0.14125 | 0.059677 | -118.3668 | 3.0314 | 2.1384 | 2.0787 | -118.3819 | -118.2769 | 3.0448 | -118.4809 | 3.1825 | 3.0976 | 0.052853 | -118.4418 | -118.4203 | 3.2061 | 3.191 | 3.296 | 3.192 | -121.5132 | 3.092 | 3.1311 | 3.1526 | 3.1498 | -118.5281
3592.5938 | 121.6599 | -3.9139 | 117.572 | 1.4211e-13 | -0.042816 | 0.0069553 | 0.023999 | -0.0058416 | -0.0029293 | -0.0022889 | -0.0032857 | 0.026011 | -0.0070868 | 0.022916 | 0.01121 | -0.21414 | -0.048958 | -1.2491 | 0.006344 | -0.017957 | 0.09618 | -3.6941 | -0.012689 | -0.040849 | -0.083823 | -0.098632 | -0.059551 | -0.038035 | -0.15041 | 0.21974 | -117.5657 | 3.6997 | 2.6648 | 2.445 | -117.59 | -117.4758 | 3.7635 | -117.6707 | 3.9012 | 3.8301 | 0.066589 | -117.6316 | -117.6101 | 3.9202 | 3.8959 | 4.0101 | 3.8649 | -121.2662 | 3.8152 | 3.8543 | 3.8758 | 3.873 | -117.7224
3594.375 | 121.6324 | -3.5751 | 118.0435 | 1.4211e-13 | -0.042602 | 0.0071689 | 0.023785 | -0.0060552 | -0.0027157 | -0.0099194 | -0.0030721 | 0.02537 | -0.0073004 | 0.022916 | 0.01121 | -0.17293 | 0.065507 | -1.1438 | 0.015501 | 0.000359 | 0.11449 | -3.5156 | -0.00811 | -0.050007 | -0.092981 | -0.10779 | -0.068708 | -0.028878 | -0.15041 | 0.059568 | -118.028 | 3.4022 | 2.4313 | 2.3717 | -118.0432 | -117.929 | 3.4247 | -118.1513 | 3.567 | 3.4822 | 0.057431 | -118.1122 | -118.0724 | 3.5906 | 3.5755 | 3.6896 | 3.6406 | -121.5591 | 3.4673 | 3.5064 | 3.5463 | 3.5251 | -118.1939
3596.1094 | 121.6553 | -7.7133 | 113.7268 | 1.4211e-13 | -0.044739 | 0.0073825 | 0.025708 | -0.0041322 | 0.0047625 | -0.0099194 | -0.0052085 | 0.028147 | -0.0083686 | 0.023344 | 0.011424 | -0.59414 | -0.67623 | -2.879 | -0.085224 | -0.10496 | 0.004608 | -7.5954 | -0.063054 | -0.10495 | -0.14335 | -0.14899 | -0.12365 | -0.083821 | -0.20078 | 0.11793 | -113.812 | 7.1192 | 4.8343 | 4.7164 | -113.8318 | -113.7222 | 7.5125 | -113.8758 | 7.6503 | 7.57 | 0.057432 | -113.8505 | -113.8106 | 7.6281 | 7.6084 | 7.7179 | 7.0371 | -121.3222 | 7.5643 | 7.5897 | 7.6295 | 7.6084 | -113.9276
3597.8906 | 121.6003 | -3.8727 | 117.7048 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.024212 | -0.0058416 | -0.0020747 | 0.0053411 | -0.0037131 | 0.025583 | -0.0070868 | 0.023344 | 0.010997 | -0.19124 | 0.042614 | -1.2308 | 0.020079 | -0.008799 | 0.10534 | -3.7949 | -0.017267 | -0.059164 | -0.097559 | -0.10321 | -0.06413 | -0.033457 | -0.15041 | 0.0778 | -117.6847 | 3.6814 | 2.6419 | 2.5641 | -117.7136 | -117.5994 | 3.7223 | -117.808 | 3.8554 | 3.7751 | 0.052853 | -117.7689 | -117.7382 | 3.8928 | 3.8639 | 3.978 | 3.9153 | -121.4997 | 3.7695 | 3.8086 | 3.8392 | 3.8135 | -117.8552
3599.6719 | 121.6141 | -4.1885 | 117.3615 | 1.4211e-13 | -0.043243 | 0.0071689 | 0.024426 | -0.0058416 | -0.0018611 | -0.0099194 | -0.0034995 | 0.025583 | -0.007514 | 0.02313 | 0.010997 | -0.24618 | -0.090166 | -1.4002 | -0.007391 | -0.022536 | 0.082444 | -4.1246 | -0.021846 | -0.059164 | -0.088402 | -0.10321 | -0.073287 | -0.038035 | -0.15957 | 0.063975 | -117.3688 | 3.9424 | 2.7883 | 2.7244 | -117.384 | -117.279 | 4.029 | -117.4647 | 4.1667 | 4.1001 | 0.071168 | -117.4347 | -117.3995 | 4.1811 | 4.166 | 4.271 | 4.0984 | -121.486 | 4.0853 | 4.1153 | 4.1505 | 4.1294 | -117.521
3601.4375 | 121.7102 | -4.3121 | 117.2379 | 1.4211e-13 | -0.04303 | 0.0069553 | 0.024212 | -0.0058416 | -0.0016473 | 0.0053411 | -0.0034995 | 0.025797 | -0.0073004 | 0.023344 | 0.011424 | -0.2645 | -0.11306 | -1.446 | -0.007391 | -0.027115 | 0.073287 | -4.2665 | -0.012689 | -0.050007 | -0.092981 | -0.10779 | -0.06413 | -0.047193 | -0.15499 | 0.045624 | -117.2452 | 4.0476 | 2.8661 | 2.8205 | -117.265 | -117.1646 | 4.1571 | -117.3456 | 4.2994 | 4.2192 | 0.06201 | -117.302 | -117.285 | 4.3047 | 4.285 | 4.3854 | 4.1991 | -121.5044 | 4.2043 | 4.248 | 4.2649 | 4.2621 | -117.3928
3603.1562 | 121.6827 | -4.3808 | 117.1143 | 1.4211e-13 | -0.042816 | 0.0065279 | 0.023999 | -0.005628 | -0.0012201 | -0.0099194 | -0.0034995 | 0.026011 | -0.0073004 | 0.023344 | 0.010997 | -0.27366 | -0.13595 | -1.4735 | -0.016548 | -0.036272 | 0.077866 | -4.3627 | -0.017267 | -0.063743 | -0.10214 | -0.11237 | -0.068708 | -0.038035 | -0.15957 | 0.018131 | -117.1308 | 4.1071 | 2.9073 | 2.8892 | -117.1505 | -117.0364 | 4.2212 | -117.2266 | 4.3635 | 4.2787 | 0.057432 | -117.183 | -117.1523 | 4.3643 | 4.3445 | 4.4587 | 4.2448 | -121.4769 | 4.2684 | 4.3121 | 4.3428 | 4.3171 | -117.2738
3604.9375 | 121.6919 | -4.5181 | 116.9724 | 1.4211e-13 | -0.042816 | 0.0069553 | 0.024212 | -0.005628 | -0.0012201 | -0.0099194 | -0.0034995 | 0.025583 | -0.0073004 | 0.023344 | 0.010783 | -0.29655 | -0.15884 | -1.533 | -0.021127 | -0.036272 | 0.06413 | -4.5046 | -0.026425 | -0.059164 | -0.10214 | -0.11237 | -0.06413 | -0.047193 | -0.15957 | 0.013513 | -116.9935 | 4.2216 | 2.9851 | 2.9716 | -117.0086 | -116.9082 | 4.3586 | -117.0847 | 4.4917 | 4.416 | 0.057432 | -117.0365 | -117.0195 | 4.497 | 4.4819 | 4.5823 | 4.3593 | -121.477 | 4.4058 | 4.454 | 4.4709 | 4.459 | -117.1319
3606.6562 | 121.6095 | -6.3858 | 115.0635 | 1.4211e-13 | -0.044739 | 0.0075963 | 0.025281 | -0.004346 | 0.0041215 | 0.0053411 | -0.0043539 | 0.027506 | -0.0079414 | 0.023344 | 0.01121 | -0.48426 | -0.5114 | -2.4074 | -0.062332 | -0.082062 | 0.036658 | -6.6521 | -0.044739 | -0.077479 | -0.12503 | -0.14442 | -0.10076 | -0.074664 | -0.19162 | -0.26633 | -115.1258 | 5.9015 | 3.9784 | 4.2447 | -115.1455 | -115.0268 | 6.1942 | -115.2079 | 6.3411 | 6.2608 | 0.06659 | -115.1642 | -115.1381 | 6.3235 | 6.3037 | 6.4225 | 5.8744 | -121.7156 | 6.2414 | 6.285 | 6.3111 | 6.3083 | -115.2551
3608.4219 | 121.6095 | -8.2214 | 113.1454 | 1.4211e-13 | -0.045594 | 0.0078099 | 0.026349 | -0.003705 | 0.0064719 | 0.012972 | -0.0058495 | 0.029643 | -0.0083686 | 0.023344 | 0.010997 | -0.65824 | -0.81816 | -3.0804 | -0.10354 | -0.12785 | -0.018285 | -8.3463 | -0.07679 | -0.10495 | -0.14793 | -0.16273 | -0.12365 | -0.092979 | -0.20994 | -0.1249 | -113.249 | 7.5632 | 5.141 | 5.2659 | -113.2733 | -113.1637 | 8.0115 | -113.3082 | 8.1446 | 8.0735 | 0.062012 | -113.2691 | -113.2384 | 8.1179 | 8.0936 | 8.2032 | 7.4033 | -121.4918 | 8.0587 | 8.0978 | 8.1285 | 8.1165 | -113.3554
3610.1562 | 121.5179 | -8.3496 | 113.0219 | 1.4211e-13 | -0.045166 | 0.0073825 | 0.025922 | -0.0034912 | 0.0060445 | 0.0053411 | -0.0052085 | 0.028788 | -0.0085822 | 0.023557 | 0.010783 | -0.58956 | -0.68996 | -2.8149 | -0.071489 | -0.10038 | 0.018344 | -7.8884 | -0.072212 | -0.10495 | -0.13877 | -0.16731 | -0.11449 | -0.083821 | -0.20536 | 0.46117 | -113.0933 | 7.76 | 5.5347 | 5.0735 | -113.1222 | -113.0035 | 8.1443 | -113.1892 | 8.2774 | 8.2108 | 0.06659 | -113.1363 | -113.1057 | 8.2781 | 8.2492 | 8.368 | 7.6596 | -120.9103 | 8.1823 | 8.2351 | 8.2658 | 8.2447 | -113.2272
3611.9375 | 121.4355 | -10.8261 | 110.5499 | 1.4211e-13 | -0.046662 | 0.0080237 | 0.026777 | -0.0032776 | 0.0094631 | -0.0022889 | -0.0069177 | 0.030925 | -0.0094368 | 0.02313 | 0.01121 | -0.74523 | -0.97384 | -3.5016 | -0.10812 | -0.13701 | -0.032021 | -9.5826 | -0.095105 | -0.12784 | -0.16166 | -0.18562 | -0.14197 | -0.11129 | -0.22367 | 1.2435 | -110.658 | 10.0809 | 7.3245 | 6.081 | -110.6869 | -110.5819 | 10.6024 | -110.7356 | 10.731 | 10.6644 | 0.062012 | -110.6919 | -110.6612 | 10.718 | 10.6891 | 10.7941 | 9.8523 | -120.1326 | 10.6405 | 10.6841 | 10.7148 | 10.6983 | -110.7736
3613.7188 | 121.4905 | -9.169 | 112.1613 | 1.4211e-13 | -0.046876 | 0.0084509 | 0.027204 | -0.0022094 | 0.012027 | -0.01755 | -0.0073449 | 0.031779 | -0.0094368 | 0.023344 | 0.010783 | -0.78643 | -1.015 | -3.7763 | -0.10812 | -0.12327 | -0.018285 | -10.4618 | -0.10884 | -0.14158 | -0.1754 | -0.1902 | -0.14655 | -0.12503 | -0.23741 | -1.2928 | -112.2694 | 8.3826 | 5.3927 | 6.6855 | -112.2845 | -112.1795 | 8.9316 | -112.3515 | 9.0602 | 8.9936 | 0.062012 | -112.3078 | -112.2863 | 9.0609 | 9.0457 | 9.1507 | 8.154 | -122.623 | 8.9788 | 9.0225 | 9.044 | 9.0274 | -112.3987
3615.4531 | 121.4218 | -9.9976 | 111.3419 | 1.4211e-13 | -0.04773 | 0.0082373 | 0.027845 | -0.001782 | 0.014805 | -0.0099194 | -0.0081995 | 0.032848 | -0.010078 | 0.02313 | 0.010997 | -0.93752 | -1.2943 | -4.3852 | -0.1539 | -0.17364 | -0.06865 | -11.9179 | -0.12716 | -0.1599 | -0.19829 | -0.21767 | -0.17402 | -0.14334 | -0.27404 | -1.9203 | -111.4958 | 9.06 | 5.6123 | 7.5326 | -111.5155 | -111.4105 | 9.7235 | -111.5595 | 9.8704 | 9.7993 | 0.075749 | -111.5159 | -111.4852 | 9.8437 | 9.8239 | 9.9289 | 8.7032 | -123.2598 | 9.7799 | 9.8235 | 9.8542 | 9.8377 | -111.6159
3617.2344 | 121.3348 | -11.4532 | 109.8404 | 1.4211e-13 | -0.047517 | 0.0082373 | 0.027845 | -0.001782 | 0.014164 | -0.0022889 | -0.0081995 | 0.033275 | -0.010078 | 0.02313 | 0.010997 | -0.88258 | -1.1936 | -4.193 | -0.14017 | -0.15075 | -0.054914 | -11.5424 | -0.12258 | -0.15532 | -0.19371 | -0.20852 | -0.17402 | -0.14334 | -0.25572 | -0.089174 | -109.9806 | 10.5707 | 7.2603 | 7.3495 | -109.9911 | -109.8953 | 11.1975 | -110.0489 | 11.3307 | 11.2595 | 0.062013 | -110.0144 | -109.9837 | 11.3131 | 11.3025 | 11.3983 | 10.2596 | -121.3828 | 11.2447 | 11.2792 | 11.3099 | 11.2979 | -110.0961
3619.0156 | 121.4401 | -12.9227 | 108.2153 | 1.4211e-13 | -0.048371 | 0.0086647 | 0.028486 | -0.0013546 | 0.016514 | -0.01755 | -0.0088403 | 0.034557 | -0.010078 | 0.023557 | 0.01121 | -1.0062 | -1.4271 | -4.6142 | -0.17679 | -0.19653 | -0.082386 | -12.6643 | -0.14089 | -0.16905 | -0.21203 | -0.23141 | -0.19233 | -0.15708 | -0.27862 | 0.25841 | -108.3921 | 11.9165 | 8.3085 | 8.0501 | -108.4119 | -108.2977 | 12.644 | -108.4467 | 12.7818 | 12.7106 | 0.066592 | -108.4077 | -108.3724 | 12.7459 | 12.7261 | 12.8403 | 11.4956 | -120.8796 | 12.6913 | 12.7303 | 12.7656 | 12.7536 | -108.494
3620.7344 | 121.3211 | -13.8519 | 107.3135 | 1.4211e-13 | -0.04944 | 0.0086647 | 0.0287 | -0.00092737 | 0.019078 | -0.0099194 | -0.0099085 | 0.035625 | -0.010719 | 0.023344 | 0.010997 | -1.1023 | -1.5507 | -5.0583 | -0.18595 | -0.21027 | -0.10528 | -13.9372 | -0.15921 | -0.18737 | -0.23034 | -0.24514 | -0.21064 | -0.17539 | -0.29236 | -0.08527 | -107.4995 | 12.7496 | 8.7937 | 8.8789 | -107.5238 | -107.4188 | 13.5596 | -107.5587 | 13.6927 | 13.6216 | 0.062014 | -107.5242 | -107.4889 | 13.666 | 13.6417 | 13.7467 | 12.3012 | -121.2507 | 13.6068 | 13.6413 | 13.6765 | 13.6646 | -107.6059
3622.5156 | 121.3211 | -16.246 | 104.7775 | 1.4211e-13 | -0.050508 | 0.0090921 | 0.029982 | 0.00056843 | 0.024419 | -0.0099194 | -0.01119 | 0.037548 | -0.011573 | 0.023344 | 0.010783 | -1.3175 | -1.9582 | -5.9648 | -0.2592 | -0.27896 | -0.17396 | -16.1946 | -0.19584 | -0.224 | -0.26239 | -0.27719 | -0.23354 | -0.20744 | -0.32899 | 0.051425 | -105.0367 | 14.9285 | 10.2813 | 10.2299 | -105.0565 | -104.9515 | 15.917 | -105.0547 | 16.0502 | 15.9836 | 0.066593 | -105.0111 | -104.985 | 15.9868 | 15.9671 | 16.0721 | 14.2878 | -120.9721 | 15.9688 | 16.0125 | 16.0386 | 16.022 | -105.1065
3624.3125 | 121.2479 | -11.499 | 109.7351 | 1.4211e-13 | -0.048371 | 0.0084509 | 0.027631 | -0.0015684 | 0.015446 | -0.01755 | -0.0081995 | 0.033489 | -0.010505 | 0.023557 | 0.011424 | -0.90547 | -1.244 | -4.2021 | -0.14932 | -0.16906 | -0.054914 | -11.9042 | -0.13173 | -0.16448 | -0.20287 | -0.22683 | -0.1786 | -0.14792 | -0.26946 | -0.40513 | -109.8844 | 10.5935 | 7.2969 | 7.702 | -109.9042 | -109.79 | 11.2296 | -109.9619 | 11.3673 | 11.2962 | 0.066592 | -109.9137 | -109.883 | 11.3497 | 11.33 | 11.4441 | 10.255 | -121.6393 | 11.2722 | 11.3204 | 11.3511 | 11.3345 | -110.0046
3626.0312 | 121.3989 | -9.3704 | 111.795 | 1.4211e-13 | -0.046876 | 0.0080237 | 0.026777 | -0.0026366 | 0.010318 | 0.0053411 | -0.0067039 | 0.030925 | -0.0092232 | 0.023557 | 0.010783 | -0.67197 | -0.85937 | -3.1949 | -0.085224 | -0.11411 | 2.9e-05 | -9.285 | -0.095105 | -0.12327 | -0.16624 | -0.17647 | -0.14655 | -0.10671 | -0.22367 | 0.085411 | -111.8803 | 8.6984 | 6.1755 | 6.0901 | -111.9092 | -111.795 | 9.1467 | -111.9715 | 9.2753 | 9.2042 | 0.057433 | -111.9416 | -111.9018 | 9.2852 | 9.2563 | 9.3705 | 8.5111 | -121.0801 | 9.194 | 9.2239 | 9.2637 | 9.2472 | -112.0187
3627.8125 | 121.1929 | -15.6143 | 105.4871 | 1.4211e-13 | -0.049653 | 0.0090921 | 0.029127 | 0.00014103 | 0.021642 | -0.0022889 | -0.010549 | 0.03648 | -0.011573 | 0.023344 | 0.010997 | -1.2168 | -1.8209 | -5.2917 | -0.25005 | -0.27896 | -0.17396 | -14.8026 | -0.16379 | -0.19653 | -0.23492 | -0.2543 | -0.2198 | -0.17539 | -0.31067 | 0.8117 | -105.7371 | 14.3975 | 10.3226 | 9.5109 | -105.766 | -105.661 | 15.3036 | -105.7414 | 15.4505 | 15.3794 | 0.07575 | -105.7069 | -105.6625 | 15.3643 | 15.3354 | 15.4404 | 13.7934 | -120.2897 | 15.36 | 15.3945 | 15.4389 | 15.4178 | -105.7977
3629.5938 | 121.051 | -17.514 | 103.3997 | 1.4211e-13 | -0.05179 | 0.0097331 | 0.030623 | 0.0016366 | 0.028479 | -0.0099194 | -0.012472 | 0.039898 | -0.012214 | 0.02313 | 0.010783 | -1.4915 | -2.3291 | -6.4455 | -0.33703 | -0.36595 | -0.24721 | -17.7881 | -0.21415 | -0.24231 | -0.28529 | -0.30009 | -0.26101 | -0.23492 | -0.34272 | -0.27404 | -103.7367 | 16.0225 | 11.0686 | 11.3426 | -103.7656 | -103.6469 | 17.1713 | -103.6997 | 17.2999 | 17.2288 | 0.057436 | -103.6607 | -103.6346 | 17.177 | 17.1481 | 17.2668 | 15.1849 | -121.1877 | 17.214 | 17.253 | 17.2791 | 17.2717 | -103.7424
3631.375 | 121.0098 | -23.6252 | 97.2107 | 1.4211e-13 | -0.054141 | 0.010374 | 0.032119 | 0.0031322 | 0.03788 | 0.012972 | -0.015463 | 0.044172 | -0.013496 | 0.023557 | 0.010997 | -1.8257 | -2.9289 | -7.8098 | -0.43776 | -0.45295 | -0.33879 | -21.9228 | -0.28283 | -0.30184 | -0.34481 | -0.35961 | -0.32053 | -0.28986 | -0.40683 | 1.7023 | -97.6485 | 21.7995 | 15.8154 | 14.113 | -97.6636 | -97.5495 | 23.2184 | -97.5703 | 23.3424 | 23.2804 | 0.062016 | -97.5312 | -97.5006 | 23.1874 | 23.1722 | 23.2864 | 20.6963 | -119.1335 | 23.2656 | 23.3047 | 23.3353 | 23.3233 | -97.6175
3633.1094 | 120.9549 | -21.7667 | 99.0555 | 1.4211e-13 | -0.053927 | 0.01016 | 0.031905 | 0.0029186 | 0.037026 | -0.0022889 | -0.014395 | 0.043744 | -0.013496 | 0.023344 | 0.010783 | -1.7662 | -2.9152 | -7.7228 | -0.42402 | -0.44838 | -0.34337 | -21.2681 | -0.2691 | -0.29268 | -0.33107 | -0.35503 | -0.31137 | -0.28528 | -0.39767 | 0.49861 | -99.4795 | 20.0005 | 14.0439 | 13.5452 | -99.5039 | -99.3988 | 21.369 | -99.4105 | 21.4976 | 21.4356 | 0.066594 | -99.3669 | -99.3408 | 21.3426 | 21.3183 | 21.4233 | 18.8515 | -120.3235 | 21.4116 | 21.4553 | 21.4814 | 21.474 | -99.4531
3634.8906 | 120.9366 | -23.1583 | 97.5128 | 1.4211e-13 | -0.054995 | 0.010801 | 0.032546 | 0.0037732 | 0.040872 | -0.0022889 | -0.014608 | 0.043317 | -0.013069 | 0.02313 | 0.010997 | -1.9036 | -3.1533 | -8.2173 | -0.46523 | -0.48959 | -0.38 | -22.8066 | -0.25994 | -0.2881 | -0.31734 | -0.34129 | -0.29764 | -0.2807 | -0.38851 | 0.35169 | -97.978 | 21.2547 | 14.941 | 14.5893 | -98.0024 | -97.8928 | 22.7698 | -97.8541 | 22.8983 | 22.8409 | 0.071173 | -97.8105 | -97.7935 | 22.693 | 22.6687 | 22.7783 | 20.005 | -120.3194 | 22.817 | 22.8606 | 22.8776 | 22.8702 | -97.9013
3636.6719 | 120.7535 | -22.2839 | 98.2361 | 1.4211e-13 | -0.056918 | 0.011015 | 0.033828 | 0.0054826 | 0.048136 | -0.0099194 | -0.015249 | 0.044813 | -0.014137 | 0.02313 | 0.011424 | -2.1691 | -3.6569 | -9.1467 | -0.56138 | -0.58116 | -0.47157 | -25.8973 | -0.29199 | -0.31099 | -0.34481 | -0.35961 | -0.32969 | -0.29444 | -0.41598 | -3.6134 | -98.7975 | 20.1148 | 13.1373 | 16.7507 | -98.8172 | -98.7077 | 21.868 | -98.5957 | 21.9919 | 21.9391 | 0.071174 | -98.5658 | -98.5305 | 21.7226 | 21.7028 | 21.8124 | 18.627 | -124.1334 | 21.9243 | 21.9542 | 21.9895 | 21.9729 | -98.6521
3638.375 | 120.7443 | -20.7825 | 99.678 | 1.4211e-13 | -0.054354 | 0.0099467 | 0.032119 | 0.0035596 | 0.039376 | -0.0022889 | -0.013327 | 0.040753 | -0.012428 | 0.023344 | 0.010997 | -1.8303 | -3.0388 | -7.3062 | -0.46523 | -0.49417 | -0.38 | -21.8771 | -0.22789 | -0.25605 | -0.29902 | -0.31382 | -0.27475 | -0.23949 | -0.36104 | -1.0946 | -100.1433 | 18.9522 | 13.4763 | 14.5709 | -100.1722 | -100.058 | 20.4214 | -99.9919 | 20.5546 | 20.4834 | 0.062015 | -99.9528 | -99.9175 | 20.3172 | 20.2883 | 20.4025 | 17.7437 | -121.5551 | 20.4687 | 20.5077 | 20.543 | 20.5264 | -100.0391
3640.1562 | 120.5658 | -24.559 | 95.9427 | 1.4211e-13 | -0.054568 | 0.01016 | 0.032119 | 0.003987 | 0.039803 | -0.01755 | -0.013327 | 0.040753 | -0.012214 | 0.022916 | 0.010997 | -1.7433 | -2.787 | -7.0269 | -0.41029 | -0.43922 | -0.32047 | -21.8084 | -0.23247 | -0.24689 | -0.28529 | -0.31382 | -0.26101 | -0.24407 | -0.36104 | 2.7507 | -96.353 | 22.8157 | 17.5321 | 14.7815 | -96.3819 | -96.2632 | 24.198 | -96.2565 | 24.3266 | 24.2737 | 0.075751 | -96.2037 | -96.1868 | 24.1487 | 24.1198 | 24.2385 | 21.7721 | -117.7511 | 24.2452 | 24.298 | 24.3149 | 24.3121 | -96.3037
3641.9375 | 120.4056 | -21.048 | 99.1974 | 1.4211e-13 | -0.0535 | 0.01016 | 0.031264 | 0.0031322 | 0.036812 | -0.0099194 | -0.012258 | 0.039471 | -0.012214 | 0.022916 | 0.010997 | -1.7067 | -2.8831 | -6.8209 | -0.44234 | -0.47127 | -0.3571 | -20.4988 | -0.20499 | -0.23316 | -0.27613 | -0.29551 | -0.25643 | -0.22576 | -0.34272 | 0.54918 | -99.6397 | 19.3413 | 14.2271 | 13.6779 | -99.6687 | -99.5545 | 20.7053 | -99.4929 | 20.843 | 20.7718 | 0.066594 | -99.4538 | -99.4231 | 20.6056 | 20.5767 | 20.6909 | 18.1649 | -119.6962 | 20.7525 | 20.7915 | 20.8222 | 20.8148 | -99.5401
3643.7188 | 120.0119 | -24.4171 | 95.5307 | 1.4211e-13 | -0.055423 | 0.010801 | 0.03276 | 0.0052688 | 0.046213 | -0.0099194 | -0.014181 | 0.043531 | -0.012855 | 0.022916 | 0.010997 | -2.0318 | -3.5058 | -7.9975 | -0.53391 | -0.56743 | -0.45783 | -24.3497 | -0.2462 | -0.27436 | -0.30818 | -0.33671 | -0.29306 | -0.26697 | -0.37935 | 0.067441 | -96.0646 | 22.3854 | 16.4196 | 16.3522 | -96.0981 | -95.9885 | 24.0378 | -95.8674 | 24.1709 | 24.1089 | 0.071173 | -95.8238 | -95.7977 | 23.8832 | 23.8497 | 23.9593 | 20.9113 | -119.8804 | 24.0804 | 24.1241 | 24.1501 | 24.1428 | -95.9101
3645.5 | 121.0602 | -0.11444 | 120.8954 | 1.4211e-13 | -0.04132 | 0.0069553 | 0.022076 | -0.0081918 | -0.010621 | 0.012972 | -0.0020039 | 0.022378 | -0.0049502 | 0.023344 | 0.01121 | 0.042253 | 0.0243 | -0.031301 | 0.024657 | 0.009517 | 0.10534 | -0.11342 | 0.033099 | -0.00422 | -0.042615 | -0.066582 | -0.013765 | 0.007751 | -0.11378 | 0.001016 | -120.8707 | 0.15669 | 0.08314 | 0.082124 | -120.8859 | -120.79 | 0.000659 | -120.962 | 0.14754 | 0.071826 | 0.071167 | -120.9092 | -120.8876 | 0.1391 | 0.12396 | 0.21978 | 0.13874 | -121.0088 | 0.047859 | 0.10068 | 0.12219 | 0.11022 | -121.0092
3647.2188 | 121.0693 | -0.15106 | 121.0602 | 1.4211e-13 | -0.04132 | 0.0069553 | 0.022076 | -0.0075508 | -0.010194 | -0.0022889 | -0.0015767 | 0.022378 | -0.0053776 | 0.023557 | 0.010783 | 0.037675 | 0.0243 | -0.026723 | 0.024657 | -0.00422 | 0.10534 | -0.10885 | 0.042256 | 0.004938 | -0.042615 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.042215 | -121.0355 | 0.18874 | 0.12434 | 0.082124 | -121.0644 | -120.9548 | 0.046438 | -121.1084 | 0.19332 | 0.10845 | 0.062009 | -121.0694 | -121.0433 | 0.17572 | 0.14684 | 0.2564 | 0.17536 | -121.169 | 0.10279 | 0.14188 | 0.16797 | 0.156 | -121.1648
3649 | 121.2753 | -0.11902 | 121.0373 | 1.4211e-13 | -0.041534 | 0.0067415 | 0.022076 | -0.0075508 | -0.010194 | -0.0099194 | -0.0015767 | 0.022806 | -0.0055912 | 0.023557 | 0.010997 | 0.046831 | 0.0243 | -0.031301 | 0.020079 | 0.004938 | 0.10992 | -0.10885 | 0.037677 | 0.004938 | -0.051772 | -0.048268 | -0.013765 | 0.016908 | -0.10004 | 0.010172 | -121.0172 | 0.16585 | 0.087718 | 0.077546 | -121.0324 | -120.9274 | 0.018974 | -121.0856 | 0.1567 | 0.067247 | 0.048273 | -121.0511 | -121.0204 | 0.1391 | 0.12396 | 0.22893 | 0.14332 | -121.1461 | 0.070751 | 0.10525 | 0.13593 | 0.12396 | -121.1373
3650.7812 | 121.257 | -0.12817 | 121.1105 | 1.4211e-13 | -0.04132 | 0.0071689 | 0.022076 | -0.0077646 | -0.010621 | -0.0099194 | -0.0017903 | 0.022592 | -0.0058048 | 0.022916 | 0.010783 | 0.046831 | 0.019721 | -0.022144 | 0.024657 | 0.000359 | 0.10992 | -0.10885 | 0.046835 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.10004 | 0.019327 | -121.0859 | 0.17501 | 0.10603 | 0.086703 | -121.1102 | -121.0006 | 0.028129 | -121.1588 | 0.17501 | 0.085559 | 0.05743 | -121.1197 | -121.089 | 0.15283 | 0.12853 | 0.23809 | 0.14789 | -121.2194 | 0.079906 | 0.11899 | 0.14966 | 0.12853 | -121.2106
3652.5625 | 121.2112 | -0.14648 | 121.138 | 1.4211e-13 | -0.041534 | 0.0067415 | 0.022289 | -0.0077646 | -0.010621 | -0.0099194 | -0.0015767 | 0.023233 | -0.0053776 | 0.023771 | 0.010997 | 0.037675 | 0.0243 | -0.026723 | 0.020079 | 0.004938 | 0.10076 | -0.10885 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.013765 | 0.016908 | -0.095467 | 0.037637 | -121.1179 | 0.18416 | 0.11976 | 0.082124 | -121.1331 | -121.0372 | 0.051017 | -121.1863 | 0.18874 | 0.10387 | 0.052852 | -121.1518 | -121.1211 | 0.16656 | 0.15142 | 0.24724 | 0.17078 | -121.2468 | 0.098216 | 0.13272 | 0.16339 | 0.14684 | -121.2335
3654.3438 | 121.3165 | -0.11902 | 121.1609 | 1.4211e-13 | -0.041534 | 0.0069553 | 0.022289 | -0.0079782 | -0.010194 | -0.0022889 | -0.0015767 | 0.022592 | -0.0055912 | 0.023344 | 0.010783 | 0.042253 | 0.019721 | -0.026723 | 0.020079 | -0.00422 | 0.11449 | -0.11342 | 0.042256 | 0.000359 | -0.047194 | -0.062004 | -0.009187 | 0.012329 | -0.10462 | 0.005594 | -121.1408 | 0.16127 | 0.092296 | 0.086702 | -121.1651 | -121.0464 | 0.014395 | -121.2229 | 0.16128 | 0.071825 | 0.05743 | -121.1701 | -121.1486 | 0.1391 | 0.1148 | 0.23351 | 0.13874 | -121.2743 | 0.057015 | 0.10983 | 0.13135 | 0.11938 | -121.2655
3656.0781 | 121.3394 | -0.1236 | 121.1838 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.022289 | -0.0077646 | -0.010194 | -0.0099194 | -0.0017903 | 0.023233 | -0.0058048 | 0.023344 | 0.011424 | 0.037675 | 0.019721 | -0.017566 | 0.024657 | 0.000359 | 0.10534 | -0.11342 | 0.042256 | -0.008798 | -0.042615 | -0.048268 | -0.013765 | 0.012329 | -0.10004 | 0.010171 | -121.1591 | 0.16127 | 0.10603 | 0.095859 | -121.1834 | -121.0784 | 0.023551 | -121.232 | 0.16585 | 0.080981 | 0.05743 | -121.1975 | -121.1714 | 0.14825 | 0.12395 | 0.22893 | 0.14332 | -121.2972 | 0.075328 | 0.10983 | 0.13592 | 0.1148 | -121.2838
3657.875 | 121.3715 | -0.1236 | 121.1838 | 1.4211e-13 | -0.041534 | 0.0067415 | 0.022076 | -0.0075508 | -0.010194 | -0.0099194 | -0.0017903 | 0.022592 | -0.0058048 | 0.023344 | 0.010783 | 0.037675 | 0.019721 | -0.022144 | 0.020079 | 0.000359 | 0.10992 | -0.11342 | 0.051413 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.021486 | -0.10462 | 0.010171 | -121.1637 | 0.16127 | 0.10145 | 0.091281 | -121.1834 | -121.0739 | 0.018972 | -121.2412 | 0.17501 | 0.080981 | 0.062009 | -121.1975 | -121.1623 | 0.14367 | 0.12395 | 0.23351 | 0.14332 | -121.2972 | 0.066171 | 0.10983 | 0.14508 | 0.12395 | -121.2884
3659.5938 | 121.4355 | -0.10986 | 121.2112 | 1.4211e-13 | -0.04132 | 0.0069553 | 0.021862 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.023019 | -0.0058048 | 0.023344 | 0.01121 | 0.042253 | 0.005985 | -0.017566 | 0.020079 | -0.00422 | 0.10992 | -0.12258 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.004608 | 0.021486 | -0.10004 | -0.01272 | -121.1912 | 0.15212 | 0.092297 | 0.10502 | -121.2155 | -121.1013 | 0.009818 | -121.2641 | 0.15212 | 0.067248 | 0.05743 | -121.2159 | -121.1898 | 0.12994 | 0.10564 | 0.21978 | 0.11585 | -121.3338 | 0.057016 | 0.10526 | 0.13135 | 0.11022 | -121.3113
3661.3594 | 121.4264 | -0.10986 | 121.1838 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022289 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.023233 | -0.0060184 | 0.023557 | 0.010997 | 0.037675 | 0.0243 | -0.026723 | 0.024657 | 0.000359 | 0.10076 | -0.118 | 0.042256 | 0.000359 | -0.038036 | -0.04369 | -0.009187 | 0.016908 | -0.10004 | -0.008141 | -121.1591 | 0.14754 | 0.08314 | 0.091281 | -121.1834 | -121.083 | 0.009818 | -121.2275 | 0.15212 | 0.071827 | 0.062009 | -121.193 | -121.1669 | 0.13452 | 0.11022 | 0.21062 | 0.13416 | -121.3018 | 0.066173 | 0.10068 | 0.12677 | 0.11022 | -121.2838
3663.1406 | 121.3348 | -0.17395 | 121.2524 | 1.4211e-13 | -0.041748 | 0.0073825 | 0.022503 | -0.0079782 | -0.010194 | -0.0099194 | -0.0015767 | 0.022806 | -0.0058048 | 0.023344 | 0.01121 | 0.046831 | 0.019721 | -0.022144 | 0.024657 | 0.000359 | 0.10992 | -0.11342 | 0.046835 | 0.004938 | -0.042615 | -0.062004 | -0.022922 | 0.016908 | -0.1092 | 0.060525 | -121.2278 | 0.22078 | 0.15181 | 0.091281 | -121.2521 | -121.1425 | 0.064747 | -121.3144 | 0.22079 | 0.13133 | 0.066588 | -121.2754 | -121.2355 | 0.19861 | 0.17431 | 0.28387 | 0.19367 | -121.3659 | 0.11195 | 0.15103 | 0.19086 | 0.17889 | -121.3616
3664.8594 | 121.3806 | -0.16937 | 121.2616 | 1.4211e-13 | -0.041534 | 0.0069553 | 0.022289 | -0.0081918 | -0.010408 | 0.0053411 | -0.0020039 | 0.022806 | -0.0062322 | 0.023557 | 0.010783 | 0.042253 | 0.0243 | -0.017566 | 0.024657 | 0.004938 | 0.10992 | -0.12258 | 0.046835 | 0.000359 | -0.033458 | -0.052847 | -0.009187 | 0.021486 | -0.10462 | 0.04679 | -121.2369 | 0.21163 | 0.15181 | 0.10502 | -121.2567 | -121.1517 | 0.064749 | -121.3144 | 0.21621 | 0.13592 | 0.071166 | -121.2708 | -121.2401 | 0.19403 | 0.17431 | 0.27929 | 0.19367 | -121.3842 | 0.11653 | 0.16019 | 0.19086 | 0.16973 | -121.3662
3666.6406 | 121.463 | -0.10986 | 121.2616 | 1.4211e-13 | -0.041748 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0017903 | 0.023019 | -0.0058048 | 0.023771 | 0.010997 | 0.042253 | 0.028878 | -0.022144 | 0.024657 | 0.000359 | 0.10534 | -0.118 | 0.046835 | 0.000359 | -0.038036 | -0.048268 | -0.004608 | 0.021486 | -0.10004 | -0.008141 | -121.2369 | 0.15212 | 0.087719 | 0.09586 | -121.2612 | -121.1563 | 0.009818 | -121.3099 | 0.1567 | 0.071827 | 0.062009 | -121.2662 | -121.2401 | 0.13452 | 0.11022 | 0.2152 | 0.13874 | -121.3796 | 0.061595 | 0.10526 | 0.13135 | 0.11022 | -121.3616
3668.4062 | 121.4401 | -0.14648 | 121.2799 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0017903 | 0.022592 | -0.0053776 | 0.023557 | 0.010783 | 0.042253 | 0.019721 | -0.026723 | 0.020079 | 0.000359 | 0.10534 | -0.12258 | 0.042256 | -0.00422 | -0.038036 | -0.048268 | -0.018344 | 0.016908 | -0.10004 | 0.023901 | -121.2598 | 0.18874 | 0.11976 | 0.09586 | -121.2795 | -121.1746 | 0.046439 | -121.3282 | 0.18874 | 0.10845 | 0.062009 | -121.2983 | -121.263 | 0.16656 | 0.14684 | 0.25182 | 0.1662 | -121.4025 | 0.098216 | 0.12814 | 0.16339 | 0.14226 | -121.38
3670.1875 | 121.4996 | -0.12817 | 121.2753 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.022076 | -0.0077646 | -0.010194 | -0.0022889 | -0.0017903 | 0.023019 | -0.0060184 | 0.023557 | 0.010997 | 0.037675 | 0.019721 | -0.022144 | 0.024657 | 0.000359 | 0.10992 | -0.12258 | 0.037677 | 0.000359 | -0.038036 | -0.052847 | -0.004608 | 0.016908 | -0.10004 | 0.005591 | -121.2507 | 0.16585 | 0.10603 | 0.10044 | -121.275 | -121.1654 | 0.028129 | -121.3282 | 0.16585 | 0.090138 | 0.062009 | -121.2799 | -121.2584 | 0.15283 | 0.12853 | 0.23809 | 0.14789 | -121.3979 | 0.075327 | 0.12357 | 0.14508 | 0.12853 | -121.3754
3671.9844 | 121.5408 | -0.10529 | 121.2982 | 1.4211e-13 | -0.041534 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.01755 | -0.0020039 | 0.022806 | -0.0062322 | 0.023557 | 0.010997 | 0.042253 | 0.019721 | -0.017566 | 0.020079 | 0.000359 | 0.10534 | -0.12258 | 0.033099 | 0.000359 | -0.042615 | -0.057425 | -0.013765 | 0.021486 | -0.10462 | -0.017297 | -121.2781 | 0.14754 | 0.08772 | 0.10502 | -121.2979 | -121.1929 | 0.000662 | -121.3556 | 0.13839 | 0.062671 | 0.062009 | -121.312 | -121.2767 | 0.12537 | 0.10565 | 0.21062 | 0.12501 | -121.4208 | 0.047861 | 0.091521 | 0.12677 | 0.10565 | -121.4028
3673.7031 | 121.4127 | -0.16022 | 121.3486 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.022289 | -0.0081918 | -0.010408 | -0.01755 | -0.0017903 | 0.022806 | -0.0060184 | 0.023344 | 0.010783 | 0.046831 | 0.010564 | -0.026723 | 0.024657 | 0.000359 | 0.10534 | -0.12716 | 0.042256 | 0.009516 | -0.033458 | -0.052847 | -0.018344 | 0.021486 | -0.11378 | 0.033055 | -121.3239 | 0.20705 | 0.13349 | 0.10044 | -121.3482 | -121.2432 | 0.046435 | -121.4014 | 0.20247 | 0.12676 | 0.080324 | -121.3669 | -121.3271 | 0.18487 | 0.16058 | 0.26555 | 0.17078 | -121.4757 | 0.10737 | 0.14187 | 0.1817 | 0.16973 | -121.4624
3675.4688 | 121.4813 | -0.14191 | 121.3669 | 1.4211e-13 | -0.041961 | 0.0071689 | 0.021862 | -0.0081918 | -0.0099803 | -0.0022889 | -0.0017903 | 0.023019 | -0.0058048 | 0.023557 | 0.010997 | 0.046831 | 0.010564 | -0.017566 | 0.024657 | 0.004938 | 0.10534 | -0.118 | 0.042256 | 0.004938 | -0.038036 | -0.048268 | -2.9e-05 | 0.021486 | -0.10462 | 0.023903 | -121.3422 | 0.18874 | 0.12434 | 0.10044 | -121.3619 | -121.2615 | 0.037283 | -121.4151 | 0.18416 | 0.10387 | 0.066588 | -121.3669 | -121.3454 | 0.16656 | 0.14685 | 0.24724 | 0.15247 | -121.4849 | 0.093639 | 0.14188 | 0.16339 | 0.14685 | -121.4715
3677.25 | 121.5958 | -0.09613 | 121.3303 | 1.4211e-13 | -0.041748 | 0.0071689 | 0.022289 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.023019 | -0.0058048 | 0.023771 | 0.010997 | 0.042253 | 0.0243 | -0.017566 | 0.024657 | 0.000359 | 0.10992 | -0.12258 | 0.042256 | 0.000359 | -0.038036 | -0.057425 | -0.004608 | 0.016908 | -0.10462 | -0.026453 | -121.3056 | 0.13838 | 0.078564 | 0.10502 | -121.3299 | -121.2203 | -0.008494 | -121.3877 | 0.13839 | 0.058094 | 0.066588 | -121.3349 | -121.3134 | 0.12079 | 0.096489 | 0.20605 | 0.12043 | -121.4528 | 0.038705 | 0.091522 | 0.11304 | 0.096489 | -121.4349
3678.9688 | 121.582 | -0.10986 | 121.3165 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022289 | -0.0079782 | -0.0099803 | -0.01755 | -0.0020039 | 0.023019 | -0.0058048 | 0.023557 | 0.010997 | 0.046831 | 0.019721 | -0.022144 | 0.024657 | 0.000359 | 0.10534 | -0.11342 | 0.037677 | 0.000359 | -0.038036 | -0.052847 | -0.004608 | 0.026065 | -0.10462 | -0.003562 | -121.2919 | 0.15669 | 0.087719 | 0.091281 | -121.3162 | -121.2112 | 0.005239 | -121.3694 | 0.14754 | 0.071827 | 0.066588 | -121.3211 | -121.2905 | 0.13452 | 0.11022 | 0.2152 | 0.12958 | -121.43 | 0.057016 | 0.10526 | 0.13593 | 0.11022 | -121.4212
3680.75 | 121.5866 | -0.13733 | 121.3531 | 1.4211e-13 | -0.041961 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022378 | -0.0058048 | 0.023557 | 0.011424 | 0.042253 | 0.0243 | -0.026723 | 0.024657 | 0.004938 | 0.10992 | -0.13174 | 0.046835 | -0.00422 | -0.042615 | -0.052847 | -0.009187 | 0.016908 | -0.1092 | 0.005588 | -121.3285 | 0.17958 | 0.11061 | 0.10502 | -121.3482 | -121.2432 | 0.028126 | -121.406 | 0.18416 | 0.094714 | 0.066588 | -121.3623 | -121.3362 | 0.16199 | 0.14227 | 0.24724 | 0.16163 | -121.4849 | 0.084482 | 0.12814 | 0.15424 | 0.13311 | -121.4624
3682.5312 | 121.6141 | -0.10529 | 121.3577 | 1.4211e-13 | -0.041748 | 0.0065279 | 0.022076 | -0.0077646 | -0.0099803 | -0.0099194 | -0.0020039 | 0.023233 | -0.0058048 | 0.023771 | 0.01121 | 0.037675 | 0.015142 | -0.022144 | 0.024657 | 0.000359 | 0.10534 | -0.13174 | 0.042256 | -0.00422 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.10004 | -0.026455 | -121.3331 | 0.14296 | 0.083142 | 0.1096 | -121.3574 | -121.2524 | 0.005241 | -121.406 | 0.14754 | 0.062671 | 0.05743 | -121.3669 | -121.3362 | 0.12994 | 0.10565 | 0.21062 | 0.12043 | -121.4895 | 0.057018 | 0.096099 | 0.12677 | 0.10107 | -121.4578
3684.25 | 121.6003 | -0.13733 | 121.3623 | 1.4211e-13 | -0.041534 | 0.0071689 | 0.022289 | -0.0077646 | -0.010194 | -0.0022889 | -0.0020039 | 0.023019 | -0.0062322 | 0.023344 | 0.010569 | 0.037675 | 0.010564 | -0.017566 | 0.024657 | -0.00422 | 0.11449 | -0.12716 | 0.042256 | -0.008798 | -0.042615 | -0.052847 | -0.009187 | 0.016908 | -0.10462 | 0.010167 | -121.3376 | 0.175 | 0.11976 | 0.1096 | -121.3665 | -121.2478 | 0.032705 | -121.4152 | 0.17958 | 0.094714 | 0.062009 | -121.3715 | -121.3454 | 0.16199 | 0.13311 | 0.25182 | 0.14789 | -121.4895 | 0.084482 | 0.12814 | 0.15424 | 0.12853 | -121.4669
3686.0156 | 121.5912 | -0.14191 | 121.3989 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.022076 | -0.0075508 | -0.010194 | -0.02518 | -0.0022175 | 0.023233 | -0.0064458 | 0.023771 | 0.010569 | 0.042253 | 0.015142 | -0.026723 | 0.024657 | 0.000359 | 0.10992 | -0.12716 | 0.046835 | 0.000359 | -0.042615 | -0.048268 | -0.004608 | 0.021486 | -0.1092 | 0.014745 | -121.3743 | 0.18416 | 0.11518 | 0.10044 | -121.3986 | -121.289 | 0.032704 | -121.4472 | 0.18874 | 0.099292 | 0.066588 | -121.4035 | -121.3774 | 0.16656 | 0.14227 | 0.25182 | 0.15705 | -121.5261 | 0.093639 | 0.1373 | 0.16339 | 0.14227 | -121.5081
3687.7969 | 121.5179 | -0.17853 | 121.4172 | 1.4211e-13 | -0.041748 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.023019 | -0.0060184 | 0.023344 | 0.010569 | 0.042253 | 0.015142 | -0.022144 | 0.024657 | 0.000359 | 0.10992 | -0.12716 | 0.037677 | 0.000359 | -0.038036 | -0.048268 | -0.004608 | 0.021486 | -0.10462 | 0.051366 | -121.3926 | 0.22078 | 0.15638 | 0.10502 | -121.4169 | -121.3073 | 0.073904 | -121.4655 | 0.2162 | 0.14049 | 0.066588 | -121.4218 | -121.3958 | 0.20319 | 0.17889 | 0.28844 | 0.19367 | -121.5444 | 0.13026 | 0.17392 | 0.20001 | 0.17889 | -121.5219
3689.5 | 121.6507 | -0.10986 | 121.376 | 1.4211e-13 | -0.041961 | 0.0071689 | 0.021862 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.023019 | -0.0060184 | 0.023344 | 0.01121 | 0.042253 | 0.019721 | -0.026723 | 0.024657 | -0.00422 | 0.10534 | -0.13174 | 0.042256 | -0.00422 | -0.038036 | -0.052847 | -0.009187 | 0.021486 | -0.10462 | -0.021878 | -121.3514 | 0.15212 | 0.08314 | 0.10502 | -121.3803 | -121.2707 | 0.005239 | -121.4289 | 0.15212 | 0.071827 | 0.066588 | -121.3852 | -121.3546 | 0.13452 | 0.10564 | 0.2152 | 0.12958 | -121.5078 | 0.057016 | 0.10068 | 0.13135 | 0.10564 | -121.4807
3691.2812 | 121.5546 | -0.15564 | 121.4401 | 1.4211e-13 | -0.041961 | 0.0067415 | 0.022076 | -0.0081918 | -0.010194 | -0.0099194 | -0.0017903 | 0.023019 | -0.0058048 | 0.023557 | 0.010997 | 0.042253 | 0.019721 | -0.022144 | 0.033814 | 0.004938 | 0.11449 | -0.13174 | 0.037677 | 0.000359 | -0.042615 | -0.048268 | -0.013765 | 0.021486 | -0.10004 | 0.023899 | -121.4063 | 0.19789 | 0.1335 | 0.1096 | -121.4352 | -121.3256 | 0.055595 | -121.4884 | 0.19332 | 0.11303 | 0.05743 | -121.4539 | -121.4186 | 0.18945 | 0.16058 | 0.27013 | 0.17536 | -121.5719 | 0.10737 | 0.14188 | 0.17713 | 0.156 | -121.5402
3693.0469 | 121.5225 | -0.17853 | 121.4539 | 1.4211e-13 | -0.041534 | 0.0069553 | 0.021862 | -0.0079782 | -0.010408 | 0.0053411 | -0.0017903 | 0.023233 | -0.0058048 | 0.023771 | 0.010997 | 0.037675 | 0.015142 | -0.017566 | 0.020079 | -0.00422 | 0.10534 | -0.12716 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.004608 | 0.016908 | -0.1092 | 0.051366 | -121.4338 | 0.2162 | 0.16096 | 0.1096 | -121.4581 | -121.3485 | 0.069325 | -121.5067 | 0.22078 | 0.13591 | 0.066588 | -121.4585 | -121.4369 | 0.19861 | 0.17431 | 0.28386 | 0.19367 | -121.581 | 0.12568 | 0.17392 | 0.19544 | 0.17889 | -121.5631
3694.8281 | 121.5775 | -0.17395 | 121.4905 | 1.4211e-13 | -0.041961 | 0.0067415 | 0.022076 | -0.0077646 | -0.010408 | -0.0022889 | -0.0020039 | 0.022592 | -0.0062322 | 0.023771 | 0.010997 | 0.037675 | 0.015142 | -0.017566 | 0.020079 | 0.000359 | 0.10992 | -0.13174 | 0.037677 | 0.009516 | -0.042615 | -0.048268 | -0.013765 | 0.016908 | -0.10004 | 0.042209 | -121.4704 | 0.21163 | 0.15638 | 0.11417 | -121.4901 | -121.3806 | 0.073905 | -121.5387 | 0.21163 | 0.13133 | 0.05743 | -121.5042 | -121.4736 | 0.19403 | 0.17431 | 0.28387 | 0.18909 | -121.6222 | 0.12568 | 0.16018 | 0.19086 | 0.18347 | -121.5905
3696.5625 | 121.6278 | -0.15564 | 121.4813 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022289 | -0.0077646 | -0.010408 | -0.0099194 | -0.0020039 | 0.023019 | -0.0055912 | 0.023557 | 0.010997 | 0.042253 | 0.019721 | -0.022144 | 0.029236 | 0.004938 | 0.10076 | -0.13174 | 0.046835 | 0.000359 | -0.042615 | -0.04369 | -0.009187 | 0.021486 | -0.095467 | 0.023899 | -121.4521 | 0.19789 | 0.1335 | 0.1096 | -121.4764 | -121.3806 | 0.060173 | -121.525 | 0.20248 | 0.11303 | 0.052852 | -121.4905 | -121.4598 | 0.18488 | 0.16058 | 0.2564 | 0.17536 | -121.6131 | 0.11195 | 0.14645 | 0.17713 | 0.156 | -121.5768
3698.3438 | 121.6782 | -0.13733 | 121.4447 | 1.4211e-13 | -0.041748 | 0.0067415 | 0.022076 | -0.0077646 | -0.010194 | -0.0099194 | -0.0020039 | 0.023019 | -0.0058048 | 0.023557 | 0.011424 | 0.046831 | 0.015142 | -0.017566 | 0.020079 | -0.00422 | 0.10992 | -0.118 | 0.042256 | 0.004938 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.10004 | 0.019325 | -121.4246 | 0.18416 | 0.11976 | 0.10044 | -121.4489 | -121.3348 | 0.037284 | -121.493 | 0.17958 | 0.094714 | 0.05743 | -121.4539 | -121.4232 | 0.15741 | 0.13311 | 0.24724 | 0.15247 | -121.5627 | 0.089061 | 0.12814 | 0.15882 | 0.14227 | -121.5447
3700.125 | 121.6049 | -0.15564 | 121.4676 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022503 | -0.0077646 | -0.0099803 | -0.01755 | -0.0017903 | 0.022806 | -0.0055912 | 0.023985 | 0.01121 | 0.046831 | 0.010564 | -0.017566 | 0.020079 | 0.000359 | 0.10076 | -0.12716 | 0.042256 | 0.000359 | -0.042615 | -0.04369 | -0.013765 | 0.016908 | -0.095467 | 0.028478 | -121.4475 | 0.20247 | 0.13807 | 0.1096 | -121.4672 | -121.3668 | 0.060173 | -121.5113 | 0.1979 | 0.11303 | 0.052852 | -121.4814 | -121.4507 | 0.17572 | 0.156 | 0.2564 | 0.1662 | -121.5948 | 0.11195 | 0.14188 | 0.17255 | 0.156 | -121.5631
3701.8438 | 121.7148 | -0.11902 | 121.4401 | 1.4211e-13 | -0.041961 | 0.0065279 | 0.022503 | -0.0077646 | -0.010408 | -0.0099194 | -0.0017903 | 0.023019 | -0.0060184 | 0.023557 | 0.010997 | 0.037675 | 0.015142 | -0.017566 | 0.029236 | -0.00422 | 0.10992 | -0.12716 | 0.037677 | -0.008798 | -0.042615 | -0.052847 | -0.018344 | 0.012329 | -0.10462 | -0.008143 | -121.4109 | 0.15669 | 0.10145 | 0.1096 | -121.4443 | -121.3302 | 0.014395 | -121.493 | 0.1567 | 0.076404 | 0.062009 | -121.4585 | -121.4278 | 0.14825 | 0.1148 | 0.22893 | 0.13416 | -121.5673 | 0.066172 | 0.10068 | 0.13135 | 0.11022 | -121.5447
3703.5469 | 121.6553 | -0.13733 | 121.4859 | 1.4211e-13 | -0.042175 | 0.0067415 | 0.022289 | -0.0081918 | -0.010194 | -0.0099194 | -0.0017903 | 0.023019 | -0.0060184 | 0.023557 | 0.010997 | 0.046831 | 0.015142 | -0.026723 | 0.024657 | 0.000359 | 0.10534 | -0.12716 | 0.042256 | 0.004938 | -0.042615 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.010167 | -121.4612 | 0.18416 | 0.11061 | 0.10044 | -121.4855 | -121.3806 | 0.032705 | -121.5342 | 0.17958 | 0.094714 | 0.062009 | -121.4951 | -121.469 | 0.16199 | 0.13769 | 0.24267 | 0.15247 | -121.6131 | 0.089061 | 0.12814 | 0.15424 | 0.14227 | -121.5905
3705.3281 | 121.6507 | -0.15564 | 121.4859 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022289 | -0.0084056 | -0.010194 | -0.0022889 | -0.0017903 | 0.022592 | -0.0062322 | 0.023557 | 0.010997 | 0.042253 | 0.015142 | -0.022144 | 0.024657 | -0.008799 | 0.10076 | -0.13632 | 0.042256 | -0.008798 | -0.042615 | -0.048268 | -0.009187 | 0.012329 | -0.1092 | 0.01932 | -121.4612 | 0.19789 | 0.1335 | 0.11418 | -121.4947 | -121.3851 | 0.046437 | -121.5342 | 0.1979 | 0.11303 | 0.066588 | -121.4951 | -121.4736 | 0.1803 | 0.14684 | 0.2564 | 0.17078 | -121.6222 | 0.10737 | 0.14645 | 0.16797 | 0.14684 | -121.5951
3707.0625 | 121.6232 | -0.15106 | 121.5179 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.022076 | -0.0077646 | -0.0097665 | -0.0022889 | -0.0015767 | 0.023019 | -0.0055912 | 0.023557 | 0.01121 | 0.046831 | 0.010564 | -0.026723 | 0.024657 | 0.000359 | 0.10992 | -0.12716 | 0.042256 | 0.004938 | -0.038036 | -0.057425 | -0.009187 | 0.021486 | -0.10462 | 0.0239 | -121.4933 | 0.19789 | 0.12434 | 0.10044 | -121.5176 | -121.408 | 0.046438 | -121.5754 | 0.19332 | 0.11303 | 0.066588 | -121.5271 | -121.4965 | 0.17572 | 0.15142 | 0.26098 | 0.16163 | -121.6451 | 0.093637 | 0.14188 | 0.17255 | 0.156 | -121.6226
3708.8594 | 121.7194 | -0.13733 | 121.5042 | 1.4211e-13 | -0.041961 | 0.0067415 | 0.022076 | -0.0084056 | -0.0099803 | -0.0022889 | -0.0022175 | 0.023019 | -0.0055912 | 0.023557 | 0.010783 | 0.042253 | 0.010564 | -0.017566 | 0.020079 | 0.000359 | 0.10534 | -0.13174 | 0.046835 | 0.000359 | -0.038036 | -0.052847 | -0.009187 | 0.016908 | -0.10004 | 0.005588 | -121.4841 | 0.17958 | 0.11976 | 0.11417 | -121.5039 | -121.3989 | 0.037284 | -121.5571 | 0.18416 | 0.099293 | 0.062009 | -121.5134 | -121.4873 | 0.15741 | 0.13769 | 0.24267 | 0.14789 | -121.636 | 0.084482 | 0.12814 | 0.15424 | 0.13769 | -121.6043
3710.5781 | 121.7514 | -0.14191 | 121.5042 | 1.4211e-13 | -0.042175 | 0.0071689 | 0.022289 | -0.0081918 | -0.0099803 | -0.0022889 | -0.0017903 | 0.023019 | -0.0060184 | 0.023985 | 0.010569 | 0.042253 | 0.015142 | -0.022144 | 0.029236 | 0.004938 | 0.10992 | -0.13174 | 0.046835 | -0.00422 | -0.038036 | -0.048268 | -0.013765 | 0.026065 | -0.10004 | 0.010166 | -121.475 | 0.18416 | 0.11976 | 0.1096 | -121.4993 | -121.3943 | 0.041862 | -121.5525 | 0.18874 | 0.10387 | 0.062009 | -121.518 | -121.4781 | 0.17114 | 0.14685 | 0.25182 | 0.15705 | -121.636 | 0.093639 | 0.12814 | 0.16797 | 0.13769 | -121.6043
3712.3438 | 121.7651 | -0.15564 | 121.4996 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022289 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.023019 | -0.0062322 | 0.023985 | 0.010783 | 0.042253 | 0.001407 | -0.026723 | 0.024657 | 0.000359 | 0.10534 | -0.12716 | 0.037677 | -0.00422 | -0.038036 | -0.052847 | -0.009187 | 0.021486 | -0.10004 | 0.028478 | -121.475 | 0.19789 | 0.12892 | 0.10044 | -121.4993 | -121.3943 | 0.055595 | -121.5525 | 0.19332 | 0.1176 | 0.062009 | -121.5088 | -121.4781 | 0.1803 | 0.156 | 0.26098 | 0.15705 | -121.6268 | 0.10279 | 0.14645 | 0.17713 | 0.15142 | -121.5997
3714.125 | 121.669 | -0.16479 | 121.5363 | 1.4211e-13 | -0.042389 | 0.0065279 | 0.022076 | -0.0081918 | -0.010408 | -0.0022889 | -0.0017903 | 0.022806 | -0.0062322 | 0.023557 | 0.010997 | 0.042253 | 0.010564 | -0.022144 | 0.015501 | -0.00422 | 0.10534 | -0.12716 | 0.042256 | 0.004938 | -0.042615 | -0.04369 | -2.9e-05 | 0.016908 | -0.10004 | 0.037633 | -121.5208 | 0.20705 | 0.14265 | 0.10502 | -121.5405 | -121.4309 | 0.06475 | -121.5799 | 0.20705 | 0.12218 | 0.05743 | -121.5363 | -121.5193 | 0.1803 | 0.16057 | 0.27013 | 0.17536 | -121.6634 | 0.1211 | 0.16477 | 0.1817 | 0.16973 | -121.6363
3715.9062 | 121.7056 | -0.14648 | 121.5683 | 1.4211e-13 | -0.041961 | 0.0071689 | 0.022076 | -0.0079782 | -0.0099803 | -0.01755 | -0.0017903 | 0.022806 | -0.0058048 | 0.023771 | 0.010783 | 0.046831 | 0.015142 | -0.022144 | 0.024657 | -0.008799 | 0.10992 | -0.12258 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.1092 | 0.023901 | -121.5436 | 0.19332 | 0.12434 | 0.10044 | -121.5771 | -121.4584 | 0.037281 | -121.6166 | 0.18874 | 0.10387 | 0.066588 | -121.5775 | -121.5468 | 0.17114 | 0.13769 | 0.2564 | 0.16163 | -121.6909 | 0.098216 | 0.1373 | 0.16797 | 0.14684 | -121.6775
3717.6719 | 121.7331 | -0.1236 | 121.5454 | 1.4211e-13 | -0.042602 | 0.0069553 | 0.022076 | -0.0075508 | -0.010408 | -0.01755 | -0.0020039 | 0.022592 | -0.0058048 | 0.023557 | 0.010997 | 0.046831 | 0.015142 | -0.022144 | 0.020079 | 0.004938 | 0.10534 | -0.12716 | 0.046835 | 0.004938 | -0.042615 | -0.048268 | -0.013765 | 0.016908 | -0.10004 | -0.003566 | -121.5253 | 0.17043 | 0.10145 | 0.10502 | -121.5405 | -121.4401 | 0.023551 | -121.5937 | 0.17043 | 0.080981 | 0.05743 | -121.5592 | -121.5285 | 0.14367 | 0.12853 | 0.22893 | 0.13874 | -121.6726 | 0.075328 | 0.10983 | 0.1405 | 0.12853 | -121.6455
3719.3906 | 121.8338 | -0.14191 | 121.5271 | 1.4211e-13 | -0.041748 | 0.0069553 | 0.022076 | -0.0077646 | -0.0099803 | -0.0099194 | -0.0017903 | 0.022806 | -0.0058048 | 0.023557 | 0.010783 | 0.042253 | 0.010564 | -0.022144 | 0.024657 | -0.00422 | 0.10534 | -0.13174 | 0.042256 | -0.00422 | -0.047194 | -0.04369 | -0.009187 | 0.026065 | -0.10462 | 0.010166 | -121.5024 | 0.18416 | 0.11976 | 0.1096 | -121.5313 | -121.4218 | 0.037283 | -121.5708 | 0.18416 | 0.094713 | 0.05743 | -121.5363 | -121.501 | 0.16656 | 0.13769 | 0.24724 | 0.15247 | -121.6588 | 0.098217 | 0.13272 | 0.16797 | 0.13769 | -121.6317
3721.1719 | 121.6736 | -0.16022 | 121.5775 | 1.4211e-13 | -0.041961 | 0.0065279 | 0.022289 | -0.0081918 | -0.010408 | -0.0022889 | -0.0017903 | 0.022592 | -0.0062322 | 0.023557 | 0.010997 | 0.055988 | 0.019721 | -0.022144 | 0.024657 | -0.008799 | 0.10534 | -0.13174 | 0.042256 | 0.004938 | -0.047194 | -0.057425 | -0.009187 | 0.026065 | -0.10004 | 0.028476 | -121.5528 | 0.21621 | 0.13807 | 0.1096 | -121.5863 | -121.4721 | 0.060172 | -121.6349 | 0.20247 | 0.11302 | 0.052851 | -121.5866 | -121.5514 | 0.18487 | 0.15142 | 0.26555 | 0.17994 | -121.7092 | 0.10279 | 0.15103 | 0.18628 | 0.16515 | -121.6775
3722.9531 | 121.7331 | -0.16937 | 121.5958 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022289 | -0.0077646 | -0.010408 | -0.0022889 | -0.0020039 | 0.023019 | -0.0058048 | 0.023771 | 0.010783 | 0.037675 | 0.010564 | -0.022144 | 0.024657 | -0.00422 | 0.10076 | -0.12716 | 0.037677 | 0.004938 | -0.038036 | -0.048268 | -0.013765 | 0.026065 | -0.095467 | 0.042211 | -121.5711 | 0.20705 | 0.14723 | 0.10502 | -121.6 | -121.495 | 0.073906 | -121.644 | 0.20705 | 0.13134 | 0.057431 | -121.6095 | -121.5697 | 0.19403 | 0.16515 | 0.27013 | 0.17994 | -121.7229 | 0.1211 | 0.15561 | 0.19544 | 0.17431 | -121.6912
3724.6719 | 121.7697 | -0.13733 | 121.5546 | 1.4211e-13 | -0.041961 | 0.0069553 | 0.022076 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.023019 | -0.0058048 | 0.023771 | 0.010997 | 0.046831 | 0.010564 | -0.022144 | 0.020079 | 0.004938 | 0.10534 | -0.13632 | 0.046835 | 0.004938 | -0.033458 | -0.048268 | -0.013765 | 0.021486 | -0.090888 | 0.001009 | -121.5345 | 0.18416 | 0.11519 | 0.11418 | -121.5496 | -121.4492 | 0.046441 | -121.6028 | 0.18416 | 0.10387 | 0.05743 | -121.5683 | -121.5331 | 0.15741 | 0.14227 | 0.24267 | 0.14789 | -121.6909 | 0.089061 | 0.12356 | 0.15882 | 0.14227 | -121.6455
3726.4375 | 121.6965 | -0.16937 | 121.6049 | 1.4211e-13 | -0.042175 | 0.0069553 | 0.021862 | -0.0081918 | -0.010408 | -0.0099194 | -0.0022175 | 0.022592 | -0.0058048 | 0.023771 | 0.010783 | 0.037675 | 0.010564 | -0.022144 | 0.020079 | 0.000359 | 0.10076 | -0.13174 | 0.042256 | 0.004938 | -0.038036 | -0.052847 | -0.009187 | 0.016908 | -0.10004 | 0.037632 | -121.5848 | 0.20705 | 0.14723 | 0.1096 | -121.6046 | -121.5042 | 0.069328 | -121.6578 | 0.21163 | 0.13134 | 0.062009 | -121.6141 | -121.588 | 0.18945 | 0.16973 | 0.27013 | 0.17994 | -121.7367 | 0.11653 | 0.16019 | 0.18628 | 0.17431 | -121.705
3728.2188 | 121.6965 | -0.17853 | 121.5866 | 1.4211e-13 | -0.041961 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.022592 | -0.0060184 | 0.023771 | 0.010783 | 0.042253 | 0.010564 | -0.017566 | 0.024657 | 0.000359 | 0.10076 | -0.13174 | 0.042256 | 0.000359 | -0.047194 | -0.04369 | -0.009187 | 0.021486 | -0.10462 | 0.046787 | -121.562 | 0.22078 | 0.16096 | 0.11417 | -121.5862 | -121.4858 | 0.073904 | -121.6303 | 0.22078 | 0.13133 | 0.05743 | -121.5958 | -121.5651 | 0.20319 | 0.17889 | 0.27929 | 0.18909 | -121.7184 | 0.13484 | 0.16934 | 0.20001 | 0.17889 | -121.6912
3730 | 121.6873 | -0.19226 | 121.6003 | 1.4211e-13 | -0.042602 | 0.0069553 | 0.021862 | -0.0079782 | -0.010408 | 0.0053411 | -0.0017903 | 0.022806 | -0.0060184 | 0.023985 | 0.010569 | 0.042253 | 0.005985 | -0.022144 | 0.020079 | -0.00422 | 0.09618 | -0.13632 | 0.046835 | 0.004938 | -0.042615 | -0.057425 | -0.004608 | 0.016908 | -0.10462 | 0.055941 | -121.5803 | 0.23451 | 0.17012 | 0.11418 | -121.6046 | -121.5042 | 0.087637 | -121.6578 | 0.2391 | 0.14965 | 0.062009 | -121.605 | -121.5834 | 0.21234 | 0.18804 | 0.28844 | 0.19825 | -121.7367 | 0.13484 | 0.18765 | 0.20917 | 0.1972 | -121.705
3731.7344 | 121.7148 | -0.18768 | 121.6095 | 1.4211e-13 | -0.042175 | 0.0067415 | 0.022076 | -0.0077646 | -0.010194 | -0.0099194 | -0.0022175 | 0.023019 | -0.0060184 | 0.023557 | 0.010356 | 0.042253 | 0.010564 | -0.017566 | 0.024657 | 0.000359 | 0.10992 | -0.13632 | 0.046835 | -0.008798 | -0.047194 | -0.057425 | -0.013765 | 0.021486 | -0.1092 | 0.051363 | -121.5848 | 0.22994 | 0.17012 | 0.11875 | -121.6091 | -121.4996 | 0.07848 | -121.6669 | 0.23452 | 0.14049 | 0.062009 | -121.6233 | -121.588 | 0.21234 | 0.18804 | 0.2976 | 0.19825 | -121.7458 | 0.13026 | 0.17392 | 0.20917 | 0.17888 | -121.7187
3733.5 | 121.7789 | -0.16022 | 121.6049 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022076 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.022806 | -0.0060184 | 0.023557 | 0.010997 | 0.046831 | 0.010564 | -0.017566 | 0.020079 | -0.00422 | 0.10076 | -0.13174 | 0.037677 | 0.000359 | -0.047194 | -0.052847 | -0.013765 | 0.016908 | -0.10462 | 0.028476 | -121.5848 | 0.20705 | 0.14265 | 0.11417 | -121.6091 | -121.5042 | 0.055593 | -121.6578 | 0.19789 | 0.11302 | 0.05743 | -121.6187 | -121.588 | 0.1803 | 0.156 | 0.26098 | 0.17078 | -121.7367 | 0.10737 | 0.14645 | 0.17713 | 0.16058 | -121.7095
3735.2812 | 121.756 | -0.1831 | 121.6141 | 1.4211e-13 | -0.042602 | 0.0069553 | 0.021862 | -0.0077646 | -0.010194 | -0.01755 | -0.0020039 | 0.023019 | -0.0060184 | 0.023985 | 0.010569 | 0.042253 | 0.010564 | -0.031301 | 0.020079 | -0.00422 | 0.10992 | -0.13174 | 0.042256 | 0.004938 | -0.038036 | -0.04369 | -0.004608 | 0.030644 | -0.095467 | 0.051364 | -121.594 | 0.22536 | 0.1518 | 0.10044 | -121.6183 | -121.5042 | 0.087638 | -121.6578 | 0.22536 | 0.14507 | 0.057431 | -121.6187 | -121.5834 | 0.20318 | 0.17888 | 0.29302 | 0.19367 | -121.7458 | 0.13941 | 0.1785 | 0.21375 | 0.18804 | -121.7095
3737.0156 | 121.7651 | -0.17853 | 121.6187 | 1.4211e-13 | -0.042175 | 0.0067415 | 0.022076 | -0.0086192 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.0058048 | 0.023771 | 0.010997 | 0.046831 | 0.015142 | -0.026723 | 0.020079 | -0.00422 | 0.10534 | -0.13632 | 0.042256 | 0.000359 | -0.038036 | -0.052847 | -0.013765 | 0.021486 | -0.10462 | 0.042208 | -121.5986 | 0.22536 | 0.1518 | 0.1096 | -121.6229 | -121.5133 | 0.073904 | -121.6715 | 0.22078 | 0.14049 | 0.066588 | -121.6324 | -121.5972 | 0.19861 | 0.17431 | 0.28386 | 0.19367 | -121.755 | 0.12568 | 0.16476 | 0.20001 | 0.17889 | -121.7233
3738.7969 | 121.7926 | -0.16022 | 121.6232 | 1.4211e-13 | -0.042389 | 0.0071689 | 0.022503 | -0.0079782 | -0.010194 | -0.0022889 | -0.0022175 | 0.023019 | -0.0058048 | 0.023557 | 0.010997 | 0.046831 | 0.005985 | -0.026723 | 0.020079 | -0.00422 | 0.10534 | -0.1409 | 0.051413 | 0.000359 | -0.042615 | -0.048268 | -2.9e-05 | 0.016908 | -0.10004 | 0.019318 | -121.6032 | 0.20705 | 0.13349 | 0.11418 | -121.6275 | -121.5179 | 0.060172 | -121.6715 | 0.21163 | 0.1176 | 0.05743 | -121.6233 | -121.6063 | 0.1803 | 0.156 | 0.26555 | 0.1662 | -121.7641 | 0.11195 | 0.16019 | 0.17713 | 0.16058 | -121.7233
3740.5 | 121.8796 | -0.13733 | 121.5912 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022076 | -0.0079782 | -0.010194 | -0.0022889 | -0.0017903 | 0.023019 | -0.0058048 | 0.023557 | 0.010997 | 0.042253 | -0.003172 | -0.031301 | 0.024657 | -0.00422 | 0.10076 | -0.1409 | 0.042256 | -0.013377 | -0.042615 | -0.057425 | -0.018344 | 0.012329 | -0.10462 | -0.00357 | -121.5665 | 0.17958 | 0.10603 | 0.1096 | -121.5954 | -121.4904 | 0.032705 | -121.6486 | 0.17958 | 0.094714 | 0.062009 | -121.6095 | -121.5789 | 0.16199 | 0.13311 | 0.23809 | 0.13416 | -121.7321 | 0.079904 | 0.11899 | 0.14966 | 0.12395 | -121.6958
3742.2812 | 121.7651 | -0.1831 | 121.6599 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | 0.0053411 | -0.0017903 | 0.023019 | -0.0058048 | 0.023344 | 0.010783 | 0.037675 | 0.010564 | -0.031301 | 0.024657 | 0.000359 | 0.10534 | -0.14548 | 0.046835 | -0.008798 | -0.038036 | -0.052847 | -0.013765 | 0.012329 | -0.10004 | 0.037627 | -121.6352 | 0.22078 | 0.1518 | 0.11418 | -121.6595 | -121.5545 | 0.08306 | -121.7127 | 0.22994 | 0.14507 | 0.062009 | -121.6736 | -121.6475 | 0.20776 | 0.18346 | 0.28844 | 0.19367 | -121.8053 | 0.13026 | 0.16934 | 0.19543 | 0.17431 | -121.7599
3744.0469 | 121.7697 | -0.1831 | 121.6599 | 1.4211e-13 | -0.042602 | 0.0069553 | 0.022076 | -0.0077646 | -0.0099803 | -0.01755 | -0.0020039 | 0.022806 | -0.0058048 | 0.023557 | 0.010569 | 0.046831 | 0.005985 | -0.022144 | 0.024657 | 0.000359 | 0.10076 | -0.14548 | 0.046835 | 0.000359 | -0.042615 | -0.048268 | -0.018344 | 0.016908 | -0.10462 | 0.037627 | -121.6352 | 0.22994 | 0.16096 | 0.12333 | -121.6595 | -121.5591 | 0.078481 | -121.7081 | 0.22994 | 0.14049 | 0.062009 | -121.6782 | -121.6429 | 0.20776 | 0.18346 | 0.28386 | 0.18909 | -121.8053 | 0.13484 | 0.16476 | 0.20001 | 0.18346 | -121.7645
3745.7812 | 121.7926 | -0.19226 | 121.6232 | 1.4211e-13 | -0.042602 | 0.0073825 | 0.022076 | -0.0081918 | -0.0099803 | 0.0053411 | -0.0020039 | 0.023019 | -0.0060184 | 0.023985 | 0.010783 | 0.042253 | 0.001407 | -0.022144 | 0.024657 | -0.008799 | 0.10076 | -0.15006 | 0.046835 | 0.004938 | -0.038036 | -0.04369 | -0.013765 | 0.021486 | -0.095467 | 0.042204 | -121.5986 | 0.23451 | 0.17012 | 0.12791 | -121.632 | -121.5225 | 0.096794 | -121.6669 | 0.2391 | 0.15423 | 0.057431 | -121.637 | -121.6017 | 0.21692 | 0.18346 | 0.29302 | 0.19367 | -121.7733 | 0.14857 | 0.1785 | 0.21375 | 0.1972 | -121.7187
3747.5625 | 121.7834 | -0.20142 | 121.6644 | 1.4211e-13 | -0.042602 | 0.0065279 | 0.022289 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.023019 | -0.0062322 | 0.023771 | 0.010997 | 0.042253 | 0.005985 | -0.026723 | 0.015501 | -0.00422 | 0.10992 | -0.14548 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.009187 | 0.021486 | -0.10004 | 0.055938 | -121.6489 | 0.24367 | 0.17469 | 0.11875 | -121.6686 | -121.5545 | 0.10137 | -121.7173 | 0.24367 | 0.1588 | 0.05743 | -121.6736 | -121.6429 | 0.21692 | 0.1972 | 0.31133 | 0.2074 | -121.8099 | 0.14857 | 0.19223 | 0.2229 | 0.20178 | -121.7645
3749.3438 | 121.8338 | -0.16022 | 121.6644 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022076 | -0.0079782 | -0.010194 | -0.01755 | -0.0017903 | 0.023019 | -0.0060184 | 0.023985 | 0.010569 | 0.042253 | 0.005985 | -0.022144 | 0.024657 | -0.00422 | 0.10076 | -0.1409 | 0.046835 | 0.000359 | -0.047194 | -0.057425 | -0.009187 | 0.026065 | -0.10004 | 0.019318 | -121.6398 | 0.20247 | 0.13807 | 0.11875 | -121.6686 | -121.5637 | 0.060172 | -121.7219 | 0.20705 | 0.11302 | 0.052851 | -121.6736 | -121.6384 | 0.18487 | 0.156 | 0.26098 | 0.1662 | -121.8053 | 0.10279 | 0.15103 | 0.18628 | 0.16058 | -121.7645
3751.0781 | 121.8338 | -0.16937 | 121.6599 | 1.4211e-13 | -0.042389 | 0.0069553 | 0.022503 | -0.0077646 | -0.010408 | -0.0099194 | -0.0017903 | 0.022806 | -0.0062322 | 0.023771 | 0.010783 | 0.046831 | 0.005985 | -0.022144 | 0.015501 | 0.000359 | 0.10534 | -0.1409 | 0.046835 | -0.00422 | -0.047194 | -0.057425 | -0.009187 | 0.012329 | -0.10462 | 0.028474 | -121.6444 | 0.2162 | 0.14723 | 0.11875 | -121.6595 | -121.5545 | 0.064749 | -121.7173 | 0.21621 | 0.12218 | 0.05743 | -121.669 | -121.6475 | 0.18487 | 0.16973 | 0.27471 | 0.17536 | -121.8008 | 0.11195 | 0.16019 | 0.1817 | 0.16515 | -121.7645
3752.8594 | 121.7926 | -0.20142 | 121.6827 | 1.4211e-13 | -0.042389 | 0.0065279 | 0.022503 | -0.0079782 | -0.010408 | -0.0099194 | -0.0017903 | 0.022592 | -0.0058048 | 0.023557 | 0.010783 | 0.046831 | 0.001407 | -0.022144 | 0.020079 | 0.000359 | 0.10076 | -0.14548 | 0.033099 | 0.004938 | -0.038036 | -0.048268 | -0.013765 | 0.026065 | -0.10462 | 0.055938 | -121.6627 | 0.24825 | 0.17927 | 0.12333 | -121.6824 | -121.582 | 0.096792 | -121.731 | 0.23452 | 0.16338 | 0.066588 | -121.6965 | -121.6567 | 0.22149 | 0.20178 | 0.30218 | 0.20282 | -121.8282 | 0.15315 | 0.18765 | 0.22748 | 0.20635 | -121.7874
3754.5781 | 121.8979 | -0.15106 | 121.6415 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022289 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.022806 | -0.0058048 | 0.023985 | 0.010569 | 0.046831 | 0.005985 | -0.022144 | 0.015501 | -0.008799 | 0.10534 | -0.1409 | 0.042256 | 0.000359 | -0.038036 | -0.04369 | -0.009187 | 0.016908 | -0.1092 | 0.010163 | -121.626 | 0.19789 | 0.12892 | 0.11875 | -121.6503 | -121.5362 | 0.041859 | -121.6852 | 0.19332 | 0.11303 | 0.071167 | -121.6507 | -121.6246 | 0.16656 | 0.14226 | 0.2564 | 0.15705 | -121.7824 | 0.10737 | 0.14188 | 0.16797 | 0.15142 | -121.7507
3756.3438 | 121.9162 | -0.14191 | 121.6599 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022717 | -0.0079782 | -0.010194 | -0.0099194 | -0.0017903 | 0.022806 | -0.0062322 | 0.024198 | 0.010569 | 0.046831 | 0.005985 | -0.022144 | 0.024657 | -0.00422 | 0.091601 | -0.14548 | 0.042256 | 0.004938 | -0.042615 | -0.04369 | -0.018344 | 0.016908 | -0.10004 | -0.003571 | -121.6352 | 0.18874 | 0.11976 | 0.12333 | -121.6641 | -121.5683 | 0.041862 | -121.7035 | 0.18416 | 0.099292 | 0.05743 | -121.6782 | -121.6429 | 0.16656 | 0.13769 | 0.23351 | 0.14789 | -121.8053 | 0.098217 | 0.12356 | 0.15882 | 0.14685 | -121.7599
3758.125 | 121.9574 | -0.15106 | 121.6461 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022503 | -0.0081918 | -0.0099803 | -0.0099194 | -0.0022175 | 0.022806 | -0.0060184 | 0.023985 | 0.010569 | 0.046831 | 0.001407 | -0.022144 | 0.020079 | -0.00422 | 0.10534 | -0.14548 | 0.033099 | -0.00422 | -0.047194 | -0.052847 | -0.009187 | 0.021486 | -0.1092 | 0.005584 | -121.626 | 0.19789 | 0.12892 | 0.12333 | -121.6503 | -121.5408 | 0.041859 | -121.699 | 0.18416 | 0.10387 | 0.062009 | -121.6553 | -121.6246 | 0.17114 | 0.14684 | 0.2564 | 0.15247 | -121.7916 | 0.098215 | 0.14188 | 0.17255 | 0.14684 | -121.7553
3759.8438 | 121.8109 | -0.17395 | 121.6782 | 1.4211e-13 | -0.042389 | 0.0069553 | 0.022289 | -0.0081918 | -0.010408 | -0.0022889 | -0.0020039 | 0.022806 | -0.0062322 | 0.023771 | 0.010783 | 0.033096 | 0.005985 | -0.022144 | 0.020079 | 0.000359 | 0.10076 | -0.13632 | 0.042256 | 0.000359 | -0.047194 | -0.057425 | -0.009187 | 0.016908 | -0.095467 | 0.03763 | -121.6581 | 0.20705 | 0.15181 | 0.11418 | -121.6778 | -121.5774 | 0.078483 | -121.7356 | 0.21621 | 0.12676 | 0.048273 | -121.6873 | -121.6613 | 0.19403 | 0.17431 | 0.27471 | 0.17993 | -121.8145 | 0.11652 | 0.16476 | 0.19086 | 0.17431 | -121.7736
3761.625 | 121.9254 | -0.15106 | 121.6782 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.0058048 | 0.023985 | 0.010783 | 0.042253 | 0.010564 | -0.022144 | 0.015501 | 0.000359 | 0.10076 | -0.1409 | 0.046835 | 0.004938 | -0.047194 | -0.052847 | -0.009187 | 0.026065 | -0.1092 | 0.010163 | -121.6627 | 0.19332 | 0.12892 | 0.11875 | -121.6778 | -121.5774 | 0.041859 | -121.731 | 0.1979 | 0.10387 | 0.062009 | -121.6873 | -121.6521 | 0.16656 | 0.15142 | 0.25182 | 0.16163 | -121.8191 | 0.098215 | 0.14188 | 0.17713 | 0.156 | -121.7874
3763.4062 | 121.9528 | -0.12817 | 121.6553 | 1.4211e-13 | -0.042389 | 0.0063141 | 0.022289 | -0.0081918 | -0.010408 | -0.0022889 | -0.0020039 | 0.022806 | -0.0058048 | 0.023985 | 0.010569 | 0.037675 | -0.003172 | -0.022144 | 0.024657 | -0.00422 | 0.09618 | -0.13632 | 0.042256 | 0.000359 | -0.038036 | -0.04369 | -0.004608 | 0.012329 | -0.10462 | -0.008146 | -121.6306 | 0.16585 | 0.10603 | 0.11418 | -121.6595 | -121.5591 | 0.02355 | -121.699 | 0.17043 | 0.090138 | 0.066588 | -121.6599 | -121.6429 | 0.15283 | 0.12395 | 0.22435 | 0.125 | -121.7916 | 0.084484 | 0.12357 | 0.1405 | 0.12853 | -121.7599
3765.125 | 121.9711 | -0.14191 | 121.6873 | 1.4211e-13 | -0.042602 | 0.0069553 | 0.022503 | -0.0079782 | -0.010194 | -0.0099194 | -0.0022175 | 0.022806 | -0.0062322 | 0.023985 | 0.010783 | 0.037675 | 0.015142 | -0.022144 | 0.015501 | -0.00422 | 0.10076 | -0.13632 | 0.042256 | -0.00422 | -0.038036 | -0.04369 | -0.004608 | 0.021486 | -0.10004 | 0.005587 | -121.6718 | 0.17958 | 0.11976 | 0.11418 | -121.6915 | -121.5866 | 0.041862 | -121.731 | 0.18416 | 0.10387 | 0.062009 | -121.6919 | -121.6658 | 0.15741 | 0.13769 | 0.24267 | 0.15705 | -121.8236 | 0.098217 | 0.1373 | 0.16339 | 0.13769 | -121.7874
3766.9062 | 121.8567 | -0.19226 | 121.6965 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022717 | -0.0081918 | -0.010408 | -0.02518 | -0.0017903 | 0.022806 | -0.0060184 | 0.023985 | 0.010356 | 0.046831 | 0.005985 | -0.022144 | 0.015501 | -0.008799 | 0.10534 | -0.13632 | 0.046835 | 0.000359 | -0.038036 | -0.052847 | -0.009187 | 0.026065 | -0.10462 | 0.055941 | -121.681 | 0.23909 | 0.17012 | 0.11418 | -121.7053 | -121.5911 | 0.087637 | -121.7493 | 0.2391 | 0.15423 | 0.066588 | -121.7057 | -121.6704 | 0.20776 | 0.18346 | 0.2976 | 0.19825 | -121.8328 | 0.13941 | 0.18307 | 0.21833 | 0.19262 | -121.8011
3768.6875 | 121.9803 | -0.16022 | 121.6873 | 1.4211e-13 | -0.042389 | 0.0071689 | 0.022289 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.022806 | -0.0058048 | 0.023771 | 0.010569 | 0.042253 | -0.003172 | -0.031301 | 0.020079 | -0.008799 | 0.09618 | -0.14548 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -2.9e-05 | 0.016908 | -0.095467 | 0.014739 | -121.6672 | 0.20247 | 0.12892 | 0.11418 | -121.6961 | -121.5911 | 0.06475 | -121.7402 | 0.20247 | 0.1176 | 0.052852 | -121.6873 | -121.6704 | 0.1803 | 0.15142 | 0.2564 | 0.15704 | -121.8328 | 0.10737 | 0.16019 | 0.17713 | 0.16058 | -121.7828
3770.4531 | 121.9208 | -0.15564 | 121.6919 | 1.4211e-13 | -0.04303 | 0.0069553 | 0.022503 | -0.0079782 | -0.010194 | -0.01755 | -0.0022175 | 0.022378 | -0.0058048 | 0.023771 | 0.010783 | 0.042253 | 0.005985 | -0.022144 | 0.020079 | -0.00422 | 0.10076 | -0.1409 | 0.042256 | 0.000359 | -0.042615 | -0.052847 | -0.004608 | 0.016908 | -0.10004 | 0.014741 | -121.6718 | 0.19789 | 0.1335 | 0.11875 | -121.6961 | -121.5911 | 0.055595 | -121.7447 | 0.1979 | 0.11303 | 0.05743 | -121.6965 | -121.675 | 0.17572 | 0.15142 | 0.2564 | 0.16162 | -121.8328 | 0.10279 | 0.15103 | 0.17255 | 0.156 | -121.7919
3772.1875 | 121.8979 | -0.17395 | 121.7194 | 1.4211e-13 | -0.042389 | 0.0067415 | 0.022289 | -0.0086192 | -0.010194 | -0.0099194 | -0.0015767 | 0.022592 | -0.0066594 | 0.023985 | 0.010783 | 0.037675 | 0.001407 | -0.017566 | 0.020079 | -0.00422 | 0.09618 | -0.1409 | 0.042256 | 0.000359 | -0.038036 | -0.052847 | -0.009187 | 0.021486 | -0.10462 | 0.033051 | -121.6993 | 0.21163 | 0.15638 | 0.12333 | -121.7236 | -121.6232 | 0.069326 | -121.7722 | 0.21621 | 0.13591 | 0.066588 | -121.7285 | -121.6979 | 0.19403 | 0.16973 | 0.27013 | 0.17536 | -121.8603 | 0.1211 | 0.16476 | 0.19544 | 0.17431 | -121.824
3773.9844 | 121.9894 | -0.14191 | 121.7056 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.022289 | -0.0081918 | -0.0099803 | -0.0099194 | -0.0017903 | 0.022806 | -0.006873 | 0.023557 | 0.010783 | 0.042253 | 0.005985 | -0.012988 | 0.020079 | -0.00422 | 0.10992 | -0.1409 | 0.02852 | 0.004938 | -0.033458 | -0.04369 | -0.004608 | 0.021486 | -0.10462 | 0.001008 | -121.6855 | 0.18416 | 0.12892 | 0.12791 | -121.7098 | -121.5957 | 0.037283 | -121.7493 | 0.17043 | 0.10845 | 0.071166 | -121.7102 | -121.6841 | 0.16199 | 0.13769 | 0.25182 | 0.14789 | -121.8465 | 0.098217 | 0.1373 | 0.16339 | 0.14685 | -121.8103
3775.7656 | 121.9986 | -0.12817 | 121.701 | 1.4211e-13 | -0.042816 | 0.0065279 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.023019 | -0.0066594 | 0.023985 | 0.010783 | 0.046831 | 0.010564 | -0.026723 | 0.020079 | 0.000359 | 0.10076 | -0.13174 | 0.046835 | 0.000359 | -0.042615 | -0.052847 | -0.009187 | 0.016908 | -0.095467 | -0.003567 | -121.681 | 0.17501 | 0.10145 | 0.10502 | -121.7007 | -121.6003 | 0.032707 | -121.7539 | 0.17501 | 0.085559 | 0.052852 | -121.7102 | -121.6841 | 0.14825 | 0.12853 | 0.22893 | 0.13874 | -121.8328 | 0.075327 | 0.11899 | 0.14508 | 0.12853 | -121.7965
3777.4688 | 121.9711 | -0.13275 | 121.7285 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.022503 | -0.0077646 | -0.010408 | -0.0099194 | -0.0022175 | 0.022806 | -0.006873 | 0.023771 | 0.010783 | 0.037675 | 0.001407 | -0.022144 | 0.024657 | -0.00422 | 0.10076 | -0.1409 | 0.042256 | 0.004938 | -0.033458 | -0.048268 | -0.009187 | 0.030644 | -0.10004 | -0.008148 | -121.7039 | 0.17043 | 0.11061 | 0.11875 | -121.7327 | -121.6278 | 0.032706 | -121.7768 | 0.17501 | 0.099293 | 0.066587 | -121.7377 | -121.6979 | 0.15741 | 0.12853 | 0.23351 | 0.13416 | -121.8694 | 0.084483 | 0.12356 | 0.1634 | 0.13769 | -121.8286
3779.2656 | 121.9528 | -0.15106 | 121.7331 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022289 | -0.0081918 | -0.010408 | -0.0022889 | -0.0020039 | 0.023019 | -0.0066594 | 0.024198 | 0.010356 | 0.046831 | 0.010564 | -0.022144 | 0.020079 | -0.00422 | 0.10076 | -0.1409 | 0.037677 | 0.004938 | -0.047194 | -0.057425 | -0.009187 | 0.016908 | -0.10004 | 0.010163 | -121.713 | 0.19789 | 0.12892 | 0.11875 | -121.7373 | -121.6323 | 0.051017 | -121.7905 | 0.18874 | 0.10387 | 0.052851 | -121.7423 | -121.7162 | 0.17114 | 0.14684 | 0.25182 | 0.16163 | -121.874 | 0.093637 | 0.14188 | 0.16797 | 0.156 | -121.8331
3781.0469 | 121.8475 | -0.19226 | 121.7514 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022289 | -0.0075508 | -0.010194 | -0.0099194 | -0.0017903 | 0.023019 | -0.006873 | 0.023985 | 0.010569 | 0.05141 | 0.005985 | -0.017566 | 0.020079 | 0.000359 | 0.09618 | -0.13632 | 0.042256 | -0.00422 | -0.033458 | -0.057425 | 0.004549 | 0.021486 | -0.10462 | 0.055941 | -121.7313 | 0.24367 | 0.17469 | 0.11875 | -121.751 | -121.6552 | 0.087637 | -121.8088 | 0.23452 | 0.1588 | 0.071166 | -121.7469 | -121.7299 | 0.21234 | 0.19262 | 0.28844 | 0.19825 | -121.8877 | 0.13484 | 0.19681 | 0.21375 | 0.18804 | -121.856
3782.8281 | 121.962 | -0.14191 | 121.7194 | 1.4211e-13 | -0.043243 | 0.0065279 | 0.022076 | -0.0079782 | -0.010408 | -0.0022889 | -0.0015767 | 0.023019 | -0.006873 | 0.023771 | 0.010356 | 0.042253 | -0.003172 | -0.017566 | 0.024657 | 0.004938 | 0.10534 | -0.1409 | 0.046835 | -0.00422 | -0.042615 | -0.052847 | -0.004608 | 0.012329 | -0.10004 | 0.001008 | -121.6947 | 0.18416 | 0.12434 | 0.12333 | -121.7144 | -121.614 | 0.041862 | -121.7722 | 0.18874 | 0.099292 | 0.05743 | -121.724 | -121.707 | 0.16656 | 0.14685 | 0.24724 | 0.13873 | -121.8603 | 0.08906 | 0.1373 | 0.15424 | 0.13769 | -121.8194
3784.6094 | 121.8842 | -0.18768 | 121.7789 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022289 | -0.0077646 | -0.010194 | -0.01755 | -0.0017903 | 0.022806 | -0.006873 | 0.024412 | 0.010356 | 0.037675 | 0.001407 | -0.017566 | 0.024657 | -0.008799 | 0.09618 | -0.1409 | 0.037677 | -0.00422 | -0.033458 | -0.04369 | -0.004608 | 0.021486 | -0.095467 | 0.046784 | -121.7542 | 0.22536 | 0.17012 | 0.12333 | -121.7877 | -121.6827 | 0.092216 | -121.8226 | 0.22536 | 0.15423 | 0.062009 | -121.7835 | -121.7574 | 0.21234 | 0.17888 | 0.28386 | 0.18909 | -121.9198 | 0.14399 | 0.18307 | 0.20917 | 0.18346 | -121.8743
3786.3906 | 121.994 | -0.13275 | 121.7285 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.022717 | -0.0079782 | -0.010194 | -0.0099194 | -0.0017903 | 0.023019 | -0.0064458 | 0.024198 | 0.010356 | 0.046831 | 0.001407 | -0.017566 | 0.024657 | -0.008799 | 0.09618 | -0.13632 | 0.037677 | -0.00422 | -0.042615 | -0.052847 | -0.004608 | 0.016908 | -0.1092 | -0.003569 | -121.7039 | 0.17958 | 0.11519 | 0.11875 | -121.7373 | -121.6323 | 0.023548 | -121.7814 | 0.17043 | 0.090136 | 0.066588 | -121.7331 | -121.7116 | 0.15741 | 0.12395 | 0.22893 | 0.13416 | -121.8648 | 0.079904 | 0.12814 | 0.14966 | 0.12853 | -121.8377
3788.1875 | 122.0123 | -0.13275 | 121.7285 | 1.4211e-13 | -0.042816 | 0.0069553 | 0.022076 | -0.0081918 | -0.010408 | -0.0022889 | -0.0020039 | 0.023019 | -0.0066594 | 0.023985 | 0.010783 | 0.042253 | 0.001407 | -0.022144 | 0.024657 | 0.000359 | 0.10076 | -0.13632 | 0.037677 | 0.000359 | -0.038036 | -0.048268 | -2.9e-05 | 0.021486 | -0.10004 | -0.003569 | -121.7039 | 0.175 | 0.11061 | 0.11418 | -121.7282 | -121.6278 | 0.032706 | -121.7768 | 0.17043 | 0.094715 | 0.062009 | -121.7285 | -121.707 | 0.15741 | 0.13311 | 0.23351 | 0.13416 | -121.8648 | 0.084483 | 0.13272 | 0.15424 | 0.13311 | -121.8286
3789.9062 | 121.875 | -0.17853 | 121.7651 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022503 | -0.0081918 | -0.010194 | -0.0099194 | -0.0020039 | 0.022806 | -0.0070868 | 0.023771 | 0.010569 | 0.046831 | -0.003172 | -0.022144 | 0.029236 | -0.008799 | 0.10076 | -0.1409 | 0.033099 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.016908 | -0.10004 | 0.037629 | -121.7359 | 0.22536 | 0.15638 | 0.11875 | -121.7739 | -121.6644 | 0.078483 | -121.8134 | 0.21163 | 0.13591 | 0.05743 | -121.7743 | -121.7482 | 0.20776 | 0.16973 | 0.27929 | 0.17536 | -121.906 | 0.13026 | 0.16934 | 0.19544 | 0.17889 | -121.8652
3791.6875 | 122.0261 | -0.11444 | 121.7468 | 1.4211e-13 | -0.042816 | 0.0069553 | 0.022289 | -0.0079782 | -0.010408 | -0.01755 | -0.0017903 | 0.022806 | -0.0064458 | 0.023985 | 0.010356 | 0.042253 | 0.001407 | -0.026723 | 0.020079 | -0.00422 | 0.09618 | -0.13174 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.026065 | -0.10462 | -0.0173 | -121.7267 | 0.15669 | 0.087718 | 0.10502 | -121.751 | -121.6506 | 0.009817 | -121.7951 | 0.1567 | 0.071826 | 0.062009 | -121.756 | -121.7208 | 0.13452 | 0.11022 | 0.21062 | 0.11585 | -121.8786 | 0.066173 | 0.10525 | 0.14051 | 0.1148 | -121.8514
3793.4062 | 121.9162 | -0.17395 | 121.7834 | 1.4211e-13 | -0.042816 | 0.0067415 | 0.022076 | -0.0077646 | -0.010408 | 0.0053411 | -0.0022175 | 0.022806 | -0.0064458 | 0.023985 | 0.010356 | 0.042253 | 0.005985 | -0.012988 | 0.020079 | 0.000359 | 0.10076 | -0.14548 | 0.037677 | 0.004938 | -0.047194 | -0.04369 | -0.009187 | 0.021486 | -0.10004 | 0.028472 | -121.7634 | 0.2162 | 0.16096 | 0.13249 | -121.7831 | -121.6827 | 0.073905 | -121.8271 | 0.21163 | 0.12676 | 0.052851 | -121.7926 | -121.762 | 0.19403 | 0.17431 | 0.27471 | 0.17993 | -121.9289 | 0.13026 | 0.16476 | 0.19544 | 0.17889 | -121.8835
3795.2031 | 121.9162 | -0.1831 | 121.7926 | 1.4211e-13 | -0.042602 | 0.0067415 | 0.022503 | -0.0077646 | -0.010835 | -0.0099194 | -0.0022175 | 0.023233 | -0.0064458 | 0.023771 | 0.010569 | 0.037675 | 0.001407 | -0.022144 | 0.024657 | -0.00422 | 0.10534 | -0.1409 | 0.046835 | 0.000359 | -0.042615 | -0.052847 | -0.004608 | 0.021486 | -0.10004 | 0.042206 | -121.7679 | 0.22078 | 0.16096 | 0.11875 | -121.7968 | -121.6873 | 0.08306 | -121.8454 | 0.22994 | 0.14049 | 0.05743 | -121.7972 | -121.7711 | 0.20776 | 0.17888 | 0.28844 | 0.18451 | -121.9335 | 0.13026 | 0.1785 | 0.20459 | 0.18346 | -121.8926
3796.9844 | 121.9894 | -0.14648 | 121.7834 | 1.4211e-13 | -0.042816 | 0.0065279 | 0.022503 | -0.0081918 | -0.010408 | -0.0099194 | -0.0017903 | 0.022592 | -0.0064458 | 0.023771 | 0.010356 | 0.046831 | 0.001407 | -0.017566 | 0.010922 | 0.000359 | 0.10076 | -0.14548 | 0.046835 | 0.000359 | -0.042615 | -0.048268 | -2.9e-05 | 0.026065 | -0.10004 | 0.001006 | -121.7725 | 0.19332 | 0.12892 | 0.12791 | -121.7831 | -121.6827 | 0.046439 | -121.8317 | 0.19332 | 0.10387 | 0.05743 | -121.7835 | -121.7574 | 0.15741 | 0.14684 | 0.24724 | 0.14789 | -121.9289 | 0.098216 | 0.14646 | 0.17255 | 0.14684 | -121.8835
3798.7031 | 121.9208 | -0.18768 | 121.8338 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022289 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.0062322 | 0.023985 | 0.010569 | 0.046831 | 0.001407 | -0.012988 | 0.020079 | -0.00422 | 0.09618 | -0.13632 | 0.042256 | 0.000359 | -0.042615 | -0.04369 | -2.9e-05 | 0.021486 | -0.10004 | 0.051363 | -121.8137 | 0.23451 | 0.17469 | 0.12333 | -121.838 | -121.7376 | 0.087638 | -121.8775 | 0.22994 | 0.14507 | 0.05743 | -121.8338 | -121.8123 | 0.20776 | 0.18346 | 0.28386 | 0.18909 | -121.9701 | 0.14399 | 0.18765 | 0.20917 | 0.18804 | -121.9338
3800.4688 | 121.9254 | -0.17853 | 121.8201 | 1.4211e-13 | -0.042816 | 0.0069553 | 0.022289 | -0.0079782 | -0.010408 | -0.0022889 | -0.0017903 | 0.023019 | -0.0066594 | 0.024198 | 0.010569 | 0.046831 | -0.003172 | -0.017566 | 0.020079 | -0.00422 | 0.10534 | -0.13632 | 0.037677 | 0.004938 | -0.033458 | -0.048268 | -2.9e-05 | 0.016908 | -0.1092 | 0.042208 | -121.8 | 0.22536 | 0.16096 | 0.11875 | -121.8243 | -121.7147 | 0.069325 | -121.8683 | 0.2162 | 0.14507 | 0.075745 | -121.8201 | -121.8032 | 0.19861 | 0.17431 | 0.28386 | 0.17536 | -121.9564 | 0.13026 | 0.1785 | 0.19544 | 0.18347 | -121.9293
3802.25 | 121.9345 | -0.20599 | 121.8018 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022717 | -0.0081918 | -0.010194 | -0.0022889 | -0.0017903 | 0.022806 | -0.0066594 | 0.024412 | 0.010569 | 0.037675 | 0.005985 | -0.012988 | 0.024657 | 0.000359 | 0.10534 | -0.14548 | 0.042256 | 0.004938 | -0.038036 | -0.048268 | -0.004608 | 0.016908 | -0.1092 | 0.060516 | -121.7771 | 0.24367 | 0.19301 | 0.13249 | -121.8014 | -121.6964 | 0.096791 | -121.85 | 0.24825 | 0.16796 | 0.071167 | -121.8064 | -121.7849 | 0.23065 | 0.20635 | 0.31133 | 0.21198 | -121.9472 | 0.15773 | 0.20139 | 0.2229 | 0.21093 | -121.911
3803.9844 | 121.9482 | -0.14648 | 121.8201 | 1.4211e-13 | -0.04303 | 0.0071689 | 0.022289 | -0.0081918 | -0.010408 | -0.01755 | -0.0020039 | 0.022806 | -0.0073004 | 0.023985 | 0.010569 | 0.05141 | 0.001407 | -0.012988 | 0.020079 | -0.00422 | 0.10534 | -0.1409 | 0.037677 | -0.00422 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.10004 | 0.005585 | -121.8 | 0.19789 | 0.1335 | 0.12791 | -121.8243 | -121.7147 | 0.046439 | -121.8683 | 0.18416 | 0.10387 | 0.05743 | -121.8293 | -121.7986 | 0.16656 | 0.14226 | 0.25182 | 0.14789 | -121.961 | 0.098216 | 0.1373 | 0.16797 | 0.14226 | -121.9201
3805.7812 | 121.9345 | -0.20599 | 121.8063 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022076 | -0.0077646 | -0.010194 | -0.0099194 | -0.0020039 | 0.022806 | -0.0066594 | 0.024198 | 0.010569 | 0.046831 | 0.001407 | -0.017566 | 0.020079 | -0.008799 | 0.10076 | -0.13632 | 0.037677 | 0.009516 | -0.038036 | -0.048268 | -0.009187 | 0.026065 | -0.1092 | 0.069674 | -121.7863 | 0.25283 | 0.18843 | 0.11875 | -121.8151 | -121.7056 | 0.096791 | -121.8546 | 0.24367 | 0.16796 | 0.071167 | -121.8155 | -121.7803 | 0.22607 | 0.1972 | 0.30675 | 0.2074 | -121.9427 | 0.15773 | 0.19681 | 0.23206 | 0.21551 | -121.9155
3807.5 | 121.9437 | -0.1831 | 121.8155 | 1.4211e-13 | -0.043243 | 0.0067415 | 0.022076 | -0.0079782 | -0.010194 | -0.0022889 | -0.0022175 | 0.022806 | -0.0066594 | 0.024198 | 0.010783 | 0.046831 | 0.001407 | -0.008409 | 0.020079 | -0.00422 | 0.10076 | -0.13632 | 0.037677 | -0.00422 | -0.042615 | -0.04369 | -0.004608 | 0.021486 | -0.10462 | 0.046785 | -121.7954 | 0.22994 | 0.1747 | 0.12791 | -121.8197 | -121.7147 | 0.078481 | -121.8592 | 0.22078 | 0.14049 | 0.062009 | -121.8201 | -121.794 | 0.20318 | 0.17888 | 0.28386 | 0.18451 | -121.9518 | 0.13941 | 0.1785 | 0.20459 | 0.17888 | -121.9201
3809.2812 | 122.0673 | -0.12817 | 121.7972 | 1.4211e-13 | -0.04303 | 0.0071689 | 0.022076 | -0.0079782 | -0.010194 | -0.02518 | -0.0024313 | 0.022592 | -0.0066594 | 0.023985 | 0.010356 | 0.037675 | 0.010564 | -0.012988 | 0.024657 | -0.00422 | 0.10076 | -0.1409 | 0.046835 | 0.000359 | -0.047194 | -0.04369 | -0.018344 | 0.021486 | -0.10004 | -0.012725 | -121.7725 | 0.16585 | 0.11519 | 0.12791 | -121.8014 | -121.6964 | 0.028129 | -121.8409 | 0.17501 | 0.08098 | 0.052851 | -121.8155 | -121.7757 | 0.15283 | 0.12395 | 0.22893 | 0.13874 | -121.9381 | 0.084484 | 0.10983 | 0.14966 | 0.12853 | -121.8972
3811.0625 | 121.9849 | -0.16022 | 121.7926 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022289 | -0.0081918 | -0.010621 | -0.0099194 | -0.0022175 | 0.022592 | -0.0066594 | 0.023985 | 0.010569 | 0.042253 | -0.003172 | -0.017566 | 0.020079 | -0.008799 | 0.09618 | -0.13632 | 0.037677 | 0.004938 | -0.047194 | -0.048268 | -0.009187 | 0.021486 | -0.10462 | 0.023897 | -121.7725 | 0.20247 | 0.14265 | 0.11875 | -121.8014 | -121.6964 | 0.055593 | -121.8409 | 0.19789 | 0.11302 | 0.05743 | -121.8018 | -121.7711 | 0.1803 | 0.15142 | 0.2564 | 0.15704 | -121.9289 | 0.11195 | 0.15103 | 0.1817 | 0.16515 | -121.8972
3812.8594 | 121.9437 | -0.19226 | 121.8384 | 1.4211e-13 | -0.04303 | 0.0071689 | 0.021862 | -0.0081918 | -0.010408 | -0.0099194 | -0.0022175 | 0.022592 | -0.0064458 | 0.024198 | 0.010569 | 0.046831 | 0.005985 | -0.017566 | 0.020079 | -0.013378 | 0.10076 | -0.14548 | 0.042256 | -0.00422 | -0.042615 | -0.048268 | -0.013765 | 0.021486 | -0.10004 | 0.046783 | -121.8183 | 0.23909 | 0.17469 | 0.12791 | -121.8518 | -121.7376 | 0.092216 | -121.8866 | 0.23452 | 0.14965 | 0.05743 | -121.8521 | -121.8169 | 0.21234 | 0.17888 | 0.29302 | 0.19825 | -121.9839 | 0.14399 | 0.1785 | 0.21375 | 0.18804 | -121.9384
3814.5625 | 121.9803 | -0.16937 | 121.8063 | 1.4211e-13 | -0.043243 | 0.0067415 | 0.022503 | -0.0084056 | -0.010408 | -0.0022889 | -0.0017903 | 0.022592 | -0.0066594 | 0.024198 | 0.010569 | 0.042253 | 0.001407 | -0.012988 | 0.020079 | -0.00422 | 0.10076 | -0.1409 | 0.042256 | -0.00422 | -0.038036 | -0.052847 | -0.013765 | 0.016908 | -0.10004 | 0.028474 | -121.7863 | 0.21163 | 0.15638 | 0.12791 | -121.8106 | -121.7056 | 0.069328 | -121.8592 | 0.21163 | 0.13134 | 0.062009 | -121.8201 | -121.7894 | 0.18945 | 0.16515 | 0.27013 | 0.17078 | -121.9472 | 0.11653 | 0.15561 | 0.18628 | 0.16515 | -121.9064
3816.3438 | 122.0535 | -0.14191 | 121.8109 | 1.4211e-13 | -0.043457 | 0.0065279 | 0.022076 | -0.0079782 | -0.010621 | -0.0022889 | -0.0020039 | 0.022592 | -0.0064458 | 0.023985 | 0.010356 | 0.046831 | -0.007751 | -0.017566 | 0.015501 | -0.00422 | 0.10534 | -0.1409 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.004608 | 0.016908 | -0.10004 | 0.001008 | -121.7954 | 0.18874 | 0.12434 | 0.12333 | -121.8151 | -121.7056 | 0.041862 | -121.8592 | 0.18416 | 0.099292 | 0.05743 | -121.8155 | -121.794 | 0.15741 | 0.13769 | 0.24724 | 0.13416 | -121.9518 | 0.093639 | 0.1373 | 0.15882 | 0.14227 | -121.911
3818.0469 | 121.9666 | -0.17853 | 121.8338 | 1.4211e-13 | -0.04303 | 0.0065279 | 0.022503 | -0.0077646 | -0.010408 | 0.012972 | -0.0020039 | 0.022592 | -0.006873 | 0.023985 | 0.010142 | 0.042253 | -0.007751 | -0.022144 | 0.020079 | -0.00422 | 0.10992 | -0.13174 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.012329 | -0.10004 | 0.046787 | -121.8137 | 0.22078 | 0.15638 | 0.1096 | -121.838 | -121.7239 | 0.078483 | -121.8821 | 0.22078 | 0.13591 | 0.05743 | -121.843 | -121.8215 | 0.19861 | 0.17431 | 0.28844 | 0.17078 | -121.9655 | 0.13026 | 0.16934 | 0.19086 | 0.17889 | -121.9338
3819.8438 | 121.994 | -0.17395 | 121.8384 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022289 | -0.0077646 | -0.010408 | -0.0099194 | -0.0020039 | 0.023019 | -0.0064458 | 0.023985 | 0.010356 | 0.05141 | 0.001407 | -0.017566 | 0.020079 | -0.00422 | 0.09618 | -0.13632 | 0.033099 | 0.000359 | -0.042615 | -0.052847 | 0.004549 | 0.021486 | -0.1092 | 0.03763 | -121.8183 | 0.22536 | 0.15638 | 0.11875 | -121.8426 | -121.7422 | 0.064747 | -121.8912 | 0.20705 | 0.13133 | 0.066588 | -121.8338 | -121.8169 | 0.19403 | 0.16973 | 0.27013 | 0.17536 | -121.9747 | 0.1211 | 0.1785 | 0.19544 | 0.17431 | -121.9476
3821.625 | 121.994 | -0.16937 | 121.8567 | 1.4211e-13 | -0.043243 | 0.0067415 | 0.022503 | -0.0084056 | -0.010408 | -0.01755 | -0.0017903 | 0.022806 | -0.0066594 | 0.024198 | 0.010569 | 0.046831 | 0.005985 | -0.017566 | 0.020079 | 0.000359 | 0.10534 | -0.14548 | 0.042256 | 0.000359 | -0.033458 | -0.052847 | -0.004608 | 0.021486 | -0.1092 | 0.023895 | -121.8366 | 0.2162 | 0.15181 | 0.12791 | -121.8563 | -121.7514 | 0.06017 | -121.9095 | 0.21163 | 0.13592 | 0.075745 | -121.8613 | -121.8352 | 0.18945 | 0.16973 | 0.27471 | 0.17536 | -122.0022 | 0.11653 | 0.16476 | 0.19086 | 0.16973 | -121.9659
3823.3906 | 122.0581 | -0.15106 | 121.8155 | 1.4211e-13 | -0.043243 | 0.0063141 | 0.022503 | -0.0079782 | -0.010194 | -0.0099194 | -0.0020039 | 0.023019 | -0.0064458 | 0.024198 | 0.010783 | 0.046831 | -0.003172 | -0.012988 | 0.020079 | -0.008799 | 0.10076 | -0.1409 | 0.042256 | 0.000359 | -0.042615 | -0.057425 | -0.009187 | 0.016908 | -0.10004 | 0.010163 | -121.7954 | 0.19789 | 0.13807 | 0.12791 | -121.8243 | -121.7147 | 0.051017 | -121.8729 | 0.19332 | 0.10845 | 0.05743 | -121.8247 | -121.7986 | 0.17114 | 0.14226 | 0.25182 | 0.14789 | -121.9564 | 0.093637 | 0.14188 | 0.16797 | 0.15142 | -121.9155
3825.1875 | 122.0215 | -0.16937 | 121.8521 | 1.4211e-13 | -0.043243 | 0.0069553 | 0.022289 | -0.0079782 | -0.010408 | -0.01755 | -0.0022175 | 0.022592 | -0.0066594 | 0.024198 | 0.010569 | 0.046831 | -0.003172 | -0.012988 | 0.020079 | 0.004938 | 0.10076 | -0.13632 | 0.037677 | 0.000359 | -0.038036 | -0.048268 | -0.009187 | 0.021486 | -0.10462 | 0.033053 | -121.832 | 0.2162 | 0.15638 | 0.12333 | -121.8472 | -121.7514 | 0.064749 | -121.9004 | 0.20705 | 0.13134 | 0.066588 | -121.8613 | -121.8306 | 0.18945 | 0.17431 | 0.27013 | 0.1662 | -121.9884 | 0.1211 | 0.16019 | 0.19086 | 0.16973 | -121.9567
3826.9062 | 122.113 | -0.13275 | 121.8246 | 1.4211e-13 | -0.043243 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0022889 | -0.0020039 | 0.022592 | -0.006873 | 0.023985 | 0.010569 | 0.05141 | 0.001407 | -0.012988 | 0.029236 | 0.000359 | 0.09618 | -0.13632 | 0.037677 | -0.00422 | -0.047194 | -0.048268 | -0.009187 | 0.016908 | -0.1092 | -0.003569 | -121.7954 | 0.18416 | 0.11976 | 0.12333 | -121.8243 | -121.7285 | 0.023548 | -121.8729 | 0.17043 | 0.085557 | 0.062009 | -121.8338 | -121.8077 | 0.16199 | 0.13311 | 0.22893 | 0.13416 | -121.961 | 0.084483 | 0.12356 | 0.14966 | 0.12853 | -121.9338
3828.7031 | 122.1176 | -0.14648 | 121.8201 | 1.4211e-13 | -0.043243 | 0.0067415 | 0.022503 | -0.0079782 | -0.010408 | -0.01755 | -0.0020039 | 0.022592 | -0.0064458 | 0.023985 | 0.010356 | 0.05141 | -0.003172 | -0.017566 | 0.024657 | -0.00422 | 0.10534 | -0.14548 | 0.037677 | 0.000359 | -0.033458 | -0.048268 | -0.009187 | 0.026065 | -0.10462 | 0.001006 | -121.7954 | 0.19789 | 0.12892 | 0.12791 | -121.8243 | -121.7147 | 0.04186 | -121.8683 | 0.18416 | 0.11303 | 0.071166 | -121.8293 | -121.794 | 0.17114 | 0.14226 | 0.25182 | 0.14331 | -121.9655 | 0.098216 | 0.1373 | 0.17255 | 0.14684 | -121.9247
3830.4062 | 122.1313 | -0.15106 | 121.8109 | 1.4211e-13 | -0.043243 | 0.0069553 | 0.022503 | -0.0079782 | -0.010835 | -0.02518 | -0.0022175 | 0.022592 | -0.0062322 | 0.024198 | 0.010356 | 0.046831 | 0.001407 | -0.022144 | 0.015501 | 0.004938 | 0.10076 | -0.13632 | 0.037677 | 0.000359 | -0.038036 | -0.04369 | -0.004608 | 0.016908 | -0.10462 | 0.014742 | -121.7954 | 0.19789 | 0.12892 | 0.11418 | -121.806 | -121.7102 | 0.046438 | -121.8546 | 0.18874 | 0.11303 | 0.066588 | -121.8155 | -121.794 | 0.16656 | 0.156 | 0.25182 | 0.15247 | -121.9472 | 0.10737 | 0.14645 | 0.16797 | 0.15142 | -121.9155
3832.1875 | 121.962 | -0.1831 | 121.875 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022289 | -0.0084056 | -0.010835 | -0.0099194 | -0.0022175 | 0.023233 | -0.0066594 | 0.023985 | 0.010142 | 0.046831 | -0.003172 | -0.022144 | 0.015501 | -0.008799 | 0.091601 | -0.13632 | 0.037677 | 0.004938 | -0.033458 | -0.052847 | -0.009187 | 0.030644 | -0.1092 | 0.046785 | -121.8595 | 0.22994 | 0.16096 | 0.11418 | -121.8838 | -121.7834 | 0.073902 | -121.9278 | 0.22078 | 0.14965 | 0.075745 | -121.8842 | -121.8444 | 0.19861 | 0.17431 | 0.27471 | 0.17993 | -122.0113 | 0.13026 | 0.17392 | 0.21375 | 0.18804 | -121.9842
3833.9688 | 122.0856 | -0.15106 | 121.843 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022503 | -0.0079782 | -0.010621 | -0.0099194 | -0.0022175 | 0.022806 | -0.0064458 | 0.023985 | 0.010569 | 0.046831 | -0.003172 | -0.017566 | 0.024657 | -0.00422 | 0.10076 | -0.13632 | 0.042256 | 0.004938 | -0.047194 | -0.052847 | -0.009187 | 0.021486 | -0.10004 | 0.014742 | -121.8183 | 0.19789 | 0.1335 | 0.11875 | -121.8472 | -121.7422 | 0.051017 | -121.8958 | 0.19332 | 0.10387 | 0.052851 | -121.8521 | -121.8215 | 0.17572 | 0.14684 | 0.25182 | 0.14789 | -121.9793 | 0.098215 | 0.14188 | 0.17255 | 0.156 | -121.943
3835.7656 | 122.1451 | -0.13733 | 121.8201 | 1.4211e-13 | -0.04303 | 0.0065279 | 0.022076 | -0.0079782 | -0.010835 | -0.01755 | -0.0017903 | 0.022592 | -0.006873 | 0.024412 | 0.010569 | 0.042253 | -0.007751 | -0.022144 | 0.024657 | -0.00422 | 0.10076 | -0.1409 | 0.046835 | 0.004938 | -0.042615 | -0.04369 | -0.009187 | 0.016908 | -0.1092 | -0.00357 | -121.7954 | 0.17958 | 0.11519 | 0.11875 | -121.8243 | -121.7193 | 0.028126 | -121.8638 | 0.18416 | 0.094714 | 0.066588 | -121.8293 | -121.8032 | 0.16199 | 0.13311 | 0.23809 | 0.12958 | -121.961 | 0.093639 | 0.12814 | 0.15424 | 0.14227 | -121.9293
3837.5469 | 122.1039 | -0.14191 | 121.8246 | 1.4211e-13 | -0.043243 | 0.0071689 | 0.022076 | -0.0084056 | -0.010621 | -0.0022889 | -0.0020039 | 0.022592 | -0.006873 | 0.023985 | 0.010569 | 0.042253 | 0.005985 | -0.022144 | 0.020079 | -0.00422 | 0.10534 | -0.1409 | 0.042256 | 0.000359 | -0.038036 | -0.052847 | 0.004549 | 0.016908 | -0.10004 | 0.001008 | -121.8046 | 0.18416 | 0.11976 | 0.11875 | -121.8289 | -121.7193 | 0.041862 | -121.8775 | 0.18416 | 0.10387 | 0.062009 | -121.8201 | -121.8077 | 0.16199 | 0.13769 | 0.24724 | 0.14789 | -121.9655 | 0.08906 | 0.14646 | 0.15882 | 0.14227 | -121.9247
3839.2812 | 122.0627 | -0.16022 | 121.875 | 1.4211e-13 | -0.043243 | 0.0065279 | 0.022289 | -0.0081918 | -0.010408 | -0.02518 | -0.0022175 | 0.022592 | -0.0066594 | 0.024412 | 0.010569 | 0.042253 | -0.003172 | -0.017566 | 0.010922 | 0.000359 | 0.10076 | -0.13632 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.004608 | 0.021486 | -0.1092 | 0.023897 | -121.8641 | 0.20247 | 0.14265 | 0.11875 | -121.8746 | -121.7742 | 0.051014 | -121.9233 | 0.20247 | 0.1176 | 0.066588 | -121.8796 | -121.8535 | 0.17114 | 0.16058 | 0.26098 | 0.15704 | -122.0113 | 0.11195 | 0.15561 | 0.1817 | 0.16058 | -121.9842
3841.0781 | 122.0215 | -0.19226 | 121.9025 | 1.4211e-13 | -0.043243 | 0.0065279 | 0.022503 | -0.0084056 | -0.010621 | -0.0022889 | -0.0017903 | 0.023019 | -0.006873 | 0.023985 | 0.010569 | 0.037675 | -0.003172 | -0.022144 | 0.020079 | -0.00422 | 0.09618 | -0.1409 | 0.046835 | 0.000359 | -0.042615 | -0.052847 | -0.009187 | 0.026065 | -0.10004 | 0.051362 | -121.8824 | 0.22994 | 0.17012 | 0.11875 | -121.9067 | -121.8063 | 0.092216 | -121.9553 | 0.2391 | 0.14965 | 0.05743 | -121.9117 | -121.8764 | 0.21234 | 0.18804 | 0.28844 | 0.18909 | -122.0434 | 0.13941 | 0.18307 | 0.21833 | 0.19262 | -122.0025
3842.875 | 122.1359 | -0.14191 | 121.8475 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022076 | -0.0081918 | -0.0099803 | 0.0053411 | -0.0020039 | 0.022806 | -0.0070868 | 0.024198 | 0.010569 | 0.042253 | -0.003172 | -0.017566 | 0.015501 | -0.00422 | 0.09618 | -0.1409 | 0.037677 | -0.00422 | -0.047194 | -0.04369 | -0.009187 | 0.012329 | -0.10462 | 0.001008 | -121.832 | 0.18416 | 0.12434 | 0.12333 | -121.8518 | -121.7514 | 0.037283 | -121.8912 | 0.17958 | 0.094713 | 0.05743 | -121.8567 | -121.8352 | 0.15741 | 0.13769 | 0.23809 | 0.13873 | -121.9884 | 0.098217 | 0.13272 | 0.15424 | 0.13769 | -121.9522
3844.5938 | 122.0352 | -0.18768 | 121.9162 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022289 | -0.0081918 | -0.010194 | -0.0099194 | -0.0020039 | 0.022592 | -0.0066594 | 0.024198 | 0.010356 | 0.042253 | -0.003172 | -0.017566 | 0.024657 | -0.008799 | 0.09618 | -0.14548 | 0.046835 | 0.000359 | -0.038036 | -0.04369 | -0.004608 | 0.016908 | -0.10462 | 0.042205 | -121.8915 | 0.22994 | 0.17012 | 0.12791 | -121.925 | -121.82 | 0.083059 | -121.9599 | 0.23452 | 0.14965 | 0.066588 | -121.9208 | -121.8993 | 0.21234 | 0.17888 | 0.28386 | 0.18451 | -122.0617 | 0.14399 | 0.18307 | 0.20459 | 0.18804 | -122.0208
3846.375 | 122.0306 | -0.19684 | 121.9162 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | -0.0022889 | -0.0020039 | 0.022806 | -0.0066594 | 0.024412 | 0.010356 | 0.046831 | -0.012329 | -0.022144 | 0.024657 | -0.00422 | 0.10076 | -0.13174 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.065097 | -121.8915 | 0.24367 | 0.17469 | 0.1096 | -121.9204 | -121.8154 | 0.092214 | -121.9645 | 0.23909 | 0.15422 | 0.062009 | -121.9254 | -121.8993 | 0.22149 | 0.19262 | 0.2976 | 0.18451 | -122.0479 | 0.14857 | 0.18765 | 0.21375 | 0.1972 | -122.0208
3848.1719 | 122.1405 | -0.14648 | 121.8475 | 1.4211e-13 | -0.043457 | 0.0065279 | 0.022289 | -0.0079782 | -0.010621 | -0.0022889 | -0.0024313 | 0.022592 | -0.0066594 | 0.024198 | 0.010356 | 0.05141 | -0.007751 | -0.017566 | 0.020079 | -0.017957 | 0.10534 | -0.1409 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.018344 | 0.021486 | -0.10462 | 0.005585 | -121.8275 | 0.19789 | 0.12892 | 0.12333 | -121.8655 | -121.7422 | 0.04186 | -121.8958 | 0.18874 | 0.10387 | 0.062009 | -121.8659 | -121.826 | 0.16656 | 0.12853 | 0.25182 | 0.13873 | -121.9884 | 0.098216 | 0.12814 | 0.16797 | 0.14684 | -121.9522
3849.9531 | 122.1634 | -0.14648 | 121.8704 | 1.4211e-13 | -0.043671 | 0.0067415 | 0.022289 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022592 | -0.0062322 | 0.023985 | 0.010356 | 0.042253 | -0.003172 | -0.017566 | 0.015501 | -0.00422 | 0.09618 | -0.1409 | 0.042256 | -0.00422 | -0.042615 | -0.048268 | -0.013765 | 0.021486 | -0.1092 | 0.005585 | -121.8549 | 0.18874 | 0.12892 | 0.12333 | -121.8746 | -121.7742 | 0.037281 | -121.9187 | 0.18874 | 0.10387 | 0.066588 | -121.8842 | -121.8489 | 0.16198 | 0.14226 | 0.24266 | 0.14331 | -122.0113 | 0.098216 | 0.13272 | 0.16797 | 0.14226 | -121.9796
3851.6719 | 122.0673 | -0.16937 | 121.8887 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022076 | -0.0079782 | -0.010621 | -0.0022889 | -0.0020039 | 0.022378 | -0.0066594 | 0.024198 | 0.010142 | 0.042253 | -0.007751 | -0.012988 | 0.020079 | -0.008799 | 0.09618 | -0.13632 | 0.042256 | 0.000359 | -0.047194 | -0.04369 | -0.009187 | 0.016908 | -0.10462 | 0.033053 | -121.8687 | 0.21163 | 0.15638 | 0.12333 | -121.8975 | -121.7926 | 0.064749 | -121.9324 | 0.21163 | 0.12218 | 0.05743 | -121.8979 | -121.8718 | 0.18945 | 0.16057 | 0.26555 | 0.16162 | -122.0251 | 0.12568 | 0.16019 | 0.18628 | 0.16973 | -121.9934
3853.4531 | 122.1039 | -0.15106 | 121.8658 | 1.4211e-13 | -0.043457 | 0.0065279 | 0.022289 | -0.0077646 | -0.010408 | -0.0022889 | -0.0017903 | 0.022806 | -0.0062322 | 0.023985 | 0.010569 | 0.05141 | -0.007751 | -0.017566 | 0.020079 | -0.00422 | 0.10076 | -0.13632 | 0.037677 | -0.00422 | -0.038036 | -0.048268 | -0.009187 | 0.021486 | -0.11378 | 0.014742 | -121.8458 | 0.20247 | 0.1335 | 0.11875 | -121.8701 | -121.7651 | 0.03728 | -121.9141 | 0.18874 | 0.11303 | 0.075746 | -121.875 | -121.8444 | 0.17114 | 0.14684 | 0.25182 | 0.14331 | -122.0022 | 0.10279 | 0.14188 | 0.17255 | 0.14684 | -121.9796
3855.1875 | 122.0352 | -0.19684 | 121.8933 | 1.4211e-13 | -0.044312 | 0.0067415 | 0.022503 | -0.0081918 | -0.010194 | -0.0022889 | -0.0020039 | 0.022806 | -0.006873 | 0.024198 | 0.010569 | 0.05141 | -0.003172 | -0.022144 | 0.024657 | -0.008799 | 0.09618 | -0.1409 | 0.042256 | 0.000359 | -0.042615 | -0.04369 | -0.013765 | 0.021486 | -0.10462 | 0.055939 | -121.8687 | 0.24825 | 0.17469 | 0.11875 | -121.9021 | -121.7971 | 0.092214 | -121.937 | 0.23909 | 0.15422 | 0.062009 | -121.9071 | -121.8718 | 0.22149 | 0.18804 | 0.29302 | 0.19367 | -122.0342 | 0.15315 | 0.18307 | 0.21832 | 0.1972 | -121.9979
3856.9844 | 122.0398 | -0.16479 | 121.8842 | 1.4211e-13 | -0.043457 | 0.0065279 | 0.021862 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.0066594 | 0.024198 | 0.010356 | 0.055988 | 0.001407 | -0.017566 | 0.024657 | 0.000359 | 0.09618 | -0.1409 | 0.033099 | 0.000359 | -0.042615 | -0.04369 | -0.004608 | 0.021486 | -0.10462 | 0.023896 | -121.8595 | 0.22078 | 0.14723 | 0.12333 | -121.8838 | -121.788 | 0.060171 | -121.9278 | 0.19789 | 0.12218 | 0.062009 | -121.8888 | -121.8627 | 0.18945 | 0.16515 | 0.26098 | 0.1662 | -122.0251 | 0.1211 | 0.16019 | 0.18628 | 0.16515 | -121.9888
3858.7812 | 122.168 | -0.14648 | 121.8887 | 1.4211e-13 | -0.043457 | 0.0069553 | 0.022076 | -0.0081918 | -0.010194 | -0.0099194 | -0.0020039 | 0.022806 | -0.0064458 | 0.024198 | 0.010142 | 0.042253 | -0.007751 | -0.022144 | 0.020079 | -0.008799 | 0.09618 | -0.1409 | 0.037677 | 0.000359 | -0.042615 | -0.052847 | -0.009187 | 0.016908 | -0.10462 | 0.005585 | -121.8687 | 0.18874 | 0.12434 | 0.11875 | -121.8975 | -121.7926 | 0.04186 | -121.9416 | 0.18416 | 0.10387 | 0.062009 | -121.8979 | -121.8718 | 0.16656 | 0.13769 | 0.24266 | 0.13873 | -122.0296 | 0.093637 | 0.1373 | 0.16339 | 0.14684 | -121.9934
3860.5781 | 122.113 | -0.16022 | 121.8887 | 1.4211e-13 | -0.043671 | 0.0067415 | 0.022289 | -0.0084056 | -0.010621 | -0.0099194 | -0.0020039 | 0.022806 | -0.006873 | 0.024412 | 0.010356 | 0.042253 | -0.012329 | -0.017566 | 0.015501 | -0.008799 | 0.10076 | -0.13632 | 0.042256 | -0.00422 | -0.038036 | -0.048268 | -2.9e-05 | 0.035222 | -0.10004 | 0.023897 | -121.8732 | 0.20247 | 0.14265 | 0.11875 | -121.8975 | -121.788 | 0.060172 | -121.937 | 0.20247 | 0.12218 | 0.062009 | -121.8888 | -121.8535 | 0.17572 | 0.15142 | 0.26098 | 0.14789 | -122.0251 | 0.11195 | 0.16019 | 0.19544 | 0.156 | -121.9888
3862.375 | 122.0947 | -0.17853 | 121.907 | 1.4211e-13 | -0.043671 | 0.0065279 | 0.022289 | -0.0079782 | -0.010621 | -0.0022889 | -0.0017903 | 0.022592 | -0.0064458 | 0.024198 | 0.0099284 | 0.042253 | -0.007751 | -0.026723 | 0.020079 | -0.008799 | 0.091601 | -0.14548 | 0.033099 | -0.00422 | -0.038036 | -0.048268 | -0.009187 | 0.026065 | -0.10004 | 0.03305 | -121.887 | 0.22078 | 0.1518 | 0.11875 | -121.9158 | -121.8154 | 0.078483 | -121.9553 | 0.21163 | 0.14049 | 0.062009 | -121.9162 | -121.881 | 0.19861 | 0.16973 | 0.27013 | 0.17078 | -122.0525 | 0.13026 | 0.16934 | 0.20459 | 0.17431 | -122.0071
3864.0938 | 122.1863 | -0.13275 | 121.9116 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022076 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.006873 | 0.024198 | 0.010142 | 0.042253 | -0.012329 | -0.017566 | 0.020079 | -0.00422 | 0.09618 | -0.1409 | 0.037677 | 0.000359 | -0.042615 | -0.04369 | -2.9e-05 | 0.026065 | -0.10462 | -0.008148 | -121.8915 | 0.175 | 0.11519 | 0.12333 | -121.9158 | -121.8154 | 0.028127 | -121.9553 | 0.17043 | 0.090136 | 0.062009 | -121.9116 | -121.8856 | 0.15283 | 0.12853 | 0.22893 | 0.12042 | -122.0525 | 0.089061 | 0.13272 | 0.15882 | 0.13311 | -122.0162
3865.8906 | 122.1039 | -0.16937 | 121.9208 | 1.4211e-13 | -0.04303 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022592 | -0.0066594 | 0.024198 | 0.0099284 | 0.046831 | -0.003172 | -0.012988 | 0.010922 | -0.008799 | 0.09618 | -0.14548 | 0.037677 | 0.004938 | -0.042615 | -0.04369 | 0.004549 | 0.021486 | -0.1092 | 0.023895 | -121.9099 | 0.2162 | 0.15638 | 0.13249 | -121.9296 | -121.8246 | 0.06017 | -121.9645 | 0.20705 | 0.12676 | 0.066588 | -121.9162 | -121.8993 | 0.18029 | 0.16057 | 0.26555 | 0.1662 | -122.0663 | 0.12568 | 0.17392 | 0.19086 | 0.17431 | -122.03
3867.6719 | 122.1542 | -0.15106 | 121.9162 | 1.4211e-13 | -0.043671 | 0.0063141 | 0.022289 | -0.0084056 | -0.010194 | 0.0053411 | -0.0022175 | 0.023019 | -0.0066594 | 0.024412 | 0.010569 | 0.046831 | -0.007751 | -0.022144 | 0.015501 | -0.008799 | 0.09618 | -0.14548 | 0.042256 | 0.004938 | -0.033458 | -0.052847 | -0.013765 | 0.021486 | -0.095467 | 0.005584 | -121.9007 | 0.19789 | 0.12892 | 0.12333 | -121.925 | -121.82 | 0.055595 | -121.969 | 0.19332 | 0.1176 | 0.062009 | -121.93 | -121.8947 | 0.16656 | 0.14226 | 0.24724 | 0.14331 | -122.0617 | 0.098215 | 0.1373 | 0.17255 | 0.156 | -122.0117
3869.4531 | 122.0673 | -0.20599 | 121.9666 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.021862 | -0.0079782 | -0.010621 | -0.0099194 | -0.0020039 | 0.022806 | -0.0066594 | 0.024198 | 0.010142 | 0.042253 | -0.007751 | -0.026723 | 0.010922 | -0.008799 | 0.10076 | -0.15006 | 0.037677 | -0.00422 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.1092 | 0.055937 | -121.9556 | 0.24825 | 0.17927 | 0.12333 | -121.9754 | -121.8658 | 0.096791 | -122.0148 | 0.24367 | 0.16338 | 0.066588 | -121.9757 | -121.9451 | 0.21692 | 0.1972 | 0.30675 | 0.19824 | -122.1166 | 0.15773 | 0.19681 | 0.22748 | 0.20177 | -122.0758
3871.1719 | 122.1039 | -0.17853 | 121.9208 | 1.4211e-13 | -0.043884 | 0.0065279 | 0.022503 | -0.0084056 | -0.010621 | -0.0022889 | -0.0020039 | 0.022592 | -0.006873 | 0.024626 | 0.010356 | 0.037675 | -0.012329 | -0.022144 | 0.020079 | -0.008799 | 0.10534 | -0.1409 | 0.042256 | 0.004938 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.1092 | 0.037629 | -121.9007 | 0.2162 | 0.15638 | 0.11875 | -121.9296 | -121.8154 | 0.069325 | -121.969 | 0.22078 | 0.13591 | 0.066588 | -121.93 | -121.8993 | 0.19861 | 0.16973 | 0.28386 | 0.1662 | -122.0617 | 0.13026 | 0.16934 | 0.20001 | 0.18347 | -122.03
3872.9531 | 122.2046 | -0.14648 | 121.9025 | 1.4211e-13 | -0.043671 | 0.0067415 | 0.022503 | -0.0077646 | -0.010408 | -0.0099194 | -0.0017903 | 0.022806 | -0.006873 | 0.024412 | 0.010356 | 0.037675 | -0.007751 | -0.017566 | 0.020079 | -0.008799 | 0.09618 | -0.15006 | 0.042256 | -0.00422 | -0.047194 | -0.04369 | -0.013765 | 0.026065 | -0.1092 | -0.003573 | -121.8824 | 0.18416 | 0.12892 | 0.13249 | -121.9113 | -121.8063 | 0.037281 | -121.9462 | 0.18874 | 0.09929 | 0.062009 | -121.9162 | -121.8764 | 0.16656 | 0.13769 | 0.24266 | 0.13873 | -122.0525 | 0.10279 | 0.13272 | 0.17255 | 0.14226 | -122.0117
3874.75 | 122.113 | -0.1831 | 121.9574 | 1.4211e-13 | -0.043884 | 0.0065279 | 0.022076 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022592 | -0.0066594 | 0.023985 | 0.010142 | 0.046831 | -0.012329 | -0.012988 | 0.010922 | -0.008799 | 0.10076 | -0.14548 | 0.037677 | 0.000359 | -0.047194 | -0.048268 | -0.004608 | 0.016908 | -0.1092 | 0.037627 | -121.9465 | 0.22994 | 0.17012 | 0.13249 | -121.9662 | -121.8566 | 0.073902 | -122.0057 | 0.22078 | 0.13591 | 0.062009 | -121.962 | -121.9405 | 0.19403 | 0.17431 | 0.28386 | 0.17078 | -122.1029 | 0.13484 | 0.1785 | 0.20001 | 0.18346 | -122.0666
3876.4688 | 122.113 | -0.20142 | 121.9666 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022289 | -0.0079782 | -0.010621 | -0.0099194 | -0.0022175 | 0.022592 | -0.0066594 | 0.024412 | 0.010356 | 0.05141 | -0.012329 | -0.017566 | 0.010922 | -0.008799 | 0.10076 | -0.14548 | 0.046835 | 0.009516 | -0.042615 | -0.052847 | -0.009187 | 0.016908 | -0.10462 | 0.055938 | -121.9556 | 0.25283 | 0.18385 | 0.12791 | -121.9754 | -121.8658 | 0.096792 | -122.0194 | 0.24825 | 0.1588 | 0.062009 | -121.9757 | -121.9496 | 0.21234 | 0.19262 | 0.30218 | 0.18909 | -122.112 | 0.14857 | 0.19223 | 0.21832 | 0.21093 | -122.0712
3878.2656 | 122.1268 | -0.1831 | 121.9666 | 1.4211e-13 | -0.043671 | 0.0065279 | 0.022289 | -0.0084056 | -0.010408 | 0.0053411 | -0.0020039 | 0.022378 | -0.0064458 | 0.024412 | 0.010356 | 0.046831 | -0.012329 | -0.017566 | 0.015501 | -0.00422 | 0.091601 | -0.1409 | 0.046835 | -0.00422 | -0.028879 | -0.052847 | -0.013765 | 0.012329 | -0.1092 | 0.042206 | -121.9511 | 0.22994 | 0.16554 | 0.12333 | -121.9708 | -121.875 | 0.073902 | -122.0194 | 0.22994 | 0.15423 | 0.080324 | -121.9803 | -121.9542 | 0.19861 | 0.17888 | 0.27471 | 0.17078 | -122.1075 | 0.13026 | 0.16934 | 0.19543 | 0.17888 | -122.0758
3880 | 122.0718 | -0.17853 | 121.9666 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | -0.0022889 | -0.0022175 | 0.022592 | -0.0070868 | 0.024198 | 0.010142 | 0.042253 | -0.007751 | -0.017566 | 0.015501 | -0.00422 | 0.09618 | -0.14548 | 0.042256 | 0.004938 | -0.038036 | -0.057425 | -2.9e-05 | 0.012329 | -0.10462 | 0.03305 | -121.9511 | 0.22078 | 0.16096 | 0.12791 | -121.9708 | -121.8704 | 0.073904 | -122.024 | 0.22078 | 0.14049 | 0.066588 | -121.9666 | -121.9542 | 0.19403 | 0.17431 | 0.27471 | 0.17078 | -122.112 | 0.1211 | 0.1785 | 0.19086 | 0.18347 | -122.0712
3881.7812 | 122.2092 | -0.14191 | 121.9437 | 1.4211e-13 | -0.043884 | 0.0071689 | 0.022503 | -0.0079782 | -0.010408 | -0.0022889 | -0.0020039 | 0.022592 | -0.006873 | 0.024198 | 0.010142 | 0.046831 | -0.012329 | -0.022144 | 0.020079 | -0.013378 | 0.09618 | -0.14548 | 0.042256 | 0.000359 | -0.033458 | -0.052847 | -2.9e-05 | 0.016908 | -0.11378 | -0.003571 | -121.9236 | 0.18874 | 0.11976 | 0.12333 | -121.957 | -121.8475 | 0.028125 | -121.9965 | 0.18416 | 0.10845 | 0.080324 | -121.9437 | -121.9268 | 0.16199 | 0.12853 | 0.23809 | 0.12958 | -122.0891 | 0.08906 | 0.14188 | 0.15882 | 0.14227 | -122.0574
3883.5625 | 122.168 | -0.15564 | 121.9574 | 1.4211e-13 | -0.044098 | 0.0067415 | 0.022289 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.0070868 | 0.024198 | 0.010569 | 0.037675 | -0.012329 | -0.022144 | 0.010922 | -0.00422 | 0.09618 | -0.1409 | 0.042256 | 0.000359 | -0.047194 | -0.048268 | -0.004608 | 0.026065 | -0.10004 | 0.014741 | -121.9465 | 0.19332 | 0.1335 | 0.11875 | -121.9616 | -121.8612 | 0.055595 | -122.0057 | 0.1979 | 0.10845 | 0.052851 | -121.962 | -121.9313 | 0.16656 | 0.15142 | 0.25182 | 0.14331 | -122.0983 | 0.10737 | 0.15103 | 0.18171 | 0.156 | -122.0574
3885.375 | 122.1039 | -0.17853 | 121.962 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.022076 | -0.0081918 | -0.010835 | -0.01755 | -0.0022175 | 0.023019 | -0.0066594 | 0.024198 | 0.010142 | 0.046831 | -0.012329 | -0.026723 | 0.020079 | -0.00422 | 0.09618 | -0.1409 | 0.042256 | 0.004938 | -0.038036 | -0.048268 | -0.004608 | 0.012329 | -0.10004 | 0.037629 | -121.9419 | 0.22536 | 0.1518 | 0.11418 | -121.9662 | -121.8658 | 0.078483 | -122.0102 | 0.22078 | 0.14049 | 0.062009 | -121.9666 | -121.9496 | 0.19861 | 0.17431 | 0.27471 | 0.1662 | -122.1029 | 0.13026 | 0.17392 | 0.19086 | 0.18347 | -122.062
3887.0938 | 122.1313 | -0.16479 | 121.9666 | 1.4211e-13 | -0.043457 | 0.0067415 | 0.022289 | -0.0086192 | -0.010621 | -0.0022889 | -0.0017903 | 0.023019 | -0.0064458 | 0.024626 | 0.0099284 | 0.046831 | -0.012329 | -0.022144 | 0.015501 | -0.00422 | 0.091601 | -0.14548 | 0.042256 | -0.00422 | -0.042615 | -0.057425 | -0.009187 | 0.016908 | -0.10462 | 0.019317 | -121.9511 | 0.21163 | 0.14265 | 0.12333 | -121.9708 | -121.875 | 0.060171 | -122.024 | 0.20705 | 0.12218 | 0.062009 | -121.9757 | -121.9496 | 0.1803 | 0.16057 | 0.2564 | 0.15247 | -122.112 | 0.10737 | 0.15561 | 0.1817 | 0.16057 | -122.0712
3888.875 | 122.0947 | -0.18768 | 121.9574 | 1.4211e-13 | -0.043884 | 0.0063141 | 0.022503 | -0.0081918 | -0.010835 | -0.0022889 | -0.0020039 | 0.022378 | -0.006873 | 0.024198 | 0.0097148 | 0.046831 | -0.012329 | -0.022144 | 0.020079 | -0.008799 | 0.09618 | -0.1409 | 0.042256 | -0.00422 | -0.038036 | -0.048268 | -0.004608 | 0.016908 | -0.1092 | 0.046784 | -121.9373 | 0.23451 | 0.16554 | 0.11875 | -121.9662 | -121.8612 | 0.07848 | -122.0057 | 0.22994 | 0.14965 | 0.071167 | -121.962 | -121.9405 | 0.20776 | 0.17888 | 0.28386 | 0.17535 | -122.0983 | 0.13941 | 0.18307 | 0.20459 | 0.18346 | -122.0666
3890.6562 | 122.1542 | -0.15564 | 121.9528 | 1.4211e-13 | -0.043884 | 0.0065279 | 0.022076 | -0.0081918 | -0.010621 | -0.0099194 | -0.0020039 | 0.022592 | -0.0070868 | 0.024198 | 0.0099284 | 0.037675 | -0.021486 | -0.022144 | 0.020079 | -0.00422 | 0.091601 | -0.14548 | 0.046835 | -0.008798 | -0.042615 | -0.052847 | -0.009187 | 0.030644 | -0.11378 | 0.010162 | -121.9327 | 0.19332 | 0.1335 | 0.12333 | -121.957 | -121.8612 | 0.041858 | -122.0057 | 0.20248 | 0.11303 | 0.071167 | -121.962 | -121.9222 | 0.17572 | 0.15142 | 0.24724 | 0.13415 | -122.0983 | 0.10279 | 0.14645 | 0.18628 | 0.14684 | -122.0666
3892.375 | 122.2321 | -0.16022 | 121.9345 | 1.4211e-13 | -0.043671 | 0.0065279 | 0.021862 | -0.0081918 | -0.010621 | -0.0022889 | -0.0017903 | 0.023019 | -0.0066594 | 0.024412 | 0.0099284 | 0.042253 | -0.016908 | -0.026723 | 0.024657 | -0.00422 | 0.091601 | -0.1409 | 0.046835 | 0.004938 | -0.047194 | -0.048268 | -0.013765 | 0.021486 | -0.10462 | 0.019318 | -121.9099 | 0.20247 | 0.13349 | 0.11418 | -121.9387 | -121.8429 | 0.055593 | -121.9828 | 0.20705 | 0.11302 | 0.05743 | -121.9483 | -121.913 | 0.18487 | 0.156 | 0.25182 | 0.14331 | -122.0754 | 0.11195 | 0.14645 | 0.1817 | 0.16515 | -122.0391
3894.1719 | 122.1725 | -0.15106 | 121.9437 | 1.4211e-13 | -0.043671 | 0.0065279 | 0.022289 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022378 | -0.0066594 | 0.024412 | 0.010356 | 0.042253 | -0.016908 | -0.022144 | 0.020079 | -0.00422 | 0.09618 | -0.14548 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.021486 | -0.10462 | 0.005584 | -121.9236 | 0.19332 | 0.12892 | 0.12333 | -121.9479 | -121.8475 | 0.046438 | -121.9919 | 0.19332 | 0.10845 | 0.062009 | -121.9529 | -121.9222 | 0.17114 | 0.14684 | 0.24724 | 0.13415 | -122.0891 | 0.10279 | 0.14188 | 0.17255 | 0.15142 | -122.0483
3895.9062 | 122.1771 | -0.17395 | 121.9757 | 1.4211e-13 | -0.043243 | 0.0063141 | 0.022289 | -0.0081918 | -0.010194 | 0.012972 | -0.0022175 | 0.022592 | -0.006873 | 0.024412 | 0.010569 | 0.046831 | -0.016908 | -0.026723 | 0.020079 | -0.008799 | 0.10076 | -0.13632 | 0.037677 | 0.004938 | -0.042615 | -0.04369 | -0.013765 | 0.021486 | -0.10462 | 0.03763 | -121.9556 | 0.22078 | 0.14723 | 0.1096 | -121.9845 | -121.8749 | 0.069326 | -122.0194 | 0.21163 | 0.13133 | 0.062009 | -121.9895 | -121.9542 | 0.19403 | 0.16515 | 0.27471 | 0.15704 | -122.112 | 0.13026 | 0.16018 | 0.19544 | 0.17889 | -122.0803
3897.6719 | 122.2366 | -0.11902 | 121.9482 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.022289 | -0.0079782 | -0.0099803 | 0.0053411 | -0.0022175 | 0.022592 | -0.0070868 | 0.024412 | 0.0099284 | 0.046831 | -0.021486 | -0.022144 | 0.020079 | 0.000359 | 0.091601 | -0.1409 | 0.037677 | 0.000359 | -0.038036 | -0.04369 | -0.004608 | 0.030644 | -0.11378 | -0.02188 | -121.9282 | 0.16585 | 0.096875 | 0.11875 | -121.9479 | -121.8566 | 0.005237 | -121.9919 | 0.1567 | 0.080983 | 0.075746 | -121.9528 | -121.9176 | 0.1391 | 0.11938 | 0.21062 | 0.097533 | -122.0891 | 0.075329 | 0.11441 | 0.14966 | 0.11938 | -122.062
3899.3906 | 122.1497 | -0.18768 | 121.9986 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.022076 | -0.0081918 | -0.010621 | -0.0099194 | -0.0024313 | 0.022592 | -0.006873 | 0.024412 | 0.010142 | 0.046831 | -0.016908 | -0.012988 | 0.010922 | -0.013378 | 0.09618 | -0.1409 | 0.037677 | 0.000359 | -0.038036 | -0.052847 | -0.004608 | 0.016908 | -0.10462 | 0.046784 | -121.9877 | 0.23451 | 0.17469 | 0.12791 | -122.012 | -121.9024 | 0.083059 | -122.0514 | 0.22536 | 0.14965 | 0.066588 | -122.0032 | -121.9817 | 0.1986 | 0.1743 | 0.28386 | 0.17077 | -122.1395 | 0.13484 | 0.18307 | 0.20459 | 0.18804 | -122.1032
3901.1719 | 122.1725 | -0.1831 | 121.9894 | 1.4211e-13 | -0.044098 | 0.0069553 | 0.022076 | -0.0081918 | -0.010408 | -0.0099194 | -0.0022175 | 0.022378 | -0.006873 | 0.024412 | 0.010356 | 0.046831 | -0.012329 | -0.017566 | 0.020079 | -0.00422 | 0.10076 | -0.14548 | 0.037677 | -0.00422 | -0.038036 | -0.052847 | -0.013765 | 0.021486 | -0.10462 | 0.037627 | -121.9694 | 0.22994 | 0.16554 | 0.12791 | -121.9937 | -121.8887 | 0.078481 | -122.0423 | 0.22078 | 0.14507 | 0.066588 | -122.0032 | -121.968 | 0.20318 | 0.17888 | 0.28386 | 0.17078 | -122.1349 | 0.13026 | 0.16934 | 0.20459 | 0.17888 | -122.0941
3902.9531 | 122.2412 | -0.15106 | 121.9711 | 1.4211e-13 | -0.044098 | 0.0067415 | 0.021862 | -0.0081918 | -0.010621 | -0.0099194 | -0.0020039 | 0.022806 | -0.006873 | 0.024412 | 0.0099284 | 0.046831 | -0.016908 | -0.022144 | 0.020079 | -0.008799 | 0.091601 | -0.1409 | 0.042256 | -0.00422 | -0.042615 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.010163 | -121.9511 | 0.19789 | 0.12892 | 0.11875 | -121.9799 | -121.8795 | 0.046438 | -122.0194 | 0.19332 | 0.10845 | 0.062009 | -121.9803 | -121.9542 | 0.17114 | 0.14226 | 0.24266 | 0.13415 | -122.112 | 0.10279 | 0.14188 | 0.16797 | 0.14684 | -122.0758
3904.7344 | 122.1268 | -0.16479 | 121.9803 | 1.4211e-13 | -0.043671 | 0.0065279 | 0.022076 | -0.0081918 | -0.010408 | -0.01755 | -0.0020039 | 0.022806 | -0.0066594 | 0.024626 | 0.010356 | 0.037675 | -0.012329 | -0.017566 | 0.015501 | -0.017957 | 0.09618 | -0.15006 | 0.042256 | 0.000359 | -0.033458 | -0.048268 | -0.004608 | 0.030644 | -0.1092 | 0.014738 | -121.9648 | 0.20247 | 0.14723 | 0.13249 | -121.9982 | -121.8841 | 0.055592 | -122.0286 | 0.20705 | 0.13134 | 0.075745 | -121.9849 | -121.9496 | 0.1803 | 0.14684 | 0.26098 | 0.15247 | -122.1303 | 0.11653 | 0.16019 | 0.19544 | 0.16515 | -122.0895
3906.4531 | 122.2137 | -0.11444 | 121.9254 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.022289 | -0.0086192 | -0.010621 | -0.0022889 | -0.0022175 | 0.022806 | -0.0064458 | 0.024626 | 0.010142 | 0.046831 | -0.012329 | -0.022144 | 0.015501 | -0.00422 | 0.091601 | -0.14548 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.004608 | 0.016908 | -0.10004 | -0.031037 | -121.9099 | 0.16127 | 0.092297 | 0.12333 | -121.9296 | -121.8338 | 0.014396 | -121.9736 | 0.1567 | 0.071826 | 0.05743 | -121.93 | -121.9084 | 0.12994 | 0.11022 | 0.20604 | 0.10211 | -122.0708 | 0.066173 | 0.10983 | 0.13135 | 0.1148 | -122.0254
3908.2656 | 122.1268 | -0.19684 | 122.0032 | 1.4211e-13 | -0.044098 | 0.0067415 | 0.022076 | -0.0084056 | -0.010408 | -0.0022889 | -0.0020039 | 0.022592 | -0.0066594 | 0.024839 | 0.0097148 | 0.042253 | -0.026065 | -0.022144 | 0.010922 | -0.00422 | 0.09618 | -0.1409 | 0.037677 | -0.008798 | -0.042615 | -0.048268 | -2.9e-05 | 0.026065 | -0.10462 | 0.055939 | -121.9923 | 0.23909 | 0.17469 | 0.11875 | -122.0074 | -121.907 | 0.092214 | -122.0514 | 0.23452 | 0.15422 | 0.062009 | -122.0032 | -121.9771 | 0.20776 | 0.19262 | 0.29302 | 0.17077 | -122.1441 | 0.14857 | 0.19681 | 0.2229 | 0.18804 | -122.1078
3909.9844 | 122.2549 | -0.13275 | 121.9757 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.021862 | -0.0084056 | -0.010408 | -0.0099194 | -0.0022175 | 0.022378 | -0.006873 | 0.024412 | 0.0099284 | 0.042253 | -0.026065 | -0.022144 | 0.015501 | -0.00422 | 0.10076 | -0.14548 | 0.042256 | 0.000359 | -0.042615 | -0.048268 | -0.009187 | 0.026065 | -0.10462 | -0.012727 | -121.9602 | 0.175 | 0.11061 | 0.12333 | -121.9799 | -121.8749 | 0.028127 | -122.024 | 0.17501 | 0.090136 | 0.062009 | -121.9849 | -121.9496 | 0.14825 | 0.12853 | 0.23351 | 0.10669 | -122.1212 | 0.084483 | 0.12356 | 0.15882 | 0.13311 | -122.0803
3911.7656 | 122.2458 | -0.15106 | 121.9894 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.022076 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022165 | -0.006873 | 0.024412 | 0.0099284 | 0.042253 | -0.016908 | -0.022144 | 0.015501 | -0.00422 | 0.10076 | -0.1409 | 0.037677 | -0.00422 | -0.042615 | -0.048268 | -0.004608 | 0.021486 | -0.10462 | 0.010163 | -121.9739 | 0.19332 | 0.12892 | 0.11875 | -121.9937 | -121.8887 | 0.046438 | -122.0377 | 0.18874 | 0.10845 | 0.062009 | -121.994 | -121.968 | 0.16656 | 0.14684 | 0.25182 | 0.13415 | -122.1303 | 0.10279 | 0.14645 | 0.17255 | 0.14684 | -122.0941
3913.5469 | 122.2687 | -0.12817 | 121.9711 | 1.4211e-13 | -0.043671 | 0.0069553 | 0.022076 | -0.0081918 | -0.010408 | -0.0099194 | -0.0020039 | 0.022592 | -0.006873 | 0.024412 | 0.010356 | 0.037675 | -0.007751 | -0.026723 | 0.010922 | -0.013378 | 0.09618 | -0.1409 | 0.042256 | -0.00422 | -0.042615 | -0.04369 | -0.009187 | 0.021486 | -0.1092 | -0.012725 | -121.9602 | 0.16585 | 0.10145 | 0.11418 | -121.9845 | -121.8749 | 0.018971 | -122.0148 | 0.17043 | 0.085559 | 0.066588 | -121.9803 | -121.9496 | 0.1391 | 0.1148 | 0.22435 | 0.12042 | -122.112 | 0.084484 | 0.11899 | 0.14966 | 0.12395 | -122.0803
3915.3594 | 122.2549 | -0.1236 | 122.0032 | 1.4211e-13 | -0.044525 | 0.0067415 | 0.022289 | -0.0086192 | -0.010408 | -0.01755 | -0.0017903 | 0.023233 | -0.0066594 | 0.024626 | 0.0099284 | 0.042253 | -0.021486 | -0.031301 | 0.015501 | -0.013378 | 0.09618 | -0.14548 | 0.037677 | -0.00422 | -0.042615 | -0.048268 | -0.004608 | 0.021486 | -0.10004 | -0.021882 | -121.9877 | 0.16585 | 0.092295 | 0.11418 | -122.0166 | -121.907 | 0.023551 | -122.0514 | 0.16127 | 0.080981 | 0.05743 | -122.0078 | -121.9817 | 0.1391 | 0.11022 | 0.21978 | 0.10211 | -122.1487 | 0.075328 | 0.11899 | 0.14508 | 0.11938 | -122.1032
3917.1562 | 122.2046 | -0.15106 | 122.0215 | 1.4211e-13 | -0.043884 | 0.0065279 | 0.022076 | -0.0081918 | -0.010621 | -0.0099194 | -0.0026449 | 0.022592 | -0.0066594 | 0.024412 | 0.010356 | 0.037675 | -0.016908 | -0.026723 | 0.020079 | -0.008799 | 0.091601 | -0.14548 | 0.042256 | 0.000359 | -0.038036 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.005584 | -122.0014 | 0.18874 | 0.12434 | 0.11875 | -122.0303 | -121.9299 | 0.046438 | -122.0698 | 0.19332 | 0.11303 | 0.066588 | -122.0307 | -122.0046 | 0.17114 | 0.14226 | 0.24266 | 0.13415 | -122.167 | 0.10279 | 0.14188 | 0.16797 | 0.15142 | -122.1261
3918.9375 | 122.2641 | -0.14191 | 121.9986 | 1.4211e-13 | -0.043884 | 0.0067415 | 0.021862 | -0.0084056 | -0.010408 | 0.0053411 | -0.0020039 | 0.022378 | -0.0066594 | 0.024839 | 0.0097148 | 0.046831 | -0.012329 | -0.026723 | 0.010922 | -0.00422 | 0.09618 | -0.14548 | 0.042256 | -0.00422 | -0.042615 | -0.052847 | -0.009187 | 0.021486 | -0.10004 | -0.003571 | -121.9877 | 0.18874 | 0.11518 | 0.11875 | -122.0028 | -121.9024 | 0.041862 | -122.0514 | 0.18416 | 0.099292 | 0.05743 | -122.0078 | -121.9771 | 0.15283 | 0.13769 | 0.23809 | 0.12958 | -122.1441 | 0.08906 | 0.13272 | 0.16339 | 0.13769 | -122.0986
3920.6562 | 122.1497 | -0.16937 | 122.0215 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.022076 | -0.0084056 | -0.010621 | -0.0099194 | -0.0022175 | 0.022592 | -0.0066594 | 0.024839 | 0.010142 | 0.046831 | -0.016908 | -0.022144 | 0.020079 | -0.008799 | 0.091601 | -0.13632 | 0.037677 | -0.00422 | -0.033458 | -0.052847 | -0.004608 | 0.016908 | -0.10462 | 0.033053 | -122.0014 | 0.2162 | 0.14723 | 0.11418 | -122.0303 | -121.9299 | 0.064749 | -122.0743 | 0.20705 | 0.13592 | 0.071166 | -122.0261 | -122.0046 | 0.18945 | 0.16057 | 0.26097 | 0.15246 | -122.1578 | 0.11653 | 0.16476 | 0.18628 | 0.16515 | -122.1261
3922.4375 | 122.1313 | -0.18768 | 122.0169 | 1.4211e-13 | -0.044312 | 0.0063141 | 0.022076 | -0.0086192 | -0.010408 | -0.0022889 | -0.0022175 | 0.022806 | -0.006873 | 0.024626 | 0.0097148 | 0.037675 | -0.012329 | -0.031301 | 0.001765 | -0.008799 | 0.09618 | -0.14548 | 0.042256 | -0.00422 | -0.038036 | -0.048268 | -0.009187 | 0.016908 | -0.1092 | 0.042205 | -122.0151 | 0.22536 | 0.15638 | 0.11418 | -122.0257 | -121.9207 | 0.07848 | -122.0652 | 0.22994 | 0.14965 | 0.071167 | -122.0261 | -122 | 0.18945 | 0.17888 | 0.28386 | 0.17535 | -122.1624 | 0.13941 | 0.1785 | 0.20459 | 0.18346 | -122.1261
3924.1562 | 122.2321 | -0.16022 | 122.0123 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.022503 | -0.0081918 | -0.010835 | 0.0053411 | -0.0020039 | 0.023019 | -0.0066594 | 0.024412 | 0.0099284 | 0.042253 | -0.016908 | -0.026723 | 0.020079 | -0.008799 | 0.091601 | -0.13632 | 0.042256 | -0.008798 | -0.047194 | -0.04369 | -0.009187 | 0.026065 | -0.10004 | 0.023897 | -121.9922 | 0.20247 | 0.13349 | 0.1096 | -122.0211 | -121.9207 | 0.060172 | -122.056 | 0.20247 | 0.11302 | 0.052851 | -122.0215 | -121.9863 | 0.1803 | 0.15142 | 0.25182 | 0.14331 | -122.1486 | 0.11653 | 0.15103 | 0.18628 | 0.15142 | -122.1124
3925.9375 | 122.1542 | -0.18768 | 122.0123 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.021862 | -0.0077646 | -0.010408 | -0.0099194 | -0.0020039 | 0.022806 | -0.006873 | 0.024626 | 0.0097148 | 0.042253 | -0.021486 | -0.031301 | 0.020079 | -0.008799 | 0.09618 | -0.14548 | 0.046835 | -0.00422 | -0.038036 | -0.048268 | -0.004608 | 0.021486 | -0.10462 | 0.042205 | -121.9922 | 0.22994 | 0.15638 | 0.11418 | -122.0211 | -121.9161 | 0.083059 | -122.0606 | 0.23452 | 0.14965 | 0.066588 | -122.0169 | -121.9908 | 0.20776 | 0.17888 | 0.28386 | 0.1662 | -122.1578 | 0.13941 | 0.18307 | 0.20917 | 0.18346 | -122.117
3927.7188 | 122.2092 | -0.16022 | 122.0123 | 1.4211e-13 | -0.043884 | 0.0069553 | 0.022076 | -0.0079782 | -0.010194 | -0.0099194 | -0.0022175 | 0.022592 | -0.0066594 | 0.024626 | 0.0099284 | 0.046831 | -0.012329 | -0.026723 | 0.015501 | -0.017957 | 0.091601 | -0.14548 | 0.042256 | -0.00422 | -0.038036 | -0.052847 | -0.009187 | 0.016908 | -0.10462 | 0.014739 | -121.9968 | 0.20705 | 0.13349 | 0.11875 | -122.0303 | -121.9207 | 0.055593 | -122.0652 | 0.20247 | 0.12218 | 0.066588 | -122.0215 | -121.9954 | 0.17572 | 0.14226 | 0.25182 | 0.14789 | -122.1578 | 0.10737 | 0.15103 | 0.17713 | 0.156 | -122.117
3929.4375 | 122.1909 | -0.1831 | 122.0032 | 1.4211e-13 | -0.044098 | 0.0063141 | 0.022076 | -0.0081918 | -0.010194 | -0.0022889 | -0.0015767 | 0.023019 | -0.0066594 | 0.024626 | 0.010142 | 0.046831 | -0.012329 | -0.031301 | 0.010922 | -0.008799 | 0.091601 | -0.14548 | 0.046835 | -0.00422 | -0.033458 | -0.052847 | -0.009187 | 0.016908 | -0.11378 | 0.037627 | -121.9923 | 0.22994 | 0.1518 | 0.11418 | -122.012 | -121.9116 | 0.069323 | -122.056 | 0.22994 | 0.14965 | 0.080324 | -122.0124 | -121.9863 | 0.19403 | 0.17431 | 0.27471 | 0.17078 | -122.1487 | 0.13026 | 0.17392 | 0.20001 | 0.17888 | -122.117
3931.2344 | 122.1863 | -0.17853 | 122.0352 | 1.4211e-13 | -0.044098 | 0.0063141 | 0.021862 | -0.0084056 | -0.010408 | -0.0022889 | -0.0022175 | 0.022806 | -0.006873 | 0.024412 | 0.0097148 | 0.046831 | -0.021486 | -0.022144 | 0.020079 | -0.013378 | 0.091601 | -0.14548 | 0.037677 | -0.008798 | -0.042615 | -0.048268 | -2.9e-05 | 0.021486 | -0.11378 | 0.03305 | -122.0151 | 0.22536 | 0.15638 | 0.12333 | -122.0486 | -121.9436 | 0.064746 | -122.0835 | 0.2162 | 0.13591 | 0.071167 | -122.0352 | -122.0137 | 0.19861 | 0.16515 | 0.27013 | 0.15704 | -122.1807 | 0.13026 | 0.1785 | 0.20001 | 0.16973 | -122.149
3933.0156 | 122.2504 | -0.14191 | 121.9986 | 1.4211e-13 | -0.044525 | 0.0065279 | 0.022076 | -0.0084056 | -0.010408 | -0.01755 | -0.0020039 | 0.022806 | -0.006873 | 0.024626 | 0.0097148 | 0.042253 | -0.026065 | -0.026723 | 0.015501 | -0.00422 | 0.10534 | -0.1409 | 0.033099 | 0.004938 | -0.047194 | -0.048268 | -0.009187 | 0.016908 | -0.10462 | 0.001008 | -121.9831 | 0.18416 | 0.11518 | 0.11418 | -122.0028 | -121.8933 | 0.037283 | -122.0469 | 0.17501 | 0.094713 | 0.05743 | -122.0078 | -121.9817 | 0.15741 | 0.13769 | 0.24724 | 0.11584 | -122.1395 | 0.093639 | 0.13272 | 0.15882 | 0.14685 | -122.1032
3934.7969 | 122.2092 | -0.16937 | 122.0398 | 1.4211e-13 | -0.044312 | 0.0065279 | 0.022503 | -0.0081918 | -0.010621 | -0.0099194 | -0.0020039 | 0.022806 | -0.0066594 | 0.024626 | 0.0099284 | 0.042253 | -0.021486 | -0.026723 | 0.020079 | -0.00422 | 0.09618 | -0.1409 | 0.042256 | 0.000359 | -0.038036 | -0.04369 | -0.004608 | 0.021486 | -0.1092 | 0.028474 | -122.0197 | 0.21163 | 0.14265 | 0.11418 | -122.044 | -121.9436 | 0.06017 | -122.0835 | 0.21163 | 0.13134 | 0.071167 | -122.0444 | -122.0183 | 0.18945 | 0.16515 | 0.26555 | 0.14789 | -122.1807 | 0.12568 | 0.16476 | 0.19086 | 0.16973 | -122.149
3936.5 | 122.2549 | -0.14191 | 122.0169 | 1.4211e-13 | -0.044098 | 0.0065279 | 0.022076 | -0.0079782 | -0.010194 | -0.0022889 | -0.0020039 | 0.022592 | -0.0066594 | 0.025053 | 0.0097148 | 0.037675 | -0.021486 | -0.026723 | 0.015501 | -0.013378 | 0.09618 | -0.14548 | 0.037677 | -0.008798 | -0.047194 | -0.04369 | -0.009187 | 0.016908 | -0.10462 | -0.003571 | -122.0014 | 0.17958 | 0.11518 | 0.11875 | -122.0303 | -121.9207 | 0.037283 | -122.0606 | 0.17958 | 0.094713 | 0.05743 | -122.0261 | -122 | 0.15741 | 0.12853 | 0.23809 | 0.12042 | -122.1624 | 0.098217 | 0.13272 | 0.15882 | 0.13311 | -122.1215
3938.2812 | 122.2641 | -0.16022 | 122.0078 | 1.4211e-13 | -0.044312 | 0.0063141 | 0.022076 | -0.0084056 | -0.010408 | -0.0022889 | -0.0020039 | 0.022592 | -0.0066594 | 0.024626 | 0.0099284 | 0.042253 | -0.021486 | -0.026723 | 0.020079 | -0.013378 | 0.091601 | -0.14548 | 0.037677 | -0.00422 | -0.038036 | -0.048268 | -0.004608 | 0.026065 | -0.1092 | 0.014739 | -121.9877 | 0.20247 | 0.13349 | 0.11875 | -122.0211 | -121.9162 | 0.051014 | -122.056 | 0.19789 | 0.12218 | 0.071167 | -122.0124 | -121.9817 | 0.1803 | 0.14684 | 0.25182 | 0.13873 | -122.1532 | 0.11195 | 0.15561 | 0.18628 | 0.156 | -122.117
3940.0625 | 122.1497 | -0.17853 | 122.0718 | 1.4211e-13 | -0.044312 | 0.0065279 | 0.021862 | -0.0081918 | -0.0099803 | -0.0099194 | -0.0022175 | 0.022592 | -0.0066594 | 0.024839 | 0.0097148 | 0.042253 | -0.021486 | -0.022144 | 0.020079 | -0.008799 | 0.091601 | -0.15464 | 0.037677 | -0.00422 | -0.038036 | -0.04369 | -0.004608 | 0.012329 | -0.1092 | 0.023892 | -122.0518 | 0.22078 | 0.15638 | 0.13249 | -122.0806 | -121.9802 | 0.069325 | -122.1155 | 0.2162 | 0.14049 | 0.071167 | -122.0764 | -122.0595 | 0.19861 | 0.16973 | 0.27013 | 0.15704 | -122.2265 | 0.13484 | 0.17392 | 0.19086 | 0.17431 | -122.181
3941.7812 | 122.2595 | -0.13733 | 122.0306 | 1.4211e-13 | -0.044525 | 0.0063141 | 0.022076 | -0.0084056 | -0.010621 | -0.0099194 | -0.0017903 | 0.022592 | -0.006873 | 0.024626 | 0.0099284 | 0.046831 | -0.016908 | -0.026723 | 0.020079 | -0.00422 | 0.09618 | -0.13632 | 0.037677 | -0.00422 | -0.033458 | -0.04369 | -0.009187 | 0.021486 | -0.10462 | 0.001009 | -122.0106 | 0.18416 | 0.11061 | 0.1096 | -122.0349 | -121.9345 | 0.032705 | -122.0743 | 0.17501 | 0.10387 | 0.071166 | -122.0398 | -122.0092 | 0.15741 | 0.13311 | 0.23351 | 0.12042 | -122.167 | 0.093639 | 0.12814 | 0.15882 | 0.13311 | -122.1353
3943.5 | 122.2183 | -0.17395 | 122.0169 | 1.4211e-13 | -0.044312 | 0.0065279 | 0.022289 | -0.0086192 | -0.010194 | -0.0099194 | -0.0020039 | 0.022592 | -0.006873 | 0.024839 | 0.0099284 | 0.042253 | -0.021486 | -0.031301 | 0.015501 | -0.013378 | 0.091601 | -0.13632 | 0.046835 | 0.000359 | -0.047194 | -0.048268 | -0.004608 | 0.021486 | -0.1092 | 0.03763 | -122.0014 | 0.2162 | 0.14265 | 0.10502 | -122.0303 | -121.9253 | 0.064747 | -122.0652 | 0.22079 | 0.12676 | 0.062009 | -122.0215 | -121.9954 | 0.18945 | 0.16057 | 0.26555 | 0.15246 | -122.1532 | 0.12568 | 0.16934 | 0.19544 | 0.17431 | -122.1261
3945.2812 | 122.3007 | -0.13275 | 122.0032 | 1.4211e-13 | -0.044525 | 0.0065279 | 0.022503 | -0.0084056 | -0.0099803 | 0.0053411 | -0.0020039 | 0.022806 | -0.0066594 | 0.024626 | 0.0097148 | 0.042253 | -0.026065 | -0.031301 | 0.010922 | -0.00422 | 0.09618 | -0.15464 | 0.042256 | -0.008798 | -0.047194 | -0.048268 | -0.009187 | 0.026065 | -0.1092 | -0.021885 | -121.9923 | 0.175 | 0.10145 | 0.12334 | -122.0074 | -121.907 | 0.023548 | -122.0514 | 0.17501 | 0.085557 | 0.062009 | -122.0124 | -121.9771 | 0.14367 | 0.12853 | 0.22893 | 0.10669 | -122.1578 | 0.084483 | 0.12356 | 0.15882 | 0.12395 | -122.1124
3947.0625 | 122.1954 | -0.16937 | 122.0856 | 1.4211e-13 | -0.044312 | 0.0065279 | 0.022076 | -0.0079782 | -0.010408 | -0.0099194 | -0.0020039 | 0.022592 | -0.0066594 | 0.024626 | 0.0097148 | 0.042253 | -0.026065 | -0.017566 | 0.015501 | -0.017957 | 0.09618 | -0.1409 | 0.037677 | 0.000359 | -0.047194 | -0.048268 | -0.004608 | 0.012329 | -0.10462 | 0.028474 | -122.0701 | 0.21163 | 0.15181 | 0.12333 | -122.1035 | -121.9894 | 0.064749 | -122.1338 | 0.20705 | 0.12218 | 0.05743 | -122.0902 | -122.0732 | 0.18487 | 0.15142 | 0.26555 | 0.14331 | -122.2265 | 0.1211 | 0.16476 | 0.1817 | 0.16973 | -122.1902
3948.8438 | 122.2137 | -0.18768 | 122.0215 | 1.4211e-13 | -0.044312 | 0.0067415 | 0.022076 | -0.0084056 | -0.010408 | -0.0022889 | -0.0020039 | 0.021951 | -0.006873 | 0.024839 | 0.0099284 | 0.033096 | -0.030644 | -0.017566 | 0.015501 | -0.013378 | 0.09618 | -0.15006 | 0.042256 | 0.000359 | -0.042615 | -0.039111 | -0.004608 | 0.021486 | -0.1092 | 0.037626 | -122.006 | 0.22078 | 0.17012 | 0.13249 | -122.0349 | -121.9253 | 0.07848 | -122.0606 | 0.22994 | 0.14507 | 0.066588 | -122.0261 | -122 | 0.20318 | 0.1743 | 0.28386 | 0.15704 | -122.1715 | 0.14857 | 0.18307 | 0.20917 | 0.18804 | -122.1307
3950.5469 | 122.2687 | -0.15564 | 122.0444 | 1.4211e-13 | -0.044312 | 0.0065279 | 0.022289 | -0.0084056 | -0.010621 | -0.0022889 | -0.0017903 | 0.021738 | -0.006873 | 0.024626 | 0.0099284 | 0.042253 | -0.026065 | -0.035879 | 0.020079 | -0.00422 | 0.087023 | -0.15006 | 0.033099 | -0.00422 | -0.042615 | -0.048268 | -0.018344 | 0.021486 | -0.10462 | 0.005583 | -122.0243 | 0.19789 | 0.11976 | 0.11418 | -122.0486 | -121.9573 | 0.051016 | -122.0926 | 0.18874 | 0.11303 | 0.062009 | -122.0627 | -122.0229 | 0.17572 | 0.15142 | 0.24266 | 0.12957 | -122.1944 | 0.10737 | 0.1373 | 0.17713 | 0.15142 | -122.149
3952.3281 | 122.168 | -0.17853 | 122.0535 | 1.4211e-13 | -0.044525 | 0.0067415 | 0.021862 | -0.0084056 | -0.010408 | -0.0022889 | -0.0020039 | 0.021738 | -0.0066594 | 0.024412 | 0.0099284 | 0.042253 | -0.021486 | -0.031301 | 0.010922 | -0.00422 | 0.09618 | -0.1409 | 0.046835 | -0.00422 | -0.038036 | -0.052847 | -0.004608 | 0.026065 | -0.1092 | 0.037629 | -122.0426 | 0.22078 | 0.14723 | 0.1096 | -122.0577 | -121.9573 | 0.069325 | -122.1064 | 0.22536 | 0.14049 | 0.071167 | -122.0581 | -122.0275 | 0.18945 | 0.17431 | 0.27471 | 0.15704 | -122.1944 | 0.12568 | 0.17392 | 0.20459 | 0.17431 | -122.1627
3954.1094 | 122.2778 | -0.14648 | 122.0261 | 1.4211e-13 | -0.044525 | 0.0065279 | 0.022076 | -0.0084056 | -0.010194 | -0.0099194 | -0.0020039 | 0.021951 | -0.0066594 | 0.024839 | 0.010142 | 0.028518 | -0.030644 | -0.031301 | 0.010922 | -0.008799 | 0.09618 | -0.1409 | 0.042256 | 0.004938 | -0.038036 | -0.048268 | -0.009187 | 0.026065 | -0.1092 | 0.005585 | -122.0151 | 0.175 | 0.11518 | 0.1096 | -122.0349 | -121.9299 | 0.037281 | -122.0743 | 0.18874 | 0.10845 | 0.071167 | -122.0352 | -122 | 0.15741 | 0.13769 | 0.24266 | 0.11584 | -122.167 | 0.098216 | 0.1373 | 0.17255 | 0.15142 | -122.1353
3955.9062 | 122.3099 | -0.14191 | 122.0261 | 1.4211e-13 | -0.044525 | 0.0061005 | 0.022289 | -0.0084056 | -0.010408 | -0.01755 | -0.0024313 | 0.021524 | -0.0066594 | 0.024412 | 0.0097148 | 0.042253 | -0.030644 | -0.026723 | 0.015501 | -0.017957 | 0.091601 | -0.14548 | 0.033099 | -0.013377 | -0.038036 | -0.04369 | -0.009187 | 0.021486 | -0.11378 | -0.003571 | -122.0106 | 0.18416 | 0.11518 | 0.11875 | -122.044 | -121.9345 | 0.028125 | -122.0698 | 0.17501 | 0.10387 | 0.075746 | -122.0352 | -122.0046 | 0.15741 | 0.12395 | 0.23351 | 0.11126 | -122.1715 | 0.098217 | 0.13272 | 0.16339 | 0.12853 | -122.1398
3957.625 | 122.2458 | -0.17395 | 122.049 | 1.4211e-13 | -0.044525 | 0.0063141 | 0.021862 | -0.0086192 | -0.010621 | -0.0099194 | -0.0022175 | 0.021738 | -0.006873 | 0.024412 | 0.010356 | 0.042253 | -0.030644 | -0.031301 | 0.010922 | -0.008799 | 0.09618 | -0.14548 | 0.042256 | -0.017956 | -0.038036 | -0.048268 | -2.9e-05 | 0.016908 | -0.10462 | 0.028472 | -122.038 | 0.2162 | 0.14265 | 0.11418 | -122.0577 | -121.9528 | 0.069326 | -122.0972 | 0.21621 | 0.13591 | 0.066588 | -122.049 | -122.032 | 0.18487 | 0.16515 | 0.27013 | 0.14331 | -122.1944 | 0.12568 | 0.17392 | 0.19086 | 0.15599 | -122.1536
3959.4062 | 122.3145 | -0.13275 | 122.0352 | 1.4211e-13 | -0.044525 | 0.0065279 | 0.021862 | -0.0081918 | -0.010621 | -0.01755 | -0.0022175 | 0.021951 | -0.006873 | 0.024839 | 0.0095012 | 0.042253 | -0.026065 | -0.031301 | 0.010922 | -0.008799 | 0.09618 | -0.14548 | 0.046835 | -0.00422 | -0.042615 | -0.052847 | -2.9e-05 | 0.021486 | -0.11378 | -0.012727 | -122.0243 | 0.175 | 0.10145 | 0.11418 | -122.044 | -121.939 | 0.018969 | -122.0881 | 0.17959 | 0.090136 | 0.071167 | -122.0352 | -122.0137 | 0.14367 | 0.12395 | 0.22893 | 0.10669 | -122.1807 | 0.079904 | 0.13272 | 0.15424 | 0.12853 | -122.149
3961.2031 | 122.2092 | -0.17395 | 122.1039 | 1.4211e-13 | -0.044312 | 0.0063141 | 0.022076 | -0.0084056 | -0.010408 | -0.01755 | -0.0020039 | 0.021524 | -0.0066594 | 0.024626 | 0.0092874 | 0.042253 | -0.035222 | -0.026723 | 0.020079 | -0.013378 | 0.091601 | -0.13632 | 0.042256 | -0.008798 | -0.051772 | -0.04369 | -0.004608 | 0.016908 | -0.1092 | 0.03763 | -122.0838 | 0.2162 | 0.14723 | 0.1096 | -122.1173 | -122.0123 | 0.064747 | -122.1476 | 0.21621 | 0.12218 | 0.057431 | -122.1085 | -122.087 | 0.19403 | 0.16057 | 0.26555 | 0.13873 | -122.2402 | 0.13026 | 0.16934 | 0.19086 | 0.16515 | -122.2131

## Thermal Data
Fire Time | B Position - Tray - Middle | B Position - Kerite 10c wo | C Position - 3' | C Position - Middle | C Position - 7' | C Position - Kerite 12c wo - 3' | C Position - Kerite 12c wo - 5'
-0.7458 | 6.9459 | 6.6982 | 6.9914 | 7.2213 | 7.0329 | 6.518 | 6.5822
0.2542 | 6.9455 | 6.6945 | 6.9937 | 7.2202 | 7.0358 | 6.5173 | 6.5945
1.2542 | 6.9468 | 6.6982 | 6.9969 | 7.2181 | 7.029 | 6.5174 | 6.5827
2.2542 | 6.9465 | 6.7032 | 7.0033 | 7.2262 | 7.0326 | 6.5146 | 6.5862
3.2542 | 6.9509 | 6.705 | 7.0092 | 7.2266 | 7.0423 | 6.5175 | 6.5926
4.2542 | 6.9506 | 6.6996 | 7.0036 | 7.2282 | 7.0355 | 6.5227 | 6.5886
5.2542 | 6.9509 | 6.6997 | 7.0058 | 7.2359 | 7.0429 | 6.5154 | 6.5866
6.2542 | 6.9773 | 6.7048 | 7.0078 | 7.2319 | 7.0399 | 6.5202 | 6.5785
7.2542 | 7.0348 | 6.7029 | 7.0088 | 7.2339 | 7.0457 | 6.5143 | 6.5905
8.2542 | 7.0484 | 6.7063 | 7.011 | 7.3001 | 7.0543 | 6.511 | 6.5898
9.2542 | 7.0588 | 6.7009 | 7.0006 | 7.4777 | 7.105 | 6.5145 | 6.589
10.2542 | 7.103 | 6.6983 | 7.1219 | 7.477 | 7.1169 | 6.5135 | 6.5885
11.2542 | 7.2094 | 6.7027 | 7.1855 | 7.6948 | 7.14 | 6.5172 | 6.5951
12.2542 | 7.5569 | 6.6995 | 7.304 | 8.2099 | 7.2221 | 6.5106 | 6.5998
13.2542 | 8.8426 | 6.6923 | 7.563 | 8.5462 | 7.3512 | 6.5046 | 6.5889
14.2542 | 9.6693 | 6.6961 | 7.7673 | 8.9959 | 7.6475 | 6.5104 | 6.5894
15.2542 | 11.341 | 6.6923 | 8.1486 | 9.5822 | 8.687 | 6.4944 | 6.585
16.2542 | 13.3611 | 6.6931 | 9.59 | 10.4633 | 9.6805 | 6.4947 | 6.5924
17.2542 | 15.8833 | 6.6985 | 10.4086 | 11.2484 | 10.3039 | 6.4924 | 6.5949
18.2542 | 17.628 | 6.7009 | 11.0298 | 13.4245 | 11.3543 | 6.4937 | 6.5984
19.2542 | 18.8576 | 6.7133 | 12.1129 | 14.3951 | 12.1259 | 6.4764 | 6.5993
20.2542 | 21.6899 | 6.7198 | 13.1295 | 15.8318 | 13.1123 | 6.4723 | 6.6023
21.2542 | 24.1217 | 6.7116 | 15.0614 | 17.7202 | 13.6728 | 6.484 | 6.5966
22.2542 | 25.0984 | 6.7178 | 15.7705 | 19.7484 | 14.308 | 6.4708 | 6.5946
23.2542 | 27.1843 | 6.7395 | 16.9007 | 21.6799 | 15.0786 | 6.4593 | 6.5984
24.2542 | 27.9831 | 6.7652 | 17.8707 | 23.8629 | 15.6637 | 6.4725 | 6.5973
25.2542 | 30.2741 | 6.7657 | 18.5838 | 26.3846 | 16.526 | 6.4826 | 6.593
26.2542 | 32.5357 | 6.7859 | 20.2643 | 28.2265 | 19.3815 | 6.4937 | 6.6003
27.2542 | 34.7383 | 6.8047 | 21.3764 | 30.426 | 20.5407 | 6.4953 | 6.599
28.2542 | 37.4092 | 6.8277 | 23.0077 | 33.2593 | 22.8231 | 6.5104 | 6.6043
29.2542 | 39.3317 | 6.8516 | 24.9229 | 35.2882 | 23.9886 | 6.5436 | 6.5961
30.2542 | 42.1964 | 6.8688 | 25.4433 | 37.7062 | 25.0062 | 6.561 | 6.5949
31.2542 | 45.1644 | 6.8869 | 25.9407 | 39.4146 | 26.5602 | 6.5906 | 6.597
32.2542 | 48.3349 | 6.9191 | 27.2482 | 41.4408 | 28.0524 | 6.6195 | 6.6062
33.2542 | 50.8008 | 6.9564 | 27.9811 | 44.402 | 28.5047 | 6.6455 | 6.6091
34.2542 | 52.7783 | 6.9856 | 28.4002 | 47.2561 | 28.8682 | 6.705 | 6.6131
35.2542 | 54.6426 | 7.0124 | 29.4369 | 49.0613 | 30.4269 | 6.7301 | 6.5997
36.2542 | 56.5045 | 7.0468 | 30.2103 | 51.4614 | 32.0836 | 6.7918 | 6.6028
37.2542 | 57.8451 | 7.0957 | 31.3272 | 53.6275 | 33.2464 | 6.8375 | 6.5971
38.2542 | 59.7615 | 7.1406 | 32.4985 | 55.8601 | 34.2692 | 6.8537 | 6.6105
39.2542 | 60.4924 | 7.1654 | 33.3001 | 57.6286 | 36.039 | 6.901 | 6.6089
40.2542 | 61.4304 | 7.217 | 34.2745 | 60.1118 | 38.9724 | 6.9284 | 6.6091
41.2542 | 62.9922 | 7.2495 | 34.7399 | 62.636 | 40.4397 | 6.9913 | 6.6056
42.2542 | 64.6949 | 7.2937 | 35.7567 | 65.4043 | 41.5289 | 7.0479 | 6.6136
43.2542 | 65.8914 | 7.322 | 37.0365 | 67.0128 | 43.0406 | 7.0819 | 6.6093
44.2542 | 68.2582 | 7.3804 | 38.581 | 68.1582 | 44.6941 | 7.1353 | 6.6111
45.2542 | 69.8379 | 7.4341 | 39.666 | 69.5349 | 45.7061 | 7.1935 | 6.6033
46.2542 | 70.9742 | 7.4613 | 40.0104 | 70.2201 | 47.1377 | 7.2413 | 6.615
47.2542 | 72.9734 | 7.5219 | 41.0189 | 70.8696 | 48.7756 | 7.2992 | 6.6091
48.2542 | 74.4852 | 7.596 | 41.766 | 72.3552 | 49.8471 | 7.3405 | 6.6162
49.2542 | 75.3463 | 7.6157 | 42.3976 | 73.2851 | 50.5899 | 7.3941 | 6.6213
50.2542 | 75.6454 | 7.6763 | 43.6866 | 74.1363 | 51.1885 | 7.4399 | 6.6149
51.2542 | 76.5501 | 7.7387 | 44.6491 | 75.7589 | 52.6114 | 7.4828 | 6.6163
52.2542 | 77.6396 | 7.8138 | 45.6059 | 77.9176 | 53.6338 | 7.5527 | 6.6125
53.2542 | 79.0915 | 7.861 | 46.7129 | 79.4053 | 54.472 | 7.5862 | 6.6101
54.2542 | 80.521 | 7.9083 | 47.5502 | 80.7263 | 55.3528 | 7.6467 | 6.6106
55.2542 | 81.0083 | 7.9703 | 47.9824 | 81.4389 | 56.5644 | 7.7062 | 6.6145
56.2542 | 82.7023 | 8.0297 | 48.8358 | 82.2406 | 57.3584 | 7.753 | 6.6139
57.2542 | 83.2151 | 8.0828 | 50.4066 | 83.45 | 59.4337 | 7.7859 | 6.6124
58.2542 | 83.9446 | 8.1587 | 51.3821 | 85.4174 | 62.0181 | 7.8633 | 6.614
59.2542 | 84.5425 | 8.2082 | 51.9581 | 86.3072 | 62.6413 | 7.913 | 6.6329
60.2542 | 84.2358 | 8.2718 | 52.4834 | 87.4649 | 62.9506 | 7.9734 | 6.6163
61.2542 | 85.7218 | 8.3307 | 52.5068 | 88.2835 | 63.4946 | 8.0273 | 6.6243
62.2542 | 86.426 | 8.3987 | 52.722 | 89.5235 | 64.2081 | 8.0764 | 6.6237
63.2542 | 86.9851 | 8.4854 | 54.0265 | 90.5917 | 66.7105 | 8.1434 | 6.6197
64.2542 | 88.7346 | 8.5205 | 54.1369 | 91.5116 | 67.3961 | 8.2024 | 6.6204
65.2542 | 89.7996 | 8.5876 | 54.244 | 92.3449 | 67.824 | 8.2599 | 6.6265
66.2542 | 90.9134 | 8.6267 | 54.7791 | 92.7258 | 68.7589 | 8.3249 | 6.6334
67.2542 | 92.8963 | 8.6838 | 54.8528 | 93.0279 | 69.9269 | 8.3685 | 6.6228
68.2542 | 93.2311 | 8.7546 | 55.6164 | 93.8316 | 70.4619 | 8.412 | 6.6273
69.2542 | 94.3379 | 8.8127 | 56.5891 | 94.4529 | 70.6359 | 8.4788 | 6.6255
70.2542 | 95.1889 | 8.8459 | 57.3885 | 95.1354 | 71.0954 | 8.5021 | 6.6345
71.2542 | 96.04 | 8.9142 | 58.7986 | 96.0737 | 71.8805 | 8.5718 | 6.6299
72.2542 | 96.8629 | 8.9759 | 59.6378 | 96.9502 | 71.985 | 8.6354 | 6.6301
73.2542 | 96.2415 | 9.0194 | 60.0713 | 98.4019 | 73.1836 | 8.6691 | 6.6347
74.2542 | 96.3362 | 9.0874 | 61.4135 | 100.0357 | 73.0961 | 8.7149 | 6.6384
75.2542 | 97.0661 | 9.1359 | 62.1961 | 101.1281 | 73.6192 | 8.792 | 6.6352
76.2542 | 97.8939 | 9.2063 | 63.5014 | 102.3125 | 74.9341 | 8.8564 | 6.6432
77.2542 | 98.0117 | 9.2497 | 65.0557 | 103.5759 | 75.5703 | 8.8938 | 6.6632
78.2542 | 98.7829 | 9.2983 | 65.5802 | 104.6716 | 76.0072 | 8.9434 | 6.6509
79.2542 | 99.8439 | 9.3751 | 66.7217 | 105.578 | 76.889 | 8.997 | 6.6476
80.2542 | 101.0172 | 9.4216 | 69.0316 | 106.7081 | 78.722 | 9.0554 | 6.654
81.2542 | 101.8575 | 9.5049 | 69.8156 | 106.7788 | 79.3931 | 9.13 | 6.6562
82.2542 | 102.6192 | 9.5442 | 70.197 | 107.6918 | 79.8653 | 9.1862 | 6.6601
83.2542 | 103.3014 | 9.5948 | 70.4204 | 108.1948 | 80.5692 | 9.2371 | 6.6589
84.2542 | 103.4777 | 9.6654 | 71.3213 | 108.6596 | 80.6706 | 9.3096 | 6.6578
85.2542 | 103.8378 | 9.7268 | 72.1196 | 109.196 | 82.1221 | 9.3614 | 6.6611
86.2542 | 103.2477 | 9.8007 | 72.5573 | 109.916 | 83.7057 | 9.4269 | 6.6592
87.2542 | 103.6961 | 9.8629 | 73.9893 | 110.9087 | 84.2198 | 9.5039 | 6.6725
88.2542 | 104.0243 | 9.921 | 74.8396 | 111.963 | 85.192 | 9.5675 | 6.6673
89.2542 | 104.4681 | 10.0002 | 74.8984 | 112.4413 | 86.4612 | 9.6388 | 6.6523
90.2542 | 105.0805 | 10.0667 | 75.7124 | 112.828 | 87.8792 | 9.6919 | 6.667
91.2542 | 105.5012 | 10.1268 | 76.1189 | 113.3344 | 88.6595 | 9.7498 | 6.6611
92.2542 | 105.7708 | 10.196 | 76.0419 | 113.8704 | 89.5171 | 9.8161 | 6.6656
93.2542 | 106.5532 | 10.2844 | 75.756 | 113.9975 | 89.7838 | 9.8658 | 6.6706
94.2542 | 107.4135 | 10.3589 | 75.6518 | 114.0813 | 90.4552 | 9.9457 | 6.6745
95.2542 | 107.9708 | 10.4342 | 76.2942 | 114.6355 | 90.5506 | 10.0083 | 6.6749
96.2542 | 108.1415 | 10.5056 | 76.7355 | 115.3345 | 91.0343 | 10.0494 | 6.673
97.2542 | 108.1932 | 10.5704 | 78.0713 | 116.5301 | 91.0837 | 10.1268 | 6.6825
98.2542 | 108.1525 | 10.6462 | 78.6946 | 117.6672 | 92.6761 | 10.2072 | 6.6863
99.2542 | 108.0724 | 10.7133 | 78.5918 | 118.8912 | 93.3499 | 10.2602 | 6.6781
100.2542 | 108.7019 | 10.807 | 78.3901 | 119.1071 | 94.2827 | 10.3259 | 6.6822
101.2542 | 109.6354 | 10.8664 | 80.2516 | 119.2613 | 94.8735 | 10.4017 | 6.6883
102.2542 | 109.912 | 10.9293 | 80.5624 | 119.9088 | 95.6798 | 10.4543 | 6.687
103.2542 | 109.8025 | 11.0181 | 80.9067 | 120.5774 | 95.6021 | 10.5297 | 6.6957
104.2542 | 110.12 | 11.1044 | 80.9153 | 121.0127 | 96.7719 | 10.5914 | 6.6959
105.2542 | 111.0456 | 11.1724 | 80.9267 | 121.3465 | 97.8755 | 10.647 | 6.6963
106.2542 | 112.2332 | 11.2549 | 80.3015 | 122.1305 | 97.977 | 10.7025 | 6.7002
107.2542 | 113.3235 | 11.3291 | 79.7844 | 122.5982 | 99.3196 | 10.7762 | 6.7004
108.2542 | 114.0595 | 11.4073 | 79.6614 | 122.9181 | 99.4786 | 10.8365 | 6.7003
109.2542 | 114.8071 | 11.486 | 81.3726 | 123.4685 | 99.9464 | 10.8803 | 6.6942
110.2542 | 115.6443 | 11.5744 | 82.0726 | 123.7447 | 100.4772 | 10.951 | 6.7064
111.2542 | 115.5504 | 11.6482 | 82.1491 | 124.0856 | 101.0409 | 10.9995 | 6.7101
112.2542 | 116.0658 | 11.7134 | 82.8202 | 124.3726 | 101.4605 | 11.0647 | 6.7003
113.2542 | 115.8282 | 11.805 | 83.8594 | 125.0074 | 101.6718 | 11.1278 | 6.703
114.2542 | 115.7138 | 11.896 | 85.7095 | 125.3412 | 102.2298 | 11.193 | 6.7184
115.2542 | 116.1885 | 11.9866 | 87.1183 | 125.2315 | 102.167 | 11.2545 | 6.7133
116.2542 | 116.1467 | 12.0599 | 87.6322 | 125.3407 | 102.2115 | 11.3197 | 6.7214
117.2542 | 116.4033 | 12.1177 | 88.2349 | 125.8538 | 102.3783 | 11.3853 | 6.7215
118.2542 | 116.0215 | 12.2088 | 88.0965 | 126.0861 | 102.5207 | 11.4361 | 6.7276
119.2542 | 116.8627 | 12.2906 | 88.3356 | 126.8677 | 103.2101 | 11.5065 | 6.7252
120.2542 | 116.996 | 12.3772 | 87.6637 | 127.4985 | 103.3528 | 11.5529 | 6.7225
121.2542 | 117.4754 | 12.4506 | 87.3178 | 127.4433 | 103.7075 | 11.6227 | 6.7312
122.2542 | 118.1413 | 12.5361 | 87.5025 | 127.7861 | 104.4715 | 11.6665 | 6.7287
123.2542 | 118.3314 | 12.6214 | 87.8841 | 128.5381 | 106.7556 | 11.711 | 6.7345
124.2542 | 118.3443 | 12.7038 | 88.5061 | 128.6361 | 107.113 | 11.7991 | 6.7389
125.2542 | 117.9652 | 12.7552 | 89.1207 | 128.7853 | 107.3364 | 11.866 | 6.7397
126.2542 | 118.2608 | 12.8439 | 88.9217 | 128.6723 | 107.4075 | 11.903 | 6.7569
127.2542 | 117.884 | 12.9168 | 89.1208 | 128.4366 | 107.2735 | 11.9457 | 6.7388
128.2542 | 117.9555 | 12.9929 | 89.6049 | 128.6391 | 106.4489 | 12.0049 | 6.7532
129.2542 | 118.1521 | 13.0706 | 90.6248 | 128.981 | 106.3126 | 12.0667 | 6.745
130.2542 | 117.852 | 13.1529 | 91.1139 | 129.2126 | 106.7448 | 12.1294 | 6.7399
131.2542 | 118.1427 | 13.2192 | 91.5085 | 129.4595 | 106.4549 | 12.1769 | 6.761
132.2542 | 118.209 | 13.2907 | 92.4044 | 129.9379 | 106.7173 | 12.2253 | 6.7614
133.2542 | 118.6518 | 13.3369 | 92.7877 | 130.7572 | 107.3875 | 12.2841 | 6.7537
134.2542 | 119.2052 | 13.44 | 92.2716 | 131.0459 | 107.7728 | 12.3471 | 6.7664
135.2542 | 118.8616 | 13.5033 | 92.1441 | 131.5077 | 107.6324 | 12.3909 | 6.7649
136.2542 | 118.5203 | 13.5844 | 93.2461 | 131.8383 | 108.0467 | 12.4488 | 6.7713
137.2542 | 118.1272 | 13.6529 | 92.4915 | 131.7569 | 108.0384 | 12.4897 | 6.7645
138.2542 | 118.5329 | 13.7313 | 92.2004 | 131.6119 | 108.6524 | 12.543 | 6.772
139.2542 | 119.1377 | 13.8118 | 91.6204 | 131.6558 | 108.6658 | 12.61 | 6.778
140.2542 | 119.6419 | 13.8846 | 91.8095 | 131.8688 | 108.9726 | 12.6652 | 6.7785
141.2542 | 120.335 | 13.9468 | 91.2231 | 131.9171 | 109.3517 | 12.7119 | 6.7909
142.2542 | 120.9305 | 14.0334 | 90.7126 | 132.3443 | 109.6317 | 12.7789 | 6.7888
143.2542 | 121.2083 | 14.0929 | 90.1959 | 132.3046 | 110.0515 | 12.8122 | 6.7904
144.2542 | 120.9238 | 14.1765 | 90.2151 | 132.548 | 110.2728 | 12.8522 | 6.7846
145.2542 | 121.5384 | 14.2557 | 90.5236 | 132.8314 | 111.0368 | 12.9159 | 6.7887
146.2542 | 122.3675 | 14.2999 | 90.785 | 133.139 | 111.4273 | 12.952 | 6.7916
147.2542 | 122.6261 | 14.3955 | 90.8639 | 133.3982 | 111.8955 | 13.0105 | 6.8135
148.2542 | 122.5429 | 14.4391 | 90.1463 | 134.1781 | 111.9089 | 13.0703 | 6.8091
149.2542 | 122.6202 | 14.5106 | 90.7783 | 134.8999 | 111.5371 | 13.1248 | 6.8069
150.2542 | 123.503 | 14.5751 | 90.9824 | 135.2082 | 111.8954 | 13.1732 | 6.8083
151.2542 | 123.1682 | 14.6517 | 90.8324 | 135.1879 | 112.4549 | 13.236 | 6.8228
152.2542 | 123.1844 | 14.7161 | 90.7417 | 135.7222 | 112.1293 | 13.274 | 6.8255
153.2542 | 123.489 | 14.7846 | 91.1061 | 135.8992 | 112.5019 | 13.326 | 6.811
154.2542 | 123.9866 | 14.8526 | 91.2082 | 136.2497 | 112.8614 | 13.3917 | 6.8273
155.2542 | 124.4334 | 14.9162 | 91.0277 | 136.3285 | 112.5296 | 13.4503 | 6.8268
156.2542 | 125.3481 | 15.0031 | 90.9066 | 136.2509 | 112.5582 | 13.5096 | 6.8388
157.2542 | 125.544 | 15.0866 | 91.5265 | 136.1361 | 112.5009 | 13.5448 | 6.8403
158.2542 | 126.009 | 15.1559 | 90.8025 | 136.0937 | 112.3196 | 13.6022 | 6.8386
159.2542 | 125.7384 | 15.2301 | 90.3294 | 136.2496 | 111.8617 | 13.6628 | 6.8466
160.2542 | 126.0279 | 15.2664 | 90.477 | 136.1614 | 111.6513 | 13.7218 | 6.8477
161.2542 | 126.0776 | 15.3506 | 90.1273 | 135.8582 | 111.8391 | 13.7793 | 6.8482
162.2542 | 126.3958 | 15.4194 | 89.4418 | 135.5166 | 112.1648 | 13.8215 | 6.8585
163.2542 | 126.5799 | 15.5265 | 89.1508 | 135.2433 | 112.3123 | 13.8757 | 6.8649
164.2542 | 126.5273 | 15.5937 | 88.733 | 135.4017 | 112.3535 | 13.9318 | 6.8735
165.2542 | 127.185 | 15.6862 | 88.9698 | 135.4997 | 112.0718 | 13.9943 | 6.8715
166.2542 | 127.0154 | 15.7505 | 89.1567 | 135.6131 | 112.2301 | 14.0484 | 6.8681
167.2542 | 127.2835 | 15.8204 | 88.8769 | 135.9427 | 112.2736 | 14.095 | 6.8867
168.2542 | 127.7558 | 15.9193 | 88.5785 | 136.3506 | 112.4641 | 14.1513 | 6.8756
169.2542 | 128.091 | 15.9919 | 88.655 | 136.1293 | 112.4481 | 14.2002 | 6.8868
170.2542 | 128.5905 | 16.0712 | 89.1939 | 135.8843 | 112.1924 | 14.2571 | 6.8896
171.2542 | 128.3036 | 16.1427 | 89.2196 | 135.7224 | 112.304 | 14.2937 | 6.8986
172.2542 | 128.4204 | 16.2088 | 89.4584 | 135.6712 | 112.4905 | 14.3362 | 6.9019
173.2542 | 128.4884 | 16.3055 | 89.2324 | 135.5618 | 112.6991 | 14.3968 | 6.9113
174.2542 | 128.712 | 16.3724 | 89.2108 | 136.0569 | 112.5524 | 14.4556 | 6.9135
175.2542 | 129.3063 | 16.4512 | 89.6184 | 136.2017 | 113.6186 | 14.4976 | 6.9307
176.2542 | 129.6364 | 16.5195 | 89.9075 | 136.1247 | 113.5856 | 14.5499 | 6.9192
177.2542 | 130.2139 | 16.592 | 89.9026 | 136.2345 | 113.324 | 14.6051 | 6.9263
178.2542 | 130.9931 | 16.6567 | 90.6629 | 136.8084 | 113.5707 | 14.6556 | 6.9342
179.2542 | 130.9299 | 16.7375 | 91.2954 | 137.0739 | 114.3934 | 14.7184 | 6.9381
180.2542 | 131.3731 | 16.8072 | 92.1836 | 137.1816 | 115.3651 | 14.7759 | 6.9393
181.2542 | 131.4027 | 16.8736 | 91.8098 | 138.2904 | 115.3775 | 14.8158 | 6.9446
182.2542 | 131.0217 | 16.947 | 91.661 | 138.8897 | 115.405 | 14.8728 | 6.9509
183.2542 | 130.5374 | 17.0142 | 91.9599 | 139.3494 | 115.3595 | 14.931 | 6.958
184.2542 | 129.6084 | 17.0914 | 93.2154 | 139.6735 | 115.6367 | 14.9695 | 6.9718
185.2542 | 129.7689 | 17.1724 | 93.0782 | 139.8632 | 116.0148 | 15.0289 | 6.9666
186.2542 | 130.2065 | 17.2148 | 93.7064 | 140.3703 | 116.0035 | 15.093 | 6.9703
187.2542 | 130.057 | 17.3042 | 94.5473 | 140.9504 | 115.5386 | 15.131 | 6.9759
188.2542 | 130.0498 | 17.3927 | 95.1415 | 141.5215 | 115.545 | 15.1956 | 6.9867
189.2542 | 129.4355 | 17.4769 | 95.7029 | 141.8446 | 116.1737 | 15.2568 | 6.9781
190.2542 | 129.4128 | 17.5651 | 96.7365 | 142.1887 | 116.695 | 15.2956 | 6.998
191.2542 | 129.7493 | 17.6387 | 96.9787 | 142.152 | 117.4646 | 15.3293 | 7.0084
192.2542 | 129.6148 | 17.7144 | 97.613 | 141.8205 | 118.0423 | 15.3815 | 7.0018
193.2542 | 129.9145 | 17.7966 | 98.5704 | 142.1698 | 118.1878 | 15.4341 | 7.013
194.2542 | 130.3033 | 17.8808 | 98.5393 | 142.5863 | 118.0907 | 15.4862 | 7.0209
195.2542 | 130.2307 | 17.9661 | 98.4389 | 142.9326 | 118.6965 | 15.5418 | 7.0179
196.2542 | 130.6218 | 18.0168 | 98.0611 | 143.2002 | 119.152 | 15.5828 | 7.0264
197.2542 | 130.8616 | 18.0898 | 98.2857 | 143.9947 | 119.6786 | 15.6472 | 7.0319
198.2542 | 131.173 | 18.1502 | 98.5202 | 144.4576 | 119.6994 | 15.6681 | 7.0427
199.2542 | 131.8837 | 18.2406 | 99.8756 | 144.49 | 119.7041 | 15.7251 | 7.0452
200.2542 | 132.1969 | 18.3123 | 101.5166 | 144.7779 | 120.3912 | 15.7774 | 7.053
201.2542 | 132.7069 | 18.391 | 101.6138 | 144.9872 | 120.241 | 15.8209 | 7.0539
202.2542 | 133.426 | 18.4607 | 101.6452 | 145.3435 | 120.9009 | 15.8731 | 7.0631
203.2542 | 133.9439 | 18.5493 | 102.6618 | 145.5691 | 120.765 | 15.9295 | 7.0672
204.2542 | 133.6783 | 18.6389 | 102.8177 | 145.7887 | 120.6175 | 15.994 | 7.0755
205.2542 | 133.7644 | 18.7058 | 102.8796 | 145.3337 | 120.4728 | 16.04 | 7.0826
206.2542 | 134.1298 | 18.7565 | 102.2654 | 145.236 | 120.7496 | 16.1037 | 7.0873
207.2542 | 134.232 | 18.8676 | 102.4739 | 145.7367 | 120.4927 | 16.1612 | 7.087
208.2542 | 134.4922 | 18.9465 | 102.0873 | 146.2494 | 120.454 | 16.2141 | 7.1014
209.2542 | 134.2211 | 19.0127 | 101.9183 | 146.4442 | 120.4882 | 16.2663 | 7.1149
210.2542 | 134.6769 | 19.0742 | 101.8324 | 146.4953 | 120.6181 | 16.2984 | 7.118
211.2542 | 135.3138 | 19.1553 | 102.2005 | 146.6265 | 121.3261 | 16.3673 | 7.1213
212.2542 | 135.3055 | 19.26 | 102.0877 | 146.9659 | 121.0297 | 16.4186 | 7.1324
213.2542 | 136.1358 | 19.3243 | 102.1463 | 147.2687 | 121.021 | 16.4799 | 7.1393
214.2542 | 136.9314 | 19.4007 | 101.9628 | 147.6129 | 121.2025 | 16.5357 | 7.1502
215.2542 | 137.7777 | 19.4642 | 101.8736 | 147.8106 | 121.4917 | 16.5625 | 7.152
216.2542 | 137.6193 | 19.5369 | 101.4654 | 148.0954 | 121.0122 | 16.6253 | 7.1645
217.2542 | 137.8738 | 19.6171 | 101.908 | 148.1226 | 121.5157 | 16.6728 | 7.1704
218.2542 | 138.3137 | 19.6947 | 101.9163 | 148.351 | 121.6952 | 16.7344 | 7.1788
219.2542 | 138.3866 | 19.7561 | 102.1264 | 148.3684 | 121.7897 | 16.7819 | 7.178
220.2542 | 139.5323 | 19.8429 | 102.6623 | 148.8668 | 121.8221 | 16.8554 | 7.2024
221.2542 | 140.0861 | 19.917 | 102.7547 | 149.3513 | 122.3598 | 16.8918 | 7.2038
222.2542 | 139.6529 | 19.9932 | 102.5391 | 150.4959 | 122.3158 | 16.9495 | 7.2121
223.2542 | 139.6013 | 20.0855 | 102.8413 | 150.9826 | 122.5879 | 16.9904 | 7.2031
224.2542 | 140.0122 | 20.1714 | 103.5112 | 151.6116 | 122.8585 | 17.0584 | 7.227
225.2542 | 140.8018 | 20.2499 | 103.8588 | 152.3916 | 122.3786 | 17.1104 | 7.2207
226.2542 | 140.6459 | 20.3492 | 104.0148 | 152.5217 | 123.2312 | 17.1607 | 7.2398
227.2542 | 141.4726 | 20.43 | 103.4748 | 152.6195 | 123.2438 | 17.2099 | 7.2483
228.2542 | 142.0752 | 20.5145 | 102.9735 | 152.975 | 123.5162 | 17.2617 | 7.2442
229.2542 | 142.1384 | 20.5799 | 102.3998 | 152.849 | 124.7678 | 17.3165 | 7.2554
230.2542 | 142.3757 | 20.6692 | 102.5771 | 152.5743 | 124.7722 | 17.3557 | 7.2754
231.2542 | 142.3541 | 20.7713 | 102.2785 | 152.4207 | 125.3675 | 17.4218 | 7.2726
232.2542 | 141.906 | 20.8622 | 102.4686 | 152.0857 | 125.0648 | 17.4882 | 7.2856
233.2542 | 141.521 | 20.9673 | 102.8028 | 151.706 | 125.6677 | 17.5439 | 7.2948
234.2542 | 141.6386 | 21.0473 | 102.6476 | 151.5293 | 125.2035 | 17.583 | 7.3109
235.2542 | 141.7815 | 21.117 | 103.096 | 151.5873 | 125.7709 | 17.6223 | 7.3144
236.2542 | 142.2247 | 21.204 | 103.4198 | 152.1248 | 125.9434 | 17.6901 | 7.308
237.2542 | 143.7872 | 21.3 | 103.7727 | 152.6212 | 126.4282 | 17.7338 | 7.3299
238.2542 | 143.5703 | 21.3855 | 104.6943 | 152.662 | 126.1679 | 17.7791 | 7.3291
239.2542 | 144.1859 | 21.4967 | 106.0318 | 153.5137 | 126.4446 | 17.8312 | 7.3478
240.2542 | 144.6507 | 21.5992 | 106.586 | 153.2515 | 127.0414 | 17.89 | 7.3479
241.2542 | 144.9339 | 21.6844 | 106.3612 | 153.3873 | 127.09 | 17.9317 | 7.3612
242.2542 | 145.8769 | 21.7738 | 106.3814 | 153.8485 | 127.8938 | 17.9912 | 7.3656
243.2542 | 146.6693 | 21.8723 | 107.7894 | 154.331 | 128.146 | 18.0285 | 7.3777
244.2542 | 147.364 | 21.9632 | 107.7717 | 154.4064 | 128.8254 | 18.089 | 7.3917
245.2542 | 147.9487 | 22.0499 | 107.8464 | 155.0565 | 129.7227 | 18.1492 | 7.3977
246.2542 | 147.8347 | 22.146 | 108.619 | 155.7417 | 129.4609 | 18.193 | 7.4093
247.2542 | 148.1893 | 22.2458 | 109.1986 | 156.1093 | 129.7423 | 18.2575 | 7.4214
248.2542 | 148.9532 | 22.325 | 110.589 | 156.5924 | 130.8923 | 18.3115 | 7.425
249.2542 | 149.5598 | 22.4045 | 110.3131 | 156.9061 | 131.159 | 18.3808 | 7.4372
250.2542 | 148.8064 | 22.5298 | 110.3073 | 157.3552 | 131.6808 | 18.4311 | 7.4352
251.2542 | 149.1975 | 22.6325 | 110.1046 | 157.3229 | 131.7148 | 18.4834 | 7.4503
252.2542 | 149.8699 | 22.7279 | 110.1001 | 157.4055 | 132.0878 | 18.5234 | 7.4605
253.2542 | 150.6378 | 22.8233 | 109.6335 | 157.921 | 132.0423 | 18.5949 | 7.4756
254.2542 | 152.1117 | 22.9342 | 110.1462 | 158.4244 | 131.8755 | 18.6661 | 7.4858
255.2542 | 152.8888 | 23.0304 | 110.3262 | 158.8272 | 131.5184 | 18.7171 | 7.4887
256.2542 | 153.6365 | 23.1229 | 110.4069 | 159.4136 | 131.7144 | 18.7926 | 7.5032
257.2542 | 154.8611 | 23.2305 | 110.7521 | 160.6353 | 132.3098 | 18.8536 | 7.5089
258.2542 | 154.6792 | 23.3128 | 111.4016 | 159.9775 | 132.5887 | 18.9164 | 7.5332
259.2542 | 155.082 | 23.4286 | 111.3475 | 160.0289 | 132.6235 | 18.973 | 7.541
260.2542 | 156.2522 | 23.5342 | 112.395 | 160.389 | 133.2527 | 19.0523 | 7.5255
261.2542 | 156.9243 | 23.6255 | 113.3179 | 160.8239 | 133.706 | 19.1311 | 7.5563
262.2542 | 157.3066 | 23.7319 | 113.507 | 161.2129 | 134.5396 | 19.2018 | 7.5572
263.2542 | 157.7076 | 23.8235 | 113.8529 | 161.4412 | 135.2748 | 19.2519 | 7.579
264.2542 | 158.7449 | 23.9348 | 113.4354 | 161.6987 | 135.9605 | 19.3313 | 7.5827
265.2542 | 159.1868 | 24.0321 | 113.5624 | 161.8637 | 136.3077 | 19.4169 | 7.591
266.2542 | 160.1986 | 24.1386 | 114.7638 | 161.5829 | 137.1074 | 19.4628 | 7.605
267.2542 | 160.5446 | 24.244 | 115.3785 | 162.8556 | 137.3268 | 19.5472 | 7.6248
268.2542 | 161.3931 | 24.3715 | 115.1336 | 163.2095 | 137.3208 | 19.6005 | 7.6292
269.2542 | 161.9616 | 24.4601 | 114.8839 | 164.8136 | 137.4377 | 19.6734 | 7.6348
270.2542 | 162.1318 | 24.5454 | 114.7115 | 164.7986 | 138.3494 | 19.7446 | 7.6467
271.2542 | 162.0845 | 24.6657 | 114.5671 | 165.1226 | 138.6809 | 19.7972 | 7.6644
272.2542 | 164.2934 | 24.765 | 114.0634 | 165.4522 | 138.9173 | 19.8642 | 7.6659
273.2542 | 163.81 | 24.8735 | 115.2121 | 165.3912 | 139.4287 | 19.9339 | 7.6774
274.2542 | 163.4945 | 24.9954 | 115.4224 | 165.8791 | 139.2682 | 20.001 | 7.6908
275.2542 | 163.3382 | 25.1081 | 115.3398 | 166.0434 | 140.0381 | 20.0717 | 7.7073
276.2542 | 164.4009 | 25.2267 | 114.9977 | 166.2735 | 140.2115 | 20.1362 | 7.7111
277.2542 | 165.2535 | 25.339 | 115.0315 | 167.1524 | 139.8451 | 20.2056 | 7.7203
278.2542 | 165.5277 | 25.4523 | 115.0365 | 167.3148 | 140.0881 | 20.2707 | 7.7358
279.2542 | 165.6013 | 25.5409 | 114.8539 | 167.4889 | 140.5548 | 20.3357 | 7.7441
280.2542 | 165.3045 | 25.6937 | 114.4136 | 167.8644 | 140.329 | 20.4275 | 7.7638
281.2542 | 165.3463 | 25.8013 | 114.4635 | 168.1986 | 140.9192 | 20.4912 | 7.77
282.2542 | 165.9931 | 25.9416 | 115.1649 | 168.6492 | 141.8097 | 20.5648 | 7.792
283.2542 | 166.6732 | 26.0583 | 116.2964 | 168.4222 | 142.3392 | 20.6199 | 7.7868
284.2542 | 168.5725 | 26.1504 | 116.2341 | 168.8426 | 142.2619 | 20.6953 | 7.8061
285.2542 | 169.6027 | 26.2728 | 118.081 | 169.0578 | 142.6192 | 20.7502 | 7.8202
286.2542 | 169.5999 | 26.3993 | 118.1661 | 170.019 | 142.8844 | 20.8299 | 7.8273
287.2542 | 169.9067 | 26.4989 | 118.5391 | 169.907 | 143.184 | 20.9059 | 7.8466
288.2542 | 171.0726 | 26.6115 | 118.7968 | 170.1515 | 143.4001 | 20.9757 | 7.8526
289.2542 | 171.3304 | 26.7646 | 119.326 | 170.4583 | 143.5829 | 21.0318 | 7.8727
290.2542 | 171.9041 | 26.8822 | 119.3859 | 170.8556 | 143.1415 | 21.1123 | 7.8743
291.2542 | 172.2425 | 26.9942 | 120.5522 | 171.271 | 142.8245 | 21.185 | 7.891
292.2542 | 172.5902 | 27.1045 | 122.1146 | 171.7723 | 143.1255 | 21.2513 | 7.9
293.2542 | 173.0131 | 27.2636 | 122.1176 | 173.2937 | 143.4011 | 21.3373 | 7.9112
294.2542 | 172.1985 | 27.3894 | 121.795 | 173.6451 | 143.4945 | 21.4028 | 7.9264
295.2542 | 172.3428 | 27.5181 | 121.6665 | 173.5766 | 143.2774 | 21.4624 | 7.9373
296.2542 | 173.2629 | 27.6683 | 122.5055 | 173.6273 | 144.2743 | 21.5388 | 7.9556
297.2542 | 174.8422 | 27.7867 | 122.6568 | 174.5146 | 144.7163 | 21.6041 | 7.9639
298.2542 | 175.3897 | 27.9311 | 122.1178 | 174.1864 | 144.6137 | 21.6734 | 7.9825
299.2542 | 176.0923 | 28.0633 | 122.7759 | 173.8293 | 144.4648 | 21.7476 | 7.9851
300.2542 | 177.2907 | 28.2154 | 123.7023 | 173.793 | 144.7802 | 21.8159 | 7.9986
301.2542 | 176.8609 | 28.365 | 123.968 | 174.0178 | 145.0808 | 21.8789 | 8.016
302.2542 | 176.8877 | 28.4975 | 124.2977 | 174.1921 | 145.6344 | 21.9584 | 8.0258
303.2542 | 177.1503 | 28.6465 | 125.0414 | 175.1854 | 146.1206 | 22.0123 | 8.0247
304.2542 | 177.1859 | 28.7904 | 124.6646 | 175.6857 | 146.0141 | 22.1009 | 8.0492
305.2542 | 177.2765 | 28.9314 | 124.1386 | 176.1503 | 146.364 | 22.165 | 8.0609
306.2542 | 177.0857 | 29.0684 | 124.3521 | 176.5948 | 146.6443 | 22.2342 | 8.0855
307.2542 | 177.3609 | 29.2007 | 124.4211 | 176.6762 | 146.8576 | 22.3094 | 8.0908
308.2542 | 176.9304 | 29.3428 | 123.88 | 176.9484 | 147.1983 | 22.3717 | 8.1106
309.2542 | 178.0395 | 29.5138 | 123.2656 | 177.0614 | 147.3014 | 22.4545 | 8.1144
310.2542 | 179.0844 | 29.6416 | 124.1381 | 176.9705 | 148.1069 | 22.5307 | 8.1328
311.2542 | 179.8117 | 29.7845 | 123.9591 | 177.2498 | 148.7405 | 22.6032 | 8.1578
312.2542 | 179.9913 | 29.9439 | 123.3358 | 177.3422 | 148.8912 | 22.6583 | 8.1616
313.2542 | 180.0479 | 30.07 | 123.5639 | 177.2161 | 148.7255 | 22.7322 | 8.1724
314.2542 | 180.0976 | 30.2114 | 124.6661 | 177.21 | 148.834 | 22.7871 | 8.1842
315.2542 | 181.0973 | 30.3653 | 124.1995 | 177.7195 | 149.5813 | 22.8685 | 8.2028
316.2542 | 181.9488 | 30.5244 | 123.7976 | 177.8471 | 149.4841 | 22.9339 | 8.2134
317.2542 | 181.7908 | 30.6753 | 123.6978 | 177.2355 | 149.6773 | 22.9862 | 8.2309
318.2542 | 183.6548 | 30.8455 | 122.9939 | 177.0538 | 150.5518 | 23.0521 | 8.2377
319.2542 | 185.388 | 31.0016 | 122.3828 | 177.4225 | 150.8468 | 23.1236 | 8.2569
320.2542 | 186.7288 | 31.1481 | 121.9718 | 177.9182 | 151.1332 | 23.1928 | 8.2673
321.2542 | 187.5627 | 31.3006 | 121.9831 | 178.1662 | 150.7589 | 23.2612 | 8.2822
322.2542 | 189.1103 | 31.4548 | 122.2111 | 178.4316 | 151.455 | 23.3225 | 8.2969
323.2542 | 188.6867 | 31.6156 | 121.9755 | 179.3882 | 151.9153 | 23.394 | 8.3023
324.2542 | 188.2564 | 31.7717 | 122.1928 | 180.0969 | 151.8979 | 23.4719 | 8.3267
325.2542 | 188.4437 | 31.9055 | 121.8037 | 179.9473 | 152.6824 | 23.5395 | 8.324
326.2542 | 188.1618 | 32.0754 | 121.6983 | 179.8474 | 153.2733 | 23.6085 | 8.3495
327.2542 | 189.2271 | 32.2324 | 121.7712 | 179.9116 | 153.3829 | 23.6792 | 8.3641
328.2542 | 190.8055 | 32.3917 | 121.866 | 179.8174 | 153.6979 | 23.7636 | 8.3828
329.2542 | 191.6297 | 32.5211 | 122.4577 | 180.0797 | 154.0101 | 23.8336 | 8.3964
330.2542 | 192.2689 | 32.7168 | 122.405 | 180.8215 | 154.4558 | 23.898 | 8.4085
331.2542 | 192.7835 | 32.8572 | 121.8833 | 181.5367 | 155.1422 | 23.9651 | 8.4268
332.2542 | 193.739 | 33.0351 | 121.8589 | 181.2835 | 155.886 | 24.047 | 8.4468
333.2542 | 194.6136 | 33.2084 | 121.7681 | 181.3616 | 156.2937 | 24.115 | 8.4654
334.2542 | 195.604 | 33.3414 | 121.8391 | 181.286 | 156.9487 | 24.1603 | 8.4734
335.2542 | 196.7622 | 33.4962 | 121.3068 | 181.0663 | 157.3684 | 24.2324 | 8.483
336.2542 | 197.6397 | 33.7082 | 121.0208 | 181.0547 | 157.4023 | 24.3103 | 8.5049
337.2542 | 199.8193 | 33.8803 | 121.4673 | 181.167 | 157.5832 | 24.3858 | 8.5275
338.2542 | 200.7245 | 34.0639 | 121.4996 | 181.5609 | 158.1649 | 24.4604 | 8.532
339.2542 | 202.3435 | 34.2141 | 121.7369 | 181.7127 | 158.4761 | 24.5345 | 8.5501
340.2542 | 203.7535 | 34.4042 | 121.6047 | 182.2583 | 158.761 | 24.6054 | 8.5774
341.2542 | 204.9229 | 34.5659 | 121.3729 | 182.578 | 160.6063 | 24.6756 | 8.5851
342.2542 | 206.1327 | 34.7415 | 122.7911 | 183.1651 | 162.7288 | 24.7311 | 8.6054
343.2542 | 206.8303 | 34.9096 | 123.1409 | 184.3285 | 163.6342 | 24.8266 | 8.6191
344.2542 | 206.9289 | 35.0817 | 125.1611 | 185.9119 | 164.4803 | 24.9102 | 8.6377
345.2542 | 207.6328 | 35.233 | 125.6028 | 186.4721 | 164.8675 | 25.0022 | 8.6556
346.2542 | 207.9181 | 35.414 | 125.7012 | 187.4515 | 165.6235 | 25.0673 | 8.6662
347.2542 | 208.4823 | 35.614 | 125.6744 | 187.4963 | 165.9605 | 25.1387 | 8.6934
348.2542 | 209.9329 | 35.7642 | 125.7381 | 187.8811 | 165.9403 | 25.2014 | 8.6966
349.2542 | 210.3222 | 35.9443 | 126.3248 | 188.6041 | 165.812 | 25.2928 | 8.7208
350.2542 | 210.4626 | 36.1345 | 127.379 | 189.0994 | 165.9459 | 25.3787 | 8.733
351.2542 | 210.9638 | 36.3228 | 128.4043 | 189.0992 | 166.1672 | 25.4626 | 8.7519
352.2542 | 210.5449 | 36.5018 | 129.1827 | 190.0136 | 166.4488 | 25.5532 | 8.7696
353.2542 | 210.1217 | 36.7032 | 130.2782 | 190.0085 | 166.3126 | 25.6148 | 8.7865
354.2542 | 210.6509 | 36.8669 | 132.8431 | 189.7965 | 166.5399 | 25.7117 | 8.8029
355.2542 | 210.1274 | 37.0537 | 133.2552 | 190.7729 | 166.6095 | 25.7908 | 8.8171
356.2542 | 209.7229 | 37.2511 | 133.3558 | 191.2211 | 167.6972 | 25.8781 | 8.84
357.2542 | 209.8697 | 37.4438 | 134.2126 | 191.7488 | 168.4788 | 25.9633 | 8.852
358.2542 | 210.1387 | 37.6254 | 134.1812 | 191.9313 | 168.7682 | 26.0352 | 8.8775
359.2542 | 210.5283 | 37.7855 | 135.3882 | 192.376 | 169.0498 | 26.1132 | 8.8844
360.2542 | 211.2038 | 37.9755 | 136.8352 | 192.4485 | 169.0912 | 26.1901 | 8.9147
361.2542 | 211.0537 | 38.2259 | 138.3583 | 192.6564 | 169.2839 | 26.2544 | 8.9233
362.2542 | 210.7056 | 38.4036 | 137.8802 | 193.2418 | 169.6613 | 26.338 | 8.9445
363.2542 | 211.0477 | 38.5871 | 137.378 | 193.4154 | 169.6077 | 26.4169 | 8.9603
364.2542 | 212.0488 | 38.7487 | 137.3803 | 193.6932 | 170.0787 | 26.4904 | 8.9676
365.2542 | 212.36 | 38.9536 | 137.0005 | 192.5917 | 169.9383 | 26.5565 | 8.9948
366.2542 | 212.6644 | 39.1764 | 136.8435 | 192.1789 | 170.0239 | 26.6278 | 9.0102
367.2542 | 213.2388 | 39.3583 | 137.4359 | 191.9351 | 169.9289 | 26.7052 | 9.0234
368.2542 | 214.0421 | 39.5378 | 138.4073 | 191.3152 | 169.7348 | 26.774 | 9.0482
369.2542 | 214.8115 | 39.7368 | 138.5484 | 190.9204 | 169.8036 | 26.8505 | 9.0698
370.2542 | 216.2136 | 39.9215 | 138.6665 | 190.6624 | 169.509 | 26.9262 | 9.0822
371.2542 | 215.4113 | 40.1181 | 138.9802 | 190.9449 | 169.7494 | 27.006 | 9.101
372.2542 | 216.2895 | 40.3 | 139.2192 | 191.599 | 170.6054 | 27.084 | 9.1189
373.2542 | 216.6254 | 40.4862 | 139.1311 | 192.6932 | 170.5406 | 27.1587 | 9.1426
374.2542 | 217.1153 | 40.6761 | 138.9324 | 192.3341 | 170.1868 | 27.2206 | 9.1638
375.2542 | 217.2808 | 40.8816 | 139.1019 | 192.6538 | 169.9765 | 27.2992 | 9.1687
376.2542 | 217.7203 | 41.0781 | 138.8498 | 192.4092 | 169.5152 | 27.381 | 9.1926
377.2542 | 218.0197 | 41.2674 | 138.3252 | 193.103 | 169.341 | 27.4557 | 9.217
378.2542 | 218.0206 | 41.482 | 137.4714 | 193.353 | 169.4928 | 27.5355 | 9.2316
379.2542 | 218.2157 | 41.6542 | 138.1507 | 193.3809 | 169.7749 | 27.6104 | 9.2483
380.2542 | 218.5764 | 41.8575 | 137.6269 | 193.5484 | 169.6562 | 27.6891 | 9.2695
381.2542 | 218.177 | 42.0195 | 137.831 | 193.405 | 170.4465 | 27.7586 | 9.288
382.2542 | 218.3916 | 42.2251 | 138.0435 | 193.2931 | 170.9544 | 27.8538 | 9.3005
383.2542 | 219.2707 | 42.4121 | 137.5794 | 193.2624 | 171.2212 | 27.9346 | 9.3213
384.2542 | 218.617 | 42.6033 | 136.9691 | 193.5853 | 172.1769 | 28.0032 | 9.3323
385.2542 | 218.9489 | 42.8085 | 136.5216 | 193.4578 | 171.9349 | 28.0924 | 9.3664
386.2542 | 219.9556 | 43.0106 | 136.6586 | 193.657 | 171.7975 | 28.1764 | 9.3774
387.2542 | 220.4891 | 43.2171 | 136.9927 | 193.4252 | 172.2253 | 28.2624 | 9.4038
388.2542 | 220.4241 | 43.4165 | 137.1839 | 193.7662 | 173.1924 | 28.3491 | 9.4129
389.2542 | 219.709 | 43.6457 | 137.3403 | 194.6725 | 173.5113 | 28.421 | 9.441
390.2542 | 221.046 | 43.8473 | 137.608 | 196.1506 | 175.0651 | 28.5002 | 9.4509
391.2542 | 220.9709 | 44.0368 | 138.0673 | 196.6774 | 175.1475 | 28.5759 | 9.4742
392.2542 | 220.915 | 44.268 | 138.741 | 197.2545 | 175.6089 | 28.6433 | 9.4992
393.2542 | 221.1635 | 44.4471 | 139.5727 | 198.0727 | 176.7048 | 28.7314 | 9.5198
394.2542 | 221.1435 | 44.6497 | 140.4234 | 198.3903 | 176.9342 | 28.8118 | 9.536
395.2542 | 221.9622 | 44.8629 | 141.7101 | 198.9971 | 176.9098 | 28.9058 | 9.5546
396.2542 | 223.0785 | 45.0794 | 141.7068 | 199.0105 | 177.4185 | 28.9871 | 9.5737
397.2542 | 224.7087 | 45.2736 | 141.6471 | 199.2003 | 177.501 | 29.075 | 9.5811
398.2542 | 224.938 | 45.496 | 142.0214 | 199.215 | 177.6006 | 29.165 | 9.6008
399.2542 | 224.535 | 45.6942 | 142.1122 | 198.8231 | 177.6742 | 29.251 | 9.616
400.2542 | 224.995 | 45.9335 | 141.6535 | 198.3087 | 177.766 | 29.342 | 9.6354
401.2542 | 226.0875 | 46.1224 | 141.2596 | 198.9944 | 177.9255 | 29.4223 | 9.6532
402.2542 | 226.4949 | 46.3569 | 141.2916 | 199.1322 | 177.9519 | 29.506 | 9.6851
403.2542 | 227.3647 | 46.5546 | 141.5069 | 199.5514 | 177.6704 | 29.589 | 9.6973
404.2542 | 229.0437 | 46.7509 | 141.7219 | 199.413 | 178.5013 | 29.6769 | 9.7214
405.2542 | 229.8103 | 46.9814 | 141.4955 | 199.4095 | 177.9748 | 29.7575 | 9.7415
406.2542 | 230.0985 | 47.1816 | 141.0543 | 199.243 | 177.6076 | 29.836 | 9.7735
407.2542 | 229.7577 | 47.4069 | 141.7315 | 199.3643 | 177.9016 | 29.9142 | 9.7932
408.2542 | 230.1095 | 47.6429 | 142.202 | 199.7456 | 178.5582 | 30 | 9.8047
409.2542 | 230.2348 | 47.8752 | 142.7972 | 199.7241 | 178.8591 | 30.0806 | 9.8301
410.2542 | 230.1714 | 48.067 | 143.1201 | 199.0244 | 179.1633 | 30.1485 | 9.8515
411.2542 | 230.2005 | 48.2928 | 143.2867 | 199.2124 | 178.9004 | 30.2266 | 9.8716
412.2542 | 230.2485 | 48.5239 | 143.0614 | 199.0177 | 178.7273 | 30.3045 | 9.8838
413.2542 | 230.9034 | 48.7287 | 143.4732 | 198.6662 | 178.7829 | 30.3769 | 9.9167
414.2542 | 231.6511 | 48.9418 | 143.2908 | 198.6543 | 179.0053 | 30.4516 | 9.9411
415.2542 | 231.2889 | 49.1605 | 143.3026 | 198.9721 | 178.8929 | 30.523 | 9.9526
416.2542 | 230.2735 | 49.3851 | 144.022 | 199.5523 | 178.4584 | 30.5966 | 9.9755
417.2542 | 230.622 | 49.6162 | 144.7801 | 199.5965 | 178.4468 | 30.6876 | 10.0038
418.2542 | 230.7826 | 49.8289 | 144.9401 | 200.5346 | 178.4496 | 30.7664 | 10.0259
419.2542 | 232.4672 | 50.0489 | 144.5331 | 201.3552 | 178.55 | 30.8363 | 10.0407
420.2542 | 234.1515 | 50.2688 | 144.4904 | 201.5327 | 178.1575 | 30.9161 | 10.056
421.2542 | 234.363 | 50.4779 | 144.6624 | 201.1191 | 178.71 | 30.9851 | 10.0927
422.2542 | 235.5932 | 50.6983 | 144.3713 | 201.4861 | 178.4384 | 31.063 | 10.1144
423.2542 | 235.4738 | 50.9131 | 143.6913 | 201.6748 | 179.7332 | 31.1425 | 10.1332
424.2542 | 236.6257 | 51.1381 | 143.6702 | 201.5477 | 179.6312 | 31.2258 | 10.1611
425.2542 | 238.0648 | 51.3544 | 144.123 | 201.2346 | 180.9657 | 31.304 | 10.1819
426.2542 | 238.1109 | 51.5811 | 144.577 | 201.2859 | 181.5059 | 31.3868 | 10.2026
427.2542 | 238.9746 | 51.7921 | 146.3271 | 201.4964 | 180.804 | 31.4579 | 10.221
428.2542 | 238.7182 | 51.9904 | 146.6674 | 201.5961 | 180.5189 | 31.5258 | 10.2478
429.2542 | 238.4981 | 52.2098 | 146.7922 | 201.5402 | 181.0258 | 31.6066 | 10.2722
430.2542 | 239.4088 | 52.4227 | 146.651 | 201.5452 | 181.1252 | 31.6743 | 10.2969
431.2542 | 238.9949 | 52.6305 | 146.7241 | 201.8008 | 181.2147 | 31.7569 | 10.3178
432.2542 | 237.9172 | 52.857 | 146.6506 | 201.3919 | 180.251 | 31.8258 | 10.3518
433.2542 | 238.0516 | 53.0786 | 146.3249 | 201.2494 | 180.7565 | 31.9063 | 10.3605
434.2542 | 237.8968 | 53.3059 | 146.1427 | 201.2477 | 180.4584 | 31.9908 | 10.3903
435.2542 | 238.2312 | 53.5102 | 145.9837 | 200.8961 | 180.5555 | 32.0616 | 10.4135
436.2542 | 239.7996 | 53.7449 | 145.2923 | 200.781 | 182.8631 | 32.1323 | 10.4363
437.2542 | 241.1115 | 53.9598 | 144.7295 | 201.3565 | 182.5649 | 32.208 | 10.4561
438.2542 | 241.1109 | 54.1629 | 144.7469 | 201.9377 | 182.1737 | 32.2938 | 10.4756
439.2542 | 241.8635 | 54.3831 | 145.6525 | 203.3598 | 182.4319 | 32.3676 | 10.5028
440.2542 | 241.8197 | 54.6021 | 146.9997 | 203.8703 | 182.4052 | 32.4356 | 10.5286
441.2542 | 243.0221 | 54.8068 | 147.4541 | 204.027 | 182.3798 | 32.5094 | 10.5558
442.2542 | 243.6951 | 55.0283 | 148.2521 | 204.6469 | 182.49 | 32.5861 | 10.583
443.2542 | 244.1461 | 55.247 | 148.78 | 205.2835 | 182.7168 | 32.6607 | 10.6012
444.2542 | 244.8395 | 55.4605 | 148.3202 | 205.6402 | 182.7875 | 32.7374 | 10.6244
445.2542 | 246.2116 | 55.7022 | 148.015 | 205.2535 | 182.3651 | 32.8174 | 10.6507
446.2542 | 246.6053 | 55.8973 | 147.795 | 204.9153 | 182.3379 | 32.8921 | 10.6674
447.2542 | 247.2175 | 56.1167 | 147.4769 | 204.7471 | 182.1399 | 32.9709 | 10.6885
448.2542 | 247.5439 | 56.3342 | 147.2041 | 204.1945 | 182.1879 | 33.0517 | 10.7182
449.2542 | 248.9077 | 56.5495 | 147.1091 | 204.0249 | 182.7966 | 33.1369 | 10.7406
450.2542 | 249.594 | 56.7933 | 146.8165 | 204.2708 | 182.7004 | 33.2092 | 10.7654
451.2542 | 250.1317 | 57.0325 | 146.7909 | 204.0201 | 183.5402 | 33.2973 | 10.7863
452.2542 | 250.7064 | 57.2655 | 146.9094 | 203.712 | 184.8485 | 33.358 | 10.8157
453.2542 | 251.2946 | 57.4785 | 146.2661 | 203.6792 | 184.8488 | 33.4531 | 10.8451
454.2542 | 251.2527 | 57.7108 | 146.0207 | 203.6885 | 184.472 | 33.5298 | 10.8681
455.2542 | 250.1217 | 57.9139 | 145.5886 | 203.4253 | 185.5896 | 33.6154 | 10.8888
456.2542 | 249.7619 | 58.179 | 145.8521 | 203.0411 | 186.0442 | 33.6899 | 10.9086
457.2542 | 248.9148 | 58.3864 | 145.6169 | 202.8025 | 186.9708 | 33.765 | 10.9407
458.2542 | 249.113 | 58.6191 | 145.3111 | 203.517 | 187.2728 | 33.8505 | 10.9678
459.2542 | 249.2732 | 58.847 | 144.8467 | 203.7676 | 188.6804 | 33.9228 | 10.9852
460.2542 | 250.6243 | 59.0664 | 145.4744 | 204.0279 | 188.5502 | 34.0042 | 11.0149
461.2542 | 251.8076 | 59.2993 | 145.2898 | 204.2351 | 189.1823 | 34.1061 | 11.0293
462.2542 | 252.2057 | 59.5412 | 144.911 | 205.3858 | 189.1083 | 34.172 | 11.0592
463.2542 | 250.6574 | 59.7872 | 144.9893 | 205.2117 | 188.9182 | 34.2552 | 11.0829
464.2542 | 250.4828 | 60.0066 | 146.361 | 205.9371 | 189.5929 | 34.3358 | 11.1093
465.2542 | 250.2997 | 60.2287 | 147.6004 | 206.0786 | 189.5512 | 34.4229 | 11.1318
466.2542 | 249.7981 | 60.4177 | 148.3606 | 206.414 | 189.575 | 34.5045 | 11.1597
467.2542 | 250.409 | 60.6658 | 149.1167 | 206.4514 | 190.7645 | 34.5872 | 11.1791
468.2542 | 251.6647 | 60.8925 | 149.2677 | 207.1202 | 191.113 | 34.6652 | 11.2066
469.2542 | 251.6293 | 61.1111 | 149.7166 | 206.5294 | 192.5476 | 34.7513 | 11.2286
470.2542 | 252.3225 | 61.3199 | 150.0262 | 206.0998 | 193.3962 | 34.8244 | 11.2626
471.2542 | 252.1141 | 61.5481 | 149.6211 | 205.931 | 193.0517 | 34.8947 | 11.2739
472.2542 | 252.6617 | 61.7751 | 149.7402 | 206.0722 | 193.0932 | 34.9829 | 11.3112
473.2542 | 253.6323 | 61.9878 | 149.906 | 206.1979 | 192.8036 | 35.056 | 11.3318
474.2542 | 253.2776 | 62.2187 | 150.0328 | 206.6313 | 192.178 | 35.1353 | 11.35
475.2542 | 253.3511 | 62.4599 | 149.728 | 206.4961 | 192.2229 | 35.2022 | 11.3818
476.2542 | 252.1216 | 62.6459 | 149.8083 | 206.1263 | 192.1681 | 35.2811 | 11.4103
477.2542 | 252.5284 | 62.8626 | 149.9375 | 206.0745 | 192.3697 | 35.3561 | 11.4274
478.2542 | 252.4298 | 63.0907 | 150.4115 | 205.7826 | 192.5596 | 35.4312 | 11.4542
479.2542 | 251.6892 | 63.3078 | 150.409 | 205.8505 | 192.8386 | 35.5061 | 11.4814
480.2542 | 252.6018 | 63.5359 | 150.2768 | 206.038 | 193.8744 | 35.5723 | 11.513
481.2542 | 252.6308 | 63.7737 | 150.1272 | 206.1899 | 194.7048 | 35.648 | 11.5349
482.2542 | 253.4435 | 64.0021 | 150.4952 | 206.7319 | 194.9255 | 35.717 | 11.5648
483.2542 | 253.2443 | 64.1962 | 152.5454 | 206.3407 | 194.6402 | 35.7862 | 11.5856
484.2542 | 253.0868 | 64.4005 | 152.9664 | 206.4795 | 194.764 | 35.8713 | 11.6137
485.2542 | 254.2263 | 64.6144 | 154.1039 | 206.4604 | 194.6131 | 35.9437 | 11.6428
486.2542 | 254.2631 | 64.8472 | 154.8933 | 206.4304 | 194.0638 | 36.0167 | 11.6622
487.2542 | 255.5816 | 65.0501 | 155.9342 | 206.1696 | 193.7519 | 36.0849 | 11.6877
488.2542 | 255.6566 | 65.2857 | 156.0213 | 205.9742 | 193.2347 | 36.1579 | 11.7255
489.2542 | 255.12 | 65.5157 | 155.7366 | 206.0173 | 192.9573 | 36.2318 | 11.7518
490.2542 | 254.9638 | 65.6987 | 156.8773 | 206.3611 | 193.0295 | 36.3118 | 11.7744
491.2542 | 254.5463 | 65.936 | 156.4065 | 206.5316 | 192.7868 | 36.3754 | 11.8071
492.2542 | 253.7941 | 66.1416 | 156.2416 | 206.2753 | 192.4231 | 36.448 | 11.8214
493.2542 | 253.5235 | 66.3347 | 155.9523 | 206.3256 | 192.3978 | 36.5122 | 11.8577
494.2542 | 253.9222 | 66.5662 | 155.6848 | 206.2696 | 192.2727 | 36.5823 | 11.8882
495.2542 | 253.6633 | 66.7955 | 155.6873 | 206.4423 | 191.8701 | 36.634 | 11.9064
496.2542 | 255.7827 | 67.0145 | 155.4767 | 206.3533 | 191.7847 | 36.6957 | 11.9253
497.2542 | 256.209 | 67.2211 | 154.9225 | 206.3554 | 191.7183 | 36.7687 | 11.9587
498.2542 | 256.1447 | 67.4525 | 154.1735 | 206.1217 | 191.7559 | 36.8425 | 11.9804
499.2542 | 256.3761 | 67.6605 | 154.0433 | 207.0192 | 191.9148 | 36.9153 | 12.0099
500.2542 | 256.3158 | 67.8789 | 153.6947 | 206.682 | 191.994 | 36.991 | 12.0357
501.2542 | 257.5452 | 68.0976 | 153.0249 | 207.0667 | 192.9395 | 37.0622 | 12.0601
502.2542 | 257.236 | 68.2786 | 152.482 | 208.7619 | 193.4074 | 37.1405 | 12.0917
503.2542 | 256.2096 | 68.5097 | 153.9987 | 208.89 | 193.5373 | 37.2184 | 12.1212
504.2542 | 255.7546 | 68.7288 | 153.8387 | 208.4732 | 194.7738 | 37.2776 | 12.1543
505.2542 | 258.1178 | 68.9551 | 153.8524 | 209.1217 | 194.2897 | 37.3558 | 12.1747
506.2542 | 256.9024 | 69.1574 | 154.3698 | 210.669 | 193.1552 | 37.4372 | 12.206
507.2542 | 256.5133 | 69.3863 | 155.4823 | 210.8582 | 193.3086 | 37.5082 | 12.2318
508.2542 | 256.9849 | 69.5959 | 155.1504 | 210.4318 | 193.0648 | 37.5831 | 12.2562
509.2542 | 257.1144 | 69.8116 | 154.7325 | 210.051 | 192.9147 | 37.6685 | 12.2745
510.2542 | 257.4636 | 70.0058 | 154.9238 | 209.8778 | 192.6343 | 37.7333 | 12.3131
511.2542 | 258.8855 | 70.2418 | 155.2204 | 209.6406 | 192.1647 | 37.8158 | 12.3421
512.2542 | 261.8508 | 70.4538 | 155.487 | 209.2914 | 192.2405 | 37.8955 | 12.3675
513.2542 | 262.4538 | 70.6475 | 154.8578 | 209.0774 | 192.3694 | 37.9694 | 12.3942
514.2542 | 262.204 | 70.8771 | 155.0147 | 209.2369 | 192.4582 | 38.0336 | 12.4234
515.2542 | 260.9213 | 71.0971 | 155.5943 | 209.4477 | 192.763 | 38.1178 | 12.4553
516.2542 | 260.4736 | 71.3084 | 157.1297 | 209.505 | 193.4745 | 38.1975 | 12.4787
517.2542 | 260.1236 | 71.5326 | 157.1133 | 209.8041 | 193.8927 | 38.2901 | 12.5054
518.2542 | 258.6992 | 71.7576 | 156.786 | 209.9208 | 194.2156 | 38.3755 | 12.5396
519.2542 | 257.4302 | 71.9613 | 156.0934 | 213.1498 | 194.753 | 38.4494 | 12.5702
520.2542 | 258.3431 | 72.1647 | 156.7996 | 212.4612 | 195.1419 | 38.5349 | 12.5894
521.2542 | 259.5191 | 72.3851 | 156.971 | 212.0727 | 196.5129 | 38.6227 | 12.6205
522.2542 | 259.9697 | 72.5986 | 157.281 | 211.9895 | 196.1864 | 38.704 | 12.6488
523.2542 | 259.1282 | 72.8035 | 157.6388 | 211.7128 | 195.5688 | 38.7809 | 12.678
524.2542 | 259.5552 | 73.0016 | 158.1425 | 211.3811 | 195.9305 | 38.8653 | 12.7077
525.2542 | 261.0517 | 73.234 | 158.0158 | 211.0585 | 195.2707 | 38.9404 | 12.7411
526.2542 | 260.4217 | 73.4614 | 157.8494 | 211.1777 | 195.7473 | 39.0168 | 12.759
527.2542 | 261.3573 | 73.6736 | 157.0842 | 211.5254 | 196.6052 | 39.1116 | 12.7806
528.2542 | 259.1207 | 73.8863 | 156.8832 | 211.2849 | 196.2457 | 39.1876 | 12.8145
529.2542 | 258.6933 | 74.0744 | 156.1072 | 210.9662 | 196.721 | 39.2574 | 12.8383
530.2542 | 259.487 | 74.2926 | 155.9315 | 212.7599 | 196.9149 | 39.332 | 12.8681
531.2542 | 259.2822 | 74.4906 | 157.1318 | 212.8502 | 196.7906 | 39.417 | 12.8984
532.2542 | 260.8014 | 74.6919 | 157.1012 | 213.066 | 196.6598 | 39.5014 | 12.9264
533.2542 | 260.1918 | 74.8778 | 158.0748 | 213.2134 | 196.8615 | 39.5743 | 12.9631
534.2542 | 261.5223 | 75.0711 | 157.9442 | 212.6166 | 196.9661 | 39.6592 | 12.9837
535.2542 | 260.8783 | 75.2924 | 158.3308 | 212.451 | 198.2371 | 39.7322 | 13.0191
536.2542 | 260.1463 | 75.5015 | 158.2719 | 212.529 | 198.5598 | 39.8085 | 13.0426
537.2542 | 260.3108 | 75.7173 | 157.9331 | 212.3706 | 199.8783 | 39.8894 | 13.068
538.2542 | 259.98 | 75.9218 | 157.2773 | 212.0155 | 200.132 | 39.9764 | 13.0986
539.2542 | 260.4806 | 76.133 | 157.3417 | 212.0964 | 199.7013 | 40.0491 | 13.1337
540.2542 | 261.1899 | 76.314 | 158.1372 | 211.874 | 198.9451 | 40.1244 | 13.1546
541.2542 | 261.4944 | 76.5313 | 157.7011 | 212.0414 | 199.5269 | 40.2066 | 13.1866
542.2542 | 261.0207 | 76.7286 | 157.823 | 212.6574 | 201.0655 | 40.2739 | 13.2028
543.2542 | 260.7911 | 76.9187 | 158.3049 | 213.1839 | 201.8133 | 40.3606 | 13.2511
544.2542 | 260.6357 | 77.1395 | 158.2615 | 213.1393 | 201.4771 | 40.4375 | 13.269
545.2542 | 259.5873 | 77.3243 | 158.6082 | 212.6701 | 201.5238 | 40.5152 | 13.2867
546.2542 | 259.6584 | 77.5373 | 158.5755 | 212.4255 | 200.8617 | 40.591 | 13.3204
547.2542 | 260.331 | 77.7435 | 158.4262 | 212.4922 | 202.5136 | 40.6703 | 13.3525
548.2542 | 260.8877 | 77.9491 | 159.3488 | 212.7725 | 201.8631 | 40.7482 | 13.3801
549.2542 | 261.9205 | 78.1549 | 160.474 | 212.6303 | 202.0506 | 40.8179 | 13.4106
550.2542 | 261.7191 | 78.3736 | 159.6597 | 212.7087 | 202.9994 | 40.8901 | 13.4425
551.2542 | 261.9112 | 78.5715 | 158.8892 | 212.4113 | 203.1889 | 40.9576 | 13.476
552.2542 | 262.0983 | 78.7773 | 158.6867 | 211.919 | 202.4297 | 41.026 | 13.5027
553.2542 | 262.2982 | 79.0061 | 158.2958 | 211.4979 | 202.3038 | 41.1025 | 13.5313
554.2542 | 262.187 | 79.2057 | 158.8505 | 211.3546 | 202.9018 | 41.1678 | 13.5663
555.2542 | 262.659 | 79.4181 | 160.4027 | 211.5769 | 203.5387 | 41.2387 | 13.5976
556.2542 | 263.9097 | 79.6231 | 161.1844 | 211.8569 | 203.6416 | 41.3075 | 13.6258
557.2542 | 264.7355 | 79.8349 | 160.942 | 212.3338 | 203.7257 | 41.3955 | 13.644
558.2542 | 265.4892 | 80.0202 | 160.5781 | 212.4754 | 203.2085 | 41.4625 | 13.6783
559.2542 | 265.2269 | 80.2484 | 160.3748 | 212.303 | 203.1611 | 41.5398 | 13.7108
560.2542 | 265.5482 | 80.4593 | 160.3246 | 212.4216 | 202.4929 | 41.6079 | 13.7372
561.2542 | 267.0746 | 80.6638 | 160.3041 | 212.3577 | 202.1795 | 41.6812 | 13.757
562.2542 | 266.6931 | 80.8765 | 159.4899 | 212.2835 | 202.45 | 41.7431 | 13.8065
563.2542 | 265.1591 | 81.1046 | 158.7542 | 212.6759 | 203.6484 | 41.8139 | 13.8267
564.2542 | 265.0924 | 81.2989 | 157.8096 | 213.2907 | 203.6273 | 41.8964 | 13.8519
565.2542 | 265.9507 | 81.5155 | 157.8812 | 214.0418 | 203.1804 | 41.9555 | 13.8851
566.2542 | 266.0872 | 81.7203 | 157.7976 | 213.4682 | 203.8178 | 42.0295 | 13.9023
567.2542 | 268.0979 | 81.9174 | 157.1587 | 213.2431 | 204.3625 | 42.0905 | 13.9434
568.2542 | 269.7272 | 82.1228 | 156.4931 | 213.3759 | 204.5225 | 42.1629 | 13.9709
569.2542 | 269.4158 | 82.3392 | 155.5744 | 213.2047 | 204.0889 | 42.2287 | 13.9929
570.2542 | 268.9358 | 82.5457 | 155.1846 | 212.9292 | 203.9689 | 42.302 | 14.0251
571.2542 | 270.039 | 82.7446 | 155.6462 | 213.0095 | 203.4087 | 42.3629 | 14.0497
572.2542 | 270.073 | 82.9582 | 156.103 | 212.9552 | 202.9842 | 42.4369 | 14.08
573.2542 | 270.0803 | 83.1498 | 156.3817 | 212.5308 | 202.4695 | 42.4999 | 14.1092
574.2542 | 270.0204 | 83.3584 | 156.7483 | 212.5926 | 203.1082 | 42.5653 | 14.1355
575.2542 | 270.4689 | 83.5789 | 156.7535 | 212.7289 | 203.0868 | 42.6299 | 14.1784
576.2542 | 271.4613 | 83.7695 | 157.4573 | 212.4245 | 203.3544 | 42.7014 | 14.2046
577.2542 | 271.8721 | 83.9911 | 158.6794 | 211.7403 | 204.1609 | 42.7675 | 14.2235
578.2542 | 271.3357 | 84.1862 | 158.6149 | 211.9174 | 204.5696 | 42.8493 | 14.2579
579.2542 | 271.0092 | 84.4075 | 158.5234 | 212.8 | 204.3884 | 42.9144 | 14.284
580.2542 | 271.4324 | 84.6232 | 159.2278 | 213.4408 | 203.8058 | 42.983 | 14.3085
581.2542 | 271.8451 | 84.8235 | 159.6815 | 213.0618 | 204.2728 | 43.0506 | 14.3422
582.2542 | 272.4219 | 85.0214 | 160.598 | 213.6261 | 204.8863 | 43.1224 | 14.3601
583.2542 | 273.221 | 85.1954 | 160.8767 | 213.9576 | 205.2419 | 43.2018 | 14.3939
584.2542 | 273.2522 | 85.4269 | 161.31 | 214.7503 | 205.7146 | 43.2813 | 14.4317
585.2542 | 272.1688 | 85.6328 | 161.9225 | 215.7583 | 205.9637 | 43.3475 | 14.4569
586.2542 | 272.3558 | 85.837 | 162.3391 | 216.2391 | 206.1473 | 43.4179 | 14.4826
587.2542 | 272.0503 | 86.031 | 163.5997 | 216.3254 | 206.0006 | 43.4947 | 14.5227
588.2542 | 269.8309 | 86.2349 | 163.0793 | 216.2134 | 206.3994 | 43.5641 | 14.5407
589.2542 | 268.9369 | 86.4461 | 163.083 | 216.6322 | 206.9916 | 43.6367 | 14.5724
590.2542 | 269.105 | 86.6462 | 163.3541 | 218.4139 | 206.6732 | 43.711 | 14.6021
591.2542 | 269.5477 | 86.8543 | 163.8406 | 218.5432 | 208.1235 | 43.7845 | 14.6449
592.2542 | 270.7097 | 87.0571 | 163.7439 | 218.2227 | 208.2477 | 43.8787 | 14.6812
593.2542 | 271.6911 | 87.2816 | 162.9269 | 217.7169 | 207.2333 | 43.9546 | 14.6947
594.2542 | 273.2071 | 87.4946 | 162.1729 | 217.7207 | 206.5492 | 44.039 | 14.7364
595.2542 | 274.4374 | 87.6875 | 162.6596 | 217.6583 | 205.6297 | 44.1061 | 14.7622
596.2542 | 274.206 | 87.9366 | 162.8502 | 217.2308 | 205.1904 | 44.1801 | 14.8041
597.2542 | 274.6215 | 88.1177 | 162.6078 | 217.1534 | 204.5038 | 44.1976 | 14.8015
598.2542 | 274.1635 | 88.3197 | 163.0896 | 217.3927 | 204.4188 | 44.2673 | 14.8336
599.2542 | 273.9184 | 88.5168 | 162.7222 | 217.246 | 203.7115 | 44.3387 | 14.8584
600.2542 | 274.498 | 88.7221 | 162.9424 | 217.3754 | 203.8848 | 44.4217 | 14.8927
601.2542 | 276.3119 | 88.9176 | 162.2919 | 217.1217 | 203.3727 | 44.5082 | 14.9182
602.2542 | 275.705 | 89.132 | 162.0145 | 217.0862 | 202.9348 | 44.5477 | 14.9402
603.2542 | 275.6507 | 89.3644 | 161.2668 | 216.8265 | 203.097 | 44.6395 | 14.994
604.2542 | 275.1449 | 89.572 | 160.4813 | 216.8787 | 203.4248 | 44.6773 | 15.0084
605.2542 | 274.6189 | 89.7582 | 160.7333 | 217.6713 | 203.8216 | 44.7356 | 15.0386
606.2542 | 273.4693 | 89.9784 | 161.3911 | 218.1698 | 204.738 | 44.8129 | 15.0567
607.2542 | 273.4991 | 90.1186 | 161.295 | 217.7298 | 204.9112 | 44.9688 | 15.1137
608.2542 | 274.6938 | 90.3852 | 160.9325 | 217.5185 | 205.2671 | 45.0016 | 15.1373
609.2542 | 274.9362 | 90.5968 | 162.4814 | 217.6348 | 204.9847 | 45.0455 | 15.1577
610.2542 | 275.7365 | 90.8215 | 162.4654 | 217.4044 | 205.0821 | 45.1056 | 15.1908
611.2542 | 274.8632 | 91.0081 | 162.6859 | 217.619 | 205.2476 | 45.1869 | 15.2188
612.2542 | 273.6904 | 91.2155 | 162.3899 | 218.1803 | 205.0355 | 45.2597 | 15.2407
613.2542 | 274.5287 | 91.4492 | 162.6961 | 218.6097 | 205.5068 | 45.319 | 15.2778
614.2542 | 277.1903 | 91.6512 | 162.4759 | 218.3825 | 205.3801 | 45.3787 | 15.3097
615.2542 | 276.3278 | 91.8542 | 162.7989 | 218.3117 | 205.2789 | 45.4596 | 15.3268
616.2542 | 276.2641 | 92.0501 | 163.2772 | 218.5172 | 205.5793 | 45.5296 | 15.358
617.2542 | 276.1588 | 92.2685 | 163.9221 | 218.4688 | 206.6158 | 45.6086 | 15.4011
618.2542 | 277.9429 | 92.4659 | 164.5105 | 218.3259 | 206.4865 | 45.7051 | 15.4399
619.2542 | 276.7164 | 92.6787 | 164.9344 | 218.8236 | 206.1058 | 45.7733 | 15.471
620.2542 | 277.7903 | 92.9067 | 165.5342 | 218.5967 | 205.6176 | 45.8438 | 15.4927
621.2542 | 278.6351 | 93.0982 | 166.1529 | 218.63 | 205.7604 | 45.9132 | 15.5174
622.2542 | 279.2979 | 93.3051 | 166.6235 | 218.5434 | 206.5387 | 45.9768 | 15.541
623.2542 | 279.5941 | 93.5247 | 166.3161 | 218.2597 | 206.6168 | 46.0555 | 15.5755
624.2542 | 279.0348 | 93.7104 | 167.2639 | 218.7948 | 207.3535 | 46.1295 | 15.5972
625.2542 | 278.7496 | 93.95 | 167.4302 | 220.1304 | 207.244 | 46.2115 | 15.6299
626.2542 | 278.728 | 94.143 | 167.1552 | 220.7075 | 206.9994 | 46.2752 | 15.6619
627.2542 | 278.929 | 94.3553 | 167.656 | 220.9435 | 206.8815 | 46.3736 | 15.6957
628.2542 | 279.5868 | 94.5566 | 167.3573 | 221.0571 | 206.7195 | 46.4504 | 15.7316
629.2542 | 278.0226 | 94.7749 | 166.7575 | 221.0738 | 206.7917 | 46.5364 | 15.7559
630.2542 | 277.8007 | 94.9648 | 166.0225 | 221.2666 | 206.9927 | 46.6249 | 15.7902
631.2542 | 278.3601 | 95.1898 | 165.6079 | 221.5983 | 207.0797 | 46.7102 | 15.8232
632.2542 | 281.437 | 95.4036 | 165.3045 | 221.3287 | 206.9974 | 46.7775 | 15.8675
633.2542 | 280.8028 | 95.5941 | 164.9239 | 222.364 | 207.3046 | 46.8246 | 15.8681
634.2542 | 281.071 | 95.8104 | 165.9023 | 222.9442 | 54.9621 | 46.8793 | 15.9001
635.2542 | 281.13 | 96.0329 | 166.156 | 222.9267 | 13.2008 | 46.9592 | 15.9396
636.2542 | 281.8834 | 96.233 | 166.2452 | 222.7003 | 174.2415 | 47.0526 | 15.9611
637.2542 | 281.6305 | 96.4521 | 169.1627 | 222.7646 | 9.6965 | 47.11 | 15.9995
638.2542 | 280.1021 | 96.6468 | 168.7613 | 222.2536 | 23.4323 | 47.1971 | 16.0168
639.2542 | 279.472 | 96.8687 | 170.1047 | 221.449 | 179.2664 | 47.2896 | 16.0617
640.2542 | 279.3999 | 97.0885 | 170.2984 | 221.5688 | 9.3697 | 47.3541 | 16.0857
641.2542 | 280.5048 | 97.2956 | 169.6232 | 222.8836 | 9.134 | 47.4555 | 16.1219
642.2542 | 280.7628 | 97.4945 | 170.3419 | 223.509 | 9.1234 | 47.5146 | 16.1319
643.2542 | 279.8712 | 97.721 | 170.3251 | 223.2415 | 9.1111 | 47.6068 | 16.1668
644.2542 | 280.0632 | 97.9153 | 170.7018 | 223.5511 | 9.1135 | 47.6921 | 16.2045
645.2542 | 280.6215 | 98.132 | 171.0021 | 223.5391 | 11.305 | 47.78 | 16.2357
646.2542 | 280.178 | 98.3435 | 170.2368 | 223.6527 | 87.8926 | 47.8857 | 16.267
647.2542 | 280.9604 | 98.5334 | 169.3803 | 223.6305 | 39.4208 | 47.9658 | 16.2909
648.2542 | 279.0463 | 98.7455 | 168.9296 | 223.8868 | 21.5798 | 48.0054 | 16.3026
649.2542 | 280.1259 | 98.9783 | 169.2167 | 223.794 | 42.3046 | 48.1395 | 16.3763
650.2542 | 281.5968 | 99.1847 | 170.1572 | 224.3277 | 9.1246 | 48.202 | 16.3836
651.2542 | 280.6989 | 99.368 | 170.4835 | 223.9854 | 9.1201 | 48.2857 | 16.4286
652.2542 | 279.6675 | 99.6003 | 170.9687 | 224.3816 | 9.1186 | 48.3444 | 16.4517
653.2542 | 278.9365 | 99.7966 | 170.9342 | 224.607 | 9.1139 | 48.4326 | 16.4767
654.2542 | 278.6554 | 100.0161 | 170.4865 | 224.241 | 9.1195 | 48.5296 | 16.5199
655.2542 | 278.006 | 100.2311 | 170.6527 | 223.9858 | 24.487 | 48.6254 | 16.5525
656.2542 | 277.7659 | 100.4307 | 171.3947 | 224.1634 | 9.1132 | 48.6813 | 16.5679
657.2542 | 278.3613 | 100.6241 | 170.7757 | 223.7862 | 17.5388 | 48.7447 | 16.5794
658.2542 | 278.4474 | 100.8514 | 170.197 | 223.5321 | 96.3236 | 48.8808 | 16.6571
659.2542 | 278.2123 | 101.0396 | 169.745 | 223.4791 | 14.713 | 48.9584 | 16.6722
660.2542 | 277.4614 | 101.2349 | 169.3944 | 223.3772 | 15.427 | 49.0373 | 16.7143
661.2542 | 276.9639 | 101.4424 | 169.3605 | 223.3935 | 9.1426 | 49.0999 | 16.7298
662.2542 | 276.7963 | 101.6424 | 168.4327 | 222.7409 | 9.1291 | 49.189 | 16.7782
663.2542 | 278.9017 | 101.8657 | 167.6167 | 221.3072 | 208.0579 | 49.4951 | 16.861
664.2542 | 280.1184 | 102.0763 | 167.0203 | 221.3627 | 207.5289 | 49.5635 | 16.8953
665.2542 | 281.9441 | 102.3059 | 167.0179 | 220.8695 | 206.8736 | 49.6381 | 16.9252
666.2542 | 282.9044 | 102.4889 | 166.9994 | 220.7921 | 206.9923 | 49.7106 | 16.9484
667.2542 | 284.2165 | 102.6899 | 167.459 | 220.7064 | 207.0914 | 49.7919 | 16.9836
668.2542 | 283.7013 | 102.9169 | 167.7952 | 222.3877 | 208.3614 | 49.87 | 17.0206
669.2542 | 282.9788 | 103.1154 | 167.8059 | 223.0034 | 208.7601 | 49.9548 | 17.0516
670.2542 | 282.1475 | 103.3092 | 170.765 | 223.1726 | 209.1046 | 50.0432 | 17.0865
671.2542 | 282.8423 | 103.5155 | 170.5858 | 223.7124 | 209.5281 | 50.1198 | 17.1123
672.2542 | 283.5646 | 103.7336 | 171.8422 | 223.7851 | 210.1242 | 50.193 | 17.1318
673.2542 | 284.8453 | 103.9326 | 171.0715 | 223.9852 | 210.3768 | 50.2711 | 17.1801
674.2542 | 285.5479 | 104.1527 | 170.3102 | 223.9015 | 210.0271 | 50.3734 | 17.2141
675.2542 | 285.5059 | 104.3673 | 169.7392 | 223.7181 | 210.0749 | 50.4624 | 17.2593
676.2542 | 285.3992 | 104.5607 | 169.5388 | 223.699 | 209.8342 | 50.4999 | 17.2622
677.2542 | 286.0429 | 104.753 | 169.4958 | 223.6069 | 210.2903 | 50.5846 | 17.3081
678.2542 | 283.8314 | 104.9811 | 169.2799 | 223.6485 | 210.4676 | 50.6752 | 17.3327
679.2542 | 283.608 | 105.1778 | 169.5756 | 223.8365 | 210.3011 | 50.7758 | 17.3648
680.2542 | 282.9963 | 105.3554 | 169.3887 | 224.0742 | 210.0313 | 50.87 | 17.4007
681.2542 | 284.0073 | 105.5873 | 169.9917 | 224.3404 | 210.5201 | 50.9488 | 17.4256
682.2542 | 284.1026 | 105.7952 | 171.4455 | 224.4253 | 210.8744 | 51.0327 | 17.4637
683.2542 | 283.2335 | 105.9936 | 172.1311 | 224.4416 | 211.2326 | 51.1273 | 17.4952
684.2542 | 283.5253 | 106.1878 | 172.7312 | 225.1391 | 211.3563 | 51.213 | 17.5195
685.2542 | 284.0561 | 106.4059 | 172.4743 | 224.7293 | 211.7145 | 51.3035 | 17.5624
686.2542 | 285.7564 | 106.638 | 172.6856 | 224.8098 | 211.6017 | 51.3831 | 17.5792
687.2542 | 285.2263 | 106.8376 | 173.3378 | 225.1391 | 211.9994 | 51.4552 | 17.6068
688.2542 | 286.7891 | 107.0214 | 173.75 | 225.6425 | 213.0735 | 51.5459 | 17.6553
689.2542 | 285.5698 | 107.2385 | 173.7542 | 226.2373 | 213.7507 | 51.6322 | 17.6859
690.2542 | 284.247 | 107.4539 | 173.5808 | 226.1035 | 213.7942 | 51.7155 | 17.704
691.2542 | 285.5014 | 107.6767 | 174.0645 | 226.6126 | 214.7055 | 51.7861 | 17.7339
692.2542 | 285.0102 | 107.8827 | 174.3225 | 226.7808 | 214.3125 | 51.837 | 17.76
693.2542 | 285.3519 | 108.0741 | 174.8172 | 227.4155 | 215.0308 | 51.9183 | 17.7938
694.2542 | 286.0809 | 108.2915 | 175.1568 | 228.3657 | 215.5115 | 51.9961 | 17.8129
695.2542 | 285.2449 | 108.5293 | 175.1463 | 227.4817 | 215.4759 | 52.0737 | 17.851
696.2542 | 285.1054 | 108.7335 | 175.4847 | 227.9965 | 214.7277 | 52.1541 | 17.8805
697.2542 | 284.3459 | 108.9561 | 175.8575 | 227.7734 | 215.0671 | 52.2474 | 17.9118
698.2542 | 285.3193 | 109.1687 | 176.7737 | 227.438 | 215.3877 | 52.3311 | 17.947
699.2542 | 284.8752 | 109.3798 | 176.8163 | 226.6118 | 215.6181 | 52.4213 | 17.9664
700.2542 | 284.355 | 109.5926 | 177.212 | 226.3271 | 215.6587 | 52.493 | 18.0122
701.2542 | 285.9054 | 109.7933 | 177.7561 | 226.2704 | 216.1005 | 52.5877 | 18.035
702.2542 | 285.8329 | 110.0034 | 177.8363 | 225.996 | 216.4233 | 52.6823 | 18.0707
703.2542 | 285.3141 | 110.2338 | 177.3784 | 225.4504 | 216.7633 | 52.7698 | 18.1024
704.2542 | 287.9955 | 110.4307 | 177.2489 | 225.4499 | 216.6381 | 52.8415 | 18.1406
705.2542 | 289.9107 | 110.6584 | 176.8584 | 225.6985 | 216.7446 | 52.9297 | 18.1638
706.2542 | 289.7517 | 110.8686 | 176.7479 | 225.4926 | 216.6465 | 53.0072 | 18.1954
707.2542 | 288.2071 | 111.0793 | 177.129 | 225.2304 | 216.8474 | 53.0995 | 18.2253
708.2542 | 287.941 | 111.2889 | 177.169 | 225.2144 | 217.5733 | 53.2024 | 18.2577
709.2542 | 288.7874 | 111.506 | 177.3865 | 225.0686 | 218.0356 | 53.2901 | 18.2999
710.2542 | 289.5703 | 111.7261 | 177.5616 | 225.2459 | 217.9803 | 53.369 | 18.3129
711.2542 | 291.6858 | 111.9363 | 176.9959 | 225.4778 | 217.7784 | 53.4614 | 18.3483
712.2542 | 291.4452 | 112.1468 | 176.6291 | 225.7131 | 218.1689 | 53.5466 | 18.381
713.2542 | 290.0882 | 112.351 | 176.6291 | 225.2608 | 218.6603 | 53.6543 | 18.4179
714.2542 | 290.9769 | 112.5669 | 176.0198 | 225.431 | 218.6484 | 53.7404 | 18.4437
715.2542 | 290.4467 | 112.7853 | 175.7872 | 226.2597 | 220.1227 | 53.8283 | 18.4759
716.2542 | 290.467 | 113.0007 | 175.3539 | 225.9256 | 218.9348 | 53.9153 | 18.4975
717.2542 | 291.1895 | 113.1938 | 175.1158 | 225.1995 | 219.1871 | 54.0013 | 18.5201
718.2542 | 292.909 | 113.4361 | 176.043 | 224.715 | 218.3945 | 54.0877 | 18.5631
719.2542 | 291.7996 | 113.6588 | 176.6078 | 224.8592 | 218.0647 | 54.163 | 18.5965
720.2542 | 290.7893 | 113.8839 | 176.5986 | 225.2651 | 217.6816 | 54.2539 | 18.6285
721.2542 | 290.8884 | 114.0888 | 176.1818 | 225.1887 | 217.8916 | 54.3402 | 18.6552
722.2542 | 290.8737 | 114.3132 | 175.9175 | 225.0703 | 218.0484 | 54.4119 | 18.691
723.2542 | 290.0844 | 114.5444 | 176.3808 | 225.9908 | 218.6989 | 54.4984 | 18.7062
724.2542 | 291.8852 | 114.7418 | 176.6526 | 226.2497 | 218.8876 | 54.5839 | 18.7578
725.2542 | 290.237 | 114.9836 | 176.8446 | 226.4854 | 219.0669 | 54.6525 | 18.7741
726.2542 | 289.9023 | 115.1953 | 176.9843 | 227.0327 | 219.5052 | 54.7431 | 18.8013
727.2542 | 289.6738 | 115.4244 | 177.1493 | 227.3479 | 220.3453 | 54.8184 | 18.8344
728.2542 | 290.237 | 115.6307 | 177.7792 | 227.3159 | 219.9649 | 54.9029 | 18.8686
729.2542 | 290.2656 | 115.835 | 178.2811 | 226.9786 | 220.0736 | 54.9769 | 18.8991
730.2542 | 289.3118 | 116.054 | 179.9468 | 226.4421 | 220.4402 | 55.0403 | 18.9262
731.2542 | 289.1226 | 116.2932 | 179.8078 | 226.1136 | 220.1865 | 55.1203 | 18.9582
732.2542 | 289.3737 | 116.494 | 179.8397 | 226.0728 | 220.1428 | 55.2161 | 18.9881
733.2542 | 290.2964 | 116.7223 | 180.5637 | 225.9882 | 220.7982 | 55.3102 | 19.0189
734.2542 | 290.127 | 116.9421 | 180.9103 | 226.3562 | 220.6585 | 55.3867 | 19.0476
735.2542 | 291.9771 | 117.1534 | 181.4457 | 227.144 | 220.6527 | 55.4695 | 19.0762
736.2542 | 291.118 | 117.3559 | 181.4637 | 226.9538 | 221.9532 | 55.579 | 19.1155
737.2542 | 290.9054 | 117.5817 | 181.4998 | 226.8985 | 222.1714 | 55.6905 | 19.1413
738.2542 | 291.2742 | 117.8071 | 182.7516 | 227.3866 | 222.1382 | 55.7711 | 19.1866
739.2542 | 290.5608 | 118.008 | 183.4447 | 227.228 | 221.7461 | 55.8725 | 19.21
740.2542 | 290.026 | 118.2335 | 183.2921 | 227.4313 | 221.8767 | 55.9445 | 19.241
741.2542 | 290.6484 | 118.449 | 182.9496 | 227.6102 | 222.7103 | 56.0407 | 19.269
742.2542 | 290.8959 | 118.6893 | 181.9932 | 228.4628 | 223.3396 | 56.1263 | 19.3058
743.2542 | 292.1746 | 118.8753 | 180.8652 | 228.9592 | 223.7556 | 56.1853 | 19.3115
744.2542 | 291.8552 | 119.1038 | 180.8844 | 228.7622 | 222.8448 | 56.283 | 19.3513
745.2542 | 292.0771 | 119.3168 | 180.2841 | 228.5049 | 222.2688 | 56.3986 | 19.3925
746.2542 | 292.7333 | 119.5475 | 179.9646 | 228.4421 | 222.203 | 56.4791 | 19.4146
747.2542 | 293.2202 | 119.7801 | 179.4636 | 227.8005 | 222.3029 | 56.5671 | 19.4511
748.2542 | 292.5103 | 119.9896 | 180.6372 | 227.9723 | 221.9857 | 56.6512 | 19.472
749.2542 | 292.1538 | 120.193 | 180.9327 | 228.6317 | 221.8254 | 56.7487 | 19.5131
750.2542 | 290.9076 | 120.4248 | 180.9845 | 229.0431 | 221.8915 | 56.8147 | 19.5206
751.2542 | 291.6895 | 120.6303 | 180.9025 | 230.078 | 222.1226 | 56.9168 | 19.5704
752.2542 | 292.3022 | 120.8515 | 180.8536 | 230.596 | 222.2734 | 57.0077 | 19.5996
753.2542 | 293.9542 | 121.0752 | 181.0475 | 231.6974 | 223.2476 | 57.107 | 19.6258
754.2542 | 292.9303 | 121.2988 | 181.7093 | 232.4985 | 223.6503 | 57.2002 | 19.6522
755.2542 | 293.838 | 121.5262 | 181.2974 | 232.0459 | 223.2175 | 57.2876 | 19.6892
756.2542 | 293.38 | 121.7428 | 180.7504 | 231.7264 | 223.0626 | 57.3784 | 19.7162
757.2542 | 293.2344 | 121.9326 | 180.9111 | 231.8634 | 223.4224 | 57.4711 | 19.7501
758.2542 | 294.0698 | 122.1713 | 181.2709 | 231.2849 | 223.0003 | 57.5685 | 19.787
759.2542 | 294.6058 | 122.3835 | 180.6917 | 230.9546 | 222.5967 | 57.6607 | 19.8215
760.2542 | 296.1623 | 122.6357 | 180.4547 | 230.5836 | 222.8702 | 57.7392 | 19.843
761.2542 | 295.6335 | 122.8638 | 179.7475 | 229.8713 | 222.7565 | 57.8169 | 19.8645
762.2542 | 295.936 | 123.0862 | 178.937 | 230.8061 | 222.8152 | 57.9037 | 19.9038
763.2542 | 294.9406 | 123.3479 | 179.354 | 230.5819 | 222.6348 | 57.9989 | 19.9406
764.2542 | 295.4846 | 123.6139 | 178.8224 | 230.7297 | 222.6967 | 58.0868 | 19.9574
765.2542 | 296.1089 | 123.8415 | 178.5737 | 230.7202 | 222.7772 | 58.1716 | 19.9863
766.2542 | 296.0376 | 124.113 | 179.0788 | 230.6723 | 222.911 | 58.2552 | 20.0085
767.2542 | 295.4161 | 124.3523 | 179.0314 | 231.0529 | 222.9077 | 58.3362 | 20.0484
768.2542 | 295.0443 | 124.5751 | 179.1519 | 230.7751 | 223.1746 | 58.4143 | 20.0842
769.2542 | 295.4001 | 124.7867 | 180.3275 | 231.5539 | 223.782 | 58.4904 | 20.1095
770.2542 | 294.9994 | 125.015 | 180.5368 | 232.2156 | 223.3059 | 58.572 | 20.1369
771.2542 | 295.17 | 125.2214 | 180.4509 | 232.2206 | 223.7858 | 58.6481 | 20.1608
772.2542 | 295.1473 | 125.4377 | 181.1708 | 232.0413 | 223.589 | 58.7264 | 20.1958
773.2542 | 294.8714 | 125.6488 | 181.3745 | 231.8077 | 223.1901 | 58.806 | 20.2313
774.2542 | 294.7148 | 125.8709 | 181.3752 | 231.1265 | 222.4856 | 58.8879 | 20.2592
775.2542 | 293.633 | 126.0735 | 180.9635 | 231.078 | 221.4633 | 58.9646 | 20.2874
776.2542 | 292.2732 | 126.2923 | 180.6297 | 231.1138 | 221.5151 | 59.0472 | 20.3146
777.2542 | 291.51 | 126.4972 | 180.7331 | 230.9203 | 220.6748 | 59.1193 | 20.3441
778.2542 | 292.3323 | 126.7157 | 181.0237 | 231.0938 | 220.8485 | 59.1979 | 20.3726
779.2542 | 292.0124 | 126.9078 | 181.087 | 231.6498 | 220.6 | 59.2709 | 20.3905
780.2542 | 291.8126 | 127.1234 | 180.7238 | 232.5511 | 219.9991 | 59.3475 | 20.4357
781.2542 | 291.4861 | 127.3029 | 180.7174 | 231.6008 | 219.4396 | 59.4188 | 20.4585
782.2542 | 292.364 | 127.5152 | 180.6392 | 231.3237 | 219.1144 | 59.4881 | 20.479
783.2542 | 292.7105 | 127.704 | 180.2904 | 230.7292 | 218.3338 | 59.5674 | 20.5143
784.2542 | 292.4792 | 127.8959 | 180.2558 | 230.2267 | 218.0572 | 59.6382 | 20.5404
785.2542 | 292.5522 | 128.1048 | 180.1277 | 229.9752 | 217.6559 | 59.7128 | 20.5683
786.2542 | 291.9403 | 128.2799 | 179.7947 | 229.6084 | 217.9372 | 59.7824 | 20.5929
787.2542 | 290.8192 | 128.4809 | 179.706 | 229.308 | 217.4193 | 59.8667 | 20.6315
788.2542 | 290.3912 | 128.6857 | 179.1481 | 229.196 | 217.1352 | 59.9511 | 20.6665
789.2542 | 289.2449 | 128.8836 | 178.6345 | 229.0485 | 217.2077 | 60.0241 | 20.6825
790.2542 | 291.0118 | 129.048 | 178.8126 | 228.6595 | 217.1837 | 60.093 | 20.7188
791.2542 | 290.388 | 129.2342 | 178.6304 | 228.514 | 217.5273 | 60.1838 | 20.7487
792.2542 | 290.5644 | 129.4219 | 178.7872 | 228.2458 | 217.8114 | 60.2652 | 20.7711
793.2542 | 289.4974 | 129.616 | 179.1274 | 228.3723 | 217.4442 | 60.346 | 20.8056
794.2542 | 289.2436 | 129.7924 | 179.4382 | 228.5015 | 217.6776 | 60.4186 | 20.8318
795.2542 | 289.3367 | 129.9706 | 179.1507 | 229.4143 | 218.0676 | 60.5047 | 20.8575
796.2542 | 288.5374 | 130.1587 | 179.1151 | 229.3362 | 217.8895 | 60.5747 | 20.8836
797.2542 | 288.2092 | 130.3498 | 179.0453 | 229.2332 | 217.2625 | 60.658 | 20.928
798.2542 | 287.7755 | 130.5266 | 179.3249 | 228.7642 | 217.6184 | 60.7376 | 20.9473
799.2542 | 288.3277 | 130.6911 | 179.3514 | 227.8884 | 217.554 | 60.8152 | 20.9686
800.2542 | 287.5754 | 130.8783 | 179.5347 | 227.5907 | 217.4278 | 60.8958 | 20.9992
801.2542 | 286.9919 | 131.0399 | 180.3309 | 227.4615 | 217.11 | 60.9745 | 21.0337
802.2542 | 287.1695 | 131.231 | 179.7098 | 227.9813 | 217.4648 | 61.0544 | 21.0657
803.2542 | 286.6433 | 131.3948 | 179.4598 | 228.0333 | 217.9011 | 61.1267 | 21.0865
804.2542 | 285.9054 | 131.5777 | 179.0661 | 227.8198 | 218.0823 | 61.1931 | 21.1133
805.2542 | 286.0395 | 131.751 | 179.0546 | 227.9575 | 218.6303 | 61.2798 | 21.14
806.2542 | 284.8586 | 131.9349 | 179.6399 | 228.4277 | 218.8288 | 61.3463 | 21.169
807.2542 | 284.3519 | 132.1122 | 179.2671 | 228.2027 | 219.5339 | 61.4223 | 21.2027
808.2542 | 284.3943 | 132.2647 | 179.0215 | 227.8681 | 219.6028 | 61.4949 | 21.2295
809.2542 | 283.3511 | 132.4359 | 178.7162 | 227.5325 | 219.3667 | 61.5716 | 21.2674
810.2542 | 282.952 | 132.6192 | 178.5666 | 227.0243 | 219.1894 | 61.6376 | 21.2869
811.2542 | 282.0702 | 132.7799 | 178.9258 | 226.967 | 219.7632 | 61.7048 | 21.316
812.2542 | 281.1402 | 132.9675 | 178.998 | 227.4469 | 219.9835 | 61.7821 | 21.3462
813.2542 | 281.1001 | 133.1294 | 179.3335 | 228.6715 | 219.6197 | 61.8472 | 21.368
814.2542 | 280.9459 | 133.296 | 180.5667 | 228.8931 | 220.0852 | 61.9141 | 21.4069
815.2542 | 281.3386 | 133.4813 | 180.4733 | 229.1897 | 220.4206 | 61.9792 | 21.4312
816.2542 | 281.7992 | 133.6389 | 180.6108 | 230.0889 | 221.6638 | 62.0501 | 21.4518
817.2542 | 281.6184 | 133.8144 | 181.6528 | 230.0919 | 222.2373 | 62.1236 | 21.4887
818.2542 | 281.7855 | 133.975 | 181.4797 | 229.8214 | 221.9917 | 62.1934 | 21.5208
819.2542 | 281.073 | 134.1385 | 181.2141 | 229.5299 | 221.6124 | 62.2715 | 21.5443
820.2542 | 282.7967 | 134.3069 | 181.4987 | 230.5751 | 222.0826 | 62.3379 | 21.5787
821.2542 | 282.6164 | 134.4742 | 181.1137 | 230.983 | 221.9115 | 62.4172 | 21.6011
822.2542 | 281.9368 | 134.6369 | 181.5649 | 231.3732 | 221.9129 | 62.4787 | 21.6383
823.2542 | 281.2131 | 134.7961 | 182.3181 | 231.2238 | 221.777 | 62.5412 | 21.6603
824.2542 | 280.5991 | 134.9777 | 182.3546 | 230.8068 | 221.7663 | 62.6127 | 21.6865
825.2542 | 279.4017 | 135.158 | 181.7583 | 230.6787 | 222.1413 | 62.6736 | 21.7174
826.2542 | 279.2042 | 135.3258 | 181.8107 | 230.1111 | 222.0733 | 62.7389 | 21.7493
827.2542 | 278.6016 | 135.4983 | 181.3881 | 229.6131 | 222.4673 | 62.808 | 21.7649
828.2542 | 279.2296 | 135.6617 | 181.0311 | 229.924 | 222.4485 | 62.8729 | 21.7897
829.2542 | 279.1064 | 135.823 | 180.7967 | 229.5863 | 223.0216 | 62.9567 | 21.8206
830.2542 | 280.2163 | 135.9918 | 180.8538 | 229.929 | 223.3278 | 63.0128 | 21.8614
831.2542 | 282.9593 | 136.1597 | 181.1014 | 229.8063 | 223.4582 | 63.081 | 21.8806
832.2542 | 284.4397 | 136.2919 | 181.8916 | 230.0811 | 223.6148 | 63.1496 | 21.9147
833.2542 | 285.0036 | 136.4789 | 182.2125 | 231.3561 | 224.0066 | 63.219 | 21.929
834.2542 | 284.6437 | 136.6425 | 182.3367 | 231.2058 | 223.795 | 63.2977 | 21.9562
835.2542 | 285.4525 | 136.7937 | 183.275 | 231.713 | 225.303 | 63.3606 | 21.9873
836.2542 | 285.9162 | 136.9387 | 183.3214 | 231.6647 | 224.9777 | 63.4429 | 22.017
837.2542 | 285.5689 | 137.1048 | 183.7938 | 231.5251 | 224.44 | 63.5107 | 22.0475
838.2542 | 286.8658 | 137.2709 | 183.5214 | 231.1619 | 224.4247 | 63.5745 | 22.0691
839.2542 | 287.1081 | 137.4146 | 184.1116 | 230.6659 | 224.0406 | 63.6542 | 22.0958
840.2542 | 287.2951 | 137.5935 | 184.8846 | 229.9861 | 224.1253 | 63.7195 | 22.1232
841.2542 | 286.5037 | 137.7603 | 184.617 | 229.7931 | 224.089 | 63.7899 | 22.1609
842.2542 | 286.5434 | 137.911 | 183.9766 | 229.7592 | 223.6523 | 63.8677 | 22.18
843.2542 | 287.436 | 138.0878 | 183.5698 | 229.7054 | 223.7337 | 63.9332 | 22.2114
844.2542 | 287.703 | 138.2498 | 183.3011 | 229.7871 | 223.0647 | 64.004 | 22.2333
845.2542 | 287.8869 | 138.391 | 182.9275 | 229.7051 | 222.5475 | 64.0772 | 22.2606
846.2542 | 287.4389 | 138.55 | 182.7737 | 229.5534 | 222.5121 | 64.1469 | 22.2951
847.2542 | 287.6248 | 138.7243 | 182.5039 | 229.505 | 222.0477 | 64.2206 | 22.3217
848.2542 | 287.9582 | 138.859 | 182.4287 | 230.2884 | 221.9032 | 64.2924 | 22.3534
849.2542 | 288.4512 | 139.0438 | 182.0022 | 230.8803 | 222.8522 | 64.3563 | 22.3756
850.2542 | 289.3032 | 139.177 | 181.9504 | 231.3573 | 222.7939 | 64.4229 | 22.4031
851.2542 | 288.1537 | 139.3369 | 181.9824 | 231.4961 | 223.1924 | 64.4943 | 22.4289
852.2542 | 288.2396 | 139.498 | 182.3239 | 231.7152 | 223.6895 | 64.5565 | 22.4425
853.2542 | 288.2875 | 139.6443 | 182.0198 | 231.4603 | 224.1393 | 64.6335 | 22.4743
854.2542 | 288.0394 | 139.8051 | 181.8528 | 231.406 | 224.3455 | 64.7067 | 22.5103
855.2542 | 287.9688 | 139.981 | 181.648 | 231.5971 | 224.7358 | 64.7786 | 22.5308
856.2542 | 289.4808 | 140.1298 | 181.406 | 231.1823 | 224.714 | 64.8433 | 22.5647
857.2542 | 289.9656 | 140.2589 | 181.3224 | 230.9512 | 224.9623 | 64.9172 | 22.5856
858.2542 | 289.0582 | 140.4166 | 181.7475 | 231.1016 | 225.0546 | 64.9839 | 22.6172
859.2542 | 288.5724 | 140.5774 | 182.1755 | 231.2263 | 225.321 | 65.0471 | 22.6446
860.2542 | 288.68 | 140.7345 | 181.9446 | 231.0739 | 225.7992 | 65.1221 | 22.6628
861.2542 | 288.0003 | 140.8817 | 181.6536 | 231.1677 | 224.9775 | 65.1951 | 22.6931
862.2542 | 287.8143 | 141.0275 | 182.135 | 231.2137 | 224.4266 | 65.2631 | 22.7053
863.2542 | 287.174 | 141.1889 | 181.8655 | 230.9204 | 224.6714 | 65.3372 | 22.7551
864.2542 | 286.1029 | 141.3365 | 182.8757 | 230.8592 | 224.1775 | 65.407 | 22.7691
865.2542 | 287.398 | 141.4745 | 182.9447 | 230.1652 | 223.3555 | 65.478 | 22.8034
866.2542 | 287.8487 | 141.6357 | 184.7136 | 230.06 | 223.0388 | 65.5356 | 22.8327
867.2542 | 288.6171 | 141.792 | 185.7453 | 229.5991 | 222.5984 | 65.6179 | 22.8557
868.2542 | 289.0048 | 141.9227 | 186.888 | 229.6617 | 222.3221 | 65.6725 | 22.8833
869.2542 | 288.2726 | 142.0908 | 186.4171 | 229.9719 | 222.4419 | 65.7452 | 22.9034
870.2542 | 288.1438 | 142.2096 | 186.4797 | 229.9604 | 222.6773 | 65.8103 | 22.9373
871.2542 | 288.3181 | 142.3529 | 186.1674 | 229.8828 | 222.6207 | 65.8874 | 22.9658
872.2542 | 289.5957 | 142.5162 | 185.6107 | 230.2764 | 222.2141 | 65.9558 | 22.9886
873.2542 | 290.1412 | 142.6607 | 185.244 | 230.8105 | 222.5376 | 66.0254 | 23.008
874.2542 | 289.589 | 142.8092 | 184.9378 | 231.1421 | 223.0036 | 66.0925 | 23.0473
875.2542 | 288.0241 | 142.9198 | 184.8469 | 231.8836 | 223.6952 | 66.1692 | 23.0691
876.2542 | 286.822 | 143.0863 | 184.8948 | 231.7053 | 223.8769 | 66.2377 | 23.0861
877.2542 | 287.1626 | 143.2275 | 184.6983 | 231.8789 | 223.77 | 66.3039 | 23.1206
878.2542 | 287.8252 | 143.3627 | 184.3677 | 231.4747 | 224.1277 | 66.3748 | 23.1372
879.2542 | 288.5091 | 143.4853 | 185.0518 | 232.0223 | 223.6947 | 66.4443 | 23.1697
880.2542 | 287.4604 | 143.6441 | 184.8958 | 232.6347 | 223.422 | 66.5232 | 23.1926
881.2542 | 286.6432 | 143.7724 | 184.8404 | 232.2961 | 222.9057 | 66.5927 | 23.2153
882.2542 | 285.5981 | 143.9347 | 184.6532 | 232.3461 | 223.4212 | 66.6674 | 23.2534
883.2542 | 285.8917 | 144.0946 | 184.7156 | 232.1669 | 224.1856 | 66.7425 | 23.276
884.2542 | 285.3738 | 144.2273 | 184.5226 | 232.3064 | 224.3913 | 66.8203 | 23.2908
885.2542 | 284.8475 | 144.3667 | 185.2107 | 232.709 | 224.4496 | 66.8804 | 23.3208
886.2542 | 287.1245 | 144.5172 | 186.0071 | 232.7245 | 224.6725 | 66.953 | 23.352
887.2542 | 286.9717 | 144.6717 | 186.6617 | 232.7369 | 224.9256 | 67.0158 | 23.3884
888.2542 | 286.2862 | 144.8104 | 185.8644 | 231.9558 | 224.6524 | 67.0863 | 23.4039
889.2542 | 285.6969 | 144.9506 | 184.9204 | 231.2988 | 224.8296 | 67.157 | 23.4442
890.2542 | 286.4661 | 145.0819 | 184.0027 | 230.9618 | 224.8051 | 67.2245 | 23.4566
891.2542 | 285.3407 | 145.2301 | 183.7853 | 232.0985 | 224.71 | 67.2904 | 23.4868
892.2542 | 286.7091 | 145.3701 | 183.5137 | 232.127 | 225.4662 | 67.3524 | 23.5114
893.2542 | 287.0278 | 145.5133 | 184.7262 | 232.0411 | 225.5821 | 67.4135 | 23.5305
894.2542 | 289.6108 | 145.6625 | 184.6963 | 232.2208 | 225.4814 | 67.4847 | 23.5747
895.2542 | 290.1986 | 145.7732 | 184.3034 | 232.0505 | 225.7214 | 67.5442 | 23.5868
896.2542 | 289.3426 | 145.9127 | 184.0373 | 232.036 | 225.8859 | 67.6071 | 23.6177
897.2542 | 288.1116 | 146.0633 | 183.7457 | 232.4693 | 225.3934 | 67.6862 | 23.6359
898.2542 | 287.0806 | 146.219 | 184.2341 | 232.6884 | 225.3464 | 67.7445 | 23.6637
899.2542 | 286.8057 | 146.3612 | 184.1672 | 232.2974 | 225.164 | 67.8151 | 23.6889
900.2542 | 287.2485 | 146.4882 | 184.8243 | 232.5847 | 225.4717 | 67.8774 | 23.7176
901.2542 | 288.6856 | 146.6466 | 185.0681 | 232.8963 | 225.6955 | 67.9394 | 23.747
902.2542 | 287.8964 | 146.7562 | 185.3557 | 232.6583 | 226.1444 | 68.0007 | 23.7733
903.2542 | 287.4121 | 146.9126 | 185.3 | 233.3607 | 226.5258 | 68.0701 | 23.7986
904.2542 | 287.6757 | 147.0416 | 185.6391 | 232.8549 | 226.9115 | 68.139 | 23.8238
905.2542 | 287.578 | 147.1747 | 185.8818 | 233.3755 | 226.7605 | 68.2053 | 23.8482
906.2542 | 287.992 | 147.3297 | 186.0777 | 233.3086 | 226.6177 | 68.2763 | 23.881
907.2542 | 290.1686 | 147.4701 | 186.543 | 233.0659 | 226.1675 | 68.3415 | 23.8986
908.2542 | 291.3397 | 147.6091 | 186.9167 | 233.4604 | 226.7635 | 68.4156 | 23.927
909.2542 | 291.2718 | 147.747 | 187.2546 | 234.3801 | 227.3636 | 68.4812 | 23.9538
910.2542 | 290.1372 | 147.877 | 187.7761 | 234.8662 | 227.6536 | 68.5613 | 23.9771
911.2542 | 291.1803 | 148.0384 | 187.9449 | 234.3415 | 228.5392 | 68.6321 | 24.0074
912.2542 | 292.9078 | 148.1922 | 188.3971 | 234.0347 | 229.7459 | 68.7116 | 24.0328
913.2542 | 292.0676 | 148.3216 | 188.5991 | 233.7219 | 229.4929 | 68.7918 | 24.0549
914.2542 | 294.0017 | 148.4673 | 189.2099 | 233.5555 | 229.7312 | 68.8692 | 24.0819
915.2542 | 295.6358 | 148.6171 | 189.5422 | 233.7269 | 230.0896 | 68.9438 | 24.1015
916.2542 | 297.7302 | 148.7698 | 190.0962 | 236.4905 | 230.4843 | 69.0434 | 24.1281
917.2542 | 298.098 | 148.8987 | 190.3081 | 236.3589 | 232.0336 | 69.1302 | 24.1554
918.2542 | 298.3364 | 149.0434 | 190.5771 | 236.9125 | 232.3875 | 69.2081 | 24.1859
919.2542 | 298.4995 | 149.1865 | 191.4502 | 237.966 | 232.9918 | 69.3053 | 24.2235
920.2542 | 300.5108 | 149.345 | 191.3053 | 238.795 | 232.8602 | 69.3871 | 24.2349
921.2542 | 300.3119 | 149.4942 | 191.465 | 239.2168 | 233.2008 | 69.4719 | 24.2718
922.2542 | 300.6523 | 149.6466 | 191.6594 | 239.2911 | 233.2524 | 69.5577 | 24.291
923.2542 | 300.4371 | 149.8061 | 192.5429 | 239.5107 | 233.2921 | 69.6448 | 24.3296
924.2542 | 300.0158 | 149.9456 | 192.6102 | 240.2911 | 233.2597 | 69.734 | 24.3471
925.2542 | 300.3389 | 150.1188 | 192.7045 | 239.9703 | 233.3126 | 69.829 | 24.3738
926.2542 | 301.2268 | 150.2731 | 193.2327 | 241.2744 | 232.9026 | 69.9086 | 24.4064
927.2542 | 301.5193 | 150.4231 | 193.8116 | 240.882 | 232.8639 | 69.9925 | 24.4292
928.2542 | 301.0516 | 150.5828 | 194.4586 | 241.1119 | 235.501 | 70.0802 | 24.4513
929.2542 | 302.8441 | 150.7592 | 194.5169 | 241.7034 | 234.606 | 70.1621 | 24.4784
930.2542 | 304.6035 | 150.9097 | 193.9615 | 242.0722 | 234.1334 | 70.2512 | 24.5081
931.2542 | 304.4119 | 151.0742 | 193.6197 | 241.8478 | 235.001 | 70.3378 | 24.5374
932.2542 | 306.8257 | 151.2441 | 193.3602 | 241.3087 | 233.9031 | 70.4349 | 24.5619
933.2542 | 308.1322 | 151.4239 | 192.9081 | 240.7804 | 234.0625 | 70.5136 | 24.5925
934.2542 | 308.9688 | 151.5782 | 193.1561 | 240.7255 | 233.7348 | 70.6057 | 24.6284
935.2542 | 311.0071 | 151.7519 | 192.8804 | 241.1915 | 233.4195 | 70.6858 | 24.6508
936.2542 | 311.0878 | 151.9262 | 192.5667 | 240.8607 | 232.7034 | 70.778 | 24.6797
937.2542 | 311.1631 | 152.0862 | 192.1868 | 240.5662 | 232.7267 | 70.8617 | 24.7081
938.2542 | 311.3149 | 152.2619 | 192.1732 | 240.4826 | 232.9277 | 70.9495 | 24.7384
939.2542 | 311.1828 | 152.4468 | 192.2209 | 240.3667 | 232.2277 | 71.0372 | 24.758
940.2542 | 311.127 | 152.6085 | 192.0776 | 240.1964 | 231.9829 | 71.1313 | 24.7889
941.2542 | 312.5967 | 152.8094 | 192.0835 | 240.2041 | 231.6634 | 71.2167 | 24.8134
942.2542 | 313.5799 | 152.9855 | 192.1977 | 240.2586 | 232.9392 | 71.3034 | 24.8416
943.2542 | 314.3027 | 153.1561 | 192.2658 | 240.6995 | 233.4888 | 71.3937 | 24.8766
944.2542 | 314.973 | 153.3272 | 193.3078 | 240.7358 | 233.9164 | 71.4785 | 24.9029
945.2542 | 314.4284 | 153.4884 | 194.203 | 240.8424 | 233.6725 | 71.5587 | 24.9269
946.2542 | 314.1823 | 153.6775 | 194.744 | 241.2065 | 234.7614 | 71.6433 | 24.9599
947.2542 | 313.6053 | 153.8651 | 195.1803 | 242.074 | 235.2939 | 71.7505 | 24.9941
948.2542 | 313.9957 | 154.0179 | 196.2268 | 241.5428 | 235.4504 | 71.8415 | 25.0038
949.2542 | 315.7803 | 154.2101 | 196.1433 | 241.0171 | 235.4938 | 71.9292 | 25.0328
950.2542 | 317.8245 | 154.4099 | 196.379 | 241.3226 | 235.3873 | 72.0164 | 25.0536
951.2542 | 318.4154 | 154.5919 | 196.3238 | 242.0548 | 235.8025 | 72.1146 | 25.0958
952.2542 | 318.2787 | 154.7751 | 196.6898 | 243.0974 | 235.4832 | 72.2079 | 25.1109
953.2542 | 318.1041 | 154.9403 | 196.9172 | 243.7002 | 236.6153 | 72.2993 | 25.1281
954.2542 | 316.5872 | 155.1356 | 197.3702 | 243.7615 | 236.4346 | 72.3892 | 25.1708
955.2542 | 315.7258 | 155.3121 | 197.2691 | 243.9271 | 236.6221 | 72.4841 | 25.1954
956.2542 | 315.0902 | 155.5069 | 197.0056 | 244.6686 | 236.7857 | 72.5738 | 25.2251
957.2542 | 316.4466 | 155.7041 | 197.6219 | 244.4025 | 236.3046 | 72.6708 | 25.2466
958.2542 | 317.6808 | 155.871 | 197.7622 | 244.0774 | 236.7504 | 72.7645 | 25.2691
959.2542 | 319.5291 | 156.0687 | 198.4162 | 244.3424 | 238.1238 | 72.8521 | 25.2912
960.2542 | 319.1661 | 156.2774 | 198.7394 | 244.629 | 237.7852 | 72.9577 | 25.3275
961.2542 | 318.7296 | 156.4578 | 198.5475 | 245.0818 | 236.98 | 73.0607 | 25.3463
962.2542 | 320.5529 | 156.6392 | 198.2061 | 244.854 | 236.6703 | 73.1449 | 25.3708
963.2542 | 321.2742 | 156.8286 | 198.5125 | 244.8816 | 236.6077 | 73.2481 | 25.3945
964.2542 | 321.4491 | 157.0312 | 198.3538 | 244.6721 | 236.8189 | 73.3386 | 25.428
965.2542 | 320.6431 | 157.2306 | 197.9206 | 245.1773 | 236.7767 | 73.4341 | 25.4585
966.2542 | 320.895 | 157.4178 | 198.262 | 245.126 | 238.1265 | 73.52 | 25.4769
967.2542 | 320.4547 | 157.6082 | 198.3281 | 244.7013 | 237.6751 | 73.6053 | 25.503
968.2542 | 320.7527 | 157.8018 | 198.2222 | 244.7559 | 238.0921 | 73.7031 | 25.5223
969.2542 | 321.1395 | 157.985 | 199.2093 | 244.5788 | 239.0526 | 73.7892 | 25.548
970.2542 | 320.5272 | 158.1892 | 199.0896 | 244.6891 | 238.9664 | 73.8855 | 25.5804
971.2542 | 320.4849 | 158.3801 | 198.6545 | 244.5055 | 239.388 | 73.9735 | 25.606
972.2542 | 321.504 | 158.5727 | 198.5077 | 244.054 | 239.5252 | 74.0655 | 25.6323
973.2542 | 322.1236 | 158.7575 | 198.7732 | 243.4012 | 239.3705 | 74.1567 | 25.6628
974.2542 | 323.12 | 158.9519 | 198.5876 | 243.352 | 238.8517 | 74.2424 | 25.6848
975.2542 | 322.8519 | 159.1303 | 198.0982 | 243.7623 | 238.9941 | 74.3304 | 25.7087
976.2542 | 322.2689 | 159.3339 | 198.6279 | 243.9559 | 239.3819 | 74.4212 | 25.7258
977.2542 | 321.4844 | 159.4961 | 199.329 | 245.2619 | 239.0514 | 74.5031 | 25.7676
978.2542 | 322.0692 | 159.6828 | 200.0957 | 245.4324 | 238.7391 | 74.6012 | 25.7871
979.2542 | 322.12 | 159.8786 | 200.5687 | 245.4975 | 238.8341 | 74.6874 | 25.8143
980.2542 | 322.3423 | 160.0793 | 200.8523 | 245.4625 | 239.4945 | 74.7717 | 25.85
981.2542 | 322.8139 | 160.2506 | 200.9539 | 245.4419 | 239.6138 | 74.8641 | 25.8597
982.2542 | 321.7788 | 160.4574 | 200.7747 | 246.1178 | 239.3335 | 74.9531 | 25.8889
983.2542 | 321.4472 | 160.6322 | 200.4327 | 246.6563 | 239.3171 | 75.0431 | 25.918
984.2542 | 321.5125 | 160.8026 | 200.2237 | 246.3195 | 239.5827 | 75.1209 | 25.9424
985.2542 | 322.3657 | 161.0072 | 199.8895 | 246.3848 | 239.8166 | 75.2153 | 25.9735
986.2542 | 320.5784 | 161.1718 | 199.6019 | 245.7486 | 239.2557 | 75.3019 | 25.9985
987.2542 | 319.6967 | 161.3674 | 199.5979 | 245.7533 | 239.3451 | 75.3874 | 26.0194
988.2542 | 321.723 | 161.558 | 199.8875 | 246.4693 | 239.0841 | 75.4679 | 26.0436
989.2542 | 322.4994 | 161.7322 | 200.3371 | 246.0542 | 239.7409 | 75.5549 | 26.0757
990.2542 | 325.1839 | 161.9041 | 199.7016 | 245.9307 | 239.9959 | 75.6416 | 26.0933
991.2542 | 324.8039 | 162.0886 | 199.9772 | 246.2792 | 240.71 | 75.7283 | 26.1316
992.2542 | 324.0756 | 162.2791 | 199.8206 | 246.5586 | 240.8732 | 75.8093 | 26.1565
993.2542 | 325.349 | 162.4526 | 200.2128 | 246.3123 | 240.6902 | 75.8974 | 26.1781
994.2542 | 325.2144 | 162.62 | 200.4671 | 246.998 | 240.7194 | 75.9778 | 26.2043
995.2542 | 324.7368 | 162.8107 | 201.3688 | 247.0211 | 240.3352 | 76.0555 | 26.227
996.2542 | 325.3408 | 162.9986 | 201.8259 | 246.7899 | 240.292 | 76.1444 | 26.2553
997.2542 | 325.6461 | 163.1692 | 201.5089 | 247.071 | 240.198 | 76.2401 | 26.2791
998.2542 | 326.901 | 163.3626 | 201.7484 | 247.169 | 240.1531 | 76.3211 | 26.3014
999.2542 | 326.8112 | 163.5583 | 201.2139 | 247.3118 | 240.2481 | 76.4033 | 26.3198
1000.2542 | 328.0782 | 163.7417 | 201.1067 | 247.5242 | 240.5578 | 76.4957 | 26.3667
1001.2542 | 328.77 | 163.9714 | 200.7384 | 247.7024 | 241.2041 | 76.583 | 26.3942
1002.2542 | 327.4432 | 164.1569 | 200.5896 | 247.6238 | 240.7351 | 76.6708 | 26.4167
1003.2542 | 327.1548 | 164.3472 | 200.9221 | 249.3869 | 240.7067 | 76.7547 | 26.4397
1004.2542 | 326.8491 | 164.545 | 201.2276 | 248.9918 | 241.0165 | 76.8362 | 26.4635
1005.2542 | 326.3854 | 164.7575 | 201.2542 | 248.5826 | 241.3255 | 76.9424 | 26.4978
1006.2542 | 325.802 | 164.9565 | 201.7265 | 248.2837 | 242.2572 | 77.0312 | 26.5069
1007.2542 | 325.0905 | 165.1469 | 201.8554 | 247.8071 | 242.1241 | 77.1333 | 26.5439
1008.2542 | 325.1459 | 165.3311 | 201.4444 | 248.0185 | 242.6626 | 77.2225 | 26.5673
1009.2542 | 323.951 | 165.54 | 201.2334 | 248.5537 | 243.046 | 77.3188 | 26.6021
1010.2542 | 323.1148 | 165.7443 | 201.2305 | 248.3603 | 243.2982 | 77.4175 | 26.6223
1011.2542 | 322.5202 | 165.9426 | 201.033 | 248.1032 | 243.4625 | 77.5086 | 26.648
1012.2542 | 322.957 | 166.139 | 200.8025 | 247.6875 | 244.0338 | 77.601 | 26.6754
1013.2542 | 322.7562 | 166.3474 | 201.0325 | 247.084 | 244.2096 | 77.693 | 26.7042
1014.2542 | 322.3352 | 166.5388 | 201.8501 | 246.7497 | 243.8058 | 77.7828 | 26.7289
1015.2542 | 322.6666 | 166.7337 | 202.7438 | 246.8085 | 245.3538 | 77.8894 | 26.7497
1016.2542 | 323.4133 | 166.9348 | 203.4496 | 247.7497 | 245.4704 | 77.9915 | 26.7815
1017.2542 | 324.3648 | 167.1438 | 204.2871 | 249.1723 | 245.1215 | 78.078 | 26.8095
1018.2542 | 325.8572 | 167.3365 | 206.1382 | 249.3198 | 246.575 | 78.1739 | 26.8322
1019.2542 | 327.7349 | 167.5354 | 206.0369 | 248.8448 | 247.8917 | 78.2685 | 26.8565
1020.2542 | 328.2586 | 167.7423 | 206.5805 | 248.5075 | 247.8388 | 78.3594 | 26.8833
1021.2542 | 329.4519 | 167.9383 | 207.7025 | 248.3416 | 247.3159 | 78.4531 | 26.9091
1022.2542 | 330.6305 | 168.1325 | 208.5265 | 248.8261 | 247.4025 | 78.5389 | 26.9356
1023.2542 | 331.9195 | 168.3439 | 208.1198 | 249.2262 | 246.7981 | 78.6315 | 26.9629
1024.2542 | 332.4789 | 168.5265 | 208.0843 | 249.4472 | 246.9374 | 78.7321 | 26.9795
1025.2542 | 333.0505 | 168.7411 | 208.0387 | 249.2228 | 247.5309 | 78.824 | 27.018
1026.2542 | 332.5609 | 168.9436 | 207.9719 | 249.6424 | 247.6148 | 78.9172 | 27.0481
1027.2542 | 332.3883 | 169.1592 | 207.7035 | 249.7908 | 247.468 | 79.0081 | 27.0709
1028.2542 | 333.5706 | 169.3628 | 207.7942 | 250.7662 | 247.5575 | 79.1082 | 27.0967
1029.2542 | 333.0018 | 169.5895 | 208.0643 | 250.6397 | 246.7328 | 79.2034 | 27.1163
1030.2542 | 332.9079 | 169.8023 | 207.8373 | 250.7716 | 247.5476 | 79.303 | 27.1447
1031.2542 | 333.6336 | 170.0105 | 207.9191 | 250.4713 | 247.8421 | 79.4041 | 27.172
1032.2542 | 334.0892 | 170.2281 | 208.417 | 250.228 | 247.4617 | 79.5081 | 27.2035
1033.2542 | 334.1633 | 170.4312 | 210.7904 | 250.7726 | 247.4154 | 79.619 | 27.2275
1034.2542 | 334.1112 | 170.6511 | 211.0445 | 252.2726 | 248.527 | 79.7295 | 27.2489
1035.2542 | 336.6072 | 170.8723 | 211.2911 | 251.9861 | 247.735 | 79.8382 | 27.2763
1036.2542 | 336.9671 | 171.0895 | 211.2112 | 251.7665 | 247.6913 | 79.9478 | 27.2933
1037.2542 | 339.2404 | 171.2978 | 211.2861 | 251.8352 | 247.5417 | 80.0543 | 27.3327
1038.2542 | 340.3262 | 171.524 | 211.1708 | 252.13 | 247.5033 | 80.1653 | 27.3606
1039.2542 | 341.1331 | 171.7259 | 211.0684 | 252.2631 | 247.4739 | 80.2626 | 27.3869
1040.2542 | 340.4729 | 171.9486 | 211.6207 | 253.2152 | 247.7225 | 80.3644 | 27.4135
1041.2542 | 340.237 | 172.1952 | 212.5281 | 253.5236 | 247.9307 | 80.459 | 27.4355
1042.2542 | 340.2013 | 172.3994 | 212.4899 | 254.7506 | 248.2932 | 80.5636 | 27.4665
1043.2542 | 339.4885 | 172.6381 | 213.1811 | 254.9637 | 249.4347 | 80.6591 | 27.4892
1044.2542 | 339.9048 | 172.8662 | 212.9547 | 255.0027 | 249.581 | 80.7564 | 27.5118
1045.2542 | 342.2774 | 173.1171 | 213.9741 | 254.3464 | 250.3073 | 80.8618 | 27.5424
1046.2542 | 344.284 | 173.3384 | 214.1732 | 254.4834 | 249.7629 | 80.9513 | 27.5701
1047.2542 | 346.2066 | 173.5544 | 213.8412 | 254.2663 | 250.1676 | 81.0495 | 27.6115
1048.2542 | 345.5388 | 173.7878 | 213.6787 | 254.1485 | 250.0498 | 81.165 | 27.6205
1049.2542 | 345.3634 | 174.017 | 213.4275 | 253.7218 | 250.1963 | 81.2754 | 27.6468
1050.2542 | 346.5364 | 174.2255 | 213.9427 | 254.0527 | 250.535 | 81.3671 | 27.6654
1051.2542 | 345.0496 | 174.4707 | 214.5 | 254.074 | 250.6963 | 81.4725 | 27.7039
1052.2542 | 347.0905 | 174.6913 | 215.8931 | 254.0945 | 250.7787 | 81.5785 | 27.7252
1053.2542 | 348.4337 | 174.9184 | 216.3511 | 255.7505 | 250.9839 | 81.6801 | 27.7391
1054.2542 | 347.1991 | 175.1508 | 216.7783 | 257.0743 | 251.132 | 81.7976 | 27.7754
1055.2542 | 346.689 | 175.395 | 216.5468 | 257.552 | 252.1296 | 81.9094 | 27.802
1056.2542 | 347.6562 | 175.6312 | 217.1403 | 258.2509 | 253.1978 | 82.0105 | 27.8201
1057.2542 | 347.3078 | 175.8583 | 217.8261 | 257.9577 | 253.0104 | 82.114 | 27.853
1058.2542 | 348.7384 | 176.0965 | 217.5473 | 257.7 | 253.3208 | 82.2102 | 27.8753
1059.2542 | 348.1471 | 176.3317 | 217.737 | 257.7164 | 253.9431 | 82.3084 | 27.9022
1060.2542 | 349.8231 | 176.5732 | 217.3398 | 257.6886 | 254.0166 | 82.4086 | 27.9388
1061.2542 | 348.4679 | 176.8034 | 217.0535 | 258.0315 | 253.7307 | 82.5062 | 27.9588
1062.2542 | 348.7216 | 177.0303 | 217.7628 | 259.6904 | 253.5524 | 82.6005 | 27.9827
1063.2542 | 349.7798 | 177.2895 | 217.2101 | 261.3203 | 254.6817 | 82.6896 | 28.0149
1064.2542 | 351.3283 | 177.5407 | 216.4839 | 260.6677 | 255.4129 | 82.7912 | 28.036
1065.2542 | 350.268 | 177.7702 | 216.1247 | 260.5602 | 254.6735 | 82.8845 | 28.0569
1066.2542 | 352.414 | 178.026 | 215.609 | 260.0727 | 255.5003 | 82.9744 | 28.0807
1067.2542 | 352.5284 | 178.2719 | 216.2493 | 260.4475 | 256.8794 | 83.0652 | 28.1154
1068.2542 | 352.5269 | 178.5099 | 217.2295 | 260.4746 | 257.2393 | 83.1611 | 28.1326
1069.2542 | 351.5629 | 178.7626 | 217.6112 | 260.5446 | 257.4198 | 83.2617 | 28.1576
1070.2542 | 351.2028 | 179.0057 | 217.134 | 259.5653 | 256.3012 | 83.3578 | 28.1815
1071.2542 | 353.1511 | 179.2488 | 216.638 | 259.2183 | 255.8487 | 83.4577 | 28.2044
1072.2542 | 353.4909 | 179.4731 | 216.6045 | 258.8841 | 256.4819 | 83.5578 | 28.2327
1073.2542 | 354.1763 | 179.7276 | 216.4335 | 258.7272 | 256.3147 | 83.6526 | 28.2573
1074.2542 | 355.5092 | 179.9649 | 216.5361 | 258.3911 | 256.2001 | 83.7535 | 28.2881
1075.2542 | 354.8354 | 180.2045 | 216.5172 | 259.832 | 256.7995 | 83.8493 | 28.3155
1076.2542 | 354.4586 | 180.475 | 216.2563 | 261.6906 | 256.8957 | 83.9514 | 28.3449
1077.2542 | 354.4485 | 180.7133 | 216.2678 | 261.4802 | 257.1301 | 84.0423 | 28.3601
1078.2542 | 353.7948 | 180.9657 | 216.0606 | 261.8413 | 256.9236 | 84.1391 | 28.3771
1079.2542 | 354.5943 | 181.2118 | 215.9544 | 261.4217 | 257.0567 | 84.2271 | 28.4113
1080.2542 | 353.7147 | 181.4523 | 215.3018 | 261.4967 | 257.3615 | 84.3218 | 28.439
1081.2542 | 355.2058 | 181.7155 | 215.0416 | 261.5383 | 257.5205 | 84.4163 | 28.4697
1082.2542 | 356.6973 | 181.9585 | 216.0211 | 261.9381 | 257.211 | 84.5216 | 28.4854
1083.2542 | 356.4962 | 182.199 | 215.5478 | 262.2318 | 257.2425 | 84.6279 | 28.5143
1084.2542 | 356.5274 | 182.4488 | 216.2654 | 262.2449 | 258.0403 | 84.7268 | 28.5337
1085.2542 | 358.1474 | 182.6896 | 216.0229 | 262.0801 | 258.3258 | 84.8269 | 28.563
1086.2542 | 358.4488 | 182.9615 | 215.6735 | 261.882 | 258.2559 | 84.9285 | 28.587
1087.2542 | 358.297 | 183.2017 | 215.2794 | 261.6853 | 258.4702 | 85.0324 | 28.6229
1088.2542 | 355.6779 | 183.4634 | 215.2529 | 261.5271 | 258.3026 | 85.1321 | 28.6442
1089.2542 | 355.0397 | 183.721 | 214.9792 | 261.2766 | 258.2013 | 85.2253 | 28.6542
1090.2542 | 354.9313 | 183.949 | 214.7582 | 261.1102 | 258.3511 | 85.3327 | 28.6849
1091.2542 | 353.6639 | 184.1984 | 214.9896 | 260.8172 | 257.5309 | 85.4292 | 28.7126
1092.2542 | 355.3563 | 184.4389 | 215.415 | 260.4706 | 257.1539 | 85.5201 | 28.7407
1093.2542 | 354.0822 | 184.687 | 215.4805 | 260.3217 | 257.042 | 85.6202 | 28.7651
1094.2542 | 353.5071 | 184.9369 | 215.189 | 260.3641 | 257.2599 | 85.7206 | 28.7916
1095.2542 | 353.5847 | 185.2003 | 214.9185 | 261.1516 | 257.1416 | 85.8262 | 28.815
1096.2542 | 354.1114 | 185.4559 | 215.2455 | 262.4096 | 257.354 | 85.6419 | 28.8401
1097.2542 | 352.8241 | 185.7161 | 215.3254 | 262.075 | 257.0856 | 85.7749 | 28.8608
1098.2542 | 350.87 | 185.9582 | 215.5795 | 261.3719 | 257.2002 | 85.894 | 28.9053
1099.2542 | 351.0613 | 186.1907 | 215.843 | 260.9218 | 256.4406 | 85.9898 | 28.9234
1100.2542 | 350.8094 | 186.4369 | 215.5626 | 261.7022 | 256.2779 | 86.1014 | 28.9512
1101.2542 | 353.058 | 186.6924 | 216.0237 | 261.4755 | 255.9233 | 86.2094 | 28.9776
1102.2542 | 354.2178 | 186.9311 | 215.8875 | 260.8444 | 255.527 | 86.312 | 28.9978
1103.2542 | 354.7275 | 187.2189 | 216.3951 | 261.4372 | 255.3652 | 86.4158 | 29.0364
1104.2542 | 355.9267 | 187.445 | 216.9327 | 261.5209 | 255.4732 | 86.5075 | 29.0549
1105.2542 | 356.6675 | 187.6708 | 217.1596 | 261.0671 | 255.2713 | 86.5979 | 29.0789
1106.2542 | 356.5191 | 187.927 | 217.3827 | 261.6376 | 255.4461 | 86.7023 | 29.1064
1107.2542 | 354.7269 | 188.1637 | 217.3494 | 262.1603 | 255.6096 | 86.8078 | 29.14
1108.2542 | 353.5822 | 188.4082 | 216.7733 | 262.0961 | 255.144 | 86.9076 | 29.1558
1109.2542 | 353.7264 | 188.6539 | 217.0824 | 262.0644 | 255.4718 | 87.0038 | 29.193
1110.2542 | 352.8153 | 188.8968 | 217.1165 | 262.4224 | 255.5487 | 87.1051 | 29.213
1111.2542 | 352.7028 | 189.1341 | 217.7089 | 262.9085 | 255.4619 | 87.2054 | 29.236
1112.2542 | 351.4111 | 189.3865 | 217.9288 | 263.1752 | 255.9474 | 87.3099 | 29.2693
1113.2542 | 352.8556 | 189.6195 | 217.8209 | 263.429 | 257.1582 | 87.4136 | 29.2801
1114.2542 | 353.1327 | 189.8616 | 217.9036 | 264.0772 | 257.0289 | 87.5057 | 29.3157
1115.2542 | 354.5065 | 190.1106 | 217.5266 | 263.8494 | 257.1727 | 87.6085 | 29.3453
1116.2542 | 355.499 | 190.3648 | 217.8026 | 264.6973 | 257.3174 | 87.7035 | 29.37
1117.2542 | 356.4762 | 190.6087 | 217.0079 | 264.9155 | 257.3776 | 87.8048 | 29.3878
1118.2542 | 358.1461 | 190.8176 | 217.76 | 265.6008 | 257.6254 | 87.9095 | 29.4153
1119.2542 | 359.0804 | 191.0585 | 218.3658 | 266.2786 | 258.598 | 88.0057 | 29.4399
1120.2542 | 361.9013 | 191.289 | 218.7679 | 266.5254 | 258.2819 | 88.0976 | 29.46
1121.2542 | 362.542 | 191.5454 | 219.2904 | 266.6442 | 258.971 | 88.1888 | 29.4855
1122.2542 | 363.6626 | 191.7824 | 219.7003 | 266.5531 | 259.7047 | 88.29 | 29.5238
1123.2542 | 365.2474 | 192.0391 | 219.9678 | 266.7356 | 259.2456 | 88.3923 | 29.5421
1124.2542 | 365.5955 | 192.2886 | 219.963 | 267.0257 | 259.3332 | 88.5077 | 29.5592
1125.2542 | 365.2853 | 192.5282 | 220.4351 | 266.8231 | 259.4953 | 88.6181 | 29.5898
1126.2542 | 363.8036 | 192.7886 | 220.9606 | 267.5994 | 259.1557 | 88.7222 | 29.6228
1127.2542 | 363.7979 | 193.0416 | 222.0455 | 268.2234 | 259.9038 | 88.8337 | 29.6388
1128.2542 | 364.4778 | 193.2811 | 221.9305 | 268.7054 | 259.7789 | 88.9341 | 29.6701
1129.2542 | 364.3761 | 193.5323 | 221.687 | 268.594 | 260.3238 | 89.0426 | 29.6895
1130.2542 | 363.5263 | 193.7899 | 221.5341 | 268.5274 | 260.0501 | 89.1474 | 29.7125
1131.2542 | 362.1729 | 194.0525 | 221.4084 | 268.9651 | 260.5451 | 89.2611 | 29.737
1132.2542 | 361.8552 | 194.2995 | 221.7906 | 269.1791 | 260.5017 | 89.3665 | 29.7702
1133.2542 | 361.1619 | 194.5674 | 221.9339 | 269.0818 | 260.5784 | 89.4723 | 29.7932
1134.2542 | 362.4578 | 194.7972 | 221.7891 | 269.1839 | 261.2691 | 89.5873 | 29.8199
1135.2542 | 362.8668 | 195.0645 | 222.4139 | 269.3547 | 261.3128 | 89.7056 | 29.8487
1136.2542 | 363.0418 | 195.3077 | 222.4688 | 269.2131 | 261.3639 | 89.8209 | 29.8661
1137.2542 | 364.2632 | 195.5307 | 222.2191 | 268.6746 | 261.199 | 89.9225 | 29.894
1138.2542 | 363.7442 | 195.8081 | 221.541 | 268.3503 | 261.6153 | 90.0299 | 29.9242
1139.2542 | 362.9077 | 196.0479 | 221.5377 | 269.1174 | 261.3602 | 90.1362 | 29.9501
1140.2542 | 362.3907 | 196.2837 | 221.6843 | 269.5534 | 261.0984 | 90.2543 | 29.9736
1141.2542 | 362.95 | 196.5617 | 221.701 | 270.5004 | 261.6274 | 90.3655 | 29.9939
1142.2542 | 363.418 | 196.8112 | 221.5517 | 270.966 | 262.5693 | 90.4649 | 30.0209
1143.2542 | 362.6033 | 197.0486 | 221.7588 | 271.5675 | 262.538 | 90.574 | 30.051
1144.2542 | 361.7235 | 197.2755 | 221.3302 | 271.1623 | 262.3496 | 90.6894 | 30.0774
1145.2542 | 361.8185 | 197.5175 | 221.4431 | 271.4366 | 263.5293 | 90.7978 | 30.1021
1146.2542 | 362.2288 | 197.7661 | 221.9907 | 271.5135 | 263.6718 | 90.9065 | 30.1341
1147.2542 | 364.8971 | 197.9839 | 222.3092 | 271.3218 | 263.1257 | 90.9947 | 30.1623
1148.2542 | 365.7044 | 198.2429 | 222.3457 | 271.0451 | 264.6335 | 91.1075 | 30.1801
1149.2542 | 367.856 | 198.4822 | 222.4222 | 271.7404 | 264.1621 | 91.2236 | 30.2096
1150.2542 | 368.5511 | 198.7163 | 222.5996 | 271.4734 | 265.0636 | 91.3192 | 30.2362
1151.2542 | 367.684 | 198.9348 | 222.9701 | 271.8585 | 266.5444 | 91.4231 | 30.2589
1152.2542 | 368.749 | 199.1579 | 223.4431 | 272.574 | 265.7592 | 91.5246 | 30.2856
1153.2542 | 370.6804 | 199.3841 | 223.5024 | 272.6528 | 265.5787 | 91.6213 | 30.3035
1154.2542 | 369.2933 | 199.5999 | 223.6505 | 273.1268 | 264.8526 | 91.7366 | 30.3319
1155.2542 | 367.3591 | 199.8189 | 223.9998 | 273.2216 | 265.8764 | 91.8413 | 30.3665
1156.2542 | 365.7104 | 200.0249 | 223.7852 | 273.3092 | 265.1374 | 91.9437 | 30.3843
1157.2542 | 365.7424 | 200.2415 | 223.7236 | 273.6013 | 265.4517 | 92.0525 | 30.4194
1158.2542 | 365.4348 | 200.4581 | 223.7874 | 274.1844 | 265.4264 | 92.1499 | 30.4331
1159.2542 | 365.072 | 200.6739 | 223.636 | 273.6117 | 265.0739 | 92.253 | 30.4644
1160.2542 | 365.3923 | 200.8879 | 223.8696 | 273.5867 | 264.8012 | 92.3648 | 30.4861
1161.2542 | 366.1328 | 201.0845 | 223.5563 | 273.8018 | 264.5561 | 92.4598 | 30.5158
1162.2542 | 367.0327 | 201.304 | 224.3662 | 273.5418 | 265.1175 | 92.564 | 30.534
1163.2542 | 367.0078 | 201.4921 | 224.6352 | 273.5123 | 264.9763 | 92.6686 | 30.5578
1164.2542 | 367.1166 | 201.6798 | 224.6658 | 273.6448 | 265.0284 | 92.7836 | 30.5753
1165.2542 | 367.8529 | 201.895 | 224.8309 | 274.1116 | 266.3694 | 92.8837 | 30.6104
1166.2542 | 369.3718 | 202.0829 | 225.1506 | 273.695 | 266.044 | 92.9991 | 30.6377
1167.2542 | 368.8113 | 202.2793 | 225.5076 | 273.199 | 265.6962 | 93.1 | 30.6581
1168.2542 | 369.766 | 202.4665 | 225.1279 | 272.79 | 265.1868 | 93.2082 | 30.6847
1169.2542 | 370.4907 | 202.6713 | 225.4966 | 272.416 | 265.5523 | 93.3098 | 30.7136
1170.2542 | 370.6149 | 202.8504 | 226.0952 | 272.7725 | 265.7577 | 93.413 | 30.7284
1171.2542 | 373.0325 | 203.0341 | 226.3184 | 274.2289 | 265.3235 | 93.5137 | 30.7632
1172.2542 | 372.9622 | 203.1945 | 227.1331 | 274.785 | 267.0687 | 93.6172 | 30.7895
1173.2542 | 372.4381 | 203.408 | 226.9 | 274.5129 | 268.3374 | 93.7269 | 30.8088
1174.2542 | 371.7894 | 203.5712 | 227.0203 | 274.1132 | 268.0504 | 93.8296 | 30.8249
1175.2542 | 371.5474 | 203.7494 | 226.7258 | 274.1551 | 267.3681 | 93.9325 | 30.8493
1176.2542 | 371.3931 | 203.9269 | 226.712 | 273.6997 | 267.2996 | 94.0387 | 30.8755
1177.2542 | 372.8423 | 204.0948 | 227.4756 | 273.3947 | 267.2874 | 94.1405 | 30.9065
1178.2542 | 373.2015 | 204.2901 | 227.5648 | 273.0212 | 267.143 | 94.2499 | 30.9247
1179.2542 | 373.8303 | 204.4246 | 228.0423 | 273.0832 | 267.0208 | 94.3613 | 30.9497
1180.2542 | 374.8088 | 204.5914 | 228.3032 | 273.2212 | 267.3386 | 94.4639 | 30.9675
1181.2542 | 374.6029 | 204.7497 | 228.183 | 273.447 | 267.4571 | 94.5741 | 30.9876
1182.2542 | 374.6519 | 204.9102 | 228.0615 | 273.8257 | 269.4558 | 94.6728 | 31.0105
1183.2542 | 375.1172 | 205.0558 | 228.3025 | 273.7465 | 269.4912 | 94.7885 | 31.0362
1184.2542 | 375.5366 | 205.1921 | 228.5316 | 273.5563 | 269.2344 | 94.8904 | 31.0606
1185.2542 | 375.7307 | 205.3471 | 228.8064 | 273.3969 | 269.037 | 94.9947 | 31.0821
1186.2542 | 375.6435 | 205.497 | 229.63 | 273.7046 | 268.5264 | 95.1018 | 31.1066
1187.2542 | 376.1867 | 205.658 | 229.5461 | 273.8599 | 269.188 | 95.1977 | 31.1323
1188.2542 | 378.0291 | 205.8199 | 229.423 | 273.2205 | 269.0245 | 95.2976 | 31.1498
1189.2542 | 376.7988 | 205.966 | 229.3998 | 272.7197 | 269.0162 | 95.4072 | 31.1766
1190.2542 | 377.83 | 206.1071 | 229.407 | 272.6924 | 269.1933 | 95.5031 | 31.2122
1191.2542 | 376.382 | 206.2755 | 228.9442 | 272.9154 | 269.5034 | 95.6087 | 31.2261
1192.2542 | 373.9975 | 206.4474 | 228.7237 | 272.8886 | 269.4716 | 95.7156 | 31.2539
1193.2542 | 373.7071 | 206.585 | 228.843 | 272.2564 | 268.9566 | 95.8087 | 31.2717
1194.2542 | 374.1099 | 206.7422 | 228.6503 | 272.0005 | 268.7264 | 95.9104 | 31.2902
1195.2542 | 374.7661 | 206.9002 | 228.7168 | 271.8809 | 268.8519 | 96.0088 | 31.303
1196.2542 | 374.3203 | 207.04 | 228.5096 | 271.9732 | 268.5458 | 96.1177 | 31.3324
1197.2542 | 372.9021 | 207.195 | 228.3599 | 273.2852 | 268.2058 | 96.2155 | 31.3624
1198.2542 | 373.1385 | 207.3275 | 229.1897 | 273.782 | 267.8179 | 96.3219 | 31.3841
1199.2542 | 372.7391 | 207.4835 | 228.8596 | 273.538 | 267.6578 | 96.4186 | 31.4055
1200.2542 | 372.6624 | 207.623 | 228.4177 | 273.1576 | 267.6966 | 96.5212 | 31.4334
1201.2542 | 374.2839 | 207.7749 | 228.3558 | 272.6543 | 267.8655 | 96.6245 | 31.4549
1202.2542 | 373.8427 | 207.9173 | 228.5326 | 272.0528 | 267.4826 | 96.7226 | 31.4772
1203.2542 | 373.7551 | 208.0669 | 228.4724 | 271.5629 | 267.3037 | 96.827 | 31.5062
1204.2542 | 374.0078 | 208.2125 | 229.0066 | 271.3981 | 267.5416 | 96.9323 | 31.5328
1205.2542 | 375.2364 | 208.3482 | 228.7981 | 271.099 | 267.6559 | 97.0301 | 31.5532
1206.2542 | 375.9274 | 208.4831 | 228.7646 | 271.9393 | 267.5148 | 97.1344 | 31.5762
1207.2542 | 374.4496 | 208.6236 | 228.5607 | 272.078 | 267.674 | 97.2429 | 31.6006
1208.2542 | 373.3689 | 208.7676 | 228.0754 | 272.0292 | 268.1143 | 97.343 | 31.6219
1209.2542 | 373.7502 | 208.8971 | 228.6972 | 273.2913 | 268.4685 | 97.445 | 31.6407
1210.2542 | 373.1963 | 209.0621 | 228.495 | 273.5156 | 268.1536 | 97.547 | 31.6729
1211.2542 | 372.5636 | 209.1911 | 228.7636 | 273.5667 | 267.5494 | 97.6555 | 31.6886
1212.2542 | 370.7231 | 209.3226 | 228.8934 | 273.9687 | 267.5027 | 97.7487 | 31.7199
1213.2542 | 370.1543 | 209.4496 | 228.8289 | 273.9834 | 267.369 | 97.8467 | 31.7508
1214.2542 | 368.7189 | 209.5712 | 228.6627 | 273.7904 | 266.7491 | 97.9415 | 31.781
1215.2542 | 367.3348 | 209.7273 | 228.9209 | 273.4746 | 266.9957 | 98.046 | 31.8009
1216.2542 | 368.5846 | 209.8707 | 228.4186 | 273.0364 | 266.5941 | 98.1439 | 31.824
1217.2542 | 369.812 | 209.9761 | 229.0904 | 273.2011 | 266.5543 | 98.2406 | 31.8562
1218.2542 | 372.46 | 210.1136 | 230.3969 | 273.2667 | 267.9182 | 98.3396 | 31.8854
1219.2542 | 374.2228 | 210.2274 | 230.5672 | 273.5408 | 267.4383 | 98.4429 | 31.9005
1220.2542 | 374.9556 | 210.3531 | 230.7931 | 274.3727 | 268.2648 | 98.5429 | 31.9231
1221.2542 | 376.3256 | 210.492 | 230.946 | 274.3726 | 268.697 | 98.6478 | 31.9422
1222.2542 | 377.2271 | 210.6131 | 230.7727 | 273.9887 | 269.8568 | 98.7597 | 31.9775
1223.2542 | 377.7196 | 210.7522 | 231.5949 | 273.6846 | 269.4287 | 98.8547 | 31.9966
1224.2542 | 378.9553 | 210.8804 | 231.1612 | 273.2483 | 269.1704 | 98.9523 | 32.0288
1225.2542 | 381.4729 | 211.0115 | 231.1186 | 273.2739 | 268.3587 | 99.0601 | 32.0497
1226.2542 | 382.3853 | 211.1234 | 231.3265 | 273.0851 | 267.6957 | 99.1672 | 32.0735
1227.2542 | 381.0318 | 211.2894 | 231.786 | 272.6788 | 267.9572 | 99.2715 | 32.1087
1228.2542 | 381.6277 | 211.4191 | 231.6038 | 273.1014 | 268.3906 | 99.3746 | 32.1202
1229.2542 | 382.4918 | 211.5552 | 231.8392 | 273.6248 | 268.3799 | 99.4592 | 32.1446
1230.2542 | 382.4196 | 211.6964 | 231.8211 | 274.3943 | 269.2954 | 99.5648 | 32.175
1231.2542 | 382.491 | 211.8306 | 231.5627 | 274.458 | 269.4278 | 99.6603 | 32.1931
1232.2542 | 384.2184 | 211.951 | 231.3869 | 274.5774 | 269.3148 | 99.7515 | 32.2148
1233.2542 | 385.1779 | 212.1026 | 232.2216 | 276.123 | 269.8116 | 99.8548 | 32.256
1234.2542 | 385.1852 | 212.2254 | 231.8366 | 275.9257 | 270.0737 | 99.942 | 32.2728
1235.2542 | 387.0267 | 212.3689 | 231.5335 | 276.4364 | 270.342 | 100.0343 | 32.2952
1236.2542 | 385.6747 | 212.5 | 231.7453 | 276.6556 | 270.3789 | 100.1307 | 32.3276
1237.2542 | 385.9794 | 212.6337 | 231.6375 | 276.8427 | 270.0243 | 100.231 | 32.3478
1238.2542 | 387.1618 | 212.7763 | 231.2603 | 276.3739 | 269.5412 | 100.3213 | 32.377
1239.2542 | 386.9448 | 212.9208 | 231.8419 | 276.0422 | 270.2722 | 100.4148 | 32.4012
1240.2542 | 386.222 | 213.0555 | 231.7773 | 275.8398 | 270.4274 | 100.5053 | 32.4272
1241.2542 | 387.2559 | 213.2126 | 231.9905 | 276.0882 | 270.9855 | 100.5999 | 32.4548
1242.2542 | 385.9787 | 213.3422 | 232.6089 | 277.195 | 271.2974 | 100.6916 | 32.4665
1243.2542 | 386.7487 | 213.4854 | 232.9428 | 279.2368 | 270.8237 | 100.7878 | 32.4951
1244.2542 | 387.7784 | 213.6363 | 232.8862 | 279.0027 | 271.1399 | 100.877 | 32.5197
1245.2542 | 388.1169 | 213.7639 | 232.6031 | 278.7732 | 271.0901 | 100.971 | 32.5482
1246.2542 | 388.0229 | 213.9044 | 233.794 | 278.4804 | 271.4196 | 101.072 | 32.5573
1247.2542 | 385.8113 | 214.0086 | 234.2022 | 278.5241 | 272.0626 | 101.1683 | 32.5886
1248.2542 | 384.859 | 214.1635 | 234.3636 | 278.6067 | 271.677 | 101.2672 | 32.6209
1249.2542 | 384.5528 | 214.3026 | 234.3899 | 278.7351 | 272.1694 | 101.3588 | 32.6493
1250.2542 | 383.0881 | 214.4562 | 234.1003 | 279.4168 | 271.7372 | 101.4725 | 32.6654
1251.2542 | 383.4813 | 214.5709 | 233.7127 | 280.657 | 271.5206 | 101.5795 | 32.7006
1252.2542 | 384.0749 | 214.7356 | 233.765 | 280.6473 | 272.1063 | 101.6831 | 32.7195
1253.2542 | 383.5201 | 214.852 | 234.2697 | 280.4339 | 272.9183 | 101.7945 | 32.7436
1254.2542 | 382.1579 | 214.9815 | 233.8603 | 280.1721 | 272.9998 | 101.9042 | 32.7759
1255.2542 | 382.4696 | 215.1295 | 233.7554 | 281.3072 | 272.2762 | 102.0173 | 32.7941
1256.2542 | 384.0692 | 215.2641 | 233.5374 | 280.523 | 272.5849 | 102.1247 | 32.8172
1257.2542 | 382.8092 | 215.3888 | 234.2967 | 280.0579 | 272.7566 | 102.2255 | 32.842
1258.2542 | 382.096 | 215.5466 | 235.3343 | 279.7405 | 273.0696 | 102.3381 | 32.8665
1259.2542 | 384.7213 | 215.6703 | 235.1999 | 279.6785 | 272.3383 | 102.4414 | 32.9019
1260.2542 | 384.6287 | 215.817 | 234.5897 | 279.6973 | 272.4703 | 102.5398 | 32.9183
1261.2542 | 385.2615 | 215.9627 | 234.2355 | 280.2584 | 272.4078 | 102.6377 | 32.955
1262.2542 | 383.2473 | 216.0928 | 234.5463 | 280.7818 | 272.0492 | 102.7399 | 32.9783
1263.2542 | 384.4965 | 216.2282 | 235.2028 | 280.631 | 271.7636 | 102.8317 | 33
1264.2542 | 382.2815 | 216.3608 | 235.336 | 280.0228 | 271.5744 | 102.922 | 33.0291
1265.2542 | 380.9899 | 216.5126 | 235.1512 | 279.0939 | 271.4385 | 103.0232 | 33.0472
1266.2542 | 380.9317 | 216.6552 | 235.4776 | 278.9757 | 272.3228 | 103.116 | 33.0826
1267.2542 | 381.4573 | 216.7929 | 235.3407 | 278.7643 | 272.2124 | 103.2113 | 33.1008
1268.2542 | 381.6556 | 216.922 | 235.954 | 278.4895 | 272.4608 | 103.3008 | 33.1229
1269.2542 | 381.9765 | 217.0779 | 236.6199 | 278.4307 | 272.8047 | 103.398 | 33.1589
1270.2542 | 384.5249 | 217.1855 | 236.2747 | 278.5023 | 272.5094 | 103.4946 | 33.1785
1271.2542 | 383.9232 | 217.3108 | 237.018 | 278.8711 | 273.0702 | 103.5861 | 33.207
1272.2542 | 384.8475 | 217.455 | 237.1492 | 278.8683 | 273.1387 | 103.6818 | 33.2253
1273.2542 | 385.1521 | 217.6127 | 237.2313 | 278.6969 | 273.5735 | 103.7791 | 33.2689
1274.2542 | 388.565 | 217.7545 | 236.6526 | 278.2718 | 273.4172 | 103.8766 | 33.2746
1275.2542 | 388.7467 | 217.8817 | 236.7599 | 278.8252 | 273.5021 | 103.9769 | 33.3122
1276.2542 | 388.4121 | 218.0182 | 236.3849 | 279.1528 | 273.9664 | 104.0716 | 33.3438
1277.2542 | 387.5592 | 218.1462 | 236.4417 | 279.4238 | 273.8041 | 104.1735 | 33.3522
1278.2542 | 387.1441 | 218.2835 | 236.5565 | 279.3196 | 273.483 | 104.2609 | 33.3793
1279.2542 | 386.9447 | 218.4402 | 236.946 | 280.1466 | 274.7048 | 104.3616 | 33.4095
1280.2542 | 387.5958 | 218.5721 | 237.3216 | 280.507 | 274.5285 | 104.4514 | 33.4346
1281.2542 | 387.2864 | 218.7249 | 237.1226 | 280.0689 | 274.8377 | 104.5534 | 33.4493
1282.2542 | 387.1025 | 218.8549 | 237.2215 | 280.4973 | 274.8053 | 104.6482 | 33.4827
1283.2542 | 387.558 | 218.9787 | 237.67 | 280.7394 | 274.474 | 104.7429 | 33.5053
1284.2542 | 389.1646 | 219.1178 | 237.6092 | 280.9635 | 276.692 | 104.842 | 33.5351
1285.2542 | 389.9943 | 219.2549 | 237.8643 | 281.2894 | 276.2371 | 104.9409 | 33.5549
1286.2542 | 390.2476 | 219.3854 | 237.8818 | 281.2027 | 276.7653 | 105.0355 | 33.5887
1287.2542 | 390.1777 | 219.5136 | 238.161 | 281.6629 | 277.1226 | 105.1285 | 33.6101
1288.2542 | 389.6344 | 219.6287 | 238.3202 | 281.4875 | 277.8128 | 105.226 | 33.6448
1289.2542 | 386.7546 | 219.7746 | 238.4738 | 283.4486 | 278.5386 | 105.3203 | 33.6658
1290.2542 | 384.5951 | 219.9333 | 239.3679 | 283.5188 | 278.8217 | 105.4222 | 33.6922
1291.2542 | 384.2753 | 220.0774 | 239.0221 | 283.2093 | 279.2228 | 105.5234 | 33.7133
1292.2542 | 383.6711 | 220.226 | 238.2197 | 282.9121 | 279.0192 | 105.6209 | 33.7483
1293.2542 | 387.1648 | 220.3625 | 237.6655 | 282.7293 | 278.5349 | 105.7214 | 33.764
1294.2542 | 387.305 | 220.5014 | 238.1754 | 282.2151 | 278.4168 | 105.8168 | 33.78
1295.2542 | 388.2105 | 220.6444 | 237.8838 | 282.7026 | 278.622 | 105.9152 | 33.8097
1296.2542 | 387.2289 | 220.7691 | 238.475 | 283.1648 | 278.0371 | 106.0249 | 33.8308
1297.2542 | 385.0725 | 220.9251 | 238.3827 | 283.1406 | 277.8509 | 106.1277 | 33.8593
1298.2542 | 385.8909 | 221.0581 | 238.5917 | 283.2531 | 277.4843 | 106.2222 | 33.8847
1299.2542 | 384.3256 | 221.2107 | 238.2547 | 283.8024 | 277.4392 | 106.3269 | 33.9219
1300.2542 | 384.6624 | 221.3446 | 238.3526 | 283.7286 | 277.231 | 106.4183 | 33.9451
1301.2542 | 383.2695 | 221.4911 | 238.2511 | 283.6382 | 277.6033 | 106.5114 | 33.9598
1302.2542 | 382.0098 | 221.6162 | 238.1767 | 283.6824 | 277.097 | 106.6165 | 33.9868
1303.2542 | 381.6417 | 221.7223 | 237.8053 | 283.0187 | 276.86 | 106.7123 | 34.0035
1304.2542 | 381.8069 | 221.8624 | 237.6439 | 283.2099 | 277.4607 | 106.8103 | 34.0409
1305.2542 | 380.1811 | 221.9849 | 237.0732 | 283.3107 | 277.3336 | 106.9109 | 34.0642
1306.2542 | 378.4134 | 222.1252 | 236.6398 | 282.9819 | 277.3119 | 107.0066 | 34.0908
1307.2542 | 376.8582 | 222.2269 | 235.9691 | 283.4732 | 277.5339 | 107.094 | 34.0997
1308.2542 | 376.3783 | 222.3676 | 236.0619 | 284.1549 | 277.8231 | 107.1864 | 34.1372
1309.2542 | 375.9819 | 222.4994 | 235.7862 | 283.6821 | 277.1637 | 107.2799 | 34.1629
1310.2542 | 375.2328 | 222.6247 | 235.748 | 283.2739 | 277.3922 | 107.3698 | 34.1865
1311.2542 | 375.3981 | 222.7621 | 236.07 | 283.5536 | 277.1184 | 107.464 | 34.2153
1312.2542 | 374.1713 | 222.8938 | 236.173 | 284.1197 | 277.297 | 107.5593 | 34.2358
1313.2542 | 375.0803 | 223.015 | 236.0637 | 284.1342 | 276.9191 | 107.6507 | 34.269
1314.2542 | 374.9464 | 223.1441 | 236.2385 | 284.2038 | 277.1157 | 107.7363 | 34.2842
1315.2542 | 374.1803 | 223.2722 | 236.2881 | 285.0388 | 276.8845 | 107.8273 | 34.306
1316.2542 | 373.3309 | 223.3892 | 236.7169 | 285.8597 | 276.9358 | 107.9184 | 34.3492
1317.2542 | 372.9274 | 223.5174 | 236.4831 | 285.5469 | 277.1929 | 107.9991 | 34.3602
1318.2542 | 373.3788 | 223.6139 | 237.1026 | 285.0537 | 277.2751 | 108.0867 | 34.3872
1319.2542 | 373.0589 | 223.718 | 236.8426 | 284.8282 | 276.9613 | 108.1807 | 34.4218
1320.2542 | 373.8658 | 223.8438 | 237.0472 | 284.9695 | 277.179 | 108.2703 | 34.4443
1321.2542 | 373.9657 | 223.9508 | 237.0435 | 285.136 | 276.9915 | 108.3556 | 34.4755
1322.2542 | 373.6277 | 224.0741 | 237.0147 | 285.1032 | 277.3869 | 108.439 | 34.4959
1323.2542 | 372.7197 | 224.1948 | 237.3646 | 285.0135 | 277.0539 | 108.5321 | 34.5285
1324.2542 | 373.2013 | 224.3132 | 237.4935 | 285.0489 | 277.79 | 108.6291 | 34.5514
1325.2542 | 373.0781 | 224.4325 | 237.6334 | 285.063 | 278.9143 | 108.7118 | 34.587
1326.2542 | 373.5644 | 224.5469 | 237.8591 | 284.7674 | 278.8303 | 108.7977 | 34.6092
1327.2542 | 374.3435 | 224.6649 | 237.8737 | 285.621 | 278.5977 | 108.8934 | 34.627
1328.2542 | 374.5714 | 224.7909 | 237.858 | 285.0157 | 278.656 | 108.9836 | 34.6614
1329.2542 | 374.7562 | 224.9165 | 238.1096 | 285.4907 | 278.5058 | 109.0837 | 34.6885
1330.2542 | 375.5156 | 225.0517 | 237.8945 | 285.9776 | 278.1381 | 109.1614 | 34.7046
1331.2542 | 375.2214 | 225.166 | 237.6447 | 286.0626 | 278.2938 | 109.2573 | 34.731
1332.2542 | 373.7105 | 225.2642 | 237.7018 | 284.9968 | 277.977 | 109.3546 | 34.7514
1333.2542 | 373.2511 | 225.3987 | 237.926 | 284.3376 | 278.2741 | 109.444 | 34.7726
1334.2542 | 373.0192 | 225.5259 | 237.9488 | 284.0542 | 278.329 | 109.5281 | 34.8087
1335.2542 | 375.4199 | 225.6436 | 238.0311 | 283.388 | 277.9071 | 109.624 | 34.843
1336.2542 | 375.8281 | 225.7533 | 237.7028 | 283.0473 | 277.8705 | 109.7225 | 34.8547
1337.2542 | 374.1928 | 225.8885 | 237.9233 | 283.2205 | 278.1757 | 109.8008 | 34.8987
1338.2542 | 373.4375 | 225.9826 | 237.6693 | 282.6375 | 277.6642 | 109.8949 | 34.9119
1339.2542 | 374.7602 | 226.1071 | 237.6773 | 282.4732 | 277.6646 | 109.9864 | 34.9422
1340.2542 | 373.704 | 226.235 | 238.5613 | 282.7044 | 278.0184 | 110.0775 | 34.9591
1341.2542 | 371.8838 | 226.3595 | 238.2052 | 282.6783 | 278.1729 | 110.1604 | 34.9911
1342.2542 | 369.9621 | 226.4521 | 238.618 | 282.0887 | 277.7528 | 110.251 | 35.018
1343.2542 | 369.7073 | 226.6055 | 238.7229 | 281.716 | 276.8815 | 110.3402 | 35.0308
1344.2542 | 370.8703 | 226.7248 | 238.8216 | 281.3481 | 276.9239 | 110.4262 | 35.0708
1345.2542 | 372.5679 | 226.8354 | 238.0716 | 281.5714 | 278.3648 | 110.5145 | 35.093
1346.2542 | 373.0908 | 226.9448 | 238.5743 | 282.1075 | 277.8195 | 110.5982 | 35.1183
1347.2542 | 374.5758 | 227.0596 | 237.9037 | 281.8589 | 277.1944 | 110.6819 | 35.1442
1348.2542 | 375.0925 | 227.1603 | 237.6642 | 281.4403 | 277.8745 | 110.7634 | 35.1654
1349.2542 | 375.4966 | 227.2732 | 237.1355 | 281.1372 | 277.9419 | 110.8512 | 35.193
1350.2542 | 372.8652 | 227.4004 | 237.195 | 281.4194 | 277.2833 | 110.938 | 35.2127
1351.2542 | 373.0766 | 227.5086 | 237.1804 | 281.471 | 276.9868 | 111.0133 | 35.2333
1352.2542 | 371.4567 | 227.6336 | 237.6932 | 281.3963 | 277.1919 | 111.0834 | 35.2648
1353.2542 | 370.9018 | 227.7511 | 237.698 | 281.4304 | 278.1601 | 111.1683 | 35.3019
1354.2542 | 370.1913 | 227.8397 | 237.8608 | 281.449 | 278.8348 | 111.2417 | 35.3142
1355.2542 | 371.0005 | 227.9476 | 238.0411 | 281.4469 | 278.4216 | 111.3154 | 35.3481
1356.2542 | 369.8904 | 228.0669 | 238.1505 | 281.3302 | 278.2306 | 111.3938 | 35.3689
1357.2542 | 368.7257 | 228.1875 | 238.0384 | 281.2997 | 278.0075 | 111.4754 | 35.3886
1358.2542 | 368.3962 | 228.3005 | 239.1226 | 281.0281 | 277.0655 | 111.5484 | 35.422
1359.2542 | 368.4209 | 228.4314 | 238.8283 | 280.7687 | 277.0219 | 111.6258 | 35.4463
1360.2542 | 369.1457 | 228.5276 | 239.0103 | 281.3007 | 276.5001 | 111.7114 | 35.472
1361.2542 | 371.2969 | 228.6508 | 239.1202 | 281.3657 | 276.6273 | 111.7827 | 35.4909
1362.2542 | 369.9364 | 228.761 | 239.4939 | 281.5188 | 276.8375 | 111.8701 | 35.5242
1363.2542 | 370.4361 | 228.8833 | 239.4293 | 281.4079 | 276.5393 | 111.9538 | 35.5399
1364.2542 | 370.3395 | 228.9794 | 239.7393 | 281.3665 | 276.6755 | 112.04 | 35.5774
1365.2542 | 371.4316 | 229.0986 | 239.6148 | 281.3525 | 276.9047 | 112.1251 | 35.593
1366.2542 | 372.5757 | 229.209 | 239.8216 | 282.5727 | 276.9102 | 112.2069 | 35.6236
1367.2542 | 371.7525 | 229.3085 | 239.6641 | 282.7825 | 276.8463 | 112.3041 | 35.6464
1368.2542 | 371.9163 | 229.4416 | 239.6618 | 282.9848 | 277.0507 | 112.3891 | 35.6708
1369.2542 | 371.3515 | 229.5264 | 239.8549 | 283.9832 | 276.7763 | 112.4839 | 35.6898
1370.2542 | 369.7385 | 229.6416 | 240.6989 | 283.8522 | 276.8322 | 112.574 | 35.7177
1371.2542 | 368.9196 | 229.75 | 240.908 | 283.3155 | 277.3006 | 112.6611 | 35.736
1372.2542 | 367.4328 | 229.9051 | 241.05 | 282.6193 | 276.9087 | 112.7574 | 35.7676
1373.2542 | 365.5037 | 230.0145 | 241.0346 | 283.1768 | 277.6778 | 112.854 | 35.7793
1374.2542 | 364.1668 | 230.1366 | 241.0313 | 283.5213 | 277.504 | 112.9358 | 35.8163
1375.2542 | 362.5105 | 230.2471 | 241.4756 | 283.5223 | 277.0202 | 113.0341 | 35.8354
1376.2542 | 362.0684 | 230.3487 | 241.7601 | 283.6758 | 277.1337 | 113.1196 | 35.8525
1377.2542 | 362.5423 | 230.4816 | 241.627 | 283.5774 | 276.4487 | 113.2141 | 35.8691
1378.2542 | 363.5625 | 230.6048 | 242.1939 | 283.4039 | 276.2471 | 113.3063 | 35.8969
1379.2542 | 363.685 | 230.7082 | 242.0725 | 284.0174 | 276.0586 | 113.3946 | 35.9251
1380.2542 | 363.8141 | 230.8354 | 242.0076 | 283.7117 | 276.0568 | 113.4843 | 35.9478
1381.2542 | 363.4884 | 230.9577 | 242.2096 | 283.6707 | 276.3694 | 113.5781 | 35.9623
1382.2542 | 363.563 | 231.067 | 242.8045 | 283.8307 | 277.6027 | 113.6777 | 35.9893
1383.2542 | 363.7968 | 231.1631 | 242.5549 | 283.6856 | 277.5715 | 113.7709 | 36.0077
1384.2542 | 365.0335 | 231.2761 | 242.6151 | 284.1169 | 277.8399 | 113.8731 | 36.0374
1385.2542 | 365.9605 | 231.3988 | 242.6829 | 284.3643 | 277.7321 | 113.9721 | 36.0502
1386.2542 | 366.5268 | 231.5145 | 242.3497 | 285.3394 | 277.8205 | 114.0764 | 36.0746
1387.2542 | 366.6503 | 231.622 | 242.2241 | 285.429 | 277.9051 | 114.1811 | 36.1031
1388.2542 | 367.8494 | 231.7302 | 241.9795 | 285.2984 | 278.0089 | 114.2798 | 36.1182
1389.2542 | 368.8396 | 231.851 | 242.1667 | 285.0379 | 278.1857 | 114.3919 | 36.1473
1390.2542 | 371.3693 | 231.967 | 241.6169 | 285.0699 | 278.1052 | 114.4982 | 36.175
1391.2542 | 372.759 | 232.0776 | 242.112 | 284.7268 | 277.8788 | 114.5979 | 36.1881
1392.2542 | 374.8744 | 232.2044 | 242.2226 | 285.2777 | 277.9791 | 114.7071 | 36.2096
1393.2542 | 374.8367 | 232.3083 | 242.1914 | 285.2167 | 277.8315 | 114.8094 | 36.2373
1394.2542 | 374.9177 | 232.4168 | 242.2343 | 286.4034 | 277.8662 | 114.9058 | 36.2584
1395.2542 | 376.5306 | 232.5305 | 242.1357 | 286.3297 | 277.432 | 115.0071 | 36.2785
1396.2542 | 376.1111 | 232.6625 | 242.3557 | 286.7273 | 277.4219 | 115.1019 | 36.3088
1397.2542 | 376.0717 | 232.7772 | 242.7025 | 287.6962 | 277.9915 | 115.1917 | 36.3276
1398.2542 | 376.8188 | 232.8931 | 243.1079 | 287.6966 | 278.2713 | 115.2876 | 36.3388
1399.2542 | 375.7015 | 233.0168 | 243.875 | 288.7522 | 278.6653 | 115.3747 | 36.3732
1400.2542 | 376.053 | 233.1215 | 244.4061 | 288.4694 | 278.2962 | 115.4637 | 36.3854
1401.2542 | 378.4996 | 233.2355 | 244.6554 | 288.704 | 279.1171 | 115.5695 | 36.4092
1402.2542 | 378.8851 | 233.3547 | 244.5551 | 288.4947 | 279.5776 | 115.672 | 36.4236
1403.2542 | 381.778 | 233.4693 | 244.736 | 288.7453 | 278.8256 | 115.7678 | 36.4499
1404.2542 | 383.636 | 233.6053 | 245.0552 | 288.5701 | 279.4427 | 115.8712 | 36.4806
1405.2542 | 384.67 | 233.736 | 245.0226 | 288.6434 | 279.607 | 115.9698 | 36.5019
1406.2542 | 385.4798 | 233.8504 | 245.6621 | 288.637 | 279.1665 | 116.0669 | 36.5268
1407.2542 | 386.4234 | 233.964 | 245.054 | 288.5156 | 279.8585 | 116.1663 | 36.5442
1408.2542 | 385.5371 | 234.099 | 245.0125 | 289.096 | 280.6064 | 116.2653 | 36.5625
1409.2542 | 386.0516 | 234.1987 | 245.5041 | 288.791 | 280.2757 | 116.3637 | 36.5815
1410.2542 | 384.4022 | 234.313 | 244.9192 | 288.7074 | 280.7562 | 116.4745 | 36.603
1411.2542 | 384.0384 | 234.4176 | 245.4113 | 288.6689 | 281.5259 | 116.5673 | 36.6233
1412.2542 | 383.5503 | 234.5599 | 244.9186 | 288.3672 | 280.8409 | 116.6549 | 36.6473
1413.2542 | 384.0688 | 234.6752 | 245.3426 | 288.1105 | 281.871 | 116.7564 | 36.6628
1414.2542 | 384.1652 | 234.8069 | 245.205 | 288.4354 | 281.4241 | 116.8458 | 36.696
1415.2542 | 384.033 | 234.9377 | 245.2034 | 288.8967 | 280.7434 | 116.9388 | 36.7088
1416.2542 | 383.1824 | 235.037 | 245.3449 | 289.0469 | 280.726 | 117.0407 | 36.7308
1417.2542 | 381.982 | 235.1612 | 245.8778 | 289.6699 | 280.8677 | 117.135 | 36.7511
1418.2542 | 383.4951 | 235.2812 | 246.3554 | 289.3238 | 280.8558 | 117.2337 | 36.7708
1419.2542 | 384.7698 | 235.4042 | 246.1108 | 289.5741 | 280.9151 | 117.3344 | 36.7928
1420.2542 | 385.4334 | 235.524 | 246.2546 | 290.2257 | 280.5693 | 117.4346 | 36.8105
1421.2542 | 387.3274 | 235.6606 | 246.7134 | 291.6341 | 280.6943 | 117.532 | 36.8336
1422.2542 | 387.6657 | 235.792 | 246.8905 | 291.8605 | 280.5164 | 117.6241 | 36.8463
1423.2542 | 387.8382 | 235.9145 | 246.851 | 291.1279 | 280.3202 | 117.7173 | 36.8662
1424.2542 | 387.1252 | 236.0686 | 247.5301 | 290.3426 | 280.7176 | 117.8097 | 36.8928
1425.2542 | 387.384 | 236.2159 | 249.1059 | 290.2143 | 281.2043 | 117.9041 | 36.909
1426.2542 | 388.6783 | 236.3368 | 249.0579 | 290.4646 | 280.8826 | 118.0024 | 36.9395
1427.2542 | 388.0596 | 236.4699 | 249.392 | 290.0571 | 281.4307 | 118.1019 | 36.9508
1428.2542 | 389.0376 | 236.6103 | 249.4424 | 290.2607 | 280.9823 | 118.1998 | 36.9847
1429.2542 | 388.7721 | 236.7373 | 249.4223 | 289.873 | 280.9277 | 118.3072 | 37.0044
1430.2542 | 389.6248 | 236.8738 | 249.953 | 289.2075 | 281.2221 | 118.3968 | 37.027
1431.2542 | 388.8478 | 236.9822 | 249.5753 | 288.7233 | 281.2368 | 118.4919 | 37.0514
1432.2542 | 388.3404 | 237.1122 | 248.829 | 289.3363 | 281.21 | 118.5863 | 37.0582
1433.2542 | 387.6504 | 237.2402 | 248.0351 | 289.2514 | 281.414 | 118.6763 | 37.0953
1434.2542 | 388.3237 | 237.3586 | 247.7018 | 289.5471 | 281.2003 | 118.7786 | 37.1177
1435.2542 | 388.0242 | 237.4841 | 247.4786 | 289.4057 | 281.0185 | 118.8742 | 37.1243
1436.2542 | 388.4351 | 237.5843 | 247.8228 | 289.2394 | 281.2237 | 118.9719 | 37.1527
1437.2542 | 389.0811 | 237.7171 | 247.7829 | 288.9089 | 280.8425 | 119.0661 | 37.1738
1438.2542 | 389.0528 | 237.8395 | 247.856 | 288.6498 | 281.0513 | 119.1586 | 37.1846
1439.2542 | 390.976 | 237.9677 | 248.2123 | 288.4611 | 280.7343 | 119.2662 | 37.2069
1440.2542 | 390.4383 | 238.0963 | 248.277 | 288.1111 | 280.5709 | 119.3644 | 37.2196
1441.2542 | 390.4441 | 238.2164 | 248.3342 | 288.2403 | 281.016 | 119.4638 | 37.2512
1442.2542 | 390.2716 | 238.3467 | 248.6048 | 288.44 | 281.3546 | 119.5541 | 37.2687
1443.2542 | 390.4801 | 238.487 | 248.3778 | 288.6507 | 281.61 | 119.6423 | 37.2907
1444.2542 | 389.1246 | 238.6188 | 248.2945 | 288.2835 | 281.8357 | 119.7379 | 37.3136
1445.2542 | 388.7825 | 238.7561 | 248.0492 | 288.6667 | 281.6437 | 119.8223 | 37.3228
1446.2542 | 389.0052 | 238.8892 | 248.1865 | 288.0217 | 281.5573 | 119.9328 | 37.3487
1447.2542 | 388.9734 | 239.0211 | 248.66 | 287.7489 | 280.7081 | 120.0381 | 37.3757
1448.2542 | 387.5053 | 239.1457 | 249.2357 | 287.6294 | 281.4127 | 120.134 | 37.3922
1449.2542 | 385.5291 | 239.2673 | 249.1623 | 287.3185 | 281.6073 | 120.2368 | 37.4079
1450.2542 | 385.8795 | 239.3909 | 248.8514 | 287.262 | 282.1752 | 120.3386 | 37.43
1451.2542 | 384.3789 | 239.526 | 248.7932 | 287.1081 | 282.3008 | 120.4277 | 37.4449
1452.2542 | 384.373 | 239.6678 | 248.7972 | 287.3087 | 282.3242 | 120.5312 | 37.4732
1453.2542 | 384.697 | 239.7999 | 249.4317 | 287.6091 | 282.3419 | 120.6244 | 37.4906
1454.2542 | 384.623 | 239.9334 | 249.4954 | 287.5642 | 281.6272 | 120.7267 | 37.5031
1455.2542 | 384.6068 | 240.0536 | 249.5873 | 288.3083 | 281.8393 | 120.8217 | 37.5251
1456.2698 | 383.6022 | 240.1858 | 249.5608 | 288.4465 | 282.3091 | 120.9225 | 37.5464
1457.2542 | 384.1346 | 240.2991 | 249.4131 | 288.8272 | 282.5997 | 121.009 | 37.5686
1458.2542 | 383.6111 | 240.4309 | 249.2441 | 289.4312 | 281.7653 | 121.1117 | 37.5976
1459.2542 | 383.5767 | 240.5482 | 249.1401 | 289.6345 | 282.7363 | 121.2118 | 37.604
1460.2542 | 385.554 | 240.6992 | 249.5598 | 289.8042 | 282.8914 | 121.3092 | 37.6236
1461.2542 | 386.5916 | 240.8398 | 249.4546 | 291.1028 | 282.4341 | 121.4102 | 37.6558
1462.2542 | 388.5608 | 240.9555 | 249.4906 | 290.5771 | 282.804 | 121.5012 | 37.6711
1463.2542 | 388.5564 | 241.0984 | 249.9546 | 290.2519 | 282.9494 | 121.5975 | 37.6995
1464.2542 | 387.9652 | 241.2486 | 250.1662 | 290.0139 | 282.7414 | 121.6924 | 37.7179
1465.2542 | 387.4284 | 241.3926 | 250.0268 | 290.4357 | 283.328 | 121.7953 | 37.7389
1466.2542 | 388.1334 | 241.5119 | 249.8613 | 290.0277 | 283.2666 | 121.8876 | 37.7509
1467.2542 | 388.8862 | 241.6833 | 250.1957 | 289.7251 | 283.4313 | 121.9817 | 37.7586
1468.2542 | 390.3479 | 241.8129 | 250.3935 | 289.6361 | 283.112 | 122.0789 | 37.7975
1469.2542 | 391.3271 | 241.942 | 250.535 | 289.8561 | 282.6553 | 122.1595 | 37.8053
1470.2542 | 392.0877 | 242.1117 | 250.6244 | 291.3517 | 282.7775 | 122.1616 | 37.8328
1471.2542 | 391.5435 | 242.2455 | 250.7537 | 291.3785 | 282.5823 | 122.2611 | 37.8588
1472.2542 | 390.2449 | 242.3691 | 250.8682 | 291.0875 | 282.2068 | 122.373 | 37.871
1473.2542 | 388.8082 | 242.4899 | 251.0383 | 291.5567 | 282.0708 | 122.4809 | 37.8895
1474.2542 | 388.0903 | 242.5963 | 250.9354 | 291.7076 | 282.0384 | 122.5752 | 37.9287
1475.2542 | 387.7652 | 242.7217 | 250.9693 | 291.8056 | 282.1307 | 122.6641 | 37.9443
1476.2542 | 386.9316 | 242.823 | 250.8742 | 292.7412 | 282.3708 | 122.766 | 37.9624
1477.2542 | 386.7543 | 242.9707 | 250.641 | 293.4539 | 282.2029 | 122.8659 | 37.9745
1478.2542 | 387.7486 | 243.1013 | 250.7813 | 293.9366 | 282.2194 | 122.957 | 37.9992
1479.2542 | 387.8798 | 243.2372 | 250.7294 | 295.1737 | 283.798 | 123.0471 | 38.0164
1480.2542 | 388.4073 | 243.372 | 250.9564 | 294.8619 | 283.3902 | 123.1446 | 38.0449
1481.2542 | 387.7145 | 243.5018 | 251.0026 | 294.8391 | 284.6738 | 123.2388 | 38.0738
1482.2542 | 387.9606 | 243.6393 | 251.5207 | 294.962 | 284.6344 | 123.3358 | 38.0889
1483.2542 | 389.5326 | 243.7818 | 251.2836 | 294.4497 | 284.7689 | 123.4243 | 38.1122
1484.2542 | 389.0161 | 243.9137 | 251.2895 | 294.3492 | 285.7408 | 123.5274 | 38.1263
1485.2542 | 390.6957 | 244.0557 | 251.7278 | 294.6517 | 285.7382 | 123.6195 | 38.1632
1486.2542 | 391.3679 | 244.1769 | 252.0659 | 295.68 | 286.0491 | 123.7179 | 38.1815
1487.2542 | 393.7058 | 244.3345 | 252.6519 | 295.452 | 286.2089 | 123.8144 | 38.1978
1488.2542 | 392.3038 | 244.4949 | 252.7248 | 296.4391 | 286.5069 | 123.9238 | 38.2207
1489.2542 | 391.9762 | 244.6439 | 253.1383 | 296.9802 | 286.94 | 124.0281 | 38.2454
1490.2542 | 391.2203 | 244.792 | 253.5822 | 296.7457 | 287.3386 | 124.122 | 38.2726
1491.2542 | 390.6345 | 244.9405 | 253.8014 | 297.094 | 287.135 | 124.2289 | 38.2937
1492.2542 | 391.1609 | 245.0824 | 253.9516 | 296.5039 | 286.6782 | 124.3258 | 38.3095
1493.2542 | 391.9644 | 245.246 | 254.0879 | 297.1933 | 286.9268 | 124.4265 | 38.3254
1494.2542 | 392.6303 | 245.4195 | 254.1453 | 297.8234 | 286.8163 | 124.528 | 38.3438
1495.2542 | 391.0086 | 245.5596 | 254.1327 | 297.7428 | 286.6854 | 124.6278 | 38.3648
1496.2542 | 389.1649 | 245.7368 | 254.0858 | 297.6818 | 286.4213 | 124.728 | 38.3888
1497.2542 | 388.1208 | 245.9063 | 253.7215 | 298.2969 | 286.5579 | 124.8303 | 38.4062
1498.2542 | 389.1302 | 246.072 | 253.7236 | 297.7819 | 286.5289 | 124.9246 | 38.41
1499.2542 | 388.8024 | 246.2265 | 253.6867 | 298.0529 | 287.0684 | 125.0264 | 38.4413
1500.2542 | 388.0752 | 246.3919 | 253.6602 | 298.2222 | 287.6793 | 125.1231 | 38.4612
1501.2542 | 387.9643 | 246.5639 | 254.1284 | 298.7543 | 286.991 | 125.2244 | 38.4836
1502.2542 | 387.3163 | 246.7276 | 254.0302 | 299.0034 | 287.0068 | 125.3253 | 38.4993
1503.2542 | 387.5452 | 246.8845 | 253.8227 | 298.6799 | 287.2439 | 125.4189 | 38.5239
1504.2542 | 388.9757 | 247.0429 | 254.2931 | 298.5552 | 286.8373 | 125.5197 | 38.5321
1505.2542 | 389.0602 | 247.2469 | 254.1704 | 298.3514 | 287.6826 | 125.6178 | 38.5583
1506.2542 | 390.1059 | 247.4138 | 254.5959 | 298.8703 | 288.2631 | 125.7153 | 38.5706
1507.2542 | 390.4104 | 247.5808 | 254.5954 | 299.3132 | 287.9395 | 125.8165 | 38.5914
1508.2542 | 390.0176 | 247.7898 | 254.7397 | 299.3236 | 288.5104 | 125.9141 | 38.6215
1509.2542 | 391.001 | 248.0036 | 255.3899 | 299.4666 | 288.528 | 126.0148 | 38.6328
1510.2542 | 393.8907 | 248.1888 | 255.9956 | 300.0012 | 288.389 | 126.1154 | 38.6353
1511.2542 | 395.4015 | 248.4298 | 256.5109 | 300.2053 | 288.0571 | 126.2156 | 38.6693
1512.2542 | 396.1535 | 248.6583 | 256.7289 | 300.7908 | 288.359 | 126.3185 | 38.6797
1513.2542 | 399.7903 | 248.8649 | 256.9057 | 300.5159 | 287.92 | 126.4181 | 38.696
1514.2542 | 401.1014 | 249.1018 | 257.6245 | 300.3341 | 288.2902 | 126.5247 | 38.7166
1515.2542 | 399.839 | 249.3385 | 257.8517 | 300.3625 | 288.0969 | 126.6306 | 38.7258
1516.2542 | 401.2082 | 249.5741 | 258.321 | 300.0893 | 287.8729 | 126.739 | 38.7518
1517.2542 | 402.4208 | 249.7956 | 258.5443 | 299.9294 | 288.0623 | 126.8518 | 38.7669
1518.2542 | 402.9925 | 250.0159 | 259.3518 | 299.7003 | 288.3947 | 126.9529 | 38.787
1519.2542 | 405.3165 | 250.2521 | 259.1477 | 300.0683 | 287.7546 | 127.0664 | 38.8019
1520.2542 | 404.8584 | 250.4828 | 258.8132 | 300.1057 | 288.6574 | 127.1775 | 38.8186
1521.2542 | 407.4619 | 250.6967 | 259.1619 | 300.2329 | 289.1848 | 127.2891 | 38.8489
1522.2542 | 409.2829 | 250.9427 | 258.5946 | 300.4852 | 288.963 | 127.4172 | 38.8489
1523.2542 | 410.7523 | 251.1833 | 259.0179 | 300.9529 | 289.5961 | 127.5286 | 38.8628
1524.2542 | 410.4301 | 251.4037 | 259.5301 | 301.093 | 289.2566 | 127.6434 | 38.8848
1525.2542 | 410.4892 | 251.6426 | 260.1369 | 300.861 | 289.2894 | 127.7642 | 38.9
1526.2542 | 407.9987 | 251.8699 | 259.9873 | 301.0667 | 289.8401 | 127.8762 | 38.9262
1527.2542 | 406.2636 | 252.1072 | 260.3441 | 301.7483 | 289.697 | 127.9879 | 38.9315
1528.2542 | 405.7082 | 252.3527 | 260.9208 | 301.7748 | 289.9543 | 128.1144 | 38.9544
1529.2542 | 407.3538 | 252.6062 | 261.0649 | 302.7552 | 291.2797 | 128.2223 | 38.9742
1530.2542 | 408.4048 | 252.8651 | 261.0497 | 302.8607 | 290.4451 | 128.3458 | 38.9966
1531.2542 | 407.5403 | 253.1022 | 261.3153 | 302.8348 | 289.7366 | 128.4602 | 39.0154
1532.2542 | 406.7877 | 253.3942 | 261.4681 | 303.5283 | 289.5867 | 128.5792 | 39.0307
1533.2542 | 408.5427 | 253.6821 | 261.4588 | 303.7567 | 289.6071 | 128.6942 | 39.047
1534.2542 | 411.2965 | 253.9705 | 262.4747 | 303.1012 | 290.5029 | 128.8217 | 39.0748
1535.2542 | 412.6913 | 254.2444 | 262.7728 | 303.1296 | 290.0694 | 128.9385 | 39.0861
1536.2542 | 414.5993 | 254.5439 | 263.5516 | 304.5686 | 291.0814 | 129.0553 | 39.1179
1537.2542 | 414.9938 | 254.8257 | 264.0886 | 304.7806 | 292.5761 | 129.1691 | 39.1385
1538.2542 | 415.8834 | 255.1313 | 264.3471 | 304.6431 | 293.3554 | 129.2833 | 39.1559
1539.2542 | 416.3618 | 255.4625 | 264.1536 | 304.7343 | 293.2507 | 129.3961 | 39.1813
1540.2542 | 417.7533 | 255.7697 | 264.6086 | 305.5319 | 293.6439 | 129.5146 | 39.1968
1541.2542 | 419.3435 | 256.0551 | 265.1979 | 306.1236 | 294.074 | 129.6195 | 39.2101
1542.2542 | 419.7745 | 256.3524 | 265.3305 | 307.24 | 294.1053 | 129.7428 | 39.2196
1543.2542 | 422.2101 | 256.6449 | 265.4627 | 308.5939 | 294.2045 | 129.86 | 39.2453
1544.2542 | 424.9859 | 256.9559 | 265.9739 | 309.6641 | 294.1968 | 129.98 | 39.2692
1545.2542 | 425.0147 | 257.256 | 266.1552 | 308.8691 | 294.214 | 130.0932 | 39.2857
1546.2542 | 424.763 | 257.5484 | 266.1445 | 308.7492 | 294.8629 | 130.2173 | 39.3117
1547.2542 | 424.4143 | 257.8321 | 266.0237 | 308.5738 | 295.145 | 130.3354 | 39.3296
1548.2542 | 425.7698 | 258.1161 | 267.0785 | 309.9473 | 295.048 | 130.4538 | 39.3449
1549.2542 | 424.6468 | 258.3837 | 266.6946 | 309.387 | 294.9984 | 130.5712 | 39.3646
1550.2542 | 426.2664 | 258.6561 | 266.7082 | 309.6968 | 296.4449 | 130.6945 | 39.3734
1551.2542 | 425.689 | 258.9181 | 266.5199 | 309.9762 | 296.6712 | 130.8101 | 39.4036
1552.2542 | 425.2581 | 259.1754 | 266.6134 | 309.7372 | 296.5932 | 130.9291 | 39.4188
1553.2542 | 427.0895 | 259.4213 | 266.6302 | 308.9011 | 296.5771 | 131.0382 | 39.4397
1554.2542 | 425.3749 | 259.6572 | 266.243 | 308.6029 | 297.0177 | 131.1557 | 39.4643
1555.2542 | 423.2525 | 259.9216 | 265.7994 | 308.4576 | 297.6951 | 131.2609 | 39.4789
1556.2542 | 422.142 | 260.1962 | 265.9688 | 308.6007 | 298.0663 | 131.3763 | 39.4958
1557.2542 | 420.232 | 260.4773 | 265.9699 | 308.5637 | 298.1769 | 131.4889 | 39.5174
1558.2542 | 420.7952 | 260.7423 | 266.1028 | 309.0142 | 298.5882 | 131.6004 | 39.5481
1559.2542 | 421.5323 | 260.8074 | 266.5363 | 309.6233 | 298.1762 | 131.717 | 39.5623
1560.2542 | 422.9963 | 260.9314 | 267.0025 | 309.6871 | 298.292 | 131.8283 | 39.5705
1561.2542 | 423.4401 | 261.0641 | 266.7151 | 309.8461 | 298.5138 | 131.9348 | 39.6016
1562.2542 | 425.7151 | 261.1947 | 266.9572 | 310.3581 | 299.1058 | 132.055 | 39.6072
1563.2542 | 425.9225 | 261.3493 | 266.9161 | 310.0369 | 299.1202 | 132.1783 | 39.6448
1564.2542 | 426.277 | 261.4851 | 267.2381 | 309.6996 | 299.0446 | 132.2919 | 39.6503
1565.2542 | 426.8381 | 261.6569 | 268.1976 | 309.5412 | 299.3094 | 132.4024 | 39.6724
1566.2542 | 426.6476 | 261.8556 | 268.8487 | 309.3743 | 299.3239 | 132.522 | 39.6914
1567.2542 | 427.3736 | 262.0577 | 269.5199 | 309.6861 | 299.352 | 132.6413 | 39.7089
1568.2542 | 426.1812 | 262.3021 | 269.3638 | 309.8822 | 298.6825 | 132.7587 | 39.739
1569.2542 | 427.5017 | 262.5335 | 269.9595 | 310.6152 | 298.9493 | 132.8664 | 39.7489
1570.2542 | 429.1131 | 262.7782 | 270.2723 | 310.872 | 299.0737 | 132.9925 | 39.7791
1571.2542 | 428.9985 | 263.0495 | 270.1896 | 311.8365 | 299.3089 | 133.1116 | 39.8025
1572.2542 | 427.3839 | 263.3066 | 270.5713 | 312.2024 | 299.3667 | 133.2246 | 39.8167
1573.2542 | 430.1491 | 263.5795 | 269.9516 | 312.3603 | 299.9314 | 133.3385 | 39.8428
1574.2542 | 430.1368 | 263.8352 | 269.8756 | 312.9688 | 300.6215 | 133.449 | 39.8574
1575.2542 | 429.6479 | 264.0813 | 270.7309 | 313.8223 | 300.5976 | 133.566 | 39.8763
1576.2542 | 428.8356 | 264.3527 | 270.7491 | 313.988 | 300.1765 | 133.683 | 39.9017
1577.2542 | 432.1364 | 264.6042 | 271.3805 | 314.2663 | 300.4307 | 133.7924 | 39.9212
1578.2542 | 432.98 | 264.8721 | 272.2388 | 314.5267 | 301.3055 | 133.9116 | 39.9469
1579.2542 | 432.8959 | 265.1574 | 272.6223 | 314.8465 | 301.0289 | 134.0282 | 39.9571
1580.2542 | 431.4801 | 265.4207 | 273.0448 | 314.8052 | 300.8014 | 134.147 | 39.9829
1581.2542 | 435.7465 | 265.6757 | 273.501 | 314.9659 | 300.9807 | 134.266 | 40
1582.2542 | 435.6736 | 265.9594 | 273.3984 | 314.8391 | 301.3795 | 134.3841 | 40.019
1583.2542 | 435.1082 | 266.2899 | 273.083 | 314.8683 | 301.546 | 134.505 | 40.0506
1584.2542 | 437 | 266.5801 | 272.7651 | 314.6526 | 301.9246 | 134.6218 | 40.055
1585.2542 | 439.7379 | 266.8718 | 272.3169 | 314.6117 | 301.5858 | 134.7446 | 40.0827
1586.2542 | 437.7277 | 267.1713 | 272.3235 | 314.362 | 300.9542 | 134.8615 | 40.0863
1587.2542 | 440.107 | 267.5013 | 272.2342 | 314.773 | 300.9708 | 134.9825 | 40.1184
1588.2542 | 440.3081 | 267.8082 | 272.6542 | 315.1352 | 300.2444 | 135.1053 | 40.1359
1589.2542 | 441.6721 | 268.147 | 272.9194 | 315.4604 | 301.5854 | 135.2326 | 40.1549
1590.2542 | 442.0841 | 268.4799 | 272.3793 | 315.6381 | 301.4179 | 135.345 | 40.1807
1591.2542 | 442.5308 | 268.7738 | 271.9151 | 315.499 | 302.0799 | 135.47 | 40.1986
1592.2542 | 442.7616 | 269.0773 | 272.2023 | 316.0296 | 302.3473 | 135.5938 | 40.2162
1593.2542 | 445.1418 | 269.3673 | 272.5208 | 315.3391 | 302.0449 | 135.7052 | 40.2294
1594.2542 | 449.0083 | 269.6566 | 272.5385 | 314.9346 | 302.419 | 135.8193 | 40.2618
1595.2542 | 452.7772 | 269.9384 | 272.9115 | 314.5099 | 302.5863 | 135.9346 | 40.2728
1596.2542 | 449.2161 | 270.1661 | 273.4229 | 314.2744 | 302.2212 | 136.0347 | 40.2901
1597.2542 | 450.8653 | 270.4136 | 273.1973 | 314.347 | 302.7266 | 136.1191 | 40.312
1598.2542 | 454.6731 | 270.6521 | 273.3845 | 314.2846 | 303.1792 | 136.2367 | 40.3368
1599.2542 | 452.466 | 270.8985 | 273.5117 | 314.0588 | 303.3657 | 136.3502 | 40.3505
1600.2542 | 454.9181 | 271.1623 | 273.7316 | 315.446 | 303.406 | 136.4793 | 40.373
1601.2542 | 452.3927 | 271.4139 | 273.7774 | 315.6217 | 303.0634 | 136.5939 | 40.3949
1602.2542 | 449.6579 | 271.6766 | 273.8085 | 315.7022 | 303.7241 | 136.7041 | 40.4024
1603.2542 | 450.4914 | 271.9291 | 274.3302 | 315.275 | 304.03 | 136.8273 | 40.4258
1604.2542 | 451.2341 | 272.1911 | 274.5686 | 315.4655 | 304.2113 | 136.9373 | 40.4447
1605.2542 | 450.7229 | 272.4581 | 274.6122 | 315.8166 | 304.042 | 137.0568 | 40.4647
1606.2542 | 454.0369 | 272.6968 | 274.6341 | 315.6545 | 303.2954 | 137.167 | 40.4835
1607.2542 | 456.4239 | 272.9336 | 274.8603 | 316.1319 | 303.4755 | 137.2843 | 40.507
1608.2542 | 451.6625 | 273.2107 | 275.1852 | 316.3317 | 303.8082 | 137.4059 | 40.5147
1609.2542 | 447.252 | 273.4705 | 274.9251 | 316.0829 | 304.3118 | 137.5169 | 40.548
1610.2542 | 448.8648 | 273.7079 | 274.6523 | 315.7132 | 304.2337 | 137.6368 | 40.5651
1611.2542 | 457.0053 | 273.9635 | 274.2737 | 315.466 | 304.0462 | 137.7533 | 40.5918
1612.2542 | 456.9024 | 274.2249 | 274.1731 | 315.2016 | 305.5214 | 137.865 | 40.605
1613.2542 | 460.9398 | 274.4791 | 274.0126 | 314.878 | 305.5955 | 137.9811 | 40.6289
1614.2542 | 465.0131 | 274.7235 | 273.9544 | 314.3095 | 305.6742 | 138.0966 | 40.6419
1615.2542 | 465.6576 | 274.9725 | 274.4431 | 313.8949 | 305.1188 | 138.2051 | 40.6653
1616.2542 | 466.2223 | 275.1956 | 275.0301 | 314.1539 | 304.9349 | 138.3226 | 40.6877
1617.2542 | 465.7882 | 275.4369 | 274.9247 | 314.2828 | 304.5885 | 138.434 | 40.6998
1618.2542 | 469.1268 | 275.6611 | 275.0533 | 314.4824 | 304.718 | 138.5454 | 40.7284
1619.2542 | 474.4264 | 275.9033 | 275.4463 | 314.124 | 304.7664 | 138.6657 | 40.7393
1620.2542 | 468.8972 | 276.1205 | 276.2669 | 314.7516 | 304.7471 | 138.7805 | 40.7624
1621.2542 | 468.6945 | 276.3365 | 276.1965 | 315.1916 | 304.5185 | 138.8902 | 40.7807
1622.2542 | 476.6868 | 276.5347 | 275.9938 | 315.1062 | 304.6739 | 138.9996 | 40.8008
1623.2542 | 483.2196 | 276.7535 | 275.4259 | 315.6785 | 305.156 | 139.1069 | 40.8244
1624.2542 | 473.8736 | 276.9603 | 276.3921 | 316.1376 | 305.5982 | 139.2259 | 40.842
1625.2542 | 475.5076 | 277.1518 | 276.7201 | 316.149 | 305.7671 | 139.3333 | 40.8661
1626.2542 | 472.2249 | 277.3744 | 276.8427 | 317.1194 | 306.0814 | 139.4447 | 40.8751
1627.2542 | 477.6693 | 277.553 | 277.2221 | 317.7468 | 306.5197 | 139.5642 | 40.8961
1628.2542 | 469.516 | 277.7414 | 277.5353 | 318.2351 | 306.7024 | 139.6669 | 40.9366
1629.2542 | 467.8351 | 277.8997 | 278.0487 | 318.2316 | 307.3879 | 139.7875 | 40.9472
1630.2542 | 465.5446 | 278.0952 | 278.5748 | 318.8373 | 307.7428 | 139.9021 | 40.9633
1631.2542 | 464.5154 | 278.2576 | 279.3762 | 319.8927 | 307.2476 | 140.013 | 40.9897
1632.2542 | 458.6427 | 278.4254 | 279.6774 | 322.0761 | 307.2533 | 140.1237 | 40.9975
1633.2542 | 459.4647 | 278.6173 | 280.0769 | 321.6907 | 307.7401 | 140.2395 | 41.0278
1634.2542 | 461.5912 | 278.806 | 280.0308 | 321.039 | 307.5106 | 140.356 | 41.0572
1635.2542 | 461.0369 | 278.9931 | 280.4594 | 320.926 | 307.6791 | 140.4732 | 41.0708
1636.2542 | 460.8526 | 279.1649 | 280.2964 | 320.7002 | 307.3089 | 140.5756 | 41.0934
1637.2542 | 466.0308 | 279.3409 | 280.2807 | 321.297 | 306.4147 | 140.6948 | 41.1096
1638.2542 | 467.5363 | 279.4787 | 280.2278 | 321.1144 | 305.8818 | 140.8046 | 41.1311
1639.2542 | 465.1996 | 279.6272 | 280.2408 | 320.3541 | 306.3207 | 140.9223 | 41.1602
1640.2542 | 469.7486 | 279.7787 | 280.2067 | 320.1391 | 305.667 | 141.0372 | 41.1839
1641.2542 | 471.3546 | 279.9537 | 280.2278 | 319.9505 | 306.3336 | 141.1527 | 41.1952
1642.2542 | 467.3051 | 280.1045 | 281.2104 | 319.9916 | 306.5549 | 141.2687 | 41.2107
1643.2542 | 465.693 | 280.2545 | 281.4597 | 320.3517 | 307.6875 | 141.3901 | 41.2432
1644.2542 | 468.6781 | 280.4196 | 282.2614 | 321.5291 | 308.3518 | 141.5018 | 41.2522
1645.2542 | 466.8401 | 280.5849 | 282.3804 | 322.3542 | 309.0206 | 141.6211 | 41.2841
1646.2542 | 463.6601 | 280.7531 | 282.1005 | 322.4404 | 309.0849 | 141.7399 | 41.3162
1647.2542 | 462.8305 | 280.9098 | 282.1215 | 323.0677 | 309.6915 | 141.8606 | 41.3341
1648.2542 | 461.1156 | 281.0607 | 281.8457 | 324.1306 | 310.1467 | 141.978 | 41.3468
1649.2542 | 459.3245 | 281.2273 | 281.9655 | 324.1364 | 310.6266 | 142.1015 | 41.3753
1650.2542 | 454.3703 | 281.3562 | 282.2268 | 323.826 | 311.136 | 142.2196 | 41.3963
1651.2542 | 453.3258 | 281.4565 | 282.8092 | 323.3139 | 311.7899 | 142.3345 | 41.4266
1652.2542 | 450.6377 | 281.578 | 283.2461 | 323.4983 | 311.4081 | 142.4445 | 41.4265
1653.2542 | 453.0779 | 281.7027 | 283.9036 | 324.3909 | 311.6678 | 142.5605 | 41.4539
1654.2542 | 448.2508 | 281.7916 | 283.9785 | 324.8776 | 311.104 | 142.6783 | 41.4858
1655.2542 | 450.0264 | 281.9097 | 283.8016 | 325.4701 | 310.7879 | 142.8023 | 41.5012
1656.2542 | 450.263 | 282.038 | 284.3002 | 326.3528 | 311.6408 | 142.8998 | 41.5122
1657.2698 | 447.1694 | 282.1388 | 285.0191 | 326.7672 | 311.8995 | 143.024 | 41.546
1658.2542 | 451.1741 | 282.2205 | 284.9042 | 326.5476 | 312.3536 | 143.151 | 41.5721
1659.2542 | 451.3715 | 282.3333 | 285.489 | 325.9745 | 312.3312 | 143.2736 | 41.5905
1660.2542 | 449.316 | 282.4433 | 284.9449 | 325.6045 | 312.0571 | 143.3901 | 41.6052
1661.2542 | 451.1621 | 282.5861 | 285.185 | 325.3716 | 311.9418 | 143.5011 | 41.6343
1662.2542 | 450.9691 | 282.7507 | 284.9853 | 325.1595 | 311.493 | 143.6232 | 41.6611
1663.2542 | 449.5187 | 282.9029 | 284.8865 | 324.7331 | 310.5613 | 143.7424 | 41.6834
1664.2542 | 451.3984 | 283.1007 | 284.8003 | 324.4875 | 310.1 | 143.8668 | 41.7003
1665.2542 | 447.6163 | 283.2902 | 284.4555 | 323.7968 | 310.1321 | 143.9754 | 41.7283
1666.2542 | 448.3653 | 283.4885 | 284.8757 | 323.6857 | 310.0931 | 144.1013 | 41.7524
1667.2542 | 448.0145 | 283.6856 | 284.9448 | 324.936 | 310.8627 | 144.2087 | 41.7722
1668.2542 | 446.1411 | 283.8741 | 285.2891 | 325.0927 | 310.4058 | 144.322 | 41.7926
1669.2542 | 445.078 | 284.1148 | 284.913 | 324.9948 | 310.2924 | 144.4394 | 41.81
1670.2542 | 443.5148 | 284.3365 | 285.063 | 324.6592 | 310.3339 | 144.5546 | 41.8343
1671.2542 | 442.8092 | 284.5943 | 284.6729 | 324.512 | 309.8138 | 144.6704 | 41.8477
1672.2542 | 442.7449 | 284.8215 | 284.8777 | 324.7302 | 309.9529 | 144.7856 | 41.881
1673.2542 | 443.0121 | 285.0332 | 285.5497 | 324.6588 | 309.359 | 144.8966 | 41.8947
1674.2542 | 449.1793 | 285.2728 | 285.0361 | 324.626 | 309.3579 | 145.0136 | 41.9273
1675.2542 | 454.8314 | 285.5046 | 284.8852 | 324.3467 | 309.3451 | 145.1236 | 41.9537
1676.2542 | 457.7686 | 285.7273 | 285.0587 | 324.3168 | 309.5126 | 145.2465 | 41.9549
1677.2542 | 471.2587 | 285.961 | 284.7523 | 324.9738 | 309.4841 | 145.3552 | 41.9877
1678.2542 | 470.0961 | 286.1921 | 284.545 | 325.534 | 308.9955 | 145.4637 | 41.9979
1679.2542 | 474.0701 | 286.4103 | 284.684 | 325.7529 | 308.6064 | 145.5818 | 42.0288
1680.2542 | 472.5577 | 286.6379 | 285.054 | 326.0491 | 308.8656 | 145.6992 | 42.0539
1681.2542 | 475.0612 | 286.8778 | 285.3986 | 325.9481 | 308.3212 | 145.8144 | 42.0677
1682.2542 | 472.4087 | 287.107 | 285.5586 | 325.8288 | 308.4623 | 145.9283 | 42.1042
1683.2542 | 469.9581 | 287.3375 | 285.5496 | 325.8664 | 309.5649 | 146.043 | 42.1247
1684.2542 | 467.3534 | 287.609 | 285.5328 | 326.1043 | 309.4831 | 146.1592 | 42.149
1685.2542 | 465.7983 | 287.871 | 285.7752 | 326.1378 | 310.1749 | 146.2706 | 42.1584
1686.2542 | 463.8451 | 288.1995 | 285.6077 | 326.885 | 311.3366 | 146.3864 | 42.1881
1687.2542 | 463.045 | 288.4894 | 285.7581 | 327.9224 | 310.3105 | 146.4977 | 42.2126
1688.2542 | 461.3225 | 288.7612 | 287.1872 | 327.715 | 310.8428 | 146.6062 | 42.2319
1689.2542 | 462.0661 | 289.0078 | 287.9434 | 327.3269 | 310.5634 | 146.7222 | 42.2507
1690.2542 | 462.412 | 289.2636 | 287.785 | 327.0734 | 311.2314 | 146.8348 | 42.2798
1691.2542 | 462.3637 | 289.5134 | 288.2088 | 328.0221 | 311.1066 | 146.9487 | 42.2923
1692.2542 | 461.7373 | 289.7918 | 288.7902 | 327.7021 | 311.7076 | 147.059 | 42.3349
1693.2542 | 458.8899 | 290.0707 | 288.7355 | 327.7209 | 312.2995 | 147.1728 | 42.3549
1694.2542 | 457.0202 | 290.3175 | 288.9838 | 327.1493 | 312.7238 | 147.2887 | 42.3668
1695.2542 | 453.23 | 290.5762 | 288.7233 | 326.8467 | 313.2422 | 147.4002 | 42.3927
1696.2542 | 450.004 | 290.8766 | 288.7962 | 326.6405 | 312.8418 | 147.5184 | 42.4165
1697.2542 | 447.479 | 291.1371 | 289.0361 | 327.0251 | 312.2873 | 147.6253 | 42.4349
1698.2542 | 445.162 | 291.4332 | 289.9393 | 327.4909 | 313.4476 | 147.7366 | 42.4594
1699.2542 | 444.8917 | 291.7192 | 289.8389 | 327.8074 | 313.5066 | 147.8777 | 42.5014
1700.2542 | 446.1007 | 292.0034 | 289.5074 | 326.9218 | 313.425 | 147.9806 | 42.506
1701.2542 | 444.5276 | 292.2932 | 289.502 | 326.9372 | 314.2775 | 148.0972 | 42.522
1702.2542 | 444.9323 | 292.627 | 289.3598 | 326.6818 | 313.722 | 148.1957 | 42.5544
1703.2542 | 447.875 | 292.9572 | 289.6996 | 326.5933 | 313.7317 | 148.3099 | 42.5792
1704.2542 | 448.5194 | 293.3061 | 289.0555 | 327.3712 | 313.5387 | 148.4331 | 42.5988
1705.2542 | 448.1451 | 293.6326 | 289.0319 | 328.4902 | 315.0705 | 148.5421 | 42.6137
1706.2542 | 447.1408 | 293.9081 | 290.2254 | 328.5944 | 315.6768 | 148.6468 | 42.6476
1707.2542 | 448.9182 | 294.22 | 290.4848 | 329.2536 | 315.0366 | 148.7722 | 42.6674
1708.2542 | 449.328 | 294.5339 | 290.8728 | 329.8048 | 314.9015 | 148.8854 | 42.687
1709.2542 | 448.6748 | 294.8176 | 290.7873 | 329.4075 | 315.1169 | 148.9949 | 42.7117
1710.2542 | 446.9597 | 295.1205 | 291.0425 | 330.1218 | 315.9448 | 149.1079 | 42.7323
1711.2542 | 445.0886 | 295.4317 | 291.3569 | 330.3046 | 315.4244 | 149.2179 | 42.748
1712.2542 | 441.5251 | 295.7373 | 291.9638 | 330.7972 | 314.8472 | 149.3343 | 42.7665
1713.2542 | 438.9638 | 296.0321 | 292.3605 | 330.5277 | 313.8466 | 149.4379 | 42.7899
1714.2542 | 436.2607 | 296.2882 | 292.9527 | 330.4162 | 314.154 | 149.554 | 42.8098
1715.2542 | 434.4785 | 296.5483 | 293.3524 | 330.6103 | 314.4888 | 149.6599 | 42.8308
1716.2542 | 433.8621 | 296.7925 | 293.9893 | 331.4354 | 314.008 | 149.76 | 42.8512
1717.2542 | 432.7261 | 297.0217 | 294.1101 | 331.7306 | 313.2124 | 149.8795 | 42.8649
1718.2542 | 431.4071 | 297.2803 | 294.1231 | 332.6025 | 313.2118 | 149.9973 | 42.8809
1719.2542 | 431.5705 | 297.5247 | 293.6405 | 332.3457 | 312.6166 | 150.1098 | 42.9079
1720.2542 | 430.0638 | 297.7448 | 293.4937 | 332.29 | 313.5785 | 150.2257 | 42.9324
1721.2542 | 427.6428 | 297.9639 | 293.8092 | 331.936 | 312.997 | 150.3453 | 42.9546
1722.2542 | 426.4595 | 298.1589 | 293.9564 | 331.2158 | 312.5774 | 150.4605 | 42.9669
1723.2542 | 426.0896 | 298.3412 | 294.2388 | 331.3918 | 312.4009 | 150.5806 | 42.9916
1724.2542 | 426.4994 | 298.562 | 294.119 | 331.6444 | 312.0669 | 150.6787 | 43.0051
1725.2542 | 428.3795 | 298.8001 | 293.8366 | 331.4497 | 311.9203 | 150.7989 | 43.0229
1726.2542 | 427.4904 | 298.9863 | 294.004 | 331.3456 | 312.0399 | 150.9206 | 43.0544
1727.2542 | 427.0507 | 299.1834 | 294.3837 | 331.2564 | 312.2273 | 151.0368 | 43.0583
1728.2542 | 426.0158 | 299.3411 | 294.7284 | 330.7943 | 312.8612 | 151.157 | 43.0872
1729.2542 | 426.7442 | 299.5468 | 294.3539 | 330.1338 | 313.54 | 151.2765 | 43.0995
1730.2542 | 427.0844 | 299.7307 | 294.8342 | 329.886 | 313.9332 | 151.3966 | 43.1337
1731.2542 | 426.8517 | 299.9055 | 294.9978 | 330.1659 | 315.1511 | 151.5103 | 43.1471
1732.2542 | 427.9515 | 300.093 | 295.0607 | 329.6952 | 314.3969 | 151.6136 | 43.1678
1733.2542 | 428.5739 | 300.2591 | 295.0013 | 329.9325 | 314.6489 | 151.7394 | 43.1813
1734.2542 | 428.4451 | 300.4094 | 294.8338 | 330.0568 | 314.4927 | 151.857 | 43.206
1735.2542 | 426.956 | 300.5913 | 294.8719 | 330.065 | 314.7062 | 151.9773 | 43.2189
1736.2542 | 427.598 | 300.7692 | 295.2237 | 331.2679 | 315.47 | 152.0931 | 43.2418
1737.2542 | 429.0023 | 300.9512 | 295.2346 | 332.0949 | 315.3882 | 152.2206 | 43.2718
1738.2542 | 432.2634 | 301.1014 | 295.6128 | 332.6184 | 315.8035 | 152.3394 | 43.2876
1739.2542 | 431.038 | 301.2672 | 296.0512 | 332.5756 | 317.3267 | 152.4811 | 43.3094
1740.2542 | 434.5466 | 301.4084 | 295.7099 | 332.5938 | 316.7941 | 152.5932 | 43.3294
1741.2542 | 434.2549 | 301.5404 | 295.4793 | 333.4982 | 316.202 | 152.7236 | 43.3461
1742.2542 | 434.1131 | 301.6658 | 295.5844 | 335.2592 | 316.4266 | 152.8503 | 43.3671
1743.2542 | 434.3878 | 301.812 | 295.5862 | 335.582 | 317.3139 | 152.9766 | 43.3826
1744.2542 | 434.9981 | 301.9492 | 295.8774 | 335.3398 | 317.2481 | 153.0993 | 43.4113
1745.2542 | 433.5177 | 302.1382 | 296.8181 | 335.6622 | 318.2917 | 153.2221 | 43.4355
1746.2542 | 435.7617 | 302.3013 | 296.8231 | 335.4159 | 317.6646 | 153.3451 | 43.4626
1747.2542 | 434.2119 | 302.4643 | 296.92 | 334.5803 | 317.7374 | 153.4624 | 43.4946
1748.2542 | 434.3815 | 302.6193 | 296.8224 | 335.1419 | 317.185 | 153.5839 | 43.5084
1749.2542 | 432.4464 | 302.8039 | 296.8106 | 334.3743 | 317.7566 | 153.7017 | 43.5153
1750.2542 | 430.7258 | 302.999 | 296.6259 | 333.7213 | 317.8047 | 153.8262 | 43.5538
1751.2542 | 429.031 | 303.1169 | 296.6185 | 333.4257 | 316.7389 | 153.9407 | 43.5793
1752.2542 | 427.396 | 303.2315 | 296.6029 | 332.7056 | 315.5644 | 154.0552 | 43.5923
1753.2542 | 424.8714 | 303.3438 | 297.6141 | 332.6593 | 314.7506 | 154.1774 | 43.6158
1754.2542 | 424.1685 | 303.4807 | 298.4761 | 333.1872 | 314.3825 | 154.2704 | 43.6311
1755.2542 | 421.1019 | 303.638 | 298.9247 | 332.8282 | 314.1871 | 154.3798 | 43.6716
1756.2542 | 419.3575 | 303.7693 | 299.1104 | 332.9188 | 313.5243 | 154.4845 | 43.6859
1757.2542 | 417.7782 | 303.8645 | 298.5239 | 332.6794 | 313.3037 | 154.5985 | 43.712
1758.2542 | 416.9757 | 303.9534 | 298.3856 | 332.6627 | 312.6168 | 154.7151 | 43.7356
1759.2542 | 416.7349 | 304.0452 | 299.3386 | 332.686 | 312.1199 | 154.8222 | 43.7536
1760.2542 | 415.3353 | 304.1384 | 299.5473 | 332.7403 | 312.7027 | 154.9303 | 43.7796
1761.2542 | 414.7618 | 304.2109 | 299.3285 | 334.2022 | 312.8697 | 155.0332 | 43.802
1762.2542 | 413.7324 | 304.2959 | 299.2925 | 333.45 | 312.1955 | 155.152 | 43.8279
1763.2542 | 412.8798 | 304.3664 | 299.0815 | 334.1551 | 311.231 | 155.2623 | 43.8504
1764.2542 | 412.304 | 304.4642 | 298.8567 | 334.1037 | 311.9623 | 155.3769 | 43.875
1765.2542 | 414.0975 | 304.5375 | 298.7582 | 333.8271 | 311.1846 | 155.4836 | 43.8945
1766.2542 | 415.9677 | 304.6128 | 298.9322 | 333.2873 | 310.9972 | 155.5856 | 43.9285
1767.2542 | 416.5102 | 304.6717 | 298.8289 | 333.2372 | 310.7994 | 155.692 | 43.9568
1768.2542 | 415.8438 | 304.7367 | 298.5634 | 334.0215 | 309.9857 | 155.7876 | 43.9794
1769.2542 | 416.075 | 304.8148 | 298.8698 | 334.1618 | 310.3049 | 155.8972 | 44.0057
1770.2542 | 414.9033 | 304.873 | 299.0158 | 333.8744 | 311.3206 | 156.006 | 44.0271
1771.2542 | 414.9026 | 304.9417 | 298.9555 | 333.9344 | 311.7278 | 156.1122 | 44.0429
1772.2542 | 415.9248 | 305.0167 | 299.3174 | 333.9096 | 312.3507 | 156.2176 | 44.0774
1773.2542 | 415.8343 | 305.1134 | 299.7197 | 334.7858 | 312.5004 | 156.3125 | 44.0943
1774.2542 | 416.0615 | 305.1701 | 299.5629 | 334.163 | 312.8448 | 156.424 | 44.1161
1775.2542 | 416.1211 | 305.236 | 299.7309 | 334.2279 | 312.2597 | 156.5288 | 44.1435
1776.2542 | 416.1022 | 305.2923 | 299.6345 | 334.7667 | 312.0401 | 156.6299 | 44.1768
1777.2542 | 417.7972 | 305.357 | 299.4618 | 335.1939 | 311.5868 | 156.7374 | 44.1932
1778.2542 | 418.7265 | 305.4068 | 299.6329 | 334.5116 | 312.6219 | 156.8451 | 44.219
1779.2542 | 419.8185 | 305.4526 | 300.5987 | 335.6416 | 312.0746 | 156.9489 | 44.2373
1780.2542 | 418.9006 | 305.4993 | 300.6959 | 335.5203 | 311.4823 | 157.0575 | 44.2578
1781.2542 | 421.0434 | 305.5106 | 300.3536 | 335.153 | 311.4783 | 157.1645 | 44.2799
1782.2542 | 420.3314 | 305.5487 | 300.6904 | 334.952 | 313.1692 | 157.2611 | 44.2945
1783.2542 | 420.18 | 305.5834 | 300.3796 | 335.6197 | 312.6998 | 157.3645 | 44.3258
1784.2542 | 421.4112 | 305.6578 | 300.2224 | 335.9348 | 313.0108 | 157.4716 | 44.3442
1785.2542 | 420.3535 | 305.7273 | 300.4284 | 336.453 | 313.3753 | 157.5789 | 44.3719
1786.2542 | 420.9536 | 305.8017 | 300.4614 | 335.9723 | 313.8843 | 157.696 | 44.3947
1787.2542 | 420.7734 | 305.8802 | 300.5614 | 336.0478 | 315.3992 | 157.7971 | 44.425
1788.2542 | 420.39 | 305.9492 | 301.3666 | 336.7575 | 316.1384 | 157.9014 | 44.44
1789.2542 | 421.8455 | 306.0382 | 300.9671 | 336.7168 | 316.301 | 158.02 | 44.4672
1790.2542 | 426.6074 | 306.1227 | 301.5689 | 337.4873 | 318.064 | 158.1398 | 44.4886
1791.2542 | 430.436 | 306.1935 | 301.9139 | 337.855 | 317.8267 | 158.2602 | 44.5091
1792.2542 | 428.819 | 306.2721 | 301.7076 | 337.4664 | 317.9448 | 158.3655 | 44.5363
1793.2542 | 428.6913 | 306.3631 | 301.9121 | 337.2479 | 318.3551 | 158.4741 | 44.567
1794.2542 | 427.867 | 306.4429 | 302.7833 | 338.6223 | 319.9581 | 158.5726 | 44.5813
1795.2542 | 427.6153 | 306.5173 | 302.6152 | 338.6618 | 321.2288 | 158.6888 | 44.5969
1796.2542 | 425.1026 | 306.6218 | 302.7474 | 339.0125 | 321.3393 | 158.79 | 44.6194
1797.2542 | 422.8649 | 306.7064 | 304.124 | 338.7643 | 320.5318 | 158.9106 | 44.6529
1798.2542 | 421.8981 | 306.781 | 304.3551 | 339.1108 | 319.9245 | 159.0222 | 44.6733
1799.2542 | 425.5673 | 306.8807 | 304.3597 | 338.1638 | 319.3694 | 159.1417 | 44.6982
1800.2542 | 424.396 | 307.0033 | 304.5456 | 337.4279 | 318.4917 | 159.2619 | 44.7253
1801.2542 | 424.477 | 307.0806 | 304.4192 | 337.2029 | 317.7457 | 159.3648 | 44.7489
1802.2542 | 423.9694 | 307.1547 | 304.2582 | 337.1545 | 317.5723 | 159.4718 | 44.7734
1803.2542 | 424.5486 | 307.259 | 303.8033 | 336.9053 | 317.1511 | 159.5741 | 44.7886
1804.2542 | 425.2961 | 307.3667 | 303.7347 | 337.1258 | 317.0698 | 159.6734 | 44.8206
1805.2542 | 428.43 | 307.429 | 304.1502 | 337.1239 | 316.1302 | 159.7689 | 44.8384
1806.2542 | 431.0127 | 307.5335 | 303.8475 | 337.5938 | 316.021 | 159.8727 | 44.8544
1807.2542 | 432.248 | 307.6315 | 304.6716 | 337.2646 | 315.8052 | 159.9652 | 44.8902
1808.2542 | 431.8845 | 307.7124 | 305.0207 | 336.1576 | 315.7558 | 160.067 | 44.9028
1809.2542 | 431.5714 | 307.8215 | 304.322 | 335.0604 | 316.1461 | 160.1607 | 44.9321
1810.2542 | 433.4422 | 307.9187 | 304.7387 | 334.9145 | 316.2536 | 160.2534 | 44.9461
1811.2542 | 436.8467 | 308.0274 | 304.8725 | 334.547 | 315.8204 | 160.331 | 44.9696
1812.2542 | 437.4257 | 308.1127 | 305.7848 | 334.1559 | 316.106 | 160.419 | 44.9935
1813.2542 | 439.7256 | 308.2188 | 305.5934 | 334.609 | 316.5344 | 160.5107 | 45.0158
1814.2542 | 440.3184 | 308.3503 | 305.5424 | 334.5645 | 317.9919 | 160.5982 | 45.0441
1815.2542 | 439.3613 | 308.4705 | 306.2758 | 334.1652 | 317.1258 | 160.688 | 45.0672
1816.2542 | 439.4492 | 308.5829 | 306.7147 | 334.6897 | 317.5351 | 160.7752 | 45.0853
1817.2542 | 439.3715 | 308.6912 | 306.3161 | 334.403 | 317.6886 | 160.8685 | 45.1007
1818.2542 | 440.361 | 308.8347 | 306.508 | 334.391 | 317.667 | 160.9594 | 45.1301
1819.2542 | 441.6905 | 308.9658 | 306.4502 | 335.7619 | 317.14 | 161.0515 | 45.1629
1820.2542 | 440.0316 | 309.0798 | 306.6255 | 335.2131 | 317.4646 | 161.1457 | 45.1734
1821.2542 | 440.1968 | 309.2235 | 307.2204 | 335.7619 | 317.8685 | 161.2533 | 45.196
1822.2542 | 439.2129 | 309.3425 | 307.49 | 336.6664 | 317.3493 | 161.3485 | 45.2174
1823.2542 | 437.4561 | 309.4581 | 307.5224 | 337.3836 | 317.9565 | 161.4508 | 45.2381
1824.2542 | 435.7122 | 309.6026 | 307.6124 | 337.6916 | 318.3112 | 161.556 | 45.2531
1825.2542 | 433.8718 | 309.7185 | 307.6987 | 337.6657 | 318.2886 | 161.6595 | 45.2903
1826.2542 | 433.9972 | 309.8556 | 307.914 | 337.6357 | 318.3393 | 161.7569 | 45.3138
1827.2542 | 433.0499 | 309.9804 | 307.9642 | 337.2261 | 318.3267 | 161.8608 | 45.3264
1828.2542 | 433.686 | 310.1006 | 308.3767 | 336.9131 | 319.0664 | 161.9506 | 45.3424
1829.2542 | 435.7793 | 310.2647 | 308.262 | 336.414 | 318.6696 | 162.0541 | 45.3763
1830.2542 | 436.2773 | 310.4039 | 308.0055 | 336.697 | 318.3447 | 162.1544 | 45.3857
1831.2542 | 438.4155 | 310.5339 | 307.5936 | 336.5647 | 318.2273 | 162.2414 | 45.4086
1832.2542 | 436.9638 | 310.6712 | 307.9383 | 337.0641 | 318.9152 | 162.3302 | 45.4354
1833.2542 | 437.0018 | 310.8086 | 307.7973 | 338.1317 | 319.355 | 162.4379 | 45.4644
1834.2542 | 437.4732 | 310.9526 | 308.0567 | 337.8942 | 320.2121 | 162.5437 | 45.469
1835.2542 | 438.2152 | 311.1322 | 307.9291 | 338.1839 | 319.8204 | 162.6491 | 45.4929
1836.2542 | 439.2196 | 311.2899 | 307.9675 | 337.4396 | 320.3084 | 162.7498 | 45.5195
1837.2542 | 439.9747 | 311.4913 | 308.2515 | 337.6319 | 320.5106 | 162.8452 | 45.5457
1838.2542 | 439.2529 | 311.6663 | 308.2279 | 337.8231 | 319.8382 | 162.948 | 45.565
1839.2542 | 441.0176 | 311.8503 | 308.3758 | 338.3609 | 319.5255 | 163.0245 | 45.5894
1840.2542 | 440.9177 | 312.023 | 308.4652 | 339.0373 | 319.3688 | 163.0969 | 45.602
1841.2542 | 440.2008 | 312.1855 | 308.4917 | 339.1861 | 318.7256 | 163.1933 | 45.6149
1842.2542 | 439.722 | 312.3459 | 308.3124 | 339.4687 | 318.91 | 163.2946 | 45.6587
1843.2542 | 438.9703 | 312.5214 | 308.5232 | 339.1794 | 320.138 | 163.3896 | 45.6734
1844.2542 | 440.3231 | 312.6949 | 308.3061 | 338.7719 | 320.4065 | 163.4865 | 45.6886
1845.2542 | 440.4835 | 312.8558 | 308.5341 | 338.4378 | 320.4562 | 163.59 | 45.7157
1846.2542 | 440.1065 | 313.0284 | 308.4055 | 338.3217 | 320.9388 | 163.6811 | 45.7437
1847.2542 | 439.9696 | 313.187 | 308.2736 | 338.5193 | 322.0044 | 163.764 | 45.7485
1848.2542 | 439.8206 | 313.3297 | 308.2246 | 338.9878 | 323.0002 | 163.8417 | 45.782
1849.2542 | 439.0825 | 313.4766 | 308.4994 | 339.0625 | 322.8162 | 163.9324 | 45.8061
1850.2542 | 437.2316 | 313.6353 | 309.1924 | 339.6689 | 322.2013 | 164.0357 | 45.8208
1851.2542 | 436.7443 | 313.8179 | 308.5581 | 340.2223 | 322.2154 | 164.1262 | 45.8488
1852.2542 | 436.2804 | 313.9585 | 308.3817 | 339.5971 | 322.5716 | 164.2201 | 45.864
1853.2542 | 435.2139 | 314.1026 | 308.9263 | 339.8592 | 322.2804 | 164.3026 | 45.8936
1854.2542 | 435.6543 | 314.2366 | 309.6496 | 340.527 | 322.2773 | 164.3889 | 45.9171
1855.2542 | 436.5931 | 314.4152 | 310.1818 | 341.562 | 322.9712 | 164.472 | 45.9281
1856.2542 | 436.8757 | 314.5343 | 310.2106 | 341.8755 | 324.0535 | 164.5571 | 45.945
1857.2542 | 435.02 | 314.6985 | 310.2344 | 342.0776 | 323.3582 | 164.6625 | 45.969
1858.2542 | 435.8966 | 314.8276 | 310.2758 | 341.713 | 323.6335 | 164.7659 | 45.9932
1859.2542 | 434.484 | 314.9631 | 310.8115 | 341.8186 | 323.0946 | 164.8649 | 46.0081
1860.2542 | 433.4718 | 315.1124 | 310.9537 | 342.0483 | 323.1659 | 164.9614 | 46.0324
1861.2542 | 433.9725 | 315.2543 | 311.277 | 343.3817 | 323.1221 | 165.0548 | 46.0447
1862.2542 | 437.9394 | 315.4421 | 311.3757 | 343.8058 | 324.0859 | 165.1451 | 46.0722
1863.2542 | 439.5009 | 315.6223 | 311.6543 | 343.2885 | 324.0869 | 165.2431 | 46.0807
1864.2542 | 441.1523 | 315.7825 | 312.1011 | 343.2443 | 324.3561 | 165.3464 | 46.0956
1865.2542 | 441.447 | 315.9317 | 313.2308 | 342.8198 | 323.9574 | 165.4436 | 46.1262
1866.2542 | 440.3222 | 316.1319 | 313.3885 | 342.9829 | 323.9679 | 165.5492 | 46.1545
1867.2542 | 440.659 | 316.2909 | 313.03 | 342.64 | 323.3351 | 165.6559 | 46.1747
1868.2542 | 442.1871 | 316.515 | 313.0464 | 341.6771 | 323.6004 | 165.7529 | 46.1885
1869.2542 | 440.6556 | 316.7334 | 313.4385 | 341.0036 | 323.8538 | 165.8541 | 46.2122
1870.2542 | 440.1045 | 316.9717 | 313.9159 | 341.3408 | 323.3308 | 165.9569 | 46.2269
1871.2542 | 439.3563 | 317.1602 | 313.8235 | 340.7999 | 323.1794 | 166.0452 | 46.258
1872.2542 | 442.9818 | 317.3873 | 313.6428 | 340.5771 | 324.2287 | 166.1362 | 46.2669
1873.2542 | 443.5226 | 317.6059 | 313.2709 | 340.8397 | 324.556 | 166.2409 | 46.2954
1874.2542 | 441.0644 | 317.8288 | 313.3555 | 341.9741 | 324.8918 | 166.3193 | 46.313
1875.2542 | 440.8774 | 318.0416 | 313.091 | 342.1767 | 324.0326 | 166.4234 | 46.3483
1876.2542 | 440.5847 | 318.2394 | 313.3999 | 341.8283 | 324.1104 | 166.5156 | 46.3695
1877.2542 | 437.6337 | 318.4581 | 314.1451 | 343.0938 | 324.395 | 166.6139 | 46.3818
1878.2542 | 436.0167 | 318.648 | 314.327 | 342.778 | 323.5568 | 166.7237 | 46.4009
1879.2542 | 435.1843 | 318.8544 | 313.796 | 342.061 | 323.433 | 166.8236 | 46.4212
1880.2542 | 434.0858 | 319.0739 | 313.9271 | 341.4754 | 323.4036 | 166.9314 | 46.4561
1881.2542 | 432.3771 | 319.277 | 314.1701 | 342.3657 | 323.1494 | 167.0258 | 46.468
1882.2542 | 431.9655 | 319.4888 | 314.2971 | 342.6471 | 322.65 | 167.1263 | 46.4872
1883.2542 | 431.4626 | 319.7015 | 313.8972 | 342.4066 | 322.4082 | 167.2357 | 46.5172
1884.2542 | 431.5074 | 319.9502 | 313.8468 | 342.2774 | 322.5354 | 167.3403 | 46.54
1885.2542 | 430.4588 | 320.1361 | 314.5669 | 342.5371 | 323.0743 | 167.4399 | 46.5585
1886.2542 | 429.4269 | 320.3463 | 314.7751 | 342.447 | 323.1487 | 167.542 | 46.5745
1887.2542 | 427.5409 | 320.5583 | 315.0203 | 342.5282 | 322.7829 | 167.6406 | 46.6126
1888.2542 | 426.5694 | 320.7734 | 315.4003 | 342.9217 | 323.1839 | 167.7365 | 46.6325
1889.2542 | 433.6816 | 321.0225 | 315.7251 | 342.822 | 323.579 | 167.8644 | 46.6503
1890.2542 | 431.8074 | 321.2359 | 316.295 | 342.3192 | 323.6298 | 167.9833 | 46.6659
1891.2542 | 430.1756 | 321.4393 | 316.2222 | 341.7118 | 323.6678 | 168.09 | 46.6956
1892.2542 | 429.2257 | 321.6398 | 315.9931 | 341.4838 | 323.7822 | 168.2044 | 46.7263
1893.2542 | 428.0884 | 321.853 | 316.1447 | 341.4527 | 324.44 | 168.3143 | 46.7396
1894.2542 | 426.1358 | 322.064 | 315.7608 | 341.7826 | 326.0942 | 168.4147 | 46.765
1895.2542 | 425.6203 | 322.2484 | 316.7036 | 342.5775 | 326.3972 | 168.5088 | 46.7901
1896.2542 | 425.6804 | 322.4411 | 316.331 | 341.9331 | 325.7419 | 168.6166 | 46.8117
1897.2542 | 425.9121 | 322.6272 | 315.9436 | 341.3073 | 325.7278 | 168.7134 | 46.838
1898.2542 | 425.4104 | 322.8039 | 315.7213 | 341.2555 | 325.2023 | 168.8104 | 46.868
1899.2542 | 424.9266 | 322.9684 | 315.6863 | 341.6163 | 325.3827 | 168.9055 | 46.8787
1900.2542 | 424.1761 | 323.1533 | 315.7505 | 342.0492 | 326.0727 | 168.9944 | 46.8931
1901.2542 | 423.7852 | 323.3191 | 315.4065 | 341.7201 | 325.3004 | 169.0873 | 46.9339
1902.2542 | 421.9494 | 323.4499 | 315.541 | 341.2698 | 325.179 | 169.1797 | 46.9498
1903.2542 | 421.6021 | 323.596 | 315.5291 | 341.1208 | 325.5484 | 169.2781 | 46.9619
1904.2542 | 421.4408 | 323.7476 | 315.8778 | 340.5885 | 325.6855 | 169.3812 | 46.9864
1905.2542 | 421.9931 | 323.8854 | 315.8815 | 340.2181 | 324.7939 | 169.4858 | 47.0085
1906.2542 | 423.9502 | 324.0384 | 315.8696 | 340.4382 | 324.3306 | 169.5688 | 47.0328
1907.2542 | 425.7323 | 324.1859 | 315.0681 | 339.9314 | 323.7049 | 169.6724 | 47.0565
1908.2542 | 429.146 | 324.3285 | 315.5103 | 340.7994 | 323.2603 | 169.7491 | 47.075
1909.2542 | 429.6998 | 324.4962 | 315.0175 | 340.9955 | 323.4781 | 169.8435 | 47.0901
1910.2542 | 431.4393 | 324.6669 | 315.0073 | 340.6088 | 323.2816 | 169.9497 | 47.1192
1911.2542 | 435.538 | 324.8322 | 315.3113 | 339.8868 | 323.6085 | 170.0397 | 47.1527
1912.2542 | 435.7466 | 325.0472 | 315.1904 | 340.1534 | 324.4443 | 170.1426 | 47.1674
1913.2542 | 436.5107 | 325.2676 | 315.4209 | 341.0369 | 324.8572 | 170.2341 | 47.1935
1914.2542 | 436.8032 | 325.479 | 315.5686 | 342.0025 | 325.1058 | 170.3386 | 47.2183
1915.2542 | 437.1207 | 325.6671 | 315.6481 | 342.6502 | 325.13 | 170.4375 | 47.244
1916.2542 | 438.0501 | 325.9185 | 315.9906 | 343.3985 | 325.4483 | 170.5354 | 47.2601
1917.2542 | 437.4705 | 326.1555 | 316.4175 | 344.5822 | 324.6325 | 170.6175 | 47.2899
1918.2542 | 438.5487 | 326.4562 | 316.77 | 344.7826 | 323.9091 | 170.7285 | 47.3072
1919.2542 | 438.8464 | 326.7499 | 317.1949 | 344.7432 | 323.8926 | 170.828 | 47.3401
1920.2542 | 439.672 | 327.0481 | 317.5054 | 344.6798 | 323.6388 | 170.9386 | 47.3602
1921.2542 | 439.5633 | 327.367 | 317.6779 | 344.7783 | 323.5295 | 171.0413 | 47.3723
1922.2542 | 439.6151 | 327.7243 | 317.7385 | 344.1072 | 323.922 | 171.1386 | 47.403
1923.2542 | 440.3623 | 328.0693 | 318.0387 | 344.571 | 323.6945 | 171.2392 | 47.4259
1924.2542 | 442.6013 | 328.4246 | 317.9601 | 344.7897 | 323.351 | 171.3343 | 47.4393
1925.2542 | 443.7621 | 328.8023 | 318.5453 | 344.8383 | 322.7886 | 171.438 | 47.4681
1926.2542 | 445.5763 | 329.1579 | 318.6961 | 345.3049 | 322.6572 | 171.5396 | 47.4807
1927.2542 | 445.6931 | 329.5143 | 318.8437 | 345.3109 | 322.5989 | 171.6385 | 47.512
1928.2542 | 444.9692 | 329.895 | 319.1142 | 345.3536 | 322.3914 | 171.7411 | 47.5281
1929.2542 | 445.5722 | 330.274 | 319.0094 | 345.058 | 324.0599 | 171.8413 | 47.5443
1930.2542 | 447.3343 | 330.6582 | 319.1471 | 345.1325 | 323.8164 | 171.9378 | 47.562
1931.2542 | 448.065 | 331.0303 | 318.9427 | 345.2886 | 324.317 | 172.0345 | 47.5876
1932.2542 | 447.3638 | 331.4259 | 318.7353 | 346.0786 | 324.3612 | 172.1256 | 47.614
1933.2542 | 449.1694 | 331.8186 | 318.4589 | 346.5436 | 324.0961 | 172.2204 | 47.6267
1934.2542 | 449.591 | 332.21 | 318.4813 | 347.1302 | 324.103 | 172.3114 | 47.6528
1935.2542 | 451.5817 | 332.5929 | 318.4399 | 347.2095 | 323.8728 | 172.4163 | 47.6698
1936.2542 | 451.1959 | 332.9847 | 318.6183 | 347.1285 | 324.0491 | 172.5055 | 47.6904
1937.2542 | 451.6017 | 333.3551 | 318.4662 | 347.9655 | 325.082 | 172.601 | 47.714
1938.2542 | 452.2852 | 333.7633 | 318.7121 | 348.0344 | 324.4465 | 172.7013 | 47.7281
1939.2542 | 452.55 | 334.163 | 319.1529 | 347.6358 | 325.1376 | 172.8001 | 47.7573
1940.2542 | 452.3638 | 334.5715 | 319.4477 | 347.1429 | 325.5164 | 172.8881 | 47.7706
1941.2542 | 453.7256 | 334.9792 | 319.4922 | 347.7654 | 325.9741 | 172.9824 | 47.7897
1942.2542 | 455.6259 | 335.3753 | 319.4099 | 348.2963 | 325.8282 | 173.0665 | 47.7996
1943.2542 | 454.2396 | 335.7948 | 319.9015 | 348.4535 | 326.8011 | 173.175 | 47.8247
1944.2542 | 454.1625 | 336.1604 | 320.7585 | 349.9504 | 326.7598 | 173.2676 | 47.8417
1945.2542 | 451.4076 | 336.5544 | 320.5789 | 349.3103 | 327.0333 | 173.3684 | 47.8642
1946.2542 | 450.5433 | 336.9295 | 320.6819 | 349.2411 | 327.7326 | 173.465 | 47.8818
1947.2542 | 450.6212 | 337.3331 | 320.4752 | 349.8484 | 328.419 | 173.5551 | 47.8933
1948.2542 | 450.8048 | 337.7124 | 320.8336 | 349.9904 | 328.0921 | 173.6628 | 47.9125
1949.2542 | 449.9999 | 338.0745 | 320.9671 | 349.6696 | 327.8565 | 173.7633 | 47.9328
1950.2542 | 450.3275 | 338.454 | 320.7805 | 349.6597 | 327.4068 | 173.8571 | 47.9575
1951.2542 | 451.4123 | 338.8113 | 320.6633 | 350.1962 | 327.4038 | 173.9532 | 47.9743
1952.2542 | 451.9122 | 339.1897 | 321.0352 | 349.9135 | 327.4829 | 174.0495 | 47.995
1953.2542 | 453.2574 | 339.5749 | 321.0643 | 350.5243 | 327.8583 | 174.1468 | 48.0094
1954.2542 | 454.8068 | 339.9492 | 321.0618 | 350.0385 | 328.689 | 174.2365 | 48.0351
1955.2542 | 452.2435 | 340.3141 | 321.0344 | 349.4743 | 329.3296 | 174.3344 | 48.0539
1956.2542 | 451.4549 | 340.6463 | 320.8887 | 349.872 | 329.8891 | 174.4328 | 48.072
1957.2542 | 451.2882 | 341.0121 | 320.7052 | 349.9345 | 329.2989 | 174.5348 | 48.0909
1958.2542 | 449.9316 | 341.3738 | 320.8243 | 349.4292 | 328.7101 | 174.6333 | 48.1157
1959.2542 | 448.4651 | 341.7279 | 320.5788 | 349.4721 | 329.0292 | 174.7111 | 48.1322
1960.2542 | 448.1719 | 342.0851 | 320.709 | 349.941 | 328.8219 | 174.7612 | 48.1549
1961.2542 | 446.3782 | 342.4441 | 321.5301 | 349.9974 | 328.2432 | 174.882 | 48.1722
1962.2542 | 444.9432 | 342.7922 | 321.7054 | 349.6483 | 328.3363 | 174.9899 | 48.1885
1963.2542 | 445.7771 | 343.1375 | 321.9877 | 350.1871 | 327.8179 | 175.0962 | 48.2105
1964.2542 | 443.9514 | 343.483 | 322.4124 | 350.3242 | 327.076 | 175.2131 | 48.2293
1965.2542 | 444.0703 | 343.8628 | 322.6637 | 350.5129 | 326.4644 | 175.3085 | 48.2504
1966.2542 | 443.1236 | 344.1854 | 322.8356 | 350.3999 | 325.9129 | 175.4202 | 48.276
1967.2542 | 441.8909 | 344.5377 | 323.198 | 350.1177 | 326.2116 | 175.5252 | 48.2902
1968.2542 | 441.399 | 344.8797 | 322.6986 | 349.5893 | 325.9005 | 175.6165 | 48.3061
1969.2542 | 441.6843 | 345.2438 | 322.1704 | 348.7889 | 327.3253 | 175.725 | 48.3321
1970.2542 | 440.2618 | 345.5615 | 322.6098 | 349.8428 | 327.4471 | 175.8251 | 48.3447
1971.2542 | 437.708 | 345.8949 | 323.1206 | 350.3136 | 327.7818 | 175.9298 | 48.3771
1972.2542 | 436.8916 | 346.2409 | 322.8426 | 350.3502 | 327.7777 | 176.0349 | 48.3831
1973.2542 | 436.0444 | 346.5532 | 323.2599 | 351.7809 | 327.2596 | 176.1403 | 48.4012
1974.2542 | 437.202 | 346.8948 | 323.645 | 351.8902 | 326.6371 | 176.2444 | 48.4237
1975.2542 | 435.7959 | 347.2262 | 324.0713 | 352.8557 | 328.4891 | 176.3398 | 48.442
1976.2542 | 434.5563 | 347.5352 | 324.0253 | 352.8778 | 327.9664 | 176.4389 | 48.4646
1977.2542 | 436.1592 | 347.8526 | 323.8404 | 352.8672 | 327.4151 | 176.5338 | 48.4755
1978.2542 | 436.3689 | 348.1759 | 324.321 | 352.8723 | 327.0478 | 176.6417 | 48.501
1979.2542 | 436.4023 | 348.4764 | 323.8665 | 354.0103 | 327.0055 | 176.7418 | 48.5157
1980.2542 | 435.997 | 348.7821 | 323.9205 | 353.5715 | 327.1534 | 176.8408 | 48.5355
1981.2542 | 435.6718 | 349.1093 | 324.1401 | 353.7021 | 327.5886 | 176.9324 | 48.5542
1982.2542 | 434.0814 | 349.4028 | 324.2629 | 354.4044 | 327.0058 | 177.0364 | 48.5674
1983.2542 | 433.047 | 349.6848 | 324.5955 | 354.1547 | 328.0609 | 177.1388 | 48.5932
1984.2542 | 433.207 | 349.9874 | 324.9257 | 355.6747 | 328.4031 | 177.2254 | 48.6175
1985.2542 | 432.66 | 350.2822 | 326.0217 | 355.4649 | 328.7767 | 177.3314 | 48.6371
1986.2542 | 432.0796 | 350.5723 | 326.5346 | 355.2498 | 328.4688 | 177.431 | 48.6582
1987.2542 | 430.4967 | 350.8197 | 326.0699 | 354.6523 | 328.9993 | 177.5179 | 48.6783
1988.2542 | 429.6417 | 351.1127 | 326.2451 | 354.974 | 329.4759 | 177.6176 | 48.6979
1989.2698 | 432.0323 | 351.3886 | 327.1163 | 354.3892 | 328.8322 | 177.7136 | 48.72
1990.2542 | 431.142 | 351.654 | 327.3084 | 354.3441 | 328.7599 | 177.8172 | 48.7349
1991.2542 | 427.7071 | 351.9206 | 327.183 | 354.0948 | 328.3121 | 177.9148 | 48.7625
1992.2542 | 427.9684 | 352.1756 | 327.2457 | 353.7509 | 328.3723 | 178.0184 | 48.7832
1993.2542 | 428.586 | 352.4163 | 327.5699 | 354.831 | 329.0807 | 178.1186 | 48.8116
1994.2542 | 430.9759 | 352.6928 | 327.5962 | 354.5456 | 329.1644 | 178.2139 | 48.8322
1995.2542 | 433.4087 | 352.9188 | 327.5454 | 354.4649 | 330.5571 | 178.309 | 48.8511
1996.2542 | 432.8295 | 353.1562 | 327.8917 | 355.1012 | 330.504 | 178.4091 | 48.8641
1997.2542 | 431.7465 | 353.3815 | 327.9244 | 355.1255 | 330.3825 | 178.5128 | 48.8903
1998.2542 | 431.8072 | 353.615 | 327.8172 | 354.9203 | 331.112 | 178.618 | 48.9011
1999.2542 | 432.9571 | 353.8534 | 328.0772 | 355.3302 | 330.9768 | 178.726 | 48.9365
2000.2542 | 433.3799 | 354.0727 | 328.8074 | 356.6156 | 331.0653 | 178.8244 | 48.9623
2001.2542 | 432.8229 | 354.265 | 328.8208 | 357.3004 | 330.4964 | 178.9371 | 48.9798
2002.2542 | 432.4371 | 354.5108 | 329.0689 | 357.5882 | 331.4388 | 179.0423 | 48.9971
2003.2542 | 432.1667 | 354.7407 | 329.0388 | 357.7041 | 332.2018 | 179.1464 | 49.0196
2004.2542 | 432.9663 | 354.9508 | 328.9857 | 357.1464 | 331.7358 | 179.2522 | 49.0397
2005.2542 | 434.2355 | 355.1885 | 328.7208 | 356.561 | 331.5452 | 179.3585 | 49.0628
2006.2542 | 435.3169 | 355.3838 | 328.8631 | 357.0821 | 331.6916 | 179.4531 | 49.0821
2007.2542 | 436.4356 | 355.5974 | 328.8939 | 357.3256 | 331.0245 | 179.5551 | 49.0896
2008.2542 | 437.6251 | 355.8111 | 328.9021 | 358.1563 | 331.0232 | 179.6747 | 49.1195
2009.2542 | 437.0322 | 355.9609 | 330.2054 | 359.4728 | 330.7357 | 179.7868 | 49.1336
2010.2542 | 436.3986 | 356.158 | 330.8711 | 359.2962 | 330.9488 | 179.8971 | 49.1559
2011.2542 | 436.4007 | 356.3335 | 331.481 | 359.3768 | 331.0831 | 180.0121 | 49.1703
2012.2542 | 437.3533 | 356.4931 | 331.685 | 359.4336 | 330.7244 | 180.1195 | 49.1823
2013.2542 | 437.1017 | 356.6443 | 332.8887 | 360.3014 | 330.3274 | 180.2305 | 49.2067
2014.2542 | 437.2702 | 356.7803 | 333.4021 | 359.5839 | 330.2664 | 180.3467 | 49.2363
2015.2542 | 439.1862 | 356.9523 | 333.5588 | 360.4071 | 330.6234 | 180.4433 | 49.2426
2016.2542 | 438.7485 | 357.1092 | 333.8402 | 360.7696 | 331.0368 | 180.5483 | 49.262
2017.2542 | 439.1051 | 357.2655 | 333.5748 | 361.234 | 331.2962 | 180.6678 | 49.2745
2018.2542 | 440.0937 | 357.3951 | 333.7689 | 360.7066 | 331.3731 | 180.7725 | 49.295
2019.2542 | 440.9868 | 357.5233 | 334.0713 | 360.4742 | 330.9831 | 180.885 | 49.3234
2020.2542 | 440.4986 | 357.6491 | 334.5184 | 360.6139 | 330.5811 | 180.9849 | 49.3386
2021.2542 | 439.5024 | 357.7742 | 333.676 | 360.1841 | 330.3518 | 181.0936 | 49.349
2022.2542 | 439.1102 | 357.8949 | 333.6511 | 360.4363 | 330.1927 | 181.2141 | 49.3732
2023.2542 | 439.1076 | 358.0206 | 334.5498 | 360.1651 | 330.4501 | 181.3268 | 49.3782
2024.2542 | 438.3023 | 358.138 | 334.4434 | 360.1851 | 329.7409 | 181.4218 | 49.4016
2025.2542 | 438.2764 | 358.255 | 334.4312 | 360.2502 | 329.2555 | 181.529 | 49.4163
2026.2542 | 438.3083 | 358.3771 | 334.661 | 361.8298 | 329.4016 | 181.6442 | 49.4419
2027.2542 | 437.124 | 358.5088 | 335.5624 | 362.6113 | 329.1512 | 181.7667 | 49.4554
2028.2542 | 436.8779 | 358.6486 | 335.537 | 362.49 | 329.2489 | 181.8697 | 49.4706
2029.2542 | 436.4938 | 358.7528 | 336.3241 | 362.5922 | 329.4234 | 181.9719 | 49.495
2030.2542 | 436.1591 | 358.8828 | 336.8828 | 362.6687 | 330.3022 | 182.0836 | 49.5087
2031.2542 | 442.7004 | 358.9946 | 336.8374 | 363.3399 | 330.7081 | 182.1826 | 49.5237
2032.2542 | 441.3097 | 359.0991 | 337.2121 | 363.8489 | 330.4551 | 182.2954 | 49.5502
2033.2542 | 439.9726 | 359.1841 | 337.9024 | 363.9665 | 330.395 | 182.4046 | 49.5617
2034.2542 | 437.9795 | 359.2775 | 337.8492 | 364.0315 | 330.2052 | 182.5119 | 49.5881
2035.2542 | 436.2524 | 359.424 | 338.1915 | 365.0445 | 329.8831 | 182.6227 | 49.611
2036.2542 | 436.0815 | 359.6099 | 338.2149 | 364.4656 | 329.5338 | 182.7231 | 49.6257
2037.2542 | 434.9315 | 359.8036 | 337.9716 | 364.5153 | 329.5335 | 182.8292 | 49.646
2038.2542 | 433.4818 | 360.0353 | 337.2459 | 364.6202 | 329.3871 | 182.9473 | 49.6654
2039.2542 | 433.6625 | 360.2521 | 337.0935 | 365.1111 | 329.3389 | 183.051 | 49.6844
2040.2542 | 434.2882 | 360.5155 | 337.5595 | 364.583 | 329.8115 | 183.1597 | 49.6949
2041.2542 | 433.3825 | 360.7751 | 338.5381 | 365.0082 | 329.6175 | 183.2706 | 49.7221
2042.2542 | 432.6836 | 361.0181 | 338.114 | 364.4906 | 329.6338 | 183.3594 | 49.7395
2043.2542 | 431.6578 | 361.2742 | 338.0019 | 365.1374 | 329.5652 | 183.4688 | 49.7609
2044.2542 | 432.4259 | 361.5223 | 337.9705 | 364.461 | 329.9854 | 183.5726 | 49.7813
2045.2542 | 432.0207 | 361.7677 | 337.9912 | 364.3862 | 330.0461 | 183.6647 | 49.7965
2046.2542 | 434.5075 | 362.0289 | 337.811 | 365.7105 | 330.2386 | 183.7795 | 49.8139
2047.2542 | 434.5318 | 362.2873 | 339.1333 | 365.7366 | 330.6692 | 183.9028 | 49.8307
2048.2542 | 434.6754 | 362.5569 | 339.147 | 365.174 | 330.8101 | 184.0064 | 49.8592
2049.2542 | 434.8518 | 362.7989 | 338.712 | 365.9827 | 330.8331 | 184.1196 | 49.8684
2050.2542 | 435.8404 | 363.0593 | 338.7349 | 366.8005 | 331.0883 | 184.2501 | 49.8944
2051.2542 | 435.5165 | 363.3256 | 338.7808 | 366.1873 | 330.9257 | 184.3689 | 49.9176
2052.2542 | 436.3234 | 363.6097 | 338.9017 | 366.0867 | 331.0901 | 184.4908 | 49.94
2053.2542 | 436.2485 | 363.901 | 339.1738 | 366.5832 | 331.3061 | 184.5935 | 49.9578
2054.2542 | 436.7276 | 364.1846 | 339.2764 | 367.0331 | 331.7092 | 184.6867 | 49.971
2055.2542 | 437.6604 | 364.4748 | 340.0694 | 367.0812 | 332.1135 | 184.8178 | 49.9923
2056.2542 | 438.2453 | 364.7677 | 340.4085 | 367.987 | 332.5794 | 184.9485 | 50.0226
2057.2542 | 437.375 | 365.0866 | 341.0944 | 368.4754 | 332.5296 | 185.068 | 50.0424
2058.2542 | 437.6953 | 365.4247 | 341.9017 | 368.4684 | 332.7337 | 185.1568 | 50.0758
2059.2542 | 438.4197 | 365.7537 | 342.2015 | 368.8292 | 332.7675 | 185.2804 | 50.0825
2060.2542 | 436.8708 | 366.0822 | 343.0835 | 368.7143 | 332.628 | 185.4014 | 50.1042
2061.2542 | 437.1406 | 366.423 | 343.2137 | 368.6687 | 332.5138 | 185.495 | 50.1253
2062.2542 | 435.3392 | 366.755 | 343.1759 | 369.0702 | 332.6505 | 185.6091 | 50.1372
2063.2542 | 434.3562 | 367.1268 | 343.4857 | 370.6485 | 332.5469 | 185.7224 | 50.166
2064.2542 | 434.0472 | 367.4721 | 343.5539 | 369.3767 | 332.4205 | 185.7781 | 50.1901
2065.2542 | 433.5969 | 367.8417 | 343.3652 | 368.7506 | 332.424 | 185.8772 | 50.2002
2066.2542 | 433.45 | 368.2411 | 342.9264 | 368.8648 | 332.311 | 185.9956 | 50.2233
2067.2542 | 434.6435 | 368.6389 | 342.6341 | 369.1671 | 332.2068 | 186.1255 | 50.2477
2068.2542 | 435.0512 | 369.0242 | 342.1802 | 369.4356 | 332.1143 | 186.2417 | 50.2648
2069.2542 | 435.581 | 369.4591 | 342.4882 | 369.1598 | 332.1118 | 186.3856 | 50.2844
2070.2542 | 435.6211 | 369.8542 | 342.0036 | 368.286 | 332.5305 | 186.4744 | 50.3004
2071.2542 | 434.6407 | 370.2981 | 342.4215 | 368.9851 | 332.334 | 186.604 | 50.3268
2072.2542 | 433.8872 | 370.7449 | 342.5608 | 369.008 | 332.5148 | 186.7168 | 50.3411
2073.2542 | 434.7438 | 371.1708 | 343.2197 | 368.3287 | 332.6211 | 186.8256 | 50.3633
2074.2542 | 434.1194 | 371.6296 | 343.057 | 368.9445 | 332.4781 | 186.6966 | 50.3892
2075.2542 | 434.9008 | 372.0722 | 343.8626 | 369.9379 | 332.337 | 182.9338 | 50.4184
2076.2542 | 435.5206 | 372.4771 | 343.5138 | 369.5081 | 332.5764 | 182.1931 | 50.4373
2077.2542 | 434.5339 | 372.9492 | 343.7285 | 369.1186 | 333.1315 | 181.8554 | 50.4484
2078.2542 | 435.1463 | 373.425 | 343.5773 | 369.3079 | 333.1766 | 181.7233 | 50.4788
2079.2542 | 435.2506 | 373.9013 | 343.0426 | 369.8904 | 333.4459 | 181.6608 | 50.4895
2080.2542 | 435.5141 | 374.4304 | 343.4639 | 370.2208 | 333.9656 | 181.6838 | 50.5215
2081.2542 | 435.9482 | 374.9958 | 343.7359 | 370.3722 | 334.0346 | 181.7144 | 50.532
2082.2542 | 435.3236 | 375.5923 | 344.344 | 370.1378 | 334.3312 | 181.8013 | 50.5667
2083.2542 | 435.7187 | 376.1762 | 343.5975 | 369.3436 | 334.6878 | 181.9308 | 50.5777
2084.2542 | 436.5511 | 376.7961 | 343.6764 | 369.6445 | 334.5995 | 182.0327 | 50.6001
2085.2542 | 437.1439 | 377.4071 | 343.7219 | 369.2249 | 335.1012 | 182.1753 | 50.6146
2086.2542 | 436.6676 | 378.0434 | 344.3233 | 369.5088 | 335.3415 | 182.3184 | 50.6351
2087.2542 | 436.4045 | 378.724 | 344.4767 | 369.4178 | 335.3822 | 182.4692 | 50.6564
2088.2542 | 435.9302 | 379.3583 | 344.825 | 369.8542 | 335.6658 | 182.5719 | 50.6695
2089.2542 | 436.6223 | 380.0636 | 344.6732 | 370.5159 | 335.7518 | 182.6638 | 50.7092
2090.2542 | 435.8121 | 380.7121 | 345.0049 | 370.6966 | 335.866 | 182.7705 | 50.7329
2091.2542 | 436.773 | 381.4214 | 345.8094 | 371.0711 | 336.1244 | 182.9013 | 50.7396
2092.2542 | 438.0592 | 382.0683 | 346.0352 | 370.2036 | 336.2553 | 183.0329 | 50.7557
2093.2542 | 438.8512 | 382.7393 | 346.258 | 370.4333 | 336.2254 | 183.1534 | 50.7811
2094.2542 | 438.5786 | 383.4007 | 346.0704 | 370.3563 | 336.7395 | 183.275 | 50.7979
2095.2542 | 437.9573 | 384.0731 | 345.9055 | 370.7381 | 337.044 | 183.3855 | 50.8241
2096.2542 | 439.0617 | 384.6531 | 346.419 | 370.4721 | 337.3238 | 183.5065 | 50.8303
2097.2542 | 440.2368 | 385.2423 | 347.1571 | 369.5743 | 337.2556 | 183.6529 | 50.8656
2098.2542 | 442.6247 | 385.7811 | 347.1242 | 369.3689 | 337.5492 | 183.7717 | 50.8865
2099.2542 | 444.1466 | 386.3354 | 347.7561 | 369.2132 | 338.1405 | 183.7877 | 50.9004
2100.2542 | 445.6722 | 386.8725 | 348.3712 | 370.0692 | 338.4138 | 183.8594 | 50.9082
2101.2542 | 445.5542 | 387.3786 | 349.3973 | 371.6431 | 338.7945 | 183.9633 | 50.9386
2102.2542 | 447.721 | 387.8724 | 349.588 | 372.339 | 339.1455 | 184.1001 | 50.9599
2103.2542 | 447.7059 | 388.3466 | 350.535 | 373.4735 | 339.445 | 184.197 | 50.9655
2104.2542 | 447.6344 | 388.8362 | 350.6565 | 373.3452 | 339.8373 | 184.3374 | 50.985
2105.2542 | 447.8945 | 389.2804 | 350.9065 | 373.4017 | 340.1204 | 184.4391 | 51.0096
2106.2542 | 447.599 | 389.7156 | 351.0825 | 373.9769 | 340.5139 | 184.5518 | 51.0318
2107.2542 | 449.067 | 390.1729 | 350.6869 | 374.9519 | 341.1236 | 184.6439 | 51.0415
2108.2542 | 448.8737 | 390.6362 | 351.0156 | 375.3014 | 341.3782 | 184.7467 | 51.0607
2109.2542 | 449.5395 | 391.0689 | 351.7035 | 376.4258 | 341.6269 | 184.8807 | 51.0714
2110.2542 | 450.2896 | 391.5155 | 351.7698 | 376.528 | 341.872 | 185.0204 | 51.1031
2111.2542 | 450.441 | 391.8899 | 352.2707 | 377.3662 | 342.0409 | 185.1452 | 51.1097
2112.2542 | 451.6394 | 392.2477 | 352.3772 | 378.408 | 342.1075 | 185.2321 | 51.1422
2113.2542 | 452.4226 | 392.5663 | 352.2399 | 378.9098 | 342.5719 | 185.3657 | 51.1635
2114.2542 | 452.2519 | 392.901 | 352.6176 | 380.1022 | 343.2557 | 185.4364 | 51.1754
2115.2542 | 451.5045 | 393.1383 | 353.0018 | 381.0402 | 343.7382 | 185.5764 | 51.1984
2116.2542 | 451.3278 | 393.3706 | 353.3024 | 381.3389 | 344.2205 | 185.7007 | 51.2085
2117.2542 | 452.5161 | 393.5083 | 353.8328 | 381.4616 | 344.8671 | 185.833 | 51.2371
2118.2542 | 453.6314 | 393.6314 | 354.1731 | 382.7587 | 345.3058 | 185.9144 | 51.2632
2119.2542 | 454.2806 | 393.7233 | 355.3488 | 382.7472 | 345.4432 | 186.0748 | 51.2845
2120.2542 | 454.4357 | 393.7796 | 355.7113 | 383.3713 | 345.5356 | 186.2144 | 51.2977
2121.2542 | 453.5626 | 393.7949 | 356.15 | 383.1476 | 345.5979 | 186.2677 | 51.3289
2122.2542 | 455.8693 | 393.659 | 356.1542 | 382.8805 | 345.8202 | 186.382 | 51.3484
2123.2542 | 458.5796 | 393.258 | 355.9306 | 383.3555 | 345.9639 | 186.3378 | 51.3619
2124.2542 | 459.5895 | 392.6763 | 356.0183 | 384.1759 | 346.226 | 186.4672 | 51.3837
2125.2542 | 461.3084 | 392.3263 | 355.9332 | 384.001 | 346.3151 | 186.6051 | 51.4055
2126.2542 | 461.6283 | 391.5295 | 356.1187 | 385.3192 | 346.7763 | 186.6946 | 51.4298
2127.2542 | 459.9434 | 391.2098 | 356.1514 | 384.732 | 346.8559 | 186.8597 | 51.4451
2128.2542 | 458.9094 | 390.8717 | 356.2149 | 384.6219 | 347.2494 | 187.0036 | 51.4637
2129.2542 | 459.9885 | 390.7146 | 356.362 | 384.5444 | 347.4352 | 187.128 | 51.4878
2130.2542 | 460.1559 | 390.82 | 357.0096 | 385.8616 | 347.5711 | 187.171 | 51.5165
2131.2542 | 460.0723 | 391.1675 | 357.3204 | 385.5646 | 347.7827 | 187.3295 | 51.5387
2132.2542 | 457.7649 | 391.6838 | 357.4304 | 386.6381 | 348.0824 | 187.4649 | 51.5693
2133.2542 | 457.4295 | 392.4101 | 357.9354 | 387.0774 | 348.4838 | 187.6499 | 51.5897
2134.2542 | 455.3086 | 393.1913 | 358.1127 | 386.9979 | 348.7189 | 187.7975 | 51.6053
2135.2542 | 454.3783 | 393.875 | 358.447 | 387.0172 | 349.1935 | 187.9684 | 51.626
2136.2542 | 451.0585 | 394.4795 | 358.8912 | 387.0934 | 349.3363 | 188.1401 | 51.6594
2137.2542 | 449.138 | 395.287 | 359.116 | 386.3409 | 349.4291 | 188.2853 | 51.6842
2138.2542 | 448.6289 | 396.204 | 359.4225 | 387.3563 | 349.7807 | 188.4616 | 51.6984
2139.2542 | 449.4951 | 397.1804 | 359.3193 | 386.3877 | 350.3026 | 188.6166 | 51.7278
2140.2542 | 451.4629 | 398.1382 | 359.8327 | 386.913 | 350.7794 | 188.7748 | 51.7555
2141.2542 | 452.7287 | 399.0559 | 360.1182 | 387.1328 | 350.9345 | 188.8888 | 51.7755
2142.2542 | 454.7151 | 399.9405 | 360.7564 | 388.0966 | 351.0612 | 189.0367 | 51.8057
2143.2542 | 455.4763 | 400.8407 | 361.3273 | 388.4056 | 351.7465 | 189.1658 | 51.8346
2144.2542 | 456.8726 | 401.8199 | 361.8205 | 388.9646 | 351.945 | 189.3196 | 51.8583
2145.2542 | 457.2948 | 402.8215 | 362.1468 | 389.5779 | 352.4821 | 189.4557 | 51.8842
2146.2542 | 456.5968 | 403.81 | 362.7928 | 389.166 | 352.7237 | 189.6079 | 51.914
2147.2542 | 457.8302 | 404.7979 | 362.8235 | 389.1892 | 353.0845 | 189.7467 | 51.9299
2148.2542 | 457.902 | 405.8037 | 363.2715 | 389.8429 | 353.7091 | 189.8692 | 51.9558
2149.2542 | 458.5073 | 406.8672 | 362.9259 | 390.2498 | 354.39 | 189.9764 | 51.9689
2150.2542 | 459.6396 | 407.9444 | 363.117 | 391.3006 | 354.6702 | 190.0484 | 52.0046
2151.2542 | 460.9244 | 409.0246 | 363.0357 | 391.0991 | 354.9939 | 190.1876 | 52.0245
2152.2542 | 461.3279 | 410.1424 | 363.4833 | 391.5123 | 355.191 | 190.3592 | 52.0463
2153.2542 | 460.851 | 411.1957 | 364.0293 | 392.0541 | 355.5304 | 190.5125 | 52.0721
2154.2542 | 460.5045 | 412.4707 | 364.5647 | 392.9991 | 355.8682 | 190.6755 | 52.1014
2155.2542 | 462.243 | 413.8354 | 364.6642 | 392.2014 | 356.2163 | 190.8245 | 52.1272
2156.2542 | 460.7233 | 415.218 | 364.8185 | 393.6582 | 356.5754 | 191.0022 | 52.1448
2157.2542 | 461.7129 | 416.5759 | 364.5645 | 394.1751 | 357.4081 | 191.1574 | 52.1666
2158.2542 | 463.051 | 418.0417 | 364.877 | 394.4059 | 357.9166 | 191.3018 | 52.1925
2159.2542 | 464.065 | 419.3686 | 365.5441 | 396.6092 | 358.8118 | 191.4516 | 52.2267
2160.2542 | 464.9882 | 420.5657 | 366.1283 | 396.5379 | 359.0993 | 191.5853 | 52.2443
2161.2542 | 465.8521 | 421.6633 | 366.0948 | 396.6752 | 359.4892 | 191.725 | 52.2652
2162.2542 | 466.9634 | 422.7008 | 366.4684 | 396.8804 | 360.1321 | 191.8759 | 52.2778
2163.2542 | 468.601 | 423.738 | 367.0016 | 396.3876 | 360.2947 | 192.052 | 52.312
2164.2542 | 469.4031 | 424.7245 | 367.4597 | 397.4705 | 360.9529 | 192.2043 | 52.3421
2165.2542 | 469.0306 | 425.6332 | 367.81 | 397.6081 | 361.8163 | 192.3201 | 52.3599
2166.2542 | 469.6903 | 426.5393 | 367.7592 | 397.5064 | 362.0309 | 192.4773 | 52.3776
2167.2542 | 469.8997 | 427.4449 | 368.1501 | 399.3004 | 363.0852 | 192.6868 | 52.4072
2168.2542 | 471.009 | 428.3208 | 368.7682 | 398.9818 | 363.3199 | 192.8174 | 52.4402
2169.2542 | 471.14 | 429.1412 | 368.7615 | 398.4506 | 363.565 | 192.8691 | 52.4623
2170.2542 | 470.9411 | 429.9225 | 369.3712 | 398.1634 | 363.7607 | 193.0293 | 52.4973
2171.2542 | 472.6179 | 430.743 | 369.5864 | 399.5125 | 364.0061 | 193.2141 | 52.5052
2172.2542 | 472.9583 | 431.4802 | 369.936 | 399.3092 | 364.3015 | 193.3352 | 52.5392
2173.2542 | 474.495 | 432.238 | 370.7774 | 400.5239 | 364.3823 | 193.5393 | 52.5678
2174.2542 | 474.2503 | 432.9384 | 371.0994 | 400.6593 | 364.4132 | 193.7335 | 52.586
2175.2542 | 475.0171 | 433.581 | 371.1237 | 400.9887 | 364.7685 | 193.8461 | 52.6209
2176.2542 | 475.9743 | 434.2602 | 371.1605 | 401.9872 | 365.3413 | 193.9749 | 52.6435
2177.2542 | 476.1888 | 434.8954 | 371.6204 | 403.6917 | 366.0553 | 194.2065 | 52.6615
2178.2542 | 476.2494 | 435.5353 | 372.0025 | 403.888 | 366.5438 | 194.3568 | 52.6925
2179.2542 | 477.0972 | 436.165 | 372.4305 | 404.0103 | 366.9507 | 194.4239 | 52.7226
2180.2542 | 479.1567 | 436.7954 | 373.3209 | 405.1582 | 367.2084 | 194.4421 | 52.7478
2181.2542 | 478.8212 | 437.4289 | 373.7535 | 405.1435 | 367.4561 | 194.6319 | 52.7734
2182.2542 | 480.2397 | 438.1875 | 373.592 | 404.3046 | 367.4551 | 194.4276 | 52.7933
2183.2542 | 483.9287 | 438.9338 | 374.328 | 406.5948 | 367.8692 | 194.623 | 52.8033
2184.2542 | 485.7722 | 439.6635 | 374.673 | 406.0802 | 368.6669 | 194.7784 | 52.8401
2185.2542 | 485.9153 | 440.398 | 374.7817 | 405.4028 | 369.2835 | 194.5005 | 52.8706
2186.2542 | 485.9595 | 441.1534 | 375.9069 | 408.3469 | 369.5768 | 194.7632 | 52.8914
2187.2542 | 485.6179 | 441.8788 | 375.7561 | 408.8075 | 370.2087 | 194.7916 | 52.9212
2188.2542 | 487.0735 | 442.5562 | 376.4355 | 408.5089 | 370.5475 | 194.8041 | 52.9396
2189.2542 | 488.8101 | 443.2035 | 377.1266 | 408.7144 | 371.1627 | 194.8863 | 52.9817
2190.2542 | 492.7678 | 443.8694 | 377.7451 | 410.0148 | 371.9332 | 194.8994 | 52.9973
2191.2542 | 493.2487 | 444.5225 | 378.7565 | 410.2958 | 372.5067 | 194.4227 | 53.0219
2192.2542 | 491.8389 | 445.159 | 380.3996 | 411.3001 | 372.8535 | 194.3932 | 53.0308
2193.2542 | 493.0901 | 445.8456 | 380.6395 | 411.7685 | 373.0929 | 194.1602 | 53.0654
2194.2542 | 499.0181 | 446.528 | 380.9589 | 413.0629 | 373.2786 | 194.3021 | 53.093
2195.2542 | 499.3145 | 447.1545 | 381.03 | 411.915 | 373.3042 | 194.3202 | 53.1202
2196.2542 | 500.0208 | 447.7591 | 381.7215 | 411.3037 | 373.4917 | 194.0789 | 53.1397
2197.2542 | 499.4366 | 448.3888 | 382.0788 | 411.9841 | 373.7614 | 194.4357 | 53.1605
2198.2542 | 497.9857 | 448.9997 | 382.2964 | 412.0058 | 373.8304 | 194.2888 | 53.1942
2199.2542 | 495.8768 | 449.6336 | 382.5296 | 412.8981 | 373.9572 | 194.3513 | 53.2145
2200.2542 | 496.8491 | 450.2104 | 382.5476 | 412.3585 | 374.0899 | 193.75 | 53.2512
2201.2542 | 497.5463 | 450.8229 | 383.1112 | 413.5719 | 374.1321 | 193.2288 | 53.2724
2202.2542 | 498.9581 | 451.4747 | 383.1933 | 413.0414 | 374.0403 | 193.3885 | 53.2863
2203.2542 | 498.1045 | 452.0977 | 383.5087 | 414.7943 | 373.9915 | 193.5692 | 53.3172
2204.2542 | 496.9093 | 452.6971 | 383.6277 | 413.7284 | 373.8309 | 193.4888 | 53.3378
2205.2542 | 495.7074 | 453.2696 | 383.4933 | 412.5331 | 374.0239 | 193.578 | 53.3603
2206.2542 | 494.8352 | 453.8268 | 383.4322 | 411.6951 | 373.8545 | 193.6921 | 53.3955
2207.2542 | 494.317 | 454.3685 | 384.6091 | 411.7722 | 373.6769 | 193.9101 | 53.4257
2208.2542 | 493.48 | 454.8973 | 384.4365 | 410.9821 | 373.3981 | 194.1248 | 53.4435
2209.2542 | 495.6919 | 455.4063 | 384.7239 | 410.9761 | 373.3866 | 194.2642 | 53.4777
2210.2542 | 498.2942 | 455.9478 | 385.3706 | 411.1553 | 374.0296 | 194.4209 | 53.4983
2211.2542 | 500.6203 | 456.4725 | 386.6241 | 411.2258 | 374.0726 | 194.5728 | 53.5309
2212.2542 | 501.2438 | 457.0518 | 386.7559 | 411.3791 | 374.0852 | 194.6288 | 53.551
2213.2542 | 500.8378 | 457.6777 | 386.9909 | 411.3519 | 374.0123 | 194.8884 | 53.5716
2214.2542 | 500.273 | 458.2943 | 387.6095 | 411.9669 | 374.0029 | 195.0514 | 53.5964
2215.2542 | 500.8304 | 458.9202 | 388.2811 | 412.2046 | 374.052 | 195.1395 | 53.623
2216.2542 | 500.7994 | 459.5116 | 388.9502 | 412.5546 | 374.0775 | 195.3159 | 53.6502
2217.2542 | 500.0384 | 460.0759 | 390.1424 | 413.7084 | 374.3388 | 195.2744 | 53.6795
2218.2542 | 500.2424 | 460.5999 | 390.5326 | 414.1684 | 374.3805 | 195.468 | 53.7029
2219.2542 | 503.2484 | 461.1271 | 390.4753 | 414.8312 | 374.659 | 195.6039 | 53.7299
2220.2542 | 503.3175 | 461.6708 | 391.3783 | 414.824 | 374.7173 | 195.7632 | 53.75
2221.2542 | 503.1508 | 462.2014 | 392.1352 | 417.5089 | 374.9868 | 195.8937 | 53.7694
2222.2542 | 503.7296 | 462.726 | 392.7725 | 417.6462 | 375.3793 | 196.0929 | 53.7962
2223.2542 | 502.3333 | 463.2484 | 393.1695 | 418.5457 | 375.8057 | 196.3045 | 53.8295
2224.2542 | 503.1651 | 463.7766 | 393.6594 | 419.2549 | 376.1418 | 196.4786 | 53.8554
2225.2542 | 502.4002 | 464.3102 | 393.9916 | 419.0752 | 376.2542 | 196.457 | 53.8707
2226.2542 | 502.1278 | 464.8284 | 393.7914 | 418.7098 | 376.4818 | 196.6658 | 53.8971
2227.2542 | 504.3016 | 465.3363 | 393.5762 | 418.1898 | 377.0593 | 196.7636 | 53.9218
2228.2542 | 503.9254 | 465.7992 | 393.9116 | 417.3789 | 377.2018 | 196.9473 | 53.9494
2229.2542 | 501.8917 | 466.2804 | 394.6197 | 416.4944 | 377.6922 | 197.0019 | 53.9692
2230.2542 | 500.857 | 466.742 | 394.2405 | 417.6389 | 378.0474 | 196.9773 | 54.0051
2231.2542 | 500.254 | 467.1634 | 394.333 | 417.27 | 378.2335 | 196.7958 | 54.0224
2232.2542 | 500.0423 | 467.6216 | 394.4138 | 417.3728 | 378.2318 | 197.2892 | 54.0545
2233.2542 | 500.2797 | 468.0477 | 395.0359 | 418.0905 | 378.4299 | 197.6373 | 54.0773
2234.2542 | 501.4302 | 468.4637 | 395.408 | 418.2226 | 378.6758 | 197.8542 | 54.1014
2235.2542 | 503.3125 | 468.8811 | 395.9625 | 420.1602 | 379.0117 | 197.9762 | 54.1298
2236.2542 | 505.2904 | 469.3181 | 395.9288 | 419.8907 | 379.4163 | 197.6216 | 54.1632
2237.2542 | 507.1814 | 469.7262 | 396.3743 | 419.6904 | 379.6474 | 199.5147 | 54.1862
2238.2542 | 507.9952 | 470.1369 | 396.9168 | 419.2725 | 379.9384 | 199.8736 | 54.2168
2239.2542 | 507.6299 | 470.5539 | 396.8456 | 419.7373 | 380.2909 | 200.1707 | 54.2358
2240.2542 | 508.7184 | 470.9406 | 397.0444 | 421.0738 | 380.4916 | 200.3856 | 54.2664
2241.2542 | 507.855 | 471.3705 | 397.0208 | 421.6635 | 380.825 | 200.5522 | 54.2968
2242.2542 | 509.0785 | 471.7458 | 397.5026 | 422.0003 | 381.1061 | 200.7308 | 54.3239
2243.2542 | 510.4424 | 472.1375 | 398.3709 | 423.3367 | 381.6441 | 200.8767 | 54.3433
2244.2542 | 510.6212 | 472.5206 | 398.5767 | 422.9837 | 382.0047 | 201.2641 | 54.369
2245.2542 | 509.9121 | 472.8752 | 398.8137 | 423.6225 | 382.6919 | 201.5057 | 54.3916
2246.2542 | 509.6786 | 473.2413 | 398.7665 | 423.123 | 383.0463 | 201.7014 | 54.4171
2247.2542 | 508.5859 | 473.585 | 398.7438 | 424.043 | 383.3539 | 201.8768 | 54.4378
2248.2542 | 508.2145 | 473.9048 | 398.6572 | 422.542 | 383.5031 | 202.0109 | 54.4654
2249.2542 | 509.5536 | 474.2451 | 398.7467 | 423.8712 | 383.5079 | 202.1736 | 54.4855
2250.2542 | 509.3283 | 474.5596 | 399.182 | 423.7542 | 384.0675 | 202.3231 | 54.5174
2251.2542 | 510.5801 | 474.8965 | 399.1654 | 423.6375 | 384.1156 | 202.4237 | 54.5557
2252.2542 | 511.0507 | 475.2106 | 399.884 | 424.0427 | 384.063 | 202.5684 | 54.5701
2253.2542 | 509.8786 | 475.579 | 399.598 | 424.7869 | 384.1756 | 202.7665 | 54.6062
2254.2542 | 510.0381 | 475.8912 | 399.7823 | 424.0574 | 384.4133 | 202.9039 | 54.6201
2255.2542 | 511.2175 | 476.2053 | 400.0375 | 424.3233 | 384.5224 | 202.9413 | 54.6538
2256.2542 | 513.2965 | 476.4923 | 400.2717 | 424.3523 | 385.1919 | 203.1233 | 54.6806
2257.2542 | 511.8411 | 476.7933 | 400.4626 | 424.8402 | 385.3426 | 203.2871 | 54.7081
2258.2542 | 509.2418 | 477.0505 | 400.8673 | 424.4028 | 385.7423 | 203.4352 | 54.7306
2259.2542 | 507.9668 | 477.3518 | 400.6668 | 424.6972 | 386.1435 | 203.5793 | 54.7594
2260.2542 | 507.4918 | 477.5945 | 400.6675 | 424.8975 | 386.2604 | 203.6622 | 54.7947
2261.2542 | 506.4149 | 477.8605 | 401.3991 | 426.7415 | 386.7527 | 203.8388 | 54.8117
2262.2542 | 505.8064 | 478.0722 | 401.8129 | 427.017 | 386.8994 | 203.9755 | 54.8469
2263.2542 | 504.5199 | 478.3432 | 402.0822 | 426.9373 | 387.0638 | 204.0958 | 54.8709
2264.2542 | 503.9601 | 478.5672 | 403.2537 | 426.748 | 387.0264 | 204.2032 | 54.8955
2265.2542 | 504.9907 | 478.7939 | 404.953 | 427.543 | 387.0948 | 204.3844 | 54.9289
2266.2542 | 505.3932 | 479.0082 | 405.9122 | 427.0884 | 387.1281 | 204.5148 | 54.9489
2267.2542 | 504.6431 | 479.2278 | 406.1657 | 426.2166 | 387.206 | 204.5494 | 54.9797
2268.2542 | 505.0119 | 479.4269 | 406.2791 | 426.2573 | 387.2889 | 204.4429 | 55.0152
2269.2542 | 505.1474 | 479.6364 | 406.0685 | 426.3757 | 387.4418 | 204.7249 | 55.0404
2270.2542 | 506.6442 | 479.8218 | 406.9955 | 425.635 | 387.4849 | 204.8389 | 55.0673
2271.2542 | 508.3151 | 479.9859 | 407.2495 | 426.6893 | 387.525 | 204.982 | 55.0931
2272.2542 | 507.9036 | 480.1798 | 407.9118 | 428.1021 | 387.8165 | 205.1127 | 55.1304
2273.2542 | 507.542 | 480.3288 | 407.4051 | 427.1377 | 388.1909 | 205.2241 | 55.1499
2274.2542 | 510.8363 | 480.5463 | 407.8352 | 426.5812 | 388.5125 | 205.3065 | 55.1824
2275.2542 | 511.0886 | 480.7608 | 407.9441 | 427.69 | 388.9486 | 205.4555 | 55.2111
2276.2542 | 510.903 | 480.9352 | 408.6942 | 428.6491 | 389.0341 | 205.591 | 55.2326
2277.2542 | 511.9052 | 481.1225 | 408.9746 | 429.7166 | 389.3795 | 205.7103 | 55.2616
2278.2542 | 511.7153 | 481.288 | 409.4502 | 431.1643 | 389.8035 | 205.8297 | 55.2936
2279.2542 | 512.666 | 481.4581 | 409.6176 | 430.8447 | 390.0237 | 205.9525 | 55.3066
2280.2542 | 511.2133 | 481.6086 | 409.9338 | 431.8584 | 390.1681 | 206.0442 | 55.3535
2281.2542 | 513.0295 | 481.7661 | 410.4514 | 432.3926 | 390.2138 | 206.0203 | 55.3836
2282.2542 | 513.4882 | 481.8903 | 411.1672 | 432.5485 | 390.3195 | 206.1159 | 55.4242
2283.2542 | 515.9468 | 482.048 | 411.4397 | 433.1725 | 390.4978 | 206.2787 | 55.4408
2284.2542 | 518.2928 | 482.2135 | 412.1937 | 433.7519 | 390.7458 | 206.4171 | 55.4673
2285.2542 | 519.8647 | 482.3654 | 412.9061 | 434.269 | 390.9528 | 206.5608 | 55.4993
2286.2542 | 522.3801 | 482.5269 | 413.6905 | 434.5759 | 390.9382 | 206.6758 | 55.5319
2287.2542 | 522.9062 | 482.68 | 415.0283 | 434.9573 | 391.3066 | 206.8071 | 55.5594
2288.2542 | 525.5604 | 482.857 | 415.1849 | 436.7247 | 391.7327 | 206.93 | 55.5866
2289.2542 | 524.8848 | 483.0689 | 415.5973 | 437.3819 | 392.4295 | 207.0555 | 55.6152
2290.2542 | 523.4117 | 483.2328 | 416.4334 | 437.4045 | 392.891 | 207.1612 | 55.6487
2291.2542 | 523.8643 | 483.3923 | 416.2167 | 437.5508 | 393.5452 | 207.0689 | 55.6685
2292.2542 | 527.5317 | 483.5209 | 416.8298 | 438.2411 | 393.9653 | 207.1871 | 55.6989
2293.2542 | 528.7525 | 483.7074 | 417.996 | 439.3084 | 394.3183 | 207.329 | 55.7364
2294.2542 | 526.561 | 483.8638 | 418.678 | 439.4935 | 395.1512 | 207.4135 | 55.7588
2295.2542 | 525.1541 | 484.0029 | 418.7066 | 440.7554 | 395.2665 | 207.4987 | 55.7816
2296.2542 | 524.9773 | 484.1278 | 418.7229 | 440.5088 | 395.4832 | 207.4483 | 55.831
2297.2542 | 526.3874 | 484.2567 | 419.0572 | 440.3814 | 395.6643 | 207.6066 | 55.8587
2298.2542 | 526.0353 | 484.3687 | 419.0316 | 441.9637 | 395.6988 | 207.7367 | 55.8906
2299.2542 | 529.3678 | 484.5323 | 418.8639 | 441.4656 | 395.9052 | 207.7221 | 55.9218
2300.2542 | 533.5838 | 484.7635 | 418.9933 | 441.9737 | 396.3586 | 207.7625 | 55.9505
2301.2542 | 534.8913 | 484.9466 | 419.2768 | 442.2577 | 396.8944 | 207.9714 | 55.9805
2302.2542 | 536.9806 | 485.1243 | 419.8254 | 442.5721 | 397.1615 | 207.9899 | 56.0189
2303.2542 | 539.4765 | 485.3274 | 420.3476 | 442.7458 | 397.167 | 208.0083 | 56.0473
2304.2542 | 538.9972 | 485.504 | 420.7404 | 442.6815 | 397.2058 | 208.0304 | 56.0855
2305.2542 | 537.3001 | 485.6624 | 420.5861 | 443.4044 | 397.4239 | 208.1765 | 56.1207
2306.2542 | 538.1396 | 485.7865 | 420.4273 | 443.5121 | 397.8559 | 208.2508 | 56.1449
2307.2542 | 537.7733 | 485.8854 | 420.4898 | 442.5296 | 398.0384 | 208.1334 | 56.1739
2308.2542 | 538.7509 | 486.0371 | 420.4938 | 442.1766 | 398.3118 | 208.2275 | 56.209
2309.2542 | 539.6151 | 486.13 | 420.587 | 442.651 | 398.5696 | 208.4433 | 56.2407
2310.2542 | 538.9453 | 486.226 | 420.6935 | 441.7554 | 398.6199 | 208.5282 | 56.2789
2311.2542 | 537.9792 | 486.3245 | 420.3408 | 441.7535 | 398.5936 | 208.4569 | 56.3145
2312.2542 | 536.4261 | 486.446 | 420.5207 | 441.7022 | 398.6861 | 208.5437 | 56.3427
2313.2542 | 537.8545 | 486.5594 | 420.5363 | 442.6157 | 398.8552 | 208.7148 | 56.3757
2314.2542 | 537.794 | 486.6981 | 421.0086 | 442.7611 | 399.3256 | 208.7049 | 56.411
2315.2542 | 538.4183 | 486.8554 | 421.8779 | 444.0904 | 399.7262 | 208.8922 | 56.4491
2316.2542 | 540.4216 | 487.014 | 421.9423 | 443.8552 | 400.2816 | 208.9955 | 56.477
2317.2542 | 538.1029 | 487.1728 | 422.4777 | 443.5768 | 400.4209 | 209.1957 | 56.5179
2318.2542 | 537.2302 | 487.3608 | 422.6476 | 443.4686 | 400.5208 | 209.314 | 56.5481
2319.2542 | 536.1811 | 487.5269 | 422.9767 | 444.1868 | 400.813 | 209.4855 | 56.5821
2320.2542 | 536.1097 | 487.6636 | 423.4382 | 444.6507 | 400.9299 | 209.5721 | 56.6238
2321.2542 | 536.7638 | 487.852 | 424.1176 | 444.7801 | 401.8201 | 209.6709 | 56.646
2322.2542 | 537.8724 | 488.0325 | 424.4337 | 445.6471 | 402.1568 | 209.8209 | 56.6882
2323.2542 | 536.3219 | 488.1703 | 424.4726 | 447.2973 | 402.2728 | 209.8864 | 56.7201
2324.2542 | 535.4578 | 488.298 | 424.5381 | 449.1782 | 402.6057 | 210.0059 | 56.7561
2325.2542 | 535.5646 | 488.4151 | 424.8768 | 449.6469 | 402.8592 | 210.089 | 56.7829
2326.2542 | 534.8447 | 488.5589 | 424.9822 | 450.3251 | 402.7646 | 209.8827 | 56.8299
2327.2542 | 532.1641 | 488.7007 | 425.4114 | 451.0323 | 402.7913 | 209.9523 | 56.8599
2328.2542 | 531.4968 | 488.8248 | 425.4007 | 451.2567 | 403.0055 | 210.0371 | 56.8918
2329.2542 | 530.6234 | 488.9425 | 425.4423 | 450.6733 | 403.332 | 210.0301 | 56.9205
2330.2542 | 531.9346 | 489.0375 | 424.8713 | 449.8167 | 403.4823 | 210.1026 | 56.9561
2331.2542 | 533.5118 | 489.1515 | 425.7392 | 449.005 | 403.5392 | 210.0356 | 56.9935
2332.2542 | 533.0843 | 489.2549 | 426.103 | 451.129 | 403.9739 | 210.1595 | 57.028
2333.2542 | 532.3467 | 489.2639 | 426.9724 | 450.7855 | 404.4257 | 210.3053 | 57.0637
2334.2542 | 531.6707 | 489.2648 | 427.5003 | 450.9217 | 404.5527 | 209.984 | 57.0935
2335.2542 | 532.4743 | 489.3151 | 427.4323 | 451.4612 | 405.1006 | 209.8361 | 57.1329
2336.2542 | 535.6595 | 489.3566 | 427.3879 | 452.1487 | 405.5937 | 209.9299 | 57.1689
2337.2542 | 537.8866 | 489.3791 | 427.4138 | 450.6418 | 405.7148 | 209.7655 | 57.1949
2338.2542 | 537.8036 | 489.3266 | 427.8927 | 451.7093 | 406.2599 | 209.9083 | 57.2313
2339.2542 | 536.7077 | 489.2877 | 428.4498 | 451.9678 | 406.8614 | 209.7716 | 57.2606
2340.2542 | 536.4696 | 489.2939 | 429.2898 | 451.5034 | 407.1071 | 209.7884 | 57.2898
2341.2542 | 538.7967 | 489.3304 | 429.9034 | 451.3789 | 407.4061 | 209.7691 | 57.3224
2342.2542 | 539.2388 | 489.4041 | 430.5501 | 451.9232 | 407.6974 | 209.882 | 57.3544
2343.2542 | 539.0605 | 489.4752 | 431.5841 | 453.1615 | 408.4069 | 209.8119 | 57.3846
2344.2542 | 537.0625 | 489.5432 | 432.0561 | 452.8845 | 408.8275 | 209.5143 | 57.4118
2345.2542 | 536.0648 | 489.5848 | 431.7446 | 453.6365 | 409.4053 | 209.5244 | 57.4457
2346.2542 | 538.6442 | 489.636 | 432.14 | 453.717 | 409.8744 | 209.4113 | 57.4781
2347.2542 | 542.0556 | 489.7221 | 433.3218 | 454.682 | 410.3323 | 208.8654 | 57.5055
2348.2542 | 543.0919 | 489.8596 | 433.421 | 454.4144 | 410.6403 | 208.6385 | 57.5433
2349.2542 | 543.6909 | 489.9781 | 433.5084 | 455.1315 | 410.9234 | 208.8399 | 57.5768
2350.2542 | 545.7065 | 490.0916 | 433.3271 | 456.1755 | 411.1745 | 208.9451 | 57.5993
2351.2542 | 542.5004 | 490.2531 | 433.937 | 456.1172 | 411.5086 | 209.058 | 57.6289
2352.2542 | 542.1068 | 490.3698 | 433.4562 | 456.3677 | 411.7836 | 209.0658 | 57.6668
2353.2542 | 542.5182 | 490.4808 | 433.4446 | 455.5821 | 412.3557 | 209.0325 | 57.694
2354.2542 | 542.7972 | 490.603 | 433.6828 | 456.3958 | 412.2385 | 209.2476 | 57.729
2355.2542 | 542.9691 | 490.7441 | 434.0915 | 456.1576 | 412.3646 | 209.4485 | 57.7641
2356.2542 | 543.2963 | 490.8579 | 434.4101 | 455.5185 | 412.2637 | 209.4548 | 57.7911
2357.2542 | 542.953 | 490.9885 | 434.6013 | 455.4515 | 412.2708 | 209.3854 | 57.8225
2358.2542 | 542.354 | 491.1165 | 434.9867 | 456.4615 | 412.5751 | 209.2511 | 57.8636
2359.2542 | 542.9239 | 491.2809 | 435.1707 | 456.8325 | 412.8679 | 209.0459 | 57.8853
2360.2542 | 543.2161 | 491.4301 | 436.253 | 456.8649 | 412.9784 | 208.8039 | 57.9264
2361.2542 | 542.9388 | 491.5801 | 436.4535 | 457.0179 | 413.0108 | 208.494 | 57.9452
2362.2542 | 543.6248 | 491.6954 | 436.5237 | 456.2369 | 412.9761 | 210.0675 | 57.9903
2363.2542 | 545.0326 | 491.8198 | 437.0462 | 457.6466 | 412.9901 | 210.5411 | 58.0177
2364.2542 | 543.4176 | 491.9466 | 437.3734 | 458.1558 | 412.922 | 210.7152 | 58.0444
2365.2542 | 542.7003 | 492.0772 | 437.2292 | 459.3628 | 413.1411 | 210.7419 | 58.0901
2366.2542 | 540.8627 | 492.2508 | 437.2908 | 458.6675 | 413.2425 | 210.54 | 58.1285
2367.2542 | 540.6969 | 492.3779 | 436.697 | 459.5892 | 413.2159 | 210.2908 | 58.1458
2368.2542 | 543.6074 | 492.5712 | 436.6895 | 458.8441 | 413.3044 | 210.3427 | 58.192
2369.2542 | 543.8501 | 492.747 | 436.6899 | 459.0374 | 413.3898 | 210.3703 | 58.2138
2370.2542 | 543.2662 | 492.9278 | 436.4844 | 459.2114 | 413.2685 | 210.2399 | 58.2449
2371.2542 | 544.2211 | 493.1215 | 436.7858 | 459.4883 | 413.7214 | 210.1492 | 58.2779
2372.2542 | 546.3573 | 493.2974 | 437.3239 | 460.7166 | 413.9874 | 210.1331 | 58.3173
2373.2542 | 546.6064 | 493.4981 | 438.8647 | 461.4026 | 414.2054 | 210.2265 | 58.3506
2374.2542 | 544.6916 | 493.6875 | 439.4672 | 461.2858 | 414.3811 | 210.1698 | 58.3811
2375.2542 | 543.3714 | 493.8705 | 439.8404 | 461.436 | 414.4979 | 210.2043 | 58.4254
2376.2542 | 542.2613 | 494.0511 | 440.5201 | 461.6489 | 414.7682 | 210.2115 | 58.4516
2377.2542 | 541.9504 | 494.2341 | 440.6008 | 461.7275 | 414.9785 | 210.1989 | 58.4818
2378.2542 | 542.51 | 494.4165 | 441.3107 | 462.2689 | 415.451 | 210.2487 | 58.5169
2379.2542 | 543.8667 | 494.5854 | 442.0381 | 463.3957 | 415.8365 | 210.3247 | 58.5584
2380.2542 | 545.1113 | 494.7761 | 442.451 | 463.187 | 416.0185 | 210.449 | 58.5893
2381.2542 | 544.9872 | 494.9528 | 442.2533 | 462.7053 | 416.204 | 210.6215 | 58.6343
2382.2542 | 543.3533 | 495.0933 | 442.5851 | 462.3559 | 416.2285 | 210.6278 | 58.665
2383.2542 | 542.7968 | 495.2478 | 442.4359 | 462.9142 | 416.0439 | 210.688 | 58.6813
2384.2542 | 541.0642 | 495.385 | 442.5292 | 462.0355 | 415.9438 | 210.3045 | 58.7261
2385.2542 | 542.659 | 495.5062 | 442.7371 | 463.2587 | 415.8738 | 210.1812 | 58.7647
2386.2542 | 544.0668 | 495.6051 | 443.5544 | 462.4753 | 415.9168 | 210.0938 | 58.8035
2387.2542 | 544.4299 | 495.7235 | 443.7176 | 462.0733 | 416.163 | 210.1198 | 58.833
2388.2542 | 544.7015 | 495.846 | 444.3656 | 461.6531 | 416.3257 | 209.9773 | 58.8615
2389.2542 | 543.4358 | 495.9584 | 444.5966 | 461.2735 | 416.3586 | 209.7597 | 58.9092
2390.2542 | 543.2818 | 496.0809 | 445.032 | 460.9995 | 416.2965 | 211.0895 | 58.9466
2391.2542 | 545.7226 | 496.2221 | 445.5844 | 461.842 | 416.4276 | 210.9993 | 58.9854
2392.2542 | 547.5244 | 496.4724 | 445.7297 | 462.4415 | 416.4316 | 211.2427 | 59.0215
2393.2542 | 548.5689 | 496.6765 | 445.874 | 462.0586 | 416.4222 | 211.5522 | 59.057
2394.2542 | 553.415 | 496.9242 | 445.974 | 462.4914 | 416.4186 | 211.7661 | 59.0809
2395.2542 | 553.3002 | 497.1653 | 446.4734 | 462.9442 | 416.6218 | 211.6976 | 59.1112
2396.2542 | 555.6387 | 497.3754 | 446.9071 | 464.4417 | 416.8763 | 211.3603 | 59.1573
2397.2542 | 557.6341 | 497.5875 | 447.7639 | 464.4428 | 416.9432 | 211.2642 | 59.1978
2398.2542 | 559.0365 | 497.8091 | 449.6224 | 465.0133 | 417.0181 | 211.5184 | 59.2219
2399.2542 | 558.5313 | 498.0278 | 449.8654 | 465.8593 | 417.3041 | 211.7174 | 59.2571
2400.2542 | 560.1483 | 498.3265 | 450.7158 | 465.8919 | 417.6489 | 211.6969 | 59.2925
2401.2542 | 558.3517 | 498.5848 | 451.5424 | 466.759 | 418.1914 | 211.8651 | 59.3339
2402.2542 | 557.7053 | 498.8396 | 452.026 | 466.6781 | 418.4586 | 211.6169 | 59.3613
2403.2542 | 556.3823 | 499.0816 | 451.8072 | 466.6464 | 418.6464 | 211.5041 | 59.3985
2404.2542 | 559.0403 | 499.311 | 451.9102 | 467.2915 | 419.0281 | 210.0791 | 59.437
2405.2542 | 561.4268 | 499.5588 | 451.7758 | 466.8396 | 419.3426 | 209.7553 | 59.4623
2406.2542 | 561.0619 | 499.7906 | 451.2443 | 467.2007 | 419.5082 | 209.7811 | 59.5004
2407.2542 | 564.0287 | 499.9775 | 451.3286 | 466.5881 | 419.8694 | 209.868 | 59.5322
2408.2542 | 565.5099 | 500.2593 | 451.1975 | 466.8632 | 420.3859 | 210.008 | 59.5675
2409.2542 | 567.2224 | 500.5885 | 451.065 | 467.4249 | 420.7043 | 210.097 | 59.5981
2410.2542 | 565.5351 | 500.8716 | 451.1672 | 467.3804 | 421.308 | 210.1952 | 59.6312
2411.2542 | 565.8087 | 501.1238 | 452.016 | 467.1829 | 421.6622 | 210.2915 | 59.6615
2412.2542 | 567.7378 | 501.3891 | 452.1282 | 468.5208 | 421.8835 | 210.3582 | 59.7102
2413.2542 | 569.5641 | 501.6152 | 452.0465 | 468.2227 | 422.1114 | 210.3968 | 59.7362
2414.2542 | 572.201 | 501.8794 | 452.4014 | 469.3969 | 422.648 | 210.5292 | 59.7807
2415.2542 | 576.8527 | 502.1726 | 452.7051 | 468.9456 | 423.0262 | 210.5748 | 59.8066
2416.2542 | 577.8651 | 502.4574 | 452.9036 | 468.405 | 423.4259 | 210.619 | 59.8531
2417.2542 | 575.8325 | 502.7023 | 453.2835 | 469.2185 | 423.7487 | 210.6924 | 59.8695
2418.2542 | 574.0904 | 502.9515 | 453.2824 | 468.598 | 424.3233 | 210.7883 | 59.9172
2419.2542 | 575.7706 | 503.2622 | 453.4374 | 468.5313 | 424.5682 | 210.8818 | 59.9464
2420.2542 | 573.8338 | 503.5483 | 453.5195 | 469.717 | 424.6847 | 210.9632 | 59.9853
2421.2542 | 575.7288 | 503.8897 | 453.599 | 469.915 | 424.77 | 211.0659 | 60.0231
2422.2542 | 574.9643 | 504.2453 | 454.3097 | 470.6236 | 424.996 | 211.164 | 60.0521
2423.2542 | 574.9707 | 504.5574 | 455.0063 | 471.3987 | 425.2102 | 211.2548 | 60.0904
2424.2542 | 571.9219 | 504.8782 | 455.2296 | 470.6624 | 425.4689 | 211.3531 | 60.1289
2425.2542 | 575.4191 | 505.2108 | 454.8882 | 469.7909 | 425.6692 | 211.4465 | 60.1622
2426.2542 | 581.1959 | 505.6071 | 455.6015 | 469.2757 | 426.0785 | 211.5347 | 60.1983
2427.2542 | 584.6139 | 506.0091 | 456.3212 | 469.8514 | 426.2194 | 211.6278 | 60.2297
2428.2542 | 583.2315 | 506.4103 | 457.2194 | 470.7432 | 426.5945 | 211.7095 | 60.2689
2429.2542 | 579.6289 | 506.7822 | 457.1697 | 470.1339 | 426.8417 | 211.8057 | 60.3008
2430.2542 | 585.7266 | 507.1786 | 456.9301 | 469.6434 | 427.3912 | 211.8952 | 60.3466
2431.2542 | 587.7395 | 507.604 | 457.4268 | 471.5122 | 427.5063 | 211.9778 | 60.375
2432.2542 | 588.5988 | 508.04 | 458.5133 | 471.4954 | 427.8093 | 212.0727 | 60.4106
2433.2542 | 588.1175 | 508.4928 | 459.1069 | 471.1443 | 427.9199 | 212.1726 | 60.4447
2434.2542 | 587.7881 | 508.8962 | 458.8535 | 470.6986 | 427.8921 | 212.2718 | 60.4796
2435.2542 | 585.585 | 509.3026 | 458.9062 | 470.0517 | 427.7561 | 212.3621 | 60.5142
2436.2542 | 586.6907 | 509.6825 | 458.5713 | 469.5836 | 427.732 | 212.4495 | 60.5528
2437.2542 | 583.2828 | 510.0551 | 458.7797 | 469.2111 | 427.7238 | 212.508 | 60.5861
2438.2542 | 581.6552 | 510.4164 | 459.4468 | 469.0847 | 427.8381 | 212.6023 | 60.6164
2439.2542 | 581.3985 | 510.7926 | 460.2976 | 470.2015 | 427.8306 | 212.712 | 60.6512
2440.2542 | 578.8861 | 511.0855 | 460.5307 | 470.3916 | 427.7122 | 212.8361 | 60.6795
2441.2542 | 576.2096 | 511.3407 | 461.1729 | 471.1993 | 427.5367 | 212.8553 | 60.7222
2442.2542 | 575.2555 | 511.5879 | 461.5317 | 471.0131 | 427.607 | 212.9168 | 60.7607
2443.2542 | 570.8661 | 511.8424 | 462.3298 | 471.1936 | 427.692 | 213.0128 | 60.7851
2444.2542 | 571.2193 | 511.4839 | 462.8396 | 472.3801 | 427.7096 | 213.1041 | 60.8207
2445.2542 | 571.5949 | 511.6394 | 463.3214 | 472.5261 | 427.8861 | 213.2126 | 60.8518
2446.2542 | 569.4109 | 511.7677 | 464.0931 | 472.9442 | 428.1017 | 213.3099 | 60.8712
2447.2542 | 567.6963 | 511.9209 | 464.0311 | 473.1427 | 428.1314 | 213.4219 | 60.9133
2448.2542 | 566.9804 | 512.0385 | 464.6851 | 472.3177 | 428.1301 | 213.5296 | 60.9426
2449.2542 | 565.8038 | 512.139 | 465.2669 | 473.4488 | 428.3871 | 213.6286 | 60.9813
2450.2542 | 567.8162 | 512.3063 | 465.4638 | 473.1713 | 428.3901 | 213.7331 | 61.0029
2451.2542 | 570.4926 | 512.3983 | 465.8822 | 474.0098 | 428.4029 | 213.8358 | 61.0337
2452.2542 | 569.9116 | 512.5547 | 466.5527 | 473.9099 | 428.4602 | 213.9332 | 61.0762
2453.2542 | 569.2248 | 512.6737 | 466.69 | 473.4138 | 428.36 | 214.0281 | 61.1071
2454.2542 | 566.3362 | 512.7852 | 467.6981 | 475.6062 | 428.8461 | 214.1244 | 61.137
2455.2542 | 564.8146 | 512.8661 | 468.5232 | 475.5714 | 429.3277 | 214.2316 | 61.1628
2456.2542 | 561.7779 | 512.9727 | 468.8552 | 476.9242 | 429.5757 | 214.3267 | 61.2031
2457.2542 | 571.2116 | 513.1138 | 469.5116 | 477.4417 | 430.0523 | 214.4298 | 61.2281
2458.2542 | 569.0175 | 513.2647 | 468.8891 | 476.8073 | 430.3175 | 214.5258 | 61.2615
2459.2542 | 568.636 | 513.4178 | 468.9937 | 477.32 | 430.3829 | 214.6415 | 61.2918
2460.2542 | 571.175 | 513.515 | 469.0909 | 478.8186 | 430.5204 | 214.745 | 61.3344
2461.2542 | 576.4759 | 513.672 | 469.2951 | 478.6223 | 430.5401 | 214.8406 | 61.3672
2462.2542 | 582.3999 | 513.8686 | 469.8868 | 478.4663 | 430.682 | 214.9691 | 61.3968
2463.2542 | 582.6759 | 514.0378 | 469.7814 | 478.3632 | 430.8661 | 215.0769 | 61.4273
2464.2542 | 580.6548 | 514.136 | 470.3655 | 479.3494 | 430.8058 | 215.1785 | 61.4679
2465.2542 | 579.6337 | 514.2044 | 470.529 | 480.1045 | 430.771 | 215.2781 | 61.5041
2466.2542 | 578.0865 | 514.2223 | 470.438 | 479.898 | 430.8674 | 215.4004 | 61.5424
2467.2542 | 576.4739 | 514.6767 | 470.016 | 480.6356 | 431.0504 | 215.4823 | 61.5673
2468.2542 | 577.2677 | 514.7076 | 469.7438 | 479.3947 | 431.2704 | 215.5761 | 61.5821
2469.2542 | 586.4362 | 514.8163 | 469.7051 | 479.8547 | 431.604 | 215.7131 | 61.6355
2470.2542 | 592.551 | 517.7244 | 470.1385 | 479.966 | 432.0233 | 215.8396 | 61.681
2471.2542 | 593.5063 | 517.8567 | 469.9217 | 479.2456 | 432.0635 | 215.9507 | 61.7098
2472.2542 | 593.0285 | 517.9927 | 470.1956 | 478.3565 | 432.1093 | 216.0615 | 61.7474
2473.2542 | 590.6502 | 518.1053 | 469.4824 | 478.7516 | 432.102 | 216.1678 | 61.7921
2474.2542 | 589.9349 | 518.2539 | 469.5314 | 479.1014 | 432.1676 | 216.2739 | 61.8314
2475.2542 | 589.8272 | 518.3617 | 469.4394 | 478.6137 | 432.2205 | 216.3733 | 61.8508
2476.2542 | 589.9562 | 518.4209 | 469.4203 | 479.8423 | 432.6646 | 216.4858 | 61.8979
2477.2542 | 589.0616 | 518.5061 | 470.1001 | 480.4392 | 433.0712 | 216.5947 | 61.9248
2478.2542 | 589.9519 | 518.5322 | 470.4669 | 481.0598 | 433.3528 | 216.6999 | 61.9569
2479.2542 | 588.3578 | 518.5145 | 471.0647 | 481.3352 | 433.7192 | 216.8249 | 61.9962
2480.2542 | 592.1469 | 518.5614 | 471.374 | 481.4176 | 433.9075 | 216.9377 | 62.0272
2481.2542 | 591.1467 | 518.6026 | 471.1324 | 481.136 | 434.025 | 217.0547 | 62.0633
2482.2542 | 593.0903 | 518.645 | 471.3035 | 481.3656 | 434.0293 | 217.1592 | 62.0959
2483.2542 | 595.1699 | 518.7474 | 471.6699 | 481.0105 | 433.8647 | 217.271 | 62.1343
2484.2542 | 595.0809 | 518.8623 | 472.1337 | 481.7425 | 433.8089 | 217.3735 | 62.1756
2485.2542 | 595.3125 | 518.9457 | 473.438 | 482.9786 | 433.8861 | 217.4804 | 62.1972
2486.2542 | 595.5106 | 519.0203 | 472.9093 | 483.0392 | 434.0153 | 217.5863 | 62.2372
2487.2542 | 595.0223 | 519.0949 | 472.5531 | 483.6375 | 434.1081 | 217.6956 | 62.27
2488.2542 | 594.4774 | 519.1954 | 472.7217 | 482.6531 | 434.1505 | 217.8138 | 62.3216
2489.2542 | 593.1889 | 519.5553 | 471.9945 | 483.4295 | 434.2026 | 217.7929 | 62.3059
2490.2542 | 595.6042 | 519.6032 | 472.6358 | 482.6608 | 434.4912 | 217.9393 | 62.3661
2491.2542 | 595.2174 | 519.7605 | 473.3421 | 483.7543 | 434.7325 | 218.0264 | 62.4086
2492.2542 | 594.5951 | 519.867 | 473.5368 | 483.1445 | 434.8851 | 218.1346 | 62.4477
2493.2542 | 596.5938 | 519.9814 | 473.9877 | 482.4324 | 434.9037 | 218.2473 | 62.4837
2494.2542 | 595.9385 | 520.1117 | 474.0356 | 483.4342 | 435.0724 | 218.3481 | 62.5123
2495.2542 | 598.6594 | 520.2493 | 475.0657 | 483.3088 | 435.1249 | 218.4348 | 62.5608
2496.2542 | 600.6534 | 520.3897 | 474.9618 | 483.246 | 435.1845 | 218.5354 | 62.5923
2497.2542 | 600.242 | 520.5759 | 474.8837 | 483.1305 | 435.2093 | 218.6235 | 62.6209
2498.2542 | 596.0802 | 521.5892 | 474.9356 | 488.1748 | 435.0338 | 218.434 | 62.6239
2499.2542 | 593.2997 | 521.8422 | 474.8688 | 490.4921 | 434.7303 | 218.3265 | 62.5011
2500.2542 | 594.5269 | 522.1032 | 474.3757 | 489.1924 | 434.4914 | 218.4744 | 62.5485
2501.2542 | 591.8296 | 522.6192 | 474.3169 | 491.8321 | 434.5677 | 218.6185 | 62.6762
2502.2542 | 592.5266 | 522.9364 | 474.9159 | 490.7705 | 434.6029 | 218.9063 | 62.8303
2503.2542 | 592.4593 | 523.2486 | 475.4307 | 491.8841 | 434.5043 | 218.8025 | 62.7275
2504.2542 | 597.7066 | 523.6111 | 475.8322 | 492.5235 | 434.3605 | 218.8599 | 62.7638
2505.2542 | 596.4562 | 523.7837 | 475.6579 | 491.6316 | 434.4555 | 219.017 | 62.8394
2506.2542 | 597.3918 | 523.8408 | 474.7063 | 491.0348 | 434.3105 | 219.0934 | 62.8446
2507.2542 | 598.2502 | 521.924 | 474.3398 | 495.5136 | 434.3026 | 10.5302 | 10.9397
2508.2542 | 598.7633 | 521.9796 | 474.7451 | 497.1232 | 434.3254 | 10.2234 | 10.8659
2509.2542 | 596.534 | 522.0482 | 473.91 | 497.4967 | 434.2204 | 10.1892 | 10.8678
2510.2542 | 603.9601 | 522.2228 | 473.9795 | 497.2742 | 434.1069 | 10.1836 | 10.8651
2511.2542 | 604.9081 | 522.4792 | 474.799 | 497.4948 | 434.1922 | 10.1772 | 10.8549
2512.2542 | 606.2418 | 522.7736 | 474.3872 | 497.1773 | 434.1828 | 10.1749 | 10.8685
2513.2542 | 616.1073 | 523.0675 | 474.8652 | 497.5109 | 434.2219 | 10.171 | 10.8561
2514.2542 | 618.1102 | 523.3461 | 474.7191 | 498.6353 | 434.3171 | 10.1707 | 10.866
2515.2542 | 617.8627 | 523.6166 | 475.0561 | 499.5898 | 434.6398 | 10.1658 | 10.865
2516.2542 | 616.8202 | 523.8822 | 475.2993 | 500.011 | 434.9179 | 10.2252 | 10.8639
2517.2542 | 614.9582 | 524.1647 | 475.1196 | 499.709 | 435.0732 | 10.167 | 10.8604
2518.2542 | 613.1276 | 524.5465 | 475.6142 | 500.0001 | 435.3718 | 10.1692 | 10.865
2519.2542 | 613.9803 | 524.9118 | 476.4646 | 501.0428 | 435.5298 | 10.1582 | 10.86
2520.2542 | 613.0912 | 525.2505 | 477.3379 | 501.2689 | 435.796 | 10.1621 | 10.8679
2521.2542 | 614.2251 | 525.5664 | 477.8018 | 500.9436 | 435.9102 | 10.1607 | 10.8605
2522.2542 | 613.584 | 525.8506 | 478.4522 | 501.4873 | 435.9825 | 10.1654 | 10.8645
2523.2542 | 612.1683 | 526.1347 | 478.7561 | 500.9093 | 436.1966 | 10.1662 | 10.8625
2524.2542 | 620.4564 | 526.3921 | 478.8693 | 500.4808 | 436.2061 | 10.1653 | 10.8611
2525.2542 | 622.8241 | 526.7012 | 479.2308 | 500.1267 | 435.9854 | 10.1606 | 10.8626
2526.2542 | 625.6771 | 527.0358 | 479.1247 | 500.5105 | 435.8787 | 10.1654 | 10.8648
2527.2542 | 621.2694 | 527.3309 | 479.0482 | 500.3868 | 435.7974 | 10.165 | 10.8689
2528.2542 | 621.8341 | 527.6336 | 478.911 | 500.1686 | 435.4948 | 10.1669 | 10.8641
2529.2542 | 624.2891 | 528.0273 | 478.3776 | 499.433 | 435.3277 | 10.1663 | 10.8705
2530.2542 | 623.328 | 528.3345 | 478.195 | 499.3241 | 435.0064 | 10.1634 | 10.8706
2531.2542 | 628.6082 | 528.7443 | 478.1695 | 498.8726 | 434.7682 | 10.1639 | 10.8717
2532.2542 | 630.5039 | 529.2084 | 477.6661 | 498.6112 | 434.5813 | 10.1714 | 10.872
2533.2542 | 633.5338 | 529.5795 | 478.0375 | 498.2218 | 434.4113 | 10.165 | 10.8643
2534.2542 | 639.9878 | 530.1057 | 478.0432 | 498.6287 | 434.308 | 10.1736 | 10.8802
2535.2542 | 639.0619 | 530.5874 | 478.5226 | 500.0838 | 434.4076 | 10.1696 | 10.8699
2536.2542 | 638.7086 | 531.0358 | 479.3811 | 500.6037 | 434.4405 | 10.1723 | 10.8712
2537.2542 | 636.4009 | 531.4668 | 479.9163 | 500.3885 | 434.4843 | 10.1704 | 10.8862
2538.2542 | 630.2358 | 531.8075 | 479.8089 | 500.0275 | 434.3024 | 10.1782 | 10.879
2539.2542 | 627.6661 | 532.1344 | 479.7067 | 500.0711 | 434.145 | 10.1734 | 10.873
2540.2542 | 622.4926 | 532.4287 | 480.2796 | 500.0753 | 434.0372 | 10.1704 | 10.8795
2541.2542 | 621.0869 | 532.6874 | 480.5911 | 499.7592 | 433.765 | 10.1774 | 10.8753
2542.2542 | 620.8173 | 532.9511 | 480.6746 | 500.582 | 433.4265 | 10.1744 | 10.8663
2543.2542 | 618.3662 | 533.1465 | 480.4745 | 500.8014 | 433.2831 | 10.1664 | 10.8803
2544.2542 | 612.2094 | 533.3221 | 480.4732 | 501.0323 | 433.2528 | 10.1772 | 10.8717
2545.2542 | 618.7669 | 533.5204 | 480.6193 | 501.3603 | 433.1631 | 10.1767 | 10.8758
2546.2542 | 617.4947 | 533.7362 | 480.781 | 501.6882 | 433.0258 | 10.1686 | 10.8737
2547.2542 | 618.7125 | 533.9581 | 481.2753 | 501.3845 | 433.0881 | 10.1755 | 10.8847
2548.2542 | 621.9396 | 534.153 | 481.1277 | 501.5869 | 432.9552 | 10.1813 | 10.8854
2549.2542 | 617.9612 | 534.3382 | 482.2251 | 501.8703 | 432.8657 | 10.1795 | 10.8849
2550.2542 | 615.9404 | 534.47 | 483.0019 | 502.8286 | 432.9337 | 10.1789 | 10.8802
2551.2542 | 612.3018 | 534.5665 | 483.3997 | 503.5857 | 432.8373 | 10.184 | 10.885
2552.2542 | 606.6573 | 534.6204 | 484.1773 | 503.6184 | 432.816 | 10.1822 | 10.8816
2553.2542 | 605.5956 | 534.728 | 484.1658 | 503.6239 | 432.5884 | 10.1781 | 10.8831
2554.2542 | 615.2757 | 534.898 | 484.3964 | 503.1987 | 432.4475 | 10.1789 | 10.8876
2555.2542 | 616.6737 | 535.121 | 483.8977 | 503.3003 | 432.2505 | 10.1827 | 10.8818
2556.2542 | 616.0436 | 535.2917 | 484.2044 | 504.3442 | 432.2264 | 10.1871 | 10.8827
2557.2542 | 619.2713 | 535.4646 | 484.8551 | 504.9585 | 432.21 | 10.1841 | 10.8897
2558.2542 | 616.2355 | 535.6284 | 485.121 | 505.3621 | 432.203 | 10.1857 | 10.8846
2559.2542 | 617.6302 | 535.7447 | 485.2881 | 505.5383 | 432.2711 | 10.1856 | 10.8845
2560.2542 | 619.567 | 535.9067 | 485.2344 | 505.088 | 432.3873 | 10.1856 | 10.8847
2561.2542 | 626.4154 | 536.1149 | 486.2596 | 505.4447 | 432.4304 | 10.1898 | 10.8815
2562.2542 | 630.1092 | 536.3619 | 486.553 | 505.8374 | 432.5133 | 10.1869 | 10.8943
2563.2542 | 631.3123 | 536.6421 | 486.3512 | 506.0422 | 432.4185 | 10.1913 | 10.8864
2564.2542 | 631.9665 | 536.8841 | 486.2842 | 505.7634 | 432.3223 | 10.1897 | 10.8876
2565.2542 | 628.2635 | 537.0228 | 486.0177 | 505.4588 | 432.3013 | 10.1887 | 10.8937
2566.2542 | 623.8563 | 537.0838 | 486.3903 | 506.6821 | 432.1215 | 10.1942 | 10.8955
2567.2542 | 621.4424 | 537.0735 | 487.1937 | 507.1823 | 432.0313 | 10.1942 | 10.89
2568.2542 | 620.48 | 537.038 | 487.4498 | 508.0863 | 432.0516 | 10.1914 | 10.8939
2569.2542 | 631.7049 | 537.0181 | 487.789 | 508.1943 | 432.0863 | 10.1924 | 10.8956
2570.2542 | 632.2857 | 537.1079 | 488.0463 | 508.0043 | 432.0402 | 10.1929 | 10.8849
2571.2542 | 629.302 | 537.1754 | 487.915 | 508.2698 | 432.0563 | 10.1983 | 10.8943
2572.2542 | 628.0203 | 537.2802 | 487.7664 | 508.3338 | 432.1338 | 10.2037 | 10.8899
2573.2542 | 628.8302 | 537.3856 | 488.1286 | 508.8141 | 432.2886 | 10.2031 | 10.9046
2574.2542 | 628.5982 | 537.5265 | 488.1067 | 509.0356 | 432.5784 | 10.1949 | 10.8983
2575.2542 | 631.6227 | 537.7075 | 488.9784 | 510.0622 | 432.8818 | 10.205 | 10.9018
2576.2542 | 636.1935 | 537.9651 | 488.9338 | 511.1911 | 433.0866 | 10.199 | 10.9001
2577.2542 | 636.658 | 538.2321 | 488.8265 | 511.4606 | 433.1864 | 10.1995 | 10.8905
2578.2542 | 637.5039 | 538.5829 | 489.8627 | 513.3615 | 433.2563 | 10.1981 | 10.9005
2579.2542 | 640.0387 | 538.8942 | 491.1739 | 513.4343 | 433.3754 | 10.2032 | 10.8987
2580.2542 | 638.4573 | 539.1399 | 491.0757 | 513.8609 | 433.6175 | 10.2018 | 10.9035
2581.2542 | 638.2445 | 539.2815 | 490.8907 | 513.9027 | 433.7633 | 10.2074 | 10.9017
2582.2542 | 636.5844 | 539.3693 | 491.149 | 514.4337 | 433.8544 | 10.2105 | 10.8932
2583.2542 | 647.9486 | 539.5323 | 491.8914 | 514.8975 | 434.1314 | 10.2153 | 10.909
2584.2542 | 648.1023 | 539.7038 | 491.9468 | 514.4625 | 434.2695 | 10.2092 | 10.9133
2585.2542 | 640.8291 | 539.8722 | 491.5661 | 514.3091 | 434.3009 | 10.2146 | 10.9116
2586.2542 | 641.717 | 540.0093 | 491.0466 | 514.943 | 434.4371 | 10.2141 | 10.9176
2587.2542 | 644.0751 | 540.1823 | 491.6406 | 515.6478 | 434.5601 | 10.2127 | 10.9116
2588.2542 | 643.9547 | 540.3373 | 492.2985 | 516.3963 | 434.2602 | 10.2088 | 10.9146
2589.2542 | 641.1709 | 540.4987 | 492.6872 | 516.356 | 434.0491 | 10.2167 | 10.9027
2590.2542 | 643.0793 | 540.5973 | 493.253 | 516.5415 | 433.9159 | 10.2128 | 10.9112
2591.2542 | 637.8785 | 540.7136 | 493.2458 | 517.0368 | 433.8353 | 10.2203 | 10.9078
2592.2542 | 635.1616 | 540.777 | 493.3811 | 518.0302 | 433.7524 | 10.2101 | 10.9097
2593.2542 | 630.7459 | 540.8238 | 493.6903 | 518.7262 | 433.7452 | 10.2216 | 10.9181
2594.2542 | 630.4555 | 540.8915 | 493.7144 | 519.7705 | 433.6471 | 10.2231 | 10.9172
2595.2542 | 627.0782 | 540.983 | 494.5952 | 519.3421 | 433.3768 | 10.2144 | 10.914
2596.2542 | 625.9649 | 541.0509 | 495.3559 | 519.7136 | 433.2802 | 10.2176 | 10.9175
2597.2542 | 631.8886 | 541.2796 | 496.1136 | 520.9641 | 433.1974 | 10.2152 | 10.9139
2598.2542 | 631.8818 | 541.5165 | 497.3422 | 522.4234 | 433.323 | 10.2159 | 10.9229
2599.2542 | 629.6126 | 541.7383 | 497.8115 | 523.0541 | 433.2801 | 10.2199 | 10.9241
2600.2542 | 627.236 | 541.9558 | 498.1398 | 523.7235 | 433.3459 | 10.2204 | 10.9145
2601.2542 | 622.5978 | 542.2038 | 498.8612 | 525.2396 | 433.3603 | 10.2191 | 10.9199
2602.2542 | 621.595 | 542.3343 | 499.0486 | 522.8762 | 433.3999 | 10.213 | 10.9259
2603.2542 | 620.0776 | 542.4216 | 499.7013 | 525.0522 | 433.3611 | 10.2148 | 10.9201
2604.2542 | 622.1712 | 542.6166 | 499.6558 | 525.6775 | 433.276 | 10.2189 | 10.9168
2605.2542 | 619.925 | 542.7792 | 499.3373 | 527.8394 | 433.2962 | 10.2141 | 10.9235
2606.2542 | 615.2336 | 542.8625 | 499.4927 | 529.178 | 433.175 | 10.2156 | 10.9259
2607.2542 | 614.4374 | 542.9324 | 499.6737 | 530.8897 | 433.2398 | 10.2171 | 10.9241
2608.2542 | 618.0978 | 543.0353 | 499.9304 | 532.3992 | 433.2656 | 10.2301 | 10.9254
2609.2542 | 614.6807 | 543.1658 | 499.8991 | 533.2593 | 433.1597 | 10.2237 | 10.9223
2610.2542 | 616.0325 | 543.295 | 500.0851 | 532.6791 | 433.1814 | 10.2348 | 10.9267
2611.2542 | 616.6045 | 543.4614 | 500.6033 | 533.5941 | 433.177 | 10.2242 | 10.9343
2612.2542 | 616.3005 | 543.5934 | 500.5626 | 535.555 | 433.2217 | 10.2231 | 10.9318
2613.2542 | 612.5387 | 543.7354 | 502.0635 | 536.7438 | 433.2436 | 10.2214 | 10.9238
2614.2542 | 614.0227 | 543.9329 | 502.4492 | 537.4269 | 433.1606 | 10.2224 | 10.9328
2615.2542 | 613.5117 | 544.1259 | 503.2157 | 538.5924 | 433.0203 | 10.2282 | 10.9247
2616.2542 | 615.1854 | 544.327 | 503.6718 | 539.2188 | 432.9204 | 10.2269 | 10.9306
2617.2542 | 614.7018 | 544.561 | 503.5507 | 538.7953 | 432.8825 | 10.2211 | 10.9298
2618.2542 | 621.0761 | 544.758 | 504.4343 | 534.607 | 432.8952 | 10.2278 | 10.9358
2619.2542 | 620.516 | 545.0426 | 505.3623 | 535.2112 | 432.8042 | 10.2294 | 10.929
2620.2542 | 617.6257 | 545.312 | 505.3908 | 536.7049 | 432.7599 | 10.2236 | 10.932
2621.2542 | 616.5412 | 545.5874 | 505.9441 | 537.7094 | 432.6175 | 10.229 | 10.9396
2622.2542 | 611.9356 | 545.8122 | 506.116 | 539.2974 | 432.5135 | 10.2272 | 10.9268
2623.2542 | 608.7556 | 546.0239 | 506.2344 | 540.2097 | 432.3156 | 10.2327 | 10.933
2624.2542 | 607.7507 | 546.1918 | 506.2755 | 540.3999 | 432.3102 | 10.2344 | 10.9392
2625.2542 | 618.9211 | 546.3576 | 507.0056 | 531.4256 | 432.2627 | 230.2077 | 67.1234
2626.2542 | 617.059 | 546.5288 | 506.7754 | 531.748 | 432.2182 | 230.7272 | 67.2466
2627.2542 | 614.2778 | 546.7338 | 506.7438 | 533.2337 | 432.1764 | 230.8123 | 67.2932
2628.2542 | 616.3872 | 546.9856 | 506.3832 | 534.4849 | 432.169 | 230.9394 | 67.3334
2629.2542 | 619.0587 | 547.3354 | 506.1988 | 536.3531 | 432.0816 | 231.0264 | 67.3602
2630.2542 | 619.2518 | 547.6406 | 505.6778 | 537.1223 | 432.1119 | 231.1578 | 67.4017
2631.2542 | 624.6761 | 547.9567 | 505.4685 | 537.33 | 432.0121 | 231.2809 | 67.4474
2632.2542 | 625.917 | 548.2232 | 505.5771 | 535.391 | 431.8877 | 231.374 | 67.485
2633.2542 | 624.3794 | 548.5294 | 506.0438 | 536.5235 | 431.8476 | 231.4802 | 67.5367
2634.2542 | 624.0756 | 548.7316 | 506.3011 | 536.8573 | 431.8677 | 231.5562 | 67.5775
2635.2542 | 623.4509 | 548.8498 | 506.4954 | 536.6063 | 431.923 | 231.6816 | 67.6254
2636.2542 | 623.1812 | 549.0504 | 506.2603 | 537.0094 | 431.7646 | 231.8088 | 67.6718
2637.2542 | 622.6075 | 549.2914 | 506.0004 | 537.4129 | 431.7506 | 231.9446 | 67.7069
2638.2542 | 619.7144 | 549.5948 | 506.163 | 538.8878 | 431.7478 | 232.0165 | 67.7421
2639.2542 | 619.4311 | 549.904 | 506.2831 | 538.7759 | 431.7217 | 232.1471 | 67.7898
2640.2542 | 619.5796 | 550.139 | 506.0528 | 539.5663 | 431.7129 | 232.2923 | 67.821
2641.2542 | 620.0242 | 550.3889 | 505.5496 | 540.9036 | 431.6108 | 232.354 | 67.8586
2642.2542 | 620.3136 | 550.6463 | 505.4362 | 545.9422 | 431.7048 | 232.4144 | 67.8891
2643.2542 | 624.1572 | 550.9262 | 505.2575 | 545.9824 | 431.6663 | 232.5311 | 67.9292
2644.2542 | 622.1646 | 551.1904 | 505.3007 | 546.4191 | 431.6115 | 232.6424 | 67.9603
2645.2542 | 620.0122 | 551.333 | 505.1839 | 546.4131 | 431.6851 | 232.7383 | 68.0009
2646.2542 | 616.2559 | 551.401 | 505.4031 | 548.4071 | 431.7991 | 232.8663 | 68.0347
2647.2542 | 613.7506 | 551.3487 | 506.0513 | 548.5595 | 431.789 | 232.9709 | 68.078
2648.2542 | 610.9379 | 551.2661 | 505.9519 | 548.7092 | 431.8122 | 233.0966 | 68.107
2649.2542 | 611.3584 | 551.3138 | 506.0911 | 549.6342 | 431.884 | 233.2475 | 68.1474
2650.2542 | 607.9427 | 551.2543 | 506.1555 | 551.6137 | 431.8534 | 233.3776 | 68.1875
2651.2542 | 610.9714 | 551.2015 | 506.4688 | 552.2028 | 431.8738 | 233.4513 | 68.2176
2652.2542 | 647.5088 | 551.1589 | 507.9565 | 514.3558 | 432.0335 | 233.9009 | 68.321
2653.2542 | 650.2329 | 551.151 | 507.9366 | 514.8786 | 432.0628 | 234.0068 | 68.37
2654.2542 | 649.91 | 551.1353 | 508.172 | 515.2838 | 432.0936 | 234.1541 | 68.4016
2655.2542 | 650.3586 | 551.1047 | 508.8038 | 515.9535 | 432.1202 | 234.2167 | 68.4397
2656.2542 | 646.2186 | 551.0834 | 508.6743 | 516.5639 | 432.2137 | 234.3601 | 68.4842
2657.2542 | 641.2605 | 551.0419 | 508.3873 | 515.7716 | 432.2397 | 234.4686 | 68.522
2658.2542 | 641.7487 | 550.9996 | 508.0604 | 515.0512 | 432.2545 | 234.6127 | 68.5646
2659.2542 | 638.7767 | 550.9786 | 508.1037 | 515.2102 | 432.3652 | 234.6725 | 68.6029
2660.2542 | 636.5426 | 550.8917 | 508.4182 | 515.0485 | 432.4173 | 234.7767 | 68.6336
2661.2542 | 637.8475 | 550.8767 | 508.7177 | 515.5221 | 432.4989 | 234.8636 | 68.6687
2662.2542 | 636.2716 | 550.9319 | 508.6185 | 515.5839 | 432.5254 | 234.9897 | 68.6881
2663.2542 | 636.369 | 551.0148 | 508.8575 | 515.7864 | 432.532 | 235.1644 | 68.7439
2664.2542 | 629.2044 | 551.0231 | 509.1651 | 515.3547 | 432.6711 | 235.2875 | 68.7721
2665.2542 | 626.9407 | 551.0976 | 510.0745 | 515.0707 | 432.6552 | 235.3465 | 68.8164
2666.2542 | 628.4268 | 551.2268 | 510.5826 | 515.0981 | 432.8945 | 235.5284 | 68.8561
2667.2542 | 633.2467 | 551.382 | 511.449 | 515.2626 | 432.9951 | 235.617 | 68.9003
2668.2542 | 637.3302 | 551.5341 | 512.0568 | 515.7071 | 433.153 | 235.6577 | 68.9332
2669.2542 | 639.8098 | 551.6676 | 512.3434 | 515.5176 | 433.2888 | 235.7664 | 68.9721
2670.2542 | 642.3459 | 551.7727 | 513.0937 | 516.7374 | 433.266 | 235.8727 | 69.0074
2671.2542 | 642.1885 | 551.8877 | 513.2571 | 516.7535 | 433.2565 | 236.0729 | 69.0603
2672.2542 | 640.408 | 552.0845 | 512.7338 | 516.0753 | 433.2724 | 236.1001 | 69.093
2673.2542 | 646.6818 | 552.2484 | 513.083 | 510.0297 | 433.2603 | 236.2733 | 69.1431
2674.2542 | 638.4302 | 552.3774 | 512.8271 | 514.977 | 433.2811 | 236.2784 | 69.1361
2675.2542 | 642.476 | 552.3748 | 514.0954 | 515.4193 | 433.3828 | 236.4095 | 69.2104
2676.2542 | 657.5663 | 552.4616 | 515.131 | 510.9508 | 433.2699 | 236.4757 | 69.2512
2677.2542 | 663.4755 | 552.7466 | 515.4871 | 510.119 | 433.3988 | 236.5954 | 69.2862
2678.2542 | 659.0125 | 553.029 | 515.219 | 514.6199 | 433.5369 | 236.7044 | 69.3209
2679.2542 | 658.445 | 553.3297 | 515.177 | 508.537 | 433.5321 | 236.8512 | 69.3722
2680.2542 | 654.3874 | 553.6368 | 514.9681 | 509.2537 | 433.6169 | 236.9491 | 69.4083
2681.2542 | 657.6335 | 554.0374 | 515.0028 | 508.9941 | 433.792 | 237.0577 | 69.4524
2682.2542 | 660.882 | 554.408 | 515.4782 | 507.6181 | 434.0933 | 237.1089 | 69.489
2683.2542 | 660.5323 | 554.6472 | 514.9546 | 505.5178 | 434.1308 | 237.3045 | 69.5228
2684.2542 | 663.2044 | 554.9732 | 515.0443 | 506.4455 | 434.2861 | 237.3814 | 69.5616
2685.2542 | 661.117 | 555.3115 | 515.6975 | 506.1964 | 434.518 | 237.3853 | 69.5957
2686.2542 | 660.9482 | 555.6141 | 516.601 | 505.1635 | 434.5565 | 237.5595 | 69.6395
2687.2542 | 666.8508 | 555.899 | 517.7547 | 504.6449 | 434.7182 | 237.6387 | 69.6792
2688.2542 | 669.1275 | 556.2066 | 519.2228 | 504.4906 | 434.7047 | 237.7936 | 69.7091
2689.2542 | 667.9068 | 556.4806 | 519.5662 | 506.1587 | 434.6882 | 237.8691 | 69.761
2690.2542 | 666.5612 | 556.7023 | 518.7988 | 504.8427 | 434.6294 | 238.0109 | 69.7923
2691.2542 | 665.6701 | 556.9801 | 518.0843 | 504.6233 | 434.7361 | 238.0991 | 69.8348
2692.2542 | 666.19 | 557.2587 | 518.2636 | 498.991 | 434.7716 | 238.2205 | 69.8741
2693.2542 | 663.4164 | 557.5101 | 518.2009 | 498.644 | 434.9636 | 238.3593 | 69.9105
2694.2542 | 664.3549 | 557.7564 | 519.1798 | 498.6028 | 435.1123 | 238.5185 | 69.9554
2695.2542 | 671.8238 | 557.96 | 519.8662 | 498.3084 | 435.1271 | 238.588 | 69.9934
2696.2542 | 681.657 | 558.3114 | 520.2423 | 497.686 | 435.1658 | 238.7376 | 70.0315
2697.2542 | 685.876 | 558.6256 | 520.6743 | 496.4185 | 435.4338 | 238.8907 | 70.0735
2698.2542 | 689.4897 | 558.9429 | 521.0312 | 496.3963 | 435.5663 | 239.0682 | 70.1179
2699.2542 | 691.123 | 559.2136 | 521.9384 | 497.4866 | 435.7472 | 239.1256 | 70.1623
2700.2542 | 692.5659 | 559.3823 | 522.7393 | 496.4925 | 435.7626 | 239.2528 | 70.1914
2701.2542 | 694.1542 | 559.5314 | 522.7 | 496.0568 | 435.3821 | 239.3565 | 70.2249
2702.2542 | 695.6783 | 559.6799 | 522.5836 | 494.8897 | 435.6063 | 239.4811 | 70.2564
2703.2542 | 696.9265 | 559.8863 | 523.3503 | 494.9084 | 435.7977 | 239.5738 | 70.3056
2704.2542 | 693.3461 | 560.1053 | 523.4569 | 494.3412 | 436.1799 | 239.6507 | 70.3404
2705.2542 | 690.4559 | 560.4232 | 522.7989 | 494.7848 | 436.4463 | 239.7273 | 70.3789
2706.2542 | 687.5321 | 560.7045 | 523.0329 | 494.8627 | 436.8567 | 239.7961 | 70.426
2707.2542 | 696.345 | 560.8698 | 524.1695 | 481.7599 | 437.2649 | 239.9883 | 70.4616
2708.2542 | 689.1105 | 561.0709 | 524.1232 | 488.3706 | 437.3839 | 240.0661 | 70.5112
2709.2542 | 679.8387 | 561.2591 | 524.5836 | 493.2573 | 437.5851 | 240.1154 | 70.5225
2710.2542 | 676.7202 | 561.4319 | 524.1826 | 493.9419 | 437.8534 | 240.3438 | 70.5656
2711.2542 | 680.7391 | 561.6449 | 524.7292 | 492.6405 | 438.3044 | 240.3383 | 70.6004
2712.2542 | 680.9957 | 561.8643 | 524.2987 | 493.7547 | 438.8914 | 240.4398 | 70.6379
2713.2542 | 683.4465 | 562.032 | 524.6101 | 491.5738 | 439.1506 | 240.6541 | 70.6764
2714.2542 | 680.5712 | 562.2192 | 523.9531 | 492.5769 | 439.1789 | 240.6535 | 70.7072
2715.2542 | 686.682 | 562.5162 | 523.8857 | 490.8205 | 439.116 | 240.8976 | 70.749
2716.2542 | 692.8367 | 562.7527 | 523.8679 | 489.921 | 438.9247 | 240.9904 | 70.7851
2717.2542 | 694.3845 | 563.0537 | 523.4218 | 488.8776 | 438.8013 | 241.0768 | 70.8263
2718.2542 | 693.547 | 563.2997 | 523.2655 | 488.2884 | 439.0074 | 241.1653 | 70.8495
2719.2542 | 697.2531 | 563.5865 | 522.5537 | 487.5841 | 439.2323 | 241.3701 | 70.8844
2720.2542 | 700.2109 | 563.9554 | 522.0391 | 487.1984 | 439.5627 | 241.4693 | 70.9225
2721.2542 | 699.5032 | 564.354 | 521.9121 | 489.2636 | 439.8517 | 241.6535 | 70.978
2722.2542 | 701.3274 | 564.6883 | 522.0871 | 488.7857 | 439.9827 | 241.8275 | 70.9933
2723.2542 | 701.8374 | 565.0125 | 522.0895 | 489.8808 | 440.4843 | 241.921 | 71.0328
2724.2542 | 702.5331 | 565.4343 | 521.6441 | 486.8849 | 440.0005 | 242.0089 | 71.0716
2725.2542 | 702.727 | 565.8844 | 521.4562 | 486.8641 | 439.6403 | 242.1072 | 71.0967
2726.2542 | 704.0933 | 566.4094 | 521.7007 | 484.6491 | 439.4463 | 242.2828 | 71.1396
2727.2542 | 704.6467 | 566.8816 | 521.4002 | 484.6863 | 439.7583 | 242.3662 | 71.1818
2728.2542 | 703.2029 | 567.4447 | 521.869 | 483.8333 | 440.5013 | 242.5333 | 71.2116
2729.2542 | 702.0311 | 567.9907 | 522.8934 | 482.8416 | 441.4136 | 242.7213 | 71.2585
2730.2542 | 701.2599 | 568.5906 | 523.2489 | 482.7296 | 441.7968 | 242.821 | 71.3001
2731.2542 | 695.5379 | 569.1613 | 523.2625 | 485.4673 | 442.3129 | 242.8597 | 71.3397
2732.2542 | 702.6128 | 569.6833 | 523.7837 | 479.0496 | 443.2221 | 243.107 | 71.3632
2733.2542 | 704.4461 | 570.1796 | 523.8763 | 476.0494 | 444.1792 | 243.2015 | 71.407
2734.2542 | 707.7104 | 570.6951 | 524.4525 | 475.9557 | 444.2672 | 243.3708 | 71.4419
2735.2542 | 715.044 | 571.0477 | 524.5506 | 472.0361 | 444.7447 | 243.3816 | 71.4921
2736.2542 | 724.4362 | 571.445 | 525.619 | 469.959 | 444.8536 | 243.6597 | 71.5268
2737.2542 | 733.2817 | 572.0254 | 526.3531 | 468.3864 | 445.4976 | 243.6642 | 71.5702
2738.2542 | 730.7639 | 572.5005 | 526.688 | 465.3115 | 446.0364 | 243.8359 | 71.6078
2739.2542 | 732.8168 | 572.9048 | 526.7875 | 460.0306 | 446.4051 | 243.9052 | 71.644
2740.2542 | 741.2995 | 573.2352 | 526.8485 | 450.8919 | 447.1032 | 243.9921 | 71.6815
2741.2542 | 745.5191 | 573.5031 | 526.3856 | 447.3609 | 447.3058 | 244.2103 | 71.7284
2742.2542 | 742.0311 | 573.7634 | 526.2851 | 451.5875 | 447.7234 | 244.284 | 71.7624
2743.2542 | 756.5678 | 574.1377 | 527.5948 | 448.4199 | 447.8036 | 244.4057 | 71.8028
2744.2542 | 755.7643 | 574.4794 | 528.3964 | 443.5051 | 448.4038 | 244.5308 | 71.8457
2745.2542 | 760.3386 | 574.7718 | 529.04 | 442.2861 | 448.422 | 244.6405 | 71.888
2746.2542 | 766.8759 | 575.096 | 530.1958 | 436.5816 | 448.5787 | 244.9699 | 71.9151
2747.2542 | 776.0104 | 575.3482 | 530.6296 | 438.1047 | 448.3594 | 245.1128 | 71.9665
2748.2542 | 780.6914 | 575.6294 | 530.7559 | 431.9763 | 448.4519 | 245.1138 | 72.0114
2749.2542 | 776.7562 | 576.0072 | 530.6791 | 431.5715 | 448.9704 | 245.2867 | 72.0515
2750.2542 | 772.8777 | 576.3634 | 530.8048 | 431.8136 | 449.3762 | 245.5692 | 72.0808
2751.2542 | 774.2348 | 576.8137 | 531.0526 | 430.3853 | 450.1734 | 245.5309 | 72.1223
2752.2542 | 776.2096 | 577.3392 | 531.0764 | 428.4998 | 451.4236 | 245.6252 | 72.1609
2753.2542 | 766.1656 | 577.7791 | 530.6335 | 436.2314 | 452.2455 | 245.8243 | 72.1933
2754.2542 | 774.0328 | 578.1959 | 531.2921 | 432.9726 | 453.1056 | 245.9478 | 72.236
2755.2542 | 784.6594 | 578.583 | 532.35 | 430.3345 | 454.1539 | 246.1114 | 72.2815
2756.2542 | 786.8564 | 578.9002 | 532.9789 | 428.5709 | 454.1017 | 246.2134 | 72.3061
2757.2542 | 788.6702 | 579.1723 | 533.5001 | 427.3159 | 453.232 | 246.3877 | 72.3561
2758.2542 | 786.7471 | 579.333 | 534.0312 | 422.2166 | 452.6217 | 246.4898 | 72.397
2759.2542 | 786.2777 | 579.5277 | 533.5594 | 419.1068 | 451.9398 | 246.7044 | 72.4262
2760.2542 | 770.7423 | 579.7191 | 532.9521 | 428.1836 | 451.3461 | 246.8085 | 72.4618
2761.2542 | 780.7356 | 579.9151 | 532.4662 | 423.0567 | 450.5594 | 246.9699 | 72.5
2762.2542 | 771.9693 | 580.0659 | 531.3364 | 427.4687 | 450.3955 | 246.9892 | 72.5355
2763.2542 | 775.1777 | 580.1906 | 530.5347 | 423.2566 | 450.2253 | 247.1721 | 72.5887
2764.2542 | 776.3553 | 580.3435 | 531.1374 | 424.7446 | 449.7126 | 247.3328 | 72.6171
2765.2542 | 778.9746 | 580.4826 | 531.456 | 422.2884 | 449.9666 | 247.432 | 72.6535
2766.2542 | 775.5343 | 580.567 | 531.3664 | 421.1362 | 449.7988 | 247.6817 | 72.6979
2767.2542 | 772.4292 | 580.5711 | 531.0953 | 421.82 | 450.2344 | 247.7374 | 72.7328
2768.2542 | 796.7271 | 580.5756 | 531.0194 | 396.0627 | 450.5818 | 247.7354 | 72.784
2769.2542 | 796.3268 | 580.6231 | 530.3671 | 394.3705 | 450.9826 | 248.0076 | 72.8145
2770.2542 | 798.3658 | 580.6809 | 529.8246 | 391.4804 | 450.9165 | 248.1133 | 72.8563
2771.2542 | 802.6224 | 580.6927 | 529.7121 | 389.1973 | 451.1295 | 248.2709 | 72.9034
2772.2542 | 798.0293 | 580.8171 | 529.66 | 394.7489 | 451.1587 | 248.5121 | 72.9459
2773.2542 | 772.1334 | 581.024 | 528.9932 | 420.7765 | 451.1288 | 248.4307 | 72.977
2774.2542 | 776.5773 | 581.2908 | 528.5849 | 413.2154 | 451.8178 | 248.688 | 73.0153
2775.2542 | 773.5527 | 581.5225 | 528.1579 | 416.6328 | 451.7064 | 248.8069 | 73.0619
2776.2542 | 790.1954 | 581.8284 | 528.404 | 401.8357 | 452.6473 | 248.9825 | 73.1059
2777.2542 | 775.4108 | 582.2488 | 528.5788 | 414.548 | 453.0347 | 249.2275 | 73.1445
2778.2542 | 759.3291 | 582.6504 | 528.3339 | 435.7083 | 453.2798 | 249.443 | 73.1956
2779.2542 | 745.3305 | 583.1429 | 528.3274 | 448.0264 | 453.3369 | 249.5677 | 73.2322
2780.2542 | 736.2669 | 583.5826 | 528.2061 | 457.8044 | 453.2415 | 249.7608 | 73.2677
2781.2542 | 703.4939 | 583.8531 | 528.0856 | 488.8021 | 453.8076 | 249.9498 | 73.3063
2782.2542 | 712.3753 | 584.0063 | 528.2725 | 479.1228 | 453.885 | 250.1968 | 73.3461
2783.2542 | 664.6939 | 584.1747 | 527.9721 | 530.3902 | 453.7388 | 250.5121 | 73.3754
2784.2542 | 663.9081 | 584.3653 | 528.0513 | 531.8076 | 453.7872 | 250.647 | 73.423
2785.2542 | 712.282 | 584.548 | 527.9953 | 481.6346 | 454.2945 | 250.7135 | 73.4858
2786.2542 | 722.9687 | 584.8032 | 527.2748 | 473.4205 | 454.9959 | 250.9418 | 73.5245
2787.2542 | 736.94 | 585.1097 | 526.4027 | 455.7731 | 455.6729 | 250.8977 | 73.5909
2788.2542 | 674.0839 | 585.4318 | 525.9359 | 520.6204 | 455.7532 | 251.1747 | 73.6143
2789.2542 | 687.5582 | 585.6775 | 525.7704 | 506.4588 | 456.5606 | 251.4853 | 73.6607
2790.2542 | 649.577 | 585.9578 | 525.7754 | 545.9636 | 456.7867 | 251.7211 | 73.7
2791.2542 | 604.1893 | 586.3371 | 526.2259 | 593.6259 | 457.0381 | 252.0554 | 73.7442
2792.2542 | 630.9353 | 586.6558 | 526.9541 | 564.4796 | 457.5844 | 252.1683 | 73.7825
2793.2542 | 628.9131 | 586.8772 | 527.0981 | 568.1439 | 457.8934 | 252.4224 | 73.8331
2794.2542 | 711.5745 | 587.0606 | 526.9078 | 482.9588 | 458.5147 | 252.3588 | 73.8692
2795.2542 | 611.5245 | 587.3331 | 526.0175 | 585.4359 | 458.5066 | 253.0277 | 73.8791
2796.2542 | 786.5204 | 587.5277 | 526.0456 | 409.7794 | 459.0671 | 252.5983 | 73.9583
2797.2542 | 655.7017 | 587.699 | 525.5376 | 545.9302 | 459.2674 | 253.1188 | 73.9967
2798.2542 | 675.7996 | 587.8126 | 525.8065 | 531.9044 | 458.9393 | 253.1313 | 74.0376
2799.2542 | 623.6213 | 588.0366 | 525.4323 | 592.6969 | 459.0031 | 253.7136 | 74.0782
2800.2542 | 656.5518 | 588.3315 | 524.8707 | 560.4366 | 458.7723 | 253.7925 | 74.1112
2801.2542 | 616.7538 | 588.5186 | 524.0232 | 600.5023 | 459.272 | 254.1363 | 74.1614
2802.2542 | 207.6693 | 588.7079 | 521.7824 | 1047.301 | 459.3157 | 255.5507 | 74.1648
2803.2542 | 217.4172 | 588.7346 | 521.207 | 1038.4548 | 458.8524 | 255.4752 | 74.2132
2804.2542 | 344.744 | 588.7122 | 521.948 | 903.0644 | 459.3281 | 255.3889 | 74.2517
2805.2542 | 344.868 | 588.7619 | 522.0976 | 902.3614 | 460.0401 | 255.6615 | 74.2968
2806.2542 | 336.9854 | 588.8182 | 522.1678 | 906.6738 | 460.3084 | 255.9691 | 74.3342
2807.2542 | 347.8628 | 588.8696 | 522.0487 | 899.0866 | 460.2591 | 256.1019 | 74.3791
2808.2542 | 372.1144 | 588.929 | 522.2555 | 880.2954 | 461.2688 | 256.2817 | 74.415
2809.2542 | 289.8761 | 589.0536 | 522.4894 | 971.1402 | 461.2517 | 256.7367 | 74.4565
2810.2542 | 265.2327 | 589.1322 | 522.5792 | 994.5016 | 461.7537 | 257.1804 | 74.4886
2811.2542 | 346.7934 | 589.0489 | 523.0285 | 894.2215 | 462.4022 | 257.0535 | 74.5562
2812.2542 | 276.3488 | 589.081 | 523.0503 | 970.3043 | 463.2752 | 257.3342 | 74.5824
2813.2542 | 289.5206 | 589.0794 | 523.7562 | 951.9257 | 464.0075 | 257.6305 | 74.6436
2814.2542 | 268.7949 | 589.0872 | 523.5944 | 972.976 | 463.9279 | 257.9095 | 74.671
2815.2542 | 256.8714 | 589.2474 | 523.619 | 986.4054 | 464.3158 | 258.3263 | 74.7205
2816.2542 | 238.9903 | 589.461 | 523.317 | 1011.165 | 466.0192 | 258.3514 | 74.7506
2817.2542 | 266.7015 | 589.685 | 523.1663 | 988.1151 | 466.2559 | 258.8219 | 74.8392
2818.2542 | 240.241 | 589.8311 | 523.6379 | 1014.3353 | 467.2471 | 258.8448 | 74.8407
2819.2542 | 233.111 | 590.1255 | 523.5058 | 1024.4182 | 467.7279 | 259.3543 | 74.8846
2820.2542 | 239.5654 | 590.4258 | 523.2188 | 1020.5741 | 467.8032 | 259.5782 | 74.9311
2821.2542 | 231.1252 | 590.7331 | 523.2816 | 1024.8395 | 468.096 | 259.639 | 74.9855
2822.2542 | 351.8357 | 590.9579 | 523.8128 | 898.4383 | 467.9539 | 259.5824 | 75.0224
2823.2542 | 342.7954 | 591.1697 | 522.9392 | 908.1636 | 467.77 | 260.0008 | 75.079
2824.2542 | 309.7116 | 591.3511 | 522.2134 | 940.5248 | 467.5394 | 260.3539 | 75.1236
2825.2542 | 307.8103 | 591.4919 | 521.5627 | 942.1958 | 468.1694 | 260.4145 | 75.1595
2826.2542 | 300.0083 | 591.5735 | 520.8461 | 947.8244 | 468.0691 | 260.1463 | 75.2063
2827.2542 | 300.7655 | 591.6309 | 520.594 | 942.5833 | 467.505 | 260.9687 | 75.2728
2828.2542 | 304.4352 | 591.7255 | 520.06 | 939.3915 | 467.2732 | 260.8508 | 75.3067
2829.2542 | 251.2311 | 591.8903 | 519.3781 | 1006.9363 | 467.5265 | 261.2478 | 75.3575
2830.2542 | 227.7055 | 592.0827 | 518.8466 | 1033.0289 | 467.7519 | 261.5883 | 75.3956
2831.2542 | 217.651 | 592.3028 | 518.524 | 1041.7689 | 467.8773 | 261.8325 | 75.4363
2832.2542 | 224.2928 | 592.4598 | 518.3488 | 1045.3927 | 468.1005 | 262.0458 | 75.4859
2833.2542 | 229.0484 | 592.6461 | 517.9818 | 1033.1229 | 467.9731 | 262.4589 | 75.5401
2834.2542 | 200.4981 | 592.8584 | 517.4014 | 1063.2814 | 468.6512 | 262.4321 | 75.5779
2835.2542 | 224.1372 | 593.0497 | 516.5395 | 1037.7426 | 468.9125 | 262.4815 | 75.6231
2836.2542 | 216.4574 | 593.3022 | 516.7322 | 1046.2926 | 468.8644 | 262.8368 | 75.667
2837.2542 | 226.202 | 593.6326 | 516.0021 | 1031.3872 | 468.8522 | 263.1159 | 75.7304
2838.2542 | 229.8157 | 593.9192 | 515.3076 | 1029.4881 | 469.4133 | 263.261 | 75.769
2839.2542 | 226.4592 | 594.3032 | 514.7744 | 1030.6058 | 469.2316 | 263.3777 | 75.8107
2840.2542 | 228.6604 | 594.5003 | 514.5594 | 1037.0098 | 469.5351 | 263.3792 | 75.8513
2841.2542 | 236.6125 | 594.8484 | 514.6963 | 1030.8261 | 469.6416 | 263.6795 | 75.9016
2842.2542 | 243.8135 | 595.1439 | 514.2286 | 1029.6305 | 471.2441 | 263.938 | 75.9596
2843.2542 | 284.935 | 595.3475 | 513.9319 | 976.5909 | 471.3059 | 264.1074 | 75.9944
2844.2542 | 867.1786 | 595.4889 | 515.9203 | 346.7837 | 473.6872 | 262.4414 | 76.0631
2845.2542 | 894.4082 | 595.6741 | 515.3508 | 314.8585 | 474.3492 | 262.2589 | 76.1275
2846.2542 | 938.7219 | 595.7941 | 515.1018 | 268.5447 | 474.8457 | 262.4589 | 76.1576
2847.2542 | 935.7191 | 595.9248 | 514.4046 | 272.7612 | 474.7605 | 262.6501 | 76.2056
2848.2542 | 912.6268 | 596.0415 | 513.5978 | 305.5798 | 474.7654 | 263.0473 | 76.2477
2849.2542 | 946.6571 | 596.1458 | 513.2299 | 266.8984 | 474.7899 | 263.3182 | 76.3067
2850.2542 | 948.5292 | 596.2124 | 513.1644 | 266.7223 | 475.115 | 263.7315 | 76.348
2851.2542 | 944.939 | 596.2499 | 512.7743 | 264.7711 | 474.7849 | 263.5368 | 76.3939
2852.2542 | 946.0141 | 596.3315 | 512.1493 | 260.3884 | 474.2747 | 263.5246 | 76.4322
2853.2542 | 938.7891 | 596.4732 | 511.0368 | 263.5762 | 474.807 | 263.5739 | 76.4949
2854.2542 | 946.0499 | 596.6052 | 509.9639 | 260.3693 | 474.3434 | 264.0463 | 76.5285
2855.2542 | 952.4886 | 596.8685 | 509.0806 | 253.6553 | 474.7071 | 264.1257 | 76.5756
2856.2542 | 960.8047 | 597.2135 | 507.9483 | 251.9602 | 474.6195 | 264.1258 | 76.6234
2857.2542 | 949.53 | 597.5917 | 507.2119 | 257.0806 | 474.3658 | 264.4315 | 76.6695
2858.2542 | 946.4887 | 597.7386 | 507.1168 | 257.0855 | 474.1219 | 264.3663 | 76.7076
2859.2542 | 962.9048 | 598.0215 | 507.0738 | 244.1306 | 473.9164 | 264.623 | 76.7629
2860.2542 | 963.778 | 598.3475 | 506.5778 | 240.6389 | 473.6969 | 264.7493 | 76.8066
2861.2542 | 969.9399 | 598.6089 | 505.6367 | 241.9932 | 474.2701 | 264.8683 | 76.8473
2862.2542 | 973.8856 | 598.9907 | 504.2741 | 233.3843 | 474.8127 | 265.182 | 76.8898
2863.2542 | 975.1585 | 599.5377 | 502.9843 | 233.2359 | 475.686 | 265.1304 | 76.9268
2864.2542 | 976.5666 | 600.0003 | 502.3499 | 230.0965 | 477.1169 | 265.3446 | 76.9808
2865.2542 | 971.7871 | 600.4248 | 501.9959 | 237.1837 | 477.5023 | 265.4653 | 77.0324
2866.2542 | 978.2789 | 600.8455 | 501.4665 | 233.9453 | 477.6864 | 265.6193 | 77.0715
2867.2542 | 982.6518 | 601.2822 | 501.1193 | 226.2068 | 477.257 | 266.024 | 77.1185
2868.2542 | 976.3666 | 601.4973 | 500.533 | 231.7952 | 477.8795 | 266.1606 | 77.1599
2869.2542 | 972.448 | 601.6843 | 500.1352 | 233.8219 | 478.059 | 266.7713 | 77.21
2870.2542 | 966.9751 | 601.8038 | 499.831 | 234.617 | 477.9862 | 266.5502 | 77.2571
2871.2542 | 960.8033 | 601.8311 | 499.2595 | 235.8561 | 478.3293 | 266.3932 | 77.2832
2872.2542 | 965.339 | 601.8401 | 498.5154 | 234.0968 | 478.976 | 266.5248 | 77.3472
2873.2542 | 975.3784 | 601.9427 | 497.8347 | 229.6273 | 479.6697 | 266.7402 | 77.3871
2874.2542 | 976.9158 | 601.9781 | 497.0536 | 232.2029 | 479.703 | 266.7798 | 77.4327
2875.2542 | 981.8972 | 602.1647 | 496.5715 | 223.0502 | 479.352 | 267.3534 | 77.4656
2876.2542 | 988.5998 | 602.3277 | 495.9141 | 217.1509 | 478.937 | 267.1776 | 77.516
2877.2542 | 995.4288 | 602.4619 | 495.3323 | 220.7749 | 479.7407 | 267.328 | 77.5628
2878.2542 | 1002.1177 | 602.6472 | 495.3144 | 212.854 | 480.8312 | 267.6433 | 77.612
2879.2542 | 986.3063 | 602.6768 | 494.872 | 217.7188 | 480.6678 | 267.7061 | 77.654
2880.2542 | 981.4206 | 602.745 | 494.7355 | 221.6167 | 480.4763 | 268.0385 | 77.6993
2881.2542 | 987.9557 | 602.7808 | 494.4602 | 213.0566 | 480.2549 | 268.447 | 77.7375
2882.2542 | 982.8785 | 602.8248 | 494.3807 | 214.281 | 480.7379 | 268.5384 | 77.7882
2883.2542 | 972.0113 | 602.9926 | 494.4696 | 223.9161 | 481.005 | 268.5834 | 77.8297
2884.2542 | 970.7461 | 603.202 | 494.2939 | 223.7075 | 482.2746 | 269.1355 | 77.8749
2885.2542 | 971.2311 | 603.3648 | 494.2969 | 222.6177 | 482.7374 | 268.9324 | 77.9234
2886.2542 | 972.6741 | 603.5945 | 494.2437 | 223.9948 | 482.6646 | 269.2183 | 77.9597
2887.2542 | 969.0969 | 603.7783 | 494.0426 | 223.5853 | 482.5862 | 269.2477 | 78.0029
2888.2542 | 967.9596 | 603.8031 | 494.096 | 224.8489 | 482.7097 | 269.4676 | 78.0484
2889.2542 | 975.7645 | 603.8182 | 494.2914 | 222.3411 | 482.2055 | 270.1853 | 78.0863
2890.2542 | 974.2362 | 603.8062 | 494.1495 | 221.6656 | 481.488 | 270.111 | 78.1329
2891.2542 | 986.5117 | 603.7981 | 494.1451 | 206.9812 | 481.0891 | 270.5883 | 78.179
2892.2542 | 972.4269 | 603.769 | 494.176 | 220.895 | 481.3595 | 270.4877 | 78.2196
2893.2542 | 985.5942 | 603.5963 | 494.0771 | 209.4967 | 480.9074 | 270.1263 | 78.2477
2894.2542 | 961.6203 | 603.5132 | 493.8448 | 237.3199 | 480.7783 | 270.335 | 78.299
2895.2542 | 1002.9305 | 603.406 | 493.7616 | 193.7723 | 481.6793 | 270.4312 | 78.3451
2896.2542 | 992.4815 | 603.3826 | 493.2677 | 202.5473 | 481.4136 | 271.1045 | 78.3868
2897.2542 | 637.183 | 603.4752 | 490.9531 | 576.49 | 480.4912 | 273.0897 | 78.4165
2898.2542 | 634.3507 | 603.5282 | 490.5861 | 575.1434 | 480.627 | 273.3437 | 78.4479
2899.2542 | 640.2605 | 603.4978 | 489.5889 | 574.9561 | 480.7763 | 273.5479 | 78.4877
2900.2542 | 642.3479 | 603.5288 | 488.426 | 572.2959 | 482.23 | 273.6219 | 78.5393
2901.2542 | 647.4343 | 603.5405 | 487.9602 | 572.8862 | 482.7493 | 274.3218 | 78.5823
2902.2542 | 644.9193 | 603.6694 | 487.7389 | 572.0957 | 482.7685 | 274.5305 | 78.6161
2903.2542 | 650.2567 | 603.6067 | 486.8092 | 574.0716 | 483.0381 | 274.3566 | 78.6653
2904.2542 | 649.8246 | 603.5614 | 486.6535 | 571.2601 | 482.7375 | 274.5079 | 78.7077
2905.2542 | 647.2211 | 603.5362 | 486.2313 | 570.8392 | 484.041 | 274.8587 | 78.7553
2906.2542 | 652.0533 | 603.4628 | 485.9212 | 569.8407 | 483.5698 | 275.3087 | 78.7965
2907.2542 | 654.0721 | 603.2782 | 486.4355 | 570.5017 | 483.2674 | 275.3554 | 78.8411
2908.2542 | 656.8249 | 603.3767 | 487.4521 | 572.2366 | 483.1063 | 275.6333 | 78.8842
2909.2542 | 656.2278 | 603.5649 | 488.6662 | 572.0259 | 482.644 | 275.7703 | 78.9238
2910.2542 | 657.2178 | 603.7055 | 490.4715 | 568.2272 | 482.3862 | 276.2638 | 78.9641
2911.2542 | 650.4627 | 603.8401 | 491.8962 | 571.4951 | 482.1628 | 276.1168 | 79.0048
2912.2542 | 651.4003 | 603.8247 | 492.7864 | 572.342 | 482.3209 | 275.9836 | 79.043
2913.2542 | 651.7608 | 603.6952 | 493.587 | 570.5249 | 485.1186 | 276.4618 | 79.0896
2914.2542 | 651.5367 | 603.5311 | 494.3112 | 568.9426 | 485.7432 | 276.6497 | 79.1252
2915.2542 | 649.1138 | 603.4197 | 494.6574 | 570.3002 | 486.1104 | 276.451 | 79.1669
2916.2542 | 646.2222 | 603.5601 | 494.9896 | 577.4425 | 487.4766 | 276.7544 | 79.2097
2917.2542 | 650.5563 | 603.7962 | 495.5662 | 577.6167 | 487.327 | 277.1645 | 79.2567
2918.2542 | 645.827 | 603.9631 | 495.8253 | 576.9904 | 488.3732 | 277.2856 | 79.2997
2919.2542 | 644.9961 | 604.1537 | 496.1699 | 576.721 | 488.7361 | 277.5166 | 79.3365
2920.2542 | 646.419 | 604.3002 | 496.3048 | 576.0953 | 489.3086 | 277.7098 | 79.3731
2921.2542 | 647.4999 | 604.4575 | 496.1311 | 573.02 | 489.3561 | 277.7859 | 79.4208
2922.2542 | 645.3095 | 604.4359 | 496.042 | 571.9689 | 489.022 | 277.8963 | 79.4629
2923.2542 | 649.8535 | 604.4193 | 495.9632 | 573.9991 | 489.1229 | 278.6191 | 79.4969
2924.2542 | 649.5485 | 604.4896 | 495.8017 | 575.4099 | 489.1196 | 278.6715 | 79.5444
2925.2542 | 647.8427 | 604.6027 | 495.5691 | 575.2541 | 489.1846 | 278.9353 | 79.5784
2926.2542 | 647.8727 | 604.5682 | 495.5951 | 575.1988 | 488.7641 | 279.0931 | 79.621
2927.2542 | 647.0649 | 604.4657 | 495.873 | 574.8624 | 488.6057 | 278.8581 | 79.6633
2928.2542 | 649.2967 | 604.5594 | 496.0333 | 574.7385 | 488.5986 | 278.9608 | 79.7003
2929.2542 | 649.3965 | 604.5686 | 495.8939 | 570.7803 | 488.6762 | 279.2427 | 79.7485
2930.2542 | 649.0858 | 604.6575 | 495.8322 | 571.7809 | 488.4855 | 279.5709 | 79.7995
2931.2542 | 644.2424 | 604.8459 | 495.8383 | 575.2947 | 488.3691 | 279.788 | 79.8483
2932.2542 | 642.3706 | 604.8979 | 496.1015 | 575.2757 | 487.542 | 279.637 | 79.8855
2933.2542 | 641.6716 | 605.0233 | 496.2847 | 575.7865 | 487.3367 | 279.8643 | 79.9219
2934.2542 | 636.3964 | 605.1831 | 496.4872 | 579.1509 | 487.2445 | 279.9727 | 79.9819
2935.2542 | 642.9249 | 605.298 | 496.6345 | 577.0359 | 487.4254 | 280.2635 | 80.0294
2936.2542 | 643.6139 | 605.4036 | 496.9454 | 580.2984 | 487.6049 | 280.8844 | 80.0735
2937.2542 | 642.571 | 605.3547 | 497.0634 | 583.7957 | 487.3303 | 281.2896 | 80.1167
2938.2542 | 640.1916 | 605.4003 | 496.958 | 587.2873 | 487.8926 | 281.363 | 80.1605
2939.2542 | 641.1122 | 605.2849 | 496.5769 | 587.8682 | 488.0544 | 281.6086 | 80.199
2940.2542 | 643.2326 | 605.2509 | 496.1914 | 588.624 | 487.9637 | 281.8413 | 80.2404
2941.2542 | 644.9301 | 605.3318 | 495.9426 | 590.8886 | 487.714 | 281.6054 | 80.2903
2942.2542 | 645.7227 | 605.3374 | 495.9308 | 592.8599 | 487.7416 | 281.8657 | 80.3322
2943.2542 | 646.5302 | 605.3172 | 495.773 | 591.9975 | 487.8663 | 281.5719 | 80.3845
2944.2542 | 643.4252 | 605.4253 | 495.637 | 591.895 | 488.0725 | 281.9075 | 80.423
2945.2542 | 639.3312 | 605.6383 | 495.4402 | 590.3722 | 487.9924 | 282.3626 | 80.4706
2946.2542 | 633.4852 | 605.7506 | 494.9741 | 592.6624 | 487.7075 | 282.6384 | 80.5177
2947.2542 | 632.991 | 605.897 | 494.2688 | 593.4115 | 488.148 | 282.4125 | 80.5531
2948.2542 | 630.0016 | 606.2828 | 493.8579 | 595.4349 | 488.3775 | 282.9102 | 80.5996
2949.2542 | 626.3872 | 606.4687 | 493.3097 | 597.6021 | 488.0926 | 282.7589 | 80.6385
2950.2542 | 618.5136 | 606.6339 | 492.9021 | 600.4426 | 488.4417 | 282.686 | 80.6841
2951.2542 | 609.936 | 606.5723 | 492.2736 | 609.2062 | 488.8295 | 282.6375 | 80.7289
2952.2542 | 611.1701 | 606.5881 | 491.8158 | 613.5319 | 489.212 | 282.7669 | 80.7744
2953.2542 | 613.4116 | 606.7493 | 491.3988 | 615.2891 | 490.2212 | 283.1132 | 80.8052
2954.2542 | 609.3626 | 606.8671 | 490.9031 | 619.0448 | 490.8178 | 282.9871 | 80.8528
2955.2542 | 605.3775 | 607.2308 | 490.6792 | 623.2312 | 491.132 | 283.0429 | 80.899
2956.2542 | 604.7741 | 607.2769 | 490.0796 | 628.0508 | 491.9823 | 282.8607 | 80.9348
2957.2542 | 601.6221 | 607.3319 | 489.6673 | 631.2035 | 491.7389 | 282.6604 | 80.9892
2958.2542 | 596.4572 | 607.4926 | 489.2435 | 633.9407 | 492.3948 | 283.031 | 81.036
2959.2542 | 598.5701 | 607.7511 | 488.7456 | 637.1988 | 493.2764 | 283.1492 | 81.0821
2960.2542 | 595.8069 | 607.9143 | 488.2533 | 639.8437 | 493.95 | 282.9306 | 81.1241
2961.2542 | 590.8531 | 607.8955 | 487.8822 | 643.8596 | 493.612 | 283.2377 | 81.1655
2962.2542 | 592.7364 | 607.8822 | 487.3988 | 644.4915 | 493.3331 | 283.2722 | 81.2138
2963.2542 | 590.0991 | 607.7576 | 487.0529 | 645.5308 | 493.5669 | 283.651 | 81.2466
2964.2542 | 580.9829 | 607.54 | 486.6458 | 649.2202 | 493.3695 | 283.8586 | 81.2978
2965.2542 | 577.0639 | 607.467 | 486.3254 | 651.8427 | 492.8766 | 284.1149 | 81.3366
2966.2542 | 573.3909 | 607.4983 | 486.0531 | 653.2498 | 492.8359 | 284.0497 | 81.3815
2967.2542 | 570.7109 | 607.5813 | 485.8262 | 654.8518 | 493.4114 | 283.9238 | 81.4284
2968.2542 | 566.6035 | 607.6835 | 485.6923 | 655.789 | 494.0331 | 284.1053 | 81.469
2969.2542 | 565.9713 | 607.711 | 485.6307 | 660.883 | 494.665 | 284.5382 | 81.5132
2970.2542 | 565.2166 | 607.627 | 485.5681 | 664.662 | 495.1133 | 284.7724 | 81.5577
2971.2542 | 567.2661 | 607.6441 | 485.4711 | 665.564 | 495.6278 | 284.8015 | 81.5918
2972.2542 | 564.9776 | 607.5569 | 485.458 | 666.6273 | 495.5281 | 284.8982 | 81.6404
2973.2542 | 562.9492 | 607.4517 | 485.2851 | 667.0837 | 496.35 | 285.208 | 81.6737
2974.2542 | 562.5921 | 607.3487 | 485.06 | 668.1722 | 496.7961 | 285.1301 | 81.7255
2975.2542 | 567.7056 | 607.4523 | 484.8512 | 667.7341 | 496.9163 | 285.0995 | 81.7678
2976.2542 | 571.1283 | 607.5521 | 484.6231 | 667.9156 | 496.6861 | 285.1653 | 81.8066
2977.2542 | 569.0996 | 607.6516 | 484.5589 | 668.887 | 496.9554 | 285.4237 | 81.8561
2978.2542 | 574.1022 | 607.7163 | 484.3202 | 667.4238 | 497.1053 | 285.5405 | 81.8913
2979.2542 | 574.2861 | 607.8254 | 483.9835 | 668.0136 | 497.277 | 285.7463 | 81.9275
2980.2542 | 572.7891 | 608.0064 | 483.7346 | 669.4789 | 497.3028 | 286.0153 | 81.9714
2981.2542 | 570.5567 | 608.1319 | 483.6077 | 670.3628 | 496.9569 | 286.0904 | 82.0083
2982.2542 | 567.4705 | 608.245 | 483.3362 | 672.4176 | 497.1055 | 286.3775 | 82.0562
2983.2542 | 563.6947 | 608.2514 | 483.1592 | 674.3482 | 497.2336 | 286.606 | 82.0875
2984.2542 | 555.782 | 608.0945 | 482.9712 | 679.91 | 497.1061 | 286.9043 | 82.1197
2985.2542 | 557.7483 | 608.1498 | 482.7688 | 681.395 | 497.2791 | 287.2992 | 82.1633
2986.2542 | 557.2791 | 608.2144 | 482.5269 | 684.4573 | 497.3253 | 287.2814 | 82.2027
2987.2542 | 558.2717 | 608.4521 | 482.2064 | 686.2562 | 497.8974 | 287.4303 | 82.2419
2988.2542 | 565.7792 | 608.6205 | 481.8533 | 686.9406 | 497.9616 | 287.509 | 82.2797
2989.2542 | 557.3816 | 608.7788 | 481.6097 | 690.969 | 498.8018 | 287.3149 | 82.3227
2990.2542 | 555.2583 | 608.8062 | 481.2941 | 691.779 | 499.3349 | 288.0782 | 82.3559
2991.2542 | 551.2984 | 608.7908 | 481.0573 | 694.894 | 499.6694 | 287.9451 | 82.4017
2992.2542 | 545.8699 | 608.8422 | 480.7504 | 701.992 | 499.974 | 288.3405 | 82.4358
2993.2542 | 539.9619 | 608.979 | 480.3894 | 705.9349 | 500.0966 | 288.2417 | 82.4703
2994.2542 | 533.2629 | 609.1493 | 480.1278 | 709.1467 | 500.6569 | 288.5461 | 82.5619
2995.2542 | 534.9191 | 609.3648 | 479.8274 | 711.5627 | 500.8562 | 288.6682 | 82.6043
2996.2542 | 530.8646 | 609.6099 | 479.6464 | 715.8687 | 500.6236 | 288.6961 | 82.6383
2997.2542 | 527.7186 | 609.8764 | 479.6439 | 720.305 | 500.4949 | 288.8322 | 82.6813
2998.2542 | 524.3436 | 610.043 | 479.4485 | 722.4566 | 500.8375 | 288.9622 | 82.7146
2999.2542 | 517.7149 | 610.0501 | 479.0032 | 724.9538 | 500.9212 | 289.0782 | 82.7618
3000.2542 | 514.6675 | 610.1105 | 478.6244 | 729.2021 | 501.1221 | 289.5683 | 82.7973
3001.2542 | 513.3185 | 610.0442 | 478.3645 | 727.1573 | 500.9269 | 289.7433 | 82.8463
3002.2542 | 505.7798 | 609.9829 | 478.0904 | 732.3327 | 500.4822 | 289.7588 | 82.878
3003.2542 | 502.6459 | 609.7843 | 477.8864 | 734.5563 | 500.4387 | 289.8405 | 82.9187
3004.2542 | 505.3035 | 609.8519 | 477.8303 | 734.4098 | 500.2652 | 289.7679 | 82.9584
3005.2542 | 500.9919 | 609.9116 | 477.773 | 740.5575 | 500.7766 | 290.4327 | 82.9978
3006.2542 | 494.816 | 609.8724 | 477.5931 | 749.7545 | 501.1274 | 290.4808 | 83.0482
3007.2542 | 489.4438 | 609.769 | 477.3581 | 754.5715 | 501.4184 | 290.6987 | 83.0861
3008.2542 | 484.6475 | 609.576 | 477.0878 | 760.0694 | 501.3033 | 290.2919 | 83.1287
3009.2542 | 481.0008 | 609.3796 | 476.9419 | 761.7376 | 501.7613 | 291.0835 | 83.159
3010.2542 | 480.3626 | 609.4144 | 476.9186 | 765.7576 | 501.4475 | 291.3418 | 83.2111
3011.2542 | 477.3497 | 609.2996 | 476.8136 | 768.773 | 501.5752 | 291.4061 | 83.2402
3012.2542 | 469.2499 | 609.1019 | 476.7082 | 776.4114 | 501.6127 | 291.6918 | 83.282
3013.2542 | 464.0686 | 608.8587 | 476.6407 | 778.2251 | 502.191 | 291.8289 | 83.3266
3014.2542 | 460.4216 | 608.8316 | 476.5027 | 782.631 | 502.4724 | 291.6688 | 83.3722
3015.2542 | 450.1221 | 608.8854 | 476.4086 | 791.6403 | 502.7026 | 292.2015 | 83.4153
3016.2542 | 444.9322 | 608.8475 | 476.328 | 796.0132 | 502.811 | 292.4742 | 83.4563
3017.2542 | 435.9042 | 608.8329 | 476.2307 | 805.272 | 502.8384 | 292.4641 | 83.5001
3018.2542 | 432.0875 | 608.7724 | 476.2322 | 808.3152 | 503.0362 | 292.6597 | 83.5459
3019.2542 | 432.1928 | 608.9285 | 476.1622 | 811.6458 | 502.9322 | 293.0216 | 83.5887
3020.2542 | 443.3951 | 609.127 | 476.0731 | 798.6439 | 503.087 | 293.0781 | 83.6382
3021.2542 | 443.2204 | 609.3995 | 475.9426 | 799.0563 | 503.1323 | 292.9902 | 83.6779
3022.2542 | 439.676 | 609.5751 | 475.5854 | 804.4382 | 503.2598 | 293.4862 | 83.7192
3023.2542 | 441.0796 | 609.7764 | 475.0164 | 810.0643 | 503.3393 | 293.7814 | 83.7622
3024.2542 | 441.9013 | 609.8859 | 474.6627 | 811.1393 | 503.9248 | 293.3 | 83.823
3025.2542 | 436.9417 | 610.0304 | 474.2961 | 815.0929 | 503.8055 | 293.9232 | 83.8526
3026.2542 | 435.8203 | 610.1175 | 474.071 | 815.3414 | 504.5598 | 294.2116 | 83.9086
3027.2542 | 434.3995 | 610.3146 | 473.8478 | 817.6096 | 505.0525 | 294.3384 | 83.9514
3028.2542 | 428.046 | 610.4547 | 473.6477 | 825.3991 | 505.3666 | 294.5939 | 83.9983
3029.2542 | 419.7469 | 610.58 | 473.4568 | 833.5922 | 506.3568 | 294.5937 | 84.0348
3030.2542 | 415.8025 | 610.605 | 473.3262 | 834.0951 | 506.5126 | 294.6935 | 84.0725
3031.2542 | 412.7318 | 610.8619 | 473.28 | 834.2453 | 506.6514 | 295.2362 | 84.1081
3032.2542 | 414.1807 | 610.948 | 473.2012 | 835.1617 | 506.7397 | 295.5283 | 84.1664
3033.2542 | 412.7552 | 611.1594 | 473.2117 | 836.5565 | 506.8537 | 295.6062 | 84.2076
3034.2542 | 415.6787 | 611.3071 | 473.3407 | 837.5432 | 507.143 | 295.7452 | 84.2465
3035.2542 | 420.7244 | 611.5923 | 473.4354 | 836.2104 | 507.0685 | 296.2121 | 84.2814
3036.2542 | 421.097 | 611.8667 | 473.5223 | 837.8115 | 507.4291 | 296.3168 | 84.3164
3037.2542 | 416.492 | 612.2233 | 473.5079 | 839.757 | 507.8131 | 296.2511 | 84.3611
3038.2542 | 409.4337 | 612.4555 | 473.5445 | 845.3282 | 508.927 | 296.7179 | 84.3974
3039.2542 | 413.1093 | 612.7151 | 473.583 | 841.0008 | 508.9655 | 296.8788 | 84.4384
3040.2542 | 449.6656 | 612.984 | 473.6778 | 798.707 | 509.1642 | 296.7223 | 84.4694
3041.2542 | 460.2358 | 613.2345 | 473.7686 | 789.091 | 508.9779 | 297.1014 | 84.5222
3042.2542 | 486.6507 | 613.5727 | 473.9275 | 760.4722 | 509.1936 | 297.3133 | 84.5483
3043.2542 | 488.4309 | 613.8983 | 474.1084 | 756.2643 | 509.5137 | 297.2973 | 84.5998
3044.2542 | 484.1177 | 614.4224 | 474.2827 | 760.5286 | 509.7153 | 297.4304 | 84.6365
3045.2542 | 488.5628 | 614.6222 | 474.3957 | 754.5756 | 509.5591 | 297.5883 | 84.6871
3046.2542 | 508.0359 | 614.832 | 474.5542 | 733.3279 | 509.3348 | 297.7712 | 84.7302
3047.2542 | 519.0327 | 614.9062 | 474.6113 | 722.4444 | 508.8584 | 297.9586 | 84.7666
3048.2542 | 529.0256 | 614.9901 | 474.7273 | 711.1427 | 509.0663 | 298.172 | 84.8102
3049.2542 | 546.2069 | 615.0098 | 474.8081 | 690.0447 | 509.267 | 298.4897 | 84.8426
3050.2542 | 556.7892 | 615.0781 | 474.8166 | 678.7654 | 509.4405 | 298.3728 | 84.8933
3051.2542 | 578.6622 | 615.1499 | 474.7127 | 658.3757 | 509.1179 | 298.6758 | 84.9358
3052.2542 | 571.2602 | 615.0664 | 474.6937 | 663.536 | 509.5185 | 298.9018 | 84.9705
3053.2542 | 594.9075 | 614.833 | 474.7445 | 635.6108 | 510.3964 | 298.9297 | 85.0169
3054.2542 | 619.5222 | 614.6643 | 474.7948 | 608.0555 | 509.5652 | 298.6146 | 85.0484
3055.2542 | 640.6092 | 614.6666 | 474.8795 | 584.8603 | 509.1058 | 298.9596 | 85.0955
3056.2542 | 630.1576 | 614.4124 | 474.9324 | 596.2349 | 509.2436 | 299.3731 | 85.1438
3057.2542 | 634.0626 | 614.5219 | 475.0459 | 589.5206 | 509.4103 | 299.0351 | 85.179
3058.2542 | 648.2836 | 614.4009 | 475.1441 | 572.667 | 509.5449 | 299.5975 | 85.2268
3059.2542 | 663.4398 | 614.4745 | 475.156 | 555.2499 | 509.3532 | 299.9493 | 85.2548
3060.2542 | 676.0429 | 614.4821 | 475.2664 | 545.027 | 509.4569 | 299.7334 | 85.3062
3061.2542 | 688.2886 | 614.4945 | 475.4258 | 529.4258 | 509.003 | 300.2298 | 85.3419
3062.2542 | 693.2529 | 614.7171 | 475.6115 | 522.9644 | 508.487 | 300.2836 | 85.3809
3063.2542 | 698.0473 | 614.5659 | 475.7386 | 517.867 | 508.4056 | 300.5583 | 85.4222
3064.2542 | 699.4317 | 614.4945 | 475.9235 | 515.5524 | 508.6082 | 300.3834 | 85.4604
3065.2542 | 702.7554 | 614.4123 | 476.0793 | 510.7273 | 508.9582 | 300.6133 | 85.5015
3066.2542 | 712.4273 | 614.4752 | 476.2895 | 502.5133 | 508.7707 | 300.6076 | 85.5414
3067.2542 | 695.7954 | 614.5466 | 476.4376 | 517.9335 | 509.0582 | 300.876 | 85.5797
3068.2542 | 709.9137 | 614.7161 | 476.5573 | 502.7869 | 509.0974 | 301.613 | 85.618
3069.2542 | 725.1032 | 614.7976 | 476.6785 | 485.3891 | 509.1548 | 301.5527 | 85.6593
3070.2542 | 737.269 | 614.7151 | 476.8053 | 472.1133 | 509.3576 | 301.5818 | 85.7046
3071.2542 | 761.3606 | 614.6068 | 476.9743 | 451.8631 | 509.2004 | 301.6721 | 85.7454
3072.2542 | 804.6519 | 614.8263 | 477.1511 | 411.2779 | 508.6716 | 301.5413 | 85.79
3073.2542 | 817.887 | 614.8291 | 477.3759 | 396.0012 | 508.2777 | 301.6495 | 85.8213
3074.2542 | 839.313 | 614.903 | 477.5892 | 370.3311 | 508.4732 | 301.9716 | 85.861
3075.2542 | 866.4673 | 615.0107 | 477.777 | 341.771 | 508.8918 | 301.9173 | 85.901
3076.2542 | 868.8017 | 614.9725 | 477.8889 | 334.4662 | 509.4706 | 302.1637 | 85.9513
3077.2542 | 885.9181 | 614.9197 | 478.0631 | 314.0451 | 509.3641 | 302.1425 | 85.9871
3078.2542 | 887.6904 | 614.8318 | 478.317 | 311.7524 | 509.2393 | 302.4053 | 86.0242
3079.2542 | 904.1825 | 614.8329 | 478.4346 | 292.2555 | 509.6241 | 302.1165 | 86.0704
3080.2542 | 915.9669 | 614.6736 | 478.4968 | 278.864 | 509.1798 | 302.8168 | 86.1112
3081.2542 | 912.8253 | 614.7228 | 478.6571 | 282.0143 | 509.1588 | 303.0622 | 86.1546
3082.2542 | 922.2071 | 614.4893 | 478.798 | 271.4397 | 509.1279 | 302.8684 | 86.1884
3083.2542 | 925.7914 | 614.2338 | 478.9661 | 268.7052 | 509.6156 | 303.1578 | 86.2288
3084.2542 | 945.8445 | 614.4546 | 479.1634 | 252.0057 | 509.9582 | 303.5244 | 86.2829
3085.2542 | 978.8438 | 614.3452 | 479.3148 | 216.0287 | 510.5533 | 303.7397 | 86.3167
3086.2542 | 994.7458 | 614.5912 | 479.4114 | 198.1466 | 510.8533 | 303.6303 | 86.3546
3087.2542 | 1041.393 | 614.7842 | 479.575 | 153.057 | 510.2955 | 303.374 | 86.3952
3088.2542 | 1072.3762 | 614.7763 | 479.7744 | 120.9895 | 510.3674 | 303.8754 | 86.431
3089.2542 | 1085.0229 | 614.9967 | 479.9057 | 110.8441 | 510.8311 | 303.9482 | 86.473
3090.2542 | 1107.1232 | 615.1305 | 480.0276 | 88.716 | 511.3241 | 304.2876 | 86.5028
3091.2542 | 1118.0645 | 615.3064 | 480.1146 | 76.9205 | 511.7793 | 304.2443 | 86.5505
3092.2542 | 1136.7138 | 615.5161 | 480.2562 | 59.6461 | 511.6602 | 304.4498 | 86.5811
3093.2542 | 1150.4263 | 615.6241 | 480.3551 | 48.9247 | 511.5354 | 304.6639 | 86.6215
3094.2542 | 1152.9346 | 616.1538 | 480.5036 | 46.3901 | 511.0306 | 304.2695 | 86.6635
3095.2542 | 1160.1516 | 616.2654 | 480.6261 | 39.0047 | 511.1144 | 304.5321 | 86.6832
3096.2542 | 1147.4681 | 616.4024 | 480.772 | 50.6939 | 510.9563 | 305.0922 | 86.7289
3097.2542 | 1158.9373 | 616.4522 | 480.8388 | 40.5045 | 511.1257 | 305.357 | 86.769
3098.2542 | 1047.1212 | 616.4512 | 480.8758 | 151.9083 | 510.7577 | 305.5055 | 86.8061
3099.2542 | NaN | 616.4086 | 479.1123 | 1245.0033 | 510.2612 | 308.2978 | 86.8257
3100.2542 | NaN | 616.8725 | 479.6664 | 1245.0039 | 510.1065 | 307.6855 | 86.8477
3101.2542 | 592.6687 | 616.7662 | 480.6964 | 641.5808 | 510.6028 | 306.6417 | 86.899
3102.2542 | 242.5691 | 616.6758 | 480.421 | 1034.596 | 510.9522 | 307.3129 | 86.9451
3103.2542 | 291.7342 | 616.7458 | 480.6357 | 980.6954 | 510.8202 | 307.1739 | 87.0046
3104.2542 | 693.7044 | 616.851 | 481.2824 | 536.6894 | 510.9795 | 306.9544 | 87.0222
3105.2542 | 181.0933 | 616.7535 | 480.7488 | 1097.5341 | 511.3181 | 308.1521 | 87.0628
3106.2542 | 340.1952 | 616.8979 | 480.4074 | 1245.0122 | 511.3002 | 308.7122 | 87.0939
3107.2542 | NaN | 616.8428 | 479.8929 | 1245.0137 | 511.0899 | 309.1766 | 87.1306
3108.2542 | NaN | 616.6895 | 479.106 | 1245.015 | 511.3127 | 311.0843 | 87.1614
3109.2542 | NaN | 616.6159 | 479.4956 | 1245.0167 | 511.7571 | 311.2116 | 87.1885
3110.2542 | NaN | 616.5531 | 480.264 | 1245.0184 | 511.7716 | 310.8282 | 87.2325
3111.2542 | NaN | 617.0339 | 481.1079 | 1245.0183 | 511.2821 | 309.8663 | 87.2793
3112.2542 | NaN | 617.1345 | 481.1714 | 1245.0199 | 511.0967 | 310.5154 | 87.3277
3113.2542 | NaN | 617.1388 | 481.0384 | 1245.0207 | 510.8565 | 310.2899 | 87.358
3114.2542 | NaN | 617.1798 | 480.7179 | 1245.0226 | 511.763 | 310.918 | 87.3966
3115.2542 | NaN | 617.1641 | 481.2087 | 1245.024 | 512.4414 | 310.6186 | 87.4428
3116.2542 | NaN | 617.4759 | 481.6206 | 1245.0255 | 512.2577 | 310.8247 | 87.4788
3117.2542 | NaN | 617.3673 | 481.8001 | 1245.0257 | 512.2375 | 311.3254 | 87.504
3118.2542 | 143.7798 | 617.1883 | 482.7033 | 1245.0279 | 512.1313 | 310.4863 | 87.5449
3119.2542 | 73.9933 | 617.1418 | 483.1007 | 1218.1656 | 511.8649 | 310.277 | 87.5714
3120.2542 | 109.5647 | 616.9558 | 482.9993 | 1245.0302 | 511.7423 | 310.2349 | 87.6232
3121.2542 | NaN | 616.843 | 482.8913 | 1245.0326 | 511.4796 | 311.1313 | 87.6618
3122.2542 | NaN | 616.7851 | 482.3495 | 1245.0332 | 511.7105 | 312.3709 | 87.6915
3123.2542 | NaN | 616.5926 | 482.9056 | 1245.0339 | 510.9905 | 311.9131 | 87.7258
3124.2542 | NaN | 616.9018 | 481.7745 | 1245.0365 | 510.8333 | 313.1185 | 87.7354
3125.2542 | NaN | 616.9104 | 481.8329 | 1245.0377 | 510.3278 | 312.9568 | 87.7982
3126.2542 | NaN | 616.6286 | 481.4748 | 1245.0393 | 510.9394 | 313.815 | 87.8299
3127.2542 | NaN | 616.3862 | 480.5016 | 1245.0401 | 511.1074 | 314.7853 | 87.8473
3128.2542 | NaN | 616.4209 | 483.3777 | 1245.041 | 510.2661 | 312.4819 | 87.8904
3129.2542 | 398.8605 | 616.2615 | 484.6944 | 840.1181 | 509.7121 | 311.1016 | 87.9225
3130.2542 | 1041.0009 | 616.5513 | 485.8922 | 162.0134 | 509.7277 | 310.7537 | 87.9754
3131.2542 | 1244.7393 | 616.4991 | 487.0373 | NaN | 509.1311 | 309.4833 | 88.0104
3132.2542 | 1244.7405 | 616.7898 | 488.053 | NaN | 509.2398 | 308.7569 | 88.0517
3133.2542 | 1244.7425 | 616.9152 | 487.3437 | NaN | 508.9919 | 309.6947 | 88.095
3134.2542 | 910.385 | 616.918 | 485.8519 | 284.6117 | 509.5832 | 311.6103 | 88.1118
3135.2542 | 1244.745 | 616.9681 | 487.9686 | NaN | 509.7044 | 309.8218 | 88.1559
3136.2542 | 1244.7463 | 616.5971 | 487.0439 | 260.072 | 510.0569 | 310.7271 | 88.1865
3137.2542 | 1244.7477 | 616.4677 | 487.4047 | NaN | 510.3567 | 311.0793 | 88.215
3138.2542 | 1234.7047 | 616.5823 | 487.3712 | -14.6662 | 509.8537 | 311.6238 | 88.2694
3139.2542 | 953.9499 | 616.547 | 486.7829 | 241.7746 | 510.0994 | 312.3049 | 88.2854
3140.2542 | 1244.7521 | 616.6593 | 489.6464 | NaN | 509.3467 | 310.0716 | 88.3236
3141.2542 | 1244.7525 | 616.7711 | 490.0533 | NaN | 509.1362 | 309.5337 | 88.359
3142.2542 | 1244.7543 | 616.4574 | 490.0618 | NaN | 509.2091 | 310.2651 | 88.3944
3143.2542 | 1244.7558 | 616.4853 | 490.854 | NaN | 509.4782 | 310.0002 | 88.4434
3144.2542 | 1244.7569 | 616.5879 | 490.5249 | NaN | 509.1276 | 310.3288 | 88.477
3145.2542 | 1244.7579 | 616.4884 | 490.7607 | NaN | 509.0595 | 310.4695 | 88.4916
3146.2542 | 1244.7596 | 616.5454 | 491.4585 | NaN | 509.6694 | 309.7568 | 88.545
3147.2542 | 1244.7603 | 616.5532 | 491.4077 | NaN | 509.117 | 309.8268 | 88.5786
3148.2542 | 1244.7619 | 616.657 | 491.4288 | NaN | 508.5884 | 310.4606 | 88.6037
3149.2542 | 1244.7634 | 616.4751 | 491.9709 | NaN | 508.8054 | 310.814 | 88.6378
3150.2542 | 1244.7636 | 616.5216 | 493.452 | NaN | 508.7058 | 310.7945 | 88.6785
3151.2542 | 1244.7655 | 616.3391 | 493.5279 | NaN | 508.8706 | 311.3946 | 88.718
3152.2542 | 1244.7666 | 616.1165 | 493.8304 | NaN | 508.3403 | 311.6014 | 88.7538
3153.2542 | 1244.768 | 616.1449 | 493.835 | NaN | 508.1607 | 311.6054 | 88.7932
3154.2542 | 1244.7684 | 616.1684 | 494.0114 | NaN | 508.6251 | 311.9358 | 88.8301
3155.2542 | 1244.7701 | 616.2372 | 493.8593 | NaN | 508.4148 | 312.1121 | 88.86
3156.2542 | 1244.772 | 616.3341 | 494.0717 | NaN | 508.1991 | 312.5395 | 88.8975
3157.2542 | 1244.7729 | 616.2782 | 494.2382 | NaN | 508.3272 | 312.2243 | 88.9366
3158.2542 | 1244.7743 | 616.5236 | 494.4967 | NaN | 508.9446 | 312.8293 | 88.9714
3159.2542 | 1244.7756 | 616.3263 | 494.8382 | NaN | 509.2602 | 312.7259 | 89.0051
3160.2542 | 1244.7768 | 616.266 | 494.7152 | NaN | 509.2352 | 313.0526 | 89.0322
3161.2542 | 1244.7789 | 616.3858 | 495.1805 | NaN | 508.9028 | 313.8476 | 89.0645
3162.2542 | 1244.7799 | 616.5526 | 494.8248 | NaN | 509.3986 | 313.9709 | 89.0886
3163.2542 | 1244.7818 | 616.4392 | 494.9531 | NaN | 509.0485 | 313.8789 | 89.1162
3164.2542 | 1244.7834 | 616.2799 | 494.7319 | NaN | 508.8725 | 314.463 | 89.1476
3165.2542 | 1244.7847 | 616.0948 | 494.8631 | NaN | 508.5117 | 314.2747 | 89.1676
3166.2542 | 1244.785 | 615.8274 | 495.1863 | NaN | 508.4545 | 314.8693 | 89.1973
3167.2542 | 1244.7857 | 615.636 | 495.4167 | NaN | 508.6963 | 314.8083 | 89.2286
3168.2542 | 1244.7872 | 615.618 | 495.4825 | NaN | 509.0708 | 315.1495 | 89.2561
3169.2542 | 1244.7892 | 615.6763 | 495.781 | NaN | 509.1386 | 315.398 | 89.3038
3170.2542 | 1244.7907 | 615.9753 | 495.9334 | NaN | 509.0408 | 316.8866 | 89.3348
3171.2542 | 1244.7922 | 615.9327 | 496.3274 | NaN | 508.6281 | 316.3199 | 89.3666
3172.2542 | 1244.7931 | 615.8939 | 497.5393 | NaN | 508.0576 | 316.5148 | 89.4057
3173.2542 | 1244.7933 | 616.093 | 497.5035 | NaN | 507.5094 | 316.5776 | 89.4409
3174.2542 | 1244.7946 | 615.9138 | 497.528 | NaN | 507.4609 | 317.0328 | 89.4746
3175.2542 | 1244.7967 | 615.786 | 497.7642 | NaN | 506.8115 | 317.2473 | 89.5109
3176.2542 | 1244.7982 | 615.754 | 497.8386 | NaN | 506.705 | 317.482 | 89.5533
3177.2542 | 1244.7992 | 615.816 | 497.7858 | NaN | 506.6663 | 317.4749 | 89.5864
3178.2542 | 1244.7995 | 615.9027 | 497.8337 | NaN | 507.0111 | 317.9255 | 89.6431
3179.2542 | 1244.8019 | 615.8241 | 497.649 | NaN | 507.7515 | 317.9789 | 89.6815
3180.2542 | 1244.8016 | 615.5767 | 497.465 | NaN | 508.041 | 318.0198 | 89.7189
3181.2542 | 1244.8036 | 615.4481 | 497.1752 | NaN | 508.1147 | 318.5366 | 89.754
3182.2542 | 1244.8051 | 615.4352 | 497.8516 | NaN | 507.9545 | 318.3082 | 89.8001
3183.2542 | 1244.8061 | 615.5486 | 498.6429 | NaN | 507.0893 | 318.6043 | 89.8336
3184.2542 | 1244.8078 | 615.3256 | 498.4248 | NaN | 508.3239 | 318.6131 | 89.8721
3185.2542 | 1244.8089 | 615.2715 | 499.1645 | NaN | 507.689 | 318.5525 | 89.9121
3186.2542 | 1244.8092 | 614.9722 | 498.853 | NaN | 507.5042 | 319.2474 | 89.9475
3187.2542 | 1244.8114 | 614.868 | 498.9728 | NaN | 507.8447 | 319.9511 | 89.988
3188.2542 | 1244.813 | 614.9568 | 498.5418 | NaN | 507.9901 | 319.6537 | 90.0176
3189.2542 | 1244.8137 | 614.7954 | 498.7434 | NaN | 507.8442 | 319.7021 | 90.046
3190.2542 | 1244.8153 | 614.8868 | 498.0683 | NaN | 507.9433 | 319.8332 | 90.0717
3191.2542 | 1244.8164 | 615.0095 | 499.1154 | NaN | 507.5309 | 320.3633 | 90.1175
3192.2542 | 1244.8164 | 615.0228 | 498.4508 | NaN | 507.3638 | 320.8573 | 90.1222
3193.2542 | 1244.8191 | 615.1165 | 498.2806 | NaN | 507.5395 | 321.0796 | 90.1649
3194.2542 | 1244.8212 | 615.2629 | 501.3999 | NaN | 506.1161 | 320.3614 | 90.197
3195.2542 | 1244.8221 | 614.9649 | 501.5053 | NaN | 505.9512 | 320.2934 | 90.2349
3196.2542 | 1244.8234 | 614.9067 | 501.7985 | NaN | 505.7449 | 320.3322 | 90.2559
3197.2542 | 1244.8252 | 615.1171 | 502.0899 | NaN | 505.2749 | 320.8127 | 90.2832
3198.2542 | 1244.8262 | 614.9217 | 502.0183 | NaN | 504.7492 | 320.8957 | 90.3228
3199.2542 | 1244.8279 | 614.7009 | 502.6991 | NaN | 503.8869 | 321.2031 | 90.3527
3200.2542 | 1244.8275 | 614.5177 | 501.6205 | NaN | 505.0964 | 321.8138 | 90.3755
3201.2542 | 1244.8273 | 614.3358 | 502.0437 | NaN | 504.6992 | 321.5429 | 90.4025
3202.2542 | 1244.8311 | 614.2882 | 503.3526 | NaN | 503.7007 | 321.2276 | 90.4333
3203.2542 | 1244.83 | 614.2696 | 502.1474 | NaN | 504.1172 | 321.8492 | 90.4621
3204.2542 | 1244.8325 | 614.239 | 503.0144 | NaN | 503.2131 | 321.5771 | 90.4994
3205.2542 | 1244.8335 | 614.2429 | 503.8163 | NaN | 502.5939 | 321.0461 | 90.5288
3206.2542 | 1244.8357 | 614.069 | 503.6504 | NaN | 502.007 | 321.4291 | 90.552
3207.2542 | 1244.8372 | 614.357 | 503.5428 | NaN | 501.9893 | 321.4742 | 90.5823
3208.2542 | 1244.8376 | 614.2344 | 504.2759 | NaN | 501.9694 | 321.4297 | 90.6153
3209.2542 | 1244.8387 | 614.1817 | 504.71 | NaN | 501.8449 | 321.797 | 90.6422
3210.2542 | 1244.8408 | 614.1032 | 505.3164 | NaN | 501.7117 | 321.3658 | 90.6801
3211.2542 | 1244.8415 | 614.0184 | 505.2158 | NaN | 501.9105 | 321.8615 | 90.717
3212.2542 | 1244.8434 | 614.031 | 505.2915 | NaN | 502.3053 | 322.3497 | 90.7398
3213.2542 | 1244.8435 | 613.8914 | 505.7144 | NaN | 502.5117 | 322.2113 | 90.7788
3214.2542 | 1244.8454 | 613.5934 | 505.6561 | NaN | 502.4448 | 322.5188 | 90.8087
3215.2542 | 1244.847 | 613.4469 | 504.4833 | NaN | 503.619 | 322.9504 | 90.8496
3216.2542 | 1244.8477 | 613.3116 | 506.2408 | NaN | 503.2596 | 322.1586 | 90.8757
3217.2542 | 1244.8485 | 613.0803 | 505.9058 | NaN | 503.6281 | 322.4941 | 90.901
3218.2542 | 1244.8495 | 612.9559 | 507.501 | NaN | 503.882 | 321.6667 | 90.9214
3219.2542 | 1244.8501 | 612.7829 | 508.0277 | NaN | 503.9385 | 322.117 | 90.9589
3220.2542 | 1244.8512 | 612.4503 | 507.9108 | NaN | 503.8727 | 322.3375 | 90.9898
3221.2542 | 1244.853 | 612.1559 | 507.4386 | NaN | 503.4986 | 322.7692 | 91.0322
3222.2542 | 1244.8545 | 611.9232 | 509.8401 | NaN | 503.5851 | 320.9943 | 91.0538
3223.2542 | 1244.8542 | 611.7554 | 508.5286 | NaN | 503.2977 | 322.5472 | 91.0643
3224.2542 | 1244.8564 | 611.6257 | 510.3504 | NaN | 503.2955 | 321.5805 | 91.1359
3225.2542 | 1244.8575 | 611.5412 | 507.7599 | NaN | 504.2992 | 323.0511 | 91.1457
3226.2542 | 1244.8584 | 611.5539 | 510.0863 | NaN | 503.5922 | 321.8699 | 91.1771
3227.2542 | 1244.8594 | 611.4764 | 510.7027 | NaN | 503.4154 | 322.0011 | 91.1964
3228.2542 | 1244.8595 | 611.6202 | 512.8874 | NaN | 502.9819 | 320.6 | 91.2287
3229.2542 | 1244.8617 | 611.5255 | 513.5967 | NaN | 504.0196 | 320.2684 | 91.2639
3230.2542 | 1244.8635 | 611.4944 | 513.5404 | NaN | 504.1598 | 320.054 | 91.2958
3231.2542 | 1244.8649 | 611.4835 | 507.2279 | NaN | 505.4715 | 324.1611 | 91.3161
3232.2542 | 1244.8653 | 611.7349 | 512.1509 | NaN | 504.3747 | 320.8415 | 91.3578
3233.2542 | 1244.8664 | 611.9627 | 511.9345 | NaN | 505.6908 | 320.9865 | 91.3914
3234.2542 | 1244.8671 | 611.848 | 511.3678 | NaN | 506.1351 | 321.7911 | 91.4453
3235.2542 | 1244.8691 | 612.1053 | 512.8472 | NaN | 505.7002 | 320.7983 | 91.4797
3236.2542 | 1244.8702 | 612.2365 | 510.103 | NaN | 505.6074 | 323.3782 | 91.5184
3237.2542 | 1244.8711 | 612.3965 | 506.1717 | NaN | 506.768 | 326.8329 | 91.5422
3238.2542 | 1244.8733 | 612.5985 | 507.4686 | NaN | 506.8357 | 326.2093 | 91.5825
3239.2542 | 1244.8746 | 612.8516 | 509.3825 | NaN | 506.1011 | 325.0104 | 91.6178
3240.2542 | 1244.8754 | 612.896 | 509.3114 | NaN | 506.879 | 324.9814 | 91.6753
3241.2542 | 1244.8761 | 612.9389 | 509.7885 | NaN | 507.0155 | 324.7192 | 91.6642
3242.2542 | 1244.8775 | 612.9612 | 510.8843 | NaN | 505.9757 | 324.3168 | 91.7149
3243.2542 | 1244.8779 | 612.9249 | 510.6637 | NaN | 507.5473 | 324.5201 | 91.7523
3244.2542 | 1244.8803 | 612.7895 | 512.7367 | NaN | 506.651 | 323.5993 | 91.7801
3245.2542 | 1244.8802 | 612.9724 | 510.4891 | NaN | 508.6592 | 326.1442 | 91.7883
3246.2542 | 1244.8825 | 613.1226 | 512.0126 | NaN | 508.3595 | 324.8147 | 91.8312
3247.2542 | 1244.8826 | 613.0299 | 513.3069 | NaN | 508.1036 | 323.9653 | 91.8549
3248.2542 | 1244.8852 | 613.0552 | 511.067 | NaN | 508.8907 | 325.6851 | 91.8721
3249.2542 | 1244.8855 | 613.3586 | 514.1838 | NaN | 507.9624 | 324.5774 | 91.9184
3250.2542 | 1244.8872 | 613.3303 | 512.6809 | NaN | 507.2968 | 325.89 | 91.9362
3251.2542 | 1244.8865 | 613.2169 | 513.6835 | NaN | 507.9696 | 325.3578 | 91.9753
3252.2542 | 1244.8887 | 613.1743 | 515.2248 | NaN | 508.2431 | 324.3654 | 91.9919
3253.2542 | 1244.8897 | 613.3259 | 514.8008 | NaN | 508.2327 | 325.2265 | 92.0374
3254.2542 | 1244.8905 | 613.2037 | 514.7721 | NaN | 508.0249 | 325.6609 | 92.0441
3255.2542 | 1244.8917 | 613.0763 | 515.8331 | NaN | 507.8873 | 325.6066 | 92.0716
3256.2542 | 1244.8935 | 613.1685 | 516.0011 | NaN | 507.0786 | 326.2261 | 92.0991
3257.2542 | 1244.894 | 613.2269 | 514.6939 | NaN | 506.9187 | 326.8265 | 92.1171
3258.2542 | 1244.8946 | 613.012 | 515.3188 | NaN | 507.528 | 326.29 | 92.139
3259.2542 | 1244.8957 | 612.9765 | 512.6808 | NaN | 507.702 | 328.4586 | 92.1836
3260.2542 | 1244.8969 | 612.9182 | 513.1689 | NaN | 508.7614 | 328.2067 | 92.1879
3261.2542 | 1244.8979 | 612.8717 | 514.8994 | NaN | 509.6746 | 326.6484 | 92.2041
3262.2542 | 1244.8983 | 613.024 | 513.02 | NaN | 509.7537 | 328.7178 | 92.2511
3263.2542 | 1244.9003 | 613.0262 | 515.3271 | NaN | 510.0505 | 327.6062 | 92.2609
3264.2542 | 1244.9018 | 613.5245 | 512.8656 | NaN | 508.8881 | 329.5597 | 92.2468
3265.2542 | 1244.9015 | 613.3426 | 519.4695 | NaN | 509.8218 | 329.4614 | 92.3346
3266.2542 | 1244.9027 | 613.0588 | 517.223 | NaN | 510.009 | 330.0869 | 92.3559
3267.2542 | 1244.905 | 612.9168 | 518.5588 | NaN | 509.5724 | 329.8494 | 92.3814
3268.2542 | 1244.9052 | 613.3893 | 519.1293 | NaN | 508.2231 | 329.984 | 92.4017
3269.2542 | 1244.906 | 613.6154 | 520.5127 | NaN | 509.5532 | 329.1529 | 92.4429
3270.2542 | 1244.9081 | 613.3563 | 519.9218 | NaN | 509.7638 | 329.3347 | 92.4673
3271.2542 | 1244.9083 | 613.5202 | 522.4198 | NaN | 508.5949 | 328.4891 | 92.4909
3272.2542 | 1244.91 | 613.2593 | 520.9798 | NaN | 507.623 | 329.762 | 92.5069
3273.2542 | 1244.9116 | 613.4783 | 519.4055 | NaN | 507.5019 | 330.8497 | 92.5398
3274.2542 | 1244.9129 | 613.4483 | 519.6349 | NaN | 506.9424 | 331.0637 | 92.563
3275.2542 | 1244.9146 | 613.4976 | 520.8695 | NaN | 506.7799 | 330.2966 | 92.5907
3276.2542 | 1244.914 | 613.3992 | 523.2891 | NaN | 506.8514 | 328.8635 | 92.6233
3277.2542 | 1244.9149 | 613.3262 | 519.7652 | NaN | 506.5919 | 331.0218 | 92.6229
3278.2542 | 1244.917 | 613.0313 | 520.9735 | NaN | 506.5099 | 330.5642 | 92.6434
3279.2542 | 1244.918 | 613.281 | 521.7194 | NaN | 505.9941 | 329.8398 | 92.6783
3280.2542 | 1244.9185 | 613.0164 | 519.5072 | NaN | 505.7237 | 331.3319 | 92.6916
3281.2542 | 1244.9197 | 612.9707 | 520.6563 | NaN | 505.2684 | 330.963 | 92.7083
3282.2542 | 1244.9199 | 613.2824 | 519.2556 | NaN | 504.4402 | 331.8745 | 92.7213
3283.2542 | 1244.9213 | 613.258 | 521.0076 | NaN | 503.9767 | 330.9185 | 92.7607
3284.2542 | 1244.923 | 613.0762 | 518.9236 | NaN | 504.2257 | 332.3881 | 92.7891
3285.2542 | 1244.9233 | 612.9095 | 517.9112 | NaN | 504.6324 | 333.2821 | 92.8105
3286.2542 | 1244.9251 | 613.3348 | 521.4224 | NaN | 503.2555 | 332.0069 | 92.8125
3287.2542 | 1244.9257 | 613.3275 | 521.2145 | NaN | 503.5664 | 332.5754 | 92.8521
3288.2542 | 1244.9266 | 613.1558 | 523.1105 | NaN | 503.3345 | 331.9441 | 92.867
3289.2542 | 1244.9275 | 613.2659 | 521.7538 | NaN | 504.4212 | 332.5274 | 92.8958
3290.2542 | 1244.9284 | 613.2898 | 519.7473 | NaN | 504.8158 | 333.2525 | 92.9106
3291.2542 | 1244.9311 | 612.9259 | 523.3548 | NaN | 504.0585 | 332.0643 | 92.9265
3292.2542 | 1244.9318 | 612.6429 | 525.0228 | NaN | 502.5251 | 331.0802 | 92.951
3293.2542 | 1244.933 | 612.4011 | 525.9936 | NaN | 502.1634 | 331.4251 | 92.9615
3294.2542 | 1244.9353 | 612.3215 | 525.939 | NaN | 501.9101 | 331.7247 | 93
3295.2542 | 1244.9356 | 611.8418 | 529.4334 | NaN | 502.7956 | 329.5053 | 93.0132
3296.2542 | 1244.9358 | 611.7054 | 529.3365 | NaN | 502.5383 | 329.8906 | 93.0276
3297.2542 | 1244.9365 | 611.558 | 529.6683 | NaN | 502.1789 | 329.925 | 93.0448
3298.2542 | 1244.9367 | 611.096 | 528.8854 | NaN | 503.0342 | 330.7299 | 93.0671
3299.2542 | 1244.9378 | 610.7342 | 530.863 | NaN | 503.8515 | 330.3428 | 93.1055
3300.2542 | 1244.9389 | 610.1393 | 534.171 | NaN | 505.2871 | 329.6522 | 93.1155
3301.2542 | 1244.9403 | 610.4873 | 536.3125 | NaN | 506.6542 | 329.0497 | 93.1325
3302.2542 | 1244.9409 | 610.4499 | 537.1038 | NaN | 506.6137 | 328.2819 | 93.1453
3303.2542 | 1244.9421 | 610.6054 | 537.7885 | NaN | 507.0493 | 328.6462 | 93.1633
3304.2542 | 1244.9436 | 610.4829 | 536.9927 | NaN | 508.1312 | 329.0407 | 93.1857
3305.2542 | 1244.9448 | 610.6189 | 538.3437 | NaN | 508.9466 | 328.5935 | 93.2075
3306.2542 | 1244.9459 | 610.6333 | 539.7762 | NaN | 508.8968 | 328.9352 | 93.2299
3307.2542 | 1244.9466 | 611.0411 | 540.0947 | NaN | 509.0277 | 328.8042 | 93.2397
3308.2542 | 1244.9472 | 611.0503 | 539.9165 | NaN | 508.8862 | 329.2856 | 93.2613
3309.2542 | 1244.9485 | 610.958 | 539.3786 | NaN | 508.9145 | 329.5845 | 93.2857
3310.2542 | 1244.9496 | 611.172 | 538.7854 | NaN | 508.6968 | 329.5336 | 93.3016
3311.2542 | 1244.9501 | 611.3427 | 539.2778 | NaN | 508.1944 | 329.468 | 93.3322
3312.2542 | 1244.9513 | 611.0272 | 539.6679 | NaN | 507.9002 | 329.8311 | 93.3417
3313.2542 | 1244.9526 | 611.6246 | 539.9922 | NaN | 507.6948 | 330.3646 | 93.3638
3314.2542 | 1244.9529 | 611.5815 | 540.9553 | NaN | 507.686 | 330.5142 | 93.3864
3315.2542 | 1244.9543 | 611.4486 | 541.1288 | NaN | 507.456 | 330.417 | 93.4101
3316.2542 | 1244.9557 | 611.5126 | 542.3877 | NaN | 508.1807 | 330.2588 | 93.4221
3317.2542 | 1244.9566 | 611.5841 | 542.9033 | NaN | 508.0466 | 330.6011 | 93.4482
3318.2542 | 1244.9575 | 611.8061 | 543.1413 | NaN | 508.6103 | 330.6404 | 93.4663
3319.2542 | 1244.958 | 612.0412 | 542.4557 | NaN | 508.7659 | 331.2549 | 93.4803
3320.2542 | 1244.9592 | 612.1831 | 543.3756 | NaN | 509.3081 | 331.7637 | 93.5018
3321.2542 | 1244.9604 | 612.552 | 543.7586 | NaN | 510.2069 | 331.2935 | 93.5266
3322.2542 | 1244.9608 | 612.3376 | 543.5922 | NaN | 510.4301 | 331.5485 | 93.5391
3323.2542 | 1244.9614 | 612.191 | 543.5291 | NaN | 510.2358 | 331.6638 | 93.5653
3324.2542 | 1244.9637 | 612.2035 | 544.3928 | NaN | 509.5153 | 332.1948 | 93.5814
3325.2542 | 1244.9631 | 612.3167 | 545.0819 | NaN | 508.7209 | 332.2454 | 93.6099
3326.2542 | 1244.9647 | 611.9867 | 544.5731 | NaN | 507.1911 | 331.6712 | 93.6216
3327.2542 | 1244.966 | 611.6923 | 544.7408 | NaN | 506.6196 | 332.0341 | 93.6474
3328.2542 | 1244.9673 | 611.8856 | 545.3909 | NaN | 506.3487 | 332.1823 | 93.6834
3329.2542 | 1244.9674 | 611.6445 | 545.0135 | NaN | 506.0005 | 332.5111 | 93.7024
3330.2542 | 1244.9696 | 611.362 | 544.9454 | NaN | 505.7073 | 333.9567 | 93.7218
3331.2542 | 1244.9696 | 611.1938 | 546.2673 | NaN | 505.4789 | 333.5127 | 93.7415
3332.2542 | 1244.971 | 610.8447 | 546.5772 | NaN | 504.7449 | 333.1026 | 93.7704
3333.2542 | 1244.9715 | 611.0582 | 546.5042 | NaN | 504.5891 | 333.993 | 93.7954
3334.2542 | 1244.9734 | 610.9209 | 546.5987 | NaN | 505.63 | 334.3811 | 93.8151
3335.2542 | 1244.974 | 610.8886 | 546.7709 | NaN | 506.1431 | 334.2313 | 93.8554
3336.2542 | 1244.975 | 610.3511 | 551.3041 | NaN | 502.8833 | 324.9135 | 93.8889
3337.2542 | 1244.9749 | 610.7862 | 558.2449 | NaN | 502.3488 | 336.6785 | 93.9123
3338.2542 | 1244.9775 | 610.1459 | 557.7885 | NaN | 501.3091 | 334.6277 | 93.9339
3339.2542 | 1244.9779 | 610.1867 | 558.3168 | NaN | 502.0169 | 333.6163 | 93.965
3340.2542 | 1244.979 | 609.9589 | 556.2294 | NaN | 502.7803 | 334.1092 | 93.987
3341.2542 | 1244.9798 | 609.894 | 557.237 | NaN | 503.4666 | 334.1012 | 94.0031
3342.2542 | 1244.9805 | 609.3662 | 556.4215 | NaN | 503.6848 | 334.0231 | 94.046
3343.2542 | 1244.981 | 609.961 | 557.6719 | NaN | 502.0202 | 332.1843 | 94.0547
3344.2542 | 1244.9828 | 610.7751 | 556.9116 | NaN | 499.4525 | 331.8332 | 94.0887
3345.2542 | 1244.9836 | 610.9405 | 558.1912 | NaN | 500.8539 | 334.9574 | 94.1171
3346.2542 | 1244.9847 | 610.9459 | 556.4103 | NaN | 502.547 | 335.4939 | 94.1353
3347.2542 | 1244.9858 | 610.4655 | 554.3228 | NaN | 503.4429 | 337.4353 | 94.1593
3348.2542 | 1244.9872 | 610.3751 | 552.031 | NaN | 504.6966 | 337.3811 | 94.1917
3349.2542 | 1244.9886 | 609.5544 | 548.0649 | NaN | 505.9923 | 338.1364 | 94.1996
3350.2542 | 1244.9881 | 609.8601 | 549.2129 | NaN | 505.1596 | 337.4061 | 94.2317
3351.2542 | 1244.9891 | 607.9833 | 543.3534 | NaN | 506.8193 | 339.151 | 94.2571
3352.2542 | 1244.989 | 608.8431 | 547.5402 | NaN | 503.6918 | 337.2005 | 94.2541
3353.2542 | 1244.992 | 606.2162 | 540.0282 | NaN | 506.7948 | 340.3046 | 94.3123
3354.2542 | 1244.9918 | 607.9807 | 544.4787 | NaN | 504.8897 | 339.5582 | 94.3265
3355.2542 | 1244.9927 | 610.298 | 555.9342 | NaN | 499.9817 | 337.096 | 94.359
3356.2542 | 1244.9947 | 611.1638 | 561.1778 | NaN | 498.136 | 336.0221 | 94.3833
3357.2542 | 1244.9947 | 611.7244 | 563.0108 | NaN | 498.1327 | 334.3962 | 94.4001
3358.2542 | 1244.9962 | 611.6913 | 566.4936 | NaN | 496.3175 | 333.3227 | 94.4341
3359.2542 | 1244.9976 | 611.6158 | 567.1684 | NaN | 496.8506 | 334.0583 | 94.4625
3360.2542 | 1244.9986 | 611.5149 | 576.7659 | NaN | 491.4581 | 331.6736 | 94.4769
3361.2542 | 1244.9985 | 610.1067 | 573.769 | NaN | 493.0166 | 333.2252 | 94.4948
3362.2542 | 1245.0015 | 608.8655 | 570.0186 | NaN | 493.8404 | 334.4161 | 94.5146
3363.2542 | 1245.0006 | 610.6177 | 577.9971 | NaN | 489.0832 | 331.5242 | 94.5435
3364.2542 | 1245.0012 | 604.3929 | 547.2866 | NaN | 503.3491 | 341.065 | 94.576
3365.2542 | 1245.0016 | 603.1433 | 542.7934 | NaN | 504.5943 | 341.6062 | 94.6067
3366.2542 | 1245.0026 | 604.5691 | 547.142 | NaN | 501.7988 | 341.2107 | 94.6355
3367.2542 | 1245.0038 | 606.4534 | 553.7339 | NaN | 497.9139 | 338.7937 | 94.6488
3368.2542 | 1245.0048 | 606.2587 | 548.8538 | NaN | 499.8547 | 340.1433 | 94.6625
3369.2542 | 1245.0064 | 610.3156 | 569.2005 | NaN | 488.8612 | 333.2685 | 94.6887
3370.2542 | 1245.0074 | 610.0665 | 570.1642 | NaN | 489.4144 | 333.0692 | 94.7207
3371.2542 | 1245.009 | 608.345 | 565.7482 | NaN | 491.7214 | 334.8918 | 94.7352
3372.2542 | 1245.009 | 607.4972 | 566.0232 | NaN | 490.6982 | 335.0703 | 94.754
3373.2542 | 1245.0088 | 609.4641 | 576.374 | NaN | 486.0166 | 332.7856 | 94.7707
3374.2542 | 1245.0108 | 606.7466 | 571.2353 | NaN | 489.2066 | 334.3776 | 94.7966
3375.2542 | 1245.0116 | 606.6552 | 570.7291 | NaN | 488.2212 | 337.1332 | 94.8074
3376.2542 | 1245.0136 | 604.3367 | 565.8957 | NaN | 488.9179 | 338.071 | 94.8448
3377.2542 | 1245.0133 | 585.8043 | 537.1049 | NaN | 502.8651 | 344.9576 | 94.8623
3378.2542 | 1245.0139 | 580.2528 | 527.4063 | NaN | 508.587 | 348.298 | 94.849
3379.2542 | 1115.6671 | 613.6561 | 514.0024 | 57.0504 | 524.7781 | 355.8325 | 94.8644
3380.2542 | 1113.4627 | 614.4324 | 514.1187 | 55.6745 | 524.7662 | 356.3415 | 94.8802
3381.2542 | 1113.753 | 614.1483 | 514.2829 | 53.9516 | 524.2616 | 356.3832 | 94.8982
3382.2542 | 1088.1569 | 614.3707 | 514.3692 | 77.9781 | 524.0694 | 356.4464 | 94.9231
3383.2542 | 1100.3058 | 613.7448 | 514.5021 | 69.6484 | 524.0211 | 356.364 | 94.9283
3384.2542 | 1105.7037 | 613.9309 | 514.2477 | 59.1087 | 524.4174 | 357.0461 | 94.9615
3385.2542 | 1117.0426 | 614.0462 | 514.292 | 45.2883 | 524.3082 | 356.941 | 94.9817
3386.2542 | 1138.2538 | 614.0676 | 514.2319 | 22.396 | 525.1135 | 357.4645 | 94.9886
3387.2542 | 1140.1931 | 614.3945 | 514.336 | 20.8895 | 525.3117 | 357.5991 | 95.0043
3388.2542 | 1150.7952 | 614.1617 | 514.3918 | 10.7228 | 524.9422 | 357.655 | 95.0248
3389.2542 | 1153.5524 | 614.0538 | 514.4002 | 3.0788 | 524.7735 | 357.8579 | 95.0558
3390.2542 | 1162.6302 | 614.5983 | 514.5802 | -7.0586 | 525.7367 | 358.2606 | 95.0695
3391.2542 | 1177.6349 | 614.366 | 514.8665 | NaN | 526.5238 | 358.6911 | 95.0916
3392.2542 | 1178.573 | 614.4021 | 514.9546 | NaN | 527.1153 | 359.1638 | 95.1201
3393.2542 | 1195.7221 | 614.23 | 515.1034 | NaN | 529.0139 | 359.2785 | 95.1364
3394.2542 | 1206.2831 | 614.463 | 515.2989 | NaN | 531.3129 | 359.7364 | 95.1461
3395.2542 | 1218.4195 | 614.2505 | 515.2978 | NaN | 531.8054 | 360.0712 | 95.1657
3396.2542 | 1245.0318 | 614.6986 | 515.3516 | NaN | 531.2417 | 360.0595 | 95.1923
3397.2542 | 1245.0325 | 615.1303 | 515.5447 | -16.2763 | 530.5356 | 359.6433 | 95.2083
3398.2542 | 1245.0333 | 614.8553 | 515.6803 | 49.2111 | 529.6263 | 360.1766 | 95.2318
3399.2542 | 1245.0343 | 615.02 | 515.9626 | 457.7036 | 528.3572 | 360.193 | 95.2576
3400.2542 | 1245.0358 | 615.0956 | 516.1867 | 807.3971 | 527.323 | 360.5615 | 95.2729
3401.2542 | 1245.0365 | 615.1559 | 516.322 | 1051.9214 | 526.8749 | 360.8445 | 95.289
3402.2542 | 1245.0378 | 614.6311 | 516.3197 | NaN | 526.7593 | 360.9314 | 95.3103
3403.2542 | 1245.0388 | 613.7473 | 516.4344 | NaN | 526.6117 | 361.1154 | 95.3264
3404.2542 | 1245.0405 | 613.7278 | 516.604 | NaN | 526.8502 | 361.2411 | 95.3453
3405.2542 | 1245.0406 | 613.9357 | 516.7665 | NaN | 527.8746 | 361.8217 | 95.3558
3406.2542 | 1245.0415 | 613.6312 | 516.8093 | NaN | 529.1223 | 362.3338 | 95.3762
3407.2542 | 1245.0429 | 613.8156 | 516.9039 | NaN | 528.9809 | 362.205 | 95.3944
3408.2542 | 1245.043 | 613.6352 | 517.1262 | NaN | 528.8987 | 362.5144 | 95.4162
3409.2542 | 1245.0458 | 613.5157 | 517.1791 | NaN | 528.8877 | 362.6932 | 95.4328
3410.2542 | 1245.0464 | 613.1584 | 517.347 | NaN | 528.1112 | 362.5204 | 95.4485
3411.2542 | 1245.046 | 612.8645 | 517.3905 | NaN | 527.9844 | 363.1311 | 95.4717
3412.2542 | 1245.0462 | 612.9673 | 517.5334 | NaN | 528.1963 | 363.4336 | 95.4882
3413.2542 | 1245.0487 | 612.6916 | 517.6906 | NaN | 528.2528 | 363.7587 | 95.5146
3414.2542 | 1245.0486 | 612.4784 | 517.7017 | NaN | 528.3336 | 363.5097 | 95.5239
3415.2542 | 1245.0495 | 612.4102 | 517.7956 | NaN | 528.6402 | 364.2397 | 95.5441
3416.2542 | 1245.0499 | 612.2297 | 517.777 | NaN | 528.6667 | 363.9727 | 95.5649
3417.2542 | 1245.0517 | 612.1636 | 517.8895 | NaN | 529.3115 | 365.0497 | 95.5802
3418.2542 | 1245.0525 | 612.4383 | 517.9917 | NaN | 529.4602 | 365.0234 | 95.5892
3419.2542 | 1245.053 | 612.2182 | 517.9987 | NaN | 529.8829 | 365.0057 | 95.6132
3420.2542 | 1245.0545 | 611.9127 | 517.9793 | NaN | 530.0599 | 365.1512 | 95.6382
3421.2542 | 1245.0551 | 611.6113 | 517.9782 | NaN | 530.6909 | 365.6755 | 95.6474
3422.2542 | 1245.0566 | 611.8992 | 517.9586 | NaN | 530.5512 | 365.6798 | 95.6665
3423.2542 | 1245.0574 | 611.929 | 517.9441 | NaN | 530.9089 | 365.8228 | 95.6916
3424.2542 | 1245.0582 | 611.7527 | 517.9904 | NaN | 530.2594 | 365.697 | 95.7049
3425.2542 | 1245.0589 | 611.7244 | 518.0291 | NaN | 530.0044 | 366.2491 | 95.7194
3426.2542 | 1245.0601 | 611.6101 | 518.112 | NaN | 530.4708 | 366.5016 | 95.7319
3427.2542 | 1245.061 | 610.8178 | 518.1928 | NaN | 530.9059 | 366.7195 | 95.7507
3428.2542 | 1245.0616 | 610.304 | 518.2665 | NaN | 531.057 | 367.0169 | 95.7767
3429.2542 | 1245.0611 | 609.9493 | 518.4692 | NaN | 530.8851 | 367.0063 | 95.7883
3430.2542 | 1245.064 | 609.8787 | 518.5046 | NaN | 530.169 | 367.2512 | 95.8173
3431.2542 | 1245.0652 | 610.169 | 518.6197 | NaN | 530.4892 | 368.1164 | 95.8354
3432.2542 | 1245.0658 | 609.7668 | 518.6804 | NaN | 531.0195 | 368.0106 | 95.8503
3433.2542 | 1245.0667 | 610.4882 | 518.5931 | NaN | 531.0478 | 368.1592 | 95.8763
3434.2542 | 1245.0668 | 610.499 | 518.5739 | NaN | 531.3438 | 368.3204 | 95.8922
3435.2542 | 1245.068 | 610.1435 | 518.5146 | NaN | 531.0939 | 368.9574 | 95.9186
3436.2542 | 1245.0691 | 610.3173 | 518.6261 | NaN | 530.9158 | 369.1404 | 95.9263
3437.2542 | 1245.0704 | 610.2339 | 518.5966 | NaN | 532.3232 | 368.8693 | 95.9492
3438.2542 | 1245.0714 | 609.9885 | 518.7156 | NaN | 532.0067 | 369.5235 | 95.9646
3439.2542 | 1245.0723 | 610.7473 | 518.7682 | NaN | 532.1026 | 369.3614 | 95.9778
3440.2542 | 1245.0726 | 610.7912 | 518.8541 | NaN | 531.3852 | 370.0157 | 96.0009
3441.2542 | 1245.0738 | 610.3848 | 518.9655 | NaN | 531.3455 | 370.1823 | 96.0217
3442.2542 | 1245.0755 | 610.5636 | 519.0882 | NaN | 532.0003 | 370.5557 | 96.0405
3443.2542 | 1245.0768 | 610.9891 | 519.2403 | NaN | 531.8655 | 370.9933 | 96.0533
3444.2542 | 1245.0771 | 610.9867 | 519.3664 | NaN | 532.1816 | 370.9766 | 96.0755
3445.2542 | 1245.0783 | 610.9668 | 519.5092 | NaN | 531.6722 | 370.9973 | 96.0889
3446.2542 | 1245.0793 | 611.2037 | 519.6947 | NaN | 531.6641 | 371.1935 | 96.1163
3447.2542 | 1245.081 | 610.8533 | 519.7847 | NaN | 531.3639 | 371.1752 | 96.1305
3448.2542 | 1245.0807 | 611.0382 | 519.7916 | NaN | 530.9332 | 370.9159 | 96.1443
3449.2542 | 1245.0819 | 611.6326 | 519.8883 | NaN | 530.5953 | 371.3693 | 96.1688
3450.2542 | 1245.0826 | 611.3331 | 519.8212 | NaN | 529.8802 | 370.9654 | 96.189
3451.2542 | 1245.0839 | 611.3686 | 519.8911 | NaN | 529.9516 | 371.7252 | 96.2014
3452.2542 | 1245.0846 | 611.7489 | 519.9009 | NaN | 530.5801 | 372.034 | 96.2326
3453.2542 | 1245.0857 | 612.1634 | 519.9794 | NaN | 530.7879 | 371.5554 | 96.2424
3454.2542 | 1245.0863 | 611.9099 | 519.9048 | NaN | 529.9979 | 371.4935 | 96.2652
3455.2542 | 1245.0878 | 612.2736 | 519.8986 | NaN | 529.0744 | 371.8122 | 96.2787
3456.2542 | 1245.0892 | 612.4832 | 520.0217 | NaN | 528.545 | 372.5327 | 96.2944
3457.2542 | 1245.0907 | 612.7131 | 520.0739 | NaN | 528.1131 | 372.639 | 96.3183
3458.2542 | 1245.0904 | 613.0154 | 520.0465 | NaN | 528.6123 | 373.0545 | 96.3404
3459.2542 | 1245.0916 | 612.3231 | 519.9926 | NaN | 528.5168 | 373.0655 | 96.3619
3460.2542 | 1245.0931 | 612.7742 | 519.8975 | NaN | 529.7994 | 373.2675 | 96.3756
3461.2542 | 1245.0932 | 613.1988 | 520.0096 | NaN | 529.6697 | 373.354 | 96.408
3462.2542 | 1245.0946 | 613.0623 | 519.9743 | NaN | 530.1421 | 373.6224 | 96.4306
3463.2542 | 1245.0955 | 612.7324 | 519.9528 | NaN | 529.8608 | 373.9674 | 96.4443
3464.2542 | 1245.0974 | 612.5717 | 520.0809 | 1219.0539 | 530.3619 | 373.9226 | 96.4662
3465.2542 | 1245.0976 | 611.6503 | 520.2406 | 850.1826 | 530.3311 | 373.9883 | 96.4862
3466.2542 | 1245.0982 | 611.731 | 520.3693 | 281.6333 | 530.1792 | 374.4748 | 96.5125
3467.2542 | 1245.0988 | 611.2834 | 520.4542 | 101.3996 | 530.5262 | 374.7619 | 96.5365
3468.2542 | 1245.1005 | 611.2642 | 520.5186 | -7.2183 | 530.8468 | 374.898 | 96.5592
3469.2542 | 1244.1894 | 611.1371 | 520.6118 | NaN | 530.7787 | 374.691 | 96.584
3470.2542 | 1210.3559 | 610.6895 | 520.623 | NaN | 532.0107 | 375.4765 | 96.5967
3471.2542 | 1205.5047 | 610.9506 | 520.6401 | NaN | 533.1346 | 375.665 | 96.6254
3472.2542 | 1206.9143 | 610.8836 | 520.6779 | NaN | 533.4054 | 376.1045 | 96.6458
3473.2542 | 1195.7102 | 611.2343 | 520.7159 | NaN | 534.4908 | 376.3835 | 96.6559
3474.2542 | 1181.6958 | 611.2699 | 520.7069 | NaN | 534.7861 | 376.079 | 96.6829
3475.2542 | 1167.8712 | 610.957 | 520.7503 | NaN | 534.8603 | 375.9734 | 96.7043
3476.2542 | 1153.1123 | 611.186 | 520.7904 | -16.2707 | 534.301 | 376.0863 | 96.7245
3477.2542 | 1128.6659 | 611.755 | 520.9032 | 9.7412 | 534.1452 | 376.4052 | 96.7445
3478.2542 | 1129.9872 | 612.0577 | 520.8965 | 7.4332 | 533.4583 | 376.4886 | 96.7668
3479.2542 | 1121.9149 | 612.1002 | 520.9622 | 13.8222 | 533.092 | 376.7014 | 96.7872
3480.2542 | 1120.7211 | 612.4693 | 521.0969 | 16.7496 | 532.1127 | 376.6041 | 96.8199
3481.2542 | 1113.9062 | 612.6029 | 521.0752 | 21.4666 | 531.4932 | 376.8245 | 96.8488
3482.2542 | 1099.8369 | 612.2798 | 521.0994 | 34.646 | 531.6166 | 376.9819 | 96.8663
3483.2542 | 1098.2251 | 612.6183 | 521.2996 | 35.4192 | 531.468 | 377.1463 | 96.8899
3484.2542 | 1094.7463 | 612.5396 | 521.3443 | 37.3487 | 532.0973 | 377.4567 | 96.9215
3485.2542 | 1094.5705 | 612.5084 | 521.3399 | 36.9821 | 531.7216 | 377.2836 | 96.9435
3486.2542 | 1103.0051 | 612.3293 | 521.3261 | 29.9669 | 531.402 | 377.6484 | 96.9736
3487.2542 | 1095.508 | 612.6254 | 521.2937 | 39.9697 | 530.9732 | 377.3502 | 96.9955
3488.2542 | 1092.216 | 612.2299 | 521.3305 | 44.1609 | 530.5245 | 377.7145 | 97.0106
3489.2542 | 1095.8945 | 613.11 | 521.3164 | 42.8944 | 530.2337 | 378.1312 | 97.0392
3490.2542 | 1098.9384 | 612.5575 | 521.2459 | 39.4407 | 529.9593 | 378.9718 | 97.0613
3491.2542 | 1095.0708 | 612.1759 | 521.2593 | 42.3684 | 529.8011 | 379.1337 | 97.0911
3492.2542 | 1084.3988 | 612.3058 | 521.1978 | 51.5551 | 529.5565 | 379.625 | 97.1018
3493.2542 | 1078.4492 | 612.2165 | 521.2615 | 57.6884 | 529.7469 | 379.8141 | 97.1346
3494.2542 | 1080.0636 | 611.8216 | 521.3526 | 54.9562 | 530.3505 | 380.1924 | 97.1532
3495.2542 | 788.2846 | 612.2399 | 521.1034 | 392.7019 | 531.9643 | 380.4423 | 97.1817
3496.2542 | 788.1157 | 612.4964 | 521.1354 | 394.1577 | 532.176 | 380.2877 | 97.1945
3497.2542 | 789.0499 | 612.8623 | 521.1043 | 393.8958 | 532.6164 | 380.6677 | 97.2199
3498.2542 | 790.4748 | 612.4894 | 521.2286 | 392.5842 | 533.3343 | 381.1029 | 97.245
3499.2542 | 793.5672 | 612.7226 | 521.2491 | 389.8463 | 534.2151 | 380.8868 | 97.2647
3500.2542 | 792.0386 | 612.1418 | 521.3956 | 391.1163 | 534.51 | 380.6169 | 97.2847
3501.2542 | 792.5411 | 611.9075 | 521.549 | 389.9835 | 534.0993 | 380.7066 | 97.3016
3502.2542 | 793.1878 | 611.9407 | 521.7242 | 388.8575 | 535.2436 | 381.6083 | 97.3289
3503.2542 | 796.1706 | 611.5354 | 521.8234 | 387.058 | 535.1951 | 381.5418 | 97.3481
3504.2542 | 796.6938 | 611.3844 | 521.9033 | 388.8697 | 534.7293 | 381.4928 | 97.3574
3505.2542 | 796.8496 | 610.9644 | 522.1375 | 387.9376 | 534.5636 | 381.8936 | 97.3852
3506.2542 | 798.1318 | 611.8583 | 522.3198 | 386.7846 | 535.0751 | 381.7904 | 97.398
3507.2542 | 797.6636 | 611.9761 | 522.3889 | 387.4821 | 534.8693 | 381.5832 | 97.4356
3508.2542 | 797.82 | 612.1379 | 522.4237 | 386.9766 | 534.9658 | 381.8157 | 97.4491
3509.2542 | 801.3854 | 612.0077 | 522.4946 | 385.3561 | 535.4504 | 382.2764 | 97.4771
3510.2542 | 805.5119 | 612.4956 | 522.5921 | 382.9256 | 534.4295 | 382.5256 | 97.4919
3511.2542 | 807.0379 | 612.7585 | 522.6839 | 380.8042 | 533.6609 | 382.4915 | 97.5169
3512.2542 | 808.3927 | 612.7879 | 522.8277 | 380.4333 | 533.4131 | 383.267 | 97.5319
3513.2542 | 807.8007 | 613.0063 | 522.9644 | 380.1317 | 534.0561 | 383.2213 | 97.5538
3514.2542 | 811.8174 | 613.3085 | 523.1814 | 377.105 | 533.4833 | 383.2363 | 97.5673
3515.2542 | 814.0172 | 613.2543 | 523.1704 | 375.3436 | 532.9002 | 383.234 | 97.5983
3516.2542 | 816.1438 | 612.9289 | 523.1761 | 374.9958 | 533.6819 | 383.2106 | 97.625
3517.2542 | 819.4825 | 612.3877 | 523.1324 | 374.205 | 533.5456 | 383.6557 | 97.6407
3518.2542 | 821.8496 | 612.3725 | 523.1771 | 373.5343 | 533.3494 | 384.072 | 97.6634
3519.2542 | 822.3169 | 612.2688 | 523.1426 | 374.3903 | 533.4618 | 383.7973 | 97.686
3520.2542 | 824.5594 | 611.9658 | 523.1951 | 371.6905 | 532.6026 | 383.1413 | 97.6909
3521.2542 | 826.5594 | 611.5751 | 523.1818 | 369.1727 | 532.6199 | 383.7447 | 97.7147
3522.2542 | 826.9604 | 611.8359 | 523.2703 | 366.7075 | 533.3525 | 384.6482 | 97.7375
3523.2542 | 832.2393 | 611.4224 | 523.1652 | 363.536 | 533.8138 | 384.3595 | 97.7599
3524.2542 | 834.4652 | 611.6005 | 523.2102 | 361.1989 | 534.2668 | 385.1156 | 97.7684
3525.2542 | 841.0638 | 610.8119 | 523.2717 | 358.3427 | 534.5703 | 385.1666 | 97.792
3526.2542 | 842.9419 | 610.9696 | 523.1631 | 352.7765 | 533.9676 | 385.1979 | 97.8165
3527.2542 | 851.0343 | 611.1954 | 523.2734 | 345.3072 | 534.0736 | 385.4703 | 97.838
3528.2542 | 853.7316 | 611.5833 | 523.3001 | 342.0115 | 534.4557 | 385.4365 | 97.8656
3529.2542 | 865.8206 | 611.4802 | 523.2573 | 330.7211 | 535.485 | 385.7159 | 97.8831
3530.2542 | 874.5729 | 611.1953 | 523.3732 | 324.3264 | 535.3044 | 385.5561 | 97.8999
3531.2542 | 888.3733 | 611.5787 | 523.1426 | 311.3011 | 535.1114 | 385.5611 | 97.9254
3532.2542 | 894.6674 | 611.1686 | 523.1266 | 305.4854 | 534.6418 | 386.1042 | 97.956
3533.2542 | 900.3752 | 611.2661 | 523.149 | 302.7353 | 534.572 | 386.1011 | 97.977
3534.2542 | 904.3441 | 611.5895 | 523.1013 | 298.7399 | 534.0148 | 386.3576 | 97.9973
3535.2542 | 906.7546 | 611.6436 | 523.0573 | 294.8153 | 533.903 | 386.5049 | 98.0323
3536.2542 | 910.4042 | 611.5096 | 523.0008 | 290.9585 | 534.6155 | 387.0745 | 98.0531
3537.2542 | 912.3948 | 611.3611 | 522.9409 | 288.0982 | 534.1495 | 387.0986 | 98.0676
3538.2542 | 914.836 | 611.5566 | 522.8816 | 285.8629 | 534.2742 | 387.1005 | 98.1099
3539.2542 | 913.0244 | 610.9865 | 522.8998 | 285.8207 | 533.9433 | 387.4539 | 98.1362
3540.2542 | 917.8127 | 610.7972 | 522.9776 | 281.8439 | 533.2958 | 387.3465 | 98.152
3541.2542 | 920.527 | 610.6824 | 522.8236 | 276.988 | 532.5155 | 387.3543 | 98.1826
3542.2542 | 922.7253 | 610.571 | 522.7874 | 271.6724 | 531.5723 | 387.5554 | 98.1923
3543.2542 | 927.1587 | 610.488 | 522.6567 | 266.1819 | 531.4987 | 387.9564 | 98.2282
3544.2542 | 927.6977 | 610.7875 | 522.7139 | 262.2986 | 531.791 | 388.0438 | 98.2451
3545.2542 | 932.8915 | 611.1459 | 522.7238 | 261.831 | 532.7542 | 388.5736 | 98.2652
3546.2542 | 931.164 | 611.3155 | 522.7921 | 261.4802 | 533.0279 | 389.2327 | 98.2995
3547.2542 | 928.5451 | 611.3439 | 522.6972 | 264.2547 | 533.4212 | 389.4575 | 98.318
3548.2542 | 985.0917 | 611.5778 | 522.1269 | 196.7231 | 533.891 | 389.472 | 98.3549
3549.2542 | 988.4127 | 611.7439 | 522.1283 | 187.4583 | 533.7928 | 389.3942 | 98.3824
3550.2542 | 985.5377 | 612.0119 | 522.0867 | 188.8843 | 533.5988 | 389.719 | 98.4067
3551.2542 | 986.6937 | 611.9365 | 522.2732 | 188.0959 | 534.9336 | 390.3233 | 98.4256
3552.2542 | 988.6348 | 612.1128 | 522.4745 | 187.073 | 535.6673 | 390.6562 | 98.461
3553.2542 | 996.1913 | 612.3319 | 522.268 | 178.6338 | 535.6632 | 391.0033 | 98.4742
3554.2542 | 999.8758 | 612.6711 | 522.2844 | 175.8968 | 535.2215 | 390.6362 | 98.5066
3555.2542 | 996.3624 | 612.4508 | 522.4274 | 179.1383 | 535.2307 | 391.1676 | 98.5174
3556.2542 | 1001.6572 | 612.5567 | 522.7324 | 176.6338 | 536.6211 | 391.5218 | 98.5491
3557.2542 | 1010.0418 | 612.6877 | 522.8689 | 169.293 | 538.5186 | 391.9026 | 98.5657
3558.2542 | 1017.0153 | 612.4315 | 522.8365 | 164.5677 | 539.7501 | 392.1296 | 98.5862
3559.2542 | 1015.1182 | 613.3507 | 522.8252 | 164.6522 | 540.0377 | 392.2352 | 98.6049
3560.2542 | 1012.7536 | 613.5898 | 523.1434 | 166.1891 | 539.3988 | 392.0101 | 98.6223
3561.2542 | 1024.3772 | 613.3514 | 523.0318 | 151.34 | 538.8315 | 392.8977 | 98.6458
3562.2542 | 1020.097 | 613.1095 | 523.3678 | 147.8824 | 538.6086 | 392.1826 | 98.6667
3563.2542 | 999.5215 | 612.6486 | 523.5475 | 179.7952 | 537.9988 | 392.779 | 98.6799
3564.2542 | 1002.0341 | 612.983 | 523.4301 | 168.981 | 538.7157 | 393.9527 | 98.7038
3565.2542 | 1029.9983 | 612.7844 | 523.2826 | 139.5928 | 537.7636 | 393.9869 | 98.716
3566.2542 | 1031.1763 | 611.8136 | 523.1721 | 138.4736 | 537.4562 | 394.0939 | 98.7482
3567.2542 | 1036.3973 | 612.009 | 523.2785 | 131.3563 | 537.0142 | 394.5041 | 98.754
3568.2542 | 1022.8366 | 611.4557 | 523.4756 | 125.8856 | 537.5223 | 395.1872 | 98.7866
3569.2542 | 1021.7668 | 611.3181 | 523.2555 | 125.7091 | 538.4011 | 395.5287 | 98.7997
3570.2542 | 1019.0711 | 610.7253 | 522.5612 | 114.7245 | 536.4623 | 394.9946 | 98.8245
3571.2542 | 1009.2489 | 610.8493 | 522.6992 | 129.0532 | 535.9385 | 395.2671 | 98.8421
3572.2542 | 1005.1301 | 610.3542 | 522.8385 | 130.1598 | 536.3832 | 395.9581 | 98.8596
3573.2542 | 1005.4741 | 610.5141 | 522.8215 | 123.8778 | 536.0332 | 396.1586 | 98.8777
3574.2542 | 1001.3458 | 610.1632 | 522.6948 | 130.7043 | 535.6831 | 396.3 | 98.8955
3575.2542 | 1011.9219 | 609.7639 | 522.582 | 115.4465 | 534.9362 | 396.8866 | 98.9363
3576.2542 | 1028.1634 | 609.4182 | 522.4799 | 102.2669 | 534.3939 | 396.7881 | 98.9416
3577.2542 | 1028.9532 | 609.1602 | 522.4584 | 91.3131 | 534.1959 | 396.8444 | 98.967
3578.2542 | 1016.2751 | 609.9159 | 522.6748 | 109.6723 | 533.8284 | 397.2577 | 98.9856
3579.2542 | 1008.1256 | 609.8906 | 522.6896 | 119.5441 | 535.0038 | 397.3597 | 99.0099
3580.2542 | 1011.4265 | 609.4101 | 522.602 | 107.424 | 534.9649 | 397.1299 | 99.035
3581.2542 | 1012.6403 | 609.2709 | 522.7817 | 109.0271 | 534.005 | 397.3113 | 99.0562
3582.2542 | 1014.7329 | 609.3785 | 522.8521 | 106.1445 | 533.0807 | 397.4998 | 99.0812
3583.2542 | 1024.7381 | 609.5901 | 522.7588 | 86.9056 | 531.9373 | 397.8305 | 99.1057
3584.2542 | 1017.8745 | 610.1171 | 523.3043 | 118.9727 | 532.0519 | 398.4214 | 99.1196
3585.2542 | 1220.3388 | 608.4835 | 522.0581 | NaN | 533.2095 | 398.5169 | 99.1459
3586.2542 | 1245.2094 | 610.0424 | 521.9146 | 245.1311 | 533.1588 | 398.4583 | 99.1803
3587.2542 | 1245.211 | 609.5664 | 521.8917 | 418.2435 | 533.7149 | 398.9716 | 99.1935
3588.2542 | 1245.2101 | 608.7212 | 521.9614 | 680.0199 | 533.9712 | 398.8177 | 99.222
3589.2542 | 1245.2118 | 608.902 | 521.8927 | 866.6648 | 533.4193 | 398.7059 | 99.2634
3590.2542 | 1245.2124 | 609.0085 | 521.9295 | 1113.3381 | 533.055 | 398.4003 | 99.2872
3591.2542 | 1245.2142 | 608.5422 | 522.0269 | 1344.3936 | 532.6481 | 399.5383 | 99.3075
3592.2542 | 1245.2139 | 609.1378 | 522.1633 | 1350.2002 | 532.5 | 399.6396 | 99.3448
3593.2542 | 1245.2145 | 608.9528 | 522.6249 | NaN | 532.6431 | 400.1698 | 99.3732
3594.2542 | 1245.2163 | 608.8176 | 522.5727 | 1192.5571 | 532.762 | 400.1495 | 99.4025
3595.2542 | 1245.2171 | 609.3416 | 522.7362 | NaN | 532.9312 | 400.386 | 99.4364
3596.2542 | 1245.2178 | 609.1565 | 522.8345 | NaN | 535.0666 | 400.8595 | 99.4658
3597.2542 | 1245.2183 | 608.4931 | 523.1746 | NaN | 535.9763 | 401.5616 | 99.5006
3598.2542 | 1245.2192 | 607.4495 | 523.2548 | NaN | 536.2393 | 401.5842 | 99.5175
3599.2542 | 1245.2196 | 606.3203 | 523.9445 | NaN | 536.7873 | 401.8172 | 99.561
3600.2542 | 1245.2204 | 604.0841 | 524.941 | NaN | 540.2694 | 402.0493 | 99.5884
3601.2542 | 1245.2219 | 606.8886 | 523.0465 | NaN | 540.1771 | 402.1978 | 99.6186
3602.2542 | 1223.4666 | 602.289 | 526.2265 | NaN | 544.1374 | 402.1969 | 99.6479
3603.2542 | 1245.2228 | 602.1311 | 525.9072 | NaN | 544.1414 | 402.7911 | 99.6591
3604.2542 | 1245.2247 | 604.8362 | 524.1592 | NaN | 542.2868 | 402.9812 | 99.6932
3605.2542 | 1245.2248 | 604.4476 | 524.513 | NaN | 542.8332 | 403.5976 | 99.7207
3606.2542 | 1245.2265 | 604.5002 | 526.4501 | NaN | 545.9509 | 403.8492 | 99.7488
3607.2542 | 1245.2265 | 604.4039 | 526.7214 | NaN | 545.1956 | 403.2487 | 99.7765
3608.2542 | 1245.228 | 604.0248 | 526.8882 | NaN | 544.6999 | 403.5015 | 99.7939
3609.2542 | 1245.228 | 603.3833 | 526.9376 | NaN | 543.7407 | 404.3372 | 99.8262
3610.2542 | 1245.2289 | 603.467 | 526.8304 | NaN | 543.8592 | 404.0478 | 99.8491
3611.2542 | 1245.2302 | 602.9536 | 527.0898 | NaN | 543.9462 | 404.4013 | 99.8791
3612.2542 | 1245.2318 | 603.6636 | 527.3552 | NaN | 543.3072 | 404.6347 | 99.9058
3613.2542 | 1051.7635 | 599.9992 | 528.0515 | -0.1479 | 542.6151 | 403.9817 | 99.931
3614.2542 | 1083.6618 | 599.1348 | 527.8539 | 199.0058 | 542.796 | 404.2709 | 99.966
3615.2542 | 936.7978 | 597.8758 | 528.7295 | NaN | 544.1287 | 405.1994 | 99.9963
3616.2542 | 979.6471 | 599.6503 | 528.6228 | NaN | 543.9674 | 405.3497 | 100.0154
3617.2542 | 977.5826 | 598.9107 | 528.8408 | NaN | 544.9774 | 406.0841 | 100.0552
3618.2542 | 938.9607 | 598.2201 | 529.2068 | NaN | 545.6627 | 406.0789 | 100.0794
3619.2542 | 904.3545 | 595.9594 | 529.7579 | NaN | 546.9371 | 406.2263 | 100.1124
3620.2542 | 848.5885 | 594.1749 | 530.0218 | NaN | 546.7573 | 406.2417 | 100.1282
3621.2542 | 795.2165 | 594.1425 | 530.9711 | NaN | 548.1247 | 405.9245 | 100.1573
3622.2542 | 881.3853 | 597.8047 | 529.9001 | NaN | 546.7808 | 407.1242 | 100.194
3623.2542 | 864.7686 | 596.9127 | 530.1295 | NaN | 547.7786 | 406.7442 | 100.2163
3624.2542 | 666.8968 | 593.0016 | 531.2482 | 29.5941 | 549.3704 | 407.3102 | 100.2547
3625.2542 | 755.4718 | 595.4562 | 530.4707 | 3.3878 | 547.4178 | 407.4789 | 100.2715
3626.2542 | 767.1395 | 595.184 | 530.8028 | NaN | 549.2739 | 407.8553 | 100.2956
3627.2542 | 764.3594 | 594.7314 | 531.2572 | NaN | 550.7485 | 407.6841 | 100.322
3628.2542 | 858.0583 | 604.734 | 530.6584 | 23.6155 | 550.4072 | 407.9173 | 100.3454
3629.2542 | 584.8521 | 601.8085 | 532.7651 | 28.2337 | 553.8432 | 408.3773 | 100.3727
3630.2542 | 691.0293 | 601.3168 | 529.4481 | NaN | 571.3939 | 408.6154 | 100.3807
3631.2542 | 886.272 | 604.6266 | 528.0978 | NaN | 567.2755 | 408.5459 | 100.4051
3632.2542 | 1035.38 | 606.0869 | 526.3153 | 538.1332 | 564.724 | 409.0962 | 100.4276
3633.2542 | 860.42 | 603.8186 | 527.314 | NaN | 567.3837 | 409.132 | 100.4398
3634.2542 | 613.8221 | 599.1015 | 528.9354 | 17.8195 | 570.4448 | 409.127 | 100.463
3635.2542 | 470.715 | 597.5174 | 530.0633 | 61.8342 | 573.7326 | 409.2438 | 100.5027
3636.2542 | 380.1444 | 596.5328 | 530.4573 | 99.854 | 575.4639 | 409.9658 | 100.5197
3637.2542 | 340.5999 | 595.5621 | 530.2058 | 63.4603 | 575.8138 | 409.6201 | 100.5451
3638.2542 | NaN | 589.1779 | 533.3599 | 212.4654 | 585.3225 | 409.4703 | 100.5649
3639.2542 | NaN | 589.4907 | 532.6234 | 213.5227 | 582.9826 | 409.9525 | 100.5927
3640.2542 | NaN | 591.381 | 532.5824 | 248.9581 | 582.3664 | 409.8315 | 100.6232
3641.2542 | 112.2555 | 606.5235 | 531.6794 | 192.8771 | 582.2293 | 410.5928 | 100.6391
3642.2542 | 98.0302 | 605.2066 | 531.1871 | 185.071 | 584.138 | 411.4644 | 100.664
3643.2542 | 361.5012 | 601.5565 | 533.1774 | 307.4642 | 590.0566 | 411.3234 | 100.6923
3644.2542 | NaN | 599.2971 | 536.0034 | 446.084 | 599.1284 | 411.114 | 100.7073
3645.2542 | 15.4082 | 600.305 | 533.2125 | 286.5293 | 588.2053 | 411.7993 | 100.7309
3646.2542 | 159.0078 | 594.163 | 531.5293 | 208.6064 | 583.8103 | 412.134 | 100.7699
3647.2542 | 189.3905 | 584.3719 | 530.3328 | 68.7433 | 581.3148 | 412.0403 | 100.7979
3648.2542 | NaN | 600.1203 | 533.2164 | 305.9123 | 590.7407 | 411.9521 | 100.8174
3649.2542 | 86.6814 | 604.7036 | 532.2564 | 297.2084 | 583.4563 | 412.2561 | 100.8503
3650.2542 | NaN | 598.1365 | 531.8118 | 392.7253 | 583.4553 | 412.35 | 100.8888
3651.2542 | 591.112 | 608.7056 | 527.4101 | 555.1104 | 536.9618 | 412.6167 | 100.9111
3652.2542 | 614.989 | 608.2612 | 527.3611 | 556.646 | 535.6664 | 413.0153 | 100.9361
3653.2542 | 621.1665 | 608.0043 | 527.3993 | 555.3248 | 535.4884 | 412.3793 | 100.9709
3654.2542 | 619.4105 | 607.7618 | 527.3975 | 554.6753 | 534.9728 | 412.1672 | 100.9929
3655.2542 | 617.7939 | 607.3634 | 527.4057 | 554.0177 | 535.8714 | 412.6316 | 101.0084
3656.2542 | 617.1282 | 606.494 | 527.4573 | 555.3538 | 535.622 | 412.6676 | 101.0499
3657.2542 | 614.2013 | 606.3083 | 527.4543 | 555.2851 | 535.1618 | 412.9506 | 101.0664
3658.2542 | 611.9461 | 606.4652 | 527.5977 | 555.1439 | 535.7103 | 412.7106 | 101.104
3659.2542 | 610.2299 | 606.2842 | 527.5564 | 555.7535 | 534.4932 | 412.2637 | 101.1231
3660.2542 | 611.5179 | 606.0918 | 527.5967 | 555.8307 | 534.1143 | 413.4304 | 101.1549
3661.2542 | 616.069 | 605.9569 | 527.4831 | 556.0857 | 535.6196 | 413.7728 | 101.1822
3662.2542 | 618.7091 | 605.8584 | 527.3781 | 555.687 | 535.2239 | 414.0531 | 101.203
3663.2542 | 616.8662 | 605.7774 | 527.4437 | 555.4275 | 536.5235 | 414.3843 | 101.2286
3664.2542 | 618.8211 | 605.6976 | 527.4145 | 554.7304 | 536.2709 | 413.9559 | 101.2435
3665.2542 | 617.3224 | 605.6572 | 527.567 | 554.8754 | 535.3807 | 414.3624 | 101.2799
3666.2542 | 617.6492 | 605.489 | 527.4919 | 554.9259 | 534.9782 | 415.2748 | 101.3016
3667.2542 | 620.2095 | 605.1911 | 527.5315 | 554.8102 | 535.6381 | 415.0012 | 101.3357
3668.2542 | 629.9266 | 605.513 | 527.4141 | 554.1743 | 535.3618 | 415.4859 | 101.3572
3669.2542 | 630.0273 | 605.809 | 527.4994 | 553.6398 | 535.4197 | 415.9577 | 101.3823
3670.2542 | 627.4851 | 605.2194 | 527.5538 | 553.465 | 534.8107 | 416.2082 | 101.416
3671.2542 | 626.3266 | 605.0669 | 527.5157 | 553.3806 | 535.4764 | 416.6195 | 101.4282
3672.2542 | 625.8052 | 605.5138 | 527.4474 | 553.2381 | 535.1775 | 416.1575 | 101.4515
3673.2542 | 635.7949 | 605.831 | 527.38 | 554.3474 | 534.6527 | 415.9468 | 101.4841
3674.2542 | 632.4462 | 605.8023 | 527.3295 | 554.9199 | 533.8447 | 416.188 | 101.5108
3675.2542 | 637.5559 | 605.8172 | 527.304 | 554.768 | 534.1341 | 417.4203 | 101.5281
3676.2542 | 638.7715 | 605.7317 | 527.1865 | 554.2559 | 533.753 | 417.5082 | 101.558
3677.2542 | 636.0381 | 605.3368 | 527.1435 | 553.9976 | 532.8005 | 417.7304 | 101.5809
3678.2542 | 637.8876 | 605.3986 | 527.0876 | 553.8802 | 531.9348 | 418.0726 | 101.6066
3679.2542 | 637.7892 | 605.573 | 526.9717 | 554.7826 | 531.0899 | 418.4125 | 101.6254
3680.2542 | 639.0071 | 605.6685 | 526.9326 | 555.2105 | 531.3156 | 418.8507 | 101.6534
3681.2542 | 642.0877 | 605.7186 | 526.8426 | 555.5593 | 532.1082 | 419.091 | 101.6763
3682.2542 | 641.6951 | 605.8021 | 526.8157 | 555.419 | 532.9095 | 419.6076 | 101.704
3683.2542 | 640.2462 | 606.1978 | 526.789 | 555.5521 | 532.3911 | 419.1641 | 101.7315
3684.2542 | 635.7985 | 606.3072 | 526.7287 | 554.9446 | 532.1354 | 419.6061 | 101.754
3685.2542 | 632.3586 | 606.0337 | 526.6571 | 554.1949 | 532.5311 | 419.3711 | 101.7736
3686.2542 | 626.0285 | 606.3308 | 526.6552 | 554.1248 | 533.4451 | 420.9902 | 101.7945
3687.2542 | 621.2299 | 606.1842 | 526.7356 | 553.5901 | 532.8031 | 420.5244 | 101.8086
3688.2542 | 616.4555 | 605.9318 | 526.871 | 553.7857 | 531.941 | 420.576 | 101.8345
3689.2542 | 615.3825 | 605.2987 | 527.0003 | 554.2265 | 531.1409 | 420.894 | 101.8602
3690.2542 | 612.7184 | 605.0037 | 527.1016 | 553.8917 | 531.0969 | 420.879 | 101.8834
3691.2542 | 619.7087 | 605.0136 | 527.1516 | 554.1962 | 530.9205 | 421.0105 | 101.9049
3692.2542 | 629.5358 | 605.1537 | 527.3138 | 555.0389 | 530.059 | 420.3083 | 101.9204
3693.2542 | 641.1281 | 604.9816 | 527.1866 | 555.0948 | 529.8425 | 421.2175 | 101.9433
3694.2542 | 647.4008 | 605.1825 | 527.3179 | 554.9644 | 529.8056 | 421.701 | 101.9611
3695.2542 | 647.7011 | 605.1446 | 527.3921 | 554.6853 | 530.5453 | 423.0957 | 101.9817
3696.2542 | 646.4632 | 605.5797 | 527.5203 | 553.9175 | 531.152 | 422.7668 | 101.9969
3697.2542 | 639.5558 | 605.3256 | 527.5346 | 553.4337 | 531.5113 | 423.255 | 102.0218
3698.2542 | 636.032 | 605.2396 | 527.5317 | 553.6856 | 531.9862 | 423.3191 | 102.0326
3699.2542 | 633.5044 | 605.3269 | 527.63 | 554.0673 | 533.2459 | 423.5421 | 102.0571
3700.2542 | 633.5902 | 604.9645 | 527.798 | 554.1779 | 533.1707 | 422.6412 | 102.0737
3701.2542 | 634.7233 | 604.7561 | 527.9213 | 554.2981 | 532.9467 | 424.7018 | 102.0858
3702.2542 | 634.126 | 605.0141 | 527.9037 | 553.87 | 532.5588 | 423.7095 | 102.1068
3703.2542 | 632.228 | 604.9375 | 527.731 | 553.48 | 532.7407 | 424.5937 | 102.1099
3704.2542 | 628.9602 | 605.2101 | 527.6606 | 553.0521 | 533.1249 | 425.2477 | 102.1424
3705.2542 | 626.714 | 605.2549 | 527.5884 | 552.4338 | 533.0089 | 424.803 | 102.159
3706.2542 | 623.7878 | 604.4068 | 527.4918 | 552.0219 | 532.8779 | 424.9989 | 102.1695
3707.2542 | 623.3807 | 603.7466 | 527.658 | 553.1825 | 532.2738 | 425.1196 | 102.1899
3708.2542 | 635.2298 | 603.8458 | 527.8361 | 553.7724 | 532.1389 | 425.6303 | 102.2084
3709.2542 | 639.8926 | 603.9075 | 527.8244 | 553.2046 | 531.9699 | 425.7835 | 102.2275
3710.2542 | 646.2579 | 603.6822 | 527.5841 | 552.3844 | 532.7416 | 426.0197 | 102.2458
3711.2542 | 645.9985 | 603.7824 | 527.4765 | 551.8166 | 533.2368 | 425.9224 | 102.2667
3712.2542 | 643.0852 | 603.9743 | 527.3789 | 551.5249 | 534.2134 | 425.7909 | 102.2795
3713.2542 | 639.7353 | 603.7739 | 527.3423 | 551.4584 | 533.3499 | 425.5785 | 102.2954
3714.2542 | 643.9129 | 603.7694 | 527.505 | 551.2627 | 532.5553 | 426.1598 | 102.3146
3715.2542 | 646.6456 | 603.8721 | 527.3969 | 551.289 | 532.6421 | 426.613 | 102.3304
3716.2542 | 646.4696 | 603.9411 | 527.3688 | 551.5574 | 533.073 | 427.0905 | 102.3598
3717.2542 | 646.8451 | 604.1487 | 527.3758 | 551.8017 | 534.4506 | 426.7423 | 102.3663
3718.2542 | 640.3691 | 604.0473 | 527.3536 | 551.8223 | 534.6572 | 427.5332 | 102.398
3719.2542 | 637.01 | 603.8693 | 527.3907 | 552.6919 | 534.1583 | 426.9577 | 102.4194
3720.2542 | 635.8902 | 603.3606 | 527.5352 | 552.7678 | 533.8193 | 427.0628 | 102.4456
3721.2542 | 635.0316 | 603.3325 | 527.4833 | 552.3866 | 533.349 | 427.4846 | 102.459
3722.2542 | 631.7382 | 603.1338 | 527.4229 | 551.7333 | 532.4245 | 427.6156 | 102.4828
3723.2542 | 632.1684 | 602.8888 | 527.3693 | 551.5848 | 532.1848 | 426.2909 | 102.4985
3724.2542 | 628.0161 | 602.8584 | 527.3491 | 551.3835 | 532.6281 | 426.394 | 102.5298
3725.2542 | 630.1696 | 602.9337 | 527.3774 | 551.3715 | 532.3981 | 426.9259 | 102.5492
3726.2542 | 632.4694 | 602.6187 | 527.2962 | 552.0422 | 533.7395 | 427.7454 | 102.567
3727.2542 | 641.2487 | 602.7881 | 527.4197 | 551.6027 | 533.3567 | 428.2226 | 102.5981
3728.2542 | 648.8311 | 603.3655 | 527.4768 | 551.4522 | 533.005 | 428.3206 | 102.623
3729.2542 | 653.7397 | 603.3898 | 527.4264 | 550.977 | 532.9737 | 429.0786 | 102.6366
3730.2542 | 656.3972 | 603.6949 | 527.5943 | 551.6406 | 533.1431 | 428.9582 | 102.6565
3731.2542 | 660.6683 | 604.0083 | 527.5949 | 551.672 | 533.1788 | 428.9673 | 102.6843
3732.2542 | 669.9986 | 604.1115 | 527.7129 | 551.2071 | 535.4811 | 429.2927 | 102.7042
3733.2542 | 664.0662 | 604.4183 | 527.7828 | 550.8608 | 535.2945 | 429.7402 | 102.7275
3734.2542 | 659.6327 | 604.4315 | 527.7676 | 551.1881 | 535.8351 | 429.7366 | 102.7557
3735.2542 | 659.6302 | 603.9566 | 527.8408 | 551.4507 | 536.545 | 429.3095 | 102.7795
3736.2542 | 653.597 | 604.1191 | 527.8555 | 551.1981 | 536.461 | 428.7347 | 102.8071
3737.2542 | 645.5202 | 604.1969 | 527.8456 | 550.6778 | 535.5568 | 428.8464 | 102.8223
3738.2542 | 639.812 | 603.8352 | 527.7084 | 550.3647 | 535.1116 | 429.0262 | 102.8416
3739.2542 | 636.3857 | 603.2459 | 527.6875 | 550.4413 | 534.8778 | 429.7243 | 102.8591
3740.2542 | 645.2338 | 603.4287 | 527.6581 | 550.0493 | 534.681 | 430.2882 | 102.8886
3741.2542 | 645.7228 | 603.4421 | 527.6767 | 549.3474 | 533.7827 | 430.748 | 102.8946
3742.2542 | 650.5065 | 603.6158 | 527.6007 | 549.2409 | 533.7878 | 430.6212 | 102.9278
3743.2542 | 652.8767 | 603.8331 | 527.5678 | 549.3138 | 533.9716 | 431.0561 | 102.9293
3744.2542 | 654.4255 | 604.1935 | 527.6863 | 550.3706 | 534.1316 | 431.5325 | 102.9662
3745.2542 | 649.1477 | 604.5282 | 527.5835 | 550.1311 | 535.1971 | 431.8847 | 102.9847
3746.2542 | 651.0967 | 604.0938 | 527.6187 | 549.9938 | 534.8767 | 432.6082 | 102.9981
3747.2542 | 661.5014 | 603.555 | 527.4574 | 549.8376 | 535.728 | 432.4142 | 103.021
3748.2542 | 665.2533 | 603.8369 | 527.5175 | 549.1769 | 536.2756 | 433.0634 | 103.0386
3749.2542 | 662.4028 | 603.6224 | 527.5815 | 548.4764 | 536.2016 | 434.125 | 103.0462
3750.2542 | 657.013 | 604.2025 | 527.5019 | 547.7477 | 535.7451 | 433.212 | 103.0636
3751.2542 | 653.8591 | 604.0396 | 527.4976 | 547.8231 | 536.3258 | 432.251 | 103.0888
3752.2542 | 657.4123 | 604.167 | 527.6015 | 548.1931 | 535.8144 | 433.7894 | 103.0936
3753.2542 | 659.6241 | 604.192 | 527.5713 | 548.4803 | 534.9806 | 432.83 | 103.1124
3754.2542 | 667.5114 | 604.0244 | 527.5691 | 542.5309 | 548.4608 | 444.2121 | 103.1253
3755.2542 | 664.4352 | 604.0218 | 527.4823 | 540.8584 | 552.5846 | 447.4785 | 103.1426
3756.2542 | 663.9541 | 603.8491 | 527.4228 | 540.4406 | 552.9553 | 447.6875 | 103.1593
3757.2542 | 660.6718 | 604.1457 | 527.5036 | 540.3113 | 553.8368 | 447.9609 | 103.1669
3758.2542 | 657.796 | 604.0212 | 527.4606 | 540.2842 | 554.1578 | 448.5172 | 103.1992
3759.2542 | 655.917 | 604.2177 | 527.3143 | 540.1853 | 555.1227 | 448.7027 | 103.2066
3760.2542 | 657.9486 | 604.1993 | 527.3004 | 539.9652 | 554.4385 | 448.9844 | 103.2246
3761.2542 | 652.4184 | 604.3543 | 527.3705 | 539.6428 | 553.9929 | 450.0329 | 103.234
3762.2542 | 649.0357 | 604.1765 | 527.3957 | 538.9283 | 554.6885 | 450.2647 | 103.2587
3763.2542 | 650.2284 | 603.8177 | 527.486 | 538.6499 | 554.0339 | 450.9484 | 103.2704
3764.2542 | 654.7667 | 604.233 | 527.3107 | 539.7278 | 552.7094 | 450.5416 | 103.2838
3765.2542 | 653.2693 | 604.4749 | 527.3591 | 540.7722 | 552.0651 | 450.9104 | 103.2953
3766.2542 | 661.1683 | 604.497 | 527.3978 | 541.0136 | 552.6377 | 451.3633 | 103.3158
3767.2542 | 657.0999 | 604.6771 | 527.4118 | 540.7718 | 552.215 | 450.0498 | 103.3351
3768.2542 | 651.9208 | 605.0221 | 527.5386 | 541.1509 | 552.0741 | 450.3022 | 103.3606
3769.2542 | 647.0164 | 604.9276 | 527.5093 | 541.4365 | 551.4021 | 450.5998 | 103.3745
3770.2542 | 652.814 | 605.1127 | 527.5719 | 541.8215 | 551.6875 | 451.0528 | 103.3885
3771.2542 | 652.1665 | 604.9788 | 527.5624 | 541.6016 | 551.493 | 451.1045 | 103.4094
3772.2542 | 653.1743 | 604.8526 | 527.5656 | 542.2465 | 551.4913 | 451.0501 | 103.4276
3773.2542 | 650.2308 | 604.9668 | 527.6606 | 542.6729 | 551.651 | 451.5672 | 103.4428
3774.2542 | 650.5687 | 604.8116 | 527.6327 | 542.6603 | 551.4198 | 451.2468 | 103.4655
3775.2542 | 653.618 | 604.8226 | 527.677 | 542.281 | 550.4155 | 451.2993 | 103.4808
3776.2542 | 655.166 | 604.2997 | 527.672 | 541.6635 | 549.5208 | 450.9866 | 103.4877
3777.2542 | 656.1524 | 604.1464 | 527.6192 | 541.2445 | 548.9172 | 451.6205 | 103.5101
3778.2542 | 668.1677 | 604.3655 | 527.6696 | 541.1753 | 548.9776 | 452.3408 | 103.53
3779.2542 | 673.9518 | 604.4623 | 527.8043 | 541.0324 | 549.5513 | 453.0973 | 103.5481
3780.2542 | 673.6111 | 603.9715 | 527.9181 | 541.2564 | 549.3547 | 453.324 | 103.5627
3781.2542 | 662.5717 | 604.3398 | 528.0839 | 541.1616 | 548.6442 | 453.0341 | 103.5842
3782.2542 | 653.7118 | 604.1387 | 528.0968 | 541.3014 | 548.1538 | 452.8614 | 103.5934
3783.2542 | 656.0356 | 603.8334 | 528.1986 | 541.6922 | 548.4814 | 452.5349 | 103.6169
3784.2542 | 660.3279 | 603.5354 | 528.2545 | 542.3003 | 548.6976 | 453.3392 | 103.6329
3785.2542 | 655.6574 | 603.4316 | 528.3808 | 542.3896 | 548.9408 | 453.818 | 103.6452
3786.2542 | 654.2072 | 603.096 | 528.4268 | 541.9788 | 548.8617 | 453.7871 | 103.6698
3787.2542 | 649.6506 | 602.8327 | 528.4695 | 541.7462 | 548.888 | 453.8476 | 103.6798
3788.2542 | 653.8094 | 603.0851 | 528.5306 | 543.4468 | 548.553 | 452.9273 | 103.7094
3789.2542 | 646.993 | 602.5945 | 528.6147 | 543.3558 | 549.4352 | 453.8387 | 103.7229
3790.2542 | 649.2189 | 602.7089 | 528.7836 | 543.278 | 550.7682 | 454.1386 | 103.7419
3791.2542 | 651.4839 | 602.4423 | 528.8732 | 543.0472 | 550.6104 | 453.9782 | 103.7602
3792.2542 | 659.8986 | 602.0967 | 528.9831 | 542.4778 | 550.3083 | 453.7793 | 103.7817
3793.2542 | 665.2938 | 602.3078 | 529.0127 | 542.1632 | 549.3679 | 453.5667 | 103.8038
3794.2542 | 668.2282 | 602.3197 | 529.0795 | 542.0109 | 548.8092 | 454.0864 | 103.8268
3795.2542 | 669.069 | 602.589 | 529.1478 | 543.2635 | 548.2617 | 454.4085 | 103.8464
3796.2542 | 671.5697 | 602.2901 | 529.1169 | 544.0507 | 549.2007 | 454.4601 | 103.8686
3797.2542 | 662.2818 | 601.8047 | 529.0328 | 543.6105 | 550.648 | 454.8375 | 103.8882
3798.2542 | 653.4043 | 601.4843 | 529.0964 | 544.088 | 550.7975 | 455.022 | 103.9101
3799.2542 | 647.984 | 601.7153 | 528.9619 | 543.6002 | 551.4484 | 454.7956 | 103.9282
3800.2542 | 655.0226 | 601.8397 | 528.8829 | 543.2106 | 550.7881 | 454.2034 | 103.9406
3801.2542 | 662.6682 | 601.592 | 528.9244 | 543.7335 | 550.2661 | 454.5787 | 103.9584
3802.2542 | 662.9448 | 601.6235 | 529.023 | 543.1907 | 549.8819 | 454.7657 | 103.9747
3803.2542 | 664.412 | 601.3492 | 528.9747 | 542.8809 | 549.0866 | 424.808 | 103.9924
3804.2542 | 667.5636 | 601.2302 | 528.9193 | 542.6271 | 547.788 | 424.4967 | 104.017
3805.2542 | 663.0775 | 601.0841 | 528.9434 | 543.42 | 548.6406 | 424.4275 | 104.0246
3806.2542 | 668.2351 | 601.2871 | 529.0469 | 543.8259 | 549.7881 | 425.0344 | 104.0364
3807.2542 | 663.3109 | 600.7086 | 529.0301 | 543.5689 | 549.2409 | 425.3809 | 104.0708
3808.2542 | 654.8315 | 600.984 | 528.966 | 544.0521 | 548.5385 | 425.0596 | 104.0849
3809.2542 | 652.1157 | 601.1626 | 528.891 | 543.5232 | 548.3164 | 425.2452 | 104.095
3810.2542 | 653.7939 | 600.2156 | 528.9368 | 543.272 | 548.6646 | 425.518 | 104.1174
3811.2542 | 650.5702 | 599.9789 | 528.8422 | 542.7684 | 548.435 | 425.7877 | 104.1404
3812.2542 | 644.8388 | 600.2561 | 529.0021 | 542.2365 | 548.4573 | 425.686 | 104.1545
3813.2542 | 641.3481 | 600.0836 | 529.0334 | 541.8149 | 548.0853 | 425.8785 | 104.1794
3814.2542 | 646.6013 | 599.6456 | 529.0185 | 541.1912 | 547.5589 | 426.4042 | 104.192
3815.2542 | 650.2901 | 600.0632 | 529.0189 | 540.6334 | 546.4653 | 426.1631 | 104.2162
3816.2542 | 645.5259 | 599.8897 | 529.0882 | 540.3856 | 545.3723 | 425.937 | 104.2425
3817.2542 | 648.4284 | 599.4942 | 529.023 | 540.3957 | 544.5523 | 426.5529 | 104.2559
3818.2542 | 653.2871 | 599.7889 | 529.1627 | 539.8735 | 543.9185 | 426.3368 | 104.2752
3819.2542 | 657.3835 | 599.6318 | 529.2755 | 539.6129 | 542.9161 | 426.1995 | 104.2911
3820.2542 | 654.0882 | 599.5056 | 529.3835 | 538.9582 | 542.3783 | 426.5175 | 104.3164
3821.2542 | 657.708 | 599.1303 | 529.4688 | 538.4276 | 541.9145 | 426.2849 | 104.3362
3822.2542 | 649.8168 | 599.1837 | 529.4612 | 538.4523 | 541.5543 | 426.4815 | 104.3564
3823.2542 | 651.3238 | 599.332 | 529.3959 | 537.8219 | 541.385 | 426.8084 | 104.3666
3824.2542 | 643.1052 | 599.4583 | 529.4556 | 537.6907 | 541.8109 | 427.0252 | 104.3961
3825.2542 | 637.0654 | 599.0167 | 529.4965 | 537.3835 | 542.512 | 427.7595 | 104.4168
3826.2542 | 633.6466 | 598.9881 | 529.4104 | 537.2475 | 542.0425 | 427.7952 | 104.4345
3827.2542 | 649.0134 | 598.9416 | 529.2488 | 537.4182 | 542.4684 | 428.0584 | 104.449
3828.2542 | 658.3762 | 598.9435 | 529.2503 | 537.5056 | 543.0129 | 428.4387 | 104.4672
3829.2542 | 650.0742 | 599.0238 | 529.2601 | 537.0092 | 542.5652 | 428.4879 | 104.4817
3830.2542 | 655.7117 | 599.3251 | 529.2494 | 537.1988 | 542.5673 | 428.9373 | 104.5063
3831.2542 | 662.1074 | 599.5288 | 529.1686 | 537.5811 | 542.8232 | 428.6915 | 104.5236
3832.2542 | 661.974 | 599.7748 | 529.1081 | 538.2469 | 543.4418 | 428.7626 | 104.5495
3833.2542 | 662.9746 | 599.2871 | 529.1355 | 538.7127 | 543.1923 | 429.2012 | 104.5732
3834.2542 | 662.1817 | 599.5347 | 528.9804 | 538.9137 | 542.8276 | 429.0076 | 104.5871
3835.2542 | 676.0846 | 599.9865 | 528.8384 | 539.372 | 542.7616 | 429.2069 | 104.6063
3836.2542 | 666.6606 | 600.1929 | 528.7263 | 539.6899 | 541.8083 | 428.9816 | 104.6203
3837.2542 | 670.5745 | 600.0727 | 528.6947 | 540.7074 | 541.1713 | 429.1984 | 104.6471
3838.2542 | 663.5178 | 600.1506 | 528.6401 | 540.2877 | 541.3535 | 429.7213 | 104.6532
3839.2542 | 661.3309 | 600.2884 | 528.538 | 541.5885 | 541.9563 | 430.064 | 104.69
3840.2542 | 660.7795 | 600.2919 | 528.4996 | 540.713 | 543.109 | 430.4035 | 104.6978
3841.2542 | 657.4257 | 600.314 | 528.2967 | 540.7226 | 544.0884 | 430.5206 | 104.7202
3842.2542 | 666.8171 | 600.2557 | 528.2245 | 540.6816 | 544.0663 | 430.4904 | 104.7463
3843.2542 | 667.4846 | 600.3269 | 528.2484 | 541.044 | 543.6274 | 431.0324 | 104.7668
3844.2542 | 660.7339 | 600.5365 | 528.1273 | 541.5301 | 542.6424 | 430.9482 | 104.7847
3845.2542 | 655.1351 | 600.8195 | 527.9695 | 541.3946 | 543.2114 | 431.3073 | 104.8081
3846.2542 | 659.197 | 601.0141 | 527.9915 | 541.5186 | 544.1145 | 431.9475 | 104.8251
3847.2542 | 665.8668 | 600.9805 | 528.0227 | 541.1846 | 543.6045 | 431.4905 | 104.8427
3848.2542 | 662.2577 | 600.8529 | 528.0344 | 541.6707 | 543.9815 | 431.7558 | 104.8636
3849.2542 | 658.8026 | 601.1096 | 527.9919 | 542.2335 | 544.5579 | 431.9544 | 104.8657
3850.2542 | 658.6803 | 601.3242 | 527.9865 | 542.707 | 544.5108 | 431.9255 | 104.8913
3851.2542 | 651.278 | 601.0279 | 527.9354 | 542.4758 | 544.4981 | 432.0472 | 104.9057
3852.2542 | 663.6701 | 601.1261 | 527.974 | 543.1062 | 543.7743 | 432.156 | 104.926
3853.2542 | 662.5146 | 601.3655 | 527.9719 | 544.1804 | 543.8564 | 432.4302 | 104.9455
3854.2542 | 668.7046 | 601.5107 | 527.9017 | 543.8789 | 544.0353 | 432.656 | 104.9569
3855.2542 | 677.2135 | 601.7241 | 528.0022 | 543.3598 | 543.5419 | 432.6823 | 104.9756
3856.2542 | 677.5103 | 601.9086 | 528.0357 | 544.0385 | 544.1678 | 432.8658 | 104.9886
3857.2542 | 678.0034 | 602.1827 | 527.928 | 544.2009 | 545.7744 | 432.9553 | 105.0118
3858.2542 | 675.868 | 602.2212 | 527.9052 | 544.7937 | 545.4373 | 432.8402 | 105.0222
3859.2542 | 672.2514 | 602.369 | 527.6263 | 544.3935 | 544.6272 | 432.7184 | 105.0359
3860.2542 | 673.9311 | 602.5625 | 527.4689 | 545.2104 | 543.5735 | 433.0799 | 105.0552
3861.2542 | 676.0668 | 602.5551 | 527.3675 | 544.8435 | 542.3237 | 432.7122 | 105.061
3862.2542 | 665.2371 | 602.7258 | 527.3063 | 544.6745 | 543.0425 | 433.2109 | 105.0752
3863.2542 | 659.4488 | 602.5022 | 527.2071 | 544.0814 | 542.6201 | 432.8257 | 105.0992
3864.2542 | 659.5501 | 602.4305 | 527.0735 | 544.0813 | 541.3006 | 432.7986 | 105.1117
3865.2542 | 668.609 | 601.6504 | 527.1045 | 544.4339 | 540.8088 | 432.9142 | 105.1199
3866.2542 | 673.0481 | 602.1331 | 527.0381 | 544.3437 | 539.7758 | 432.7613 | 105.139
3867.2542 | 666.3722 | 602.2002 | 526.9626 | 543.9181 | 540.3165 | 433.2299 | 105.1492
3868.2542 | 657.2093 | 601.7638 | 526.971 | 543.5179 | 539.3258 | 433.0871 | 105.1505
3869.2542 | 649.6775 | 601.4828 | 526.8585 | 542.7991 | 537.3126 | 432.8609 | 105.1795
3870.2542 | 644.5548 | 601.422 | 526.8693 | 543.1044 | 537.7614 | 433.0502 | 105.1953
3871.2542 | 640.8364 | 601.252 | 526.9015 | 541.856 | 535.3617 | 432.5662 | 105.2177
3872.2542 | 641.8156 | 601.3796 | 526.8303 | 541.5517 | 536.0579 | 433.1001 | 105.2309
3873.2542 | 642.6 | 601.2917 | 526.7576 | 541.1547 | 534.9204 | 433.4175 | 105.2486
3874.2542 | 636.5724 | 601.4442 | 526.7102 | 541.4806 | 534.679 | 433.0081 | 105.2593
3875.2542 | 637.4531 | 600.9961 | 526.6503 | 540.8097 | 533.0142 | 432.7708 | 105.2707
3876.2542 | 631.3464 | 600.8714 | 526.5575 | 541.0424 | 532.4495 | 432.816 | 105.2872
3877.2542 | 632.8633 | 600.9038 | 526.4779 | 541.3972 | 532.8396 | 433.2639 | 105.2973
3878.2542 | 634.457 | 600.7083 | 526.3182 | 541.3558 | 532.1911 | 432.938 | 105.3146
3879.2542 | 629.3948 | 600.6215 | 526.3258 | 541.4336 | 533.7791 | 433.4131 | 105.3349
3880.2542 | 626.4134 | 600.1347 | 526.2915 | 541.2273 | 534.6951 | 433.461 | 105.3497
3881.2542 | 630.4757 | 599.8134 | 526.2813 | 541.3048 | 534.5048 | 433.6809 | 105.3658
3882.2542 | 643.9503 | 599.8802 | 526.266 | 541.4768 | 533.7294 | 433.9103 | 105.3798
3883.2542 | 644.7885 | 599.6686 | 526.1571 | 540.654 | 533.0045 | 433.9741 | 105.4066
3884.2542 | 642.777 | 599.0743 | 526.1478 | 539.4685 | 532.7785 | 434.2106 | 105.4273
3885.2542 | 638.5377 | 598.6741 | 526.2071 | 536.7585 | 532.742 | 435.3828 | 105.4523
3886.2542 | 639.3071 | 598.1872 | 526.396 | 536.082 | 532.8217 | 434.6948 | 105.4738
3887.2542 | 644.293 | 597.7454 | 526.5071 | 534.7398 | 534.936 | 434.9672 | 105.5159
3888.2542 | 650.7195 | 597.2151 | 526.5703 | 530.128 | 535.144 | 434.9762 | 105.5278
3889.2542 | 646.8119 | 597.1205 | 526.5816 | 529.777 | 534.8099 | 435.1111 | 105.5575
3890.2542 | 658.6146 | 596.8625 | 526.6283 | 529.8129 | 533.9746 | 434.9575 | 105.5893
3891.2542 | 653.4169 | 596.5747 | 526.4794 | 529.9447 | 533.6446 | 434.9547 | 105.6202
3892.2542 | 650.6537 | 596.3559 | 526.4551 | 530.0311 | 533.1144 | 435.0219 | 105.636
3893.2542 | 652.392 | 596.3175 | 526.4329 | 529.8695 | 532.2704 | 434.9451 | 105.6609
3894.2542 | 656.7546 | 596.0378 | 526.6023 | 530.0259 | 532.9328 | 435.6706 | 105.6787
3895.2542 | 658.6135 | 595.6397 | 526.6222 | 532.0034 | 532.0672 | 435.2728 | 105.6971
3896.2542 | 649.5992 | 595.2221 | 526.7047 | 532.5714 | 531.4721 | 435.1362 | 105.7206
3897.2542 | 658.2215 | 594.8726 | 526.7576 | 531.7676 | 530.598 | 435.0259 | 105.7345
3898.2542 | 665.8235 | 594.6239 | 526.7255 | 531.0998 | 530.8832 | 435.3445 | 105.7708
3899.2542 | 664.3497 | 594.5411 | 526.8059 | 531.0077 | 531.0953 | 435.6371 | 105.779
3900.2542 | 659.3091 | 595.0104 | 526.8736 | 531.4429 | 531.851 | 435.7839 | 105.7921
3901.2542 | 656.9603 | 594.7016 | 526.8744 | 532.43 | 531.6146 | 435.8206 | 105.8119
3902.2542 | 666.6595 | 594.8643 | 526.6973 | 533.6066 | 530.72 | 435.5255 | 105.8296
3903.2542 | 666.4488 | 595.0682 | 526.7407 | 533.7733 | 530.6212 | 435.6815 | 105.8558
3904.2542 | 672.5504 | 595.0025 | 526.7286 | 534.0686 | 530.6904 | 435.9384 | 105.8702
3905.2542 | 670.7315 | 595.1225 | 526.7432 | 533.4918 | 531.3828 | 435.9933 | 105.8883
3906.2542 | 671.209 | 595.3887 | 526.6921 | 533.3284 | 531.7991 | 436.2443 | 105.9091
3907.2542 | 663.5653 | 595.0518 | 526.7283 | 533.9149 | 531.3146 | 436.1736 | 105.9247
3908.2542 | 659.0761 | 594.8752 | 526.6662 | 535.0179 | 530.9134 | 436.3468 | 105.9527
3909.2542 | 663.4642 | 594.9999 | 526.6855 | 534.5036 | 531.3566 | 436.3807 | 105.9624
3910.2542 | 664.6054 | 594.7899 | 526.623 | 533.8603 | 531.6445 | 436.6807 | 105.9805
3911.2542 | 654.4259 | 594.4228 | 526.5425 | 533.3698 | 531.5468 | 436.6638 | 106.0154
3912.2542 | 648.8103 | 594.6731 | 526.5357 | 532.7551 | 532.105 | 437.1174 | 106.0278
3913.2542 | 646.4601 | 594.6852 | 526.4364 | 532.2522 | 533.0924 | 437.3683 | 106.0418
3914.2542 | 641.5679 | 594.559 | 526.402 | 532.0079 | 533.0941 | 437.309 | 106.0644
3915.2542 | 647.1499 | 593.7795 | 526.377 | 531.8383 | 532.6998 | 437.1505 | 106.0843
3916.2542 | 652.5846 | 593.7303 | 526.339 | 531.6093 | 532.5676 | 437.0923 | 106.0957
3917.2542 | 655.1214 | 593.4475 | 526.4079 | 532.1385 | 533.482 | 437.6495 | 106.111
3918.2542 | 656.9064 | 593.2771 | 526.4708 | 531.9777 | 533.3694 | 437.6227 | 106.1389
3919.2542 | 661.3738 | 593.5388 | 526.5183 | 531.5327 | 533.0881 | 437.7499 | 106.1517
3920.2542 | 668.252 | 593.3287 | 526.595 | 531.0147 | 532.6669 | 437.6772 | 106.1746
3921.2542 | 661.844 | 593.5067 | 526.6608 | 530.8418 | 532.6158 | 437.5722 | 106.1917
3922.2542 | 665.2483 | 593.0698 | 526.7766 | 530.453 | 532.4301 | 437.7113 | 106.2119
3923.2542 | 665.4004 | 593.1986 | 526.809 | 530.0891 | 531.6473 | 437.6533 | 106.2375
3924.2542 | 667.2283 | 593.1576 | 526.8061 | 529.7399 | 531.2262 | 438.1064 | 106.2512
3925.2542 | 656.1312 | 592.4259 | 526.799 | 529.8521 | 531.7169 | 438.2085 | 106.2811
3926.2542 | 648.521 | 592.6972 | 526.9415 | 530.1705 | 532.3095 | 438.599 | 106.2994
3927.2542 | 648.9375 | 592.407 | 526.9691 | 531.0186 | 531.9718 | 438.6788 | 106.3094
3928.2542 | 658.3488 | 592.4193 | 526.9854 | 531.4533 | 531.5626 | 438.7221 | 106.3189
3929.2542 | 661.5974 | 592.2717 | 527.0438 | 531.5121 | 531.6026 | 439.1008 | 106.3422
3930.2542 | 659.8202 | 592.2708 | 527.1271 | 530.8282 | 531.3301 | 439.0241 | 106.3653
3931.2542 | 652.4318 | 592.2925 | 527.0639 | 530.7625 | 530.9003 | 438.9774 | 106.3891
3932.2542 | 647.278 | 592.3165 | 527.0899 | 531.101 | 530.2044 | 438.6597 | 106.4092
3933.2542 | 642.1957 | 591.9174 | 526.9913 | 530.7687 | 530.1141 | 438.8776 | 106.417
3934.2542 | 639.5241 | 591.8913 | 527.0367 | 530.363 | 529.9755 | 438.9698 | 106.4401
3935.2542 | 642.3983 | 591.6309 | 526.9267 | 530.2549 | 529.5945 | 439.283 | 106.4612
3936.2542 | 645.8077 | 591.5978 | 526.903 | 530.097 | 529.8061 | 439.4994 | 106.4687
3937.2542 | 644.9595 | 590.8905 | 526.9251 | 530.3831 | 530.3983 | 439.4815 | 106.4896
3938.2542 | 641.2712 | 590.7836 | 526.881 | 530.3908 | 531.5012 | 439.7312 | 106.5066
3939.2542 | 644.3366 | 591.0363 | 526.822 | 531.9016 | 531.0608 | 439.4873 | 106.5238
3940.2542 | 644.2118 | 591.1396 | 526.8775 | 532.4224 | 531.6584 | 440.0376 | 106.5397
3941.2542 | 656.0602 | 590.9002 | 526.9111 | 533.0035 | 531.6349 | 439.76 | 106.5576
3942.2542 | 661.7992 | 590.6432 | 526.9002 | 532.5798 | 531.9497 | 439.9636 | 106.5701
3943.2542 | 656.3799 | 590.7876 | 527.0089 | 532.7554 | 533.0725 | 439.9048 | 106.6068
3944.2542 | 655.887 | 590.8474 | 527.0814 | 532.3239 | 533.0562 | 439.9395 | 106.618
3945.2542 | 667.0617 | 590.9872 | 527.1147 | 531.9677 | 532.784 | 439.8556 | 106.6358
3946.2542 | 667.7321 | 591.5514 | 527.2548 | 531.5848 | 532.0865 | 438.2347 | 106.6417
3947.2542 | 671.8467 | 591.5763 | 527.2223 | 531.5837 | 521.1647 | 412.8921 | 106.6727
3948.2542 | 675.6917 | 591.4493 | 527.3757 | 531.5195 | 520.1211 | 411.6214 | 106.6836
3949.2542 | 674.1462 | 591.8194 | 527.5013 | 531.3996 | 519.9978 | 411.2323 | 106.7069
3950.2542 | 668.164 | 591.2989 | 527.6175 | 532.1353 | 519.7155 | 411.2566 | 106.7191
3951.2542 | 672.3249 | 591.0552 | 527.5928 | 532.0574 | 519.9005 | 411.9402 | 106.7499
3952.2542 | 663.3785 | 590.8159 | 527.6287 | 531.9541 | 520.3757 | 412.1092 | 106.765
3953.2542 | 660.2384 | 590.3519 | 527.7204 | 532.0547 | 519.9314 | 412.1228 | 106.7852
3954.2542 | 667.7031 | 590.1407 | 527.7811 | 531.7316 | 519.7154 | 412.1376 | 106.7981
3955.2542 | 665.6006 | 589.2283 | 527.6337 | 531.5724 | 519.8281 | 412.2747 | 106.8215
3956.2542 | 662.6499 | 589.8084 | 527.5767 | 531.0546 | 519.6931 | 412.7746 | 106.8453
3957.2542 | 657.5867 | 590.1471 | 527.4672 | 530.8061 | 519.8793 | 420.4428 | 87.759
3958.2542 | 648.1158 | 589.9637 | 527.3966 | 530.6288 | 519.2018 | 420.4407 | 87.2063
3959.2542 | 642.636 | 589.9546 | 527.2986 | 530.469 | 518.7848 | 420.5802 | 87.2936
3960.2542 | 645.4602 | 589.7921 | 527.0849 | 530.0678 | 518.8515 | 420.8003 | 87.3181