## Test Conditions
DESIREE-FIRE Intermediate Scale Test 11 - Circuit Data Only
Test Date: | 2009-11-25
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:02 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:26
Fire Time | 15:38
Offset | 2:13 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 7980 | seconds
Heat Source Offset | 2:12 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 7945 | seconds
Heat Source Stop Time | 16:53
Test Duration | 1:15 | hours:minutes:seconds
| 4500 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
Large Coil | EPR/CPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Raw Data
Time \ (C) | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2
1.6875 | 0.030518 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | 0 | 0.001068 | 4.7424 | 6.4682 | 4.3167 | 4.6967 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 5.8319 | 6.102 | 2.6871 | 0.022888 | 0.013733 | 0.013733 | 0.013733 | -7.7728 | 0.013733 | 0.013733
3.3594 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 3.1998 | 4.7791 | 5.4199 | 6.3812 | 0.018311 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 4.2389 | 6.3675 | 4.6234 | 0.013733 | 0.004578 | 0.009155 | 0.018311 | -6.5231 | 0.032043 | 0.022888
5.0781 | 0.030518 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0 | 0.002136 | 1.1902 | 3.4195 | 5.1956 | 6.4407 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 2.9755 | 5.777 | 5.3329 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | -5.5252 | 0.013733 | 0.013733
6.75 | 0.045776 | 0.006409 | 0.004272 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.4715 | 2.2614 | 4.7241 | 6.1798 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 1.9958 | 5.1773 | 5.3421 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | -4.6463 | 0.013733 | 0.018311
8.4219 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | -0.001068 | 0 | 0.001068 | -1.5427 | 1.3504 | 4.2389 | 5.8823 | 0.018311 | 0.013733 | 0.004578 | 0.061035 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 1.1673 | 4.5593 | 5.1315 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | -3.772 | 0.009155 | 0.013733
10.1562 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -2.1286 | 0.68665 | 3.7949 | 5.5939 | 0.013733 | 0.013733 | 0.004578 | 0.061035 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | 0.44861 | 3.9276 | 4.8569 | 0.013733 | 0.009155 | 0.009155 | 0.013733 | -2.8931 | 0.013733 | 0.013733
11.8281 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.003204 | -2.417 | 0.18768 | 3.3737 | 5.3238 | 0.018311 | 0.013733 | 0.022888 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.15564 | 3.2684 | 4.5319 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | -2.0325 | 0.018311 | 0.013733
13.5781 | 0.061035 | 0.001068 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0 | -2.4719 | -0.15106 | 2.9755 | 5.0629 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.63629 | 2.6047 | 4.1565 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | -1.2131 | 0.013733 | 0.027466
15.2344 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.002136 | 0 | 0.002136 | -2.4353 | -0.4303 | 2.5864 | 4.7882 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0.001068 | 0.004272 | 0.002136 | -0.001068 | -1.0254 | 1.9318 | 3.7674 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | -0.4715 | 0.018311 | 0.013733
16.9688 | 0.045776 | 0.004272 | 0 | 0.002136 | 0 | 0.001068 | 0.001068 | -2.3117 | -0.60425 | 2.2247 | 4.5181 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -1.3184 | 1.2772 | 3.3142 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | 0.1236 | 0.013733 | 0.009155
18.7031 | 0.015259 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -2.1606 | -0.72327 | 1.8768 | 4.2618 | 0.022888 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.002136 | -1.5244 | 0.68207 | 2.861 | 0.018311 | 0.027466 | 0.009155 | 0.013733 | 0.66376 | 0.013733 | 0.013733
20.375 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0 | 0.003204 | 0.002136 | -1.9958 | -0.80566 | 1.5747 | 4.01 | 0.018311 | 0.018311 | 0.013733 | 0.076294 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | -1.6754 | 0.15106 | 2.3758 | 0.018311 | 0.013733 | 0.013733 | 0.004578 | 1.1032 | 0.022888 | 0.018311
22.1094 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0 | 0.001068 | 0.002136 | -1.8219 | -0.84686 | 1.2817 | 3.7399 | 0.004578 | 0.018311 | 0.013733 | 0.045776 | -0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -1.7487 | -0.32959 | 1.8814 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.4786 | 0.022888 | 0.018311
23.8281 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | -0.002136 | 0.001068 | 0.002136 | -1.6571 | -0.88806 | 1.0117 | 3.4836 | 0.018311 | 0.013733 | 0.022888 | 0.030518 | 0.004272 | 0.002136 | 0 | 0.001068 | 0.002136 | -1.7944 | -0.72784 | 1.3962 | 0.018311 | 0.013733 | 0.009155 | 0.018311 | 1.8082 | 0.013733 | 0.009155
25.5625 | 0.030518 | 0.003204 | 0 | 0.002136 | 0 | 0.002136 | 0 | -1.5244 | -0.91553 | 0.77362 | 3.241 | 0.013733 | 0.027466 | 0.018311 | 0.045776 | 0 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | -1.7853 | -1.0483 | 0.94757 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 2.0279 | 0.013733 | 0.018311
27.2344 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.004272 | -1.387 | -0.91553 | 0.54474 | 2.9755 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0 | 0.002136 | 0.001068 | 0.002136 | -1.7761 | -1.3138 | 0.51727 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 2.243 | 0.018311 | 0.018311
28.9688 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0 | 0 | 0.001068 | -1.268 | -0.90637 | 0.36163 | 2.7283 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0 | 0.001068 | 0.002136 | 0.002136 | -1.7395 | -1.5244 | 0.13275 | 0.018311 | 0.004578 | 0.018311 | 0.018311 | 2.3941 | 0.013733 | 0.018311
30.6875 | 0.061035 | 0.005341 | 0 | 0.001068 | -0.002136 | 0.001068 | 0 | -1.1719 | -0.89722 | 0.19226 | 2.4857 | 0.004578 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0 | -1.68 | -1.68 | -0.21973 | 0.013733 | 0.009155 | 0.013733 | 0.009155 | 2.5131 | 0.013733 | 0.013733
32.3594 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0 | -1.0941 | -0.89722 | 0.041199 | 2.2522 | 0.018311 | 0.018311 | 0.018311 | 0.030518 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -1.6296 | -1.7944 | -0.51727 | 0.004578 | 0.018311 | 0.009155 | 0.013733 | 2.623 | 0.022888 | 0.018311
34.0938 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | -0.002136 | 0 | 0 | -1.0208 | -0.89264 | -0.10071 | 2.005 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0 | -1.5701 | -1.886 | -0.78735 | 0.018311 | 0.022888 | 0.009155 | 0.009155 | 2.7008 | 0.022888 | 0.018311
35.8281 | 0.061035 | 0.003204 | 0.002136 | 0 | -0.001068 | 0.001068 | 0 | -0.97504 | -0.88806 | -0.22888 | 1.7715 | 0.013733 | 0.013733 | 0.004578 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -1.4969 | -1.9501 | -1.0208 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 2.7328 | 0.022888 | 0.018311
37.5156 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | 0 | 0.001068 | -0.92468 | -0.88348 | -0.32959 | 1.561 | 0.013733 | 0.004578 | 0.009155 | 0.061035 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.001068 | -1.4328 | -1.9684 | -1.2085 | 0.009155 | 0.013733 | 0.022888 | 0.022888 | 2.8015 | 0.018311 | 0.013733
39.2344 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0 | 0.002136 | -0.86517 | -0.87891 | -0.4303 | 1.3504 | 0.018311 | 0.018311 | 0.009155 | 0.061035 | 0.001068 | 0.001068 | 0.003204 | 0.003204 | 0.001068 | -1.3779 | -1.9958 | -1.3733 | 0.004578 | 0.013733 | 0.013733 | 0.018311 | 2.3666 | 0.018311 | 0.013733
40.9688 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.002136 | 0.002136 | 0.001068 | -0.83313 | -0.86517 | -0.49896 | 1.1719 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0 | -1.3229 | -1.9821 | -1.4969 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 2.4216 | 0.018311 | 0.013733
42.6406 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.003204 | 0.001068 | -0.80109 | -0.8606 | -0.58594 | 0.97046 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -1.268 | -1.9913 | -1.6205 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 2.4719 | 0.018311 | 0.013733
44.3125 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0 | -0.7782 | -0.84686 | -0.66376 | 0.77362 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -1.2085 | -1.9821 | -1.7441 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 2.5269 | 0.018311 | 0.013733
46.0469 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | -0.003204 | 0.002136 | 0.002136 | -0.76904 | -0.87433 | -0.737 | 0.60883 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -1.1673 | -1.9501 | -1.8311 | 0.018311 | 0.009155 | 0.009155 | 0.009155 | 2.5452 | 0.018311 | 0.018311
47.7812 | 0.061035 | 0.001068 | 0.002136 | 0 | -0.002136 | 0.002136 | 0.002136 | -0.70038 | -0.81482 | -0.70038 | 0.54932 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.003204 | -1.1032 | -1.8631 | -1.8036 | 0.013733 | 0.004578 | 0.018311 | 0.009155 | 2.5864 | 0.013733 | 0.018311
49.4375 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | -0.002136 | 0.001068 | 0.001068 | -0.74158 | -0.89722 | -0.78278 | 0.37994 | 0.018311 | 0.013733 | 0.018311 | 0.015259 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | -1.0849 | -1.8723 | -1.8814 | 0.004578 | 0.013733 | 0.013733 | 0.013733 | 2.6459 | 0.013733 | 0.018311
51.1875 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.70496 | -0.89264 | -0.84228 | 0.22888 | 0.018311 | 0.004578 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -1.0437 | -1.8677 | -1.9547 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 2.4628 | 0.018311 | 0.018311
52.8594 | 0.045776 | 0.005341 | 0.002136 | 0 | -0.002136 | 0.001068 | 0.001068 | -0.67749 | -0.86517 | -0.88348 | 0.10071 | 0.009155 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.99335 | -1.8311 | -1.9913 | 0.009155 | 0.009155 | 0.013733 | 0.013733 | 2.2476 | 0.018311 | 0.018311
54.5938 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.65918 | -0.85602 | -0.92468 | -0.022888 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.94757 | -1.7853 | -2.0187 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 2.092 | 0.018311 | 0.018311
56.2812 | 0.061035 | 0.004272 | 0.002136 | 0 | -0.002136 | 0.001068 | 0 | -0.64545 | -0.85602 | -0.9613 | -0.15106 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0 | 0.003204 | 0.002136 | 0.001068 | -0.89722 | -1.7349 | -2.0325 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 1.973 | 0.018311 | 0.018311
58.0156 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.63629 | -0.84228 | -0.99792 | -0.25635 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0 | 0.002136 | 0.001068 | 0.001068 | -0.85602 | -1.6891 | -2.037 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 1.886 | 0.018311 | 0.013733
59.75 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.002136 | 0 | -0.62256 | -0.83771 | -1.0071 | -0.34332 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.82398 | -1.6113 | -2.0096 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 1.8127 | 0.018311 | 0.018311
61.4375 | 0.015259 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.003204 | -0.63171 | -0.84228 | -1.03 | -0.42114 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.004272 | -0.79193 | -1.5701 | -1.9913 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 1.7624 | 0.022888 | 0.018311
63.1719 | 0.045776 | 0.002136 | 0 | 0.003204 | -0.003204 | 0.001068 | 0.001068 | -0.65002 | -0.8606 | -1.0437 | -0.49896 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.7782 | -1.5244 | -1.9547 | 0.013733 | 0.004578 | 0.013733 | 0.013733 | 1.6891 | 0.018311 | 0.018311
64.8281 | 0.045776 | 0.003204 | 0.001068 | 0.001068 | -0.001068 | 0.001068 | 0 | -0.64545 | -0.84228 | -1.0574 | -0.56305 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | -0.75073 | -1.4832 | -1.9363 | 0.013733 | 0.013733 | 0.009155 | 0.009155 | 1.593 | 0.018311 | 0.009155
66.5 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.003204 | 0.001068 | -0.63171 | -0.84228 | -1.0849 | -0.64545 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.74158 | -1.4465 | -1.9135 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.5015 | 0.018311 | 0.013733
68.2344 | 0.030518 | 0.005341 | 0.004272 | 0.002136 | -0.001068 | 0.001068 | 0.001068 | -0.64545 | -0.84686 | -1.1124 | -0.71411 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.737 | -1.4328 | -1.8997 | 0.013733 | 0.013733 | 0.013733 | 0.004578 | 1.4191 | 0.013733 | 0.018311
69.9688 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.001068 | -0.63171 | -0.85144 | -1.1307 | -0.7782 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.72784 | -1.4099 | -1.8997 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 1.3138 | 0.013733 | 0.013733
71.6406 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | -0.001068 | 0.001068 | 0.002136 | -0.63171 | -0.84686 | -1.1307 | -0.8194 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.70496 | -1.3641 | -1.8494 | 0.013733 | 0.004578 | 0.009155 | 0.018311 | 1.2222 | 0.013733 | 0.009155
73.3281 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.63629 | -0.84686 | -1.1444 | -0.87433 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.70038 | -1.3504 | -1.8356 | 0.018311 | 0.013733 | 0.009155 | 0.009155 | 1.1261 | 0.009155 | 0.013733
75.0625 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | -0.004272 | 0 | 0.001068 | -0.62714 | -0.85144 | -1.1627 | -0.92468 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.70038 | -1.3367 | -1.8311 | 0.013733 | 0.009155 | 0.022888 | 0.009155 | 1.0345 | 0.013733 | 0.018311
76.7188 | 0.015259 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.002136 | 0 | -0.63171 | -0.8606 | -1.1719 | -0.97046 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.67749 | -1.3046 | -1.799 | 0.018311 | 0.009155 | 0.013733 | 0.009155 | 0.97046 | 0.013733 | 0.018311
78.4062 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0 | -0.62714 | -0.84686 | -1.1719 | -1.0025 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.67291 | -1.2772 | -1.7899 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.86517 | 0.018311 | 0.013733
80.1406 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.85602 | -1.1902 | -1.0529 | 0.013733 | 0.013733 | 0.009155 | 0.015259 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.66834 | -1.2726 | -1.7715 | 0.018311 | 0.004578 | 0.013733 | 0.004578 | 0.79651 | 0.018311 | 0.009155
81.8594 | 0.045776 | 0.004272 | 0.001068 | 0 | -0.001068 | 0 | 0 | -0.63629 | -0.85144 | -1.1993 | -1.0849 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.6546 | -1.2497 | -1.7487 | 0.004578 | 0.013733 | 0.013733 | 0.018311 | 0.72784 | 0.013733 | 0.009155
83.5469 | 0.076294 | 0.003204 | 0.003204 | 0.001068 | -0.001068 | 0 | 0.001068 | -0.63629 | -0.86517 | -1.2131 | -1.1169 | 0.013733 | 0.009155 | 0.013733 | 0.030518 | 0.005341 | 0 | 0.001068 | 0.002136 | 0 | -0.66376 | -1.2405 | -1.7212 | 0.004578 | 0.013733 | 0.013733 | 0.018311 | 0.66376 | 0.013733 | 0.013733
85.2188 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | -0.002136 | 0.002136 | 0.001068 | -0.63171 | -0.8606 | -1.1993 | -1.1307 | 0.013733 | 0 | 0.009155 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.6546 | -1.2131 | -1.6937 | 0.009155 | 0.004578 | 0.013733 | 0.018311 | 0.58594 | 0.022888 | 0.013733
86.9531 | 0.061035 | 0.005341 | 0.001068 | 0 | -0.001068 | 0.002136 | 0 | -0.61798 | -0.85602 | -1.2131 | -1.1627 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.6546 | -1.2131 | -1.6983 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.54016 | 0.018311 | 0.009155
88.6094 | 0.015259 | 0.003204 | 0 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.59509 | -0.83771 | -1.2222 | -1.1902 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.005341 | 0 | 0.001068 | 0.002136 | 0.003204 | -0.65002 | -1.1948 | -1.6891 | 0.018311 | 0.009155 | 0.018311 | 0.009155 | 0.37994 | 0.013733 | 0.013733
90.2812 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.6134 | -0.84228 | -1.2039 | -1.1993 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | -0.64087 | -1.181 | -1.6525 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.41199 | 0.027466 | 0.009155
92 | 0.061035 | 0.003204 | 0.001068 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.84686 | -1.2085 | -1.2131 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.62714 | -1.1536 | -1.6159 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 0.5127 | 0.013733 | 0.013733
93.7344 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.61798 | -0.90637 | -1.268 | -1.2634 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | -0.70496 | -1.2405 | -1.5701 | 0.013733 | 0 | 0.009155 | 0.018311 | 0.65918 | 0.018311 | 0.022888
95.4688 | 0.061035 | 0.006409 | 0.001068 | 0.003204 | -0.001068 | 0 | 0.001068 | -0.67291 | -0.92468 | -1.2589 | -1.2543 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | -0.65002 | -1.1856 | -1.5884 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.58136 | 0.013733 | 0.013733
97.1406 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0 | 0.001068 | 0 | -0.6546 | -0.89264 | -1.2817 | -1.2955 | 0.004578 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.65002 | -1.1902 | -1.6067 | 0.009155 | 0.009155 | 0.013733 | 0.004578 | 1.3 | 0.018311 | 0.018311
98.8906 | 0.061035 | 0.003204 | 0.001068 | 0 | 0 | 0.002136 | 0.001068 | -0.61798 | -0.8606 | -1.2726 | -1.3229 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.66376 | -1.2085 | -1.6663 | 0.013733 | 0.004578 | 0.013733 | 0.018311 | 0.81024 | 0.018311 | 0.013733
100.625 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.002136 | -0.6134 | -0.86517 | -1.268 | -1.3596 | 0.004578 | 0.009155 | 0.018311 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.65002 | -1.181 | -1.6113 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 0.58136 | 0.013733 | 0.022888
102.2969 | 0.061035 | 0.005341 | 0 | 0.002136 | -0.001068 | 0 | 0.001068 | -0.60425 | -0.86975 | -1.2634 | -1.3641 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | -0.63629 | -1.181 | -1.6205 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | 0.32501 | 0.022888 | 0.013733
104.0312 | 0.045776 | 0.003204 | 0.001068 | 0 | 0 | -0.001068 | 0.001068 | -0.63629 | -0.89722 | -1.2817 | -1.387 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0 | -0.64087 | -1.1765 | -1.6571 | 0.009155 | 0.009155 | 0.013733 | 0.013733 | 0.20599 | 0.018311 | 0.018311
105.7656 | 0.030518 | 0.004272 | 0.001068 | 0.001068 | -0.002136 | 0 | 0.002136 | -0.62714 | -0.8606 | -1.2909 | -1.4008 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | -0.62256 | -1.1627 | -1.6342 | 0 | 0.009155 | 0.009155 | 0.013733 | -0.013733 | 0.013733 | 0.018311
107.4531 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | -0.002136 | 0 | 0 | -0.60883 | -0.8606 | -1.2817 | -1.4099 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.62256 | -1.1398 | -1.6113 | 0.009155 | 0.009155 | 0.022888 | 0.009155 | -0.073242 | 0.018311 | 0.018311
109.1875 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.61798 | -0.8606 | -1.2863 | -1.4145 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | -0.60883 | -1.1444 | -1.5884 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | -0.018311 | 0.013733 | 0.013733
110.8438 | 0.045776 | 0.004272 | 0.002136 | 0 | -0.001068 | 0.002136 | 0.001068 | -0.6134 | -0.84228 | -1.2817 | -1.4328 | 0.013733 | 0.018311 | 0.009155 | 0.030518 | 0.002136 | 0 | 0.001068 | 0.001068 | 0.002136 | -0.6134 | -1.1124 | -1.5656 | 0.009155 | 0.009155 | 0.009155 | 0.013733 | 0.032043 | 0.018311 | 0.013733
112.5156 | 0.030518 | 0.005341 | 0.001068 | 0.001068 | -0.001068 | 0.002136 | 0.002136 | -0.60883 | -0.86517 | -1.2863 | -1.442 | 0.009155 | 0.013733 | 0.009155 | 0.030518 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.61798 | -1.1124 | -1.561 | 0.009155 | 0.009155 | 0.009155 | 0.018311 | 0.10529 | 0.018311 | 0.013733
114.2344 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.001068 | 0 | -0.60425 | -0.85144 | -1.2817 | -1.4511 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.6134 | -1.1032 | -1.5518 | 0.022888 | 0.013733 | 0.013733 | 0.013733 | 0.15564 | 0.009155 | 0.009155
115.8906 | 0.030518 | 0.002136 | 0.002136 | 0.003204 | -0.002136 | 0 | 0.001068 | -0.59967 | -0.86975 | -1.2909 | -1.474 | 0.018311 | 0.013733 | 0.009155 | 0.030518 | 0 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.6134 | -1.1124 | -1.5518 | 0.009155 | 0.018311 | 0.004578 | 0.018311 | 0.16479 | 0.013733 | 0.018311
117.625 | 0.045776 | 0.002136 | 0 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.58594 | -0.84228 | -1.2634 | -1.4465 | 0.009155 | 0.013733 | 0.018311 | 0.015259 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.60883 | -1.0803 | -1.5244 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | 0.16479 | 0.018311 | 0.013733
119.2969 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | 0 | 0 | -0.59509 | -0.85602 | -1.2817 | -1.4786 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0 | 0.004272 | 0.002136 | 0.002136 | -0.62256 | -1.0986 | -1.5381 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 0.16022 | 0.013733 | 0.013733
121.0312 | 0.076294 | 0.004272 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.60883 | -0.85144 | -1.2817 | -1.474 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.6134 | -1.0941 | -1.5244 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.14648 | 0.013733 | 0.013733
122.7031 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0 | -0.001068 | 0 | -0.62714 | -0.86975 | -1.2863 | -1.4877 | 0.013733 | 0.013733 | 0.004578 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.60883 | -1.0803 | -1.5198 | 0.009155 | 0.027466 | 0.013733 | 0.013733 | 0.13733 | 0.009155 | 0.022888
124.4375 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.63171 | -0.87433 | -1.2909 | -1.4877 | 0.009155 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | -0.61798 | -1.0757 | -1.4969 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.11902 | 0.013733 | 0.013733
126.0938 | 0.030518 | 0.005341 | 0.001068 | 0.001068 | -0.002136 | 0.002136 | 0.002136 | -0.6134 | -0.85602 | -1.2726 | -1.4603 | 0.013733 | 0.018311 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.60425 | -1.0666 | -1.4832 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.09613 | 0.009155 | 0.013733
127.8125 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.002136 | -0.001068 | -0.60883 | -0.8606 | -1.2726 | -1.4786 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.6134 | -1.0757 | -1.4786 | 0.013733 | 0.018311 | 0.009155 | 0.009155 | 0.068665 | 0.009155 | 0.013733
129.4844 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | 0 | -0.59967 | -0.86517 | -1.2772 | -1.4786 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.61798 | -1.0849 | -1.4877 | 0.009155 | 0.018311 | 0.013733 | 0.009155 | 0.054932 | 0.018311 | 0.018311
131.2188 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0 | 0.002136 | -0.59052 | -0.86975 | -1.2863 | -1.5106 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0 | 0.001068 | 0.001068 | 0.001068 | -0.63171 | -1.1078 | -1.5015 | 0.013733 | 0.009155 | 0.009155 | 0.009155 | 0.059509 | 0.009155 | 0.018311
132.9531 | 0.030518 | 0.004272 | 0.002136 | 0.001068 | -0.002136 | 0.001068 | 0.001068 | -0.60883 | -0.87433 | -1.2863 | -1.5106 | 0.013733 | 0.004578 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.6134 | -1.0895 | -1.4969 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.009155 | 0.018311
134.6875 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | -0.002136 | 0.001068 | 0.002136 | -0.59967 | -0.86517 | -1.2772 | -1.4923 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.59967 | -1.062 | -1.4603 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.041199 | 0.018311 | 0.018311
136.375 | 0.030518 | 0.004272 | 0.003204 | 0 | -0.002136 | 0.001068 | 0.002136 | -0.59509 | -0.8606 | -1.2863 | -1.5152 | 0.009155 | 0.018311 | 0.004578 | 0.015259 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.6134 | -1.0757 | -1.474 | 0.009155 | 0.013733 | 0.009155 | 0.009155 | 0.054932 | 0.022888 | 0.009155
138.1094 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.58594 | -0.84686 | -1.2817 | -1.506 | 0.018311 | 0.022888 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.6134 | -1.0712 | -1.4694 | 0.013733 | 0.009155 | 0.013733 | 0.009155 | 0.041199 | 0.013733 | 0.018311
139.7656 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.60425 | -0.85602 | -1.2543 | -1.4877 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0 | 0.001068 | 0.001068 | 0.001068 | -0.60425 | -1.062 | -1.4557 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.036621 | 0.009155 | 0.018311
141.4531 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0.001068 | -0.59967 | -0.85602 | -1.2726 | -1.506 | 0.009155 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.6134 | -1.0849 | -1.4648 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | 0.022888
143.1875 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.61798 | -0.87891 | -1.2909 | -1.5106 | 0.009155 | 0.009155 | 0.009155 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.60883 | -1.0803 | -1.4786 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.022888 | 0.018311 | 0.018311
144.8594 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0.002136 | -0.61798 | -0.87433 | -1.3 | -1.5289 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.59967 | -1.0757 | -1.4694 | 0.004578 | 0.018311 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.018311
146.5938 | 0.045776 | 0.003204 | 0 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.62256 | -0.86517 | -1.2863 | -1.5152 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -0.59509 | -1.0574 | -1.4557 | 0.004578 | 0.009155 | 0.013733 | 0.009155 | 0.027466 | 0.013733 | 0.018311
148.2656 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.002136 | -0.61798 | -0.88806 | -1.3046 | -1.5381 | 0.009155 | 0.009155 | 0.009155 | 0.061035 | 0.001068 | 0.001068 | 0.004272 | 0.002136 | 0.004272 | -0.60425 | -1.0666 | -1.4603 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.018311
149.9844 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | -0.002136 | 0.001068 | 0.002136 | -0.60883 | -0.86975 | -1.2863 | -1.5152 | 0.009155 | 0.018311 | 0.004578 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.59052 | -1.0483 | -1.442 | 0.018311 | 0.009155 | 0.018311 | 0.009155 | 0.022888 | 0.018311 | 0.022888
151.7344 | 0.045776 | 0.004272 | 0 | 0.001068 | -0.002136 | 0.001068 | 0.001068 | -0.60425 | -0.86975 | -1.3092 | -1.5381 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.60883 | -1.0666 | -1.4648 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | -0.004578 | 0.013733 | 0.018311
153.4219 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | -0.003204 | 0.002136 | 0.001068 | -0.59509 | -0.8606 | -1.2817 | -1.5106 | 0.018311 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.59967 | -1.0483 | -1.4282 | 0.013733 | 0.009155 | 0.009155 | 0.009155 | 0.009155 | 0.022888 | 0.022888
155.1562 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0 | -0.59509 | -0.8606 | -1.2817 | -1.5198 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.59967 | -1.0574 | -1.4328 | 0.013733 | 0.027466 | 0.013733 | 0.013733 | -0.009155 | 0.009155 | 0.009155
156.8906 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | -0.002136 | 0.001068 | 0.002136 | -0.59509 | -0.88348 | -1.3046 | -1.5335 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0 | -0.61798 | -1.0757 | -1.4603 | 0.004578 | 0.013733 | 0.013733 | 0.018311 | 0.004578 | 0.018311 | 0.022888
158.5625 | 0.045776 | 0.005341 | 0 | 0.002136 | -0.002136 | 0 | 0.002136 | -0.60425 | -0.86517 | -1.3046 | -1.5427 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.001068 | 0 | 0.001068 | -0.6134 | -1.0849 | -1.4648 | 0.009155 | 0.009155 | 0.009155 | 0.013733 | 0 | 0.018311 | 0.018311
160.2344 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.60883 | -0.8606 | -1.2817 | -1.5289 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.59967 | -1.0529 | -1.4374 | 0.009155 | 0.013733 | 0.004578 | 0.009155 | 0.018311 | 0.018311 | 0.018311
161.9531 | 0.030518 | 0.006409 | 0 | 0.003204 | -0.002136 | 0.002136 | 0 | -0.59509 | -0.87433 | -1.2909 | -1.5289 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.60883 | -1.0574 | -1.4511 | 0.009155 | 0.004578 | 0.022888 | 0.018311 | 0.013733 | 0.013733 | 0.013733
163.625 | 0.030518 | 0.004272 | 0.001068 | 0.001068 | -0.002136 | 0.001068 | 0.001068 | -0.59052 | -0.84228 | -1.2817 | -1.5335 | 0.009155 | 0.004578 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.60883 | -1.0666 | -1.4511 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | -0.009155 | 0.018311 | 0.018311
165.2969 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.59052 | -0.86975 | -1.3046 | -1.5564 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -1.0803 | -1.4694 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.018311 | 0.022888
167.0312 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.001068 | 0 | -0.60883 | -0.84228 | -1.2863 | -1.5381 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0 | -0.60883 | -1.0666 | -1.442 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.004578 | 0.013733 | 0.018311
168.7031 | 0.030518 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.002136 | 0.002136 | -0.61798 | -0.87433 | -1.2909 | -1.5472 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | 0 | -0.6134 | -1.0712 | -1.4557 | 0.022888 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.018311
170.4219 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.59509 | -0.88348 | -1.3138 | -1.5656 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.6134 | -1.0849 | -1.4694 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.004578 | 0.013733 | 0.018311
172.0938 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | -0.002136 | 0.001068 | 0.002136 | -0.6134 | -0.8606 | -1.2955 | -1.5518 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.60425 | -1.0666 | -1.4603 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.018311
173.8281 | 0.045776 | 0.003204 | 0.002136 | 0 | 0 | 0.003204 | 0 | -0.6134 | -0.8606 | -1.2863 | -1.5472 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0 | 0.003204 | 0.001068 | -0.61798 | -1.0666 | -1.442 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0 | 0.018311 | 0.009155
175.5 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | -0.002136 | 0 | 0 | -0.6134 | -0.86517 | -1.2909 | -1.5518 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | -0.61798 | -1.0712 | -1.442 | 0.004578 | 0.013733 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | 0.013733
177.2188 | 0.045776 | 0.005341 | 0 | 0.003204 | -0.003204 | 0.001068 | 0.001068 | -0.59967 | -0.85602 | -1.2909 | -1.5518 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.6134 | -1.0712 | -1.4603 | 0.013733 | 0.018311 | 0.013733 | 0.004578 | -0.009155 | 0.009155 | 0.009155
178.9688 | 0.030518 | 0.006409 | 0.001068 | 0.003204 | -0.001068 | 0.002136 | 0.002136 | -0.59052 | -0.85602 | -1.3 | -1.5701 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.61798 | -1.0895 | -1.474 | 0.009155 | 0.018311 | 0.013733 | 0.009155 | 0 | 0.013733 | 0.018311
180.7031 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.002136 | -0.59509 | -0.8606 | -1.2863 | -1.5518 | 0.009155 | 0.009155 | 0.013733 | 0.030518 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | 0.001068 | -0.60883 | -1.0666 | -1.4557 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.018311
182.4219 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0 | -0.59052 | -0.87433 | -1.3138 | -1.5793 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.60883 | -1.0803 | -1.4648 | 0.009155 | 0.009155 | 0.004578 | 0.018311 | 0.018311 | 0.009155 | 0.027466
184.0938 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.60883 | -0.86517 | -1.3138 | -1.5747 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.59509 | -1.0666 | -1.4648 | 0.009155 | 0.018311 | 0.004578 | 0.013733 | 0.009155 | 0.018311 | 0.013733
185.75 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.001068 | -0.60425 | -0.85144 | -1.2955 | -1.561 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0 | 0.001068 | 0.001068 | 0.001068 | -0.59967 | -1.0529 | -1.442 | 0.013733 | 0.009155 | 0.004578 | 0.009155 | 0.013733 | 0.018311 | 0.013733
187.4219 | 0.030518 | 0.004272 | 0 | 0.002136 | -0.002136 | -0.001068 | 0.002136 | -0.59967 | -0.86517 | -1.3184 | -1.5884 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | -0.60425 | -1.0757 | -1.4465 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.022888
189.1562 | 0.015259 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0 | -0.60883 | -0.8606 | -1.3046 | -1.5747 | 0.018311 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.59509 | -1.062 | -1.4603 | 0.009155 | 0.009155 | 0.009155 | 0.013733 | 0.018311 | 0.022888 | 0.013733
190.875 | 0.045776 | 0.001068 | 0.002136 | 0 | 0 | 0.002136 | 0.002136 | -0.61798 | -0.87433 | -1.3138 | -1.5839 | 0.004578 | 0.009155 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.60883 | -1.062 | -1.442 | 0.018311 | 0.013733 | 0.022888 | 0.009155 | 0.027466 | 0.018311 | 0.022888
192.5469 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.003204 | -0.62256 | -0.86975 | -1.3229 | -1.5839 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.59967 | -1.0666 | -1.4465 | 0.004578 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.018311
194.2188 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | -0.002136 | 0.002136 | 0.001068 | -0.60883 | -0.86517 | -1.3229 | -1.593 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -0.59967 | -1.0574 | -1.4465 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.022888
195.9375 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.62714 | -0.88348 | -1.3229 | -1.5839 | 0.009155 | 0.022888 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.59967 | -1.0574 | -1.4374 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | 0.018311
197.6719 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0 | -0.62256 | -0.87891 | -1.3138 | -1.5793 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0 | -0.60425 | -1.062 | -1.4328 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 0.022888
199.3438 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | -0.002136 | 0.003204 | 0.001068 | -0.60425 | -0.87433 | -1.3229 | -1.5976 | 0.013733 | 0.004578 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.59967 | -1.062 | -1.442 | 0.004578 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | 0.022888 | 0.022888
201.0781 | 0.076294 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.6134 | -0.86517 | -1.3046 | -1.5839 | 0.013733 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.60425 | -1.0574 | -1.442 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.009155 | 0.009155 | 0.018311
202.75 | 0.030518 | 0.001068 | 0.002136 | 0.002136 | -0.002136 | 0.002136 | 0.002136 | -0.6134 | -0.86975 | -1.3092 | -1.5793 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.59967 | -1.0574 | -1.4328 | 0.018311 | 0.013733 | 0.022888 | 0.009155 | 0.004578 | 0.018311 | 0.018311
204.4219 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0.002136 | -0.60883 | -0.88348 | -1.3092 | -1.5839 | 0.004578 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.61798 | -1.0712 | -1.4557 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | -0.022888 | 0.022888 | 0.013733
206.1562 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | -0.002136 | 0.001068 | 0.003204 | -0.59052 | -0.87433 | -1.3046 | -1.5884 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.6134 | -1.0712 | -1.4557 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | -0.10529 | 0.022888 | 0.018311
207.8125 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | -0.002136 | 0.002136 | 0.001068 | -0.60883 | -0.86517 | -1.3046 | -1.5839 | 0 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | -0.60883 | -1.062 | -1.4465 | 0.018311 | 0.018311 | 0.018311 | 0.004578 | -0.14191 | 0.018311 | 0.013733
209.4844 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | -0.002136 | 0.002136 | 0.001068 | -0.59967 | -0.86975 | -1.3229 | -1.6113 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | -0.6134 | -1.0849 | -1.4786 | 0.018311 | 0.009155 | 0.013733 | 0.009155 | -0.1236 | 0.009155 | 0.009155
211.2188 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.58136 | -0.85602 | -1.3 | -1.5839 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.60883 | -1.0849 | -1.474 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.082397 | 0.018311 | 0.022888
212.9531 | 0.061035 | 0.002136 | 0 | 0.001068 | -0.001068 | 0.002136 | 0.001068 | -0.60883 | -0.86975 | -1.3229 | -1.5976 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.60425 | -1.0895 | -1.4786 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | -0.041199 | 0.013733 | 0.013733
214.625 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.60883 | -0.86975 | -1.3229 | -1.6113 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.59509 | -1.0757 | -1.4648 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0 | 0.018311 | 0.018311
216.2969 | 0.045776 | 0.004272 | 0 | 0.001068 | 0.001068 | 0.002136 | 0 | -0.6134 | -0.86517 | -1.3092 | -1.5884 | 0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.59509 | -1.062 | -1.4603 | 0.013733 | 0.018311 | 0.009155 | 0.009155 | 0.022888 | 0.013733 | 0.018311
218.0156 | 0.076294 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.002136 | -0.60425 | -0.87433 | -1.3092 | -1.6022 | 0.009155 | 0.009155 | 0.009155 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.59509 | -1.062 | -1.4557 | 0.013733 | 0.022888 | 0.013733 | 0.009155 | 0.022888 | 0.018311 | 0.018311
219.7656 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.60883 | -0.86975 | -1.3321 | -1.6113 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.60883 | -1.0757 | -1.4648 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | 0.013733 | 0.022888 | 0.009155
221.5312 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.60883 | -0.85602 | -1.3138 | -1.6113 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.59967 | -1.0574 | -1.4511 | 0.013733 | 0.009155 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | 0.018311
224.4688 | 0.076294 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.62256 | -0.86517 | -1.3184 | -1.6022 | 0.004578 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | -0.64087 | -1.0849 | -1.4877 | 0.013733 | 0.018311 | 0.022888 | 0.009155 | -0.018311 | 0.009155 | 0.018311
227.6719 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | -0.001068 | 0 | 0 | -0.63629 | -0.86517 | -1.3367 | -1.6159 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.001068 | -0.6546 | -1.0986 | -1.4832 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | -0.041199 | 0.013733 | 0.013733
229.6406 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.6546 | -0.89722 | -1.3367 | -1.6113 | 0.009155 | 0.013733 | 0.018311 | 0.015259 | 0.002136 | 0 | 0.003204 | 0.002136 | 0.003204 | -0.62714 | -1.0712 | -1.4511 | 0.009155 | 0.004578 | 0.009155 | 0.013733 | 0.21057 | 0.022888 | 0.013733
231.3906 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0 | 0.002136 | -0.62256 | -0.86975 | -1.3504 | -1.6296 | 0.018311 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -0.63171 | -1.0849 | -1.4694 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | 0.15564 | 0.018311 | 0.022888
233.125 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.59967 | -0.84228 | -1.3275 | -1.6205 | 0.009155 | 0.009155 | 0.004578 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | -0.64545 | -1.0941 | -1.4648 | 0.013733 | 0.009155 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 0.013733
234.7969 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | -0.001068 | 0 | 0.002136 | -0.59509 | -0.85602 | -1.3138 | -1.6159 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.63171 | -1.0895 | -1.4694 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | -0.059509 | 0.013733 | 0.013733
236.5312 | 0.061035 | 0.003204 | 0.002136 | 0 | -0.001068 | -0.001068 | 0.002136 | -0.58136 | -0.82855 | -1.3138 | -1.6113 | 0.004578 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.64545 | -1.0986 | -1.4648 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | -0.11902 | 0.022888 | 0.018311
238.25 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.001068 | -0.56763 | -0.83771 | -1.3229 | -1.6159 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | -0.62256 | -1.0986 | -1.4969 | 0.013733 | 0.022888 | 0.013733 | 0.013733 | -0.09613 | 0.018311 | 0.018311
239.9062 | 0.015259 | 0.003204 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0 | -0.59052 | -0.83313 | -1.3321 | -1.6525 | 0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.64087 | -1.1215 | -1.5015 | 0.004578 | 0.013733 | 0.018311 | 0.018311 | -0.1831 | 0.013733 | 0.022888
241.6406 | 0.030518 | 0.004272 | 0.001068 | 0.001068 | -0.002136 | 0.001068 | 0 | -0.59052 | -0.84228 | -1.3184 | -1.6434 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.63629 | -1.1215 | -1.506 | 0.018311 | 0.009155 | 0.009155 | 0.013733 | 0.12817 | 0.018311 | 0.018311
243.375 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0 | -0.58594 | -0.84228 | -1.3229 | -1.6434 | 0.004578 | 0.009155 | 0.009155 | 0.061035 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.62256 | -1.1124 | -1.5152 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | -0.022888 | 0.013733 | 0.018311
245.0312 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0 | -0.60883 | -0.85144 | -1.3092 | -1.6067 | 0.004578 | 0.009155 | 0.013733 | 0.045776 | 0 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.61798 | -1.0849 | -1.4923 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | -0.40741 | 0.013733 | 0.022888
246.7188 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | -0.001068 | 0 | 0.001068 | -0.6134 | -0.8606 | -1.3184 | -1.6296 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.6134 | -1.0986 | -1.5106 | 0.018311 | 0.009155 | 0.013733 | 0.022888 | -0.59967 | 0.013733 | 0.018311
248.4531 | 0.030518 | 0.002136 | 0 | 0.002136 | -0.002136 | 0.001068 | 0 | -0.61798 | -0.84686 | -1.3092 | -1.6205 | 0.013733 | 0.004578 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | -0.61798 | -1.0803 | -1.4877 | 0.009155 | 0.004578 | 0.013733 | 0.009155 | -0.62256 | 0.018311 | 0.022888
250.1875 | 0.061035 | 0.004272 | 0 | 0.001068 | -0.001068 | 0 | 0 | -0.62714 | -0.88348 | -1.3321 | -1.6296 | 0.009155 | 0.009155 | 0.009155 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | -0.001068 | -0.63171 | -1.0941 | -1.4923 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.46234 | 0.018311 | 0.013733
251.8438 | 0.030518 | 0.004272 | 0.001068 | 0 | 0 | 0 | -0.001068 | -0.62256 | -0.86975 | -1.3229 | -1.6296 | 0.013733 | 0.022888 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.6134 | -1.0849 | -1.4786 | 0.009155 | 0.013733 | 0.004578 | 0.009155 | -0.27466 | 0.018311 | 0.009155
253.5781 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.62714 | -0.87433 | -1.3596 | -1.6525 | 0.018311 | 0.009155 | 0.018311 | 0.030518 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.6134 | -1.0941 | -1.5106 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.27466 | 0.022888 | 0.018311
255.25 | 0.030518 | 0.005341 | 0.004272 | 0.001068 | 0 | 0 | -0.001068 | -0.58136 | -0.80566 | -1.3916 | -1.7166 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.60883 | -1.1215 | -1.5564 | 0.004578 | 0.009155 | 0.013733 | 0.009155 | 0.17853 | 0.018311 | 0.018311
256.9219 | 0.030518 | 0.003204 | 0.002136 | 0 | -0.002136 | 0.001068 | 0.001068 | -0.60425 | -0.8194 | -1.3733 | -1.712 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0 | 0.002136 | -0.58136 | -1.0803 | -1.5244 | 0.013733 | 0.013733 | 0.009155 | 0.009155 | 0.32959 | 0.018311 | 0.013733
258.6562 | 0.015259 | 0.005341 | 0 | 0.003204 | -0.002136 | 0.001068 | 0.001068 | -0.59052 | -0.78735 | -1.3824 | -1.7349 | 0.018311 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.58136 | -1.0712 | -1.5198 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 0.42114 | 0.022888 | 0.013733
260.3906 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | -0.001068 | 0 | 0.001068 | -0.62714 | -0.81482 | -1.355 | -1.7166 | 0.009155 | 0.009155 | 0.009155 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.002136 | -0.59052 | -1.0437 | -1.4832 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.47607 | 0.018311 | 0.018311
262.0625 | 0.030518 | 0.005341 | 0.001068 | 0.004272 | -0.001068 | 0.001068 | 0.002136 | -0.70953 | -0.88806 | -1.355 | -1.6754 | 0.013733 | 0.013733 | 0.004578 | 0.061035 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | -0.60425 | -1.0162 | -1.4191 | 0.009155 | 0.009155 | 0.018311 | 0.013733 | 0.49896 | 0.018311 | 0.018311
263.7969 | 0.030518 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0 | -0.68665 | -0.86975 | -1.3184 | -1.6434 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | 0.001068 | -0.63171 | -1.0162 | -1.3733 | 0.018311 | 0.013733 | 0.004578 | 0.013733 | 0.17853 | 0.018311 | 0.013733
265.5312 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0 | 0 | 0.001068 | -0.67749 | -0.90179 | -1.3641 | -1.68 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.66834 | -1.0941 | -1.4557 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | -0.11902 | 0.013733 | 0.018311
267.1875 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0 | 0 | 0.002136 | -0.68207 | -0.9613 | -1.062 | -1.2955 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.6134 | -0.89264 | -1.1078 | 0.018311 | 0.004578 | 0.013733 | 0.018311 | 0.17853 | 0.013733 | 0.022888
268.8594 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | -0.002136 | 0.001068 | 0.001068 | -0.74616 | -1.0803 | -1.1948 | -1.3962 | 0.013733 | 0.009155 | 0.013733 | 0.030518 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -0.75989 | -1.1124 | -1.3092 | 0.022888 | 0.013733 | 0.018311 | 0.013733 | 0.027466 | 0.013733 | 0.022888
270.5938 | 0.030518 | 0.003204 | 0.001068 | 0 | -0.001068 | 0 | 0.002136 | -0.70953 | -1.1398 | -1.0254 | -1.1444 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.71869 | -1.0712 | -1.1993 | 0.009155 | 0.009155 | 0.004578 | 0.013733 | 0.18768 | 0.013733 | 0.018311
272.3281 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | -0.001068 | 0.002136 | 0 | -0.62256 | -1.1581 | -1.1169 | -1.2085 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0 | 0.002136 | 0.002136 | 0.002136 | -0.77362 | -1.2451 | -1.387 | 0.013733 | 0.009155 | 0.013733 | 0.009155 | 0.20599 | 0.013733 | 0.013733
273.9844 | 0.045776 | 0.003204 | -0.001068 | 0.001068 | -0.001068 | 0.001068 | 0.002136 | -0.50812 | -1.0803 | -1.268 | -1.4053 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.737 | -1.4008 | -1.6663 | 0.018311 | 0.018311 | 0.009155 | 0.022888 | 0.13733 | 0.022888 | 0.013733
275.7188 | 0.045776 | 0.004272 | 0 | 0.002136 | -0.002136 | 0.001068 | 0.001068 | -0.29297 | -0.83771 | -1.3046 | -1.5244 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.6134 | -1.387 | -1.799 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.15564 | 0.018311 | 0.018311
277.3906 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0 | -0.29755 | -0.78278 | -1.2863 | -1.5381 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.48065 | -1.2589 | -1.7853 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.16479 | 0.027466 | 0.018311
279.0625 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.33417 | -0.76446 | -1.2451 | -1.5198 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.40741 | -1.1124 | -1.6937 | 0.013733 | 0.022888 | 0.018311 | 0.013733 | 0.15564 | 0.013733 | 0.022888
280.75 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.42114 | -0.7782 | -1.2314 | -1.4877 | 0.004578 | 0.013733 | 0.009155 | 0.030518 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.36621 | -0.98877 | -1.5793 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.13275 | 0.018311 | 0.018311
282.4844 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0 | 0 | 0.001068 | -0.4715 | -0.80566 | -1.2589 | -1.5106 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | 0.001068 | -0.37079 | -0.93384 | -1.5152 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.059509 | 0.009155 | 0.013733
284.1562 | 0.045776 | 0.004272 | 0 | 0 | 0 | 0.003204 | 0.001068 | -0.55389 | -0.84686 | -1.2268 | -1.4511 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.36163 | -0.83313 | -1.3641 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | 0.073242 | 0.013733 | 0.013733
285.8125 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.001068 | 0.001068 | -0.5722 | -0.83771 | -1.3 | -1.5335 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.001068 | 0.004272 | 0.002136 | 0.002136 | 0.004272 | -0.39825 | -0.84686 | -1.3596 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.004578 | 0.018311 | 0.022888
287.5469 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.48981 | -0.72327 | -1.5701 | -1.9226 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.43945 | -1.0071 | -1.6113 | 0.004578 | 0.004578 | 0.009155 | 0.009155 | -0.1831 | 0.009155 | 0.022888
289.2188 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | -0.002136 | 0.002136 | -0.001068 | -0.45776 | -0.5722 | -1.4511 | -1.8539 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | 0.001068 | -0.33417 | -0.79651 | -1.4191 | 0.018311 | 0.009155 | 0.013733 | 0.009155 | -0.07782 | 0.018311 | 0.018311
290.9375 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | -0.002136 | 0.001068 | 0.001068 | -0.58594 | -0.65918 | -1.3641 | -1.7578 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0 | 0.002136 | 0.001068 | 0.001068 | -0.3479 | -0.68207 | -1.236 | 0.013733 | 0.009155 | 0.013733 | 0.009155 | -0.086975 | 0.013733 | 0.018311
292.625 | 0.030518 | 0.005341 | 0.003204 | 0.002136 | -0.002136 | 0.002136 | 0.003204 | -0.74616 | -0.78735 | -1.2726 | -1.6067 | 0.022888 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.4303 | -0.62256 | -1.0483 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | -0.43488 | 0.018311 | 0.009155
294.3594 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0.002136 | -0.84686 | -0.9201 | -1.2863 | -1.5839 | 0.013733 | 0.009155 | 0.009155 | 0.030518 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | -0.54474 | -0.70038 | -1.0162 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | -0.29297 | 0.013733 | 0.013733
296.0156 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.003204 | 0.002136 | -0.81024 | -0.95215 | -1.3596 | -1.6571 | 0.013733 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.63629 | -0.85144 | -1.1078 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | -0.26093 | 0.013733 | 0.013733
297.75 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.75073 | -0.87891 | -1.3458 | -1.6342 | 0.004578 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.67291 | -0.91553 | -1.1673 | 0.009155 | 0.013733 | 0.009155 | 0.009155 | 0.018311 | -0.004578 | -0.09613
299.4844 | 0.061035 | 0.52445 | -0.48279 | -0.18692 | -0.1207 | -0.27344 | -0.15915 | 0.059509 | -0.027466 | 0.054932 | 0.027466 | -0.045776 | -0.17395 | -0.082397 | 0.045776 | -0.001068 | -0.19867 | -0.064087 | -0.18051 | -0.09079 | -0.018311 | 0.022888 | -0.054932 | -0.068665 | -0.064087 | -0.21973 | -0.13275 | 0.041199 | 0.009155 | -0.10986
301.1406 | 0.045776 | 0.55222 | -0.47745 | -0.16235 | -0.12711 | -0.28412 | -0.16129 | 0.018311 | -0.068665 | 0.059509 | -0.027466 | -0.17395 | -0.10529 | -0.009155 | 0.061035 | -0.027771 | -0.23605 | -0.053406 | -0.16663 | -0.10361 | 0.032043 | 0.082397 | -0.032043 | -0.17395 | -0.15564 | -0.18768 | -0.11444 | -0.054932 | 0.050354 | -0.091553
302.8125 | 0.045776 | 0.51804 | -0.46677 | -0.16556 | -0.13779 | -0.25848 | -0.15274 | 0.027466 | -0.032043 | 0.091553 | -0.013733 | -0.2243 | -0.09613 | 0 | 0.045776 | -0.038452 | -0.24353 | -0.042725 | -0.16876 | -0.10468 | 0.032043 | 0.064087 | -0.027466 | -0.2243 | -0.20142 | -0.15106 | -0.064087 | -0.050354 | 0.041199 | -0.091553
304.5469 | 0.045776 | 0.52124 | -0.45715 | -0.18372 | -0.13779 | -0.24567 | -0.14954 | 0.091553 | -0.027466 | 0.086975 | 0.032043 | -0.11444 | -0.14191 | -0.059509 | 0.045776 | -0.041656 | -0.23071 | -0.05127 | -0.16556 | -0.11002 | 0 | 0.050354 | -0.022888 | -0.1236 | -0.07782 | -0.18768 | -0.12817 | 0.018311 | -0.013733 | -0.091553
306.2812 | 0.045776 | 0.51376 | -0.46463 | -0.18692 | -0.14313 | -0.2681 | -0.15915 | 0.10071 | 0.050354 | 0.14648 | 0.059509 | -0.13275 | -0.17395 | -0.07782 | 0.045776 | -0.045929 | -0.2243 | -0.057678 | -0.16876 | -0.10681 | 0.068665 | 0.15106 | 0.018311 | -0.12817 | -0.082397 | -0.21515 | -0.14191 | -0.004578 | 0.013733 | -0.09613
308 | 0.061035 | 0.52445 | -0.45929 | -0.18372 | -0.15488 | -0.2478 | -0.15808 | -0.022888 | -0.14191 | 0.018311 | -0.064087 | -0.15106 | -0.086975 | 0.018311 | 0.030518 | -0.042725 | -0.21683 | -0.038452 | -0.16342 | -0.10361 | -0.036621 | -0.064087 | -0.10071 | -0.16937 | -0.13275 | -0.16022 | -0.07782 | -0.050354 | 0.027466 | -0.07782
309.6875 | 0.045776 | 0.50308 | -0.45822 | -0.20187 | -0.13992 | -0.25101 | -0.15488 | 0.045776 | -0.054932 | 0.050354 | 0.013733 | -0.059509 | -0.16022 | -0.050354 | 0.030518 | -0.040588 | -0.21683 | -0.042725 | -0.16876 | -0.10788 | -0.027466 | 0.022888 | -0.059509 | -0.073242 | -0.059509 | -0.19226 | -0.13275 | 0.050354 | -0.018311 | -0.10529
311.4219 | 0.045776 | 0.51804 | -0.4657 | -0.1976 | -0.14206 | -0.27451 | -0.15915 | 0.013733 | -0.059509 | 0.068665 | -0.027466 | -0.20142 | -0.12817 | -0.022888 | 0.045776 | -0.061951 | -0.22644 | -0.041656 | -0.16876 | -0.11002 | 0.041199 | 0.09613 | -0.041199 | -0.19684 | -0.13733 | -0.17853 | -0.1236 | -0.068665 | 0.068665 | -0.09613
313.0938 | 0.030518 | 0.50949 | -0.45288 | -0.19226 | -0.14954 | -0.26489 | -0.1506 | 0.07782 | 0.027466 | 0.12817 | 0.045776 | -0.16022 | -0.12817 | -0.027466 | 0.045776 | -0.055542 | -0.23498 | -0.050201 | -0.17303 | -0.11643 | 0.13733 | 0.21057 | 0.059509 | -0.16937 | -0.14648 | -0.21057 | -0.12817 | 0.068665 | 0 | -0.11902
314.7812 | 0.030518 | 0.50629 | -0.45181 | -0.18692 | -0.12497 | -0.2478 | -0.15488 | 0.064087 | -0.027466 | 0.064087 | 0.054932 | -0.082397 | -0.16022 | -0.082397 | 0.045776 | -0.03952 | -0.2243 | -0.052338 | -0.15808 | -0.11536 | 0 | 0.045776 | -0.041199 | -0.054932 | -0.050354 | -0.19226 | -0.13275 | 0.045776 | -0.009155 | -0.086975
316.4531 | 0.045776 | 0.51163 | -0.45502 | -0.19974 | -0.1442 | -0.27557 | -0.15488 | 0.11902 | 0.050354 | 0.14191 | 0.064087 | -0.16479 | -0.14191 | -0.054932 | 0.045776 | -0.05661 | -0.21896 | -0.050201 | -0.17838 | -0.11643 | 0.13275 | 0.23804 | 0.09613 | -0.15564 | -0.13733 | -0.21057 | -0.14648 | 0.07782 | 0.009155 | -0.12817
318.1719 | 0.030518 | 0.49347 | -0.45609 | -0.18265 | -0.13886 | -0.25742 | -0.16129 | 0.064087 | -0.027466 | 0.059509 | 0.041199 | -0.041199 | -0.1831 | -0.082397 | 0.061035 | -0.041656 | -0.20935 | -0.03952 | -0.16663 | -0.10788 | -0.009155 | 0.050354 | -0.064087 | -0.068665 | -0.045776 | -0.20599 | -0.15106 | 0.041199 | 0.004578 | -0.10071
319.8438 | 0.045776 | 0.50842 | -0.4689 | -0.18585 | -0.14633 | -0.27237 | -0.1709 | 0.10986 | 0.09613 | 0.16022 | 0.073242 | -0.16479 | -0.15106 | -0.064087 | 0.045776 | -0.065155 | -0.22751 | -0.048065 | -0.16022 | -0.11215 | 0.15106 | 0.23346 | 0.073242 | -0.15106 | -0.13733 | -0.21515 | -0.14191 | 0.054932 | -0.009155 | -0.10986
321.5938 | 0.030518 | 0.50629 | -0.45181 | -0.17517 | -0.13779 | -0.25848 | -0.15167 | 0.11902 | 0.09613 | 0.16022 | 0.068665 | -0.16479 | -0.1831 | -0.064087 | 0.030518 | -0.068359 | -0.23285 | -0.05661 | -0.16342 | -0.10468 | 0.1236 | 0.22888 | 0.073242 | -0.14191 | -0.13275 | -0.21057 | -0.15106 | 0.041199 | 0.022888 | -0.10071
323.3281 | 0.061035 | 0.4924 | -0.4454 | -0.17944 | -0.13245 | -0.23926 | -0.14633 | -0.018311 | -0.10529 | 0.022888 | -0.036621 | -0.1236 | -0.10071 | -0.004578 | 0.030518 | -0.055542 | -0.22324 | -0.045929 | -0.16449 | -0.11429 | -0.086975 | -0.064087 | -0.13275 | -0.12817 | -0.1236 | -0.15106 | -0.073242 | -0.091553 | 0.032043 | -0.059509
324.9844 | 0.015259 | 0.49347 | -0.45395 | -0.18906 | -0.14847 | -0.25101 | -0.16022 | 0.045776 | -0.032043 | 0.045776 | 0.027466 | -0.036621 | -0.17395 | -0.068665 | 0.045776 | -0.046997 | -0.22217 | -0.054474 | -0.16235 | -0.11215 | -0.013733 | 0.041199 | -0.054932 | -0.068665 | -0.073242 | -0.1831 | -0.13275 | 0.059509 | 0.018311 | -0.10529
326.7188 | 0.030518 | 0.49347 | -0.45609 | -0.19546 | -0.1442 | -0.25955 | -0.15381 | 0.064087 | 0.004578 | 0.082397 | 0.036621 | -0.07782 | -0.17853 | -0.064087 | 0.045776 | -0.059814 | -0.21469 | -0.05127 | -0.16769 | -0.10681 | 0.013733 | 0.086975 | -0.036621 | -0.086975 | -0.064087 | -0.21057 | -0.13733 | 0.009155 | 0.009155 | -0.086975
328.4531 | 0.045776 | 0.4924 | -0.45822 | -0.19226 | -0.15167 | -0.26276 | -0.15488 | 0.091553 | 0.041199 | 0.12817 | 0.068665 | -0.10529 | -0.16937 | -0.07782 | 0.045776 | -0.059814 | -0.22751 | -0.050201 | -0.17197 | -0.11322 | 0.041199 | 0.13275 | -0.004578 | -0.082397 | -0.064087 | -0.21515 | -0.14191 | 0.004578 | 0.036621 | -0.10071
330.125 | 0.045776 | 0.49881 | -0.46463 | -0.18372 | -0.14099 | -0.27771 | -0.16235 | 0.045776 | -0.027466 | 0.091553 | 0.009155 | -0.15564 | -0.13275 | -0.036621 | 0.030518 | -0.066223 | -0.22644 | -0.042725 | -0.17517 | -0.1239 | 0.073242 | 0.16022 | 0.018311 | -0.15106 | -0.13275 | -0.19226 | -0.1236 | 0.059509 | 0.022888 | -0.10071
331.8125 | 0.045776 | 0.49881 | -0.45075 | -0.18585 | -0.14526 | -0.25528 | -0.16556 | 0.059509 | -0.022888 | 0.059509 | 0.018311 | -0.050354 | -0.16479 | -0.054932 | 0.030518 | -0.049133 | -0.23178 | -0.040588 | -0.16556 | -0.11963 | -0.013733 | 0.068665 | -0.036621 | -0.050354 | -0.041199 | -0.21515 | -0.14191 | 0.027466 | 0.027466 | -0.091553
333.5625 | 0.061035 | 0.50736 | -0.46356 | -0.19119 | -0.12817 | -0.27771 | -0.15701 | 0.1236 | 0.09613 | 0.16937 | 0.068665 | -0.14648 | -0.16937 | -0.073242 | 0.030518 | -0.066223 | -0.24033 | -0.05127 | -0.16983 | -0.11536 | 0.13275 | 0.23346 | 0.082397 | -0.15564 | -0.1236 | -0.20142 | -0.15106 | 0.045776 | 0.027466 | -0.10529
335.2344 | 0.015259 | 0.50522 | -0.45929 | -0.19333 | -0.14313 | -0.2681 | -0.15701 | 0 | -0.059509 | 0.07782 | -0.004578 | -0.19226 | -0.11902 | -0.013733 | 0.030518 | -0.053406 | -0.24353 | -0.046997 | -0.16342 | -0.11322 | 0.041199 | 0.11444 | -0.013733 | -0.16022 | -0.13733 | -0.16022 | -0.11902 | 0.013733 | 0.045776 | -0.10071
336.9531 | 0.030518 | 0.49881 | -0.46997 | -0.17731 | -0.15167 | -0.23819 | -0.15915 | -0.022888 | -0.16022 | -0.004578 | -0.064087 | -0.14648 | -0.082397 | 0.018311 | 0.030518 | -0.040588 | -0.23178 | -0.042725 | -0.14954 | -0.11856 | -0.064087 | -0.064087 | -0.14191 | -0.14191 | -0.13733 | -0.11902 | -0.073242 | -0.054932 | 0.050354 | -0.045776
338.625 | 0.030518 | 0.50095 | -0.45822 | -0.18051 | -0.12176 | -0.24353 | -0.14954 | 0.10529 | -0.009155 | 0.10071 | 0.027466 | -0.10529 | -0.13733 | -0.032043 | 0.045776 | -0.049133 | -0.22964 | -0.050201 | -0.15488 | -0.10788 | 0 | 0.036621 | -0.054932 | -0.11444 | -0.10071 | -0.16479 | -0.10071 | -0.022888 | 0.013733 | -0.082397
340.2969 | 0.030518 | 0.52551 | -0.47104 | -0.17838 | -0.15595 | -0.27451 | -0.16022 | 0 | -0.045776 | 0.07782 | -0.022888 | -0.21973 | -0.07782 | -0.013733 | 0.061035 | -0.0737 | -0.23819 | -0.045929 | -0.17731 | -0.11749 | 0.059509 | 0.09613 | -0.041199 | -0.17853 | -0.16022 | -0.16479 | -0.091553 | -0.073242 | 0.054932 | -0.073242
341.9531 | 0.015259 | 0.49454 | -0.46249 | -0.18158 | -0.14313 | -0.25421 | -0.15915 | 0.018311 | -0.054932 | 0.10529 | -0.013733 | -0.23804 | -0.068665 | 0.018311 | 0.045776 | -0.068359 | -0.23285 | -0.043793 | -0.16449 | -0.12497 | 0.036621 | 0.086975 | -0.018311 | -0.2243 | -0.19226 | -0.12817 | -0.064087 | -0.068665 | 0.041199 | -0.064087
343.6875 | 0.045776 | 0.49347 | -0.45288 | -0.17838 | -0.14954 | -0.24139 | -0.15595 | 0.045776 | -0.064087 | 0.059509 | -0.022888 | -0.13275 | -0.12817 | -0.018311 | 0.030518 | -0.043793 | -0.2243 | -0.032043 | -0.15167 | -0.11215 | -0.054932 | -0.027466 | -0.10986 | -0.11902 | -0.10529 | -0.14648 | -0.073242 | -0.091553 | 0.054932 | -0.064087
345.3594 | 0.045776 | 0.52445 | -0.46463 | -0.16983 | -0.15381 | -0.26276 | -0.15808 | 0.004578 | -0.10986 | 0.041199 | -0.059509 | -0.19684 | -0.082397 | 0.022888 | 0.061035 | -0.057678 | -0.24567 | -0.044861 | -0.16129 | -0.11536 | 0.013733 | 0.054932 | -0.045776 | -0.21057 | -0.17395 | -0.13733 | -0.073242 | -0.027466 | 0.041199 | -0.07782
347.0156 | 0.045776 | 0.51376 | -0.44968 | -0.1976 | -0.13245 | -0.28198 | -0.15488 | 0.004578 | -0.054932 | 0.045776 | -0.018311 | -0.17395 | -0.10986 | -0.013733 | 0.045776 | -0.069427 | -0.23498 | -0.049133 | -0.1741 | -0.10681 | 0.027466 | 0.11902 | -0.045776 | -0.17395 | -0.12817 | -0.15106 | -0.086975 | -0.027466 | 0.059509 | -0.073242
348.6875 | 0.045776 | 0.49667 | -0.44968 | -0.18799 | -0.1442 | -0.2478 | -0.15488 | -0.013733 | -0.12817 | 0.036621 | -0.059509 | -0.16937 | -0.082397 | 0.018311 | 0.045776 | -0.061951 | -0.23926 | -0.044861 | -0.16556 | -0.11749 | -0.009155 | -0.004578 | -0.068665 | -0.1831 | -0.16937 | -0.15106 | -0.064087 | -0.027466 | 0.036621 | -0.073242
350.4375 | 0.045776 | 0.49988 | -0.46249 | -0.18265 | -0.1442 | -0.27023 | -0.15488 | 0.036621 | -0.032043 | 0.10986 | -0.022888 | -0.23804 | -0.068665 | 0.004578 | 0.030518 | -0.070496 | -0.23819 | -0.03952 | -0.16876 | -0.12283 | 0.064087 | 0.10529 | -0.022888 | -0.22888 | -0.17853 | -0.16022 | -0.073242 | -0.091553 | 0.059509 | -0.054932
352.1562 | 0.061035 | 0.48599 | -0.45609 | -0.1709 | -0.13992 | -0.24353 | -0.15701 | -0.041199 | -0.16479 | -0.013733 | -0.054932 | -0.14648 | -0.09613 | 0.009155 | 0.061035 | -0.053406 | -0.24139 | -0.043793 | -0.16129 | -0.11643 | -0.07782 | -0.09613 | -0.14191 | -0.15106 | -0.1236 | -0.1236 | -0.054932 | -0.10071 | 0.045776 | -0.054932
353.8281 | 0.030518 | 0.51697 | -0.46463 | -0.18372 | -0.1506 | -0.27023 | -0.16129 | 0 | -0.059509 | 0.045776 | -0.004578 | -0.17395 | -0.10071 | 0.013733 | 0.045776 | -0.086517 | -0.24033 | -0.059814 | -0.16769 | -0.11002 | 0.041199 | 0.11444 | -0.018311 | -0.16479 | -0.12817 | -0.15106 | -0.10529 | -0.013733 | 0.045776 | -0.09613
355.5625 | 0.030518 | 0.50415 | -0.45395 | -0.19226 | -0.1506 | -0.26489 | -0.15701 | 0.009155 | -0.045776 | 0.082397 | -0.054932 | -0.22888 | -0.064087 | 0.018311 | 0.030518 | -0.087585 | -0.23605 | -0.053406 | -0.15915 | -0.12176 | 0.07782 | 0.082397 | -0.036621 | -0.19226 | -0.16479 | -0.15564 | -0.10529 | -0.082397 | 0.064087 | -0.082397
357.2344 | 0.030518 | 0.49561 | -0.44754 | -0.19653 | -0.13245 | -0.24353 | -0.16556 | 0.068665 | -0.013733 | 0.064087 | 0.022888 | -0.054932 | -0.16022 | -0.054932 | 0.045776 | -0.057678 | -0.24353 | -0.043793 | -0.16663 | -0.11643 | 0.032043 | 0.082397 | -0.032043 | -0.073242 | -0.054932 | -0.19684 | -0.1236 | 0.009155 | 0.032043 | -0.091553
358.9062 | 0.045776 | 0.50842 | -0.45075 | -0.18906 | -0.15381 | -0.24033 | -0.14313 | -0.022888 | -0.15106 | 0 | -0.054932 | -0.14648 | -0.086975 | 0 | 0.030518 | -0.040588 | -0.23178 | -0.03418 | -0.15274 | -0.12497 | -0.082397 | -0.068665 | -0.15106 | -0.15106 | -0.09613 | -0.11902 | -0.064087 | -0.086975 | 0.045776 | -0.050354
360.6406 | 0.076294 | 0.50095 | -0.45075 | -0.18906 | -0.14633 | -0.25314 | -0.15915 | -0.018311 | -0.13275 | 0.018311 | -0.064087 | -0.15106 | -0.082397 | 0.027466 | 0.061035 | -0.052338 | -0.24246 | -0.037384 | -0.16022 | -0.11643 | -0.022888 | -0.009155 | -0.07782 | -0.17395 | -0.16479 | -0.11444 | -0.073242 | -0.041199 | 0.045776 | -0.073242
362.375 | 0.045776 | 0.49347 | -0.45929 | -0.18372 | -0.1442 | -0.25101 | -0.15595 | -0.064087 | -0.17395 | 0 | -0.068665 | -0.13275 | -0.09613 | 0.018311 | 0.030518 | -0.055542 | -0.23178 | -0.029907 | -0.14954 | -0.11749 | -0.086975 | -0.091553 | -0.16479 | -0.13733 | -0.11902 | -0.12817 | -0.064087 | -0.082397 | 0.041199 | -0.068665
364.0312 | 0.030518 | 0.49774 | -0.45395 | -0.18799 | -0.15701 | -0.25314 | -0.1442 | -0.027466 | -0.14191 | -0.009155 | -0.073242 | -0.14191 | -0.068665 | 0.022888 | 0.061035 | -0.05127 | -0.23392 | -0.03952 | -0.16235 | -0.11429 | -0.059509 | -0.068665 | -0.1236 | -0.13733 | -0.1236 | -0.12817 | -0.068665 | -0.050354 | 0.032043 | -0.086975
365.7188 | 0.045776 | 0.50629 | -0.46036 | -0.19867 | -0.16235 | -0.27237 | -0.15701 | 0.041199 | -0.036621 | 0.09613 | -0.045776 | -0.21057 | -0.082397 | 0.004578 | 0.061035 | -0.064087 | -0.22858 | -0.05127 | -0.17197 | -0.11536 | 0.041199 | 0.07782 | -0.045776 | -0.20599 | -0.17853 | -0.11444 | -0.068665 | -0.086975 | 0.059509 | -0.064087
367.3906 | 0.030518 | 0.50095 | -0.44861 | -0.18478 | -0.15488 | -0.24674 | -0.15381 | -0.032043 | -0.16022 | -0.013733 | -0.054932 | -0.13275 | -0.07782 | 0.013733 | 0.076294 | -0.060883 | -0.23392 | -0.045929 | -0.15701 | -0.12497 | -0.09613 | -0.07782 | -0.16479 | -0.14191 | -0.11444 | -0.11444 | -0.041199 | -0.086975 | 0.041199 | -0.064087
369.0469 | 0.045776 | 0.50949 | -0.46249 | -0.1976 | -0.13779 | -0.27985 | -0.16022 | 0.004578 | -0.054932 | 0.050354 | -0.013733 | -0.17395 | -0.11902 | -0.009155 | 0.030518 | -0.071564 | -0.23498 | -0.046997 | -0.16663 | -0.11536 | 0.027466 | 0.10529 | -0.045776 | -0.16937 | -0.1236 | -0.15564 | -0.086975 | -0.036621 | 0.054932 | -0.073242
370.7188 | 0.045776 | 0.5159 | -0.45822 | -0.19012 | -0.15274 | -0.25742 | -0.16235 | 0.022888 | -0.027466 | 0.07782 | -0.009155 | -0.19684 | -0.10986 | -0.018311 | 0.045776 | -0.070496 | -0.23498 | -0.035248 | -0.16449 | -0.12817 | 0.045776 | 0.091553 | -0.041199 | -0.15106 | -0.15106 | -0.16022 | -0.086975 | -0.082397 | 0.068665 | -0.073242
372.4531 | 0.045776 | 0.49347 | -0.45075 | -0.18265 | -0.14099 | -0.24567 | -0.16129 | 0.082397 | -0.004578 | 0.064087 | 0.054932 | -0.045776 | -0.19684 | -0.073242 | 0.045776 | -0.052338 | -0.24033 | -0.03952 | -0.15808 | -0.12924 | -0.022888 | 0.045776 | -0.050354 | -0.082397 | -0.091553 | -0.17853 | -0.10986 | 0.041199 | -0.009155 | -0.09613
374.1875 | 0.045776 | 0.49667 | -0.44647 | -0.17624 | -0.14954 | -0.24887 | -0.15381 | -0.032043 | -0.14191 | -0.013733 | -0.064087 | -0.1236 | -0.082397 | 0.009155 | 0.030518 | -0.058746 | -0.24246 | -0.037384 | -0.15488 | -0.11002 | -0.073242 | -0.082397 | -0.13733 | -0.12817 | -0.1236 | -0.12817 | -0.054932 | -0.068665 | 0.036621 | -0.059509
375.8594 | 0.045776 | 0.50736 | -0.45075 | -0.19119 | -0.1506 | -0.28625 | -0.16022 | 0.022888 | -0.027466 | 0.073242 | -0.041199 | -0.21057 | -0.073242 | 0.009155 | 0.030518 | -0.076904 | -0.23819 | -0.05127 | -0.16663 | -0.11215 | 0.041199 | 0.07782 | -0.032043 | -0.20599 | -0.1831 | -0.11902 | -0.041199 | -0.10071 | 0.064087 | -0.045776
377.5938 | 0.061035 | 0.48599 | -0.44968 | -0.19333 | -0.1506 | -0.2446 | -0.15701 | 0.036621 | -0.036621 | 0.068665 | 0 | -0.11902 | -0.11902 | -0.022888 | 0.045776 | -0.055542 | -0.23285 | -0.053406 | -0.15915 | -0.12497 | -0.032043 | 0 | -0.082397 | -0.10986 | -0.091553 | -0.15564 | -0.091553 | -0.082397 | 0.032043 | -0.073242
379.3125 | 0.030518 | 0.50629 | -0.46143 | -0.18906 | -0.15274 | -0.27878 | -0.15701 | 0.050354 | 0.013733 | 0.10529 | 0.022888 | -0.14191 | -0.12817 | -0.018311 | 0.045776 | -0.072632 | -0.23071 | -0.046997 | -0.17303 | -0.1207 | 0.11444 | 0.19684 | 0.050354 | -0.14648 | -0.13733 | -0.19226 | -0.10986 | 0.059509 | 0.036621 | -0.11444
380.9844 | 0.030518 | 0.49454 | -0.44861 | -0.18906 | -0.1442 | -0.23498 | -0.16342 | 0.082397 | -0.004578 | 0.091553 | 0.032043 | -0.091553 | -0.12817 | -0.013733 | 0.045776 | -0.054474 | -0.24674 | -0.045929 | -0.15701 | -0.12176 | 0.009155 | 0.032043 | -0.041199 | -0.10071 | -0.091553 | -0.16022 | -0.10071 | 0.018311 | 0.009155 | -0.082397
382.7188 | 0.061035 | 0.49667 | -0.46249 | -0.18692 | -0.14206 | -0.26062 | -0.15701 | 0.022888 | -0.027466 | 0.10986 | -0.013733 | -0.23346 | -0.07782 | 0.013733 | 0.015259 | -0.0737 | -0.23392 | -0.042725 | -0.16129 | -0.11963 | 0.050354 | 0.09613 | -0.032043 | -0.20142 | -0.20142 | -0.14648 | -0.073242 | -0.10071 | 0.054932 | -0.036621
384.4688 | 0.030518 | 0.49774 | -0.45929 | -0.18265 | -0.1506 | -0.23819 | -0.15701 | 0.073242 | -0.027466 | 0.082397 | 0 | -0.10529 | -0.11444 | -0.018311 | 0.061035 | -0.048065 | -0.23819 | -0.033112 | -0.15915 | -0.10895 | -0.027466 | 0.009155 | -0.068665 | -0.10071 | -0.10071 | -0.16479 | -0.086975 | -0.086975 | 0.022888 | -0.07782
386.1406 | 0.045776 | 0.4924 | -0.44968 | -0.20721 | -0.1442 | -0.26169 | -0.14954 | 0.059509 | -0.032043 | 0.054932 | 0.036621 | -0.018311 | -0.16479 | -0.059509 | 0.061035 | -0.065155 | -0.22858 | -0.038452 | -0.17731 | -0.12176 | -0.027466 | 0.036621 | -0.054932 | -0.059509 | -0.045776 | -0.18768 | -0.11902 | 0.059509 | 0.018311 | -0.086975
387.8125 | 0.045776 | 0.49667 | -0.45929 | -0.19119 | -0.13565 | -0.26169 | -0.15595 | 0.07782 | 0.054932 | 0.13275 | 0.082397 | -0.10071 | -0.16022 | -0.059509 | 0.045776 | -0.072632 | -0.22537 | -0.050201 | -0.1709 | -0.12283 | 0.050354 | 0.16022 | 0.013733 | -0.091553 | -0.073242 | -0.21057 | -0.13275 | -0.004578 | 0.022888 | -0.086975
389.4844 | 0.061035 | 0.47424 | -0.46036 | -0.19119 | -0.14313 | -0.26062 | -0.15915 | 0.054932 | -0.027466 | 0.064087 | 0.009155 | -0.041199 | -0.15106 | -0.045776 | 0.015259 | -0.060883 | -0.23178 | -0.048065 | -0.16983 | -0.12604 | 0.004578 | 0.086975 | -0.032043 | -0.059509 | -0.050354 | -0.18768 | -0.11444 | 0 | 0.036621 | -0.10071
391.2188 | 0.061035 | 0.48813 | -0.45929 | -0.17517 | -0.13779 | -0.2478 | -0.15595 | 0.068665 | -0.013733 | 0.086975 | 0.036621 | -0.073242 | -0.15106 | -0.032043 | 0.030518 | -0.065155 | -0.23498 | -0.053406 | -0.15167 | -0.11643 | 0.004578 | 0.054932 | -0.032043 | -0.11444 | -0.086975 | -0.1831 | -0.07782 | 0.004578 | 0 | -0.082397
392.9062 | 0.045776 | 0.49988 | -0.4454 | -0.1741 | -0.1474 | -0.25207 | -0.15167 | -0.050354 | -0.14648 | -0.009155 | -0.073242 | -0.12817 | -0.073242 | 0.018311 | 0.045776 | -0.057678 | -0.24246 | -0.043793 | -0.16235 | -0.1207 | -0.059509 | -0.059509 | -0.14191 | -0.1236 | -0.11444 | -0.11902 | -0.059509 | -0.064087 | 0.041199 | -0.068665
394.6406 | 0.045776 | 0.50522 | -0.45715 | -0.20187 | -0.15381 | -0.27344 | -0.16342 | -0.004578 | -0.064087 | 0.068665 | -0.045776 | -0.2243 | -0.054932 | 0.032043 | 0.045776 | -0.086517 | -0.23285 | -0.049133 | -0.17197 | -0.1207 | 0.045776 | 0.10529 | -0.027466 | -0.19226 | -0.14191 | -0.16022 | -0.086975 | -0.082397 | 0.068665 | -0.073242
396.3906 | 0.045776 | 0.48706 | -0.4454 | -0.19226 | -0.13992 | -0.25955 | -0.16876 | 0.10529 | 0.054932 | 0.14191 | 0.082397 | -0.11444 | -0.15564 | -0.054932 | 0.061035 | -0.068359 | -0.21896 | -0.041656 | -0.18265 | -0.12711 | 0.068665 | 0.17395 | 0.022888 | -0.10986 | -0.082397 | -0.18768 | -0.12817 | -0.004578 | 0.027466 | -0.091553
398.0469 | 0.061035 | 0.50201 | -0.45822 | -0.18585 | -0.14526 | -0.25955 | -0.15381 | 0.11902 | 0.068665 | 0.15106 | 0.073242 | -0.11902 | -0.16022 | -0.064087 | 0.030518 | -0.070496 | -0.23605 | -0.046997 | -0.17197 | -0.13351 | 0.082397 | 0.19684 | 0.032043 | -0.1236 | -0.09613 | -0.17853 | -0.12817 | 0.018311 | 0.027466 | -0.082397
399.7188 | 0.061035 | 0.4924 | -0.45288 | -0.1976 | -0.15595 | -0.26062 | -0.17197 | 0.11902 | 0.086975 | 0.15106 | 0.091553 | -0.11902 | -0.15564 | -0.064087 | 0.015259 | -0.075836 | -0.2446 | -0.035248 | -0.17624 | -0.11856 | 0.10986 | 0.21057 | 0.054932 | -0.1236 | -0.10529 | -0.20142 | -0.13275 | 0.018311 | 0.018311 | -0.10529
401.3906 | 0.045776 | 0.48279 | -0.45181 | -0.18372 | -0.14313 | -0.24246 | -0.16556 | 0.068665 | -0.004578 | 0.07782 | 0.032043 | -0.082397 | -0.12817 | -0.036621 | 0.061035 | -0.053406 | -0.23178 | -0.03418 | -0.15808 | -0.12604 | 0.004578 | 0.068665 | -0.036621 | -0.09613 | -0.082397 | -0.17853 | -0.11444 | 0.036621 | 0.004578 | -0.086975
403.0469 | 0.015259 | 0.50308 | -0.45502 | -0.16876 | -0.15488 | -0.25314 | -0.14633 | 0.009155 | -0.045776 | 0.068665 | -0.018311 | -0.19684 | -0.059509 | 0.009155 | 0.030518 | -0.068359 | -0.2446 | -0.044861 | -0.14954 | -0.1207 | 0.018311 | 0.073242 | -0.036621 | -0.21057 | -0.17853 | -0.13275 | -0.07782 | -0.027466 | 0.045776 | -0.073242
404.7188 | 0.045776 | 0.47745 | -0.45395 | -0.19546 | -0.15167 | -0.24887 | -0.14847 | 0.09613 | -0.013733 | 0.073242 | 0.059509 | -0.045776 | -0.17853 | -0.064087 | 0.030518 | -0.050201 | -0.24139 | -0.044861 | -0.15701 | -0.12604 | -0.018311 | 0.041199 | -0.045776 | -0.09613 | -0.064087 | -0.16937 | -0.091553 | 0.032043 | -0.018311 | -0.09613
406.4688 | 0.030518 | 0.49774 | -0.46036 | -0.19012 | -0.15167 | -0.2681 | -0.15808 | 0.050354 | -0.013733 | 0.041199 | 0.022888 | -0.041199 | -0.14648 | -0.064087 | 0.045776 | -0.075836 | -0.23285 | -0.052338 | -0.16022 | -0.11108 | -0.009155 | 0.073242 | -0.032043 | -0.054932 | -0.013733 | -0.20142 | -0.13275 | 0.036621 | 0.009155 | -0.086975
408.2031 | 0.030518 | 0.4892 | -0.44113 | -0.19867 | -0.14847 | -0.24674 | -0.16449 | 0.059509 | -0.022888 | 0.073242 | 0.032043 | -0.054932 | -0.14191 | -0.027466 | 0.061035 | -0.059814 | -0.23285 | -0.050201 | -0.16022 | -0.1207 | -0.009155 | 0.059509 | -0.059509 | -0.10986 | -0.086975 | -0.16479 | -0.10071 | 0.036621 | 0.004578 | -0.091553
409.9375 | 0.061035 | 0.49774 | -0.46356 | -0.19653 | -0.14313 | -0.28305 | -0.16983 | 0.013733 | -0.036621 | 0.064087 | 0.013733 | -0.14648 | -0.11444 | -0.013733 | 0.030518 | -0.082245 | -0.24246 | -0.042725 | -0.17731 | -0.11749 | 0.045776 | 0.14191 | 0.004578 | -0.16022 | -0.12817 | -0.16022 | -0.10986 | 0.036621 | 0.013733 | -0.10071
411.6094 | 0.045776 | 0.48172 | -0.44647 | -0.19226 | -0.14099 | -0.24353 | -0.14313 | 0.013733 | -0.07782 | 0.054932 | -0.018311 | -0.10986 | -0.11902 | -0.004578 | 0.030518 | -0.05661 | -0.23498 | -0.03952 | -0.15274 | -0.11963 | -0.086975 | -0.045776 | -0.11902 | -0.10986 | -0.091553 | -0.13733 | -0.073242 | -0.091553 | 0.032043 | -0.054932
413.2812 | 0.030518 | 0.49347 | -0.44861 | -0.20508 | -0.15488 | -0.2713 | -0.15488 | 0.022888 | -0.027466 | 0.11444 | -0.013733 | -0.21515 | -0.07782 | 0.018311 | 0.045776 | -0.072632 | -0.23498 | -0.037384 | -0.1709 | -0.11643 | 0.068665 | 0.091553 | -0.036621 | -0.19226 | -0.16479 | -0.11444 | -0.064087 | -0.091553 | 0.054932 | -0.059509
415 | 0.045776 | 0.49881 | -0.44861 | -0.1741 | -0.14313 | -0.25101 | -0.14633 | 0.032043 | -0.032043 | 0.091553 | -0.009155 | -0.21057 | -0.073242 | 0.022888 | 0.045776 | -0.068359 | -0.23926 | -0.042725 | -0.15488 | -0.11749 | 0.041199 | 0.082397 | -0.022888 | -0.19226 | -0.19226 | -0.13733 | -0.054932 | -0.045776 | 0.041199 | -0.059509
416.6875 | 0.045776 | 0.48386 | -0.44647 | -0.18799 | -0.14313 | -0.24567 | -0.15808 | 0.068665 | -0.004578 | 0.068665 | 0.036621 | -0.045776 | -0.15106 | -0.064087 | 0.045776 | -0.061951 | -0.23926 | -0.03418 | -0.15808 | -0.12924 | -0.009155 | 0.027466 | -0.064087 | -0.082397 | -0.07782 | -0.17395 | -0.09613 | 0.054932 | -0.004578 | -0.086975
418.4219 | 0.061035 | 0.4924 | -0.45502 | -0.20508 | -0.1474 | -0.26382 | -0.16129 | 0.10529 | 0.07782 | 0.16479 | 0.073242 | -0.11902 | -0.16479 | -0.054932 | 0.045776 | -0.077972 | -0.23605 | -0.041656 | -0.16876 | -0.1207 | 0.10986 | 0.20142 | 0.050354 | -0.1236 | -0.086975 | -0.20142 | -0.11902 | 0.009155 | 0.036621 | -0.086975
420.1562 | 0.045776 | 0.49027 | -0.45075 | -0.19119 | -0.13779 | -0.24567 | -0.1709 | 0.050354 | -0.050354 | 0.027466 | 0.036621 | -0.036621 | -0.13733 | -0.064087 | 0.045776 | -0.058746 | -0.24033 | -0.050201 | -0.15808 | -0.13245 | 0.009155 | 0.059509 | -0.041199 | -0.041199 | -0.036621 | -0.1831 | -0.1236 | 0.059509 | -0.009155 | -0.073242
421.8438 | 0.045776 | 0.50201 | -0.44861 | -0.16556 | -0.13565 | -0.24033 | -0.15595 | 0.013733 | -0.064087 | 0.054932 | -0.009155 | -0.10071 | -0.10986 | -0.004578 | 0.030518 | -0.059814 | -0.24033 | -0.041656 | -0.15167 | -0.12283 | -0.054932 | -0.036621 | -0.11902 | -0.13275 | -0.10986 | -0.11902 | -0.064087 | -0.09613 | 0.032043 | -0.045776
423.5781 | 0.045776 | 0.49347 | -0.4422 | -0.18265 | -0.1474 | -0.26062 | -0.15167 | -0.041199 | -0.15106 | -0.004578 | -0.050354 | -0.12817 | -0.082397 | 0.027466 | 0.061035 | -0.067291 | -0.23819 | -0.037384 | -0.15488 | -0.11963 | -0.09613 | -0.073242 | -0.15106 | -0.11902 | -0.10529 | -0.1236 | -0.059509 | -0.073242 | 0.045776 | -0.050354
425.3125 | 0.030518 | 0.47638 | -0.45929 | -0.20721 | -0.15274 | -0.25635 | -0.15488 | 0.027466 | -0.050354 | 0.054932 | 0.032043 | -0.018311 | -0.13733 | -0.041199 | 0.061035 | -0.066223 | -0.22644 | -0.041656 | -0.16769 | -0.11856 | -0.027466 | 0.054932 | -0.059509 | -0.064087 | -0.045776 | -0.17395 | -0.11444 | 0.064087 | -0.009155 | -0.086975
426.9844 | 0.045776 | 0.49027 | -0.44968 | -0.19867 | -0.15595 | -0.28305 | -0.16449 | -0.009155 | -0.045776 | 0.07782 | -0.036621 | -0.19226 | -0.07782 | 0.022888 | 0.045776 | -0.082245 | -0.23285 | -0.042725 | -0.16663 | -0.11536 | 0.054932 | 0.09613 | -0.022888 | -0.17853 | -0.13275 | -0.14648 | -0.082397 | -0.068665 | 0.073242 | -0.064087
428.7188 | 0.030518 | 0.48279 | -0.45395 | -0.19012 | -0.16129 | -0.28519 | -0.17197 | 0.09613 | 0.059509 | 0.11444 | 0.045776 | -0.11902 | -0.13733 | -0.022888 | 0.030518 | -0.076904 | -0.24674 | -0.053406 | -0.15915 | -0.12283 | 0.14191 | 0.20599 | 0.086975 | -0.12817 | -0.10986 | -0.18768 | -0.12817 | 0.073242 | -0.004578 | -0.091553
430.3906 | 0.030518 | 0.4924 | -0.46249 | -0.1944 | -0.1474 | -0.26489 | -0.16769 | 0.1236 | 0.073242 | 0.14648 | 0.073242 | -0.13275 | -0.15106 | -0.041199 | 0.030518 | -0.074768 | -0.22751 | -0.035248 | -0.17197 | -0.1207 | 0.15564 | 0.23346 | 0.059509 | -0.1236 | -0.11902 | -0.18768 | -0.11444 | 0.068665 | 0.022888 | -0.10071
432.0469 | 0.045776 | 0.48599 | -0.45715 | -0.17731 | -0.15701 | -0.24674 | -0.15915 | -0.045776 | -0.15106 | -0.013733 | -0.059509 | -0.11444 | -0.054932 | 0.027466 | 0.045776 | -0.060883 | -0.23926 | -0.033112 | -0.14847 | -0.1207 | -0.045776 | -0.091553 | -0.14648 | -0.1236 | -0.11444 | -0.09613 | -0.036621 | -0.068665 | 0.045776 | -0.050354
433.7188 | 0.030518 | 0.47745 | -0.45822 | -0.17517 | -0.14099 | -0.23819 | -0.15701 | 0.086975 | -0.013733 | 0.082397 | 0.032043 | -0.091553 | -0.12817 | -0.013733 | 0.030518 | -0.057678 | -0.23926 | -0.043793 | -0.15595 | -0.12497 | 0.018311 | 0.036621 | -0.059509 | -0.082397 | -0.073242 | -0.13275 | -0.068665 | -0.004578 | 0.022888 | -0.068665
435.4531 | 0.045776 | 0.49133 | -0.45181 | -0.19226 | -0.13886 | -0.26596 | -0.14633 | 0.027466 | -0.032043 | 0.1236 | -0.013733 | -0.20599 | -0.064087 | 0.032043 | 0.030518 | -0.083313 | -0.23178 | -0.041656 | -0.16342 | -0.11856 | 0.082397 | 0.10529 | -0.032043 | -0.20599 | -0.18768 | -0.13733 | -0.064087 | -0.073242 | 0.059509 | -0.068665
437.1875 | 0.045776 | 0.48706 | -0.45502 | -0.1944 | -0.1442 | -0.2681 | -0.16556 | 0.1236 | 0.068665 | 0.14648 | 0.082397 | -0.11902 | -0.17395 | -0.050354 | 0.045776 | -0.080109 | -0.23605 | -0.046997 | -0.15915 | -0.11856 | 0.11444 | 0.19684 | 0.032043 | -0.11902 | -0.09613 | -0.20599 | -0.10986 | 0.032043 | 0.022888 | -0.086975
438.8594 | 0.030518 | 0.48492 | -0.45609 | -0.20294 | -0.14954 | -0.26703 | -0.16449 | 0.036621 | -0.009155 | 0.082397 | 0.013733 | -0.13275 | -0.12817 | -0.004578 | 0.045776 | -0.09079 | -0.22537 | -0.048065 | -0.18158 | -0.12604 | 0.10071 | 0.14191 | 0.004578 | -0.15106 | -0.11902 | -0.16937 | -0.09613 | 0.059509 | 0.009155 | -0.10986
440.5938 | 0.045776 | 0.49774 | -0.45502 | -0.19012 | -0.15595 | -0.24567 | -0.16342 | -0.018311 | -0.09613 | 0.032043 | -0.064087 | -0.14648 | -0.054932 | 0.045776 | 0.015259 | -0.065155 | -0.24033 | -0.032043 | -0.14954 | -0.12711 | 0.013733 | -0.004578 | -0.064087 | -0.16479 | -0.17395 | -0.11902 | -0.041199 | -0.045776 | 0.041199 | -0.07782
442.25 | 0.045776 | 0.47852 | -0.4454 | -0.18372 | -0.16235 | -0.24994 | -0.15595 | -0.050354 | -0.15106 | -0.018311 | -0.054932 | -0.10986 | -0.073242 | 0.027466 | 0.030518 | -0.055542 | -0.22964 | -0.042725 | -0.16129 | -0.12176 | -0.050354 | -0.07782 | -0.14648 | -0.11444 | -0.1236 | -0.11902 | -0.036621 | -0.054932 | 0.022888 | -0.054932
443.9219 | 0.045776 | 0.47852 | -0.45609 | -0.17944 | -0.16235 | -0.25207 | -0.15381 | -0.041199 | -0.14191 | -0.004578 | -0.068665 | -0.10529 | -0.059509 | 0.022888 | 0.030518 | -0.054474 | -0.23498 | -0.03418 | -0.14313 | -0.10895 | -0.059509 | -0.07782 | -0.16022 | -0.1236 | -0.10529 | -0.10986 | -0.041199 | -0.07782 | 0.027466 | -0.041199
445.6562 | 0.045776 | 0.46997 | -0.44861 | -0.18906 | -0.14633 | -0.25101 | -0.15274 | 0.068665 | -0.004578 | 0.073242 | 0.032043 | -0.073242 | -0.14191 | -0.022888 | 0.045776 | -0.065155 | -0.23819 | -0.041656 | -0.15808 | -0.13031 | 0.032043 | 0.050354 | -0.036621 | -0.091553 | -0.082397 | -0.15564 | -0.09613 | 0.032043 | -0.004578 | -0.09613
447.3906 | 0.030518 | 0.47745 | -0.44006 | -0.1976 | -0.14847 | -0.24353 | -0.15915 | -0.068665 | -0.14648 | -0.009155 | -0.059509 | -0.10071 | -0.068665 | 0.036621 | 0.045776 | -0.067291 | -0.23926 | -0.038452 | -0.16769 | -0.11536 | -0.068665 | -0.091553 | -0.15106 | -0.1236 | -0.091553 | -0.10986 | -0.050354 | -0.091553 | 0.041199 | -0.045776
449.0469 | 0.030518 | 0.49988 | -0.46356 | -0.19333 | -0.13245 | -0.28946 | -0.16449 | 0.009155 | -0.036621 | 0.054932 | -0.027466 | -0.15564 | -0.09613 | 0.018311 | 0.061035 | -0.084381 | -0.24353 | -0.03952 | -0.16449 | -0.11963 | 0.050354 | 0.07782 | -0.041199 | -0.16022 | -0.13733 | -0.14648 | -0.073242 | -0.050354 | 0.054932 | -0.059509
450.7188 | 0.030518 | 0.49133 | -0.45075 | -0.19012 | -0.15488 | -0.26703 | -0.15274 | 0.013733 | -0.018311 | 0.1236 | -0.022888 | -0.19226 | -0.059509 | 0 | 0.015259 | -0.076904 | -0.24139 | -0.05127 | -0.16022 | -0.12924 | 0.068665 | 0.09613 | -0.022888 | -0.19684 | -0.1831 | -0.11902 | -0.059509 | -0.09613 | 0.045776 | -0.054932
452.4688 | 0.076294 | 0.47745 | -0.44647 | -0.19119 | -0.15488 | -0.26276 | -0.16556 | 0.036621 | -0.027466 | 0.10071 | -0.032043 | -0.19226 | -0.068665 | 0.032043 | 0.015259 | -0.077972 | -0.24567 | -0.05127 | -0.16342 | -0.12711 | 0.045776 | 0.073242 | -0.045776 | -0.19684 | -0.19226 | -0.10986 | -0.050354 | -0.082397 | 0.073242 | -0.045776
454.2031 | 0.045776 | 0.48599 | -0.44754 | -0.19974 | -0.15167 | -0.2681 | -0.1709 | 0.13275 | 0.09613 | 0.15564 | 0.068665 | -0.11902 | -0.16022 | -0.064087 | 0.076294 | -0.087585 | -0.23071 | -0.043793 | -0.16129 | -0.14099 | 0.13733 | 0.21973 | 0.064087 | -0.11902 | -0.10529 | -0.17395 | -0.12817 | 0.059509 | 0.022888 | -0.091553
455.875 | 0.030518 | 0.48492 | -0.44968 | -0.19653 | -0.15701 | -0.23712 | -0.15381 | 0.068665 | -0.004578 | 0.091553 | 0.032043 | -0.054932 | -0.11444 | -0.036621 | 0.030518 | -0.061951 | -0.23178 | -0.03952 | -0.14954 | -0.13779 | 0.045776 | 0.050354 | -0.041199 | -0.09613 | -0.07782 | -0.16022 | -0.086975 | 0.009155 | -0.013733 | -0.073242
457.5469 | 0.045776 | 0.47958 | -0.44754 | -0.18051 | -0.1474 | -0.25207 | -0.15915 | 0.073242 | -0.022888 | 0.050354 | 0.032043 | -0.059509 | -0.14191 | -0.022888 | 0.045776 | -0.066223 | -0.23819 | -0.03952 | -0.15915 | -0.12711 | 0.013733 | 0.064087 | -0.050354 | -0.09613 | -0.073242 | -0.15106 | -0.082397 | 0.041199 | -0.022888 | -0.086975
459.2812 | 0.030518 | 0.47424 | -0.46036 | -0.19012 | -0.1442 | -0.27664 | -0.15701 | 0.10986 | 0.086975 | 0.16479 | 0.07782 | -0.11444 | -0.15106 | -0.059509 | 0.030518 | -0.081177 | -0.24567 | -0.054474 | -0.17303 | -0.13031 | 0.13733 | 0.23346 | 0.068665 | -0.13275 | -0.091553 | -0.19684 | -0.13733 | 0.036621 | 0.013733 | -0.10071
460.9531 | 0.045776 | 0.47958 | -0.45288 | -0.18692 | -0.14313 | -0.25635 | -0.16342 | 0.059509 | -0.027466 | 0.059509 | 0.032043 | 0 | -0.14648 | -0.059509 | 0.015259 | -0.060883 | -0.24246 | -0.043793 | -0.16342 | -0.13138 | 0.009155 | 0.045776 | -0.064087 | -0.041199 | -0.018311 | -0.16479 | -0.10986 | 0.045776 | 0.018311 | -0.064087
462.6875 | 0.045776 | 0.48172 | -0.45075 | -0.19546 | -0.14954 | -0.25848 | -0.15915 | 0.022888 | -0.032043 | 0.10071 | -0.018311 | -0.19226 | -0.082397 | 0.036621 | 0.030518 | -0.069427 | -0.23178 | -0.030975 | -0.15595 | -0.13565 | 0.068665 | 0.091553 | -0.018311 | -0.21515 | -0.1831 | -0.11444 | -0.045776 | -0.07782 | 0.064087 | -0.041199
464.4219 | 0.045776 | 0.48492 | -0.46143 | -0.1944 | -0.1474 | -0.26062 | -0.15595 | 0.082397 | 0.032043 | 0.1236 | 0.068665 | -0.059509 | -0.16022 | -0.045776 | 0.045776 | -0.071564 | -0.24033 | -0.052338 | -0.16342 | -0.12604 | 0.064087 | 0.10986 | -0.032043 | -0.059509 | -0.041199 | -0.18768 | -0.10529 | 0.004578 | 0.027466 | -0.073242
466.0781 | 0.030518 | 0.50415 | -0.45288 | -0.18692 | -0.1474 | -0.27344 | -0.16129 | 0.009155 | -0.032043 | 0.07782 | -0.013733 | -0.16022 | -0.10986 | -0.013733 | 0.076294 | -0.0737 | -0.24139 | -0.048065 | -0.16235 | -0.12604 | 0.064087 | 0.086975 | -0.045776 | -0.14191 | -0.12817 | -0.14191 | -0.068665 | -0.073242 | 0.050354 | -0.073242
467.75 | 0.015259 | 0.48706 | -0.45822 | -0.19974 | -0.14847 | -0.27451 | -0.16022 | 0.068665 | 0.013733 | 0.10986 | 0.032043 | -0.11902 | -0.11444 | -0.027466 | 0.061035 | -0.079041 | -0.2478 | -0.046997 | -0.17624 | -0.13672 | 0.15106 | 0.20142 | 0.041199 | -0.13733 | -0.12817 | -0.16937 | -0.086975 | 0.073242 | 0.032043 | -0.086975
469.4219 | 0.015259 | 0.48813 | -0.45075 | -0.18585 | -0.15808 | -0.26169 | -0.15915 | 0.041199 | -0.027466 | 0.091553 | -0.018311 | -0.19684 | -0.059509 | 0.022888 | 0.045776 | -0.069427 | -0.23712 | -0.03952 | -0.15488 | -0.13351 | 0.07782 | 0.10071 | -0.027466 | -0.1831 | -0.1831 | -0.10986 | -0.050354 | -0.091553 | 0.054932 | -0.059509
471.1406 | 0.030518 | 0.49133 | -0.44006 | -0.17624 | -0.15274 | -0.24246 | -0.15167 | -0.013733 | -0.11902 | 0.013733 | -0.050354 | -0.11902 | -0.068665 | 0.027466 | 0.030518 | -0.067291 | -0.24353 | -0.05127 | -0.15915 | -0.13245 | 0.013733 | -0.018311 | -0.086975 | -0.15564 | -0.12817 | -0.10986 | -0.045776 | -0.041199 | 0.018311 | -0.059509
472.8281 | 0.045776 | 0.49774 | -0.45075 | -0.18906 | -0.15701 | -0.25528 | -0.15915 | -0.018311 | -0.10071 | 0.036621 | -0.059509 | -0.13733 | -0.059509 | 0.032043 | 0.030518 | -0.071564 | -0.23392 | -0.03418 | -0.16449 | -0.13138 | 0.018311 | 0.022888 | -0.064087 | -0.16937 | -0.16022 | -0.10986 | -0.045776 | -0.027466 | 0.027466 | -0.064087
474.5625 | 0.030518 | 0.47424 | -0.46036 | -0.1976 | -0.14847 | -0.26276 | -0.15274 | 0.041199 | -0.022888 | 0.027466 | 0.022888 | -0.013733 | -0.15106 | -0.059509 | 0.045776 | -0.070496 | -0.24033 | -0.042725 | -0.15701 | -0.12283 | 0 | 0.050354 | -0.073242 | -0.045776 | -0.041199 | -0.16937 | -0.10529 | 0.054932 | 0.004578 | -0.09613
476.2344 | 0.061035 | 0.49027 | -0.43579 | -0.19546 | -0.15595 | -0.25207 | -0.15701 | 0.009155 | -0.050354 | 0.068665 | -0.036621 | -0.16479 | -0.073242 | 0.036621 | 0.045776 | -0.071564 | -0.23605 | -0.044861 | -0.16342 | -0.13245 | 0.054932 | 0.059509 | -0.036621 | -0.18768 | -0.16937 | -0.1236 | -0.064087 | -0.045776 | 0.027466 | -0.054932
477.9219 | 0.030518 | 0.47211 | -0.45288 | -0.18265 | -0.15488 | -0.24246 | -0.15274 | 0.073242 | -0.027466 | 0.064087 | 0.045776 | -0.018311 | -0.14648 | -0.073242 | 0.030518 | -0.061951 | -0.2446 | -0.040588 | -0.14954 | -0.13565 | 0 | 0.045776 | -0.059509 | -0.10071 | -0.073242 | -0.15106 | -0.091553 | 0.045776 | -0.009155 | -0.086975
479.6094 | 0.045776 | 0.49454 | -0.44754 | -0.18585 | -0.15808 | -0.26489 | -0.15701 | 0.013733 | -0.045776 | 0.086975 | -0.004578 | -0.19226 | -0.064087 | 0.013733 | 0.045776 | -0.077972 | -0.24567 | -0.048065 | -0.16556 | -0.1207 | 0.050354 | 0.064087 | -0.045776 | -0.19684 | -0.16022 | -0.10986 | -0.064087 | -0.045776 | 0.036621 | -0.07782
481.3438 | 0.045776 | 0.47211 | -0.45929 | -0.19119 | -0.14206 | -0.25955 | -0.15381 | 0.059509 | -0.064087 | 0.036621 | 0.027466 | -0.022888 | -0.15106 | -0.041199 | 0.061035 | -0.0737 | -0.22751 | -0.05661 | -0.15808 | -0.11963 | -0.018311 | 0.045776 | -0.059509 | -0.064087 | -0.022888 | -0.16937 | -0.11444 | 0.059509 | 0.009155 | -0.073242
483 | 0.061035 | 0.48172 | -0.45609 | -0.18906 | -0.1506 | -0.27771 | -0.16769 | 0.041199 | 0 | 0.082397 | 0.009155 | -0.12817 | -0.11444 | -0.022888 | 0.061035 | -0.089722 | -0.23712 | -0.044861 | -0.17197 | -0.1207 | 0.10071 | 0.16479 | 0.032043 | -0.13275 | -0.11444 | -0.17395 | -0.091553 | 0.054932 | 0.009155 | -0.07782
484.7344 | 0.045776 | 0.47531 | -0.44968 | -0.18372 | -0.13672 | -0.26276 | -0.15488 | 0.091553 | 0 | 0.064087 | 0.068665 | -0.009155 | -0.17395 | -0.054932 | 0.061035 | -0.059814 | -0.23178 | -0.042725 | -0.16235 | -0.13458 | 0.004578 | 0.045776 | -0.059509 | -0.086975 | -0.064087 | -0.16479 | -0.086975 | 0.041199 | -0.004578 | -0.091553
486.4062 | 0.045776 | 0.4689 | -0.46463 | -0.20721 | -0.14099 | -0.2681 | -0.16556 | 0.12817 | 0.07782 | 0.14648 | 0.086975 | -0.091553 | -0.13733 | -0.036621 | 0.061035 | -0.077972 | -0.23926 | -0.048065 | -0.17303 | -0.12924 | 0.14191 | 0.21973 | 0.064087 | -0.13275 | -0.09613 | -0.1831 | -0.1236 | 0.050354 | 0.022888 | -0.07782
488.0625 | 0.045776 | 0.46036 | -0.44861 | -0.19867 | -0.14633 | -0.24567 | -0.16449 | -0.018311 | -0.14648 | 0.013733 | -0.036621 | -0.091553 | -0.09613 | 0.009155 | 0.061035 | -0.067291 | -0.23285 | -0.040588 | -0.16022 | -0.13138 | -0.091553 | -0.073242 | -0.16022 | -0.09613 | -0.10986 | -0.10071 | -0.032043 | -0.10071 | 0.022888 | -0.032043
489.7344 | 0.045776 | 0.47958 | -0.46677 | -0.19226 | -0.15808 | -0.2681 | -0.15274 | 0.12817 | 0.07782 | 0.14648 | 0.07782 | -0.10529 | -0.15106 | -0.054932 | 0.061035 | -0.0737 | -0.23285 | -0.043793 | -0.17197 | -0.13351 | 0.11902 | 0.21057 | 0.045776 | -0.11444 | -0.10071 | -0.18768 | -0.10529 | 0.027466 | 0.018311 | -0.07782
491.4688 | 0.045776 | 0.49347 | -0.46677 | -0.18906 | -0.14633 | -0.2681 | -0.16663 | 0.009155 | -0.054932 | 0.059509 | -0.004578 | -0.14191 | -0.09613 | 0.013733 | 0.045776 | -0.09079 | -0.24887 | -0.03952 | -0.1741 | -0.12604 | 0.064087 | 0.11902 | -0.027466 | -0.14191 | -0.10071 | -0.13733 | -0.068665 | -0.009155 | 0.032043 | -0.068665
493.2031 | 0.091553 | 0.47852 | -0.45075 | -0.18692 | -0.16022 | -0.26382 | -0.15488 | 0.054932 | -0.032043 | 0.064087 | 0.027466 | -0.022888 | -0.15564 | -0.041199 | 0.030518 | -0.069427 | -0.24246 | -0.03952 | -0.16342 | -0.12604 | 0.018311 | 0.068665 | -0.045776 | -0.036621 | 0 | -0.17853 | -0.1236 | 0.018311 | 0.013733 | -0.068665
494.875 | 0.061035 | 0.47424 | -0.4422 | -0.19012 | -0.15488 | -0.24139 | -0.15381 | 0.073242 | -0.032043 | 0.082397 | 0.013733 | -0.086975 | -0.10071 | 0.004578 | 0.030518 | -0.063019 | -0.23926 | -0.03418 | -0.14526 | -0.12711 | 0.013733 | 0.022888 | -0.086975 | -0.09613 | -0.073242 | -0.1236 | -0.073242 | -0.073242 | 0.045776 | -0.036621
496.5469 | 0.030518 | 0.47531 | -0.45715 | -0.18585 | -0.15488 | -0.24033 | -0.14954 | 0.018311 | -0.082397 | 0.041199 | -0.018311 | -0.073242 | -0.091553 | 0.004578 | 0.045776 | -0.058746 | -0.24353 | -0.040588 | -0.15488 | -0.13138 | -0.059509 | -0.050354 | -0.15106 | -0.10071 | -0.082397 | -0.11444 | -0.050354 | -0.082397 | 0.032043 | -0.027466
498.2656 | 0.045776 | 0.50308 | -0.4657 | -0.17838 | -0.1474 | -0.27985 | -0.15808 | 0.013733 | -0.036621 | 0.073242 | -0.045776 | -0.20599 | -0.064087 | 0.027466 | 0.030518 | -0.083313 | -0.2446 | -0.048065 | -0.16663 | -0.11002 | 0.086975 | 0.10529 | -0.032043 | -0.14648 | -0.11902 | -0.13733 | -0.064087 | -0.086975 | 0.064087 | -0.068665
499.9375 | 0.061035 | 0.48706 | -0.44754 | -0.20508 | -0.15915 | -0.27344 | -0.15274 | 0.1236 | 0.064087 | 0.14648 | 0.082397 | -0.086975 | -0.14648 | -0.064087 | 0.030518 | -0.0737 | -0.24353 | -0.050201 | -0.16769 | -0.13672 | 0.086975 | 0.19226 | 0.036621 | -0.10071 | -0.091553 | -0.16479 | -0.10071 | 0.018311 | 0.009155 | -0.07782
501.6719 | 0.045776 | 0.49454 | -0.44968 | -0.18906 | -0.14633 | -0.27023 | -0.16235 | 0.036621 | -0.054932 | 0.064087 | -0.018311 | -0.13733 | -0.091553 | 0.009155 | 0.061035 | -0.074768 | -0.25421 | -0.03952 | -0.1709 | -0.12604 | 0.050354 | 0.082397 | -0.050354 | -0.13733 | -0.11902 | -0.11444 | -0.068665 | -0.064087 | 0.064087 | -0.064087
503.3281 | 0.045776 | 0.46356 | -0.44754 | -0.1976 | -0.15701 | -0.24246 | -0.15167 | 0.10529 | 0 | 0.09613 | 0.041199 | -0.054932 | -0.1236 | -0.018311 | 0.030518 | -0.068359 | -0.22858 | -0.02243 | -0.16022 | -0.14206 | 0.022888 | 0.050354 | -0.041199 | -0.086975 | -0.086975 | -0.14648 | -0.086975 | 0.013733 | 0.013733 | -0.064087
505.0156 | 0.030518 | 0.47531 | -0.45395 | -0.20721 | -0.15701 | -0.27023 | -0.15915 | 0.13733 | 0.091553 | 0.16022 | 0.086975 | -0.10071 | -0.13733 | -0.059509 | 0.061035 | -0.086517 | -0.24246 | -0.042725 | -0.16556 | -0.13245 | 0.13733 | 0.21973 | 0.07782 | -0.11444 | -0.09613 | -0.19226 | -0.1236 | 0.050354 | 0 | -0.086975
506.7656 | 0.045776 | 0.47318 | -0.45288 | -0.18906 | -0.14847 | -0.26703 | -0.16235 | 0.022888 | -0.041199 | 0.050354 | -0.013733 | -0.12817 | -0.082397 | 0.009155 | 0.045776 | -0.086517 | -0.24994 | -0.045929 | -0.1709 | -0.11536 | 0.054932 | 0.10529 | -0.027466 | -0.12817 | -0.1236 | -0.13733 | -0.073242 | -0.004578 | 0.064087 | -0.064087
508.5 | 0.045776 | 0.46677 | -0.4454 | -0.18585 | -0.1474 | -0.23285 | -0.15808 | 0.07782 | 0 | 0.064087 | 0.027466 | -0.068665 | -0.10529 | -0.013733 | 0.045776 | -0.059814 | -0.24353 | -0.045929 | -0.14099 | -0.13245 | 0.009155 | 0.009155 | -0.082397 | -0.10071 | -0.068665 | -0.15106 | -0.07782 | -0.082397 | 0.022888 | -0.036621
510.1562 | 0.045776 | 0.48706 | -0.4422 | -0.18158 | -0.16342 | -0.25528 | -0.14526 | 0.050354 | -0.018311 | 0.091553 | 0.004578 | -0.17395 | -0.07782 | 0.036621 | 0.030518 | -0.079041 | -0.23926 | -0.042725 | -0.1506 | -0.13565 | 0.050354 | 0.068665 | -0.036621 | -0.19226 | -0.1831 | -0.10986 | -0.022888 | -0.045776 | 0.027466 | -0.059509
511.8281 | 0.030518 | 0.49454 | -0.45181 | -0.17731 | -0.15167 | -0.24567 | -0.1506 | -0.018311 | -0.091553 | 0.013733 | -0.050354 | -0.13733 | -0.073242 | 0.045776 | 0.045776 | -0.067291 | -0.24353 | -0.044861 | -0.14313 | -0.13458 | 0.018311 | 0.009155 | -0.064087 | -0.16022 | -0.15564 | -0.091553 | -0.036621 | -0.036621 | 0.022888 | -0.059509
513.5781 | 0.061035 | 0.47531 | -0.44647 | -0.19119 | -0.13992 | -0.24674 | -0.15381 | 0.068665 | -0.032043 | 0.07782 | 0.004578 | -0.064087 | -0.073242 | -0.022888 | 0.015259 | -0.061951 | -0.25207 | -0.03952 | -0.15595 | -0.12283 | -0.004578 | 0 | -0.07782 | -0.07782 | -0.086975 | -0.13733 | -0.068665 | -0.054932 | 0.045776 | -0.045776
515.25 | 0.045776 | 0.46249 | -0.46249 | -0.21149 | -0.14313 | -0.26489 | -0.16449 | 0.059509 | -0.013733 | 0.054932 | 0.041199 | -0.004578 | -0.16022 | -0.064087 | 0.045776 | -0.0737 | -0.22964 | -0.03952 | -0.17517 | -0.12604 | -0.013733 | 0.045776 | -0.059509 | -0.027466 | -0.022888 | -0.14648 | -0.091553 | 0.041199 | 0.009155 | -0.073242
516.9219 | 0.061035 | 0.49133 | -0.45715 | -0.20615 | -0.15701 | -0.27664 | -0.15808 | -0.004578 | -0.045776 | 0.059509 | -0.032043 | -0.13733 | -0.10529 | 0.009155 | 0.045776 | -0.088654 | -0.23498 | -0.03952 | -0.16983 | -0.12176 | 0.041199 | 0.086975 | -0.041199 | -0.13733 | -0.12817 | -0.13275 | -0.064087 | -0.050354 | 0.045776 | -0.050354
518.6562 | 0.061035 | 0.47424 | -0.45181 | -0.18158 | -0.14313 | -0.24674 | -0.15595 | 0.059509 | -0.022888 | 0.068665 | 0.032043 | -0.045776 | -0.1236 | -0.018311 | 0.030518 | -0.05661 | -0.2478 | -0.043793 | -0.15381 | -0.13672 | 0.013733 | 0.059509 | -0.045776 | -0.091553 | -0.082397 | -0.16479 | -0.082397 | 0.032043 | -0.004578 | -0.068665
520.3906 | 0.045776 | 0.48492 | -0.45181 | -0.19119 | -0.14954 | -0.27237 | -0.16876 | 0.045776 | -0.013733 | 0.10986 | -0.027466 | -0.17395 | -0.068665 | 0.032043 | 0.061035 | -0.074768 | -0.24567 | -0.03952 | -0.16022 | -0.12817 | 0.073242 | 0.09613 | -0.036621 | -0.18768 | -0.15564 | -0.10529 | -0.041199 | -0.086975 | 0.054932 | -0.045776
522.0625 | 0.045776 | 0.49133 | -0.45715 | -0.18585 | -0.15808 | -0.25421 | -0.16663 | -0.004578 | -0.11444 | 0.041199 | -0.050354 | -0.14648 | -0.041199 | 0.032043 | 0.045776 | -0.064087 | -0.24887 | -0.040588 | -0.15167 | -0.13245 | 0.018311 | 0.013733 | -0.064087 | -0.16937 | -0.16022 | -0.10986 | -0.041199 | -0.022888 | 0.018311 | -0.032043
523.7344 | 0.015259 | 0.46356 | -0.44113 | -0.19653 | -0.14206 | -0.24246 | -0.1474 | 0.091553 | -0.022888 | 0.068665 | 0.032043 | -0.041199 | -0.1236 | -0.022888 | 0.030518 | -0.060883 | -0.23605 | -0.045929 | -0.15595 | -0.13458 | 0.004578 | 0.027466 | -0.050354 | -0.09613 | -0.064087 | -0.13733 | -0.082397 | 0.050354 | -0.027466 | -0.07782
525.4688 | 0.015259 | 0.46036 | -0.44968 | -0.19333 | -0.15274 | -0.24994 | -0.16663 | 0.064087 | -0.027466 | 0.07782 | 0.050354 | -0.050354 | -0.11902 | -0.022888 | 0.045776 | -0.065155 | -0.23819 | -0.046997 | -0.16663 | -0.1239 | 0.009155 | 0.054932 | -0.041199 | -0.086975 | -0.073242 | -0.13275 | -0.09613 | 0.054932 | -0.009155 | -0.073242
527.1875 | 0.030518 | 0.48706 | -0.44968 | -0.17731 | -0.15915 | -0.26276 | -0.16129 | -0.022888 | -0.12817 | 0.009155 | -0.059509 | -0.10529 | -0.068665 | 0.027466 | 0.045776 | -0.072632 | -0.25314 | -0.043793 | -0.15488 | -0.11856 | -0.004578 | -0.018311 | -0.07782 | -0.16479 | -0.11444 | -0.10071 | -0.045776 | -0.045776 | 0.027466 | -0.045776
528.8594 | 0.030518 | 0.4892 | -0.45181 | -0.20187 | -0.15595 | -0.27771 | -0.16769 | 0.032043 | -0.032043 | 0.068665 | 0 | -0.13275 | -0.11444 | 0.004578 | 0.030518 | -0.079041 | -0.23819 | -0.057678 | -0.17303 | -0.13245 | 0.068665 | 0.13733 | 0 | -0.13275 | -0.11902 | -0.14648 | -0.09613 | 0.050354 | 0.027466 | -0.07782
530.5938 | 0.030518 | 0.48599 | -0.45929 | -0.18799 | -0.16449 | -0.26703 | -0.16449 | 0.018311 | -0.054932 | 0.073242 | -0.032043 | -0.17853 | -0.064087 | 0.036621 | 0.076294 | -0.088654 | -0.24674 | -0.043793 | -0.16876 | -0.13458 | 0.054932 | 0.091553 | -0.036621 | -0.14191 | -0.13275 | -0.1236 | -0.064087 | -0.07782 | 0.07782 | -0.041199
532.3281 | 0.045776 | 0.48279 | -0.44754 | -0.17838 | -0.15381 | -0.2446 | -0.1741 | 0.068665 | -0.036621 | 0.073242 | 0.018311 | -0.064087 | -0.10529 | -0.013733 | 0.045776 | -0.071564 | -0.25101 | -0.03952 | -0.14313 | -0.12283 | -0.013733 | 0.004578 | -0.086975 | -0.09613 | -0.091553 | -0.1236 | -0.054932 | -0.064087 | 0.036621 | -0.041199
534 | 0.045776 | 0.47318 | -0.45181 | -0.18799 | -0.16663 | -0.24567 | -0.16129 | 0.07782 | -0.032043 | 0.086975 | 0.013733 | -0.059509 | -0.10529 | -0.009155 | 0.045776 | -0.071564 | -0.24567 | -0.041656 | -0.15274 | -0.12497 | -0.013733 | 0 | -0.073242 | -0.091553 | -0.07782 | -0.14648 | -0.064087 | -0.068665 | 0.036621 | -0.054932
535.7344 | 0.061035 | 0.48279 | -0.45288 | -0.20508 | -0.15701 | -0.27985 | -0.16769 | 0.013733 | -0.050354 | 0.07782 | -0.022888 | -0.14648 | -0.082397 | -0.009155 | 0.045776 | -0.086517 | -0.23819 | -0.045929 | -0.17731 | -0.12817 | 0.050354 | 0.082397 | -0.036621 | -0.15106 | -0.1236 | -0.11902 | -0.073242 | -0.045776 | 0.050354 | -0.045776
537.4688 | 0.045776 | 0.48386 | -0.46677 | -0.19226 | -0.14526 | -0.24994 | -0.16663 | -0.045776 | -0.16479 | -0.018311 | -0.082397 | -0.086975 | -0.059509 | 0.032043 | 0.061035 | -0.070496 | -0.24139 | -0.033112 | -0.15381 | -0.13886 | -0.054932 | -0.09613 | -0.14191 | -0.09613 | -0.086975 | -0.11444 | -0.036621 | -0.073242 | 0.027466 | -0.036621
539.1875 | 0.030518 | 0.4657 | -0.45288 | -0.19119 | -0.1506 | -0.24033 | -0.15488 | 0.009155 | -0.12817 | 0.009155 | -0.027466 | -0.054932 | -0.086975 | 0.004578 | 0.045776 | -0.066223 | -0.24033 | -0.035248 | -0.1474 | -0.12497 | -0.091553 | -0.059509 | -0.15106 | -0.10529 | -0.086975 | -0.10986 | -0.032043 | -0.091553 | 0.041199 | -0.027466
540.8594 | 0.030518 | 0.47958 | -0.45075 | -0.21469 | -0.16235 | -0.28412 | -0.16129 | 0.050354 | -0.004578 | 0.073242 | 0.022888 | -0.11444 | -0.11444 | -0.013733 | 0.030518 | -0.093994 | -0.24246 | -0.042725 | -0.17197 | -0.12283 | 0.10986 | 0.16937 | 0.022888 | -0.1236 | -0.11902 | -0.15106 | -0.086975 | 0.059509 | 0.018311 | -0.09613
542.6094 | 0.061035 | 0.4689 | -0.44434 | -0.20615 | -0.15595 | -0.26062 | -0.16983 | 0.11902 | 0.064087 | 0.14648 | 0.07782 | -0.068665 | -0.13733 | -0.036621 | 0.045776 | -0.086517 | -0.24033 | -0.048065 | -0.15488 | -0.12711 | 0.10071 | 0.19684 | 0.036621 | -0.11444 | -0.064087 | -0.17853 | -0.1236 | 0.009155 | 0.009155 | -0.073242
544.3438 | 0.061035 | 0.47104 | -0.44113 | -0.18585 | -0.13886 | -0.23819 | -0.16022 | 0.091553 | -0.032043 | 0.082397 | 0.013733 | -0.054932 | -0.10071 | -0.013733 | 0.015259 | -0.05661 | -0.24353 | -0.042725 | -0.16235 | -0.13779 | 0.004578 | 0 | -0.073242 | -0.082397 | -0.07782 | -0.13733 | -0.045776 | -0.054932 | 0.018311 | -0.045776
546.0156 | 0.015259 | 0.47104 | -0.44434 | -0.20187 | -0.15274 | -0.26062 | -0.16449 | 0.073242 | -0.022888 | 0.054932 | 0.036621 | 0.013733 | -0.13275 | -0.064087 | 0.045776 | -0.066223 | -0.23819 | -0.038452 | -0.16129 | -0.1239 | -0.004578 | 0.045776 | -0.059509 | -0.032043 | -0.004578 | -0.16479 | -0.10529 | 0.041199 | 0 | -0.068665
547.7031 | 0.061035 | 0.47745 | -0.45609 | -0.18265 | -0.15595 | -0.2681 | -0.16022 | 0.027466 | -0.050354 | 0.082397 | -0.018311 | -0.17853 | -0.059509 | 0.022888 | 0.030518 | -0.079041 | -0.2446 | -0.03952 | -0.16129 | -0.12711 | 0.059509 | 0.091553 | -0.027466 | -0.18768 | -0.17853 | -0.10986 | -0.036621 | -0.068665 | 0.064087 | -0.050354
549.4375 | 0.061035 | 0.47104 | -0.44434 | -0.20615 | -0.16129 | -0.25101 | -0.15701 | -0.018311 | -0.13733 | 0.013733 | -0.068665 | -0.091553 | -0.064087 | 0.050354 | 0.045776 | -0.071564 | -0.22858 | -0.041656 | -0.16235 | -0.12817 | -0.036621 | -0.050354 | -0.11444 | -0.12817 | -0.10071 | -0.10986 | -0.036621 | -0.036621 | 0.018311 | -0.064087
551.0938 | 0.030518 | 0.47211 | -0.44647 | -0.20187 | -0.15808 | -0.27985 | -0.1709 | 0.11444 | 0.073242 | 0.13275 | 0.054932 | -0.10071 | -0.13275 | -0.027466 | 0.045776 | -0.085449 | -0.23392 | -0.05127 | -0.16983 | -0.13565 | 0.15106 | 0.21973 | 0.082397 | -0.11902 | -0.091553 | -0.16937 | -0.091553 | 0.068665 | 0.022888 | -0.082397
552.7812 | 0.045776 | 0.47638 | -0.44754 | -0.19012 | -0.17197 | -0.2446 | -0.15381 | 0.054932 | -0.054932 | 0.068665 | -0.004578 | -0.064087 | -0.10071 | -0.004578 | 0.045776 | -0.060883 | -0.2446 | -0.040588 | -0.14099 | -0.12176 | -0.018311 | -0.009155 | -0.10529 | -0.10071 | -0.068665 | -0.11902 | -0.059509 | -0.07782 | 0.045776 | -0.032043
554.5312 | 0.045776 | 0.47424 | -0.45609 | -0.19546 | -0.17838 | -0.25848 | -0.15488 | 0.073242 | -0.032043 | 0.050354 | 0.045776 | 0.004578 | -0.14648 | -0.050354 | 0.030518 | -0.075836 | -0.25742 | -0.05127 | -0.16235 | -0.11963 | -0.022888 | 0.036621 | -0.073242 | -0.022888 | -0.027466 | -0.16479 | -0.09613 | 0.050354 | 0.004578 | -0.059509
556.2656 | 0.061035 | 0.4924 | -0.44754 | -0.1741 | -0.14954 | -0.25848 | -0.16129 | 0.041199 | -0.068665 | 0.086975 | -0.013733 | -0.15106 | -0.054932 | 0.036621 | 0.045776 | -0.077972 | -0.26062 | -0.035248 | -0.16342 | -0.13992 | 0.050354 | 0.064087 | -0.036621 | -0.17395 | -0.14191 | -0.10986 | -0.041199 | -0.041199 | 0.041199 | -0.045776
557.9531 | 0.045776 | 0.47104 | -0.45395 | -0.1944 | -0.1474 | -0.26916 | -0.16129 | 0.036621 | -0.036621 | 0.10986 | -0.027466 | -0.16937 | -0.07782 | 0.041199 | 0.045776 | -0.087585 | -0.24033 | -0.048065 | -0.15915 | -0.12924 | 0.064087 | 0.10071 | -0.027466 | -0.17395 | -0.16022 | -0.091553 | -0.027466 | -0.07782 | 0.050354 | -0.050354
559.6875 | 0.045776 | 0.47104 | -0.45075 | -0.19119 | -0.14954 | -0.25101 | -0.15915 | 0.013733 | -0.10529 | 0.027466 | -0.036621 | -0.073242 | -0.07782 | 0.013733 | 0.061035 | -0.061951 | -0.25207 | -0.043793 | -0.14954 | -0.13031 | -0.082397 | -0.064087 | -0.13275 | -0.10529 | -0.059509 | -0.10529 | -0.036621 | -0.10529 | 0.036621 | -0.050354
561.3594 | 0.030518 | 0.46783 | -0.46036 | -0.20081 | -0.16663 | -0.27664 | -0.16022 | 0.13275 | 0.07782 | 0.15106 | 0.07782 | -0.09613 | -0.15106 | -0.054932 | 0.045776 | -0.089722 | -0.2446 | -0.046997 | -0.16449 | -0.12497 | 0.091553 | 0.20599 | 0.045776 | -0.10071 | -0.086975 | -0.16937 | -0.11444 | 0.022888 | 0.018311 | -0.086975
563.0469 | 0.061035 | 0.46249 | -0.44434 | -0.20294 | -0.14313 | -0.26276 | -0.16129 | 0.064087 | -0.041199 | 0.050354 | 0.041199 | 0.004578 | -0.12817 | -0.036621 | 0.045776 | -0.069427 | -0.24887 | -0.041656 | -0.1506 | -0.13351 | 0 | 0.041199 | -0.036621 | -0.027466 | 0 | -0.17395 | -0.1236 | 0.073242 | -0.013733 | -0.07782
564.7188 | 0.045776 | 0.47318 | -0.44327 | -0.17838 | -0.15488 | -0.2478 | -0.15701 | 0.027466 | -0.091553 | 0.059509 | -0.013733 | -0.064087 | -0.10529 | 0.018311 | 0.045776 | -0.069427 | -0.24139 | -0.043793 | -0.15915 | -0.12817 | -0.045776 | -0.050354 | -0.13275 | -0.11444 | -0.068665 | -0.10986 | -0.045776 | -0.086975 | 0.032043 | -0.027466
566.4531 | 0.015259 | 0.49027 | -0.44754 | -0.20721 | -0.16342 | -0.28198 | -0.16449 | 0.032043 | -0.050354 | 0.086975 | -0.022888 | -0.1236 | -0.091553 | 0.004578 | 0.030518 | -0.081177 | -0.25207 | -0.040588 | -0.17517 | -0.12604 | 0.041199 | 0.086975 | -0.032043 | -0.15106 | -0.11902 | -0.11902 | -0.045776 | -0.07782 | 0.064087 | -0.041199
568.1875 | 0.045776 | 0.46677 | -0.45181 | -0.20401 | -0.15274 | -0.2713 | -0.16556 | 0.11902 | 0.036621 | 0.11902 | 0.07782 | -0.050354 | -0.16022 | -0.041199 | 0.045776 | -0.0737 | -0.23819 | -0.041656 | -0.17197 | -0.13351 | 0.045776 | 0.11902 | 0 | -0.041199 | -0.032043 | -0.17853 | -0.10071 | 0.009155 | 0.022888 | -0.064087
569.8594 | 0.045776 | 0.47745 | -0.45181 | -0.1944 | -0.16235 | -0.26062 | -0.1741 | 0.07782 | -0.004578 | 0.086975 | 0.036621 | -0.009155 | -0.16479 | -0.059509 | 0.030518 | -0.075836 | -0.2446 | -0.042725 | -0.16449 | -0.13351 | 0.013733 | 0.082397 | -0.041199 | -0.036621 | -0.027466 | -0.16022 | -0.091553 | 0.009155 | 0.027466 | -0.07782
571.5938 | 0.030518 | 0.48065 | -0.45715 | -0.19012 | -0.15701 | -0.27344 | -0.16449 | 0.036621 | -0.050354 | 0.068665 | -0.022888 | -0.12817 | -0.064087 | 0.004578 | 0.030518 | -0.074768 | -0.25848 | -0.049133 | -0.16449 | -0.11963 | 0.059509 | 0.09613 | -0.022888 | -0.13275 | -0.10529 | -0.1236 | -0.054932 | -0.064087 | 0.050354 | -0.036621
573.3281 | 0.030518 | 0.46677 | -0.45609 | -0.20401 | -0.15274 | -0.25207 | -0.1709 | 0.13733 | 0.073242 | 0.15106 | 0.068665 | -0.068665 | -0.13733 | -0.022888 | 0.045776 | -0.085449 | -0.23819 | -0.053406 | -0.16876 | -0.1506 | 0.13275 | 0.21057 | 0.073242 | -0.11902 | -0.086975 | -0.17395 | -0.10071 | 0.054932 | 0.018311 | -0.073242
575 | 0.045776 | 0.47958 | -0.4657 | -0.19119 | -0.16129 | -0.26703 | -0.16556 | 0.041199 | -0.07782 | 0.064087 | -0.004578 | -0.1236 | -0.082397 | 0.009155 | 0.045776 | -0.077972 | -0.25635 | -0.043793 | -0.16235 | -0.13779 | 0.045776 | 0.082397 | -0.050354 | -0.14191 | -0.10986 | -0.13733 | -0.036621 | -0.064087 | 0.054932 | -0.059509
576.7344 | 0.030518 | 0.4657 | -0.44113 | -0.1741 | -0.15701 | -0.24139 | -0.15808 | 0.004578 | -0.15106 | 0.009155 | -0.050354 | -0.073242 | -0.07782 | 0.027466 | 0.030518 | -0.055542 | -0.25101 | -0.038452 | -0.1506 | -0.13565 | -0.086975 | -0.086975 | -0.16479 | -0.082397 | -0.091553 | -0.082397 | -0.022888 | -0.09613 | 0.045776 | -0.027466
578.4062 | 0.030518 | 0.46463 | -0.45075 | -0.1976 | -0.15915 | -0.25635 | -0.16449 | 0.041199 | -0.059509 | 0.09613 | -0.009155 | -0.19226 | -0.059509 | 0.045776 | 0.045776 | -0.088654 | -0.25207 | -0.03952 | -0.15488 | -0.13779 | 0.059509 | 0.086975 | -0.027466 | -0.19226 | -0.15106 | -0.086975 | -0.027466 | -0.07782 | 0.036621 | -0.050354
580.1406 | 0.045776 | 0.4689 | -0.46249 | -0.18692 | -0.1442 | -0.2446 | -0.15701 | -0.027466 | -0.15106 | -0.027466 | -0.064087 | -0.09613 | -0.068665 | 0.041199 | 0.045776 | -0.065155 | -0.24887 | -0.041656 | -0.15808 | -0.12817 | -0.050354 | -0.064087 | -0.12817 | -0.07782 | -0.068665 | -0.091553 | -0.013733 | -0.036621 | 0.036621 | -0.041199
581.7969 | 0.015259 | 0.47531 | -0.46036 | -0.20508 | -0.16663 | -0.27344 | -0.15915 | 0.09613 | 0.027466 | 0.10986 | 0.059509 | -0.09613 | -0.11444 | -0.009155 | 0.030518 | -0.085449 | -0.24994 | -0.045929 | -0.1741 | -0.1207 | 0.15106 | 0.19226 | 0.064087 | -0.13733 | -0.10071 | -0.16937 | -0.086975 | 0.068665 | 0.009155 | -0.068665
583.5312 | 0.030518 | 0.48279 | -0.4454 | -0.20508 | -0.14633 | -0.25207 | -0.16556 | 0.11902 | 0.041199 | 0.14648 | 0.073242 | -0.07782 | -0.13733 | -0.059509 | 0.030518 | -0.074768 | -0.24994 | -0.035248 | -0.16983 | -0.12924 | 0.073242 | 0.15564 | 0.022888 | -0.07782 | -0.059509 | -0.16479 | -0.07782 | 0.013733 | 0.013733 | -0.068665
585.2031 | 0.045776 | 0.47104 | -0.45181 | -0.18906 | -0.16663 | -0.23819 | -0.15915 | 0.036621 | -0.10986 | 0.013733 | -0.027466 | -0.064087 | -0.07782 | 0.009155 | 0.045776 | -0.064087 | -0.24033 | -0.045929 | -0.14954 | -0.12711 | -0.091553 | -0.054932 | -0.15106 | -0.10986 | -0.068665 | -0.10529 | -0.022888 | -0.09613 | 0.027466 | -0.018311
586.9062 | 0.061035 | 0.48279 | -0.46356 | -0.1944 | -0.15381 | -0.27344 | -0.16449 | 0.13733 | 0.086975 | 0.15564 | 0.07782 | -0.082397 | -0.12817 | -0.027466 | 0.030518 | -0.081177 | -0.2478 | -0.046997 | -0.15701 | -0.12604 | 0.14191 | 0.21515 | 0.064087 | -0.091553 | -0.086975 | -0.16937 | -0.10986 | 0.068665 | 0.004578 | -0.07782
588.6094 | 0.030518 | 0.48386 | -0.46463 | -0.18051 | -0.16449 | -0.25635 | -0.16129 | -0.022888 | -0.17395 | -0.022888 | -0.068665 | -0.086975 | -0.045776 | 0.041199 | 0.061035 | -0.063019 | -0.23498 | -0.048065 | -0.15701 | -0.12497 | -0.059509 | -0.073242 | -0.13733 | -0.10986 | -0.09613 | -0.082397 | -0.027466 | -0.041199 | 0.045776 | -0.027466
590.3281 | 0.030518 | 0.46997 | -0.46249 | -0.19653 | -0.16342 | -0.27985 | -0.16129 | 0.12817 | 0.064087 | 0.14191 | 0.059509 | -0.086975 | -0.1236 | -0.036621 | 0.015259 | -0.088654 | -0.25421 | -0.049133 | -0.16983 | -0.13245 | 0.13733 | 0.21057 | 0.059509 | -0.11444 | -0.09613 | -0.16022 | -0.11444 | 0.064087 | 0.013733 | -0.064087
591.9844 | 0.015259 | 0.46249 | -0.45181 | -0.19119 | -0.14633 | -0.27451 | -0.15808 | 0.12817 | 0.059509 | 0.14648 | 0.086975 | -0.07782 | -0.15106 | -0.032043 | 0.045776 | -0.083313 | -0.24674 | -0.048065 | -0.16235 | -0.13351 | 0.086975 | 0.1831 | 0.036621 | -0.086975 | -0.059509 | -0.16022 | -0.10071 | 0.018311 | 0.032043 | -0.064087
593.7344 | 0.045776 | 0.48065 | -0.44968 | -0.19012 | -0.15915 | -0.2478 | -0.15595 | -0.022888 | -0.16479 | -0.032043 | -0.050354 | -0.07782 | -0.054932 | 0.041199 | 0.030518 | -0.064087 | -0.2478 | -0.042725 | -0.15167 | -0.12497 | -0.07782 | -0.086975 | -0.14191 | -0.091553 | -0.10071 | -0.10986 | -0.027466 | -0.073242 | 0.036621 | -0.041199
595.4688 | 0.030518 | 0.46997 | -0.45609 | -0.19867 | -0.15167 | -0.27023 | -0.16022 | 0.054932 | -0.027466 | 0.10986 | -0.009155 | -0.16479 | -0.050354 | 0.032043 | 0.045776 | -0.081177 | -0.2478 | -0.052338 | -0.15488 | -0.12604 | 0.059509 | 0.068665 | -0.036621 | -0.17395 | -0.16937 | -0.086975 | -0.027466 | -0.09613 | 0.054932 | -0.059509
597.1406 | 0.030518 | 0.45929 | -0.44434 | -0.20828 | -0.14954 | -0.24567 | -0.15488 | 0.091553 | -0.022888 | 0.082397 | 0.07782 | 0.009155 | -0.16479 | -0.054932 | 0.030518 | -0.070496 | -0.24674 | -0.048065 | -0.15701 | -0.12711 | -0.018311 | 0.050354 | -0.045776 | -0.064087 | -0.068665 | -0.13733 | -0.073242 | 0.050354 | 0.009155 | -0.073242
598.8125 | 0.045776 | 0.47211 | -0.45395 | -0.18906 | -0.15274 | -0.25314 | -0.14954 | 0.086975 | -0.013733 | 0.091553 | 0.041199 | -0.041199 | -0.11444 | -0.018311 | 0.030518 | -0.072632 | -0.2446 | -0.042725 | -0.1474 | -0.12924 | 0.004578 | 0.041199 | -0.050354 | -0.082397 | -0.086975 | -0.12817 | -0.064087 | -0.018311 | 0.013733 | -0.041199
600.5625 | 0.061035 | 0.46997 | -0.45502 | -0.19974 | -0.1474 | -0.25421 | -0.15701 | 0.073242 | -0.041199 | 0.059509 | 0.045776 | -0.009155 | -0.12817 | -0.027466 | 0.045776 | -0.067291 | -0.2478 | -0.046997 | -0.15808 | -0.12711 | -0.018311 | 0.054932 | -0.041199 | -0.07782 | -0.050354 | -0.14648 | -0.073242 | 0.054932 | -0.022888 | -0.068665
602.2344 | 0.076294 | 0.47104 | -0.45609 | -0.18158 | -0.16449 | -0.27023 | -0.15595 | -0.032043 | -0.16937 | -0.018311 | -0.082397 | -0.086975 | -0.059509 | 0.054932 | 0.061035 | -0.068359 | -0.24567 | -0.044861 | -0.15488 | -0.1207 | -0.073242 | -0.073242 | -0.13275 | -0.11444 | -0.086975 | -0.09613 | -0.018311 | -0.050354 | 0.027466 | -0.050354
603.9688 | 0.045776 | 0.47531 | -0.4657 | -0.20187 | -0.16663 | -0.28198 | -0.16769 | 0.12817 | 0.059509 | 0.13733 | 0.064087 | -0.09613 | -0.12817 | -0.045776 | 0.015259 | -0.076904 | -0.24994 | -0.03952 | -0.17197 | -0.12497 | 0.13733 | 0.2243 | 0.086975 | -0.10071 | -0.091553 | -0.16937 | -0.10986 | 0.073242 | 0.009155 | -0.068665
605.7031 | 0.045776 | 0.4689 | -0.4422 | -0.19119 | -0.14633 | -0.25101 | -0.16663 | 0.054932 | -0.068665 | 0.050354 | 0.004578 | -0.054932 | -0.073242 | 0.004578 | 0.015259 | -0.071564 | -0.24033 | -0.040588 | -0.15381 | -0.1239 | -0.050354 | -0.027466 | -0.10986 | -0.086975 | -0.068665 | -0.10986 | -0.032043 | -0.07782 | 0.027466 | -0.022888
607.4375 | 0.045776 | 0.46783 | -0.45502 | -0.20401 | -0.16449 | -0.28198 | -0.16769 | 0.018311 | -0.045776 | 0.073242 | -0.004578 | -0.14191 | -0.10071 | 0.009155 | 0.030518 | -0.086517 | -0.24887 | -0.050201 | -0.16449 | -0.12283 | 0.032043 | 0.091553 | -0.036621 | -0.14191 | -0.10071 | -0.11902 | -0.045776 | -0.064087 | 0.050354 | -0.041199
609.1719 | 0.030518 | 0.4657 | -0.45502 | -0.20294 | -0.14526 | -0.24887 | -0.17197 | 0.073242 | -0.054932 | 0.032043 | 0.032043 | 0.018311 | -0.15106 | -0.022888 | 0.045776 | -0.065155 | -0.24033 | -0.036316 | -0.16342 | -0.12497 | -0.036621 | 0.027466 | -0.068665 | -0.032043 | -0.032043 | -0.15106 | -0.082397 | 0.064087 | 0.004578 | -0.059509
610.8438 | 0.061035 | 0.48386 | -0.46143 | -0.20615 | -0.15488 | -0.28412 | -0.16235 | 0.14191 | 0.09613 | 0.16479 | 0.09613 | -0.073242 | -0.13275 | -0.018311 | 0.015259 | -0.087585 | -0.24887 | -0.058746 | -0.16556 | -0.12924 | 0.10986 | 0.21515 | 0.073242 | -0.10529 | -0.073242 | -0.17395 | -0.09613 | 0.050354 | 0.022888 | -0.07782
612.5938 | 0.045776 | 0.46249 | -0.439 | -0.20508 | -0.15808 | -0.25635 | -0.16449 | 0.064087 | -0.045776 | 0.041199 | 0.009155 | 0.009155 | -0.11444 | -0.032043 | 0.045776 | -0.068359 | -0.24567 | -0.043793 | -0.15808 | -0.13779 | 0.004578 | 0.064087 | -0.050354 | -0.018311 | -0.018311 | -0.15564 | -0.07782 | 0.022888 | 0.018311 | -0.068665
614.3281 | 0.045776 | 0.47638 | -0.45395 | -0.19867 | -0.16022 | -0.24994 | -0.17517 | -0.027466 | -0.13733 | -0.013733 | -0.054932 | -0.086975 | -0.041199 | 0.036621 | 0.030518 | -0.0737 | -0.24674 | -0.044861 | -0.16556 | -0.11963 | -0.059509 | -0.059509 | -0.12817 | -0.10071 | -0.10071 | -0.091553 | -0.013733 | -0.050354 | 0.027466 | -0.018311
616.0469 | 0.061035 | 0.48813 | -0.46036 | -0.19119 | -0.16235 | -0.26276 | -0.1709 | 0.032043 | -0.041199 | 0.07782 | -0.013733 | -0.13733 | -0.086975 | 0.004578 | 0.045776 | -0.082245 | -0.26062 | -0.03952 | -0.16129 | -0.12924 | 0.041199 | 0.086975 | -0.027466 | -0.13275 | -0.11902 | -0.12817 | -0.050354 | -0.073242 | 0.073242 | -0.045776
617.7188 | 0.030518 | 0.47318 | -0.44861 | -0.1976 | -0.16129 | -0.2681 | -0.17624 | 0.1236 | 0.045776 | 0.12817 | 0.086975 | -0.054932 | -0.1236 | -0.036621 | 0.061035 | -0.086517 | -0.25421 | -0.050201 | -0.17197 | -0.13779 | 0.054932 | 0.14648 | 0.022888 | -0.059509 | -0.054932 | -0.17853 | -0.091553 | 0.022888 | 0.018311 | -0.07782
619.3906 | 0.030518 | 0.48706 | -0.45395 | -0.19226 | -0.14954 | -0.26062 | -0.15595 | 0.059509 | -0.036621 | 0.091553 | -0.027466 | -0.16937 | -0.068665 | 0.041199 | 0.030518 | -0.080109 | -0.25742 | -0.043793 | -0.16129 | -0.12817 | 0.032043 | 0.082397 | -0.027466 | -0.1831 | -0.1831 | -0.091553 | -0.032043 | -0.054932 | 0.059509 | -0.045776
621.0625 | 0.061035 | 0.47211 | -0.45822 | -0.21469 | -0.14633 | -0.27237 | -0.15808 | 0.07782 | -0.013733 | 0.091553 | 0.027466 | -0.10071 | -0.10071 | 0 | 0.045776 | -0.077972 | -0.2478 | -0.038452 | -0.16449 | -0.13351 | 0.11902 | 0.17853 | 0.041199 | -0.10529 | -0.11444 | -0.15106 | -0.082397 | 0.068665 | 0.022888 | -0.073242
622.7344 | 0.030518 | 0.45395 | -0.45395 | -0.20615 | -0.15915 | -0.2446 | -0.16769 | 0.086975 | -0.022888 | 0.064087 | 0.059509 | 0.009155 | -0.1236 | -0.027466 | 0.030518 | -0.0737 | -0.22751 | -0.044861 | -0.14954 | -0.13779 | -0.009155 | 0.027466 | -0.054932 | -0.064087 | -0.064087 | -0.1236 | -0.054932 | 0.054932 | -0.009155 | -0.045776
624.4688 | 0.030518 | 0.47638 | -0.45609 | -0.18158 | -0.15274 | -0.2713 | -0.16235 | 0.13733 | 0.07782 | 0.15564 | 0.086975 | -0.064087 | -0.13275 | -0.041199 | 0.045776 | -0.086517 | -0.25635 | -0.046997 | -0.15488 | -0.13245 | 0.082397 | 0.20142 | 0.027466 | -0.082397 | -0.054932 | -0.16479 | -0.091553 | 0.009155 | 0.032043 | -0.064087
626.1875 | 0.045776 | 0.46249 | -0.45502 | -0.20294 | -0.15595 | -0.27878 | -0.16342 | 0.10986 | 0.036621 | 0.10071 | 0.068665 | -0.004578 | -0.13733 | -0.064087 | 0.045776 | -0.072632 | -0.24033 | -0.048065 | -0.16129 | -0.12604 | 0.027466 | 0.09613 | -0.036621 | -0.036621 | -0.013733 | -0.15106 | -0.086975 | 0.013733 | 0.036621 | -0.064087
627.8594 | 0.061035 | 0.46249 | -0.45395 | -0.2179 | -0.14954 | -0.27023 | -0.16663 | 0.11902 | 0.086975 | 0.15106 | 0.073242 | -0.082397 | -0.1236 | -0.032043 | 0.030518 | -0.087585 | -0.22858 | -0.045929 | -0.16235 | -0.13458 | 0.10529 | 0.21515 | 0.068665 | -0.11444 | -0.082397 | -0.16479 | -0.10071 | 0.054932 | 0.013733 | -0.091553
629.6094 | 0.045776 | 0.48172 | -0.46463 | -0.19867 | -0.16342 | -0.27023 | -0.16983 | 0.14191 | 0.086975 | 0.16937 | 0.091553 | -0.068665 | -0.14648 | -0.041199 | 0.045776 | -0.084381 | -0.25421 | -0.05127 | -0.15915 | -0.14313 | 0.1236 | 0.21973 | 0.07782 | -0.10529 | -0.09613 | -0.15564 | -0.091553 | 0.073242 | 0.009155 | -0.07782
631.3438 | 0.030518 | 0.4657 | -0.44434 | -0.18478 | -0.15488 | -0.23392 | -0.15167 | 0.018311 | -0.091553 | 0.027466 | -0.032043 | -0.064087 | -0.086975 | 0.027466 | 0.030518 | -0.074768 | -0.25101 | -0.049133 | -0.14954 | -0.12604 | -0.082397 | -0.064087 | -0.13733 | -0.09613 | -0.086975 | -0.10071 | -0.022888 | -0.091553 | 0.032043 | -0.036621
633.0156 | 0.061035 | 0.46249 | -0.44327 | -0.20721 | -0.16342 | -0.24994 | -0.1474 | 0.068665 | -0.027466 | 0.07782 | 0.013733 | -0.054932 | -0.11444 | -0.004578 | 0.030518 | -0.065155 | -0.24887 | -0.038452 | -0.15488 | -0.12604 | -0.027466 | 0.022888 | -0.068665 | -0.091553 | -0.068665 | -0.13275 | -0.054932 | -0.068665 | 0.027466 | -0.036621
634.7656 | 0.030518 | 0.46677 | -0.44968 | -0.20615 | -0.15701 | -0.26703 | -0.16129 | 0.10071 | 0.041199 | 0.1236 | 0.07782 | -0.032043 | -0.13275 | -0.036621 | 0.045776 | -0.081177 | -0.24887 | -0.040588 | -0.16983 | -0.12817 | 0.054932 | 0.14191 | -0.009155 | -0.050354 | -0.018311 | -0.17395 | -0.10986 | 0.018311 | 0.022888 | -0.082397
636.4219 | 0.045776 | 0.45395 | -0.4422 | -0.20508 | -0.16022 | -0.2446 | -0.1506 | 0.073242 | -0.009155 | 0.082397 | 0.041199 | -0.027466 | -0.1236 | -0.009155 | 0.030518 | -0.064087 | -0.24353 | -0.042725 | -0.15595 | -0.13565 | 0.004578 | 0.064087 | -0.036621 | -0.045776 | -0.073242 | -0.1236 | -0.073242 | 0.041199 | 0.013733 | -0.068665
638.1562 | 0.045776 | 0.45822 | -0.45288 | -0.19226 | -0.1474 | -0.27344 | -0.15701 | 0.10529 | 0.068665 | 0.14191 | 0.09613 | -0.073242 | -0.14191 | -0.059509 | 0.015259 | -0.069427 | -0.2446 | -0.052338 | -0.16342 | -0.1207 | 0.07782 | 0.20142 | 0.036621 | -0.064087 | -0.059509 | -0.17395 | -0.10986 | 0.022888 | 0.022888 | -0.059509
639.8281 | 0.030518 | 0.45609 | -0.45288 | -0.1976 | -0.15488 | -0.25742 | -0.15915 | 0.032043 | -0.045776 | 0.068665 | 0 | -0.15564 | -0.064087 | 0.045776 | 0.061035 | -0.081177 | -0.24139 | -0.040588 | -0.16342 | -0.13672 | 0.022888 | 0.054932 | -0.045776 | -0.18768 | -0.17853 | -0.10071 | -0.013733 | -0.045776 | 0.027466 | -0.050354
641.5625 | 0.045776 | 0.47852 | -0.45181 | -0.18051 | -0.14847 | -0.25528 | -0.15701 | 0.018311 | -0.036621 | 0.068665 | 0 | -0.13733 | -0.050354 | 0.041199 | 0.061035 | -0.066223 | -0.25421 | -0.038452 | -0.14633 | -0.12711 | 0.013733 | 0.054932 | -0.036621 | -0.1831 | -0.16022 | -0.091553 | -0.032043 | -0.050354 | 0.041199 | -0.022888
643.2969 | 0.045776 | 0.44861 | -0.43686 | -0.20081 | -0.14954 | -0.25314 | -0.16129 | -0.036621 | -0.14648 | -0.022888 | -0.045776 | -0.07782 | -0.068665 | 0.036621 | 0.045776 | -0.058746 | -0.2446 | -0.037384 | -0.14526 | -0.13672 | -0.086975 | -0.082397 | -0.15564 | -0.091553 | -0.091553 | -0.07782 | -0.027466 | -0.068665 | 0.022888 | -0.022888
644.9531 | 0.045776 | 0.45929 | -0.45715 | -0.20828 | -0.16342 | -0.26916 | -0.16342 | 0.045776 | -0.009155 | 0.059509 | 0.027466 | 0.027466 | -0.14648 | -0.045776 | 0.076294 | -0.071564 | -0.24567 | -0.05661 | -0.16022 | -0.1239 | 0 | 0.073242 | -0.050354 | 0.004578 | 0.004578 | -0.16022 | -0.10529 | 0.032043 | 0.009155 | -0.068665
646.625 | 0.045776 | 0.46356 | -0.44434 | -0.2211 | -0.14206 | -0.27023 | -0.16342 | 0.050354 | -0.027466 | 0.068665 | 0.036621 | 0 | -0.13733 | -0.059509 | 0.030518 | -0.068359 | -0.24674 | -0.040588 | -0.16983 | -0.12924 | 0.013733 | 0.07782 | -0.041199 | -0.018311 | 0.013733 | -0.15106 | -0.082397 | 0.022888 | 0.022888 | -0.064087
648.3594 | 0.030518 | 0.46997 | -0.44968 | -0.20721 | -0.15701 | -0.27771 | -0.16129 | 0.004578 | -0.054932 | 0.050354 | -0.009155 | -0.11902 | -0.10986 | 0.013733 | 0.045776 | -0.085449 | -0.25207 | -0.043793 | -0.16342 | -0.13031 | 0.041199 | 0.09613 | -0.036621 | -0.10529 | -0.091553 | -0.1236 | -0.032043 | -0.059509 | 0.036621 | -0.045776
650.0312 | 0.030518 | 0.48279 | -0.44754 | -0.1944 | -0.14847 | -0.2478 | -0.16449 | -0.032043 | -0.16479 | -0.022888 | -0.050354 | -0.064087 | -0.064087 | 0.050354 | 0.030518 | -0.072632 | -0.24994 | -0.043793 | -0.16342 | -0.13458 | -0.068665 | -0.082397 | -0.16022 | -0.10071 | -0.086975 | -0.10071 | -0.009155 | -0.059509 | 0.032043 | -0.018311
651.7031 | 0.045776 | 0.46249 | -0.45502 | -0.19546 | -0.16235 | -0.25955 | -0.16983 | 0.073242 | -0.032043 | 0.050354 | 0.045776 | 0.018311 | -0.14191 | -0.041199 | 0.045776 | -0.070496 | -0.24246 | -0.041656 | -0.15701 | -0.1239 | -0.027466 | 0.054932 | -0.045776 | -0.013733 | -0.004578 | -0.15564 | -0.09613 | 0.036621 | 0.013733 | -0.059509
653.4531 | 0.045776 | 0.46677 | -0.46143 | -0.1944 | -0.1474 | -0.27344 | -0.15915 | 0.10986 | 0.054932 | 0.13733 | 0.10071 | -0.041199 | -0.1236 | -0.054932 | 0.030518 | -0.076904 | -0.25101 | -0.045929 | -0.16769 | -0.13138 | 0.041199 | 0.15564 | 0.018311 | -0.064087 | -0.041199 | -0.1831 | -0.10529 | 0 | 0.022888 | -0.036621
655.2188 | 0.045776 | 0.4657 | -0.46249 | -0.1944 | -0.15915 | -0.25955 | -0.15915 | 0.045776 | -0.036621 | 0.045776 | 0.013733 | 0.013733 | -0.14648 | -0.045776 | 0.045776 | -0.072632 | -0.25848 | -0.045929 | -0.16022 | -0.13138 | -0.004578 | 0.09613 | -0.036621 | -0.027466 | 0.004578 | -0.15564 | -0.086975 | 0.022888 | 0.022888 | -0.050354
656.8906 | 0.030518 | 0.45715 | -0.44968 | -0.21042 | -0.16129 | -0.26169 | -0.16235 | 0.064087 | -0.045776 | 0.045776 | 0.013733 | 0.009155 | -0.1236 | -0.032043 | 0.045776 | -0.077972 | -0.23926 | -0.045929 | -0.16769 | -0.12604 | 0 | 0.054932 | -0.045776 | -0.018311 | 0 | -0.15564 | -0.07782 | 0.022888 | 0.022888 | -0.068665
658.6406 | 0.076294 | 0.45502 | -0.44327 | -0.18372 | -0.16022 | -0.24887 | -0.15915 | 0.086975 | -0.032043 | 0.059509 | 0.045776 | -0.036621 | -0.1236 | 0.009155 | 0.045776 | -0.064087 | -0.24887 | -0.03952 | -0.1442 | -0.14206 | -0.018311 | 0.054932 | -0.050354 | -0.064087 | -0.064087 | -0.11902 | -0.068665 | 0.054932 | 0.009155 | -0.059509
660.375 | 0.045776 | 0.48279 | -0.45929 | -0.20615 | -0.15595 | -0.28198 | -0.16663 | 0.13275 | 0.068665 | 0.14191 | 0.082397 | -0.059509 | -0.15106 | -0.045776 | 0.015259 | -0.082245 | -0.24674 | -0.05661 | -0.16449 | -0.13138 | 0.091553 | 0.20599 | 0.036621 | -0.10986 | -0.073242 | -0.16022 | -0.086975 | 0.036621 | 0.018311 | -0.059509
662.0312 | 0.045776 | 0.47424 | -0.45502 | -0.18478 | -0.15595 | -0.24246 | -0.16129 | -0.027466 | -0.16479 | -0.027466 | -0.059509 | -0.07782 | -0.045776 | 0.041199 | 0.045776 | -0.055542 | -0.25101 | -0.044861 | -0.15488 | -0.13138 | -0.086975 | -0.09613 | -0.15564 | -0.086975 | -0.086975 | -0.07782 | -0.004578 | -0.068665 | 0.027466 | -0.036621
663.7031 | 0.045776 | 0.47104 | -0.44647 | -0.20401 | -0.17731 | -0.25635 | -0.15915 | -0.059509 | -0.16937 | -0.036621 | -0.045776 | -0.059509 | -0.064087 | 0.036621 | 0.045776 | -0.067291 | -0.24353 | -0.043793 | -0.1506 | -0.12711 | -0.073242 | -0.091553 | -0.13733 | -0.10986 | -0.068665 | -0.07782 | -0.009155 | -0.07782 | 0.045776 | -0.018311
665.4375 | 0.015259 | 0.48386 | -0.44647 | -0.20187 | -0.15701 | -0.28091 | -0.16983 | 0.022888 | -0.050354 | 0.068665 | -0.009155 | -0.11444 | -0.091553 | 0.018311 | 0.030518 | -0.085449 | -0.25101 | -0.048065 | -0.16556 | -0.13245 | 0.022888 | 0.07782 | -0.050354 | -0.11902 | -0.11902 | -0.11444 | -0.036621 | -0.050354 | 0.059509 | -0.045776
667.0938 | 0.045776 | 0.45822 | -0.45609 | -0.18906 | -0.15595 | -0.23819 | -0.16556 | -0.018311 | -0.13733 | -0.004578 | -0.045776 | -0.064087 | -0.086975 | 0.041199 | 0.030518 | -0.065155 | -0.2478 | -0.036316 | -0.15381 | -0.1239 | -0.10071 | -0.09613 | -0.16022 | -0.086975 | -0.07782 | -0.082397 | -0.013733 | -0.09613 | 0.036621 | -0.032043
668.7656 | 0.015259 | 0.47745 | -0.45609 | -0.20081 | -0.1474 | -0.26169 | -0.17838 | 0 | -0.059509 | 0.059509 | -0.027466 | -0.15564 | -0.027466 | 0.050354 | 0.061035 | -0.082245 | -0.24674 | -0.041656 | -0.16663 | -0.10788 | 0.036621 | 0.086975 | -0.022888 | -0.15106 | -0.10986 | -0.10529 | -0.036621 | -0.068665 | 0.082397 | -0.036621
670.4844 | 0.030518 | 0.47638 | -0.4657 | -0.1976 | -0.16449 | -0.26596 | -0.17517 | 0.036621 | -0.022888 | 0.07782 | 0.027466 | -0.082397 | -0.10529 | 0 | 0.076294 | -0.080109 | -0.25955 | -0.05127 | -0.16022 | -0.13672 | 0.059509 | 0.14648 | 0.018311 | -0.10529 | -0.091553 | -0.14191 | -0.073242 | 0.068665 | 0.022888 | -0.091553
672.2188 | 0.045776 | 0.46783 | -0.45181 | -0.19546 | -0.15488 | -0.24246 | -0.17197 | -0.018311 | -0.15106 | -0.004578 | -0.036621 | -0.059509 | -0.07782 | 0.036621 | 0.061035 | -0.065155 | -0.24887 | -0.036316 | -0.1506 | -0.13031 | -0.11902 | -0.09613 | -0.16937 | -0.091553 | -0.082397 | -0.09613 | -0.018311 | -0.09613 | 0.032043 | -0.036621
673.9062 | 0.045776 | 0.46143 | -0.45075 | -0.19546 | -0.17303 | -0.25314 | -0.15915 | -0.041199 | -0.14191 | -0.018311 | -0.054932 | -0.073242 | -0.054932 | 0.059509 | 0.045776 | -0.075836 | -0.24033 | -0.05127 | -0.15701 | -0.13245 | -0.054932 | -0.054932 | -0.13275 | -0.10529 | -0.082397 | -0.07782 | -0.009155 | -0.036621 | 0.036621 | -0.041199
675.6406 | 0.061035 | 0.45609 | -0.45715 | -0.21149 | -0.1474 | -0.25314 | -0.16129 | 0.054932 | -0.041199 | 0.032043 | 0.032043 | 0.004578 | -0.14191 | -0.022888 | 0.030518 | -0.069427 | -0.2446 | -0.041656 | -0.15595 | -0.12817 | -0.045776 | 0.032043 | -0.073242 | -0.032043 | -0.018311 | -0.14191 | -0.07782 | 0.068665 | 0.009155 | -0.050354
677.3594 | 0.061035 | 0.45822 | -0.44647 | -0.19867 | -0.15595 | -0.24887 | -0.16129 | -0.022888 | -0.14191 | 0 | -0.059509 | -0.045776 | -0.07782 | 0.036621 | 0.061035 | -0.064087 | -0.24994 | -0.035248 | -0.1506 | -0.12604 | -0.10529 | -0.07782 | -0.16479 | -0.086975 | -0.068665 | -0.09613 | -0.022888 | -0.082397 | 0.036621 | -0.027466
679.0938 | 0.061035 | 0.4689 | -0.45715 | -0.2211 | -0.16342 | -0.27985 | -0.17303 | 0.11902 | 0.068665 | 0.15106 | 0.07782 | -0.073242 | -0.10071 | -0.022888 | 0.030518 | -0.092926 | -0.24246 | -0.05127 | -0.18906 | -0.13672 | 0.13275 | 0.21515 | 0.068665 | -0.091553 | -0.082397 | -0.16022 | -0.086975 | 0.068665 | 0.018311 | -0.07782
680.7812 | 0.045776 | 0.46356 | -0.45609 | -0.19974 | -0.16556 | -0.28519 | -0.16983 | 0.022888 | -0.064087 | 0.050354 | -0.013733 | -0.091553 | -0.082397 | 0.022888 | 0.061035 | -0.089722 | -0.24567 | -0.046997 | -0.16769 | -0.14206 | 0.027466 | 0.10071 | -0.032043 | -0.11444 | -0.09613 | -0.1236 | -0.045776 | -0.009155 | 0.041199 | -0.054932
682.5156 | 0.045776 | 0.47531 | -0.45075 | -0.1976 | -0.15701 | -0.26596 | -0.18158 | 0.036621 | -0.045776 | 0.059509 | -0.036621 | -0.15564 | -0.050354 | 0.032043 | 0.045776 | -0.076904 | -0.25101 | -0.040588 | -0.16342 | -0.13351 | 0.050354 | 0.068665 | -0.045776 | -0.17853 | -0.15564 | -0.082397 | -0.018311 | -0.073242 | 0.054932 | -0.036621
684.1875 | 0.030518 | 0.46249 | -0.44647 | -0.20721 | -0.15808 | -0.23926 | -0.16663 | -0.022888 | -0.15564 | -0.041199 | -0.059509 | -0.068665 | -0.054932 | 0.045776 | 0.061035 | -0.072632 | -0.24887 | -0.041656 | -0.1506 | -0.13351 | -0.073242 | -0.07782 | -0.14648 | -0.10071 | -0.07782 | -0.086975 | -0.013733 | -0.045776 | 0.032043 | -0.032043
685.8594 | 0.045776 | 0.46463 | -0.46036 | -0.1944 | -0.16876 | -0.23819 | -0.16129 | 0.050354 | -0.059509 | 0.045776 | 0.018311 | -0.064087 | -0.10529 | 0.009155 | 0.045776 | -0.060883 | -0.2446 | -0.044861 | -0.1506 | -0.13245 | -0.045776 | -0.009155 | -0.086975 | -0.091553 | -0.07782 | -0.1236 | -0.045776 | -0.073242 | 0.032043 | -0.032043
687.6094 | 0.030518 | 0.47531 | -0.44968 | -0.19546 | -0.15488 | -0.26382 | -0.15488 | -0.018311 | -0.15106 | -0.018311 | -0.054932 | -0.086975 | -0.064087 | 0.054932 | 0.076294 | -0.072632 | -0.24353 | -0.029907 | -0.15808 | -0.12497 | -0.050354 | -0.059509 | -0.13275 | -0.091553 | -0.091553 | -0.09613 | -0.013733 | -0.041199 | 0.018311 | -0.045776
689.3438 | 0.061035 | 0.46463 | -0.44647 | -0.20187 | -0.16342 | -0.25635 | -0.16556 | -0.022888 | -0.13275 | -0.004578 | -0.059509 | -0.07782 | -0.064087 | 0.054932 | 0.045776 | -0.074768 | -0.24139 | -0.036316 | -0.16342 | -0.13458 | -0.050354 | -0.059509 | -0.11444 | -0.10986 | -0.068665 | -0.086975 | -0.018311 | -0.036621 | 0.027466 | -0.045776
691.0156 | 0.030518 | 0.45609 | -0.44647 | -0.21042 | -0.15488 | -0.24887 | -0.15915 | 0.073242 | -0.027466 | 0.059509 | 0.027466 | -0.036621 | -0.09613 | -0.004578 | 0.061035 | -0.061951 | -0.24887 | -0.037384 | -0.15488 | -0.13245 | -0.032043 | 0.004578 | -0.073242 | -0.068665 | -0.045776 | -0.11444 | -0.045776 | -0.064087 | 0.018311 | -0.041199
692.75 | 0.030518 | 0.46356 | -0.45929 | -0.19226 | -0.15595 | -0.2681 | -0.15381 | 0.036621 | -0.054932 | 0.041199 | 0.036621 | 0.032043 | -0.13275 | -0.032043 | 0.045776 | -0.067291 | -0.25635 | -0.046997 | -0.17197 | -0.12711 | -0.050354 | 0.050354 | -0.036621 | -0.036621 | -0.022888 | -0.14191 | -0.07782 | 0.086975 | 0 | -0.073242
694.4844 | 0.045776 | 0.48813 | -0.45609 | -0.1944 | -0.16876 | -0.27878 | -0.16876 | 0.032043 | -0.050354 | 0.082397 | -0.045776 | -0.14191 | -0.041199 | 0.050354 | 0.045776 | -0.089722 | -0.25207 | -0.046997 | -0.15915 | -0.12924 | 0.036621 | 0.086975 | -0.027466 | -0.16479 | -0.1236 | -0.07782 | -0.032043 | -0.07782 | 0.073242 | -0.054932
696.1562 | 0.045776 | 0.46143 | -0.46143 | -0.20828 | -0.15808 | -0.27771 | -0.17944 | 0.16022 | 0.09613 | 0.15106 | 0.091553 | -0.059509 | -0.13275 | -0.032043 | 0.045776 | -0.084381 | -0.2478 | -0.055542 | -0.15808 | -0.12924 | 0.11444 | 0.22888 | 0.073242 | -0.086975 | -0.082397 | -0.1831 | -0.09613 | 0.059509 | 0.018311 | -0.068665
697.8281 | 0.030518 | 0.47745 | -0.46143 | -0.21255 | -0.15274 | -0.2713 | -0.16769 | 0.032043 | -0.064087 | 0.054932 | -0.018311 | -0.10071 | -0.091553 | 0.018311 | 0.030518 | -0.087585 | -0.2446 | -0.040588 | -0.16876 | -0.14099 | 0.018311 | 0.07782 | -0.054932 | -0.10986 | -0.091553 | -0.13275 | -0.036621 | -0.045776 | 0.064087 | -0.041199
699.5625 | 0.061035 | 0.48599 | -0.45181 | -0.20294 | -0.15808 | -0.28305 | -0.18158 | 0.041199 | -0.045776 | 0.073242 | -0.009155 | -0.15564 | -0.07782 | 0.027466 | 0.045776 | -0.074768 | -0.25635 | -0.043793 | -0.15915 | -0.13138 | 0.064087 | 0.07782 | -0.032043 | -0.12817 | -0.11444 | -0.11444 | -0.041199 | -0.064087 | 0.064087 | -0.036621
701.25 | 0.030518 | 0.4454 | -0.44113 | -0.20721 | -0.16129 | -0.24033 | -0.16449 | 0.086975 | -0.036621 | 0.07782 | 0.032043 | -0.050354 | -0.09613 | -0.004578 | 0.030518 | -0.057678 | -0.23285 | -0.038452 | -0.14206 | -0.14633 | -0.022888 | 0.013733 | -0.073242 | -0.073242 | -0.054932 | -0.11902 | -0.041199 | -0.059509 | 0.018311 | -0.022888
702.9219 | 0.045776 | 0.46997 | -0.4689 | -0.20721 | -0.16876 | -0.28625 | -0.16556 | 0.14648 | 0.09613 | 0.14191 | 0.07782 | -0.064087 | -0.12817 | -0.027466 | 0.045776 | -0.086517 | -0.25207 | -0.043793 | -0.16235 | -0.14206 | 0.11902 | 0.22888 | 0.059509 | -0.10529 | -0.082397 | -0.15106 | -0.086975 | 0.064087 | 0 | -0.073242
704.5938 | 0.045776 | 0.45288 | -0.45075 | -0.1944 | -0.15915 | -0.24246 | -0.15808 | 0.086975 | -0.036621 | 0.068665 | 0.059509 | 0.027466 | -0.14648 | -0.045776 | 0.030518 | -0.066223 | -0.24994 | -0.036316 | -0.15488 | -0.14526 | -0.018311 | 0.041199 | -0.036621 | -0.059509 | -0.041199 | -0.13275 | -0.050354 | 0.041199 | -0.022888 | -0.054932
706.25 | 0.061035 | 0.49347 | -0.45609 | -0.18799 | -0.16556 | -0.27557 | -0.1709 | 0.068665 | 0.018311 | 0.086975 | 0.036621 | -0.073242 | -0.086975 | 0 | 0.045776 | -0.085449 | -0.26596 | -0.044861 | -0.16663 | -0.12817 | 0.10071 | 0.19226 | 0.050354 | -0.091553 | -0.091553 | -0.15564 | -0.082397 | 0.082397 | 0 | -0.064087
707.9375 | 0.045776 | 0.45822 | -0.45502 | -0.20615 | -0.15274 | -0.26276 | -0.17731 | 0.082397 | -0.022888 | 0.045776 | 0.041199 | 0.054932 | -0.15564 | -0.050354 | 0.030518 | -0.066223 | -0.24139 | -0.043793 | -0.16129 | -0.12924 | -0.013733 | 0.045776 | -0.064087 | 0.004578 | 0.018311 | -0.13275 | -0.068665 | 0.054932 | 0.013733 | -0.073242
709.6719 | 0.030518 | 0.45822 | -0.45822 | -0.21255 | -0.15167 | -0.2681 | -0.16663 | 0.1236 | 0.054932 | 0.11902 | 0.068665 | -0.032043 | -0.16022 | -0.036621 | 0.030518 | -0.068359 | -0.24674 | -0.037384 | -0.17197 | -0.13351 | 0.045776 | 0.13733 | 0 | -0.045776 | 0 | -0.16022 | -0.086975 | 0.009155 | 0.018311 | -0.045776
711.3438 | 0.061035 | 0.46356 | -0.45609 | -0.20294 | -0.16663 | -0.25314 | -0.16556 | 0.068665 | -0.059509 | 0.10071 | 0 | -0.13275 | -0.050354 | 0.041199 | 0.030518 | -0.079041 | -0.25207 | -0.045929 | -0.15274 | -0.13138 | 0.027466 | 0.059509 | -0.036621 | -0.17395 | -0.15106 | -0.09613 | -0.022888 | -0.027466 | 0.027466 | -0.032043
713.0938 | 0.030518 | 0.46783 | -0.44754 | -0.18906 | -0.15701 | -0.25528 | -0.15595 | 0.036621 | -0.073242 | 0.064087 | 0 | -0.13733 | -0.059509 | 0.036621 | 0.030518 | -0.075836 | -0.25421 | -0.040588 | -0.16022 | -0.13672 | 0.027466 | 0.068665 | -0.041199 | -0.16937 | -0.14648 | -0.091553 | -0.018311 | -0.032043 | 0.036621 | -0.041199
714.7812 | 0.045776 | 0.44647 | -0.45181 | -0.20294 | -0.14526 | -0.24887 | -0.16129 | 0.068665 | -0.032043 | 0.054932 | 0.041199 | -0.018311 | -0.11444 | 0 | 0.061035 | -0.072632 | -0.23926 | -0.033112 | -0.14633 | -0.14526 | -0.009155 | 0.054932 | -0.036621 | -0.073242 | -0.068665 | -0.1236 | -0.054932 | 0.059509 | 0 | -0.050354
716.4531 | 0.015259 | 0.4689 | -0.46783 | -0.19974 | -0.14633 | -0.28305 | -0.15488 | 0.059509 | -0.009155 | 0.091553 | 0.032043 | -0.082397 | -0.10986 | 0.009155 | 0.030518 | -0.091858 | -0.25207 | -0.03952 | -0.15808 | -0.13351 | 0.10071 | 0.17395 | 0.041199 | -0.11444 | -0.086975 | -0.12817 | -0.082397 | 0.073242 | 0.013733 | -0.07782
718.1875 | 0.061035 | 0.46463 | -0.46036 | -0.19974 | -0.15915 | -0.25955 | -0.17303 | 0.059509 | -0.036621 | 0.050354 | 0.050354 | 0.022888 | -0.13733 | -0.027466 | 0.061035 | -0.064087 | -0.24674 | -0.029907 | -0.15915 | -0.13351 | -0.027466 | 0.036621 | -0.041199 | 0.004578 | -0.018311 | -0.15106 | -0.068665 | 0.059509 | -0.009155 | -0.050354
719.875 | 0.030518 | 0.47852 | -0.4657 | -0.19012 | -0.15915 | -0.26916 | -0.1709 | 0.018311 | -0.054932 | 0.054932 | -0.009155 | -0.10071 | -0.086975 | 0.022888 | 0.030518 | -0.085449 | -0.24674 | -0.040588 | -0.16769 | -0.13458 | 0.036621 | 0.10529 | -0.027466 | -0.11444 | -0.091553 | -0.1236 | -0.059509 | -0.004578 | 0.032043 | -0.054932
721.6094 | 0.045776 | 0.4689 | -0.439 | -0.20081 | -0.16129 | -0.24246 | -0.16449 | -0.022888 | -0.14648 | -0.013733 | -0.064087 | -0.064087 | -0.059509 | 0.059509 | 0.061035 | -0.066223 | -0.24887 | -0.03952 | -0.14847 | -0.13351 | -0.041199 | -0.068665 | -0.12817 | -0.073242 | -0.09613 | -0.082397 | -0.009155 | -0.032043 | 0.022888 | -0.022888
723.3438 | 0.045776 | 0.45715 | -0.45822 | -0.2211 | -0.15808 | -0.26703 | -0.1741 | 0.1236 | 0.082397 | 0.15106 | 0.09613 | -0.064087 | -0.14648 | -0.036621 | 0.030518 | -0.083313 | -0.24033 | -0.048065 | -0.15381 | -0.13031 | 0.091553 | 0.20599 | 0.059509 | -0.10986 | -0.07782 | -0.15564 | -0.073242 | 0.032043 | 0.041199 | -0.068665
725.0156 | 0.061035 | 0.47104 | -0.46356 | -0.19226 | -0.15595 | -0.2478 | -0.16235 | -0.022888 | -0.12817 | 0.013733 | -0.045776 | -0.07782 | -0.054932 | 0.041199 | 0.045776 | -0.067291 | -0.24994 | -0.048065 | -0.14313 | -0.14206 | -0.054932 | -0.022888 | -0.07782 | -0.13733 | -0.11902 | -0.07782 | 0 | -0.018311 | 0.032043 | -0.045776
726.75 | 0.045776 | 0.45502 | -0.4657 | -0.20187 | -0.15915 | -0.28839 | -0.1709 | 0.14191 | 0.09613 | 0.14191 | 0.07782 | -0.059509 | -0.13275 | -0.009155 | 0.030518 | -0.084381 | -0.25314 | -0.03952 | -0.16235 | -0.12924 | 0.10529 | 0.21973 | 0.082397 | -0.10529 | -0.086975 | -0.15564 | -0.073242 | 0.068665 | 0.004578 | -0.073242
728.4844 | 0.045776 | 0.46036 | -0.45822 | -0.20828 | -0.17517 | -0.26916 | -0.17197 | 0.10071 | 0.027466 | 0.10529 | 0.054932 | -0.073242 | -0.10986 | -0.009155 | 0.030518 | -0.082245 | -0.2478 | -0.040588 | -0.16663 | -0.13992 | 0.11444 | 0.20599 | 0.064087 | -0.10529 | -0.086975 | -0.14648 | -0.059509 | 0.07782 | 0.036621 | -0.064087
730.1719 | 0.045776 | 0.44861 | -0.45822 | -0.18692 | -0.16022 | -0.24353 | -0.16769 | 0.09613 | -0.018311 | 0.036621 | 0.041199 | 0.036621 | -0.15106 | -0.041199 | 0.030518 | -0.057678 | -0.25528 | -0.043793 | -0.14847 | -0.14954 | -0.018311 | 0.045776 | -0.073242 | -0.022888 | -0.013733 | -0.1236 | -0.07782 | 0.064087 | -0.009155 | -0.064087
731.8438 | 0.030518 | 0.4689 | -0.46036 | -0.19226 | -0.16449 | -0.27237 | -0.1741 | 0.14191 | 0.073242 | 0.14191 | 0.082397 | -0.086975 | -0.11902 | -0.027466 | 0.076294 | -0.086517 | -0.25207 | -0.052338 | -0.1474 | -0.13565 | 0.13275 | 0.22888 | 0.082397 | -0.10071 | -0.07782 | -0.16022 | -0.073242 | 0.082397 | 0.027466 | -0.07782
733.5 | 0.045776 | 0.46783 | -0.46036 | -0.19226 | -0.15915 | -0.27771 | -0.17197 | 0.050354 | -0.059509 | 0.073242 | -0.013733 | -0.11444 | -0.068665 | 0.027466 | 0.045776 | -0.074768 | -0.25207 | -0.045929 | -0.15488 | -0.13138 | 0.045776 | 0.10529 | -0.036621 | -0.11902 | -0.091553 | -0.11444 | -0.050354 | -0.059509 | 0.059509 | -0.041199
735.1875 | 0.045776 | 0.47745 | -0.46036 | -0.19012 | -0.15167 | -0.25955 | -0.15915 | 0.059509 | -0.059509 | 0.07782 | -0.004578 | -0.16479 | -0.054932 | 0.059509 | 0.030518 | -0.075836 | -0.24994 | -0.041656 | -0.16022 | -0.14099 | 0.050354 | 0.10986 | -0.032043 | -0.15564 | -0.13733 | -0.086975 | -0.027466 | -0.073242 | 0.036621 | -0.018311
736.8594 | 0.061035 | 0.45288 | -0.45181 | -0.20187 | -0.16235 | -0.22964 | -0.16449 | 0.045776 | -0.082397 | 0.022888 | -0.004578 | -0.054932 | -0.073242 | 0.009155 | 0.045776 | -0.055542 | -0.24353 | -0.042725 | -0.15381 | -0.13886 | -0.07782 | -0.050354 | -0.13275 | -0.07782 | -0.07782 | -0.10071 | -0.018311 | -0.086975 | 0.018311 | -0.032043
738.5781 | 0.045776 | 0.4689 | -0.45609 | -0.18799 | -0.16342 | -0.27771 | -0.16342 | 0.050354 | -0.022888 | 0.09613 | -0.013733 | -0.15106 | -0.054932 | 0.050354 | 0.045776 | -0.082245 | -0.25848 | -0.043793 | -0.16342 | -0.13138 | 0.045776 | 0.086975 | -0.032043 | -0.16479 | -0.15564 | -0.091553 | 0.004578 | -0.082397 | 0.059509 | -0.027466
740.2656 | 0.045776 | 0.44006 | -0.43686 | -0.20294 | -0.16556 | -0.24139 | -0.15808 | 0.086975 | -0.032043 | 0.073242 | 0.027466 | -0.054932 | -0.10071 | -0.004578 | 0.045776 | -0.059814 | -0.24353 | -0.041656 | -0.1506 | -0.13031 | -0.018311 | 0.018311 | -0.07782 | -0.064087 | -0.059509 | -0.10529 | -0.032043 | -0.064087 | 0.013733 | -0.032043
741.9219 | 0.030518 | 0.47424 | -0.4689 | -0.20294 | -0.15167 | -0.28519 | -0.16235 | 0.13733 | 0.091553 | 0.15564 | 0.09613 | -0.045776 | -0.13275 | -0.041199 | 0.045776 | -0.075836 | -0.25635 | -0.048065 | -0.1709 | -0.12924 | 0.10071 | 0.21057 | 0.059509 | -0.091553 | -0.068665 | -0.16479 | -0.086975 | 0.045776 | 0.013733 | -0.059509
743.6562 | 0.030518 | 0.46677 | -0.46463 | -0.21255 | -0.15167 | -0.27771 | -0.17517 | 0.064087 | -0.013733 | 0.086975 | 0.022888 | -0.082397 | -0.10071 | 0 | 0.045776 | -0.076904 | -0.24887 | -0.042725 | -0.16556 | -0.13458 | 0.086975 | 0.17395 | 0.032043 | -0.09613 | -0.07782 | -0.14191 | -0.068665 | 0.068665 | 0 | -0.064087
745.375 | 0.045776 | 0.45181 | -0.45929 | -0.20615 | -0.15915 | -0.24567 | -0.16449 | 0.10529 | -0.009155 | 0.082397 | 0.068665 | 0.018311 | -0.14648 | -0.045776 | 0.045776 | -0.05661 | -0.25207 | -0.03418 | -0.14847 | -0.13886 | -0.018311 | 0.041199 | -0.054932 | -0.050354 | -0.032043 | -0.10529 | -0.050354 | 0.059509 | 0 | -0.045776
747.1094 | 0.030518 | 0.45822 | -0.45395 | -0.19333 | -0.15167 | -0.26596 | -0.15808 | 0.059509 | -0.036621 | 0.082397 | -0.009155 | -0.14191 | -0.059509 | 0.041199 | 0.045776 | -0.066223 | -0.27023 | -0.040588 | -0.15701 | -0.14099 | 0.022888 | 0.054932 | -0.032043 | -0.16022 | -0.13733 | -0.086975 | -0.009155 | -0.027466 | 0.032043 | -0.045776
748.7812 | 0.045776 | 0.4689 | -0.44968 | -0.21042 | -0.16449 | -0.25421 | -0.15915 | -0.013733 | -0.13275 | 0.004578 | -0.050354 | -0.064087 | -0.054932 | 0.050354 | 0.091553 | -0.0737 | -0.24139 | -0.030975 | -0.15274 | -0.13672 | -0.032043 | -0.022888 | -0.09613 | -0.13275 | -0.12817 | -0.07782 | -0.009155 | -0.036621 | 0.018311 | -0.032043
750.5156 | 0.045776 | 0.45288 | -0.44113 | -0.2179 | -0.15701 | -0.24353 | -0.15701 | 0.086975 | -0.004578 | 0.091553 | 0.032043 | -0.027466 | -0.10986 | 0.004578 | 0.061035 | -0.069427 | -0.23819 | -0.036316 | -0.1474 | -0.13672 | -0.018311 | 0.032043 | -0.054932 | -0.086975 | -0.059509 | -0.11444 | -0.027466 | -0.032043 | 0.009155 | -0.027466
752.25 | 0.061035 | 0.45502 | -0.46036 | -0.19546 | -0.15701 | -0.27451 | -0.16556 | 0.12817 | 0.073242 | 0.15564 | 0.091553 | -0.027466 | -0.14648 | -0.027466 | 0.045776 | -0.079041 | -0.25635 | -0.045929 | -0.16129 | -0.13458 | 0.07782 | 0.21057 | 0.059509 | -0.086975 | -0.054932 | -0.13733 | -0.07782 | 0.041199 | 0.018311 | -0.054932
753.9375 | 0.061035 | 0.48279 | -0.4689 | -0.1976 | -0.15595 | -0.28305 | -0.16235 | 0.022888 | -0.045776 | 0.064087 | -0.009155 | -0.10529 | -0.059509 | 0.009155 | 0.045776 | -0.081177 | -0.2681 | -0.03952 | -0.16876 | -0.13031 | 0.018311 | 0.09613 | -0.045776 | -0.11902 | -0.09613 | -0.10986 | -0.022888 | -0.054932 | 0.059509 | -0.045776
755.6719 | 0.061035 | 0.45395 | -0.45395 | -0.20081 | -0.16663 | -0.26169 | -0.17517 | 0.14648 | 0.073242 | 0.13733 | 0.082397 | -0.068665 | -0.11902 | -0.050354 | 0.045776 | -0.081177 | -0.24887 | -0.053406 | -0.17197 | -0.14313 | 0.10071 | 0.21057 | 0.064087 | -0.07782 | -0.073242 | -0.16479 | -0.10529 | 0.045776 | 0.013733 | -0.059509
757.4062 | 0.030518 | 0.4689 | -0.44327 | -0.20721 | -0.15701 | -0.27664 | -0.17303 | 0.15106 | 0.068665 | 0.15106 | 0.082397 | -0.059509 | -0.13275 | -0.032043 | 0.030518 | -0.077972 | -0.25314 | -0.059814 | -0.16342 | -0.14526 | 0.11902 | 0.21973 | 0.068665 | -0.091553 | -0.086975 | -0.15564 | -0.091553 | 0.059509 | 0 | -0.07782
759.1406 | 0.030518 | 0.46143 | -0.45609 | -0.20081 | -0.15274 | -0.26169 | -0.16342 | 0.16479 | 0.054932 | 0.14191 | 0.086975 | -0.045776 | -0.15106 | -0.045776 | 0.045776 | -0.077972 | -0.26062 | -0.042725 | -0.16342 | -0.14313 | 0.082397 | 0.20599 | 0.032043 | -0.064087 | -0.082397 | -0.13275 | -0.073242 | 0.032043 | 0.022888 | -0.032043
760.8125 | 0.030518 | 0.44434 | -0.45609 | -0.19867 | -0.16556 | -0.2446 | -0.15381 | 0.1236 | -0.027466 | 0.064087 | 0.054932 | 0.036621 | -0.1236 | -0.045776 | 0.045776 | -0.054474 | -0.24674 | -0.049133 | -0.1474 | -0.14206 | -0.027466 | 0.050354 | -0.041199 | -0.054932 | -0.064087 | -0.11444 | -0.027466 | 0.073242 | -0.018311 | -0.045776
762.4844 | 0.045776 | 0.46356 | -0.45822 | -0.20187 | -0.15701 | -0.27344 | -0.17197 | 0.059509 | -0.059509 | 0.068665 | 0 | -0.10071 | -0.073242 | 0.022888 | 0.030518 | -0.080109 | -0.23926 | -0.043793 | -0.16129 | -0.13565 | 0.032043 | 0.086975 | -0.022888 | -0.11902 | -0.07782 | -0.09613 | -0.032043 | -0.045776 | 0.054932 | -0.032043
764.1719 | 0.045776 | 0.45502 | -0.45181 | -0.21042 | -0.16235 | -0.25955 | -0.16556 | 0.13733 | 0.073242 | 0.13275 | 0.10529 | -0.036621 | -0.13733 | -0.032043 | 0.061035 | -0.084381 | -0.25101 | -0.052338 | -0.1709 | -0.13351 | 0.082397 | 0.19226 | 0.041199 | -0.059509 | -0.059509 | -0.14648 | -0.07782 | 0.018311 | 0.027466 | -0.036621
765.8438 | 0.045776 | 0.46783 | -0.46036 | -0.19653 | -0.15274 | -0.25635 | -0.16769 | 0.018311 | -0.13733 | 0.013733 | -0.068665 | -0.082397 | -0.045776 | 0.068665 | 0.061035 | -0.067291 | -0.25635 | -0.040588 | -0.15381 | -0.13992 | -0.013733 | -0.004578 | -0.082397 | -0.13275 | -0.12817 | -0.086975 | -0.009155 | -0.018311 | 0.032043 | -0.032043
767.5156 | 0.045776 | 0.44754 | -0.45395 | -0.20508 | -0.16235 | -0.24139 | -0.16129 | -0.022888 | -0.12817 | 0.009155 | -0.036621 | -0.045776 | -0.068665 | 0.054932 | 0.061035 | -0.063019 | -0.24567 | -0.038452 | -0.14847 | -0.13672 | -0.09613 | -0.064087 | -0.17395 | -0.082397 | -0.064087 | -0.07782 | 0 | -0.082397 | 0.045776 | -0.036621
769.1875 | 0.030518 | 0.4657 | -0.45181 | -0.20508 | -0.16129 | -0.26382 | -0.16663 | 0.050354 | -0.032043 | 0.032043 | 0.032043 | 0.009155 | -0.1236 | -0.022888 | 0.076294 | -0.061951 | -0.25207 | -0.043793 | -0.15381 | -0.13992 | -0.022888 | 0.064087 | -0.032043 | -0.022888 | -0.009155 | -0.14191 | -0.073242 | 0.082397 | -0.004578 | -0.041199
770.875 | 0.045776 | 0.45822 | -0.45075 | -0.19867 | -0.15808 | -0.25848 | -0.16449 | 0.073242 | -0.041199 | 0.045776 | 0.064087 | 0.013733 | -0.1236 | -0.022888 | 0.030518 | -0.075836 | -0.25207 | -0.042725 | -0.15488 | -0.12817 | -0.009155 | 0.073242 | -0.022888 | -0.018311 | 0.013733 | -0.14648 | -0.07782 | 0.059509 | 0.004578 | -0.050354
772.6094 | 0.030518 | 0.48065 | -0.45715 | -0.20187 | -0.15595 | -0.25955 | -0.17303 | 0.064087 | -0.013733 | 0.064087 | 0.036621 | 0.018311 | -0.12817 | -0.032043 | 0.045776 | -0.069427 | -0.25207 | -0.05127 | -0.16876 | -0.12817 | -0.018311 | 0.086975 | -0.036621 | -0.009155 | 0.022888 | -0.13275 | -0.050354 | 0.027466 | 0.018311 | -0.050354
774.3438 | 0.030518 | 0.46249 | -0.46249 | -0.20294 | -0.1474 | -0.27451 | -0.16983 | 0.10529 | 0.064087 | 0.12817 | 0.086975 | -0.045776 | -0.13733 | -0.041199 | 0.045776 | -0.079041 | -0.25421 | -0.045929 | -0.15915 | -0.13886 | 0.041199 | 0.16479 | 0.018311 | -0.059509 | -0.027466 | -0.15564 | -0.073242 | 0.018311 | 0.022888 | -0.045776
776 | 0.045776 | 0.4422 | -0.4454 | -0.19546 | -0.16556 | -0.25101 | -0.15488 | -0.036621 | -0.15564 | -0.009155 | -0.041199 | -0.050354 | -0.064087 | 0.045776 | 0.045776 | -0.070496 | -0.2478 | -0.038452 | -0.16235 | -0.13031 | -0.09613 | -0.068665 | -0.14191 | -0.068665 | -0.054932 | -0.068665 | 0.009155 | -0.07782 | 0.041199 | -0.032043
777.7344 | 0.030518 | 0.44647 | -0.45929 | -0.21576 | -0.16022 | -0.26169 | -0.16342 | 0.059509 | -0.045776 | 0.032043 | 0.041199 | 0.027466 | -0.11902 | -0.027466 | 0.045776 | -0.063019 | -0.24353 | -0.041656 | -0.16022 | -0.13672 | -0.036621 | 0.068665 | -0.036621 | -0.027466 | 0.004578 | -0.15106 | -0.07782 | 0.068665 | -0.004578 | -0.064087
779.3906 | 0.045776 | 0.46997 | -0.4689 | -0.20508 | -0.14847 | -0.28946 | -0.16983 | 0.073242 | 0 | 0.091553 | 0.041199 | -0.059509 | -0.09613 | 0.004578 | 0.030518 | -0.089722 | -0.25742 | -0.044861 | -0.17197 | -0.13245 | 0.10071 | 0.19226 | 0.054932 | -0.09613 | -0.068665 | -0.15106 | -0.059509 | 0.068665 | 0.004578 | -0.073242
781.0625 | 0.076294 | 0.46783 | -0.45288 | -0.20828 | -0.16235 | -0.24887 | -0.16556 | 0 | -0.15106 | -0.009155 | -0.050354 | -0.07782 | -0.054932 | 0.041199 | 0.061035 | -0.065155 | -0.25421 | -0.048065 | -0.15701 | -0.13031 | -0.050354 | -0.041199 | -0.09613 | -0.11902 | -0.09613 | -0.082397 | 0.009155 | -0.027466 | 0.022888 | -0.022888
782.75 | 0.030518 | 0.46783 | -0.4422 | -0.20508 | -0.15274 | -0.26169 | -0.15915 | 0.050354 | -0.045776 | 0.091553 | 0.009155 | -0.14648 | -0.050354 | 0.068665 | 0.015259 | -0.080109 | -0.25101 | -0.041656 | -0.1506 | -0.13886 | 0.022888 | 0.054932 | -0.041199 | -0.15106 | -0.14648 | -0.07782 | -0.004578 | -0.032043 | 0.032043 | -0.022888
784.4844 | 0.030518 | 0.46143 | -0.45609 | -0.21042 | -0.1741 | -0.26382 | -0.16342 | 0.064087 | -0.050354 | 0.022888 | 0.054932 | 0.022888 | -0.1236 | -0.013733 | 0.045776 | -0.067291 | -0.25207 | -0.053406 | -0.15167 | -0.13672 | -0.018311 | 0.068665 | -0.050354 | -0.022888 | -0.009155 | -0.14191 | -0.059509 | 0.082397 | -0.009155 | -0.073242
786.2188 | 0.076294 | 0.45822 | -0.45822 | -0.21255 | -0.15488 | -0.29159 | -0.16983 | 0.12817 | 0.054932 | 0.11902 | 0.07782 | -0.054932 | -0.10071 | -0.032043 | 0.045776 | -0.089722 | -0.25314 | -0.043793 | -0.1741 | -0.13565 | 0.12817 | 0.21973 | 0.082397 | -0.091553 | -0.082397 | -0.14648 | -0.086975 | 0.07782 | 0.018311 | -0.07782
787.9062 | 0.061035 | 0.45181 | -0.44754 | -0.19867 | -0.16769 | -0.24353 | -0.16983 | 0.10071 | -0.032043 | 0.07782 | 0.032043 | -0.018311 | -0.10529 | -0.004578 | 0.061035 | -0.055542 | -0.25314 | -0.049133 | -0.14206 | -0.13245 | -0.013733 | 0.032043 | -0.064087 | -0.064087 | -0.054932 | -0.10986 | -0.036621 | -0.050354 | 0.018311 | -0.027466
789.625 | 0.061035 | 0.45929 | -0.45181 | -0.20828 | -0.15488 | -0.27344 | -0.16983 | 0.068665 | -0.036621 | 0.050354 | 0.041199 | 0.013733 | -0.1236 | -0.013733 | 0.061035 | -0.081177 | -0.24353 | -0.040588 | -0.16556 | -0.1239 | -0.004578 | 0.068665 | -0.032043 | -0.004578 | 0.013733 | -0.13275 | -0.064087 | 0.032043 | 0.018311 | -0.036621
791.375 | 0.045776 | 0.46677 | -0.45609 | -0.2243 | -0.16342 | -0.2713 | -0.17731 | 0.10529 | 0.068665 | 0.11902 | 0.073242 | -0.064087 | -0.10986 | -0.009155 | 0.061035 | -0.086517 | -0.2446 | -0.048065 | -0.1709 | -0.13351 | 0.12817 | 0.21973 | 0.07782 | -0.082397 | -0.082397 | -0.14648 | -0.073242 | 0.091553 | 0.036621 | -0.064087
793.1094 | 0.030518 | 0.4657 | -0.44861 | -0.1976 | -0.15701 | -0.24353 | -0.16663 | -0.022888 | -0.14191 | -0.022888 | -0.054932 | -0.050354 | -0.054932 | 0.054932 | 0.030518 | -0.063019 | -0.2478 | -0.03418 | -0.15701 | -0.13565 | -0.073242 | -0.059509 | -0.13733 | -0.073242 | -0.073242 | -0.086975 | 0.009155 | -0.036621 | 0.054932 | -0.041199
794.7812 | 0.061035 | 0.45822 | -0.44434 | -0.19012 | -0.15808 | -0.26596 | -0.16556 | -0.027466 | -0.14648 | -0.022888 | -0.054932 | -0.050354 | -0.032043 | 0.059509 | 0.045776 | -0.069427 | -0.2478 | -0.038452 | -0.15167 | -0.1239 | -0.041199 | -0.050354 | -0.1236 | -0.10071 | -0.091553 | -0.07782 | 0.004578 | -0.022888 | 0.041199 | -0.041199
796.5156 | 0.045776 | 0.46036 | -0.44861 | -0.20721 | -0.1506 | -0.25528 | -0.14954 | 0.064087 | -0.050354 | 0.07782 | 0.013733 | -0.14191 | -0.050354 | 0.050354 | 0.061035 | -0.079041 | -0.25528 | -0.03952 | -0.15381 | -0.13138 | 0.013733 | 0.068665 | -0.050354 | -0.16937 | -0.13733 | -0.091553 | -0.004578 | -0.032043 | 0.036621 | -0.036621
798.1875 | 0.061035 | 0.45822 | -0.45502 | -0.20401 | -0.1474 | -0.24246 | -0.16876 | 0.041199 | -0.064087 | 0.054932 | 0.018311 | -0.041199 | -0.086975 | 0.018311 | 0.045776 | -0.065155 | -0.25207 | -0.041656 | -0.14954 | -0.12817 | -0.068665 | -0.041199 | -0.11444 | -0.082397 | -0.054932 | -0.10071 | -0.027466 | -0.073242 | 0.054932 | -0.009155
799.8594 | 0.061035 | 0.46463 | -0.45822 | -0.19012 | -0.15808 | -0.25742 | -0.17303 | -0.009155 | -0.10529 | 0.018311 | -0.054932 | -0.091553 | -0.041199 | 0.064087 | 0.045776 | -0.075836 | -0.26062 | -0.036316 | -0.15274 | -0.14099 | -0.013733 | 0.009155 | -0.073242 | -0.13733 | -0.11444 | -0.07782 | -0.009155 | -0.013733 | 0.013733 | -0.027466
801.5781 | 0.030518 | 0.4422 | -0.45929 | -0.21683 | -0.16663 | -0.27023 | -0.16769 | 0.13275 | 0.041199 | 0.11902 | 0.086975 | -0.045776 | -0.13275 | -0.041199 | 0.045776 | -0.088654 | -0.25635 | -0.042725 | -0.16022 | -0.13565 | 0.041199 | 0.16022 | 0.009155 | -0.050354 | -0.013733 | -0.16022 | -0.07782 | 0.022888 | 0.013733 | -0.059509
803.25 | 0.045776 | 0.43686 | -0.44006 | -0.21042 | -0.15274 | -0.26169 | -0.16876 | 0.09613 | -0.022888 | 0.07782 | 0.050354 | -0.018311 | -0.10071 | -0.013733 | 0.015259 | -0.067291 | -0.2446 | -0.033112 | -0.15381 | -0.13565 | -0.004578 | 0.045776 | -0.022888 | -0.064087 | -0.045776 | -0.10529 | -0.036621 | 0.027466 | -0.004578 | -0.036621
804.9375 | 0.030518 | 0.46143 | -0.45929 | -0.19333 | -0.17517 | -0.28412 | -0.16983 | -0.004578 | -0.054932 | 0.068665 | -0.022888 | -0.14191 | -0.059509 | 0.045776 | 0.015259 | -0.095062 | -0.26596 | -0.044861 | -0.16235 | -0.12711 | 0.036621 | 0.082397 | -0.036621 | -0.1236 | -0.10529 | -0.11902 | -0.022888 | -0.073242 | 0.050354 | -0.013733
806.6719 | 0.061035 | 0.47745 | -0.45822 | -0.1976 | -0.15595 | -0.25528 | -0.16663 | 0 | -0.14191 | -0.018311 | -0.064087 | -0.068665 | -0.050354 | 0.073242 | 0.045776 | -0.065155 | -0.25207 | -0.042725 | -0.1474 | -0.13672 | -0.054932 | -0.054932 | -0.10529 | -0.07782 | -0.09613 | -0.082397 | 0 | -0.018311 | 0.032043 | -0.032043
808.4062 | 0.045776 | 0.45288 | -0.45609 | -0.2243 | -0.14954 | -0.25635 | -0.16235 | 0.082397 | -0.018311 | 0.036621 | 0.050354 | 0.050354 | -0.13733 | -0.041199 | 0.045776 | -0.063019 | -0.24674 | -0.03418 | -0.16129 | -0.12817 | -0.027466 | 0.032043 | -0.064087 | -0.004578 | 0 | -0.10529 | -0.07782 | 0.054932 | 0.013733 | -0.064087
810.0938 | 0.030518 | 0.47852 | -0.46036 | -0.2211 | -0.17624 | -0.27771 | -0.16876 | 0.009155 | -0.045776 | 0.045776 | 0 | -0.086975 | -0.082397 | 0.027466 | 0.045776 | -0.099335 | -0.25207 | -0.049133 | -0.15167 | -0.13245 | 0.041199 | 0.10986 | -0.022888 | -0.11444 | -0.10986 | -0.10071 | -0.036621 | 0.013733 | 0.045776 | -0.068665
811.7656 | 0.045776 | 0.46463 | -0.44861 | -0.19867 | -0.16129 | -0.24139 | -0.16663 | 0.068665 | -0.050354 | 0.036621 | 0.027466 | -0.041199 | -0.10071 | 0.022888 | 0.030518 | -0.065155 | -0.24994 | -0.028839 | -0.14313 | -0.1442 | -0.041199 | -0.027466 | -0.086975 | -0.07782 | -0.050354 | -0.10529 | -0.032043 | -0.068665 | 0.041199 | -0.022888
813.5 | 0.045776 | 0.45609 | -0.45715 | -0.19974 | -0.15915 | -0.26916 | -0.15915 | 0.032043 | -0.041199 | 0.086975 | -0.009155 | -0.13275 | -0.032043 | 0.073242 | 0.045776 | -0.083313 | -0.24887 | -0.035248 | -0.15808 | -0.13672 | 0.027466 | 0.068665 | -0.041199 | -0.16937 | -0.14648 | -0.073242 | 0.009155 | -0.050354 | 0.036621 | -0.027466
815.25 | 0.015259 | 0.44861 | -0.45181 | -0.21042 | -0.16983 | -0.26916 | -0.17838 | 0.068665 | -0.032043 | 0.059509 | 0.050354 | 0.041199 | -0.12817 | -0.027466 | 0.030518 | -0.069427 | -0.23926 | -0.036316 | -0.15167 | -0.13351 | -0.013733 | 0.054932 | -0.054932 | 0 | 0.013733 | -0.13733 | -0.10071 | 0.045776 | 0.022888 | -0.064087
816.9219 | 0.045776 | 0.45075 | -0.45929 | -0.20294 | -0.15595 | -0.2681 | -0.16983 | 0.073242 | -0.013733 | 0.059509 | 0.036621 | 0.004578 | -0.13733 | -0.036621 | 0.061035 | -0.079041 | -0.25742 | -0.054474 | -0.16022 | -0.13565 | 0.004578 | 0.073242 | -0.036621 | -0.013733 | 0.009155 | -0.12817 | -0.064087 | 0.018311 | 0.041199 | -0.045776
818.6562 | 0.061035 | 0.49561 | -0.46036 | -0.19974 | -0.15381 | -0.27023 | -0.1709 | 0.064087 | 0.004578 | 0.07782 | 0.041199 | -0.082397 | -0.10986 | 0.009155 | 0.061035 | -0.088654 | -0.25101 | -0.050201 | -0.16342 | -0.13672 | 0.086975 | 0.17853 | 0.050354 | -0.091553 | -0.086975 | -0.12817 | -0.059509 | 0.068665 | 0.018311 | -0.059509
820.3438 | 0.045776 | 0.47531 | -0.46356 | -0.19974 | -0.14954 | -0.27023 | -0.17303 | 0.10986 | 0.036621 | 0.1236 | 0.050354 | -0.059509 | -0.10529 | -0.009155 | 0.045776 | -0.080109 | -0.25742 | -0.044861 | -0.16129 | -0.13672 | 0.11902 | 0.21515 | 0.064087 | -0.086975 | -0.07782 | -0.16022 | -0.059509 | 0.082397 | 0.009155 | -0.064087
822.0625 | 0.045776 | 0.42618 | -0.45288 | -0.21896 | -0.16342 | -0.24246 | -0.16235 | 0.091553 | -0.018311 | 0.059509 | 0.054932 | 0.009155 | -0.10529 | 0.013733 | 0.030518 | -0.074768 | -0.23178 | -0.040588 | -0.1442 | -0.14954 | 0 | 0.059509 | -0.050354 | -0.036621 | -0.036621 | -0.11444 | -0.059509 | 0.045776 | -0.009155 | -0.050354
823.7344 | 0.045776 | 0.46997 | -0.45288 | -0.21469 | -0.15488 | -0.28091 | -0.16663 | 0.018311 | -0.054932 | 0.041199 | -0.013733 | -0.082397 | -0.064087 | 0.018311 | 0.045776 | -0.087585 | -0.24674 | -0.054474 | -0.15915 | -0.14206 | 0.032043 | 0.09613 | -0.032043 | -0.1236 | -0.09613 | -0.091553 | -0.018311 | -0.032043 | 0.064087 | -0.022888
825.4219 | 0.030518 | 0.45715 | -0.45609 | -0.20828 | -0.16556 | -0.27237 | -0.17517 | 0.14191 | 0.073242 | 0.1236 | 0.082397 | -0.050354 | -0.11444 | -0.013733 | 0.045776 | -0.076904 | -0.25528 | -0.041656 | -0.15274 | -0.13992 | 0.14191 | 0.21515 | 0.082397 | -0.091553 | -0.07782 | -0.14648 | -0.068665 | 0.073242 | 0.018311 | -0.059509
827.0938 | 0.030518 | 0.44327 | -0.45609 | -0.20401 | -0.14954 | -0.24674 | -0.17624 | 0.091553 | -0.022888 | 0.059509 | 0.059509 | 0.050354 | -0.1236 | -0.018311 | 0.061035 | -0.063019 | -0.25314 | -0.042725 | -0.15381 | -0.13886 | -0.009155 | 0.059509 | -0.027466 | 0.004578 | 0 | -0.13275 | -0.07782 | 0.073242 | -0.004578 | -0.059509
828.7812 | 0.030518 | 0.42831 | -0.46143 | -0.20294 | -0.16235 | -0.24887 | -0.16449 | 0.07782 | -0.004578 | 0.050354 | 0.068665 | 0.050354 | -0.14648 | -0.036621 | 0.045776 | -0.068359 | -0.24246 | -0.040588 | -0.13886 | -0.13992 | -0.013733 | 0.054932 | -0.041199 | -0.027466 | -0.013733 | -0.12817 | -0.064087 | 0.073242 | -0.013733 | -0.054932
830.5156 | 0.045776 | 0.45715 | -0.44861 | -0.19333 | -0.15808 | -0.24674 | -0.16449 | -0.027466 | -0.16479 | -0.022888 | -0.041199 | -0.054932 | -0.045776 | 0.050354 | 0.045776 | -0.074768 | -0.26276 | -0.041656 | -0.14847 | -0.12283 | -0.10986 | -0.082397 | -0.14648 | -0.091553 | -0.073242 | -0.059509 | 0.009155 | -0.073242 | 0.036621 | -0.032043
832.25 | 0.030518 | 0.48599 | -0.4657 | -0.20401 | -0.16769 | -0.29266 | -0.16876 | 0.050354 | -0.004578 | 0.054932 | 0.022888 | -0.068665 | -0.09613 | 0.022888 | 0.045776 | -0.093994 | -0.25421 | -0.058746 | -0.15167 | -0.12497 | 0.059509 | 0.15564 | 0.022888 | -0.10529 | -0.07782 | -0.1236 | -0.050354 | 0.064087 | 0.018311 | -0.059509
833.9219 | 0.045776 | 0.47211 | -0.46463 | -0.21683 | -0.16663 | -0.27878 | -0.16556 | 0.027466 | -0.045776 | 0.032043 | -0.009155 | -0.10071 | -0.073242 | 0.022888 | 0.030518 | -0.091858 | -0.26169 | -0.041656 | -0.15915 | -0.14206 | 0 | 0.09613 | -0.036621 | -0.11444 | -0.07782 | -0.091553 | -0.050354 | -0.013733 | 0.045776 | -0.036621
835.6719 | 0.045776 | 0.46783 | -0.45929 | -0.21255 | -0.16129 | -0.27237 | -0.16663 | 0.14191 | 0.059509 | 0.12817 | 0.082397 | -0.027466 | -0.10529 | -0.027466 | 0.045776 | -0.072632 | -0.27237 | -0.054474 | -0.15915 | -0.14099 | 0.041199 | 0.16937 | 0.032043 | -0.050354 | -0.041199 | -0.13275 | -0.068665 | 0.032043 | 0.013733 | -0.018311
837.4062 | 0.030518 | 0.44327 | -0.45822 | -0.2243 | -0.16556 | -0.25528 | -0.17197 | 0.09613 | -0.022888 | 0.045776 | 0.068665 | 0.064087 | -0.1236 | -0.032043 | 0.030518 | -0.061951 | -0.23605 | -0.037384 | -0.16022 | -0.14313 | -0.041199 | 0.045776 | -0.059509 | 0.004578 | 0.018311 | -0.1236 | -0.064087 | 0.054932 | 0.009155 | -0.041199
839.125 | 0.045776 | 0.46783 | -0.46463 | -0.1976 | -0.1709 | -0.2681 | -0.16663 | 0.068665 | -0.027466 | 0.086975 | -0.009155 | -0.15564 | -0.050354 | 0.050354 | 0.045776 | -0.076904 | -0.25635 | -0.053406 | -0.15274 | -0.13351 | 0.045776 | 0.091553 | -0.018311 | -0.16937 | -0.13275 | -0.073242 | 0 | -0.07782 | 0.054932 | -0.009155
840.8125 | 0.045776 | 0.47104 | -0.46997 | -0.20828 | -0.1442 | -0.2681 | -0.15595 | 0.15106 | 0.07782 | 0.14191 | 0.10529 | -0.027466 | -0.13733 | -0.036621 | 0.045776 | -0.087585 | -0.25101 | -0.044861 | -0.15381 | -0.14954 | 0.068665 | 0.20599 | 0.036621 | -0.064087 | -0.050354 | -0.13275 | -0.064087 | 0.013733 | 0.022888 | -0.045776
842.5469 | 0.061035 | 0.4689 | -0.45395 | -0.18799 | -0.15915 | -0.25955 | -0.16769 | 0.064087 | -0.045776 | 0.073242 | 0.004578 | -0.10986 | -0.045776 | 0.054932 | 0.076294 | -0.077972 | -0.25101 | -0.044861 | -0.13992 | -0.1474 | 0.036621 | 0.059509 | -0.032043 | -0.14191 | -0.14191 | -0.082397 | 0 | -0.027466 | 0.022888 | -0.004578
844.2812 | 0.045776 | 0.45929 | -0.45715 | -0.20615 | -0.15167 | -0.26596 | -0.16556 | 0.14648 | 0.073242 | 0.14191 | 0.10071 | -0.032043 | -0.1236 | -0.018311 | 0.045776 | -0.082245 | -0.26062 | -0.046997 | -0.14633 | -0.13672 | 0.068665 | 0.20599 | 0.032043 | -0.068665 | -0.064087 | -0.1236 | -0.073242 | 0.022888 | 0.032043 | -0.045776
845.9531 | 0.030518 | 0.44861 | -0.45715 | -0.21576 | -0.15915 | -0.25955 | -0.17731 | 0.082397 | -0.018311 | 0.045776 | 0.054932 | 0.022888 | -0.12817 | -0.032043 | 0.045776 | -0.072632 | -0.25101 | -0.040588 | -0.15274 | -0.13779 | -0.013733 | 0.068665 | -0.032043 | 0.004578 | 0.018311 | -0.13733 | -0.068665 | 0.027466 | 0.018311 | -0.045776
847.6875 | 0.045776 | 0.48172 | -0.46143 | -0.19867 | -0.1709 | -0.27771 | -0.16876 | 0.027466 | -0.050354 | 0.036621 | -0.013733 | -0.091553 | -0.073242 | 0.032043 | 0.045776 | -0.092926 | -0.25742 | -0.043793 | -0.15167 | -0.13886 | 0.009155 | 0.09613 | -0.027466 | -0.10071 | -0.091553 | -0.09613 | -0.018311 | -0.009155 | 0.041199 | -0.036621
849.4219 | 0.061035 | 0.45288 | -0.44968 | -0.1976 | -0.15701 | -0.23285 | -0.16022 | 0.086975 | -0.027466 | 0.054932 | 0.022888 | -0.013733 | -0.09613 | 0.013733 | 0.045776 | -0.074768 | -0.25635 | -0.042725 | -0.14847 | -0.14206 | -0.027466 | 0.009155 | -0.086975 | -0.064087 | -0.050354 | -0.091553 | -0.027466 | -0.068665 | 0.022888 | -0.009155
851.1094 | 0.091553 | 0.4657 | -0.45075 | -0.21362 | -0.16449 | -0.26169 | -0.16663 | 0.004578 | -0.10986 | -0.004578 | -0.068665 | -0.054932 | -0.059509 | 0.050354 | 0.061035 | -0.071564 | -0.25207 | -0.049133 | -0.14313 | -0.13565 | -0.045776 | -0.032043 | -0.11902 | -0.11902 | -0.10071 | -0.059509 | 0.009155 | -0.022888 | 0.032043 | -0.009155
852.7969 | 0.045776 | 0.45929 | -0.45609 | -0.22858 | -0.1709 | -0.27557 | -0.16342 | 0.032043 | -0.027466 | 0.054932 | 0.022888 | -0.07782 | -0.073242 | 0.032043 | 0.045776 | -0.092926 | -0.24246 | -0.044861 | -0.16556 | -0.13779 | 0.032043 | 0.11902 | -0.018311 | -0.10071 | -0.07782 | -0.10529 | -0.036621 | 0.022888 | 0.018311 | -0.041199
854.4688 | 0.015259 | 0.45609 | -0.44968 | -0.20721 | -0.16876 | -0.24994 | -0.16235 | 0.036621 | -0.054932 | 0.064087 | -0.009155 | -0.11902 | -0.050354 | 0.064087 | 0.045776 | -0.085449 | -0.25314 | -0.045929 | -0.14313 | -0.14847 | 0.022888 | 0.054932 | -0.041199 | -0.14648 | -0.12817 | -0.086975 | -0.009155 | -0.013733 | 0.032043 | -0.032043
856.1406 | 0.045776 | 0.45395 | -0.45288 | -0.20828 | -0.15701 | -0.25848 | -0.16129 | 0.032043 | -0.027466 | 0.09613 | -0.013733 | -0.14648 | -0.041199 | 0.068665 | 0.061035 | -0.083313 | -0.25742 | -0.037384 | -0.15167 | -0.14954 | 0.054932 | 0.091553 | -0.032043 | -0.16022 | -0.14191 | -0.086975 | -0.013733 | -0.068665 | 0.054932 | -0.018311
857.8125 | 0.045776 | 0.46677 | -0.44968 | -0.20615 | -0.1709 | -0.26489 | -0.16342 | 0.041199 | -0.032043 | 0.10071 | -0.004578 | -0.15106 | -0.036621 | 0.082397 | 0.030518 | -0.092926 | -0.25528 | -0.046997 | -0.14206 | -0.14206 | 0.045776 | 0.10071 | -0.032043 | -0.16479 | -0.16022 | -0.064087 | -0.013733 | -0.064087 | 0.041199 | -0.018311
859.5469 | 0.045776 | 0.4454 | -0.44968 | -0.20828 | -0.17517 | -0.23605 | -0.15488 | 0.09613 | 0.004578 | 0.09613 | 0.036621 | 0.004578 | -0.09613 | 0 | 0.061035 | -0.064087 | -0.2446 | -0.03952 | -0.1474 | -0.13992 | -0.022888 | 0.050354 | -0.054932 | -0.041199 | -0.059509 | -0.10071 | -0.032043 | 0.013733 | 0.009155 | -0.032043
861.2812 | 0.076294 | 0.4657 | -0.44968 | -0.21149 | -0.16235 | -0.25314 | -0.15595 | -0.018311 | -0.13275 | -0.013733 | -0.050354 | -0.041199 | -0.054932 | 0.068665 | 0.045776 | -0.066223 | -0.24674 | -0.038452 | -0.14847 | -0.13031 | -0.064087 | -0.054932 | -0.13733 | -0.09613 | -0.068665 | -0.059509 | -0.009155 | -0.027466 | 0.036621 | -0.018311
862.9531 | 0.030518 | 0.44754 | -0.46036 | -0.21149 | -0.16663 | -0.25528 | -0.1709 | -0.027466 | -0.14648 | -0.027466 | -0.045776 | -0.045776 | -0.050354 | 0.068665 | 0.045776 | -0.080109 | -0.25528 | -0.038452 | -0.14313 | -0.14099 | -0.082397 | -0.091553 | -0.15564 | -0.073242 | -0.086975 | -0.059509 | 0.022888 | -0.064087 | 0.032043 | -0.018311
864.6875 | 0.030518 | 0.47104 | -0.44434 | -0.21469 | -0.16876 | -0.26062 | -0.1741 | -0.018311 | -0.10986 | 0.009155 | -0.059509 | -0.073242 | -0.045776 | 0.068665 | 0.045776 | -0.076904 | -0.2478 | -0.046997 | -0.15381 | -0.13138 | -0.032043 | 0.004578 | -0.086975 | -0.14191 | -0.11444 | -0.059509 | 0.004578 | -0.022888 | 0.032043 | -0.036621
866.4375 | 0.045776 | 0.44968 | -0.44968 | -0.21576 | -0.15595 | -0.27237 | -0.17838 | 0.045776 | -0.009155 | 0.050354 | 0.054932 | 0.022888 | -0.13733 | -0.032043 | 0.045776 | -0.072632 | -0.24887 | -0.043793 | -0.16235 | -0.13672 | -0.009155 | 0.07782 | -0.036621 | -0.004578 | 0.013733 | -0.13733 | -0.068665 | 0.027466 | 0.004578 | -0.041199
868.1719 | 0.061035 | 0.45609 | -0.44754 | -0.19546 | -0.16556 | -0.25314 | -0.17624 | -0.041199 | -0.14191 | -0.041199 | -0.054932 | -0.036621 | -0.022888 | 0.068665 | 0.030518 | -0.068359 | -0.25101 | -0.045929 | -0.14847 | -0.14526 | -0.086975 | -0.073242 | -0.13733 | -0.073242 | -0.068665 | -0.082397 | -0.004578 | -0.027466 | 0.022888 | -0.004578
869.8438 | 0.061035 | 0.44113 | -0.46463 | -0.19974 | -0.16449 | -0.25528 | -0.16876 | 0.09613 | 0.009155 | 0.07782 | 0.045776 | -0.004578 | -0.091553 | 0.009155 | 0.061035 | -0.071564 | -0.25635 | -0.043793 | -0.14633 | -0.13672 | -0.018311 | 0.054932 | -0.050354 | -0.050354 | -0.050354 | -0.086975 | -0.045776 | 0.009155 | 0.022888 | -0.027466
871.5781 | 0.061035 | 0.45609 | -0.44327 | -0.21042 | -0.16235 | -0.25207 | -0.16129 | 0.009155 | -0.086975 | 0.041199 | -0.004578 | -0.022888 | -0.073242 | 0.041199 | 0.045776 | -0.072632 | -0.23926 | -0.050201 | -0.14206 | -0.12924 | -0.10529 | -0.059509 | -0.13733 | -0.073242 | -0.045776 | -0.07782 | -0.009155 | -0.082397 | 0.036621 | -0.018311
873.3125 | 0.030518 | 0.4657 | -0.46036 | -0.21683 | -0.17303 | -0.29587 | -0.16876 | 0.11444 | 0.10071 | 0.16022 | 0.10986 | -0.059509 | -0.11444 | 0.004578 | 0.045776 | -0.092926 | -0.25101 | -0.060883 | -0.16983 | -0.13992 | 0.09613 | 0.23346 | 0.064087 | -0.073242 | -0.064087 | -0.13275 | -0.07782 | 0.07782 | 0.013733 | -0.054932
874.9844 | 0.045776 | 0.47104 | -0.46249 | -0.20401 | -0.16342 | -0.28839 | -0.18906 | 0.032043 | -0.050354 | 0.064087 | 0 | -0.082397 | -0.07782 | 0.013733 | 0.045776 | -0.085449 | -0.26169 | -0.037384 | -0.16129 | -0.13565 | 0.013733 | 0.086975 | -0.050354 | -0.10529 | -0.09613 | -0.09613 | -0.032043 | -0.050354 | 0.059509 | -0.041199
876.7188 | 0.061035 | 0.49454 | -0.45715 | -0.20187 | -0.15915 | -0.28198 | -0.17303 | 0.11902 | 0.073242 | 0.10986 | 0.068665 | -0.064087 | -0.12817 | -0.004578 | 0.030518 | -0.083313 | -0.26062 | -0.049133 | -0.16022 | -0.13886 | 0.13733 | 0.2243 | 0.082397 | -0.07782 | -0.091553 | -0.14191 | -0.082397 | 0.10071 | 0.013733 | -0.050354
878.4531 | 0.061035 | 0.4454 | -0.44327 | -0.20508 | -0.15488 | -0.24033 | -0.16983 | 0.082397 | -0.032043 | 0.068665 | 0.022888 | -0.018311 | -0.082397 | 0.009155 | 0.061035 | -0.063019 | -0.25528 | -0.045929 | -0.13672 | -0.13672 | -0.036621 | -0.004578 | -0.10071 | -0.059509 | -0.064087 | -0.10071 | -0.013733 | -0.045776 | 0.036621 | -0.013733
880.1406 | 0.030518 | 0.45609 | -0.46249 | -0.20401 | -0.15701 | -0.25314 | -0.15808 | -0.013733 | -0.12817 | 0.004578 | -0.054932 | -0.054932 | -0.050354 | 0.091553 | 0.045776 | -0.0737 | -0.25101 | -0.043793 | -0.14313 | -0.14954 | -0.045776 | -0.018311 | -0.11444 | -0.10071 | -0.10071 | -0.068665 | 0.009155 | -0.009155 | 0.036621 | -0.027466
881.8125 | 0.045776 | 0.4422 | -0.45181 | -0.20615 | -0.16022 | -0.25421 | -0.17197 | 0.09613 | 0 | 0.054932 | 0.054932 | 0.050354 | -0.11444 | 0.004578 | 0.045776 | -0.072632 | -0.25101 | -0.043793 | -0.14954 | -0.1474 | -0.022888 | 0.059509 | -0.050354 | -0.050354 | -0.041199 | -0.11444 | -0.041199 | 0.073242 | -0.009155 | -0.045776
883.5469 | 0.045776 | 0.45609 | -0.45715 | -0.20935 | -0.16449 | -0.28519 | -0.17197 | 0.032043 | -0.054932 | 0.073242 | -0.013733 | -0.13733 | -0.059509 | 0.050354 | 0.045776 | -0.09613 | -0.2446 | -0.032043 | -0.15808 | -0.13245 | 0.036621 | 0.10071 | -0.032043 | -0.10071 | -0.09613 | -0.091553 | -0.036621 | -0.064087 | 0.086975 | -0.022888
885.2344 | 0.061035 | 0.45288 | -0.45395 | -0.19867 | -0.14633 | -0.24674 | -0.16769 | 0.022888 | -0.09613 | 0.022888 | -0.013733 | -0.032043 | -0.073242 | 0.036621 | 0.045776 | -0.065155 | -0.25955 | -0.040588 | -0.15488 | -0.13779 | -0.091553 | -0.059509 | -0.16022 | -0.050354 | -0.059509 | -0.086975 | 0 | -0.082397 | 0.027466 | -0.022888
886.9062 | 0.076294 | 0.45288 | -0.45395 | -0.2211 | -0.16556 | -0.27023 | -0.16235 | -0.041199 | -0.16022 | -0.027466 | -0.054932 | -0.036621 | -0.045776 | 0.07782 | 0.030518 | -0.068359 | -0.24994 | -0.023499 | -0.15274 | -0.14099 | -0.091553 | -0.07782 | -0.15564 | -0.07782 | -0.050354 | -0.054932 | 0.009155 | -0.045776 | 0.036621 | 0
888.6406 | 0.061035 | 0.46143 | -0.45502 | -0.21896 | -0.16129 | -0.27985 | -0.16983 | 0.07782 | 0.022888 | 0.10986 | 0.041199 | -0.064087 | -0.09613 | 0.013733 | 0.045776 | -0.081177 | -0.25314 | -0.044861 | -0.16769 | -0.13886 | 0.10986 | 0.19684 | 0.059509 | -0.086975 | -0.068665 | -0.13733 | -0.068665 | 0.082397 | 0.027466 | -0.059509
890.375 | 0.045776 | 0.44754 | -0.45715 | -0.22858 | -0.16769 | -0.25528 | -0.16663 | 0.064087 | -0.032043 | 0.050354 | 0.064087 | 0.032043 | -0.12817 | -0.022888 | 0.030518 | -0.063019 | -0.24246 | -0.037384 | -0.15381 | -0.15274 | -0.027466 | 0.054932 | -0.032043 | -0.004578 | 0.013733 | -0.14191 | -0.059509 | 0.07782 | 0.009155 | -0.041199
892.1094 | 0.030518 | 0.45715 | -0.44754 | -0.20187 | -0.16342 | -0.26489 | -0.16449 | -0.018311 | -0.12817 | 0 | -0.045776 | -0.041199 | -0.036621 | 0.07782 | 0.045776 | -0.075836 | -0.25207 | -0.029907 | -0.15381 | -0.13779 | -0.054932 | -0.045776 | -0.13275 | -0.10071 | -0.09613 | -0.082397 | 0 | -0.013733 | 0.032043 | -0.041199
893.7969 | 0.061035 | 0.46463 | -0.45181 | -0.20401 | -0.16556 | -0.27451 | -0.16556 | 0.045776 | -0.032043 | 0.073242 | 0.009155 | -0.13733 | -0.054932 | 0.059509 | 0.061035 | -0.072632 | -0.26169 | -0.040588 | -0.15701 | -0.13565 | 0.027466 | 0.059509 | -0.022888 | -0.13733 | -0.14648 | -0.068665 | -0.013733 | -0.022888 | 0.032043 | -0.027466
895.5469 | 0.045776 | 0.46783 | -0.47531 | -0.21896 | -0.14954 | -0.28519 | -0.1741 | 0.13275 | 0.10071 | 0.13733 | 0.082397 | -0.050354 | -0.13275 | -0.018311 | 0.045776 | -0.089722 | -0.25742 | -0.053406 | -0.16342 | -0.14206 | 0.10529 | 0.23346 | 0.068665 | -0.086975 | -0.068665 | -0.13275 | -0.059509 | 0.068665 | 0.022888 | -0.064087
897.2188 | 0.030518 | 0.46463 | -0.45822 | -0.20081 | -0.16556 | -0.25528 | -0.17838 | -0.004578 | -0.10071 | 0.041199 | -0.036621 | -0.09613 | -0.036621 | 0.07782 | 0.045776 | -0.067291 | -0.26169 | -0.043793 | -0.14847 | -0.13672 | 0 | 0.045776 | -0.041199 | -0.13733 | -0.14191 | -0.059509 | -0.018311 | -0.018311 | 0.027466 | -0.022888
898.8906 | 0.076294 | 0.47745 | -0.46249 | -0.20187 | -0.15595 | -0.27878 | -0.16876 | 0.027466 | -0.022888 | 0.064087 | -0.013733 | -0.09613 | -0.064087 | 0.045776 | 0.045776 | -0.083313 | -0.25207 | -0.055542 | -0.15595 | -0.13565 | 0.041199 | 0.073242 | -0.045776 | -0.09613 | -0.10071 | -0.10529 | -0.022888 | -0.050354 | 0.07782 | -0.009155
900.625 | 0.045776 | 0.4422 | -0.46249 | -0.20935 | -0.15488 | -0.25207 | -0.16342 | 0.07782 | -0.041199 | 0.032043 | 0.059509 | 0.041199 | -0.11902 | -0.009155 | 0.061035 | -0.080109 | -0.24246 | -0.038452 | -0.15274 | -0.1442 | -0.041199 | 0.041199 | -0.054932 | 0 | -0.004578 | -0.11902 | -0.050354 | 0.073242 | -0.004578 | -0.059509
902.3594 | 0.030518 | 0.45715 | -0.45929 | -0.21896 | -0.15808 | -0.26169 | -0.1709 | 0.082397 | -0.022888 | 0.050354 | 0.050354 | 0.054932 | -0.13275 | -0.022888 | 0.045776 | -0.071564 | -0.25314 | -0.03952 | -0.15274 | -0.14206 | -0.013733 | 0.064087 | -0.050354 | 0.004578 | 0 | -0.13275 | -0.059509 | 0.045776 | 0.013733 | -0.027466
904.0938 | 0.030518 | 0.44647 | -0.45609 | -0.20294 | -0.17197 | -0.23605 | -0.16769 | 0.091553 | 0.004578 | 0.086975 | 0.045776 | -0.018311 | -0.086975 | 0.013733 | 0.030518 | -0.071564 | -0.25207 | -0.042725 | -0.1474 | -0.13992 | -0.018311 | 0.027466 | -0.050354 | -0.068665 | -0.036621 | -0.10071 | -0.036621 | -0.004578 | 0.004578 | -0.022888
905.7656 | 0.015259 | 0.43579 | -0.4454 | -0.20615 | -0.15701 | -0.2478 | -0.16556 | -0.027466 | -0.13733 | -0.009155 | -0.036621 | -0.027466 | -0.064087 | 0.073242 | 0.030518 | -0.072632 | -0.2446 | -0.049133 | -0.15488 | -0.13779 | -0.12817 | -0.091553 | -0.15564 | -0.091553 | -0.054932 | -0.07782 | 0.018311 | -0.068665 | 0.041199 | 0
907.4844 | 0.061035 | 0.47318 | -0.4422 | -0.19653 | -0.15488 | -0.26276 | -0.16769 | 0.027466 | -0.041199 | 0.059509 | -0.009155 | -0.10986 | -0.036621 | 0.064087 | 0.076294 | -0.083313 | -0.25314 | -0.035248 | -0.15167 | -0.13351 | 0.027466 | 0.059509 | -0.018311 | -0.13733 | -0.13733 | -0.07782 | 0.013733 | -0.036621 | 0.032043 | -0.022888
909.2031 | 0.045776 | 0.46997 | -0.45075 | -0.21255 | -0.16663 | -0.27878 | -0.16769 | 0.036621 | -0.041199 | 0.059509 | 0 | -0.091553 | -0.073242 | 0.027466 | 0.030518 | -0.089722 | -0.25101 | -0.040588 | -0.16663 | -0.13351 | 0.036621 | 0.091553 | -0.032043 | -0.10529 | -0.09613 | -0.091553 | -0.009155 | -0.064087 | 0.054932 | -0.045776
910.9531 | 0.061035 | 0.45395 | -0.45822 | -0.20615 | -0.15595 | -0.26703 | -0.16342 | 0.07782 | -0.022888 | 0.036621 | 0.054932 | 0.032043 | -0.11444 | -0.013733 | 0.061035 | -0.066223 | -0.25528 | -0.043793 | -0.1506 | -0.1506 | -0.022888 | 0.059509 | -0.054932 | -0.004578 | -0.004578 | -0.11902 | -0.068665 | 0.073242 | -0.004578 | -0.041199
912.6406 | 0.015259 | 0.4657 | -0.45822 | -0.20828 | -0.15488 | -0.28519 | -0.16342 | 0.12817 | 0.064087 | 0.12817 | 0.091553 | -0.027466 | -0.12817 | -0.013733 | 0.061035 | -0.074768 | -0.25421 | -0.053406 | -0.16556 | -0.13992 | 0.059509 | 0.19226 | 0.022888 | -0.050354 | -0.032043 | -0.13275 | -0.082397 | 0.027466 | 0.041199 | -0.045776
914.3125 | 0.030518 | 0.44647 | -0.45075 | -0.21149 | -0.15381 | -0.26916 | -0.17197 | 0.11902 | 0.013733 | 0.086975 | 0.073242 | 0.018311 | -0.13733 | -0.022888 | 0.030518 | -0.074768 | -0.2446 | -0.040588 | -0.17624 | -0.13779 | 0.004578 | 0.091553 | -0.027466 | -0.004578 | -0.004578 | -0.10986 | -0.059509 | 0.009155 | 0.022888 | -0.036621
915.9844 | 0.045776 | 0.45609 | -0.45288 | -0.21362 | -0.16342 | -0.26916 | -0.16556 | 0.13733 | 0.064087 | 0.14191 | 0.10529 | -0.027466 | -0.13275 | -0.018311 | 0.045776 | -0.093994 | -0.25314 | -0.048065 | -0.15808 | -0.13992 | 0.068665 | 0.19226 | 0.032043 | -0.068665 | -0.054932 | -0.14191 | -0.064087 | 0.022888 | 0.022888 | -0.050354
917.7188 | 0.045776 | 0.43793 | -0.45075 | -0.21469 | -0.16342 | -0.25207 | -0.16342 | 0.07782 | -0.045776 | 0.022888 | 0.045776 | 0.045776 | -0.11902 | -0.018311 | 0.045776 | -0.067291 | -0.24567 | -0.040588 | -0.1506 | -0.1442 | -0.032043 | 0.064087 | -0.036621 | 0 | 0.009155 | -0.12817 | -0.050354 | 0.073242 | -0.009155 | -0.045776
919.4531 | 0.030518 | 0.43366 | -0.45609 | -0.19974 | -0.1506 | -0.25421 | -0.1709 | 0.091553 | -0.022888 | 0.059509 | 0.045776 | 0 | -0.091553 | 0.004578 | 0.061035 | -0.066223 | -0.25528 | -0.029907 | -0.14847 | -0.14206 | -0.018311 | 0.050354 | -0.050354 | -0.054932 | -0.045776 | -0.11444 | -0.027466 | 0.050354 | 0.004578 | -0.036621
921.1875 | 0.030518 | 0.45822 | -0.47318 | -0.21149 | -0.15274 | -0.28305 | -0.16983 | 0.14191 | 0.091553 | 0.15564 | 0.091553 | -0.027466 | -0.1236 | -0.013733 | 0.061035 | -0.088654 | -0.26062 | -0.038452 | -0.16449 | -0.1442 | 0.11902 | 0.24719 | 0.059509 | -0.073242 | -0.07782 | -0.14191 | -0.054932 | 0.073242 | 0.013733 | -0.064087
922.875 | 0.045776 | 0.48386 | -0.45715 | -0.19546 | -0.15488 | -0.28732 | -0.18478 | 0.054932 | -0.045776 | 0.064087 | -0.004578 | -0.086975 | -0.054932 | 0.032043 | 0.030518 | -0.082245 | -0.25207 | -0.040588 | -0.1506 | -0.13458 | 0.032043 | 0.10529 | -0.041199 | -0.091553 | -0.09613 | -0.09613 | -0.027466 | -0.041199 | 0.064087 | -0.045776
924.5469 | 0.061035 | 0.439 | -0.44968 | -0.1976 | -0.16663 | -0.24887 | -0.16663 | 0.086975 | -0.022888 | 0.064087 | 0.036621 | -0.009155 | -0.10986 | 0.032043 | 0.030518 | -0.057678 | -0.24887 | -0.043793 | -0.14526 | -0.1474 | -0.032043 | 0.009155 | -0.082397 | -0.050354 | -0.054932 | -0.10071 | -0.013733 | -0.045776 | 0.022888 | -0.032043
926.2969 | 0.061035 | 0.45288 | -0.45502 | -0.21149 | -0.16449 | -0.25101 | -0.15701 | -0.009155 | -0.15564 | -0.022888 | -0.045776 | -0.050354 | -0.027466 | 0.068665 | 0.030518 | -0.079041 | -0.26489 | -0.041656 | -0.14099 | -0.13351 | -0.068665 | -0.064087 | -0.12817 | -0.068665 | -0.059509 | -0.059509 | 0.009155 | -0.045776 | 0.036621 | -0.004578
927.9688 | 0.045776 | 0.43579 | -0.44754 | -0.21255 | -0.16556 | -0.25742 | -0.15808 | 0.09613 | 0.004578 | 0.073242 | 0.054932 | 0 | -0.10071 | 0 | 0.045776 | -0.075836 | -0.23819 | -0.035248 | -0.1442 | -0.13779 | 0.013733 | 0.041199 | -0.045776 | -0.059509 | -0.036621 | -0.086975 | -0.036621 | 0.032043 | 0 | -0.018311
929.6406 | 0.030518 | 0.45075 | -0.45822 | -0.20615 | -0.17624 | -0.2713 | -0.1709 | 0.10529 | 0.036621 | 0.10071 | 0.091553 | 0.013733 | -0.14191 | -0.018311 | 0.061035 | -0.072632 | -0.24139 | -0.042725 | -0.16342 | -0.13351 | 0.004578 | 0.11444 | -0.022888 | -0.009155 | -0.004578 | -0.14191 | -0.064087 | 0.022888 | 0.027466 | -0.054932
931.3906 | 0.045776 | 0.46677 | -0.44434 | -0.21469 | -0.15701 | -0.27237 | -0.16983 | 0.041199 | -0.013733 | 0.11444 | -0.013733 | -0.12817 | -0.027466 | 0.068665 | 0.030518 | -0.093994 | -0.25314 | -0.046997 | -0.16129 | -0.13031 | 0.059509 | 0.09613 | -0.041199 | -0.14648 | -0.14191 | -0.050354 | -0.009155 | -0.064087 | 0.068665 | -0.004578
933.125 | 0.061035 | 0.45502 | -0.439 | -0.20935 | -0.15488 | -0.26596 | -0.15915 | 0.091553 | 0 | 0.082397 | 0.054932 | -0.009155 | -0.10986 | 0.004578 | 0.061035 | -0.063019 | -0.25528 | -0.032043 | -0.14847 | -0.13992 | 0.009155 | 0.059509 | -0.036621 | -0.050354 | -0.045776 | -0.10529 | -0.045776 | 0.041199 | -0.022888 | -0.032043
934.8125 | 0.045776 | 0.42938 | -0.43579 | -0.2179 | -0.17303 | -0.2478 | -0.15808 | -0.041199 | -0.13733 | -0.009155 | -0.036621 | -0.036621 | -0.059509 | 0.064087 | 0.045776 | -0.058746 | -0.24674 | -0.040588 | -0.14847 | -0.13672 | -0.12817 | -0.07782 | -0.17395 | -0.068665 | -0.068665 | -0.07782 | 0.013733 | -0.07782 | 0.036621 | -0.013733
936.5469 | 0.045776 | 0.45395 | -0.46143 | -0.2211 | -0.1506 | -0.2713 | -0.16876 | 0.10529 | 0.036621 | 0.10986 | 0.091553 | 0.027466 | -0.14191 | -0.018311 | 0.061035 | -0.077972 | -0.24674 | -0.040588 | -0.15701 | -0.13565 | 0.013733 | 0.10071 | -0.041199 | 0.009155 | 0.004578 | -0.1236 | -0.059509 | 0.045776 | 0.036621 | -0.032043
938.2812 | 0.061035 | 0.45715 | -0.46249 | -0.21042 | -0.15915 | -0.27344 | -0.17838 | 0.1236 | 0.07782 | 0.12817 | 0.10529 | -0.022888 | -0.11902 | -0.018311 | 0.030518 | -0.083313 | -0.25421 | -0.049133 | -0.16235 | -0.13886 | 0.082397 | 0.21515 | 0.018311 | -0.059509 | -0.050354 | -0.12817 | -0.059509 | 0.041199 | 0.032043 | -0.054932
939.9531 | 0.045776 | 0.46677 | -0.46783 | -0.20508 | -0.16022 | -0.2713 | -0.1741 | 0.032043 | -0.054932 | 0.054932 | -0.032043 | -0.1236 | -0.022888 | 0.086975 | 0.076294 | -0.086517 | -0.25101 | -0.042725 | -0.15488 | -0.14313 | 0.045776 | 0.07782 | -0.041199 | -0.13733 | -0.10986 | -0.07782 | -0.013733 | -0.064087 | 0.068665 | -0.009155
941.6875 | 0.061035 | 0.44647 | -0.4454 | -0.1976 | -0.15274 | -0.24246 | -0.16449 | 0.064087 | -0.050354 | 0.050354 | 0.009155 | -0.004578 | -0.091553 | 0.027466 | 0.061035 | -0.054474 | -0.22217 | -0.042725 | -0.15381 | -0.14313 | -0.064087 | -0.032043 | -0.10071 | -0.045776 | -0.041199 | -0.07782 | 0 | -0.059509 | 0.054932 | 0
943.4219 | 0.045776 | 0.45715 | -0.45609 | -0.20615 | -0.15915 | -0.2681 | -0.16022 | 0.045776 | -0.027466 | 0.068665 | 0.022888 | -0.10986 | -0.041199 | 0.064087 | 0.030518 | -0.085449 | -0.24353 | -0.035248 | -0.15808 | -0.13565 | 0.027466 | 0.054932 | -0.041199 | -0.14191 | -0.13275 | -0.050354 | 0.004578 | -0.027466 | 0.032043 | -0.022888
945.1562 | 0.061035 | 0.46463 | -0.4657 | -0.22003 | -0.16663 | -0.28519 | -0.17838 | 0.013733 | -0.036621 | 0.041199 | -0.004578 | -0.082397 | -0.07782 | 0.036621 | 0.061035 | -0.088654 | -0.24567 | -0.040588 | -0.16449 | -0.1442 | 0.013733 | 0.091553 | -0.041199 | -0.091553 | -0.09613 | -0.082397 | -0.013733 | -0.013733 | 0.064087 | -0.041199
946.8438 | 0.045776 | 0.46036 | -0.46036 | -0.20508 | -0.15915 | -0.25101 | -0.17624 | 0.07782 | -0.022888 | 0.045776 | 0.041199 | 0.050354 | -0.1236 | -0.009155 | 0.076294 | -0.077972 | -0.25528 | -0.045929 | -0.15167 | -0.13779 | -0.009155 | 0.082397 | -0.036621 | 0.013733 | 0.009155 | -0.1236 | -0.064087 | 0.032043 | 0.022888 | -0.036621
948.5781 | 0.045776 | 0.45929 | -0.45181 | -0.21149 | -0.15488 | -0.26916 | -0.17838 | 0.064087 | -0.018311 | 0.09613 | -0.004578 | -0.11902 | -0.041199 | 0.059509 | 0.061035 | -0.085449 | -0.2681 | -0.049133 | -0.15274 | -0.14206 | 0.036621 | 0.064087 | -0.045776 | -0.12817 | -0.13733 | -0.054932 | 0.013733 | -0.082397 | 0.059509 | -0.009155
950.3125 | 0.061035 | 0.46249 | -0.46677 | -0.20828 | -0.14313 | -0.27771 | -0.16983 | 0.027466 | -0.050354 | 0.059509 | 0.013733 | -0.054932 | -0.07782 | 0.032043 | 0.045776 | -0.085449 | -0.25101 | -0.048065 | -0.16235 | -0.1442 | 0.022888 | 0.10529 | -0.022888 | -0.091553 | -0.091553 | -0.10071 | -0.027466 | 0.032043 | 0.041199 | -0.032043
951.9844 | 0.045776 | 0.45288 | -0.45609 | -0.1944 | -0.1474 | -0.25101 | -0.16556 | 0.050354 | -0.041199 | 0.073242 | 0.018311 | -0.11902 | -0.027466 | 0.054932 | 0.045776 | -0.0737 | -0.26703 | -0.043793 | -0.13886 | -0.13992 | 0.022888 | 0.054932 | -0.027466 | -0.14648 | -0.13733 | -0.082397 | 0.004578 | -0.013733 | 0.032043 | -0.009155
953.7188 | 0.045776 | 0.45181 | -0.47104 | -0.20615 | -0.16663 | -0.27985 | -0.17944 | 0.10529 | 0.032043 | 0.091553 | 0.050354 | -0.045776 | -0.10529 | 0.013733 | 0.061035 | -0.081177 | -0.25635 | -0.048065 | -0.16235 | -0.14633 | 0.10071 | 0.19226 | 0.054932 | -0.091553 | -0.07782 | -0.12817 | -0.059509 | 0.082397 | 0.018311 | -0.073242
955.4688 | 0.030518 | 0.46356 | -0.46997 | -0.20828 | -0.16129 | -0.28091 | -0.17303 | 0.086975 | -0.004578 | 0.068665 | 0.036621 | -0.054932 | -0.082397 | 0.013733 | 0.045776 | -0.082245 | -0.25742 | -0.045929 | -0.14847 | -0.14526 | 0.091553 | 0.15564 | 0.013733 | -0.086975 | -0.064087 | -0.11444 | -0.027466 | 0.07782 | 0.013733 | -0.064087
957.2031 | 0.061035 | 0.4657 | -0.45288 | -0.19119 | -0.15274 | -0.23605 | -0.17731 | 0.086975 | -0.064087 | 0.045776 | 0.018311 | 0.009155 | -0.09613 | 0.027466 | 0.045776 | -0.069427 | -0.2446 | -0.03418 | -0.13779 | -0.14313 | -0.054932 | -0.009155 | -0.11444 | -0.050354 | -0.054932 | -0.09613 | -0.013733 | -0.064087 | 0.036621 | -0.009155
958.875 | 0.030518 | 0.45822 | -0.47318 | -0.20615 | -0.16129 | -0.25742 | -0.16556 | 0.073242 | -0.036621 | 0.086975 | 0.018311 | -0.09613 | -0.050354 | 0.050354 | 0.030518 | -0.074768 | -0.26062 | -0.053406 | -0.1474 | -0.14206 | 0.022888 | 0.054932 | -0.045776 | -0.13733 | -0.13733 | -0.068665 | 0 | -0.036621 | 0.027466 | -0.022888
960.5469 | 0.045776 | 0.44968 | -0.44113 | -0.21576 | -0.15915 | -0.24567 | -0.15701 | 0.1236 | -0.004578 | 0.068665 | 0.045776 | 0.018311 | -0.11444 | -0.004578 | 0.030518 | -0.060883 | -0.24674 | -0.048065 | -0.15381 | -0.13458 | -0.022888 | 0.022888 | -0.050354 | -0.045776 | -0.050354 | -0.086975 | -0.036621 | -0.018311 | 0.022888 | -0.022888
962.2969 | 0.061035 | 0.47638 | -0.46249 | -0.20828 | -0.15488 | -0.27451 | -0.16022 | 0.059509 | 0.004578 | 0.086975 | -0.013733 | -0.10986 | -0.064087 | 0.050354 | 0.015259 | -0.091858 | -0.25207 | -0.049133 | -0.15167 | -0.13458 | 0.022888 | 0.059509 | -0.054932 | -0.15564 | -0.14648 | -0.050354 | 0.018311 | -0.050354 | 0.073242 | -0.009155
963.9688 | 0.045776 | 0.44434 | -0.47104 | -0.22324 | -0.15701 | -0.25848 | -0.16769 | 0.07782 | -0.022888 | 0.036621 | 0.036621 | 0.054932 | -0.11902 | -0.018311 | 0.030518 | -0.061951 | -0.25207 | -0.035248 | -0.15701 | -0.14633 | -0.018311 | 0.059509 | -0.054932 | 0.018311 | 0.045776 | -0.14191 | -0.050354 | 0.045776 | 0.032043 | -0.041199
965.7031 | 0.076294 | 0.45715 | -0.44327 | -0.20721 | -0.16129 | -0.2478 | -0.16129 | -0.009155 | -0.13733 | -0.009155 | -0.027466 | -0.022888 | -0.068665 | 0.073242 | 0.076294 | -0.070496 | -0.26276 | -0.035248 | -0.1506 | -0.13351 | -0.10529 | -0.073242 | -0.15106 | -0.059509 | -0.059509 | -0.045776 | 0.013733 | -0.064087 | 0.050354 | -0.013733
967.4531 | 0.045776 | 0.45609 | -0.45181 | -0.21896 | -0.15274 | -0.28091 | -0.18051 | 0.13733 | 0.086975 | 0.15564 | 0.09613 | -0.045776 | -0.11902 | -0.027466 | 0.061035 | -0.091858 | -0.24139 | -0.050201 | -0.16342 | -0.13779 | 0.082397 | 0.21973 | 0.059509 | -0.068665 | -0.054932 | -0.14191 | -0.064087 | 0.041199 | 0.018311 | -0.050354
969.1719 | 0.061035 | 0.44647 | -0.46143 | -0.22217 | -0.16769 | -0.27664 | -0.1741 | 0.14648 | 0.059509 | 0.1236 | 0.10071 | -0.045776 | -0.10529 | -0.009155 | 0.061035 | -0.070496 | -0.24994 | -0.043793 | -0.15701 | -0.13992 | 0.054932 | 0.17853 | 0.009155 | -0.036621 | -0.018311 | -0.13275 | -0.068665 | 0.036621 | 0.027466 | -0.036621
970.8438 | 0.061035 | 0.45181 | -0.44647 | -0.20935 | -0.17624 | -0.24246 | -0.16876 | 0.11444 | -0.009155 | 0.073242 | 0.041199 | -0.009155 | -0.09613 | 0.004578 | 0.045776 | -0.068359 | -0.24887 | -0.03952 | -0.14633 | -0.1474 | -0.009155 | 0.018311 | -0.068665 | -0.059509 | -0.050354 | -0.091553 | -0.018311 | -0.009155 | 0.022888 | -0.018311
972.5781 | 0.030518 | 0.44434 | -0.45181 | -0.18692 | -0.16235 | -0.25421 | -0.16342 | 0.036621 | -0.086975 | 0.022888 | -0.013733 | -0.009155 | -0.091553 | 0.045776 | 0.045776 | -0.058746 | -0.24567 | -0.033112 | -0.1442 | -0.13351 | -0.082397 | -0.059509 | -0.14191 | -0.045776 | -0.045776 | -0.073242 | -0.009155 | -0.073242 | 0.027466 | -0.013733
974.3125 | 0.045776 | 0.44754 | -0.45395 | -0.21042 | -0.17197 | -0.25101 | -0.16983 | 0.073242 | -0.036621 | 0.054932 | 0.032043 | -0.004578 | -0.086975 | 0.004578 | 0.061035 | -0.064087 | -0.25314 | -0.041656 | -0.14954 | -0.13779 | -0.032043 | 0.009155 | -0.082397 | -0.059509 | -0.041199 | -0.10071 | -0.018311 | -0.054932 | 0.032043 | 0.004578
975.9844 | 0.045776 | 0.44754 | -0.4454 | -0.20935 | -0.15915 | -0.25421 | -0.16342 | 0.068665 | -0.027466 | 0.073242 | 0.032043 | -0.013733 | -0.082397 | 0.036621 | 0.076294 | -0.074768 | -0.2446 | -0.03418 | -0.1506 | -0.13779 | -0.050354 | -0.004578 | -0.07782 | -0.073242 | -0.032043 | -0.10071 | -0.018311 | -0.054932 | 0.013733 | -0.027466
977.7188 | 0.045776 | 0.47745 | -0.45929 | -0.21149 | -0.15274 | -0.29907 | -0.17624 | 0.027466 | -0.036621 | 0.059509 | -0.004578 | -0.091553 | -0.07782 | 0.027466 | 0.045776 | -0.10147 | -0.26276 | -0.044861 | -0.16983 | -0.13031 | 0.018311 | 0.091553 | -0.032043 | -0.11444 | -0.068665 | -0.082397 | -0.013733 | -0.050354 | 0.064087 | -0.009155
979.4531 | 0.061035 | 0.45715 | -0.45609 | -0.20401 | -0.15595 | -0.25635 | -0.17197 | 0.004578 | -0.1236 | -0.009155 | -0.032043 | -0.013733 | -0.054932 | 0.059509 | 0.061035 | -0.065155 | -0.25635 | -0.03952 | -0.1506 | -0.1506 | -0.11444 | -0.07782 | -0.14648 | -0.059509 | -0.064087 | -0.050354 | 0.013733 | -0.086975 | 0.032043 | -0.013733
981.2031 | 0.045776 | 0.45075 | -0.44968 | -0.21042 | -0.16983 | -0.2681 | -0.16235 | -0.009155 | -0.13275 | -0.004578 | -0.045776 | -0.045776 | -0.041199 | 0.059509 | 0.045776 | -0.0737 | -0.24033 | -0.046997 | -0.15167 | -0.14206 | -0.054932 | -0.022888 | -0.09613 | -0.10071 | -0.09613 | -0.050354 | 0.013733 | -0.022888 | 0.032043 | -0.018311
982.9062 | 0.061035 | 0.45929 | -0.45288 | -0.20187 | -0.1506 | -0.24674 | -0.17197 | -0.022888 | -0.16022 | -0.013733 | -0.041199 | -0.022888 | -0.036621 | 0.068665 | 0.061035 | -0.065155 | -0.25742 | -0.03952 | -0.15488 | -0.13138 | -0.10071 | -0.07782 | -0.15564 | -0.068665 | -0.073242 | -0.073242 | 0.004578 | -0.068665 | 0.050354 | -0.009155
984.625 | 0.030518 | 0.45075 | -0.44647 | -0.21149 | -0.15595 | -0.25314 | -0.16876 | -0.022888 | -0.1236 | 0.004578 | -0.027466 | -0.022888 | -0.064087 | 0.059509 | 0.045776 | -0.065155 | -0.25101 | -0.041656 | -0.15488 | -0.13672 | -0.11444 | -0.082397 | -0.16479 | -0.064087 | -0.054932 | -0.054932 | 0.022888 | -0.073242 | 0.032043 | -0.009155
986.3125 | 0.061035 | 0.46677 | -0.45715 | -0.20401 | -0.15595 | -0.27451 | -0.16769 | 0.022888 | -0.027466 | 0.064087 | -0.004578 | -0.14191 | -0.041199 | 0.068665 | 0.045776 | -0.09079 | -0.25742 | -0.036316 | -0.15808 | -0.14206 | 0.013733 | 0.082397 | -0.022888 | -0.16022 | -0.13733 | -0.054932 | 0.013733 | -0.064087 | 0.054932 | -0.009155
987.9844 | 0.030518 | 0.45288 | -0.44968 | -0.21576 | -0.15915 | -0.26169 | -0.1741 | 0.068665 | -0.027466 | 0.059509 | 0.073242 | 0.045776 | -0.1236 | -0.022888 | 0.045776 | -0.065155 | -0.25742 | -0.040588 | -0.15701 | -0.15381 | -0.036621 | 0.050354 | -0.045776 | -0.009155 | -0.004578 | -0.12817 | -0.054932 | 0.064087 | -0.018311 | -0.036621
989.7188 | 0.061035 | 0.45502 | -0.45075 | -0.21255 | -0.15167 | -0.25742 | -0.16449 | 0.082397 | -0.018311 | 0.054932 | 0.068665 | 0.045776 | -0.13733 | 0.009155 | 0.061035 | -0.0737 | -0.2446 | -0.041656 | -0.16449 | -0.13992 | -0.041199 | 0.068665 | -0.050354 | -0.013733 | 0 | -0.1236 | -0.054932 | 0.082397 | -0.004578 | -0.064087
991.4688 | 0.045776 | 0.44113 | -0.45822 | -0.19974 | -0.15274 | -0.25955 | -0.16235 | 0.091553 | 0.004578 | 0.054932 | 0.07782 | 0.059509 | -0.12817 | -0.018311 | 0.061035 | -0.071564 | -0.26489 | -0.038452 | -0.15808 | -0.13458 | -0.050354 | 0.054932 | -0.050354 | -0.018311 | -0.032043 | -0.086975 | -0.013733 | 0.064087 | -0.022888 | -0.041199
993.2031 | 0.061035 | 0.46143 | -0.45395 | -0.19012 | -0.17197 | -0.26276 | -0.16769 | -0.022888 | -0.13733 | -0.018311 | -0.041199 | -0.036621 | -0.027466 | 0.068665 | 0.030518 | -0.066223 | -0.26169 | -0.03952 | -0.15701 | -0.13886 | -0.082397 | -0.064087 | -0.1236 | -0.064087 | -0.064087 | -0.064087 | 0.004578 | -0.004578 | 0.036621 | -0.004578
994.875 | 0.061035 | 0.48172 | -0.44968 | -0.20828 | -0.15701 | -0.27451 | -0.18051 | 0.027466 | -0.050354 | 0.068665 | 0.004578 | -0.13275 | -0.041199 | 0.086975 | 0.045776 | -0.082245 | -0.25635 | -0.044861 | -0.16235 | -0.13886 | 0.009155 | 0.073242 | -0.027466 | -0.16022 | -0.15564 | -0.050354 | 0.018311 | -0.050354 | 0.050354 | -0.018311
996.625 | 0.030518 | 0.47424 | -0.45715 | -0.2211 | -0.16235 | -0.28732 | -0.1741 | 0.004578 | -0.050354 | 0.041199 | -0.004578 | -0.07782 | -0.068665 | 0.027466 | 0.030518 | -0.091858 | -0.25635 | -0.055542 | -0.1709 | -0.12924 | 0 | 0.10529 | -0.018311 | -0.086975 | -0.068665 | -0.073242 | -0.027466 | -0.004578 | 0.054932 | -0.050354
998.3594 | 0.045776 | 0.45181 | -0.45822 | -0.22217 | -0.14633 | -0.27985 | -0.17838 | 0.14648 | 0.091553 | 0.13733 | 0.10071 | -0.041199 | -0.10071 | 0 | 0.045776 | -0.086517 | -0.2446 | -0.038452 | -0.16983 | -0.14954 | 0.10529 | 0.21057 | 0.073242 | -0.068665 | -0.059509 | -0.13733 | -0.054932 | 0.07782 | 0.018311 | -0.059509
1000.0156 | 0.045776 | 0.44968 | -0.45181 | -0.20081 | -0.16983 | -0.24033 | -0.15915 | -0.032043 | -0.15564 | -0.022888 | -0.041199 | -0.027466 | -0.050354 | 0.064087 | 0.015259 | -0.070496 | -0.25314 | -0.03952 | -0.14313 | -0.1506 | -0.10529 | -0.09613 | -0.14648 | -0.082397 | -0.064087 | -0.054932 | 0.013733 | -0.059509 | 0.045776 | -0.009155
1001.6875 | 0.030518 | 0.45395 | -0.46036 | -0.21683 | -0.15167 | -0.27451 | -0.16983 | 0.12817 | 0.073242 | 0.12817 | 0.10529 | -0.009155 | -0.11444 | -0.009155 | 0.045776 | -0.082245 | -0.25101 | -0.038452 | -0.16235 | -0.14313 | 0.073242 | 0.16937 | 0.022888 | -0.041199 | -0.018311 | -0.12817 | -0.059509 | 0.036621 | 0.036621 | -0.041199
1003.4219 | 0.030518 | 0.47104 | -0.46997 | -0.20721 | -0.16876 | -0.27664 | -0.17944 | 0.032043 | -0.045776 | 0.050354 | 0.009155 | -0.054932 | -0.059509 | 0.027466 | 0.061035 | -0.080109 | -0.25955 | -0.048065 | -0.16342 | -0.14206 | 0.004578 | 0.10071 | -0.050354 | -0.091553 | -0.082397 | -0.086975 | -0.022888 | -0.022888 | 0.064087 | -0.032043
1005.0938 | 0.061035 | 0.45181 | -0.45395 | -0.21042 | -0.15808 | -0.2446 | -0.16449 | 0.10986 | -0.004578 | 0.07782 | 0.045776 | 0 | -0.091553 | 0.004578 | 0.030518 | -0.059814 | -0.25101 | -0.03418 | -0.14633 | -0.14633 | -0.022888 | 0.013733 | -0.059509 | -0.041199 | -0.027466 | -0.082397 | -0.027466 | -0.032043 | 0.027466 | -0.027466
1006.7656 | 0.045776 | 0.46143 | -0.46036 | -0.20294 | -0.15915 | -0.25528 | -0.16876 | -0.018311 | -0.14648 | -0.027466 | -0.050354 | -0.036621 | -0.045776 | 0.054932 | 0.045776 | -0.0737 | -0.25101 | -0.03952 | -0.14633 | -0.13351 | -0.086975 | -0.086975 | -0.16479 | -0.073242 | -0.064087 | -0.073242 | -0.004578 | -0.068665 | 0.059509 | 0.009155
1008.5 | 0.061035 | 0.45288 | -0.46356 | -0.1976 | -0.16129 | -0.26382 | -0.15915 | -0.027466 | -0.14191 | -0.022888 | -0.045776 | -0.032043 | -0.036621 | 0.068665 | 0.045776 | -0.0737 | -0.25207 | -0.041656 | -0.15488 | -0.14206 | -0.064087 | -0.050354 | -0.13275 | -0.068665 | -0.068665 | -0.064087 | 0.013733 | -0.022888 | 0.036621 | -0.009155
1010.1719 | 0.045776 | 0.45395 | -0.4657 | -0.20187 | -0.16342 | -0.25742 | -0.16235 | -0.022888 | -0.10529 | 0.004578 | -0.022888 | -0.059509 | -0.027466 | 0.054932 | 0.061035 | -0.079041 | -0.26596 | -0.049133 | -0.14954 | -0.13779 | -0.022888 | 0.009155 | -0.068665 | -0.12817 | -0.10529 | -0.059509 | -0.004578 | -0.009155 | 0.018311 | -0.018311
1011.8438 | 0.030518 | 0.43793 | -0.44968 | -0.21255 | -0.16449 | -0.25528 | -0.15915 | -0.009155 | -0.15106 | -0.018311 | -0.041199 | -0.013733 | -0.064087 | 0.054932 | 0.030518 | -0.058746 | -0.25421 | -0.03418 | -0.15488 | -0.1474 | -0.10529 | -0.091553 | -0.16479 | -0.059509 | -0.045776 | -0.073242 | 0.013733 | -0.059509 | 0.054932 | -0.032043
1013.5938 | 0.061035 | 0.44006 | -0.46249 | -0.21576 | -0.16235 | -0.26382 | -0.17624 | 0.07782 | -0.045776 | 0.027466 | 0.041199 | 0.059509 | -0.11902 | 0.004578 | 0.030518 | -0.061951 | -0.24139 | -0.049133 | -0.16022 | -0.13886 | -0.045776 | 0.050354 | -0.059509 | -0.018311 | 0.009155 | -0.10986 | -0.041199 | 0.07782 | 0.009155 | -0.045776
1015.3438 | 0.030518 | 0.45075 | -0.46036 | -0.21362 | -0.15915 | -0.26703 | -0.16663 | 0.068665 | -0.009155 | 0.064087 | 0.059509 | 0.041199 | -0.14191 | -0.022888 | 0.030518 | -0.074768 | -0.25528 | -0.037384 | -0.16449 | -0.14526 | -0.022888 | 0.086975 | -0.045776 | -0.018311 | 0.018311 | -0.1236 | -0.054932 | 0.036621 | 0.018311 | -0.022888
1017.0156 | 0.061035 | 0.45395 | -0.4657 | -0.21469 | -0.16663 | -0.28198 | -0.18478 | 0.027466 | -0.050354 | 0.068665 | -0.022888 | -0.10071 | -0.059509 | 0.059509 | 0.045776 | -0.095062 | -0.26062 | -0.055542 | -0.17303 | -0.14526 | 0.018311 | 0.086975 | -0.027466 | -0.11902 | -0.082397 | -0.091553 | -0.013733 | -0.041199 | 0.07782 | -0.013733
1018.75 | 0.030518 | 0.4422 | -0.44327 | -0.21042 | -0.15915 | -0.25528 | -0.17197 | 0.059509 | -0.013733 | 0.036621 | 0.064087 | 0.068665 | -0.13733 | -0.013733 | 0.030518 | -0.061951 | -0.24567 | -0.040588 | -0.15915 | -0.14954 | -0.036621 | 0.045776 | -0.082397 | -0.009155 | 0.013733 | -0.10529 | -0.045776 | 0.086975 | 0 | -0.032043
1020.5 | 0.030518 | 0.44861 | -0.45502 | -0.20508 | -0.15488 | -0.25528 | -0.16876 | -0.018311 | -0.15106 | -0.032043 | -0.050354 | 0 | -0.054932 | 0.064087 | 0.045776 | -0.067291 | -0.24994 | -0.030975 | -0.14526 | -0.13458 | -0.09613 | -0.09613 | -0.15564 | -0.073242 | -0.054932 | -0.064087 | 0 | -0.064087 | 0.018311 | 0
1022.1719 | 0.061035 | 0.4657 | -0.46356 | -0.20721 | -0.14633 | -0.28091 | -0.16876 | 0.022888 | -0.027466 | 0.073242 | -0.018311 | -0.10529 | -0.064087 | 0.054932 | 0.061035 | -0.085449 | -0.25742 | -0.041656 | -0.1709 | -0.13351 | 0.032043 | 0.09613 | -0.027466 | -0.10986 | -0.091553 | -0.086975 | -0.022888 | -0.041199 | 0.068665 | -0.018311
1023.8438 | 0.030518 | 0.44861 | -0.46463 | -0.22537 | -0.16022 | -0.26276 | -0.17731 | 0.073242 | -0.027466 | 0.032043 | 0.050354 | 0.082397 | -0.12817 | -0.022888 | 0.030518 | -0.083313 | -0.25955 | -0.029907 | -0.16556 | -0.14526 | -0.045776 | 0.032043 | -0.068665 | -0.018311 | 0.009155 | -0.10529 | -0.032043 | 0.07782 | 0.004578 | -0.032043
1025.5312 | 0.045776 | 0.46783 | -0.45715 | -0.20615 | -0.15808 | -0.28305 | -0.16449 | 0.10986 | 0.045776 | 0.10529 | 0.059509 | -0.050354 | -0.09613 | 0.004578 | 0.045776 | -0.09079 | -0.26276 | -0.058746 | -0.16769 | -0.14099 | 0.11444 | 0.21057 | 0.054932 | -0.086975 | -0.073242 | -0.12817 | -0.045776 | 0.09613 | 0.027466 | -0.054932
1027.2031 | 0.061035 | 0.45715 | -0.4657 | -0.22324 | -0.16129 | -0.29159 | -0.18265 | 0.059509 | 0.009155 | 0.082397 | 0.032043 | -0.054932 | -0.082397 | 0.018311 | 0.030518 | -0.089722 | -0.25742 | -0.050201 | -0.16876 | -0.1474 | 0.073242 | 0.16937 | 0.027466 | -0.086975 | -0.07782 | -0.082397 | -0.041199 | 0.091553 | 0.013733 | -0.041199
1028.8906 | 0.061035 | 0.44113 | -0.45822 | -0.20508 | -0.15808 | -0.25955 | -0.18585 | 0.10071 | 0.022888 | 0.07782 | 0.082397 | 0.041199 | -0.11902 | -0.013733 | 0.045776 | -0.079041 | -0.2478 | -0.038452 | -0.16022 | -0.14526 | 0 | 0.082397 | -0.045776 | -0.009155 | 0.013733 | -0.11902 | -0.036621 | 0.018311 | 0.022888 | -0.036621
1030.6406 | 0.045776 | 0.46143 | -0.46036 | -0.1976 | -0.16556 | -0.25314 | -0.16769 | 0 | -0.11902 | -0.004578 | -0.064087 | -0.041199 | -0.018311 | 0.068665 | 0.045776 | -0.059814 | -0.2478 | -0.038452 | -0.1506 | -0.14847 | -0.036621 | -0.054932 | -0.11444 | -0.082397 | -0.086975 | -0.059509 | 0.022888 | -0.018311 | 0.027466 | -0.027466
1032.375 | 0.015259 | 0.46356 | -0.46249 | -0.20508 | -0.16022 | -0.26596 | -0.16556 | 0.059509 | -0.032043 | 0.082397 | 0.013733 | -0.11444 | -0.059509 | 0.073242 | 0.030518 | -0.087585 | -0.24994 | -0.049133 | -0.14313 | -0.14313 | 0.032043 | 0.07782 | -0.045776 | -0.14648 | -0.13733 | -0.050354 | 0.009155 | -0.013733 | 0.054932 | -0.018311
1034.0938 | 0.061035 | 0.44327 | -0.46249 | -0.22217 | -0.15488 | -0.2681 | -0.16663 | 0.086975 | -0.041199 | 0.013733 | 0.050354 | 0.059509 | -0.11902 | -0.004578 | 0.045776 | -0.063019 | -0.24567 | -0.040588 | -0.15808 | -0.13565 | -0.036621 | 0.041199 | -0.064087 | -0.013733 | 0 | -0.13275 | -0.032043 | 0.082397 | -0.004578 | -0.050354
1035.7812 | 0.045776 | 0.45502 | -0.45288 | -0.1976 | -0.16556 | -0.25848 | -0.16556 | 0.045776 | -0.041199 | 0.068665 | 0.013733 | -0.12817 | -0.027466 | 0.09613 | 0.045776 | -0.089722 | -0.25314 | -0.03952 | -0.1474 | -0.14099 | 0.022888 | 0.086975 | -0.036621 | -0.15564 | -0.13275 | -0.041199 | 0.022888 | -0.045776 | 0.050354 | -0.018311
1037.4688 | 0.061035 | 0.4657 | -0.46677 | -0.19119 | -0.18692 | -0.26382 | -0.16983 | 0.004578 | -0.11444 | 0.004578 | -0.036621 | -0.064087 | -0.041199 | 0.082397 | 0.045776 | -0.065155 | -0.25955 | -0.042725 | -0.14633 | -0.1442 | -0.009155 | 0.009155 | -0.073242 | -0.11902 | -0.086975 | -0.059509 | 0.009155 | -0.009155 | 0.022888 | -0.013733
1039.1406 | 0.030518 | 0.45181 | -0.45715 | -0.22537 | -0.16876 | -0.2681 | -0.17303 | 0.068665 | -0.013733 | 0.041199 | 0.032043 | 0.054932 | -0.11902 | -0.013733 | 0.045776 | -0.066223 | -0.2478 | -0.041656 | -0.16342 | -0.13565 | -0.013733 | 0.07782 | -0.036621 | 0.032043 | 0.032043 | -0.13275 | -0.082397 | 0.041199 | 0 | -0.022888
1040.8125 | 0.045776 | 0.44327 | -0.47104 | -0.20828 | -0.17303 | -0.27237 | -0.17197 | 0.10986 | 0.050354 | 0.09613 | 0.10071 | 0.013733 | -0.13275 | -0.032043 | 0.030518 | -0.083313 | -0.25207 | -0.042725 | -0.16663 | -0.14099 | 0.004578 | 0.10986 | -0.018311 | 0.013733 | 0.018311 | -0.13275 | -0.073242 | 0.027466 | 0.032043 | -0.050354
1042.5625 | 0.015259 | 0.45502 | -0.46783 | -0.2179 | -0.16983 | -0.27771 | -0.17624 | 0.032043 | -0.064087 | 0.064087 | -0.022888 | -0.11444 | -0.032043 | 0.073242 | 0.061035 | -0.086517 | -0.25955 | -0.046997 | -0.17731 | -0.13992 | 0.027466 | 0.086975 | -0.036621 | -0.12817 | -0.10986 | -0.07782 | -0.004578 | -0.050354 | 0.064087 | 0
1044.3125 | 0.061035 | 0.45181 | -0.45822 | -0.20828 | -0.16449 | -0.24567 | -0.16983 | -0.009155 | -0.14648 | -0.032043 | -0.050354 | -0.013733 | -0.045776 | 0.064087 | 0.030518 | -0.05661 | -0.25101 | -0.041656 | -0.14526 | -0.14954 | -0.07782 | -0.09613 | -0.15106 | -0.073242 | -0.064087 | -0.064087 | 0.045776 | -0.041199 | 0.054932 | 0
1045.9844 | 0.045776 | 0.45929 | -0.46036 | -0.21576 | -0.17197 | -0.29159 | -0.1741 | 0.045776 | -0.045776 | 0.050354 | -0.004578 | -0.059509 | -0.068665 | 0.041199 | 0.030518 | -0.091858 | -0.24674 | -0.050201 | -0.16876 | -0.13351 | 0.013733 | 0.082397 | -0.036621 | -0.09613 | -0.082397 | -0.086975 | -0.009155 | -0.036621 | 0.064087 | -0.018311
1047.7188 | 0.061035 | 0.44647 | -0.46463 | -0.20401 | -0.15808 | -0.24994 | -0.17624 | -0.018311 | -0.15106 | -0.041199 | -0.036621 | -0.022888 | -0.054932 | 0.064087 | 0.030518 | -0.059814 | -0.24674 | -0.045929 | -0.1474 | -0.14633 | -0.091553 | -0.086975 | -0.16479 | -0.068665 | -0.064087 | -0.054932 | 0.036621 | -0.064087 | 0.054932 | 0
1049.4531 | 0.030518 | 0.45502 | -0.45395 | -0.20081 | -0.17303 | -0.25207 | -0.14847 | 0.004578 | -0.10529 | 0 | -0.022888 | -0.018311 | -0.054932 | 0.059509 | 0.061035 | -0.058746 | -0.25528 | -0.037384 | -0.1442 | -0.1442 | -0.13733 | -0.07782 | -0.15564 | -0.068665 | -0.041199 | -0.041199 | 0.009155 | -0.07782 | 0.050354 | 0.009155
1051.1875 | 0.045776 | 0.44754 | -0.45929 | -0.19974 | -0.15808 | -0.27451 | -0.15701 | 0.13275 | 0.082397 | 0.14191 | 0.07782 | -0.027466 | -0.11902 | -0.004578 | 0.030518 | -0.080109 | -0.24674 | -0.045929 | -0.16129 | -0.13351 | 0.064087 | 0.16022 | 0.036621 | -0.032043 | -0.022888 | -0.13275 | -0.050354 | 0.041199 | 0.041199 | -0.032043
1052.875 | 0.061035 | 0.42725 | -0.4422 | -0.22858 | -0.16129 | -0.25314 | -0.16449 | 0.082397 | -0.018311 | 0.086975 | 0.073242 | 0.004578 | -0.091553 | 0.004578 | 0.045776 | -0.071564 | -0.24246 | -0.03952 | -0.16129 | -0.13886 | -0.004578 | 0.059509 | -0.027466 | -0.036621 | -0.018311 | -0.086975 | -0.022888 | 0.036621 | 0 | -0.027466
1054.625 | 0.045776 | 0.44327 | -0.46036 | -0.2211 | -0.15274 | -0.27771 | -0.16556 | 0.1236 | 0.091553 | 0.14648 | 0.09613 | -0.018311 | -0.10071 | -0.013733 | 0.061035 | -0.086517 | -0.2478 | -0.053406 | -0.16129 | -0.1442 | 0.059509 | 0.19684 | 0.027466 | -0.045776 | -0.041199 | -0.13733 | -0.064087 | 0.032043 | 0.032043 | -0.041199
1056.3594 | 0.061035 | 0.44861 | -0.46356 | -0.21469 | -0.17197 | -0.25742 | -0.15808 | -0.009155 | -0.16022 | -0.022888 | -0.054932 | -0.027466 | -0.041199 | 0.086975 | 0.015259 | -0.0737 | -0.25848 | -0.023499 | -0.15488 | -0.14526 | -0.082397 | -0.073242 | -0.13275 | -0.059509 | -0.054932 | -0.045776 | 0.027466 | -0.050354 | 0.032043 | 0.009155
1058.1094 | 0.030518 | 0.43579 | -0.46249 | -0.21683 | -0.16876 | -0.25955 | -0.16129 | 0.082397 | -0.004578 | 0.059509 | 0.054932 | 0.013733 | -0.10986 | 0.013733 | 0.045776 | -0.086517 | -0.2446 | -0.032043 | -0.15915 | -0.13992 | -0.018311 | 0.059509 | -0.050354 | -0.022888 | -0.036621 | -0.10071 | -0.018311 | 0.068665 | 0 | -0.054932
1059.7812 | 0.061035 | 0.46036 | -0.46356 | -0.19653 | -0.17197 | -0.27451 | -0.17303 | 0.059509 | -0.018311 | 0.082397 | 0.027466 | -0.10071 | -0.059509 | 0.059509 | 0.061035 | -0.070496 | -0.25314 | -0.030975 | -0.16022 | -0.13565 | 0.004578 | 0.068665 | -0.045776 | -0.14648 | -0.15106 | -0.082397 | 0.009155 | -0.004578 | 0.022888 | -0.013733
1061.5312 | 0.061035 | 0.439 | -0.46249 | -0.21683 | -0.18051 | -0.27771 | -0.16769 | 0.10529 | 0.059509 | 0.10986 | 0.10071 | -0.004578 | -0.1236 | -0.022888 | 0.045776 | -0.082245 | -0.25207 | -0.035248 | -0.16342 | -0.14313 | 0.027466 | 0.15564 | 0.013733 | -0.009155 | -0.013733 | -0.1236 | -0.054932 | 0.041199 | 0.036621 | -0.032043
1063.2812 | 0.061035 | 0.46463 | -0.44861 | -0.19867 | -0.15808 | -0.26489 | -0.16983 | 0.041199 | -0.032043 | 0.082397 | 0.013733 | -0.11902 | -0.032043 | 0.064087 | 0.076294 | -0.077972 | -0.2681 | -0.045929 | -0.15915 | -0.15167 | 0.018311 | 0.064087 | -0.041199 | -0.15106 | -0.13275 | -0.059509 | 0.018311 | -0.032043 | 0.050354 | -0.013733
1064.9531 | 0.030518 | 0.43045 | -0.45502 | -0.22003 | -0.16129 | -0.25421 | -0.16556 | 0.086975 | -0.009155 | 0.068665 | 0.068665 | 0.022888 | -0.10071 | 0.018311 | 0.045776 | -0.065155 | -0.2446 | -0.048065 | -0.16769 | -0.1474 | -0.009155 | 0.054932 | -0.036621 | -0.018311 | -0.041199 | -0.073242 | -0.027466 | 0.073242 | 0 | -0.032043
1066.6719 | 0.045776 | 0.45715 | -0.46249 | -0.2211 | -0.16235 | -0.29373 | -0.16663 | 0.12817 | 0.11444 | 0.15564 | 0.10529 | -0.022888 | -0.12817 | 0.009155 | 0.015259 | -0.095062 | -0.25528 | -0.045929 | -0.15915 | -0.13458 | 0.10986 | 0.21973 | 0.068665 | -0.054932 | -0.036621 | -0.13275 | -0.07782 | 0.091553 | 0.022888 | -0.059509
1068.3594 | 0.030518 | 0.44647 | -0.46249 | -0.20721 | -0.16556 | -0.25955 | -0.17517 | 0.082397 | -0.013733 | 0.032043 | 0.073242 | 0.059509 | -0.11902 | -0.009155 | 0.045776 | -0.070496 | -0.26169 | -0.036316 | -0.1506 | -0.14847 | 0.004578 | 0.050354 | -0.054932 | 0.009155 | 0.022888 | -0.11444 | -0.045776 | 0.068665 | 0.009155 | -0.036621
1070.0312 | 0.030518 | 0.44434 | -0.45609 | -0.19653 | -0.1709 | -0.27771 | -0.1741 | 0.036621 | -0.032043 | 0.086975 | 0.004578 | -0.12817 | -0.041199 | 0.086975 | 0.061035 | -0.076904 | -0.26703 | -0.054474 | -0.15167 | -0.13886 | 0.054932 | 0.091553 | -0.018311 | -0.15106 | -0.1236 | -0.064087 | -0.004578 | -0.050354 | 0.050354 | -0.004578
1071.7031 | 0.061035 | 0.42725 | -0.45502 | -0.21469 | -0.16342 | -0.26169 | -0.16342 | 0.10071 | -0.004578 | 0.07782 | 0.064087 | 0.022888 | -0.091553 | 0.004578 | 0.076294 | -0.071564 | -0.25101 | -0.041656 | -0.15595 | -0.13992 | 0.013733 | 0.050354 | -0.036621 | -0.032043 | -0.041199 | -0.091553 | -0.032043 | 0.068665 | 0.004578 | -0.036621
1073.4531 | 0.045776 | 0.45075 | -0.45929 | -0.22324 | -0.16342 | -0.25742 | -0.14954 | 0.086975 | 0 | 0.064087 | 0.07782 | 0.045776 | -0.12817 | -0.009155 | 0.045776 | -0.068359 | -0.2446 | -0.046997 | -0.15595 | -0.14526 | -0.013733 | 0.054932 | -0.041199 | -0.032043 | -0.032043 | -0.073242 | -0.022888 | 0.068665 | 0.004578 | -0.045776
1075.1875 | 0.061035 | 0.45075 | -0.45822 | -0.19226 | -0.15915 | -0.26382 | -0.16449 | -0.036621 | -0.13733 | -0.018311 | -0.050354 | -0.054932 | -0.036621 | 0.064087 | 0.045776 | -0.067291 | -0.25955 | -0.035248 | -0.14847 | -0.12924 | -0.07782 | -0.086975 | -0.14648 | -0.059509 | -0.064087 | -0.059509 | 0.032043 | -0.041199 | 0.054932 | 0
1076.8438 | 0.015259 | 0.4454 | -0.46249 | -0.21149 | -0.16769 | -0.28946 | -0.17838 | 0.1236 | 0.10071 | 0.14191 | 0.10529 | -0.027466 | -0.14191 | 0 | 0.045776 | -0.092926 | -0.26062 | -0.041656 | -0.16983 | -0.13779 | 0.10529 | 0.22888 | 0.082397 | -0.054932 | -0.059509 | -0.15106 | -0.054932 | 0.082397 | 0.013733 | -0.041199
1078.6094 | 0.030518 | 0.45181 | -0.44861 | -0.21576 | -0.1474 | -0.2713 | -0.18692 | 0.073242 | -0.027466 | 0.045776 | 0.045776 | 0.059509 | -0.11444 | -0.022888 | 0.045776 | -0.065155 | -0.26596 | -0.046997 | -0.16769 | -0.13245 | -0.013733 | 0.059509 | -0.036621 | 0.022888 | 0.032043 | -0.11444 | -0.054932 | 0.068665 | 0.022888 | -0.027466
1080.375 | 0.045776 | 0.44434 | -0.45822 | -0.20828 | -0.16983 | -0.27557 | -0.17517 | 0.11902 | 0.064087 | 0.12817 | 0.086975 | -0.004578 | -0.12817 | 0 | 0.030518 | -0.084381 | -0.25528 | -0.038452 | -0.15915 | -0.13779 | 0.068665 | 0.16479 | 0.022888 | -0.032043 | -0.009155 | -0.12817 | -0.059509 | 0.032043 | 0.018311 | -0.022888
1082.125 | 0.061035 | 0.45715 | -0.46249 | -0.22217 | -0.16342 | -0.28091 | -0.17197 | 0.15564 | 0.082397 | 0.14191 | 0.10986 | -0.027466 | -0.11902 | -0.018311 | 0.061035 | -0.086517 | -0.26169 | -0.054474 | -0.17838 | -0.14526 | 0.086975 | 0.21057 | 0.064087 | -0.059509 | -0.050354 | -0.10986 | -0.059509 | 0.041199 | 0.004578 | -0.050354
1083.7969 | 0.045776 | 0.45395 | -0.46677 | -0.20187 | -0.15701 | -0.28305 | -0.17944 | 0.050354 | 0 | 0.073242 | 0.041199 | -0.050354 | -0.068665 | 0.022888 | 0.030518 | -0.088654 | -0.26276 | -0.041656 | -0.15701 | -0.14099 | 0.082397 | 0.14648 | 0.027466 | -0.091553 | -0.07782 | -0.10986 | -0.022888 | 0.09613 | 0.018311 | -0.054932
1085.5469 | 0 | 0.45609 | -0.45822 | -0.19974 | -0.16022 | -0.23498 | -0.16876 | 0.059509 | -0.050354 | 0.045776 | 0.018311 | 0.004578 | -0.073242 | 0.041199 | 0.061035 | -0.066223 | -0.26169 | -0.044861 | -0.14847 | -0.15167 | -0.036621 | -0.022888 | -0.10529 | -0.054932 | -0.032043 | -0.073242 | 0.013733 | -0.064087 | 0.027466 | 0
1087.2969 | 0.045776 | 0.48492 | -0.45609 | -0.19974 | -0.18051 | -0.27451 | -0.16129 | 0.045776 | -0.045776 | 0.050354 | 0.009155 | -0.064087 | -0.07782 | 0.054932 | 0.045776 | -0.092926 | -0.25635 | -0.050201 | -0.16022 | -0.13138 | 0.027466 | 0.09613 | -0.032043 | -0.091553 | -0.059509 | -0.082397 | -0.013733 | 0.009155 | 0.054932 | -0.018311
1088.9531 | 0.076294 | 0.4422 | -0.45075 | -0.20615 | -0.16983 | -0.2446 | -0.16556 | 0.10529 | -0.004578 | 0.082397 | 0.059509 | 0.004578 | -0.082397 | 0.027466 | 0.061035 | -0.067291 | -0.24674 | -0.035248 | -0.15808 | -0.14847 | 0.013733 | 0.036621 | -0.054932 | -0.054932 | -0.045776 | -0.091553 | -0.013733 | 0.027466 | 0.009155 | -0.036621
1090.6875 | 0.045776 | 0.4422 | -0.44968 | -0.2211 | -0.15595 | -0.26276 | -0.16129 | 0.09613 | 0 | 0.054932 | 0.050354 | 0.018311 | -0.086975 | 0.018311 | 0.061035 | -0.069427 | -0.24887 | -0.027771 | -0.15595 | -0.14206 | 0 | 0.059509 | -0.036621 | -0.032043 | -0.022888 | -0.07782 | -0.018311 | 0.073242 | -0.004578 | -0.032043
1092.4375 | 0.061035 | 0.45395 | -0.46036 | -0.20721 | -0.1741 | -0.28305 | -0.16342 | 0.027466 | -0.036621 | 0.064087 | -0.027466 | -0.10529 | -0.032043 | 0.07782 | 0.045776 | -0.082245 | -0.25848 | -0.038452 | -0.1709 | -0.14099 | 0.050354 | 0.091553 | -0.036621 | -0.13275 | -0.07782 | -0.082397 | 0.004578 | -0.054932 | 0.064087 | -0.022888
1094.1094 | 0.045776 | 0.44861 | -0.45075 | -0.20401 | -0.15915 | -0.25528 | -0.1709 | -0.004578 | -0.1236 | -0.018311 | -0.022888 | -0.013733 | -0.050354 | 0.054932 | 0.030518 | -0.067291 | -0.25421 | -0.036316 | -0.14526 | -0.14313 | -0.086975 | -0.068665 | -0.15564 | -0.050354 | -0.064087 | -0.054932 | 0.018311 | -0.064087 | 0.050354 | -0.013733
1095.7812 | 0.030518 | 0.46143 | -0.45929 | -0.22324 | -0.16129 | -0.27985 | -0.17197 | 0.13275 | 0.10071 | 0.14191 | 0.10071 | -0.036621 | -0.11444 | -0.022888 | 0.045776 | -0.081177 | -0.25207 | -0.046997 | -0.16769 | -0.1442 | 0.12817 | 0.2243 | 0.068665 | -0.064087 | -0.059509 | -0.14191 | -0.036621 | 0.082397 | 0.032043 | -0.041199
1097.5312 | 0.045776 | 0.45502 | -0.4689 | -0.20935 | -0.17303 | -0.27344 | -0.17517 | 0.10071 | 0.018311 | 0.07782 | 0.045776 | -0.059509 | -0.086975 | 0.013733 | 0.045776 | -0.087585 | -0.26703 | -0.050201 | -0.16556 | -0.14313 | 0.09613 | 0.1831 | 0.041199 | -0.064087 | -0.059509 | -0.10529 | -0.036621 | 0.082397 | 0.009155 | -0.045776
1099.2656 | 0.045776 | 0.48813 | -0.46463 | -0.21362 | -0.16342 | -0.28091 | -0.17944 | 0.045776 | -0.032043 | 0.054932 | 0.004578 | -0.050354 | -0.07782 | 0.054932 | 0.030518 | -0.09079 | -0.26062 | -0.054474 | -0.16663 | -0.14526 | 0.036621 | 0.07782 | -0.050354 | -0.091553 | -0.086975 | -0.073242 | -0.004578 | -0.036621 | 0.054932 | -0.009155
1101 | 0.061035 | 0.42831 | -0.45395 | -0.2211 | -0.16556 | -0.25207 | -0.15808 | -0.004578 | -0.12817 | -0.004578 | -0.041199 | -0.032043 | -0.032043 | 0.059509 | 0.045776 | -0.068359 | -0.24994 | -0.041656 | -0.15381 | -0.15167 | -0.032043 | -0.045776 | -0.11444 | -0.086975 | -0.091553 | -0.050354 | 0.013733 | -0.004578 | 0.041199 | -0.018311
1102.6719 | 0.045776 | 0.44434 | -0.4454 | -0.19974 | -0.17731 | -0.25207 | -0.16663 | 0.009155 | -0.12817 | -0.032043 | -0.041199 | 0 | -0.064087 | 0.054932 | 0.030518 | -0.05661 | -0.25635 | -0.03952 | -0.14847 | -0.14206 | -0.09613 | -0.082397 | -0.15564 | -0.045776 | -0.054932 | -0.059509 | 0.009155 | -0.068665 | 0.036621 | 0.018311
1104.4219 | 0.061035 | 0.44647 | -0.45288 | -0.21042 | -0.15488 | -0.26596 | -0.16556 | 0.045776 | -0.022888 | 0.086975 | 0 | -0.13275 | -0.032043 | 0.091553 | 0.045776 | -0.079041 | -0.25421 | -0.052338 | -0.15808 | -0.14633 | 0.064087 | 0.10529 | -0.022888 | -0.14191 | -0.13275 | -0.050354 | 0.004578 | -0.050354 | 0.045776 | 0.018311
1106.1562 | 0.045776 | 0.44754 | -0.45715 | -0.20828 | -0.16769 | -0.24353 | -0.17197 | 0.041199 | -0.073242 | 0.018311 | -0.004578 | 0.004578 | -0.07782 | 0.027466 | 0.045776 | -0.055542 | -0.26489 | -0.043793 | -0.14526 | -0.13886 | -0.086975 | -0.059509 | -0.15564 | -0.068665 | -0.045776 | -0.054932 | 0.009155 | -0.064087 | 0.045776 | -0.013733
1107.8281 | 0.061035 | 0.4689 | -0.46463 | -0.20828 | -0.17303 | -0.28198 | -0.17624 | 0.027466 | -0.041199 | 0.050354 | 0.022888 | -0.041199 | -0.068665 | 0.050354 | 0.045776 | -0.09079 | -0.25848 | -0.046997 | -0.16342 | -0.13992 | 0.045776 | 0.11444 | -0.027466 | -0.073242 | -0.045776 | -0.091553 | -0.004578 | 0.036621 | 0.059509 | -0.036621
1109.5781 | 0.045776 | 0.45075 | -0.45609 | -0.22217 | -0.16449 | -0.27664 | -0.17624 | 0.018311 | -0.041199 | 0.036621 | 0.004578 | -0.045776 | -0.07782 | 0.054932 | 0.045776 | -0.09079 | -0.26169 | -0.050201 | -0.1741 | -0.14526 | 0.022888 | 0.082397 | -0.036621 | -0.09613 | -0.07782 | -0.082397 | -0.013733 | 0 | 0.041199 | -0.032043
1111.25 | 0.061035 | 0.46997 | -0.46249 | -0.21149 | -0.17517 | -0.27985 | -0.18051 | 0.10071 | 0.018311 | 0.086975 | 0.064087 | -0.036621 | -0.091553 | 0.022888 | 0.045776 | -0.085449 | -0.24674 | -0.041656 | -0.15167 | -0.14633 | 0.11444 | 0.17853 | 0.036621 | -0.07782 | -0.064087 | -0.11444 | -0.032043 | 0.091553 | 0.018311 | -0.045776
1112.9531 | 0.045776 | 0.47104 | -0.45502 | -0.19974 | -0.17731 | -0.26169 | -0.16342 | 0.059509 | -0.013733 | 0.10071 | 0.009155 | -0.10071 | -0.045776 | 0.064087 | 0.061035 | -0.081177 | -0.26489 | -0.030975 | -0.15274 | -0.13565 | 0.045776 | 0.059509 | -0.050354 | -0.12817 | -0.13733 | -0.027466 | 0.018311 | -0.07782 | 0.045776 | -0.013733
1114.625 | 0.061035 | 0.44861 | -0.45395 | -0.20294 | -0.17197 | -0.24887 | -0.16342 | 0.004578 | -0.13733 | -0.022888 | -0.045776 | -0.018311 | -0.041199 | 0.082397 | 0.076294 | -0.067291 | -0.24887 | -0.027771 | -0.1442 | -0.15595 | -0.068665 | -0.091553 | -0.16022 | -0.059509 | -0.054932 | -0.054932 | 0.032043 | -0.059509 | 0.045776 | -0.004578
1116.3594 | 0.030518 | 0.46356 | -0.44754 | -0.20615 | -0.16876 | -0.26169 | -0.16235 | 0.059509 | -0.036621 | 0.054932 | 0 | -0.082397 | -0.041199 | 0.073242 | 0.076294 | -0.067291 | -0.2681 | -0.040588 | -0.1506 | -0.14954 | 0.045776 | 0.059509 | -0.036621 | -0.11902 | -0.11444 | -0.064087 | 0.009155 | -0.018311 | 0.041199 | -0.022888
1118.0938 | 0.045776 | 0.45395 | -0.45822 | -0.2179 | -0.15915 | -0.26062 | -0.16449 | 0.022888 | -0.11902 | 0 | -0.054932 | -0.036621 | -0.036621 | 0.068665 | 0.061035 | -0.071564 | -0.25207 | -0.040588 | -0.15915 | -0.13992 | -0.018311 | -0.013733 | -0.10071 | -0.10529 | -0.09613 | -0.054932 | 0.004578 | -0.027466 | 0.041199 | -0.013733
1119.75 | 0.061035 | 0.46143 | -0.46783 | -0.21042 | -0.16983 | -0.28091 | -0.16876 | 0.091553 | 0.013733 | 0.073242 | 0.041199 | -0.050354 | -0.07782 | 0.027466 | 0.061035 | -0.084381 | -0.25955 | -0.052338 | -0.16556 | -0.1442 | 0.11444 | 0.19226 | 0.041199 | -0.073242 | -0.073242 | -0.10071 | -0.050354 | 0.086975 | 0.009155 | -0.032043
1121.4219 | 0.061035 | 0.44434 | -0.46463 | -0.22858 | -0.16556 | -0.2681 | -0.1741 | 0.15564 | 0.10529 | 0.14648 | 0.11902 | -0.009155 | -0.10986 | -0.018311 | 0.045776 | -0.076904 | -0.25955 | -0.050201 | -0.15915 | -0.1474 | 0.10071 | 0.20599 | 0.041199 | -0.050354 | -0.045776 | -0.12817 | -0.068665 | 0.050354 | 0.009155 | -0.032043
1123.0938 | 0.015259 | 0.44434 | -0.45929 | -0.20294 | -0.15701 | -0.23926 | -0.17197 | 0.032043 | -0.10529 | -0.004578 | -0.013733 | -0.013733 | -0.054932 | 0.068665 | 0.061035 | -0.060883 | -0.25314 | -0.040588 | -0.13779 | -0.14633 | -0.091553 | -0.068665 | -0.16479 | -0.036621 | -0.032043 | -0.07782 | 0.022888 | -0.073242 | 0.032043 | 0.009155
1124.7656 | 0.045776 | 0.4422 | -0.46036 | -0.20721 | -0.16876 | -0.25848 | -0.1709 | 0.10529 | -0.004578 | 0.045776 | 0.07782 | 0.045776 | -0.10529 | 0 | 0.045776 | -0.068359 | -0.2681 | -0.038452 | -0.15701 | -0.1442 | -0.009155 | 0.041199 | -0.054932 | -0.050354 | -0.004578 | -0.10071 | -0.022888 | 0.059509 | -0.013733 | -0.045776
1126.4531 | 0.045776 | 0.45395 | -0.46677 | -0.21576 | -0.16129 | -0.28091 | -0.16663 | 0.064087 | -0.027466 | 0.09613 | 0.009155 | -0.11444 | -0.036621 | 0.082397 | 0.015259 | -0.084381 | -0.26382 | -0.046997 | -0.16876 | -0.14099 | 0.064087 | 0.09613 | -0.027466 | -0.13275 | -0.11444 | -0.036621 | 0.022888 | -0.073242 | 0.050354 | 0.004578
1128.1406 | 0.061035 | 0.45715 | -0.46463 | -0.23392 | -0.1709 | -0.28519 | -0.16876 | 0.041199 | -0.045776 | 0.068665 | -0.004578 | -0.073242 | -0.068665 | 0.022888 | 0.030518 | -0.075836 | -0.24353 | -0.045929 | -0.1709 | -0.14633 | 0.041199 | 0.09613 | -0.036621 | -0.082397 | -0.045776 | -0.091553 | 0 | -0.059509 | 0.050354 | -0.009155
1129.8125 | 0.061035 | 0.43579 | -0.45288 | -0.20187 | -0.16556 | -0.25421 | -0.15701 | 0.045776 | -0.091553 | 0.004578 | -0.009155 | -0.004578 | -0.068665 | 0.050354 | 0.045776 | -0.066223 | -0.24887 | -0.033112 | -0.14633 | -0.15274 | -0.07782 | -0.050354 | -0.15564 | -0.045776 | -0.054932 | -0.041199 | 0.018311 | -0.064087 | 0.050354 | 0.004578
1131.5469 | 0.045776 | 0.46249 | -0.45822 | -0.20508 | -0.17197 | -0.26916 | -0.1709 | 0.050354 | -0.036621 | 0.10071 | -0.004578 | -0.12817 | -0.041199 | 0.086975 | 0.045776 | -0.082245 | -0.24887 | -0.033112 | -0.15701 | -0.14847 | 0.059509 | 0.09613 | -0.027466 | -0.15106 | -0.14191 | -0.045776 | 0.036621 | -0.059509 | 0.050354 | -0.004578
1133.2188 | 0.076294 | 0.46463 | -0.45715 | -0.21576 | -0.16983 | -0.28198 | -0.16983 | 0.036621 | -0.018311 | 0.045776 | 0.009155 | -0.045776 | -0.050354 | 0.045776 | 0.030518 | -0.076904 | -0.24887 | -0.041656 | -0.17517 | -0.13351 | 0.054932 | 0.10986 | -0.013733 | -0.073242 | -0.064087 | -0.086975 | -0.013733 | 0.041199 | 0.041199 | -0.032043
1134.8906 | 0.045776 | 0.45181 | -0.46249 | -0.20615 | -0.18372 | -0.25421 | -0.16663 | 0.004578 | -0.09613 | 0.004578 | -0.036621 | -0.032043 | -0.050354 | 0.064087 | 0.045776 | -0.063019 | -0.25528 | -0.043793 | -0.14847 | -0.1442 | 0 | -0.036621 | -0.073242 | -0.11444 | -0.11902 | -0.064087 | 0.013733 | -0.027466 | 0.022888 | 0.009155
1136.5625 | 0.045776 | 0.45609 | -0.45288 | -0.19974 | -0.1709 | -0.25207 | -0.17624 | 0.018311 | -0.10529 | -0.004578 | -0.050354 | -0.022888 | -0.018311 | 0.068665 | 0.045776 | -0.0737 | -0.25848 | -0.033112 | -0.16235 | -0.13992 | 0 | -0.009155 | -0.091553 | -0.10986 | -0.10529 | -0.045776 | 0.022888 | -0.013733 | 0.041199 | -0.004578
1138.3125 | 0.045776 | 0.4422 | -0.45929 | -0.22217 | -0.18265 | -0.28625 | -0.17303 | 0.13275 | 0.050354 | 0.11444 | 0.082397 | 0.018311 | -0.10986 | -0.013733 | 0.045776 | -0.067291 | -0.24567 | -0.053406 | -0.15915 | -0.13886 | 0.032043 | 0.11902 | -0.009155 | 0.022888 | 0.009155 | -0.10986 | -0.059509 | 0.027466 | 0.022888 | -0.050354
1139.9844 | 0.045776 | 0.42938 | -0.45502 | -0.2179 | -0.15381 | -0.25101 | -0.15915 | 0.004578 | -0.13733 | -0.022888 | -0.022888 | -0.009155 | -0.059509 | 0.07782 | 0.061035 | -0.069427 | -0.2478 | -0.044861 | -0.15595 | -0.14099 | -0.086975 | -0.068665 | -0.16022 | -0.059509 | -0.041199 | -0.041199 | 0.036621 | -0.064087 | 0.054932 | -0.004578
1141.7188 | 0.030518 | 0.45609 | -0.45502 | -0.22003 | -0.16876 | -0.29373 | -0.17624 | 0.14648 | 0.10986 | 0.14191 | 0.10986 | -0.018311 | -0.09613 | -0.013733 | 0.030518 | -0.09613 | -0.25742 | -0.048065 | -0.16449 | -0.14313 | 0.11444 | 0.23346 | 0.064087 | -0.050354 | -0.068665 | -0.1236 | -0.054932 | 0.086975 | 0.036621 | -0.041199
1143.4688 | 0.045776 | 0.4422 | -0.45181 | -0.21042 | -0.15915 | -0.25101 | -0.16663 | -0.004578 | -0.11444 | -0.022888 | -0.041199 | -0.027466 | -0.022888 | 0.082397 | 0.076294 | -0.066223 | -0.25742 | -0.038452 | -0.15381 | -0.14526 | -0.036621 | -0.050354 | -0.10986 | -0.082397 | -0.068665 | -0.059509 | 0.018311 | -0.018311 | 0.032043 | -0.004578
1145.1562 | 0.061035 | 0.45075 | -0.44434 | -0.21576 | -0.1741 | -0.26916 | -0.16983 | 0.004578 | -0.12817 | -0.009155 | -0.050354 | -0.018311 | -0.054932 | 0.07782 | 0.045776 | -0.076904 | -0.25421 | -0.032043 | -0.1442 | -0.14206 | -0.022888 | -0.032043 | -0.11444 | -0.091553 | -0.086975 | -0.059509 | 0.013733 | -0.018311 | 0.041199 | 0
1146.8281 | 0.045776 | 0.44647 | -0.45715 | -0.22964 | -0.16663 | -0.28839 | -0.17197 | 0.13733 | 0.09613 | 0.15106 | 0.10529 | -0.032043 | -0.13275 | -0.004578 | 0.061035 | -0.082245 | -0.2478 | -0.045929 | -0.1709 | -0.14847 | 0.11444 | 0.20599 | 0.054932 | -0.068665 | -0.036621 | -0.12817 | -0.041199 | 0.036621 | 0.027466 | -0.022888
1148.5156 | 0.030518 | 0.45395 | -0.4657 | -0.21362 | -0.15808 | -0.25421 | -0.18158 | 0.07782 | -0.022888 | 0.009155 | 0.059509 | 0.054932 | -0.10529 | 0 | 0.045776 | -0.063019 | -0.26169 | -0.035248 | -0.16342 | -0.1474 | -0.013733 | 0.041199 | -0.045776 | -0.009155 | 0.004578 | -0.12817 | -0.045776 | 0.086975 | -0.004578 | -0.032043
1150.2031 | 0.061035 | 0.44327 | -0.46463 | -0.19867 | -0.1474 | -0.25635 | -0.16876 | 0.064087 | -0.041199 | 0.036621 | 0.009155 | 0 | -0.073242 | 0.041199 | 0.061035 | -0.067291 | -0.25421 | -0.03952 | -0.1442 | -0.13992 | -0.059509 | -0.041199 | -0.11902 | -0.050354 | -0.050354 | -0.050354 | 0.018311 | -0.059509 | 0.045776 | 0
1151.875 | 0.045776 | 0.42831 | -0.45181 | -0.21469 | -0.14954 | -0.26382 | -0.16663 | 0.10071 | -0.004578 | 0.086975 | 0.064087 | 0.013733 | -0.091553 | 0.022888 | 0.015259 | -0.060883 | -0.25314 | -0.030975 | -0.14847 | -0.14526 | 0.009155 | 0.050354 | -0.032043 | -0.027466 | -0.032043 | -0.091553 | -0.027466 | 0.036621 | 0.004578 | -0.018311
1153.5625 | 0.061035 | 0.44968 | -0.45929 | -0.21896 | -0.15808 | -0.29373 | -0.17517 | 0.027466 | -0.013733 | 0.050354 | 0.022888 | -0.045776 | -0.068665 | 0.036621 | 0.030518 | -0.099335 | -0.24674 | -0.046997 | -0.16983 | -0.13351 | 0.045776 | 0.13275 | 0.004578 | -0.082397 | -0.059509 | -0.09613 | -0.018311 | 0.091553 | 0.032043 | -0.041199
1155.3125 | 0.061035 | 0.4422 | -0.45715 | -0.2211 | -0.15808 | -0.26382 | -0.16235 | 0 | -0.086975 | 0.027466 | -0.018311 | -0.073242 | -0.036621 | 0.10071 | 0.045776 | -0.076904 | -0.25421 | -0.035248 | -0.15808 | -0.14847 | 0.041199 | 0.027466 | -0.045776 | -0.1236 | -0.11444 | -0.050354 | 0.013733 | 0.004578 | 0.036621 | -0.018311
1156.9844 | 0.045776 | 0.44434 | -0.44968 | -0.22003 | -0.16449 | -0.25635 | -0.16769 | 0.073242 | -0.009155 | 0.022888 | 0.054932 | 0.091553 | -0.13733 | 0.004578 | 0.045776 | -0.067291 | -0.24139 | -0.040588 | -0.15808 | -0.14633 | -0.009155 | 0.036621 | -0.073242 | 0.004578 | 0.004578 | -0.091553 | -0.027466 | 0.082397 | 0.013733 | -0.022888
1158.7344 | 0.030518 | 0.44968 | -0.46036 | -0.20935 | -0.16449 | -0.26276 | -0.17944 | 0.10071 | 0.045776 | 0.086975 | 0.07782 | 0.036621 | -0.12817 | -0.004578 | 0.061035 | -0.0737 | -0.25742 | -0.045929 | -0.17517 | -0.13886 | 0.013733 | 0.10071 | -0.027466 | 0.018311 | 0.022888 | -0.10529 | -0.050354 | 0.032043 | 0.013733 | -0.004578
1160.4844 | 0.061035 | 0.44754 | -0.4657 | -0.21042 | -0.17197 | -0.27985 | -0.17838 | 0.13275 | 0.10071 | 0.15564 | 0.11444 | -0.022888 | -0.13275 | -0.027466 | 0.061035 | -0.079041 | -0.25955 | -0.048065 | -0.16876 | -0.1474 | 0.11902 | 0.21515 | 0.059509 | -0.059509 | -0.054932 | -0.13733 | -0.050354 | 0.059509 | 0.022888 | -0.045776
1162.1562 | 0.045776 | 0.45822 | -0.45929 | -0.2179 | -0.16235 | -0.27771 | -0.17731 | 0.073242 | 0 | 0.07782 | 0.036621 | -0.041199 | -0.082397 | 0.018311 | 0.061035 | -0.080109 | -0.25314 | -0.053406 | -0.16663 | -0.1442 | 0.086975 | 0.15564 | 0.032043 | -0.073242 | -0.054932 | -0.073242 | -0.032043 | 0.091553 | 0.009155 | -0.054932
1163.8906 | 0.061035 | 0.44327 | -0.45502 | -0.19333 | -0.1709 | -0.24033 | -0.16022 | 0.009155 | -0.1236 | -0.018311 | -0.036621 | -0.009155 | -0.050354 | 0.050354 | 0.045776 | -0.0737 | -0.25742 | -0.041656 | -0.13672 | -0.1474 | -0.091553 | -0.09613 | -0.15106 | -0.045776 | -0.054932 | -0.073242 | 0.018311 | -0.059509 | 0.059509 | 0.013733
1165.5781 | 0.061035 | 0.45075 | -0.46783 | -0.22324 | -0.15915 | -0.26276 | -0.17197 | 0.086975 | 0 | 0.032043 | 0.059509 | 0.086975 | -0.12817 | -0.004578 | 0.061035 | -0.0737 | -0.23819 | -0.028839 | -0.15701 | -0.13351 | -0.018311 | 0.041199 | -0.064087 | 0.027466 | 0.032043 | -0.10986 | -0.036621 | 0.09613 | 0.004578 | -0.041199
1167.25 | 0.030518 | 0.46356 | -0.47424 | -0.21576 | -0.17303 | -0.29159 | -0.18265 | 0.068665 | 0.027466 | 0.082397 | 0.054932 | -0.041199 | -0.082397 | 0.027466 | 0.061035 | -0.092926 | -0.25742 | -0.063019 | -0.16235 | -0.13779 | 0.10529 | 0.19684 | 0.041199 | -0.064087 | -0.068665 | -0.10986 | -0.027466 | 0.10986 | 0.009155 | -0.045776
1168.9375 | 0.030518 | 0.45075 | -0.44327 | -0.20401 | -0.17197 | -0.24994 | -0.16342 | 0.032043 | -0.11444 | -0.013733 | -0.018311 | 0.004578 | -0.050354 | 0.036621 | 0.015259 | -0.049133 | -0.25207 | -0.045929 | -0.14099 | -0.1506 | -0.10071 | -0.054932 | -0.14191 | -0.022888 | -0.036621 | -0.050354 | 0.022888 | -0.059509 | 0.045776 | 0
1170.6875 | 0.061035 | 0.47958 | -0.46783 | -0.21149 | -0.1709 | -0.2713 | -0.17731 | 0.022888 | -0.041199 | 0.054932 | -0.018311 | -0.1236 | -0.013733 | 0.09613 | 0.076294 | -0.082245 | -0.26276 | -0.058746 | -0.16235 | -0.13351 | 0.054932 | 0.082397 | -0.032043 | -0.09613 | -0.073242 | -0.064087 | -0.004578 | -0.041199 | 0.073242 | 0.004578
1172.4219 | 0.045776 | 0.46463 | -0.46356 | -0.22537 | -0.16449 | -0.27557 | -0.18051 | 0.09613 | 0.013733 | 0.091553 | 0.059509 | -0.036621 | -0.082397 | 0.018311 | 0.061035 | -0.085449 | -0.25742 | -0.043793 | -0.17303 | -0.14847 | 0.10986 | 0.18768 | 0.041199 | -0.068665 | -0.059509 | -0.09613 | -0.032043 | 0.09613 | 0.013733 | -0.050354
1174.0938 | 0.045776 | 0.45609 | -0.45929 | -0.20935 | -0.17197 | -0.27878 | -0.18051 | 0.032043 | -0.032043 | 0.059509 | -0.018311 | -0.11444 | -0.032043 | 0.086975 | 0.076294 | -0.074768 | -0.25528 | -0.037384 | -0.16342 | -0.15381 | 0.050354 | 0.086975 | -0.036621 | -0.09613 | -0.09613 | -0.07782 | -0.004578 | -0.064087 | 0.073242 | -0.013733
1175.7656 | 0.076294 | 0.45075 | -0.4689 | -0.21683 | -0.15915 | -0.27878 | -0.1741 | 0.13733 | 0.082397 | 0.13733 | 0.086975 | -0.027466 | -0.10071 | 0.018311 | 0.045776 | -0.083313 | -0.24674 | -0.045929 | -0.15488 | -0.14954 | 0.13733 | 0.20599 | 0.050354 | -0.064087 | -0.068665 | -0.11444 | -0.041199 | 0.10071 | 0.009155 | -0.036621
1177.5156 | 0.045776 | 0.4422 | -0.4657 | -0.22217 | -0.16556 | -0.26703 | -0.18585 | 0.15106 | 0.09613 | 0.13733 | 0.10986 | -0.022888 | -0.11444 | -0.009155 | 0.076294 | -0.075836 | -0.24887 | -0.05127 | -0.16235 | -0.14526 | 0.13275 | 0.22888 | 0.073242 | -0.050354 | -0.064087 | -0.1236 | -0.068665 | 0.07782 | 0.018311 | -0.045776
1179.25 | 0.045776 | 0.49988 | -0.47104 | -0.19119 | -0.15915 | -0.2713 | -0.18265 | 0.16479 | 0.082397 | 0.10071 | 0.086975 | -0.022888 | -0.091553 | -0.004578 | 0.045776 | -0.084381 | -0.27771 | -0.053406 | -0.15595 | -0.13992 | 0.15106 | 0.20142 | 0.064087 | -0.068665 | -0.054932 | -0.12817 | -0.054932 | 0.09613 | 0.013733 | -0.041199
1180.9219 | 0.076294 | 0.44113 | -0.46463 | -0.20187 | -0.16129 | -0.23819 | -0.18265 | 0.022888 | -0.13275 | -0.013733 | -0.050354 | -0.032043 | -0.036621 | 0.07782 | 0.061035 | -0.060883 | -0.25207 | -0.03952 | -0.1506 | -0.14954 | -0.032043 | -0.059509 | -0.13275 | -0.073242 | -0.054932 | -0.054932 | 0.018311 | 0 | 0.032043 | -0.004578
1182.6719 | 0.061035 | 0.44647 | -0.45929 | -0.20828 | -0.16556 | -0.2446 | -0.16556 | 0.086975 | -0.032043 | 0.045776 | 0.022888 | 0.004578 | -0.073242 | 0.041199 | 0.045776 | -0.053406 | -0.25848 | -0.042725 | -0.14954 | -0.14633 | -0.022888 | -0.022888 | -0.11444 | -0.045776 | -0.032043 | -0.091553 | 0 | -0.050354 | 0.050354 | 0
1184.3594 | 0.045776 | 0.44968 | -0.44861 | -0.21896 | -0.16235 | -0.25528 | -0.16769 | 0 | -0.13275 | -0.027466 | -0.045776 | -0.022888 | -0.036621 | 0.07782 | 0.045776 | -0.057678 | -0.24887 | -0.03952 | -0.15595 | -0.13565 | -0.064087 | -0.07782 | -0.1236 | -0.054932 | -0.045776 | -0.050354 | 0.032043 | -0.018311 | 0.041199 | -0.004578
1186.0312 | 0.030518 | 0.45929 | -0.46249 | -0.22003 | -0.15381 | -0.28412 | -0.17838 | 0.14191 | 0.091553 | 0.15106 | 0.11444 | 0 | -0.11444 | -0.013733 | 0.030518 | -0.085449 | -0.25742 | -0.054474 | -0.16663 | -0.13458 | 0.12817 | 0.22888 | 0.064087 | -0.059509 | -0.045776 | -0.1236 | -0.045776 | 0.054932 | 0.036621 | -0.041199
1187.7031 | 0.045776 | 0.45715 | -0.45822 | -0.20935 | -0.1741 | -0.28519 | -0.1709 | 0.15564 | 0.10071 | 0.16022 | 0.09613 | -0.018311 | -0.11444 | -0.036621 | 0.061035 | -0.080109 | -0.25635 | -0.060883 | -0.16342 | -0.15381 | 0.10986 | 0.23346 | 0.068665 | -0.064087 | -0.064087 | -0.14191 | -0.059509 | 0.064087 | 0.036621 | -0.032043
1189.3906 | 0.045776 | 0.45502 | -0.46463 | -0.21362 | -0.16556 | -0.25848 | -0.17303 | 0.086975 | -0.036621 | 0.027466 | 0.045776 | 0.068665 | -0.11902 | -0.004578 | 0.061035 | -0.067291 | -0.25955 | -0.03418 | -0.15488 | -0.1442 | -0.018311 | 0.032043 | -0.059509 | 0.004578 | 0.009155 | -0.091553 | -0.027466 | 0.07782 | -0.009155 | -0.050354
1191.0781 | 0.061035 | 0.44861 | -0.46036 | -0.2179 | -0.15915 | -0.28198 | -0.18051 | 0.032043 | -0.036621 | 0.054932 | -0.004578 | -0.036621 | -0.068665 | 0.050354 | 0.045776 | -0.074768 | -0.25635 | -0.043793 | -0.16449 | -0.14633 | 0.036621 | 0.09613 | -0.054932 | -0.073242 | -0.086975 | -0.07782 | -0.009155 | -0.022888 | 0.059509 | -0.022888
1192.75 | 0.045776 | 0.45288 | -0.45822 | -0.21255 | -0.1709 | -0.26382 | -0.17303 | 0.022888 | -0.11902 | -0.004578 | -0.041199 | -0.045776 | -0.018311 | 0.07782 | 0.076294 | -0.065155 | -0.24887 | -0.040588 | -0.14954 | -0.15381 | -0.009155 | -0.004578 | -0.086975 | -0.10529 | -0.086975 | -0.032043 | 0.013733 | -0.009155 | 0.045776 | -0.013733
1194.5 | 0.061035 | 0.46463 | -0.45181 | -0.20615 | -0.16449 | -0.25635 | -0.1709 | 0.045776 | -0.054932 | 0.068665 | 0.004578 | -0.09613 | -0.041199 | 0.082397 | 0.015259 | -0.059814 | -0.25528 | -0.041656 | -0.14206 | -0.14847 | 0.041199 | 0.059509 | -0.041199 | -0.1236 | -0.11444 | -0.050354 | 0.009155 | -0.013733 | 0.032043 | -0.022888
1196.25 | 0.061035 | 0.43366 | -0.46249 | -0.20721 | -0.17731 | -0.24246 | -0.16129 | 0.09613 | -0.013733 | 0.059509 | 0.059509 | 0.013733 | -0.086975 | 0.032043 | 0.030518 | -0.059814 | -0.25314 | -0.028839 | -0.1506 | -0.14847 | 0.018311 | 0.059509 | -0.018311 | -0.018311 | -0.013733 | -0.09613 | -0.013733 | 0.073242 | -0.009155 | -0.032043
1197.9219 | 0.045776 | 0.46249 | -0.46249 | -0.20615 | -0.16876 | -0.29373 | -0.17303 | 0.022888 | -0.027466 | 0.059509 | 0.004578 | -0.068665 | -0.068665 | 0.054932 | 0.061035 | -0.083313 | -0.26062 | -0.055542 | -0.15808 | -0.14206 | 0.041199 | 0.10071 | -0.036621 | -0.082397 | -0.082397 | -0.068665 | 0 | -0.045776 | 0.068665 | -0.018311
1199.6562 | 0.045776 | 0.45715 | -0.47318 | -0.21896 | -0.16342 | -0.28305 | -0.17197 | 0.15564 | 0.12817 | 0.16022 | 0.10529 | -0.013733 | -0.11444 | 0.004578 | 0.061035 | -0.083313 | -0.26169 | -0.059814 | -0.16129 | -0.14847 | 0.13733 | 0.22888 | 0.073242 | -0.050354 | -0.068665 | -0.11902 | -0.068665 | 0.09613 | 0.022888 | -0.050354
1201.3281 | 0.030518 | 0.45181 | -0.44327 | -0.20081 | -0.16769 | -0.24246 | -0.17517 | -0.004578 | -0.11444 | 0 | -0.013733 | -0.027466 | -0.041199 | 0.073242 | 0.061035 | -0.063019 | -0.24887 | -0.035248 | -0.14633 | -0.15808 | -0.091553 | -0.07782 | -0.17395 | -0.050354 | -0.045776 | -0.054932 | 0.022888 | -0.064087 | 0.041199 | 0.004578
1203 | 0.061035 | 0.43579 | -0.46036 | -0.23285 | -0.15488 | -0.27237 | -0.16663 | 0.13275 | 0.11902 | 0.14648 | 0.09613 | -0.013733 | -0.11444 | 0.009155 | 0.045776 | -0.093994 | -0.23712 | -0.05661 | -0.1741 | -0.15274 | 0.13275 | 0.22888 | 0.068665 | -0.064087 | -0.045776 | -0.11902 | -0.041199 | 0.07782 | 0.013733 | -0.036621
1204.75 | 0.045776 | 0.44754 | -0.4657 | -0.21576 | -0.17303 | -0.2681 | -0.1709 | 0.15564 | 0.10986 | 0.15106 | 0.10529 | 0.004578 | -0.1236 | -0.018311 | 0.061035 | -0.077972 | -0.26916 | -0.05127 | -0.15488 | -0.1474 | 0.11444 | 0.21515 | 0.059509 | -0.073242 | -0.045776 | -0.12817 | -0.041199 | 0.050354 | 0.022888 | -0.059509
1206.4375 | 0.045776 | 0.44647 | -0.45288 | -0.20187 | -0.16876 | -0.24994 | -0.16342 | 0.11902 | 0.009155 | 0.064087 | 0.07782 | 0.054932 | -0.14191 | -0.009155 | 0.030518 | -0.059814 | -0.25528 | -0.045929 | -0.14526 | -0.15167 | 0.022888 | 0.045776 | -0.045776 | -0.018311 | -0.013733 | -0.091553 | -0.009155 | 0.086975 | 0.009155 | -0.045776
1208.1719 | 0.030518 | 0.44968 | -0.47531 | -0.20508 | -0.16769 | -0.27985 | -0.1741 | 0.14648 | 0.091553 | 0.13733 | 0.11902 | -0.036621 | -0.11444 | -0.004578 | 0.045776 | -0.081177 | -0.2681 | -0.048065 | -0.15701 | -0.14206 | 0.10071 | 0.21057 | 0.050354 | -0.041199 | -0.041199 | -0.11902 | -0.036621 | 0.059509 | 0.036621 | -0.050354
1209.8438 | 0.061035 | 0.45181 | -0.45288 | -0.21149 | -0.15488 | -0.26489 | -0.16235 | 0.027466 | -0.064087 | 0.041199 | -0.018311 | -0.082397 | -0.041199 | 0.07782 | 0.061035 | -0.069427 | -0.25314 | -0.038452 | -0.1442 | -0.13565 | 0.036621 | 0.050354 | -0.041199 | -0.10986 | -0.10986 | -0.059509 | 0.009155 | -0.009155 | 0.032043 | -0.009155
1211.5938 | 0.045776 | 0.44861 | -0.44861 | -0.21576 | -0.16342 | -0.24887 | -0.16876 | 0.07782 | -0.036621 | 0.064087 | 0.032043 | 0.013733 | -0.07782 | 0.041199 | 0.076294 | -0.065155 | -0.24567 | -0.048065 | -0.13886 | -0.14633 | -0.041199 | -0.009155 | -0.10529 | -0.032043 | -0.045776 | -0.073242 | 0.004578 | -0.054932 | 0.050354 | 0
1213.3281 | 0.045776 | 0.45075 | -0.45395 | -0.2211 | -0.17197 | -0.27451 | -0.1741 | 0.064087 | -0.036621 | 0.068665 | 0.009155 | -0.10071 | -0.036621 | 0.073242 | 0.045776 | -0.083313 | -0.25528 | -0.040588 | -0.15808 | -0.13779 | 0.022888 | 0.059509 | -0.022888 | -0.1236 | -0.10986 | -0.036621 | 0.004578 | -0.009155 | 0.036621 | -0.018311
1215 | 0.076294 | 0.43259 | -0.45395 | -0.22644 | -0.17197 | -0.26276 | -0.16983 | 0.086975 | -0.009155 | 0.059509 | 0.09613 | 0.059509 | -0.13733 | -0.004578 | 0.045776 | -0.070496 | -0.25207 | -0.037384 | -0.16235 | -0.14526 | -0.004578 | 0.041199 | -0.050354 | -0.009155 | -0.004578 | -0.086975 | -0.041199 | 0.073242 | -0.004578 | -0.022888
1216.7344 | 0.061035 | 0.46249 | -0.4689 | -0.22751 | -0.16663 | -0.29907 | -0.17303 | 0.013733 | -0.041199 | 0.050354 | 0.004578 | -0.064087 | -0.064087 | 0.050354 | 0.030518 | -0.085449 | -0.2478 | -0.042725 | -0.16769 | -0.12497 | 0.036621 | 0.11902 | -0.013733 | -0.082397 | -0.073242 | -0.07782 | 0.004578 | 0.027466 | 0.059509 | -0.018311
1218.4844 | 0.076294 | 0.46997 | -0.4657 | -0.21149 | -0.17197 | -0.27023 | -0.18265 | 0.018311 | -0.032043 | 0.050354 | -0.027466 | -0.12817 | -0.032043 | 0.086975 | 0.061035 | -0.081177 | -0.26169 | -0.05127 | -0.15274 | -0.1474 | 0.050354 | 0.086975 | -0.027466 | -0.1236 | -0.10529 | -0.059509 | 0.009155 | -0.059509 | 0.068665 | 0.004578
1220.2188 | 0.061035 | 0.43259 | -0.45181 | -0.20935 | -0.16342 | -0.24033 | -0.16235 | 0.064087 | -0.041199 | 0.045776 | 0.004578 | -0.004578 | -0.073242 | 0.041199 | 0.045776 | -0.05661 | -0.24887 | -0.043793 | -0.15274 | -0.15701 | -0.059509 | -0.045776 | -0.10986 | -0.036621 | -0.022888 | -0.050354 | 0 | -0.068665 | 0.050354 | 0.004578
1221.875 | 0.045776 | 0.45502 | -0.45929 | -0.2243 | -0.16129 | -0.27985 | -0.1741 | 0.11902 | 0.073242 | 0.13275 | 0.068665 | -0.059509 | -0.073242 | 0.054932 | 0.045776 | -0.085449 | -0.2446 | -0.048065 | -0.17624 | -0.14954 | 0.10071 | 0.19226 | 0.022888 | -0.10986 | -0.091553 | -0.07782 | -0.009155 | 0.09613 | 0.022888 | -0.032043
1223.625 | 0.030518 | 0.4454 | -0.45181 | -0.20828 | -0.15488 | -0.25101 | -0.16876 | 0.064087 | -0.018311 | 0.068665 | 0.050354 | 0.050354 | -0.10529 | 0.013733 | 0.045776 | -0.057678 | -0.26169 | -0.050201 | -0.16342 | -0.15167 | 0.027466 | 0.07782 | -0.041199 | -0.004578 | -0.009155 | -0.09613 | -0.018311 | 0.082397 | -0.009155 | -0.032043
1225.3594 | 0.061035 | 0.45502 | -0.46783 | -0.22003 | -0.16342 | -0.27557 | -0.17303 | 0.07782 | 0.036621 | 0.12817 | 0.041199 | -0.07782 | -0.036621 | 0.054932 | 0.030518 | -0.069427 | -0.25635 | -0.05127 | -0.16449 | -0.14526 | 0.086975 | 0.19684 | 0.004578 | -0.10071 | -0.07782 | -0.073242 | 0.004578 | 0.050354 | 0.027466 | -0.032043
1227.0938 | 0.061035 | 0.439 | -0.45929 | -0.20401 | -0.16342 | -0.25528 | -0.16769 | 0.045776 | -0.045776 | 0.064087 | 0.045776 | 0.022888 | -0.068665 | 0.022888 | 0.030518 | -0.063019 | -0.25101 | -0.048065 | -0.14847 | -0.14206 | -0.009155 | 0.064087 | -0.050354 | 0.013733 | 0 | -0.10986 | -0.032043 | 0.082397 | 0 | -0.027466
1228.7656 | 0.045776 | 0.44006 | -0.45288 | -0.20081 | -0.15915 | -0.25101 | -0.16129 | 0.10529 | 0.004578 | 0.086975 | 0.054932 | 0.018311 | -0.086975 | 0.009155 | 0.030518 | -0.061951 | -0.25635 | -0.045929 | -0.15381 | -0.14847 | 0.013733 | 0.045776 | -0.050354 | -0.045776 | -0.027466 | -0.07782 | -0.009155 | -0.009155 | 0.018311 | 0
1230.5156 | 0.061035 | 0.44861 | -0.45075 | -0.20081 | -0.15488 | -0.25955 | -0.1709 | 0.064087 | -0.054932 | 0.054932 | 0.041199 | 0.004578 | -0.086975 | 0.032043 | 0.076294 | -0.072632 | -0.25955 | -0.036316 | -0.14633 | -0.13565 | -0.036621 | -0.022888 | -0.10071 | -0.022888 | 0 | -0.086975 | -0.022888 | -0.059509 | 0.045776 | 0.022888
1232.25 | 0.045776 | 0.46463 | -0.47318 | -0.20828 | -0.16129 | -0.27878 | -0.16983 | 0.082397 | 0.027466 | 0.09613 | 0.041199 | -0.050354 | -0.064087 | 0.027466 | 0.061035 | -0.087585 | -0.25207 | -0.046997 | -0.15915 | -0.13351 | 0.045776 | 0.068665 | -0.013733 | -0.11444 | -0.091553 | -0.064087 | 0.004578 | -0.07782 | 0.068665 | -0.022888
1233.9219 | 0.061035 | 0.4454 | -0.46249 | -0.22217 | -0.15808 | -0.25314 | -0.16342 | 0.050354 | -0.082397 | 0.036621 | 0.013733 | 0.022888 | -0.10071 | 0.050354 | 0.061035 | -0.058746 | -0.25528 | -0.041656 | -0.14847 | -0.1442 | -0.054932 | -0.041199 | -0.10529 | -0.022888 | -0.013733 | -0.086975 | -0.004578 | -0.050354 | 0.050354 | 0.022888
1235.6719 | 0.030518 | 0.45609 | -0.47104 | -0.2211 | -0.16129 | -0.28732 | -0.17838 | 0.073242 | -0.009155 | 0.041199 | 0.018311 | -0.073242 | -0.059509 | 0.050354 | 0.030518 | -0.089722 | -0.25848 | -0.038452 | -0.17303 | -0.14313 | 0.036621 | 0.068665 | -0.027466 | -0.091553 | -0.07782 | -0.07782 | -0.013733 | -0.054932 | 0.09613 | -0.013733
1237.4062 | 0.045776 | 0.44434 | -0.46249 | -0.21255 | -0.17944 | -0.25314 | -0.1709 | 0.022888 | -0.11444 | -0.004578 | 0 | 0.032043 | -0.07782 | 0.036621 | 0.061035 | -0.065155 | -0.24674 | -0.035248 | -0.1506 | -0.1442 | -0.050354 | -0.07782 | -0.11444 | -0.009155 | -0.009155 | -0.082397 | 0.004578 | -0.041199 | 0.054932 | 0.013733
1239.0781 | 0.045776 | 0.46249 | -0.46143 | -0.20935 | -0.16769 | -0.26489 | -0.16769 | 0.018311 | -0.086975 | 0 | -0.009155 | 0.013733 | -0.073242 | 0.050354 | 0.045776 | -0.068359 | -0.25101 | -0.035248 | -0.15274 | -0.13565 | -0.041199 | -0.036621 | -0.09613 | -0.036621 | -0.036621 | -0.09613 | 0.009155 | -0.009155 | 0.041199 | 0.004578
1240.7656 | 0.045776 | 0.43579 | -0.46356 | -0.21683 | -0.15915 | -0.25314 | -0.16663 | 0.091553 | -0.018311 | 0.082397 | 0.036621 | 0.009155 | -0.10986 | 0.041199 | 0.030518 | -0.057678 | -0.25207 | -0.027771 | -0.15488 | -0.14633 | -0.009155 | 0.022888 | -0.073242 | -0.022888 | -0.022888 | -0.091553 | 0 | -0.032043 | 0.022888 | 0.004578
1242.5 | 0.045776 | 0.439 | -0.46143 | -0.2179 | -0.16129 | -0.26276 | -0.16556 | 0.013733 | -0.07782 | 0.009155 | 0 | 0.022888 | -0.059509 | 0.050354 | 0.076294 | -0.060883 | -0.25207 | -0.041656 | -0.16129 | -0.1442 | -0.009155 | 0.050354 | -0.082397 | -0.018311 | -0.004578 | -0.07782 | -0.004578 | 0.10071 | 0.009155 | -0.018311
1244.2344 | 0.045776 | 0.44754 | -0.4657 | -0.22751 | -0.16022 | -0.27451 | -0.17838 | 0.073242 | -0.013733 | 0.073242 | 0.032043 | -0.032043 | -0.086975 | 0.045776 | 0.061035 | -0.076904 | -0.26169 | -0.043793 | -0.17731 | -0.13992 | 0 | 0.10986 | -0.064087 | -0.022888 | -0.032043 | -0.07782 | -0.009155 | 0.027466 | 0.009155 | -0.009155
1245.8906 | 0.061035 | 0.46783 | -0.45502 | -0.1976 | -0.15274 | -0.26916 | -0.17624 | 0.10529 | 0.009155 | 0.091553 | 0.073242 | -0.054932 | -0.073242 | 0.045776 | 0.045776 | -0.076904 | -0.27023 | -0.046997 | -0.15488 | -0.1442 | 0.054932 | 0.10071 | 0 | -0.10071 | -0.10071 | -0.07782 | -0.004578 | -0.032043 | 0.068665 | -0.036621
1247.5625 | 0.045776 | 0.46249 | -0.46143 | -0.23071 | -0.16663 | -0.28946 | -0.19012 | 0.050354 | -0.022888 | 0.050354 | 0.032043 | -0.032043 | -0.054932 | 0.036621 | 0.030518 | -0.085449 | -0.25207 | -0.043793 | -0.18158 | -0.15167 | 0.050354 | 0.12817 | 0.004578 | -0.086975 | -0.086975 | -0.07782 | 0 | 0.07782 | 0.036621 | -0.041199
1249.2344 | 0.045776 | 0.45502 | -0.46356 | -0.22217 | -0.15488 | -0.27664 | -0.18478 | 0.022888 | -0.050354 | 0.022888 | 0.018311 | -0.041199 | -0.059509 | 0.050354 | 0.076294 | -0.085449 | -0.24887 | -0.041656 | -0.16449 | -0.13886 | 0 | 0.068665 | -0.041199 | -0.082397 | -0.07782 | -0.064087 | 0.004578 | -0.004578 | 0.059509 | -0.036621
1250.9062 | 0.045776 | 0.45288 | -0.46249 | -0.19119 | -0.16556 | -0.27237 | -0.17944 | 0.10071 | 0.032043 | 0.09613 | 0.073242 | -0.041199 | -0.082397 | 0.036621 | 0.045776 | -0.084381 | -0.26169 | -0.044861 | -0.14954 | -0.15808 | 0.068665 | 0.091553 | 0.004578 | -0.09613 | -0.086975 | -0.068665 | -0.018311 | -0.050354 | 0.064087 | -0.013733
1252.6406 | 0.045776 | 0.45715 | -0.46997 | -0.21362 | -0.15488 | -0.25848 | -0.17624 | 0.045776 | -0.032043 | 0.050354 | 0 | 0.027466 | -0.064087 | 0.045776 | 0.045776 | -0.0737 | -0.26169 | -0.050201 | -0.15488 | -0.1506 | 0.009155 | 0.064087 | -0.073242 | -0.009155 | -0.022888 | -0.073242 | -0.009155 | 0.054932 | 0.013733 | -0.009155
1254.3906 | 0.045776 | 0.44113 | -0.4657 | -0.21149 | -0.15595 | -0.23926 | -0.16876 | 0.050354 | -0.07782 | 0.027466 | 0.022888 | 0.013733 | -0.07782 | 0.032043 | 0.045776 | -0.063019 | -0.25848 | -0.043793 | -0.13565 | -0.14633 | -0.068665 | -0.036621 | -0.1236 | -0.032043 | -0.018311 | -0.086975 | 0.004578 | -0.036621 | 0.045776 | 0.050354
1256.125 | 0.045776 | 0.45929 | -0.46997 | -0.22537 | -0.16449 | -0.29907 | -0.16876 | 0.027466 | -0.045776 | 0.022888 | 0.022888 | -0.041199 | -0.045776 | 0.059509 | 0.045776 | -0.09079 | -0.25314 | -0.050201 | -0.17303 | -0.15274 | 0.032043 | 0.091553 | -0.032043 | -0.091553 | -0.068665 | -0.064087 | -0.009155 | 0.032043 | 0.045776 | -0.022888
1257.7969 | 0.045776 | 0.43793 | -0.45181 | -0.20401 | -0.16663 | -0.25955 | -0.16556 | 0.10529 | -0.004578 | 0.10071 | 0.050354 | 0.022888 | -0.07782 | 0.027466 | 0.061035 | -0.063019 | -0.25848 | -0.041656 | -0.15701 | -0.14526 | 0.036621 | 0.073242 | -0.045776 | -0.041199 | -0.022888 | -0.07782 | -0.022888 | 0.050354 | -0.018311 | 0.004578
1259.4844 | 0.045776 | 0.45502 | -0.45929 | -0.20615 | -0.15808 | -0.25955 | -0.16769 | 0.09613 | -0.018311 | 0.073242 | 0.032043 | 0.009155 | -0.082397 | 0.045776 | 0.045776 | -0.074768 | -0.26169 | -0.037384 | -0.13992 | -0.1474 | -0.009155 | 0.013733 | -0.07782 | -0.036621 | -0.018311 | -0.07782 | -0.013733 | -0.027466 | 0.032043 | 0.022888
1261.1562 | 0.045776 | 0.42725 | -0.45715 | -0.2243 | -0.16769 | -0.2681 | -0.17944 | 0.032043 | -0.068665 | 0.032043 | 0.009155 | 0.036621 | -0.068665 | 0.059509 | 0.061035 | -0.068359 | -0.2478 | -0.044861 | -0.16769 | -0.13779 | -0.009155 | 0.045776 | -0.10529 | -0.009155 | -0.022888 | -0.086975 | 0 | 0.091553 | -0.018311 | -0.004578
1262.8281 | 0.045776 | 0.44754 | -0.47318 | -0.21042 | -0.16983 | -0.28946 | -0.17731 | 0.10529 | 0.036621 | 0.10071 | 0.045776 | -0.041199 | -0.068665 | 0.041199 | 0.030518 | -0.085449 | -0.2713 | -0.049133 | -0.17624 | -0.14099 | 0.10986 | 0.19684 | 0.050354 | -0.10071 | -0.086975 | -0.07782 | -0.004578 | 0.082397 | 0.013733 | -0.068665
1264.5781 | 0.045776 | 0.44861 | -0.46249 | -0.22324 | -0.16983 | -0.28091 | -0.17944 | 0.11444 | 0.041199 | 0.13275 | 0.059509 | -0.068665 | -0.082397 | 0.050354 | 0.045776 | -0.083313 | -0.25421 | -0.041656 | -0.16876 | -0.14633 | 0.091553 | 0.19226 | 0.022888 | -0.086975 | -0.09613 | -0.07782 | -0.013733 | 0.045776 | 0.013733 | -0.022888
1266.25 | 0.045776 | 0.42511 | -0.45181 | -0.21896 | -0.17197 | -0.25314 | -0.16449 | 0.032043 | -0.1236 | -0.009155 | 0.004578 | 0.027466 | -0.07782 | 0.036621 | 0.045776 | -0.057678 | -0.2478 | -0.033112 | -0.15274 | -0.14313 | -0.050354 | -0.086975 | -0.11444 | -0.018311 | -0.004578 | -0.07782 | 0 | -0.045776 | 0.036621 | 0.004578
1267.9375 | 0.045776 | 0.44434 | -0.46463 | -0.19974 | -0.16129 | -0.2446 | -0.16235 | 0.068665 | -0.032043 | 0.064087 | 0.022888 | 0.027466 | -0.07782 | 0.050354 | 0.030518 | -0.058746 | -0.26062 | -0.041656 | -0.14099 | -0.14313 | -0.027466 | -0.013733 | -0.086975 | -0.018311 | -0.018311 | -0.086975 | 0 | -0.050354 | 0.032043 | 0.027466
1269.6875 | 0.045776 | 0.45822 | -0.44968 | -0.20721 | -0.17197 | -0.25635 | -0.16342 | 0.073242 | -0.045776 | 0.059509 | 0.027466 | 0.013733 | -0.073242 | 0.059509 | 0.061035 | -0.067291 | -0.25742 | -0.03952 | -0.14847 | -0.14526 | -0.045776 | -0.027466 | -0.086975 | -0.027466 | -0.004578 | -0.07782 | 0 | -0.041199 | 0.050354 | 0.027466
1271.375 | 0.061035 | 0.4454 | -0.45929 | -0.21896 | -0.15488 | -0.28305 | -0.15167 | 0.09613 | 0.022888 | 0.082397 | 0.064087 | -0.036621 | -0.082397 | 0.018311 | 0.030518 | -0.077972 | -0.26596 | -0.043793 | -0.16129 | -0.13886 | 0.045776 | 0.068665 | 0.004578 | -0.10986 | -0.082397 | -0.07782 | -0.004578 | -0.018311 | 0.054932 | -0.027466
1273.1094 | 0.061035 | 0.4422 | -0.45715 | -0.22217 | -0.17303 | -0.25742 | -0.17731 | 0.009155 | -0.073242 | 0.027466 | 0.009155 | 0.027466 | -0.064087 | 0.050354 | 0.061035 | -0.065155 | -0.2446 | -0.036316 | -0.16129 | -0.1442 | -0.032043 | 0.059509 | -0.068665 | -0.013733 | -0.018311 | -0.10071 | -0.004578 | 0.10529 | -0.009155 | -0.018311
1274.7812 | 0.061035 | 0.44434 | -0.46356 | -0.21255 | -0.15915 | -0.27878 | -0.17838 | 0 | -0.045776 | 0.036621 | 0 | 0.022888 | -0.059509 | 0.036621 | 0.030518 | -0.083313 | -0.25421 | -0.030975 | -0.16129 | -0.1442 | -0.004578 | 0.064087 | -0.059509 | -0.018311 | -0.009155 | -0.064087 | -0.009155 | 0.059509 | 0 | 0.009155
1276.5312 | 0.045776 | 0.45181 | -0.47211 | -0.22217 | -0.16342 | -0.28732 | -0.1709 | 0.068665 | 0.027466 | 0.09613 | 0.054932 | -0.050354 | -0.082397 | 0.041199 | 0.061035 | -0.1004 | -0.25848 | -0.043793 | -0.17731 | -0.13886 | 0.10071 | 0.1831 | 0.032043 | -0.091553 | -0.07782 | -0.054932 | 0.004578 | 0.086975 | 0.022888 | -0.041199
1278.2031 | 0.045776 | 0.45609 | -0.47104 | -0.21042 | -0.17197 | -0.29587 | -0.18799 | 0.018311 | -0.041199 | 0.027466 | 0.004578 | -0.050354 | -0.068665 | 0.054932 | 0.091553 | -0.092926 | -0.25528 | -0.050201 | -0.15915 | -0.14206 | 0.027466 | 0.086975 | -0.032043 | -0.064087 | -0.059509 | -0.059509 | -0.004578 | 0.022888 | 0.045776 | -0.022888
1279.875 | 0.030518 | 0.45288 | -0.46463 | -0.21255 | -0.16556 | -0.26916 | -0.19012 | 0.11902 | 0.068665 | 0.13275 | 0.054932 | -0.041199 | -0.073242 | 0.041199 | 0.061035 | -0.071564 | -0.25421 | -0.053406 | -0.17731 | -0.1506 | 0.09613 | 0.20142 | 0.050354 | -0.091553 | -0.082397 | -0.086975 | -0.018311 | 0.086975 | 0.018311 | -0.032043
1281.6094 | 0.061035 | 0.43366 | -0.46249 | -0.19119 | -0.16449 | -0.2446 | -0.17197 | 0.10071 | -0.018311 | 0.07782 | 0.068665 | 0.032043 | -0.073242 | 0.036621 | 0.045776 | -0.054474 | -0.25207 | -0.03952 | -0.15595 | -0.15274 | 0.036621 | 0.054932 | -0.041199 | -0.027466 | -0.022888 | -0.091553 | -0.018311 | 0.07782 | -0.013733 | -0.027466
1283.3438 | 0.061035 | 0.44754 | -0.46463 | -0.23178 | -0.16663 | -0.27985 | -0.18051 | 0.022888 | -0.027466 | 0.022888 | 0.022888 | -0.041199 | -0.064087 | 0.045776 | 0.061035 | -0.083313 | -0.2478 | -0.045929 | -0.16876 | -0.1442 | 0.041199 | 0.082397 | -0.013733 | -0.073242 | -0.082397 | -0.068665 | 0.013733 | 0.054932 | 0.045776 | -0.018311
1285.0781 | 0.061035 | 0.439 | -0.47211 | -0.22003 | -0.16235 | -0.27451 | -0.17944 | 0.10529 | 0.059509 | 0.12817 | 0.068665 | -0.045776 | -0.07782 | 0.036621 | 0.045776 | -0.077972 | -0.26703 | -0.053406 | -0.15381 | -0.14847 | 0.086975 | 0.20142 | 0.013733 | -0.086975 | -0.07782 | -0.068665 | 0 | 0.064087 | 0.027466 | -0.054932
1286.7656 | 0.045776 | 0.44754 | -0.44754 | -0.20294 | -0.16556 | -0.24246 | -0.15701 | 0.050354 | -0.09613 | 0.018311 | 0 | 0.009155 | -0.07782 | 0.022888 | 0.045776 | -0.066223 | -0.25314 | -0.037384 | -0.15274 | -0.16129 | -0.068665 | -0.059509 | -0.11444 | -0.009155 | 0.004578 | -0.068665 | 0 | -0.054932 | 0.050354 | 0.027466
1288.4844 | 0.061035 | 0.45075 | -0.45609 | -0.22324 | -0.16556 | -0.27664 | -0.1741 | 0.11902 | 0.073242 | 0.12817 | 0.059509 | -0.045776 | -0.064087 | 0.018311 | 0.045776 | -0.089722 | -0.26169 | -0.041656 | -0.16663 | -0.13779 | 0.10529 | 0.19226 | 0.027466 | -0.09613 | -0.082397 | -0.082397 | -0.004578 | 0.082397 | 0.013733 | -0.022888
1290.2188 | 0.030518 | 0.45288 | -0.45288 | -0.21469 | -0.1709 | -0.27985 | -0.17838 | 0.027466 | -0.027466 | 0.027466 | 0.009155 | -0.050354 | -0.064087 | 0.045776 | 0.061035 | -0.087585 | -0.27237 | -0.048065 | -0.15915 | -0.15167 | 0.027466 | 0.07782 | -0.041199 | -0.086975 | -0.086975 | -0.064087 | 0.013733 | -0.013733 | 0.054932 | -0.036621
1291.8906 | 0.045776 | 0.45609 | -0.4689 | -0.21042 | -0.16449 | -0.27557 | -0.17731 | 0.054932 | 0.022888 | 0.064087 | 0.018311 | -0.068665 | -0.068665 | 0.045776 | 0.045776 | -0.075836 | -0.2681 | -0.050201 | -0.15167 | -0.13779 | 0.054932 | 0.059509 | -0.027466 | -0.07782 | -0.091553 | -0.07782 | -0.013733 | -0.059509 | 0.086975 | -0.027466
1293.6406 | 0.061035 | 0.4689 | -0.45288 | -0.20294 | -0.16022 | -0.2681 | -0.17303 | 0.11444 | 0.036621 | 0.091553 | 0.07782 | -0.059509 | -0.07782 | 0.036621 | 0.061035 | -0.060883 | -0.26916 | -0.040588 | -0.15274 | -0.15488 | 0.064087 | 0.09613 | 0.018311 | -0.09613 | -0.082397 | -0.064087 | -0.009155 | -0.054932 | 0.068665 | -0.018311
1295.4062 | 0.045776 | 0.44113 | -0.46356 | -0.20081 | -0.15808 | -0.2446 | -0.16235 | 0.091553 | -0.041199 | 0.059509 | 0.032043 | 0.013733 | -0.064087 | 0.032043 | 0.061035 | -0.064087 | -0.25742 | -0.036316 | -0.14526 | -0.14954 | -0.004578 | -0.004578 | -0.09613 | -0.022888 | -0.018311 | -0.086975 | -0.013733 | -0.036621 | 0.032043 | 0.009155
1297.1406 | 0.030518 | 0.47318 | -0.46997 | -0.21042 | -0.15701 | -0.29053 | -0.1709 | 0.041199 | 0.004578 | 0.041199 | 0.027466 | -0.059509 | -0.07782 | 0.036621 | 0.030518 | -0.077972 | -0.26596 | -0.042725 | -0.15808 | -0.14099 | 0.022888 | 0.068665 | -0.041199 | -0.086975 | -0.086975 | -0.07782 | -0.004578 | -0.036621 | 0.086975 | -0.009155
1298.8281 | 0.030518 | 0.45609 | -0.47852 | -0.21362 | -0.17303 | -0.27023 | -0.18265 | 0.059509 | -0.027466 | 0.018311 | 0.009155 | -0.036621 | -0.054932 | 0.054932 | 0.045776 | -0.066223 | -0.25528 | -0.038452 | -0.16449 | -0.14633 | 0.009155 | 0.059509 | -0.050354 | -0.091553 | -0.091553 | -0.064087 | 0.018311 | -0.027466 | 0.082397 | -0.032043
1300.5156 | 0.030518 | 0.46143 | -0.46677 | -0.20615 | -0.16129 | -0.26382 | -0.1741 | 0.068665 | -0.009155 | 0.036621 | 0.009155 | -0.059509 | -0.082397 | 0.036621 | 0.061035 | -0.075836 | -0.26169 | -0.05661 | -0.15381 | -0.14954 | 0.027466 | 0.064087 | -0.045776 | -0.082397 | -0.073242 | -0.064087 | 0.004578 | -0.059509 | 0.068665 | -0.022888
1302.1875 | 0.045776 | 0.45181 | -0.45929 | -0.20081 | -0.15808 | -0.23819 | -0.16556 | 0.054932 | -0.086975 | 0.027466 | 0.018311 | 0.018311 | -0.073242 | 0.036621 | 0.045776 | -0.042725 | -0.25207 | -0.043793 | -0.14099 | -0.15167 | -0.068665 | -0.050354 | -0.12817 | -0.027466 | -0.013733 | -0.045776 | -0.013733 | -0.045776 | 0.032043 | 0.032043
1303.8594 | 0.045776 | 0.44006 | -0.46249 | -0.22751 | -0.16449 | -0.26276 | -0.16876 | 0.041199 | -0.064087 | 0.009155 | 0.009155 | 0.036621 | -0.059509 | 0.050354 | 0.045776 | -0.070496 | -0.2446 | -0.041656 | -0.1506 | -0.14099 | -0.013733 | 0.059509 | -0.086975 | -0.022888 | -0.018311 | -0.07782 | 0 | 0.10986 | -0.022888 | 0
1305.5312 | 0.076294 | 0.46463 | -0.46783 | -0.20294 | -0.16663 | -0.26169 | -0.16235 | 0.10071 | 0.032043 | 0.073242 | 0.059509 | -0.032043 | -0.09613 | 0.013733 | 0.061035 | -0.081177 | -0.27344 | -0.052338 | -0.15274 | -0.14526 | 0.036621 | 0.073242 | 0 | -0.07782 | -0.07782 | -0.086975 | -0.032043 | -0.004578 | 0.045776 | 0.009155
1307.25 | 0.045776 | 0.47211 | -0.46249 | -0.21149 | -0.16983 | -0.28091 | -0.1709 | 0.073242 | 0.004578 | 0.073242 | 0.018311 | -0.045776 | -0.050354 | 0.07782 | 0.045776 | -0.082245 | -0.2478 | -0.040588 | -0.16235 | -0.13245 | 0.045776 | 0.068665 | -0.032043 | -0.10071 | -0.082397 | -0.064087 | 0.013733 | -0.050354 | 0.054932 | -0.036621
1308.9219 | 0.045776 | 0.45715 | -0.45715 | -0.21362 | -0.1709 | -0.26062 | -0.17624 | 0.11444 | 0.036621 | 0.091553 | 0.050354 | -0.054932 | -0.086975 | 0.036621 | 0.045776 | -0.081177 | -0.26276 | -0.048065 | -0.14847 | -0.15595 | 0.068665 | 0.10071 | 0.009155 | -0.10529 | -0.091553 | -0.07782 | 0.009155 | -0.027466 | 0.073242 | -0.009155
1310.6094 | 0.061035 | 0.43152 | -0.4689 | -0.22751 | -0.1506 | -0.27344 | -0.18906 | 0.091553 | 0.022888 | 0.09613 | 0.041199 | -0.032043 | -0.068665 | 0.027466 | 0.045776 | -0.077972 | -0.25742 | -0.050201 | -0.17197 | -0.14633 | 0.050354 | 0.11902 | -0.036621 | -0.041199 | -0.022888 | -0.059509 | 0.018311 | 0.045776 | 0.009155 | -0.018311
1312.2812 | 0.076294 | 0.4422 | -0.44968 | -0.21149 | -0.17517 | -0.25635 | -0.16769 | 0.10529 | 0.036621 | 0.09613 | 0.064087 | -0.054932 | -0.091553 | 0.041199 | 0.030518 | -0.084381 | -0.24674 | -0.044861 | -0.15381 | -0.14206 | 0.073242 | 0.10071 | 0.013733 | -0.091553 | -0.086975 | -0.073242 | -0.018311 | -0.050354 | 0.054932 | -0.018311
1313.9531 | 0.030518 | 0.4657 | -0.47852 | -0.20721 | -0.15915 | -0.27664 | -0.17303 | 0.09613 | 0.013733 | 0.07782 | 0.027466 | -0.045776 | -0.082397 | 0.045776 | 0.045776 | -0.082245 | -0.26916 | -0.037384 | -0.15701 | -0.14526 | 0.041199 | 0.073242 | -0.032043 | -0.10529 | -0.086975 | -0.064087 | 0.009155 | -0.064087 | 0.068665 | -0.013733
1315.7031 | 0.045776 | 0.44434 | -0.46463 | -0.21469 | -0.16449 | -0.25635 | -0.17838 | 0.032043 | -0.050354 | 0.027466 | -0.009155 | 0.018311 | -0.064087 | 0.054932 | 0.045776 | -0.064087 | -0.24246 | -0.037384 | -0.16556 | -0.13992 | 0.004578 | 0.064087 | -0.082397 | -0.013733 | -0.013733 | -0.059509 | 0 | 0.059509 | 0.004578 | -0.022888
1317.4375 | 0.045776 | 0.43579 | -0.80215 | -0.21683 | 0.18265 | -0.2681 | -0.16983 | 61.3632 | -63.2401 | 0.036621 | -63.4323 | 61.1481 | 63.4506 | 63.3224 | 0.061035 | -0.057678 | 0.092926 | 0.29907 | -0.16556 | -0.13672 | -0.018311 | 0.045776 | -63.6154 | 61.1114 | 61.1252 | 63.2217 | 63.3911 | 124.8322 | 63.2675 | 61.235
1319.1719 | 0.061035 | 0.43045 | -0.80109 | -0.20721 | 0.17731 | -0.26062 | -0.16983 | 61.3724 | -63.2172 | 0.054932 | -63.382 | 61.1481 | 63.382 | 63.2767 | 0.091553 | -0.05661 | 0.098267 | 0.30441 | -0.15595 | -0.15595 | 0.009155 | 0.054932 | -63.5834 | 61.1206 | 61.1206 | 63.1668 | 63.3682 | 124.8413 | 63.2675 | 61.203
1320.8594 | 0.045776 | 0.43259 | -0.79147 | -0.21469 | 0.18478 | -0.26382 | -0.16342 | 61.3312 | -63.2217 | 0.027466 | -63.4048 | 61.1343 | 63.3636 | 63.2904 | 0.030518 | -0.063019 | 0.10361 | 0.30014 | -0.16129 | -0.13672 | 0 | 0.041199 | -63.6154 | 61.1023 | 61.084 | 63.1439 | 63.3774 | 124.791 | 63.2629 | 61.1984
1322.5938 | 0.045776 | 0.4454 | -0.80215 | -0.23712 | 0.19119 | -0.28412 | -0.16556 | 61.3449 | -63.1302 | 0.086975 | -63.3545 | 61.084 | 63.3316 | 63.2767 | 0.030518 | -0.071564 | 0.10254 | 0.30334 | -0.18372 | -0.13992 | 0.032043 | 0.11444 | -63.5696 | 61.0611 | 61.0565 | 63.1348 | 63.3636 | 124.7314 | 63.2675 | 61.1984
1324.3281 | 0.045776 | 0.44006 | -0.80963 | -0.20828 | 0.17944 | -0.26169 | -0.17624 | 61.3174 | -63.1943 | 0.027466 | -63.3865 | 61.1343 | 63.3179 | 63.2355 | 0.045776 | -0.057678 | 0.088654 | 0.30868 | -0.15488 | -0.13351 | 0.009155 | 0.059509 | -63.5834 | 61.0886 | 61.1023 | 63.1119 | 63.3362 | 124.7498 | 63.2309 | 61.1938
1325.9844 | 0.061035 | 0.46677 | -0.80322 | -0.21362 | 0.18372 | -0.29587 | -0.18692 | 61.3129 | -63.1668 | 0.036621 | -63.3636 | 61.0703 | 63.3133 | 63.2217 | 0.061035 | -0.072632 | 0.091858 | 0.29907 | -0.16983 | -0.13245 | 0.059509 | 0.11444 | -63.5147 | 61.0107 | 61.0062 | 63.089 | 63.3362 | 124.7177 | 63.2767 | 61.1526
1327.7188 | 0.030518 | 0.45609 | -0.79788 | -0.20935 | 0.17731 | -0.26062 | -0.16342 | 61.3953 | -63.1027 | 0.091553 | -63.3179 | 61.0565 | 63.295 | 63.1989 | 0.045776 | -0.059814 | 0.088654 | 0.29907 | -0.1474 | -0.15488 | 0.064087 | 0.086975 | -63.501 | 61.0107 | 60.9695 | 63.0981 | 63.3087 | 124.617 | 63.3179 | 61.1801
1329.3906 | 0.076294 | 0.43579 | -0.80536 | -0.21896 | 0.16556 | -0.27344 | -0.16983 | 61.3678 | -63.0661 | 0.1236 | -63.3133 | 61.0245 | 63.2767 | 63.1989 | 0.061035 | -0.066223 | 0.076904 | 0.29694 | -0.16342 | -0.14847 | 0.13733 | 0.20599 | -63.4644 | 60.9924 | 60.9695 | 63.0707 | 63.3179 | 124.6811 | 63.2492 | 61.171
1331.1406 | 0.061035 | 0.46249 | -0.80643 | -0.21469 | 0.17838 | -0.2713 | -0.1709 | 61.3541 | -63.0524 | 0.10071 | -63.327 | 61.0382 | 63.2767 | 63.1943 | 0.061035 | -0.086517 | 0.086517 | 0.29694 | -0.15808 | -0.14099 | 0.14191 | 0.19226 | -63.446 | 60.9741 | 60.9467 | 63.089 | 63.2996 | 124.6994 | 63.2309 | 61.1435
1332.8125 | 0.076294 | 0.44647 | -0.78934 | -0.20721 | 0.16663 | -0.24033 | -0.16449 | 61.2717 | -63.2034 | -0.004578 | -63.3682 | 61.084 | 63.2767 | 63.1851 | 0.030518 | -0.052338 | 0.091858 | 0.30334 | -0.1474 | -0.1506 | -0.018311 | -0.073242 | -63.5834 | 61.0703 | 61.0519 | 63.0753 | 63.3179 | 124.585 | 63.2767 | 61.1893
1334.5469 | 0.045776 | 0.4657 | -0.80109 | -0.20401 | 0.17624 | -0.26276 | -0.15915 | 61.3815 | -63.0707 | 0.086975 | -63.2996 | 61.0428 | 63.2675 | 63.1805 | 0.045776 | -0.063019 | 0.086517 | 0.29907 | -0.15808 | -0.14847 | 0.086975 | 0.082397 | -63.4918 | 60.9741 | 60.9695 | 63.0707 | 63.2858 | 124.5941 | 63.2904 | 61.1572
1336.2812 | 0.061035 | 0.44861 | -0.79788 | -0.22217 | 0.18478 | -0.26062 | -0.16022 | 61.3449 | -63.0936 | 0.073242 | -63.3087 | 61.0428 | 63.2538 | 63.1897 | 0.045776 | -0.072632 | 0.09079 | 0.29587 | -0.1442 | -0.13779 | 0.082397 | 0.07782 | -63.4872 | 60.9924 | 60.9604 | 63.0661 | 63.2812 | 124.6078 | 63.2675 | 61.1481
1337.9531 | 0.045776 | 0.4454 | -0.80643 | -0.22217 | 0.1741 | -0.27557 | -0.1741 | 61.3541 | -63.089 | 0.1236 | -63.295 | 61.0062 | 63.2446 | 63.1714 | 0.10681 | -0.074768 | 0.089722 | 0.2948 | -0.17731 | -0.15167 | 0.091553 | 0.17395 | -63.4964 | 61.0016 | 61.0016 | 63.0798 | 63.2996 | 124.6582 | 63.2355 | 61.1572
1339.6875 | 0.061035 | 0.45075 | -0.79468 | -0.22003 | 0.17731 | -0.27237 | -0.17624 | 61.3358 | -63.0844 | 0.073242 | -63.3316 | 61.0107 | 63.2721 | 63.1897 | 0.015259 | -0.09079 | 0.077972 | 0.30655 | -0.15915 | -0.14206 | 0.073242 | 0.07782 | -63.4918 | 60.965 | 60.9467 | 63.0524 | 63.2904 | 124.5255 | 63.2767 | 61.1481
1341.4219 | 0.045776 | 0.45822 | -0.80856 | -0.2179 | 0.19333 | -0.27451 | -0.17624 | 61.2717 | -63.1348 | 0.018311 | -63.327 | 61.0474 | 63.2629 | 63.1943 | 0.045776 | -0.076904 | 0.084381 | 0.29373 | -0.15808 | -0.13886 | 0.050354 | 0.082397 | -63.5193 | 60.9604 | 60.9512 | 63.0707 | 63.3041 | 124.5758 | 63.2629 | 61.1481
1343.1406 | 0.045776 | 0.44327 | -0.80963 | -0.21149 | 0.19226 | -0.27023 | -0.18265 | 61.322 | -63.0844 | 0.10529 | -63.3133 | 61.0565 | 63.2721 | 63.1851 | 0.045776 | -0.067291 | 0.099335 | 0.28625 | -0.15274 | -0.14526 | 0.073242 | 0.11902 | -63.5284 | 61.0519 | 61.0016 | 63.089 | 63.2996 | 124.6124 | 63.2172 | 61.1572
1344.8281 | 0.045776 | 0.44647 | -0.80429 | -0.21896 | 0.17624 | -0.27237 | -0.16449 | 61.3083 | -63.121 | 0.059509 | -63.327 | 61.0016 | 63.2492 | 63.1989 | 0.045776 | -0.067291 | 0.089722 | 0.29053 | -0.17624 | -0.1506 | 0.059509 | 0.064087 | -63.5193 | 60.9833 | 60.9695 | 63.0661 | 63.2996 | 124.5346 | 63.2812 | 61.1526
1346.5625 | 0.045776 | 0.43686 | -0.7872 | -0.1976 | 0.17624 | -0.23926 | -0.15701 | 61.2854 | -63.1851 | 0.004578 | -63.3408 | 61.1206 | 63.2401 | 63.2034 | 0.061035 | -0.054474 | 0.09079 | 0.30014 | -0.14099 | -0.13779 | -0.018311 | -0.064087 | -63.5559 | 61.0474 | 61.0291 | 63.0615 | 63.2767 | 124.5529 | 63.2584 | 61.1755
1348.25 | 0.045776 | 0.42831 | -0.80536 | -0.1976 | 0.17624 | -0.25101 | -0.15701 | 61.2854 | -63.1805 | -0.004578 | -63.3591 | 61.1023 | 63.2629 | 63.1897 | 0.045776 | -0.059814 | 0.077972 | 0.28839 | -0.14206 | -0.14847 | -0.013733 | -0.050354 | -63.5742 | 61.0474 | 61.0291 | 63.0844 | 63.2858 | 124.5575 | 63.2721 | 61.171
1349.9531 | 0.061035 | 0.4422 | -0.79575 | -0.20721 | 0.18799 | -0.25742 | -0.15274 | 61.3403 | -63.0844 | 0.10529 | -63.2996 | 61.084 | 63.2492 | 63.1668 | 0.061035 | -0.045929 | 0.087585 | 0.30121 | -0.14633 | -0.13351 | 0.059509 | 0.073242 | -63.5101 | 61.0245 | 61.0336 | 63.0386 | 63.2675 | 124.5895 | 63.2034 | 61.1893
1351.6875 | 0.045776 | 0.46463 | -0.80643 | -0.22537 | 0.18692 | -0.28839 | -0.16556 | 61.2808 | -63.0936 | 0.050354 | -63.3041 | 61.0153 | 63.2217 | 63.1851 | 0.061035 | -0.083313 | 0.074768 | 0.29587 | -0.16769 | -0.13245 | 0.086975 | 0.13275 | -63.446 | 60.9604 | 60.965 | 63.0707 | 63.2629 | 124.6216 | 63.2034 | 61.116
1353.3906 | 0.076294 | 0.4454 | -0.79681 | -0.20081 | 0.17838 | -0.25314 | -0.16983 | 61.3037 | -63.1348 | 0.036621 | -63.3133 | 61.0519 | 63.2446 | 63.1714 | 0.045776 | -0.055542 | 0.077972 | 0.30548 | -0.14313 | -0.15274 | -0.022888 | -0.009155 | -63.5788 | 61.0474 | 61.0428 | 63.0569 | 63.2812 | 124.5117 | 63.2309 | 61.2122
1355.2188 | 0.061035 | 0.46783 | -0.80215 | -0.21255 | 0.17731 | -0.29694 | -0.1709 | 61.2762 | -63.1073 | 0.041199 | -63.3316 | 60.9924 | 63.2492 | 63.1668 | 0.045776 | -0.077972 | 0.070496 | 0.298 | -0.16769 | -0.1442 | 0.050354 | 0.073242 | -63.5056 | 60.9512 | 60.9695 | 63.0615 | 63.2675 | 124.5117 | 63.2675 | 61.1481
1357.0781 | 0.030518 | 0.46249 | -0.80002 | -0.21576 | 0.19119 | -0.26489 | -0.17517 | 61.2854 | -63.1577 | 0.032043 | -63.3408 | 61.0794 | 63.2767 | 63.1943 | 0.061035 | -0.060883 | 0.077972 | 0.29373 | -0.16663 | -0.1474 | 0.022888 | 0.041199 | -63.5559 | 61.0474 | 61.0245 | 63.0707 | 63.2904 | 124.6445 | 63.1714 | 61.1481
1358.8906 | 0.045776 | 0.45181 | -0.80215 | -0.22003 | 0.1709 | -0.27557 | -0.18158 | 61.2808 | -63.1027 | 0.041199 | -63.3041 | 60.9924 | 63.2401 | 63.1622 | 0.045776 | -0.075836 | 0.083313 | 0.28519 | -0.16449 | -0.14206 | 0.045776 | 0.07782 | -63.5056 | 60.9558 | 60.9695 | 63.0753 | 63.2767 | 124.5117 | 63.2446 | 61.1343
1360.6406 | 0.061035 | 0.43472 | -0.78827 | -0.2179 | 0.16983 | -0.24246 | -0.16876 | 61.3403 | -63.0753 | 0.10986 | -63.2858 | 61.1023 | 63.2355 | 63.1485 | 0.045776 | -0.063019 | 0.089722 | 0.2948 | -0.15167 | -0.1506 | 0.045776 | 0.045776 | -63.4964 | 61.0382 | 61.0062 | 63.0615 | 63.2812 | 124.5529 | 63.1851 | 61.1389
1362.3281 | 0.076294 | 0.42191 | -0.8139 | -0.21469 | 0.1709 | -0.27023 | -0.1709 | 61.2488 | -63.1485 | 0.018311 | -63.3316 | 61.0794 | 63.2401 | 63.176 | 0.030518 | -0.066223 | 0.085449 | 0.2948 | -0.15701 | -0.13672 | 0 | 0.045776 | -63.5513 | 61.0428 | 61.0428 | 63.0432 | 63.2584 | 124.6216 | 63.1851 | 61.1389
1363.9688 | 0.061035 | 0.44113 | -0.80429 | -0.2211 | 0.18051 | -0.2713 | -0.17303 | 61.3129 | -63.0249 | 0.13733 | -63.2629 | 60.9879 | 63.2309 | 63.1531 | 0.015259 | -0.075836 | 0.086517 | 0.29373 | -0.1709 | -0.13138 | 0.1236 | 0.20599 | -63.414 | 60.9421 | 60.9604 | 63.0524 | 63.2584 | 124.6033 | 63.1943 | 61.0977
1365.6719 | 0.015259 | 0.46143 | -0.80856 | -0.20935 | 0.16556 | -0.27664 | -0.17624 | 61.2259 | -63.1073 | 0.027466 | -63.3224 | 61.0016 | 63.2309 | 63.1668 | 0.030518 | -0.082245 | 0.080109 | 0.29907 | -0.16769 | -0.13672 | 0.068665 | 0.10071 | -63.4872 | 60.9375 | 60.9375 | 63.0569 | 63.2858 | 124.5575 | 63.1943 | 61.1023
1367.3281 | 0.045776 | 0.45822 | -0.8107 | -0.20401 | 0.16876 | -0.28091 | -0.18372 | 61.2808 | -63.0936 | 0.041199 | -63.3133 | 60.9924 | 63.2217 | 63.1393 | 0.030518 | -0.0737 | 0.082245 | 0.28732 | -0.15808 | -0.14633 | 0.054932 | 0.073242 | -63.4872 | 60.9467 | 60.9375 | 63.0615 | 63.2721 | 124.4797 | 63.2263 | 61.1343
1368.9844 | 0.076294 | 0.45929 | -0.79254 | -0.20081 | 0.17731 | -0.26596 | -0.18372 | 61.2579 | -63.1119 | 0.027466 | -63.3179 | 61.0107 | 63.2401 | 63.1622 | 0.076294 | -0.074768 | 0.0737 | 0.29159 | -0.15488 | -0.15488 | 0.054932 | 0.082397 | -63.4872 | 60.9558 | 60.9512 | 63.0524 | 63.2721 | 124.5163 | 63.2446 | 61.1252
1370.6406 | 0.045776 | 0.45181 | -0.80215 | -0.21149 | 0.17944 | -0.26489 | -0.17303 | 61.2991 | -63.0981 | 0.045776 | -63.3224 | 60.997 | 63.208 | 63.1668 | 0.030518 | -0.072632 | 0.076904 | 0.28412 | -0.16022 | -0.1474 | 0.050354 | 0.064087 | -63.4872 | 60.9375 | 60.9512 | 63.0524 | 63.2721 | 124.4659 | 63.2492 | 61.1298
1372.3438 | 0.030518 | 0.45609 | -0.80002 | -0.21469 | 0.18478 | -0.27557 | -0.18265 | 61.2762 | -63.1119 | 0.018311 | -63.3087 | 60.997 | 63.2446 | 63.1531 | 0.045776 | -0.068359 | 0.079041 | 0.28625 | -0.15701 | -0.13565 | 0.045776 | 0.068665 | -63.501 | 60.9375 | 60.9695 | 63.0569 | 63.2492 | 124.4934 | 63.2401 | 61.116
1374.0156 | 0.061035 | 0.44006 | -0.80002 | -0.1944 | 0.16769 | -0.23605 | -0.17517 | 61.2717 | -63.1714 | 0.004578 | -63.3224 | 61.0977 | 63.2309 | 63.1439 | 0.091553 | -0.053406 | 0.084381 | 0.30014 | -0.1442 | -0.14847 | -0.022888 | -0.059509 | -63.5468 | 61.0382 | 61.0153 | 63.0066 | 63.2629 | 124.4751 | 63.2355 | 61.1801
1375.6719 | 0.076294 | 0.44434 | -0.79254 | -0.20401 | 0.16556 | -0.24246 | -0.15381 | 61.2396 | -63.1668 | -0.018311 | -63.3316 | 61.0748 | 63.2217 | 63.1714 | 0.045776 | -0.067291 | 0.086517 | 0.29373 | -0.14099 | -0.14206 | -0.018311 | -0.064087 | -63.5605 | 61.0245 | 61.0336 | 63.0661 | 63.2858 | 124.4614 | 63.208 | 61.1481
1377.3281 | 0.076294 | 0.45609 | -0.79788 | -0.20401 | 0.1709 | -0.25848 | -0.16663 | 61.2671 | -63.121 | 0.018311 | -63.3041 | 61.0519 | 63.2309 | 63.1485 | 0.061035 | -0.061951 | 0.068359 | 0.29907 | -0.14954 | -0.1474 | 0.027466 | 0.009155 | -63.4964 | 60.9879 | 60.965 | 63.0524 | 63.2446 | 124.4934 | 63.2263 | 61.116
1378.9844 | 0.061035 | 0.45822 | -0.79361 | -0.19974 | 0.16342 | -0.26276 | -0.16022 | 61.3083 | -63.0524 | 0.07782 | -63.2492 | 60.9833 | 63.1989 | 63.1439 | 0.076294 | -0.072632 | 0.071564 | 0.298 | -0.14847 | -0.13031 | 0.073242 | 0.068665 | -63.4323 | 60.9421 | 60.9421 | 63.0249 | 63.2584 | 124.5117 | 63.2263 | 61.1389
1380.6562 | 0.045776 | 0.44861 | -0.79681 | -0.2179 | 0.16663 | -0.24246 | -0.15808 | 61.235 | -63.1531 | 0.004578 | -63.3224 | 61.0565 | 63.2172 | 63.1531 | 0.076294 | -0.066223 | 0.085449 | 0.29266 | -0.15488 | -0.14526 | -0.013733 | -0.050354 | -63.533 | 61.0016 | 60.9924 | 63.0615 | 63.2492 | 124.4843 | 63.208 | 61.116
1382.3125 | 0.076294 | 0.44861 | -0.79361 | -0.21149 | 0.17838 | -0.27023 | -0.16876 | 61.2991 | -63.0386 | 0.086975 | -63.2446 | 60.9787 | 63.1897 | 63.1119 | 0.061035 | -0.080109 | 0.087585 | 0.29266 | -0.15167 | -0.14633 | 0.068665 | 0.068665 | -63.4323 | 60.9375 | 60.9192 | 63.0341 | 63.2446 | 124.4797 | 63.2355 | 61.116
1383.9688 | 0.061035 | 0.44327 | -0.80215 | -0.21149 | 0.16663 | -0.24353 | -0.15381 | 61.2946 | -63.0478 | 0.10071 | -63.2355 | 61.0703 | 63.1989 | 63.1119 | 0.045776 | -0.065155 | 0.085449 | 0.29159 | -0.15488 | -0.14954 | 0.045776 | 0.050354 | -63.4689 | 61.0062 | 61.0153 | 63.0524 | 63.2446 | 124.498 | 63.1805 | 61.1069
1385.6406 | 0.045776 | 0.45075 | -0.79895 | -0.22858 | 0.17303 | -0.28519 | -0.17197 | 61.2854 | -62.9929 | 0.14191 | -63.2584 | 60.9467 | 63.2126 | 63.121 | 0.061035 | -0.091858 | 0.085449 | 0.27878 | -0.16129 | -0.13565 | 0.11902 | 0.21515 | -63.414 | 60.9009 | 60.9329 | 63.0295 | 63.2401 | 124.5392 | 63.1805 | 61.084
1387.2969 | 0.061035 | 0.4454 | -0.79468 | -0.23712 | 0.18478 | -0.26703 | -0.18692 | 61.2579 | -63.0203 | 0.09613 | -63.2538 | 61.0062 | 63.2172 | 63.1439 | 0.045776 | -0.080109 | 0.095062 | 0.28732 | -0.16663 | -0.14954 | 0.073242 | 0.13733 | -63.4415 | 60.9695 | 60.9787 | 63.0478 | 63.2629 | 124.53 | 63.1577 | 61.1114
1388.9688 | 0.061035 | 0.4422 | -0.80429 | -0.22324 | 0.17197 | -0.26596 | -0.16983 | 61.2534 | -63.0341 | 0.082397 | -63.2584 | 61.0153 | 63.1989 | 63.1073 | 0.045776 | -0.075836 | 0.079041 | 0.30121 | -0.16663 | -0.14313 | 0.054932 | 0.11444 | -63.4827 | 60.9833 | 60.9695 | 63.0341 | 63.2584 | 124.5071 | 63.1714 | 61.1023
1390.6406 | 0.061035 | 0.41977 | -0.78079 | -0.20401 | 0.15488 | -0.2478 | -0.16983 | 61.2625 | -63.0707 | 0.091553 | -63.2584 | 61.0703 | 63.2172 | 63.1256 | 0.076294 | -0.054474 | 0.080109 | 0.29053 | -0.15274 | -0.15808 | 0.059509 | 0.086975 | -63.446 | 61.0153 | 60.9833 | 63.0066 | 63.2629 | 124.5666 | 63.1577 | 61.1481
1392.2969 | 0.045776 | 0.44647 | -0.79681 | -0.20615 | 0.17303 | -0.25635 | -0.16342 | 61.2167 | -63.1256 | 0 | -63.3087 | 61.0611 | 63.2172 | 63.1393 | 0.061035 | -0.061951 | 0.082245 | 0.29159 | -0.16342 | -0.14954 | -0.004578 | -0.054932 | -63.5101 | 61.0153 | 60.965 | 63.0295 | 63.2538 | 124.4568 | 63.1943 | 61.1069
1393.9531 | 0.061035 | 0.45288 | -0.79788 | -0.19974 | 0.18158 | -0.25207 | -0.16129 | 61.1847 | -63.1485 | -0.009155 | -63.3087 | 61.0519 | 63.2034 | 63.1302 | 0.061035 | -0.067291 | 0.076904 | 0.29159 | -0.14847 | -0.13672 | -0.027466 | -0.064087 | -63.533 | 61.0153 | 61.0062 | 63.0066 | 63.2401 | 124.4156 | 63.2034 | 61.1526
1395.6406 | 0.045776 | 0.44006 | -0.79041 | -0.2211 | 0.16983 | -0.24567 | -0.16022 | 61.2808 | -63.0295 | 0.10529 | -63.2492 | 61.0519 | 63.1714 | 63.121 | 0.045776 | -0.053406 | 0.082245 | 0.29266 | -0.1474 | -0.13351 | 0.036621 | 0.082397 | -63.446 | 60.9924 | 61.0062 | 63.0157 | 63.2263 | 124.498 | 63.1714 | 61.1298
1397.2969 | 0.076294 | 0.43793 | -0.79361 | -0.20721 | 0.17731 | -0.26596 | -0.16129 | 61.1984 | -63.1348 | 0.004578 | -63.295 | 61.0748 | 63.1897 | 63.1073 | 0.030518 | -0.052338 | 0.083313 | 0.28625 | -0.14847 | -0.13458 | -0.054932 | -0.059509 | -63.5422 | 61.0153 | 60.9833 | 63.0341 | 63.2446 | 124.4293 | 63.208 | 61.1435
1398.9531 | 0.045776 | 0.45181 | -0.79254 | -0.20615 | 0.17731 | -0.26489 | -0.17624 | 61.203 | -63.1119 | 0.009155 | -63.2858 | 61.0474 | 63.2034 | 63.1302 | 0.045776 | -0.054474 | 0.072632 | 0.29373 | -0.1506 | -0.13779 | -0.032043 | -0.041199 | -63.501 | 60.9924 | 60.9879 | 63.0249 | 63.2355 | 124.4614 | 63.1943 | 61.084
1400.625 | 0.045776 | 0.44113 | -0.79468 | -0.24567 | 0.15595 | -0.27451 | -0.17838 | 61.1938 | -63.1165 | 0.027466 | -63.2858 | 61.0336 | 63.1851 | 63.1485 | 0.076294 | -0.070496 | 0.088654 | 0.298 | -0.17838 | -0.1474 | 0 | 0.054932 | -63.501 | 60.997 | 60.997 | 63.0386 | 63.2401 | 124.5438 | 63.1302 | 61.1069
1402.2812 | 0.045776 | 0.4454 | -0.79575 | -0.23285 | 0.17731 | -0.27451 | -0.18265 | 61.1984 | -63.089 | 0.022888 | -63.2904 | 61.0199 | 63.1943 | 63.1256 | 0.045776 | -0.0737 | 0.080109 | 0.30014 | -0.16769 | -0.1506 | 0.013733 | 0.064087 | -63.4872 | 60.9879 | 61.0153 | 63.0432 | 63.2446 | 124.498 | 63.1714 | 61.1023
1403.9375 | 0.061035 | 0.43366 | -0.79147 | -0.22537 | 0.17944 | -0.27023 | -0.17197 | 61.1801 | -63.089 | 0.041199 | -63.295 | 61.0336 | 63.2034 | 63.1348 | 0.061035 | -0.065155 | 0.091858 | 0.29907 | -0.17624 | -0.15274 | 0.004578 | 0.045776 | -63.4735 | 61.0062 | 60.997 | 63.0432 | 63.2355 | 124.5255 | 63.1393 | 61.0977
1405.625 | 0.045776 | 0.44647 | -0.79575 | -0.20294 | 0.17838 | -0.25635 | -0.16769 | 61.1893 | -63.1073 | -0.009155 | -63.2904 | 61.0291 | 63.1897 | 63.0936 | 0.045776 | -0.072632 | 0.086517 | 0.298 | -0.1442 | -0.14099 | -0.022888 | -0.045776 | -63.4872 | 61.0016 | 60.9741 | 63.002 | 63.2538 | 124.4476 | 63.1805 | 61.1069
1407.2812 | 0.045776 | 0.4454 | -0.79468 | -0.20187 | 0.18265 | -0.27023 | -0.16663 | 61.203 | -63.1119 | 0.004578 | -63.2812 | 61.0336 | 63.1943 | 63.1256 | 0.045776 | -0.067291 | 0.070496 | 0.28946 | -0.15595 | -0.14313 | 0.022888 | -0.018311 | -63.4644 | 60.9558 | 60.9741 | 63.0112 | 63.2172 | 124.4522 | 63.176 | 61.0748
1408.9375 | 0.045776 | 0.47211 | -0.80963 | -0.20721 | 0.16876 | -0.28732 | -0.17838 | 61.1984 | -63.0432 | 0.045776 | -63.2629 | 60.965 | 63.1989 | 63.1119 | 0.061035 | -0.087585 | 0.063019 | 0.28091 | -0.16769 | -0.13672 | 0.082397 | 0.13275 | -63.414 | 60.91 | 60.9467 | 63.0066 | 63.2217 | 124.4888 | 63.1531 | 61.0474
1410.7188 | 0.045776 | 0.44113 | -0.79681 | -0.2179 | 0.17624 | -0.27664 | -0.16663 | 61.2717 | -63.0066 | 0.10986 | -63.2263 | 60.9695 | 63.1943 | 63.1165 | 0.061035 | -0.075836 | 0.077972 | 0.28198 | -0.16449 | -0.14954 | 0.068665 | 0.16937 | -63.414 | 60.9604 | 60.9695 | 62.9974 | 63.208 | 124.4705 | 63.1256 | 61.084
1412.4375 | 0.061035 | 0.44861 | -0.79361 | -0.20828 | 0.16449 | -0.25742 | -0.16769 | 61.2167 | -63.0981 | 0.032043 | -63.2812 | 61.0107 | 63.1805 | 63.1119 | 0.045776 | -0.066223 | 0.079041 | 0.29266 | -0.15167 | -0.1506 | 0.027466 | -0.004578 | -63.4506 | 60.9467 | 60.9421 | 63.0203 | 63.2172 | 124.4568 | 63.1943 | 61.0977
1414.125 | 0.045776 | 0.43045 | -0.78293 | -0.22751 | 0.17517 | -0.25314 | -0.17517 | 61.203 | -63.1027 | 0.027466 | -63.2675 | 61.0291 | 63.176 | 63.121 | 0.045776 | -0.063019 | 0.095062 | 0.29053 | -0.16342 | -0.15381 | 0.032043 | 0.068665 | -63.4598 | 60.997 | 60.9924 | 63.0112 | 63.1989 | 124.5346 | 63.1165 | 61.0977
1415.7969 | 0.061035 | 0.44113 | -0.78934 | -0.19974 | 0.16769 | -0.24139 | -0.16983 | 61.2213 | -63.089 | 0.032043 | -63.2675 | 61.0336 | 63.1851 | 63.0936 | 0.061035 | -0.063019 | 0.089722 | 0.28839 | -0.15167 | -0.14633 | -0.013733 | -0.032043 | -63.501 | 60.9924 | 60.997 | 63.002 | 63.1989 | 124.3835 | 63.1805 | 61.1252
1417.5312 | 0.061035 | 0.43366 | -0.77652 | -0.21362 | 0.18478 | -0.26062 | -0.15488 | 61.171 | -63.1393 | -0.009155 | -63.2812 | 61.0428 | 63.1897 | 63.1256 | 0.030518 | -0.067291 | 0.09079 | 0.298 | -0.1506 | -0.14526 | -0.041199 | -0.041199 | -63.501 | 60.9787 | 60.9879 | 63.0203 | 63.208 | 124.3835 | 63.1714 | 61.1069
1419.2656 | 0.045776 | 0.42511 | -0.80749 | -0.21362 | 0.17517 | -0.26276 | -0.15167 | 61.2579 | -63.0112 | 0.09613 | -63.2217 | 61.0336 | 63.1714 | 63.089 | 0.061035 | -0.058746 | 0.082245 | 0.29587 | -0.16235 | -0.1442 | 0.050354 | 0.068665 | -63.4415 | 60.9787 | 60.9787 | 63.002 | 63.1943 | 124.4522 | 63.1439 | 61.0977
1421 | 0.045776 | 0.42404 | -0.79254 | -0.21042 | 0.16556 | -0.25314 | -0.15701 | 61.2442 | -63.0157 | 0.10529 | -63.2172 | 61.0291 | 63.1577 | 63.0798 | 0.045776 | -0.05661 | 0.074768 | 0.30228 | -0.15381 | -0.1442 | 0.050354 | 0.068665 | -63.4277 | 60.9741 | 60.9833 | 62.9837 | 63.2034 | 124.4476 | 63.1531 | 61.1069
1422.6875 | 0.045776 | 0.44861 | -0.80002 | -0.20401 | 0.16342 | -0.29159 | -0.17624 | 61.2396 | -62.9929 | 0.091553 | -63.2217 | 60.91 | 63.1668 | 63.089 | 0.045776 | -0.083313 | 0.072632 | 0.28625 | -0.14847 | -0.14206 | 0.073242 | 0.09613 | -63.3911 | 60.8917 | 60.9329 | 63.0157 | 63.2263 | 124.3607 | 63.1805 | 61.0977
1424.3594 | 0.045776 | 0.44006 | -0.79468 | -0.22964 | 0.1741 | -0.298 | -0.17197 | 61.2488 | -62.9471 | 0.11902 | -63.2126 | 60.9512 | 63.1668 | 63.0844 | 0.045776 | -0.079041 | 0.086517 | 0.27985 | -0.1709 | -0.15167 | 0.10986 | 0.21057 | -63.3499 | 60.8871 | 60.9146 | 63.0066 | 63.2172 | 124.4934 | 63.1348 | 61.0428
1426.0312 | 0.061035 | 0.44754 | -0.79575 | -0.21683 | 0.17197 | -0.25528 | -0.17731 | 61.1984 | -63.0615 | 0.022888 | -63.2629 | 61.0107 | 63.176 | 63.1027 | 0.045776 | -0.060883 | 0.068359 | 0.2948 | -0.1442 | -0.13672 | 0.027466 | 0.018311 | -63.4323 | 60.9375 | 60.9238 | 62.9929 | 63.1943 | 124.4202 | 63.2034 | 61.0703
1427.7188 | 0.030518 | 0.4422 | -0.80109 | -0.22964 | 0.17517 | -0.28091 | -0.16983 | 61.1526 | -63.0569 | 0.027466 | -63.2538 | 60.9283 | 63.1805 | 63.1073 | 0.045776 | -0.083313 | 0.086517 | 0.29587 | -0.17303 | -0.14099 | 0.045776 | 0.068665 | -63.4232 | 60.9009 | 60.878 | 63.0203 | 63.2492 | 124.4156 | 63.2126 | 61.0474
1429.4531 | 0.030518 | 0.4422 | -0.80109 | -0.21149 | 0.17517 | -0.28198 | -0.18478 | 61.1618 | -63.0432 | 0.032043 | -63.2538 | 60.9467 | 63.1851 | 63.1302 | 0.061035 | -0.077972 | 0.087585 | 0.28412 | -0.16342 | -0.13886 | 0.059509 | 0.09613 | -63.4003 | 60.9238 | 60.9146 | 63.0203 | 63.2355 | 124.4293 | 63.1577 | 61.0565
1431.1875 | 0.061035 | 0.43045 | -0.79147 | -0.22537 | 0.15701 | -0.24246 | -0.16769 | 61.235 | -63.0249 | 0.07782 | -63.2126 | 61.0245 | 63.1668 | 63.0661 | 0.030518 | -0.058746 | 0.084381 | 0.29373 | -0.1442 | -0.14847 | 0.064087 | 0.082397 | -63.4232 | 60.9833 | 60.9375 | 63.002 | 63.2263 | 124.4888 | 63.0936 | 61.0748
1432.875 | 0.045776 | 0.45822 | -0.80002 | -0.2211 | 0.17624 | -0.28519 | -0.17624 | 61.1526 | -63.0386 | 0.013733 | -63.2584 | 60.9604 | 63.1943 | 63.1073 | 0.045776 | -0.074768 | 0.075836 | 0.28839 | -0.16663 | -0.12924 | 0.032043 | 0.07782 | -63.4186 | 60.8963 | 60.8963 | 63.0112 | 63.2172 | 124.3927 | 63.1851 | 61.0336
1434.6094 | 0.030518 | 0.45395 | -0.7872 | -0.19012 | 0.15808 | -0.24887 | -0.17731 | 61.1893 | -63.0936 | -0.009155 | -63.2629 | 61.0199 | 63.176 | 63.0844 | 0.045776 | -0.064087 | 0.083313 | 0.298 | -0.14954 | -0.15381 | -0.004578 | -0.073242 | -63.4827 | 61.0016 | 60.9512 | 62.9883 | 63.1989 | 124.3881 | 63.176 | 61.0977
1436.3594 | 0.061035 | 0.45181 | -0.78079 | -0.21469 | 0.17517 | -0.26276 | -0.16663 | 61.2442 | -63.0112 | 0.045776 | -63.1989 | 60.9329 | 63.1943 | 63.0753 | 0.076294 | -0.063019 | 0.075836 | 0.2948 | -0.14633 | -0.15167 | 0.032043 | 0.032043 | -63.382 | 60.8917 | 60.9192 | 63.002 | 63.2034 | 124.3835 | 63.176 | 61.0703
1438.0938 | 0.061035 | 0.4422 | -0.78613 | -0.20935 | 0.18158 | -0.25207 | -0.15915 | 61.1481 | -63.1302 | -0.054932 | -63.2812 | 61.0107 | 63.1714 | 63.1256 | 0.045776 | -0.061951 | 0.081177 | 0.29266 | -0.1474 | -0.14847 | -0.054932 | -0.10071 | -63.501 | 60.9695 | 60.9421 | 63.0066 | 63.1943 | 124.3607 | 63.1714 | 61.1069
1439.7812 | 0.045776 | 0.43579 | -0.7872 | -0.20828 | 0.16769 | -0.25528 | -0.16342 | 61.171 | -63.0753 | -0.036621 | -63.2629 | 60.9741 | 63.1851 | 63.1256 | 0.045776 | -0.059814 | 0.080109 | 0.30014 | -0.1474 | -0.14954 | -0.013733 | -0.041199 | -63.4277 | 60.9238 | 60.9192 | 63.0066 | 63.1989 | 124.3927 | 63.1668 | 61.0428
1441.5312 | 0.061035 | 0.43152 | -0.78934 | -0.21683 | 0.18265 | -0.26382 | -0.1709 | 61.1526 | -63.0478 | 0.068665 | -63.2492 | 61.0153 | 63.1577 | 63.0981 | 0.061035 | -0.079041 | 0.085449 | 0.29159 | -0.16663 | -0.13245 | 0.054932 | 0.10529 | -63.4552 | 60.9787 | 60.9695 | 62.9837 | 63.1805 | 124.4522 | 63.1302 | 61.0657
1443.25 | 0.045776 | 0.46997 | -0.81177 | -0.20187 | 0.16129 | -0.28305 | -0.17731 | 61.1664 | -63.0432 | 0.041199 | -63.2492 | 60.9512 | 63.1622 | 63.089 | 0.045776 | -0.086517 | 0.0737 | 0.28732 | -0.16769 | -0.14099 | 0.064087 | 0.11902 | -63.3957 | 60.9009 | 60.9238 | 62.9745 | 63.1989 | 124.379 | 63.1439 | 61.0794
1444.9375 | 0.045776 | 0.45075 | -0.79895 | -0.22751 | 0.17303 | -0.27771 | -0.17731 | 61.2259 | -62.9425 | 0.14648 | -63.1851 | 60.9375 | 63.1348 | 63.0753 | 0.061035 | -0.089722 | 0.072632 | 0.29053 | -0.16876 | -0.14847 | 0.16937 | 0.22888 | -63.3316 | 60.8871 | 60.878 | 62.9745 | 63.1805 | 124.4614 | 63.1165 | 61.0291
1446.6875 | 0.030518 | 0.44327 | -0.79681 | -0.2243 | 0.1709 | -0.26276 | -0.17838 | 61.2305 | -62.9517 | 0.17395 | -63.1805 | 60.9467 | 63.1439 | 63.0661 | 0.061035 | -0.074768 | 0.074768 | 0.28732 | -0.17303 | -0.14633 | 0.15564 | 0.2243 | -63.3636 | 60.9055 | 60.9009 | 62.9883 | 63.1897 | 124.4293 | 63.0981 | 61.0382
1448.4219 | 0.061035 | 0.45075 | -0.80429 | -0.21042 | 0.1709 | -0.27451 | -0.17731 | 61.2442 | -62.9196 | 0.17853 | -63.1714 | 60.9467 | 63.1668 | 63.0569 | 0.061035 | -0.072632 | 0.071564 | 0.28412 | -0.16342 | -0.16342 | 0.15106 | 0.25635 | -63.327 | 60.9009 | 60.9009 | 62.9654 | 63.1668 | 124.4064 | 63.0981 | 61.0657
1450.1406 | 0.045776 | 0.44647 | -0.78613 | -0.22217 | 0.17731 | -0.2681 | -0.18372 | 61.2396 | -62.9196 | 0.17395 | -63.1851 | 60.9238 | 63.1531 | 63.0615 | 0.061035 | -0.081177 | 0.079041 | 0.28625 | -0.16129 | -0.15167 | 0.16937 | 0.25177 | -63.3316 | 60.8871 | 60.8643 | 62.9608 | 63.1668 | 124.4247 | 63.0936 | 61.0611
1451.8125 | 0.045776 | 0.43472 | -0.79147 | -0.21042 | 0.17303 | -0.25421 | -0.17624 | 61.1755 | -63.0569 | 0.041199 | -63.2217 | 61.0199 | 63.1531 | 63.0981 | 0.045776 | -0.058746 | 0.088654 | 0.28732 | -0.14847 | -0.15915 | 0.059509 | 0.091553 | -63.4369 | 60.9695 | 60.9375 | 62.97 | 63.176 | 124.4659 | 63.0936 | 61.0428
1453.4844 | 0.030518 | 0.4657 | -0.79681 | -0.20615 | 0.17517 | -0.29266 | -0.1709 | 61.1618 | -63.0066 | 0.036621 | -63.2172 | 60.9329 | 63.1668 | 63.0707 | 0.045776 | -0.081177 | 0.072632 | 0.28412 | -0.16663 | -0.14099 | 0.064087 | 0.10071 | -63.414 | 60.8643 | 60.8963 | 62.9837 | 63.1989 | 124.3515 | 63.1393 | 61.0657
1455.2031 | 0.061035 | 0.42831 | -0.79575 | -0.22751 | 0.17303 | -0.27771 | -0.16663 | 61.2488 | -62.9059 | 0.16479 | -63.1851 | 60.9375 | 63.1348 | 63.0524 | 0.045776 | -0.087585 | 0.084381 | 0.28732 | -0.16342 | -0.14313 | 0.18768 | 0.27008 | -63.2858 | 60.8871 | 60.8734 | 62.9471 | 63.1897 | 124.4339 | 63.0844 | 61.0153
1456.875 | 0.045776 | 0.43793 | -0.79788 | -0.21896 | 0.17517 | -0.24994 | -0.1709 | 61.1618 | -63.0386 | 0.054932 | -63.2263 | 60.997 | 63.1439 | 63.1165 | 0.045776 | -0.055542 | 0.063019 | 0.28946 | -0.15381 | -0.15274 | 0.041199 | 0.073242 | -63.446 | 60.965 | 60.9512 | 62.9745 | 63.1851 | 124.4476 | 63.0798 | 61.0611
1458.5469 | 0.061035 | 0.46356 | -0.78827 | -0.19119 | 0.17303 | -0.25528 | -0.16129 | 61.1755 | -63.0569 | -0.041199 | -63.2446 | 61.0153 | 63.1668 | 63.0753 | 0.061035 | -0.064087 | 0.068359 | 0.28839 | -0.14847 | -0.14313 | -0.032043 | -0.050354 | -63.4323 | 60.9283 | 60.9055 | 62.9745 | 63.1668 | 124.3469 | 63.1531 | 61.0153
1460.2188 | 0.061035 | 0.45395 | -0.79681 | -0.21896 | 0.16342 | -0.29694 | -0.18158 | 61.2122 | -62.9379 | 0.12817 | -63.1714 | 60.9604 | 63.1119 | 63.0524 | 0.045776 | -0.074768 | 0.076904 | 0.27985 | -0.16876 | -0.14633 | 0.17395 | 0.23346 | -63.3133 | 60.8826 | 60.878 | 62.9608 | 63.1577 | 124.4385 | 63.0707 | 61.0245
1461.9062 | 0.076294 | 0.46036 | -0.80002 | -0.21042 | 0.16342 | -0.27344 | -0.18692 | 61.1801 | -62.9883 | 0.045776 | -63.2034 | 60.9192 | 63.1165 | 63.0569 | 0.061035 | -0.079041 | 0.059814 | 0.27771 | -0.16342 | -0.14206 | 0.059509 | 0.091553 | -63.3728 | 60.878 | 60.8917 | 62.97 | 63.1805 | 124.3149 | 63.1531 | 61.0474
1463.6406 | 0.045776 | 0.43793 | -0.80002 | -0.21255 | 0.17731 | -0.27451 | -0.16769 | 61.2488 | -62.9288 | 0.17853 | -63.1668 | 60.9283 | 63.1302 | 63.0569 | 0.030518 | -0.085449 | 0.071564 | 0.28519 | -0.16556 | -0.15595 | 0.16479 | 0.24719 | -63.327 | 60.878 | 60.8597 | 62.97 | 63.176 | 124.3927 | 63.0707 | 61.0474
1465.3125 | 0.045776 | 0.43366 | -0.79254 | -0.22537 | 0.15701 | -0.26062 | -0.18265 | 61.1572 | -63.0341 | 0.059509 | -63.2126 | 60.9833 | 63.1393 | 63.0798 | 0.061035 | -0.052338 | 0.086517 | 0.29053 | -0.16449 | -0.15381 | 0.059509 | 0.09613 | -63.4369 | 60.9467 | 60.9421 | 62.97 | 63.1805 | 124.3927 | 63.0569 | 61.0382
1466.9844 | 0.045776 | 0.4454 | -0.79681 | -0.23285 | 0.18051 | -0.27878 | -0.16983 | 61.2259 | -62.915 | 0.16479 | -63.1577 | 60.9283 | 63.1119 | 63.0753 | 0.045776 | -0.064087 | 0.077972 | 0.29266 | -0.16342 | -0.14526 | 0.15564 | 0.21515 | -63.3545 | 60.9009 | 60.9055 | 62.9471 | 63.1714 | 124.3881 | 63.0936 | 61.0382
1468.6719 | 0.030518 | 0.43579 | -0.78613 | -0.20508 | 0.1741 | -0.23926 | -0.16449 | 61.1252 | -63.0615 | -0.009155 | -63.2263 | 60.9879 | 63.1302 | 63.0615 | 0.045776 | -0.05661 | 0.077972 | 0.2948 | -0.14954 | -0.14206 | -0.059509 | -0.068665 | -63.4827 | 60.9467 | 60.9238 | 62.9837 | 63.208 | 124.2828 | 63.1622 | 61.0748
1470.3281 | 0.091553 | 0.42191 | -0.79147 | -0.2211 | 0.15488 | -0.2478 | -0.16556 | 61.1435 | -63.0249 | -0.004578 | -63.2172 | 60.9833 | 63.1622 | 63.0798 | 0.076294 | -0.059814 | 0.079041 | 0.28946 | -0.1442 | -0.14633 | -0.050354 | -0.045776 | -63.4598 | 60.9238 | 60.9146 | 62.9837 | 63.1805 | 124.2874 | 63.1302 | 61.0474
1471.9844 | 0.045776 | 0.44327 | -0.80109 | -0.21149 | 0.16556 | -0.25742 | -0.15381 | 61.116 | -63.0524 | -0.064087 | -63.2401 | 60.9833 | 63.1577 | 63.0936 | 0.076294 | -0.059814 | 0.070496 | 0.28839 | -0.15701 | -0.14633 | -0.054932 | -0.086975 | -63.4506 | 60.9329 | 60.9192 | 62.9745 | 63.1989 | 124.324 | 63.1393 | 61.0611
1473.6406 | 0.061035 | 0.44754 | -0.79254 | -0.19546 | 0.16342 | -0.25635 | -0.16769 | 61.1252 | -63.0478 | -0.054932 | -63.2217 | 60.9695 | 63.1531 | 63.0798 | 0.045776 | -0.063019 | 0.072632 | 0.28946 | -0.14633 | -0.14313 | -0.064087 | -0.068665 | -63.4415 | 60.9329 | 60.9329 | 62.9745 | 63.1989 | 124.3286 | 63.1531 | 61.0474
1475.3125 | 0.061035 | 0.45075 | -0.79468 | -0.21469 | 0.18265 | -0.28198 | -0.16663 | 61.1984 | -62.9379 | 0.073242 | -63.176 | 60.9055 | 63.1073 | 63.0203 | 0.030518 | -0.080109 | 0.069427 | 0.28625 | -0.16556 | -0.13672 | 0.050354 | 0.07782 | -63.3408 | 60.8231 | 60.8734 | 62.9837 | 63.176 | 124.2645 | 63.1485 | 61.0428
1476.9688 | 0.045776 | 0.46356 | -0.80002 | -0.19974 | 0.1474 | -0.28625 | -0.17624 | 61.1755 | -62.9883 | 0.041199 | -63.1943 | 60.9009 | 63.1119 | 63.0524 | 0.015259 | -0.075836 | 0.0737 | 0.27771 | -0.15701 | -0.14526 | 0.050354 | 0.073242 | -63.3591 | 60.8734 | 60.878 | 62.9242 | 63.1393 | 124.2599 | 63.1393 | 61.0611
1478.625 | 0.045776 | 0.45181 | -0.8107 | -0.22644 | 0.1709 | -0.28305 | -0.1741 | 61.2213 | -62.9105 | 0.12817 | -63.1531 | 60.9238 | 63.1165 | 63.0295 | 0.061035 | -0.071564 | 0.071564 | 0.27344 | -0.1709 | -0.14633 | 0.1831 | 0.23804 | -63.2904 | 60.8459 | 60.8688 | 62.9379 | 63.1485 | 124.4064 | 63.0981 | 61.0291
1480.2812 | 0.030518 | 0.4454 | -0.80109 | -0.22217 | 0.16983 | -0.27023 | -0.18051 | 61.235 | -62.9105 | 0.17853 | -63.1439 | 60.9283 | 63.1027 | 63.0249 | 0.061035 | -0.0737 | 0.0737 | 0.28198 | -0.16449 | -0.15381 | 0.17853 | 0.25635 | -63.3133 | 60.8963 | 60.8871 | 62.9333 | 63.1256 | 124.3698 | 63.0798 | 61.0245
1481.9531 | 0.045776 | 0.45715 | -0.79254 | -0.2243 | 0.17624 | -0.2713 | -0.18372 | 61.1755 | -62.9791 | 0.07782 | -63.1805 | 60.9375 | 63.1073 | 63.0478 | 0.061035 | -0.075836 | 0.072632 | 0.28625 | -0.16235 | -0.15381 | 0.1236 | 0.17853 | -63.3179 | 60.8551 | 60.8871 | 62.9288 | 63.1577 | 124.3881 | 63.089 | 61.0382
1483.6094 | 0.061035 | 0.45395 | -0.80429 | -0.20187 | 0.16663 | -0.27557 | -0.17624 | 61.1526 | -62.9837 | 0.068665 | -63.1851 | 60.9329 | 63.1165 | 63.0524 | 0.045776 | -0.072632 | 0.074768 | 0.28625 | -0.15381 | -0.15167 | 0.09613 | 0.13275 | -63.3499 | 60.8551 | 60.8826 | 62.9791 | 63.1485 | 124.3561 | 63.0981 | 61.0245
1485.2656 | 0.045776 | 0.4689 | -0.79681 | -0.20294 | 0.17944 | -0.26382 | -0.17197 | 61.1801 | -62.9974 | 0.073242 | -63.176 | 60.9283 | 63.1348 | 63.0569 | 0.045776 | -0.069427 | 0.070496 | 0.28732 | -0.15488 | -0.15167 | 0.11902 | 0.14191 | -63.3453 | 60.8963 | 60.878 | 62.97 | 63.1668 | 124.379 | 63.0753 | 61.0474
1486.9219 | 0.061035 | 0.46249 | -0.79788 | -0.22003 | 0.16983 | -0.26596 | -0.16769 | 61.1572 | -63.002 | 0.050354 | -63.1897 | 60.91 | 63.1439 | 63.0478 | 0.030518 | -0.076904 | 0.0737 | 0.27878 | -0.16663 | -0.15381 | 0.082397 | 0.10986 | -63.3591 | 60.8826 | 60.8826 | 62.9745 | 63.176 | 124.3332 | 63.0981 | 61.0428
1488.6094 | 0.045776 | 0.43472 | -0.80002 | -0.2179 | 0.16449 | -0.26169 | -0.16876 | 61.1984 | -62.9562 | 0.1236 | -63.1714 | 60.9421 | 63.1256 | 63.0249 | 0.045776 | -0.060883 | 0.079041 | 0.28946 | -0.16022 | -0.15915 | 0.10071 | 0.13275 | -63.3957 | 60.9375 | 60.9238 | 62.9837 | 63.1485 | 124.3378 | 63.0707 | 61.0519
1490.2656 | 0.061035 | 0.42191 | -0.78827 | -0.21683 | 0.16983 | -0.23712 | -0.16556 | 61.2122 | -62.9837 | 0.045776 | -63.1622 | 60.965 | 63.1073 | 63.0249 | 0.030518 | -0.058746 | 0.082245 | 0.28625 | -0.13565 | -0.15595 | 0.018311 | 0.004578 | -63.3957 | 60.9238 | 60.8963 | 62.9517 | 63.1851 | 124.2874 | 63.1073 | 61.0611
1491.9219 | 0.045776 | 0.44968 | -0.77866 | -0.19546 | 0.16983 | -0.23712 | -0.16129 | 61.1847 | -62.9654 | 0.059509 | -63.1851 | 60.9329 | 63.1119 | 63.0432 | 0.061035 | -0.05661 | 0.075836 | 0.28625 | -0.13992 | -0.15274 | 0.041199 | 0.018311 | -63.4094 | 60.9146 | 60.8734 | 62.9608 | 63.1577 | 124.2783 | 63.089 | 61.0428
1493.625 | 0.045776 | 0.45502 | -0.80109 | -0.21469 | 0.17944 | -0.28305 | -0.17624 | 61.1481 | -62.9562 | 0.045776 | -63.1989 | 60.8871 | 63.1027 | 63.0478 | 0.030518 | -0.075836 | 0.070496 | 0.28412 | -0.16235 | -0.13565 | 0.059509 | 0.086975 | -63.3636 | 60.8734 | 60.8551 | 62.9562 | 63.176 | 124.2599 | 63.1165 | 61.0474
1495.3125 | 0.061035 | 0.46249 | -0.80856 | -0.20721 | 0.17197 | -0.26916 | -0.16983 | 61.1664 | -62.9105 | 0.10071 | -63.1622 | 60.9146 | 63.0981 | 63.0569 | 0.045776 | -0.085449 | 0.060883 | 0.28305 | -0.15274 | -0.13138 | 0.15564 | 0.21515 | -63.2858 | 60.8688 | 60.8459 | 62.9608 | 63.1531 | 124.3927 | 63.0707 | 61.0062
1496.9688 | 0.045776 | 0.45609 | -0.79895 | -0.20828 | 0.18372 | -0.27451 | -0.17197 | 61.1664 | -62.9608 | 0.050354 | -63.1805 | 60.8917 | 63.1165 | 63.0157 | 0.045776 | -0.085449 | 0.080109 | 0.27771 | -0.16129 | -0.1474 | 0.068665 | 0.073242 | -63.3499 | 60.8597 | 60.8505 | 62.9654 | 63.1577 | 124.2462 | 63.1165 | 61.0245
1498.6562 | 0.045776 | 0.4454 | -0.78934 | -0.23178 | 0.16449 | -0.24994 | -0.16342 | 61.1481 | -62.9883 | 0.059509 | -63.176 | 60.9787 | 63.0981 | 63.0478 | 0.061035 | -0.050201 | 0.085449 | 0.29159 | -0.15167 | -0.15274 | 0.054932 | 0.082397 | -63.3636 | 60.9375 | 60.8963 | 62.9791 | 63.1577 | 124.3927 | 63.0798 | 61.0336
1500.3594 | 0.045776 | 0.46463 | -0.7872 | -0.21576 | 0.17197 | -0.28305 | -0.17197 | 61.171 | -62.9105 | 0.068665 | -63.1668 | 60.8871 | 63.1073 | 63.0295 | 0.045776 | -0.083313 | 0.068359 | 0.28412 | -0.15808 | -0.14206 | 0.068665 | 0.082397 | -63.3362 | 60.8231 | 60.8047 | 62.9562 | 63.1577 | 124.2233 | 63.1027 | 61.0199
1502.0156 | 0.030518 | 0.45075 | -0.79147 | -0.21362 | 0.16983 | -0.25848 | -0.16342 | 61.1893 | -62.9242 | 0.064087 | -63.1393 | 60.878 | 63.1027 | 63.0478 | 0.030518 | -0.0737 | 0.066223 | 0.28625 | -0.1506 | -0.1506 | 0.054932 | 0.068665 | -63.3133 | 60.8231 | 60.8231 | 62.9608 | 63.1485 | 124.2554 | 63.1256 | 60.997
1503.6719 | 0.061035 | 0.46036 | -0.80536 | -0.20401 | 0.16129 | -0.27451 | -0.17197 | 61.1572 | -62.9425 | 0.050354 | -63.1714 | 60.8688 | 63.1027 | 63.0249 | 0.030518 | -0.069427 | 0.066223 | 0.28412 | -0.1506 | -0.14633 | 0.068665 | 0.091553 | -63.3362 | 60.8322 | 60.8551 | 62.9333 | 63.1531 | 124.2325 | 63.1119 | 61.0153
1505.3281 | 0.076294 | 0.4689 | -0.79681 | -0.20508 | 0.16876 | -0.27557 | -0.17731 | 61.1389 | -62.9745 | 0.059509 | -63.1851 | 60.8871 | 63.1027 | 63.0295 | 0.045776 | -0.080109 | 0.067291 | 0.29159 | -0.16663 | -0.13672 | 0.091553 | 0.13733 | -63.3224 | 60.8368 | 60.8505 | 62.9379 | 63.1439 | 124.3149 | 63.1027 | 61.0016
1506.9844 | 0.061035 | 0.42084 | -0.79147 | -0.23071 | 0.1709 | -0.26276 | -0.16876 | 61.1435 | -63.0203 | 0.059509 | -63.1805 | 60.9924 | 63.1165 | 63.0615 | 0.061035 | -0.063019 | 0.087585 | 0.28625 | -0.16449 | -0.15274 | 0.041199 | 0.082397 | -63.3865 | 60.9421 | 60.9329 | 62.9379 | 63.1348 | 124.3607 | 63.0386 | 61.0062
1508.6562 | 0.061035 | 0.44861 | -0.79361 | -0.20828 | 0.15595 | -0.24994 | -0.16235 | 61.0931 | -63.0249 | -0.059509 | -63.1989 | 60.9467 | 63.1256 | 63.0478 | 0.045776 | -0.065155 | 0.074768 | 0.29587 | -0.14954 | -0.15381 | -0.036621 | -0.091553 | -63.4048 | 60.9283 | 60.8688 | 62.97 | 63.1714 | 124.2874 | 63.121 | 61.0062
1510.3125 | 0.061035 | 0.4422 | -0.79361 | -0.20935 | 0.16449 | -0.26596 | -0.16235 | 61.116 | -62.9745 | -0.004578 | -63.1851 | 60.9055 | 63.1027 | 63.0432 | 0.045776 | -0.067291 | 0.075836 | 0.28091 | -0.14633 | -0.1442 | 0.018311 | 0.004578 | -63.3224 | 60.8414 | 60.8139 | 62.9517 | 63.1393 | 124.2828 | 63.1256 | 60.9695
1511.9688 | 0.030518 | 0.45288 | -0.78934 | -0.20081 | 0.16983 | -0.25848 | -0.16235 | 61.1069 | -63.0203 | -0.050354 | -63.1943 | 60.9329 | 63.1256 | 63.0478 | 0.061035 | -0.05661 | 0.079041 | 0.27771 | -0.13886 | -0.1442 | -0.032043 | -0.068665 | -63.3957 | 60.8871 | 60.878 | 62.9562 | 63.1485 | 124.2554 | 63.1119 | 60.997
1513.6562 | 0.061035 | 0.44647 | -0.80215 | -0.21255 | 0.16022 | -0.25635 | -0.16663 | 61.1526 | -62.9517 | 0.09613 | -63.1348 | 60.9512 | 63.1119 | 63.0386 | 0.061035 | -0.071564 | 0.092926 | 0.29373 | -0.15595 | -0.1442 | 0.045776 | 0.091553 | -63.3408 | 60.91 | 60.8871 | 62.9425 | 63.1668 | 124.3286 | 63.0478 | 61.0062
1515.3281 | 0.045776 | 0.43152 | -0.79788 | -0.21576 | 0.16876 | -0.25101 | -0.15915 | 61.1343 | -62.9471 | 0.054932 | -63.1577 | 60.9375 | 63.0936 | 63.0157 | 0.076294 | -0.05661 | 0.082245 | 0.28946 | -0.14633 | -0.14526 | 0.004578 | 0.009155 | -63.3774 | 60.8871 | 60.8871 | 62.9242 | 63.1439 | 124.2188 | 63.1073 | 61.0153
1517 | 0.061035 | 0.44861 | -0.79361 | -0.21042 | 0.17944 | -0.27771 | -0.16769 | 61.1481 | -62.9059 | 0.068665 | -63.1393 | 60.8734 | 63.1027 | 62.9974 | 0.061035 | -0.084381 | 0.067291 | 0.28305 | -0.15915 | -0.15167 | 0.054932 | 0.09613 | -63.295 | 60.8231 | 60.8551 | 62.9379 | 63.1256 | 124.2096 | 63.1073 | 61.0199
1518.6719 | 0.045776 | 0.44327 | -0.80856 | -0.22537 | 0.15167 | -0.29373 | -0.18051 | 61.1252 | -62.9333 | 0.086975 | -63.1393 | 60.8963 | 63.0798 | 63.0112 | 0.061035 | -0.077972 | 0.074768 | 0.28091 | -0.17944 | -0.14099 | 0.11902 | 0.18768 | -63.2858 | 60.8643 | 60.8322 | 62.915 | 63.1119 | 124.3149 | 63.0569 | 60.9695
1520.375 | 0.061035 | 0.44327 | -0.78293 | -0.20401 | 0.16129 | -0.24887 | -0.16342 | 61.116 | -63.0478 | -0.004578 | -63.1851 | 60.9375 | 63.0844 | 63.0203 | 0.061035 | -0.068359 | 0.076904 | 0.28839 | -0.15274 | -0.16022 | -0.068665 | -0.073242 | -63.414 | 60.91 | 60.91 | 62.9333 | 63.1439 | 124.205 | 63.0798 | 61.0382
1522.0312 | 0.061035 | 0.43472 | -0.78613 | -0.2211 | 0.15915 | -0.24994 | -0.16663 | 61.1526 | -62.9517 | 0.050354 | -63.1439 | 60.9238 | 63.0798 | 63.0203 | 0.061035 | -0.061951 | 0.085449 | 0.29053 | -0.14633 | -0.14633 | 0.009155 | 0.018311 | -63.3591 | 60.8826 | 60.878 | 62.9471 | 63.1485 | 124.2279 | 63.0753 | 61.0062
1523.6875 | 0.061035 | 0.45181 | -0.79895 | -0.21149 | 0.17838 | -0.26596 | -0.16235 | 61.1023 | -62.9608 | 0.004578 | -63.1851 | 60.9055 | 63.0844 | 63.0524 | 0.061035 | -0.075836 | 0.071564 | 0.29159 | -0.14526 | -0.14313 | 0.009155 | 0.018311 | -63.3041 | 60.8322 | 60.8231 | 62.9379 | 63.1439 | 124.2645 | 63.0936 | 60.9787
1525.3438 | 0.061035 | 0.44968 | -0.79361 | -0.20828 | 0.16449 | -0.26596 | -0.16769 | 61.1206 | -62.9562 | 0.027466 | -63.1393 | 60.878 | 63.089 | 63.0203 | 0.061035 | -0.081177 | 0.077972 | 0.28198 | -0.16022 | -0.14954 | 0.027466 | 0.022888 | -63.3041 | 60.8276 | 60.8322 | 62.9425 | 63.121 | 124.2554 | 63.0844 | 60.9924
1527.0156 | 0.045776 | 0.4422 | -0.79895 | -0.23285 | 0.17624 | -0.28732 | -0.18692 | 61.0977 | -62.9837 | 0.045776 | -63.1439 | 60.878 | 63.0798 | 63.0203 | 0.061035 | -0.082245 | 0.0737 | 0.28519 | -0.1709 | -0.14526 | 0.068665 | 0.11902 | -63.3133 | 60.8322 | 60.8551 | 62.915 | 63.1256 | 124.2645 | 63.0524 | 61.0062
1528.7031 | 0.076294 | 0.43793 | -0.78934 | -0.21469 | 0.17944 | -0.23605 | -0.18158 | 61.116 | -62.9974 | 0.018311 | -63.1714 | 60.9192 | 63.0707 | 63.0203 | 0.076294 | -0.053406 | 0.09079 | 0.29266 | -0.14313 | -0.1506 | -0.045776 | -0.045776 | -63.4048 | 60.8917 | 60.8826 | 62.9425 | 63.1668 | 124.1867 | 63.0798 | 61.0153
1530.3594 | 0.061035 | 0.42831 | -0.79147 | -0.21149 | 0.15595 | -0.2478 | -0.17303 | 61.1298 | -62.9242 | 0.068665 | -63.1439 | 60.9146 | 63.0844 | 62.9929 | 0.045776 | -0.070496 | 0.076904 | 0.28839 | -0.14847 | -0.14954 | 0.027466 | 0.022888 | -63.3408 | 60.878 | 60.8597 | 62.9196 | 63.1531 | 124.2416 | 63.0524 | 61.0062
1532.0156 | 0.045776 | 0.45288 | -0.80536 | -0.21255 | 0.16556 | -0.25848 | -0.16983 | 61.0611 | -63.0157 | -0.045776 | -63.1943 | 60.9421 | 63.121 | 63.002 | 0.045776 | -0.071564 | 0.076904 | 0.28519 | -0.14633 | -0.13565 | -0.050354 | -0.09613 | -63.3911 | 60.8826 | 60.8551 | 62.9288 | 63.176 | 124.2279 | 63.0615 | 60.9787
1533.6719 | 0.030518 | 0.44861 | -0.79895 | -0.20721 | 0.16342 | -0.26169 | -0.16876 | 61.084 | -62.9837 | -0.036621 | -63.1805 | 60.9009 | 63.0981 | 63.0203 | 0.061035 | -0.067291 | 0.061951 | 0.27451 | -0.15595 | -0.14526 | -0.027466 | -0.032043 | -63.3453 | 60.8322 | 60.8368 | 62.915 | 63.1348 | 124.2508 | 63.0753 | 60.9833
1535.3281 | 0.030518 | 0.44327 | -0.79361 | -0.21683 | 0.17197 | -0.26382 | -0.16663 | 61.0703 | -63.0432 | -0.059509 | -63.1851 | 60.9192 | 63.0753 | 62.9929 | 0.061035 | -0.053406 | 0.058746 | 0.28946 | -0.15701 | -0.12924 | -0.068665 | -0.09613 | -63.382 | 60.878 | 60.91 | 62.9013 | 63.121 | 124.2279 | 63.0569 | 60.9833
1537 | 0.045776 | 0.44647 | -0.8107 | -0.23071 | 0.17303 | -0.298 | -0.1709 | 61.0794 | -62.9745 | 0.036621 | -63.1622 | 60.8551 | 63.0524 | 63.002 | 0.045776 | -0.09079 | 0.075836 | 0.27023 | -0.1741 | -0.13779 | 0.050354 | 0.10986 | -63.327 | 60.8231 | 60.8505 | 62.9105 | 63.1302 | 124.2096 | 63.0661 | 60.9787
1538.6875 | 0.076294 | 0.44647 | -0.78934 | -0.21149 | 0.17838 | -0.26276 | -0.17944 | 61.1481 | -62.915 | 0.036621 | -63.1256 | 60.8688 | 63.0707 | 62.97 | 0.045776 | -0.068359 | 0.082245 | 0.29159 | -0.15701 | -0.14526 | 0.032043 | 0.041199 | -63.2858 | 60.8047 | 60.7864 | 62.8967 | 63.1165 | 124.2325 | 63.0707 | 60.9741
1540.3438 | 0.045776 | 0.44968 | -0.79575 | -0.20081 | 0.1709 | -0.25742 | -0.16663 | 61.0977 | -62.9883 | -0.032043 | -63.176 | 60.8826 | 63.089 | 63.0066 | 0.061035 | -0.063019 | 0.076904 | 0.28946 | -0.15808 | -0.13672 | -0.018311 | -0.050354 | -63.3316 | 60.8597 | 60.8414 | 62.9288 | 63.1393 | 124.2233 | 63.0615 | 60.9695
1542 | 0.045776 | 0.44861 | -0.78507 | -0.21362 | 0.16769 | -0.27771 | -0.1741 | 61.1252 | -62.8922 | 0.073242 | -63.1027 | 60.8414 | 63.0844 | 63.0066 | 0.045776 | -0.080109 | 0.063019 | 0.27771 | -0.16022 | -0.1474 | 0.068665 | 0.064087 | -63.2858 | 60.8276 | 60.8185 | 62.9105 | 63.121 | 124.1638 | 63.0981 | 60.9879
1543.6562 | 0.061035 | 0.44006 | -0.79041 | -0.22324 | 0.16342 | -0.28625 | -0.17624 | 61.1526 | -62.8464 | 0.16937 | -63.0981 | 60.8734 | 63.0661 | 62.9791 | 0.061035 | -0.079041 | 0.077972 | 0.28091 | -0.16769 | -0.1474 | 0.15106 | 0.21515 | -63.2767 | 60.8368 | 60.8459 | 62.9105 | 63.1073 | 124.2462 | 63.0524 | 60.9924
1545.3125 | 0.061035 | 0.43686 | -0.79468 | -0.2243 | 0.17303 | -0.27344 | -0.17624 | 61.0886 | -62.9745 | 0.086975 | -63.1622 | 60.9283 | 63.0798 | 63.0066 | 0.045776 | -0.067291 | 0.085449 | 0.28625 | -0.16449 | -0.15595 | 0.07782 | 0.11444 | -63.3499 | 60.878 | 60.8688 | 62.9379 | 63.121 | 124.2599 | 63.0112 | 60.997
1546.9688 | 0.061035 | 0.45929 | -0.79147 | -0.19012 | 0.16769 | -0.26703 | -0.16769 | 61.1389 | -62.8738 | 0.054932 | -63.1119 | 60.8688 | 63.0478 | 62.9745 | 0.045776 | -0.083313 | 0.067291 | 0.28091 | -0.16235 | -0.15808 | 0.07782 | 0.073242 | -63.2767 | 60.8002 | 60.7864 | 62.9105 | 63.1073 | 124.1638 | 63.0844 | 60.9512
1548.6406 | 0.045776 | 0.44647 | -0.80215 | -0.2211 | 0.16129 | -0.27878 | -0.17731 | 61.1664 | -62.8326 | 0.15106 | -63.1119 | 60.8643 | 63.0753 | 62.9562 | 0.045776 | -0.087585 | 0.065155 | 0.27878 | -0.16129 | -0.14526 | 0.21057 | 0.24261 | -63.2217 | 60.8185 | 60.8093 | 62.883 | 63.1027 | 124.2828 | 63.0112 | 60.9604
1550.3125 | 0.061035 | 0.43793 | -0.80322 | -0.2179 | 0.16663 | -0.26382 | -0.17303 | 61.084 | -62.9745 | 0.054932 | -63.1439 | 60.9283 | 63.0936 | 63.0066 | 0.045776 | -0.063019 | 0.074768 | 0.28305 | -0.16235 | -0.14633 | 0.054932 | 0.082397 | -63.3545 | 60.8963 | 60.91 | 62.9059 | 63.1165 | 124.2783 | 63.002 | 61.0016
1551.9688 | 0.030518 | 0.45181 | -0.80109 | -0.22324 | 0.18158 | -0.27664 | -0.17624 | 61.1618 | -62.8372 | 0.17853 | -63.1073 | 60.8643 | 63.0478 | 62.9837 | 0.076294 | -0.060883 | 0.069427 | 0.27451 | -0.16876 | -0.14526 | 0.16937 | 0.24719 | -63.2446 | 60.8322 | 60.8139 | 62.8738 | 63.0936 | 124.2371 | 63.0066 | 60.9695
1553.6406 | 0.061035 | 0.43472 | -0.78613 | -0.18585 | 0.16663 | -0.24994 | -0.1709 | 61.0565 | -63.0203 | -0.059509 | -63.1531 | 60.9329 | 63.0798 | 63.0157 | 0.045776 | -0.060883 | 0.075836 | 0.28946 | -0.13886 | -0.1442 | -0.045776 | -0.091553 | -63.4232 | 60.8643 | 60.8551 | 62.9288 | 63.1577 | 124.1684 | 63.0753 | 61.0062
1555.3438 | 0.045776 | 0.43366 | -0.79361 | -0.20828 | 0.15274 | -0.25101 | -0.15167 | 61.0565 | -62.9929 | -0.054932 | -63.1531 | 60.9238 | 63.0844 | 62.9974 | 0.076294 | -0.064087 | 0.063019 | 0.28839 | -0.14313 | -0.13992 | -0.045776 | -0.091553 | -63.3774 | 60.8917 | 60.8551 | 62.8967 | 63.1393 | 124.1959 | 63.0615 | 60.9787
1557 | 0.045776 | 0.45822 | -0.78507 | -0.20935 | 0.16663 | -0.29053 | -0.16663 | 61.1069 | -62.8922 | 0.059509 | -63.1256 | 60.8414 | 63.0478 | 62.9837 | 0.045776 | -0.074768 | 0.071564 | 0.28412 | -0.15808 | -0.14526 | 0.054932 | 0.07782 | -63.2858 | 60.8185 | 60.8047 | 62.8876 | 63.1165 | 124.1501 | 63.0661 | 60.965
1558.6719 | 0.045776 | 0.43472 | -0.79254 | -0.22964 | 0.16129 | -0.27237 | -0.17624 | 61.084 | -62.9379 | 0.082397 | -63.1348 | 60.9238 | 63.0753 | 63.002 | 0.045776 | -0.05661 | 0.085449 | 0.28946 | -0.17197 | -0.15488 | 0.073242 | 0.11444 | -63.3408 | 60.878 | 60.8963 | 62.9059 | 63.0981 | 124.2325 | 63.0203 | 60.9695
1560.3281 | 0.030518 | 0.44113 | -0.79788 | -0.23071 | 0.15915 | -0.2681 | -0.1741 | 61.0657 | -62.9562 | 0.07782 | -63.1393 | 60.9283 | 63.0615 | 62.9837 | 0.061035 | -0.063019 | 0.088654 | 0.28198 | -0.17624 | -0.15167 | 0.054932 | 0.082397 | -63.3499 | 60.91 | 60.8871 | 62.9013 | 63.1302 | 124.2416 | 63.0157 | 60.9741
1561.9688 | 0.030518 | 0.4454 | -0.80002 | -0.23392 | 0.16556 | -0.28091 | -0.17731 | 61.1435 | -62.8235 | 0.16479 | -63.0707 | 60.878 | 63.0386 | 62.9791 | 0.061035 | -0.082245 | 0.081177 | 0.28198 | -0.16663 | -0.13779 | 0.17853 | 0.25635 | -63.2126 | 60.791 | 60.8139 | 62.8738 | 63.0844 | 124.2783 | 63.0203 | 60.9467
1563.6406 | 0.061035 | 0.44968 | -0.79147 | -0.19867 | 0.15808 | -0.24994 | -0.16876 | 61.0657 | -62.9974 | -0.059509 | -63.1577 | 60.9146 | 63.0661 | 62.9974 | 0.076294 | -0.058746 | 0.061951 | 0.28839 | -0.13992 | -0.14633 | -0.032043 | -0.073242 | -63.3545 | 60.8597 | 60.8368 | 62.915 | 63.1165 | 124.1867 | 63.0615 | 60.9833
1565.3125 | 0.061035 | 0.4454 | -0.79361 | -0.20828 | 0.15274 | -0.27664 | -0.15595 | 61.1298 | -62.883 | 0.050354 | -63.0798 | 60.8231 | 63.0569 | 62.9608 | 0.045776 | -0.067291 | 0.070496 | 0.28305 | -0.14954 | -0.15595 | 0.054932 | 0.050354 | -63.2629 | 60.7864 | 60.8002 | 62.8693 | 63.0936 | 124.1501 | 63.0478 | 60.9558
1566.9688 | 0.045776 | 0.45288 | -0.79254 | -0.21362 | 0.17517 | -0.28412 | -0.17731 | 61.1206 | -62.8601 | 0.10986 | -63.089 | 60.8368 | 63.0707 | 62.9608 | 0.076294 | -0.086517 | 0.065155 | 0.27771 | -0.16769 | -0.14526 | 0.16479 | 0.21515 | -63.208 | 60.8185 | 60.8047 | 62.8693 | 63.1073 | 124.2508 | 63.0112 | 60.9512
1568.6406 | 0.061035 | 0.44113 | -0.77972 | -0.20615 | 0.15488 | -0.25742 | -0.15488 | 61.1114 | -62.8967 | 0.045776 | -63.1027 | 60.8734 | 63.0432 | 62.9837 | 0.061035 | -0.067291 | 0.069427 | 0.27878 | -0.1474 | -0.14633 | 0.036621 | 0.045776 | -63.2675 | 60.791 | 60.7864 | 62.8876 | 63.0981 | 124.1776 | 63.0386 | 60.9329
1570.3281 | 0.015259 | 0.44754 | -0.80963 | -0.22537 | 0.16235 | -0.27985 | -0.16983 | 61.0748 | -62.9105 | 0.022888 | -63.1393 | 60.8459 | 63.0386 | 62.9654 | 0.045776 | -0.071564 | 0.075836 | 0.27985 | -0.16342 | -0.1442 | 0.068665 | 0.086975 | -63.2996 | 60.8231 | 60.8093 | 62.9059 | 63.1027 | 124.1364 | 63.0798 | 60.9558
1571.9844 | 0.045776 | 0.45075 | -0.80536 | -0.20294 | 0.16876 | -0.26489 | -0.18372 | 61.084 | -62.9105 | 0.032043 | -63.1256 | 60.8459 | 63.0341 | 62.9425 | 0.030518 | -0.069427 | 0.059814 | 0.27451 | -0.16129 | -0.14206 | 0.064087 | 0.10071 | -63.3087 | 60.8002 | 60.8002 | 62.8876 | 63.1027 | 124.1501 | 63.0707 | 60.9421
1573.6406 | 0.030518 | 0.46036 | -0.79361 | -0.20721 | 0.16342 | -0.27557 | -0.17731 | 61.0657 | -62.9242 | 0.045776 | -63.1073 | 60.8322 | 63.0432 | 62.9883 | 0.030518 | -0.077972 | 0.065155 | 0.28091 | -0.15167 | -0.14633 | 0.073242 | 0.1236 | -63.2812 | 60.8047 | 60.8093 | 62.883 | 63.0936 | 124.1867 | 63.0341 | 60.9375
1575.3281 | 0.045776 | 0.43366 | -0.80536 | -0.21683 | 0.16449 | -0.24567 | -0.16449 | 61.084 | -62.9654 | 0.059509 | -63.1302 | 60.9055 | 63.0524 | 62.9654 | 0.076294 | -0.058746 | 0.081177 | 0.2948 | -0.14954 | -0.15381 | 0.045776 | 0.091553 | -63.3453 | 60.878 | 60.8643 | 62.8784 | 63.089 | 124.2645 | 62.9929 | 60.9558
1576.9844 | 0.061035 | 0.44968 | -0.80215 | -0.21576 | 0.17731 | -0.25742 | -0.17731 | 61.116 | -62.8647 | 0.059509 | -63.089 | 60.8093 | 63.0432 | 62.9471 | 0.061035 | -0.0737 | 0.082245 | 0.28519 | -0.15701 | -0.14954 | 0.050354 | 0.07782 | -63.2446 | 60.7727 | 60.7636 | 62.8967 | 63.0936 | 124.1226 | 63.0661 | 60.9467
1578.6406 | 0.030518 | 0.46677 | -0.80429 | -0.20081 | 0.16449 | -0.27664 | -0.16876 | 61.1114 | -62.8464 | 0.045776 | -63.1073 | 60.8368 | 63.0432 | 62.9837 | 0.061035 | -0.077972 | 0.064087 | 0.27771 | -0.14633 | -0.14313 | 0.064087 | 0.073242 | -63.2767 | 60.7727 | 60.7864 | 62.8967 | 63.089 | 124.0906 | 63.0524 | 60.9467
1580.2969 | 0.045776 | 0.44861 | -0.784 | -0.20187 | 0.16876 | -0.25314 | -0.16769 | 61.1114 | -62.8738 | 0.041199 | -63.0753 | 60.8002 | 63.0524 | 62.9791 | 0.061035 | -0.0737 | 0.060883 | 0.28946 | -0.1506 | -0.1442 | 0.064087 | 0.041199 | -63.2538 | 60.759 | 60.7681 | 62.8784 | 63.0844 | 124.1318 | 63.0661 | 60.9375
1581.9531 | 0.061035 | 0.45609 | -0.80215 | -0.20187 | 0.16449 | -0.26169 | -0.16769 | 61.116 | -62.8601 | 0.054932 | -63.0844 | 60.8139 | 63.0569 | 62.9608 | 0.045776 | -0.063019 | 0.055542 | 0.28732 | -0.14847 | -0.14633 | 0.059509 | 0.086975 | -63.2446 | 60.791 | 60.759 | 62.8876 | 63.0798 | 124.118 | 63.0661 | 60.9421
1583.625 | 0.045776 | 0.44113 | -0.80002 | -0.21362 | 0.16449 | -0.24674 | -0.15915 | 61.116 | -62.9059 | 0.07782 | -63.0753 | 60.91 | 63.0386 | 62.9837 | 0.061035 | -0.049133 | 0.075836 | 0.28091 | -0.14526 | -0.15167 | 0.064087 | 0.068665 | -63.2858 | 60.8551 | 60.8459 | 62.8647 | 63.0844 | 124.2142 | 62.9837 | 60.9421
1585.2812 | 0.061035 | 0.41229 | -0.77972 | -0.22537 | 0.18585 | -0.25314 | -0.15701 | 61.0657 | -62.9105 | 0.068665 | -63.089 | 60.8963 | 63.0341 | 62.9745 | 0.045776 | -0.064087 | 0.081177 | 0.28946 | -0.16235 | -0.1442 | 0.045776 | 0.091553 | -63.3087 | 60.8505 | 60.8459 | 62.8967 | 63.0798 | 124.2279 | 62.9608 | 60.9283
1586.9375 | 0.061035 | 0.42084 | -0.79681 | -0.22324 | 0.18051 | -0.24994 | -0.16769 | 61.084 | -62.8693 | 0.082397 | -63.0798 | 60.9055 | 63.0341 | 62.9608 | 0.061035 | -0.060883 | 0.086517 | 0.29373 | -0.15167 | -0.1506 | 0.050354 | 0.054932 | -63.2904 | 60.8505 | 60.8185 | 62.8693 | 63.089 | 124.1867 | 63.0112 | 60.9604
1588.625 | 0.045776 | 0.439 | -0.79147 | -0.22537 | 0.15915 | -0.29053 | -0.1741 | 61.0886 | -62.8235 | 0.1831 | -63.0661 | 60.8322 | 63.0157 | 62.9242 | 0.045776 | -0.069427 | 0.076904 | 0.28305 | -0.1741 | -0.14313 | 0.11902 | 0.25177 | -63.2263 | 60.8047 | 60.791 | 62.8601 | 63.0798 | 124.1867 | 62.9929 | 60.9421
1590.2812 | 0.045776 | 0.43259 | -0.79041 | -0.22964 | 0.18692 | -0.27557 | -0.16876 | 61.0519 | -62.9059 | 0.091553 | -63.0981 | 60.8917 | 63.002 | 62.9608 | 0.045776 | -0.074768 | 0.077972 | 0.28519 | -0.15488 | -0.14526 | 0.073242 | 0.13275 | -63.3224 | 60.8368 | 60.8551 | 62.8693 | 63.0936 | 124.1821 | 62.9837 | 60.9375
1591.9375 | 0.061035 | 0.43152 | -0.79681 | -0.22324 | 0.16983 | -0.28732 | -0.1741 | 61.0291 | -62.9013 | 0.059509 | -63.1119 | 60.8414 | 63.0203 | 62.9837 | 0.061035 | -0.081177 | 0.072632 | 0.29053 | -0.17517 | -0.14313 | 0.082397 | 0.12817 | -63.2675 | 60.8002 | 60.7864 | 62.8601 | 63.089 | 124.1455 | 63.0112 | 60.9421
1593.625 | 0.030518 | 0.46249 | -0.79575 | -0.20294 | 0.16663 | -0.27451 | -0.18372 | 61.0611 | -62.8922 | 0.050354 | -63.1073 | 60.8414 | 63.0066 | 62.97 | 0.045776 | -0.082245 | 0.052338 | 0.29373 | -0.15381 | -0.14313 | 0.059509 | 0.082397 | -63.2629 | 60.8093 | 60.7773 | 62.8601 | 63.1027 | 124.0906 | 63.0432 | 60.965
1595.3281 | 0.061035 | 0.44327 | -0.80322 | -0.22964 | 0.16342 | -0.2478 | -0.1709 | 61.0794 | -62.8693 | 0.10071 | -63.0844 | 60.8688 | 63.0295 | 62.9471 | 0.045776 | -0.05661 | 0.066223 | 0.28839 | -0.14313 | -0.15701 | 0.082397 | 0.12817 | -63.2904 | 60.8551 | 60.8459 | 62.8876 | 63.0936 | 124.1684 | 62.9791 | 60.9741
1597.0156 | 0.045776 | 0.45288 | -0.79575 | -0.2211 | 0.16129 | -0.27878 | -0.17624 | 61.0931 | -62.8052 | 0.1236 | -63.0615 | 60.8414 | 63.0157 | 62.9288 | 0.045776 | -0.069427 | 0.074768 | 0.28732 | -0.16235 | -0.14954 | 0.17395 | 0.2243 | -63.1805 | 60.7864 | 60.7773 | 62.8647 | 63.0753 | 124.2279 | 62.9929 | 60.9055
1598.6719 | 0.030518 | 0.439 | -0.79254 | -0.21255 | 0.17838 | -0.26916 | -0.18265 | 61.0977 | -62.8418 | 0.10071 | -63.0798 | 60.8368 | 63.0249 | 62.9562 | 0.045776 | -0.080109 | 0.061951 | 0.28625 | -0.15595 | -0.1442 | 0.16022 | 0.20599 | -63.1989 | 60.7636 | 60.7681 | 62.8372 | 63.0615 | 124.2142 | 62.9929 | 60.9283
1600.3281 | 0.061035 | 0.44006 | -0.79254 | -0.22003 | 0.17517 | -0.27344 | -0.16449 | 61.1343 | -62.796 | 0.16937 | -63.0432 | 60.8276 | 63.0203 | 62.9425 | 0.061035 | -0.067291 | 0.0737 | 0.27344 | -0.15274 | -0.16129 | 0.18768 | 0.25177 | -63.1851 | 60.7864 | 60.7864 | 62.8326 | 63.0753 | 124.1913 | 62.9974 | 60.9192
1601.9844 | 0.061035 | 0.4454 | -0.78507 | -0.19119 | 0.17731 | -0.25101 | -0.16983 | 61.1389 | -62.8372 | 0.064087 | -63.0569 | 60.8093 | 63.0112 | 62.9425 | 0.045776 | -0.072632 | 0.060883 | 0.28091 | -0.14099 | -0.1474 | 0.073242 | 0.082397 | -63.2355 | 60.759 | 60.7727 | 62.8555 | 63.0661 | 124.0906 | 63.0203 | 60.9467
1603.6562 | 0.076294 | 0.43686 | -0.79788 | -0.22644 | 0.16449 | -0.26489 | -0.16556 | 61.0474 | -62.915 | 0.064087 | -63.1027 | 60.9146 | 63.0295 | 62.97 | 0.030518 | -0.065155 | 0.071564 | 0.28839 | -0.15701 | -0.15167 | 0.073242 | 0.082397 | -63.3087 | 60.878 | 60.8322 | 62.8601 | 63.0798 | 124.2004 | 62.9745 | 60.9512
1605.3125 | 0.045776 | 0.44647 | -0.78827 | -0.20615 | 0.16449 | -0.25528 | -0.18051 | 61.0336 | -62.9013 | 0.050354 | -63.1073 | 60.9009 | 63.0295 | 62.9654 | 0.045776 | -0.058746 | 0.076904 | 0.2948 | -0.15167 | -0.14954 | 0.059509 | 0.086975 | -63.3041 | 60.8551 | 60.8231 | 62.8738 | 63.1073 | 124.1959 | 62.9883 | 60.9055
1606.9688 | 0.076294 | 0.43579 | -0.78827 | -0.22537 | 0.17838 | -0.2478 | -0.16342 | 61.0245 | -62.9196 | 0.054932 | -63.089 | 60.8963 | 63.0432 | 62.9517 | 0.076294 | -0.058746 | 0.081177 | 0.28946 | -0.15167 | -0.14633 | 0.041199 | 0.09613 | -63.2996 | 60.8551 | 60.8185 | 62.8922 | 63.0707 | 124.205 | 62.9654 | 60.91
1608.6406 | 0.045776 | 0.41977 | -0.79147 | -0.22751 | 0.16876 | -0.26276 | -0.1741 | 61.0153 | -62.9196 | 0.059509 | -63.0936 | 60.8963 | 63.0203 | 62.9471 | 0.045776 | -0.061951 | 0.072632 | 0.29053 | -0.16235 | -0.13886 | 0.050354 | 0.082397 | -63.3133 | 60.8322 | 60.8322 | 62.8464 | 63.0798 | 124.205 | 62.9745 | 60.9009
1610.2969 | 0.030518 | 0.43472 | -0.79468 | -0.22858 | 0.1741 | -0.27557 | -0.16769 | 61.0657 | -62.7777 | 0.16479 | -63.0341 | 60.8276 | 62.9974 | 62.8922 | 0.045776 | -0.080109 | 0.071564 | 0.29159 | -0.15701 | -0.14206 | 0.13733 | 0.24719 | -63.1943 | 60.8047 | 60.7864 | 62.8464 | 63.0707 | 124.1501 | 62.97 | 60.9192
1611.9531 | 0.061035 | 0.45288 | -0.79895 | -0.21255 | 0.16663 | -0.29159 | -0.17838 | 61.0336 | -62.8464 | 0.082397 | -63.0615 | 60.8551 | 63.0157 | 62.9425 | 0.061035 | -0.083313 | 0.075836 | 0.29159 | -0.16556 | -0.1474 | 0.11902 | 0.19226 | -63.2034 | 60.7727 | 60.7819 | 62.8555 | 63.0753 | 124.173 | 62.9837 | 60.91
1613.6406 | 0.061035 | 0.44434 | -0.80002 | -0.19867 | 0.16876 | -0.26916 | -0.1741 | 61.0748 | -62.8189 | 0.064087 | -63.0753 | 60.8047 | 63.002 | 62.9471 | 0.061035 | -0.070496 | 0.057678 | 0.27451 | -0.15915 | -0.15167 | 0.064087 | 0.091553 | -63.2263 | 60.7452 | 60.7681 | 62.8372 | 63.0615 | 124.0402 | 63.0341 | 60.9329
1615.2969 | 0.076294 | 0.45609 | -0.80109 | -0.20615 | 0.16876 | -0.27344 | -0.17731 | 61.0336 | -62.8784 | 0.036621 | -63.0936 | 60.8322 | 63.0341 | 62.9471 | 0.045776 | -0.067291 | 0.055542 | 0.28519 | -0.15915 | -0.13886 | 0.050354 | 0.082397 | -63.2538 | 60.7819 | 60.7636 | 62.851 | 63.0798 | 124.0677 | 63.0295 | 60.9512
1616.9531 | 0.030518 | 0.46356 | -0.79254 | -0.20828 | 0.1506 | -0.27985 | -0.17944 | 61.0428 | -62.8555 | 0.091553 | -63.0753 | 60.8368 | 63.002 | 62.9379 | 0.061035 | -0.086517 | 0.066223 | 0.27237 | -0.16342 | -0.14633 | 0.10986 | 0.15564 | -63.2172 | 60.7819 | 60.7773 | 62.8418 | 63.0569 | 124.1592 | 62.97 | 60.8871
1618.6094 | 0.045776 | 0.45502 | -0.80963 | -0.2179 | 0.16769 | -0.26596 | -0.18051 | 61.0291 | -62.8647 | 0.045776 | -63.0936 | 60.8322 | 62.9929 | 62.9471 | 0.061035 | -0.081177 | 0.074768 | 0.28198 | -0.15488 | -0.15381 | 0.082397 | 0.11902 | -63.2446 | 60.7773 | 60.7773 | 62.8555 | 63.0707 | 124.1318 | 62.9608 | 60.9146
1620.2812 | 0.045776 | 0.4454 | -0.79895 | -0.20294 | 0.16769 | -0.27344 | -0.17944 | 61.0748 | -62.8601 | 0.059509 | -63.089 | 60.8139 | 63.0112 | 62.9517 | 0.061035 | -0.076904 | 0.067291 | 0.28091 | -0.1474 | -0.13245 | 0.050354 | 0.064087 | -63.2446 | 60.7498 | 60.759 | 62.8372 | 63.0753 | 124.0448 | 63.0341 | 60.9238
1621.9375 | 0.061035 | 0.439 | -0.7872 | -0.19546 | 0.16449 | -0.23285 | -0.16983 | 61.0336 | -62.9425 | -0.059509 | -63.1073 | 60.8826 | 63.0524 | 62.9517 | 0.061035 | -0.054474 | 0.067291 | 0.29053 | -0.14099 | -0.15595 | -0.050354 | -0.10529 | -63.327 | 60.8414 | 60.8185 | 62.851 | 63.0798 | 124.086 | 63.0249 | 60.9421
1623.6406 | 0.061035 | 0.45288 | -0.79468 | -0.20294 | 0.1709 | -0.27344 | -0.15595 | 61.0977 | -62.8281 | 0.07782 | -63.0386 | 60.7864 | 62.9929 | 62.9288 | 0.045776 | -0.076904 | 0.072632 | 0.28839 | -0.15701 | -0.13779 | 0.068665 | 0.07782 | -63.2172 | 60.7315 | 60.7681 | 62.8601 | 63.0844 | 124.0265 | 63.0112 | 60.9375
1625.3125 | 0.076294 | 0.42511 | -0.79041 | -0.20508 | 0.1741 | -0.25848 | -0.17303 | 61.1069 | -62.8326 | 0.050354 | -63.0295 | 60.8368 | 62.9883 | 62.9288 | 0.045776 | -0.077972 | 0.05661 | 0.29053 | -0.14526 | -0.14954 | 0.036621 | 0.041199 | -63.208 | 60.759 | 60.7498 | 62.8464 | 63.0295 | 124.0814 | 63.002 | 60.9192
1626.9688 | 0.045776 | 0.4689 | -0.79788 | -0.20187 | 0.16129 | -0.26489 | -0.17624 | 61.084 | -62.8143 | 0.068665 | -63.0707 | 60.7956 | 62.9974 | 62.9242 | 0.045776 | -0.076904 | 0.066223 | 0.28305 | -0.1506 | -0.15167 | 0.068665 | 0.086975 | -63.2309 | 60.7681 | 60.7544 | 62.8693 | 63.0569 | 124.0219 | 63.0203 | 60.9283
1628.6406 | 0.061035 | 0.43045 | -0.79575 | -0.23285 | 0.15915 | -0.25848 | -0.17731 | 61.0336 | -62.8967 | 0.073242 | -63.089 | 60.8688 | 62.9974 | 62.9562 | 0.045776 | -0.064087 | 0.079041 | 0.28839 | -0.16129 | -0.13886 | 0.068665 | 0.09613 | -63.2858 | 60.8597 | 60.8276 | 62.8784 | 63.0478 | 124.1364 | 62.9745 | 60.9055
1630.3438 | 0.061035 | 0.43259 | -0.7872 | -0.21042 | 0.16556 | -0.23819 | -0.15915 | 60.9924 | -62.9791 | -0.036621 | -63.1165 | 60.8734 | 63.0112 | 62.9425 | 0.061035 | -0.064087 | 0.079041 | 0.29907 | -0.1474 | -0.15381 | -0.050354 | -0.09613 | -63.327 | 60.8139 | 60.7956 | 62.8601 | 63.0798 | 124.0494 | 62.9929 | 60.9512
1632 | 0.045776 | 0.44113 | -0.79575 | -0.21896 | 0.17303 | -0.23926 | -0.16129 | 61.0428 | -62.8738 | 0.064087 | -63.0524 | 60.8871 | 62.9974 | 62.9333 | 0.045776 | -0.063019 | 0.076904 | 0.28732 | -0.15381 | -0.15167 | 0.059509 | 0.091553 | -63.2629 | 60.8047 | 60.7727 | 62.8464 | 63.0569 | 124.1684 | 62.9517 | 60.8917
1633.6719 | 0.045776 | 0.45822 | -0.79147 | -0.20615 | 0.15808 | -0.25421 | -0.16663 | 60.9787 | -62.9288 | -0.050354 | -63.0936 | 60.878 | 63.002 | 62.9333 | 0.045776 | -0.060883 | 0.077972 | 0.28732 | -0.15167 | -0.13779 | -0.068665 | -0.091553 | -63.3087 | 60.8047 | 60.7681 | 62.8555 | 63.089 | 124.0677 | 63.002 | 60.9283
1635.375 | 0.061035 | 0.44006 | -0.78186 | -0.20401 | 0.15701 | -0.26062 | -0.16129 | 61.0519 | -62.8281 | 0.07782 | -63.0615 | 60.8643 | 62.9745 | 62.9288 | 0.030518 | -0.05661 | 0.074768 | 0.28732 | -0.14954 | -0.13992 | 0.050354 | 0.068665 | -63.2401 | 60.8047 | 60.7956 | 62.8235 | 63.0569 | 124.1272 | 62.9517 | 60.9283
1637.0469 | 0.061035 | 0.45288 | -0.79361 | -0.21896 | 0.16556 | -0.29373 | -0.1709 | 61.0062 | -62.8281 | 0.050354 | -63.0753 | 60.791 | 62.9883 | 62.9288 | 0.061035 | -0.082245 | 0.095062 | 0.27771 | -0.16022 | -0.14206 | 0.045776 | 0.082397 | -63.2172 | 60.7452 | 60.7544 | 62.8555 | 63.0569 | 124.0311 | 62.9974 | 60.9009
1638.7031 | 0.045776 | 0.43793 | -0.80215 | -0.23178 | 0.16556 | -0.28091 | -0.17517 | 61.0245 | -62.8372 | 0.086975 | -63.0386 | 60.8231 | 63.002 | 62.9105 | 0.061035 | -0.077972 | 0.0737 | 0.28946 | -0.16769 | -0.14526 | 0.1236 | 0.1831 | -63.1714 | 60.7498 | 60.7544 | 62.8189 | 63.0524 | 124.1272 | 62.9425 | 60.9009
1640.3594 | 0.045776 | 0.41977 | -0.78613 | -0.22217 | 0.16449 | -0.25635 | -0.16449 | 61.0107 | -62.9013 | 0.050354 | -63.0661 | 60.8826 | 62.9791 | 62.9379 | 0.061035 | -0.05661 | 0.082245 | 0.28946 | -0.16129 | -0.16129 | 0.041199 | 0.091553 | -63.2858 | 60.8505 | 60.8368 | 62.8326 | 63.0295 | 124.1501 | 62.9379 | 60.9192
1642.0156 | 0.076294 | 0.43472 | -0.79147 | -0.22751 | 0.17838 | -0.28839 | -0.17517 | 61.084 | -62.764 | 0.16479 | -63.0157 | 60.8047 | 62.9791 | 62.9242 | 0.045776 | -0.080109 | 0.076904 | 0.28839 | -0.16876 | -0.15701 | 0.16479 | 0.27008 | -63.1348 | 60.7681 | 60.7544 | 62.8326 | 63.0341 | 124.1226 | 62.9379 | 60.91
1643.6719 | 0.045776 | 0.42191 | -0.78613 | -0.23605 | 0.15915 | -0.24887 | -0.17944 | 61.0062 | -62.8693 | 0.073242 | -63.0478 | 60.8871 | 62.9883 | 62.9013 | 0.015259 | -0.061951 | 0.075836 | 0.27664 | -0.15167 | -0.15701 | 0.050354 | 0.091553 | -63.2492 | 60.8231 | 60.8093 | 62.851 | 63.0203 | 124.1638 | 62.9333 | 60.9055
1645.3438 | 0.045776 | 0.44861 | -0.79788 | -0.20508 | 0.17838 | -0.27451 | -0.16663 | 61.0428 | -62.796 | 0.064087 | -63.0386 | 60.7727 | 62.9974 | 62.9196 | 0.061035 | -0.071564 | 0.0737 | 0.28091 | -0.15274 | -0.1506 | 0.059509 | 0.082397 | -63.1851 | 60.7407 | 60.7086 | 62.8464 | 63.0569 | 124.0082 | 62.9974 | 60.8917
1647 | 0.030518 | 0.439 | -0.79895 | -0.22217 | 0.16342 | -0.27985 | -0.18158 | 61.0794 | -62.7182 | 0.15564 | -63.002 | 60.7773 | 62.9837 | 62.9105 | 0.076294 | -0.071564 | 0.085449 | 0.28839 | -0.16449 | -0.15381 | 0.17395 | 0.25635 | -63.1577 | 60.7407 | 60.7452 | 62.8052 | 63.0112 | 124.1089 | 62.9517 | 60.8917
1648.6719 | 0.061035 | 0.43259 | -0.79254 | -0.23819 | 0.15167 | -0.26062 | -0.16876 | 60.9924 | -62.883 | 0.050354 | -63.0661 | 60.8551 | 62.9883 | 62.9379 | 0.045776 | -0.067291 | 0.084381 | 0.28625 | -0.15274 | -0.1442 | 0.050354 | 0.07782 | -63.2812 | 60.8231 | 60.8231 | 62.8372 | 63.0478 | 124.1318 | 62.9379 | 60.9146
1650.375 | 0.045776 | 0.43793 | -0.79041 | -0.2211 | 0.15808 | -0.28198 | -0.1709 | 60.997 | -62.8372 | 0.041199 | -63.0569 | 60.7819 | 62.9654 | 62.8922 | 0.061035 | -0.074768 | 0.067291 | 0.28305 | -0.16022 | -0.1474 | 0.059509 | 0.09613 | -63.2126 | 60.7498 | 60.7498 | 62.8189 | 63.0478 | 124.0173 | 63.002 | 60.9329
1652.0312 | 0.045776 | 0.46463 | -0.79788 | -0.19333 | 0.1709 | -0.27451 | -0.17197 | 61.0336 | -62.8052 | 0.059509 | -63.0386 | 60.7727 | 62.9654 | 62.9059 | 0.030518 | -0.068359 | 0.075836 | 0.28519 | -0.15701 | -0.13992 | 0.068665 | 0.086975 | -63.2126 | 60.7544 | 60.7315 | 62.8235 | 63.0615 | 123.967 | 62.9883 | 60.9009
1653.6875 | 0.076294 | 0.44113 | -0.79254 | -0.18906 | 0.15808 | -0.2478 | -0.16663 | 61.0153 | -62.883 | -0.022888 | -63.0707 | 60.8414 | 62.9974 | 62.9196 | 0.076294 | -0.057678 | 0.069427 | 0.28732 | -0.13992 | -0.14633 | -0.004578 | -0.013733 | -63.2492 | 60.7544 | 60.759 | 62.8143 | 63.0341 | 124.0265 | 62.9974 | 60.8963
1655.3906 | 0.045776 | 0.44861 | -0.78186 | -0.20187 | 0.16983 | -0.25742 | -0.16129 | 61.0565 | -62.8006 | 0.050354 | -63.0295 | 60.7773 | 63.002 | 62.9105 | 0.061035 | -0.071564 | 0.067291 | 0.27557 | -0.15167 | -0.15808 | 0.050354 | 0.045776 | -63.1851 | 60.7498 | 60.7407 | 62.8098 | 63.0203 | 124.0173 | 62.9745 | 60.9009
1657.0469 | 0.045776 | 0.45395 | -0.80536 | -0.22537 | 0.15274 | -0.27771 | -0.17624 | 61.0245 | -62.8143 | 0.027466 | -63.0569 | 60.7681 | 62.9837 | 62.9333 | 0.061035 | -0.080109 | 0.067291 | 0.27664 | -0.15915 | -0.14099 | 0.064087 | 0.07782 | -63.2217 | 60.7224 | 60.7498 | 62.8006 | 63.0569 | 123.9899 | 62.9974 | 60.8963
1658.7031 | 0.045776 | 0.45502 | -0.79361 | -0.21469 | 0.16235 | -0.27985 | -0.17731 | 61.0153 | -62.8235 | 0.091553 | -63.0295 | 60.8002 | 62.9654 | 62.8876 | 0.045776 | -0.077972 | 0.072632 | 0.28839 | -0.16663 | -0.15167 | 0.13275 | 0.17853 | -63.1714 | 60.7361 | 60.7681 | 62.8326 | 63.0203 | 124.1135 | 62.9425 | 60.8734
1660.3594 | 0.045776 | 0.44113 | -0.79681 | -0.2179 | 0.16556 | -0.26062 | -0.17303 | 61.0519 | -62.8052 | 0.12817 | -63.0249 | 60.8368 | 62.9608 | 62.9196 | 0.045776 | -0.066223 | 0.081177 | 0.28412 | -0.16556 | -0.15595 | 0.09613 | 0.15564 | -63.2355 | 60.8047 | 60.8047 | 62.8281 | 63.0112 | 124.0814 | 62.9288 | 60.9192
1662.0469 | 0.030518 | 0.44006 | -0.78934 | -0.22964 | 0.16129 | -0.26276 | -0.17303 | 61.0794 | -62.7548 | 0.17395 | -62.9745 | 60.791 | 62.9837 | 62.883 | 0.045776 | -0.082245 | 0.079041 | 0.29053 | -0.16342 | -0.15488 | 0.16937 | 0.24719 | -63.1485 | 60.7498 | 60.7498 | 62.8006 | 63.002 | 124.0723 | 62.9288 | 60.8826
1663.7031 | 0.045776 | 0.439 | -0.79575 | -0.21149 | 0.16663 | -0.27557 | -0.17944 | 61.084 | -62.7365 | 0.16937 | -62.9974 | 60.8002 | 62.9883 | 62.8693 | 0.061035 | -0.0737 | 0.072632 | 0.27985 | -0.17197 | -0.15381 | 0.17853 | 0.24261 | -63.1073 | 60.7315 | 60.7452 | 62.8006 | 63.0386 | 124.0906 | 62.9425 | 60.8963
1665.3594 | 0.030518 | 0.43793 | -0.80002 | -0.22324 | 0.1709 | -0.25848 | -0.17197 | 60.9879 | -62.8601 | 0.068665 | -63.0569 | 60.8414 | 62.9883 | 62.915 | 0.045776 | -0.063019 | 0.067291 | 0.29907 | -0.15701 | -0.14633 | 0.050354 | 0.10071 | -63.2721 | 60.8459 | 60.7956 | 62.8281 | 63.0569 | 124.0997 | 62.9288 | 60.9238
1667.0938 | 0.045776 | 0.43259 | -0.78293 | -0.20081 | 0.17731 | -0.23605 | -0.16663 | 60.9879 | -62.8418 | 0.022888 | -63.0478 | 60.8505 | 62.9608 | 62.9196 | 0.061035 | -0.065155 | 0.079041 | 0.30014 | -0.14313 | -0.15274 | -0.032043 | -0.022888 | -63.2767 | 60.7956 | 60.7681 | 62.8464 | 63.0478 | 123.9853 | 62.9654 | 60.91
1668.75 | 0.076294 | 0.4454 | -0.79895 | -0.20187 | 0.16342 | -0.25955 | -0.16342 | 60.9833 | -62.851 | -0.022888 | -63.0524 | 60.8047 | 62.9608 | 62.9105 | 0.045776 | -0.065155 | 0.072632 | 0.28198 | -0.15274 | -0.14526 | 0.004578 | 0.013733 | -63.1989 | 60.7452 | 60.7224 | 62.8189 | 63.0112 | 124.0356 | 62.97 | 60.8917
1670.4375 | 0.045776 | 0.45075 | -0.80109 | -0.22964 | 0.16983 | -0.28305 | -0.17944 | 60.9467 | -62.8143 | 0.050354 | -63.0295 | 60.7819 | 62.9745 | 62.9059 | 0.045776 | -0.081177 | 0.071564 | 0.28198 | -0.16769 | -0.14847 | 0.073242 | 0.1236 | -63.1989 | 60.704 | 60.7361 | 62.8052 | 63.0478 | 124.0219 | 62.9333 | 60.8643
1672.1094 | 0.045776 | 0.44113 | -0.79041 | -0.21362 | 0.16449 | -0.2478 | -0.16556 | 60.9558 | -62.9333 | -0.045776 | -63.089 | 60.8368 | 62.9654 | 62.8784 | 0.045776 | -0.058746 | 0.074768 | 0.29266 | -0.14954 | -0.13886 | -0.059509 | -0.07782 | -63.295 | 60.8093 | 60.7819 | 62.8098 | 63.0386 | 123.9578 | 62.97 | 60.91
1673.7656 | 0.076294 | 0.45822 | -0.78934 | -0.20935 | 0.15488 | -0.2713 | -0.16663 | 61.0245 | -62.7594 | 0.068665 | -63.0157 | 60.7544 | 62.9791 | 62.9105 | 0.045776 | -0.076904 | 0.065155 | 0.27985 | -0.14633 | -0.13886 | 0.059509 | 0.082397 | -63.1577 | 60.7132 | 60.7086 | 62.8052 | 63.0157 | 123.9624 | 63.0112 | 60.8917
1675.4219 | 0.061035 | 0.439 | -0.79681 | -0.20935 | 0.18585 | -0.26062 | -0.16235 | 61.0199 | -62.7686 | 0.068665 | -63.0066 | 60.759 | 62.9745 | 62.8876 | 0.030518 | -0.068359 | 0.063019 | 0.28305 | -0.14633 | -0.1442 | 0.059509 | 0.073242 | -63.1805 | 60.704 | 60.704 | 62.8281 | 63.0157 | 123.9716 | 62.9837 | 60.8963
1677.0938 | 0.045776 | 0.45395 | -0.79361 | -0.21896 | 0.17197 | -0.29053 | -0.18372 | 60.965 | -62.8372 | 0.045776 | -63.0478 | 60.7773 | 62.9837 | 62.8967 | 0.045776 | -0.0737 | 0.068359 | 0.28732 | -0.16556 | -0.1506 | 0.059509 | 0.1236 | -63.176 | 60.7498 | 60.7452 | 62.8006 | 63.0157 | 124.0173 | 62.9654 | 60.8688
1678.7656 | 0.045776 | 0.43152 | -0.78827 | -0.21896 | 0.16876 | -0.25207 | -0.1709 | 61.0016 | -62.8418 | 0.07782 | -63.0249 | 60.8459 | 62.97 | 62.9242 | 0.030518 | -0.068359 | 0.064087 | 0.28839 | -0.14633 | -0.16876 | 0.041199 | 0.082397 | -63.2217 | 60.8231 | 60.791 | 62.8189 | 63.0386 | 124.0906 | 62.9105 | 60.8826
1680.4688 | 0.076294 | 0.439 | -0.784 | -0.21362 | 0.16876 | -0.26276 | -0.16235 | 61.0336 | -62.7869 | 0.050354 | -62.9791 | 60.7819 | 62.9379 | 62.8784 | 0.076294 | -0.072632 | 0.071564 | 0.30548 | -0.15488 | -0.15701 | 0.054932 | 0.041199 | -63.1805 | 60.7269 | 60.6903 | 62.8189 | 63.0524 | 123.9853 | 62.97 | 60.8871
1682.1406 | 0.091553 | 0.42618 | -0.79575 | -0.22964 | 0.16449 | -0.25207 | -0.16983 | 60.9924 | -62.8235 | 0.073242 | -63.0203 | 60.8414 | 62.9562 | 62.8784 | 0.061035 | -0.059814 | 0.077972 | 0.28519 | -0.15381 | -0.1474 | 0.045776 | 0.091553 | -63.2126 | 60.7773 | 60.7773 | 62.8006 | 63.0249 | 124.0952 | 62.8922 | 60.8826
1683.7969 | 0.076294 | 0.43472 | -0.79681 | -0.22324 | 0.16129 | -0.27771 | -0.16876 | 61.0016 | -62.7502 | 0.16479 | -62.9791 | 60.7636 | 62.9654 | 62.8876 | 0.045776 | -0.076904 | 0.084381 | 0.28091 | -0.16022 | -0.13245 | 0.12817 | 0.21973 | -63.1805 | 60.759 | 60.7544 | 62.8143 | 63.0341 | 124.0311 | 62.9242 | 60.8871
1685.4531 | 0.045776 | 0.43472 | -0.79681 | -0.22858 | 0.17197 | -0.26276 | -0.1709 | 60.9787 | -62.7914 | 0.11444 | -63.0157 | 60.8093 | 62.9471 | 62.8922 | 0.030518 | -0.071564 | 0.081177 | 0.29053 | -0.16876 | -0.15381 | 0.059509 | 0.13275 | -63.2172 | 60.7864 | 60.7727 | 62.8326 | 63.0157 | 124.0265 | 62.8922 | 60.8917
1687.1094 | 0.045776 | 0.45609 | -0.78613 | -0.19867 | 0.15808 | -0.25207 | -0.1741 | 60.9467 | -62.883 | -0.054932 | -63.0569 | 60.8093 | 62.9883 | 62.9013 | 0.045776 | -0.063019 | 0.066223 | 0.29266 | -0.14633 | -0.1474 | -0.068665 | -0.086975 | -63.2767 | 60.8139 | 60.7636 | 62.8098 | 63.0386 | 123.9716 | 62.9654 | 60.8871
1688.7656 | 0.045776 | 0.45288 | -0.79681 | -0.1976 | 0.16449 | -0.25742 | -0.16876 | 60.9695 | -62.8006 | 0.004578 | -63.0203 | 60.8002 | 62.9608 | 62.8784 | 0.061035 | -0.064087 | 0.058746 | 0.28305 | -0.14099 | -0.1474 | 0.013733 | 0.027466 | -63.176 | 60.7224 | 60.6995 | 62.8052 | 62.9929 | 123.9761 | 62.9517 | 60.8414
1690.4219 | 0.061035 | 0.43366 | -0.78613 | -0.22324 | 0.15701 | -0.25742 | -0.16663 | 61.0062 | -62.8052 | 0.068665 | -62.9974 | 60.8368 | 62.9791 | 62.8738 | 0.061035 | -0.057678 | 0.065155 | 0.27985 | -0.14526 | -0.1474 | 0.059509 | 0.073242 | -63.1851 | 60.7819 | 60.7727 | 62.7731 | 63.0066 | 124.0494 | 62.8876 | 60.8734
1692.1406 | 0.045776 | 0.44006 | -0.79041 | -0.20294 | 0.16342 | -0.25207 | -0.17517 | 60.9329 | -62.8967 | -0.045776 | -63.0478 | 60.8276 | 62.9562 | 62.9059 | 0.076294 | -0.05661 | 0.074768 | 0.28946 | -0.15167 | -0.13992 | -0.068665 | -0.082397 | -63.2767 | 60.791 | 60.7773 | 62.8098 | 63.0295 | 123.9532 | 62.9562 | 60.9055
1693.7969 | 0.076294 | 0.42511 | -0.79254 | -0.20294 | 0.16342 | -0.25528 | -0.15915 | 60.9421 | -62.8601 | -0.013733 | -63.0341 | 60.8185 | 62.9471 | 62.8738 | 0.045776 | -0.064087 | 0.071564 | 0.28625 | -0.14206 | -0.14633 | -0.073242 | -0.054932 | -63.2721 | 60.7681 | 60.7864 | 62.8098 | 63.0341 | 123.9441 | 62.9562 | 60.8688
1695.4688 | 0.061035 | 0.43259 | -0.79681 | -0.22964 | 0.15808 | -0.27344 | -0.16769 | 60.9283 | -62.8326 | 0.059509 | -63.0341 | 60.8368 | 62.9745 | 62.8647 | 0.061035 | -0.066223 | 0.075836 | 0.27878 | -0.15808 | -0.14099 | 0.032043 | 0.10071 | -63.1989 | 60.7864 | 60.7819 | 62.8235 | 63.0066 | 124.0768 | 62.8922 | 60.8414
1697.125 | 0.045776 | 0.45502 | -0.79468 | -0.21683 | 0.16129 | -0.27557 | -0.16876 | 60.9329 | -62.851 | -0.036621 | -63.0249 | 60.8093 | 62.9791 | 62.9059 | 0.061035 | -0.084381 | 0.074768 | 0.29373 | -0.16022 | -0.14847 | -0.027466 | -0.027466 | -63.2034 | 60.7452 | 60.7178 | 62.8052 | 63.0249 | 123.9624 | 62.9608 | 60.8368
1698.7812 | 0.061035 | 0.46677 | -0.80429 | -0.21683 | 0.17624 | -0.30441 | -0.1709 | 60.9558 | -62.7914 | 0.050354 | -63.0341 | 60.7407 | 62.9425 | 62.8555 | 0.061035 | -0.089722 | 0.064087 | 0.27664 | -0.16342 | -0.1474 | 0.041199 | 0.082397 | -63.1714 | 60.7132 | 60.759 | 62.7869 | 63.002 | 123.9212 | 62.9517 | 60.8826
1700.4375 | 0.076294 | 0.44861 | -0.80215 | -0.2179 | 0.1741 | -0.29694 | -0.17838 | 60.965 | -62.796 | 0.073242 | -63.0157 | 60.7681 | 62.9333 | 62.851 | 0.045776 | -0.072632 | 0.060883 | 0.28305 | -0.16556 | -0.14099 | 0.09613 | 0.15564 | -63.1531 | 60.7269 | 60.7132 | 62.7914 | 63.0066 | 124.0356 | 62.8967 | 60.8231
1702.0938 | 0.061035 | 0.44006 | -0.79147 | -0.21576 | 0.1741 | -0.2681 | -0.17731 | 61.0016 | -62.7686 | 0.13275 | -62.9745 | 60.8002 | 62.9425 | 62.851 | 0.061035 | -0.063019 | 0.070496 | 0.28412 | -0.16342 | -0.15595 | 0.091553 | 0.16022 | -63.1989 | 60.7819 | 60.7864 | 62.7823 | 62.9791 | 123.999 | 62.883 | 60.8917
1703.75 | 0.061035 | 0.4454 | -0.79254 | -0.22537 | 0.16769 | -0.27451 | -0.18799 | 61.0474 | -62.7045 | 0.17853 | -62.9471 | 60.7819 | 62.9242 | 62.8601 | 0.030518 | -0.082245 | 0.072632 | 0.27878 | -0.16663 | -0.15915 | 0.15106 | 0.24261 | -63.1073 | 60.6857 | 60.7132 | 62.7731 | 62.9929 | 124.0448 | 62.8967 | 60.8322
1705.4062 | 0.061035 | 0.43259 | -0.78613 | -0.22644 | 0.15381 | -0.23819 | -0.17517 | 60.9558 | -62.8372 | 0.059509 | -63.0249 | 60.8139 | 62.9471 | 62.8922 | 0.030518 | -0.065155 | 0.076904 | 0.28198 | -0.15488 | -0.15808 | 0.036621 | 0.073242 | -63.2217 | 60.7956 | 60.7636 | 62.8006 | 63.0066 | 124.0494 | 62.8784 | 60.8734
1707.0625 | 0.061035 | 0.43579 | -0.79788 | -0.20615 | 0.17731 | -0.25421 | -0.15808 | 60.9192 | -62.8693 | -0.054932 | -63.0295 | 60.8368 | 62.9517 | 62.8967 | 0.076294 | -0.063019 | 0.0737 | 0.28839 | -0.14526 | -0.14313 | -0.041199 | -0.086975 | -63.2675 | 60.7452 | 60.7773 | 62.8189 | 63.0112 | 123.9304 | 62.9425 | 60.8643
1708.7188 | 0.061035 | 0.46249 | -0.79895 | -0.22537 | 0.16129 | -0.28625 | -0.17517 | 60.9512 | -62.7731 | 0.09613 | -62.9791 | 60.759 | 62.9517 | 62.8647 | 0.076294 | -0.095062 | 0.0737 | 0.28625 | -0.18051 | -0.13779 | 0.13275 | 0.19684 | -63.1302 | 60.704 | 60.7132 | 62.7914 | 62.9791 | 124.0311 | 62.8922 | 60.8139
1710.375 | 0.045776 | 0.44327 | -0.79361 | -0.21576 | 0.17624 | -0.27451 | -0.18265 | 61.0199 | -62.7045 | 0.16937 | -62.9654 | 60.759 | 62.915 | 62.8555 | 0.045776 | -0.083313 | 0.072632 | 0.27344 | -0.16556 | -0.14847 | 0.16937 | 0.25635 | -63.0981 | 60.6949 | 60.7498 | 62.7823 | 63.0066 | 124.0128 | 62.8922 | 60.8414
1712.0312 | 0.030518 | 0.4422 | -0.80215 | -0.21683 | 0.15595 | -0.27878 | -0.1741 | 60.9741 | -62.764 | 0.091553 | -62.9974 | 60.7636 | 62.9425 | 62.8647 | 0.061035 | -0.074768 | 0.070496 | 0.28839 | -0.16876 | -0.1506 | 0.12817 | 0.18768 | -63.1256 | 60.7224 | 60.7086 | 62.7731 | 63.0066 | 124.0311 | 62.8876 | 60.8368
1713.6875 | 0.061035 | 0.43579 | -0.784 | -0.21362 | 0.16769 | -0.23605 | -0.16449 | 61.0199 | -62.7594 | 0.082397 | -62.9745 | 60.8047 | 62.9242 | 62.8555 | 0.030518 | -0.059814 | 0.068359 | 0.29053 | -0.14847 | -0.15808 | 0.050354 | 0.054932 | -63.1943 | 60.7636 | 60.7361 | 62.7686 | 63.0112 | 123.9716 | 62.8967 | 60.8414
1715.3438 | 0.061035 | 0.43472 | -0.79575 | -0.20187 | 0.1741 | -0.2478 | -0.17517 | 60.9833 | -62.7777 | 0.07782 | -62.9791 | 60.8139 | 62.9562 | 62.851 | 0.061035 | -0.069427 | 0.065155 | 0.27771 | -0.13779 | -0.16129 | 0.064087 | 0.082397 | -63.1805 | 60.7864 | 60.7361 | 62.7869 | 63.0112 | 124.0036 | 62.8967 | 60.8322
1717.0156 | 0.061035 | 0.44968 | -0.78613 | -0.21469 | 0.16983 | -0.25955 | -0.16556 | 60.8963 | -62.883 | -0.059509 | -63.0478 | 60.8322 | 62.9654 | 62.8922 | 0.076294 | -0.045929 | 0.0737 | 0.29053 | -0.13886 | -0.13886 | -0.054932 | -0.091553 | -63.2629 | 60.7452 | 60.7407 | 62.7686 | 63.0157 | 123.9075 | 62.9608 | 60.8826
1718.6875 | 0.061035 | 0.43472 | -0.78613 | -0.20508 | 0.15808 | -0.25955 | -0.16769 | 60.9009 | -62.8372 | -0.050354 | -63.0249 | 60.8047 | 62.9517 | 62.8418 | 0.061035 | -0.076904 | 0.077972 | 0.29159 | -0.14526 | -0.14633 | -0.064087 | -0.09613 | -63.2446 | 60.7498 | 60.7498 | 62.8098 | 63.0295 | 123.9258 | 62.9471 | 60.8505
1720.3438 | 0.061035 | 0.45502 | -0.79681 | -0.20828 | 0.16235 | -0.2713 | -0.15595 | 60.9741 | -62.7457 | 0.041199 | -62.9608 | 60.7498 | 62.9562 | 62.8601 | 0.045776 | -0.081177 | 0.071564 | 0.27344 | -0.15488 | -0.14847 | 0.036621 | 0.073242 | -63.121 | 60.6766 | 60.6766 | 62.7869 | 62.9837 | 123.9212 | 62.9333 | 60.8597
1721.9844 | 0.061035 | 0.44434 | -0.79575 | -0.20187 | 0.17517 | -0.25848 | -0.16449 | 60.9146 | -62.8464 | -0.050354 | -63.0386 | 60.8139 | 62.9425 | 62.8922 | 0.061035 | -0.063019 | 0.063019 | 0.28625 | -0.15381 | -0.13458 | -0.073242 | -0.082397 | -63.2309 | 60.7498 | 60.7361 | 62.7823 | 62.9974 | 123.9304 | 62.9288 | 60.8368
1723.6562 | 0.061035 | 0.4657 | -0.78934 | -0.20935 | 0.16449 | -0.28305 | -0.17197 | 60.9741 | -62.7365 | 0.064087 | -62.97 | 60.6903 | 62.8967 | 62.8555 | 0.061035 | -0.081177 | 0.061951 | 0.27451 | -0.1709 | -0.13779 | 0.054932 | 0.064087 | -63.1393 | 60.6857 | 60.6995 | 62.7502 | 62.9974 | 123.8617 | 62.9425 | 60.8597
1725.3125 | 0.061035 | 0.45288 | -0.80536 | -0.22217 | 0.1709 | -0.28412 | -0.18692 | 60.9558 | -62.7457 | 0.10071 | -62.9883 | 60.7452 | 62.9288 | 62.8326 | 0.091553 | -0.074768 | 0.068359 | 0.28091 | -0.17624 | -0.13886 | 0.14648 | 0.20142 | -63.0798 | 60.704 | 60.7224 | 62.7457 | 62.9929 | 124.0219 | 62.8876 | 60.8505
1726.9688 | 0.045776 | 0.44113 | -0.80002 | -0.23926 | 0.15701 | -0.298 | -0.18158 | 60.9512 | -62.7869 | 0.07782 | -62.9837 | 60.7681 | 62.9333 | 62.8464 | 0.061035 | -0.09079 | 0.070496 | 0.28305 | -0.18372 | -0.14954 | 0.09613 | 0.14648 | -63.1302 | 60.7132 | 60.6857 | 62.7457 | 62.9745 | 123.999 | 62.9013 | 60.8322
1728.6562 | 0.045776 | 0.43152 | -0.79041 | -0.2179 | 0.18051 | -0.24567 | -0.1709 | 60.9467 | -62.8281 | 0.068665 | -62.9974 | 60.8276 | 62.9425 | 62.8647 | 0.076294 | -0.072632 | 0.082245 | 0.2948 | -0.14847 | -0.16449 | 0.032043 | 0.07782 | -63.2034 | 60.8002 | 60.7636 | 62.7777 | 62.97 | 124.0311 | 62.8555 | 60.8505
1730.3594 | 0.061035 | 0.44968 | -0.784 | -0.1976 | 0.17944 | -0.26276 | -0.16342 | 60.9879 | -62.7319 | 0.059509 | -62.9654 | 60.7224 | 62.9105 | 62.8738 | 0.015259 | -0.083313 | 0.0737 | 0.29907 | -0.15274 | -0.16022 | 0.068665 | 0.068665 | -63.1165 | 60.6445 | 60.6766 | 62.7777 | 62.97 | 123.9029 | 62.9288 | 60.8322
1732.0312 | 0.061035 | 0.44434 | -0.79575 | -0.21683 | 0.15701 | -0.28091 | -0.17197 | 61.0153 | -62.677 | 0.1831 | -62.9288 | 60.7452 | 62.8876 | 62.851 | 0.061035 | -0.079041 | 0.069427 | 0.29053 | -0.16876 | -0.15915 | 0.16937 | 0.26093 | -63.0753 | 60.6857 | 60.7086 | 62.7502 | 62.9745 | 123.9944 | 62.8601 | 60.8459
1733.6875 | 0.061035 | 0.4422 | -0.79361 | -0.21896 | 0.16983 | -0.28198 | -0.18158 | 60.9375 | -62.7869 | 0.054932 | -62.9837 | 60.7636 | 62.9288 | 62.8418 | 0.030518 | -0.091858 | 0.076904 | 0.28198 | -0.15915 | -0.15701 | 0.10071 | 0.13275 | -63.1348 | 60.6903 | 60.7086 | 62.7686 | 62.9837 | 123.9761 | 62.883 | 60.8459
1735.3438 | 0.015259 | 0.46463 | -0.80215 | -0.22217 | 0.16129 | -0.27237 | -0.17624 | 60.9741 | -62.7411 | 0.091553 | -62.9654 | 60.759 | 62.9059 | 62.8418 | 0.045776 | -0.0737 | 0.068359 | 0.28198 | -0.1741 | -0.15915 | 0.16022 | 0.20142 | -63.1119 | 60.6903 | 60.6812 | 62.7411 | 62.9654 | 124.0128 | 62.8784 | 60.8276
1737 | 0.045776 | 0.44113 | -0.784 | -0.22751 | 0.16663 | -0.27985 | -0.18585 | 60.9787 | -62.7502 | 0.086975 | -62.97 | 60.7361 | 62.915 | 62.8372 | 0.045776 | -0.074768 | 0.064087 | 0.27985 | -0.17303 | -0.1506 | 0.15564 | 0.18768 | -63.1027 | 60.6949 | 60.6903 | 62.7594 | 62.9745 | 123.999 | 62.8693 | 60.8231
1738.6719 | 0.045776 | 0.42618 | -0.78293 | -0.21255 | 0.16129 | -0.22964 | -0.16022 | 60.9604 | -62.8098 | 0.013733 | -63.0066 | 60.7956 | 62.9288 | 62.8555 | 0.061035 | -0.055542 | 0.0737 | 0.30121 | -0.13245 | -0.16449 | -0.045776 | -0.050354 | -63.2355 | 60.759 | 60.7086 | 62.7914 | 63.0157 | 123.8709 | 62.9059 | 60.8688
1740.3281 | 0.045776 | 0.45822 | -0.80215 | -0.20828 | 0.16129 | -0.27557 | -0.16556 | 60.9604 | -62.7365 | 0.050354 | -62.9883 | 60.6857 | 62.9196 | 62.8464 | 0.061035 | -0.079041 | 0.065155 | 0.27985 | -0.1506 | -0.13779 | 0.086975 | 0.086975 | -63.1302 | 60.672 | 60.672 | 62.7686 | 62.9974 | 123.8525 | 62.9333 | 60.8505
1741.9688 | 0.045776 | 0.44327 | -0.80002 | -0.21255 | 0.16876 | -0.25528 | -0.1709 | 60.9375 | -62.764 | -0.004578 | -63.002 | 60.7452 | 62.9379 | 62.8693 | 0.061035 | -0.069427 | 0.066223 | 0.28625 | -0.13886 | -0.15167 | 0.045776 | 0.018311 | -63.1439 | 60.6903 | 60.6674 | 62.7502 | 62.9837 | 123.9212 | 62.9379 | 60.8368
1743.6406 | 0.061035 | 0.4422 | -0.80002 | -0.23392 | 0.16983 | -0.26382 | -0.17303 | 60.9238 | -62.796 | 0.059509 | -63.0066 | 60.7956 | 62.9105 | 62.8738 | 0.061035 | -0.05127 | 0.072632 | 0.28839 | -0.15274 | -0.1442 | 0.041199 | 0.086975 | -63.2034 | 60.7727 | 60.7315 | 62.796 | 63.002 | 124.0036 | 62.8647 | 60.8276
1745.2969 | 0.076294 | 0.42938 | -0.77972 | -0.23285 | 0.16235 | -0.24994 | -0.17197 | 60.9467 | -62.7548 | 0.082397 | -62.9608 | 60.7864 | 62.9333 | 62.8555 | 0.030518 | -0.065155 | 0.086517 | 0.28946 | -0.15167 | -0.15488 | 0.064087 | 0.086975 | -63.1531 | 60.7315 | 60.7132 | 62.7274 | 62.9883 | 123.9899 | 62.883 | 60.8368
1746.9531 | 0.045776 | 0.43366 | -0.79041 | -0.2243 | 0.17197 | -0.24674 | -0.16129 | 60.878 | -62.8372 | -0.032043 | -63.002 | 60.8047 | 62.9608 | 62.8601 | 0.030518 | -0.067291 | 0.0737 | 0.29053 | -0.14526 | -0.14206 | -0.07782 | -0.086975 | -63.2584 | 60.7544 | 60.7132 | 62.764 | 63.0066 | 123.8571 | 62.9013 | 60.8459
1748.6406 | 0.076294 | 0.4422 | -0.80749 | -0.22217 | 0.15488 | -0.29694 | -0.17624 | 60.8688 | -62.7686 | 0.050354 | -62.9791 | 60.7178 | 62.9196 | 62.8464 | 0.061035 | -0.0737 | 0.061951 | 0.28305 | -0.16556 | -0.13992 | 0.054932 | 0.09613 | -63.1439 | 60.6812 | 60.6949 | 62.764 | 62.97 | 123.912 | 62.9105 | 60.8643
1750.2969 | 0.061035 | 0.43152 | -0.79788 | -0.22644 | 0.15595 | -0.26596 | -0.17197 | 60.9329 | -62.7502 | 0.10529 | -62.9745 | 60.7636 | 62.8876 | 62.8326 | 0.061035 | -0.0737 | 0.071564 | 0.28625 | -0.17197 | -0.14526 | 0.068665 | 0.1236 | -63.176 | 60.7452 | 60.7361 | 62.764 | 62.97 | 123.9258 | 62.8647 | 60.8551
1751.9531 | 0.061035 | 0.4422 | -0.79681 | -0.20081 | 0.16342 | -0.24994 | -0.16663 | 60.878 | -62.8372 | -0.032043 | -63.0112 | 60.8139 | 62.9013 | 62.8601 | 0.045776 | -0.043793 | 0.077972 | 0.28732 | -0.1442 | -0.15167 | -0.07782 | -0.064087 | -63.2401 | 60.7498 | 60.7224 | 62.7731 | 62.9929 | 123.848 | 62.9196 | 60.8597
1753.625 | 0.045776 | 0.46143 | -0.80322 | -0.20401 | 0.16983 | -0.28839 | -0.17517 | 60.9192 | -62.7411 | 0.036621 | -62.9837 | 60.7315 | 62.9288 | 62.851 | 0.045776 | -0.082245 | 0.068359 | 0.28625 | -0.15595 | -0.1442 | 0.045776 | 0.082397 | -63.1531 | 60.6812 | 60.672 | 62.764 | 62.9791 | 123.8663 | 62.9013 | 60.8276
1755.2969 | 0.045776 | 0.42938 | -0.78186 | -0.21362 | 0.15915 | -0.25742 | -0.16556 | 60.8871 | -62.8464 | -0.054932 | -63.0203 | 60.7819 | 62.915 | 62.8464 | 0.076294 | -0.063019 | 0.075836 | 0.29053 | -0.15595 | -0.15381 | -0.050354 | -0.091553 | -63.2126 | 60.7819 | 60.7361 | 62.7869 | 62.9837 | 123.8709 | 62.9059 | 60.8322
1756.9688 | 0.061035 | 0.4422 | -0.80002 | -0.21042 | 0.15808 | -0.26382 | -0.16342 | 60.8871 | -62.796 | -0.022888 | -62.9974 | 60.7544 | 62.9105 | 62.8464 | 0.045776 | -0.068359 | 0.060883 | 0.28412 | -0.1442 | -0.14954 | -0.022888 | -0.022888 | -63.1485 | 60.6903 | 60.6995 | 62.7777 | 62.9608 | 123.8937 | 62.8922 | 60.8047
1758.6406 | 0.045776 | 0.42404 | -0.78934 | -0.21683 | 0.17197 | -0.25955 | -0.16342 | 60.91 | -62.7869 | 0.027466 | -62.9791 | 60.7819 | 62.9242 | 62.8464 | 0.030518 | -0.065155 | 0.068359 | 0.28625 | -0.1506 | -0.15808 | -0.036621 | -0.027466 | -63.2126 | 60.704 | 60.7224 | 62.764 | 62.9837 | 123.848 | 62.9196 | 60.8551
1760.2969 | 0.045776 | 0.439 | -0.78507 | -0.20828 | 0.17197 | -0.25955 | -0.16663 | 60.8551 | -62.8418 | -0.041199 | -63.0203 | 60.7956 | 62.9196 | 62.8372 | 0.045776 | -0.060883 | 0.074768 | 0.28946 | -0.1506 | -0.14954 | -0.068665 | -0.07782 | -63.2355 | 60.7269 | 60.7086 | 62.7777 | 62.9837 | 123.8342 | 62.9105 | 60.8505
1761.9531 | 0.045776 | 0.42725 | -0.79361 | -0.22324 | 0.16769 | -0.26062 | -0.16449 | 60.9329 | -62.7228 | 0.086975 | -62.9471 | 60.7452 | 62.915 | 62.8326 | 0.061035 | -0.064087 | 0.081177 | 0.30228 | -0.15915 | -0.15381 | 0.045776 | 0.073242 | -63.1256 | 60.7086 | 60.7178 | 62.7502 | 62.9562 | 123.9304 | 62.851 | 60.8139
1763.625 | 0.045776 | 0.46463 | -0.79788 | -0.21149 | 0.16235 | -0.298 | -0.17303 | 60.9009 | -62.7136 | 0.050354 | -62.9654 | 60.6766 | 62.8738 | 62.8555 | 0.061035 | -0.0737 | 0.058746 | 0.28091 | -0.16663 | -0.13351 | 0.041199 | 0.07782 | -63.1119 | 60.6674 | 60.6812 | 62.7548 | 62.9425 | 123.8205 | 62.9013 | 60.8368
1765.2812 | 0.061035 | 0.439 | -0.79575 | -0.23926 | 0.17197 | -0.27344 | -0.18372 | 60.9192 | -62.7182 | 0.15106 | -62.9333 | 60.7636 | 62.8922 | 62.8281 | 0.030518 | -0.0737 | 0.075836 | 0.28839 | -0.17731 | -0.15595 | 0.10529 | 0.16022 | -63.1531 | 60.7269 | 60.7224 | 62.7548 | 62.9379 | 123.9029 | 62.8372 | 60.8505
1766.9375 | 0.045776 | 0.44754 | -0.79361 | -0.19867 | 0.15595 | -0.25314 | -0.1709 | 60.8643 | -62.8235 | -0.064087 | -63.002 | 60.7681 | 62.9013 | 62.8098 | 0.061035 | -0.067291 | 0.061951 | 0.29053 | -0.1442 | -0.14206 | -0.036621 | -0.068665 | -63.1851 | 60.704 | 60.6766 | 62.7594 | 62.9608 | 123.8754 | 62.9059 | 60.8093
1768.5938 | 0.045776 | 0.47852 | -0.80215 | -0.21576 | 0.15488 | -0.29266 | -0.18372 | 60.8688 | -62.7548 | 0.018311 | -62.9745 | 60.7224 | 62.9059 | 62.8052 | 0.045776 | -0.091858 | 0.059814 | 0.27985 | -0.15595 | -0.14313 | 0.036621 | 0.09613 | -63.1256 | 60.6674 | 60.672 | 62.764 | 62.97 | 123.8617 | 62.8738 | 60.7956
1770.3125 | 0.045776 | 0.43472 | -0.7872 | -0.2211 | 0.17197 | -0.24353 | -0.16556 | 60.9329 | -62.7502 | 0.073242 | -62.9517 | 60.7636 | 62.8967 | 62.8418 | 0.061035 | -0.067291 | 0.068359 | 0.2948 | -0.15915 | -0.15274 | 0.054932 | 0.07782 | -63.1256 | 60.7224 | 60.7224 | 62.7319 | 62.9517 | 123.9349 | 62.8372 | 60.8047
1771.9844 | 0.045776 | 0.42831 | -0.80215 | -0.22644 | 0.16235 | -0.2713 | -0.18158 | 60.8871 | -62.7548 | 0.10529 | -62.9745 | 60.7819 | 62.9013 | 62.8464 | 0.045776 | -0.077972 | 0.082245 | 0.27985 | -0.16983 | -0.14847 | 0.073242 | 0.10529 | -63.1485 | 60.7407 | 60.7315 | 62.7686 | 62.97 | 123.8983 | 62.8372 | 60.8185
1773.6406 | 0.061035 | 0.43579 | -0.79895 | -0.22644 | 0.16449 | -0.27985 | -0.1709 | 60.9055 | -62.7319 | 0.1236 | -62.9517 | 60.7407 | 62.8647 | 62.8098 | 0.045776 | -0.070496 | 0.075836 | 0.298 | -0.17517 | -0.15808 | 0.068665 | 0.13275 | -63.1577 | 60.7132 | 60.6995 | 62.7502 | 62.9517 | 123.8846 | 62.8326 | 60.8231
1775.3125 | 0.045776 | 0.42938 | -0.80002 | -0.23178 | 0.16983 | -0.2681 | -0.17197 | 60.9009 | -62.7228 | 0.12817 | -62.9333 | 60.7498 | 62.883 | 62.8281 | 0.061035 | -0.079041 | 0.076904 | 0.27985 | -0.16342 | -0.15167 | 0.09613 | 0.13733 | -63.1439 | 60.7315 | 60.704 | 62.7502 | 62.9517 | 123.88 | 62.8326 | 60.8047
1776.9688 | 0.045776 | 0.42725 | -0.78507 | -0.2243 | 0.1709 | -0.2713 | -0.18158 | 60.8551 | -62.7686 | 0.07782 | -62.9837 | 60.7681 | 62.8967 | 62.8418 | 0.045776 | -0.071564 | 0.092926 | 0.28732 | -0.15808 | -0.15595 | 0.068665 | 0.12817 | -63.1485 | 60.7544 | 60.7224 | 62.7594 | 62.9745 | 123.9075 | 62.8235 | 60.8231
1778.6406 | 0.045776 | 0.42511 | -0.79468 | -0.20935 | 0.16449 | -0.26916 | -0.17838 | 60.9055 | -62.6999 | 0.13733 | -62.9196 | 60.7681 | 62.8967 | 62.8464 | 0.045776 | -0.074768 | 0.070496 | 0.27985 | -0.16556 | -0.14633 | 0.086975 | 0.15564 | -63.1256 | 60.7224 | 60.7269 | 62.7319 | 62.9425 | 123.8846 | 62.8464 | 60.8322
1780.3125 | 0.030518 | 0.45609 | -0.79254 | -0.1976 | 0.16129 | -0.26062 | -0.17624 | 60.9055 | -62.7319 | 0.022888 | -62.9471 | 60.7224 | 62.8784 | 62.8235 | 0.030518 | -0.081177 | 0.071564 | 0.29694 | -0.14099 | -0.16342 | 0.022888 | 0.041199 | -63.1119 | 60.6857 | 60.6445 | 62.7365 | 62.9471 | 123.8663 | 62.8922 | 60.8093
1781.9688 | 0.045776 | 0.42618 | -0.79468 | -0.18906 | 0.16556 | -0.25207 | -0.1709 | 60.878 | -62.8006 | -0.018311 | -62.9837 | 60.7681 | 62.8784 | 62.8189 | 0.030518 | -0.05661 | 0.072632 | 0.28839 | -0.13886 | -0.15488 | -0.068665 | -0.068665 | -63.2263 | 60.7315 | 60.7269 | 62.7411 | 62.9608 | 123.8068 | 62.8876 | 60.8368
1783.6406 | 0.061035 | 0.41977 | -0.77972 | -0.22644 | 0.17303 | -0.26062 | -0.15915 | 60.91 | -62.7136 | 0.086975 | -62.9242 | 60.7544 | 62.883 | 62.8006 | 0.061035 | -0.070496 | 0.0737 | 0.29053 | -0.15488 | -0.14526 | 0.054932 | 0.09613 | -63.1165 | 60.7132 | 60.7132 | 62.7365 | 62.9608 | 123.912 | 62.8326 | 60.8368
1785.3438 | 0.030518 | 0.42725 | -0.79681 | -0.22964 | 0.16876 | -0.28625 | -0.18799 | 60.9283 | -62.6358 | 0.16022 | -62.9105 | 60.6949 | 62.8464 | 62.8052 | 0.045776 | -0.086517 | 0.072632 | 0.27237 | -0.15701 | -0.15167 | 0.16479 | 0.24719 | -63.0157 | 60.6537 | 60.6628 | 62.7365 | 62.9425 | 123.9304 | 62.8281 | 60.7956
1787.0156 | 0.045776 | 0.44327 | -0.79361 | -0.20294 | 0.16769 | -0.24887 | -0.16449 | 60.9055 | -62.7411 | 0.036621 | -62.9562 | 60.7864 | 62.9059 | 62.8189 | 0.045776 | -0.060883 | 0.067291 | 0.28946 | -0.13565 | -0.15167 | -0.022888 | -0.022888 | -63.1714 | 60.7315 | 60.6766 | 62.7457 | 62.9517 | 123.8022 | 62.8922 | 60.8231
1788.6875 | 0.061035 | 0.42618 | -0.78827 | -0.20935 | 0.16556 | -0.25314 | -0.17303 | 60.878 | -62.7686 | 0.036621 | -62.9562 | 60.7452 | 62.8967 | 62.8235 | 0.061035 | -0.074768 | 0.084381 | 0.28305 | -0.15274 | -0.15274 | -0.041199 | -0.036621 | -63.1943 | 60.7178 | 60.7132 | 62.7411 | 62.9562 | 123.7839 | 62.8738 | 60.8231
1790.3438 | 0.045776 | 0.45075 | -0.78934 | -0.21469 | 0.16022 | -0.28732 | -0.16235 | 60.8734 | -62.6816 | 0.068665 | -62.9471 | 60.6491 | 62.883 | 62.8189 | 0.076294 | -0.092926 | 0.080109 | 0.28198 | -0.16342 | -0.1506 | 0.036621 | 0.07782 | -63.0981 | 60.6354 | 60.6308 | 62.7457 | 62.9654 | 123.793 | 62.9242 | 60.8002
1792 | 0.045776 | 0.44861 | -0.80429 | -0.21896 | 0.17624 | -0.28839 | -0.18906 | 60.9009 | -62.6724 | 0.12817 | -62.9059 | 60.6995 | 62.8876 | 62.8052 | 0.061035 | -0.087585 | 0.067291 | 0.27451 | -0.17624 | -0.1442 | 0.14191 | 0.21973 | -63.0295 | 60.6628 | 60.6308 | 62.7228 | 62.9425 | 123.912 | 62.8235 | 60.7864
1793.6562 | 0.061035 | 0.43472 | -0.78827 | -0.21683 | 0.16876 | -0.25528 | -0.17517 | 60.8643 | -62.8143 | -0.064087 | -62.9883 | 60.7819 | 62.883 | 62.8418 | 0.045776 | -0.064087 | 0.067291 | 0.28519 | -0.13886 | -0.15488 | -0.059509 | -0.10071 | -63.1805 | 60.7224 | 60.6903 | 62.764 | 62.9517 | 123.8159 | 62.9059 | 60.7819
1795.3125 | 0.061035 | 0.44113 | -0.79681 | -0.23071 | 0.16342 | -0.29694 | -0.18051 | 60.9192 | -62.6495 | 0.14191 | -62.9196 | 60.7132 | 62.8693 | 62.8006 | 0.045776 | -0.087585 | 0.072632 | 0.29053 | -0.16983 | -0.15595 | 0.14648 | 0.2243 | -63.0203 | 60.6583 | 60.6491 | 62.7274 | 62.9059 | 123.9166 | 62.8372 | 60.7773
1796.9688 | 0.061035 | 0.4187 | -0.79468 | -0.23819 | 0.18265 | -0.24353 | -0.17303 | 60.8826 | -62.7594 | 0.068665 | -62.9379 | 60.791 | 62.8876 | 62.8143 | 0.076294 | -0.072632 | 0.077972 | 0.29587 | -0.15595 | -0.16022 | 0.036621 | 0.082397 | -63.1348 | 60.7224 | 60.6949 | 62.7274 | 62.9379 | 123.9441 | 62.8235 | 60.7956
1798.6406 | 0.045776 | 0.42618 | -0.77866 | -0.22537 | 0.16342 | -0.25101 | -0.16129 | 60.8917 | -62.7228 | 0.054932 | -62.9242 | 60.7498 | 62.851 | 62.8052 | 0.045776 | -0.068359 | 0.076904 | 0.29694 | -0.1474 | -0.15167 | 0.009155 | 0.018311 | -63.1485 | 60.6995 | 60.672 | 62.7457 | 62.9562 | 123.8022 | 62.8555 | 60.7864
1800.2969 | 0.045776 | 0.43579 | -0.784 | -0.21362 | 0.16983 | -0.26062 | -0.15808 | 60.8231 | -62.7914 | -0.022888 | -62.9791 | 60.7407 | 62.883 | 62.8189 | 0.061035 | -0.065155 | 0.075836 | 0.29373 | -0.15274 | -0.1506 | -0.073242 | -0.07782 | -63.2034 | 60.704 | 60.6903 | 62.7274 | 62.9562 | 123.7839 | 62.8738 | 60.8047
1801.9531 | 0.045776 | 0.4155 | -0.78293 | -0.22644 | 0.15701 | -0.26489 | -0.16022 | 60.8826 | -62.6953 | 0.09613 | -62.915 | 60.7819 | 62.8738 | 62.8143 | 0.061035 | -0.068359 | 0.080109 | 0.29373 | -0.14847 | -0.14099 | 0.041199 | 0.064087 | -63.1165 | 60.6949 | 60.6674 | 62.7182 | 62.9333 | 123.8754 | 62.851 | 60.8047
1803.6406 | 0.045776 | 0.4422 | -0.79681 | -0.23071 | 0.16556 | -0.30121 | -0.16876 | 60.8917 | -62.6038 | 0.16479 | -62.9013 | 60.6995 | 62.8601 | 62.7823 | 0.045776 | -0.087585 | 0.0737 | 0.28412 | -0.17303 | -0.14526 | 0.15106 | 0.24719 | -63.0295 | 60.64 | 60.6308 | 62.7136 | 62.9425 | 123.9075 | 62.8326 | 60.791
1805.2969 | 0.045776 | 0.44006 | -0.79575 | -0.2243 | 0.17197 | -0.27664 | -0.18799 | 60.8871 | -62.6816 | 0.15106 | -62.8967 | 60.704 | 62.8601 | 62.7823 | 0.030518 | -0.077972 | 0.082245 | 0.29053 | -0.1709 | -0.15701 | 0.082397 | 0.16937 | -63.1073 | 60.6949 | 60.6812 | 62.7274 | 62.915 | 123.848 | 62.8098 | 60.7956
1806.9531 | 0.045776 | 0.42618 | -0.784 | -0.2211 | 0.16876 | -0.25314 | -0.16342 | 60.8871 | -62.7045 | 0.082397 | -62.9196 | 60.7544 | 62.8647 | 62.796 | 0.061035 | -0.065155 | 0.083313 | 0.29587 | -0.13886 | -0.16342 | 0.054932 | 0.059509 | -63.0936 | 60.7132 | 60.6903 | 62.709 | 62.9517 | 123.8663 | 62.8098 | 60.791
1808.6406 | 0.045776 | 0.42938 | -0.80749 | -0.22537 | 0.17517 | -0.28412 | -0.17838 | 60.8871 | -62.6633 | 0.15564 | -62.8922 | 60.7086 | 62.8555 | 62.8006 | 0.061035 | -0.081177 | 0.063019 | 0.28412 | -0.15595 | -0.14954 | 0.11902 | 0.19226 | -63.0798 | 60.6857 | 60.6674 | 62.7136 | 62.915 | 123.8434 | 62.8418 | 60.8047
1810.3125 | 0.061035 | 0.42725 | -0.79147 | -0.2179 | 0.14633 | -0.24246 | -0.16769 | 60.8734 | -62.7228 | 0.045776 | -62.9425 | 60.7498 | 62.8647 | 62.7731 | 0.061035 | -0.057678 | 0.070496 | 0.28305 | -0.13886 | -0.15167 | -0.022888 | -0.018311 | -63.1439 | 60.6857 | 60.7132 | 62.7228 | 62.9471 | 123.7747 | 62.8784 | 60.8276
1811.9688 | 0.045776 | 0.41443 | -0.78934 | -0.2243 | 0.15808 | -0.24994 | -0.16983 | 60.8597 | -62.7182 | 0.068665 | -62.9288 | 60.7727 | 62.883 | 62.7869 | 0.061035 | -0.068359 | 0.083313 | 0.29159 | -0.14954 | -0.15808 | 0.059509 | 0.086975 | -63.1073 | 60.6903 | 60.6995 | 62.7182 | 62.9379 | 123.8892 | 62.8006 | 60.7864
1813.6406 | 0.061035 | 0.41977 | -0.78613 | -0.22217 | 0.18265 | -0.25528 | -0.16983 | 60.8002 | -62.7914 | -0.036621 | -62.9654 | 60.759 | 62.8693 | 62.8098 | 0.061035 | -0.061951 | 0.077972 | 0.28198 | -0.15274 | -0.14206 | -0.068665 | -0.091553 | -63.1805 | 60.6995 | 60.6812 | 62.7502 | 62.9333 | 123.761 | 62.8647 | 60.7819
1815.3125 | 0.061035 | 0.45075 | -0.78186 | -0.20935 | 0.15701 | -0.25955 | -0.16876 | 60.8597 | -62.6862 | 0.064087 | -62.915 | 60.7498 | 62.851 | 62.8052 | 0.045776 | -0.059814 | 0.085449 | 0.28625 | -0.14099 | -0.14526 | 0.041199 | 0.068665 | -63.089 | 60.6903 | 60.6995 | 62.7136 | 62.9333 | 123.8709 | 62.8143 | 60.7727
1816.9688 | 0.061035 | 0.42511 | -0.78934 | -0.20401 | 0.16769 | -0.25742 | -0.16556 | 60.8047 | -62.7686 | -0.009155 | -62.9517 | 60.7498 | 62.883 | 62.8235 | 0.045776 | -0.061951 | 0.0737 | 0.28625 | -0.13779 | -0.1474 | -0.091553 | -0.068665 | -63.1577 | 60.6995 | 60.6903 | 62.7274 | 62.9562 | 123.7701 | 62.8418 | 60.8139
1818.6406 | 0.045776 | 0.47638 | -0.80002 | -0.21896 | 0.16342 | -0.30762 | -0.18372 | 60.7956 | -62.709 | 0.045776 | -62.9288 | 60.7086 | 62.8647 | 62.796 | 0.076294 | -0.093994 | 0.064087 | 0.28091 | -0.16556 | -0.13992 | 0.059509 | 0.14648 | -63.0615 | 60.6354 | 60.6491 | 62.7274 | 62.9425 | 123.848 | 62.8281 | 60.8002
1820.3125 | 0.061035 | 0.43472 | -0.7872 | -0.22324 | 0.16449 | -0.25207 | -0.16983 | 60.8139 | -62.8189 | -0.064087 | -62.9608 | 60.7544 | 62.8693 | 62.7869 | 0.015259 | -0.057678 | 0.068359 | 0.28625 | -0.15701 | -0.14313 | -0.086975 | -0.086975 | -63.1714 | 60.704 | 60.6812 | 62.7319 | 62.9379 | 123.7473 | 62.851 | 60.7864
1821.9688 | 0.045776 | 0.41977 | -0.79361 | -0.21255 | 0.15808 | -0.25742 | -0.16663 | 60.8002 | -62.7777 | -0.059509 | -62.9562 | 60.7315 | 62.8601 | 62.7914 | 0.061035 | -0.069427 | 0.060883 | 0.29373 | -0.14954 | -0.14206 | -0.082397 | -0.10071 | -63.1531 | 60.6857 | 60.6812 | 62.7274 | 62.9242 | 123.7976 | 62.8647 | 60.7681
1823.625 | 0.030518 | 0.45181 | -0.80002 | -0.23178 | 0.17197 | -0.30655 | -0.1741 | 60.8047 | -62.7228 | 0.041199 | -62.9242 | 60.6903 | 62.8647 | 62.8098 | 0.076294 | -0.089722 | 0.068359 | 0.28412 | -0.17197 | -0.13351 | 0.054932 | 0.11444 | -63.0524 | 60.6537 | 60.6674 | 62.6953 | 62.915 | 123.8342 | 62.851 | 60.7819
1825.2969 | 0.061035 | 0.43579 | -0.79254 | -0.21042 | 0.1709 | -0.25314 | -0.17197 | 60.8231 | -62.7869 | -0.036621 | -62.9562 | 60.7452 | 62.8601 | 62.8281 | 0.045776 | -0.057678 | 0.077972 | 0.29373 | -0.14633 | -0.16449 | -0.09613 | -0.10986 | -63.1943 | 60.704 | 60.6949 | 62.7365 | 62.9379 | 123.7427 | 62.851 | 60.8047
1826.9688 | 0.045776 | 0.42511 | -0.79361 | -0.20508 | 0.16022 | -0.25101 | -0.16556 | 60.8185 | -62.7869 | -0.036621 | -62.9654 | 60.759 | 62.8647 | 62.796 | 0.045776 | -0.061951 | 0.063019 | 0.28839 | -0.13779 | -0.14847 | -0.091553 | -0.10986 | -63.2034 | 60.6857 | 60.6903 | 62.7228 | 62.9425 | 123.7473 | 62.8601 | 60.8276
1828.625 | 0.045776 | 0.44647 | -0.78293 | -0.21683 | 0.16663 | -0.26489 | -0.16983 | 60.8093 | -62.764 | -0.050354 | -62.9608 | 60.7178 | 62.8555 | 62.8281 | 0.045776 | -0.075836 | 0.082245 | 0.28839 | -0.14847 | -0.13992 | -0.036621 | -0.073242 | -63.1439 | 60.6674 | 60.6674 | 62.7228 | 62.9242 | 123.793 | 62.8738 | 60.7864
1830.2969 | 0.061035 | 0.44006 | -0.80215 | -0.23285 | 0.17624 | -0.2681 | -0.17303 | 60.8185 | -62.7411 | 0.045776 | -62.9288 | 60.759 | 62.8693 | 62.8281 | 0.045776 | -0.075836 | 0.068359 | 0.28305 | -0.16983 | -0.1442 | 0.032043 | 0.086975 | -63.1256 | 60.7132 | 60.6995 | 62.7182 | 62.9013 | 123.8892 | 62.796 | 60.759
1831.9688 | 0.076294 | 0.41977 | -0.80856 | -0.23605 | 0.16769 | -0.27451 | -0.18478 | 60.8139 | -62.7319 | 0.068665 | -62.9196 | 60.7407 | 62.8418 | 62.7777 | 0.045776 | -0.079041 | 0.074768 | 0.28625 | -0.1709 | -0.1474 | 0.045776 | 0.09613 | -63.1256 | 60.6995 | 60.6949 | 62.7228 | 62.9196 | 123.8434 | 62.7914 | 60.8047
1833.625 | 0.061035 | 0.42938 | -0.78613 | -0.2446 | 0.16876 | -0.26489 | -0.18158 | 60.8139 | -62.7457 | 0.050354 | -62.9242 | 60.7544 | 62.8555 | 62.7914 | 0.091553 | -0.083313 | 0.088654 | 0.29159 | -0.16235 | -0.15381 | 0.045776 | 0.07782 | -63.1256 | 60.6857 | 60.6857 | 62.6907 | 62.9425 | 123.88 | 62.7869 | 60.7544
1835.3125 | 0.061035 | 0.42084 | -0.79041 | -0.23285 | 0.16022 | -0.2713 | -0.17838 | 60.8231 | -62.7182 | 0.073242 | -62.9379 | 60.7361 | 62.8464 | 62.8006 | 0.061035 | -0.082245 | 0.086517 | 0.29266 | -0.16876 | -0.15274 | 0.041199 | 0.086975 | -63.121 | 60.6949 | 60.6903 | 62.7182 | 62.915 | 123.848 | 62.7869 | 60.8047
1836.9688 | 0.061035 | 0.43366 | -0.79147 | -0.20294 | 0.16022 | -0.25742 | -0.1741 | 60.7864 | -62.7731 | -0.064087 | -62.9471 | 60.7452 | 62.8464 | 62.8098 | 0.045776 | -0.070496 | 0.071564 | 0.29587 | -0.14313 | -0.1474 | -0.064087 | -0.091553 | -63.1577 | 60.6766 | 60.6857 | 62.7274 | 62.9379 | 123.761 | 62.851 | 60.7773
1838.6406 | 0.045776 | 0.43793 | -0.79254 | -0.22324 | 0.18051 | -0.28625 | -0.17944 | 60.8414 | -62.6633 | 0.13733 | -62.8967 | 60.7086 | 62.8647 | 62.7731 | 0.061035 | -0.075836 | 0.069427 | 0.28412 | -0.1709 | -0.15488 | 0.07782 | 0.14191 | -63.0844 | 60.6537 | 60.704 | 62.6953 | 62.8967 | 123.7976 | 62.8052 | 60.7819
1840.3594 | 0.061035 | 0.43686 | -0.78293 | -0.21469 | 0.16769 | -0.26062 | -0.1741 | 60.8139 | -62.7411 | 0.050354 | -62.9196 | 60.759 | 62.851 | 62.796 | 0.045776 | -0.063019 | 0.064087 | 0.29053 | -0.1506 | -0.14954 | 0.036621 | 0.086975 | -63.121 | 60.7086 | 60.7224 | 62.6907 | 62.883 | 123.8663 | 62.7823 | 60.7498
1842.0156 | 0.030518 | 0.43259 | -0.79788 | -0.22858 | 0.17517 | -0.298 | -0.16449 | 60.8688 | -62.645 | 0.15106 | -62.8693 | 60.6857 | 62.851 | 62.7686 | 0.061035 | -0.089722 | 0.083313 | 0.27878 | -0.16663 | -0.15701 | 0.09613 | 0.18768 | -63.0615 | 60.6812 | 60.6628 | 62.6999 | 62.9059 | 123.8068 | 62.796 | 60.7636
1843.6719 | 0.061035 | 0.42511 | -0.79895 | -0.24033 | 0.16022 | -0.27771 | -0.17731 | 60.8643 | -62.6312 | 0.14648 | -62.8693 | 60.6995 | 62.8372 | 62.7502 | 0.061035 | -0.082245 | 0.082245 | 0.27878 | -0.17517 | -0.16129 | 0.091553 | 0.17853 | -63.0707 | 60.6445 | 60.6674 | 62.6907 | 62.8922 | 123.8068 | 62.7869 | 60.7819
1845.3438 | 0.061035 | 0.45502 | -0.7872 | -0.21042 | 0.15274 | -0.25635 | -0.16663 | 60.8459 | -62.6907 | 0.050354 | -62.8876 | 60.7773 | 62.8464 | 62.8006 | 0.061035 | -0.066223 | 0.0737 | 0.28519 | -0.14954 | -0.1442 | 0.054932 | 0.086975 | -63.0844 | 60.6812 | 60.6628 | 62.7045 | 62.9196 | 123.8525 | 62.7869 | 60.759
1847 | 0.045776 | 0.42297 | -0.79895 | -0.21576 | 0.15274 | -0.24674 | -0.17731 | 60.8505 | -62.677 | 0.059509 | -62.915 | 60.7315 | 62.8281 | 62.8006 | 0.045776 | -0.070496 | 0.0737 | 0.29373 | -0.13779 | -0.15274 | 0.009155 | 0.018311 | -63.0981 | 60.6628 | 60.672 | 62.7045 | 62.9196 | 123.7518 | 62.8098 | 60.759
1848.6562 | 0.045776 | 0.4454 | -0.80215 | -0.20508 | 0.16876 | -0.27344 | -0.1741 | 60.8597 | -62.6312 | 0.064087 | -62.8738 | 60.6491 | 62.8464 | 62.796 | 0.045776 | -0.086517 | 0.070496 | 0.27451 | -0.15274 | -0.14313 | 0.050354 | 0.059509 | -63.0386 | 60.5988 | 60.6079 | 62.6907 | 62.8876 | 123.7335 | 62.8464 | 60.759
1850.3125 | 0.045776 | 0.43579 | -0.80215 | -0.23605 | 0.16342 | -0.28732 | -0.18478 | 60.8734 | -62.5809 | 0.15564 | -62.8555 | 60.672 | 62.796 | 62.7457 | 0.061035 | -0.09079 | 0.069427 | 0.2713 | -0.17517 | -0.14954 | 0.16022 | 0.2655 | -62.97 | 60.6216 | 60.6262 | 62.6678 | 62.8784 | 123.848 | 62.8006 | 60.7178
1851.9688 | 0.045776 | 0.44434 | -0.79468 | -0.24246 | 0.15381 | -0.27878 | -0.18265 | 60.8643 | -62.6404 | 0.10986 | -62.8693 | 60.6674 | 62.8372 | 62.7686 | 0.061035 | -0.085449 | 0.066223 | 0.29159 | -0.16876 | -0.15701 | 0.15564 | 0.21057 | -63.0066 | 60.5988 | 60.6262 | 62.6862 | 62.8967 | 123.8297 | 62.7777 | 60.7361
1853.6719 | 0.061035 | 0.43366 | -0.78827 | -0.23178 | 0.1709 | -0.27771 | -0.18478 | 60.8734 | -62.5992 | 0.16479 | -62.8418 | 60.6674 | 62.851 | 62.764 | 0.045776 | -0.075836 | 0.075836 | 0.29053 | -0.16663 | -0.15595 | 0.14648 | 0.23346 | -63.0157 | 60.6171 | 60.6079 | 62.6999 | 62.883 | 123.793 | 62.8098 | 60.7636
1855.3438 | 0.061035 | 0.42831 | -0.784 | -0.22644 | 0.16129 | -0.25635 | -0.17944 | 60.8276 | -62.6953 | 0.082397 | -62.9013 | 60.7269 | 62.8418 | 62.7594 | 0.015259 | -0.079041 | 0.072632 | 0.28946 | -0.16022 | -0.15915 | 0.064087 | 0.10986 | -63.1027 | 60.704 | 60.6537 | 62.6907 | 62.9013 | 123.7839 | 62.8052 | 60.7956
1857 | 0.045776 | 0.40802 | -0.79575 | -0.23392 | 0.16129 | -0.24887 | -0.16235 | 60.8459 | -62.6862 | 0.064087 | -62.8784 | 60.7498 | 62.8281 | 62.7777 | 0.045776 | -0.060883 | 0.084381 | 0.28732 | -0.15808 | -0.16342 | 0.041199 | 0.064087 | -63.0981 | 60.6903 | 60.6583 | 62.6816 | 62.9105 | 123.8297 | 62.7548 | 60.759
1858.6719 | 0.045776 | 0.44006 | -0.79895 | -0.21896 | 0.16449 | -0.27344 | -0.17624 | 60.8139 | -62.677 | 0.086975 | -62.915 | 60.7315 | 62.8418 | 62.7457 | 0.061035 | -0.0737 | 0.080109 | 0.28412 | -0.16663 | -0.14206 | 0.07782 | 0.11444 | -63.1027 | 60.6857 | 60.672 | 62.6999 | 62.9013 | 123.793 | 62.7731 | 60.7636
1860.3438 | 0.061035 | 0.42725 | -0.79681 | -0.20935 | 0.15915 | -0.24887 | -0.1709 | 60.7819 | -62.7594 | -0.054932 | -62.9242 | 60.7224 | 62.8555 | 62.8052 | 0.061035 | -0.061951 | 0.063019 | 0.28732 | -0.1474 | -0.14954 | -0.045776 | -0.082397 | -63.1393 | 60.6628 | 60.6491 | 62.6999 | 62.9059 | 123.7289 | 62.8464 | 60.7452
1862 | 0.045776 | 0.42725 | -0.78827 | -0.21362 | 0.16663 | -0.25207 | -0.16235 | 60.8093 | -62.6907 | 0.041199 | -62.9105 | 60.7178 | 62.8418 | 62.7594 | 0.045776 | -0.063019 | 0.0737 | 0.28946 | -0.13458 | -0.15167 | -0.041199 | -0.045776 | -63.1348 | 60.6537 | 60.6537 | 62.7228 | 62.915 | 123.6923 | 62.8235 | 60.7681
1863.6719 | 0.061035 | 0.44434 | -0.79895 | -0.20294 | 0.16342 | -0.27237 | -0.17303 | 60.7864 | -62.7182 | -0.059509 | -62.9242 | 60.7132 | 62.8464 | 62.7914 | 0.061035 | -0.066223 | 0.0737 | 0.28305 | -0.1506 | -0.14313 | -0.041199 | -0.07782 | -63.1027 | 60.64 | 60.6308 | 62.6999 | 62.9105 | 123.7289 | 62.8326 | 60.7498
1865.3281 | 0.030518 | 0.44861 | -0.80429 | -0.2243 | 0.15808 | -0.30121 | -0.16983 | 60.8368 | -62.6175 | 0.12817 | -62.8601 | 60.6812 | 62.8235 | 62.7594 | 0.061035 | -0.089722 | 0.060883 | 0.2713 | -0.16983 | -0.1506 | 0.14648 | 0.21973 | -62.9745 | 60.6125 | 60.6308 | 62.6724 | 62.8693 | 123.8159 | 62.7731 | 60.704
1866.9844 | 0.045776 | 0.44327 | -0.79575 | -0.19653 | 0.16235 | -0.26276 | -0.1741 | 60.8002 | -62.7594 | -0.050354 | -62.9379 | 60.7132 | 62.851 | 62.7777 | 0.061035 | -0.070496 | 0.070496 | 0.28625 | -0.1474 | -0.15274 | -0.068665 | -0.09613 | -63.1256 | 60.6766 | 60.6537 | 62.7045 | 62.9013 | 123.7335 | 62.8281 | 60.7498
1868.6719 | 0.061035 | 0.43152 | -0.79681 | -0.23712 | 0.17197 | -0.27664 | -0.17303 | 60.8459 | -62.5946 | 0.16479 | -62.8372 | 60.6491 | 62.8052 | 62.7228 | 0.076294 | -0.086517 | 0.068359 | 0.27557 | -0.16663 | -0.15167 | 0.14648 | 0.25635 | -63.0066 | 60.6033 | 60.5988 | 62.6678 | 62.883 | 123.7656 | 62.7731 | 60.7727
1870.3438 | 0.030518 | 0.47318 | -0.80643 | -0.20828 | 0.15915 | -0.28519 | -0.17624 | 60.8093 | -62.677 | 0.045776 | -62.915 | 60.6491 | 62.8235 | 62.7502 | 0.061035 | -0.086517 | 0.061951 | 0.28198 | -0.16769 | -0.1474 | 0.041199 | 0.07782 | -63.0661 | 60.6125 | 60.6125 | 62.6678 | 62.883 | 123.7061 | 62.8372 | 60.7819
1871.9844 | 0.045776 | 0.45395 | -0.80002 | -0.20081 | 0.1741 | -0.25207 | -0.16876 | 60.8871 | -62.6312 | 0.059509 | -62.8601 | 60.6354 | 62.8189 | 62.7548 | 0.061035 | -0.0737 | 0.050201 | 0.28198 | -0.1506 | -0.15274 | 0.045776 | 0.073242 | -63.0203 | 60.5942 | 60.6079 | 62.7045 | 62.8647 | 123.6877 | 62.8372 | 60.7452
1873.6406 | 0.030518 | 0.42938 | -0.79788 | -0.22537 | 0.16769 | -0.26916 | -0.18051 | 60.8688 | -62.6266 | 0.14648 | -62.8418 | 60.6674 | 62.8098 | 62.7457 | 0.061035 | -0.0737 | 0.079041 | 0.28732 | -0.16663 | -0.15915 | 0.11444 | 0.17853 | -63.0524 | 60.6674 | 60.6628 | 62.6907 | 62.8876 | 123.7701 | 62.7823 | 60.759
1875.2969 | 0.030518 | 0.42084 | -0.78827 | -0.23392 | 0.16663 | -0.25207 | -0.18265 | 60.8231 | -62.7136 | 0.059509 | -62.915 | 60.7452 | 62.8098 | 62.7686 | 0.061035 | -0.067291 | 0.083313 | 0.298 | -0.16022 | -0.15915 | 0.032043 | 0.064087 | -63.1119 | 60.6766 | 60.6537 | 62.6907 | 62.8784 | 123.8113 | 62.7686 | 60.7544
1876.9531 | 0.061035 | 0.4422 | -0.79147 | -0.21683 | 0.16983 | -0.27771 | -0.16663 | 60.8368 | -62.6083 | 0.16022 | -62.8647 | 60.6583 | 62.8235 | 62.7457 | 0.045776 | -0.082245 | 0.080109 | 0.298 | -0.16342 | -0.15808 | 0.10986 | 0.1831 | -63.0478 | 60.64 | 60.64 | 62.6862 | 62.883 | 123.7473 | 62.7502 | 60.759
1878.6406 | 0.061035 | 0.42938 | -0.78186 | -0.20187 | 0.16342 | -0.24246 | -0.17197 | 60.8597 | -62.6358 | 0.07782 | -62.8601 | 60.7132 | 62.8052 | 62.7502 | 0.076294 | -0.069427 | 0.079041 | 0.29373 | -0.1442 | -0.14633 | 0.032043 | 0.032043 | -63.0615 | 60.6308 | 60.6445 | 62.677 | 62.883 | 123.761 | 62.7869 | 60.7269
1880.3125 | 0.045776 | 0.43472 | -0.79254 | -0.21896 | 0.16876 | -0.27664 | -0.1741 | 60.8459 | -62.6038 | 0.073242 | -62.8601 | 60.6537 | 62.8143 | 62.7365 | 0.045776 | -0.089722 | 0.069427 | 0.29373 | -0.1474 | -0.14526 | 0.073242 | 0.068665 | -63.0295 | 60.585 | 60.5988 | 62.6862 | 62.8876 | 123.6694 | 62.8235 | 60.7681
1882 | 0.045776 | 0.4422 | -0.79468 | -0.2179 | 0.16983 | -0.2948 | -0.17624 | 60.8871 | -62.5488 | 0.17395 | -62.8326 | 60.6674 | 62.8189 | 62.764 | 0.030518 | -0.080109 | 0.072632 | 0.27344 | -0.16342 | -0.14099 | 0.16937 | 0.24719 | -62.97 | 60.6125 | 60.6079 | 62.6495 | 62.8922 | 123.7885 | 62.7502 | 60.7361
1883.6719 | 0.076294 | 0.43793 | -0.80002 | -0.23285 | 0.17303 | -0.26703 | -0.17624 | 60.878 | -62.5671 | 0.17853 | -62.8235 | 60.6674 | 62.7914 | 62.7411 | 0.030518 | -0.077972 | 0.087585 | 0.28625 | -0.16129 | -0.16663 | 0.16937 | 0.22888 | -63.002 | 60.6079 | 60.6125 | 62.6633 | 62.8738 | 123.7564 | 62.7686 | 60.7361
1885.375 | 0.045776 | 0.43366 | -0.79575 | -0.20615 | 0.1709 | -0.24033 | -0.16449 | 60.8551 | -62.6541 | 0.050354 | -62.8922 | 60.7224 | 62.8235 | 62.7457 | 0.076294 | -0.060883 | 0.067291 | 0.29159 | -0.13351 | -0.15595 | -0.004578 | -0.022888 | -63.0844 | 60.64 | 60.6216 | 62.6999 | 62.9059 | 123.6832 | 62.7869 | 60.759
1887.0312 | 0.076294 | 0.42938 | -0.79361 | -0.20828 | 0.16663 | -0.25207 | -0.16449 | 60.7498 | -62.7548 | -0.036621 | -62.9517 | 60.6995 | 62.8418 | 62.7731 | 0.045776 | -0.064087 | 0.069427 | 0.28839 | -0.14954 | -0.1506 | -0.059509 | -0.10529 | -63.1302 | 60.6674 | 60.6445 | 62.6862 | 62.9059 | 123.6786 | 62.8189 | 60.7727
1888.6875 | 0.061035 | 0.42618 | -0.7872 | -0.23392 | 0.16983 | -0.25314 | -0.1709 | 60.791 | -62.6541 | 0.064087 | -62.8555 | 60.7269 | 62.8235 | 62.7457 | 0.061035 | -0.071564 | 0.060883 | 0.28519 | -0.14633 | -0.1506 | 0.041199 | 0.086975 | -63.0661 | 60.6583 | 60.6308 | 62.6862 | 62.8555 | 123.8113 | 62.7457 | 60.7086
1890.3594 | 0.045776 | 0.42938 | -0.78186 | -0.23392 | 0.15915 | -0.25421 | -0.17197 | 60.8231 | -62.6083 | 0.07782 | -62.8647 | 60.6766 | 62.8189 | 62.7594 | 0.061035 | -0.064087 | 0.076904 | 0.28412 | -0.15274 | -0.15595 | 0.041199 | 0.086975 | -63.0341 | 60.64 | 60.6171 | 62.709 | 62.8693 | 123.761 | 62.7594 | 60.7269
1892.0156 | 0.015259 | 0.42297 | -0.79361 | -0.24567 | 0.17303 | -0.27771 | -0.16556 | 60.7681 | -62.6862 | 0.068665 | -62.8922 | 60.7361 | 62.8281 | 62.7502 | 0.045776 | -0.080109 | 0.084381 | 0.29159 | -0.16235 | -0.13672 | 0.045776 | 0.07782 | -63.0844 | 60.6537 | 60.6583 | 62.7045 | 62.8784 | 123.7839 | 62.7411 | 60.7269
1893.6719 | 0.061035 | 0.42618 | -0.79575 | -0.23392 | 0.15488 | -0.27771 | -0.17624 | 60.7681 | -62.6724 | 0.082397 | -62.8967 | 60.7086 | 62.8235 | 62.7411 | 0.045776 | -0.083313 | 0.0737 | 0.28839 | -0.1741 | -0.14526 | 0.050354 | 0.1236 | -63.0753 | 60.6354 | 60.64 | 62.6816 | 62.8922 | 123.7381 | 62.7594 | 60.7407
1895.3438 | 0.045776 | 0.45181 | -0.80643 | -0.22644 | 0.16022 | -0.28732 | -0.18799 | 60.7544 | -62.6495 | 0.022888 | -62.8693 | 60.6537 | 62.8281 | 62.7319 | 0.076294 | -0.098267 | 0.063019 | 0.28519 | -0.16342 | -0.14526 | 0.041199 | 0.10529 | -63.0524 | 60.5988 | 60.5804 | 62.6724 | 62.883 | 123.6786 | 62.8006 | 60.7132
1897 | 0.045776 | 0.44113 | -0.79681 | -0.21576 | 0.16556 | -0.28091 | -0.17838 | 60.8002 | -62.6266 | 0.059509 | -62.8922 | 60.6262 | 62.7823 | 62.7319 | 0.061035 | -0.089722 | 0.063019 | 0.27237 | -0.16022 | -0.1506 | 0.059509 | 0.059509 | -63.0203 | 60.5804 | 60.5896 | 62.6633 | 62.8601 | 123.6465 | 62.796 | 60.7498
1898.6875 | 0.061035 | 0.42831 | -0.78827 | -0.2179 | 0.16663 | -0.25848 | -0.17303 | 60.8231 | -62.6633 | 0.064087 | -62.8555 | 60.7224 | 62.796 | 62.7548 | 0.076294 | -0.067291 | 0.077972 | 0.27878 | -0.13992 | -0.16129 | 0.045776 | 0.09613 | -63.0524 | 60.6583 | 60.6216 | 62.6633 | 62.8555 | 123.7793 | 62.7686 | 60.7407
1900.3594 | 0.061035 | 0.44327 | -0.79361 | -0.20828 | 0.15915 | -0.25742 | -0.16983 | 60.7819 | -62.7136 | -0.045776 | -62.9059 | 60.6949 | 62.8052 | 62.7548 | 0.045776 | -0.081177 | 0.071564 | 0.29159 | -0.1474 | -0.15274 | -0.022888 | -0.064087 | -63.0844 | 60.6171 | 60.5988 | 62.677 | 62.883 | 123.6877 | 62.8098 | 60.7224
1902.0469 | 0.045776 | 0.44006 | -0.79788 | -0.20828 | 0.15488 | -0.26169 | -0.16342 | 60.7636 | -62.7274 | -0.050354 | -62.9013 | 60.7132 | 62.8281 | 62.7777 | 0.030518 | -0.074768 | 0.072632 | 0.29053 | -0.14847 | -0.14313 | -0.059509 | -0.082397 | -63.1073 | 60.64 | 60.6262 | 62.6907 | 62.8922 | 123.6969 | 62.8006 | 60.7224
1903.7031 | 0.061035 | 0.46356 | -0.80749 | -0.20721 | 0.16983 | -0.29159 | -0.1741 | 60.8093 | -62.59 | 0.059509 | -62.8647 | 60.6079 | 62.7823 | 62.7502 | 0.061035 | -0.085449 | 0.063019 | 0.27344 | -0.15915 | -0.1442 | 0.054932 | 0.064087 | -63.0066 | 60.5621 | 60.5667 | 62.6862 | 62.883 | 123.6053 | 62.8326 | 60.6949
1905.3594 | 0.061035 | 0.4422 | -0.79681 | -0.23178 | 0.17303 | -0.28091 | -0.18478 | 60.8597 | -62.5534 | 0.16479 | -62.8143 | 60.6216 | 62.764 | 62.6816 | 0.061035 | -0.075836 | 0.071564 | 0.27557 | -0.16663 | -0.15915 | 0.16022 | 0.25635 | -62.9379 | 60.5896 | 60.5942 | 62.6358 | 62.8647 | 123.7701 | 62.7457 | 60.7132
1907.0312 | 0.061035 | 0.43152 | -0.79361 | -0.21149 | 0.1709 | -0.25101 | -0.17624 | 60.7727 | -62.7457 | -0.064087 | -62.9105 | 60.7178 | 62.8052 | 62.7319 | 0.061035 | -0.061951 | 0.0737 | 0.27878 | -0.14206 | -0.16022 | -0.064087 | -0.10529 | -63.121 | 60.6445 | 60.5942 | 62.6633 | 62.9105 | 123.6694 | 62.8281 | 60.7452
1908.6875 | 0.061035 | 0.439 | -0.78827 | -0.19974 | 0.16449 | -0.25207 | -0.1709 | 60.8002 | -62.6678 | 0.013733 | -62.8738 | 60.704 | 62.8006 | 62.7548 | 0.061035 | -0.068359 | 0.079041 | 0.28625 | -0.1474 | -0.15381 | -0.041199 | -0.059509 | -63.1119 | 60.6445 | 60.6216 | 62.6724 | 62.8967 | 123.6328 | 62.8143 | 60.7452
1910.3438 | 0.045776 | 0.43152 | -0.78827 | -0.20401 | 0.16663 | -0.26062 | -0.1741 | 60.7498 | -62.709 | -0.064087 | -62.9105 | 60.6949 | 62.8235 | 62.7594 | 0.061035 | -0.072632 | 0.077972 | 0.28305 | -0.15274 | -0.14099 | -0.064087 | -0.086975 | -63.0981 | 60.6537 | 60.6125 | 62.677 | 62.9059 | 123.6923 | 62.8235 | 60.7315
1912.0156 | 0.045776 | 0.44113 | -0.79895 | -0.23712 | 0.15595 | -0.29159 | -0.1709 | 60.7773 | -62.6312 | 0.073242 | -62.8372 | 60.6354 | 62.7869 | 62.7365 | 0.061035 | -0.083313 | 0.068359 | 0.27664 | -0.1741 | -0.14954 | 0.10071 | 0.15564 | -62.9974 | 60.553 | 60.5988 | 62.6358 | 62.8464 | 123.7335 | 62.764 | 60.7132
1913.6875 | 0.061035 | 0.44754 | -0.80109 | -0.23178 | 0.17197 | -0.29266 | -0.18372 | 60.8459 | -62.558 | 0.17395 | -62.8006 | 60.6583 | 62.7823 | 62.709 | 0.061035 | -0.087585 | 0.068359 | 0.27771 | -0.16983 | -0.15488 | 0.16022 | 0.25177 | -62.9425 | 60.5713 | 60.5804 | 62.6312 | 62.8555 | 123.7244 | 62.7686 | 60.6949
1915.3594 | 0.061035 | 0.45822 | -0.79041 | -0.20081 | 0.15915 | -0.27344 | -0.16449 | 60.8368 | -62.5809 | 0.054932 | -62.8281 | 60.6125 | 62.7731 | 62.7045 | 0.061035 | -0.080109 | 0.068359 | 0.27557 | -0.1474 | -0.15595 | 0.059509 | 0.073242 | -62.9929 | 60.5667 | 60.5392 | 62.6404 | 62.8647 | 123.6099 | 62.8052 | 60.7269
1917.0156 | 0.061035 | 0.44113 | -0.80322 | -0.21469 | 0.15595 | -0.27985 | -0.18478 | 60.8002 | -62.6266 | 0.082397 | -62.851 | 60.6537 | 62.7914 | 62.7228 | 0.061035 | -0.083313 | 0.079041 | 0.28091 | -0.16129 | -0.16342 | 0.11902 | 0.16479 | -62.9883 | 60.585 | 60.5484 | 62.645 | 62.8647 | 123.7381 | 62.7411 | 60.7086
1918.6875 | 0.045776 | 0.43686 | -0.79041 | -0.23285 | 0.16983 | -0.27023 | -0.18051 | 60.8185 | -62.6221 | 0.10071 | -62.8418 | 60.6628 | 62.7914 | 62.7319 | 0.061035 | -0.081177 | 0.071564 | 0.29159 | -0.16876 | -0.16129 | 0.12817 | 0.18768 | -62.9745 | 60.5988 | 60.6033 | 62.6541 | 62.8738 | 123.761 | 62.7274 | 60.6995
1920.3438 | 0.030518 | 0.42831 | -0.79041 | -0.23071 | 0.15808 | -0.25848 | -0.17624 | 60.7956 | -62.6678 | 0.082397 | -62.883 | 60.6812 | 62.796 | 62.7274 | 0.061035 | -0.079041 | 0.074768 | 0.29053 | -0.16022 | -0.15595 | 0.073242 | 0.10529 | -63.0615 | 60.6445 | 60.6583 | 62.645 | 62.8555 | 123.7244 | 62.7411 | 60.7407
1922 | 0.045776 | 0.43259 | -0.7872 | -0.2211 | 0.15701 | -0.26382 | -0.18478 | 60.8185 | -62.6129 | 0.086975 | -62.8281 | 60.6354 | 62.8006 | 62.7365 | 0.061035 | -0.080109 | 0.072632 | 0.29373 | -0.15915 | -0.16342 | 0.13733 | 0.17853 | -62.9654 | 60.585 | 60.5942 | 62.6221 | 62.8555 | 123.7427 | 62.7411 | 60.704
1923.6875 | 0.061035 | 0.44754 | -0.79681 | -0.21469 | 0.15915 | -0.27878 | -0.19012 | 60.791 | -62.645 | 0.059509 | -62.8647 | 60.64 | 62.8098 | 62.7228 | 0.045776 | -0.080109 | 0.074768 | 0.28625 | -0.17197 | -0.16129 | 0.10529 | 0.12817 | -63.0066 | 60.5759 | 60.5942 | 62.6587 | 62.8738 | 123.7152 | 62.7502 | 60.7315
1925.3438 | 0.061035 | 0.42084 | -0.78079 | -0.22644 | 0.15701 | -0.25314 | -0.17517 | 60.7819 | -62.6678 | 0.064087 | -62.8738 | 60.7224 | 62.7823 | 62.7319 | 0.061035 | -0.067291 | 0.083313 | 0.29266 | -0.16022 | -0.15915 | 0.086975 | 0.10071 | -63.0661 | 60.6628 | 60.6354 | 62.6541 | 62.8784 | 123.7335 | 62.7274 | 60.7224
1927 | 0.030518 | 0.41977 | -0.79147 | -0.21469 | 0.15274 | -0.24674 | -0.17303 | 60.8002 | -62.6358 | 0.059509 | -62.8281 | 60.7086 | 62.796 | 62.7228 | 0.030518 | -0.065155 | 0.086517 | 0.28839 | -0.14099 | -0.16235 | 0.054932 | 0.082397 | -63.0341 | 60.6445 | 60.6033 | 62.6541 | 62.8784 | 123.7381 | 62.7274 | 60.7132
1928.6719 | 0.015259 | 0.43793 | -0.79788 | -0.21255 | 0.15701 | -0.28412 | -0.16983 | 60.8505 | -62.5214 | 0.17853 | -62.7914 | 60.6171 | 62.7502 | 62.7182 | 0.061035 | -0.082245 | 0.082245 | 0.28946 | -0.15274 | -0.14526 | 0.17395 | 0.25177 | -62.9288 | 60.5576 | 60.5759 | 62.6404 | 62.8326 | 123.7473 | 62.7365 | 60.704
1930.3281 | 0.061035 | 0.42618 | -0.79361 | -0.23605 | 0.15488 | -0.26596 | -0.17731 | 60.7819 | -62.6541 | 0.091553 | -62.8784 | 60.6857 | 62.796 | 62.7548 | 0.045776 | -0.058746 | 0.0737 | 0.28091 | -0.15701 | -0.14847 | 0.086975 | 0.1236 | -63.0524 | 60.6354 | 60.6354 | 62.677 | 62.8326 | 123.7061 | 62.7319 | 60.7269
1931.9844 | 0.061035 | 0.41763 | -0.79575 | -0.2211 | 0.15915 | -0.25635 | -0.1741 | 60.7681 | -62.6587 | 0.064087 | -62.8784 | 60.704 | 62.8006 | 62.7274 | 0.076294 | -0.058746 | 0.079041 | 0.28732 | -0.15915 | -0.15595 | 0.07782 | 0.09613 | -63.0615 | 60.6766 | 60.6537 | 62.6724 | 62.8555 | 123.7289 | 62.7228 | 60.7178
1933.6406 | 0.061035 | 0.42938 | -0.78934 | -0.22324 | 0.15167 | -0.27557 | -0.17944 | 60.8231 | -62.5626 | 0.14648 | -62.8098 | 60.6583 | 62.7686 | 62.6953 | 0.076294 | -0.09079 | 0.071564 | 0.28412 | -0.15595 | -0.14633 | 0.11444 | 0.19684 | -63.002 | 60.6125 | 60.6079 | 62.6495 | 62.8464 | 123.6786 | 62.7182 | 60.7269
1935.3281 | 0.061035 | 0.44006 | -0.79575 | -0.20187 | 0.15701 | -0.24887 | -0.16983 | 60.7773 | -62.6724 | -0.041199 | -62.8876 | 60.6812 | 62.8052 | 62.7411 | 0.061035 | -0.068359 | 0.053406 | 0.28412 | -0.1442 | -0.1474 | -0.013733 | -0.041199 | -63.0524 | 60.5942 | 60.5713 | 62.6541 | 62.883 | 123.6649 | 62.8006 | 60.7224
1937 | 0.061035 | 0.44113 | -0.78934 | -0.20721 | 0.16342 | -0.26276 | -0.15808 | 60.7498 | -62.677 | -0.054932 | -62.883 | 60.6812 | 62.7869 | 62.7274 | 0.030518 | -0.080109 | 0.075836 | 0.28732 | -0.14633 | -0.13992 | -0.041199 | -0.064087 | -63.0615 | 60.5942 | 60.6079 | 62.6541 | 62.8647 | 123.6511 | 62.7731 | 60.704
1938.6719 | 0.061035 | 0.4422 | -0.80109 | -0.23178 | 0.16235 | -0.29373 | -0.18585 | 60.7498 | -62.6129 | 0.032043 | -62.8555 | 60.6216 | 62.7914 | 62.7228 | 0.061035 | -0.084381 | 0.058746 | 0.28198 | -0.16663 | -0.14954 | 0.041199 | 0.091553 | -63.002 | 60.5621 | 60.585 | 62.6587 | 62.8647 | 123.6191 | 62.7777 | 60.6903
1940.3281 | 0.061035 | 0.44754 | -0.78827 | -0.22003 | 0.15167 | -0.28732 | -0.18799 | 60.7681 | -62.6266 | 0.068665 | -62.8326 | 60.6354 | 62.7914 | 62.7182 | 0.061035 | -0.080109 | 0.054474 | 0.28412 | -0.16449 | -0.14206 | 0.07782 | 0.1236 | -62.9929 | 60.5576 | 60.5713 | 62.6404 | 62.8693 | 123.6832 | 62.7548 | 60.6903
1941.9844 | 0.045776 | 0.44754 | -0.79468 | -0.2179 | 0.13779 | -0.26489 | -0.17944 | 60.8505 | -62.59 | 0.059509 | -62.8418 | 60.6125 | 62.7731 | 62.7228 | 0.030518 | -0.083313 | 0.061951 | 0.29159 | -0.16235 | -0.14847 | 0.059509 | 0.082397 | -62.9883 | 60.5576 | 60.5621 | 62.6404 | 62.8647 | 123.5596 | 62.7686 | 60.7132
1943.6562 | 0.061035 | 0.43579 | -0.80215 | -0.22644 | 0.15381 | -0.27023 | -0.16769 | 60.8505 | -62.5442 | 0.17395 | -62.7914 | 60.6216 | 62.7594 | 62.6862 | 0.045776 | -0.071564 | 0.072632 | 0.28732 | -0.15381 | -0.16342 | 0.16479 | 0.24261 | -62.9517 | 60.585 | 60.5621 | 62.6083 | 62.8464 | 123.6694 | 62.7274 | 60.7361
1945.3125 | 0.061035 | 0.42618 | -0.79254 | -0.23071 | 0.17197 | -0.25421 | -0.17731 | 60.759 | -62.645 | 0.064087 | -62.8555 | 60.6812 | 62.7869 | 62.6953 | 0.045776 | -0.069427 | 0.072632 | 0.29053 | -0.16235 | -0.16449 | 0.064087 | 0.10529 | -63.0432 | 60.6628 | 60.6171 | 62.6541 | 62.8372 | 123.6877 | 62.7182 | 60.7132
1946.9688 | 0.061035 | 0.42618 | -0.7872 | -0.22751 | 0.16449 | -0.25314 | -0.16876 | 60.791 | -62.6358 | 0.059509 | -62.8418 | 60.6949 | 62.7502 | 62.7228 | 0.061035 | -0.060883 | 0.075836 | 0.29053 | -0.1474 | -0.16449 | 0.050354 | 0.086975 | -63.0112 | 60.6308 | 60.6033 | 62.6587 | 62.8601 | 123.7473 | 62.7045 | 60.6903
1948.6406 | 0.030518 | 0.4422 | -0.80322 | -0.21255 | 0.17303 | -0.28198 | -0.17731 | 60.7498 | -62.6221 | 0.027466 | -62.8464 | 60.6079 | 62.796 | 62.7457 | 0.061035 | -0.082245 | 0.0737 | 0.28732 | -0.16556 | -0.14847 | 0.064087 | 0.11444 | -63.0066 | 60.553 | 60.5713 | 62.6495 | 62.8784 | 123.642 | 62.7777 | 60.7086
1950.3281 | 0.045776 | 0.44113 | -0.80749 | -0.23071 | 0.16556 | -0.27771 | -0.18158 | 60.8414 | -62.5259 | 0.14648 | -62.8006 | 60.6171 | 62.7411 | 62.7045 | 0.015259 | -0.076904 | 0.066223 | 0.28412 | -0.17197 | -0.15381 | 0.17853 | 0.24719 | -62.8922 | 60.5667 | 60.5621 | 62.6404 | 62.8143 | 123.7015 | 62.7319 | 60.6903
1951.9844 | 0.076294 | 0.43152 | -0.80536 | -0.22003 | 0.16235 | -0.27344 | -0.17197 | 60.8551 | -62.5214 | 0.15106 | -62.8006 | 60.6171 | 62.7731 | 62.677 | 0.030518 | -0.075836 | 0.074768 | 0.27878 | -0.16449 | -0.15808 | 0.1831 | 0.26093 | -62.9196 | 60.553 | 60.553 | 62.6221 | 62.8052 | 123.7015 | 62.7457 | 60.6995
1953.6562 | 0.061035 | 0.44861 | -0.79147 | -0.22858 | 0.16342 | -0.26703 | -0.17517 | 60.7636 | -62.6266 | 0.036621 | -62.851 | 60.6216 | 62.7914 | 62.7365 | 0.061035 | -0.085449 | 0.067291 | 0.28519 | -0.15274 | -0.14954 | 0.054932 | 0.082397 | -62.9974 | 60.5804 | 60.5301 | 62.6266 | 62.8464 | 123.6145 | 62.764 | 60.7361
1955.3125 | 0.061035 | 0.43793 | -0.79041 | -0.22751 | 0.16983 | -0.26916 | -0.18478 | 60.8505 | -62.5214 | 0.17395 | -62.7914 | 60.6125 | 62.7548 | 62.6953 | 0.061035 | -0.082245 | 0.066223 | 0.29159 | -0.15274 | -0.16129 | 0.17395 | 0.25635 | -62.9196 | 60.5438 | 60.5667 | 62.6404 | 62.8418 | 123.6969 | 62.7228 | 60.6766
1956.9688 | 0.045776 | 0.42191 | -0.79468 | -0.21042 | 0.16876 | -0.23498 | -0.16769 | 60.7773 | -62.6266 | 0.073242 | -62.8143 | 60.6903 | 62.7502 | 62.709 | 0.076294 | -0.063019 | 0.081177 | 0.27985 | -0.14847 | -0.17624 | 0.059509 | 0.086975 | -63.0249 | 60.6491 | 60.6262 | 62.6358 | 62.8464 | 123.7106 | 62.6999 | 60.6857
1958.6406 | 0.061035 | 0.44647 | -0.79468 | -0.21255 | 0.16129 | -0.25421 | -0.17944 | 60.7727 | -62.6221 | -0.022888 | -62.8418 | 60.6216 | 62.7548 | 62.7182 | 0.061035 | -0.077972 | 0.070496 | 0.28091 | -0.13672 | -0.14633 | 0.027466 | 0.022888 | -62.9791 | 60.5759 | 60.5576 | 62.6678 | 62.8326 | 123.6237 | 62.7686 | 60.6628
1960.2969 | 0.061035 | 0.46036 | -0.79361 | -0.19119 | 0.15595 | -0.25421 | -0.1709 | 60.8093 | -62.5488 | 0.064087 | -62.8189 | 60.5804 | 62.7686 | 62.6953 | 0.045776 | -0.086517 | 0.046997 | 0.27985 | -0.13779 | -0.1474 | 0.068665 | 0.07782 | -62.9425 | 60.5621 | 60.5072 | 62.6358 | 62.8418 | 123.5733 | 62.7686 | 60.704
1961.9531 | 0.045776 | 0.42725 | -0.79147 | -0.20828 | 0.16022 | -0.24887 | -0.16342 | 60.759 | -62.6724 | -0.054932 | -62.8601 | 60.6766 | 62.7594 | 62.7182 | 0.045776 | -0.065155 | 0.071564 | 0.27985 | -0.13992 | -0.1474 | -0.059509 | -0.091553 | -63.0524 | 60.6079 | 60.5804 | 62.6541 | 62.8693 | 123.6008 | 62.764 | 60.7178
1963.625 | 0.061035 | 0.45715 | -0.80536 | -0.20294 | 0.15488 | -0.2713 | -0.16769 | 60.8002 | -62.5305 | 0.082397 | -62.8189 | 60.5759 | 62.764 | 62.709 | 0.045776 | -0.081177 | 0.055542 | 0.28412 | -0.15488 | -0.15274 | 0.054932 | 0.073242 | -62.9471 | 60.5301 | 60.5301 | 62.645 | 62.8372 | 123.5641 | 62.7686 | 60.6995
1965.3125 | 0.091553 | 0.45929 | -0.79147 | -0.21255 | 0.15488 | -0.27451 | -0.17303 | 60.7864 | -62.59 | 0.059509 | -62.8555 | 60.6033 | 62.7548 | 62.7182 | 0.076294 | -0.082245 | 0.064087 | 0.27344 | -0.16449 | -0.14313 | 0.050354 | 0.086975 | -62.9745 | 60.5621 | 60.5621 | 62.6221 | 62.8281 | 123.5779 | 62.7777 | 60.7086
1966.9688 | 0.061035 | 0.42191 | -0.79575 | -0.24033 | 0.16983 | -0.26596 | -0.18372 | 60.8276 | -62.5351 | 0.1831 | -62.7869 | 60.6216 | 62.7594 | 62.6633 | 0.045776 | -0.082245 | 0.076904 | 0.28732 | -0.17624 | -0.16449 | 0.13275 | 0.23804 | -62.9471 | 60.5576 | 60.553 | 62.6221 | 62.8281 | 123.6557 | 62.7182 | 60.7086
1968.6406 | 0.030518 | 0.42511 | -0.784 | -0.22217 | 0.16556 | -0.25101 | -0.16769 | 60.8047 | -62.6038 | 0.07782 | -62.8006 | 60.6903 | 62.7594 | 62.7182 | 0.076294 | -0.065155 | 0.076904 | 0.30121 | -0.14847 | -0.1709 | 0.045776 | 0.073242 | -63.002 | 60.6033 | 60.6125 | 62.6404 | 62.8418 | 123.6923 | 62.709 | 60.6812
1970.2969 | 0.061035 | 0.43472 | -0.78186 | -0.21362 | 0.16556 | -0.24567 | -0.15808 | 60.8002 | -62.5854 | 0.082397 | -62.8052 | 60.6674 | 62.764 | 62.7045 | 0.045776 | -0.065155 | 0.068359 | 0.28198 | -0.15701 | -0.16022 | 0.032043 | 0.041199 | -62.9837 | 60.6079 | 60.6033 | 62.6404 | 62.8601 | 123.6282 | 62.7136 | 60.7132
1971.9531 | 0.045776 | 0.42084 | -0.79575 | -0.22751 | 0.16342 | -0.26169 | -0.16235 | 60.7452 | -62.6038 | 0.073242 | -62.8189 | 60.6628 | 62.7777 | 62.709 | 0.045776 | -0.066223 | 0.074768 | 0.28412 | -0.15595 | -0.15488 | 0.045776 | 0.082397 | -62.9883 | 60.6033 | 60.5942 | 62.6587 | 62.8098 | 123.7106 | 62.7045 | 60.6812
1973.625 | 0.045776 | 0.4422 | -0.78827 | -0.20615 | 0.16235 | -0.27344 | -0.16876 | 60.7681 | -62.5717 | 0.022888 | -62.8098 | 60.6033 | 62.7411 | 62.7136 | 0.045776 | -0.080109 | 0.060883 | 0.27985 | -0.14633 | -0.14526 | 0.027466 | 0.054932 | -62.9608 | 60.5484 | 60.5255 | 62.6129 | 62.8143 | 123.5916 | 62.764 | 60.6812
1975.3281 | 0.045776 | 0.42297 | -0.77652 | -0.20508 | 0.15701 | -0.27344 | -0.16449 | 60.7086 | -62.6587 | -0.045776 | -62.8647 | 60.64 | 62.7686 | 62.7182 | 0.061035 | -0.064087 | 0.0737 | 0.30121 | -0.16449 | -0.15167 | -0.068665 | -0.068665 | -63.0478 | 60.6125 | 60.5988 | 62.6541 | 62.8464 | 123.5916 | 62.7502 | 60.6995
1977 | 0.030518 | 0.42938 | -0.78079 | -0.21362 | 0.15381 | -0.2713 | -0.17197 | 60.7544 | -62.6083 | 0.07782 | -62.8052 | 60.6537 | 62.7686 | 62.7136 | 0.076294 | -0.063019 | 0.069427 | 0.28519 | -0.15167 | -0.16022 | 0.036621 | 0.09613 | -63.002 | 60.6125 | 60.6216 | 62.6083 | 62.8143 | 123.6877 | 62.7045 | 60.7086
1978.6562 | 0.061035 | 0.45181 | -0.78293 | -0.20935 | 0.16129 | -0.26382 | -0.17731 | 60.7315 | -62.6266 | -0.041199 | -62.8372 | 60.6033 | 62.7823 | 62.7182 | 0.045776 | -0.080109 | 0.064087 | 0.28305 | -0.1474 | -0.15488 | -0.004578 | 0 | -62.9791 | 60.5667 | 60.553 | 62.6541 | 62.8326 | 123.587 | 62.764 | 60.6812
1980.3125 | 0.030518 | 0.46249 | -0.79147 | -0.21255 | 0.15488 | -0.28946 | -0.17517 | 60.7681 | -62.558 | 0.059509 | -62.8189 | 60.5759 | 62.7548 | 62.6907 | 0.030518 | -0.072632 | 0.061951 | 0.27985 | -0.15808 | -0.14633 | 0.045776 | 0.073242 | -62.9562 | 60.4935 | 60.5301 | 62.6358 | 62.8738 | 123.5275 | 62.7823 | 60.6766
1981.9688 | 0.030518 | 0.439 | -0.79147 | -0.22217 | 0.16769 | -0.27344 | -0.18372 | 60.8002 | -62.5122 | 0.1831 | -62.7777 | 60.585 | 62.7319 | 62.677 | 0.045776 | -0.081177 | 0.076904 | 0.27557 | -0.15701 | -0.15381 | 0.16022 | 0.25635 | -62.9059 | 60.5438 | 60.5667 | 62.6083 | 62.796 | 123.6237 | 62.6953 | 60.672
1983.6562 | 0.030518 | 0.45288 | -0.79681 | -0.21896 | 0.15808 | -0.27664 | -0.18158 | 60.791 | -62.5534 | 0.045776 | -62.8189 | 60.5804 | 62.7274 | 62.7045 | 0.045776 | -0.091858 | 0.059814 | 0.28305 | -0.16556 | -0.15915 | 0.050354 | 0.054932 | -62.9471 | 60.5164 | 60.5438 | 62.6221 | 62.8418 | 123.555 | 62.764 | 60.704
1985.3281 | 0.045776 | 0.43579 | -0.80215 | -0.22217 | 0.16235 | -0.27878 | -0.18906 | 60.7361 | -62.6175 | 0.032043 | -62.8189 | 60.5988 | 62.7457 | 62.7182 | 0.061035 | -0.081177 | 0.069427 | 0.27878 | -0.17303 | -0.15488 | 0.064087 | 0.10986 | -62.9745 | 60.553 | 60.553 | 62.5992 | 62.8143 | 123.5962 | 62.7274 | 60.6674
1986.9844 | 0.030518 | 0.41657 | -0.79468 | -0.2243 | 0.16235 | -0.26276 | -0.17944 | 60.7498 | -62.6083 | 0.10071 | -62.8281 | 60.6537 | 62.7457 | 62.6907 | 0.061035 | -0.068359 | 0.082245 | 0.28625 | -0.16129 | -0.16556 | 0.068665 | 0.1236 | -63.0066 | 60.6354 | 60.5896 | 62.6541 | 62.8326 | 123.6282 | 62.6862 | 60.6949
1988.6562 | 0.030518 | 0.43686 | -0.79361 | -0.21683 | 0.16342 | -0.28412 | -0.18265 | 60.7819 | -62.558 | 0.086975 | -62.796 | 60.5942 | 62.7274 | 62.6862 | 0.045776 | -0.085449 | 0.070496 | 0.28091 | -0.16663 | -0.15488 | 0.12817 | 0.16022 | -62.9333 | 60.5438 | 60.553 | 62.6083 | 62.8006 | 123.6832 | 62.709 | 60.6857
1990.3281 | 0.045776 | 0.43579 | -0.80429 | -0.22537 | 0.16342 | -0.27451 | -0.18051 | 60.8368 | -62.5168 | 0.18768 | -62.7686 | 60.5804 | 62.7365 | 62.6907 | 0.045776 | -0.079041 | 0.061951 | 0.28412 | -0.15808 | -0.1506 | 0.16479 | 0.24719 | -62.9013 | 60.5621 | 60.5484 | 62.6038 | 62.796 | 123.6374 | 62.6862 | 60.6766
1991.9844 | 0.045776 | 0.43686 | -0.79788 | -0.21896 | 0.17303 | -0.26169 | -0.17303 | 60.8231 | -62.5122 | 0.16022 | -62.7594 | 60.5988 | 62.7457 | 62.6587 | 0.076294 | -0.077972 | 0.077972 | 0.29266 | -0.15381 | -0.16022 | 0.15106 | 0.23804 | -62.9288 | 60.5759 | 60.5621 | 62.6129 | 62.8189 | 123.6191 | 62.6862 | 60.6903
1993.6406 | 0.045776 | 0.42191 | -0.79147 | -0.22644 | 0.15595 | -0.24139 | -0.1709 | 60.7269 | -62.6221 | 0.045776 | -62.8281 | 60.6812 | 62.7548 | 62.6953 | 0.045776 | -0.071564 | 0.084381 | 0.28305 | -0.1506 | -0.16342 | 0.054932 | 0.09613 | -63.002 | 60.6262 | 60.585 | 62.6221 | 62.8189 | 123.674 | 62.709 | 60.6628
1995.3438 | 0.045776 | 0.43366 | -0.79147 | -0.21255 | 0.15167 | -0.27451 | -0.17197 | 60.7956 | -62.4847 | 0.1831 | -62.7594 | 60.6033 | 62.7457 | 62.6862 | 0.045776 | -0.074768 | 0.064087 | 0.28305 | -0.15701 | -0.1474 | 0.15564 | 0.25635 | -62.9242 | 60.5438 | 60.5209 | 62.6221 | 62.8052 | 123.6282 | 62.6999 | 60.672
1997.0312 | 0.045776 | 0.43045 | -0.79788 | -0.19546 | 0.16235 | -0.25742 | -0.16983 | 60.791 | -62.5305 | 0.041199 | -62.7777 | 60.585 | 62.7411 | 62.6633 | 0.045776 | -0.076904 | 0.069427 | 0.27237 | -0.13672 | -0.15381 | 0.032043 | 0.054932 | -62.9379 | 60.5164 | 60.4935 | 62.6221 | 62.8326 | 123.555 | 62.7457 | 60.6537
1998.6875 | 0.061035 | 0.439 | -0.78827 | -0.20828 | 0.15701 | -0.24887 | -0.16876 | 60.7269 | -62.6312 | -0.041199 | -62.851 | 60.6262 | 62.764 | 62.6953 | 0.045776 | -0.069427 | 0.060883 | 0.29373 | -0.14313 | -0.15381 | -0.027466 | -0.050354 | -62.9974 | 60.5576 | 60.5255 | 62.6312 | 62.8143 | 123.5779 | 62.7457 | 60.6628
2000.3594 | 0.061035 | 0.44434 | -0.79361 | -0.21255 | 0.15381 | -0.26916 | -0.17303 | 60.7727 | -62.5214 | 0.054932 | -62.7914 | 60.585 | 62.7502 | 62.6587 | 0.061035 | -0.074768 | 0.081177 | 0.27664 | -0.1506 | -0.1474 | 0.054932 | 0.07782 | -62.9288 | 60.5255 | 60.498 | 62.6083 | 62.8189 | 123.5184 | 62.764 | 60.6491
2002.0156 | 0.045776 | 0.44968 | -0.79681 | -0.21469 | 0.16342 | -0.28519 | -0.17838 | 60.7269 | -62.59 | 0.041199 | -62.8235 | 60.5896 | 62.7365 | 62.6816 | 0.076294 | -0.079041 | 0.069427 | 0.27451 | -0.16663 | -0.14633 | 0.054932 | 0.10986 | -62.9471 | 60.5347 | 60.5438 | 62.5992 | 62.8281 | 123.5687 | 62.7319 | 60.6674
2003.6719 | 0.030518 | 0.41657 | -0.78613 | -0.21576 | 0.15915 | -0.23392 | -0.16663 | 60.7773 | -62.5763 | 0.086975 | -62.7869 | 60.64 | 62.7502 | 62.6816 | 0.045776 | -0.061951 | 0.0737 | 0.29053 | -0.1474 | -0.15701 | 0.050354 | 0.082397 | -62.9654 | 60.5667 | 60.585 | 62.59 | 62.8143 | 123.6282 | 62.6953 | 60.6857
2005.3281 | 0.045776 | 0.45181 | -0.79361 | -0.21149 | 0.15701 | -0.27237 | -0.15915 | 60.7773 | -62.5259 | 0.050354 | -62.7731 | 60.553 | 62.7228 | 62.6862 | 0.045776 | -0.070496 | 0.054474 | 0.28305 | -0.15167 | -0.14526 | 0.064087 | 0.082397 | -62.9196 | 60.5209 | 60.5301 | 62.6038 | 62.8006 | 123.5138 | 62.7228 | 60.6674
2006.9844 | 0.030518 | 0.42831 | -0.79254 | -0.22858 | 0.16769 | -0.29053 | -0.18372 | 60.8185 | -62.4756 | 0.17395 | -62.7457 | 60.5896 | 62.709 | 62.6633 | 0.061035 | -0.089722 | 0.066223 | 0.28198 | -0.16663 | -0.15274 | 0.15564 | 0.24719 | -62.8876 | 60.5209 | 60.5392 | 62.6083 | 62.7914 | 123.6237 | 62.7045 | 60.6628
2008.6562 | 0.045776 | 0.43045 | -0.79468 | -0.21149 | 0.16129 | -0.25742 | -0.16769 | 60.8002 | -62.5442 | 0.041199 | -62.7731 | 60.5942 | 62.7228 | 62.6816 | 0.061035 | -0.085449 | 0.067291 | 0.29053 | -0.13779 | -0.16342 | 0.050354 | 0.041199 | -62.9196 | 60.5301 | 60.5026 | 62.6038 | 62.7914 | 123.5458 | 62.7182 | 60.6766
2010.3281 | 0.076294 | 0.44113 | -0.79681 | -0.21149 | 0.15381 | -0.28625 | -0.18265 | 60.7544 | -62.558 | 0.050354 | -62.8143 | 60.585 | 62.7228 | 62.677 | 0.045776 | -0.085449 | 0.071564 | 0.28091 | -0.16129 | -0.1506 | 0.045776 | 0.073242 | -62.9425 | 60.5164 | 60.5118 | 62.6175 | 62.8281 | 123.5138 | 62.7548 | 60.6766
2011.9844 | 0.076294 | 0.45288 | -0.80322 | -0.21576 | 0.16342 | -0.29159 | -0.17624 | 60.7086 | -62.5992 | 0.050354 | -62.8189 | 60.5896 | 62.7457 | 62.6862 | 0.076294 | -0.083313 | 0.071564 | 0.28839 | -0.16449 | -0.16235 | 0.073242 | 0.13275 | -62.9379 | 60.5255 | 60.5255 | 62.6038 | 62.8189 | 123.5916 | 62.709 | 60.6628
2013.6562 | 0.030518 | 0.44434 | -0.77759 | -0.20081 | 0.15381 | -0.23712 | -0.16983 | 60.7407 | -62.6495 | -0.045776 | -62.8372 | 60.6537 | 62.7548 | 62.6862 | 0.045776 | -0.063019 | 0.061951 | 0.28946 | -0.14206 | -0.16129 | -0.009155 | -0.054932 | -62.9791 | 60.5713 | 60.5392 | 62.6175 | 62.8098 | 123.555 | 62.7319 | 60.6812
2015.3281 | 0.030518 | 0.43259 | -0.79254 | -0.21362 | 0.16129 | -0.25421 | -0.16556 | 60.7956 | -62.5488 | 0.045776 | -62.7686 | 60.5667 | 62.7045 | 62.6678 | 0.061035 | -0.079041 | 0.067291 | 0.28732 | -0.1474 | -0.15701 | 0.041199 | 0.036621 | -62.9196 | 60.5026 | 60.5026 | 62.5992 | 62.796 | 123.5504 | 62.7411 | 60.6537
2016.9844 | 0.061035 | 0.45822 | -0.79361 | -0.22751 | 0.15274 | -0.27451 | -0.17624 | 60.7361 | -62.5626 | 0.045776 | -62.8098 | 60.5759 | 62.7274 | 62.6678 | 0.045776 | -0.076904 | 0.057678 | 0.28412 | -0.14954 | -0.14847 | 0.045776 | 0.086975 | -62.9517 | 60.5255 | 60.5301 | 62.6266 | 62.8006 | 123.4955 | 62.7548 | 60.6766
2018.6406 | 0.076294 | 0.42404 | -0.784 | -0.21149 | 0.16235 | -0.23498 | -0.17197 | 60.7361 | -62.6358 | -0.027466 | -62.8372 | 60.6262 | 62.7319 | 62.677 | 0.076294 | -0.065155 | 0.0737 | 0.298 | -0.14099 | -0.15701 | -0.054932 | -0.07782 | -63.0661 | 60.5804 | 60.5667 | 62.6129 | 62.8326 | 123.5092 | 62.7274 | 60.704
2020.2969 | 0.045776 | 0.4454 | -0.79361 | -0.21042 | 0.15701 | -0.27023 | -0.17303 | 60.7864 | -62.5168 | 0.050354 | -62.7686 | 60.553 | 62.7411 | 62.6678 | 0.061035 | -0.084381 | 0.070496 | 0.27237 | -0.15274 | -0.14526 | 0.064087 | 0.07782 | -62.9105 | 60.5118 | 60.4935 | 62.5854 | 62.8143 | 123.5458 | 62.7228 | 60.6537
2021.9688 | 0.045776 | 0.42938 | -0.78613 | -0.21576 | 0.16983 | -0.23712 | -0.16556 | 60.759 | -62.5946 | 0.036621 | -62.796 | 60.6171 | 62.7045 | 62.6678 | 0.045776 | -0.066223 | 0.071564 | 0.27985 | -0.15167 | -0.15915 | -0.018311 | -0.036621 | -63.002 | 60.585 | 60.5804 | 62.6129 | 62.8189 | 123.5046 | 62.7411 | 60.6812
2023.625 | 0.061035 | 0.43366 | -0.79895 | -0.22003 | 0.15488 | -0.24994 | -0.16022 | 60.6857 | -62.6541 | -0.050354 | -62.8372 | 60.6262 | 62.7228 | 62.6907 | 0.076294 | -0.074768 | 0.071564 | 0.28946 | -0.1474 | -0.14633 | -0.073242 | -0.091553 | -63.0341 | 60.5804 | 60.5621 | 62.6083 | 62.8098 | 123.5275 | 62.764 | 60.6903
2025.2812 | 0.061035 | 0.439 | -0.79788 | -0.20615 | 0.16556 | -0.2713 | -0.1709 | 60.759 | -62.5397 | 0.022888 | -62.7777 | 60.5759 | 62.7045 | 62.6724 | 0.030518 | -0.091858 | 0.057678 | 0.27771 | -0.1506 | -0.15167 | 0.013733 | 0.045776 | -62.9105 | 60.5164 | 60.4935 | 62.6129 | 62.8235 | 123.5413 | 62.7319 | 60.6628
2026.9375 | 0.061035 | 0.43793 | -0.80109 | -0.24246 | 0.16129 | -0.28412 | -0.18478 | 60.8002 | -62.4573 | 0.18768 | -62.7228 | 60.5484 | 62.709 | 62.645 | 0.061035 | -0.092926 | 0.067291 | 0.28625 | -0.17624 | -0.1474 | 0.15106 | 0.26093 | -62.8555 | 60.498 | 60.5392 | 62.5854 | 62.8143 | 123.6237 | 62.6816 | 60.6445
2028.6406 | 0.076294 | 0.44647 | -0.78934 | -0.21683 | 0.16022 | -0.24246 | -0.16556 | 60.7086 | -62.6633 | -0.059509 | -62.8143 | 60.64 | 62.7502 | 62.6724 | 0.076294 | -0.063019 | 0.069427 | 0.28839 | -0.14099 | -0.14954 | -0.064087 | -0.086975 | -63.0295 | 60.5804 | 60.553 | 62.6358 | 62.8326 | 123.5367 | 62.7182 | 60.6583
2030.2969 | 0.045776 | 0.45181 | -0.80215 | -0.20615 | 0.16129 | -0.27664 | -0.1741 | 60.7544 | -62.5076 | 0.059509 | -62.7686 | 60.5621 | 62.7228 | 62.6724 | 0.061035 | -0.086517 | 0.068359 | 0.28091 | -0.16449 | -0.15274 | 0.050354 | 0.086975 | -62.9105 | 60.5026 | 60.498 | 62.6175 | 62.8143 | 123.5046 | 62.7228 | 60.6445
2031.9531 | 0.061035 | 0.46463 | -0.80002 | -0.20508 | 0.16342 | -0.27771 | -0.17303 | 60.7727 | -62.4847 | 0.16937 | -62.7319 | 60.5988 | 62.7182 | 62.6495 | 0.045776 | -0.086517 | 0.05661 | 0.27664 | -0.15488 | -0.15808 | 0.15564 | 0.23804 | -62.883 | 60.5209 | 60.4935 | 62.5854 | 62.8052 | 123.5641 | 62.6678 | 60.6537
2033.6094 | 0.045776 | 0.41336 | -0.784 | -0.23071 | 0.16022 | -0.24994 | -0.16876 | 60.7773 | -62.5534 | 0.082397 | -62.7731 | 60.64 | 62.6999 | 62.6495 | 0.045776 | -0.066223 | 0.075836 | 0.29053 | -0.15808 | -0.15488 | 0.045776 | 0.059509 | -62.9471 | 60.5804 | 60.5209 | 62.6083 | 62.8098 | 123.5641 | 62.677 | 60.672
2035.2969 | 0.061035 | 0.44647 | -0.79361 | -0.21255 | 0.15595 | -0.26916 | -0.17517 | 60.759 | -62.5259 | 0.054932 | -62.764 | 60.553 | 62.7228 | 62.6678 | 0.045776 | -0.079041 | 0.058746 | 0.28839 | -0.14313 | -0.14954 | 0.036621 | 0.059509 | -62.8967 | 60.4935 | 60.4889 | 62.6312 | 62.8189 | 123.5092 | 62.7274 | 60.6354
2036.9844 | 0.030518 | 0.44861 | -0.78507 | -0.23178 | 0.15488 | -0.26916 | -0.18265 | 60.7681 | -62.5259 | 0.059509 | -62.7731 | 60.5621 | 62.7136 | 62.6678 | 0.030518 | -0.083313 | 0.065155 | 0.28198 | -0.16235 | -0.16129 | 0.059509 | 0.086975 | -62.8967 | 60.4843 | 60.4889 | 62.5946 | 62.8098 | 123.4772 | 62.7228 | 60.6491
2038.6406 | 0.061035 | 0.42831 | -0.79895 | -0.22217 | 0.16556 | -0.27664 | -0.16556 | 60.7086 | -62.5671 | 0.041199 | -62.7869 | 60.5576 | 62.7319 | 62.6862 | 0.076294 | -0.088654 | 0.065155 | 0.27664 | -0.15808 | -0.14954 | 0.050354 | 0.091553 | -62.9562 | 60.5164 | 60.5255 | 62.5946 | 62.8052 | 123.5046 | 62.7319 | 60.672
2040.3125 | 0.045776 | 0.42938 | -0.79468 | -0.22537 | 0.14847 | -0.26169 | -0.17838 | 60.7132 | -62.5946 | 0.045776 | -62.8006 | 60.6674 | 62.7182 | 62.6816 | 0.045776 | -0.069427 | 0.063019 | 0.298 | -0.16663 | -0.1709 | 0.032043 | 0.07782 | -62.9929 | 60.5988 | 60.5942 | 62.6083 | 62.7869 | 123.6099 | 62.6587 | 60.6812
2041.9844 | 0.045776 | 0.43366 | -0.78827 | -0.21149 | 0.15488 | -0.2478 | -0.16235 | 60.6766 | -62.6404 | -0.054932 | -62.8189 | 60.64 | 62.709 | 62.6862 | 0.061035 | -0.068359 | 0.065155 | 0.28946 | -0.13779 | -0.15808 | -0.073242 | -0.10986 | -63.0249 | 60.5621 | 60.5621 | 62.6129 | 62.8098 | 123.5001 | 62.709 | 60.6903
2043.6719 | 0.061035 | 0.43579 | -0.79254 | -0.23178 | 0.16129 | -0.27985 | -0.18051 | 60.7224 | -62.5671 | 0.054932 | -62.7869 | 60.5804 | 62.6999 | 62.6633 | 0.045776 | -0.089722 | 0.058746 | 0.28091 | -0.16983 | -0.14526 | 0.050354 | 0.068665 | -62.9333 | 60.5118 | 60.5301 | 62.5854 | 62.8052 | 123.4772 | 62.7274 | 60.6537
2045.3438 | 0.030518 | 0.41229 | -0.7872 | -0.22537 | 0.16449 | -0.24353 | -0.17517 | 60.6995 | -62.6083 | 0.054932 | -62.7869 | 60.6354 | 62.7274 | 62.6816 | 0.061035 | -0.061951 | 0.075836 | 0.28305 | -0.15274 | -0.16449 | 0.041199 | 0.086975 | -62.97 | 60.6079 | 60.5942 | 62.59 | 62.8006 | 123.6145 | 62.6678 | 60.64
2047 | 0.045776 | 0.43152 | -0.79681 | -0.2179 | 0.16556 | -0.24353 | -0.18478 | 60.7315 | -62.5351 | 0.091553 | -62.764 | 60.6354 | 62.7319 | 62.6678 | 0.030518 | -0.063019 | 0.070496 | 0.28091 | -0.14847 | -0.15808 | 0.036621 | 0.082397 | -62.9379 | 60.5621 | 60.5118 | 62.6038 | 62.7914 | 123.5825 | 62.6541 | 60.6216
2048.6719 | 0.061035 | 0.43045 | -0.78079 | -0.22858 | 0.16449 | -0.25955 | -0.16342 | 60.7178 | -62.5534 | 0.07782 | -62.7548 | 60.64 | 62.7045 | 62.6495 | 0.061035 | -0.074768 | 0.077972 | 0.30014 | -0.15274 | -0.14954 | 0.045776 | 0.07782 | -62.9425 | 60.5484 | 60.5484 | 62.6221 | 62.8052 | 123.5779 | 62.645 | 60.6857
2050.375 | 0.045776 | 0.44754 | -0.80215 | -0.22964 | 0.16129 | -0.29907 | -0.16983 | 60.6628 | -62.5397 | 0.07782 | -62.7823 | 60.5576 | 62.7182 | 62.677 | 0.061035 | -0.10254 | 0.069427 | 0.27878 | -0.17303 | -0.1442 | 0.086975 | 0.16022 | -62.9013 | 60.5118 | 60.4843 | 62.5946 | 62.7914 | 123.5641 | 62.6678 | 60.6171
2052.0625 | 0.076294 | 0.46249 | -0.78827 | -0.19867 | 0.16129 | -0.27344 | -0.18158 | 60.7452 | -62.4985 | 0.07782 | -62.7502 | 60.5667 | 62.6953 | 62.6266 | 0.030518 | -0.076904 | 0.057678 | 0.29587 | -0.1506 | -0.14313 | 0.073242 | 0.068665 | -62.9013 | 60.5026 | 60.4706 | 62.5809 | 62.8189 | 123.4451 | 62.709 | 60.6537
2053.7188 | 0.061035 | 0.45181 | -0.79361 | -0.21149 | 0.16556 | -0.2713 | -0.18372 | 60.7132 | -62.5122 | 0.054932 | -62.8006 | 60.5438 | 62.7228 | 62.6404 | 0.076294 | -0.084381 | 0.059814 | 0.27985 | -0.15488 | -0.1474 | 0.050354 | 0.064087 | -62.9333 | 60.5118 | 60.4797 | 62.5809 | 62.7777 | 123.4497 | 62.7274 | 60.6445
2055.4219 | 0.030518 | 0.42725 | -0.7872 | -0.21042 | 0.15701 | -0.2681 | -0.18372 | 60.7452 | -62.5259 | 0.073242 | -62.7411 | 60.5667 | 62.709 | 62.6541 | 0.045776 | -0.092926 | 0.058746 | 0.28625 | -0.15595 | -0.16449 | 0.050354 | 0.073242 | -62.8922 | 60.4935 | 60.4568 | 62.5854 | 62.7869 | 123.4589 | 62.7457 | 60.6445
2057.0781 | 0.030518 | 0.45715 | -0.78613 | -0.21362 | 0.15488 | -0.27557 | -0.17197 | 60.7498 | -62.5122 | 0.073242 | -62.7548 | 60.5484 | 62.7045 | 62.6633 | 0.061035 | -0.086517 | 0.063019 | 0.28519 | -0.15595 | -0.14954 | 0.068665 | 0.068665 | -62.9105 | 60.4706 | 60.4706 | 62.5763 | 62.8006 | 123.436 | 62.7045 | 60.6583
2058.7344 | 0.045776 | 0.44434 | -0.79254 | -0.22217 | 0.16983 | -0.26703 | -0.18051 | 60.7224 | -62.5442 | 0.068665 | -62.7594 | 60.5759 | 62.6907 | 62.6358 | 0.061035 | -0.093994 | 0.060883 | 0.28412 | -0.16556 | -0.15595 | 0.10529 | 0.15564 | -62.9013 | 60.5301 | 60.498 | 62.5854 | 62.764 | 123.5779 | 62.6907 | 60.6262
2060.3906 | 0.030518 | 0.42191 | -0.76904 | -0.21896 | 0.15381 | -0.23392 | -0.16663 | 60.7544 | -62.5809 | 0.032043 | -62.7731 | 60.6125 | 62.7045 | 62.6633 | 0.045776 | -0.058746 | 0.076904 | 0.29159 | -0.12817 | -0.17197 | -0.009155 | -0.045776 | -63.002 | 60.585 | 60.5392 | 62.5992 | 62.8098 | 123.4634 | 62.6953 | 60.6903
2062.0625 | 0.030518 | 0.45502 | -0.80643 | -0.21042 | 0.15595 | -0.28091 | -0.18158 | 60.759 | -62.4619 | 0.1236 | -62.7182 | 60.5713 | 62.6953 | 62.6404 | 0.076294 | -0.080109 | 0.069427 | 0.26489 | -0.15701 | -0.15488 | 0.17853 | 0.21057 | -62.8647 | 60.4797 | 60.4752 | 62.5717 | 62.764 | 123.6008 | 62.645 | 60.6216
2063.7188 | 0.061035 | 0.44754 | -0.7872 | -0.22324 | 0.14847 | -0.28198 | -0.18158 | 60.6812 | -62.558 | 0.050354 | -62.7777 | 60.5438 | 62.6953 | 62.6312 | 0.061035 | -0.084381 | 0.071564 | 0.28198 | -0.16129 | -0.15701 | 0.068665 | 0.11444 | -62.915 | 60.5072 | 60.4935 | 62.5626 | 62.764 | 123.5138 | 62.677 | 60.6171
2065.4219 | 0.061035 | 0.42618 | -0.79468 | -0.23071 | 0.16769 | -0.25742 | -0.17944 | 60.7819 | -62.4527 | 0.17395 | -62.7319 | 60.5576 | 62.6816 | 62.6221 | 0.030518 | -0.079041 | 0.075836 | 0.28519 | -0.16983 | -0.16769 | 0.16479 | 0.24261 | -62.8647 | 60.498 | 60.5255 | 62.5626 | 62.764 | 123.5458 | 62.6358 | 60.64
2067.0781 | 0.061035 | 0.4422 | -0.79147 | -0.21469 | 0.16449 | -0.25742 | -0.17517 | 60.7681 | -62.5031 | 0.050354 | -62.7457 | 60.5576 | 62.6907 | 62.6358 | 0.061035 | -0.088654 | 0.064087 | 0.27878 | -0.14206 | -0.15808 | 0.045776 | 0.045776 | -62.8967 | 60.498 | 60.4706 | 62.5992 | 62.7731 | 123.4818 | 62.6999 | 60.6354
2068.7344 | 0.076294 | 0.45822 | -0.79254 | -0.22537 | 0.16129 | -0.27664 | -0.17731 | 60.704 | -62.5305 | 0.054932 | -62.7686 | 60.5576 | 62.7045 | 62.6404 | 0.061035 | -0.082245 | 0.068359 | 0.28732 | -0.16449 | -0.15488 | 0.07782 | 0.1236 | -62.915 | 60.5072 | 60.4889 | 62.5626 | 62.796 | 123.5229 | 62.6907 | 60.6354
2070.3906 | 0.045776 | 0.42084 | -0.80429 | -0.22751 | 0.15274 | -0.25742 | -0.16663 | 60.6995 | -62.5717 | 0.07782 | -62.7823 | 60.6445 | 62.6724 | 62.6358 | 0.045776 | -0.068359 | 0.077972 | 0.30121 | -0.15595 | -0.16022 | 0.064087 | 0.10986 | -62.9654 | 60.585 | 60.5759 | 62.5809 | 62.7914 | 123.5458 | 62.6541 | 60.6674
2072.0469 | 0.061035 | 0.43152 | -0.80109 | -0.22217 | 0.16876 | -0.25101 | -0.1741 | 60.6949 | -62.5626 | 0.073242 | -62.796 | 60.6033 | 62.709 | 62.6404 | 0.061035 | -0.072632 | 0.079041 | 0.28946 | -0.16342 | -0.1506 | 0.064087 | 0.10986 | -62.9562 | 60.5896 | 60.5667 | 62.6083 | 62.7686 | 123.5275 | 62.6495 | 60.6354
2073.7188 | 0.045776 | 0.439 | -0.79468 | -0.2211 | 0.16983 | -0.26276 | -0.16769 | 60.6857 | -62.5534 | 0.073242 | -62.7823 | 60.6216 | 62.7136 | 62.6495 | 0.045776 | -0.072632 | 0.070496 | 0.28091 | -0.16129 | -0.15274 | 0.068665 | 0.10986 | -62.9562 | 60.585 | 60.5347 | 62.6038 | 62.7823 | 123.5367 | 62.6678 | 60.6491
2075.3906 | 0.061035 | 0.42297 | -0.78613 | -0.19653 | 0.16129 | -0.2446 | -0.16663 | 60.7132 | -62.5351 | 0.041199 | -62.7731 | 60.6125 | 62.7136 | 62.6358 | 0.030518 | -0.071564 | 0.072632 | 0.29053 | -0.13672 | -0.15488 | -0.009155 | 0 | -62.97 | 60.5576 | 60.5301 | 62.5992 | 62.8098 | 123.4543 | 62.6999 | 60.6537
2077.1094 | 0.061035 | 0.42297 | -0.79575 | -0.23071 | 0.15167 | -0.25101 | -0.16556 | 60.7361 | -62.5076 | 0.07782 | -62.7457 | 60.6079 | 62.677 | 62.6129 | 0.061035 | -0.064087 | 0.080109 | 0.29266 | -0.1474 | -0.15915 | 0.041199 | 0.073242 | -62.9196 | 60.5667 | 60.5438 | 62.5671 | 62.7777 | 123.555 | 62.6633 | 60.64
2078.7656 | 0.061035 | 0.44968 | -0.79895 | -0.2243 | 0.15167 | -0.29159 | -0.16663 | 60.6491 | -62.5442 | 0.054932 | -62.764 | 60.5438 | 62.6816 | 62.6266 | 0.030518 | -0.089722 | 0.072632 | 0.28625 | -0.16556 | -0.14099 | 0.059509 | 0.11902 | -62.9059 | 60.4843 | 60.4843 | 62.5671 | 62.7914 | 123.4909 | 62.6541 | 60.6262
2080.4219 | 0.030518 | 0.42938 | -0.79147 | -0.23285 | 0.16449 | -0.25742 | -0.17731 | 60.6674 | -62.5763 | 0.045776 | -62.7823 | 60.6354 | 62.7045 | 62.6587 | 0.045776 | -0.055542 | 0.071564 | 0.28305 | -0.15701 | -0.15701 | 0.018311 | 0.073242 | -62.9745 | 60.5576 | 60.5621 | 62.558 | 62.7731 | 123.555 | 62.6221 | 60.6537
2082.0938 | 0.045776 | 0.43686 | -0.79041 | -0.23285 | 0.1506 | -0.28519 | -0.18158 | 60.672 | -62.5214 | 0.041199 | -62.7594 | 60.5438 | 62.6907 | 62.6175 | 0.045776 | -0.089722 | 0.079041 | 0.28625 | -0.17944 | -0.15595 | 0.059509 | 0.068665 | -62.9013 | 60.4797 | 60.4843 | 62.5946 | 62.7823 | 123.4406 | 62.7228 | 60.6537
2083.75 | 0.061035 | 0.44861 | -0.79575 | -0.21042 | 0.15701 | -0.26703 | -0.16449 | 60.7361 | -62.471 | 0.059509 | -62.7319 | 60.553 | 62.6816 | 62.6083 | 0.061035 | -0.079041 | 0.065155 | 0.28839 | -0.14954 | -0.15808 | 0.059509 | 0.068665 | -62.8738 | 60.4752 | 60.5072 | 62.5809 | 62.7731 | 123.436 | 62.709 | 60.6491
2085.4219 | 0.045776 | 0.45502 | -0.79254 | -0.20935 | 0.16129 | -0.27985 | -0.17838 | 60.704 | -62.5305 | 0.041199 | -62.7731 | 60.5576 | 62.7045 | 62.6083 | 0.030518 | -0.084381 | 0.058746 | 0.28198 | -0.15701 | -0.1506 | 0.041199 | 0.082397 | -62.9105 | 60.4889 | 60.498 | 62.5534 | 62.7686 | 123.4451 | 62.6862 | 60.6537
2087.0938 | 0.045776 | 0.42618 | -0.78507 | -0.22537 | 0.16342 | -0.24353 | -0.17517 | 60.7086 | -62.5488 | 0.07782 | -62.7319 | 60.6308 | 62.6907 | 62.645 | 0.061035 | -0.066223 | 0.076904 | 0.28839 | -0.15701 | -0.16129 | 0.041199 | 0.07782 | -62.9288 | 60.5438 | 60.5347 | 62.5946 | 62.796 | 123.5641 | 62.6266 | 60.6262
2088.75 | 0.061035 | 0.42618 | -0.80109 | -0.22751 | 0.15701 | -0.25101 | -0.16556 | 60.6903 | -62.5305 | 0.054932 | -62.7411 | 60.6171 | 62.6953 | 62.6358 | 0.061035 | -0.0737 | 0.075836 | 0.29694 | -0.14206 | -0.15167 | 0.041199 | 0.07782 | -62.9288 | 60.5484 | 60.5164 | 62.59 | 62.796 | 123.555 | 62.6495 | 60.6262
2090.4375 | 0.061035 | 0.42831 | -0.78827 | -0.21683 | 0.16235 | -0.25314 | -0.15915 | 60.6445 | -62.6083 | -0.027466 | -62.7777 | 60.5804 | 62.6907 | 62.6266 | 0.045776 | -0.071564 | 0.074768 | 0.28732 | -0.14099 | -0.15167 | -0.068665 | -0.082397 | -62.9883 | 60.5301 | 60.5255 | 62.5946 | 62.796 | 123.436 | 62.7045 | 60.6674
2092.1094 | 0.061035 | 0.43472 | -0.79788 | -0.21469 | 0.16449 | -0.28091 | -0.16022 | 60.7086 | -62.4756 | 0.064087 | -62.7548 | 60.5118 | 62.677 | 62.6312 | 0.030518 | -0.10361 | 0.067291 | 0.27771 | -0.14847 | -0.14954 | 0.059509 | 0.073242 | -62.8647 | 60.4843 | 60.4706 | 62.5671 | 62.7869 | 123.4177 | 62.6953 | 60.6308
2093.7656 | 0.076294 | 0.44861 | -0.79254 | -0.21042 | 0.1506 | -0.26382 | -0.17517 | 60.7086 | -62.4847 | 0.022888 | -62.7136 | 60.553 | 62.6724 | 62.6221 | 0.076294 | -0.086517 | 0.053406 | 0.28091 | -0.14847 | -0.16449 | 0.022888 | 0.027466 | -62.8738 | 60.4706 | 60.4706 | 62.5671 | 62.7594 | 123.4589 | 62.7136 | 60.6171
2095.4844 | 0.045776 | 0.42938 | -0.77331 | -0.21149 | 0.15701 | -0.25528 | -0.16983 | 60.7269 | -62.5397 | 0.07782 | -62.7274 | 60.6079 | 62.6999 | 62.6404 | 0.061035 | -0.059814 | 0.070496 | 0.28625 | -0.16129 | -0.16235 | 0.041199 | 0.068665 | -62.9196 | 60.553 | 60.5255 | 62.5626 | 62.7457 | 123.5458 | 62.6404 | 60.6171
2097.1562 | 0.061035 | 0.43366 | -0.78934 | -0.20935 | 0.16769 | -0.26169 | -0.16663 | 60.6445 | -62.5946 | -0.073242 | -62.7823 | 60.5896 | 62.7136 | 62.6541 | 0.045776 | -0.070496 | 0.072632 | 0.28198 | -0.1442 | -0.1474 | -0.068665 | -0.086975 | -62.9745 | 60.5255 | 60.5164 | 62.5946 | 62.7869 | 123.4634 | 62.6862 | 60.6125
2098.8125 | 0.076294 | 0.44647 | -0.79361 | -0.21255 | 0.15167 | -0.27023 | -0.17731 | 60.7178 | -62.4893 | 0.050354 | -62.709 | 60.5209 | 62.677 | 62.5946 | 0.030518 | -0.077972 | 0.059814 | 0.27771 | -0.15274 | -0.14526 | 0.036621 | 0.036621 | -62.8647 | 60.466 | 60.4477 | 62.5809 | 62.7731 | 123.4314 | 62.7136 | 60.6216
2100.5 | 0.045776 | 0.44754 | -0.79895 | -0.22644 | 0.14847 | -0.28625 | -0.17303 | 60.7132 | -62.471 | 0.064087 | -62.7274 | 60.5209 | 62.6678 | 62.6266 | 0.061035 | -0.082245 | 0.081177 | 0.27771 | -0.16129 | -0.1474 | 0.045776 | 0.059509 | -62.8738 | 60.4706 | 60.4797 | 62.5671 | 62.796 | 123.3902 | 62.7045 | 60.6216
2102.1562 | 0.061035 | 0.43259 | -0.79254 | -0.23819 | 0.16983 | -0.27451 | -0.16983 | 60.7132 | -62.4847 | 0.14191 | -62.7136 | 60.5621 | 62.6678 | 62.6175 | 0.061035 | -0.084381 | 0.059814 | 0.28732 | -0.1709 | -0.15915 | 0.086975 | 0.17395 | -62.8922 | 60.5484 | 60.5392 | 62.5854 | 62.7502 | 123.4909 | 62.6266 | 60.6583
2103.8125 | 0.076294 | 0.42404 | -0.80215 | -0.24246 | 0.16342 | -0.2713 | -0.18158 | 60.6995 | -62.5168 | 0.10986 | -62.7274 | 60.5759 | 62.6495 | 62.6175 | 0.045776 | -0.079041 | 0.069427 | 0.28625 | -0.16769 | -0.16876 | 0.050354 | 0.10529 | -62.9379 | 60.5484 | 60.5484 | 62.5671 | 62.764 | 123.4909 | 62.6038 | 60.64
2105.5312 | 0.045776 | 0.43045 | -0.80215 | -0.21683 | 0.15381 | -0.27664 | -0.19012 | 60.7269 | -62.4115 | 0.14191 | -62.7045 | 60.5347 | 62.6816 | 62.5946 | 0.030518 | -0.097198 | 0.065155 | 0.27344 | -0.1709 | -0.16129 | 0.16937 | 0.25635 | -62.8143 | 60.4752 | 60.4568 | 62.5351 | 62.7502 | 123.5275 | 62.6266 | 60.6079
2107.2031 | 0.076294 | 0.44006 | -0.78507 | -0.21576 | 0.15915 | -0.24887 | -0.17197 | 60.672 | -62.5809 | 0.045776 | -62.7457 | 60.6216 | 62.6953 | 62.6175 | 0.045776 | -0.070496 | 0.079041 | 0.29373 | -0.14847 | -0.15915 | 0.036621 | 0.073242 | -62.9379 | 60.5667 | 60.5347 | 62.5626 | 62.764 | 123.5413 | 62.6266 | 60.6216
2108.875 | 0.061035 | 0.439 | -0.78613 | -0.2179 | 0.15274 | -0.28305 | -0.1944 | 60.6674 | -62.5076 | 0.086975 | -62.7182 | 60.5301 | 62.6633 | 62.6038 | 0.076294 | -0.088654 | 0.061951 | 0.27878 | -0.15808 | -0.15274 | 0.12817 | 0.18768 | -62.851 | 60.5026 | 60.4797 | 62.5397 | 62.7411 | 123.5184 | 62.6129 | 60.5942
2110.5938 | 0.061035 | 0.42404 | -0.7872 | -0.2179 | 0.15595 | -0.23926 | -0.16129 | 60.6628 | -62.6038 | -0.041199 | -62.7823 | 60.5988 | 62.7045 | 62.6358 | 0.061035 | -0.060883 | 0.071564 | 0.30014 | -0.13992 | -0.16342 | -0.086975 | -0.091553 | -63.0066 | 60.5484 | 60.5347 | 62.5671 | 62.7777 | 123.3948 | 62.677 | 60.6445
2112.25 | 0.076294 | 0.45502 | -0.79147 | -0.19974 | 0.15915 | -0.26382 | -0.17303 | 60.7086 | -62.4527 | 0.064087 | -62.7274 | 60.5118 | 62.6724 | 62.6038 | 0.045776 | -0.095062 | 0.057678 | 0.27664 | -0.1442 | -0.14954 | 0.064087 | 0.086975 | -62.851 | 60.4614 | 60.4385 | 62.5809 | 62.7502 | 123.3994 | 62.6953 | 60.6033
2113.9062 | 0.030518 | 0.45288 | -0.78507 | -0.20828 | 0.16663 | -0.2713 | -0.17517 | 60.7178 | -62.4847 | 0.059509 | -62.7182 | 60.5209 | 62.6633 | 62.6221 | 0.045776 | -0.075836 | 0.059814 | 0.28946 | -0.14954 | -0.14633 | 0.054932 | 0.068665 | -62.8601 | 60.4477 | 60.4706 | 62.5488 | 62.7777 | 123.3948 | 62.6816 | 60.5942
2115.625 | 0.015259 | 0.44434 | -0.7872 | -0.24674 | 0.14847 | -0.28412 | -0.1741 | 60.6812 | -62.4893 | 0.086975 | -62.7228 | 60.5484 | 62.6724 | 62.6221 | 0.061035 | -0.088654 | 0.070496 | 0.27985 | -0.1741 | -0.15381 | 0.12817 | 0.17395 | -62.8418 | 60.4797 | 60.4935 | 62.558 | 62.7457 | 123.5092 | 62.6358 | 60.6033
2117.2969 | 0.045776 | 0.42297 | -0.79895 | -0.22858 | 0.16342 | -0.25955 | -0.18585 | 60.6766 | -62.5122 | 0.10986 | -62.7411 | 60.5713 | 62.6678 | 62.6129 | 0.061035 | -0.067291 | 0.082245 | 0.28732 | -0.16022 | -0.15915 | 0.07782 | 0.1236 | -62.9288 | 60.5392 | 60.5301 | 62.5717 | 62.764 | 123.4772 | 62.6175 | 60.6445
2118.9844 | 0.045776 | 0.42831 | -0.77652 | -0.21576 | 0.1741 | -0.25101 | -0.1741 | 60.704 | -62.4985 | 0.07782 | -62.7228 | 60.6171 | 62.6816 | 62.6358 | 0.045776 | -0.067291 | 0.084381 | 0.28946 | -0.13565 | -0.15808 | 0.064087 | 0.086975 | -62.8922 | 60.5347 | 60.5301 | 62.5854 | 62.7411 | 123.5092 | 62.6221 | 60.6033
2120.6406 | 0.061035 | 0.44647 | -0.78613 | -0.19226 | 0.16449 | -0.25848 | -0.16342 | 60.6995 | -62.4435 | 0.073242 | -62.709 | 60.498 | 62.6587 | 62.6129 | 0.061035 | -0.081177 | 0.066223 | 0.28519 | -0.14954 | -0.1506 | 0.041199 | 0.064087 | -62.8601 | 60.4477 | 60.434 | 62.5671 | 62.7823 | 123.4131 | 62.6862 | 60.6079
2122.3125 | 0.061035 | 0.43045 | -0.80002 | -0.23605 | 0.15701 | -0.2713 | -0.1709 | 60.704 | -62.439 | 0.16479 | -62.6953 | 60.5621 | 62.677 | 62.5946 | 0.061035 | -0.077972 | 0.059814 | 0.27023 | -0.16342 | -0.15381 | 0.11444 | 0.21057 | -62.8647 | 60.4843 | 60.5026 | 62.5717 | 62.7594 | 123.4634 | 62.6312 | 60.6125
2123.9688 | 0.045776 | 0.41336 | -0.79041 | -0.21255 | 0.15701 | -0.24674 | -0.16342 | 60.7086 | -62.4985 | 0.073242 | -62.7182 | 60.5713 | 62.6541 | 62.6221 | 0.061035 | -0.0737 | 0.072632 | 0.28625 | -0.14526 | -0.16022 | 0.036621 | 0.050354 | -62.9013 | 60.5347 | 60.5072 | 62.5854 | 62.7274 | 123.4726 | 62.6129 | 60.6079
2125.6406 | 0.061035 | 0.45715 | -0.79681 | -0.20615 | 0.14954 | -0.27344 | -0.16129 | 60.6812 | -62.4435 | 0.064087 | -62.7319 | 60.5072 | 62.6678 | 62.6175 | 0.061035 | -0.087585 | 0.052338 | 0.27451 | -0.15595 | -0.14526 | 0.041199 | 0.07782 | -62.8647 | 60.4706 | 60.4477 | 62.5671 | 62.7502 | 123.3719 | 62.6953 | 60.6262
2127.2969 | 0.045776 | 0.44968 | -0.79788 | -0.2179 | 0.16129 | -0.28198 | -0.18372 | 60.6537 | -62.5031 | 0.07782 | -62.7274 | 60.5026 | 62.645 | 62.5992 | 0.061035 | -0.086517 | 0.05661 | 0.28305 | -0.16663 | -0.14526 | 0.059509 | 0.13733 | -62.8418 | 60.4843 | 60.4935 | 62.5259 | 62.7365 | 123.5046 | 62.6129 | 60.5942
2128.9531 | 0.045776 | 0.41016 | -0.77866 | -0.23285 | 0.15274 | -0.24674 | -0.17624 | 60.7269 | -62.4939 | 0.073242 | -62.7274 | 60.6079 | 62.6587 | 62.59 | 0.045776 | -0.065155 | 0.075836 | 0.28946 | -0.15595 | -0.16663 | 0.041199 | 0.082397 | -62.8876 | 60.5118 | 60.5026 | 62.5397 | 62.764 | 123.4863 | 62.6175 | 60.6171
2130.6406 | 0.076294 | 0.4422 | -0.78613 | -0.20615 | 0.16556 | -0.26703 | -0.17517 | 60.7224 | -62.4573 | 0.041199 | -62.6953 | 60.5347 | 62.6633 | 62.59 | 0.045776 | -0.0737 | 0.067291 | 0.29907 | -0.14633 | -0.16235 | 0.009155 | 0.059509 | -62.851 | 60.466 | 60.4431 | 62.5809 | 62.7319 | 123.4039 | 62.6724 | 60.5988
2132.2969 | 0.076294 | 0.45181 | -0.79254 | -0.21042 | 0.16342 | -0.28625 | -0.18478 | 60.6354 | -62.4985 | 0.050354 | -62.7548 | 60.5164 | 62.645 | 62.59 | 0.061035 | -0.095062 | 0.060883 | 0.27985 | -0.16876 | -0.15274 | 0.054932 | 0.11444 | -62.8647 | 60.4706 | 60.4706 | 62.5397 | 62.7594 | 123.436 | 62.6404 | 60.6079
2133.9531 | 0.061035 | 0.43793 | -0.80109 | -0.23178 | 0.15595 | -0.27878 | -0.1741 | 60.6445 | -62.5305 | 0.032043 | -62.7319 | 60.5347 | 62.6724 | 62.6129 | 0.061035 | -0.085449 | 0.063019 | 0.28839 | -0.16129 | -0.15381 | 0.009155 | 0.073242 | -62.8876 | 60.466 | 60.4614 | 62.5488 | 62.7502 | 123.4039 | 62.6404 | 60.6171
2135.6406 | 0.076294 | 0.44006 | -0.7872 | -0.20935 | 0.16876 | -0.24887 | -0.16663 | 60.7269 | -62.4573 | 0.036621 | -62.6816 | 60.5118 | 62.6541 | 62.5992 | 0.076294 | -0.079041 | 0.055542 | 0.28625 | -0.13886 | -0.16663 | 0.032043 | 0.041199 | -62.851 | 60.4477 | 60.4294 | 62.5854 | 62.7274 | 123.3948 | 62.6678 | 60.585
2137.2969 | 0.045776 | 0.439 | -0.79041 | -0.23926 | 0.15488 | -0.27237 | -0.18372 | 60.7269 | -62.4161 | 0.17853 | -62.6816 | 60.5164 | 62.6266 | 62.5854 | 0.030518 | -0.082245 | 0.068359 | 0.28198 | -0.1709 | -0.16022 | 0.14191 | 0.24719 | -62.8143 | 60.4614 | 60.4706 | 62.5259 | 62.7365 | 123.4634 | 62.6129 | 60.5988
2138.9531 | 0.076294 | 0.46249 | -0.80322 | -0.20828 | 0.15274 | -0.27771 | -0.18692 | 60.6628 | -62.471 | 0.036621 | -62.7365 | 60.5072 | 62.645 | 62.558 | 0.061035 | -0.084381 | 0.059814 | 0.27023 | -0.1506 | -0.15488 | 0.013733 | 0.059509 | -62.8784 | 60.4477 | 60.4523 | 62.5305 | 62.7411 | 123.3856 | 62.645 | 60.6033
2140.6562 | 0.061035 | 0.43259 | -0.79575 | -0.23498 | 0.16342 | -0.25207 | -0.18692 | 60.6537 | -62.5397 | 0.07782 | -62.7411 | 60.585 | 62.6541 | 62.6083 | 0.045776 | -0.066223 | 0.0737 | 0.29373 | -0.1474 | -0.16235 | 0.027466 | 0.10986 | -62.9288 | 60.5347 | 60.5392 | 62.5488 | 62.7319 | 123.4772 | 62.5946 | 60.6354
2142.3125 | 0.045776 | 0.41122 | -0.77225 | -0.21683 | 0.14633 | -0.24567 | -0.17197 | 60.7224 | -62.5076 | 0.045776 | -62.7136 | 60.5942 | 62.6633 | 62.6129 | 0.045776 | -0.067291 | 0.070496 | 0.2948 | -0.13992 | -0.16129 | -0.009155 | 0.013733 | -62.9105 | 60.5164 | 60.5026 | 62.5534 | 62.764 | 123.3765 | 62.645 | 60.6354
2143.9688 | 0.030518 | 0.43793 | -0.78934 | -0.22003 | 0.15167 | -0.25528 | -0.15915 | 60.6583 | -62.5076 | -0.022888 | -62.7457 | 60.5484 | 62.6678 | 62.6083 | 0.045776 | -0.088654 | 0.060883 | 0.29694 | -0.14847 | -0.1506 | -0.022888 | 0.013733 | -62.8647 | 60.4706 | 60.4477 | 62.558 | 62.7731 | 123.4268 | 62.6633 | 60.5896
2145.6406 | 0.061035 | 0.45075 | -0.79361 | -0.20828 | 0.15701 | -0.27985 | -0.16983 | 60.6857 | -62.4435 | 0.059509 | -62.6999 | 60.4889 | 62.6587 | 62.5946 | 0.045776 | -0.083313 | 0.068359 | 0.26916 | -0.14954 | -0.14526 | 0.036621 | 0.059509 | -62.8555 | 60.4568 | 60.434 | 62.5534 | 62.7502 | 123.3536 | 62.6999 | 60.5804
2147.2969 | 0.030518 | 0.44006 | -0.7872 | -0.22324 | 0.1442 | -0.28625 | -0.17944 | 60.6583 | -62.4756 | 0.045776 | -62.7274 | 60.5301 | 62.6495 | 62.5992 | 0.045776 | -0.083313 | 0.055542 | 0.27664 | -0.16876 | -0.1506 | 0.027466 | 0.07782 | -62.883 | 60.4568 | 60.4706 | 62.5671 | 62.7548 | 123.3719 | 62.6724 | 60.5942
2148.9688 | 0.045776 | 0.41122 | -0.77652 | -0.23819 | 0.15381 | -0.23712 | -0.16556 | 60.6674 | -62.5442 | -0.009155 | -62.7457 | 60.5804 | 62.677 | 62.6083 | 0.045776 | -0.058746 | 0.081177 | 0.28412 | -0.14099 | -0.16876 | -0.064087 | -0.054932 | -62.9471 | 60.5255 | 60.5392 | 62.5534 | 62.7548 | 123.381 | 62.6495 | 60.6308
2150.6406 | 0.076294 | 0.42938 | -0.78186 | -0.22751 | 0.15274 | -0.25955 | -0.16342 | 60.6308 | -62.5397 | 0.059509 | -62.7365 | 60.6262 | 62.6633 | 62.6129 | 0.061035 | -0.068359 | 0.077972 | 0.29266 | -0.1506 | -0.15381 | 0.009155 | 0.064087 | -62.9242 | 60.5392 | 60.5072 | 62.558 | 62.7502 | 123.4909 | 62.6358 | 60.5942
2152.3438 | 0.045776 | 0.44113 | -0.79895 | -0.22324 | 0.13672 | -0.2948 | -0.1741 | 60.6171 | -62.4802 | 0.059509 | -62.7365 | 60.5118 | 62.6587 | 62.5946 | 0.061035 | -0.088654 | 0.076904 | 0.27344 | -0.16769 | -0.14206 | 0.068665 | 0.15106 | -62.851 | 60.4523 | 60.4752 | 62.5488 | 62.7365 | 123.468 | 62.6404 | 60.5576
2154 | 0.061035 | 0.43259 | -0.80215 | -0.23926 | 0.15701 | -0.28198 | -0.18692 | 60.6308 | -62.4939 | 0.073242 | -62.7182 | 60.5392 | 62.645 | 62.5992 | 0.045776 | -0.088654 | 0.069427 | 0.29373 | -0.16769 | -0.15595 | 0.068665 | 0.12817 | -62.8555 | 60.4431 | 60.4706 | 62.5305 | 62.7228 | 123.4451 | 62.6404 | 60.6033
2155.6719 | 0.045776 | 0.43152 | -0.78507 | -0.20294 | 0.15167 | -0.23926 | -0.17517 | 60.6308 | -62.558 | -0.022888 | -62.7548 | 60.5713 | 62.6541 | 62.6083 | 0.030518 | -0.066223 | 0.069427 | 0.28198 | -0.13992 | -0.15701 | -0.086975 | -0.07782 | -62.97 | 60.553 | 60.4935 | 62.5488 | 62.7411 | 123.3582 | 62.6541 | 60.6171
2157.3281 | 0.045776 | 0.45181 | -0.79468 | -0.22751 | 0.15701 | -0.29266 | -0.1741 | 60.6262 | -62.4893 | 0.050354 | -62.7182 | 60.5255 | 62.6587 | 62.59 | 0.030518 | -0.086517 | 0.068359 | 0.27664 | -0.15167 | -0.15167 | 0.041199 | 0.11902 | -62.8601 | 60.4568 | 60.4568 | 62.5351 | 62.7365 | 123.4131 | 62.6495 | 60.5988
2159 | 0.076294 | 0.41977 | -0.79681 | -0.24246 | 0.1442 | -0.26596 | -0.16876 | 60.6262 | -62.5305 | 0.073242 | -62.7274 | 60.585 | 62.6678 | 62.6221 | 0.045776 | -0.074768 | 0.0737 | 0.29373 | -0.15915 | -0.14954 | 0.045776 | 0.11902 | -62.9105 | 60.5438 | 60.5301 | 62.5305 | 62.7182 | 123.4634 | 62.59 | 60.6079
2160.6562 | 0.045776 | 0.43045 | -0.78934 | -0.2211 | 0.15701 | -0.26276 | -0.1709 | 60.6125 | -62.5259 | 0.073242 | -62.7411 | 60.553 | 62.6495 | 62.6175 | 0.045776 | -0.083313 | 0.066223 | 0.28091 | -0.16235 | -0.14526 | 0.032043 | 0.09613 | -62.9105 | 60.5392 | 60.5118 | 62.5671 | 62.7411 | 123.4451 | 62.5717 | 60.5942
2162.3594 | 0.045776 | 0.42831 | -0.78827 | -0.22003 | 0.16235 | -0.25101 | -0.17517 | 60.6171 | -62.5214 | 0.054932 | -62.7136 | 60.5988 | 62.6587 | 62.5854 | 0.030518 | -0.069427 | 0.069427 | 0.29907 | -0.15808 | -0.15808 | 0.009155 | 0.082397 | -62.9105 | 60.5255 | 60.5301 | 62.5397 | 62.7411 | 123.4726 | 62.5809 | 60.5896
2164.0156 | 0.030518 | 0.42725 | -0.77866 | -0.22858 | 0.17197 | -0.25528 | -0.17197 | 60.672 | -62.4664 | 0.073242 | -62.6953 | 60.585 | 62.6495 | 62.6083 | 0.015259 | -0.071564 | 0.080109 | 0.29159 | -0.14313 | -0.14526 | 0.036621 | 0.059509 | -62.8601 | 60.5209 | 60.5164 | 62.5351 | 62.7594 | 123.468 | 62.5992 | 60.5804
2165.6719 | 0.076294 | 0.42725 | -0.78507 | -0.19974 | 0.16449 | -0.24994 | -0.16876 | 60.6171 | -62.4939 | -0.032043 | -62.7457 | 60.5392 | 62.6541 | 62.5992 | 0.061035 | -0.085449 | 0.055542 | 0.28305 | -0.14526 | -0.1474 | -0.027466 | 0 | -62.8647 | 60.4614 | 60.4248 | 62.558 | 62.7457 | 123.3902 | 62.6404 | 60.5667
2167.3281 | 0.030518 | 0.42084 | -0.79041 | -0.24033 | 0.16449 | -0.27344 | -0.17624 | 60.6857 | -62.4023 | 0.16479 | -62.6678 | 60.5072 | 62.645 | 62.5763 | 0.061035 | -0.074768 | 0.070496 | 0.28519 | -0.17624 | -0.1474 | 0.10986 | 0.22888 | -62.8189 | 60.4797 | 60.4843 | 62.5305 | 62.7365 | 123.4177 | 62.59 | 60.5988
2168.9844 | 0.045776 | 0.43045 | -0.78079 | -0.2179 | 0.14954 | -0.25528 | -0.1741 | 60.6308 | -62.5168 | -0.027466 | -62.7365 | 60.5392 | 62.6175 | 62.6129 | 0.045776 | -0.070496 | 0.072632 | 0.28625 | -0.14633 | -0.14954 | 0 | 0.013733 | -62.8647 | 60.466 | 60.4156 | 62.5442 | 62.7411 | 123.3856 | 62.6312 | 60.5896
2170.6562 | 0.061035 | 0.44647 | -0.80109 | -0.21362 | 0.1474 | -0.29373 | -0.18265 | 60.6033 | -62.4573 | 0.045776 | -62.7365 | 60.4935 | 62.6266 | 62.5763 | 0.061035 | -0.097198 | 0.055542 | 0.27878 | -0.15701 | -0.15274 | 0.018311 | 0.07782 | -62.8693 | 60.4477 | 60.434 | 62.5305 | 62.7686 | 123.3444 | 62.6495 | 60.5988
2172.3125 | 0.030518 | 0.4187 | -0.77866 | -0.2243 | 0.16235 | -0.25101 | -0.17517 | 60.6216 | -62.5214 | 0.050354 | -62.7228 | 60.5942 | 62.6358 | 62.5809 | 0.045776 | -0.069427 | 0.077972 | 0.27985 | -0.15915 | -0.16342 | 0 | 0.086975 | -62.9013 | 60.5301 | 60.5026 | 62.558 | 62.7274 | 123.4772 | 62.59 | 60.5759
2173.9688 | 0.045776 | 0.43579 | -0.79681 | -0.20294 | 0.16022 | -0.25528 | -0.1709 | 60.6079 | -62.5305 | -0.050354 | -62.7502 | 60.5759 | 62.6495 | 62.5992 | 0.061035 | -0.072632 | 0.063019 | 0.27985 | -0.13992 | -0.15274 | -0.073242 | -0.073242 | -62.915 | 60.4843 | 60.4843 | 62.5351 | 62.7182 | 123.3948 | 62.6312 | 60.585
2175.6562 | 0.061035 | 0.42725 | -0.79575 | -0.24139 | 0.15808 | -0.28091 | -0.16663 | 60.6766 | -62.4023 | 0.1831 | -62.6678 | 60.5026 | 62.6175 | 62.5671 | 0.076294 | -0.087585 | 0.069427 | 0.28305 | -0.16876 | -0.15915 | 0.14191 | 0.2655 | -62.7823 | 60.4477 | 60.4568 | 62.5122 | 62.7319 | 123.4222 | 62.5992 | 60.5713
2177.3125 | 0.061035 | 0.42511 | -0.7872 | -0.22964 | 0.16129 | -0.2446 | -0.18051 | 60.6079 | -62.5031 | 0.050354 | -62.7045 | 60.6216 | 62.6541 | 62.5854 | 0.076294 | -0.067291 | 0.074768 | 0.29694 | -0.15595 | -0.16769 | 0.013733 | 0.082397 | -62.883 | 60.5164 | 60.4935 | 62.5351 | 62.7548 | 123.4772 | 62.5946 | 60.5896
2178.9688 | 0.061035 | 0.43472 | -0.79147 | -0.20294 | 0.15274 | -0.26062 | -0.17624 | 60.6262 | -62.5168 | -0.018311 | -62.7274 | 60.5347 | 62.645 | 62.59 | 0.061035 | -0.083313 | 0.075836 | 0.29694 | -0.1442 | -0.1506 | -0.032043 | -0.041199 | -62.883 | 60.466 | 60.4202 | 62.5488 | 62.7502 | 123.3994 | 62.6724 | 60.5759
2180.6406 | 0.030518 | 0.45929 | -0.79788 | -0.21362 | 0.13779 | -0.28412 | -0.17517 | 60.6079 | -62.439 | 0.045776 | -62.7136 | 60.498 | 62.6312 | 62.5763 | 0.061035 | -0.088654 | 0.065155 | 0.27344 | -0.15381 | -0.13992 | 0.027466 | 0.068665 | -62.8418 | 60.4385 | 60.4385 | 62.5442 | 62.7365 | 123.3261 | 62.6541 | 60.5713
2182.2969 | 0.076294 | 0.44434 | -0.79041 | -0.22324 | 0.15701 | -0.27985 | -0.17624 | 60.672 | -62.3978 | 0.13275 | -62.6678 | 60.4935 | 62.6221 | 62.5717 | 0.030518 | -0.09079 | 0.05661 | 0.28091 | -0.16983 | -0.15595 | 0.13733 | 0.21973 | -62.764 | 60.4477 | 60.4385 | 62.5168 | 62.6953 | 123.4543 | 62.6129 | 60.5576
2183.9531 | 0.045776 | 0.42831 | -0.80643 | -0.23071 | 0.15274 | -0.28519 | -0.16983 | 60.6857 | -62.3932 | 0.13275 | -62.6724 | 60.498 | 62.6312 | 62.5671 | 0.061035 | -0.097198 | 0.061951 | 0.28519 | -0.17624 | -0.16235 | 0.16479 | 0.2243 | -62.764 | 60.4477 | 60.4431 | 62.4893 | 62.7045 | 123.436 | 62.5809 | 60.5759
2185.6406 | 0.061035 | 0.45502 | -0.79147 | -0.21683 | 0.16983 | -0.27771 | -0.18799 | 60.64 | -62.4619 | 0.036621 | -62.7228 | 60.5164 | 62.6358 | 62.5763 | 0.045776 | -0.09079 | 0.068359 | 0.28198 | -0.15274 | -0.15808 | 0.032043 | 0.064087 | -62.8555 | 60.4568 | 60.434 | 62.5351 | 62.7365 | 123.3307 | 62.6358 | 60.5896
2187.2969 | 0.076294 | 0.41443 | -0.784 | -0.22003 | 0.16022 | -0.2478 | -0.1709 | 60.672 | -62.4802 | 0.059509 | -62.6999 | 60.6125 | 62.6404 | 62.6083 | 0.045776 | -0.075836 | 0.067291 | 0.29159 | -0.1442 | -0.16769 | 0.022888 | 0.086975 | -62.8784 | 60.5347 | 60.4797 | 62.5214 | 62.7411 | 123.468 | 62.5763 | 60.5942
2188.9531 | 0.061035 | 0.44647 | -0.78613 | -0.1976 | 0.15488 | -0.25421 | -0.16129 | 60.672 | -62.4207 | 0.054932 | -62.6862 | 60.4843 | 62.6221 | 62.5763 | 0.045776 | -0.089722 | 0.0737 | 0.27771 | -0.14206 | -0.15595 | 0.018311 | 0.054932 | -62.8143 | 60.4248 | 60.4065 | 62.5534 | 62.709 | 123.3444 | 62.6404 | 60.5347
2190.6406 | 0.061035 | 0.44754 | -0.79468 | -0.20615 | 0.14313 | -0.26596 | -0.16769 | 60.6857 | -62.439 | 0.032043 | -62.6724 | 60.4843 | 62.6404 | 62.5717 | 0.076294 | -0.076904 | 0.061951 | 0.28412 | -0.14847 | -0.15381 | 0.032043 | 0.032043 | -62.8235 | 60.4523 | 60.4248 | 62.5351 | 62.7182 | 123.3536 | 62.6221 | 60.585
2192.2969 | 0.045776 | 0.41763 | -0.7872 | -0.22217 | 0.15701 | -0.24567 | -0.17303 | 60.6674 | -62.4619 | 0.068665 | -62.677 | 60.5484 | 62.6358 | 62.5809 | 0.045776 | -0.069427 | 0.077972 | 0.28198 | -0.14206 | -0.15808 | 0.036621 | 0.082397 | -62.8647 | 60.5118 | 60.4935 | 62.5397 | 62.7136 | 123.436 | 62.5717 | 60.5942
2193.9531 | 0.061035 | 0.42084 | -0.79788 | -0.23498 | 0.16342 | -0.2713 | -0.1741 | 60.5988 | -62.4939 | 0.050354 | -62.7045 | 60.5438 | 62.6541 | 62.59 | 0.030518 | -0.071564 | 0.067291 | 0.29694 | -0.15274 | -0.15488 | 0.018311 | 0.07782 | -62.8922 | 60.5301 | 60.4935 | 62.5534 | 62.7319 | 123.4543 | 62.5763 | 60.5896
2195.6562 | 0.045776 | 0.42725 | -0.80002 | -0.22964 | 0.15808 | -0.25635 | -0.16556 | 60.5896 | -62.4939 | 0.045776 | -62.7045 | 60.5713 | 62.6266 | 62.59 | 0.076294 | -0.0737 | 0.067291 | 0.28412 | -0.15595 | -0.14847 | 0.013733 | 0.064087 | -62.9013 | 60.4889 | 60.5255 | 62.5122 | 62.7182 | 123.4497 | 62.5717 | 60.5759
2197.3125 | 0.061035 | 0.43045 | -0.78507 | -0.21683 | 0.15595 | -0.25207 | -0.16769 | 60.5988 | -62.4985 | -0.013733 | -62.7182 | 60.5255 | 62.6495 | 62.5992 | 0.076294 | -0.072632 | 0.0737 | 0.28732 | -0.14206 | -0.15167 | -0.10071 | -0.082397 | -62.9379 | 60.498 | 60.498 | 62.5397 | 62.7457 | 123.317 | 62.6358 | 60.6125
2198.9688 | 0.030518 | 0.44006 | -0.79895 | -0.22003 | 0.14099 | -0.28519 | -0.16876 | 60.6308 | -62.4161 | 0.054932 | -62.6999 | 60.4706 | 62.6083 | 62.558 | 0.045776 | -0.093994 | 0.053406 | 0.27878 | -0.15701 | -0.1506 | 0.036621 | 0.064087 | -62.8372 | 60.4065 | 60.4202 | 62.5305 | 62.7365 | 123.2895 | 62.6724 | 60.5759
2200.6562 | 0.076294 | 0.42831 | -0.78613 | -0.23712 | 0.15595 | -0.27664 | -0.18158 | 60.6491 | -62.3978 | 0.15564 | -62.6495 | 60.5209 | 62.6221 | 62.5626 | 0.076294 | -0.079041 | 0.075836 | 0.28519 | -0.16983 | -0.15595 | 0.09613 | 0.20142 | -62.8281 | 60.4706 | 60.4523 | 62.5305 | 62.7136 | 123.3948 | 62.5809 | 60.5759
2202.3125 | 0.061035 | 0.42084 | -0.79041 | -0.21469 | 0.16876 | -0.24567 | -0.16129 | 60.6033 | -62.5214 | -0.018311 | -62.7274 | 60.5576 | 62.6221 | 62.5992 | 0.061035 | -0.058746 | 0.071564 | 0.2948 | -0.14313 | -0.15915 | -0.09613 | -0.073242 | -62.9288 | 60.5026 | 60.4843 | 62.5076 | 62.7319 | 123.3078 | 62.6312 | 60.6079
2203.9844 | 0.045776 | 0.39948 | -0.78079 | -0.23285 | 0.16235 | -0.25421 | -0.16556 | 60.6537 | -62.4481 | 0.07782 | -62.6862 | 60.5713 | 62.6038 | 62.5854 | 0.045776 | -0.067291 | 0.084381 | 0.28946 | -0.15595 | -0.16022 | 0.022888 | 0.041199 | -62.8281 | 60.5026 | 60.4797 | 62.4847 | 62.7182 | 123.3994 | 62.5854 | 60.5667
2205.6406 | 0.045776 | 0.43045 | -0.78293 | -0.20508 | 0.1506 | -0.25955 | -0.16022 | 60.553 | -62.5534 | -0.054932 | -62.7274 | 60.5484 | 62.6404 | 62.59 | 0.061035 | -0.077972 | 0.064087 | 0.28412 | -0.14526 | -0.15488 | -0.086975 | -0.09613 | -62.9471 | 60.4935 | 60.4843 | 62.5397 | 62.7274 | 123.317 | 62.6358 | 60.6171
2207.3125 | 0.045776 | 0.43793 | -0.79361 | -0.23605 | 0.14313 | -0.29373 | -0.1709 | 60.5667 | -62.4619 | 0.041199 | -62.7182 | 60.4889 | 62.6358 | 62.5763 | 0.061035 | -0.089722 | 0.079041 | 0.27878 | -0.1741 | -0.15274 | 0.013733 | 0.10071 | -62.8464 | 60.4202 | 60.4568 | 62.4939 | 62.7365 | 123.3582 | 62.6266 | 60.5759
2208.9844 | 0.061035 | 0.43793 | -0.78293 | -0.22324 | 0.15595 | -0.27664 | -0.17944 | 60.6445 | -62.4298 | 0.13733 | -62.6633 | 60.5209 | 62.6083 | 62.5671 | 0.076294 | -0.080109 | 0.063019 | 0.28091 | -0.1709 | -0.1506 | 0.086975 | 0.16937 | -62.851 | 60.498 | 60.4614 | 62.5259 | 62.709 | 123.3719 | 62.5854 | 60.5896
2210.6562 | 0.061035 | 0.47104 | -0.79468 | -0.21362 | 0.14847 | -0.28198 | -0.17197 | 60.585 | -62.471 | 0.045776 | -62.6999 | 60.498 | 62.6266 | 62.5442 | 0.045776 | -0.09079 | 0.069427 | 0.27451 | -0.15808 | -0.14633 | 0.050354 | 0.11444 | -62.8418 | 60.4431 | 60.434 | 62.5305 | 62.7319 | 123.3582 | 62.6038 | 60.5484
2212.3125 | 0.030518 | 0.44006 | -0.79468 | -0.22858 | 0.16342 | -0.27451 | -0.17624 | 60.6857 | -62.3932 | 0.16937 | -62.645 | 60.4752 | 62.6038 | 62.5626 | 0.061035 | -0.087585 | 0.055542 | 0.27557 | -0.15488 | -0.1709 | 0.14191 | 0.24261 | -62.7731 | 60.4568 | 60.4431 | 62.5031 | 62.7136 | 123.3902 | 62.6038 | 60.5759
2213.9844 | 0.045776 | 0.43045 | -0.78934 | -0.22964 | 0.15381 | -0.27237 | -0.18692 | 60.6995 | -62.3657 | 0.16479 | -62.6495 | 60.5026 | 62.59 | 62.5397 | 0.061035 | -0.093994 | 0.058746 | 0.28625 | -0.16235 | -0.16556 | 0.14191 | 0.26093 | -62.7594 | 60.4614 | 60.4385 | 62.5122 | 62.677 | 123.4131 | 62.5763 | 60.553
2215.6562 | 0.076294 | 0.42404 | -0.79147 | -0.23178 | 0.16129 | -0.26276 | -0.17517 | 60.6537 | -62.4252 | 0.13275 | -62.6724 | 60.5576 | 62.6083 | 62.5351 | 0.061035 | -0.077972 | 0.068359 | 0.28519 | -0.16342 | -0.15488 | 0.07782 | 0.13275 | -62.8693 | 60.4935 | 60.4843 | 62.5305 | 62.7319 | 123.3765 | 62.5809 | 60.5713
2217.3438 | 0.045776 | 0.42084 | -0.79361 | -0.22644 | 0.13992 | -0.25848 | -0.17838 | 60.672 | -62.4023 | 0.16479 | -62.6495 | 60.4889 | 62.6129 | 62.5717 | 0.045776 | -0.089722 | 0.079041 | 0.28305 | -0.16022 | -0.15701 | 0.1236 | 0.21973 | -62.8052 | 60.4614 | 60.4568 | 62.4893 | 62.6953 | 123.3765 | 62.5626 | 60.5896
2219 | 0.061035 | 0.42297 | -0.78507 | -0.20828 | 0.16022 | -0.22858 | -0.16876 | 60.6491 | -62.4802 | 0.018311 | -62.6999 | 60.5484 | 62.6266 | 62.5946 | 0.045776 | -0.063019 | 0.071564 | 0.29373 | -0.14206 | -0.1709 | -0.027466 | -0.018311 | -62.9105 | 60.4843 | 60.4568 | 62.5488 | 62.709 | 123.2986 | 62.6312 | 60.5804
2220.6719 | 0.061035 | 0.43045 | -0.79468 | -0.23926 | 0.14847 | -0.29159 | -0.17731 | 60.6445 | -62.3886 | 0.13275 | -62.6404 | 60.5072 | 62.6358 | 62.5397 | 0.045776 | -0.095062 | 0.058746 | 0.28091 | -0.16449 | -0.15808 | 0.15106 | 0.22888 | -62.7548 | 60.4523 | 60.4248 | 62.4985 | 62.7274 | 123.4131 | 62.558 | 60.5347
2222.3281 | 0.076294 | 0.42297 | -0.77759 | -0.20935 | 0.14633 | -0.23712 | -0.16663 | 60.6537 | -62.4619 | 0.036621 | -62.6953 | 60.5392 | 62.6358 | 62.5763 | 0.061035 | -0.064087 | 0.063019 | 0.2948 | -0.13565 | -0.16235 | -0.004578 | -0.022888 | -62.8922 | 60.4889 | 60.4797 | 62.5214 | 62.7274 | 123.3032 | 62.6083 | 60.585
2223.9844 | 0.045776 | 0.43366 | -0.78934 | -0.19974 | 0.16876 | -0.26382 | -0.16663 | 60.6033 | -62.4435 | -0.009155 | -62.6999 | 60.4935 | 62.6266 | 62.5992 | 0.061035 | -0.074768 | 0.057678 | 0.27985 | -0.14099 | -0.1506 | -0.004578 | 0.018311 | -62.8326 | 60.4248 | 60.4111 | 62.5168 | 62.709 | 123.3353 | 62.5992 | 60.5255
2225.6562 | 0.045776 | 0.42084 | -0.784 | -0.23178 | 0.17197 | -0.24994 | -0.17303 | 60.64 | -62.4435 | 0.068665 | -62.6633 | 60.5392 | 62.5854 | 62.5534 | 0.061035 | -0.0737 | 0.067291 | 0.28946 | -0.1506 | -0.15488 | 0.032043 | 0.054932 | -62.8235 | 60.4706 | 60.4752 | 62.4939 | 62.7045 | 123.3948 | 62.5717 | 60.5621
2227.3594 | 0.045776 | 0.44113 | -0.79147 | -0.21042 | 0.15915 | -0.25955 | -0.16556 | 60.585 | -62.4756 | -0.018311 | -62.7182 | 60.5118 | 62.6358 | 62.558 | 0.045776 | -0.071564 | 0.05661 | 0.28625 | -0.1474 | -0.14847 | -0.013733 | 0 | -62.8281 | 60.4156 | 60.4385 | 62.5168 | 62.6862 | 123.3398 | 62.6358 | 60.553
2229.0312 | 0.061035 | 0.42511 | -0.784 | -0.21683 | 0.14847 | -0.27237 | -0.18478 | 60.6354 | -62.4023 | 0.07782 | -62.6633 | 60.4843 | 62.5946 | 62.5259 | 0.030518 | -0.087585 | 0.0737 | 0.27664 | -0.16022 | -0.15274 | 0.027466 | 0.064087 | -62.8006 | 60.4065 | 60.4477 | 62.5168 | 62.7228 | 123.2483 | 62.6358 | 60.585
2230.7031 | 0.076294 | 0.43152 | -0.79041 | -0.23392 | 0.14847 | -0.27985 | -0.18158 | 60.6628 | -62.4023 | 0.15106 | -62.6495 | 60.4889 | 62.5992 | 62.5305 | 0.045776 | -0.0737 | 0.075836 | 0.28091 | -0.1709 | -0.1506 | 0.10986 | 0.21973 | -62.7914 | 60.4477 | 60.4614 | 62.5168 | 62.6953 | 123.3353 | 62.5626 | 60.5759
2232.3906 | 0.045776 | 0.44968 | -0.80215 | -0.20615 | 0.1474 | -0.27878 | -0.17731 | 60.6079 | -62.4298 | 0.041199 | -62.6953 | 60.466 | 62.5946 | 62.5442 | 0.015259 | -0.09079 | 0.066223 | 0.27878 | -0.16449 | -0.15381 | 0.018311 | 0.064087 | -62.8326 | 60.4431 | 60.4156 | 62.5031 | 62.7319 | 123.2986 | 62.6312 | 60.5576
2234.0625 | 0.030518 | 0.39734 | -0.78079 | -0.24033 | 0.16769 | -0.25314 | -0.17517 | 60.64 | -62.4664 | 0.07782 | -62.6678 | 60.553 | 62.5992 | 62.5671 | 0.045776 | -0.068359 | 0.089722 | 0.27771 | -0.14954 | -0.17197 | 0.022888 | 0.059509 | -62.851 | 60.5164 | 60.4614 | 62.5031 | 62.6953 | 123.4085 | 62.558 | 60.585
2235.7344 | 0.061035 | 0.42297 | -0.77972 | -0.20721 | 0.14847 | -0.27237 | -0.15488 | 60.6491 | -62.4252 | 0.036621 | -62.6587 | 60.4752 | 62.5992 | 62.5626 | 0.061035 | -0.093994 | 0.067291 | 0.28412 | -0.13886 | -0.15701 | 0.009155 | 0.036621 | -62.796 | 60.4111 | 60.3745 | 62.5168 | 62.677 | 123.317 | 62.5992 | 60.5621
2237.4062 | 0.061035 | 0.42725 | -0.78079 | -0.2243 | 0.15274 | -0.29053 | -0.17303 | 60.64 | -62.384 | 0.15564 | -62.6266 | 60.4843 | 62.5534 | 62.5214 | 0.076294 | -0.084381 | 0.072632 | 0.28412 | -0.1741 | -0.15274 | 0.12817 | 0.2243 | -62.7869 | 60.4523 | 60.4385 | 62.4939 | 62.6907 | 123.3627 | 62.5534 | 60.5713
2239.0625 | 0.030518 | 0.41977 | -0.79041 | -0.2211 | 0.15274 | -0.23712 | -0.16129 | 60.6125 | -62.4527 | 0.036621 | -62.6724 | 60.5301 | 62.6221 | 62.5671 | 0.061035 | -0.068359 | 0.075836 | 0.28946 | -0.14633 | -0.16129 | -0.022888 | -0.022888 | -62.8922 | 60.466 | 60.4523 | 62.4985 | 62.6907 | 123.2849 | 62.6038 | 60.5896
2240.7344 | 0.045776 | 0.43472 | -0.79895 | -0.22537 | 0.15381 | -0.29266 | -0.18692 | 60.5804 | -62.4207 | 0.059509 | -62.6633 | 60.4889 | 62.5992 | 62.5626 | 0.045776 | -0.093994 | 0.063019 | 0.28091 | -0.17838 | -0.15488 | 0.073242 | 0.16022 | -62.796 | 60.4202 | 60.4385 | 62.5076 | 62.7136 | 123.3902 | 62.5717 | 60.5438
2242.4062 | 0.045776 | 0.43152 | -0.79041 | -0.22644 | 0.15488 | -0.27451 | -0.16983 | 60.64 | -62.3795 | 0.15564 | -62.6266 | 60.4935 | 62.5809 | 62.5397 | 0.061035 | -0.075836 | 0.067291 | 0.28625 | -0.15701 | -0.16983 | 0.11902 | 0.21515 | -62.8098 | 60.4431 | 60.4614 | 62.4939 | 62.6816 | 123.3444 | 62.5626 | 60.5621
2244.0938 | 0.045776 | 0.43793 | -0.78827 | -0.21255 | 0.14206 | -0.24139 | -0.16876 | 60.5667 | -62.5214 | -0.041199 | -62.6999 | 60.5301 | 62.6266 | 62.5763 | 0.045776 | -0.065155 | 0.064087 | 0.30014 | -0.13779 | -0.15808 | -0.07782 | -0.086975 | -62.9333 | 60.498 | 60.4614 | 62.5305 | 62.7411 | 123.2574 | 62.59 | 60.5942
2245.7656 | 0.045776 | 0.45075 | -0.79361 | -0.22324 | 0.1474 | -0.29159 | -0.18051 | 60.5621 | -62.439 | 0.032043 | -62.6953 | 60.5026 | 62.6083 | 62.5717 | 0.061035 | -0.10574 | 0.066223 | 0.27451 | -0.15701 | -0.1442 | 0.022888 | 0.073242 | -62.8281 | 60.4202 | 60.3928 | 62.5259 | 62.7045 | 123.2758 | 62.6129 | 60.5576
2247.4375 | 0.045776 | 0.42938 | -0.7872 | -0.22217 | 0.15274 | -0.25742 | -0.17624 | 60.6125 | -62.439 | 0.10529 | -62.6633 | 60.5164 | 62.5946 | 62.5397 | 0.076294 | -0.074768 | 0.064087 | 0.28412 | -0.15701 | -0.16022 | 0.050354 | 0.12817 | -62.8601 | 60.4797 | 60.4706 | 62.5031 | 62.6999 | 123.3398 | 62.5442 | 60.585
2249.1094 | 0.030518 | 0.42404 | -0.784 | -0.20615 | 0.14206 | -0.25421 | -0.17838 | 60.6354 | -62.439 | 0.073242 | -62.6541 | 60.5438 | 62.5992 | 62.5671 | 0.061035 | -0.064087 | 0.068359 | 0.28412 | -0.13458 | -0.16129 | 0.032043 | 0.068665 | -62.8326 | 60.5118 | 60.4431 | 62.5168 | 62.6862 | 123.3856 | 62.5717 | 60.553
2250.7812 | 0.061035 | 0.42618 | -0.78293 | -0.20401 | 0.15701 | -0.2478 | -0.1741 | 60.5713 | -62.4893 | -0.054932 | -62.7045 | 60.5347 | 62.6175 | 62.5626 | 0.061035 | -0.072632 | 0.072632 | 0.2948 | -0.14313 | -0.15595 | -0.073242 | -0.09613 | -62.8922 | 60.4843 | 60.4385 | 62.5031 | 62.6953 | 123.3078 | 62.6175 | 60.5621
2252.4531 | 0.061035 | 0.4422 | -0.78827 | -0.23178 | 0.15808 | -0.28519 | -0.18051 | 60.5896 | -62.4161 | 0.059509 | -62.6724 | 60.4797 | 62.6129 | 62.5351 | 0.045776 | -0.092926 | 0.074768 | 0.28091 | -0.16342 | -0.15274 | 0.018311 | 0.068665 | -62.8143 | 60.4111 | 60.4156 | 62.5305 | 62.7182 | 123.2574 | 62.6404 | 60.5438
2254.1094 | 0.030518 | 0.42618 | -0.79468 | -0.23498 | 0.16983 | -0.26489 | -0.18478 | 60.6537 | -62.3566 | 0.15564 | -62.6358 | 60.5072 | 62.59 | 62.5214 | 0.061035 | -0.087585 | 0.057678 | 0.28305 | -0.17197 | -0.16342 | 0.10071 | 0.21973 | -62.7823 | 60.4248 | 60.434 | 62.4847 | 62.6587 | 123.3444 | 62.59 | 60.5347
2255.7656 | 0.030518 | 0.40695 | -0.77225 | -0.23712 | 0.16235 | -0.24674 | -0.17197 | 60.64 | -62.4344 | 0.064087 | -62.6541 | 60.5576 | 62.6083 | 62.5534 | 0.045776 | -0.069427 | 0.076904 | 0.29053 | -0.14633 | -0.17197 | 0.022888 | 0.064087 | -62.8372 | 60.4797 | 60.4797 | 62.4939 | 62.6816 | 123.3902 | 62.5305 | 60.5301
2257.4219 | 0.061035 | 0.4454 | -0.78079 | -0.20828 | 0.14954 | -0.25955 | -0.1709 | 60.6308 | -62.3932 | 0.032043 | -62.6404 | 60.4752 | 62.6083 | 62.5534 | 0.061035 | -0.080109 | 0.064087 | 0.27771 | -0.13992 | -0.15381 | 0.004578 | 0.022888 | -62.796 | 60.4202 | 60.3973 | 62.4847 | 62.6953 | 123.2986 | 62.5946 | 60.5164
2259.0781 | 0.076294 | 0.40482 | -0.77759 | -0.23498 | 0.15167 | -0.25742 | -0.15274 | 60.5621 | -62.5259 | -0.045776 | -62.6953 | 60.5438 | 62.6129 | 62.5397 | 0.030518 | -0.074768 | 0.079041 | 0.28625 | -0.16342 | -0.14633 | -0.082397 | -0.10986 | -62.9196 | 60.4752 | 60.4752 | 62.5168 | 62.7136 | 123.2895 | 62.59 | 60.5759
2260.75 | 0.061035 | 0.42511 | -0.77972 | -0.2179 | 0.16342 | -0.26062 | -0.16449 | 60.6262 | -62.4207 | 0.050354 | -62.6633 | 60.5072 | 62.6129 | 62.5442 | 0.061035 | -0.063019 | 0.066223 | 0.29266 | -0.14954 | -0.16876 | -0.009155 | 0.013733 | -62.8601 | 60.4431 | 60.4568 | 62.4756 | 62.6724 | 123.2712 | 62.5671 | 60.5713
2262.4062 | 0.076294 | 0.44113 | -0.80002 | -0.21362 | 0.15488 | -0.26916 | -0.17303 | 60.6308 | -62.3703 | 0.045776 | -62.6312 | 60.4477 | 62.59 | 62.5305 | 0.076294 | -0.088654 | 0.058746 | 0.27878 | -0.1506 | -0.15167 | 0.027466 | 0.064087 | -62.7869 | 60.3836 | 60.3928 | 62.4985 | 62.6907 | 123.2712 | 62.6175 | 60.5438
2264.0625 | 0.045776 | 0.45075 | -0.80109 | -0.22964 | 0.13565 | -0.28198 | -0.18585 | 60.6308 | -62.3428 | 0.16937 | -62.6266 | 60.4752 | 62.5763 | 62.5442 | 0.061035 | -0.084381 | 0.053406 | 0.28091 | -0.16022 | -0.15167 | 0.1236 | 0.22888 | -62.764 | 60.4065 | 60.4385 | 62.4939 | 62.677 | 123.3353 | 62.5534 | 60.5484
2265.7188 | 0.061035 | 0.42938 | -0.79361 | -0.20721 | 0.14526 | -0.24567 | -0.17944 | 60.5759 | -62.4985 | -0.064087 | -62.7045 | 60.5301 | 62.6221 | 62.5763 | 0.045776 | -0.082245 | 0.052338 | 0.28839 | -0.14313 | -0.15701 | -0.068665 | -0.09613 | -62.8647 | 60.4523 | 60.434 | 62.5031 | 62.6862 | 123.2849 | 62.6038 | 60.5621
2267.375 | 0.061035 | 0.43793 | -0.79468 | -0.23285 | 0.1474 | -0.28625 | -0.18372 | 60.6537 | -62.3611 | 0.13733 | -62.6266 | 60.4614 | 62.5763 | 62.5351 | 0.045776 | -0.098267 | 0.05661 | 0.27344 | -0.16449 | -0.15915 | 0.16022 | 0.25177 | -62.7228 | 60.4294 | 60.4294 | 62.4847 | 62.6587 | 123.3765 | 62.558 | 60.5118
2269.0312 | 0.045776 | 0.41657 | -0.78613 | -0.21362 | 0.15381 | -0.23819 | -0.18799 | 60.6308 | -62.4207 | 0.07782 | -62.6495 | 60.5209 | 62.5992 | 62.5442 | 0.061035 | -0.075836 | 0.0737 | 0.28946 | -0.14847 | -0.16983 | 0.032043 | 0.059509 | -62.8235 | 60.498 | 60.4706 | 62.4802 | 62.6816 | 123.381 | 62.5488 | 60.5392
2270.7031 | 0.061035 | 0.43579 | -0.79788 | -0.2179 | 0.15808 | -0.28946 | -0.18692 | 60.6354 | -62.3337 | 0.15564 | -62.6175 | 60.4523 | 62.5763 | 62.5488 | 0.061035 | -0.1004 | 0.066223 | 0.28198 | -0.16663 | -0.16449 | 0.15106 | 0.23346 | -62.7182 | 60.3836 | 60.4156 | 62.4939 | 62.677 | 123.3673 | 62.5488 | 60.5072
2272.375 | 0.045776 | 0.43472 | -0.77759 | -0.20828 | 0.15381 | -0.25742 | -0.17197 | 60.6445 | -62.3978 | 0.054932 | -62.6266 | 60.4477 | 62.5809 | 62.5076 | 0.045776 | -0.080109 | 0.064087 | 0.29587 | -0.15167 | -0.16235 | 0.022888 | 0.045776 | -62.7731 | 60.3882 | 60.3653 | 62.4893 | 62.6953 | 123.2574 | 62.5854 | 60.5347
2274.0469 | 0.076294 | 0.43366 | -0.79895 | -0.21683 | 0.15274 | -0.24887 | -0.17197 | 60.6262 | -62.3978 | 0.027466 | -62.6312 | 60.4797 | 62.6038 | 62.5259 | 0.061035 | -0.083313 | 0.065155 | 0.28305 | -0.14526 | -0.17303 | -0.004578 | 0.013733 | -62.7777 | 60.3973 | 60.3973 | 62.4847 | 62.6862 | 123.2758 | 62.5946 | 60.5118
2275.7188 | 0.061035 | 0.43472 | -0.80002 | -0.22858 | 0.16342 | -0.28519 | -0.1741 | 60.5759 | -62.4252 | 0.059509 | -62.6587 | 60.4614 | 62.5809 | 62.5671 | 0.076294 | -0.098267 | 0.075836 | 0.27771 | -0.16022 | -0.16022 | 0.068665 | 0.13733 | -62.7914 | 60.4156 | 60.4065 | 62.4847 | 62.709 | 123.3261 | 62.5626 | 60.498
2277.3906 | 0.076294 | 0.42511 | -0.78079 | -0.23071 | 0.1506 | -0.25955 | -0.18372 | 60.6125 | -62.4298 | 0.091553 | -62.6633 | 60.5164 | 62.6083 | 62.5442 | 0.061035 | -0.070496 | 0.075836 | 0.29159 | -0.16769 | -0.16983 | 0.054932 | 0.11902 | -62.8418 | 60.4614 | 60.4614 | 62.4802 | 62.6907 | 123.317 | 62.5442 | 60.5576
2279.0625 | 0.045776 | 0.44006 | -0.77972 | -0.1976 | 0.15381 | -0.2446 | -0.18051 | 60.553 | -62.5122 | -0.059509 | -62.6999 | 60.5392 | 62.6221 | 62.5397 | 0.045776 | -0.071564 | 0.067291 | 0.29266 | -0.14099 | -0.16342 | -0.073242 | -0.11902 | -62.9013 | 60.4889 | 60.4431 | 62.5214 | 62.6999 | 123.262 | 62.5854 | 60.5667
2280.75 | 0.076294 | 0.42938 | -0.79681 | -0.21362 | 0.15274 | -0.25742 | -0.16129 | 60.553 | -62.5031 | -0.045776 | -62.6907 | 60.5255 | 62.59 | 62.5534 | 0.045776 | -0.064087 | 0.059814 | 0.27985 | -0.13458 | -0.15595 | -0.068665 | -0.086975 | -62.8876 | 60.4523 | 60.4477 | 62.5031 | 62.7136 | 123.2849 | 62.5854 | 60.5392
2282.4062 | 0.061035 | 0.44113 | -0.80002 | -0.22324 | 0.13458 | -0.28519 | -0.18906 | 60.5759 | -62.3932 | 0.054932 | -62.6633 | 60.4385 | 62.6038 | 62.5168 | 0.045776 | -0.089722 | 0.061951 | 0.27878 | -0.15701 | -0.14847 | 0.018311 | 0.073242 | -62.7914 | 60.3836 | 60.3928 | 62.5076 | 62.6907 | 123.2208 | 62.5946 | 60.5438
2284.0625 | 0.076294 | 0.39093 | -0.78079 | -0.24246 | 0.16022 | -0.25207 | -0.16663 | 60.6216 | -62.4207 | 0.07782 | -62.6404 | 60.5438 | 62.5717 | 62.5351 | 0.061035 | -0.074768 | 0.086517 | 0.28732 | -0.15274 | -0.16983 | 0.027466 | 0.059509 | -62.8189 | 60.466 | 60.4385 | 62.4893 | 62.6907 | 123.3444 | 62.5305 | 60.5301
2285.7188 | 0.061035 | 0.43472 | -0.78079 | -0.20721 | 0.14954 | -0.25101 | -0.17303 | 60.5484 | -62.5031 | -0.059509 | -62.6862 | 60.5301 | 62.5946 | 62.5488 | 0.045776 | -0.071564 | 0.068359 | 0.29266 | -0.14633 | -0.16022 | -0.068665 | -0.086975 | -62.883 | 60.4523 | 60.4385 | 62.4985 | 62.6862 | 123.2712 | 62.5534 | 60.553
2287.4062 | 0.061035 | 0.43045 | -0.79468 | -0.22751 | 0.15808 | -0.28625 | -0.17838 | 60.6171 | -62.3337 | 0.16937 | -62.6175 | 60.4523 | 62.5763 | 62.5351 | 0.076294 | -0.093994 | 0.064087 | 0.28946 | -0.17517 | -0.15701 | 0.13275 | 0.24261 | -62.7548 | 60.4019 | 60.4202 | 62.4802 | 62.6724 | 123.3078 | 62.5442 | 60.5576
2289.0625 | 0.045776 | 0.40482 | -0.77652 | -0.22217 | 0.15701 | -0.25742 | -0.16983 | 60.5988 | -62.4207 | 0.073242 | -62.6266 | 60.5438 | 62.59 | 62.5351 | 0.030518 | -0.0737 | 0.083313 | 0.29159 | -0.14847 | -0.1709 | 0.032043 | 0.07782 | -62.8189 | 60.4523 | 60.4523 | 62.5076 | 62.6816 | 123.3627 | 62.5259 | 60.5118
2290.7188 | 0.045776 | 0.43152 | -0.79468 | -0.19653 | 0.16235 | -0.26382 | -0.18692 | 60.6033 | -62.3886 | 0.032043 | -62.6266 | 60.4614 | 62.5671 | 62.5259 | 0.061035 | -0.087585 | 0.059814 | 0.28625 | -0.15274 | -0.15488 | 0.004578 | 0.032043 | -62.7686 | 60.3928 | 60.3653 | 62.5031 | 62.6678 | 123.2712 | 62.5671 | 60.5347
2292.3906 | 0.061035 | 0.44861 | -0.80749 | -0.22217 | 0.15167 | -0.28732 | -0.17197 | 60.553 | -62.3886 | 0.041199 | -62.6633 | 60.4248 | 62.5854 | 62.5122 | 0.045776 | -0.087585 | 0.067291 | 0.27664 | -0.16022 | -0.15488 | 0.027466 | 0.068665 | -62.7869 | 60.3882 | 60.3836 | 62.4847 | 62.6816 | 123.2162 | 62.59 | 60.5072
2294.0469 | 0.030518 | 0.42191 | -0.78079 | -0.23926 | 0.16022 | -0.25635 | -0.17303 | 60.5621 | -62.4573 | 0.059509 | -62.6678 | 60.5347 | 62.5992 | 62.5351 | 0.076294 | -0.069427 | 0.065155 | 0.29587 | -0.16342 | -0.1474 | 0.018311 | 0.07782 | -62.851 | 60.4797 | 60.4568 | 62.4802 | 62.6495 | 123.3261 | 62.5214 | 60.5438
2295.7031 | 0.061035 | 0.42725 | -0.77545 | -0.22003 | 0.15808 | -0.23712 | -0.17303 | 60.5759 | -62.4344 | 0.018311 | -62.6587 | 60.5209 | 62.6038 | 62.5397 | 0.061035 | -0.070496 | 0.067291 | 0.27985 | -0.1442 | -0.15808 | -0.050354 | -0.041199 | -62.8738 | 60.434 | 60.4523 | 62.4893 | 62.6953 | 123.2117 | 62.5809 | 60.5667
2297.375 | 0.076294 | 0.42297 | -0.78827 | -0.21362 | 0.14526 | -0.2478 | -0.1741 | 60.5301 | -62.4893 | -0.068665 | -62.677 | 60.5026 | 62.59 | 62.5626 | 0.061035 | -0.082245 | 0.070496 | 0.28091 | -0.13779 | -0.14954 | -0.086975 | -0.10529 | -62.8738 | 60.4706 | 60.434 | 62.4939 | 62.6862 | 123.2529 | 62.5992 | 60.5301
2299.0625 | 0.045776 | 0.43152 | -0.78613 | -0.21683 | 0.15701 | -0.2681 | -0.1709 | 60.5392 | -62.4802 | -0.045776 | -62.7045 | 60.498 | 62.5946 | 62.5671 | 0.076294 | -0.077972 | 0.065155 | 0.29266 | -0.15488 | -0.15915 | -0.086975 | -0.082397 | -62.8555 | 60.4431 | 60.4294 | 62.5076 | 62.6678 | 123.2574 | 62.5763 | 60.5209
2300.7344 | 0.045776 | 0.4454 | -0.79681 | -0.24567 | 0.14313 | -0.29053 | -0.1741 | 60.5438 | -62.4252 | 0.054932 | -62.6404 | 60.4568 | 62.5763 | 62.5305 | 0.061035 | -0.099335 | 0.074768 | 0.27664 | -0.16876 | -0.1506 | 0.045776 | 0.12817 | -62.7869 | 60.4156 | 60.3973 | 62.4756 | 62.6678 | 123.3078 | 62.5809 | 60.5164
2302.4062 | 0.076294 | 0.42725 | -0.78079 | -0.23178 | 0.16342 | -0.25421 | -0.17303 | 60.585 | -62.4481 | 0.064087 | -62.6495 | 60.5301 | 62.5671 | 62.5214 | 0.045776 | -0.064087 | 0.072632 | 0.29694 | -0.15488 | -0.16983 | 0.018311 | 0.082397 | -62.8189 | 60.4614 | 60.4843 | 62.4573 | 62.6633 | 123.3398 | 62.5259 | 60.5438
2304.1094 | 0.045776 | 0.41977 | -0.7872 | -0.21896 | 0.15595 | -0.26062 | -0.1709 | 60.6033 | -62.4069 | 0.07782 | -62.6221 | 60.5118 | 62.5717 | 62.558 | 0.045776 | -0.071564 | 0.0737 | 0.28732 | -0.1442 | -0.15915 | 0.022888 | 0.068665 | -62.8098 | 60.4568 | 60.466 | 62.4893 | 62.6587 | 123.3307 | 62.5305 | 60.5438
2305.7812 | 0.061035 | 0.42831 | -0.7872 | -0.20294 | 0.15488 | -0.26596 | -0.16663 | 60.5392 | -62.471 | -0.045776 | -62.677 | 60.5118 | 62.5992 | 62.5442 | 0.045776 | -0.084381 | 0.071564 | 0.28732 | -0.1442 | -0.1474 | -0.064087 | -0.059509 | -62.8326 | 60.4111 | 60.4248 | 62.5031 | 62.677 | 123.2483 | 62.5809 | 60.4889
2307.4375 | 0.045776 | 0.43259 | -0.80856 | -0.22324 | 0.15381 | -0.29587 | -0.18051 | 60.5392 | -62.4069 | 0.050354 | -62.645 | 60.4431 | 62.5671 | 62.5488 | 0.030518 | -0.098267 | 0.061951 | 0.28198 | -0.17303 | -0.15595 | 0.045776 | 0.1236 | -62.7686 | 60.4019 | 60.4065 | 62.4802 | 62.677 | 123.3032 | 62.5397 | 60.5026
2309.0938 | 0.045776 | 0.40695 | -0.77759 | -0.22003 | 0.15595 | -0.24674 | -0.16769 | 60.6171 | -62.4161 | 0.07782 | -62.6221 | 60.498 | 62.5626 | 62.5305 | 0.061035 | -0.074768 | 0.072632 | 0.29159 | -0.14313 | -0.16022 | 0.036621 | 0.07782 | -62.8006 | 60.466 | 60.4385 | 62.4893 | 62.677 | 123.3307 | 62.5351 | 60.5347
2310.7656 | 0.030518 | 0.44006 | -0.78507 | -0.21469 | 0.1506 | -0.26916 | -0.18478 | 60.5667 | -62.4298 | -0.004578 | -62.6404 | 60.4477 | 62.5992 | 62.5351 | 0.045776 | -0.088654 | 0.071564 | 0.2948 | -0.15274 | -0.14633 | -0.009155 | 0.004578 | -62.7777 | 60.379 | 60.3882 | 62.4893 | 62.6633 | 123.2437 | 62.558 | 60.5118
2312.4375 | 0.061035 | 0.43366 | -0.7872 | -0.23498 | 0.14847 | -0.29373 | -0.18051 | 60.64 | -62.2971 | 0.17395 | -62.5946 | 60.434 | 62.5488 | 62.4939 | 0.061035 | -0.093994 | 0.058746 | 0.28305 | -0.17624 | -0.16342 | 0.14191 | 0.24261 | -62.7136 | 60.3928 | 60.3882 | 62.4619 | 62.6541 | 123.3124 | 62.5442 | 60.4843
2314.0938 | 0.061035 | 0.41443 | -0.77331 | -0.2179 | 0.15274 | -0.25528 | -0.16876 | 60.6308 | -62.3886 | 0.059509 | -62.6266 | 60.5164 | 62.5488 | 62.5305 | 0.045776 | -0.069427 | 0.065155 | 0.29907 | -0.15167 | -0.16876 | 0.036621 | 0.064087 | -62.796 | 60.4614 | 60.4568 | 62.4756 | 62.6587 | 123.2941 | 62.5259 | 60.5209
2315.7656 | 0.076294 | 0.43686 | -0.784 | -0.22751 | 0.15595 | -0.29053 | -0.16983 | 60.5576 | -62.4161 | 0.045776 | -62.645 | 60.4385 | 62.5671 | 62.5122 | 0.061035 | -0.098267 | 0.0737 | 0.28305 | -0.16876 | -0.15381 | 0.022888 | 0.064087 | -62.8006 | 60.3973 | 60.3745 | 62.4893 | 62.6678 | 123.2117 | 62.5809 | 60.5209
2317.4375 | 0.045776 | 0.439 | -0.78293 | -0.22644 | 0.15808 | -0.28625 | -0.18158 | 60.6354 | -62.3245 | 0.16937 | -62.5992 | 60.4523 | 62.5214 | 62.4893 | 0.045776 | -0.09613 | 0.063019 | 0.28091 | -0.16876 | -0.1474 | 0.14648 | 0.24719 | -62.7228 | 60.4202 | 60.379 | 62.4435 | 62.6404 | 123.2849 | 62.4985 | 60.5209
2319.0938 | 0.061035 | 0.41122 | -0.78186 | -0.20828 | 0.15595 | -0.23178 | -0.16876 | 60.6308 | -62.3932 | 0.059509 | -62.6221 | 60.498 | 62.5717 | 62.5259 | 0.061035 | -0.072632 | 0.074768 | 0.28412 | -0.13992 | -0.17517 | 0.004578 | 0.022888 | -62.8052 | 60.4294 | 60.4248 | 62.4756 | 62.6953 | 123.2483 | 62.5397 | 60.5392
2320.75 | 0.076294 | 0.44754 | -0.79361 | -0.2179 | 0.13672 | -0.28198 | -0.1741 | 60.5576 | -62.3703 | 0.059509 | -62.6541 | 60.4523 | 62.5488 | 62.5214 | 0.045776 | -0.09613 | 0.058746 | 0.29373 | -0.15167 | -0.15274 | 0.022888 | 0.082397 | -62.7914 | 60.3882 | 60.3561 | 62.4756 | 62.6541 | 123.2025 | 62.5717 | 60.5209
2322.4375 | 0.045776 | 0.41763 | -0.78079 | -0.21042 | 0.15274 | -0.24994 | -0.16876 | 60.6308 | -62.3749 | 0.073242 | -62.6175 | 60.4935 | 62.5809 | 62.5122 | 0.045776 | -0.066223 | 0.0737 | 0.29053 | -0.1442 | -0.16663 | 0.022888 | 0.036621 | -62.8006 | 60.434 | 60.4431 | 62.4664 | 62.6587 | 123.2758 | 62.5259 | 60.5164
2324.1094 | 0.061035 | 0.43259 | -0.79147 | -0.20935 | 0.14313 | -0.25635 | -0.16769 | 60.5576 | -62.4252 | -0.009155 | -62.645 | 60.4614 | 62.5488 | 62.5031 | 0.061035 | -0.087585 | 0.072632 | 0.28519 | -0.14206 | -0.15167 | -0.009155 | 0.013733 | -62.7823 | 60.3745 | 60.3745 | 62.4893 | 62.6404 | 123.2483 | 62.5717 | 60.498
2325.7812 | 0.045776 | 0.42191 | -0.79681 | -0.23926 | 0.14954 | -0.28625 | -0.17197 | 60.5988 | -62.3154 | 0.17853 | -62.5763 | 60.4156 | 62.5854 | 62.5122 | 0.061035 | -0.086517 | 0.0737 | 0.28839 | -0.16235 | -0.15808 | 0.13733 | 0.23804 | -62.709 | 60.3973 | 60.3836 | 62.4619 | 62.6495 | 123.2758 | 62.5305 | 60.5026
2327.4531 | 0.030518 | 0.43045 | -0.78293 | -0.23712 | 0.1442 | -0.27237 | -0.18585 | 60.585 | -62.3566 | 0.13733 | -62.6129 | 60.4706 | 62.5671 | 62.4985 | 0.061035 | -0.09079 | 0.070496 | 0.28198 | -0.15808 | -0.15488 | 0.064087 | 0.13275 | -62.8052 | 60.4294 | 60.4385 | 62.4664 | 62.6816 | 123.2666 | 62.5214 | 60.5392
2329.125 | 0.045776 | 0.42831 | -0.78613 | -0.21042 | 0.15808 | -0.24353 | -0.16235 | 60.6308 | -62.3703 | 0.07782 | -62.5946 | 60.5026 | 62.5671 | 62.5259 | 0.061035 | -0.076904 | 0.076904 | 0.29587 | -0.13351 | -0.16983 | 0.013733 | 0.041199 | -62.8006 | 60.434 | 60.4202 | 62.471 | 62.6862 | 123.2666 | 62.5488 | 60.5118
2330.7969 | 0.045776 | 0.42938 | -0.78507 | -0.24033 | 0.15274 | -0.28625 | -0.18158 | 60.6033 | -62.3016 | 0.17853 | -62.59 | 60.4294 | 62.5397 | 62.4802 | 0.045776 | -0.095062 | 0.061951 | 0.28091 | -0.16235 | -0.15808 | 0.13733 | 0.26093 | -62.7136 | 60.3928 | 60.3745 | 62.4527 | 62.645 | 123.2803 | 62.4893 | 60.5026
2332.4688 | 0.030518 | 0.42511 | -0.77972 | -0.2211 | 0.14847 | -0.24674 | -0.17731 | 60.5164 | -62.4756 | -0.054932 | -62.677 | 60.5209 | 62.5717 | 62.5259 | 0.061035 | -0.063019 | 0.075836 | 0.29694 | -0.13672 | -0.16129 | -0.073242 | -0.07782 | -62.8693 | 60.4568 | 60.4385 | 62.4619 | 62.6541 | 123.1842 | 62.5717 | 60.5209
2334.125 | 0.061035 | 0.41977 | -0.7872 | -0.23071 | 0.15701 | -0.27023 | -0.16983 | 60.553 | -62.3657 | 0.10986 | -62.6358 | 60.4797 | 62.5809 | 62.5031 | 0.045776 | -0.087585 | 0.067291 | 0.28412 | -0.15488 | -0.1506 | 0.050354 | 0.12817 | -62.8098 | 60.4706 | 60.4523 | 62.4893 | 62.6724 | 123.2437 | 62.5076 | 60.5255
2335.7812 | 0.061035 | 0.44434 | -0.7872 | -0.19867 | 0.14206 | -0.25955 | -0.17517 | 60.585 | -62.3703 | 0.032043 | -62.6175 | 60.4477 | 62.5626 | 62.5259 | 0.045776 | -0.086517 | 0.050201 | 0.28519 | -0.13565 | -0.15595 | 0.009155 | 0.036621 | -62.7411 | 60.379 | 60.379 | 62.4802 | 62.6495 | 123.2208 | 62.5717 | 60.498
2337.4375 | 0.076294 | 0.44434 | -0.80322 | -0.22003 | 0.14313 | -0.28946 | -0.18585 | 60.553 | -62.3978 | 0.027466 | -62.6495 | 60.4752 | 62.5351 | 62.5122 | 0.076294 | -0.080109 | 0.059814 | 0.28198 | -0.17303 | -0.15701 | 0.013733 | 0.091553 | -62.7869 | 60.379 | 60.4156 | 62.471 | 62.6633 | 123.2117 | 62.5534 | 60.5026
2339.0938 | 0.045776 | 0.40161 | -0.77972 | -0.2211 | 0.15808 | -0.2446 | -0.16556 | 60.6216 | -62.384 | 0.07782 | -62.6129 | 60.4889 | 62.5534 | 62.4985 | 0.030518 | -0.060883 | 0.065155 | 0.28198 | -0.14526 | -0.16876 | 0.013733 | 0.041199 | -62.8052 | 60.4523 | 60.4294 | 62.4619 | 62.6678 | 123.2529 | 62.5442 | 60.5118
2340.7656 | 0.045776 | 0.41122 | -0.77438 | -0.22217 | 0.15167 | -0.24674 | -0.15915 | 60.6079 | -62.3657 | 0.086975 | -62.6175 | 60.5026 | 62.5717 | 62.5076 | 0.045776 | -0.071564 | 0.063019 | 0.27557 | -0.1442 | -0.15701 | 0.032043 | 0.059509 | -62.7823 | 60.4431 | 60.4111 | 62.4802 | 62.6358 | 123.2758 | 62.5168 | 60.5209
2342.4219 | 0.061035 | 0.44327 | -0.79361 | -0.22324 | 0.16129 | -0.26916 | -0.17197 | 60.5804 | -62.3383 | 0.050354 | -62.5946 | 60.4294 | 62.5488 | 62.5031 | 0.030518 | -0.091858 | 0.061951 | 0.29266 | -0.15274 | -0.15915 | 0.013733 | 0.041199 | -62.7502 | 60.3699 | 60.3424 | 62.4893 | 62.6541 | 123.2025 | 62.5488 | 60.5209
2344.0781 | 0.061035 | 0.45075 | -0.79468 | -0.20294 | 0.14633 | -0.28091 | -0.16449 | 60.5713 | -62.3474 | 0.054932 | -62.6266 | 60.3973 | 62.5717 | 62.5031 | 0.045776 | -0.092926 | 0.066223 | 0.27451 | -0.1506 | -0.15167 | 0.032043 | 0.059509 | -62.7594 | 60.3607 | 60.3516 | 62.4435 | 62.6724 | 123.1384 | 62.5809 | 60.498
2345.75 | 0.061035 | 0.40161 | -0.78186 | -0.22537 | 0.15595 | -0.24674 | -0.1741 | 60.6262 | -62.3886 | 0.07782 | -62.6175 | 60.466 | 62.5488 | 62.5031 | 0.061035 | -0.061951 | 0.074768 | 0.28305 | -0.1442 | -0.1709 | -0.018311 | 0.041199 | -62.796 | 60.4568 | 60.4156 | 62.4527 | 62.6404 | 123.2254 | 62.5534 | 60.5255
2347.4219 | 0.061035 | 0.42191 | -0.79468 | -0.20721 | 0.15595 | -0.26169 | -0.1741 | 60.5438 | -62.4435 | -0.041199 | -62.6678 | 60.4843 | 62.5854 | 62.5351 | 0.045776 | -0.083313 | 0.069427 | 0.27771 | -0.14526 | -0.15808 | -0.036621 | -0.050354 | -62.8006 | 60.3973 | 60.3836 | 62.4893 | 62.6495 | 123.2162 | 62.5626 | 60.4797
2349.0938 | 0.061035 | 0.41229 | -0.79041 | -0.21255 | 0.15915 | -0.24353 | -0.1709 | 60.5621 | -62.4023 | 0.027466 | -62.6266 | 60.4752 | 62.5488 | 62.5122 | 0.061035 | -0.077972 | 0.070496 | 0.27664 | -0.13458 | -0.16342 | -0.064087 | -0.041199 | -62.8464 | 60.4065 | 60.4248 | 62.4756 | 62.6678 | 123.1705 | 62.5763 | 60.5392
2350.7656 | 0.061035 | 0.42618 | -0.78934 | -0.21896 | 0.15701 | -0.26276 | -0.1741 | 60.5118 | -62.4664 | -0.045776 | -62.6633 | 60.4843 | 62.5763 | 62.5259 | 0.061035 | -0.076904 | 0.067291 | 0.28625 | -0.14099 | -0.15595 | -0.09613 | -0.10529 | -62.8647 | 60.4294 | 60.4111 | 62.4939 | 62.6724 | 123.1888 | 62.5671 | 60.498
2352.4219 | 0.030518 | 0.46036 | -0.79681 | -0.22324 | 0.13886 | -0.29159 | -0.18692 | 60.5255 | -62.3932 | 0.036621 | -62.6358 | 60.4294 | 62.558 | 62.5076 | 0.045776 | -0.10788 | 0.063019 | 0.28198 | -0.17197 | -0.15274 | 0.009155 | 0.091553 | -62.7777 | 60.3516 | 60.3653 | 62.4664 | 62.6587 | 123.2025 | 62.5534 | 60.5072
2354.0781 | 0.076294 | 0.4155 | -0.78827 | -0.23605 | 0.16235 | -0.2478 | -0.16769 | 60.5392 | -62.439 | 0.068665 | -62.6175 | 60.4843 | 62.5305 | 62.5259 | 0.061035 | -0.077972 | 0.071564 | 0.28839 | -0.16876 | -0.16983 | 0.009155 | 0.07782 | -62.8052 | 60.4385 | 60.434 | 62.4527 | 62.6678 | 123.317 | 62.5122 | 60.4889
2355.75 | 0.045776 | 0.42618 | -0.76797 | -0.22217 | 0.16235 | -0.24674 | -0.16663 | 60.5026 | -62.4664 | -0.027466 | -62.6495 | 60.5026 | 62.5763 | 62.5122 | 0.015259 | -0.079041 | 0.077972 | 0.30014 | -0.1506 | -0.16983 | -0.1236 | -0.09613 | -62.8784 | 60.4431 | 60.4294 | 62.4573 | 62.6816 | 123.1567 | 62.5442 | 60.5255
2357.4219 | 0.045776 | 0.44113 | -0.78293 | -0.22324 | 0.14847 | -0.29159 | -0.18585 | 60.5301 | -62.3886 | 0.041199 | -62.6404 | 60.4065 | 62.5442 | 62.5122 | 0.045776 | -0.091858 | 0.069427 | 0.27985 | -0.17197 | -0.1506 | 0.009155 | 0.07782 | -62.7777 | 60.3882 | 60.3836 | 62.4573 | 62.6678 | 123.1842 | 62.5397 | 60.498
2359.0781 | 0.061035 | 0.42511 | -0.79361 | -0.24674 | 0.16769 | -0.26062 | -0.17731 | 60.5301 | -62.4252 | 0.07782 | -62.6312 | 60.4797 | 62.5442 | 62.5076 | 0.030518 | -0.086517 | 0.068359 | 0.29587 | -0.16235 | -0.16449 | 0.045776 | 0.10071 | -62.8006 | 60.4477 | 60.4614 | 62.471 | 62.645 | 123.2391 | 62.5168 | 60.5301
2360.75 | 0.061035 | 0.43045 | -0.78507 | -0.20721 | 0.15595 | -0.25848 | -0.18051 | 60.5392 | -62.4344 | -0.041199 | -62.6678 | 60.4889 | 62.5854 | 62.4893 | 0.076294 | -0.071564 | 0.058746 | 0.28839 | -0.14206 | -0.15274 | -0.068665 | -0.086975 | -62.8281 | 60.4019 | 60.4156 | 62.471 | 62.6587 | 123.1888 | 62.5626 | 60.5072
2362.4219 | 0.045776 | 0.43793 | -0.78079 | -0.21683 | 0.14633 | -0.2446 | -0.17838 | 60.5255 | -62.439 | -0.036621 | -62.6587 | 60.498 | 62.5626 | 62.5076 | 0.015259 | -0.069427 | 0.067291 | 0.28305 | -0.1474 | -0.17197 | -0.073242 | -0.086975 | -62.8326 | 60.4111 | 60.3973 | 62.4893 | 62.677 | 123.1979 | 62.5626 | 60.5072
2364.0781 | 0.061035 | 0.46997 | -0.80215 | -0.21576 | 0.14633 | -0.29373 | -0.19012 | 60.5255 | -62.352 | 0.064087 | -62.6083 | 60.434 | 62.5351 | 62.4802 | 0.045776 | -0.10788 | 0.05661 | 0.28412 | -0.15701 | -0.14099 | 0.07782 | 0.15106 | -62.7411 | 60.3653 | 60.379 | 62.4619 | 62.6404 | 123.262 | 62.5076 | 60.4843
2365.7344 | 0.061035 | 0.42404 | -0.7872 | -0.24033 | 0.14313 | -0.25955 | -0.16663 | 60.5484 | -62.4298 | 0.045776 | -62.6038 | 60.4843 | 62.558 | 62.4893 | 0.045776 | -0.079041 | 0.063019 | 0.29159 | -0.16022 | -0.1709 | 0.022888 | 0.09613 | -62.8143 | 60.4523 | 60.4614 | 62.439 | 62.6633 | 123.2941 | 62.471 | 60.5255
2367.3906 | 0.061035 | 0.43793 | -0.79681 | -0.21042 | 0.1474 | -0.25101 | -0.1709 | 60.5255 | -62.439 | -0.041199 | -62.6633 | 60.4797 | 62.5351 | 62.5397 | 0.061035 | -0.091858 | 0.066223 | 0.28625 | -0.13886 | -0.15915 | -0.064087 | -0.082397 | -62.8189 | 60.4065 | 60.3836 | 62.4756 | 62.6587 | 123.2025 | 62.5626 | 60.498
2369.0625 | 0.045776 | 0.42618 | -0.79788 | -0.23285 | 0.15381 | -0.24674 | -0.17838 | 60.5255 | -62.4252 | 0.073242 | -62.6175 | 60.4935 | 62.5488 | 62.4985 | 0.061035 | -0.074768 | 0.069427 | 0.29266 | -0.16022 | -0.16129 | 0.032043 | 0.059509 | -62.8006 | 60.4523 | 60.4248 | 62.4481 | 62.6312 | 123.2941 | 62.4847 | 60.498
2370.7344 | 0.030518 | 0.42831 | -0.7872 | -0.21896 | 0.14847 | -0.26382 | -0.17944 | 60.5118 | -62.4573 | -0.054932 | -62.6678 | 60.4752 | 62.5626 | 62.5214 | 0.045776 | -0.075836 | 0.061951 | 0.29053 | -0.15274 | -0.15595 | -0.091553 | -0.09613 | -62.8464 | 60.4156 | 60.434 | 62.471 | 62.6633 | 123.1842 | 62.5442 | 60.498
2372.4062 | 0.076294 | 0.42297 | -0.80002 | -0.23819 | 0.14313 | -0.2713 | -0.18158 | 60.5255 | -62.4298 | 0.050354 | -62.6266 | 60.5164 | 62.5763 | 62.5168 | 0.076294 | -0.072632 | 0.064087 | 0.28091 | -0.16449 | -0.16983 | 0.022888 | 0.07782 | -62.8143 | 60.4477 | 60.4431 | 62.4481 | 62.6495 | 123.2483 | 62.4985 | 60.5072
2374.0625 | 0.030518 | 0.39627 | -0.78079 | -0.23178 | 0.15808 | -0.24887 | -0.16876 | 60.5438 | -62.4207 | 0.009155 | -62.6358 | 60.4752 | 62.5259 | 62.4985 | 0.061035 | -0.071564 | 0.080109 | 0.30121 | -0.15915 | -0.16449 | -0.068665 | -0.036621 | -62.8326 | 60.4202 | 60.4385 | 62.4756 | 62.6678 | 123.1384 | 62.5397 | 60.5392
2375.7344 | 0.045776 | 0.43366 | -0.79468 | -0.22324 | 0.14847 | -0.28732 | -0.17731 | 60.5713 | -62.3245 | 0.059509 | -62.6038 | 60.4065 | 62.5397 | 62.4847 | 0.045776 | -0.093994 | 0.052338 | 0.28305 | -0.15915 | -0.15381 | 0.032043 | 0.064087 | -62.7319 | 60.3333 | 60.3607 | 62.4756 | 62.6678 | 123.1201 | 62.5442 | 60.5026
2377.4062 | 0.030518 | 0.42404 | -0.784 | -0.24139 | 0.14954 | -0.27237 | -0.17944 | 60.5255 | -62.3978 | 0.07782 | -62.645 | 60.5026 | 62.5534 | 62.5031 | 0.061035 | -0.091858 | 0.077972 | 0.27985 | -0.16769 | -0.15595 | 0.027466 | 0.086975 | -62.8098 | 60.4477 | 60.4248 | 62.4985 | 62.645 | 123.2574 | 62.4847 | 60.5072
2379.0781 | 0.091553 | 0.44968 | -0.80002 | -0.22537 | 0.14847 | -0.27771 | -0.17944 | 60.5392 | -62.3428 | 0.045776 | -62.6358 | 60.4202 | 62.5305 | 62.4756 | 0.076294 | -0.09613 | 0.060883 | 0.27985 | -0.16022 | -0.15381 | 0.022888 | 0.082397 | -62.7457 | 60.3561 | 60.3699 | 62.439 | 62.6358 | 123.143 | 62.5351 | 60.5026
2380.7344 | 0.030518 | 0.41977 | -0.79681 | -0.24887 | 0.16022 | -0.2681 | -0.18372 | 60.553 | -62.3657 | 0.10529 | -62.6129 | 60.4752 | 62.5305 | 62.4893 | 0.061035 | -0.080109 | 0.074768 | 0.29053 | -0.16449 | -0.16342 | 0.045776 | 0.11444 | -62.8006 | 60.434 | 60.4156 | 62.4619 | 62.6404 | 123.2208 | 62.5031 | 60.5118
2382.4375 | 0.045776 | 0.43686 | -0.78507 | -0.22964 | 0.14526 | -0.28732 | -0.17944 | 60.5072 | -62.384 | 0.045776 | -62.6221 | 60.4568 | 62.5534 | 62.4802 | 0.061035 | -0.099335 | 0.067291 | 0.29053 | -0.16556 | -0.15915 | 0.041199 | 0.10986 | -62.7548 | 60.3745 | 60.3745 | 62.4573 | 62.6358 | 123.2071 | 62.5351 | 60.5026
2384.1094 | 0.061035 | 0.4187 | -0.78079 | -0.24033 | 0.15381 | -0.26489 | -0.18585 | 60.5576 | -62.3566 | 0.10986 | -62.6083 | 60.4843 | 62.5351 | 62.471 | 0.076294 | -0.072632 | 0.067291 | 0.28412 | -0.16342 | -0.1709 | 0.050354 | 0.10986 | -62.8006 | 60.4431 | 60.4248 | 62.4619 | 62.645 | 123.2162 | 62.4985 | 60.5301
2385.7812 | 0.045776 | 0.43472 | -0.78079 | -0.20615 | 0.15274 | -0.25314 | -0.16342 | 60.5255 | -62.4298 | -0.050354 | -62.6541 | 60.466 | 62.5854 | 62.5076 | 0.045776 | -0.079041 | 0.064087 | 0.28412 | -0.13886 | -0.15808 | -0.041199 | -0.073242 | -62.8098 | 60.4065 | 60.3836 | 62.4664 | 62.6312 | 123.1934 | 62.5351 | 60.5026
2387.4531 | 0.030518 | 0.41443 | -0.77545 | -0.22003 | 0.15167 | -0.23819 | -0.16342 | 60.5576 | -62.3886 | 0.022888 | -62.6175 | 60.4843 | 62.5351 | 62.4893 | 0.045776 | -0.0737 | 0.063019 | 0.29373 | -0.13886 | -0.16663 | -0.045776 | -0.032043 | -62.8143 | 60.4385 | 60.4065 | 62.471 | 62.6587 | 123.143 | 62.5488 | 60.5118
2389.1094 | 0.091553 | 0.42191 | -0.78079 | -0.20294 | 0.15595 | -0.25848 | -0.16235 | 60.4752 | -62.4802 | -0.032043 | -62.645 | 60.4889 | 62.558 | 62.4756 | 0.045776 | -0.066223 | 0.065155 | 0.29053 | -0.13992 | -0.15915 | -0.073242 | -0.082397 | -62.8464 | 60.4248 | 60.4019 | 62.4527 | 62.6633 | 123.1567 | 62.5488 | 60.498
2390.7812 | 0.045776 | 0.43045 | -0.79575 | -0.23712 | 0.14633 | -0.29159 | -0.17731 | 60.5347 | -62.3611 | 0.064087 | -62.59 | 60.4248 | 62.5351 | 62.4802 | 0.045776 | -0.091858 | 0.052338 | 0.27237 | -0.17517 | -0.14633 | 0.068665 | 0.14648 | -62.7274 | 60.3653 | 60.3653 | 62.439 | 62.6266 | 123.2254 | 62.5168 | 60.4935
2392.4688 | 0.045776 | 0.42404 | -0.784 | -0.23178 | 0.14847 | -0.24567 | -0.18051 | 60.5072 | -62.4573 | -0.059509 | -62.6541 | 60.4889 | 62.5671 | 62.4985 | 0.061035 | -0.065155 | 0.061951 | 0.29159 | -0.15701 | -0.15808 | -0.082397 | -0.09613 | -62.8372 | 60.4156 | 60.4202 | 62.4527 | 62.6633 | 123.1567 | 62.5534 | 60.5255
2394.125 | 0.061035 | 0.43045 | -0.79681 | -0.23819 | 0.15595 | -0.28625 | -0.19012 | 60.5942 | -62.2696 | 0.17395 | -62.5671 | 60.4156 | 62.5122 | 62.4619 | 0.061035 | -0.10147 | 0.057678 | 0.27878 | -0.17197 | -0.15274 | 0.13733 | 0.24261 | -62.6724 | 60.3607 | 60.3516 | 62.4527 | 62.6175 | 123.2483 | 62.5031 | 60.4614
2395.7812 | 0.061035 | 0.42725 | -0.78293 | -0.23498 | 0.15595 | -0.27451 | -0.17731 | 60.5301 | -62.384 | 0.041199 | -62.6129 | 60.4385 | 62.5351 | 62.4939 | 0.061035 | -0.092926 | 0.059814 | 0.29053 | -0.16876 | -0.1474 | 0.032043 | 0.064087 | -62.7457 | 60.347 | 60.3516 | 62.4527 | 62.6083 | 123.1567 | 62.5305 | 60.498
2397.4531 | 0.030518 | 0.44647 | -0.78827 | -0.22858 | 0.16663 | -0.28091 | -0.18051 | 60.6216 | -62.2833 | 0.17395 | -62.5671 | 60.4202 | 62.5214 | 62.4893 | 0.061035 | -0.088654 | 0.067291 | 0.29373 | -0.16769 | -0.1741 | 0.16022 | 0.23804 | -62.6862 | 60.3561 | 60.3516 | 62.4161 | 62.6038 | 123.2208 | 62.471 | 60.4843
2399.125 | 0.045776 | 0.41763 | -0.78827 | -0.22217 | 0.15488 | -0.24139 | -0.17517 | 60.5713 | -62.3749 | 0.064087 | -62.59 | 60.498 | 62.5351 | 62.4985 | 0.045776 | -0.069427 | 0.064087 | 0.28412 | -0.14526 | -0.17517 | 0.054932 | 0.068665 | -62.7823 | 60.4248 | 60.4111 | 62.4344 | 62.645 | 123.2529 | 62.471 | 60.4706
2400.7969 | 0.045776 | 0.42084 | -0.78827 | -0.21469 | 0.15274 | -0.25314 | -0.1741 | 60.5621 | -62.3474 | 0.018311 | -62.6038 | 60.434 | 62.5442 | 62.4939 | 0.076294 | -0.083313 | 0.059814 | 0.28198 | -0.14633 | -0.15915 | 0.018311 | 0.022888 | -62.7228 | 60.3607 | 60.3516 | 62.4573 | 62.6083 | 123.1659 | 62.5397 | 60.4752
2402.5 | 0.045776 | 0.41229 | -0.7872 | -0.23498 | 0.1442 | -0.26062 | -0.17517 | 60.5118 | -62.3886 | 0.059509 | -62.6129 | 60.5072 | 62.558 | 62.4802 | 0.061035 | -0.079041 | 0.071564 | 0.27771 | -0.15381 | -0.16022 | 0.022888 | 0.068665 | -62.8098 | 60.434 | 60.4202 | 62.4481 | 62.6358 | 123.2391 | 62.471 | 60.498
2404.1562 | 0.045776 | 0.4187 | -0.78507 | -0.22003 | 0.14313 | -0.25207 | -0.16983 | 60.553 | -62.352 | 0.073242 | -62.5854 | 60.4935 | 62.5442 | 62.4847 | 0.045776 | -0.070496 | 0.075836 | 0.27985 | -0.14633 | -0.15808 | 0.045776 | 0.082397 | -62.7548 | 60.4248 | 60.4248 | 62.4344 | 62.6358 | 123.2346 | 62.4802 | 60.4889
2405.8281 | 0.061035 | 0.42511 | -0.77652 | -0.23071 | 0.15167 | -0.25742 | -0.18265 | 60.4935 | -62.3932 | -0.004578 | -62.6175 | 60.4568 | 62.5488 | 62.4847 | 0.061035 | -0.076904 | 0.069427 | 0.29587 | -0.14099 | -0.16342 | -0.07782 | -0.068665 | -62.8372 | 60.4202 | 60.4065 | 62.4481 | 62.6404 | 123.1247 | 62.5397 | 60.4935
2407.5625 | 0.076294 | 0.43472 | -0.76904 | -0.22324 | 0.15167 | -0.25848 | -0.17197 | 60.585 | -62.3428 | 0.07782 | -62.5946 | 60.4523 | 62.5076 | 62.471 | 0.045776 | -0.0737 | 0.072632 | 0.30334 | -0.15167 | -0.16235 | 0.027466 | 0.045776 | -62.7548 | 60.3973 | 60.4065 | 62.4344 | 62.6221 | 123.2208 | 62.5076 | 60.4889
2409.2344 | 0.030518 | 0.43793 | -0.79041 | -0.21469 | 0.1442 | -0.29907 | -0.17731 | 60.5118 | -62.3428 | 0.07782 | -62.6083 | 60.3928 | 62.4939 | 62.4664 | 0.030518 | -0.10254 | 0.054474 | 0.28305 | -0.16556 | -0.15381 | 0.027466 | 0.073242 | -62.7411 | 60.3561 | 60.3424 | 62.4481 | 62.6495 | 123.1018 | 62.5351 | 60.5118
2410.9062 | 0.045776 | 0.42191 | -0.79254 | -0.23498 | 0.1506 | -0.27344 | -0.18372 | 60.5209 | -62.4023 | 0.041199 | -62.5992 | 60.4614 | 62.5214 | 62.4664 | 0.045776 | -0.068359 | 0.076904 | 0.29053 | -0.16235 | -0.16022 | 0.022888 | 0.073242 | -62.7869 | 60.4477 | 60.4248 | 62.4435 | 62.6266 | 123.2391 | 62.471 | 60.4843
2412.6094 | 0.045776 | 0.42404 | -0.79788 | -0.22858 | 0.16342 | -0.28091 | -0.17838 | 60.5438 | -62.3383 | 0.1236 | -62.5854 | 60.4568 | 62.5214 | 62.4893 | 0.045776 | -0.087585 | 0.066223 | 0.2681 | -0.16129 | -0.16342 | 0.050354 | 0.14191 | -62.7731 | 60.4202 | 60.4065 | 62.4619 | 62.6266 | 123.1979 | 62.471 | 60.5072
2414.2656 | 0.061035 | 0.43472 | -0.78827 | -0.21469 | 0.15808 | -0.25528 | -0.17624 | 60.4889 | -62.4252 | -0.059509 | -62.645 | 60.4843 | 62.5397 | 62.5214 | 0.045776 | -0.084381 | 0.069427 | 0.2948 | -0.13886 | -0.16022 | -0.07782 | -0.11444 | -62.8281 | 60.4156 | 60.4065 | 62.4435 | 62.6541 | 123.1613 | 62.5305 | 60.5072
2415.9219 | 0.061035 | 0.44327 | -0.79681 | -0.21683 | 0.14847 | -0.28732 | -0.17624 | 60.553 | -62.3108 | 0.068665 | -62.59 | 60.3928 | 62.5259 | 62.4802 | 0.061035 | -0.10147 | 0.066223 | 0.28519 | -0.15274 | -0.15701 | 0.036621 | 0.068665 | -62.7274 | 60.3195 | 60.3241 | 62.4161 | 62.6312 | 123.0972 | 62.5305 | 60.4843
2417.625 | 0.061035 | 0.42725 | -0.7872 | -0.22751 | 0.14847 | -0.25528 | -0.17838 | 60.5118 | -62.384 | 0.045776 | -62.6129 | 60.4752 | 62.5488 | 62.4619 | 0.061035 | -0.079041 | 0.061951 | 0.28091 | -0.15274 | -0.14954 | 0.022888 | 0.068665 | -62.7914 | 60.4523 | 60.4294 | 62.4481 | 62.645 | 123.2483 | 62.4985 | 60.4706
2419.2969 | 0.061035 | 0.42831 | -0.7872 | -0.2179 | 0.15167 | -0.25314 | -0.17303 | 60.5026 | -62.4069 | -0.036621 | -62.6312 | 60.4523 | 62.5259 | 62.4847 | 0.030518 | -0.084381 | 0.070496 | 0.29373 | -0.14526 | -0.16876 | -0.045776 | -0.073242 | -62.7869 | 60.3836 | 60.3882 | 62.4619 | 62.645 | 123.1522 | 62.5305 | 60.4889
2420.9688 | 0.045776 | 0.43366 | -0.79361 | -0.23071 | 0.15274 | -0.28839 | -0.17303 | 60.5118 | -62.3611 | 0.041199 | -62.5992 | 60.4019 | 62.5214 | 62.471 | 0.061035 | -0.089722 | 0.080109 | 0.27985 | -0.1741 | -0.15381 | 0.027466 | 0.064087 | -62.7502 | 60.3241 | 60.3699 | 62.4481 | 62.6312 | 123.1155 | 62.5351 | 60.4843
2422.6562 | 0.061035 | 0.44754 | -0.79041 | -0.21149 | 0.15381 | -0.27237 | -0.18265 | 60.5347 | -62.3291 | 0.041199 | -62.6083 | 60.3973 | 62.5168 | 62.4619 | 0.030518 | -0.095062 | 0.057678 | 0.28305 | -0.15274 | -0.16556 | 0.018311 | 0.073242 | -62.7411 | 60.3607 | 60.3378 | 62.4527 | 62.6175 | 123.1018 | 62.5351 | 60.4843
2424.3125 | 0.061035 | 0.4155 | -0.77759 | -0.23392 | 0.15488 | -0.26489 | -0.17731 | 60.5484 | -62.352 | 0.13733 | -62.5763 | 60.4431 | 62.5214 | 62.4664 | 0.045776 | -0.0737 | 0.0737 | 0.28625 | -0.16663 | -0.18051 | 0.068665 | 0.11902 | -62.7686 | 60.4019 | 60.4202 | 62.4481 | 62.6221 | 123.1705 | 62.4802 | 60.5026
2425.9844 | 0.030518 | 0.43152 | -0.78613 | -0.22964 | 0.14954 | -0.27344 | -0.17624 | 60.5804 | -62.2925 | 0.059509 | -62.5671 | 60.3836 | 62.5168 | 62.471 | 0.061035 | -0.09613 | 0.058746 | 0.29907 | -0.14847 | -0.16449 | 0.041199 | 0.064087 | -62.7182 | 60.3424 | 60.3287 | 62.4481 | 62.6312 | 123.111 | 62.5259 | 60.4889
2427.6562 | 0.076294 | 0.42404 | -0.78079 | -0.23285 | 0.14099 | -0.26062 | -0.17197 | 60.5164 | -62.384 | 0.068665 | -62.6129 | 60.4752 | 62.5259 | 62.4802 | 0.045776 | -0.075836 | 0.068359 | 0.28412 | -0.15808 | -0.16342 | 0.045776 | 0.11444 | -62.7869 | 60.4248 | 60.4202 | 62.4344 | 62.6175 | 123.1705 | 62.4802 | 60.4889
2429.3281 | 0.045776 | 0.4155 | -0.78079 | -0.2179 | 0.15808 | -0.23498 | -0.16556 | 60.553 | -62.3383 | 0.082397 | -62.59 | 60.4706 | 62.5076 | 62.4527 | 0.061035 | -0.076904 | 0.063019 | 0.28732 | -0.1506 | -0.17303 | 0.050354 | 0.068665 | -62.764 | 60.4202 | 60.3836 | 62.4481 | 62.6175 | 123.2117 | 62.4802 | 60.4706
2431 | 0.076294 | 0.42725 | -0.78507 | -0.22751 | 0.1506 | -0.28625 | -0.18265 | 60.5072 | -62.3245 | 0.032043 | -62.5992 | 60.4111 | 62.5122 | 62.4664 | 0.061035 | -0.095062 | 0.061951 | 0.28412 | -0.16663 | -0.14847 | 0.032043 | 0.068665 | -62.7365 | 60.3287 | 60.3561 | 62.4435 | 62.6266 | 123.1247 | 62.5351 | 60.4843
2432.6719 | 0.045776 | 0.43472 | -0.79895 | -0.20401 | 0.15595 | -0.26062 | -0.17624 | 60.5621 | -62.3291 | 0.022888 | -62.5717 | 60.4385 | 62.5305 | 62.4802 | 0.076294 | -0.083313 | 0.059814 | 0.27985 | -0.13992 | -0.15701 | 0.009155 | 0.018311 | -62.7136 | 60.3424 | 60.3149 | 62.4298 | 62.59 | 123.1384 | 62.5259 | 60.4614
2434.3594 | 0.061035 | 0.42831 | -0.80536 | -0.22644 | 0.14847 | -0.28732 | -0.18051 | 60.5576 | -62.265 | 0.14648 | -62.5442 | 60.3882 | 62.4985 | 62.4619 | 0.061035 | -0.089722 | 0.068359 | 0.27237 | -0.16022 | -0.15381 | 0.15564 | 0.2243 | -62.6495 | 60.3333 | 60.3424 | 62.4298 | 62.6038 | 123.23 | 62.4664 | 60.4523
2436.0156 | 0.045776 | 0.41443 | -0.77972 | -0.24246 | 0.1506 | -0.26382 | -0.17197 | 60.5438 | -62.352 | 0.12817 | -62.5854 | 60.4523 | 62.5122 | 62.4802 | 0.076294 | -0.083313 | 0.069427 | 0.28305 | -0.16449 | -0.16235 | 0.045776 | 0.1236 | -62.7686 | 60.434 | 60.4156 | 62.3978 | 62.6404 | 123.1842 | 62.4481 | 60.498
2437.6719 | 0.076294 | 0.44647 | -0.79147 | -0.20935 | 0.13992 | -0.27557 | -0.18158 | 60.5347 | -62.3245 | 0.059509 | -62.6083 | 60.3745 | 62.5031 | 62.4527 | 0.045776 | -0.1004 | 0.05127 | 0.26916 | -0.1506 | -0.15595 | 0.045776 | 0.054932 | -62.7457 | 60.3287 | 60.3378 | 62.4298 | 62.6312 | 123.0881 | 62.5122 | 60.4706
2439.3281 | 0.061035 | 0.40482 | -0.78934 | -0.23819 | 0.15915 | -0.26169 | -0.1709 | 60.5118 | -62.3611 | 0.059509 | -62.6083 | 60.4752 | 62.5031 | 62.4985 | 0.045776 | -0.086517 | 0.075836 | 0.27985 | -0.16129 | -0.15915 | 0.032043 | 0.09613 | -62.7777 | 60.4294 | 60.3973 | 62.4435 | 62.6312 | 123.1979 | 62.471 | 60.4935
2440.9844 | 0.076294 | 0.41122 | -0.7872 | -0.21042 | 0.14954 | -0.24033 | -0.17517 | 60.5713 | -62.3428 | 0.041199 | -62.5671 | 60.4614 | 62.5259 | 62.4664 | 0.061035 | -0.068359 | 0.083313 | 0.29053 | -0.13779 | -0.16235 | -0.013733 | 0.009155 | -62.7823 | 60.4019 | 60.379 | 62.4481 | 62.6358 | 123.1201 | 62.5168 | 60.5026
2442.6562 | 0.076294 | 0.41977 | -0.78613 | -0.22858 | 0.16663 | -0.25528 | -0.16129 | 60.553 | -62.3383 | 0.073242 | -62.5717 | 60.466 | 62.5122 | 62.4847 | 0.061035 | -0.076904 | 0.075836 | 0.29053 | -0.14954 | -0.15808 | 0.032043 | 0.082397 | -62.7457 | 60.4111 | 60.4111 | 62.4252 | 62.6129 | 123.2025 | 62.4573 | 60.4889
2444.3281 | 0.045776 | 0.4187 | -0.77652 | -0.21469 | 0.14099 | -0.25207 | -0.1709 | 60.4706 | -62.4069 | -0.054932 | -62.6175 | 60.4523 | 62.5305 | 62.5031 | 0.045776 | -0.076904 | 0.069427 | 0.29266 | -0.14206 | -0.1474 | -0.10071 | -0.073242 | -62.851 | 60.4294 | 60.4202 | 62.4573 | 62.6633 | 123.111 | 62.5259 | 60.4889
2445.9844 | 0.061035 | 0.42511 | -0.79041 | -0.21896 | 0.14847 | -0.24994 | -0.16235 | 60.4477 | -62.439 | -0.036621 | -62.6266 | 60.4752 | 62.5214 | 62.4893 | 0.061035 | -0.087585 | 0.071564 | 0.28305 | -0.15274 | -0.1506 | -0.07782 | -0.091553 | -62.8098 | 60.3928 | 60.3973 | 62.4435 | 62.6404 | 123.1064 | 62.5259 | 60.4752
2447.6406 | 0.061035 | 0.43579 | -0.79361 | -0.23926 | 0.13458 | -0.298 | -0.18692 | 60.5392 | -62.2604 | 0.15106 | -62.5442 | 60.3928 | 62.4985 | 62.439 | 0.076294 | -0.10254 | 0.063019 | 0.28519 | -0.17838 | -0.14847 | 0.14648 | 0.2243 | -62.6495 | 60.3699 | 60.3424 | 62.3886 | 62.6038 | 123.2162 | 62.4756 | 60.4431
2449.3125 | 0.076294 | 0.42938 | -0.77652 | -0.2179 | 0.14847 | -0.25848 | -0.1741 | 60.5026 | -62.3749 | 0.059509 | -62.5809 | 60.466 | 62.5122 | 62.4573 | 0.045776 | -0.0737 | 0.059814 | 0.298 | -0.14633 | -0.15915 | 0.027466 | 0.086975 | -62.7594 | 60.4156 | 60.3928 | 62.4115 | 62.6129 | 123.2346 | 62.4573 | 60.4797
2450.9844 | 0.061035 | 0.42618 | -0.78079 | -0.20615 | 0.13779 | -0.26382 | -0.17517 | 60.5118 | -62.3657 | -0.009155 | -62.5854 | 60.4385 | 62.5351 | 62.4939 | 0.061035 | -0.084381 | 0.061951 | 0.2713 | -0.15488 | -0.16342 | -0.018311 | 0.022888 | -62.7136 | 60.3424 | 60.3378 | 62.439 | 62.5992 | 123.1247 | 62.5214 | 60.4706
2452.6875 | 0.030518 | 0.42831 | -0.79468 | -0.23392 | 0.14847 | -0.29053 | -0.19119 | 60.5576 | -62.2559 | 0.14191 | -62.5534 | 60.3973 | 62.5076 | 62.4527 | 0.045776 | -0.092926 | 0.069427 | 0.29053 | -0.18265 | -0.15274 | 0.13733 | 0.2243 | -62.6587 | 60.3241 | 60.3653 | 62.4069 | 62.5854 | 123.2117 | 62.4527 | 60.434
2454.4062 | 0.061035 | 0.42297 | -0.78507 | -0.2211 | 0.14847 | -0.24567 | -0.17303 | 60.5438 | -62.3199 | 0.064087 | -62.558 | 60.4385 | 62.4985 | 62.4619 | 0.061035 | -0.069427 | 0.066223 | 0.29159 | -0.15167 | -0.16342 | 0.027466 | 0.07782 | -62.7274 | 60.4065 | 60.3928 | 62.3795 | 62.59 | 123.1934 | 62.4664 | 60.466
2456.0625 | 0.061035 | 0.40695 | -0.78079 | -0.23071 | 0.13565 | -0.25848 | -0.1709 | 60.4752 | -62.4115 | -0.068665 | -62.6038 | 60.4614 | 62.5076 | 62.4893 | 0.061035 | -0.074768 | 0.072632 | 0.29587 | -0.15808 | -0.15488 | -0.082397 | -0.09613 | -62.796 | 60.3882 | 60.3836 | 62.4481 | 62.6221 | 123.1155 | 62.5076 | 60.4431
2457.7344 | 0.045776 | 0.44006 | -0.78934 | -0.2211 | 0.15274 | -0.26489 | -0.18265 | 60.4843 | -62.3657 | -0.032043 | -62.6083 | 60.4248 | 62.5351 | 62.4893 | 0.015259 | -0.076904 | 0.071564 | 0.27557 | -0.13886 | -0.15915 | -0.050354 | -0.045776 | -62.7365 | 60.3378 | 60.3378 | 62.4298 | 62.6129 | 123.1293 | 62.5031 | 60.4477
2459.4219 | 0.045776 | 0.43152 | -0.78827 | -0.24139 | 0.15701 | -0.28091 | -0.17197 | 60.4889 | -62.3657 | 0.018311 | -62.5992 | 60.379 | 62.5214 | 62.4481 | 0.061035 | -0.099335 | 0.068359 | 0.27557 | -0.16556 | -0.1506 | 0.009155 | 0.086975 | -62.7182 | 60.3424 | 60.3378 | 62.4023 | 62.6358 | 123.0972 | 62.4847 | 60.4568
2461.0938 | 0.076294 | 0.42618 | -0.78186 | -0.22537 | 0.14847 | -0.27451 | -0.16663 | 60.5072 | -62.3337 | 0.091553 | -62.59 | 60.4431 | 62.5031 | 62.4619 | 0.045776 | -0.074768 | 0.069427 | 0.29373 | -0.15595 | -0.16235 | 0.032043 | 0.11444 | -62.764 | 60.4065 | 60.4202 | 62.4252 | 62.6266 | 123.1476 | 62.4573 | 60.4889
2462.7656 | 0.045776 | 0.41657 | -0.77759 | -0.20615 | 0.1474 | -0.25101 | -0.17838 | 60.4706 | -62.4115 | -0.036621 | -62.6175 | 60.466 | 62.5214 | 62.4847 | 0.061035 | -0.071564 | 0.075836 | 0.28625 | -0.13458 | -0.16556 | -0.10986 | -0.10986 | -62.8418 | 60.4019 | 60.3973 | 62.439 | 62.6083 | 123.0835 | 62.4985 | 60.4797
2464.4375 | 0.061035 | 0.42297 | -0.79895 | -0.2211 | 0.13992 | -0.28732 | -0.18051 | 60.4614 | -62.3337 | 0.054932 | -62.5854 | 60.3928 | 62.4893 | 62.471 | 0.076294 | -0.10681 | 0.069427 | 0.27557 | -0.16556 | -0.15488 | 0.054932 | 0.11902 | -62.6862 | 60.3516 | 60.3561 | 62.4298 | 62.6221 | 123.1338 | 62.4802 | 60.4248
2466.1094 | 0.045776 | 0.43366 | -0.78507 | -0.22964 | 0.1442 | -0.26169 | -0.17944 | 60.498 | -62.3657 | 0.073242 | -62.6038 | 60.4614 | 62.4985 | 62.4664 | 0.061035 | -0.071564 | 0.069427 | 0.28732 | -0.16342 | -0.16876 | 0.036621 | 0.091553 | -62.7731 | 60.4065 | 60.4019 | 62.4161 | 62.6129 | 123.1796 | 62.4847 | 60.4752
2467.7656 | 0.061035 | 0.4155 | -0.77972 | -0.20935 | 0.1506 | -0.25101 | -0.1709 | 60.5621 | -62.3108 | 0.073242 | -62.5671 | 60.4523 | 62.4893 | 62.4527 | 0.076294 | -0.072632 | 0.066223 | 0.29159 | -0.1474 | -0.16022 | 0.018311 | 0.041199 | -62.7548 | 60.3973 | 60.3928 | 62.4115 | 62.5992 | 123.1338 | 62.4664 | 60.4843
2469.4375 | 0.091553 | 0.41763 | -0.79147 | -0.22324 | 0.15595 | -0.25742 | -0.16983 | 60.4843 | -62.384 | -0.032043 | -62.6129 | 60.4431 | 62.5351 | 62.4756 | 0.045776 | -0.083313 | 0.05661 | 0.29266 | -0.1506 | -0.15274 | -0.059509 | -0.050354 | -62.7686 | 60.3699 | 60.347 | 62.4527 | 62.5992 | 123.0972 | 62.4985 | 60.4477
2471.1406 | 0.045776 | 0.41443 | -0.79254 | -0.22537 | 0.15488 | -0.28732 | -0.17731 | 60.5484 | -62.2467 | 0.16937 | -62.5214 | 60.3882 | 62.4802 | 62.4481 | 0.076294 | -0.09079 | 0.068359 | 0.27664 | -0.16769 | -0.16449 | 0.13275 | 0.26093 | -62.6587 | 60.3607 | 60.3378 | 62.4023 | 62.6083 | 123.1613 | 62.4527 | 60.4523
2472.8125 | 0.045776 | 0.41122 | -0.79361 | -0.22964 | 0.16235 | -0.24139 | -0.16876 | 60.5576 | -62.3154 | 0.07782 | -62.5671 | 60.4614 | 62.4893 | 62.4435 | 0.061035 | -0.068359 | 0.068359 | 0.28412 | -0.12924 | -0.16556 | 0.009155 | 0.041199 | -62.7319 | 60.4111 | 60.379 | 62.3886 | 62.6358 | 123.143 | 62.4435 | 60.4752
2474.4844 | 0.076294 | 0.43472 | -0.79254 | -0.21896 | 0.14526 | -0.26489 | -0.18265 | 60.5301 | -62.2787 | 0.059509 | -62.5305 | 60.3607 | 62.5076 | 62.4252 | 0.045776 | -0.091858 | 0.059814 | 0.27451 | -0.15488 | -0.15701 | 0 | 0.036621 | -62.6862 | 60.3058 | 60.2921 | 62.4298 | 62.5992 | 123.0927 | 62.4985 | 60.4523
2476.1562 | 0.045776 | 0.43152 | -0.8107 | -0.23819 | 0.14313 | -0.28946 | -0.18051 | 60.5209 | -62.2742 | 0.13275 | -62.5351 | 60.4248 | 62.5076 | 62.439 | 0.061035 | -0.10361 | 0.060883 | 0.27557 | -0.16769 | -0.15488 | 0.11902 | 0.21515 | -62.6495 | 60.3378 | 60.3195 | 62.3978 | 62.5992 | 123.1934 | 62.4664 | 60.434
2477.8125 | 0.061035 | 0.43472 | -0.79041 | -0.24353 | 0.14633 | -0.27237 | -0.18799 | 60.5576 | -62.2467 | 0.14648 | -62.5214 | 60.3928 | 62.4847 | 62.4481 | 0.061035 | -0.088654 | 0.068359 | 0.27237 | -0.16876 | -0.15808 | 0.13733 | 0.21973 | -62.6404 | 60.3561 | 60.3424 | 62.3978 | 62.5946 | 123.1888 | 62.4619 | 60.4477
2479.4688 | 0.061035 | 0.41229 | -0.77652 | -0.22858 | 0.16129 | -0.23285 | -0.1709 | 60.5621 | -62.3108 | 0.086975 | -62.5351 | 60.4385 | 62.4847 | 62.439 | 0.061035 | -0.072632 | 0.066223 | 0.29373 | -0.14954 | -0.16876 | 0.022888 | 0.041199 | -62.7182 | 60.3653 | 60.3653 | 62.4161 | 62.6266 | 123.1247 | 62.471 | 60.466
2481.125 | 0.045776 | 0.45288 | -0.79041 | -0.20721 | 0.1442 | -0.27023 | -0.17517 | 60.5438 | -62.2833 | 0.045776 | -62.5442 | 60.3607 | 62.5031 | 62.4435 | 0.045776 | -0.085449 | 0.05661 | 0.28519 | -0.15274 | -0.15701 | 0.032043 | 0.059509 | -62.6907 | 60.2966 | 60.3104 | 62.4252 | 62.6083 | 123.0881 | 62.5259 | 60.4385
2482.7969 | 0.061035 | 0.4187 | -0.78507 | -0.24033 | 0.14633 | -0.26382 | -0.17838 | 60.4889 | -62.352 | 0.045776 | -62.5763 | 60.4797 | 62.5122 | 62.471 | 0.076294 | -0.084381 | 0.067291 | 0.28519 | -0.15488 | -0.15808 | 0.022888 | 0.068665 | -62.7731 | 60.4202 | 60.4294 | 62.4115 | 62.6083 | 123.2071 | 62.4344 | 60.4706
2484.4844 | 0.045776 | 0.43366 | -0.78613 | -0.22537 | 0.15488 | -0.29159 | -0.18478 | 60.5118 | -62.2879 | 0.091553 | -62.5351 | 60.3928 | 62.5031 | 62.4481 | 0.045776 | -0.10895 | 0.063019 | 0.28091 | -0.1741 | -0.15808 | 0.09613 | 0.19684 | -62.6587 | 60.3241 | 60.3241 | 62.3932 | 62.5717 | 123.1796 | 62.4481 | 60.4156
2486.1406 | 0.076294 | 0.40161 | -0.784 | -0.24139 | 0.14099 | -0.26489 | -0.16876 | 60.4935 | -62.3749 | 0.050354 | -62.5626 | 60.4706 | 62.4985 | 62.4481 | 0.045776 | -0.0737 | 0.069427 | 0.28946 | -0.15167 | -0.1741 | 0.032043 | 0.091553 | -62.7502 | 60.3928 | 60.3928 | 62.4115 | 62.5809 | 123.2071 | 62.4298 | 60.4523
2487.7969 | 0.045776 | 0.43366 | -0.78507 | -0.19653 | 0.14954 | -0.26703 | -0.17197 | 60.5118 | -62.2971 | 0.027466 | -62.5442 | 60.4156 | 62.5076 | 62.4619 | 0.061035 | -0.086517 | 0.058746 | 0.28198 | -0.14526 | -0.16022 | 0.018311 | 0.027466 | -62.6953 | 60.3104 | 60.3149 | 62.4252 | 62.6129 | 123.0927 | 62.5168 | 60.4385
2489.4531 | 0.061035 | 0.41443 | -0.79254 | -0.23392 | 0.13992 | -0.28946 | -0.16663 | 60.553 | -62.2421 | 0.17395 | -62.5214 | 60.379 | 62.4847 | 62.4344 | 0.045776 | -0.098267 | 0.067291 | 0.28519 | -0.17197 | -0.16769 | 0.13733 | 0.24719 | -62.645 | 60.3287 | 60.3378 | 62.4115 | 62.5854 | 123.1293 | 62.4435 | 60.4614
2491.1406 | 0.045776 | 0.41122 | -0.79041 | -0.2211 | 0.15167 | -0.23392 | -0.17838 | 60.5392 | -62.3337 | 0.054932 | -62.5488 | 60.4477 | 62.4756 | 62.4435 | 0.045776 | -0.067291 | 0.055542 | 0.28946 | -0.14099 | -0.16129 | -0.013733 | -0.004578 | -62.7686 | 60.379 | 60.3699 | 62.4298 | 62.6175 | 123.0606 | 62.4756 | 60.466
2492.8125 | 0.045776 | 0.42831 | -0.78613 | -0.23605 | 0.15488 | -0.28839 | -0.17944 | 60.5164 | -62.2925 | 0.10071 | -62.5442 | 60.4019 | 62.4939 | 62.4481 | 0.076294 | -0.095062 | 0.068359 | 0.28198 | -0.17944 | -0.1474 | 0.11902 | 0.21515 | -62.6495 | 60.3378 | 60.3149 | 62.3978 | 62.59 | 123.1842 | 62.4344 | 60.4431
2494.4844 | 0.061035 | 0.43472 | -0.7872 | -0.2211 | 0.13138 | -0.28412 | -0.17944 | 60.4935 | -62.3062 | 0.032043 | -62.5717 | 60.3653 | 62.4802 | 62.439 | 0.045776 | -0.079041 | 0.064087 | 0.29907 | -0.16235 | -0.16129 | 0.032043 | 0.068665 | -62.7274 | 60.3104 | 60.3424 | 62.4069 | 62.6038 | 123.0515 | 62.4939 | 60.4797
2496.1406 | 0.045776 | 0.41657 | -0.784 | -0.23498 | 0.14526 | -0.25528 | -0.18158 | 60.5026 | -62.3703 | 0.059509 | -62.5809 | 60.4477 | 62.5122 | 62.471 | 0.030518 | -0.071564 | 0.071564 | 0.29587 | -0.15701 | -0.16342 | 0.027466 | 0.073242 | -62.764 | 60.4019 | 60.4202 | 62.4161 | 62.59 | 123.2025 | 62.4344 | 60.4477
2497.7969 | 0.061035 | 0.4187 | -0.78507 | -0.21149 | 0.14206 | -0.24674 | -0.17303 | 60.4797 | -62.3886 | -0.041199 | -62.5992 | 60.4568 | 62.5031 | 62.4573 | 0.030518 | -0.067291 | 0.066223 | 0.28839 | -0.13245 | -0.15915 | -0.086975 | -0.09613 | -62.8326 | 60.379 | 60.3882 | 62.4161 | 62.6175 | 123.0469 | 62.4847 | 60.4706
2499.4688 | 0.076294 | 0.41443 | -0.79254 | -0.22537 | 0.13672 | -0.26489 | -0.17303 | 60.4843 | -62.3383 | 0.045776 | -62.5671 | 60.4523 | 62.5031 | 62.439 | 0.045776 | -0.077972 | 0.072632 | 0.298 | -0.13992 | -0.16449 | 0.018311 | 0.086975 | -62.7411 | 60.3973 | 60.4111 | 62.4115 | 62.59 | 123.1796 | 62.4527 | 60.4385
2501.1406 | 0.045776 | 0.43259 | -0.78934 | -0.21042 | 0.14313 | -0.25528 | -0.17624 | 60.4523 | -62.384 | -0.059509 | -62.5992 | 60.4477 | 62.5076 | 62.4344 | 0.030518 | -0.083313 | 0.060883 | 0.28732 | -0.15167 | -0.16129 | -0.086975 | -0.073242 | -62.7731 | 60.3745 | 60.3607 | 62.4481 | 62.6221 | 123.0743 | 62.4985 | 60.434
2502.8125 | 0.045776 | 0.42618 | -0.79254 | -0.24033 | 0.1474 | -0.29053 | -0.18692 | 60.5438 | -62.2192 | 0.16022 | -62.5351 | 60.3973 | 62.5122 | 62.4344 | 0.045776 | -0.10574 | 0.063019 | 0.28198 | -0.17517 | -0.15488 | 0.16022 | 0.26093 | -62.5992 | 60.3195 | 60.3104 | 62.3932 | 62.5763 | 123.1567 | 62.4435 | 60.4202
2504.4844 | 0.061035 | 0.41657 | -0.78079 | -0.23178 | 0.15274 | -0.23819 | -0.1741 | 60.5347 | -62.3245 | 0.07782 | -62.5442 | 60.4431 | 62.4939 | 62.4252 | 0.045776 | -0.063019 | 0.061951 | 0.29694 | -0.14526 | -0.16663 | 0.036621 | 0.064087 | -62.709 | 60.3699 | 60.3836 | 62.3932 | 62.6129 | 123.143 | 62.4344 | 60.4752
2506.1875 | 0.045776 | 0.43259 | -0.80643 | -0.22537 | 0.14954 | -0.28625 | -0.18051 | 60.553 | -62.2101 | 0.16022 | -62.5031 | 60.3745 | 62.4847 | 62.4252 | 0.045776 | -0.10468 | 0.059814 | 0.27451 | -0.15595 | -0.16022 | 0.15106 | 0.25635 | -62.645 | 60.3287 | 60.3149 | 62.3795 | 62.5671 | 123.1384 | 62.4344 | 60.4156
2507.8438 | 0.061035 | 0.43152 | -0.77545 | -0.20721 | 0.14526 | -0.25314 | -0.18051 | 60.4889 | -62.3703 | -0.036621 | -62.59 | 60.4431 | 62.4939 | 62.4252 | 0.061035 | -0.080109 | 0.070496 | 0.28625 | -0.14954 | -0.16556 | -0.036621 | -0.059509 | -62.7411 | 60.347 | 60.3424 | 62.4161 | 62.5946 | 123.0972 | 62.5259 | 60.4568
2509.5625 | 0.061035 | 0.43793 | -0.78079 | -0.2179 | 0.14099 | -0.27771 | -0.17303 | 60.5301 | -62.2742 | 0.054932 | -62.5351 | 60.347 | 62.5076 | 62.4344 | 0.045776 | -0.085449 | 0.048065 | 0.27878 | -0.14313 | -0.16022 | 0.036621 | 0.07782 | -62.6541 | 60.3058 | 60.3012 | 62.4023 | 62.5809 | 123.0469 | 62.4985 | 60.4935
2511.2656 | 0.061035 | 0.43579 | -0.79895 | -0.23498 | 0.13992 | -0.28625 | -0.18478 | 60.5072 | -62.2925 | 0.10529 | -62.5305 | 60.4202 | 62.4847 | 62.4298 | 0.061035 | -0.09079 | 0.064087 | 0.27985 | -0.16663 | -0.15701 | 0.1236 | 0.18768 | -62.6404 | 60.3287 | 60.3241 | 62.4069 | 62.59 | 123.1522 | 62.4527 | 60.4248
2512.9531 | 0.061035 | 0.43579 | -0.78827 | -0.22751 | 0.14954 | -0.28198 | -0.19012 | 60.5713 | -62.2009 | 0.15564 | -62.5076 | 60.379 | 62.4802 | 62.4481 | 0.061035 | -0.09613 | 0.066223 | 0.27664 | -0.16129 | -0.16556 | 0.13733 | 0.24719 | -62.6266 | 60.3378 | 60.3241 | 62.3978 | 62.5626 | 123.1613 | 62.4161 | 60.4294
2514.6094 | 0.061035 | 0.4155 | -0.77652 | -0.22858 | 0.13138 | -0.24246 | -0.17197 | 60.5255 | -62.3337 | 0.054932 | -62.5397 | 60.4385 | 62.4893 | 62.4298 | 0.045776 | -0.072632 | 0.0737 | 0.29266 | -0.15274 | -0.16876 | 0.027466 | 0.068665 | -62.7274 | 60.347 | 60.3699 | 62.4161 | 62.558 | 123.1522 | 62.4207 | 60.4568
2516.2656 | 0.045776 | 0.44647 | -0.79468 | -0.21576 | 0.13672 | -0.27237 | -0.18265 | 60.4889 | -62.2879 | 0.059509 | -62.5717 | 60.3699 | 62.4802 | 62.4527 | 0.061035 | -0.10468 | 0.054474 | 0.27771 | -0.16556 | -0.15488 | 0.027466 | 0.082397 | -62.7136 | 60.3149 | 60.3149 | 62.4207 | 62.6038 | 123.0331 | 62.4847 | 60.4706
2517.9219 | 0.061035 | 0.42297 | -0.78507 | -0.23819 | 0.14526 | -0.25421 | -0.18799 | 60.5255 | -62.2467 | 0.16479 | -62.5122 | 60.3882 | 62.471 | 62.4573 | 0.061035 | -0.087585 | 0.069427 | 0.28198 | -0.15701 | -0.16663 | 0.10071 | 0.19226 | -62.6907 | 60.3378 | 60.3516 | 62.3886 | 62.5626 | 123.1064 | 62.4619 | 60.4523
2519.5781 | 0.030518 | 0.4187 | -0.78507 | -0.21042 | 0.15595 | -0.24994 | -0.17303 | 60.466 | -62.3795 | -0.054932 | -62.5992 | 60.4477 | 62.4985 | 62.4573 | 0.045776 | -0.079041 | 0.063019 | 0.28625 | -0.13245 | -0.1741 | -0.064087 | -0.086975 | -62.7594 | 60.347 | 60.3378 | 62.4161 | 62.5946 | 123.0652 | 62.4985 | 60.4477
2521.2344 | 0.045776 | 0.44754 | -0.80643 | -0.22751 | 0.1474 | -0.28305 | -0.18799 | 60.4889 | -62.2879 | 0.07782 | -62.5397 | 60.379 | 62.5031 | 62.4527 | 0.076294 | -0.092926 | 0.066223 | 0.26916 | -0.16129 | -0.16129 | 0.10529 | 0.17853 | -62.6495 | 60.3149 | 60.3195 | 62.3749 | 62.5717 | 123.1384 | 62.4069 | 60.3928
2522.9062 | 0.061035 | 0.41229 | -0.784 | -0.21362 | 0.15488 | -0.25848 | -0.1741 | 60.5072 | -62.352 | -0.041199 | -62.5763 | 60.434 | 62.5031 | 62.4573 | 0.061035 | -0.084381 | 0.052338 | 0.29266 | -0.14847 | -0.16235 | -0.041199 | -0.045776 | -62.7319 | 60.3561 | 60.3333 | 62.4115 | 62.6038 | 123.0835 | 62.4802 | 60.4248
2524.625 | 0.045776 | 0.42511 | -0.79468 | -0.2243 | 0.1442 | -0.27023 | -0.1709 | 60.5164 | -62.2559 | 0.068665 | -62.5397 | 60.3424 | 62.4939 | 62.4435 | 0.076294 | -0.086517 | 0.058746 | 0.27878 | -0.14633 | -0.15915 | 0.041199 | 0.068665 | -62.6907 | 60.2966 | 60.2829 | 62.4252 | 62.5992 | 123.0148 | 62.4756 | 60.4385
2526.3281 | 0.061035 | 0.4187 | -0.79788 | -0.22324 | 0.13458 | -0.26596 | -0.17303 | 60.4752 | -62.3383 | 0.082397 | -62.5717 | 60.434 | 62.4756 | 62.4252 | 0.076294 | -0.080109 | 0.064087 | 0.27985 | -0.15915 | -0.15808 | 0.041199 | 0.10529 | -62.7457 | 60.4065 | 60.3882 | 62.4207 | 62.5854 | 123.1247 | 62.439 | 60.434
2528 | 0.061035 | 0.41977 | -0.79575 | -0.23285 | 0.15274 | -0.26596 | -0.16556 | 60.4935 | -62.3199 | 0.09613 | -62.5671 | 60.4294 | 62.4847 | 62.4435 | 0.045776 | -0.089722 | 0.071564 | 0.28625 | -0.15488 | -0.16235 | 0.054932 | 0.1236 | -62.7457 | 60.3653 | 60.3653 | 62.4069 | 62.5809 | 123.0972 | 62.4252 | 60.4431
2529.6719 | 0.045776 | 0.41122 | -0.78934 | -0.21576 | 0.1506 | -0.24246 | -0.17303 | 60.466 | -62.3657 | -0.027466 | -62.5854 | 60.4523 | 62.4939 | 62.4527 | 0.076294 | -0.075836 | 0.071564 | 0.28732 | -0.13886 | -0.16663 | -0.09613 | -0.064087 | -62.7869 | 60.347 | 60.3561 | 62.4435 | 62.6266 | 123.0194 | 62.4847 | 60.4523
2531.3438 | 0.061035 | 0.42511 | -0.78934 | -0.2243 | 0.15808 | -0.28839 | -0.18265 | 60.4706 | -62.2971 | 0.041199 | -62.5534 | 60.3561 | 62.4802 | 62.4252 | 0.045776 | -0.09613 | 0.057678 | 0.28625 | -0.17838 | -0.15915 | 0.004578 | 0.07782 | -62.6907 | 60.3012 | 60.3149 | 62.4115 | 62.5946 | 123.024 | 62.4893 | 60.4065
2533.0156 | 0.061035 | 0.44861 | -0.80215 | -0.21362 | 0.1506 | -0.28625 | -0.17944 | 60.5118 | -62.2559 | 0.050354 | -62.5397 | 60.3607 | 62.5122 | 62.439 | 0.061035 | -0.089722 | 0.058746 | 0.28519 | -0.15488 | -0.16022 | 0.032043 | 0.068665 | -62.6862 | 60.3241 | 60.3012 | 62.384 | 62.5854 | 123.0011 | 62.5031 | 60.4523
2534.6719 | 0.045776 | 0.42084 | -0.77972 | -0.25742 | 0.15488 | -0.26596 | -0.17731 | 60.466 | -62.3337 | 0.068665 | -62.558 | 60.4156 | 62.4893 | 62.4435 | 0.061035 | -0.085449 | 0.065155 | 0.29159 | -0.15488 | -0.16876 | 0.041199 | 0.082397 | -62.7457 | 60.3928 | 60.3836 | 62.3978 | 62.5717 | 123.1247 | 62.4344 | 60.4385
2536.3281 | 0.045776 | 0.44113 | -0.79681 | -0.2243 | 0.1506 | -0.28839 | -0.18265 | 60.466 | -62.2833 | 0.068665 | -62.5259 | 60.3882 | 62.4756 | 62.4298 | 0.045776 | -0.10574 | 0.071564 | 0.26703 | -0.16876 | -0.15915 | 0.073242 | 0.13275 | -62.6587 | 60.3287 | 60.3195 | 62.4161 | 62.59 | 123.1247 | 62.4527 | 60.4156
2538.0625 | 0.076294 | 0.41016 | -0.77652 | -0.21683 | 0.1506 | -0.25955 | -0.1709 | 60.5164 | -62.2879 | 0.009155 | -62.558 | 60.3836 | 62.471 | 62.4298 | 0.061035 | -0.074768 | 0.069427 | 0.28305 | -0.13886 | -0.15167 | 0.022888 | 0.022888 | -62.6678 | 60.3241 | 60.3058 | 62.4023 | 62.6083 | 123.0698 | 62.471 | 60.4065
2539.7188 | 0.030518 | 0.42938 | -0.78613 | -0.22003 | 0.14099 | -0.27557 | -0.16769 | 60.5301 | -62.265 | 0.054932 | -62.5214 | 60.3378 | 62.4756 | 62.4527 | 0.045776 | -0.092926 | 0.05661 | 0.28519 | -0.14847 | -0.16876 | 0.050354 | 0.068665 | -62.6633 | 60.2921 | 60.2783 | 62.3978 | 62.5992 | 123.0148 | 62.5122 | 60.4431
2541.3906 | 0.061035 | 0.439 | -0.79361 | -0.23178 | 0.1506 | -0.2681 | -0.17303 | 60.5576 | -62.2055 | 0.16937 | -62.4985 | 60.3653 | 62.4619 | 62.4435 | 0.061035 | -0.09079 | 0.059814 | 0.28091 | -0.16876 | -0.16556 | 0.15106 | 0.25635 | -62.6266 | 60.3058 | 60.3195 | 62.3795 | 62.5626 | 123.1155 | 62.4481 | 60.4294
2543.0938 | 0.061035 | 0.44647 | -0.77972 | -0.2211 | 0.15274 | -0.27985 | -0.18692 | 60.4752 | -62.3062 | 0.041199 | -62.5534 | 60.3699 | 62.4847 | 62.4252 | 0.061035 | -0.098267 | 0.065155 | 0.28519 | -0.16129 | -0.15701 | 0.036621 | 0.073242 | -62.6999 | 60.3241 | 60.3104 | 62.4023 | 62.5854 | 123.024 | 62.4893 | 60.4477
2544.75 | 0.061035 | 0.40909 | -0.77652 | -0.2478 | 0.14526 | -0.26916 | -0.18051 | 60.4935 | -62.3199 | 0.073242 | -62.5717 | 60.4523 | 62.4893 | 62.4435 | 0.045776 | -0.074768 | 0.067291 | 0.28946 | -0.15274 | -0.16769 | 0.036621 | 0.086975 | -62.7365 | 60.3928 | 60.379 | 62.3978 | 62.5763 | 123.1155 | 62.4344 | 60.4431
2546.4062 | 0.061035 | 0.41763 | -0.78293 | -0.19226 | 0.15488 | -0.25207 | -0.16876 | 60.5301 | -62.265 | 0.032043 | -62.5122 | 60.379 | 62.471 | 62.4344 | 0.045776 | -0.089722 | 0.05661 | 0.27557 | -0.15381 | -0.16022 | 0.032043 | 0.032043 | -62.6633 | 60.2875 | 60.2783 | 62.4115 | 62.5671 | 123.0652 | 62.4435 | 60.4156
2548.0781 | 0.061035 | 0.42725 | -0.78186 | -0.22003 | 0.13672 | -0.26276 | -0.1741 | 60.5347 | -62.2604 | 0.036621 | -62.4985 | 60.3607 | 62.4847 | 62.4207 | 0.045776 | -0.079041 | 0.055542 | 0.28305 | -0.14954 | -0.16449 | 0.032043 | 0.045776 | -62.6678 | 60.2829 | 60.2875 | 62.3749 | 62.5534 | 123.0377 | 62.4435 | 60.4294
2549.7344 | 0.045776 | 0.43152 | -0.79254 | -0.2179 | 0.15488 | -0.26596 | -0.17303 | 60.5209 | -62.2604 | 0.073242 | -62.5168 | 60.3516 | 62.471 | 62.4023 | 0.061035 | -0.087585 | 0.068359 | 0.28091 | -0.14206 | -0.16449 | 0.036621 | 0.073242 | -62.645 | 60.2966 | 60.2966 | 62.3886 | 62.6038 | 122.9965 | 62.4893 | 60.4156
2551.4219 | 0.061035 | 0.40695 | -0.79468 | -0.23071 | 0.14099 | -0.24246 | -0.1709 | 60.5347 | -62.2971 | 0.054932 | -62.5214 | 60.4019 | 62.4481 | 62.439 | 0.061035 | -0.072632 | 0.077972 | 0.29587 | -0.14313 | -0.17624 | 0.004578 | 0.013733 | -62.7228 | 60.3516 | 60.379 | 62.3978 | 62.5717 | 123.0606 | 62.4298 | 60.434
2553.0781 | 0.061035 | 0.44327 | -0.79041 | -0.22858 | 0.1474 | -0.30014 | -0.18158 | 60.4568 | -62.3062 | 0.045776 | -62.5397 | 60.3561 | 62.4893 | 62.439 | 0.061035 | -0.099335 | 0.050201 | 0.28839 | -0.15167 | -0.15595 | 0.036621 | 0.09613 | -62.6907 | 60.3058 | 60.3104 | 62.4069 | 62.5809 | 123.0286 | 62.471 | 60.4248
2554.7344 | 0.061035 | 0.40375 | -0.77866 | -0.22217 | 0.1506 | -0.2478 | -0.18906 | 60.5072 | -62.3016 | 0.064087 | -62.5122 | 60.4202 | 62.4802 | 62.4435 | 0.091553 | -0.074768 | 0.077972 | 0.29587 | -0.14847 | -0.17838 | 0.027466 | 0.086975 | -62.6907 | 60.3699 | 60.3333 | 62.3932 | 62.5488 | 123.143 | 62.384 | 60.4477
2556.3906 | 0.045776 | 0.43793 | -0.79041 | -0.20721 | 0.15915 | -0.26596 | -0.1709 | 60.498 | -62.2879 | 0.009155 | -62.5305 | 60.3561 | 62.4939 | 62.4298 | 0.076294 | -0.087585 | 0.068359 | 0.28305 | -0.14313 | -0.16022 | 0.013733 | 0.027466 | -62.6541 | 60.3012 | 60.2783 | 62.4023 | 62.5717 | 123.0469 | 62.4573 | 60.4065
2558.0625 | 0.061035 | 0.40054 | -0.77331 | -0.23712 | 0.13565 | -0.25101 | -0.1709 | 60.4752 | -62.3108 | 0.082397 | -62.5168 | 60.4477 | 62.4619 | 62.4344 | 0.030518 | -0.075836 | 0.070496 | 0.28412 | -0.15808 | -0.16449 | 0.018311 | 0.086975 | -62.7045 | 60.3653 | 60.347 | 62.4161 | 62.5992 | 123.1338 | 62.4115 | 60.434
2559.7344 | 0.045776 | 0.41977 | -0.78507 | -0.21255 | 0.15381 | -0.2478 | -0.17517 | 60.498 | -62.2742 | 0.07782 | -62.5259 | 60.4248 | 62.4847 | 62.4207 | 0.030518 | -0.070496 | 0.060883 | 0.2948 | -0.14526 | -0.15488 | 0.036621 | 0.082397 | -62.6862 | 60.3699 | 60.3241 | 62.3932 | 62.5671 | 123.1155 | 62.439 | 60.4294
2561.4062 | 0.045776 | 0.41657 | -0.78079 | -0.20508 | 0.14206 | -0.26062 | -0.18158 | 60.4294 | -62.3474 | -0.054932 | -62.5671 | 60.4202 | 62.4847 | 62.439 | 0.045776 | -0.086517 | 0.076904 | 0.29053 | -0.14633 | -0.15488 | -0.082397 | -0.082397 | -62.7457 | 60.347 | 60.3012 | 62.3978 | 62.5946 | 123.0423 | 62.4847 | 60.4248
2563.0938 | 0.061035 | 0.42084 | -0.7872 | -0.24887 | 0.14526 | -0.28305 | -0.18158 | 60.4248 | -62.3108 | 0.068665 | -62.5397 | 60.4294 | 62.4847 | 62.439 | 0.061035 | -0.082245 | 0.072632 | 0.30014 | -0.16876 | -0.15915 | 0.032043 | 0.10986 | -62.709 | 60.379 | 60.379 | 62.3886 | 62.5534 | 123.111 | 62.4435 | 60.4568
2564.7656 | 0.076294 | 0.42297 | -0.77652 | -0.2243 | 0.1506 | -0.26169 | -0.16876 | 60.5072 | -62.2787 | 0.050354 | -62.5076 | 60.4202 | 62.4664 | 62.3978 | 0.045776 | -0.084381 | 0.063019 | 0.28625 | -0.13565 | -0.15701 | -0.013733 | 0.032043 | -62.709 | 60.3561 | 60.3424 | 62.4023 | 62.5992 | 123.0286 | 62.471 | 60.4385
2566.4375 | 0.045776 | 0.41977 | -0.78507 | -0.21896 | 0.14633 | -0.27664 | -0.18478 | 60.4294 | -62.2971 | -0.009155 | -62.5397 | 60.379 | 62.4847 | 62.4115 | 0.045776 | -0.09613 | 0.060883 | 0.28519 | -0.14954 | -0.15595 | -0.018311 | 0.004578 | -62.6678 | 60.2829 | 60.2692 | 62.4115 | 62.59 | 123.0469 | 62.471 | 60.4065
2568.1406 | 0.076294 | 0.41657 | -0.77972 | -0.2179 | 0.15381 | -0.25314 | -0.18051 | 60.4797 | -62.2879 | 0.045776 | -62.5259 | 60.3973 | 62.4664 | 62.4298 | 0.045776 | -0.074768 | 0.066223 | 0.29373 | -0.13886 | -0.15595 | -0.027466 | -0.018311 | -62.7274 | 60.3745 | 60.3149 | 62.4207 | 62.5763 | 123.0103 | 62.471 | 60.4568
2569.7969 | 0.030518 | 0.44647 | -0.79895 | -0.22537 | 0.13458 | -0.27664 | -0.16449 | 60.4843 | -62.2421 | 0.032043 | -62.4985 | 60.3516 | 62.4481 | 62.4069 | 0.061035 | -0.089722 | 0.0737 | 0.28412 | -0.15274 | -0.15595 | 0.013733 | 0.054932 | -62.6541 | 60.2783 | 60.2646 | 62.3978 | 62.558 | 123.024 | 62.4619 | 60.3973
2571.4844 | 0.045776 | 0.41229 | -0.78186 | -0.21683 | 0.15381 | -0.25101 | -0.16983 | 60.4248 | -62.3566 | -0.018311 | -62.5534 | 60.4019 | 62.471 | 62.4252 | 0.061035 | -0.075836 | 0.074768 | 0.28305 | -0.1442 | -0.16022 | -0.11444 | -0.09613 | -62.7823 | 60.3745 | 60.3287 | 62.3978 | 62.6038 | 122.9874 | 62.4939 | 60.4385
2573.1562 | 0.045776 | 0.43579 | -0.7872 | -0.22324 | 0.15808 | -0.26596 | -0.17517 | 60.4614 | -62.2833 | 0.004578 | -62.5168 | 60.347 | 62.4527 | 62.439 | 0.045776 | -0.087585 | 0.065155 | 0.27664 | -0.15488 | -0.1506 | -0.004578 | 0.013733 | -62.6587 | 60.3104 | 60.2692 | 62.4069 | 62.5671 | 123.0469 | 62.4573 | 60.3928
2574.8281 | 0.076294 | 0.43366 | -0.78934 | -0.23392 | 0.14206 | -0.29159 | -0.18692 | 60.4477 | -62.2787 | 0.050354 | -62.5351 | 60.3516 | 62.4619 | 62.4115 | 0.045776 | -0.098267 | 0.072632 | 0.27771 | -0.17944 | -0.15167 | 0.004578 | 0.068665 | -62.6724 | 60.2966 | 60.3149 | 62.3795 | 62.5854 | 122.9874 | 62.4802 | 60.4202
2576.5156 | 0.045776 | 0.43152 | -0.79147 | -0.23712 | 0.14099 | -0.29373 | -0.19867 | 60.4156 | -62.3062 | 0.050354 | -62.5305 | 60.3653 | 62.4573 | 62.4207 | 0.030518 | -0.097198 | 0.057678 | 0.27451 | -0.16876 | -0.15915 | 0.041199 | 0.10529 | -62.6633 | 60.3149 | 60.2737 | 62.3749 | 62.5763 | 123.0377 | 62.4664 | 60.4156
2578.2031 | 0.045776 | 0.41336 | -0.77225 | -0.2211 | 0.14847 | -0.23392 | -0.17197 | 60.4935 | -62.2742 | 0.07782 | -62.5076 | 60.434 | 62.4847 | 62.4252 | 0.061035 | -0.080109 | 0.057678 | 0.28946 | -0.14847 | -0.17838 | 0.036621 | 0.059509 | -62.6953 | 60.3561 | 60.3287 | 62.3886 | 62.5442 | 123.1064 | 62.4115 | 60.4065
2579.8594 | 0.045776 | 0.43793 | -0.78293 | -0.21683 | 0.14633 | -0.26169 | -0.16876 | 60.4385 | -62.3474 | -0.045776 | -62.5626 | 60.4111 | 62.4893 | 62.439 | 0.061035 | -0.088654 | 0.061951 | 0.28839 | -0.14313 | -0.15915 | -0.059509 | -0.064087 | -62.7136 | 60.3195 | 60.3195 | 62.3978 | 62.5763 | 123.0377 | 62.4573 | 60.3882
2581.5781 | 0.076294 | 0.40375 | -0.77118 | -0.21896 | 0.1506 | -0.24567 | -0.18158 | 60.4935 | -62.265 | 0.07782 | -62.5122 | 60.4065 | 62.4527 | 62.4207 | 0.045776 | -0.079041 | 0.074768 | 0.28519 | -0.14206 | -0.15381 | 0.018311 | 0.054932 | -62.6953 | 60.3378 | 60.347 | 62.3749 | 62.558 | 123.0789 | 62.4207 | 60.4248
2583.2344 | 0.061035 | 0.44434 | -0.79681 | -0.21362 | 0.14313 | -0.27878 | -0.1741 | 60.4706 | -62.2192 | 0.068665 | -62.5076 | 60.3378 | 62.439 | 62.3886 | 0.076294 | -0.098267 | 0.053406 | 0.27344 | -0.15167 | -0.15488 | 0.027466 | 0.054932 | -62.6587 | 60.2646 | 60.2783 | 62.3932 | 62.5717 | 122.9599 | 62.4893 | 60.4294
2584.8906 | 0.061035 | 0.39841 | -0.78827 | -0.24567 | 0.14526 | -0.25635 | -0.17624 | 60.4431 | -62.3291 | 0.059509 | -62.5305 | 60.4477 | 62.4802 | 62.4023 | 0.061035 | -0.083313 | 0.074768 | 0.28946 | -0.16342 | -0.16983 | 0.013733 | 0.064087 | -62.7365 | 60.3745 | 60.3561 | 62.384 | 62.5763 | 123.0972 | 62.4023 | 60.4156
2586.6094 | 0.045776 | 0.41443 | -0.78613 | -0.24139 | 0.14633 | -0.24887 | -0.17731 | 60.466 | -62.2742 | 0.054932 | -62.5031 | 60.4202 | 62.4573 | 62.4115 | 0.045776 | -0.084381 | 0.076904 | 0.29907 | -0.16235 | -0.17624 | 0.022888 | 0.086975 | -62.6816 | 60.3424 | 60.3653 | 62.384 | 62.5397 | 123.0927 | 62.4115 | 60.4294
2588.2656 | 0.030518 | 0.43366 | -0.78079 | -0.20081 | 0.13351 | -0.27451 | -0.17944 | 60.4797 | -62.2192 | 0.059509 | -62.4893 | 60.3241 | 62.4527 | 62.4161 | 0.076294 | -0.082245 | 0.052338 | 0.28732 | -0.15381 | -0.16129 | 0.009155 | 0.045776 | -62.6404 | 60.2737 | 60.26 | 62.4023 | 62.5763 | 122.9874 | 62.4939 | 60.4019
2589.9219 | 0.076294 | 0.42618 | -0.79041 | -0.24139 | 0.1506 | -0.29373 | -0.18478 | 60.498 | -62.1872 | 0.14648 | -62.4847 | 60.347 | 62.4573 | 62.4161 | 0.030518 | -0.10468 | 0.064087 | 0.27451 | -0.17303 | -0.15808 | 0.15106 | 0.23346 | -62.59 | 60.2875 | 60.2875 | 62.3611 | 62.558 | 123.111 | 62.4023 | 60.3699
2591.6094 | 0.061035 | 0.40802 | -0.78613 | -0.24139 | 0.15167 | -0.25207 | -0.18051 | 60.4477 | -62.3383 | 0.064087 | -62.5305 | 60.4294 | 62.4619 | 62.4298 | 0.045776 | -0.079041 | 0.080109 | 0.2948 | -0.1709 | -0.16556 | 0.032043 | 0.07782 | -62.7136 | 60.3745 | 60.3607 | 62.3978 | 62.5626 | 123.0743 | 62.3932 | 60.4248
2593.2656 | 0.061035 | 0.42404 | -0.79041 | -0.21362 | 0.1474 | -0.25742 | -0.18372 | 60.4477 | -62.3337 | -0.045776 | -62.5488 | 60.4248 | 62.4756 | 62.4252 | 0.076294 | -0.080109 | 0.066223 | 0.27771 | -0.12924 | -0.16449 | -0.064087 | -0.07782 | -62.7228 | 60.3241 | 60.3058 | 62.384 | 62.5717 | 123.0057 | 62.4527 | 60.4019
2594.9375 | 0.061035 | 0.42404 | -0.78934 | -0.22003 | 0.14847 | -0.24887 | -0.16983 | 60.4111 | -62.3566 | -0.059509 | -62.5626 | 60.3973 | 62.4664 | 62.4252 | 0.045776 | -0.081177 | 0.064087 | 0.29266 | -0.13886 | -0.16022 | -0.068665 | -0.10071 | -62.7457 | 60.3561 | 60.3287 | 62.4023 | 62.59 | 123.024 | 62.4527 | 60.4111
2596.625 | 0.076294 | 0.40375 | -0.78079 | -0.23819 | 0.15595 | -0.24887 | -0.17624 | 60.466 | -62.2559 | 0.073242 | -62.5122 | 60.4202 | 62.4619 | 62.4252 | 0.061035 | -0.084381 | 0.068359 | 0.28946 | -0.1506 | -0.16876 | 0.045776 | 0.068665 | -62.6816 | 60.3653 | 60.3149 | 62.3749 | 62.5763 | 123.0927 | 62.4344 | 60.4111
2598.2812 | 0.045776 | 0.42191 | -0.784 | -0.2211 | 0.1506 | -0.2681 | -0.16769 | 60.4294 | -62.3016 | -0.027466 | -62.5397 | 60.3653 | 62.471 | 62.3932 | 0.061035 | -0.085449 | 0.052338 | 0.28091 | -0.1442 | -0.16876 | -0.022888 | -0.009155 | -62.6816 | 60.3012 | 60.2646 | 62.3795 | 62.558 | 123.0331 | 62.4664 | 60.4019
2599.9375 | 0.045776 | 0.43686 | -0.78934 | -0.24353 | 0.13992 | -0.28946 | -0.18478 | 60.4019 | -62.2559 | 0.068665 | -62.5214 | 60.3699 | 62.471 | 62.4069 | 0.045776 | -0.097198 | 0.067291 | 0.28091 | -0.16449 | -0.15595 | 0.064087 | 0.14648 | -62.6404 | 60.2829 | 60.2875 | 62.3703 | 62.5626 | 123.0835 | 62.4298 | 60.379
2601.6406 | 0.045776 | 0.4155 | -0.77866 | -0.20828 | 0.15381 | -0.24033 | -0.18692 | 60.4614 | -62.3016 | 0.022888 | -62.5214 | 60.4065 | 62.4664 | 62.4252 | 0.030518 | -0.063019 | 0.058746 | 0.2948 | -0.13672 | -0.16235 | -0.032043 | -0.022888 | -62.7182 | 60.3378 | 60.3241 | 62.3932 | 62.5534 | 122.9736 | 62.4435 | 60.434
2603.3438 | 0.045776 | 0.42297 | -0.79041 | -0.23178 | 0.14633 | -0.27237 | -0.17624 | 60.4156 | -62.3062 | 0.050354 | -62.5214 | 60.4294 | 62.4619 | 62.4069 | 0.061035 | -0.095062 | 0.057678 | 0.27344 | -0.15381 | -0.15915 | 0.013733 | 0.07782 | -62.7182 | 60.3561 | 60.3378 | 62.3978 | 62.5763 | 123.111 | 62.3749 | 60.3882
2605 | 0.030518 | 0.43579 | -0.79361 | -0.22324 | 0.16235 | -0.28625 | -0.17944 | 60.4202 | -62.2467 | 0.082397 | -62.5031 | 60.3699 | 62.439 | 62.3932 | 0.061035 | -0.10788 | 0.064087 | 0.27985 | -0.16449 | -0.15595 | 0.091553 | 0.16479 | -62.6266 | 60.2966 | 60.2829 | 62.3703 | 62.5442 | 123.0881 | 62.384 | 60.3973
2606.6719 | 0.045776 | 0.41657 | -0.79041 | -0.24887 | 0.1442 | -0.26276 | -0.18265 | 60.434 | -62.3016 | 0.09613 | -62.5305 | 60.4248 | 62.4435 | 62.4207 | 0.061035 | -0.074768 | 0.074768 | 0.27344 | -0.16876 | -0.16342 | 0.036621 | 0.10986 | -62.6999 | 60.347 | 60.347 | 62.384 | 62.5626 | 123.056 | 62.4023 | 60.3836
2608.375 | 0.061035 | 0.42404 | -0.77866 | -0.2211 | 0.15488 | -0.25635 | -0.18265 | 60.4111 | -62.3428 | -0.036621 | -62.5534 | 60.4202 | 62.4893 | 62.4298 | 0.045776 | -0.066223 | 0.071564 | 0.28839 | -0.1506 | -0.16342 | -0.068665 | -0.091553 | -62.7502 | 60.3516 | 60.3149 | 62.384 | 62.5854 | 122.9416 | 62.4435 | 60.434
2610.0625 | 0.061035 | 0.45288 | -0.79788 | -0.2243 | 0.13672 | -0.29694 | -0.19012 | 60.4019 | -62.2696 | 0.045776 | -62.5214 | 60.3378 | 62.4664 | 62.4252 | 0.045776 | -0.095062 | 0.063019 | 0.2681 | -0.15915 | -0.16129 | 0.032043 | 0.10529 | -62.6404 | 60.3058 | 60.2921 | 62.384 | 62.558 | 123.0331 | 62.4344 | 60.4019
2611.7344 | 0.045776 | 0.41016 | -0.79147 | -0.22324 | 0.1474 | -0.25635 | -0.17624 | 60.434 | -62.3245 | 0.050354 | -62.5259 | 60.4294 | 62.4619 | 62.439 | 0.030518 | -0.066223 | 0.055542 | 0.27557 | -0.15915 | -0.16129 | 0.013733 | 0.068665 | -62.7182 | 60.3516 | 60.3333 | 62.352 | 62.5763 | 123.1018 | 62.3703 | 60.4065
2613.4062 | 0.045776 | 0.42297 | -0.78507 | -0.21896 | 0.14206 | -0.25101 | -0.17624 | 60.4202 | -62.3474 | -0.064087 | -62.558 | 60.4202 | 62.4664 | 62.4207 | 0.076294 | -0.077972 | 0.065155 | 0.27771 | -0.14313 | -0.15595 | -0.086975 | -0.091553 | -62.7365 | 60.3516 | 60.3195 | 62.4161 | 62.5534 | 122.9965 | 62.4619 | 60.4156
2615.0781 | 0.045776 | 0.41657 | -0.77545 | -0.22858 | 0.14526 | -0.25421 | -0.16449 | 60.4706 | -62.2833 | 0.086975 | -62.4985 | 60.4202 | 62.4252 | 62.4161 | 0.015259 | -0.076904 | 0.0737 | 0.28625 | -0.14847 | -0.16876 | 0.022888 | 0.07782 | -62.6678 | 60.3195 | 60.3516 | 62.3886 | 62.5717 | 123.0881 | 62.3978 | 60.4111
2616.7344 | 0.061035 | 0.4422 | -0.79681 | -0.21469 | 0.13992 | -0.27344 | -0.1741 | 60.4614 | -62.2101 | 0.064087 | -62.4939 | 60.3058 | 62.4527 | 62.3978 | 0.091553 | -0.089722 | 0.052338 | 0.27664 | -0.15595 | -0.15488 | 0.041199 | 0.086975 | -62.6221 | 60.2829 | 60.2509 | 62.3703 | 62.5442 | 122.9462 | 62.439 | 60.4156
2618.3906 | 0.061035 | 0.41229 | -0.78934 | -0.24887 | 0.14633 | -0.27771 | -0.18372 | 60.4797 | -62.2192 | 0.15106 | -62.4756 | 60.4111 | 62.4344 | 62.3886 | 0.045776 | -0.086517 | 0.070496 | 0.28091 | -0.16769 | -0.16342 | 0.059509 | 0.15106 | -62.6678 | 60.3104 | 60.3287 | 62.3474 | 62.5488 | 123.0331 | 62.4207 | 60.4248
2620.0469 | 0.061035 | 0.44861 | -0.78827 | -0.22537 | 0.14313 | -0.28412 | -0.17944 | 60.4889 | -62.2147 | 0.054932 | -62.4939 | 60.347 | 62.4161 | 62.3932 | 0.061035 | -0.089722 | 0.060883 | 0.2948 | -0.15595 | -0.16129 | 0.032043 | 0.054932 | -62.645 | 60.2783 | 60.2509 | 62.3566 | 62.5671 | 122.9279 | 62.471 | 60.4156
2621.7188 | 0.045776 | 0.42404 | -0.7872 | -0.24246 | 0.13992 | -0.27878 | -0.18478 | 60.5118 | -62.1872 | 0.16937 | -62.471 | 60.3561 | 62.4252 | 62.3749 | 0.045776 | -0.093994 | 0.064087 | 0.27878 | -0.16876 | -0.17303 | 0.13733 | 0.23346 | -62.6083 | 60.2921 | 60.2737 | 62.3657 | 62.5442 | 123.0377 | 62.4069 | 60.4065
2623.4219 | 0.045776 | 0.42191 | -0.78613 | -0.21896 | 0.14526 | -0.25528 | -0.18585 | 60.4431 | -62.3016 | -0.018311 | -62.5305 | 60.3653 | 62.439 | 62.3886 | 0.061035 | -0.089722 | 0.063019 | 0.27557 | -0.13992 | -0.16449 | -0.004578 | -0.009155 | -62.6678 | 60.2829 | 60.2737 | 62.3886 | 62.5671 | 123.0011 | 62.4664 | 60.3607
2625.0938 | 0.045776 | 0.41016 | -0.78827 | -0.23498 | 0.1506 | -0.2478 | -0.18265 | 60.4477 | -62.3108 | 0.059509 | -62.4985 | 60.4202 | 62.4435 | 62.4161 | 0.061035 | -0.070496 | 0.065155 | 0.28412 | -0.15595 | -0.16022 | 0.018311 | 0.082397 | -62.6999 | 60.3836 | 60.3653 | 62.352 | 62.5214 | 123.0927 | 62.3978 | 60.3973
2626.75 | 0.076294 | 0.4422 | -0.79254 | -0.21896 | 0.13886 | -0.27664 | -0.18158 | 60.466 | -62.2055 | 0.054932 | -62.5076 | 60.3104 | 62.439 | 62.3932 | 0.061035 | -0.099335 | 0.05661 | 0.27344 | -0.14526 | -0.15808 | 0.041199 | 0.068665 | -62.6358 | 60.2554 | 60.2509 | 62.3749 | 62.5763 | 122.9416 | 62.4435 | 60.4202
2628.4375 | 0.076294 | 0.41763 | -0.79468 | -0.22751 | 0.1506 | -0.2681 | -0.17944 | 60.4935 | -62.2284 | 0.1236 | -62.4802 | 60.3928 | 62.4435 | 62.3978 | 0.045776 | -0.086517 | 0.069427 | 0.27451 | -0.15915 | -0.15274 | 0.068665 | 0.13733 | -62.6862 | 60.347 | 60.3424 | 62.3978 | 62.5351 | 123.024 | 62.3886 | 60.3836
2630.1094 | 0.045776 | 0.43152 | -0.78293 | -0.2211 | 0.14526 | -0.25101 | -0.18265 | 60.4889 | -62.2421 | 0.068665 | -62.4939 | 60.4202 | 62.439 | 62.3978 | 0.045776 | -0.068359 | 0.05661 | 0.28625 | -0.13886 | -0.15915 | 0.041199 | 0.054932 | -62.6633 | 60.3333 | 60.3241 | 62.384 | 62.5442 | 123.0377 | 62.3978 | 60.4065
2631.7812 | 0.045776 | 0.42404 | -0.78613 | -0.21255 | 0.1474 | -0.25955 | -0.16876 | 60.4523 | -62.2467 | 0.027466 | -62.4847 | 60.3561 | 62.439 | 62.4069 | 0.076294 | -0.081177 | 0.058746 | 0.28732 | -0.14206 | -0.15701 | 0.009155 | 0.041199 | -62.6358 | 60.2737 | 60.2783 | 62.3657 | 62.5214 | 122.9919 | 62.4527 | 60.3836
2633.4375 | 0.030518 | 0.43579 | -0.78827 | -0.23819 | 0.14099 | -0.2948 | -0.18265 | 60.5072 | -62.178 | 0.16937 | -62.471 | 60.3378 | 62.4435 | 62.3978 | 0.076294 | -0.086517 | 0.066223 | 0.27878 | -0.17944 | -0.16342 | 0.13733 | 0.26093 | -62.59 | 60.2875 | 60.2554 | 62.352 | 62.5397 | 123.0515 | 62.4023 | 60.3745
2635.125 | 0.061035 | 0.41336 | -0.78186 | -0.20721 | 0.13672 | -0.24887 | -0.16876 | 60.4385 | -62.3337 | -0.004578 | -62.5305 | 60.4202 | 62.471 | 62.3978 | 0.045776 | -0.086517 | 0.061951 | 0.29587 | -0.13992 | -0.16129 | -0.07782 | -0.059509 | -62.7548 | 60.3195 | 60.3241 | 62.3749 | 62.5763 | 122.937 | 62.4481 | 60.4156
2636.7969 | 0.045776 | 0.439 | -0.7872 | -0.24033 | 0.14099 | -0.29373 | -0.18906 | 60.4889 | -62.1597 | 0.14648 | -62.4664 | 60.3424 | 62.4435 | 62.3978 | 0.061035 | -0.1004 | 0.063019 | 0.27985 | -0.16769 | -0.15595 | 0.15564 | 0.25635 | -62.5671 | 60.2966 | 60.2829 | 62.3566 | 62.5397 | 123.0698 | 62.4023 | 60.3607
2638.4688 | 0.045776 | 0.4422 | -0.77866 | -0.21149 | 0.14099 | -0.26382 | -0.16983 | 60.4797 | -62.2238 | 0.045776 | -62.471 | 60.3195 | 62.439 | 62.3978 | 0.030518 | -0.086517 | 0.059814 | 0.27771 | -0.14099 | -0.16129 | 0.022888 | 0.045776 | -62.6175 | 60.2783 | 60.2417 | 62.384 | 62.558 | 122.9645 | 62.4481 | 60.4202
2640.1406 | 0.045776 | 0.41443 | -0.77652 | -0.21469 | 0.15167 | -0.24674 | -0.17731 | 60.4568 | -62.2971 | -0.004578 | -62.5122 | 60.4019 | 62.4619 | 62.4069 | 0.061035 | -0.071564 | 0.069427 | 0.28305 | -0.14206 | -0.16983 | -0.07782 | -0.036621 | -62.7228 | 60.3378 | 60.3241 | 62.3795 | 62.5809 | 122.9416 | 62.4435 | 60.4294
2641.8125 | 0.061035 | 0.41336 | -0.78613 | -0.22003 | 0.14847 | -0.25101 | -0.1709 | 60.3928 | -62.3474 | -0.045776 | -62.5442 | 60.4111 | 62.4573 | 62.4115 | 0.045776 | -0.074768 | 0.064087 | 0.29159 | -0.15274 | -0.15808 | -0.086975 | -0.09613 | -62.7457 | 60.3333 | 60.3104 | 62.3886 | 62.5534 | 122.9416 | 62.439 | 60.434
2643.4844 | 0.076294 | 0.392 | -0.77652 | -0.24567 | 0.14313 | -0.24674 | -0.16769 | 60.4477 | -62.2879 | 0.068665 | -62.4802 | 60.4065 | 62.4619 | 62.3978 | 0.045776 | -0.082245 | 0.063019 | 0.29053 | -0.15808 | -0.16876 | 0.032043 | 0.082397 | -62.6678 | 60.3607 | 60.3287 | 62.3795 | 62.5214 | 123.0652 | 62.3795 | 60.3928
2645.1406 | 0.061035 | 0.439 | -0.79681 | -0.22751 | 0.15488 | -0.29587 | -0.17624 | 60.4019 | -62.2559 | 0.041199 | -62.4985 | 60.3195 | 62.4161 | 62.3886 | 0.061035 | -0.10574 | 0.068359 | 0.29159 | -0.15808 | -0.1506 | 0.013733 | 0.082397 | -62.6587 | 60.2875 | 60.26 | 62.3611 | 62.5534 | 122.9416 | 62.4573 | 60.4019
2646.7969 | 0.061035 | 0.41657 | -0.78293 | -0.24033 | 0.13992 | -0.2681 | -0.18372 | 60.4202 | -62.2971 | 0.054932 | -62.5259 | 60.4065 | 62.4344 | 62.3978 | 0.045776 | -0.079041 | 0.060883 | 0.29907 | -0.16556 | -0.16556 | 0.013733 | 0.073242 | -62.7045 | 60.3607 | 60.347 | 62.3566 | 62.5442 | 123.0469 | 62.3886 | 60.4202
2648.4531 | 0.076294 | 0.43579 | -0.77652 | -0.21149 | 0.14099 | -0.26596 | -0.1741 | 60.4706 | -62.2055 | 0.050354 | -62.4756 | 60.3195 | 62.4252 | 62.3932 | 0.045776 | -0.095062 | 0.049133 | 0.28519 | -0.14526 | -0.14954 | 0.022888 | 0.054932 | -62.6221 | 60.2417 | 60.2463 | 62.3703 | 62.5397 | 122.9691 | 62.4435 | 60.3973
2650.125 | 0.061035 | 0.42618 | -0.79254 | -0.23178 | 0.13351 | -0.2681 | -0.18585 | 60.4111 | -62.2879 | 0.059509 | -62.5076 | 60.4202 | 62.4344 | 62.4069 | 0.045776 | -0.076904 | 0.070496 | 0.29266 | -0.16342 | -0.16022 | 0.018311 | 0.073242 | -62.6907 | 60.3653 | 60.3333 | 62.3749 | 62.5351 | 123.056 | 62.3886 | 60.3973
2651.7812 | 0.061035 | 0.4187 | -0.78293 | -0.21042 | 0.15274 | -0.25635 | -0.17944 | 60.4019 | -62.352 | -0.036621 | -62.5351 | 60.3928 | 62.4481 | 62.4115 | 0.045776 | -0.077972 | 0.066223 | 0.28732 | -0.13779 | -0.16556 | -0.07782 | -0.086975 | -62.7731 | 60.3333 | 60.3287 | 62.3886 | 62.59 | 122.9416 | 62.4481 | 60.4248
2653.4375 | 0.061035 | 0.45288 | -0.79254 | -0.22858 | 0.13565 | -0.28839 | -0.17944 | 60.4202 | -62.2421 | 0.045776 | -62.5168 | 60.3378 | 62.4115 | 62.4023 | 0.061035 | -0.10147 | 0.066223 | 0.27878 | -0.16769 | -0.14954 | 0.004578 | 0.082397 | -62.6541 | 60.2692 | 60.2692 | 62.3749 | 62.5488 | 122.9507 | 62.4481 | 60.4065
2655.1094 | 0.045776 | 0.41977 | -0.77866 | -0.20401 | 0.14633 | -0.26703 | -0.17944 | 60.4202 | -62.352 | -0.050354 | -62.5305 | 60.4202 | 62.4573 | 62.4207 | 0.030518 | -0.070496 | 0.061951 | 0.29266 | -0.13779 | -0.15701 | -0.086975 | -0.09613 | -62.764 | 60.3378 | 60.3012 | 62.3566 | 62.5626 | 122.9279 | 62.4298 | 60.4065
2656.7812 | 0.045776 | 0.42831 | -0.78507 | -0.22003 | 0.14954 | -0.27237 | -0.17197 | 60.4706 | -62.2101 | 0.045776 | -62.4527 | 60.3104 | 62.4252 | 62.3886 | 0.091553 | -0.088654 | 0.058746 | 0.27451 | -0.14847 | -0.16769 | 0.004578 | 0.050354 | -62.6266 | 60.2737 | 60.228 | 62.3795 | 62.5534 | 122.9645 | 62.4435 | 60.3745
2658.4531 | 0.061035 | 0.41763 | -0.78613 | -0.2446 | 0.13565 | -0.28091 | -0.19546 | 60.4935 | -62.1735 | 0.16937 | -62.4527 | 60.3378 | 62.4252 | 62.3749 | 0.045776 | -0.099335 | 0.064087 | 0.28305 | -0.1741 | -0.16556 | 0.12817 | 0.24719 | -62.5809 | 60.2737 | 60.2646 | 62.3703 | 62.5305 | 123.0057 | 62.3932 | 60.3745
2660.125 | 0.045776 | 0.43793 | -0.78827 | -0.23605 | 0.1474 | -0.28198 | -0.18478 | 60.4889 | -62.1597 | 0.16022 | -62.4527 | 60.3287 | 62.4161 | 62.384 | 0.045776 | -0.10361 | 0.065155 | 0.27237 | -0.1709 | -0.16235 | 0.15106 | 0.24719 | -62.5671 | 60.2646 | 60.2692 | 62.3428 | 62.5214 | 123.0515 | 62.3795 | 60.379
2661.7812 | 0.015259 | 0.41016 | -0.7872 | -0.24033 | 0.1442 | -0.25528 | -0.18585 | 60.4202 | -62.2971 | 0.064087 | -62.5168 | 60.434 | 62.4161 | 62.3886 | 0.061035 | -0.069427 | 0.069427 | 0.28412 | -0.16876 | -0.16876 | 0.018311 | 0.064087 | -62.6907 | 60.3424 | 60.3241 | 62.3657 | 62.5305 | 123.0652 | 62.3657 | 60.4248
2663.4375 | 0.030518 | 0.42511 | -0.79468 | -0.20401 | 0.1474 | -0.25101 | -0.17303 | 60.4294 | -62.2971 | -0.018311 | -62.5259 | 60.3561 | 62.4252 | 62.3886 | 0.045776 | -0.080109 | 0.060883 | 0.29159 | -0.14206 | -0.16663 | -0.013733 | -0.027466 | -62.6358 | 60.2692 | 60.2371 | 62.3703 | 62.5351 | 122.9782 | 62.3932 | 60.3699
2665.0938 | 0.030518 | 0.41229 | -0.78934 | -0.23605 | 0.1506 | -0.27557 | -0.16769 | 60.4889 | -62.1872 | 0.16022 | -62.4619 | 60.3333 | 62.4023 | 62.352 | 0.061035 | -0.10361 | 0.063019 | 0.27985 | -0.16876 | -0.15488 | 0.11444 | 0.2243 | -62.6038 | 60.2829 | 60.2966 | 62.3611 | 62.5397 | 123.0194 | 62.3749 | 60.3836
2666.7656 | 0.045776 | 0.42725 | -0.79147 | -0.23498 | 0.15808 | -0.26916 | -0.18372 | 60.466 | -62.2009 | 0.064087 | -62.4802 | 60.3195 | 62.4023 | 62.3795 | 0.045776 | -0.099335 | 0.068359 | 0.28305 | -0.15595 | -0.15808 | 0.032043 | 0.068665 | -62.6312 | 60.2371 | 60.2325 | 62.3611 | 62.5626 | 122.905 | 62.439 | 60.4156
2668.4375 | 0.061035 | 0.42831 | -0.79041 | -0.22537 | 0.14954 | -0.27557 | -0.18051 | 60.4935 | -62.178 | 0.19226 | -62.4527 | 60.3241 | 62.3886 | 62.3657 | 0.076294 | -0.093994 | 0.071564 | 0.27878 | -0.16556 | -0.17197 | 0.13733 | 0.25177 | -62.5854 | 60.2737 | 60.2463 | 62.3566 | 62.5168 | 123.0011 | 62.3566 | 60.3973
2670.1094 | 0.045776 | 0.41763 | -0.77438 | -0.21149 | 0.15167 | -0.24353 | -0.17624 | 60.4111 | -62.3337 | -0.027466 | -62.5214 | 60.4065 | 62.4435 | 62.3978 | 0.045776 | -0.070496 | 0.066223 | 0.28732 | -0.13351 | -0.1741 | -0.09613 | -0.10529 | -62.764 | 60.347 | 60.3241 | 62.3749 | 62.558 | 122.9279 | 62.4161 | 60.3928
2671.7812 | 0.061035 | 0.41657 | -0.78613 | -0.2243 | 0.13779 | -0.25101 | -0.16983 | 60.3836 | -62.3337 | -0.059509 | -62.5351 | 60.3836 | 62.4298 | 62.3978 | 0.061035 | -0.075836 | 0.069427 | 0.28519 | -0.13992 | -0.15701 | -0.07782 | -0.09613 | -62.7274 | 60.347 | 60.2921 | 62.3978 | 62.5534 | 122.9599 | 62.4161 | 60.4065
2673.4531 | 0.076294 | 0.43045 | -0.79041 | -0.25314 | 0.1506 | -0.29159 | -0.18585 | 60.4019 | -62.2467 | 0.064087 | -62.4985 | 60.3333 | 62.4435 | 62.3932 | 0.061035 | -0.092926 | 0.070496 | 0.28732 | -0.16556 | -0.16235 | 0.073242 | 0.14648 | -62.6129 | 60.2737 | 60.2509 | 62.3383 | 62.5488 | 123.0103 | 62.4069 | 60.3653
2675.125 | 0.045776 | 0.45181 | -0.78827 | -0.2211 | 0.15167 | -0.27557 | -0.17944 | 60.4568 | -62.2147 | 0.059509 | -62.4939 | 60.3149 | 62.4252 | 62.384 | 0.061035 | -0.087585 | 0.060883 | 0.29266 | -0.15701 | -0.15808 | 0.041199 | 0.073242 | -62.6312 | 60.2417 | 60.2371 | 62.3657 | 62.5442 | 122.9141 | 62.4573 | 60.4065
2676.7812 | 0.045776 | 0.40695 | -0.78186 | -0.25101 | 0.16022 | -0.2681 | -0.18585 | 60.4706 | -62.2009 | 0.14648 | -62.4527 | 60.3561 | 62.4069 | 62.3795 | 0.076294 | -0.087585 | 0.064087 | 0.27878 | -0.16769 | -0.16876 | 0.091553 | 0.17853 | -62.6404 | 60.3287 | 60.2921 | 62.3657 | 62.5076 | 123.0057 | 62.3703 | 60.4065
2678.4531 | 0.061035 | 0.42084 | -0.78186 | -0.23071 | 0.14099 | -0.27451 | -0.19119 | 60.4889 | -62.1872 | 0.1831 | -62.4481 | 60.3241 | 62.3978 | 62.3795 | 0.045776 | -0.09079 | 0.060883 | 0.28946 | -0.16876 | -0.16769 | 0.12817 | 0.24261 | -62.5809 | 60.3012 | 60.2921 | 62.3383 | 62.5168 | 123.0148 | 62.3703 | 60.4202
2680.125 | 0.061035 | 0.43793 | -0.79147 | -0.20828 | 0.1474 | -0.2681 | -0.16876 | 60.4935 | -62.2009 | 0.059509 | -62.4619 | 60.3195 | 62.4161 | 62.3657 | 0.061035 | -0.087585 | 0.045929 | 0.28839 | -0.14099 | -0.16876 | 0.045776 | 0.07782 | -62.5992 | 60.2463 | 60.228 | 62.3611 | 62.5122 | 122.9233 | 62.4298 | 60.4111
2681.7812 | 0.061035 | 0.41977 | -0.7872 | -0.22858 | 0.13672 | -0.27878 | -0.18585 | 60.4156 | -62.265 | 0.036621 | -62.5031 | 60.3333 | 62.4344 | 62.3978 | 0.045776 | -0.086517 | 0.061951 | 0.27451 | -0.15808 | -0.16342 | 0.027466 | 0.068665 | -62.6541 | 60.2783 | 60.26 | 62.3703 | 62.5259 | 122.9324 | 62.4252 | 60.4065
2683.4531 | 0.061035 | 0.41977 | -0.78507 | -0.21362 | 0.1474 | -0.23498 | -0.17197 | 60.4202 | -62.3108 | -0.036621 | -62.5259 | 60.3928 | 62.4252 | 62.3611 | 0.061035 | -0.070496 | 0.059814 | 0.28412 | -0.13886 | -0.16663 | -0.09613 | -0.086975 | -62.7457 | 60.3378 | 60.3012 | 62.3795 | 62.5534 | 122.9233 | 62.4207 | 60.4294
2685.1094 | 0.045776 | 0.4187 | -0.78613 | -0.22858 | 0.14206 | -0.27878 | -0.17944 | 60.4706 | -62.1552 | 0.19226 | -62.4435 | 60.3241 | 62.4115 | 62.3749 | 0.045776 | -0.095062 | 0.050201 | 0.27664 | -0.15808 | -0.16129 | 0.14191 | 0.24719 | -62.5717 | 60.2646 | 60.2554 | 62.3337 | 62.5442 | 122.9919 | 62.3703 | 60.3745
2686.7656 | 0.061035 | 0.41657 | -0.78079 | -0.1976 | 0.13458 | -0.24353 | -0.16449 | 60.4111 | -62.3291 | -0.054932 | -62.5259 | 60.379 | 62.4435 | 62.3795 | 0.045776 | -0.072632 | 0.067291 | 0.28305 | -0.14099 | -0.16129 | -0.091553 | -0.10071 | -62.7365 | 60.3241 | 60.2921 | 62.3932 | 62.5397 | 122.9553 | 62.4207 | 60.3836
2688.4219 | 0.091553 | 0.44006 | -0.79147 | -0.23605 | 0.13458 | -0.29587 | -0.18158 | 60.4248 | -62.1964 | 0.09613 | -62.4664 | 60.3378 | 62.4252 | 62.3611 | 0.076294 | -0.11215 | 0.058746 | 0.27771 | -0.16342 | -0.14099 | 0.10071 | 0.18768 | -62.5671 | 60.26 | 60.2325 | 62.3291 | 62.5031 | 123.0194 | 62.3749 | 60.3333
2690.0938 | 0.076294 | 0.41657 | -0.77438 | -0.22217 | 0.13779 | -0.23071 | -0.17303 | 60.4431 | -62.2696 | 0.068665 | -62.4664 | 60.4019 | 62.4252 | 62.3795 | 0.045776 | -0.0737 | 0.079041 | 0.29266 | -0.15167 | -0.18051 | 0.032043 | 0.09613 | -62.6587 | 60.3241 | 60.3241 | 62.3657 | 62.5351 | 123.024 | 62.3474 | 60.3882
2691.75 | 0.030518 | 0.42618 | -0.79147 | -0.21896 | 0.13351 | -0.24994 | -0.16235 | 60.4019 | -62.2925 | -0.050354 | -62.5259 | 60.3928 | 62.439 | 62.3795 | 0.030518 | -0.0737 | 0.058746 | 0.29159 | -0.14526 | -0.16235 | -0.068665 | -0.086975 | -62.6907 | 60.3149 | 60.3058 | 62.3795 | 62.5534 | 122.9416 | 62.4115 | 60.4019
2693.4219 | 0.045776 | 0.41229 | -0.79147 | -0.23392 | 0.14313 | -0.24674 | -0.16663 | 60.4248 | -62.233 | 0.073242 | -62.471 | 60.3928 | 62.4298 | 62.3978 | 0.045776 | -0.084381 | 0.058746 | 0.28946 | -0.14526 | -0.15701 | 0.036621 | 0.086975 | -62.6541 | 60.3287 | 60.3104 | 62.3657 | 62.5259 | 123.0469 | 62.3291 | 60.3836
2695.0938 | 0.061035 | 0.41016 | -0.78293 | -0.21896 | 0.14847 | -0.26169 | -0.1709 | 60.3607 | -62.3062 | -0.050354 | -62.5214 | 60.3745 | 62.4435 | 62.3978 | 0.061035 | -0.076904 | 0.059814 | 0.27451 | -0.13672 | -0.16342 | -0.10071 | -0.091553 | -62.7136 | 60.3012 | 60.3058 | 62.3749 | 62.5442 | 122.9279 | 62.4344 | 60.3928
2696.7969 | 0.045776 | 0.40054 | -0.78613 | -0.2179 | 0.14633 | -0.24994 | -0.16342 | 60.4477 | -62.2055 | 0.068665 | -62.4847 | 60.3653 | 62.4207 | 62.3657 | 0.045776 | -0.079041 | 0.057678 | 0.28519 | -0.14526 | -0.15381 | -0.004578 | 0.045776 | -62.6678 | 60.3104 | 60.2966 | 62.3611 | 62.558 | 122.9782 | 62.4023 | 60.4065
2698.4688 | 0.061035 | 0.41336 | -0.79041 | -0.22003 | 0.1442 | -0.27664 | -0.16876 | 60.4202 | -62.1826 | 0.054932 | -62.4573 | 60.3149 | 62.4023 | 62.3611 | 0.030518 | -0.091858 | 0.061951 | 0.27878 | -0.15167 | -0.14847 | 0 | 0.073242 | -62.5992 | 60.2371 | 60.2234 | 62.3703 | 62.5214 | 122.9279 | 62.4069 | 60.3745
2700.1406 | 0.015259 | 0.42938 | -0.78507 | -0.2478 | 0.14526 | -0.28519 | -0.17838 | 60.4431 | -62.1414 | 0.16937 | -62.439 | 60.3104 | 62.3978 | 62.3657 | 0.061035 | -0.097198 | 0.059814 | 0.27664 | -0.17838 | -0.16129 | 0.13275 | 0.27008 | -62.5763 | 60.2554 | 60.228 | 62.3428 | 62.5259 | 122.9965 | 62.4115 | 60.3561
2701.7969 | 0.045776 | 0.41016 | -0.78079 | -0.24994 | 0.16129 | -0.26062 | -0.1741 | 60.3973 | -62.2879 | 0.059509 | -62.4847 | 60.3699 | 62.4069 | 62.3657 | 0.061035 | -0.076904 | 0.075836 | 0.29266 | -0.16769 | -0.17303 | 0.018311 | 0.086975 | -62.6541 | 60.347 | 60.3333 | 62.3474 | 62.5168 | 123.0423 | 62.352 | 60.3882
2703.4688 | 0.045776 | 0.42084 | -0.77866 | -0.24994 | 0.13886 | -0.28412 | -0.17624 | 60.466 | -62.146 | 0.16022 | -62.4435 | 60.3058 | 62.4069 | 62.3795 | 0.076294 | -0.09613 | 0.071564 | 0.27771 | -0.17197 | -0.16983 | 0.13275 | 0.2655 | -62.5671 | 60.26 | 60.2554 | 62.3337 | 62.5122 | 122.9874 | 62.3566 | 60.3699
2705.1562 | 0.061035 | 0.4187 | -0.77759 | -0.20508 | 0.12497 | -0.2478 | -0.17517 | 60.3882 | -62.3703 | -0.041199 | -62.5442 | 60.3836 | 62.4344 | 62.4115 | 0.061035 | -0.068359 | 0.058746 | 0.298 | -0.1442 | -0.16556 | -0.091553 | -0.10986 | -62.7228 | 60.3241 | 60.3241 | 62.3611 | 62.5442 | 122.905 | 62.4023 | 60.4111
2706.8281 | 0.061035 | 0.41336 | -0.78934 | -0.24033 | 0.1474 | -0.28732 | -0.1741 | 60.466 | -62.1735 | 0.17395 | -62.4435 | 60.3149 | 62.4207 | 62.3474 | 0.030518 | -0.082245 | 0.065155 | 0.27771 | -0.16235 | -0.16342 | 0.12817 | 0.24261 | -62.5809 | 60.2509 | 60.2783 | 62.3154 | 62.5397 | 122.9782 | 62.3795 | 60.4065
2708.4844 | 0.076294 | 0.42191 | -0.77225 | -0.20401 | 0.13565 | -0.23605 | -0.17731 | 60.4019 | -62.3108 | -0.041199 | -62.5351 | 60.3516 | 62.4344 | 62.3886 | 0.045776 | -0.0737 | 0.063019 | 0.29159 | -0.14847 | -0.1709 | -0.086975 | -0.064087 | -62.7319 | 60.3333 | 60.3333 | 62.384 | 62.5534 | 122.8912 | 62.4023 | 60.4065
2710.1406 | 0.061035 | 0.439 | -0.79361 | -0.23392 | 0.14633 | -0.29373 | -0.18478 | 60.4294 | -62.1643 | 0.1236 | -62.4435 | 60.3241 | 62.3978 | 62.3886 | 0.061035 | -0.10788 | 0.067291 | 0.27878 | -0.16556 | -0.16342 | 0.12817 | 0.21515 | -62.558 | 60.26 | 60.2509 | 62.352 | 62.5168 | 123.0148 | 62.3703 | 60.347
2711.7969 | 0.045776 | 0.40588 | -0.77652 | -0.24033 | 0.14954 | -0.26596 | -0.17838 | 60.4477 | -62.2192 | 0.13733 | -62.4619 | 60.3516 | 62.4023 | 62.384 | 0.061035 | -0.093994 | 0.064087 | 0.28519 | -0.16983 | -0.17197 | 0.054932 | 0.14648 | -62.6495 | 60.3333 | 60.3104 | 62.3474 | 62.5442 | 122.9736 | 62.3611 | 60.3973
2713.4688 | 0.076294 | 0.42511 | -0.78827 | -0.22644 | 0.15488 | -0.24674 | -0.17731 | 60.466 | -62.178 | 0.073242 | -62.4664 | 60.3058 | 62.3795 | 62.3611 | 0.045776 | -0.084381 | 0.068359 | 0.28305 | -0.16556 | -0.15915 | 0.059509 | 0.073242 | -62.5992 | 60.2417 | 60.228 | 62.3657 | 62.5397 | 122.8867 | 62.4207 | 60.379
2715.1406 | 0.061035 | 0.43152 | -0.79468 | -0.22217 | 0.1474 | -0.28519 | -0.18906 | 60.4111 | -62.2238 | 0.036621 | -62.4847 | 60.3241 | 62.4344 | 62.3703 | 0.061035 | -0.095062 | 0.059814 | 0.27557 | -0.16022 | -0.15488 | 0.022888 | 0.064087 | -62.6312 | 60.2783 | 60.228 | 62.3611 | 62.5442 | 122.8958 | 62.3978 | 60.379
2716.7969 | 0.045776 | 0.41657 | -0.77225 | -0.23285 | 0.12497 | -0.24033 | -0.17624 | 60.4568 | -62.233 | 0.073242 | -62.4664 | 60.3882 | 62.4207 | 62.3703 | 0.045776 | -0.074768 | 0.0737 | 0.28732 | -0.14313 | -0.17197 | 0.027466 | 0.073242 | -62.6404 | 60.3241 | 60.26 | 62.3474 | 62.5214 | 123.0194 | 62.3337 | 60.3653
2718.4531 | 0.045776 | 0.43472 | -0.79147 | -0.21149 | 0.1474 | -0.27985 | -0.17303 | 60.4248 | -62.1826 | 0.041199 | -62.4847 | 60.2829 | 62.4344 | 62.3749 | 0.045776 | -0.092926 | 0.065155 | 0.28198 | -0.15595 | -0.16129 | 0.027466 | 0.068665 | -62.6221 | 60.2646 | 60.2234 | 62.3474 | 62.5351 | 122.8683 | 62.4298 | 60.3836
2720.1094 | 0.045776 | 0.42725 | -0.7872 | -0.24033 | 0.14206 | -0.26489 | -0.18051 | 60.3836 | -62.2513 | 0.059509 | -62.5122 | 60.3653 | 62.439 | 62.3703 | 0.030518 | -0.083313 | 0.060883 | 0.28305 | -0.15915 | -0.17624 | 0.036621 | 0.10529 | -62.6816 | 60.3378 | 60.3516 | 62.3703 | 62.5351 | 122.9919 | 62.3474 | 60.3928
2721.7656 | 0.076294 | 0.42938 | -0.77545 | -0.20615 | 0.13565 | -0.24246 | -0.18051 | 60.3928 | -62.3016 | -0.054932 | -62.5122 | 60.3836 | 62.4161 | 62.3795 | 0.030518 | -0.068359 | 0.060883 | 0.28519 | -0.13245 | -0.15701 | -0.086975 | -0.09613 | -62.6999 | 60.2921 | 60.3012 | 62.3657 | 62.5214 | 122.9095 | 62.4344 | 60.379
2723.4375 | 0.030518 | 0.42725 | -0.7872 | -0.23926 | 0.15595 | -0.28625 | -0.18265 | 60.4065 | -62.2147 | 0.082397 | -62.4619 | 60.3195 | 62.3932 | 62.3795 | 0.076294 | -0.10895 | 0.064087 | 0.28305 | -0.18051 | -0.15701 | 0.07782 | 0.15564 | -62.59 | 60.2692 | 60.2692 | 62.3383 | 62.5259 | 122.9919 | 62.3886 | 60.3699
2725.1094 | 0.045776 | 0.41336 | -0.77652 | -0.22644 | 0.14313 | -0.24246 | -0.17303 | 60.434 | -62.2284 | 0.059509 | -62.4527 | 60.4019 | 62.4023 | 62.3886 | 0.061035 | -0.072632 | 0.05661 | 0.28625 | -0.16129 | -0.16983 | 0.027466 | 0.07782 | -62.645 | 60.3287 | 60.3104 | 62.3474 | 62.5442 | 123.0148 | 62.3428 | 60.3836
2726.7812 | 0.045776 | 0.41229 | -0.77866 | -0.21255 | 0.13565 | -0.2478 | -0.17731 | 60.3882 | -62.2925 | -0.064087 | -62.5168 | 60.379 | 62.4207 | 62.384 | 0.045776 | -0.077972 | 0.065155 | 0.28625 | -0.14313 | -0.16983 | -0.07782 | -0.09613 | -62.7182 | 60.3195 | 60.2783 | 62.3703 | 62.5534 | 122.9141 | 62.4298 | 60.3653
2728.4531 | 0.045776 | 0.42618 | -0.79788 | -0.23926 | 0.14847 | -0.28519 | -0.17624 | 60.4523 | -62.1368 | 0.17853 | -62.4161 | 60.3104 | 62.4023 | 62.3383 | 0.061035 | -0.10788 | 0.068359 | 0.27878 | -0.17624 | -0.15701 | 0.15564 | 0.27008 | -62.5351 | 60.2463 | 60.2554 | 62.3199 | 62.5214 | 122.9828 | 62.3428 | 60.3745
2730.125 | 0.030518 | 0.42938 | -0.77438 | -0.21469 | 0.14206 | -0.25101 | -0.16769 | 60.4523 | -62.2101 | 0.068665 | -62.4664 | 60.379 | 62.4069 | 62.3657 | 0.061035 | -0.081177 | 0.059814 | 0.28839 | -0.13992 | -0.16556 | 0.032043 | 0.068665 | -62.6312 | 60.2875 | 60.2966 | 62.3428 | 62.4893 | 123.0011 | 62.3611 | 60.3836
2731.7969 | 0.045776 | 0.41229 | -0.76904 | -0.20187 | 0.14526 | -0.25742 | -0.16769 | 60.3653 | -62.3062 | -0.032043 | -62.5031 | 60.3699 | 62.4298 | 62.384 | 0.076294 | -0.070496 | 0.068359 | 0.27985 | -0.13351 | -0.16769 | -0.10529 | -0.091553 | -62.7182 | 60.3287 | 60.2829 | 62.3611 | 62.5397 | 122.8729 | 62.4069 | 60.3928
2733.5 | 0.045776 | 0.41122 | -0.77866 | -0.2243 | 0.15701 | -0.25635 | -0.16769 | 60.4294 | -62.2055 | 0.07782 | -62.4664 | 60.379 | 62.4207 | 62.3657 | 0.045776 | -0.082245 | 0.075836 | 0.29587 | -0.15167 | -0.16663 | 0.004578 | 0.07782 | -62.6266 | 60.3104 | 60.2875 | 62.3611 | 62.5122 | 122.9736 | 62.3749 | 60.3973
2735.1719 | 0.030518 | 0.41336 | -0.78827 | -0.23605 | 0.13886 | -0.28732 | -0.18265 | 60.3516 | -62.2375 | 0.068665 | -62.4847 | 60.3699 | 62.4252 | 62.3703 | 0.045776 | -0.1004 | 0.072632 | 0.28519 | -0.16769 | -0.15381 | 0.022888 | 0.13275 | -62.6678 | 60.2875 | 60.2921 | 62.3611 | 62.5122 | 122.9691 | 62.352 | 60.379
2736.8438 | 0.061035 | 0.40909 | -0.784 | -0.22324 | 0.14954 | -0.25635 | -0.17731 | 60.3516 | -62.2879 | -0.059509 | -62.5168 | 60.3882 | 62.439 | 62.3749 | 0.061035 | -0.079041 | 0.058746 | 0.27451 | -0.14526 | -0.16449 | -0.09613 | -0.09613 | -62.709 | 60.3241 | 60.2783 | 62.3474 | 62.5305 | 122.9095 | 62.3932 | 60.3745
2738.5781 | 0.076294 | 0.41657 | -0.78079 | -0.2179 | 0.14206 | -0.25848 | -0.18158 | 60.3836 | -62.2147 | -0.009155 | -62.4802 | 60.3149 | 62.3886 | 62.3611 | 0.030518 | -0.082245 | 0.058746 | 0.27771 | -0.14099 | -0.16876 | -0.004578 | 0.032043 | -62.5809 | 60.228 | 60.2325 | 62.3383 | 62.5168 | 122.9279 | 62.4069 | 60.3653
2740.25 | 0.061035 | 0.41657 | -0.79147 | -0.24567 | 0.14954 | -0.27878 | -0.18372 | 60.4294 | -62.1414 | 0.16479 | -62.4252 | 60.2921 | 62.384 | 62.3337 | 0.045776 | -0.095062 | 0.058746 | 0.29694 | -0.16769 | -0.15808 | 0.11444 | 0.23804 | -62.5671 | 60.2509 | 60.26 | 62.3245 | 62.5214 | 122.9507 | 62.3703 | 60.3745
2741.9375 | 0.045776 | 0.42938 | -0.78507 | -0.23178 | 0.1442 | -0.25101 | -0.19012 | 60.3882 | -62.2604 | 0.045776 | -62.471 | 60.3836 | 62.4435 | 62.3474 | 0.061035 | -0.077972 | 0.065155 | 0.27451 | -0.15381 | -0.16022 | 0.004578 | 0.073242 | -62.6724 | 60.3378 | 60.3195 | 62.3566 | 62.5214 | 123.0011 | 62.3383 | 60.3745
2743.6406 | 0.061035 | 0.42938 | -0.77438 | -0.21469 | 0.13458 | -0.2478 | -0.17517 | 60.4248 | -62.2192 | 0.082397 | -62.4527 | 60.3607 | 62.4069 | 62.352 | 0.045776 | -0.072632 | 0.069427 | 0.27664 | -0.13886 | -0.17197 | 0.022888 | 0.082397 | -62.6266 | 60.3058 | 60.3058 | 62.3245 | 62.5214 | 122.9965 | 62.3245 | 60.3561
2745.3125 | 0.061035 | 0.43259 | -0.78613 | -0.23178 | 0.14954 | -0.28625 | -0.17197 | 60.3882 | -62.2238 | 0.041199 | -62.471 | 60.3012 | 62.3978 | 62.3474 | 0.076294 | -0.10468 | 0.068359 | 0.27664 | -0.16449 | -0.16449 | 0.018311 | 0.073242 | -62.6266 | 60.2325 | 60.2325 | 62.3795 | 62.5168 | 122.8867 | 62.4069 | 60.3561
2747 | 0.045776 | 0.41122 | -0.79041 | -0.21469 | 0.12924 | -0.24887 | -0.18051 | 60.3653 | -62.2971 | -0.036621 | -62.5214 | 60.4019 | 62.4207 | 62.3795 | 0.045776 | -0.082245 | 0.065155 | 0.27878 | -0.13138 | -0.1709 | -0.091553 | -0.09613 | -62.6999 | 60.3104 | 60.2783 | 62.3611 | 62.5305 | 122.9095 | 62.3932 | 60.3836
2748.6562 | 0.045776 | 0.41229 | -0.78293 | -0.24139 | 0.1442 | -0.28412 | -0.18799 | 60.434 | -62.1231 | 0.18768 | -62.4252 | 60.3195 | 62.3795 | 62.352 | 0.061035 | -0.10574 | 0.060883 | 0.27664 | -0.16663 | -0.16342 | 0.13275 | 0.24719 | -62.558 | 60.2463 | 60.2554 | 62.3245 | 62.4893 | 122.9416 | 62.352 | 60.3516
2750.3281 | 0.061035 | 0.41763 | -0.77438 | -0.22964 | 0.13351 | -0.24674 | -0.16556 | 60.4431 | -62.2055 | 0.073242 | -62.439 | 60.3607 | 62.3886 | 62.3428 | 0.061035 | -0.080109 | 0.052338 | 0.28412 | -0.1474 | -0.18051 | 0.022888 | 0.050354 | -62.6358 | 60.2921 | 60.2875 | 62.3337 | 62.5031 | 122.9645 | 62.3566 | 60.3607
2752 | 0.045776 | 0.40054 | -0.77972 | -0.23285 | 0.14206 | -0.25314 | -0.1709 | 60.4294 | -62.2284 | 0.07782 | -62.439 | 60.379 | 62.4252 | 62.3566 | 0.015259 | -0.079041 | 0.069427 | 0.28412 | -0.15488 | -0.16342 | 0.004578 | 0.073242 | -62.6312 | 60.2966 | 60.3012 | 62.3245 | 62.4985 | 122.9965 | 62.3291 | 60.3745
2753.6719 | 0.061035 | 0.4187 | -0.78293 | -0.22003 | 0.13672 | -0.25101 | -0.1741 | 60.4385 | -62.2101 | 0.068665 | -62.4435 | 60.3561 | 62.4069 | 62.3703 | 0.030518 | -0.088654 | 0.05127 | 0.29159 | -0.14206 | -0.16129 | 0.004578 | 0.032043 | -62.6312 | 60.2921 | 60.2783 | 62.3337 | 62.5168 | 122.9141 | 62.3703 | 60.3882
2755.3438 | 0.045776 | 0.43152 | -0.7872 | -0.21683 | 0.14206 | -0.28198 | -0.1709 | 60.4248 | -62.1689 | 0.050354 | -62.4344 | 60.2921 | 62.3703 | 62.3566 | 0.045776 | -0.098267 | 0.057678 | 0.28305 | -0.15701 | -0.16342 | 0.018311 | 0.054932 | -62.5854 | 60.2142 | 60.2371 | 62.352 | 62.5031 | 122.8683 | 62.4161 | 60.3653
2757.0469 | 0.076294 | 0.42831 | -0.79361 | -0.22644 | 0.14313 | -0.29053 | -0.17838 | 60.3882 | -62.2101 | 0.054932 | -62.4664 | 60.2921 | 62.3886 | 62.3749 | 0.061035 | -0.099335 | 0.075836 | 0.27451 | -0.16235 | -0.16129 | 0.009155 | 0.068665 | -62.6038 | 60.2417 | 60.26 | 62.3291 | 62.5122 | 122.8455 | 62.4161 | 60.3745
2758.7344 | 0.030518 | 0.40695 | -0.77331 | -0.22003 | 0.13992 | -0.24139 | -0.17303 | 60.4614 | -62.2101 | 0.050354 | -62.4435 | 60.3424 | 62.4207 | 62.3474 | 0.061035 | -0.074768 | 0.069427 | 0.29587 | -0.13886 | -0.17517 | -0.009155 | 0.018311 | -62.6587 | 60.3149 | 60.2829 | 62.3383 | 62.4939 | 122.9095 | 62.384 | 60.3836
2760.3906 | 0.061035 | 0.45181 | -0.79361 | -0.22217 | 0.13351 | -0.29373 | -0.18265 | 60.3607 | -62.2147 | 0.036621 | -62.4664 | 60.2966 | 62.4069 | 62.352 | 0.045776 | -0.1004 | 0.057678 | 0.27451 | -0.16235 | -0.16022 | 0.009155 | 0.091553 | -62.6083 | 60.2463 | 60.2509 | 62.3383 | 62.5168 | 122.8821 | 62.4207 | 60.3699
2762.0469 | 0.061035 | 0.43045 | -0.78507 | -0.24139 | 0.15595 | -0.28732 | -0.17944 | 60.3928 | -62.2192 | 0.064087 | -62.4527 | 60.3333 | 62.3978 | 62.3566 | 0.061035 | -0.092926 | 0.061951 | 0.28946 | -0.17517 | -0.1709 | 0.064087 | 0.15106 | -62.5717 | 60.2371 | 60.2463 | 62.3062 | 62.4985 | 122.9691 | 62.3474 | 60.3882
2763.7344 | 0.061035 | 0.439 | -0.77866 | -0.21896 | 0.14313 | -0.25848 | -0.17624 | 60.4477 | -62.1826 | 0.050354 | -62.4435 | 60.2875 | 62.4023 | 62.3657 | 0.061035 | -0.084381 | 0.053406 | 0.27878 | -0.13992 | -0.17197 | 0.018311 | 0.036621 | -62.5946 | 60.2371 | 60.1822 | 62.3291 | 62.4985 | 122.8912 | 62.3978 | 60.3333
2765.3906 | 0.045776 | 0.4155 | -0.79361 | -0.23285 | 0.15808 | -0.25635 | -0.17517 | 60.4202 | -62.2147 | 0.10986 | -62.4619 | 60.3424 | 62.3795 | 62.3566 | 0.045776 | -0.077972 | 0.066223 | 0.28198 | -0.1709 | -0.16342 | 0.054932 | 0.12817 | -62.6541 | 60.3149 | 60.2921 | 62.3428 | 62.4985 | 122.9416 | 62.3428 | 60.4065
2767.0625 | 0.045776 | 0.40695 | -0.7872 | -0.20721 | 0.14847 | -0.24353 | -0.17517 | 60.3607 | -62.2787 | -0.045776 | -62.5076 | 60.3699 | 62.3886 | 62.3795 | 0.076294 | -0.072632 | 0.057678 | 0.29694 | -0.12924 | -0.16983 | -0.09613 | -0.09613 | -62.7136 | 60.2921 | 60.2921 | 62.3383 | 62.5214 | 122.85 | 62.4161 | 60.4019
2768.7344 | 0.045776 | 0.40909 | -0.77225 | -0.23178 | 0.13779 | -0.25421 | -0.17517 | 60.4523 | -62.1918 | 0.073242 | -62.4527 | 60.3561 | 62.3886 | 62.3428 | 0.045776 | -0.076904 | 0.077972 | 0.28732 | -0.14633 | -0.17838 | 0.032043 | 0.068665 | -62.6266 | 60.3012 | 60.2875 | 62.3291 | 62.5031 | 122.937 | 62.3657 | 60.3653
2770.3906 | 0.045776 | 0.42404 | -0.79254 | -0.23605 | 0.14099 | -0.29266 | -0.18265 | 60.3836 | -62.1552 | 0.091553 | -62.4344 | 60.3104 | 62.3978 | 62.3291 | 0.061035 | -0.10574 | 0.061951 | 0.26382 | -0.16663 | -0.15274 | 0.10986 | 0.20599 | -62.5534 | 60.2417 | 60.2371 | 62.3428 | 62.4985 | 122.9828 | 62.3428 | 60.3378
2772.0469 | 0.045776 | 0.38132 | -0.78186 | -0.2478 | 0.13886 | -0.2478 | -0.17944 | 60.4614 | -62.2055 | 0.073242 | -62.4527 | 60.347 | 62.3886 | 62.3474 | 0.045776 | -0.0737 | 0.083313 | 0.29587 | -0.1442 | -0.1741 | 0 | 0.045776 | -62.6404 | 60.3104 | 60.2783 | 62.3245 | 62.5122 | 122.9141 | 62.3611 | 60.3745
2773.7031 | 0.045776 | 0.42084 | -0.79147 | -0.22537 | 0.13458 | -0.26382 | -0.17303 | 60.3745 | -62.2559 | -0.050354 | -62.4939 | 60.3333 | 62.3795 | 62.3566 | 0.045776 | -0.087585 | 0.067291 | 0.28198 | -0.15488 | -0.15274 | -0.054932 | -0.054932 | -62.6541 | 60.2783 | 60.2371 | 62.3474 | 62.4893 | 122.8821 | 62.3795 | 60.3424
2775.4062 | 0.061035 | 0.439 | -0.78934 | -0.23498 | 0.13458 | -0.28625 | -0.17838 | 60.3516 | -62.2192 | 0.045776 | -62.471 | 60.3058 | 62.3932 | 62.3383 | 0.076294 | -0.092926 | 0.064087 | 0.28519 | -0.16235 | -0.15808 | 0.018311 | 0.11444 | -62.5992 | 60.2417 | 60.2417 | 62.3428 | 62.5351 | 122.9004 | 62.384 | 60.347
2777.0625 | 0.061035 | 0.41336 | -0.77652 | -0.23712 | 0.13672 | -0.24353 | -0.19119 | 60.3928 | -62.2559 | 0.041199 | -62.4527 | 60.3745 | 62.4207 | 62.3474 | 0.061035 | -0.080109 | 0.068359 | 0.2948 | -0.15167 | -0.16449 | 0.032043 | 0.10071 | -62.6358 | 60.3149 | 60.2921 | 62.3245 | 62.5031 | 123.0057 | 62.3291 | 60.379
2778.75 | 0.045776 | 0.42831 | -0.78186 | -0.23605 | 0.13779 | -0.29587 | -0.18478 | 60.3882 | -62.2055 | 0.050354 | -62.4756 | 60.2875 | 62.3749 | 62.3428 | 0.061035 | -0.095062 | 0.065155 | 0.28305 | -0.1709 | -0.16022 | 0.032043 | 0.07782 | -62.6038 | 60.2234 | 60.2509 | 62.2971 | 62.5168 | 122.85 | 62.3978 | 60.3561
2780.4375 | 0.061035 | 0.41229 | -0.76477 | -0.22644 | 0.13992 | -0.23712 | -0.18906 | 60.4568 | -62.1964 | 0.07782 | -62.4344 | 60.3745 | 62.3657 | 62.352 | 0.061035 | -0.069427 | 0.076904 | 0.29053 | -0.1442 | -0.17838 | 0.036621 | 0.073242 | -62.6129 | 60.2921 | 60.3104 | 62.3245 | 62.4939 | 122.9553 | 62.3566 | 60.3745
2782.0938 | 0.076294 | 0.44754 | -0.79147 | -0.21896 | 0.13672 | -0.298 | -0.18478 | 60.3561 | -62.2238 | 0.032043 | -62.471 | 60.2921 | 62.3886 | 62.3474 | 0.045776 | -0.10361 | 0.060883 | 0.28412 | -0.15808 | -0.1506 | 0.041199 | 0.10986 | -62.6038 | 60.2325 | 60.2463 | 62.352 | 62.5031 | 122.8821 | 62.3657 | 60.3561
2783.7656 | 0.061035 | 0.40161 | -0.78507 | -0.23819 | 0.14099 | -0.26062 | -0.17624 | 60.3653 | -62.2375 | 0.054932 | -62.471 | 60.3653 | 62.4023 | 62.3657 | 0.061035 | -0.072632 | 0.083313 | 0.28625 | -0.15274 | -0.17838 | 0.022888 | 0.07782 | -62.6633 | 60.3241 | 60.3104 | 62.3428 | 62.5076 | 122.9691 | 62.3337 | 60.3607
2785.4219 | 0.045776 | 0.43472 | -0.78613 | -0.22964 | 0.13779 | -0.28732 | -0.18478 | 60.3882 | -62.2147 | 0.036621 | -62.4664 | 60.3058 | 62.3932 | 62.3245 | 0.061035 | -0.09613 | 0.058746 | 0.29159 | -0.15915 | -0.15167 | 0.027466 | 0.073242 | -62.6083 | 60.2371 | 60.2417 | 62.352 | 62.5031 | 122.8638 | 62.4069 | 60.3516
2787.0938 | 0.061035 | 0.41657 | -0.77866 | -0.22751 | 0.1506 | -0.2681 | -0.18372 | 60.4019 | -62.1918 | 0.10529 | -62.4527 | 60.3378 | 62.3749 | 62.352 | 0.045776 | -0.088654 | 0.067291 | 0.28412 | -0.15595 | -0.15808 | 0.036621 | 0.13275 | -62.6404 | 60.3149 | 60.2966 | 62.3474 | 62.5122 | 122.9187 | 62.3291 | 60.379
2788.7656 | 0.045776 | 0.4155 | -0.77438 | -0.21896 | 0.13565 | -0.24353 | -0.16876 | 60.4156 | -62.2238 | 0.018311 | -62.4619 | 60.3745 | 62.4115 | 62.3566 | 0.061035 | -0.070496 | 0.070496 | 0.28732 | -0.14206 | -0.16663 | -0.041199 | -0.027466 | -62.677 | 60.2921 | 60.2692 | 62.3474 | 62.5214 | 122.8409 | 62.4023 | 60.3745
2790.4688 | 0.061035 | 0.42191 | -0.80109 | -0.21683 | 0.14313 | -0.28412 | -0.1741 | 60.4065 | -62.1368 | 0.068665 | -62.4481 | 60.2737 | 62.3795 | 62.3383 | 0.045776 | -0.10254 | 0.057678 | 0.27771 | -0.1474 | -0.15167 | 0.050354 | 0.068665 | -62.5763 | 60.2142 | 60.2371 | 62.3108 | 62.5031 | 122.8363 | 62.4023 | 60.3424
2792.1406 | 0.076294 | 0.42618 | -0.77331 | -0.23712 | 0.14847 | -0.26382 | -0.18265 | 60.3653 | -62.2147 | 0.07782 | -62.471 | 60.3424 | 62.3932 | 62.352 | 0.015259 | -0.0737 | 0.065155 | 0.28412 | -0.16022 | -0.16022 | 0.050354 | 0.10529 | -62.645 | 60.3287 | 60.3241 | 62.3337 | 62.5031 | 122.9233 | 62.3474 | 60.3607
2793.8281 | 0.061035 | 0.41763 | -0.77652 | -0.2243 | 0.13565 | -0.25207 | -0.17517 | 60.3653 | -62.2696 | -0.054932 | -62.4985 | 60.379 | 62.4023 | 62.3474 | 0.030518 | -0.082245 | 0.05661 | 0.28305 | -0.13779 | -0.16663 | -0.073242 | -0.091553 | -62.677 | 60.3104 | 60.2692 | 62.3337 | 62.5168 | 122.8683 | 62.384 | 60.3699
2795.5469 | 0.061035 | 0.42618 | -0.77866 | -0.23605 | 0.14633 | -0.28625 | -0.17517 | 60.434 | -62.1048 | 0.16479 | -62.3978 | 60.2783 | 62.3474 | 62.3154 | 0.061035 | -0.092926 | 0.063019 | 0.27557 | -0.1741 | -0.16022 | 0.13733 | 0.2655 | -62.4985 | 60.2417 | 60.2371 | 62.2879 | 62.5031 | 122.9553 | 62.3383 | 60.3333
2797.2031 | 0.061035 | 0.42191 | -0.77759 | -0.22003 | 0.14313 | -0.26169 | -0.18051 | 60.3882 | -62.2375 | -0.032043 | -62.471 | 60.3333 | 62.3978 | 62.3795 | 0.045776 | -0.087585 | 0.05661 | 0.28625 | -0.14099 | -0.16556 | -0.022888 | 0.009155 | -62.5992 | 60.2371 | 60.2554 | 62.3291 | 62.4893 | 122.8912 | 62.384 | 60.3516
2798.875 | 0.030518 | 0.41977 | -0.79788 | -0.23926 | 0.15167 | -0.28946 | -0.18906 | 60.434 | -62.1323 | 0.16022 | -62.4161 | 60.3149 | 62.3749 | 62.3383 | 0.076294 | -0.092926 | 0.055542 | 0.28198 | -0.16769 | -0.17624 | 0.091553 | 0.21057 | -62.5809 | 60.2737 | 60.2509 | 62.3016 | 62.4939 | 122.905 | 62.352 | 60.3607
2800.5938 | 0.045776 | 0.42191 | -0.78827 | -0.23819 | 0.1506 | -0.28091 | -0.18051 | 60.4614 | -62.1231 | 0.16479 | -62.4069 | 60.3058 | 62.3749 | 62.3428 | 0.061035 | -0.10681 | 0.067291 | 0.28625 | -0.16663 | -0.16876 | 0.15564 | 0.25635 | -62.5305 | 60.2417 | 60.2371 | 62.2971 | 62.4893 | 122.9233 | 62.3428 | 60.3699
2802.2656 | 0.061035 | 0.42297 | -0.78934 | -0.22644 | 0.1474 | -0.27985 | -0.17944 | 60.4568 | -62.1231 | 0.16937 | -62.4207 | 60.3241 | 62.3611 | 62.3245 | 0.061035 | -0.10254 | 0.067291 | 0.28946 | -0.16556 | -0.16449 | 0.13275 | 0.25635 | -62.5214 | 60.2325 | 60.2371 | 62.3108 | 62.5122 | 122.9279 | 62.3428 | 60.3424
2803.9219 | 0.061035 | 0.40909 | -0.77652 | -0.21362 | 0.15274 | -0.23071 | -0.17838 | 60.4614 | -62.1872 | 0.064087 | -62.4435 | 60.3653 | 62.3703 | 62.3657 | 0.045776 | -0.0737 | 0.075836 | 0.28305 | -0.13351 | -0.17303 | 0.013733 | 0.032043 | -62.6266 | 60.3104 | 60.3012 | 62.3245 | 62.4939 | 122.9141 | 62.3749 | 60.379
2805.6094 | 0.061035 | 0.4454 | -0.79681 | -0.22964 | 0.13992 | -0.28305 | -0.18158 | 60.4019 | -62.1643 | 0.11444 | -62.4298 | 60.3058 | 62.3611 | 62.3337 | 0.061035 | -0.11429 | 0.058746 | 0.27664 | -0.17303 | -0.15488 | 0.1236 | 0.21515 | -62.5442 | 60.2417 | 60.2325 | 62.3016 | 62.4802 | 122.9691 | 62.352 | 60.3195
2807.2812 | 0.030518 | 0.40909 | -0.77652 | -0.21683 | 0.1442 | -0.23712 | -0.17303 | 60.4568 | -62.1826 | 0.059509 | -62.439 | 60.379 | 62.3566 | 62.3245 | 0.045776 | -0.066223 | 0.058746 | 0.29053 | -0.1442 | -0.16449 | 0.018311 | 0.054932 | -62.6129 | 60.2783 | 60.2646 | 62.3016 | 62.4985 | 122.9095 | 62.3337 | 60.3653
2808.9531 | 0.045776 | 0.42191 | -0.78186 | -0.23392 | 0.13672 | -0.28198 | -0.17944 | 60.3699 | -62.1689 | 0.054932 | -62.4435 | 60.2783 | 62.3886 | 62.3383 | 0.061035 | -0.10147 | 0.060883 | 0.27344 | -0.15808 | -0.15595 | 0.013733 | 0.064087 | -62.5763 | 60.2234 | 60.228 | 62.3474 | 62.4985 | 122.8226 | 62.3978 | 60.3333
2810.6562 | 0.045776 | 0.42297 | -0.79254 | -0.23285 | 0.13992 | -0.27771 | -0.17731 | 60.4385 | -62.1002 | 0.1831 | -62.4023 | 60.3149 | 62.352 | 62.352 | 0.061035 | -0.11322 | 0.067291 | 0.27023 | -0.16129 | -0.16556 | 0.13733 | 0.25635 | -62.5305 | 60.2554 | 60.2325 | 62.3016 | 62.4939 | 122.9187 | 62.3337 | 60.3241
2812.3281 | 0.061035 | 0.40695 | -0.78293 | -0.21683 | 0.16022 | -0.2478 | -0.16983 | 60.4294 | -62.1689 | 0.07782 | -62.4252 | 60.3561 | 62.3795 | 62.3611 | 0.061035 | -0.068359 | 0.065155 | 0.28412 | -0.13992 | -0.16983 | 0.022888 | 0.064087 | -62.6175 | 60.2737 | 60.2646 | 62.3108 | 62.4893 | 122.905 | 62.3291 | 60.3561
2814.0156 | 0.091553 | 0.42618 | -0.78293 | -0.21149 | 0.13351 | -0.25314 | -0.1709 | 60.347 | -62.2467 | -0.054932 | -62.4756 | 60.3424 | 62.384 | 62.3703 | 0.045776 | -0.080109 | 0.0737 | 0.29694 | -0.14633 | -0.15595 | -0.073242 | -0.07782 | -62.6678 | 60.2829 | 60.2371 | 62.3337 | 62.5168 | 122.8638 | 62.3611 | 60.3378
2815.7031 | 0.061035 | 0.42191 | -0.79147 | -0.23605 | 0.14206 | -0.28732 | -0.18158 | 60.3653 | -62.1918 | 0.045776 | -62.4527 | 60.2829 | 62.3611 | 62.3291 | 0.061035 | -0.097198 | 0.061951 | 0.29159 | -0.16556 | -0.15488 | 0.013733 | 0.082397 | -62.5946 | 60.2188 | 60.2188 | 62.3291 | 62.4985 | 122.8226 | 62.4069 | 60.3561
2817.375 | 0.061035 | 0.4155 | -0.784 | -0.22964 | 0.14206 | -0.25848 | -0.18372 | 60.3745 | -62.2238 | 0.064087 | -62.4664 | 60.3516 | 62.4161 | 62.3291 | 0.045776 | -0.076904 | 0.052338 | 0.28625 | -0.16129 | -0.16769 | 0.036621 | 0.091553 | -62.645 | 60.3241 | 60.2966 | 62.2971 | 62.4847 | 122.9141 | 62.3108 | 60.3561
2819.0469 | 0.061035 | 0.42084 | -0.784 | -0.21683 | 0.14099 | -0.2446 | -0.18372 | 60.3516 | -62.2559 | -0.068665 | -62.4939 | 60.3653 | 62.3978 | 62.3566 | 0.076294 | -0.082245 | 0.052338 | 0.27771 | -0.13565 | -0.16129 | -0.073242 | -0.09613 | -62.6633 | 60.3012 | 60.2692 | 62.352 | 62.5168 | 122.8683 | 62.384 | 60.3424
2820.7188 | 0.061035 | 0.42084 | -0.78827 | -0.2478 | 0.13886 | -0.27557 | -0.17517 | 60.3928 | -62.1414 | 0.13275 | -62.4252 | 60.3241 | 62.3749 | 62.3062 | 0.061035 | -0.084381 | 0.068359 | 0.28519 | -0.16449 | -0.17517 | 0.050354 | 0.14648 | -62.6083 | 60.2875 | 60.2921 | 62.3245 | 62.5076 | 122.9004 | 62.3428 | 60.3516
2822.3906 | 0.045776 | 0.43686 | -0.79575 | -0.23071 | 0.14099 | -0.29266 | -0.18158 | 60.3424 | -62.1918 | 0.064087 | -62.4435 | 60.2966 | 62.3611 | 62.3566 | 0.061035 | -0.10254 | 0.068359 | 0.27878 | -0.16876 | -0.15381 | 0.082397 | 0.15564 | -62.5488 | 60.2234 | 60.228 | 62.3199 | 62.5214 | 122.9233 | 62.3566 | 60.3287
2824.0781 | 0.061035 | 0.38666 | -0.77438 | -0.2446 | 0.1442 | -0.23926 | -0.17944 | 60.4385 | -62.2055 | 0.050354 | -62.439 | 60.3287 | 62.3611 | 62.3657 | 0.076294 | -0.076904 | 0.070496 | 0.29053 | -0.1442 | -0.17838 | -0.004578 | 0.004578 | -62.645 | 60.2783 | 60.2554 | 62.3016 | 62.4893 | 122.8455 | 62.384 | 60.379
2825.75 | 0.061035 | 0.42938 | -0.77972 | -0.21255 | 0.15274 | -0.27237 | -0.16769 | 60.4248 | -62.1368 | 0.068665 | -62.4252 | 60.2692 | 62.4023 | 62.3291 | 0.045776 | -0.086517 | 0.05661 | 0.28732 | -0.15595 | -0.15701 | 0.041199 | 0.064087 | -62.5488 | 60.1868 | 60.1913 | 62.3337 | 62.4985 | 122.8317 | 62.384 | 60.3424
2827.4531 | 0.045776 | 0.4155 | -0.78186 | -0.21683 | 0.1239 | -0.24887 | -0.17731 | 60.3287 | -62.2879 | -0.068665 | -62.4847 | 60.3378 | 62.3886 | 62.3703 | 0.061035 | -0.080109 | 0.065155 | 0.27985 | -0.14099 | -0.16663 | -0.07782 | -0.07782 | -62.677 | 60.3012 | 60.3012 | 62.3291 | 62.5076 | 122.8226 | 62.384 | 60.3745
2829.125 | 0.030518 | 0.41229 | -0.784 | -0.23605 | 0.15595 | -0.27985 | -0.18692 | 60.4156 | -62.114 | 0.17853 | -62.4069 | 60.2921 | 62.3566 | 62.3154 | 0.061035 | -0.10361 | 0.060883 | 0.28305 | -0.16769 | -0.17303 | 0.14648 | 0.24719 | -62.5259 | 60.228 | 60.2463 | 62.3062 | 62.4573 | 122.9141 | 62.3199 | 60.3287
2830.7969 | 0.030518 | 0.43579 | -0.79681 | -0.2179 | 0.14313 | -0.26916 | -0.17731 | 60.4065 | -62.1277 | 0.068665 | -62.4252 | 60.2554 | 62.3749 | 62.3154 | 0.030518 | -0.097198 | 0.055542 | 0.27451 | -0.14313 | -0.16022 | 0.045776 | 0.068665 | -62.5534 | 60.2234 | 60.1776 | 62.3291 | 62.4847 | 122.8226 | 62.3657 | 60.3699
2832.4531 | 0.045776 | 0.40695 | -0.77011 | -0.24139 | 0.13992 | -0.25848 | -0.17517 | 60.4019 | -62.1918 | 0.086975 | -62.4207 | 60.3424 | 62.3703 | 62.3703 | 0.030518 | -0.076904 | 0.071564 | 0.28839 | -0.14954 | -0.17624 | 0.027466 | 0.09613 | -62.6083 | 60.2737 | 60.2554 | 62.3062 | 62.4756 | 122.937 | 62.3062 | 60.3149
2834.1094 | 0.030518 | 0.44006 | -0.7872 | -0.21576 | 0.1474 | -0.27557 | -0.16769 | 60.3973 | -62.146 | 0.064087 | -62.4298 | 60.2829 | 62.3703 | 62.3245 | 0.030518 | -0.088654 | 0.053406 | 0.27985 | -0.1442 | -0.15808 | 0.041199 | 0.07782 | -62.5671 | 60.2051 | 60.2188 | 62.3062 | 62.4985 | 122.8043 | 62.3657 | 60.3378
2835.7812 | 0.061035 | 0.43686 | -0.78827 | -0.2211 | 0.15167 | -0.298 | -0.18799 | 60.3424 | -62.1964 | 0.045776 | -62.4527 | 60.3012 | 62.3749 | 62.3383 | 0.045776 | -0.10147 | 0.064087 | 0.2681 | -0.15274 | -0.16449 | 0.036621 | 0.11444 | -62.5946 | 60.2417 | 60.2325 | 62.3062 | 62.471 | 122.8683 | 62.3703 | 60.3516
2837.4375 | 0.076294 | 0.40268 | -0.78186 | -0.24353 | 0.13779 | -0.24674 | -0.17944 | 60.4202 | -62.1826 | 0.082397 | -62.4161 | 60.3561 | 62.3886 | 62.352 | 0.045776 | -0.080109 | 0.058746 | 0.28732 | -0.13458 | -0.17197 | 0.027466 | 0.086975 | -62.5992 | 60.2783 | 60.26 | 62.3199 | 62.4893 | 122.9416 | 62.3245 | 60.347
2839.1094 | 0.045776 | 0.42404 | -0.79575 | -0.23285 | 0.1442 | -0.27878 | -0.17197 | 60.3516 | -62.2009 | 0.027466 | -62.4527 | 60.2875 | 62.3703 | 62.352 | 0.061035 | -0.10574 | 0.063019 | 0.26596 | -0.16022 | -0.16449 | 0.013733 | 0.091553 | -62.5809 | 60.2142 | 60.2234 | 62.3245 | 62.4802 | 122.8455 | 62.3749 | 60.3424
2840.7812 | 0.061035 | 0.42618 | -0.77759 | -0.22217 | 0.13992 | -0.25848 | -0.16876 | 60.379 | -62.2238 | 0.045776 | -62.4527 | 60.3516 | 62.384 | 62.3199 | 0.045776 | -0.085449 | 0.063019 | 0.28412 | -0.14847 | -0.16449 | 0.013733 | 0.091553 | -62.6266 | 60.3058 | 60.2783 | 62.3337 | 62.471 | 122.9507 | 62.3199 | 60.3607
2842.4531 | 0.076294 | 0.42511 | -0.7872 | -0.22217 | 0.14206 | -0.25314 | -0.16449 | 60.379 | -62.2284 | -0.027466 | -62.4802 | 60.3104 | 62.3795 | 62.3474 | 0.061035 | -0.083313 | 0.055542 | 0.28519 | -0.13245 | -0.16342 | -0.036621 | -0.022888 | -62.6083 | 60.2463 | 60.2188 | 62.3291 | 62.4985 | 122.8546 | 62.3657 | 60.3241
2844.125 | 0.045776 | 0.41657 | -0.79468 | -0.2446 | 0.13565 | -0.28519 | -0.18051 | 60.3928 | -62.114 | 0.11902 | -62.3978 | 60.2829 | 62.3474 | 62.3474 | 0.045776 | -0.099335 | 0.064087 | 0.27557 | -0.1709 | -0.15915 | 0.13275 | 0.2243 | -62.5031 | 60.2051 | 60.2051 | 62.3016 | 62.4847 | 122.9416 | 62.3245 | 60.3058
2845.8125 | 0.045776 | 0.42831 | -0.7872 | -0.23926 | 0.14847 | -0.26382 | -0.17731 | 60.3836 | -62.1689 | 0.1236 | -62.4298 | 60.3195 | 62.3611 | 62.3016 | 0.061035 | -0.079041 | 0.070496 | 0.28519 | -0.15274 | -0.17197 | 0.045776 | 0.13733 | -62.6175 | 60.2737 | 60.2554 | 62.3154 | 62.4664 | 122.8729 | 62.3108 | 60.3928
2847.5469 | 0.045776 | 0.41657 | -0.77331 | -0.21255 | 0.13992 | -0.23285 | -0.18051 | 60.3378 | -62.2604 | -0.054932 | -62.4756 | 60.3561 | 62.3886 | 62.352 | 0.076294 | -0.071564 | 0.068359 | 0.27878 | -0.14313 | -0.17303 | -0.073242 | -0.09613 | -62.6633 | 60.2829 | 60.2692 | 62.3291 | 62.5122 | 122.8638 | 62.3657 | 60.3653
2849.2031 | 0.045776 | 0.40482 | -0.78934 | -0.24139 | 0.1474 | -0.2713 | -0.18051 | 60.4019 | -62.1368 | 0.16022 | -62.384 | 60.2829 | 62.3749 | 62.3245 | 0.061035 | -0.093994 | 0.0737 | 0.28732 | -0.15381 | -0.16663 | 0.10986 | 0.21973 | -62.5763 | 60.2646 | 60.2509 | 62.2787 | 62.4527 | 122.8729 | 62.3245 | 60.3195
2850.875 | 0.045776 | 0.42297 | -0.79147 | -0.22751 | 0.13458 | -0.27344 | -0.17731 | 60.3516 | -62.1506 | 0.091553 | -62.4207 | 60.2966 | 62.384 | 62.3199 | 0.061035 | -0.09079 | 0.059814 | 0.27451 | -0.16449 | -0.15701 | 0.10071 | 0.1831 | -62.5305 | 60.2325 | 60.2005 | 62.3016 | 62.471 | 122.8958 | 62.3291 | 60.3241
2852.5938 | 0.045776 | 0.42511 | -0.77545 | -0.22644 | 0.14526 | -0.27557 | -0.19012 | 60.434 | -62.1048 | 0.17395 | -62.4069 | 60.2692 | 62.3383 | 62.3154 | 0.061035 | -0.095062 | 0.05127 | 0.27771 | -0.15701 | -0.16449 | 0.15106 | 0.25177 | -62.5168 | 60.2188 | 60.2142 | 62.2742 | 62.4847 | 122.8958 | 62.3154 | 60.3287
2854.2656 | 0.061035 | 0.41229 | -0.76797 | -0.21362 | 0.13672 | -0.23071 | -0.17944 | 60.4477 | -62.1735 | 0.054932 | -62.4298 | 60.3378 | 62.3474 | 62.3566 | 0.061035 | -0.069427 | 0.064087 | 0.29053 | -0.14099 | -0.16876 | 0.018311 | 0.022888 | -62.6083 | 60.2646 | 60.26 | 62.3108 | 62.4756 | 122.8592 | 62.352 | 60.3882
2855.9688 | 0.061035 | 0.41977 | -0.79254 | -0.22858 | 0.13672 | -0.24674 | -0.18158 | 60.3928 | -62.1872 | 0.059509 | -62.4115 | 60.3378 | 62.3657 | 62.3337 | 0.045776 | -0.077972 | 0.061951 | 0.28732 | -0.13565 | -0.17197 | 0.036621 | 0.09613 | -62.6083 | 60.2921 | 60.2737 | 62.3154 | 62.4619 | 122.937 | 62.3337 | 60.3149
2857.6406 | 0.061035 | 0.40375 | -0.79147 | -0.23285 | 0.13886 | -0.25528 | -0.17517 | 60.3836 | -62.1735 | 0.07782 | -62.4207 | 60.3607 | 62.3703 | 62.3199 | 0.061035 | -0.09079 | 0.064087 | 0.28305 | -0.1442 | -0.1741 | 0.032043 | 0.07782 | -62.5809 | 60.2921 | 60.26 | 62.3108 | 62.471 | 122.9233 | 62.3154 | 60.3516
2859.2969 | 0.061035 | 0.44647 | -0.77225 | -0.21042 | 0.13245 | -0.28732 | -0.17944 | 60.3607 | -62.1368 | 0.059509 | -62.4298 | 60.26 | 62.3703 | 62.3337 | 0.061035 | -0.10574 | 0.057678 | 0.27771 | -0.15595 | -0.16129 | 0.009155 | 0.082397 | -62.59 | 60.1959 | 60.2097 | 62.3199 | 62.4573 | 122.7951 | 62.3886 | 60.3104
2860.9688 | 0.061035 | 0.44327 | -0.79468 | -0.23498 | 0.13245 | -0.28732 | -0.1709 | 60.3424 | -62.1735 | 0.041199 | -62.4435 | 60.2921 | 62.3657 | 62.3474 | 0.061035 | -0.1004 | 0.05661 | 0.27985 | -0.15915 | -0.15701 | 0.004578 | 0.09613 | -62.5763 | 60.2188 | 60.2097 | 62.3199 | 62.5031 | 122.8317 | 62.3474 | 60.3195
2862.625 | 0.045776 | 0.40588 | -0.76584 | -0.23712 | 0.1442 | -0.24246 | -0.16769 | 60.4248 | -62.1826 | 0.082397 | -62.4207 | 60.3378 | 62.3566 | 62.3154 | 0.061035 | -0.070496 | 0.065155 | 0.27664 | -0.15381 | -0.17944 | 0.027466 | 0.09613 | -62.5946 | 60.2692 | 60.2554 | 62.3062 | 62.4802 | 122.9141 | 62.3245 | 60.3378
2864.2969 | 0.030518 | 0.41122 | -0.78827 | -0.23285 | 0.14206 | -0.27237 | -0.17624 | 60.4065 | -62.1277 | 0.14648 | -62.3978 | 60.3104 | 62.352 | 62.3108 | 0.045776 | -0.092926 | 0.064087 | 0.29053 | -0.16235 | -0.16342 | 0.07782 | 0.16022 | -62.5946 | 60.2646 | 60.2417 | 62.2925 | 62.471 | 122.8821 | 62.3108 | 60.347
2865.9844 | 0.045776 | 0.43045 | -0.79041 | -0.23819 | 0.13992 | -0.27878 | -0.18051 | 60.4156 | -62.1094 | 0.15564 | -62.3749 | 60.2921 | 62.3474 | 62.3199 | 0.045776 | -0.09613 | 0.067291 | 0.29159 | -0.16556 | -0.16129 | 0.10529 | 0.2243 | -62.5351 | 60.2417 | 60.2554 | 62.2833 | 62.4619 | 122.8775 | 62.3016 | 60.3241
2867.6562 | 0.061035 | 0.41657 | -0.78613 | -0.22003 | 0.1506 | -0.23712 | -0.17944 | 60.4065 | -62.1597 | 0.036621 | -62.4252 | 60.3287 | 62.3383 | 62.3016 | 0.061035 | -0.076904 | 0.068359 | 0.28519 | -0.13138 | -0.17517 | -0.022888 | 0.009155 | -62.6175 | 60.2875 | 60.2554 | 62.3245 | 62.4939 | 122.8088 | 62.3245 | 60.3516
2869.3438 | 0.076294 | 0.44861 | -0.78613 | -0.23498 | 0.13779 | -0.30121 | -0.18051 | 60.3653 | -62.1506 | 0.082397 | -62.4161 | 60.2737 | 62.3657 | 62.3108 | 0.061035 | -0.10147 | 0.057678 | 0.28946 | -0.16663 | -0.16235 | 0.091553 | 0.19226 | -62.5305 | 60.2142 | 60.2051 | 62.2925 | 62.4756 | 122.905 | 62.3016 | 60.3378
2871.0156 | 0.076294 | 0.44006 | -0.7872 | -0.22751 | 0.13138 | -0.29159 | -0.17944 | 60.3882 | -62.1323 | 0.091553 | -62.4023 | 60.2966 | 62.3703 | 62.3199 | 0.015259 | -0.10788 | 0.060883 | 0.27237 | -0.16129 | -0.16663 | 0.11444 | 0.20142 | -62.5168 | 60.228 | 60.2005 | 62.2925 | 62.4664 | 122.9233 | 62.2879 | 60.3287
2872.6719 | 0.061035 | 0.40161 | -0.77545 | -0.23605 | 0.13351 | -0.24994 | -0.16449 | 60.4431 | -62.1735 | 0.068665 | -62.4115 | 60.3287 | 62.352 | 62.2971 | 0.030518 | -0.068359 | 0.059814 | 0.29373 | -0.13992 | -0.18051 | 0.054932 | 0.064087 | -62.6038 | 60.3012 | 60.2692 | 62.3016 | 62.4756 | 122.8821 | 62.3291 | 60.3516
2874.3594 | 0.061035 | 0.40054 | -0.76904 | -0.22858 | 0.14954 | -0.24674 | -0.16983 | 60.4019 | -62.1735 | 0.082397 | -62.4069 | 60.3378 | 62.3703 | 62.3245 | 0.030518 | -0.083313 | 0.071564 | 0.2948 | -0.1474 | -0.1709 | 0.036621 | 0.07782 | -62.5809 | 60.2646 | 60.2692 | 62.3245 | 62.4756 | 122.9233 | 62.3245 | 60.3195
2876.0469 | 0.030518 | 0.4155 | -0.80643 | -0.23285 | 0.14954 | -0.28412 | -0.18372 | 60.3928 | -62.0911 | 0.16479 | -62.3886 | 60.2921 | 62.3566 | 62.3154 | 0.045776 | -0.10254 | 0.063019 | 0.27557 | -0.16129 | -0.1709 | 0.11444 | 0.22888 | -62.5397 | 60.2463 | 60.2325 | 62.2971 | 62.4664 | 122.8683 | 62.3108 | 60.3104
2877.7031 | 0.045776 | 0.38452 | -0.76691 | -0.22644 | 0.14633 | -0.23498 | -0.16876 | 60.4111 | -62.1506 | 0.07782 | -62.4069 | 60.3149 | 62.3703 | 62.3245 | 0.045776 | -0.077972 | 0.065155 | 0.28732 | -0.14954 | -0.16769 | 0.004578 | 0.050354 | -62.5946 | 60.2371 | 60.2509 | 62.3199 | 62.4985 | 122.8546 | 62.3245 | 60.3516
2879.3906 | 0.045776 | 0.42191 | -0.77652 | -0.22003 | 0.13245 | -0.28305 | -0.17517 | 60.3745 | -62.1231 | 0.054932 | -62.4207 | 60.2554 | 62.3611 | 62.3199 | 0.045776 | -0.10147 | 0.063019 | 0.27237 | -0.15167 | -0.16983 | 0.041199 | 0.091553 | -62.5259 | 60.1822 | 60.1959 | 62.2925 | 62.471 | 122.7951 | 62.3749 | 60.3058
2881.0781 | 0.061035 | 0.41657 | -0.77759 | -0.21683 | 0.13886 | -0.25207 | -0.18051 | 60.3149 | -62.2787 | -0.059509 | -62.4802 | 60.3195 | 62.3474 | 62.3291 | 0.061035 | -0.076904 | 0.063019 | 0.28412 | -0.14206 | -0.15915 | -0.09613 | -0.091553 | -62.6587 | 60.2646 | 60.2554 | 62.3199 | 62.4847 | 122.8043 | 62.3657 | 60.347
2882.7344 | 0.045776 | 0.41443 | -0.78079 | -0.2446 | 0.14526 | -0.27451 | -0.18799 | 60.379 | -62.1277 | 0.13275 | -62.3932 | 60.3104 | 62.3566 | 62.3245 | 0.045776 | -0.09079 | 0.068359 | 0.27557 | -0.16556 | -0.16022 | 0.091553 | 0.19226 | -62.5626 | 60.2646 | 60.2692 | 62.3154 | 62.4481 | 122.85 | 62.3062 | 60.3378
2884.3906 | 0.045776 | 0.41763 | -0.77972 | -0.21683 | 0.13351 | -0.24994 | -0.17944 | 60.3333 | -62.233 | -0.050354 | -62.4664 | 60.3378 | 62.3795 | 62.3291 | 0.045776 | -0.084381 | 0.05661 | 0.28946 | -0.1506 | -0.17303 | -0.054932 | -0.073242 | -62.6129 | 60.2509 | 60.2371 | 62.3154 | 62.4802 | 122.8363 | 62.3611 | 60.3378
2886.0625 | 0.030518 | 0.40161 | -0.77011 | -0.24887 | 0.1442 | -0.25955 | -0.19226 | 60.3561 | -62.2101 | 0.050354 | -62.4252 | 60.3333 | 62.352 | 62.3291 | 0.091553 | -0.087585 | 0.075836 | 0.29266 | -0.15595 | -0.16983 | 0.009155 | 0.091553 | -62.5809 | 60.2966 | 60.3012 | 62.2879 | 62.4573 | 122.9233 | 62.2971 | 60.3241
2887.75 | 0.061035 | 0.42618 | -0.78613 | -0.22964 | 0.14313 | -0.28519 | -0.17731 | 60.379 | -62.114 | 0.15564 | -62.4023 | 60.3012 | 62.3428 | 62.2971 | 0.061035 | -0.097198 | 0.060883 | 0.28625 | -0.15274 | -0.15488 | 0.07782 | 0.19684 | -62.558 | 60.26 | 60.2371 | 62.3108 | 62.4527 | 122.8592 | 62.3016 | 60.3195
2889.4219 | 0.061035 | 0.4155 | -0.77652 | -0.21683 | 0.13245 | -0.26596 | -0.1741 | 60.3836 | -62.1414 | 0.027466 | -62.4069 | 60.2737 | 62.352 | 62.3291 | 0.061035 | -0.098267 | 0.05661 | 0.27985 | -0.14313 | -0.16449 | 0.009155 | 0.036621 | -62.5442 | 60.2371 | 60.2097 | 62.3016 | 62.4802 | 122.8317 | 62.3474 | 60.3058
2891.0938 | 0.045776 | 0.40695 | -0.79041 | -0.23712 | 0.13351 | -0.28305 | -0.18585 | 60.3745 | -62.1597 | 0.1236 | -62.4115 | 60.2783 | 62.3657 | 62.3337 | 0.061035 | -0.085449 | 0.064087 | 0.28305 | -0.15915 | -0.16983 | 0.050354 | 0.13275 | -62.5946 | 60.2646 | 60.2463 | 62.3199 | 62.4847 | 122.8638 | 62.3062 | 60.3561
2892.7656 | 0.045776 | 0.42511 | -0.79041 | -0.25207 | 0.13351 | -0.28198 | -0.17624 | 60.4385 | -62.0682 | 0.15564 | -62.3795 | 60.2692 | 62.3245 | 62.3016 | 0.061035 | -0.099335 | 0.060883 | 0.28198 | -0.16556 | -0.1741 | 0.1236 | 0.24719 | -62.4847 | 60.2005 | 60.228 | 62.2879 | 62.4619 | 122.8775 | 62.2879 | 60.2966
2894.4375 | 0.030518 | 0.40802 | -0.784 | -0.2243 | 0.13992 | -0.2446 | -0.16769 | 60.3745 | -62.2055 | 0.009155 | -62.4435 | 60.3287 | 62.3749 | 62.2971 | 0.061035 | -0.071564 | 0.068359 | 0.29266 | -0.13031 | -0.17303 | -0.064087 | -0.045776 | -62.6358 | 60.2646 | 60.2783 | 62.3108 | 62.4985 | 122.7722 | 62.3703 | 60.3607
2896.0938 | 0.061035 | 0.439 | -0.78613 | -0.23178 | 0.13351 | -0.27451 | -0.17197 | 60.3287 | -62.1735 | 0.045776 | -62.4298 | 60.2646 | 62.3566 | 62.3199 | 0.076294 | -0.10574 | 0.054474 | 0.27664 | -0.15808 | -0.16449 | 0.027466 | 0.07782 | -62.5717 | 60.2188 | 60.228 | 62.3062 | 62.471 | 122.8088 | 62.3383 | 60.3195
2897.7656 | 0.045776 | 0.45395 | -0.79575 | -0.21469 | 0.13565 | -0.28305 | -0.18799 | 60.347 | -62.1506 | 0.073242 | -62.4115 | 60.2829 | 62.3428 | 62.3199 | 0.030518 | -0.091858 | 0.050201 | 0.28625 | -0.16235 | -0.16556 | 0.07782 | 0.14648 | -62.5351 | 60.2234 | 60.2188 | 62.2742 | 62.4619 | 122.8775 | 62.3062 | 60.3287
2899.4375 | 0.076294 | 0.41229 | -0.784 | -0.21576 | 0.14206 | -0.23819 | -0.16983 | 60.4248 | -62.1643 | 0.068665 | -62.4069 | 60.3287 | 62.3611 | 62.3383 | 0.061035 | -0.075836 | 0.066223 | 0.28625 | -0.13245 | -0.17197 | -0.004578 | 0.032043 | -62.5992 | 60.2783 | 60.2188 | 62.3062 | 62.4847 | 122.8134 | 62.3199 | 60.3378
2901.0938 | 0.061035 | 0.44327 | -0.79681 | -0.22324 | 0.13779 | -0.27557 | -0.17944 | 60.3607 | -62.1689 | 0.045776 | -62.439 | 60.2188 | 62.3337 | 62.3108 | 0.061035 | -0.11322 | 0.060883 | 0.27344 | -0.15167 | -0.16556 | 0.027466 | 0.086975 | -62.5534 | 60.1959 | 60.1959 | 62.2925 | 62.4664 | 122.7814 | 62.3749 | 60.3104
2902.7656 | 0.045776 | 0.42084 | -0.77652 | -0.22751 | 0.13779 | -0.24674 | -0.17303 | 60.3973 | -62.1689 | 0.082397 | -62.4161 | 60.3333 | 62.3566 | 62.3199 | 0.061035 | -0.075836 | 0.058746 | 0.28519 | -0.1474 | -0.1741 | 0.041199 | 0.07782 | -62.5763 | 60.2554 | 60.2417 | 62.3062 | 62.4756 | 122.8912 | 62.2787 | 60.3149
2904.4531 | 0.061035 | 0.42511 | -0.79147 | -0.23819 | 0.14099 | -0.27557 | -0.19226 | 60.3973 | -62.0773 | 0.17853 | -62.3657 | 60.2829 | 62.3337 | 62.3245 | 0.061035 | -0.10147 | 0.058746 | 0.27237 | -0.15701 | -0.16556 | 0.14648 | 0.25635 | -62.4985 | 60.2142 | 60.1868 | 62.2833 | 62.4893 | 122.8638 | 62.3062 | 60.3149
2906.1406 | 0.045776 | 0.42831 | -0.79575 | -0.2243 | 0.1506 | -0.26916 | -0.17624 | 60.3882 | -62.114 | 0.064087 | -62.4115 | 60.228 | 62.3383 | 62.3108 | 0.076294 | -0.10468 | 0.067291 | 0.27771 | -0.15274 | -0.16556 | 0.032043 | 0.068665 | -62.5442 | 60.2005 | 60.1776 | 62.3245 | 62.4939 | 122.7539 | 62.3795 | 60.3424
2907.8125 | 0.030518 | 0.42938 | -0.78613 | -0.25314 | 0.13458 | -0.27344 | -0.18692 | 60.3607 | -62.1277 | 0.07782 | -62.4069 | 60.2737 | 62.3428 | 62.3108 | 0.061035 | -0.097198 | 0.054474 | 0.28412 | -0.1741 | -0.16663 | 0.10529 | 0.17853 | -62.5122 | 60.2097 | 60.2142 | 62.2971 | 62.4664 | 122.8958 | 62.3108 | 60.2921
2909.4844 | 0.061035 | 0.40695 | -0.77118 | -0.23071 | 0.12711 | -0.2446 | -0.1741 | 60.4202 | -62.1506 | 0.07782 | -62.4023 | 60.3424 | 62.3703 | 62.3108 | 0.061035 | -0.069427 | 0.063019 | 0.29053 | -0.14633 | -0.18265 | 0.032043 | 0.064087 | -62.59 | 60.2737 | 60.2554 | 62.2971 | 62.4573 | 122.8912 | 62.2879 | 60.3104
2911.1719 | 0.045776 | 0.42404 | -0.78934 | -0.21469 | 0.15274 | -0.26062 | -0.18265 | 60.3836 | -62.1002 | 0.054932 | -62.3886 | 60.2417 | 62.3337 | 62.3199 | 0.061035 | -0.082245 | 0.05127 | 0.28412 | -0.14099 | -0.16129 | 0.022888 | 0.064087 | -62.5259 | 60.1776 | 60.1776 | 62.2833 | 62.5031 | 122.7768 | 62.3657 | 60.3058
2912.8438 | 0.061035 | 0.41016 | -0.78613 | -0.23926 | 0.13138 | -0.27451 | -0.18799 | 60.4065 | -62.0773 | 0.16022 | -62.3703 | 60.2737 | 62.3108 | 62.3199 | 0.030518 | -0.097198 | 0.066223 | 0.2713 | -0.16129 | -0.16983 | 0.15564 | 0.2655 | -62.4939 | 60.2005 | 60.2051 | 62.3154 | 62.4527 | 122.8683 | 62.2879 | 60.3104
2914.5156 | 0.061035 | 0.43579 | -0.78293 | -0.20081 | 0.13992 | -0.27664 | -0.18585 | 60.3928 | -62.114 | 0.054932 | -62.4161 | 60.2554 | 62.3474 | 62.3245 | 0.061035 | -0.091858 | 0.065155 | 0.28519 | -0.15915 | -0.16876 | 0.032043 | 0.068665 | -62.5534 | 60.1776 | 60.1776 | 62.3154 | 62.4756 | 122.7493 | 62.3428 | 60.3012
2916.2031 | 0.061035 | 0.44113 | -0.79468 | -0.21683 | 0.14206 | -0.25421 | -0.1741 | 60.3882 | -62.114 | 0.068665 | -62.3978 | 60.2646 | 62.3474 | 62.3154 | 0.045776 | -0.093994 | 0.044861 | 0.28839 | -0.14313 | -0.16663 | 0.036621 | 0.068665 | -62.5442 | 60.1913 | 60.1547 | 62.3062 | 62.5168 | 122.7585 | 62.3337 | 60.3241
2917.8594 | 0.061035 | 0.40695 | -0.76797 | -0.23392 | 0.15274 | -0.23819 | -0.17303 | 60.4248 | -62.146 | 0.068665 | -62.4115 | 60.3333 | 62.3337 | 62.3108 | 0.076294 | -0.057678 | 0.059814 | 0.29159 | -0.14633 | -0.17517 | 0.022888 | 0.036621 | -62.59 | 60.2646 | 60.26 | 62.2879 | 62.471 | 122.8317 | 62.3199 | 60.3516
2919.5312 | 0.030518 | 0.41122 | -0.79575 | -0.25742 | 0.14633 | -0.27451 | -0.17838 | 60.434 | -62.0544 | 0.16479 | -62.3703 | 60.2554 | 62.352 | 62.2879 | 0.061035 | -0.10254 | 0.063019 | 0.28625 | -0.17838 | -0.16342 | 0.14648 | 0.2655 | -62.4802 | 60.1868 | 60.2188 | 62.2925 | 62.4344 | 122.8683 | 62.3108 | 60.3241
2921.2344 | 0.045776 | 0.42191 | -0.76584 | -0.23819 | 0.13779 | -0.27985 | -0.19546 | 60.4111 | -62.0819 | 0.15564 | -62.3749 | 60.2829 | 62.3428 | 62.3108 | 0.076294 | -0.09079 | 0.061951 | 0.28946 | -0.17624 | -0.17731 | 0.14648 | 0.25635 | -62.471 | 60.1913 | 60.2097 | 62.2604 | 62.439 | 122.905 | 62.3108 | 60.3241
2922.9375 | 0.061035 | 0.43366 | -0.78934 | -0.20508 | 0.13886 | -0.25314 | -0.17517 | 60.3973 | -62.1094 | 0.13275 | -62.384 | 60.2875 | 62.3474 | 62.3016 | 0.045776 | -0.092926 | 0.044861 | 0.28519 | -0.13886 | -0.17197 | 0.091553 | 0.17395 | -62.5626 | 60.26 | 60.2509 | 62.3016 | 62.4573 | 122.8546 | 62.2879 | 60.3241
2924.5938 | 0.061035 | 0.40695 | -0.77225 | -0.21469 | 0.13886 | -0.23712 | -0.1741 | 60.3333 | -62.2375 | -0.050354 | -62.4481 | 60.3195 | 62.352 | 62.3154 | 0.061035 | -0.087585 | 0.063019 | 0.29159 | -0.13565 | -0.18372 | -0.068665 | -0.082397 | -62.6633 | 60.2692 | 60.2371 | 62.3245 | 62.4756 | 122.7722 | 62.3291 | 60.3378
2926.2969 | 0.045776 | 0.39734 | -0.78293 | -0.20828 | 0.14633 | -0.24994 | -0.16876 | 60.2921 | -62.2604 | -0.041199 | -62.4664 | 60.3378 | 62.3611 | 62.3245 | 0.061035 | -0.087585 | 0.063019 | 0.27878 | -0.13138 | -0.15808 | -0.064087 | -0.086975 | -62.6266 | 60.2646 | 60.2554 | 62.3383 | 62.4939 | 122.7859 | 62.352 | 60.3607
2927.9688 | 0.045776 | 0.42191 | -0.79254 | -0.2478 | 0.14954 | -0.28946 | -0.17624 | 60.3928 | -62.0773 | 0.14191 | -62.3749 | 60.2509 | 62.3108 | 62.3016 | 0.045776 | -0.091858 | 0.065155 | 0.28519 | -0.16556 | -0.16449 | 0.15106 | 0.24719 | -62.4893 | 60.1913 | 60.173 | 62.2925 | 62.4481 | 122.8958 | 62.3154 | 60.2966
2929.6562 | 0.076294 | 0.42191 | -0.78934 | -0.22217 | 0.1442 | -0.26703 | -0.17944 | 60.3882 | -62.0956 | 0.054932 | -62.3886 | 60.2371 | 62.3245 | 62.3199 | 0.045776 | -0.098267 | 0.054474 | 0.28091 | -0.14847 | -0.16022 | 0.050354 | 0.082397 | -62.5168 | 60.1868 | 60.173 | 62.2833 | 62.471 | 122.7493 | 62.3566 | 60.3333
2931.3125 | 0.061035 | 0.4155 | -0.7872 | -0.2478 | 0.15488 | -0.27771 | -0.18051 | 60.3882 | -62.1048 | 0.15106 | -62.3886 | 60.2875 | 62.3428 | 62.3062 | 0.061035 | -0.077972 | 0.065155 | 0.28625 | -0.16769 | -0.16769 | 0.09613 | 0.16022 | -62.5626 | 60.2783 | 60.2325 | 62.2879 | 62.4664 | 122.8409 | 62.3108 | 60.3287
2932.9844 | 0.061035 | 0.4155 | -0.79254 | -0.23605 | 0.14206 | -0.26062 | -0.17624 | 60.3424 | -62.1826 | 0.073242 | -62.439 | 60.3653 | 62.3428 | 62.3199 | 0.030518 | -0.087585 | 0.072632 | 0.28732 | -0.15915 | -0.16876 | 0.041199 | 0.10529 | -62.5992 | 60.2966 | 60.2737 | 62.2925 | 62.4664 | 122.8592 | 62.2833 | 60.3241
2934.6875 | 0.076294 | 0.41336 | -0.78186 | -0.21896 | 0.12817 | -0.24887 | -0.17731 | 60.3378 | -62.2284 | -0.059509 | -62.439 | 60.3149 | 62.3657 | 62.3062 | 0.061035 | -0.087585 | 0.060883 | 0.2948 | -0.14206 | -0.18051 | -0.064087 | -0.082397 | -62.6221 | 60.26 | 60.2737 | 62.3291 | 62.4939 | 122.8043 | 62.3245 | 60.3058
2936.3594 | 0.045776 | 0.41122 | -0.77866 | -0.22751 | 0.14313 | -0.24567 | -0.17944 | 60.3699 | -62.1323 | 0.07782 | -62.3886 | 60.3378 | 62.352 | 62.3383 | 0.061035 | -0.081177 | 0.059814 | 0.29053 | -0.14847 | -0.16342 | 0.036621 | 0.082397 | -62.5534 | 60.2646 | 60.2463 | 62.2833 | 62.4527 | 122.8592 | 62.2879 | 60.3149
2938.0312 | 0.076294 | 0.42084 | -0.78293 | -0.22217 | 0.12711 | -0.26596 | -0.1709 | 60.3516 | -62.1414 | 0.018311 | -62.4069 | 60.2646 | 62.3337 | 62.3016 | 0.061035 | -0.083313 | 0.053406 | 0.28412 | -0.13886 | -0.16342 | 0.013733 | 0.036621 | -62.5305 | 60.228 | 60.1593 | 62.3154 | 62.4756 | 122.8088 | 62.3795 | 60.2829
2939.7031 | 0.045776 | 0.42191 | -0.79147 | -0.24887 | 0.15167 | -0.28839 | -0.18478 | 60.3973 | -62.059 | 0.16479 | -62.3703 | 60.26 | 62.3428 | 62.2787 | 0.061035 | -0.10254 | 0.066223 | 0.28946 | -0.16235 | -0.16342 | 0.14191 | 0.26093 | -62.4619 | 60.2051 | 60.173 | 62.2833 | 62.4619 | 122.8912 | 62.3016 | 60.2737
2941.375 | 0.045776 | 0.41443 | -0.79254 | -0.23178 | 0.15381 | -0.27451 | -0.17303 | 60.3973 | -62.0819 | 0.16022 | -62.3566 | 60.2371 | 62.3199 | 62.2971 | 0.061035 | -0.10574 | 0.064087 | 0.28519 | -0.14954 | -0.1709 | 0.12817 | 0.23346 | -62.4893 | 60.1868 | 60.2051 | 62.2742 | 62.439 | 122.8317 | 62.3154 | 60.3195
2943.0312 | 0.061035 | 0.40268 | -0.77011 | -0.20828 | 0.13779 | -0.25207 | -0.17624 | 60.3287 | -62.2101 | -0.022888 | -62.4619 | 60.3104 | 62.3474 | 62.3154 | 0.061035 | -0.065155 | 0.065155 | 0.28625 | -0.13565 | -0.16876 | -0.091553 | -0.068665 | -62.6678 | 60.2875 | 60.228 | 62.3245 | 62.4893 | 122.7539 | 62.3428 | 60.347
2944.6875 | 0.045776 | 0.439 | -0.79041 | -0.22644 | 0.15595 | -0.28519 | -0.18585 | 60.3333 | -62.1323 | 0.032043 | -62.4207 | 60.26 | 62.3337 | 62.3108 | 0.061035 | -0.10681 | 0.058746 | 0.27023 | -0.15701 | -0.15381 | 0.022888 | 0.07782 | -62.5488 | 60.2005 | 60.1639 | 62.2971 | 62.4664 | 122.7585 | 62.3611 | 60.3012
2946.375 | 0.045776 | 0.4155 | -0.784 | -0.23712 | 0.1442 | -0.27237 | -0.18265 | 60.4019 | -62.0956 | 0.17395 | -62.352 | 60.2509 | 62.3062 | 62.3062 | 0.061035 | -0.088654 | 0.054474 | 0.27237 | -0.16983 | -0.17944 | 0.11444 | 0.23346 | -62.5076 | 60.2051 | 60.2188 | 62.2925 | 62.4573 | 122.8363 | 62.3062 | 60.3104
2948.0312 | 0.045776 | 0.41229 | -0.78613 | -0.21683 | 0.13458 | -0.25742 | -0.17838 | 60.3195 | -62.2375 | -0.045776 | -62.4527 | 60.3287 | 62.3291 | 62.3291 | 0.061035 | -0.077972 | 0.058746 | 0.29587 | -0.14206 | -0.1741 | -0.082397 | -0.10529 | -62.6358 | 60.2783 | 60.228 | 62.3016 | 62.4985 | 122.7951 | 62.3566 | 60.347
2949.7031 | 0.061035 | 0.40802 | -0.79575 | -0.23819 | 0.13672 | -0.27878 | -0.18158 | 60.3928 | -62.0819 | 0.17395 | -62.3703 | 60.2737 | 62.3428 | 62.2742 | 0.045776 | -0.097198 | 0.060883 | 0.28305 | -0.15701 | -0.16876 | 0.10986 | 0.22888 | -62.4939 | 60.228 | 60.1868 | 62.2971 | 62.471 | 122.8363 | 62.2971 | 60.3058
2951.375 | 0.045776 | 0.41443 | -0.77866 | -0.20508 | 0.14847 | -0.24033 | -0.16876 | 60.3241 | -62.1964 | -0.022888 | -62.4344 | 60.3149 | 62.3566 | 62.3062 | 0.061035 | -0.074768 | 0.059814 | 0.27985 | -0.13458 | -0.16556 | -0.082397 | -0.068665 | -62.6312 | 60.2463 | 60.2783 | 62.2925 | 62.4619 | 122.7493 | 62.3337 | 60.3333
2953.0469 | 0.030518 | 0.41336 | -0.77331 | -0.23392 | 0.1474 | -0.28305 | -0.17517 | 60.3882 | -62.059 | 0.16937 | -62.3611 | 60.2646 | 62.3199 | 62.2604 | 0.030518 | -0.10361 | 0.059814 | 0.27451 | -0.16449 | -0.16983 | 0.13733 | 0.25177 | -62.4893 | 60.1822 | 60.1868 | 62.2604 | 62.4802 | 122.8455 | 62.3062 | 60.3241
2954.7031 | 0.061035 | 0.43686 | -0.77972 | -0.2179 | 0.14313 | -0.25955 | -0.17197 | 60.3699 | -62.1002 | 0.059509 | -62.3795 | 60.2142 | 62.3199 | 62.3062 | 0.045776 | -0.10574 | 0.052338 | 0.28305 | -0.1474 | -0.15808 | 0.045776 | 0.082397 | -62.5076 | 60.1822 | 60.1913 | 62.2604 | 62.439 | 122.7448 | 62.352 | 60.2966
2956.375 | 0.045776 | 0.40695 | -0.76477 | -0.23392 | 0.13672 | -0.23926 | -0.17838 | 60.3561 | -62.1643 | 0.073242 | -62.3795 | 60.3424 | 62.3337 | 62.3062 | 0.061035 | -0.086517 | 0.060883 | 0.27985 | -0.13779 | -0.17838 | 0.032043 | 0.07782 | -62.5671 | 60.2783 | 60.2463 | 62.2971 | 62.4619 | 122.8867 | 62.2925 | 60.3058
2958.0938 | 0.045776 | 0.4155 | -0.78934 | -0.2179 | 0.13672 | -0.24887 | -0.17197 | 60.2966 | -62.2238 | -0.059509 | -62.4527 | 60.3012 | 62.3474 | 62.3062 | 0.045776 | -0.079041 | 0.058746 | 0.28519 | -0.14313 | -0.1709 | -0.086975 | -0.086975 | -62.6175 | 60.2509 | 60.2509 | 62.3291 | 62.4756 | 122.7905 | 62.3337 | 60.3241
2959.7656 | 0.061035 | 0.42618 | -0.78827 | -0.23712 | 0.12604 | -0.28305 | -0.17624 | 60.3653 | -62.0956 | 0.059509 | -62.3932 | 60.2463 | 62.3383 | 62.2879 | 0.045776 | -0.10468 | 0.058746 | 0.28412 | -0.16342 | -0.15701 | 0.036621 | 0.082397 | -62.5259 | 60.1639 | 60.1593 | 62.2879 | 62.4664 | 122.7127 | 62.3566 | 60.3012
2961.4688 | 0.061035 | 0.44113 | -0.79041 | -0.2211 | 0.13779 | -0.28305 | -0.17838 | 60.3378 | -62.1277 | 0.027466 | -62.4115 | 60.2646 | 62.3337 | 62.2742 | 0.030518 | -0.091858 | 0.058746 | 0.27985 | -0.15915 | -0.1709 | 0.027466 | 0.07782 | -62.5488 | 60.1822 | 60.1913 | 62.2879 | 62.4664 | 122.7585 | 62.3291 | 60.3149
2963.1406 | 0.030518 | 0.42084 | -0.77972 | -0.2211 | 0.13992 | -0.25421 | -0.17624 | 60.3516 | -62.1918 | 0.045776 | -62.3978 | 60.3333 | 62.3383 | 62.3016 | 0.030518 | -0.086517 | 0.069427 | 0.28839 | -0.14633 | -0.17731 | 0.027466 | 0.082397 | -62.5671 | 60.2875 | 60.2692 | 62.265 | 62.439 | 122.8867 | 62.2787 | 60.3149
2964.8125 | 0.045776 | 0.4155 | -0.77759 | -0.25207 | 0.13138 | -0.28625 | -0.18478 | 60.3836 | -62.0636 | 0.16937 | -62.3566 | 60.2646 | 62.3108 | 62.2971 | 0.045776 | -0.1004 | 0.057678 | 0.28091 | -0.16129 | -0.16663 | 0.13733 | 0.24261 | -62.4527 | 60.2005 | 60.2097 | 62.2696 | 62.439 | 122.8592 | 62.2787 | 60.2875
2966.5312 | 0.061035 | 0.43045 | -0.78613 | -0.23605 | 0.1442 | -0.28198 | -0.1944 | 60.3745 | -62.0865 | 0.14648 | -62.3611 | 60.2737 | 62.3108 | 62.2742 | 0.061035 | -0.085449 | 0.054474 | 0.298 | -0.16769 | -0.17624 | 0.14191 | 0.23346 | -62.4664 | 60.1913 | 60.1913 | 62.2467 | 62.4573 | 122.8775 | 62.2696 | 60.3104
2968.2031 | 0.061035 | 0.40695 | -0.78613 | -0.21469 | 0.14313 | -0.2478 | -0.18372 | 60.4248 | -62.1323 | 0.054932 | -62.4069 | 60.3104 | 62.3383 | 62.3154 | 0.045776 | -0.079041 | 0.0737 | 0.30228 | -0.13138 | -0.1709 | -0.004578 | 0.013733 | -62.5671 | 60.26 | 60.2554 | 62.2742 | 62.4527 | 122.7631 | 62.3108 | 60.3516
2969.9062 | 0.061035 | 0.40909 | -0.77866 | -0.21149 | 0.13992 | -0.24994 | -0.18265 | 60.3424 | -62.178 | -0.009155 | -62.4161 | 60.2966 | 62.352 | 62.3062 | 0.045776 | -0.0737 | 0.060883 | 0.27664 | -0.12817 | -0.17197 | -0.07782 | -0.054932 | -62.6266 | 60.2325 | 60.2692 | 62.2971 | 62.4802 | 122.7493 | 62.3291 | 60.3287
2971.6094 | 0.045776 | 0.41229 | -0.78186 | -0.23392 | 0.13138 | -0.25101 | -0.16769 | 60.347 | -62.1735 | 0.004578 | -62.4161 | 60.2921 | 62.3245 | 62.3108 | 0.045776 | -0.066223 | 0.066223 | 0.29053 | -0.15274 | -0.16449 | -0.059509 | -0.045776 | -62.6266 | 60.26 | 60.2509 | 62.3062 | 62.4481 | 122.7631 | 62.3245 | 60.3378
2973.2812 | 0.045776 | 0.41016 | -0.78613 | -0.2446 | 0.11856 | -0.30121 | -0.18265 | 60.3836 | -62.0499 | 0.16479 | -62.3566 | 60.2325 | 62.3245 | 62.2925 | 0.030518 | -0.11536 | 0.058746 | 0.27237 | -0.16663 | -0.15915 | 0.12817 | 0.25177 | -62.4527 | 60.1822 | 60.1913 | 62.2604 | 62.4481 | 122.8729 | 62.2787 | 60.2829
2974.9531 | 0.045776 | 0.42404 | -0.78827 | -0.22324 | 0.13458 | -0.26169 | -0.17517 | 60.3699 | -62.1231 | 0.027466 | -62.3978 | 60.2692 | 62.3428 | 62.2971 | 0.061035 | -0.083313 | 0.055542 | 0.28625 | -0.13992 | -0.17197 | 0.004578 | 0.050354 | -62.5305 | 60.2005 | 60.1776 | 62.2833 | 62.4619 | 122.7676 | 62.3337 | 60.3058
2976.6562 | 0.061035 | 0.40054 | -0.76691 | -0.24033 | 0.13672 | -0.25635 | -0.17197 | 60.3607 | -62.1643 | 0.07782 | -62.3932 | 60.3424 | 62.3337 | 62.2971 | 0.061035 | -0.072632 | 0.048065 | 0.27985 | -0.14526 | -0.17944 | 0.032043 | 0.086975 | -62.5626 | 60.2554 | 60.2417 | 62.3016 | 62.4573 | 122.8729 | 62.2742 | 60.3104
2978.3281 | 0.030518 | 0.42725 | -0.78293 | -0.20935 | 0.1474 | -0.27557 | -0.17731 | 60.3607 | -62.1277 | 0.041199 | -62.3703 | 60.2417 | 62.3199 | 62.2971 | 0.061035 | -0.09613 | 0.053406 | 0.28519 | -0.1442 | -0.16235 | 0.013733 | 0.054932 | -62.5031 | 60.1822 | 60.1593 | 62.3154 | 62.4481 | 122.7859 | 62.3474 | 60.3104
2980 | 0.030518 | 0.41763 | -0.77972 | -0.23498 | 0.13779 | -0.2713 | -0.18478 | 60.3745 | -62.0682 | 0.16937 | -62.3428 | 60.2325 | 62.3062 | 62.2925 | 0.045776 | -0.10361 | 0.063019 | 0.27878 | -0.16235 | -0.16663 | 0.11444 | 0.24261 | -62.4939 | 60.2097 | 60.2051 | 62.265 | 62.439 | 122.8226 | 62.2604 | 60.3195
2981.7031 | 0.076294 | 0.42084 | -0.78613 | -0.23285 | 0.15488 | -0.26596 | -0.17838 | 60.3104 | -62.178 | 0.068665 | -62.4252 | 60.3195 | 62.3154 | 62.2879 | 0.045776 | -0.088654 | 0.064087 | 0.28412 | -0.16876 | -0.1709 | 0.036621 | 0.10529 | -62.5854 | 60.2646 | 60.2783 | 62.2971 | 62.4527 | 122.8409 | 62.2696 | 60.3195
2983.375 | 0.045776 | 0.40482 | -0.77652 | -0.20508 | 0.14206 | -0.24567 | -0.17944 | 60.2966 | -62.2147 | -0.073242 | -62.4298 | 60.3424 | 62.352 | 62.3108 | 0.076294 | -0.088654 | 0.064087 | 0.28732 | -0.13992 | -0.16022 | -0.10529 | -0.10529 | -62.6312 | 60.2371 | 60.2234 | 62.2833 | 62.4756 | 122.7676 | 62.3154 | 60.3287
2985.0625 | 0.061035 | 0.43045 | -0.77866 | -0.23178 | 0.13245 | -0.28412 | -0.18478 | 60.3241 | -62.114 | 0.050354 | -62.3932 | 60.228 | 62.3108 | 62.2879 | 0.061035 | -0.11215 | 0.066223 | 0.28305 | -0.15488 | -0.16983 | 0.013733 | 0.073242 | -62.5122 | 60.1868 | 60.1639 | 62.265 | 62.471 | 122.7219 | 62.3474 | 60.3149
2986.75 | 0.045776 | 0.43686 | -0.78934 | -0.23178 | 0.13672 | -0.27771 | -0.19546 | 60.3195 | -62.1094 | 0.054932 | -62.4023 | 60.2371 | 62.3291 | 62.3062 | 0.076294 | -0.10361 | 0.049133 | 0.27344 | -0.14954 | -0.16129 | 0.018311 | 0.068665 | -62.5305 | 60.173 | 60.173 | 62.265 | 62.4802 | 122.7219 | 62.3474 | 60.2966
2988.4531 | 0.045776 | 0.42725 | -0.78186 | -0.2179 | 0.13992 | -0.26276 | -0.16983 | 60.3882 | -62.0956 | 0.054932 | -62.3749 | 60.2371 | 62.3016 | 62.3016 | 0.061035 | -0.09613 | 0.050201 | 0.28305 | -0.1506 | -0.16449 | 0.032043 | 0.082397 | -62.4893 | 60.173 | 60.173 | 62.2604 | 62.4481 | 122.7356 | 62.3428 | 60.3149
2990.1094 | 0.061035 | 0.40268 | -0.76263 | -0.23819 | 0.13351 | -0.25955 | -0.18051 | 60.3195 | -62.2055 | 0.045776 | -62.4115 | 60.3378 | 62.3337 | 62.3154 | 0.061035 | -0.072632 | 0.060883 | 0.27451 | -0.15701 | -0.17838 | 0.032043 | 0.082397 | -62.5671 | 60.2921 | 60.2371 | 62.2879 | 62.4344 | 122.8592 | 62.2833 | 60.2646
2991.7656 | 0.030518 | 0.41122 | -0.784 | -0.2243 | 0.13565 | -0.2478 | -0.17838 | 60.2966 | -62.2238 | -0.059509 | -62.4344 | 60.347 | 62.3291 | 62.2971 | 0.045776 | -0.084381 | 0.063019 | 0.29373 | -0.14099 | -0.16769 | -0.082397 | -0.10071 | -62.6404 | 60.2509 | 60.2234 | 62.2833 | 62.4664 | 122.7631 | 62.3337 | 60.3058
2993.4375 | 0.045776 | 0.40375 | -0.78827 | -0.22751 | 0.13672 | -0.25528 | -0.18478 | 60.3561 | -62.1414 | 0.07782 | -62.3749 | 60.3104 | 62.3474 | 62.3062 | 0.045776 | -0.079041 | 0.057678 | 0.28839 | -0.15381 | -0.17517 | 0.027466 | 0.082397 | -62.5534 | 60.2371 | 60.2463 | 62.2375 | 62.4298 | 122.85 | 62.2787 | 60.2966
2995.1094 | 0.045776 | 0.41443 | -0.79361 | -0.24033 | 0.15701 | -0.28198 | -0.18265 | 60.3653 | -62.0453 | 0.17395 | -62.352 | 60.2417 | 62.3245 | 62.2742 | 0.045776 | -0.10574 | 0.072632 | 0.27985 | -0.16769 | -0.16235 | 0.13275 | 0.24719 | -62.4802 | 60.1547 | 60.2051 | 62.2787 | 62.4115 | 122.8317 | 62.2742 | 60.2829
2996.7969 | 0.061035 | 0.40268 | -0.77759 | -0.21469 | 0.13779 | -0.25207 | -0.16556 | 60.3378 | -62.1643 | 0.013733 | -62.4023 | 60.3287 | 62.3154 | 62.2925 | 0.076294 | -0.069427 | 0.05661 | 0.29907 | -0.1442 | -0.17838 | -0.050354 | -0.013733 | -62.6083 | 60.2646 | 60.2097 | 62.2879 | 62.4573 | 122.731 | 62.3428 | 60.3058
2998.5 | 0.061035 | 0.40802 | -0.77652 | -0.22751 | 0.12604 | -0.25528 | -0.17303 | 60.2509 | -62.2421 | -0.041199 | -62.4481 | 60.3241 | 62.3154 | 62.3154 | 0.030518 | -0.086517 | 0.070496 | 0.28198 | -0.13351 | -0.16129 | -0.086975 | -0.091553 | -62.6129 | 60.228 | 60.2325 | 62.2971 | 62.4435 | 122.731 | 62.3199 | 60.3516
3000.1562 | 0.030518 | 0.42084 | -0.80109 | -0.22644 | 0.13672 | -0.30014 | -0.19333 | 60.3195 | -62.0636 | 0.13733 | -62.3566 | 60.2463 | 62.2879 | 62.3016 | 0.045776 | -0.11002 | 0.059814 | 0.28305 | -0.17517 | -0.16556 | 0.13733 | 0.24261 | -62.4527 | 60.1685 | 60.1593 | 62.2787 | 62.4573 | 122.8546 | 62.2513 | 60.2921
3001.8125 | 0.061035 | 0.40482 | -0.78079 | -0.25421 | 0.12604 | -0.25207 | -0.17517 | 60.3424 | -62.1552 | 0.073242 | -62.3703 | 60.3287 | 62.3383 | 62.3016 | 0.045776 | -0.076904 | 0.063019 | 0.28519 | -0.15381 | -0.16769 | 0.013733 | 0.082397 | -62.558 | 60.2737 | 60.2371 | 62.2604 | 62.4435 | 122.8729 | 62.2696 | 60.2921
3003.5 | 0.045776 | 0.43259 | -0.78293 | -0.21576 | 0.13565 | -0.2681 | -0.17731 | 60.3745 | -62.1002 | 0.054932 | -62.3749 | 60.2417 | 62.3199 | 62.3062 | 0.045776 | -0.098267 | 0.052338 | 0.28732 | -0.14633 | -0.16983 | 0.022888 | 0.064087 | -62.4893 | 60.1639 | 60.173 | 62.2787 | 62.4527 | 122.7859 | 62.3291 | 60.3012
3005.1719 | 0.045776 | 0.41122 | -0.78186 | -0.24567 | 0.1442 | -0.26916 | -0.18265 | 60.3104 | -62.1689 | 0.064087 | -62.4252 | 60.3241 | 62.3245 | 62.3199 | 0.045776 | -0.10468 | 0.064087 | 0.29587 | -0.16556 | -0.16769 | 0.032043 | 0.10986 | -62.5763 | 60.2921 | 60.2371 | 62.3016 | 62.439 | 122.8134 | 62.2696 | 60.3287
3006.8438 | 0.076294 | 0.44113 | -0.79254 | -0.2211 | 0.14099 | -0.27985 | -0.19119 | 60.3104 | -62.1323 | 0.036621 | -62.4115 | 60.2417 | 62.3154 | 62.2971 | 0.045776 | -0.099335 | 0.060883 | 0.27664 | -0.15808 | -0.16556 | 0.018311 | 0.09613 | -62.5442 | 60.1547 | 60.1639 | 62.2925 | 62.4664 | 122.7448 | 62.3474 | 60.3012
3008.5156 | 0.076294 | 0.40695 | -0.77972 | -0.24246 | 0.13138 | -0.27237 | -0.18372 | 60.3149 | -62.1643 | 0.064087 | -62.4207 | 60.3104 | 62.3154 | 62.3016 | 0.045776 | -0.09613 | 0.066223 | 0.28091 | -0.15915 | -0.17517 | 0.041199 | 0.10529 | -62.5671 | 60.2554 | 60.2463 | 62.2787 | 62.4619 | 122.8134 | 62.2971 | 60.2966
3010.1875 | 0.030518 | 0.43045 | -0.77225 | -0.21683 | 0.13565 | -0.2681 | -0.17838 | 60.3699 | -62.0865 | 0.050354 | -62.3703 | 60.2417 | 62.3428 | 62.2696 | 0.045776 | -0.10361 | 0.05127 | 0.27237 | -0.1506 | -0.16983 | 0.045776 | 0.073242 | -62.4847 | 60.1776 | 60.1593 | 62.2787 | 62.439 | 122.7219 | 62.3428 | 60.2966
3011.8594 | 0.030518 | 0.40695 | -0.78186 | -0.22964 | 0.14099 | -0.25528 | -0.18051 | 60.3653 | -62.1506 | 0.064087 | -62.3703 | 60.3104 | 62.3245 | 62.2971 | 0.030518 | -0.081177 | 0.060883 | 0.28412 | -0.15381 | -0.16876 | 0.036621 | 0.082397 | -62.5534 | 60.2509 | 60.228 | 62.265 | 62.4435 | 122.85 | 62.2604 | 60.2875
3013.5625 | 0.045776 | 0.41229 | -0.7637 | -0.22003 | 0.13031 | -0.24994 | -0.16556 | 60.2921 | -62.2055 | -0.059509 | -62.4207 | 60.3195 | 62.3108 | 62.3154 | 0.030518 | -0.082245 | 0.05661 | 0.29159 | -0.14526 | -0.16556 | -0.082397 | -0.10071 | -62.5992 | 60.2234 | 60.2509 | 62.2787 | 62.4344 | 122.7493 | 62.3245 | 60.2783
3015.25 | 0.030518 | 0.40909 | -0.77118 | -0.25101 | 0.13565 | -0.25314 | -0.17303 | 60.3333 | -62.1368 | 0.068665 | -62.3703 | 60.2966 | 62.3291 | 62.3016 | 0.061035 | -0.088654 | 0.070496 | 0.28839 | -0.15274 | -0.1709 | 0.036621 | 0.10071 | -62.5488 | 60.2463 | 60.228 | 62.2559 | 62.4756 | 122.85 | 62.2604 | 60.3149
3016.9375 | 0.061035 | 0.40695 | -0.79361 | -0.25101 | 0.12817 | -0.30014 | -0.17731 | 60.3745 | -62.0499 | 0.15106 | -62.3383 | 60.2417 | 62.3108 | 62.2742 | 0.030518 | -0.1004 | 0.066223 | 0.26916 | -0.1741 | -0.17517 | 0.14648 | 0.26093 | -62.439 | 60.1868 | 60.1868 | 62.2696 | 62.4298 | 122.85 | 62.2604 | 60.2829
3018.6406 | 0.045776 | 0.42725 | -0.77866 | -0.22003 | 0.12817 | -0.27985 | -0.18158 | 60.3424 | -62.1185 | 0.036621 | -62.3978 | 60.26 | 62.3154 | 62.3062 | 0.045776 | -0.098267 | 0.045929 | 0.27985 | -0.16129 | -0.16022 | 0.032043 | 0.064087 | -62.5351 | 60.1639 | 60.1822 | 62.2833 | 62.4527 | 122.7219 | 62.3383 | 60.3058
3020.3125 | 0.045776 | 0.40695 | -0.77866 | -0.22858 | 0.13458 | -0.24567 | -0.18585 | 60.3149 | -62.1918 | 0.045776 | -62.3886 | 60.3241 | 62.3154 | 62.2971 | 0.076294 | -0.079041 | 0.057678 | 0.28946 | -0.14633 | -0.18051 | 0.022888 | 0.086975 | -62.5717 | 60.2509 | 60.2554 | 62.2971 | 62.4115 | 122.8592 | 62.2742 | 60.3104
3021.9844 | 0.045776 | 0.40375 | -0.77438 | -0.22003 | 0.13458 | -0.2478 | -0.18372 | 60.379 | -62.1185 | 0.050354 | -62.3703 | 60.2966 | 62.3154 | 62.2833 | 0.045776 | -0.085449 | 0.067291 | 0.28946 | -0.13886 | -0.18372 | -0.004578 | 0.036621 | -62.5626 | 60.2463 | 60.2188 | 62.2879 | 62.4619 | 122.7676 | 62.2971 | 60.3241
3023.6719 | 0.045776 | 0.41229 | -0.78507 | -0.23285 | 0.14099 | -0.28839 | -0.19333 | 60.2921 | -62.1048 | 0.091553 | -62.3795 | 60.26 | 62.2971 | 62.2742 | 0.045776 | -0.11856 | 0.054474 | 0.26489 | -0.16556 | -0.16983 | 0.07782 | 0.17853 | -62.4847 | 60.1776 | 60.1822 | 62.2559 | 62.439 | 122.8271 | 62.2742 | 60.2783
3025.375 | 0.045776 | 0.4155 | -0.79254 | -0.22537 | 0.13138 | -0.29159 | -0.18051 | 60.379 | -62.0636 | 0.17395 | -62.3474 | 60.2417 | 62.3062 | 62.2559 | 0.091553 | -0.098267 | 0.059814 | 0.27664 | -0.16556 | -0.1741 | 0.12817 | 0.25177 | -62.4664 | 60.1913 | 60.1593 | 62.2696 | 62.4435 | 122.7997 | 62.2696 | 60.3058
3027.0469 | 0.076294 | 0.41977 | -0.77759 | -0.21683 | 0.13886 | -0.24353 | -0.17731 | 60.3928 | -62.114 | 0.064087 | -62.3795 | 60.3012 | 62.3016 | 62.2787 | 0.061035 | -0.084381 | 0.05661 | 0.28732 | -0.13245 | -0.18478 | 0 | 0.027466 | -62.5626 | 60.2554 | 60.2188 | 62.2696 | 62.4481 | 122.7585 | 62.2787 | 60.3104
3028.7344 | 0.076294 | 0.40695 | -0.77759 | -0.22858 | 0.13992 | -0.25421 | -0.17197 | 60.3561 | -62.114 | 0.073242 | -62.3703 | 60.2829 | 62.3245 | 62.2833 | 0.061035 | -0.093994 | 0.048065 | 0.28946 | -0.14526 | -0.1741 | 0.041199 | 0.082397 | -62.5351 | 60.2509 | 60.2142 | 62.2696 | 62.4344 | 122.8317 | 62.2604 | 60.2737
3030.4219 | 0.045776 | 0.4155 | -0.7872 | -0.23605 | 0.13672 | -0.27023 | -0.17838 | 60.2921 | -62.1414 | 0.09613 | -62.4023 | 60.2921 | 62.3291 | 62.2696 | 0.076294 | -0.1004 | 0.066223 | 0.27985 | -0.15915 | -0.16342 | 0.041199 | 0.1236 | -62.5717 | 60.2509 | 60.2234 | 62.3062 | 62.4344 | 122.7951 | 62.2513 | 60.3149
3032.0781 | 0.076294 | 0.42831 | -0.79361 | -0.21896 | 0.13672 | -0.26916 | -0.1709 | 60.3424 | -62.0682 | 0.073242 | -62.3657 | 60.2371 | 62.3062 | 62.2925 | 0.030518 | -0.098267 | 0.048065 | 0.27664 | -0.14954 | -0.15915 | 0.027466 | 0.091553 | -62.471 | 60.1639 | 60.1593 | 62.2971 | 62.4435 | 122.7036 | 62.3291 | 60.3012
3033.75 | 0.045776 | 0.4155 | -0.78934 | -0.24567 | 0.14313 | -0.28519 | -0.18585 | 60.3745 | -62.0178 | 0.17395 | -62.3337 | 60.228 | 62.2971 | 62.2787 | 0.061035 | -0.10895 | 0.065155 | 0.28305 | -0.16556 | -0.16876 | 0.14191 | 0.2655 | -62.4481 | 60.1822 | 60.173 | 62.2696 | 62.4252 | 122.8134 | 62.2971 | 60.2692
3035.4688 | 0.030518 | 0.39841 | -0.76477 | -0.21683 | 0.13992 | -0.24246 | -0.16983 | 60.3516 | -62.1323 | 0.032043 | -62.384 | 60.3149 | 62.3199 | 62.2925 | 0.030518 | -0.076904 | 0.05661 | 0.28625 | -0.13245 | -0.17944 | -0.045776 | -0.004578 | -62.5809 | 60.2325 | 60.2097 | 62.2787 | 62.4619 | 122.7264 | 62.3291 | 60.3012
3037.1406 | 0.030518 | 0.44006 | -0.77438 | -0.2446 | 0.13458 | -0.28305 | -0.18265 | 60.3333 | -62.0911 | 0.045776 | -62.3886 | 60.2188 | 62.3383 | 62.2604 | 0.045776 | -0.10681 | 0.064087 | 0.28091 | -0.16342 | -0.16663 | 0.036621 | 0.064087 | -62.5168 | 60.1547 | 60.1593 | 62.2742 | 62.4435 | 122.6852 | 62.3291 | 60.2829
3038.8125 | 0.045776 | 0.40375 | -0.77331 | -0.2243 | 0.13779 | -0.23926 | -0.16876 | 60.3653 | -62.1231 | 0.050354 | -62.384 | 60.3012 | 62.3428 | 62.2879 | 0.061035 | -0.077972 | 0.055542 | 0.29159 | -0.14206 | -0.17731 | -0.009155 | 0 | -62.5671 | 60.2509 | 60.2325 | 62.2742 | 62.4252 | 122.7036 | 62.3199 | 60.3149
3040.4844 | 0.061035 | 0.43152 | -0.78079 | -0.20721 | 0.12711 | -0.27985 | -0.17517 | 60.3333 | -62.0911 | 0.059509 | -62.3703 | 60.2234 | 62.3154 | 62.2925 | 0.076294 | -0.099335 | 0.055542 | 0.27344 | -0.14847 | -0.16663 | 0.041199 | 0.064087 | -62.5122 | 60.1547 | 60.173 | 62.2742 | 62.4344 | 122.6944 | 62.3566 | 60.3058
3042.1562 | 0.061035 | 0.40375 | -0.77759 | -0.22537 | 0.13672 | -0.24994 | -0.17838 | 60.2875 | -62.2147 | -0.041199 | -62.4207 | 60.3195 | 62.2971 | 62.3016 | 0.045776 | -0.076904 | 0.052338 | 0.27985 | -0.14847 | -0.16876 | -0.10071 | -0.09613 | -62.6404 | 60.2188 | 60.2463 | 62.3016 | 62.4893 | 122.7081 | 62.3199 | 60.3195
3043.8125 | 0.061035 | 0.42297 | -0.78507 | -0.22644 | 0.13351 | -0.28091 | -0.17624 | 60.3424 | -62.0773 | 0.059509 | -62.3749 | 60.2371 | 62.3016 | 62.2971 | 0.061035 | -0.10574 | 0.050201 | 0.27451 | -0.15915 | -0.16129 | 0.041199 | 0.07782 | -62.5168 | 60.1501 | 60.1456 | 62.2742 | 62.439 | 122.6852 | 62.3062 | 60.3287
3045.4844 | 0.045776 | 0.42618 | -0.79361 | -0.23178 | 0.13458 | -0.28732 | -0.18478 | 60.3149 | -62.0956 | 0.09613 | -62.352 | 60.2646 | 62.3108 | 62.2787 | 0.030518 | -0.10895 | 0.058746 | 0.26916 | -0.15915 | -0.16235 | 0.10071 | 0.18768 | -62.4619 | 60.173 | 60.1547 | 62.2833 | 62.4298 | 122.8317 | 62.265 | 60.2737
3047.1562 | 0.076294 | 0.41763 | -0.78293 | -0.2446 | 0.13565 | -0.29373 | -0.18478 | 60.3745 | -62.059 | 0.15106 | -62.3245 | 60.2509 | 62.3108 | 62.2787 | 0.045776 | -0.10681 | 0.059814 | 0.28519 | -0.17624 | -0.1741 | 0.16022 | 0.24261 | -62.4207 | 60.173 | 60.1685 | 62.265 | 62.4252 | 122.8317 | 62.2513 | 60.2646
3048.8125 | 0.045776 | 0.40268 | -0.77438 | -0.22003 | 0.13458 | -0.24139 | -0.16556 | 60.2921 | -62.2101 | -0.041199 | -62.4161 | 60.3058 | 62.3428 | 62.3062 | 0.045776 | -0.085449 | 0.058746 | 0.27344 | -0.13138 | -0.17838 | -0.082397 | -0.09613 | -62.6404 | 60.2371 | 60.2188 | 62.2833 | 62.4619 | 122.7036 | 62.3199 | 60.3241
3050.5 | 0.045776 | 0.40695 | -0.78186 | -0.23605 | 0.13779 | -0.26596 | -0.18372 | 60.2829 | -62.146 | 0.07782 | -62.3978 | 60.3104 | 62.3016 | 62.3016 | 0.030518 | -0.086517 | 0.060883 | 0.27664 | -0.16342 | -0.16983 | 0.041199 | 0.11444 | -62.5671 | 60.2554 | 60.2142 | 62.2879 | 62.4344 | 122.8043 | 62.2559 | 60.2921
3052.1875 | 0.030518 | 0.43366 | -0.79147 | -0.22217 | 0.13992 | -0.28305 | -0.18372 | 60.2829 | -62.1323 | 0.045776 | -62.3932 | 60.2371 | 62.3291 | 62.2971 | 0.030518 | -0.11002 | 0.052338 | 0.27023 | -0.15274 | -0.16129 | 0.041199 | 0.10986 | -62.5076 | 60.2005 | 60.1639 | 62.2879 | 62.4847 | 122.7493 | 62.3062 | 60.2737
3053.8438 | 0.045776 | 0.40268 | -0.77011 | -0.24674 | 0.12711 | -0.25635 | -0.18906 | 60.3058 | -62.1552 | 0.068665 | -62.384 | 60.3241 | 62.3291 | 62.2971 | 0.045776 | -0.079041 | 0.057678 | 0.29159 | -0.15488 | -0.1709 | 0.009155 | 0.082397 | -62.5717 | 60.26 | 60.2554 | 62.2742 | 62.4207 | 122.8409 | 62.2559 | 60.2966
3055.5156 | 0.030518 | 0.43579 | -0.78613 | -0.21255 | 0.13351 | -0.27985 | -0.18265 | 60.3333 | -62.1002 | 0.032043 | -62.3932 | 60.2325 | 62.3245 | 62.2833 | 0.061035 | -0.098267 | 0.050201 | 0.27985 | -0.15488 | -0.16449 | 0.036621 | 0.07782 | -62.5168 | 60.1868 | 60.1501 | 62.265 | 62.439 | 122.6898 | 62.3154 | 60.2829
3057.2031 | 0.045776 | 0.40909 | -0.77866 | -0.23498 | 0.13565 | -0.26916 | -0.18906 | 60.3561 | -62.0636 | 0.14648 | -62.3291 | 60.2646 | 62.3108 | 62.2742 | 0.030518 | -0.09613 | 0.064087 | 0.27344 | -0.16235 | -0.17624 | 0.10529 | 0.21057 | -62.5122 | 60.2097 | 60.1913 | 62.2513 | 62.4619 | 122.7768 | 62.2604 | 60.3012
3058.875 | 0.045776 | 0.42938 | -0.78507 | -0.21255 | 0.1506 | -0.24887 | -0.17944 | 60.3195 | -62.146 | -0.018311 | -62.3886 | 60.2829 | 62.3154 | 62.2833 | 0.061035 | -0.09079 | 0.058746 | 0.27985 | -0.14099 | -0.16769 | 0.009155 | 0.022888 | -62.5122 | 60.1685 | 60.1639 | 62.2879 | 62.4298 | 122.7768 | 62.3108 | 60.2509
3060.5469 | 0.061035 | 0.38773 | -0.78079 | -0.23605 | 0.15488 | -0.23498 | -0.17838 | 60.3378 | -62.1277 | 0.073242 | -62.352 | 60.3104 | 62.3199 | 62.2742 | 0.076294 | -0.075836 | 0.065155 | 0.28519 | -0.1506 | -0.17517 | 0.036621 | 0.086975 | -62.5397 | 60.2646 | 60.2005 | 62.2604 | 62.4481 | 122.8363 | 62.2559 | 60.2737
3062.2031 | 0.045776 | 0.42404 | -0.78186 | -0.23178 | 0.1207 | -0.29373 | -0.17303 | 60.3149 | -62.0728 | 0.10071 | -62.352 | 60.2554 | 62.2971 | 62.265 | 0.061035 | -0.11002 | 0.054474 | 0.28091 | -0.16022 | -0.16022 | 0.13275 | 0.21515 | -62.4573 | 60.1639 | 60.1639 | 62.2696 | 62.439 | 122.818 | 62.265 | 60.26
3063.8594 | 0.045776 | 0.40802 | -0.77545 | -0.23498 | 0.13992 | -0.26276 | -0.18585 | 60.3058 | -62.1552 | 0.045776 | -62.3932 | 60.3149 | 62.3337 | 62.2879 | 0.076294 | -0.082245 | 0.068359 | 0.28305 | -0.16769 | -0.16556 | 0.036621 | 0.09613 | -62.5717 | 60.2554 | 60.2325 | 62.2833 | 62.4161 | 122.8226 | 62.265 | 60.3058
3065.5938 | 0.045776 | 0.41229 | -0.77866 | -0.23178 | 0.13886 | -0.26169 | -0.17624 | 60.3561 | -62.0682 | 0.050354 | -62.3474 | 60.2051 | 62.2971 | 62.2696 | 0.076294 | -0.099335 | 0.054474 | 0.28198 | -0.13886 | -0.1741 | 0.032043 | 0.059509 | -62.4756 | 60.173 | 60.1273 | 62.2971 | 62.4435 | 122.7264 | 62.3154 | 60.3012
3067.3125 | 0.045776 | 0.41016 | -0.7872 | -0.24033 | 0.13672 | -0.26596 | -0.18265 | 60.3241 | -62.0911 | 0.1236 | -62.3566 | 60.3012 | 62.2879 | 62.2925 | 0.076294 | -0.099335 | 0.05661 | 0.28946 | -0.16235 | -0.16556 | 0.064087 | 0.15106 | -62.5534 | 60.2188 | 60.2234 | 62.2604 | 62.4298 | 122.7585 | 62.2742 | 60.2829
3068.9688 | 0.045776 | 0.41763 | -0.78079 | -0.2211 | 0.1239 | -0.24994 | -0.17303 | 60.2875 | -62.1735 | -0.068665 | -62.4207 | 60.2966 | 62.2925 | 62.3062 | 0.061035 | -0.087585 | 0.065155 | 0.28946 | -0.14099 | -0.17624 | -0.050354 | -0.064087 | -62.5717 | 60.2142 | 60.1959 | 62.2742 | 62.4344 | 122.7493 | 62.3337 | 60.2737
3070.6562 | 0.045776 | 0.40268 | -0.77011 | -0.22003 | 0.14633 | -0.24246 | -0.1709 | 60.3287 | -62.1323 | 0.032043 | -62.3795 | 60.3058 | 62.2925 | 62.2833 | 0.030518 | -0.072632 | 0.065155 | 0.28519 | -0.14633 | -0.17303 | -0.022888 | -0.009155 | -62.5671 | 60.2234 | 60.2097 | 62.265 | 62.4756 | 122.7173 | 62.3062 | 60.2783
3072.3594 | 0.061035 | 0.41122 | -0.78186 | -0.2243 | 0.13458 | -0.27451 | -0.16663 | 60.3424 | -62.059 | 0.041199 | -62.352 | 60.2097 | 62.3154 | 62.2696 | 0.045776 | -0.099335 | 0.064087 | 0.27023 | -0.13779 | -0.16876 | 0.009155 | 0.054932 | -62.4802 | 60.1318 | 60.1227 | 62.2787 | 62.4435 | 122.7173 | 62.3016 | 60.26
3074.0312 | 0.045776 | 0.41763 | -0.79468 | -0.24567 | 0.13245 | -0.29587 | -0.19546 | 60.3378 | -62.0544 | 0.1236 | -62.3337 | 60.2692 | 62.2833 | 62.265 | 0.030518 | -0.11002 | 0.066223 | 0.27664 | -0.18372 | -0.16449 | 0.13733 | 0.21973 | -62.4435 | 60.1685 | 60.1364 | 62.2513 | 62.4298 | 122.8317 | 62.2604 | 60.2737
3075.7188 | 0.045776 | 0.41336 | -0.77011 | -0.21683 | 0.13565 | -0.25207 | -0.17303 | 60.2692 | -62.1964 | -0.073242 | -62.4069 | 60.347 | 62.3337 | 62.2833 | 0.061035 | -0.083313 | 0.064087 | 0.27878 | -0.13992 | -0.17303 | -0.073242 | -0.091553 | -62.59 | 60.2188 | 60.2005 | 62.2742 | 62.4481 | 122.731 | 62.3337 | 60.3058
3077.375 | 0.045776 | 0.41443 | -0.77759 | -0.25207 | 0.13138 | -0.27771 | -0.17197 | 60.347 | -62.0316 | 0.17853 | -62.3291 | 60.2417 | 62.2925 | 62.2925 | 0.061035 | -0.10574 | 0.063019 | 0.28519 | -0.16556 | -0.17838 | 0.13733 | 0.27008 | -62.4527 | 60.173 | 60.1318 | 62.2467 | 62.3978 | 122.7859 | 62.2559 | 60.2783
3079.0469 | 0.045776 | 0.41016 | -0.78079 | -0.2211 | 0.12283 | -0.23819 | -0.18265 | 60.3653 | -62.0865 | 0.068665 | -62.3749 | 60.3058 | 62.3199 | 62.2742 | 0.061035 | -0.074768 | 0.059814 | 0.28732 | -0.13992 | -0.17944 | 0.004578 | 0.050354 | -62.5442 | 60.2234 | 60.1959 | 62.265 | 62.4115 | 122.7631 | 62.2787 | 60.2921
3080.7188 | 0.015259 | 0.40695 | -0.77011 | -0.21042 | 0.1442 | -0.2478 | -0.18372 | 60.2692 | -62.1918 | -0.022888 | -62.4023 | 60.2966 | 62.3062 | 62.2787 | 0.045776 | -0.086517 | 0.050201 | 0.28305 | -0.13458 | -0.16876 | -0.09613 | -0.086975 | -62.6221 | 60.2417 | 60.2371 | 62.2833 | 62.4481 | 122.6852 | 62.3108 | 60.3516
3082.375 | 0.045776 | 0.42725 | -0.79361 | -0.23392 | 0.13245 | -0.29159 | -0.18051 | 60.347 | -62.0087 | 0.17853 | -62.3245 | 60.2371 | 62.3062 | 62.2559 | 0.030518 | -0.099335 | 0.060883 | 0.27451 | -0.16983 | -0.16556 | 0.13733 | 0.27008 | -62.4344 | 60.1685 | 60.1776 | 62.2421 | 62.4161 | 122.7814 | 62.2604 | 60.2646
3084.0312 | 0.061035 | 0.41016 | -0.7637 | -0.23178 | 0.13886 | -0.24674 | -0.18158 | 60.347 | -62.1277 | 0.022888 | -62.3703 | 60.2783 | 62.2971 | 62.2833 | 0.061035 | -0.087585 | 0.060883 | 0.29159 | -0.13886 | -0.16876 | -0.027466 | 0.004578 | -62.5626 | 60.2417 | 60.228 | 62.2604 | 62.4527 | 122.699 | 62.2879 | 60.3058
3085.7031 | 0.045776 | 0.42938 | -0.77759 | -0.22964 | 0.11536 | -0.29266 | -0.19974 | 60.2966 | -62.0956 | 0.032043 | -62.3657 | 60.228 | 62.3199 | 62.2742 | 0.076294 | -0.10788 | 0.064087 | 0.28198 | -0.16556 | -0.16663 | 0.022888 | 0.07782 | -62.5214 | 60.1685 | 60.1639 | 62.2696 | 62.4527 | 122.6944 | 62.3062 | 60.2921
3087.4062 | 0.076294 | 0.40482 | -0.77972 | -0.24353 | 0.14526 | -0.27985 | -0.18265 | 60.3378 | -62.0499 | 0.17395 | -62.3383 | 60.228 | 62.2971 | 62.2742 | 0.061035 | -0.1004 | 0.063019 | 0.27771 | -0.16769 | -0.17303 | 0.10986 | 0.22888 | -62.471 | 60.1868 | 60.1822 | 62.2467 | 62.4161 | 122.7768 | 62.2467 | 60.3104
3089.0938 | 0.076294 | 0.439 | -0.78293 | -0.23071 | 0.14954 | -0.28305 | -0.19333 | 60.2921 | -62.0956 | 0.086975 | -62.352 | 60.2646 | 62.2879 | 62.2742 | 0.091553 | -0.11002 | 0.05661 | 0.27771 | -0.16769 | -0.16235 | 0.09613 | 0.17853 | -62.4619 | 60.1913 | 60.1639 | 62.2742 | 62.4161 | 122.8134 | 62.265 | 60.26
3090.75 | 0.045776 | 0.40161 | -0.77652 | -0.21683 | 0.14633 | -0.2446 | -0.1741 | 60.26 | -62.2147 | -0.059509 | -62.4207 | 60.2921 | 62.3108 | 62.2971 | 0.061035 | -0.071564 | 0.058746 | 0.28732 | -0.13031 | -0.17197 | -0.073242 | -0.10529 | -62.5992 | 60.2554 | 60.2142 | 62.2879 | 62.4664 | 122.6761 | 62.3428 | 60.3149
3092.4219 | 0.030518 | 0.40375 | -0.78079 | -0.24246 | 0.14099 | -0.2681 | -0.1709 | 60.2829 | -62.146 | 0.064087 | -62.3978 | 60.3012 | 62.3199 | 62.3108 | 0.061035 | -0.084381 | 0.05661 | 0.29053 | -0.15808 | -0.17303 | 0.054932 | 0.10986 | -62.5534 | 60.2417 | 60.228 | 62.2879 | 62.4207 | 122.7997 | 62.265 | 60.2966
3094.125 | 0.045776 | 0.40802 | -0.79147 | -0.23712 | 0.14526 | -0.27771 | -0.17944 | 60.347 | -62.0132 | 0.16479 | -62.3245 | 60.2325 | 62.2833 | 62.265 | 0.061035 | -0.097198 | 0.058746 | 0.2713 | -0.17303 | -0.17517 | 0.13275 | 0.27466 | -62.4435 | 60.173 | 60.1685 | 62.2375 | 62.4207 | 122.7676 | 62.2467 | 60.2783
3095.7812 | 0.045776 | 0.39627 | -0.77438 | -0.23071 | 0.13458 | -0.24674 | -0.1709 | 60.3333 | -62.114 | 0.073242 | -62.3566 | 60.2875 | 62.3016 | 62.265 | 0.061035 | -0.0737 | 0.058746 | 0.29587 | -0.13458 | -0.17731 | 0.045776 | 0.082397 | -62.5305 | 60.228 | 60.2097 | 62.2284 | 62.4435 | 122.7997 | 62.2559 | 60.2829
3097.4688 | 0.030518 | 0.3952 | -0.77866 | -0.21362 | 0.1239 | -0.23392 | -0.1741 | 60.3424 | -62.1185 | 0.041199 | -62.3795 | 60.2829 | 62.3062 | 62.2833 | 0.045776 | -0.085449 | 0.064087 | 0.29159 | -0.13245 | -0.16556 | -0.027466 | 0.004578 | -62.5534 | 60.2325 | 60.2142 | 62.2696 | 62.4527 | 122.699 | 62.2971 | 60.3149
3099.1562 | 0.045776 | 0.4187 | -0.77331 | -0.22964 | 0.13779 | -0.26062 | -0.17197 | 60.3378 | -62.0865 | 0.041199 | -62.3383 | 60.2142 | 62.3016 | 62.2604 | 0.045776 | -0.09613 | 0.048065 | 0.28198 | -0.15701 | -0.16342 | 0.027466 | 0.054932 | -62.4756 | 60.141 | 60.1593 | 62.2559 | 62.4252 | 122.699 | 62.3062 | 60.2554
3100.8281 | 0.045776 | 0.41443 | -0.77652 | -0.25314 | 0.13672 | -0.26062 | -0.18692 | 60.2783 | -62.1506 | 0.050354 | -62.3795 | 60.3012 | 62.3291 | 62.2879 | 0.061035 | -0.083313 | 0.065155 | 0.28198 | -0.15915 | -0.16983 | 0.009155 | 0.091553 | -62.5534 | 60.2509 | 60.2417 | 62.265 | 62.4207 | 122.8226 | 62.2604 | 60.2463
3102.5 | 0.030518 | 0.42725 | -0.7872 | -0.22537 | 0.13351 | -0.27878 | -0.18158 | 60.2921 | -62.0865 | 0.050354 | -62.3749 | 60.2051 | 62.3108 | 62.2696 | 0.061035 | -0.11002 | 0.058746 | 0.27771 | -0.16022 | -0.16663 | 0.036621 | 0.073242 | -62.4893 | 60.141 | 60.1456 | 62.2879 | 62.4481 | 122.6532 | 62.3108 | 60.3012
3104.1719 | 0.045776 | 0.4187 | -0.78079 | -0.21255 | 0.14099 | -0.24353 | -0.1741 | 60.2966 | -62.1689 | -0.036621 | -62.4069 | 60.2554 | 62.3108 | 62.2787 | 0.061035 | -0.084381 | 0.057678 | 0.28519 | -0.14313 | -0.16129 | -0.032043 | -0.032043 | -62.5168 | 60.2005 | 60.1639 | 62.2559 | 62.4252 | 122.7173 | 62.3154 | 60.2783
3105.8281 | 0.045776 | 0.41763 | -0.78079 | -0.24139 | 0.14099 | -0.28198 | -0.18478 | 60.2737 | -62.1002 | 0.059509 | -62.3795 | 60.2646 | 62.2879 | 62.2696 | 0.030518 | -0.11002 | 0.058746 | 0.27557 | -0.16769 | -0.16983 | 0.082397 | 0.14648 | -62.4802 | 60.1547 | 60.173 | 62.2696 | 62.4207 | 122.8043 | 62.2787 | 60.2875
3107.5156 | 0.061035 | 0.41763 | -0.78507 | -0.22858 | 0.14206 | -0.2713 | -0.18799 | 60.3195 | -62.0728 | 0.054932 | -62.3657 | 60.2005 | 62.2971 | 62.2696 | 0.045776 | -0.10361 | 0.063019 | 0.28946 | -0.15808 | -0.16342 | 0.041199 | 0.068665 | -62.5076 | 60.1593 | 60.141 | 62.2742 | 62.4207 | 122.6669 | 62.3199 | 60.2554
3109.2031 | 0.030518 | 0.39841 | -0.76477 | -0.2243 | 0.14526 | -0.2446 | -0.17731 | 60.3653 | -62.1048 | 0.064087 | -62.3703 | 60.3012 | 62.3016 | 62.2696 | 0.045776 | -0.080109 | 0.063019 | 0.29373 | -0.13886 | -0.18265 | 0.018311 | 0.022888 | -62.5305 | 60.2005 | 60.2051 | 62.265 | 62.4298 | 122.7402 | 62.2787 | 60.3058
3110.8594 | 0.030518 | 0.41977 | -0.78827 | -0.24246 | 0.14526 | -0.28198 | -0.17838 | 60.3333 | -62.0361 | 0.12817 | -62.3245 | 60.2509 | 62.2925 | 62.233 | 0.076294 | -0.11322 | 0.057678 | 0.28198 | -0.16129 | -0.16129 | 0.15564 | 0.24719 | -62.4344 | 60.1501 | 60.1501 | 62.2513 | 62.3978 | 122.8088 | 62.2604 | 60.26
3112.5938 | 0.061035 | 0.41229 | -0.77759 | -0.22003 | 0.14099 | -0.24674 | -0.1709 | 60.2921 | -62.1872 | -0.064087 | -62.4115 | 60.2829 | 62.3154 | 62.2925 | 0.076294 | -0.075836 | 0.053406 | 0.30548 | -0.13992 | -0.1741 | -0.07782 | -0.10071 | -62.6038 | 60.2371 | 60.228 | 62.2833 | 62.4573 | 122.7081 | 62.2879 | 60.3149
3114.2656 | 0.061035 | 0.41229 | -0.78293 | -0.23392 | 0.13565 | -0.27878 | -0.17944 | 60.3424 | -62.0361 | 0.17395 | -62.3062 | 60.2234 | 62.2879 | 62.2559 | 0.061035 | -0.10788 | 0.055542 | 0.27878 | -0.15701 | -0.17517 | 0.13733 | 0.23804 | -62.4527 | 60.1593 | 60.1685 | 62.265 | 62.4207 | 122.7539 | 62.2559 | 60.2829
3115.9219 | 0.030518 | 0.42618 | -0.78293 | -0.21362 | 0.14099 | -0.25742 | -0.1741 | 60.2966 | -62.1872 | -0.054932 | -62.3978 | 60.2875 | 62.3108 | 62.3016 | 0.076294 | -0.075836 | 0.059814 | 0.28839 | -0.13992 | -0.17303 | -0.045776 | -0.064087 | -62.5397 | 60.1959 | 60.173 | 62.2742 | 62.4161 | 122.7264 | 62.2925 | 60.2646
3117.625 | 0.061035 | 0.42297 | -0.78186 | -0.2243 | 0.14313 | -0.26169 | -0.17197 | 60.3378 | -62.0636 | 0.059509 | -62.3383 | 60.2005 | 62.3062 | 62.2604 | 0.045776 | -0.092926 | 0.049133 | 0.26703 | -0.14099 | -0.15488 | 0.027466 | 0.059509 | -62.4527 | 60.1089 | 60.1273 | 62.2604 | 62.4435 | 122.6852 | 62.3016 | 60.26
3119.2969 | 0.061035 | 0.40375 | -0.77972 | -0.23819 | 0.13779 | -0.25528 | -0.17624 | 60.3012 | -62.178 | 0.050354 | -62.3703 | 60.2875 | 62.3199 | 62.2879 | 0.061035 | -0.087585 | 0.063019 | 0.28732 | -0.15701 | -0.16876 | 0.009155 | 0.086975 | -62.5397 | 60.2234 | 60.2371 | 62.2696 | 62.4298 | 122.8043 | 62.2421 | 60.2783
3120.9688 | 0.076294 | 0.40909 | -0.7872 | -0.22751 | 0.12604 | -0.26169 | -0.17303 | 60.2646 | -62.1597 | -0.059509 | -62.3978 | 60.3058 | 62.2925 | 62.2787 | 0.030518 | -0.09079 | 0.059814 | 0.28091 | -0.14847 | -0.16022 | -0.068665 | -0.086975 | -62.5626 | 60.2371 | 60.1913 | 62.2879 | 62.4481 | 122.7219 | 62.3108 | 60.2646
3122.6406 | 0.045776 | 0.4155 | -0.78186 | -0.22537 | 0.12711 | -0.27985 | -0.16876 | 60.2554 | -62.1277 | 0.068665 | -62.3886 | 60.2737 | 62.2742 | 62.2742 | 0.045776 | -0.091858 | 0.0737 | 0.27771 | -0.15274 | -0.16129 | 0.045776 | 0.11902 | -62.5442 | 60.2554 | 60.2142 | 62.2742 | 62.4435 | 122.7631 | 62.2833 | 60.2737
3124.3125 | 0.061035 | 0.41443 | -0.784 | -0.2179 | 0.12924 | -0.24567 | -0.17944 | 60.26 | -62.146 | -0.054932 | -62.4069 | 60.2737 | 62.3016 | 62.2696 | 0.030518 | -0.09079 | 0.059814 | 0.29266 | -0.14847 | -0.16769 | -0.045776 | -0.041199 | -62.5351 | 60.1913 | 60.1822 | 62.2742 | 62.4619 | 122.7356 | 62.3245 | 60.2737
3125.9844 | 0.045776 | 0.41763 | -0.79254 | -0.24994 | 0.13565 | -0.28839 | -0.18265 | 60.3012 | -62.0636 | 0.068665 | -62.3657 | 60.2005 | 62.2742 | 62.265 | 0.061035 | -0.10788 | 0.05661 | 0.2713 | -0.16876 | -0.16769 | 0.018311 | 0.068665 | -62.4893 | 60.1639 | 60.1456 | 62.2696 | 62.439 | 122.6624 | 62.2971 | 60.2783
3127.6719 | 0.061035 | 0.41977 | -0.77866 | -0.22964 | 0.13458 | -0.26596 | -0.19119 | 60.2737 | -62.1368 | 0.064087 | -62.3932 | 60.2966 | 62.3199 | 62.2513 | 0.061035 | -0.093994 | 0.063019 | 0.29159 | -0.14954 | -0.1709 | 0.041199 | 0.1236 | -62.5534 | 60.2737 | 60.228 | 62.2559 | 62.4115 | 122.7631 | 62.2467 | 60.2966
3129.3438 | 0.061035 | 0.43366 | -0.78186 | -0.2179 | 0.11856 | -0.27451 | -0.17197 | 60.3241 | -62.0453 | 0.068665 | -62.3383 | 60.2371 | 62.265 | 62.2787 | 0.061035 | -0.091858 | 0.054474 | 0.27771 | -0.1506 | -0.16876 | 0.036621 | 0.068665 | -62.4802 | 60.1593 | 60.1501 | 62.2696 | 62.4527 | 122.6578 | 62.3062 | 60.2554
3131 | 0.076294 | 0.392 | -0.7872 | -0.22644 | 0.13458 | -0.24139 | -0.17624 | 60.3104 | -62.1231 | 0.018311 | -62.3795 | 60.3058 | 62.2696 | 62.2604 | 0.061035 | -0.075836 | 0.058746 | 0.28305 | -0.14099 | -0.17517 | -0.068665 | -0.041199 | -62.5992 | 60.2142 | 60.1959 | 62.2696 | 62.4252 | 122.6807 | 62.3016 | 60.3149
3132.6719 | 0.061035 | 0.42831 | -0.78934 | -0.23605 | 0.14954 | -0.28519 | -0.18585 | 60.2417 | -62.1048 | 0.045776 | -62.3611 | 60.2325 | 62.3062 | 62.2742 | 0.061035 | -0.10574 | 0.053406 | 0.28412 | -0.16235 | -0.15274 | 0.022888 | 0.10986 | -62.4893 | 60.1547 | 60.1456 | 62.2513 | 62.4298 | 122.699 | 62.2787 | 60.2783
3134.3438 | 0.030518 | 0.4187 | -0.78507 | -0.24033 | 0.12817 | -0.26489 | -0.18265 | 60.2875 | -62.1506 | 0.054932 | -62.3795 | 60.3058 | 62.2925 | 62.2742 | 0.076294 | -0.084381 | 0.059814 | 0.27878 | -0.16022 | -0.16663 | 0.018311 | 0.086975 | -62.558 | 60.2371 | 60.2097 | 62.2696 | 62.4298 | 122.8088 | 62.265 | 60.2966
3136.0156 | 0.045776 | 0.39414 | -0.77759 | -0.22003 | 0.14633 | -0.24994 | -0.17517 | 60.3333 | -62.0865 | 0.082397 | -62.3383 | 60.2875 | 62.2742 | 62.2742 | 0.030518 | -0.085449 | 0.061951 | 0.2713 | -0.13138 | -0.17838 | 0.041199 | 0.086975 | -62.5214 | 60.2325 | 60.2051 | 62.2559 | 62.4344 | 122.7905 | 62.2513 | 60.2737
3137.6875 | 0.076294 | 0.41977 | -0.79041 | -0.2478 | 0.13672 | -0.28625 | -0.17944 | 60.2554 | -62.114 | 0.054932 | -62.352 | 60.2051 | 62.2787 | 62.2604 | 0.045776 | -0.11429 | 0.05127 | 0.27878 | -0.16983 | -0.16342 | 0.027466 | 0.1236 | -62.5076 | 60.1547 | 60.1868 | 62.2559 | 62.4252 | 122.7173 | 62.2742 | 60.2692
3139.3594 | 0.045776 | 0.40588 | -0.77972 | -0.22324 | 0.13992 | -0.24246 | -0.1741 | 60.3378 | -62.0956 | 0.032043 | -62.352 | 60.2966 | 62.2833 | 62.265 | 0.061035 | -0.067291 | 0.059814 | 0.29053 | -0.12497 | -0.16663 | -0.009155 | 0.004578 | -62.5442 | 60.2005 | 60.1959 | 62.2696 | 62.4115 | 122.6898 | 62.2879 | 60.2875
3141.0312 | 0.030518 | 0.392 | -0.77438 | -0.23605 | 0.13672 | -0.25101 | -0.16983 | 60.2966 | -62.1094 | 0.059509 | -62.3291 | 60.2829 | 62.2879 | 62.2513 | 0.045776 | -0.087585 | 0.065155 | 0.28412 | -0.15595 | -0.16663 | 0.032043 | 0.10071 | -62.5214 | 60.2142 | 60.2142 | 62.2604 | 62.4115 | 122.7951 | 62.2467 | 60.2692
3142.7031 | 0.045776 | 0.42404 | -0.79254 | -0.22537 | 0.14847 | -0.28732 | -0.16983 | 60.3012 | -62.0453 | 0.068665 | -62.3428 | 60.1868 | 62.2833 | 62.2742 | 0.045776 | -0.10361 | 0.061951 | 0.27985 | -0.15274 | -0.16342 | 0.032043 | 0.064087 | -62.4893 | 60.141 | 60.1547 | 62.2604 | 62.4207 | 122.644 | 62.2971 | 60.2783
3144.375 | 0.061035 | 0.41229 | -0.78079 | -0.24353 | 0.13245 | -0.26596 | -0.18478 | 60.2783 | -62.1368 | 0.041199 | -62.3703 | 60.3333 | 62.2696 | 62.2742 | 0.061035 | -0.077972 | 0.074768 | 0.29053 | -0.16342 | -0.17624 | 0.013733 | 0.073242 | -62.5442 | 60.2509 | 60.2371 | 62.2742 | 62.4298 | 122.8043 | 62.2513 | 60.2509
3146.0625 | 0.045776 | 0.43793 | -0.78293 | -0.21362 | 0.12283 | -0.29053 | -0.18906 | 60.2371 | -62.0956 | 0.041199 | -62.3886 | 60.2463 | 62.2925 | 62.2925 | 0.076294 | -0.10681 | 0.061951 | 0.27451 | -0.13992 | -0.16983 | 0.032043 | 0.10529 | -62.4939 | 60.1685 | 60.1456 | 62.2467 | 62.4344 | 122.7081 | 62.265 | 60.2646
3147.7344 | 0.030518 | 0.40375 | -0.78507 | -0.24139 | 0.13886 | -0.27344 | -0.17624 | 60.2829 | -62.1368 | 0.07782 | -62.3795 | 60.3104 | 62.3016 | 62.2742 | 0.076294 | -0.093994 | 0.070496 | 0.29053 | -0.16663 | -0.17197 | 0.036621 | 0.10986 | -62.5397 | 60.2417 | 60.2188 | 62.2513 | 62.4298 | 122.7631 | 62.2375 | 60.2692
3149.4219 | 0.076294 | 0.41977 | -0.78079 | -0.24033 | 0.12924 | -0.28519 | -0.18799 | 60.2875 | -62.0956 | 0.036621 | -62.384 | 60.2325 | 62.2925 | 62.2604 | 0.045776 | -0.10574 | 0.060883 | 0.27664 | -0.16449 | -0.16449 | 0.022888 | 0.07782 | -62.4985 | 60.1685 | 60.1547 | 62.2559 | 62.4207 | 122.6624 | 62.3108 | 60.2463
3151.125 | 0.061035 | 0.40695 | -0.78613 | -0.23498 | 0.12924 | -0.24567 | -0.17838 | 60.3012 | -62.1277 | 0.050354 | -62.3657 | 60.3012 | 62.2787 | 62.2467 | 0.076294 | -0.089722 | 0.068359 | 0.29053 | -0.1442 | -0.18265 | 0.032043 | 0.07782 | -62.5305 | 60.2646 | 60.2234 | 62.2421 | 62.4344 | 122.818 | 62.2284 | 60.26
3152.7969 | 0.045776 | 0.44113 | -0.78934 | -0.20828 | 0.13031 | -0.27664 | -0.16983 | 60.3058 | -62.0544 | 0.041199 | -62.3703 | 60.1959 | 62.2925 | 62.2421 | 0.061035 | -0.1004 | 0.054474 | 0.28305 | -0.15381 | -0.16129 | 0.022888 | 0.073242 | -62.4847 | 60.1501 | 60.1318 | 62.2467 | 62.4344 | 122.6349 | 62.2925 | 60.2692
3154.5 | 0.045776 | 0.40695 | -0.78079 | -0.23498 | 0.13886 | -0.24567 | -0.1709 | 60.3287 | -62.0956 | 0.068665 | -62.3474 | 60.2875 | 62.3016 | 62.2559 | 0.061035 | -0.082245 | 0.054474 | 0.29159 | -0.14526 | -0.16769 | 0.045776 | 0.07782 | -62.5122 | 60.2234 | 60.2051 | 62.265 | 62.4115 | 122.7631 | 62.2467 | 60.26
3156.2031 | 0.030518 | 0.42297 | -0.77652 | -0.21469 | 0.15167 | -0.27023 | -0.17197 | 60.3195 | -62.0499 | 0.054932 | -62.3245 | 60.2234 | 62.2742 | 62.2513 | 0.061035 | -0.098267 | 0.068359 | 0.27023 | -0.14847 | -0.15808 | 0.032043 | 0.050354 | -62.4756 | 60.1318 | 60.1227 | 62.2787 | 62.4252 | 122.6807 | 62.3154 | 60.2737
3157.875 | 0.061035 | 0.4187 | -0.784 | -0.24674 | 0.1442 | -0.25955 | -0.17838 | 60.2646 | -62.1323 | 0.054932 | -62.3703 | 60.3195 | 62.2742 | 62.2559 | 0.045776 | -0.092926 | 0.067291 | 0.28412 | -0.15381 | -0.15701 | 0.018311 | 0.086975 | -62.5488 | 60.2371 | 60.2188 | 62.2742 | 62.4298 | 122.7768 | 62.2284 | 60.2737
3159.5938 | 0.061035 | 0.40909 | -0.77652 | -0.2211 | 0.1442 | -0.24353 | -0.18692 | 60.3104 | -62.0865 | 0.091553 | -62.3428 | 60.3058 | 62.2971 | 62.2604 | 0.045776 | -0.086517 | 0.066223 | 0.28412 | -0.13779 | -0.17303 | 0.032043 | 0.073242 | -62.5031 | 60.2097 | 60.1776 | 62.233 | 62.4207 | 122.7722 | 62.2238 | 60.2692
3161.2656 | 0.061035 | 0.42831 | -0.7872 | -0.22537 | 0.11536 | -0.27985 | -0.17624 | 60.2921 | -62.0316 | 0.054932 | -62.3474 | 60.2005 | 62.2787 | 62.2513 | 0.061035 | -0.10361 | 0.054474 | 0.27985 | -0.15595 | -0.16663 | 0.018311 | 0.073242 | -62.4802 | 60.1318 | 60.1135 | 62.2604 | 62.4207 | 122.644 | 62.3245 | 60.2554
3162.9375 | 0.076294 | 0.39948 | -0.784 | -0.24033 | 0.13245 | -0.24674 | -0.16876 | 60.3104 | -62.1048 | 0.036621 | -62.3657 | 60.2966 | 62.2833 | 62.2513 | 0.045776 | -0.09613 | 0.063019 | 0.29053 | -0.13886 | -0.16983 | -0.050354 | -0.009155 | -62.5488 | 60.2051 | 60.173 | 62.2559 | 62.4252 | 122.6532 | 62.2925 | 60.2921
3164.6719 | 0.076294 | 0.41657 | -0.78827 | -0.22964 | 0.11856 | -0.28625 | -0.18372 | 60.26 | -62.0956 | 0.07782 | -62.3474 | 60.2188 | 62.2742 | 62.2421 | 0.061035 | -0.11749 | 0.059814 | 0.27237 | -0.17944 | -0.16235 | 0.073242 | 0.13733 | -62.4527 | 60.1639 | 60.141 | 62.2421 | 62.4023 | 122.7631 | 62.2513 | 60.2371
3166.3438 | 0.061035 | 0.40268 | -0.76477 | -0.22858 | 0.12924 | -0.2446 | -0.18051 | 60.3149 | -62.1185 | 0.027466 | -62.3566 | 60.2829 | 62.2696 | 62.2513 | 0.045776 | -0.086517 | 0.070496 | 0.29053 | -0.14099 | -0.18265 | -0.027466 | -0.018311 | -62.5626 | 60.2188 | 60.1959 | 62.2742 | 62.439 | 122.6578 | 62.2833 | 60.2737
3168 | 0.045776 | 0.43472 | -0.79041 | -0.24139 | 0.14633 | -0.29159 | -0.20081 | 60.2371 | -62.0911 | 0.050354 | -62.3566 | 60.2417 | 62.2787 | 62.265 | 0.061035 | -0.10254 | 0.050201 | 0.27985 | -0.15808 | -0.17303 | 0.041199 | 0.12817 | -62.471 | 60.173 | 60.1685 | 62.2696 | 62.3886 | 122.7036 | 62.2559 | 60.2692
3169.6875 | 0.045776 | 0.3952 | -0.78079 | -0.2243 | 0.12817 | -0.24033 | -0.18478 | 60.3104 | -62.1277 | 0.009155 | -62.3566 | 60.2554 | 62.2879 | 62.2513 | 0.061035 | -0.081177 | 0.060883 | 0.27985 | -0.13992 | -0.17944 | -0.050354 | -0.045776 | -62.5763 | 60.228 | 60.1776 | 62.265 | 62.4207 | 122.6578 | 62.2971 | 60.2966
3171.375 | 0.045776 | 0.41229 | -0.784 | -0.24994 | 0.13245 | -0.27557 | -0.18478 | 60.3149 | -62.0178 | 0.16479 | -62.3062 | 60.2188 | 62.2604 | 62.2421 | 0.061035 | -0.10895 | 0.061951 | 0.27344 | -0.17303 | -0.16342 | 0.11902 | 0.24719 | -62.439 | 60.1501 | 60.1547 | 62.233 | 62.3978 | 122.731 | 62.2604 | 60.26
3173.0469 | 0 | 0.43793 | -0.78827 | -0.22751 | 0.13031 | -0.27557 | -0.19012 | 60.2921 | -62.0361 | 0.068665 | -62.3474 | 60.2188 | 62.2742 | 62.2559 | 0.061035 | -0.10895 | 0.053406 | 0.27237 | -0.15274 | -0.16129 | 0.032043 | 0.059509 | -62.4847 | 60.1456 | 60.1273 | 62.2696 | 62.4252 | 122.6349 | 62.3016 | 60.2692
3174.7031 | 0.045776 | 0.38879 | -0.77972 | -0.23926 | 0.12604 | -0.25421 | -0.19012 | 60.3058 | -62.1094 | 0.054932 | -62.3383 | 60.3058 | 62.2833 | 62.2284 | 0.045776 | -0.079041 | 0.063019 | 0.28412 | -0.14847 | -0.18051 | 0.013733 | 0.086975 | -62.5122 | 60.2325 | 60.1913 | 62.2467 | 62.4115 | 122.7951 | 62.2238 | 60.26
3176.375 | 0.061035 | 0.42191 | -0.784 | -0.22964 | 0.13245 | -0.28946 | -0.18158 | 60.2646 | -62.0728 | 0.041199 | -62.352 | 60.2325 | 62.2604 | 62.2421 | 0.045776 | -0.11002 | 0.05661 | 0.26703 | -0.14954 | -0.16556 | 0.018311 | 0.073242 | -62.4893 | 60.1364 | 60.141 | 62.2513 | 62.4252 | 122.6486 | 62.2787 | 60.2463
3178.0312 | 0.045776 | 0.40268 | -0.77972 | -0.2478 | 0.14099 | -0.26916 | -0.19226 | 60.3241 | -62.0407 | 0.16022 | -62.3154 | 60.228 | 62.2787 | 62.2467 | 0.061035 | -0.10895 | 0.066223 | 0.27985 | -0.16449 | -0.16556 | 0.10986 | 0.21515 | -62.4756 | 60.2097 | 60.1822 | 62.2513 | 62.4069 | 122.7448 | 62.2467 | 60.2554
3179.7031 | 0.045776 | 0.40375 | -0.77225 | -0.24887 | 0.12711 | -0.27451 | -0.18906 | 60.3378 | -62.0087 | 0.16479 | -62.2971 | 60.2051 | 62.2696 | 62.2421 | 0.061035 | -0.10895 | 0.055542 | 0.27664 | -0.16022 | -0.18585 | 0.14191 | 0.26093 | -62.439 | 60.1547 | 60.1685 | 62.233 | 62.3886 | 122.7264 | 62.2421 | 60.26
3181.3594 | 0.045776 | 0.41977 | -0.77652 | -0.21255 | 0.13351 | -0.24246 | -0.1709 | 60.2966 | -62.0911 | -0.009155 | -62.3566 | 60.2554 | 62.2971 | 62.2467 | 0.076294 | -0.088654 | 0.048065 | 0.27771 | -0.14099 | -0.1709 | -0.009155 | 0.032043 | -62.4756 | 60.1593 | 60.1227 | 62.2742 | 62.4115 | 122.6898 | 62.2879 | 60.2509
3183.0156 | 0.061035 | 0.40375 | -0.78186 | -0.24353 | 0.14526 | -0.26596 | -0.16876 | 60.2737 | -62.1231 | 0.068665 | -62.3657 | 60.2737 | 62.2833 | 62.2559 | 0.061035 | -0.083313 | 0.059814 | 0.28625 | -0.16129 | -0.18051 | 0.045776 | 0.1236 | -62.5259 | 60.2234 | 60.2051 | 62.2513 | 62.3932 | 122.7264 | 62.233 | 60.2646
3184.6875 | 0.030518 | 0.40482 | -0.77759 | -0.24353 | 0.13992 | -0.25101 | -0.18265 | 60.2646 | -62.1231 | 0.045776 | -62.3566 | 60.3104 | 62.2833 | 62.2467 | 0.045776 | -0.088654 | 0.069427 | 0.29053 | -0.16022 | -0.17517 | 0.022888 | 0.082397 | -62.5397 | 60.228 | 60.2234 | 62.265 | 62.439 | 122.7676 | 62.2421 | 60.2692
3186.3438 | 0.045776 | 0.43045 | -0.77438 | -0.2243 | 0.14313 | -0.26916 | -0.17838 | 60.3149 | -62.0224 | 0.050354 | -62.3245 | 60.1959 | 62.2696 | 62.2421 | 0.045776 | -0.10574 | 0.046997 | 0.28412 | -0.14847 | -0.16983 | 0.041199 | 0.07782 | -62.4802 | 60.1318 | 60.1318 | 62.2696 | 62.4161 | 122.6532 | 62.3016 | 60.2783
3188 | 0.045776 | 0.41122 | -0.77545 | -0.23605 | 0.13672 | -0.2713 | -0.18478 | 60.3241 | -62.0132 | 0.16479 | -62.3062 | 60.26 | 62.2604 | 62.2421 | 0.061035 | -0.10147 | 0.061951 | 0.28305 | -0.16556 | -0.17838 | 0.10986 | 0.21515 | -62.4664 | 60.2097 | 60.1593 | 62.2421 | 62.3932 | 122.7264 | 62.2375 | 60.2554
3189.7031 | 0.091553 | 0.40054 | -0.77866 | -0.21255 | 0.1442 | -0.22537 | -0.17624 | 60.3058 | -62.1231 | 0.004578 | -62.3474 | 60.2875 | 62.2925 | 62.265 | 0.030518 | -0.083313 | 0.045929 | 0.28732 | -0.11963 | -0.1741 | -0.050354 | -0.045776 | -62.5626 | 60.2188 | 60.1868 | 62.2696 | 62.4161 | 122.6624 | 62.2696 | 60.2921
3191.375 | 0.045776 | 0.40054 | -0.78293 | -0.22217 | 0.13351 | -0.25207 | -0.18372 | 60.26 | -62.1826 | -0.059509 | -62.3932 | 60.3012 | 62.3016 | 62.2696 | 0.061035 | -0.082245 | 0.059814 | 0.28946 | -0.1442 | -0.17303 | -0.082397 | -0.10071 | -62.5717 | 60.1959 | 60.2142 | 62.2604 | 62.4252 | 122.6349 | 62.265 | 60.2783
3193.0469 | 0.045776 | 0.39948 | -0.76477 | -0.21683 | 0.11856 | -0.2478 | -0.1709 | 60.3195 | -62.0819 | 0.041199 | -62.3428 | 60.2554 | 62.2696 | 62.2604 | 0.061035 | -0.088654 | 0.05127 | 0.28839 | -0.1442 | -0.16556 | -0.036621 | 0.018311 | -62.5351 | 60.1913 | 60.2097 | 62.2604 | 62.4252 | 122.6669 | 62.2696 | 60.2829
3194.7344 | 0.030518 | 0.4155 | -0.77972 | -0.2243 | 0.12604 | -0.26062 | -0.18158 | 60.3287 | -62.0407 | 0.041199 | -62.3108 | 60.2051 | 62.2604 | 62.2513 | 0.045776 | -0.093994 | 0.057678 | 0.27878 | -0.15274 | -0.16129 | 0 | 0.068665 | -62.4573 | 60.1273 | 60.141 | 62.2559 | 62.4207 | 122.6761 | 62.2742 | 60.26
3196.4062 | 0.045776 | 0.392 | -0.77118 | -0.24353 | 0.13672 | -0.26276 | -0.18051 | 60.2509 | -62.1414 | 0.064087 | -62.3611 | 60.2829 | 62.2879 | 62.2513 | 0.061035 | -0.089722 | 0.065155 | 0.28625 | -0.15808 | -0.16876 | 0.009155 | 0.086975 | -62.5122 | 60.2188 | 60.1959 | 62.2421 | 62.3978 | 122.7905 | 62.2238 | 60.2509
3198.0625 | 0.061035 | 0.44647 | -0.79254 | -0.2211 | 0.1207 | -0.29053 | -0.18478 | 60.2875 | -62.0316 | 0.11444 | -62.3199 | 60.228 | 62.2696 | 62.2375 | 0.045776 | -0.11108 | 0.046997 | 0.27451 | -0.15595 | -0.16022 | 0.10529 | 0.21973 | -62.4207 | 60.1639 | 60.141 | 62.2467 | 62.3978 | 122.7676 | 62.2284 | 60.2509
3199.7344 | 0.061035 | 0.40695 | -0.77331 | -0.22964 | 0.14099 | -0.24887 | -0.18906 | 60.2966 | -62.1048 | 0.068665 | -62.3383 | 60.3012 | 62.2879 | 62.2421 | 0.045776 | -0.088654 | 0.052338 | 0.27451 | -0.13992 | -0.17197 | 0.018311 | 0.09613 | -62.5031 | 60.2051 | 60.1822 | 62.2467 | 62.4161 | 122.7585 | 62.2375 | 60.2692
3201.4062 | 0.076294 | 0.41229 | -0.78827 | -0.2179 | 0.12924 | -0.25955 | -0.1741 | 60.2325 | -62.1552 | -0.059509 | -62.384 | 60.2921 | 62.2742 | 62.265 | 0.045776 | -0.081177 | 0.058746 | 0.28519 | -0.14847 | -0.16983 | -0.10986 | -0.09613 | -62.5717 | 60.1959 | 60.2188 | 62.2833 | 62.4298 | 122.6761 | 62.2742 | 60.2509
3203.0781 | 0.076294 | 0.41336 | -0.77866 | -0.25421 | 0.13458 | -0.29587 | -0.18478 | 60.3287 | -61.9766 | 0.16479 | -62.2833 | 60.2417 | 62.2559 | 62.2284 | 0.061035 | -0.11215 | 0.055542 | 0.27771 | -0.17517 | -0.17624 | 0.11902 | 0.2655 | -62.4161 | 60.1456 | 60.173 | 62.2421 | 62.3978 | 122.7493 | 62.2147 | 60.228
3204.75 | 0.045776 | 0.40054 | -0.77652 | -0.22644 | 0.13672 | -0.25635 | -0.17197 | 60.3287 | -62.0544 | 0.07782 | -62.3383 | 60.2646 | 62.2833 | 62.2421 | 0.061035 | -0.088654 | 0.064087 | 0.29266 | -0.1442 | -0.1709 | 0.027466 | 0.045776 | -62.5031 | 60.2234 | 60.1913 | 62.2696 | 62.4023 | 122.7356 | 62.233 | 60.2554
3206.4219 | 0.061035 | 0.39414 | -0.78613 | -0.2478 | 0.13458 | -0.27985 | -0.17731 | 60.2417 | -62.1094 | 0.059509 | -62.3657 | 60.3104 | 62.2787 | 62.2421 | 0.061035 | -0.095062 | 0.070496 | 0.27237 | -0.16342 | -0.1709 | 0.027466 | 0.10986 | -62.5305 | 60.2554 | 60.228 | 62.265 | 62.4161 | 122.7402 | 62.2238 | 60.2646
3208.125 | 0.045776 | 0.41122 | -0.78827 | -0.23285 | 0.14313 | -0.26382 | -0.18585 | 60.2463 | -62.114 | 0.054932 | -62.3703 | 60.2921 | 62.2879 | 62.2742 | 0.045776 | -0.087585 | 0.065155 | 0.27664 | -0.15488 | -0.16769 | 0.018311 | 0.073242 | -62.5351 | 60.2142 | 60.2051 | 62.2604 | 62.4252 | 122.7631 | 62.2147 | 60.26
3209.7812 | 0.045776 | 0.39627 | -0.77331 | -0.2211 | 0.13031 | -0.24674 | -0.1709 | 60.2463 | -62.1597 | -0.068665 | -62.3657 | 60.2829 | 62.3062 | 62.2604 | 0.061035 | -0.09079 | 0.060883 | 0.29587 | -0.13992 | -0.1709 | -0.082397 | -0.082397 | -62.5626 | 60.2097 | 60.1913 | 62.2833 | 62.4344 | 122.6669 | 62.2879 | 60.2554
3211.4375 | 0.045776 | 0.40054 | -0.77866 | -0.25207 | 0.13672 | -0.26703 | -0.17838 | 60.2463 | -62.1323 | 0.068665 | -62.3657 | 60.2875 | 62.2879 | 62.2467 | 0.045776 | -0.10147 | 0.065155 | 0.28198 | -0.16876 | -0.1709 | 0.032043 | 0.09613 | -62.5259 | 60.2188 | 60.2325 | 62.2604 | 62.3978 | 122.7264 | 62.2238 | 60.2737
3213.0938 | 0.045776 | 0.41122 | -0.77759 | -0.21255 | 0.12924 | -0.27344 | -0.17731 | 60.3058 | -62.0407 | 0.041199 | -62.3199 | 60.228 | 62.2787 | 62.2421 | 0.045776 | -0.099335 | 0.058746 | 0.2713 | -0.14954 | -0.16769 | 0.027466 | 0.054932 | -62.4527 | 60.1135 | 60.1318 | 62.2559 | 62.3886 | 122.6532 | 62.3016 | 60.2509
3214.7656 | 0.061035 | 0.40054 | -0.76904 | -0.24139 | 0.12924 | -0.25955 | -0.17838 | 60.2646 | -62.1277 | 0.041199 | -62.3337 | 60.2921 | 62.2787 | 62.2787 | 0.076294 | -0.084381 | 0.053406 | 0.28412 | -0.14633 | -0.18692 | 0.018311 | 0.09613 | -62.5168 | 60.2371 | 60.2325 | 62.2375 | 62.4252 | 122.7768 | 62.2192 | 60.2509
3216.4375 | 0.061035 | 0.41336 | -0.78186 | -0.22964 | 0.14313 | -0.26276 | -0.16556 | 60.2875 | -62.0636 | 0.027466 | -62.3062 | 60.228 | 62.2879 | 62.2421 | 0.045776 | -0.11322 | 0.049133 | 0.27344 | -0.14206 | -0.16983 | 0 | 0.032043 | -62.4619 | 60.1227 | 60.1227 | 62.233 | 62.4161 | 122.6715 | 62.2559 | 60.26
3218.125 | 0.061035 | 0.40375 | -0.77545 | -0.22537 | 0.13779 | -0.24353 | -0.18585 | 60.2463 | -62.1826 | -0.059509 | -62.3886 | 60.2875 | 62.2787 | 62.265 | 0.076294 | -0.088654 | 0.064087 | 0.28839 | -0.14954 | -0.17303 | -0.091553 | -0.09613 | -62.5626 | 60.2051 | 60.2234 | 62.2604 | 62.4344 | 122.6395 | 62.2696 | 60.26
3219.7812 | 0.030518 | 0.43259 | -0.7872 | -0.22537 | 0.11963 | -0.29373 | -0.18692 | 60.2554 | -62.0544 | 0.045776 | -62.3749 | 60.2142 | 62.2696 | 62.2192 | 0.076294 | -0.11429 | 0.054474 | 0.28198 | -0.15488 | -0.16556 | 0.027466 | 0.073242 | -62.4802 | 60.141 | 60.1181 | 62.2604 | 62.439 | 122.612 | 62.2787 | 60.2371
3221.4531 | 0.045776 | 0.41122 | -0.78186 | -0.25314 | 0.13672 | -0.27557 | -0.18158 | 60.3241 | -62.0087 | 0.19226 | -62.3062 | 60.2188 | 62.2421 | 62.2421 | 0.061035 | -0.10147 | 0.054474 | 0.27664 | -0.16235 | -0.18051 | 0.11444 | 0.24261 | -62.4115 | 60.1364 | 60.1456 | 62.2467 | 62.3795 | 122.7127 | 62.2238 | 60.2463
3223.125 | 0.045776 | 0.41229 | -0.78827 | -0.21042 | 0.12711 | -0.24887 | -0.18265 | 60.3104 | -62.0728 | 0.068665 | -62.3383 | 60.2783 | 62.2696 | 62.2513 | 0.045776 | -0.085449 | 0.050201 | 0.28732 | -0.13351 | -0.18372 | 0.036621 | 0.07782 | -62.5031 | 60.2142 | 60.2051 | 62.2238 | 62.3932 | 122.7493 | 62.2284 | 60.2554
3224.7969 | 0.045776 | 0.41229 | -0.78293 | -0.23498 | 0.11643 | -0.26062 | -0.18158 | 60.3104 | -62.0316 | 0.036621 | -62.3108 | 60.1959 | 62.2879 | 62.2284 | 0.045776 | -0.10681 | 0.055542 | 0.27771 | -0.13886 | -0.16983 | 0.004578 | 0.022888 | -62.4619 | 60.1318 | 60.1227 | 62.265 | 62.3978 | 122.6624 | 62.2787 | 60.2325
3226.5156 | 0.045776 | 0.40268 | -0.77118 | -0.24353 | 0.13565 | -0.27664 | -0.19012 | 60.3058 | -62.0361 | 0.059509 | -62.3337 | 60.1959 | 62.2559 | 62.233 | 0.015259 | -0.10788 | 0.064087 | 0.27557 | -0.15381 | -0.1741 | 0.036621 | 0.073242 | -62.4619 | 60.1593 | 60.1364 | 62.2375 | 62.4344 | 122.612 | 62.2833 | 60.2646
3228.1875 | 0.076294 | 0.41443 | -0.77759 | -0.22644 | 0.13458 | -0.25848 | -0.17624 | 60.2783 | -62.1185 | -0.022888 | -62.3657 | 60.2692 | 62.2742 | 62.2421 | 0.091553 | -0.085449 | 0.064087 | 0.28732 | -0.14313 | -0.17944 | -0.041199 | -0.027466 | -62.4847 | 60.1593 | 60.1639 | 62.2513 | 62.4023 | 122.6807 | 62.2879 | 60.2463
3229.8438 | 0.045776 | 0.40909 | -0.77438 | -0.23392 | 0.13351 | -0.28198 | -0.18478 | 60.2921 | -62.0544 | 0.045776 | -62.3611 | 60.1868 | 62.2971 | 62.2375 | 0.045776 | -0.10574 | 0.055542 | 0.28198 | -0.16983 | -0.1709 | 0.027466 | 0.07782 | -62.4847 | 60.1044 | 60.1364 | 62.2421 | 62.3978 | 122.6074 | 62.2971 | 60.2509
3231.5781 | 0.061035 | 0.41336 | -0.78293 | -0.22324 | 0.13351 | -0.25528 | -0.18051 | 60.3195 | -62.0499 | 0.041199 | -62.3154 | 60.2188 | 62.2604 | 62.2147 | 0.076294 | -0.093994 | 0.054474 | 0.27985 | -0.14206 | -0.17944 | 0.013733 | 0.036621 | -62.4481 | 60.1456 | 60.1181 | 62.2421 | 62.4115 | 122.6715 | 62.2742 | 60.2417
3233.3906 | 0.045776 | 0.41016 | -0.784 | -0.22964 | 0.13458 | -0.25848 | -0.17517 | 60.2783 | -62.0956 | 0.054932 | -62.3108 | 60.2966 | 62.2559 | 62.2604 | 0.030518 | -0.095062 | 0.057678 | 0.29587 | -0.13886 | -0.18051 | 0.032043 | 0.082397 | -62.5214 | 60.1913 | 60.1868 | 62.2604 | 62.4115 | 122.7814 | 62.2238 | 60.2554
3235.1719 | 0.061035 | 0.45181 | -0.79575 | -0.22537 | 0.14847 | -0.2948 | -0.18799 | 60.2371 | -62.0865 | 0.041199 | -62.3428 | 60.2234 | 62.2604 | 62.2559 | 0.030518 | -0.11963 | 0.046997 | 0.26916 | -0.15595 | -0.15808 | 0.013733 | 0.09613 | -62.4802 | 60.1547 | 60.1501 | 62.2513 | 62.4252 | 122.6532 | 62.265 | 60.2463
3237.0312 | 0.045776 | 0.42084 | -0.78827 | -0.23819 | 0.13458 | -0.28625 | -0.18051 | 60.2371 | -62.0682 | 0.064087 | -62.3474 | 60.2325 | 62.2696 | 62.2284 | 0.061035 | -0.1207 | 0.058746 | 0.27664 | -0.16983 | -0.16769 | 0.068665 | 0.13275 | -62.4619 | 60.173 | 60.1227 | 62.233 | 62.3749 | 122.7219 | 62.2559 | 60.2371
3239.1406 | 0.061035 | 0.40695 | -0.77438 | -0.2179 | 0.13779 | -0.23819 | -0.17838 | 60.2829 | -62.1231 | -0.009155 | -62.3795 | 60.2783 | 62.2833 | 62.2604 | 0.061035 | -0.076904 | 0.05127 | 0.27771 | -0.13458 | -0.18372 | -0.07782 | -0.064087 | -62.5809 | 60.2097 | 60.1868 | 62.2604 | 62.4298 | 122.6303 | 62.265 | 60.2692
3241.4531 | 0.045776 | 0.41657 | -0.77545 | -0.24353 | 0.13992 | -0.28839 | -0.18692 | 60.2783 | -62.027 | 0.10986 | -62.3108 | 60.2234 | 62.2604 | 62.2284 | 0.061035 | -0.11856 | 0.05661 | 0.27771 | -0.16663 | -0.16022 | 0.12817 | 0.19226 | -62.4161 | 60.141 | 60.1318 | 62.2284 | 62.4069 | 122.7448 | 62.2284 | 60.2188
3243.2188 | 0.045776 | 0.43045 | -0.77225 | -0.22537 | 0.13565 | -0.24994 | -0.18265 | 60.3149 | -62.0224 | 0.045776 | -62.3154 | 60.1959 | 62.2742 | 62.2604 | 0.030518 | -0.10147 | 0.05127 | 0.28946 | -0.14633 | -0.18158 | 0.045776 | 0.073242 | -62.4527 | 60.1273 | 60.0998 | 62.2787 | 62.4069 | 122.6212 | 62.2925 | 60.2371
3244.9062 | 0.061035 | 0.40268 | -0.78507 | -0.24994 | 0.13458 | -0.27023 | -0.19653 | 60.3104 | -61.9995 | 0.17395 | -62.2879 | 60.228 | 62.2513 | 62.2284 | 0.030518 | -0.10468 | 0.061951 | 0.27557 | -0.15808 | -0.17517 | 0.11444 | 0.24261 | -62.4344 | 60.1456 | 60.1318 | 62.2421 | 62.3795 | 122.7173 | 62.2284 | 60.2417
3246.5938 | 0.045776 | 0.38025 | -0.76263 | -0.24994 | 0.13992 | -0.24353 | -0.18158 | 60.3149 | -62.059 | 0.082397 | -62.3199 | 60.3012 | 62.2559 | 62.2467 | 0.045776 | -0.083313 | 0.069427 | 0.29053 | -0.14954 | -0.18158 | 0.054932 | 0.091553 | -62.4847 | 60.2051 | 60.173 | 62.2284 | 62.4161 | 122.7539 | 62.2238 | 60.228
3248.2969 | 0.030518 | 0.37811 | -0.76797 | -0.23819 | 0.13351 | -0.24139 | -0.17731 | 60.2966 | -62.0865 | 0.064087 | -62.3245 | 60.2692 | 62.2696 | 62.2467 | 0.061035 | -0.089722 | 0.080109 | 0.29373 | -0.1474 | -0.17838 | 0.041199 | 0.073242 | -62.4802 | 60.1959 | 60.1868 | 62.2147 | 62.384 | 122.7264 | 62.2421 | 60.2417
3250.7969 | 0.045776 | 0.38773 | -0.77225 | -0.23712 | 0.12497 | -0.26062 | -0.17731 | 60.2966 | -62.0132 | 0.041199 | -62.2971 | 60.2188 | 62.2833 | 62.233 | 0.061035 | -0.10468 | 0.065155 | 0.29159 | -0.1506 | -0.17303 | 0.027466 | 0.059509 | -62.4527 | 60.1273 | 60.1044 | 62.2787 | 62.4161 | 122.6578 | 62.2925 | 60.2509
3253.125 | 0.045776 | 0.40695 | -0.77972 | -0.24246 | 0.14313 | -0.27344 | -0.1741 | 60.228 | -62.0819 | 0.086975 | -62.352 | 60.2554 | 62.2513 | 62.2513 | 0.045776 | -0.097198 | 0.05127 | 0.28412 | -0.15808 | -0.16983 | 0.036621 | 0.12817 | -62.5168 | 60.1959 | 60.228 | 62.2559 | 62.4023 | 122.7173 | 62.233 | 60.2463
3254.8125 | 0.045776 | 0.39093 | -0.77011 | -0.24033 | 0.11536 | -0.27664 | -0.19546 | 60.2737 | -62.0453 | 0.12817 | -62.3245 | 60.2371 | 62.2742 | 62.2101 | 0.061035 | -0.10681 | 0.065155 | 0.27878 | -0.16663 | -0.16983 | 0.068665 | 0.15564 | -62.4802 | 60.1959 | 60.1913 | 62.265 | 62.3886 | 122.6807 | 62.2192 | 60.2371
3256.4844 | 0.030518 | 0.40695 | -0.77972 | -0.21362 | 0.13031 | -0.25742 | -0.17838 | 60.2875 | -62.0178 | 0.059509 | -62.3291 | 60.1913 | 62.2742 | 62.2467 | 0.030518 | -0.10895 | 0.050201 | 0.27451 | -0.14633 | -0.1709 | 0.036621 | 0.091553 | -62.4298 | 60.141 | 60.0998 | 62.2238 | 62.4023 | 122.6074 | 62.265 | 60.2646
3258.1562 | 0.061035 | 0.41122 | -0.79254 | -0.24567 | 0.13138 | -0.28839 | -0.19012 | 60.2417 | -62.1048 | 0.07782 | -62.3657 | 60.2783 | 62.3016 | 62.2559 | 0.045776 | -0.087585 | 0.065155 | 0.28625 | -0.15167 | -0.16556 | 0.045776 | 0.1236 | -62.4985 | 60.2188 | 60.1959 | 62.2604 | 62.4115 | 122.6852 | 62.2375 | 60.2509
3259.8281 | 0.076294 | 0.39948 | -0.78507 | -0.21469 | 0.13351 | -0.24353 | -0.18051 | 60.2371 | -62.1185 | -0.036621 | -62.3611 | 60.2921 | 62.2833 | 62.2513 | 0.045776 | -0.091858 | 0.052338 | 0.28412 | -0.13245 | -0.17624 | -0.086975 | -0.073242 | -62.5626 | 60.2142 | 60.1868 | 62.2604 | 62.4344 | 122.6212 | 62.2559 | 60.2829
3261.5 | 0.045776 | 0.4155 | -0.77331 | -0.2478 | 0.13031 | -0.28946 | -0.18692 | 60.2509 | -62.0316 | 0.091553 | -62.3108 | 60.2371 | 62.2604 | 62.2375 | 0.045776 | -0.11108 | 0.063019 | 0.28412 | -0.16663 | -0.1741 | 0.10986 | 0.20599 | -62.4069 | 60.1501 | 60.1364 | 62.233 | 62.3886 | 122.7356 | 62.2009 | 60.2371
3263.1719 | 0.030518 | 0.40054 | -0.77545 | -0.22217 | 0.12924 | -0.24353 | -0.17838 | 60.26 | -62.1185 | -0.009155 | -62.3611 | 60.2646 | 62.2833 | 62.2513 | 0.045776 | -0.082245 | 0.05661 | 0.29694 | -0.12924 | -0.18158 | -0.07782 | -0.064087 | -62.5534 | 60.2097 | 60.1868 | 62.2833 | 62.4161 | 122.5983 | 62.2696 | 60.2829
3264.8281 | 0.045776 | 0.40909 | -0.78507 | -0.25101 | 0.13031 | -0.28091 | -0.17624 | 60.2875 | -61.9675 | 0.16022 | -62.2879 | 60.2097 | 62.2604 | 62.2147 | 0.061035 | -0.11002 | 0.055542 | 0.28305 | -0.16342 | -0.16449 | 0.14191 | 0.27008 | -62.4069 | 60.1318 | 60.1273 | 62.2559 | 62.3795 | 122.699 | 62.2238 | 60.2142
3266.5156 | 0.076294 | 0.41763 | -0.77011 | -0.2211 | 0.13458 | -0.25635 | -0.17944 | 60.26 | -62.1231 | -0.064087 | -62.3795 | 60.2646 | 62.2833 | 62.2696 | 0.061035 | -0.077972 | 0.053406 | 0.28732 | -0.13351 | -0.17197 | -0.050354 | -0.068665 | -62.5305 | 60.1913 | 60.173 | 62.2559 | 62.4207 | 122.6532 | 62.2604 | 60.2417
3268.1875 | 0.015259 | 0.40802 | -0.78613 | -0.2446 | 0.13886 | -0.26489 | -0.18158 | 60.2463 | -62.1094 | 0.054932 | -62.3566 | 60.2509 | 62.2742 | 62.2467 | 0.045776 | -0.099335 | 0.063019 | 0.28305 | -0.15915 | -0.17303 | 0.022888 | 0.10986 | -62.5076 | 60.2188 | 60.228 | 62.2559 | 62.4069 | 122.699 | 62.1918 | 60.2554
3269.8906 | 0.061035 | 0.41229 | -0.78079 | -0.24994 | 0.12283 | -0.26382 | -0.18799 | 60.2234 | -62.1002 | 0.059509 | -62.352 | 60.2875 | 62.2787 | 62.233 | 0.076294 | -0.10468 | 0.060883 | 0.27985 | -0.15915 | -0.1709 | 0.041199 | 0.10529 | -62.5031 | 60.228 | 60.228 | 62.2604 | 62.4252 | 122.699 | 62.2147 | 60.2692
3271.5625 | 0.045776 | 0.42404 | -0.78827 | -0.2179 | 0.12924 | -0.28732 | -0.19119 | 60.2188 | -62.0773 | 0.041199 | -62.3337 | 60.1959 | 62.2742 | 62.2375 | 0.045776 | -0.10788 | 0.061951 | 0.2713 | -0.16235 | -0.15701 | 0.032043 | 0.1236 | -62.4619 | 60.1364 | 60.1318 | 62.2421 | 62.4252 | 122.6715 | 62.2467 | 60.228
3273.2344 | 0.045776 | 0.40054 | -0.76691 | -0.23712 | 0.13565 | -0.2446 | -0.1741 | 60.3195 | -62.0499 | 0.07782 | -62.3245 | 60.2783 | 62.2787 | 62.2101 | 0.061035 | -0.087585 | 0.068359 | 0.28839 | -0.12604 | -0.18478 | 0.032043 | 0.054932 | -62.4847 | 60.1776 | 60.1822 | 62.2284 | 62.4115 | 122.6898 | 62.2238 | 60.2783
3274.9062 | 0.076294 | 0.40161 | -0.76904 | -0.22644 | 0.14099 | -0.24353 | -0.17197 | 60.2921 | -62.0544 | 0.059509 | -62.3291 | 60.2692 | 62.2879 | 62.233 | 0.061035 | -0.080109 | 0.059814 | 0.28412 | -0.1442 | -0.17838 | 0.027466 | 0.086975 | -62.4802 | 60.2005 | 60.1868 | 62.2421 | 62.3932 | 122.731 | 62.1918 | 60.2325
3276.5781 | 0.045776 | 0.42084 | -0.78186 | -0.22964 | 0.13458 | -0.30441 | -0.18478 | 60.2371 | -62.0499 | 0.082397 | -62.3108 | 60.2142 | 62.2467 | 62.2604 | 0.045776 | -0.11108 | 0.058746 | 0.27451 | -0.15701 | -0.16449 | 0.07782 | 0.18768 | -62.4207 | 60.1456 | 60.1318 | 62.2192 | 62.4069 | 122.7173 | 62.2101 | 60.2142
3278.25 | 0.045776 | 0.4155 | -0.78293 | -0.22858 | 0.13458 | -0.25635 | -0.17303 | 60.2463 | -62.1231 | -0.050354 | -62.3886 | 60.2692 | 62.2696 | 62.2604 | 0.061035 | -0.083313 | 0.048065 | 0.28946 | -0.1442 | -0.16449 | -0.068665 | -0.082397 | -62.5122 | 60.1776 | 60.1547 | 62.2604 | 62.4115 | 122.6532 | 62.2879 | 60.2325
3279.9219 | 0.061035 | 0.41016 | -0.77866 | -0.2478 | 0.11643 | -0.29159 | -0.17624 | 60.2097 | -62.0636 | 0.059509 | -62.3245 | 60.2188 | 62.2696 | 62.2421 | 0.045776 | -0.11108 | 0.057678 | 0.28198 | -0.16983 | -0.17303 | 0.059509 | 0.13733 | -62.4481 | 60.1273 | 60.1501 | 62.2421 | 62.384 | 122.7036 | 62.2284 | 60.2371
3281.5938 | 0.045776 | 0.41122 | -0.77759 | -0.21896 | 0.1442 | -0.24246 | -0.17944 | 60.2921 | -62.0911 | 0.064087 | -62.3291 | 60.2875 | 62.265 | 62.2513 | 0.076294 | -0.086517 | 0.049133 | 0.29373 | -0.13779 | -0.18906 | 0.022888 | 0.091553 | -62.4802 | 60.2005 | 60.1868 | 62.2604 | 62.4069 | 122.7402 | 62.2284 | 60.2234
3283.2656 | 0.061035 | 0.41443 | -0.77759 | -0.25314 | 0.12711 | -0.27344 | -0.18692 | 60.2371 | -62.1048 | 0.07782 | -62.3566 | 60.2692 | 62.2787 | 62.2284 | 0.045776 | -0.09613 | 0.064087 | 0.29053 | -0.15701 | -0.16769 | 0.041199 | 0.10071 | -62.5122 | 60.2188 | 60.2142 | 62.2375 | 62.4069 | 122.7081 | 62.2055 | 60.26
3284.9219 | 0.061035 | 0.42404 | -0.784 | -0.2243 | 0.13672 | -0.26489 | -0.17517 | 60.2921 | -62.0132 | 0.050354 | -62.3062 | 60.1913 | 62.2696 | 62.2284 | 0.030518 | -0.10254 | 0.052338 | 0.27664 | -0.14099 | -0.16449 | 0.022888 | 0.068665 | -62.4252 | 60.1227 | 60.1044 | 62.2513 | 62.4115 | 122.6257 | 62.2879 | 60.2325
3286.5938 | 0.061035 | 0.41336 | -0.79681 | -0.23498 | 0.13351 | -0.28091 | -0.19333 | 60.3012 | -61.9904 | 0.17395 | -62.2742 | 60.2097 | 62.2513 | 62.2055 | 0.045776 | -0.10574 | 0.05661 | 0.27237 | -0.15808 | -0.17517 | 0.1236 | 0.2655 | -62.4115 | 60.1364 | 60.1547 | 62.2284 | 62.3703 | 122.6898 | 62.2009 | 60.2509
3288.2656 | 0.076294 | 0.41336 | -0.77545 | -0.21362 | 0.12176 | -0.25421 | -0.18158 | 60.2463 | -62.1323 | -0.054932 | -62.3611 | 60.2646 | 62.2559 | 62.2421 | 0.045776 | -0.082245 | 0.059814 | 0.29587 | -0.14847 | -0.17303 | -0.054932 | -0.064087 | -62.5214 | 60.2005 | 60.173 | 62.2604 | 62.4252 | 122.6624 | 62.2421 | 60.2371
3289.9375 | 0.061035 | 0.40695 | -0.75943 | -0.23712 | 0.12817 | -0.24139 | -0.18478 | 60.2371 | -62.1414 | -0.022888 | -62.352 | 60.2966 | 62.2559 | 62.2467 | 0.030518 | -0.081177 | 0.059814 | 0.29587 | -0.14633 | -0.16983 | -0.07782 | -0.073242 | -62.5671 | 60.2234 | 60.2051 | 62.2787 | 62.4344 | 122.5937 | 62.2513 | 60.26
3291.6094 | 0.061035 | 0.42191 | -0.78293 | -0.23178 | 0.13138 | -0.28732 | -0.18372 | 60.2142 | -62.0682 | 0.064087 | -62.3337 | 60.2417 | 62.2559 | 62.2375 | 0.061035 | -0.1207 | 0.054474 | 0.27664 | -0.16769 | -0.16235 | 0.045776 | 0.14648 | -62.4435 | 60.1364 | 60.1456 | 62.265 | 62.3703 | 122.7036 | 62.2375 | 60.2051
3293.3125 | 0.045776 | 0.41977 | -0.78186 | -0.23392 | 0.13245 | -0.25848 | -0.17731 | 60.3058 | -62.027 | 0.032043 | -62.2879 | 60.228 | 62.2238 | 62.2238 | 0.076294 | -0.099335 | 0.046997 | 0.28305 | -0.13992 | -0.17517 | 0.018311 | 0.045776 | -62.4481 | 60.1135 | 60.1181 | 62.2513 | 62.3932 | 122.644 | 62.2559 | 60.2325
3294.9844 | 0.045776 | 0.3952 | -0.76691 | -0.25421 | 0.13779 | -0.25101 | -0.18372 | 60.2417 | -62.1094 | 0.041199 | -62.3245 | 60.2829 | 62.2787 | 62.2421 | 0.045776 | -0.082245 | 0.065155 | 0.28198 | -0.15381 | -0.18051 | 0.022888 | 0.086975 | -62.4893 | 60.2188 | 60.2234 | 62.2513 | 62.4023 | 122.7631 | 62.1918 | 60.228
3296.6406 | 0.045776 | 0.42725 | -0.79147 | -0.22217 | 0.1239 | -0.28946 | -0.18799 | 60.2325 | -62.0636 | 0.041199 | -62.3291 | 60.2188 | 62.2742 | 62.2009 | 0.061035 | -0.10895 | 0.048065 | 0.27985 | -0.16342 | -0.16983 | 0.018311 | 0.10071 | -62.4573 | 60.1364 | 60.1273 | 62.2604 | 62.4115 | 122.6395 | 62.2421 | 60.2234
3298.3281 | 0.045776 | 0.42084 | -0.78507 | -0.24246 | 0.13245 | -0.26169 | -0.18478 | 60.2371 | -62.1048 | 0.068665 | -62.3428 | 60.2829 | 62.233 | 62.2284 | 0.076294 | -0.083313 | 0.058746 | 0.27664 | -0.15381 | -0.17517 | 0.027466 | 0.09613 | -62.5214 | 60.2188 | 60.1959 | 62.2604 | 62.384 | 122.7173 | 62.233 | 60.2509
3300.0156 | 0.076294 | 0.39948 | -0.78079 | -0.22217 | 0.1239 | -0.24674 | -0.17517 | 60.2188 | -62.1506 | -0.045776 | -62.352 | 60.2737 | 62.2696 | 62.2467 | 0.061035 | -0.082245 | 0.05661 | 0.28305 | -0.13245 | -0.17517 | -0.086975 | -0.10529 | -62.558 | 60.2005 | 60.1685 | 62.2513 | 62.4161 | 122.6257 | 62.2513 | 60.2417
3301.6875 | 0.030518 | 0.41016 | -0.77866 | -0.23926 | 0.15274 | -0.26916 | -0.18692 | 60.2371 | -62.0956 | 0.059509 | -62.352 | 60.2921 | 62.2513 | 62.2467 | 0.061035 | -0.092926 | 0.052338 | 0.28839 | -0.16022 | -0.1741 | 0.018311 | 0.09613 | -62.5122 | 60.2097 | 60.228 | 62.2421 | 62.4115 | 122.7173 | 62.2055 | 60.2646
3303.4062 | 0.045776 | 0.42084 | -0.78079 | -0.22644 | 0.12604 | -0.27985 | -0.18692 | 60.2829 | -62.0132 | 0.045776 | -62.3016 | 60.1822 | 62.265 | 62.233 | 0.030518 | -0.10254 | 0.055542 | 0.27985 | -0.15808 | -0.16235 | 0.041199 | 0.073242 | -62.4298 | 60.1227 | 60.1044 | 62.2604 | 62.4023 | 122.5983 | 62.2696 | 60.2463
3305.1094 | 0.045776 | 0.4155 | -0.78186 | -0.2446 | 0.13779 | -0.2681 | -0.18478 | 60.2234 | -62.0865 | 0.050354 | -62.3383 | 60.2737 | 62.2513 | 62.2284 | 0.061035 | -0.085449 | 0.055542 | 0.29053 | -0.15595 | -0.16129 | 0.018311 | 0.09613 | -62.5122 | 60.2097 | 60.2097 | 62.2742 | 62.4069 | 122.7219 | 62.2147 | 60.2509
3306.7812 | 0.061035 | 0.40054 | -0.78079 | -0.24567 | 0.12604 | -0.26916 | -0.18585 | 60.2325 | -62.0911 | 0.059509 | -62.3383 | 60.2829 | 62.265 | 62.2238 | 0.030518 | -0.097198 | 0.069427 | 0.28519 | -0.16022 | -0.16769 | 0.018311 | 0.091553 | -62.5168 | 60.2097 | 60.1868 | 62.2513 | 62.4115 | 122.7127 | 62.1826 | 60.2509
3308.4844 | 0.030518 | 0.41657 | -0.77866 | -0.24674 | 0.13779 | -0.28412 | -0.18051 | 60.2783 | -61.9904 | 0.13733 | -62.2925 | 60.2142 | 62.2467 | 62.1964 | 0.045776 | -0.11749 | 0.063019 | 0.28412 | -0.16983 | -0.17944 | 0.14191 | 0.23804 | -62.3657 | 60.0906 | 60.1273 | 62.2192 | 62.384 | 122.7264 | 62.2009 | 60.2371
3310.2031 | 0.076294 | 0.42511 | -0.77545 | -0.24033 | 0.11749 | -0.2713 | -0.1944 | 60.2646 | -62.0636 | 0.045776 | -62.3337 | 60.2097 | 62.265 | 62.2009 | 0.061035 | -0.11215 | 0.050201 | 0.27771 | -0.15808 | -0.16556 | 0.041199 | 0.07782 | -62.471 | 60.1547 | 60.1135 | 62.2375 | 62.3932 | 122.5937 | 62.2513 | 60.2463
3311.8594 | 0.076294 | 0.41763 | -0.77866 | -0.24674 | 0.13565 | -0.26596 | -0.19012 | 60.2783 | -62.0682 | 0.10529 | -62.3199 | 60.2692 | 62.2513 | 62.2696 | 0.061035 | -0.086517 | 0.064087 | 0.28305 | -0.15488 | -0.1741 | 0.073242 | 0.12817 | -62.4985 | 60.2371 | 60.1913 | 62.2421 | 62.3932 | 122.6852 | 62.2101 | 60.26
3313.5312 | 0.061035 | 0.40054 | -0.76904 | -0.22324 | 0.11536 | -0.24139 | -0.18372 | 60.2921 | -62.0956 | 0.009155 | -62.3428 | 60.2692 | 62.2559 | 62.2467 | 0.045776 | -0.091858 | 0.057678 | 0.28839 | -0.13458 | -0.17303 | -0.059509 | -0.041199 | -62.5488 | 60.1776 | 60.1868 | 62.233 | 62.4069 | 122.5983 | 62.2604 | 60.2463
3315.2031 | 0.061035 | 0.39948 | -0.77866 | -0.2446 | 0.1474 | -0.2713 | -0.17517 | 60.3058 | -62.0041 | 0.15564 | -62.2833 | 60.2463 | 62.233 | 62.2238 | 0.045776 | -0.10574 | 0.071564 | 0.29053 | -0.15808 | -0.17624 | 0.091553 | 0.20599 | -62.471 | 60.1959 | 60.173 | 62.233 | 62.3886 | 122.6807 | 62.233 | 60.228
3316.9062 | 0.045776 | 0.392 | -0.77759 | -0.23498 | 0.14099 | -0.23712 | -0.17197 | 60.3012 | -62.059 | 0.068665 | -62.3108 | 60.2829 | 62.2559 | 62.2238 | 0.045776 | -0.095062 | 0.053406 | 0.29266 | -0.13886 | -0.19226 | 0.041199 | 0.091553 | -62.4756 | 60.1822 | 60.1913 | 62.2513 | 62.3749 | 122.7219 | 62.2055 | 60.2463
3318.5781 | 0.045776 | 0.42938 | -0.784 | -0.22537 | 0.12817 | -0.29053 | -0.18478 | 60.2188 | -62.0361 | 0.073242 | -62.3199 | 60.2188 | 62.265 | 62.2147 | 0.061035 | -0.11322 | 0.064087 | 0.26703 | -0.15701 | -0.16235 | 0.068665 | 0.15564 | -62.4252 | 60.141 | 60.1318 | 62.2375 | 62.4023 | 122.7036 | 62.2467 | 60.2371
3320.2344 | 0.045776 | 0.3952 | -0.76584 | -0.22858 | 0.11963 | -0.24353 | -0.17517 | 60.2371 | -62.146 | -0.054932 | -62.3566 | 60.2921 | 62.2833 | 62.233 | 0.061035 | -0.084381 | 0.059814 | 0.29587 | -0.14099 | -0.1741 | -0.10071 | -0.10071 | -62.5671 | 60.1685 | 60.1822 | 62.2604 | 62.4023 | 122.6028 | 62.2513 | 60.2737
3321.8906 | 0.045776 | 0.42938 | -0.78934 | -0.22537 | 0.11322 | -0.28091 | -0.18372 | 60.2325 | -62.0499 | 0.041199 | -62.3428 | 60.2005 | 62.265 | 62.2238 | 0.045776 | -0.11856 | 0.059814 | 0.27771 | -0.16235 | -0.16876 | 0.027466 | 0.086975 | -62.4527 | 60.1456 | 60.1273 | 62.2513 | 62.4161 | 122.6212 | 62.2742 | 60.2051
3323.5625 | 0.030518 | 0.41016 | -0.77972 | -0.22858 | 0.14206 | -0.25528 | -0.17731 | 60.2829 | -62.0728 | 0.068665 | -62.2879 | 60.2737 | 62.265 | 62.2375 | 0.045776 | -0.080109 | 0.058746 | 0.29266 | -0.13031 | -0.1709 | 0.032043 | 0.091553 | -62.4802 | 60.173 | 60.1593 | 62.2467 | 62.3886 | 122.731 | 62.2055 | 60.2463
3325.2344 | 0.061035 | 0.40054 | -0.77118 | -0.2478 | 0.13138 | -0.2713 | -0.16769 | 60.2829 | -62.0178 | 0.064087 | -62.3016 | 60.1959 | 62.2879 | 62.233 | 0.061035 | -0.098267 | 0.059814 | 0.28305 | -0.15595 | -0.16342 | 0.050354 | 0.091553 | -62.4115 | 60.1227 | 60.1044 | 62.2559 | 62.4023 | 122.5891 | 62.265 | 60.2463
3326.9062 | 0.061035 | 0.41122 | -0.79361 | -0.23605 | 0.12711 | -0.2713 | -0.19119 | 60.2783 | -62.0499 | 0.11444 | -62.3108 | 60.2417 | 62.2513 | 62.233 | 0.045776 | -0.09613 | 0.055542 | 0.28519 | -0.16129 | -0.1741 | 0.059509 | 0.15564 | -62.5031 | 60.1959 | 60.1959 | 62.2421 | 62.4161 | 122.6761 | 62.2101 | 60.2509
3328.5781 | 0.061035 | 0.40054 | -0.77438 | -0.21362 | 0.13031 | -0.25955 | -0.17303 | 60.2325 | -62.1552 | -0.059509 | -62.3611 | 60.2783 | 62.2559 | 62.2101 | 0.045776 | -0.092926 | 0.052338 | 0.29587 | -0.14526 | -0.17838 | -0.082397 | -0.086975 | -62.558 | 60.2188 | 60.173 | 62.2604 | 62.4252 | 122.6212 | 62.2787 | 60.2692
3330.2656 | 0.061035 | 0.39841 | -0.76691 | -0.22217 | 0.13138 | -0.2478 | -0.1741 | 60.2646 | -62.0956 | 0.004578 | -62.3474 | 60.2371 | 62.2742 | 62.2238 | 0.045776 | -0.072632 | 0.068359 | 0.29694 | -0.14099 | -0.16983 | -0.068665 | -0.041199 | -62.5397 | 60.1959 | 60.2005 | 62.2375 | 62.3978 | 122.5845 | 62.265 | 60.2875
3331.9219 | 0.061035 | 0.42831 | -0.78079 | -0.22858 | 0.13458 | -0.28519 | -0.18906 | 60.2371 | -62.0316 | 0.050354 | -62.3154 | 60.2097 | 62.2421 | 62.2055 | 0.061035 | -0.11002 | 0.054474 | 0.27878 | -0.13992 | -0.15915 | 0.022888 | 0.073242 | -62.4481 | 60.1135 | 60.1044 | 62.2467 | 62.3703 | 122.5891 | 62.2604 | 60.2554
3333.5938 | 0.045776 | 0.43152 | -0.78613 | -0.23392 | 0.12176 | -0.2948 | -0.18692 | 60.2188 | -62.0682 | 0.041199 | -62.3428 | 60.2097 | 62.265 | 62.2375 | 0.045776 | -0.097198 | 0.049133 | 0.27344 | -0.15701 | -0.17517 | 0.004578 | 0.07782 | -62.471 | 60.1364 | 60.1227 | 62.2559 | 62.3932 | 122.6212 | 62.2421 | 60.2325
3335.25 | 0.076294 | 0.38559 | -0.76904 | -0.24246 | 0.13031 | -0.23498 | -0.17624 | 60.3287 | -62.059 | 0.073242 | -62.3062 | 60.2783 | 62.265 | 62.2238 | 0.061035 | -0.080109 | 0.063019 | 0.28412 | -0.14633 | -0.17731 | 0.032043 | 0.050354 | -62.4847 | 60.2005 | 60.1639 | 62.233 | 62.3886 | 122.6669 | 62.2101 | 60.2463
3336.9219 | 0.045776 | 0.39627 | -0.76477 | -0.23285 | 0.13138 | -0.25101 | -0.17197 | 60.2966 | -62.0453 | 0.07782 | -62.3062 | 60.2554 | 62.2375 | 62.2147 | 0.076294 | -0.097198 | 0.058746 | 0.29266 | -0.14633 | -0.17197 | 0.022888 | 0.050354 | -62.4939 | 60.1822 | 60.1913 | 62.2604 | 62.3795 | 122.6715 | 62.233 | 60.2417
3338.5781 | 0.045776 | 0.41229 | -0.78507 | -0.24246 | 0.12283 | -0.298 | -0.18265 | 60.2921 | -61.9354 | 0.16022 | -62.2787 | 60.1868 | 62.2192 | 62.2238 | 0.030518 | -0.12604 | 0.058746 | 0.28091 | -0.16983 | -0.17624 | 0.14648 | 0.26093 | -62.3749 | 60.1089 | 60.1364 | 62.2421 | 62.3749 | 122.7036 | 62.2101 | 60.2097
3340.25 | 0.061035 | 0.41336 | -0.77118 | -0.22644 | 0.12283 | -0.25955 | -0.17731 | 60.2371 | -62.0865 | -0.041199 | -62.352 | 60.2417 | 62.2742 | 62.2238 | 0.076294 | -0.098267 | 0.052338 | 0.29694 | -0.13565 | -0.17731 | -0.018311 | -0.013733 | -62.4573 | 60.141 | 60.1318 | 62.2421 | 62.3978 | 122.6349 | 62.2787 | 60.228
3341.9375 | 0.061035 | 0.41763 | -0.784 | -0.21896 | 0.14313 | -0.26916 | -0.17838 | 60.2829 | -61.9949 | 0.059509 | -62.2971 | 60.2142 | 62.2375 | 62.2284 | 0.061035 | -0.10788 | 0.059814 | 0.28732 | -0.14954 | -0.16449 | 0.027466 | 0.068665 | -62.4252 | 60.1089 | 60.0815 | 62.2696 | 62.4023 | 122.5983 | 62.2787 | 60.2417
3343.6094 | 0.061035 | 0.40695 | -0.76584 | -0.24567 | 0.12711 | -0.26489 | -0.19546 | 60.2234 | -62.1048 | 0.054932 | -62.3474 | 60.2646 | 62.2513 | 62.2192 | 0.061035 | -0.10361 | 0.059814 | 0.28091 | -0.16556 | -0.1709 | 0.027466 | 0.11444 | -62.4985 | 60.2005 | 60.2234 | 62.2421 | 62.3886 | 122.6944 | 62.2055 | 60.2554
3345.2812 | 0.030518 | 0.41977 | -0.77011 | -0.22217 | 0.13565 | -0.26062 | -0.18799 | 60.2829 | -62.0224 | 0.036621 | -62.2971 | 60.2142 | 62.2604 | 62.2238 | 0.030518 | -0.095062 | 0.057678 | 0.28625 | -0.13779 | -0.1741 | -0.004578 | 0.041199 | -62.4298 | 60.1227 | 60.0952 | 62.2559 | 62.3932 | 122.6303 | 62.2421 | 60.2234
3347 | 0.045776 | 0.40161 | -0.7872 | -0.22858 | 0.13779 | -0.2478 | -0.17731 | 60.2097 | -62.1094 | -0.050354 | -62.3611 | 60.2829 | 62.2375 | 62.2375 | 0.061035 | -0.088654 | 0.050201 | 0.28305 | -0.14206 | -0.17624 | -0.059509 | -0.068665 | -62.5168 | 60.141 | 60.1501 | 62.2513 | 62.4161 | 122.6166 | 62.2787 | 60.2142
3348.6719 | 0.045776 | 0.41229 | -0.784 | -0.25314 | 0.12711 | -0.28412 | -0.17944 | 60.2829 | -61.9537 | 0.17853 | -62.265 | 60.2142 | 62.2375 | 62.2055 | 0.045776 | -0.10681 | 0.065155 | 0.2713 | -0.16235 | -0.16769 | 0.13275 | 0.24261 | -62.4023 | 60.1318 | 60.1181 | 62.2604 | 62.3886 | 122.6669 | 62.2147 | 60.2188
3350.3438 | 0.061035 | 0.42404 | -0.78186 | -0.23178 | 0.11643 | -0.28732 | -0.18585 | 60.2142 | -62.0728 | 0.041199 | -62.3337 | 60.2097 | 62.2604 | 62.2284 | 0.030518 | -0.10895 | 0.043793 | 0.28091 | -0.15595 | -0.17197 | 0.013733 | 0.10071 | -62.4573 | 60.141 | 60.1135 | 62.2513 | 62.384 | 122.5983 | 62.2604 | 60.228
3352 | 0.076294 | 0.3952 | -0.77972 | -0.24887 | 0.12817 | -0.25848 | -0.18906 | 60.2325 | -62.1048 | 0.059509 | -62.3337 | 60.2554 | 62.2421 | 62.2375 | 0.061035 | -0.089722 | 0.064087 | 0.28305 | -0.16022 | -0.17838 | 0.027466 | 0.091553 | -62.5031 | 60.2005 | 60.2051 | 62.2696 | 62.3795 | 122.6761 | 62.2009 | 60.2509
3353.6719 | 0.045776 | 0.41657 | -0.77972 | -0.24887 | 0.11536 | -0.27878 | -0.18051 | 60.2692 | -61.9949 | 0.10986 | -62.3016 | 60.228 | 62.2421 | 62.2284 | 0.030518 | -0.10681 | 0.057678 | 0.29159 | -0.16876 | -0.16983 | 0.11902 | 0.20599 | -62.3932 | 60.1456 | 60.1135 | 62.233 | 62.3978 | 122.7173 | 62.2101 | 60.2234
3355.3906 | 0.076294 | 0.42725 | -0.79254 | -0.23498 | 0.11749 | -0.28412 | -0.18478 | 60.2509 | -62.0361 | 0.064087 | -62.3062 | 60.2325 | 62.2604 | 62.2055 | 0.061035 | -0.11429 | 0.05661 | 0.27985 | -0.15488 | -0.1741 | 0.073242 | 0.15564 | -62.4207 | 60.1456 | 60.141 | 62.2421 | 62.3795 | 122.6898 | 62.1964 | 60.2188
3357.0625 | 0.076294 | 0.40909 | -0.78079 | -0.21469 | 0.12924 | -0.25101 | -0.1741 | 60.2966 | -62.0361 | 0.018311 | -62.3016 | 60.2188 | 62.2421 | 62.2147 | 0.061035 | -0.087585 | 0.042725 | 0.2681 | -0.13672 | -0.17197 | 0.009155 | 0.022888 | -62.4435 | 60.1227 | 60.0769 | 62.2604 | 62.384 | 122.6395 | 62.2742 | 60.2234
3358.7188 | 0.030518 | 0.39414 | -0.78827 | -0.24887 | 0.12497 | -0.25848 | -0.18478 | 60.2371 | -62.0728 | 0.064087 | -62.3245 | 60.2875 | 62.2604 | 62.2421 | 0.061035 | -0.097198 | 0.072632 | 0.27557 | -0.1506 | -0.18799 | 0.032043 | 0.10986 | -62.5076 | 60.2188 | 60.1685 | 62.2513 | 62.4069 | 122.6898 | 62.2009 | 60.2463
3360.4375 | 0.076294 | 0.39093 | -0.77545 | -0.24033 | 0.13565 | -0.26062 | -0.18265 | 60.2188 | -62.0773 | 0.050354 | -62.3383 | 60.2966 | 62.233 | 62.2238 | 0.061035 | -0.09079 | 0.059814 | 0.28625 | -0.14633 | -0.17517 | 0.018311 | 0.073242 | -62.5122 | 60.2097 | 60.1913 | 62.2375 | 62.4115 | 122.7264 | 62.2101 | 60.1959
3362.0938 | 0.015259 | 0.43793 | -0.79254 | -0.22858 | 0.12497 | -0.27878 | -0.17517 | 60.228 | -62.0407 | 0.045776 | -62.3291 | 60.1868 | 62.2421 | 62.2238 | 0.061035 | -0.11108 | 0.05127 | 0.27237 | -0.15595 | -0.17303 | 0.027466 | 0.091553 | -62.4481 | 60.1135 | 60.1181 | 62.2375 | 62.4252 | 122.5983 | 62.2604 | 60.2097
3363.7656 | 0.045776 | 0.39841 | -0.77225 | -0.2478 | 0.13779 | -0.2681 | -0.18799 | 60.2829 | -61.9858 | 0.15564 | -62.2696 | 60.2234 | 62.2513 | 62.233 | 0.045776 | -0.099335 | 0.059814 | 0.28305 | -0.16769 | -0.18478 | 0.10986 | 0.19684 | -62.4344 | 60.141 | 60.1685 | 62.2284 | 62.3795 | 122.6578 | 62.2055 | 60.2371
3365.4844 | 0.061035 | 0.41657 | -0.77759 | -0.24246 | 0.12283 | -0.25848 | -0.17838 | 60.2234 | -62.0819 | 0.054932 | -62.352 | 60.2737 | 62.2513 | 62.2375 | 0.045776 | -0.084381 | 0.063019 | 0.29159 | -0.15381 | -0.18051 | 0.045776 | 0.10071 | -62.5076 | 60.1913 | 60.1776 | 62.265 | 62.3932 | 122.7036 | 62.1872 | 60.2417
3367.1562 | 0.045776 | 0.40268 | -0.76904 | -0.22217 | 0.13031 | -0.24139 | -0.1709 | 60.2188 | -62.1048 | -0.050354 | -62.3428 | 60.26 | 62.265 | 62.265 | 0.030518 | -0.087585 | 0.05661 | 0.28091 | -0.13458 | -0.16769 | -0.050354 | -0.064087 | -62.5076 | 60.1547 | 60.1273 | 62.2467 | 62.4115 | 122.6349 | 62.2513 | 60.228
3368.8281 | 0.045776 | 0.39734 | -0.77225 | -0.23178 | 0.13031 | -0.2446 | -0.16769 | 60.3058 | -62.0361 | 0.068665 | -62.3062 | 60.2692 | 62.2375 | 62.2192 | 0.030518 | -0.080109 | 0.061951 | 0.29587 | -0.14206 | -0.1741 | 0.009155 | 0.045776 | -62.4847 | 60.1868 | 60.1639 | 62.2421 | 62.3932 | 122.6212 | 62.2101 | 60.2509
3370.5156 | 0.015259 | 0.39414 | -0.77652 | -0.25528 | 0.13458 | -0.28305 | -0.1741 | 60.2692 | -61.9766 | 0.16479 | -62.265 | 60.2188 | 62.2787 | 62.2101 | 0.061035 | -0.10147 | 0.055542 | 0.27771 | -0.16129 | -0.16556 | 0.10529 | 0.21973 | -62.4298 | 60.1639 | 60.1501 | 62.2513 | 62.3886 | 122.644 | 62.2192 | 60.2188
3372.1875 | 0.076294 | 0.40161 | -0.77972 | -0.21576 | 0.13351 | -0.24994 | -0.17517 | 60.2142 | -62.146 | -0.073242 | -62.3611 | 60.2554 | 62.265 | 62.233 | 0.061035 | -0.081177 | 0.05661 | 0.28519 | -0.13992 | -0.1741 | -0.073242 | -0.091553 | -62.5168 | 60.1868 | 60.1776 | 62.2604 | 62.4115 | 122.6166 | 62.265 | 60.2417
3373.9219 | 0.061035 | 0.38773 | -0.784 | -0.21896 | 0.1207 | -0.24674 | -0.16449 | 60.2509 | -62.0865 | -0.009155 | -62.3337 | 60.2554 | 62.2879 | 62.2238 | 0.061035 | -0.088654 | 0.048065 | 0.28412 | -0.13458 | -0.17624 | -0.045776 | -0.022888 | -62.5259 | 60.1776 | 60.1959 | 62.265 | 62.3978 | 122.5754 | 62.233 | 60.2646
3375.5938 | 0.045776 | 0.40161 | -0.77652 | -0.26062 | 0.13031 | -0.28305 | -0.18158 | 60.2646 | -61.9904 | 0.15106 | -62.2742 | 60.2097 | 62.233 | 62.2101 | 0.030518 | -0.11215 | 0.060883 | 0.28625 | -0.16235 | -0.16769 | 0.082397 | 0.20599 | -62.4344 | 60.1547 | 60.1685 | 62.2513 | 62.3795 | 122.6624 | 62.1918 | 60.228
3377.2656 | 0.045776 | 0.40268 | -0.77759 | -0.24353 | 0.12924 | -0.27664 | -0.1944 | 60.2646 | -61.9858 | 0.15106 | -62.2787 | 60.2005 | 62.2421 | 62.2101 | 0.045776 | -0.11322 | 0.061951 | 0.27557 | -0.18372 | -0.18478 | 0.10071 | 0.20599 | -62.4298 | 60.1456 | 60.1822 | 62.2375 | 62.3749 | 122.6578 | 62.2055 | 60.2417
3378.9531 | 0.061035 | 0.39841 | -0.77331 | -0.22751 | 0.12176 | -0.24674 | -0.17838 | 60.2692 | -62.0499 | 0.036621 | -62.3062 | 60.2554 | 62.233 | 62.2284 | 0.045776 | -0.089722 | 0.048065 | 0.28519 | -0.15488 | -0.18372 | -0.013733 | 0.013733 | -62.4847 | 60.1776 | 60.1639 | 62.2284 | 62.4023 | 122.5891 | 62.2284 | 60.2463
3380.6406 | 0.076294 | 0.39414 | -0.77225 | -0.21683 | 0.12176 | -0.25528 | -0.19012 | 60.2051 | -62.1323 | -0.054932 | -62.3428 | 60.2646 | 62.2787 | 62.2375 | 0.045776 | -0.087585 | 0.05127 | 0.29159 | -0.13992 | -0.1709 | -0.082397 | -0.10071 | -62.5397 | 60.1868 | 60.1776 | 62.265 | 62.4023 | 122.6028 | 62.265 | 60.2371
3382.3125 | 0.061035 | 0.40588 | -0.78293 | -0.24353 | 0.13458 | -0.28305 | -0.19119 | 60.2005 | -62.0636 | 0.091553 | -62.3291 | 60.2463 | 62.265 | 62.2101 | 0.030518 | -0.10574 | 0.066223 | 0.27344 | -0.15915 | -0.1709 | 0.027466 | 0.12817 | -62.4847 | 60.1868 | 60.1913 | 62.265 | 62.384 | 122.6578 | 62.2009 | 60.228
3383.9688 | 0.045776 | 0.39841 | -0.77972 | -0.22537 | 0.12497 | -0.25635 | -0.18051 | 60.2051 | -62.1414 | -0.054932 | -62.352 | 60.2737 | 62.2421 | 62.2467 | 0.030518 | -0.089722 | 0.055542 | 0.28839 | -0.13458 | -0.17944 | -0.11902 | -0.091553 | -62.5488 | 60.1959 | 60.1913 | 62.2696 | 62.4023 | 122.5754 | 62.2513 | 60.2646
3385.625 | 0.030518 | 0.40375 | -0.784 | -0.25207 | 0.1239 | -0.28946 | -0.18692 | 60.2646 | -62.0087 | 0.14191 | -62.2787 | 60.2142 | 62.2513 | 62.1918 | 0.045776 | -0.11749 | 0.061951 | 0.28305 | -0.16663 | -0.1741 | 0.073242 | 0.16937 | -62.4527 | 60.1547 | 60.2142 | 62.2375 | 62.3703 | 122.6532 | 62.2009 | 60.2554
3387.2969 | 0.045776 | 0.42618 | -0.78827 | -0.2211 | 0.12817 | -0.29587 | -0.19226 | 60.2188 | -62.0499 | 0.022888 | -62.3428 | 60.173 | 62.2238 | 62.2238 | 0.045776 | -0.11002 | 0.052338 | 0.28519 | -0.16022 | -0.1741 | 0.013733 | 0.064087 | -62.4435 | 60.1135 | 60.0998 | 62.2421 | 62.4069 | 122.58 | 62.2696 | 60.2325
3388.9688 | 0.061035 | 0.43045 | -0.78934 | -0.22003 | 0.13458 | -0.28625 | -0.18906 | 60.2325 | -62.0682 | 0.022888 | -62.3291 | 60.2005 | 62.2467 | 62.2101 | 0.045776 | -0.11536 | 0.049133 | 0.27985 | -0.15915 | -0.17197 | 0.009155 | 0.073242 | -62.4527 | 60.1227 | 60.1501 | 62.233 | 62.3978 | 122.5845 | 62.2421 | 60.2417
3390.6406 | 0.061035 | 0.42511 | -0.79361 | -0.24033 | 0.13886 | -0.27344 | -0.19119 | 60.2463 | -62.059 | 0.032043 | -62.3245 | 60.2051 | 62.2375 | 62.2238 | 0.061035 | -0.11108 | 0.043793 | 0.28519 | -0.15915 | -0.17944 | 0.018311 | 0.068665 | -62.4527 | 60.1273 | 60.1135 | 62.233 | 62.4069 | 122.58 | 62.2284 | 60.2417
3392.3438 | 0.061035 | 0.41443 | -0.77011 | -0.22003 | 0.13458 | -0.2446 | -0.17197 | 60.2509 | -62.1185 | -0.059509 | -62.3703 | 60.2692 | 62.2467 | 62.2375 | 0.076294 | -0.091858 | 0.058746 | 0.28091 | -0.1474 | -0.18478 | -0.054932 | -0.082397 | -62.4985 | 60.1868 | 60.1547 | 62.2467 | 62.3932 | 122.612 | 62.265 | 60.2234
3394.0156 | 0.045776 | 0.4187 | -0.77759 | -0.23605 | 0.13672 | -0.28305 | -0.18478 | 60.2234 | -62.0682 | 0.045776 | -62.3383 | 60.2051 | 62.2375 | 62.2101 | 0.076294 | -0.11856 | 0.064087 | 0.27771 | -0.16342 | -0.18051 | 0.045776 | 0.12817 | -62.4481 | 60.1318 | 60.1318 | 62.2604 | 62.384 | 122.6395 | 62.2467 | 60.2188
3395.6875 | 0.045776 | 0.42297 | -0.79147 | -0.22644 | 0.13031 | -0.26062 | -0.18158 | 60.2921 | -61.9995 | 0.050354 | -62.2879 | 60.1822 | 62.2559 | 62.2467 | 0.030518 | -0.10681 | 0.042725 | 0.28519 | -0.13886 | -0.17517 | 0.036621 | 0.07782 | -62.4069 | 60.1181 | 60.1044 | 62.2742 | 62.3703 | 122.58 | 62.2559 | 60.2234
3397.3906 | 0.061035 | 0.40482 | -0.77331 | -0.22964 | 0.11749 | -0.23498 | -0.18799 | 60.2325 | -62.1368 | -0.059509 | -62.3428 | 60.2737 | 62.2604 | 62.2284 | 0.061035 | -0.089722 | 0.060883 | 0.28946 | -0.13672 | -0.17517 | -0.082397 | -0.10986 | -62.5397 | 60.2005 | 60.1776 | 62.2513 | 62.4207 | 122.612 | 62.2604 | 60.26
3399.0625 | 0.045776 | 0.38559 | -0.77225 | -0.23392 | 0.13565 | -0.25421 | -0.18158 | 60.26 | -62.059 | 0.068665 | -62.2879 | 60.2875 | 62.2375 | 62.2284 | 0.045776 | -0.087585 | 0.069427 | 0.27771 | -0.1442 | -0.16983 | 0.032043 | 0.082397 | -62.4619 | 60.1593 | 60.173 | 62.2421 | 62.384 | 122.6944 | 62.1964 | 60.2463
3400.7344 | 0.045776 | 0.41763 | -0.77331 | -0.23926 | 0.11536 | -0.28198 | -0.1741 | 60.2234 | -62.0316 | 0.045776 | -62.3245 | 60.1547 | 62.2467 | 62.2192 | 0.030518 | -0.11429 | 0.060883 | 0.27878 | -0.16769 | -0.1741 | 0.013733 | 0.068665 | -62.4481 | 60.1135 | 60.1089 | 62.2513 | 62.3795 | 122.5571 | 62.2559 | 60.2371
3402.4531 | 0.030518 | 0.40054 | -0.77438 | -0.22217 | 0.13031 | -0.25101 | -0.19012 | 60.2051 | -62.1185 | -0.064087 | -62.3566 | 60.2966 | 62.2513 | 62.2375 | 0.061035 | -0.081177 | 0.057678 | 0.29266 | -0.14206 | -0.17731 | -0.086975 | -0.07782 | -62.5122 | 60.173 | 60.1685 | 62.265 | 62.3795 | 122.612 | 62.2559 | 60.2188
3404.1094 | 0.061035 | 0.40482 | -0.77331 | -0.23498 | 0.12497 | -0.26276 | -0.17731 | 60.2005 | -62.0728 | 0.073242 | -62.3291 | 60.2463 | 62.2559 | 62.2192 | 0.061035 | -0.10147 | 0.069427 | 0.2948 | -0.15595 | -0.17624 | 0.041199 | 0.10986 | -62.4847 | 60.2234 | 60.1959 | 62.2467 | 62.3795 | 122.6761 | 62.178 | 60.2463
3405.7969 | 0.030518 | 0.41122 | -0.77225 | -0.2243 | 0.12711 | -0.27344 | -0.18051 | 60.2692 | -61.9904 | 0.050354 | -62.2604 | 60.1639 | 62.233 | 62.1918 | 0.061035 | -0.10254 | 0.054474 | 0.28091 | -0.15167 | -0.18265 | 0.022888 | 0.07782 | -62.4069 | 60.1135 | 60.0677 | 62.2696 | 62.3978 | 122.5845 | 62.265 | 60.2051
3407.5156 | 0.061035 | 0.40161 | -0.77545 | -0.24674 | 0.12924 | -0.27664 | -0.17731 | 60.2692 | -61.9583 | 0.16022 | -62.265 | 60.2142 | 62.2375 | 62.1826 | 0.061035 | -0.10147 | 0.052338 | 0.27237 | -0.14954 | -0.17303 | 0.10071 | 0.23346 | -62.4115 | 60.141 | 60.1181 | 62.2284 | 62.352 | 122.6486 | 62.1872 | 60.228
3409.2031 | 0.091553 | 0.41657 | -0.77866 | -0.25742 | 0.1207 | -0.29053 | -0.19119 | 60.2966 | -61.9263 | 0.16022 | -62.2513 | 60.2005 | 62.2284 | 62.2009 | 0.030518 | -0.13031 | 0.059814 | 0.27878 | -0.16983 | -0.17944 | 0.14191 | 0.26093 | -62.3795 | 60.0952 | 60.0815 | 62.2421 | 62.3657 | 122.6715 | 62.2055 | 60.2188
3410.875 | 0.045776 | 0.42831 | -0.78934 | -0.2243 | 0.11963 | -0.28839 | -0.18692 | 60.2325 | -62.0087 | 0.064087 | -62.2971 | 60.2325 | 62.2604 | 62.2238 | 0.030518 | -0.11856 | 0.050201 | 0.2681 | -0.15808 | -0.17197 | 0.073242 | 0.16479 | -62.3978 | 60.1227 | 60.1227 | 62.2467 | 62.3886 | 122.6898 | 62.2147 | 60.2188
3412.5625 | 0.045776 | 0.41336 | -0.784 | -0.22858 | 0.13245 | -0.27451 | -0.19867 | 60.2783 | -61.9354 | 0.13733 | -62.2604 | 60.2188 | 62.2375 | 62.1918 | 0.030518 | -0.11108 | 0.059814 | 0.28305 | -0.15915 | -0.17624 | 0.16479 | 0.25177 | -62.3749 | 60.1089 | 60.0906 | 62.2192 | 62.3703 | 122.7036 | 62.1964 | 60.2097
3414.25 | 0.061035 | 0.40588 | -0.77866 | -0.23819 | 0.13245 | -0.26382 | -0.18158 | 60.2921 | -61.9675 | 0.16479 | -62.2513 | 60.2005 | 62.2147 | 62.2009 | 0.061035 | -0.09613 | 0.053406 | 0.27771 | -0.16235 | -0.1741 | 0.12817 | 0.24261 | -62.4023 | 60.1593 | 60.1547 | 62.2055 | 62.3428 | 122.6578 | 62.1964 | 60.2234
3415.9219 | 0.030518 | 0.42084 | -0.78507 | -0.23392 | 0.12924 | -0.28198 | -0.18692 | 60.2325 | -62.0316 | 0.064087 | -62.3016 | 60.228 | 62.2421 | 62.233 | 0.076294 | -0.10681 | 0.053406 | 0.27237 | -0.16663 | -0.16876 | 0.086975 | 0.17853 | -62.4207 | 60.1227 | 60.1181 | 62.2009 | 62.384 | 122.6532 | 62.2009 | 60.2188
3417.5781 | 0.061035 | 0.40695 | -0.784 | -0.22003 | 0.12497 | -0.2446 | -0.17838 | 60.2463 | -62.0728 | -0.018311 | -62.3108 | 60.228 | 62.2513 | 62.2421 | 0.045776 | -0.085449 | 0.041656 | 0.2713 | -0.12497 | -0.16449 | 0.004578 | 0.018311 | -62.4344 | 60.1273 | 60.0906 | 62.2604 | 62.4023 | 122.6212 | 62.2284 | 60.228
3419.2969 | 0.045776 | 0.40909 | -0.7872 | -0.23071 | 0.13351 | -0.26596 | -0.18799 | 60.26 | -61.9949 | 0.1236 | -62.2879 | 60.228 | 62.233 | 62.2009 | 0.045776 | -0.098267 | 0.052338 | 0.27664 | -0.14847 | -0.16663 | 0.050354 | 0.15564 | -62.4756 | 60.1822 | 60.1501 | 62.2559 | 62.3795 | 122.6395 | 62.1918 | 60.2509
3420.9688 | 0.061035 | 0.41763 | -0.7872 | -0.22217 | 0.12604 | -0.25421 | -0.18372 | 60.2829 | -61.9812 | 0.050354 | -62.2879 | 60.1913 | 62.2467 | 62.2284 | 0.061035 | -0.11215 | 0.045929 | 0.28091 | -0.13565 | -0.16449 | 0.036621 | 0.09613 | -62.4252 | 60.1044 | 60.0906 | 62.2284 | 62.3932 | 122.5754 | 62.2513 | 60.2371
3422.6562 | 0.045776 | 0.3952 | -0.77118 | -0.20828 | 0.1239 | -0.23926 | -0.18051 | 60.2371 | -62.1094 | -0.036621 | -62.3291 | 60.2509 | 62.265 | 62.2284 | 0.061035 | -0.09079 | 0.061951 | 0.28091 | -0.13458 | -0.17838 | -0.082397 | -0.068665 | -62.5214 | 60.1868 | 60.1593 | 62.2467 | 62.4298 | 122.5479 | 62.233 | 60.26
3424.3281 | 0.045776 | 0.4187 | -0.79254 | -0.2446 | 0.12283 | -0.28305 | -0.18158 | 60.2051 | -62.0316 | 0.054932 | -62.3062 | 60.1822 | 62.2238 | 62.2284 | 0.030518 | -0.11749 | 0.050201 | 0.27771 | -0.16342 | -0.15915 | 0.068665 | 0.16022 | -62.4115 | 60.1364 | 60.1089 | 62.2467 | 62.3749 | 122.6852 | 62.1964 | 60.2097
3426 | 0.076294 | 0.41122 | -0.77759 | -0.23819 | 0.11963 | -0.27557 | -0.18265 | 60.228 | -62.0544 | 0.059509 | -62.3383 | 60.2646 | 62.2559 | 62.2192 | 0.045776 | -0.097198 | 0.053406 | 0.29159 | -0.14847 | -0.17517 | 0.041199 | 0.10529 | -62.4847 | 60.2188 | 60.173 | 62.2513 | 62.384 | 122.6532 | 62.1964 | 60.2325
3427.7031 | 0.045776 | 0.40588 | -0.77438 | -0.22644 | 0.12283 | -0.24567 | -0.17838 | 60.228 | -62.0773 | 0.050354 | -62.3016 | 60.2737 | 62.2559 | 62.2284 | 0.030518 | -0.093994 | 0.05661 | 0.29373 | -0.15167 | -0.18051 | 0.018311 | 0.09613 | -62.4573 | 60.2005 | 60.1959 | 62.2147 | 62.384 | 122.7173 | 62.1643 | 60.2051
3429.4375 | 0.030518 | 0.42618 | -0.77118 | -0.2446 | 0.13138 | -0.28519 | -0.19012 | 60.2783 | -61.9492 | 0.16937 | -62.2696 | 60.1959 | 62.2238 | 62.1872 | 0.030518 | -0.10574 | 0.060883 | 0.27451 | -0.16129 | -0.1741 | 0.15106 | 0.27466 | -62.3428 | 60.1135 | 60.0998 | 62.2467 | 62.3795 | 122.6944 | 62.178 | 60.1868
3431.0938 | 0.045776 | 0.40375 | -0.77225 | -0.22324 | 0.13351 | -0.24887 | -0.17303 | 60.2142 | -62.1048 | -0.059509 | -62.3383 | 60.2646 | 62.2559 | 62.2147 | 0.045776 | -0.088654 | 0.055542 | 0.29053 | -0.12924 | -0.1741 | -0.068665 | -0.073242 | -62.5122 | 60.173 | 60.1364 | 62.2421 | 62.3749 | 122.6074 | 62.2421 | 60.2371
3432.7812 | 0.076294 | 0.39948 | -0.77118 | -0.25421 | 0.13458 | -0.28519 | -0.17624 | 60.2829 | -61.9492 | 0.16479 | -62.2513 | 60.1913 | 62.2375 | 62.2055 | 0.061035 | -0.099335 | 0.061951 | 0.28198 | -0.15915 | -0.18372 | 0.13733 | 0.27008 | -62.3703 | 60.0906 | 60.1135 | 62.2009 | 62.3703 | 122.6486 | 62.178 | 60.1868
3434.5 | 0.030518 | 0.41122 | -0.77972 | -0.24033 | 0.13351 | -0.27771 | -0.18906 | 60.2692 | -61.9812 | 0.14191 | -62.2604 | 60.1822 | 62.2375 | 62.2238 | 0.030518 | -0.1004 | 0.059814 | 0.27878 | -0.16129 | -0.17624 | 0.10071 | 0.21057 | -62.4344 | 60.1501 | 60.1318 | 62.2467 | 62.3703 | 122.6349 | 62.2009 | 60.2371
3436.1719 | 0.061035 | 0.40268 | -0.77866 | -0.21683 | 0.13031 | -0.25314 | -0.16983 | 60.228 | -62.1048 | -0.064087 | -62.3474 | 60.2463 | 62.2238 | 62.2421 | 0.030518 | -0.086517 | 0.055542 | 0.28625 | -0.13992 | -0.18265 | -0.054932 | -0.068665 | -62.4847 | 60.1547 | 60.1364 | 62.2421 | 62.3749 | 122.5983 | 62.2375 | 60.2371
3437.8438 | 0.061035 | 0.40268 | -0.77331 | -0.2478 | 0.12924 | -0.28412 | -0.18799 | 60.3012 | -61.94 | 0.15564 | -62.2375 | 60.2051 | 62.233 | 62.2238 | 0.045776 | -0.11215 | 0.063019 | 0.2681 | -0.17624 | -0.16983 | 0.13733 | 0.27466 | -62.3795 | 60.141 | 60.1318 | 62.2009 | 62.3749 | 122.6486 | 62.1918 | 60.2188
3439.5312 | 0.091553 | 0.4155 | -0.78079 | -0.22324 | 0.12817 | -0.25314 | -0.18265 | 60.2371 | -62.0728 | -0.018311 | -62.3245 | 60.2325 | 62.233 | 62.233 | 0.045776 | -0.091858 | 0.057678 | 0.27878 | -0.13779 | -0.1709 | -0.009155 | 0.004578 | -62.4481 | 60.1181 | 60.0861 | 62.2513 | 62.3657 | 122.6074 | 62.2421 | 60.2234
3441.1875 | 0.061035 | 0.39307 | -0.76584 | -0.2478 | 0.12924 | -0.26062 | -0.18692 | 60.228 | -62.0911 | 0.054932 | -62.3199 | 60.2783 | 62.233 | 62.2101 | 0.061035 | -0.09079 | 0.070496 | 0.28091 | -0.15595 | -0.17838 | 0.022888 | 0.073242 | -62.4847 | 60.2234 | 60.1822 | 62.2375 | 62.3795 | 122.6807 | 62.1872 | 60.228
3442.8594 | 0.061035 | 0.39307 | -0.76477 | -0.24674 | 0.13351 | -0.24887 | -0.16876 | 60.2646 | -62.0636 | 0.064087 | -62.2879 | 60.2692 | 62.2192 | 62.2147 | 0.045776 | -0.086517 | 0.05661 | 0.29159 | -0.1506 | -0.18372 | 0.041199 | 0.09613 | -62.4619 | 60.1959 | 60.173 | 62.2284 | 62.3886 | 122.6898 | 62.1506 | 60.2188
3444.5312 | 0.045776 | 0.41763 | -0.77972 | -0.2211 | 0.14633 | -0.28091 | -0.18158 | 60.2554 | -61.9949 | 0.054932 | -62.3154 | 60.1685 | 62.233 | 62.2284 | 0.045776 | -0.11108 | 0.045929 | 0.27664 | -0.15274 | -0.16342 | 0.032043 | 0.073242 | -62.439 | 60.0632 | 60.1181 | 62.2421 | 62.3795 | 122.5342 | 62.2513 | 60.2509
3446.2031 | 0.030518 | 0.39307 | -0.77225 | -0.23712 | 0.12604 | -0.25528 | -0.1944 | 60.2234 | -62.0865 | 0.041199 | -62.3108 | 60.2554 | 62.2559 | 62.2467 | 0.045776 | -0.091858 | 0.069427 | 0.28305 | -0.15488 | -0.18051 | 0.022888 | 0.091553 | -62.4756 | 60.2051 | 60.2051 | 62.2559 | 62.3703 | 122.7036 | 62.1735 | 60.2005
3447.875 | 0.045776 | 0.39414 | -0.77438 | -0.22217 | 0.12924 | -0.25528 | -0.1741 | 60.2005 | -62.114 | -0.073242 | -62.3428 | 60.26 | 62.265 | 62.2513 | 0.045776 | -0.087585 | 0.058746 | 0.29053 | -0.13779 | -0.17731 | -0.07782 | -0.073242 | -62.5076 | 60.1639 | 60.1547 | 62.2787 | 62.4252 | 122.5983 | 62.2467 | 60.2188
3449.5469 | 0.045776 | 0.38986 | -0.77225 | -0.22537 | 0.13351 | -0.25742 | -0.1741 | 60.1822 | -62.1277 | -0.07782 | -62.352 | 60.2463 | 62.2513 | 62.2147 | 0.030518 | -0.099335 | 0.046997 | 0.28625 | -0.11963 | -0.17517 | -0.091553 | -0.082397 | -62.5259 | 60.1547 | 60.1685 | 62.2284 | 62.4023 | 122.5571 | 62.2055 | 60.2142
3451.2031 | 0.061035 | 0.40268 | -0.77866 | -0.24567 | 0.1239 | -0.27771 | -0.18799 | 60.2417 | -61.9766 | 0.16479 | -62.2742 | 60.1822 | 62.2238 | 62.2238 | 0.061035 | -0.10681 | 0.065155 | 0.27985 | -0.17624 | -0.16876 | 0.10529 | 0.2243 | -62.3978 | 60.1501 | 60.1639 | 62.2192 | 62.3749 | 122.6395 | 62.2009 | 60.2142
3452.875 | 0.045776 | 0.40695 | -0.77225 | -0.23819 | 0.13031 | -0.25421 | -0.19119 | 60.2051 | -62.0865 | -0.068665 | -62.3474 | 60.2554 | 62.2421 | 62.2147 | 0.030518 | -0.091858 | 0.060883 | 0.28519 | -0.13245 | -0.16769 | -0.073242 | -0.059509 | -62.4939 | 60.1639 | 60.173 | 62.2421 | 62.3932 | 122.5937 | 62.2375 | 60.2005
3454.5469 | 0.045776 | 0.40909 | -0.77972 | -0.24033 | 0.1239 | -0.2713 | -0.18906 | 60.1868 | -62.0773 | 0.073242 | -62.3245 | 60.26 | 62.2421 | 62.2284 | 0.061035 | -0.091858 | 0.05661 | 0.28946 | -0.16663 | -0.16235 | 0.009155 | 0.11444 | -62.4756 | 60.2005 | 60.2097 | 62.233 | 62.3749 | 122.6624 | 62.178 | 60.2417
3456.2188 | 0.045776 | 0.42297 | -0.79361 | -0.22537 | 0.12176 | -0.28412 | -0.19546 | 60.2417 | -62.0041 | 0.054932 | -62.3062 | 60.1639 | 62.2284 | 62.1826 | 0.045776 | -0.11002 | 0.041656 | 0.27985 | -0.16769 | -0.16983 | 0.022888 | 0.068665 | -62.4252 | 60.0952 | 60.0998 | 62.2421 | 62.3932 | 122.5296 | 62.265 | 60.2325
3457.9062 | 0.030518 | 0.39734 | -0.77972 | -0.23712 | 0.13565 | -0.24353 | -0.1709 | 60.2783 | -62.0178 | 0.059509 | -62.2833 | 60.2737 | 62.2421 | 62.1964 | 0.061035 | -0.087585 | 0.050201 | 0.28519 | -0.1506 | -0.17197 | 0.004578 | 0.032043 | -62.4573 | 60.1685 | 60.1639 | 62.233 | 62.3795 | 122.6212 | 62.2101 | 60.2142
3459.5781 | 0.045776 | 0.40802 | -0.78293 | -0.24353 | 0.13565 | -0.28732 | -0.18799 | 60.1868 | -62.0453 | 0.045776 | -62.3062 | 60.1822 | 62.233 | 62.2238 | 0.076294 | -0.11856 | 0.060883 | 0.27771 | -0.15915 | -0.16342 | 0.018311 | 0.10071 | -62.4252 | 60.1318 | 60.0998 | 62.2421 | 62.4069 | 122.5937 | 62.2284 | 60.1776
3461.25 | 0.061035 | 0.39734 | -0.76797 | -0.21469 | 0.12176 | -0.24139 | -0.18585 | 60.2188 | -62.1323 | -0.073242 | -62.3245 | 60.2417 | 62.2375 | 62.265 | 0.076294 | -0.086517 | 0.057678 | 0.28305 | -0.14313 | -0.18265 | -0.082397 | -0.09613 | -62.5076 | 60.173 | 60.1639 | 62.2559 | 62.3932 | 122.5937 | 62.233 | 60.2188
3462.9219 | 0.045776 | 0.37918 | -0.77866 | -0.22751 | 0.12924 | -0.24994 | -0.17944 | 60.2829 | -62.0224 | 0.064087 | -62.2879 | 60.2509 | 62.2467 | 62.2101 | 0.015259 | -0.088654 | 0.03952 | 0.28732 | -0.13886 | -0.17624 | 0 | 0.050354 | -62.471 | 60.1822 | 60.173 | 62.2467 | 62.3795 | 122.6028 | 62.2101 | 60.2371
3464.5938 | 0.061035 | 0.39414 | -0.77866 | -0.24887 | 0.12176 | -0.25955 | -0.1709 | 60.2005 | -62.0865 | 0.050354 | -62.3154 | 60.2554 | 62.2467 | 62.2101 | 0.061035 | -0.089722 | 0.072632 | 0.28625 | -0.15701 | -0.17838 | 0.027466 | 0.082397 | -62.471 | 60.1868 | 60.173 | 62.2375 | 62.3795 | 122.6852 | 62.1643 | 60.2005
3466.25 | 0.045776 | 0.42831 | -0.78827 | -0.22858 | 0.1239 | -0.29907 | -0.19226 | 60.1639 | -62.0499 | 0.041199 | -62.3016 | 60.2142 | 62.2375 | 62.2101 | 0.030518 | -0.12176 | 0.052338 | 0.28305 | -0.16556 | -0.16556 | 0.036621 | 0.1236 | -62.4252 | 60.1227 | 60.141 | 62.2421 | 62.3749 | 122.612 | 62.1964 | 60.2188
3467.9375 | 0.030518 | 0.39734 | -0.7637 | -0.2243 | 0.13779 | -0.24567 | -0.17517 | 60.2737 | -62.0499 | 0.07782 | -62.2879 | 60.2554 | 62.2467 | 62.2009 | 0.045776 | -0.091858 | 0.053406 | 0.28305 | -0.14526 | -0.17303 | 0.032043 | 0.082397 | -62.4344 | 60.1639 | 60.173 | 62.2147 | 62.3611 | 122.6807 | 62.1872 | 60.228
3469.6094 | 0.061035 | 0.39948 | -0.77866 | -0.25848 | 0.12604 | -0.28091 | -0.18692 | 60.26 | -61.9537 | 0.16937 | -62.2513 | 60.1822 | 62.2147 | 62.1918 | 0.045776 | -0.10468 | 0.061951 | 0.27451 | -0.17197 | -0.17944 | 0.13275 | 0.25635 | -62.3749 | 60.1135 | 60.1181 | 62.2284 | 62.3611 | 122.6212 | 62.1735 | 60.2417
3471.2656 | 0.045776 | 0.40375 | -0.77331 | -0.21896 | 0.12283 | -0.25528 | -0.17731 | 60.2234 | -62.0682 | -0.027466 | -62.3062 | 60.2188 | 62.2284 | 62.1826 | 0.061035 | -0.099335 | 0.054474 | 0.28091 | -0.13458 | -0.17197 | -0.009155 | 0.004578 | -62.4161 | 60.1181 | 60.0952 | 62.2192 | 62.3611 | 122.6028 | 62.2238 | 60.1868
3472.9375 | 0.045776 | 0.41122 | -0.77759 | -0.24887 | 0.12497 | -0.27344 | -0.19119 | 60.2188 | -62.0499 | 0.086975 | -62.3154 | 60.228 | 62.2513 | 62.233 | 0.045776 | -0.10574 | 0.060883 | 0.28625 | -0.16983 | -0.1741 | 0.032043 | 0.12817 | -62.4847 | 60.1639 | 60.2051 | 62.2375 | 62.3795 | 122.6395 | 62.1872 | 60.228
3474.6094 | 0.061035 | 0.42404 | -0.78934 | -0.22964 | 0.13138 | -0.28091 | -0.18692 | 60.2371 | -62.0132 | 0.041199 | -62.3016 | 60.1868 | 62.2421 | 62.1872 | 0.030518 | -0.10895 | 0.052338 | 0.27451 | -0.16022 | -0.17303 | 0.022888 | 0.07782 | -62.4207 | 60.1135 | 60.1364 | 62.2375 | 62.3703 | 122.5433 | 62.2559 | 60.2188
3476.2969 | 0.030518 | 0.40054 | -0.76904 | -0.25314 | 0.11963 | -0.26596 | -0.19012 | 60.2188 | -62.0728 | 0.068665 | -62.3154 | 60.3012 | 62.233 | 62.2192 | 0.045776 | -0.09613 | 0.060883 | 0.27985 | -0.16342 | -0.17197 | 0.027466 | 0.091553 | -62.4847 | 60.2097 | 60.1913 | 62.233 | 62.3795 | 122.6395 | 62.1826 | 60.2371
3478.0312 | 0.045776 | 0.40268 | -0.77118 | -0.22324 | 0.1239 | -0.25528 | -0.17944 | 60.2142 | -62.0911 | -0.059509 | -62.3428 | 60.2188 | 62.2467 | 62.2147 | 0.030518 | -0.091858 | 0.058746 | 0.28625 | -0.13351 | -0.18051 | -0.054932 | -0.059509 | -62.4893 | 60.1639 | 60.1273 | 62.2467 | 62.4252 | 122.5754 | 62.2238 | 60.2051
3479.7031 | 0.061035 | 0.40268 | -0.76797 | -0.2243 | 0.13565 | -0.24994 | -0.18478 | 60.2417 | -62.0499 | 0.041199 | -62.2833 | 60.2737 | 62.2375 | 62.2147 | 0.061035 | -0.09613 | 0.048065 | 0.28091 | -0.13779 | -0.17197 | 0.027466 | 0.091553 | -62.4619 | 60.1913 | 60.173 | 62.2421 | 62.384 | 122.6807 | 62.1689 | 60.2554
3481.3906 | 0.045776 | 0.4155 | -0.77652 | -0.23605 | 0.11429 | -0.29587 | -0.17303 | 60.2097 | -61.9949 | 0.091553 | -62.2787 | 60.1868 | 62.2421 | 62.2055 | 0.015259 | -0.12497 | 0.058746 | 0.27771 | -0.16556 | -0.16556 | 0.091553 | 0.1831 | -62.3749 | 60.1044 | 60.141 | 62.233 | 62.3566 | 122.6624 | 62.2009 | 60.1868
3483.0625 | 0.045776 | 0.39734 | -0.77011 | -0.21896 | 0.13672 | -0.2478 | -0.17517 | 60.2325 | -62.0956 | -0.022888 | -62.3245 | 60.2509 | 62.2375 | 62.2192 | 0.045776 | -0.097198 | 0.046997 | 0.28198 | -0.13031 | -0.17838 | -0.068665 | -0.054932 | -62.5305 | 60.1868 | 60.1776 | 62.2467 | 62.3886 | 122.5296 | 62.2513 | 60.2463
3484.7344 | 0.045776 | 0.40054 | -0.77331 | -0.23071 | 0.13245 | -0.25314 | -0.17731 | 60.2005 | -62.0956 | -0.068665 | -62.3337 | 60.26 | 62.265 | 62.2238 | 0.061035 | -0.089722 | 0.050201 | 0.2948 | -0.1506 | -0.1741 | -0.068665 | -0.073242 | -62.4985 | 60.1593 | 60.1547 | 62.2559 | 62.384 | 122.5845 | 62.2284 | 60.2234
3486.4531 | 0.045776 | 0.39948 | -0.76691 | -0.23498 | 0.12711 | -0.24887 | -0.17624 | 60.2188 | -62.0911 | -0.018311 | -62.3291 | 60.2188 | 62.2192 | 62.1964 | 0.045776 | -0.09613 | 0.065155 | 0.29159 | -0.1442 | -0.18906 | -0.091553 | -0.054932 | -62.5168 | 60.1913 | 60.1822 | 62.2421 | 62.3932 | 122.5342 | 62.2192 | 60.2371
3488.1094 | 0.061035 | 0.39734 | -0.79681 | -0.25421 | 0.13138 | -0.28732 | -0.18265 | 60.2463 | -61.9492 | 0.16937 | -62.233 | 60.1822 | 62.2238 | 62.2101 | 0.045776 | -0.11643 | 0.069427 | 0.26703 | -0.16235 | -0.16983 | 0.12817 | 0.2655 | -62.352 | 60.1135 | 60.1044 | 62.2147 | 62.3611 | 122.6212 | 62.1826 | 60.1959
3489.7656 | 0.045776 | 0.38773 | -0.76477 | -0.24033 | 0.12176 | -0.24033 | -0.18372 | 60.2829 | -62.027 | 0.059509 | -62.2971 | 60.2463 | 62.2604 | 62.1964 | 0.045776 | -0.080109 | 0.063019 | 0.28519 | -0.14526 | -0.18158 | -0.004578 | 0.036621 | -62.4756 | 60.1868 | 60.141 | 62.2421 | 62.3749 | 122.58 | 62.2055 | 60.26
3491.4375 | 0.045776 | 0.40054 | -0.77759 | -0.26169 | 0.13351 | -0.29907 | -0.18265 | 60.2051 | -62.0087 | 0.10529 | -62.2742 | 60.1913 | 62.2238 | 62.2009 | 0.045776 | -0.10788 | 0.064087 | 0.27985 | -0.17838 | -0.16556 | 0.11902 | 0.19684 | -62.3566 | 60.1227 | 60.0952 | 62.2284 | 62.352 | 122.6624 | 62.1735 | 60.1868
3493.1094 | 0.015259 | 0.41229 | -0.77652 | -0.23178 | 0.12497 | -0.24994 | -0.19333 | 60.2051 | -62.0773 | -0.036621 | -62.3337 | 60.2325 | 62.2559 | 62.2009 | 0.076294 | -0.1004 | 0.055542 | 0.28946 | -0.14099 | -0.18692 | -0.036621 | -0.036621 | -62.4527 | 60.141 | 60.1044 | 62.265 | 62.3749 | 122.612 | 62.2284 | 60.1868
3494.7812 | 0.015259 | 0.38559 | -0.77652 | -0.23819 | 0.11856 | -0.25528 | -0.18265 | 60.2142 | -62.0865 | 0.032043 | -62.3062 | 60.2554 | 62.2421 | 62.2238 | 0.045776 | -0.097198 | 0.067291 | 0.27451 | -0.16556 | -0.17944 | 0.032043 | 0.086975 | -62.471 | 60.1868 | 60.173 | 62.233 | 62.3795 | 122.6807 | 62.178 | 60.2188
3496.4688 | 0.015259 | 0.40375 | -0.7872 | -0.24033 | 0.1239 | -0.29907 | -0.19546 | 60.1959 | -61.9949 | 0.091553 | -62.2879 | 60.2051 | 62.233 | 62.1964 | 0.045776 | -0.11429 | 0.043793 | 0.27664 | -0.16129 | -0.17517 | 0.10986 | 0.19226 | -62.3749 | 60.1181 | 60.1135 | 62.2375 | 62.3657 | 122.6532 | 62.1872 | 60.2097
3498.1406 | 0.061035 | 0.39948 | -0.76584 | -0.23178 | 0.12604 | -0.25207 | -0.1741 | 60.2692 | -62.0132 | 0.064087 | -62.2742 | 60.2463 | 62.2101 | 62.2238 | 0.045776 | -0.083313 | 0.046997 | 0.29159 | -0.14099 | -0.17624 | 0.036621 | 0.073242 | -62.4344 | 60.1593 | 60.1593 | 62.233 | 62.3703 | 122.6395 | 62.1918 | 60.2371
3499.8125 | 0.030518 | 0.40695 | -0.77011 | -0.21042 | 0.13992 | -0.27344 | -0.17838 | 60.2509 | -61.9812 | 0.045776 | -62.2787 | 60.1547 | 62.233 | 62.2147 | 0.045776 | -0.11215 | 0.050201 | 0.28625 | -0.15488 | -0.17838 | 0.041199 | 0.086975 | -62.3795 | 60.1044 | 60.0769 | 62.2604 | 62.3703 | 122.5342 | 62.2238 | 60.2097
3501.5 | 0.045776 | 0.392 | -0.76263 | -0.23605 | 0.12604 | -0.24994 | -0.18265 | 60.2554 | -62.0224 | 0.064087 | -62.2787 | 60.2463 | 62.2559 | 62.2055 | 0.030518 | -0.09079 | 0.064087 | 0.29159 | -0.14206 | -0.18372 | 0.022888 | 0.086975 | -62.4481 | 60.173 | 60.1822 | 62.233 | 62.3611 | 122.6578 | 62.178 | 60.228
3503.1562 | 0.045776 | 0.40268 | -0.77652 | -0.25528 | 0.12283 | -0.28091 | -0.18478 | 60.2692 | -61.9308 | 0.16479 | -62.2513 | 60.1959 | 62.2284 | 62.2009 | 0.030518 | -0.11963 | 0.060883 | 0.27985 | -0.16556 | -0.1741 | 0.14191 | 0.2655 | -62.3611 | 60.1181 | 60.0952 | 62.2055 | 62.3566 | 122.6303 | 62.1918 | 60.1685
3504.8281 | 0.030518 | 0.3952 | -0.78293 | -0.23498 | 0.12817 | -0.27451 | -0.18478 | 60.2097 | -62.0499 | 0.068665 | -62.3154 | 60.2463 | 62.2421 | 62.2009 | 0.045776 | -0.095062 | 0.061951 | 0.27664 | -0.15701 | -0.1741 | 0.041199 | 0.12817 | -62.471 | 60.1776 | 60.1685 | 62.2559 | 62.3611 | 122.6212 | 62.1735 | 60.2142
3506.5 | 0.045776 | 0.40695 | -0.76797 | -0.2243 | 0.13245 | -0.26169 | -0.17838 | 60.26 | -61.9949 | 0.050354 | -62.2742 | 60.1685 | 62.2284 | 62.1735 | 0.030518 | -0.11215 | 0.046997 | 0.27237 | -0.15167 | -0.17944 | 0.032043 | 0.064087 | -62.3978 | 60.0861 | 60.0906 | 62.2284 | 62.384 | 122.5433 | 62.2284 | 60.2463
3508.1875 | 0.061035 | 0.43686 | -0.78827 | -0.21896 | 0.13245 | -0.28198 | -0.18265 | 60.1868 | -62.0316 | 0.018311 | -62.3108 | 60.1913 | 62.2147 | 62.1918 | 0.045776 | -0.11856 | 0.041656 | 0.27344 | -0.15167 | -0.16663 | 0.027466 | 0.082397 | -62.4344 | 60.1364 | 60.0998 | 62.2421 | 62.3749 | 122.5708 | 62.2238 | 60.228
3509.8594 | 0.045776 | 0.42084 | -0.77972 | -0.23178 | 0.12817 | -0.27237 | -0.17944 | 60.2325 | -62.027 | 0.032043 | -62.3108 | 60.1822 | 62.2147 | 62.1872 | 0.061035 | -0.11215 | 0.040588 | 0.27557 | -0.15381 | -0.17197 | 0.032043 | 0.07782 | -62.439 | 60.0952 | 60.1273 | 62.2421 | 62.3657 | 122.5388 | 62.2513 | 60.1959
3511.5312 | 0.045776 | 0.39093 | -0.76904 | -0.25101 | 0.11749 | -0.24567 | -0.17838 | 60.2737 | -62.0407 | 0.07782 | -62.2833 | 60.2554 | 62.2284 | 62.1918 | 0.045776 | -0.085449 | 0.057678 | 0.28305 | -0.13458 | -0.18906 | 0.041199 | 0.10529 | -62.4619 | 60.1913 | 60.1547 | 62.2238 | 62.3886 | 122.6624 | 62.1552 | 60.2371
3513.1875 | 0.076294 | 0.43045 | -0.78186 | -0.23071 | 0.13245 | -0.28839 | -0.17731 | 60.1959 | -62.0361 | 0.027466 | -62.3016 | 60.2005 | 62.2284 | 62.2147 | 0.045776 | -0.1207 | 0.05127 | 0.28519 | -0.15915 | -0.16983 | 0.041199 | 0.091553 | -62.4252 | 60.1181 | 60.1135 | 62.2467 | 62.3886 | 122.5891 | 62.1872 | 60.2234
3514.9219 | 0.030518 | 0.40054 | -0.77972 | -0.22217 | 0.1239 | -0.25848 | -0.19012 | 60.2692 | -62.0041 | 0.018311 | -62.2742 | 60.1868 | 62.2147 | 62.2055 | 0.061035 | -0.092926 | 0.061951 | 0.28625 | -0.14954 | -0.18158 | 0.018311 | 0.022888 | -62.3978 | 60.1181 | 60.0906 | 62.2375 | 62.3611 | 122.5708 | 62.2467 | 60.1959
3516.5781 | 0.030518 | 0.38879 | -0.784 | -0.24887 | 0.12817 | -0.24674 | -0.18265 | 60.2554 | -62.0453 | 0.064087 | -62.2696 | 60.2783 | 62.2513 | 62.2101 | 0.061035 | -0.09079 | 0.065155 | 0.29053 | -0.14954 | -0.18265 | 0.045776 | 0.082397 | -62.4527 | 60.1913 | 60.1776 | 62.2147 | 62.3795 | 122.6761 | 62.178 | 60.2188
3518.25 | 0.061035 | 0.39734 | -0.78293 | -0.25848 | 0.12283 | -0.28412 | -0.19333 | 60.2646 | -61.9492 | 0.17853 | -62.2375 | 60.1959 | 62.2238 | 62.1964 | 0.030518 | -0.10468 | 0.055542 | 0.28839 | -0.16449 | -0.17197 | 0.12817 | 0.25177 | -62.3703 | 60.1089 | 60.1364 | 62.2284 | 62.3474 | 122.6303 | 62.1918 | 60.2005
3519.9219 | 0.045776 | 0.40375 | -0.78507 | -0.21896 | 0.13458 | -0.24887 | -0.17838 | 60.2097 | -62.0911 | -0.064087 | -62.3291 | 60.2325 | 62.2467 | 62.2238 | 0.045776 | -0.092926 | 0.048065 | 0.28198 | -0.13565 | -0.17517 | -0.045776 | -0.082397 | -62.4756 | 60.1501 | 60.1273 | 62.2284 | 62.3749 | 122.58 | 62.2467 | 60.2051
3521.5781 | 0.061035 | 0.38879 | -0.7605 | -0.22644 | 0.12924 | -0.25207 | -0.16983 | 60.2463 | -62.0178 | 0.073242 | -62.2833 | 60.228 | 62.2284 | 62.1918 | 0.061035 | -0.09079 | 0.046997 | 0.28305 | -0.13886 | -0.16983 | 0.032043 | 0.086975 | -62.4481 | 60.173 | 60.173 | 62.2238 | 62.3703 | 122.6624 | 62.1964 | 60.2188
3523.2969 | 0.030518 | 0.39093 | -0.76904 | -0.22858 | 0.12924 | -0.2478 | -0.18265 | 60.1685 | -62.1185 | -0.059509 | -62.3428 | 60.2692 | 62.2375 | 62.2147 | 0.045776 | -0.085449 | 0.064087 | 0.30548 | -0.14206 | -0.16769 | -0.086975 | -0.082397 | -62.5214 | 60.173 | 60.1547 | 62.2513 | 62.3978 | 122.5525 | 62.2147 | 60.2142
3524.9688 | 0.061035 | 0.39307 | -0.76584 | -0.24246 | 0.12817 | -0.25314 | -0.16449 | 60.2371 | -62.0178 | 0.064087 | -62.2696 | 60.26 | 62.2375 | 62.2055 | 0.076294 | -0.091858 | 0.064087 | 0.28732 | -0.13992 | -0.17197 | 0.022888 | 0.091553 | -62.4435 | 60.173 | 60.173 | 62.2284 | 62.3703 | 122.6578 | 62.1643 | 60.2097
3526.625 | 0.030518 | 0.41229 | -0.79361 | -0.2478 | 0.1239 | -0.30762 | -0.18692 | 60.228 | -61.94 | 0.13733 | -62.2604 | 60.1776 | 62.2147 | 62.178 | 0.061035 | -0.11963 | 0.059814 | 0.26916 | -0.16983 | -0.16876 | 0.12817 | 0.24261 | -62.352 | 60.1135 | 60.0952 | 62.2238 | 62.3474 | 122.6578 | 62.1689 | 60.1913
3528.3125 | 0.045776 | 0.39414 | -0.76691 | -0.23392 | 0.12817 | -0.24139 | -0.18158 | 60.2692 | -62.027 | 0.032043 | -62.2787 | 60.2234 | 62.233 | 62.1964 | 0.061035 | -0.082245 | 0.059814 | 0.28732 | -0.13779 | -0.18478 | -0.009155 | 0.013733 | -62.471 | 60.1456 | 60.1501 | 62.2421 | 62.3978 | 122.5525 | 62.2192 | 60.228
3529.9844 | 0.045776 | 0.39734 | -0.79041 | -0.23498 | 0.12817 | -0.29587 | -0.1944 | 60.2325 | -61.9446 | 0.17395 | -62.2375 | 60.1822 | 62.233 | 62.1964 | 0.045776 | -0.11322 | 0.053406 | 0.27451 | -0.16769 | -0.18051 | 0.13275 | 0.24719 | -62.3749 | 60.1089 | 60.0952 | 62.233 | 62.3383 | 122.6166 | 62.2101 | 60.2005
3531.6562 | 0.045776 | 0.4155 | -0.77545 | -0.2179 | 0.13351 | -0.26916 | -0.18372 | 60.2509 | -61.9858 | 0.045776 | -62.2604 | 60.1685 | 62.2284 | 62.2192 | 0.045776 | -0.10361 | 0.05661 | 0.28198 | -0.13672 | -0.18158 | 0.018311 | 0.073242 | -62.384 | 60.0998 | 60.0906 | 62.2467 | 62.3795 | 122.5479 | 62.2192 | 60.1959
3533.3438 | 0.061035 | 0.41977 | -0.7872 | -0.22644 | 0.12604 | -0.28519 | -0.18372 | 60.2234 | -61.9766 | 0.050354 | -62.2925 | 60.1639 | 62.2009 | 62.2147 | 0.045776 | -0.10681 | 0.035248 | 0.28091 | -0.15167 | -0.1709 | 0.027466 | 0.068665 | -62.4161 | 60.0815 | 60.0815 | 62.2421 | 62.3611 | 122.5113 | 62.2467 | 60.1868
3535.0156 | 0.045776 | 0.41763 | -0.77545 | -0.23285 | 0.12283 | -0.27237 | -0.18585 | 60.2234 | -62.0224 | 0.032043 | -62.2833 | 60.1913 | 62.2101 | 62.1964 | 0.061035 | -0.11856 | 0.053406 | 0.27664 | -0.16129 | -0.17197 | 0.018311 | 0.064087 | -62.4207 | 60.1181 | 60.1135 | 62.2147 | 62.3749 | 122.5388 | 62.2375 | 60.2417
3536.7188 | 0.030518 | 0.40054 | -0.78934 | -0.24246 | 0.12497 | -0.27878 | -0.18799 | 60.2005 | -62.0224 | 0.032043 | -62.2971 | 60.2142 | 62.2192 | 62.2055 | 0.061035 | -0.10254 | 0.064087 | 0.27771 | -0.15808 | -0.16556 | 0.018311 | 0.086975 | -62.4252 | 60.1135 | 60.0952 | 62.2467 | 62.3795 | 122.5388 | 62.2375 | 60.2142
3538.4531 | 0.045776 | 0.41122 | -0.79147 | -0.2179 | 0.12711 | -0.2681 | -0.18478 | 60.26 | -62.0087 | 0.041199 | -62.2925 | 60.173 | 62.2559 | 62.1918 | 0.045776 | -0.098267 | 0.042725 | 0.25955 | -0.15274 | -0.17303 | 0.036621 | 0.073242 | -62.4207 | 60.1089 | 60.0769 | 62.2467 | 62.384 | 122.5159 | 62.233 | 60.2051
3540.125 | 0.045776 | 0.38879 | -0.77438 | -0.2446 | 0.13138 | -0.24246 | -0.18478 | 60.2783 | -62.0224 | 0.050354 | -62.2787 | 60.2463 | 62.2147 | 62.2055 | 0.045776 | -0.086517 | 0.060883 | 0.29159 | -0.14526 | -0.19012 | 0.036621 | 0.07782 | -62.4435 | 60.1639 | 60.1913 | 62.2147 | 62.3566 | 122.6624 | 62.1689 | 60.2188
3541.8125 | 0.045776 | 0.40482 | -0.78827 | -0.25635 | 0.13779 | -0.28198 | -0.18799 | 60.3104 | -61.908 | 0.16479 | -62.2284 | 60.1868 | 62.2101 | 62.178 | 0.061035 | -0.11643 | 0.075836 | 0.28091 | -0.17303 | -0.18265 | 0.15564 | 0.25635 | -62.352 | 60.1089 | 60.1089 | 62.2238 | 62.3611 | 122.6303 | 62.1552 | 60.2051
3543.5 | 0.030518 | 0.39734 | -0.77545 | -0.24994 | 0.12711 | -0.27451 | -0.18906 | 60.2829 | -61.9537 | 0.16022 | -62.2375 | 60.2051 | 62.2284 | 62.1872 | 0.061035 | -0.11215 | 0.043793 | 0.28305 | -0.16235 | -0.18692 | 0.11902 | 0.21973 | -62.3978 | 60.1181 | 60.141 | 62.2467 | 62.3566 | 122.6257 | 62.1689 | 60.2188
3545.1562 | 0.061035 | 0.40802 | -0.78293 | -0.20721 | 0.13245 | -0.25421 | -0.18051 | 60.2737 | -61.972 | 0.027466 | -62.233 | 60.2005 | 62.2192 | 62.1872 | 0.076294 | -0.097198 | 0.053406 | 0.28305 | -0.13992 | -0.18051 | 0.018311 | 0.045776 | -62.4023 | 60.0861 | 60.0815 | 62.2284 | 62.3611 | 122.5708 | 62.233 | 60.1959
3546.8281 | 0.061035 | 0.41336 | -0.7872 | -0.23605 | 0.11749 | -0.27557 | -0.18158 | 60.2509 | -61.9583 | 0.12817 | -62.2513 | 60.1959 | 62.2284 | 62.1964 | 0.045776 | -0.11429 | 0.050201 | 0.27557 | -0.16342 | -0.17197 | 0.14648 | 0.22888 | -62.3566 | 60.0952 | 60.0861 | 62.2147 | 62.3703 | 122.6486 | 62.178 | 60.1913
3548.5156 | 0.061035 | 0.41229 | -0.77972 | -0.2179 | 0.12497 | -0.26489 | -0.1741 | 60.2554 | -61.9766 | 0.059509 | -62.2696 | 60.1776 | 62.2192 | 62.1872 | 0.045776 | -0.10895 | 0.043793 | 0.27237 | -0.14313 | -0.17197 | 0.050354 | 0.07782 | -62.4115 | 60.1089 | 60.0677 | 62.2192 | 62.3703 | 122.525 | 62.2192 | 60.2051
3550.1875 | 0.045776 | 0.392 | -0.75836 | -0.25528 | 0.1239 | -0.24246 | -0.1709 | 60.26 | -62.0224 | 0.07782 | -62.2742 | 60.2646 | 62.2238 | 62.2055 | 0.076294 | -0.09079 | 0.067291 | 0.28839 | -0.13992 | -0.18585 | 0.045776 | 0.082397 | -62.439 | 60.1868 | 60.1639 | 62.2147 | 62.3749 | 122.6578 | 62.1735 | 60.2097
3551.8438 | 0.045776 | 0.4187 | -0.7872 | -0.23605 | 0.11749 | -0.28305 | -0.18372 | 60.1776 | -61.9995 | 0.054932 | -62.2833 | 60.2142 | 62.2238 | 62.2055 | 0.061035 | -0.1207 | 0.055542 | 0.27985 | -0.16022 | -0.16876 | 0.073242 | 0.15564 | -62.3932 | 60.1135 | 60.0815 | 62.2101 | 62.3657 | 122.6532 | 62.2101 | 60.1868
3553.5156 | 0.045776 | 0.38879 | -0.78079 | -0.24887 | 0.13031 | -0.27344 | -0.18692 | 60.2463 | -61.9446 | 0.16479 | -62.2238 | 60.1822 | 62.2055 | 62.1918 | 0.076294 | -0.10147 | 0.05661 | 0.27985 | -0.16022 | -0.17731 | 0.13733 | 0.23804 | -62.384 | 60.1273 | 60.1273 | 62.2284 | 62.3795 | 122.6212 | 62.1964 | 60.1959
3555.1719 | 0.030518 | 0.40802 | -0.77972 | -0.21683 | 0.13779 | -0.24353 | -0.18372 | 60.2692 | -61.9675 | 0.045776 | -62.2604 | 60.1776 | 62.2192 | 62.1872 | 0.045776 | -0.1004 | 0.046997 | 0.27878 | -0.13565 | -0.17197 | 0.036621 | 0.045776 | -62.3932 | 60.1181 | 60.0769 | 62.2559 | 62.3657 | 122.5708 | 62.2375 | 60.2188
3556.8594 | 0.061035 | 0.41122 | -0.77011 | -0.23605 | 0.13565 | -0.23819 | -0.17517 | 60.2783 | -62.0178 | 0.036621 | -62.2787 | 60.2417 | 62.2284 | 62.1735 | 0.030518 | -0.084381 | 0.05661 | 0.28091 | -0.13138 | -0.18585 | 0.004578 | 0.013733 | -62.4802 | 60.173 | 60.1318 | 62.2375 | 62.3795 | 122.5433 | 62.2055 | 60.2371
3558.5469 | 0.061035 | 0.3952 | -0.77438 | -0.23712 | 0.12497 | -0.26169 | -0.1741 | 60.2142 | -62.0544 | -0.027466 | -62.3154 | 60.2142 | 62.2375 | 62.2055 | 0.045776 | -0.093994 | 0.058746 | 0.29159 | -0.14313 | -0.16235 | -0.036621 | -0.022888 | -62.4481 | 60.1318 | 60.1089 | 62.2147 | 62.3611 | 122.5708 | 62.233 | 60.2142
3560.2188 | 0.045776 | 0.40268 | -0.76904 | -0.24353 | 0.13458 | -0.24353 | -0.17197 | 60.1685 | -62.1048 | -0.045776 | -62.3337 | 60.2417 | 62.2513 | 62.2375 | 0.045776 | -0.089722 | 0.067291 | 0.28305 | -0.13458 | -0.18478 | -0.07782 | -0.07782 | -62.5076 | 60.1547 | 60.1685 | 62.2284 | 62.3886 | 122.5388 | 62.2375 | 60.2371
3561.8906 | 0.061035 | 0.39307 | -0.78293 | -0.22751 | 0.13351 | -0.25635 | -0.16876 | 60.1776 | -62.1185 | -0.073242 | -62.3154 | 60.2463 | 62.2421 | 62.2055 | 0.061035 | -0.089722 | 0.063019 | 0.29373 | -0.13779 | -0.17624 | -0.086975 | -0.091553 | -62.5076 | 60.1639 | 60.141 | 62.2513 | 62.3795 | 122.525 | 62.2284 | 60.1868
3563.5469 | 0.061035 | 0.3952 | -0.78827 | -0.25207 | 0.1239 | -0.28946 | -0.1944 | 60.2325 | -61.9492 | 0.16479 | -62.2467 | 60.1776 | 62.2147 | 62.178 | 0.061035 | -0.11002 | 0.059814 | 0.27985 | -0.16983 | -0.17838 | 0.10529 | 0.22888 | -62.384 | 60.1318 | 60.141 | 62.2238 | 62.3657 | 122.6074 | 62.1918 | 60.2142
3565.2188 | 0.045776 | 0.42191 | -0.78613 | -0.23392 | 0.12283 | -0.27771 | -0.1741 | 60.2417 | -61.9492 | 0.14191 | -62.2467 | 60.1776 | 62.2009 | 62.2238 | 0.045776 | -0.1207 | 0.046997 | 0.27771 | -0.15167 | -0.16769 | 0.09613 | 0.21515 | -62.4023 | 60.1318 | 60.1089 | 62.2238 | 62.3611 | 122.6166 | 62.178 | 60.228
3566.8906 | 0.061035 | 0.41443 | -0.77652 | -0.25635 | 0.1239 | -0.28732 | -0.19867 | 60.1639 | -62.0224 | 0.045776 | -62.2833 | 60.2005 | 62.2147 | 62.2055 | 0.045776 | -0.11643 | 0.053406 | 0.28305 | -0.16235 | -0.1741 | 0.041199 | 0.13733 | -62.3886 | 60.1044 | 60.0861 | 62.2467 | 62.352 | 122.6074 | 62.1735 | 60.1822
3568.5938 | 0.061035 | 0.41977 | -0.76797 | -0.22537 | 0.13245 | -0.25101 | -0.18478 | 60.2509 | -62.0132 | -0.004578 | -62.2925 | 60.173 | 62.2421 | 62.1872 | 0.061035 | -0.097198 | 0.041656 | 0.27985 | -0.13886 | -0.18799 | 0.013733 | 0.032043 | -62.3932 | 60.1135 | 60.0723 | 62.2238 | 62.3337 | 122.5845 | 62.2375 | 60.2234
3570.25 | 0.061035 | 0.38559 | -0.77545 | -0.24139 | 0.12283 | -0.24246 | -0.17517 | 60.1913 | -62.1002 | -0.036621 | -62.3199 | 60.2646 | 62.233 | 62.2009 | 0.030518 | -0.093994 | 0.079041 | 0.28946 | -0.14206 | -0.19119 | -0.09613 | -0.073242 | -62.5259 | 60.1822 | 60.1547 | 62.2421 | 62.3749 | 122.5067 | 62.2238 | 60.2097
3571.9219 | 0.061035 | 0.39948 | -0.79041 | -0.24033 | 0.1207 | -0.27237 | -0.18585 | 60.1913 | -62.0087 | 0.082397 | -62.3016 | 60.2554 | 62.2284 | 62.2147 | 0.030518 | -0.10147 | 0.057678 | 0.28412 | -0.16129 | -0.17517 | 0.041199 | 0.11902 | -62.4527 | 60.1959 | 60.1501 | 62.2375 | 62.3886 | 122.6074 | 62.1552 | 60.2097
3573.5938 | 0.030518 | 0.39414 | -0.77652 | -0.25742 | 0.13138 | -0.28091 | -0.19333 | 60.2325 | -61.9583 | 0.13275 | -62.2421 | 60.2234 | 62.1872 | 62.1826 | 0.061035 | -0.12176 | 0.063019 | 0.29159 | -0.16556 | -0.17303 | 0.091553 | 0.20142 | -62.4069 | 60.1364 | 60.1318 | 62.2055 | 62.384 | 122.5983 | 62.1735 | 60.2005
3575.2656 | 0.015259 | 0.40695 | -0.784 | -0.21469 | 0.13565 | -0.26276 | -0.19333 | 60.2417 | -61.9675 | 0.050354 | -62.2696 | 60.1501 | 62.2101 | 62.1964 | 0.061035 | -0.11215 | 0.048065 | 0.28412 | -0.14526 | -0.17197 | 0.032043 | 0.086975 | -62.384 | 60.0815 | 60.0586 | 62.2604 | 62.3932 | 122.5159 | 62.233 | 60.2142
3576.9375 | 0.045776 | 0.38452 | -0.77972 | -0.24567 | 0.13031 | -0.24567 | -0.17944 | 60.2646 | -62.0087 | 0.068665 | -62.2833 | 60.2371 | 62.2238 | 62.2009 | 0.061035 | -0.089722 | 0.064087 | 0.2948 | -0.14099 | -0.18158 | 0.022888 | 0.050354 | -62.4573 | 60.1685 | 60.1639 | 62.2101 | 62.3611 | 122.6028 | 62.1964 | 60.2188
3578.6094 | 0.061035 | 0.40588 | -0.77331 | -0.22217 | 0.12497 | -0.25742 | -0.18799 | 60.1913 | -62.059 | -0.036621 | -62.3291 | 60.2051 | 62.2284 | 62.2101 | 0.061035 | -0.085449 | 0.049133 | 0.28625 | -0.14313 | -0.17517 | -0.013733 | -0.022888 | -62.4298 | 60.141 | 60.1135 | 62.2421 | 62.3474 | 122.5708 | 62.2284 | 60.1913
3580.2656 | 0.045776 | 0.3952 | -0.77225 | -0.25314 | 0.1239 | -0.26489 | -0.18692 | 60.1868 | -62.0682 | 0.059509 | -62.3108 | 60.26 | 62.2238 | 62.2009 | 0.045776 | -0.091858 | 0.065155 | 0.29053 | -0.15915 | -0.17197 | 0.013733 | 0.10071 | -62.471 | 60.2005 | 60.1593 | 62.2467 | 62.3749 | 122.6303 | 62.1826 | 60.2051
3581.9219 | 0.061035 | 0.42618 | -0.78293 | -0.22644 | 0.11536 | -0.28305 | -0.19119 | 60.2051 | -61.9766 | 0.036621 | -62.2879 | 60.1639 | 62.2284 | 62.2055 | 0.045776 | -0.11749 | 0.055542 | 0.28198 | -0.14633 | -0.1741 | 0.018311 | 0.07782 | -62.4161 | 60.0906 | 60.0861 | 62.2467 | 62.3749 | 122.5021 | 62.2238 | 60.2005
3583.5938 | 0.076294 | 0.41977 | -0.77331 | -0.22644 | 0.13458 | -0.26489 | -0.18372 | 60.2417 | -61.9812 | 0.041199 | -62.2559 | 60.1639 | 62.2238 | 62.1735 | 0.061035 | -0.10788 | 0.050201 | 0.27771 | -0.1442 | -0.17624 | 0.041199 | 0.073242 | -62.3749 | 60.0815 | 60.1044 | 62.2375 | 62.3886 | 122.5296 | 62.2238 | 60.2051
3585.2656 | 0.045776 | 0.38025 | -0.77438 | -0.2211 | 0.11856 | -0.24887 | -0.18051 | 60.1822 | -62.0956 | -0.064087 | -62.3245 | 60.2371 | 62.2238 | 62.2284 | 0.045776 | -0.086517 | 0.045929 | 0.2713 | -0.13351 | -0.17197 | -0.10529 | -0.11444 | -62.5259 | 60.1822 | 60.173 | 62.2421 | 62.4115 | 122.5296 | 62.2192 | 60.228
3586.9375 | 0.030518 | 0.40375 | -0.78186 | -0.25207 | 0.13351 | -0.29053 | -0.18799 | 60.26 | -61.9446 | 0.1236 | -62.2467 | 60.1868 | 62.2055 | 62.1643 | 0.076294 | -0.11429 | 0.048065 | 0.27557 | -0.17517 | -0.17197 | 0.15564 | 0.24261 | -62.3428 | 60.1273 | 60.0998 | 62.2238 | 62.3657 | 122.6578 | 62.1689 | 60.1456
3588.6094 | 0.061035 | 0.40802 | -0.76797 | -0.23071 | 0.12497 | -0.26169 | -0.19012 | 60.228 | -62.0636 | -0.041199 | -62.3108 | 60.2142 | 62.233 | 62.2238 | 0.045776 | -0.079041 | 0.059814 | 0.29159 | -0.14206 | -0.19119 | -0.036621 | -0.036621 | -62.4252 | 60.1273 | 60.141 | 62.2559 | 62.3795 | 122.58 | 62.2284 | 60.2051
3590.2656 | 0.061035 | 0.392 | -0.77972 | -0.24887 | 0.13458 | -0.26489 | -0.18051 | 60.1868 | -62.0544 | 0.064087 | -62.2971 | 60.26 | 62.2604 | 62.2284 | 0.045776 | -0.10895 | 0.072632 | 0.28519 | -0.16235 | -0.18265 | 0.013733 | 0.09613 | -62.4619 | 60.1868 | 60.173 | 62.2467 | 62.3566 | 122.6395 | 62.1552 | 60.2005
3591.9375 | 0.045776 | 0.41229 | -0.79041 | -0.2211 | 0.11643 | -0.26382 | -0.18265 | 60.2463 | -61.9492 | 0.054932 | -62.2787 | 60.1639 | 62.2055 | 62.1826 | 0.045776 | -0.11749 | 0.054474 | 0.28305 | -0.14633 | -0.1741 | 0.041199 | 0.082397 | -62.384 | 60.1044 | 60.0815 | 62.2604 | 62.3611 | 122.5159 | 62.2284 | 60.2097
3593.625 | 0.045776 | 0.40161 | -0.78186 | -0.23819 | 0.11643 | -0.26169 | -0.18051 | 60.2188 | -62.0636 | 0.036621 | -62.2879 | 60.2646 | 62.2192 | 62.2009 | 0.030518 | -0.098267 | 0.066223 | 0.28519 | -0.15381 | -0.18906 | 0.022888 | 0.091553 | -62.4664 | 60.1776 | 60.1776 | 62.2284 | 62.352 | 122.6715 | 62.178 | 60.1959
3595.2969 | 0.045776 | 0.41763 | -0.78613 | -0.22964 | 0.1207 | -0.27878 | -0.17731 | 60.1868 | -62.0132 | 0.050354 | -62.2833 | 60.1959 | 62.2192 | 62.1872 | 0.076294 | -0.1207 | 0.044861 | 0.27023 | -0.15808 | -0.17303 | 0.022888 | 0.07782 | -62.4207 | 60.1135 | 60.0769 | 62.233 | 62.3749 | 122.5159 | 62.233 | 60.2051
3596.9531 | 0.061035 | 0.38773 | -0.76797 | -0.22217 | 0.13458 | -0.24139 | -0.17303 | 60.2325 | -62.0682 | -0.013733 | -62.3016 | 60.2509 | 62.233 | 62.2284 | 0.045776 | -0.081177 | 0.054474 | 0.28091 | -0.14206 | -0.18265 | -0.068665 | -0.045776 | -62.5076 | 60.1639 | 60.1639 | 62.233 | 62.3932 | 122.5159 | 62.2192 | 60.2371
3598.625 | 0.030518 | 0.42511 | -0.78507 | -0.24567 | 0.12604 | -0.28412 | -0.18265 | 60.2325 | -61.94 | 0.13733 | -62.2421 | 60.1913 | 62.2375 | 62.1597 | 0.045776 | -0.11856 | 0.050201 | 0.27344 | -0.17197 | -0.1709 | 0.15106 | 0.23346 | -62.3245 | 60.1089 | 60.0861 | 62.2101 | 62.3337 | 122.6395 | 62.1597 | 60.1685
3600.2969 | 0.045776 | 0.40695 | -0.75729 | -0.24033 | 0.13245 | -0.24887 | -0.17303 | 60.2097 | -62.1048 | -0.064087 | -62.3383 | 60.2417 | 62.233 | 62.2238 | 0.045776 | -0.086517 | 0.053406 | 0.28305 | -0.14206 | -0.17624 | -0.073242 | -0.086975 | -62.4939 | 60.1776 | 60.1227 | 62.233 | 62.3749 | 122.5433 | 62.2147 | 60.2234
3601.9844 | 0.045776 | 0.38238 | -0.76477 | -0.23712 | 0.12283 | -0.24674 | -0.17624 | 60.2371 | -61.9995 | 0.068665 | -62.2604 | 60.2371 | 62.2101 | 62.2055 | 0.061035 | -0.092926 | 0.049133 | 0.29373 | -0.14633 | -0.18478 | 0.027466 | 0.086975 | -62.4252 | 60.1364 | 60.1639 | 62.2009 | 62.3749 | 122.644 | 62.1552 | 60.2234
3603.6719 | 0.045776 | 0.40695 | -0.77011 | -0.23285 | 0.13031 | -0.24567 | -0.18265 | 60.1593 | -62.114 | -0.068665 | -62.3337 | 60.2325 | 62.2192 | 62.1918 | 0.045776 | -0.091858 | 0.05661 | 0.2948 | -0.14526 | -0.17197 | -0.09613 | -0.09613 | -62.5168 | 60.1776 | 60.141 | 62.2467 | 62.3795 | 122.5479 | 62.2192 | 60.228
3605.3438 | 0.076294 | 0.40054 | -0.76797 | -0.24887 | 0.12497 | -0.28732 | -0.18265 | 60.2509 | -61.9354 | 0.16479 | -62.2467 | 60.1685 | 62.233 | 62.1872 | 0.061035 | -0.12176 | 0.057678 | 0.28839 | -0.18051 | -0.16769 | 0.13275 | 0.26093 | -62.3474 | 60.1089 | 60.0998 | 62.2101 | 62.3474 | 122.6028 | 62.1506 | 60.1822
3607.0156 | 0.045776 | 0.42191 | -0.79254 | -0.2446 | 0.10574 | -0.28305 | -0.19333 | 60.1685 | -62.0132 | 0.036621 | -62.2879 | 60.173 | 62.2055 | 62.1964 | 0.045776 | -0.11643 | 0.050201 | 0.27451 | -0.15808 | -0.18051 | 0.032043 | 0.10071 | -62.4298 | 60.1089 | 60.0952 | 62.2284 | 62.3703 | 122.5433 | 62.2147 | 60.2051
3608.6719 | 0.030518 | 0.39841 | -0.78507 | -0.21255 | 0.12604 | -0.25101 | -0.18051 | 60.2097 | -62.0728 | -0.054932 | -62.3154 | 60.2463 | 62.2284 | 62.2009 | 0.045776 | -0.09079 | 0.057678 | 0.27985 | -0.13779 | -0.17624 | -0.045776 | -0.050354 | -62.4527 | 60.1547 | 60.1227 | 62.2421 | 62.3749 | 122.5571 | 62.2147 | 60.2005
3610.3438 | 0.030518 | 0.40375 | -0.78293 | -0.24567 | 0.12604 | -0.27023 | -0.18265 | 60.2188 | -61.972 | 0.12817 | -62.2604 | 60.2142 | 62.1964 | 62.1918 | 0.061035 | -0.093994 | 0.060883 | 0.27023 | -0.15595 | -0.1741 | 0.068665 | 0.14191 | -62.4344 | 60.1868 | 60.1501 | 62.2513 | 62.3611 | 122.5937 | 62.1689 | 60.2097
3612.0156 | 0.045776 | 0.38666 | -0.77652 | -0.21896 | 0.1239 | -0.24246 | -0.17838 | 60.1868 | -62.0956 | -0.045776 | -62.3291 | 60.2463 | 62.233 | 62.2009 | 0.061035 | -0.085449 | 0.05661 | 0.29159 | -0.13351 | -0.18906 | -0.086975 | -0.10071 | -62.5351 | 60.1639 | 60.1456 | 62.2421 | 62.3795 | 122.5159 | 62.1918 | 60.2463
3613.6875 | 0.030518 | 0.39948 | -0.77438 | -0.25421 | 0.11536 | -0.28625 | -0.18265 | 60.2463 | -61.9171 | 0.17395 | -62.233 | 60.1776 | 62.2055 | 62.178 | 0.045776 | -0.11536 | 0.058746 | 0.28519 | -0.15488 | -0.18051 | 0.1236 | 0.25177 | -62.3611 | 60.1273 | 60.1089 | 62.2147 | 62.3611 | 122.5937 | 62.178 | 60.2142
3615.3906 | 0.045776 | 0.41443 | -0.784 | -0.2446 | 0.11749 | -0.28839 | -0.1944 | 60.2097 | -61.9904 | 0.10071 | -62.2513 | 60.2005 | 62.2101 | 62.1735 | 0.030518 | -0.11108 | 0.046997 | 0.28091 | -0.16449 | -0.16556 | 0.10986 | 0.19684 | -62.3657 | 60.1044 | 60.1135 | 62.2101 | 62.3566 | 122.644 | 62.1643 | 60.1868
3617.0625 | 0.061035 | 0.41229 | -0.78079 | -0.22964 | 0.13351 | -0.27451 | -0.20401 | 60.2737 | -61.9217 | 0.14648 | -62.233 | 60.1868 | 62.2055 | 62.1964 | 0.045776 | -0.12283 | 0.05127 | 0.2713 | -0.15701 | -0.17303 | 0.14191 | 0.24261 | -62.3154 | 60.0952 | 60.0906 | 62.1964 | 62.3337 | 122.644 | 62.1735 | 60.173
3618.75 | 0.045776 | 0.41443 | -0.77118 | -0.24567 | 0.12497 | -0.27344 | -0.18585 | 60.2783 | -61.9125 | 0.15106 | -62.2147 | 60.1776 | 62.1918 | 62.1735 | 0.045776 | -0.11856 | 0.048065 | 0.28305 | -0.15488 | -0.18799 | 0.13275 | 0.26093 | -62.352 | 60.0998 | 60.0906 | 62.2238 | 62.3566 | 122.6257 | 62.146 | 60.1685
3620.4531 | 0.030518 | 0.41657 | -0.78079 | -0.23819 | 0.13138 | -0.27771 | -0.19226 | 60.2783 | -61.9171 | 0.15106 | -62.2421 | 60.1639 | 62.1964 | 62.1735 | 0.061035 | -0.10788 | 0.043793 | 0.27985 | -0.1506 | -0.17838 | 0.14191 | 0.24261 | -62.3428 | 60.1044 | 60.1181 | 62.1964 | 62.3566 | 122.6349 | 62.1552 | 60.1868
3622.1094 | 0.030518 | 0.41977 | -0.78827 | -0.22003 | 0.11749 | -0.2713 | -0.18799 | 60.2509 | -62.0087 | 0.022888 | -62.2742 | 60.1913 | 62.2101 | 62.1918 | 0.076294 | -0.10895 | 0.046997 | 0.27985 | -0.14526 | -0.18051 | 0.032043 | 0.068665 | -62.4298 | 60.1135 | 60.0906 | 62.2101 | 62.3657 | 122.5204 | 62.2421 | 60.1913
3623.7812 | 0.045776 | 0.38879 | -0.7637 | -0.23605 | 0.11749 | -0.23285 | -0.17197 | 60.2692 | -62.027 | 0.064087 | -62.2559 | 60.2509 | 62.2192 | 62.2192 | 0.045776 | -0.084381 | 0.063019 | 0.28091 | -0.14313 | -0.1976 | 0.050354 | 0.073242 | -62.4344 | 60.1868 | 60.1639 | 62.2238 | 62.3657 | 122.6532 | 62.1689 | 60.2051
3625.4844 | 0.061035 | 0.42191 | -0.80322 | -0.23071 | 0.12924 | -0.28198 | -0.18158 | 60.1776 | -61.9995 | 0.036621 | -62.2879 | 60.1776 | 62.2559 | 62.2238 | 0.061035 | -0.11963 | 0.054474 | 0.27878 | -0.15808 | -0.17838 | 0.018311 | 0.082397 | -62.4069 | 60.1044 | 60.1181 | 62.233 | 62.3749 | 122.5616 | 62.2055 | 60.2097
3627.1406 | 0.076294 | 0.39948 | -0.78827 | -0.21469 | 0.13458 | -0.24353 | -0.18265 | 60.2188 | -62.059 | -0.032043 | -62.3016 | 60.2325 | 62.2055 | 62.1964 | 0.045776 | -0.097198 | 0.050201 | 0.28305 | -0.13138 | -0.18051 | -0.018311 | -0.018311 | -62.4252 | 60.141 | 60.0861 | 62.2147 | 62.3795 | 122.5616 | 62.2284 | 60.2005
3628.8281 | 0.030518 | 0.38773 | -0.77438 | -0.22537 | 0.11963 | -0.25207 | -0.17944 | 60.2142 | -62.0499 | -0.032043 | -62.3108 | 60.2142 | 62.2192 | 62.1964 | 0.030518 | -0.095062 | 0.038452 | 0.2948 | -0.13138 | -0.16983 | -0.004578 | -0.004578 | -62.4298 | 60.1227 | 60.0998 | 62.2238 | 62.352 | 122.5708 | 62.2192 | 60.1822
3630.5156 | 0.030518 | 0.392 | -0.77759 | -0.24887 | 0.1207 | -0.24887 | -0.17624 | 60.2188 | -62.0224 | 0.068665 | -62.2604 | 60.2371 | 62.2238 | 62.1964 | 0.061035 | -0.095062 | 0.059814 | 0.28519 | -0.15274 | -0.18692 | 0.036621 | 0.09613 | -62.4298 | 60.1639 | 60.1822 | 62.2192 | 62.3749 | 122.644 | 62.1735 | 60.1959
3632.1875 | 0.061035 | 0.41443 | -0.78079 | -0.22964 | 0.11108 | -0.26916 | -0.1741 | 60.2371 | -61.9492 | 0.050354 | -62.2696 | 60.1639 | 62.2055 | 62.1689 | 0.061035 | -0.11002 | 0.050201 | 0.27985 | -0.1506 | -0.17731 | 0.041199 | 0.082397 | -62.3932 | 60.0632 | 60.0906 | 62.2238 | 62.3886 | 122.5204 | 62.2284 | 60.2142
3633.8594 | 0.045776 | 0.37918 | -0.76904 | -0.25421 | 0.12711 | -0.2478 | -0.18051 | 60.2463 | -62.0453 | 0.068665 | -62.2604 | 60.2692 | 62.2101 | 62.1964 | 0.045776 | -0.088654 | 0.060883 | 0.28839 | -0.14313 | -0.1741 | 0.032043 | 0.086975 | -62.4252 | 60.1456 | 60.1318 | 62.2192 | 62.3657 | 122.6395 | 62.1552 | 60.2005
3635.5312 | 0.045776 | 0.41657 | -0.79041 | -0.2478 | 0.10574 | -0.298 | -0.19653 | 60.2005 | -61.972 | 0.11444 | -62.2559 | 60.1913 | 62.2009 | 62.2101 | 0.061035 | -0.11963 | 0.053406 | 0.27557 | -0.16449 | -0.1741 | 0.11444 | 0.22888 | -62.3474 | 60.1135 | 60.0906 | 62.2284 | 62.352 | 122.6349 | 62.1735 | 60.1822
3637.2031 | 0.045776 | 0.38452 | -0.77011 | -0.2211 | 0.12497 | -0.24246 | -0.18372 | 60.173 | -62.0773 | -0.050354 | -62.3108 | 60.2371 | 62.2238 | 62.178 | 0.045776 | -0.093994 | 0.050201 | 0.28305 | -0.13351 | -0.18265 | -0.082397 | -0.11444 | -62.5076 | 60.173 | 60.1547 | 62.2559 | 62.384 | 122.5342 | 62.2284 | 60.2051
3638.875 | 0.061035 | 0.40482 | -0.76797 | -0.22964 | 0.1239 | -0.25848 | -0.17731 | 60.1913 | -62.0956 | -0.068665 | -62.3154 | 60.228 | 62.2375 | 62.2101 | 0.045776 | -0.079041 | 0.033112 | 0.298 | -0.13992 | -0.18051 | -0.064087 | -0.07782 | -62.4802 | 60.1776 | 60.1456 | 62.233 | 62.384 | 122.5571 | 62.2238 | 60.2142
3640.5781 | 0.030518 | 0.41763 | -0.77331 | -0.22644 | 0.13138 | -0.27878 | -0.18051 | 60.2417 | -61.9675 | 0.059509 | -62.2604 | 60.141 | 62.2238 | 62.1964 | 0.061035 | -0.10254 | 0.046997 | 0.27451 | -0.15595 | -0.16556 | 0.032043 | 0.091553 | -62.3703 | 60.0906 | 60.0861 | 62.233 | 62.3566 | 122.5159 | 62.2192 | 60.1913
3642.25 | 0.045776 | 0.40054 | -0.77011 | -0.23819 | 0.11002 | -0.25955 | -0.17944 | 60.1959 | -62.0636 | 0.032043 | -62.2833 | 60.2554 | 62.2101 | 62.2147 | 0.076294 | -0.092926 | 0.061951 | 0.27664 | -0.15701 | -0.18158 | 0.009155 | 0.09613 | -62.4527 | 60.1959 | 60.1685 | 62.2284 | 62.3703 | 122.6486 | 62.1368 | 60.1959
3643.9375 | 0.045776 | 0.40482 | -0.77972 | -0.25314 | 0.12711 | -0.27023 | -0.18265 | 60.1593 | -62.0499 | 0.041199 | -62.2879 | 60.2509 | 62.1964 | 62.2009 | 0.076294 | -0.089722 | 0.058746 | 0.27771 | -0.15701 | -0.17517 | 0.022888 | 0.086975 | -62.4756 | 60.1913 | 60.1776 | 62.2513 | 62.3474 | 122.6303 | 62.1506 | 60.2005
3645.6406 | 0.045776 | 0.392 | -0.76691 | -0.23498 | 0.1207 | -0.24674 | -0.17303 | 60.173 | -62.059 | -0.059509 | -62.3016 | 60.2417 | 62.233 | 62.2147 | 0.076294 | -0.097198 | 0.054474 | 0.28519 | -0.13886 | -0.17517 | -0.10529 | -0.091553 | -62.5259 | 60.1639 | 60.1364 | 62.2375 | 62.384 | 122.5159 | 62.2238 | 60.2417
3647.3125 | 0.030518 | 0.40802 | -0.77011 | -0.26169 | 0.13351 | -0.28946 | -0.19012 | 60.2188 | -61.9492 | 0.1236 | -62.233 | 60.1822 | 62.2055 | 62.1918 | 0.045776 | -0.13351 | 0.072632 | 0.27451 | -0.18265 | -0.17517 | 0.13275 | 0.24261 | -62.3337 | 60.0769 | 60.1135 | 62.2147 | 62.3383 | 122.644 | 62.1735 | 60.1547
3648.9844 | 0.030518 | 0.39627 | -0.78186 | -0.21683 | 0.12711 | -0.25314 | -0.17624 | 60.1776 | -62.0819 | -0.064087 | -62.3108 | 60.2417 | 62.2192 | 62.2101 | 0.061035 | -0.11002 | 0.054474 | 0.29053 | -0.14633 | -0.1709 | -0.054932 | -0.045776 | -62.4664 | 60.1273 | 60.1227 | 62.2467 | 62.3749 | 122.5616 | 62.2192 | 60.1822
3650.6562 | 0.061035 | 0.39307 | -0.77225 | -0.23392 | 0.12924 | -0.24246 | -0.1741 | 60.26 | -61.9995 | 0.073242 | -62.2559 | 60.2188 | 62.2101 | 62.178 | 0.061035 | -0.088654 | 0.059814 | 0.2948 | -0.14313 | -0.18372 | 0.018311 | 0.07782 | -62.4435 | 60.173 | 60.1456 | 62.2147 | 62.3428 | 122.5983 | 62.1872 | 60.2142
3652.3594 | 0.061035 | 0.38345 | -0.77011 | -0.25207 | 0.13351 | -0.26382 | -0.18478 | 60.1547 | -62.0407 | 0.050354 | -62.2971 | 60.2554 | 62.2238 | 62.1918 | 0.061035 | -0.099335 | 0.068359 | 0.28091 | -0.16556 | -0.17838 | 0.009155 | 0.082397 | -62.471 | 60.173 | 60.1776 | 62.2421 | 62.3657 | 122.6395 | 62.1597 | 60.1959
3654.0156 | 0.061035 | 0.40268 | -0.784 | -0.22217 | 0.12924 | -0.26596 | -0.1741 | 60.1776 | -62.0499 | -0.045776 | -62.3154 | 60.2234 | 62.2147 | 62.2147 | 0.015259 | -0.09613 | 0.054474 | 0.28839 | -0.13886 | -0.18158 | -0.041199 | -0.036621 | -62.4344 | 60.1181 | 60.0998 | 62.2513 | 62.3749 | 122.5662 | 62.2238 | 60.1776
3655.7188 | 0.030518 | 0.40802 | -0.77652 | -0.23819 | 0.11215 | -0.26916 | -0.18906 | 60.1685 | -62.0499 | 0.059509 | -62.3062 | 60.2463 | 62.2192 | 62.2101 | 0.045776 | -0.11002 | 0.05127 | 0.29053 | -0.15488 | -0.17731 | 0.027466 | 0.11444 | -62.4527 | 60.1639 | 60.1776 | 62.2284 | 62.352 | 122.6166 | 62.1597 | 60.1913
3657.4531 | 0.045776 | 0.40909 | -0.76797 | -0.25635 | 0.13779 | -0.27344 | -0.19119 | 60.2188 | -61.9675 | 0.13275 | -62.233 | 60.2097 | 62.2101 | 62.1826 | 0.061035 | -0.10895 | 0.054474 | 0.27664 | -0.15808 | -0.18585 | 0.064087 | 0.15564 | -62.439 | 60.1593 | 60.1547 | 62.2101 | 62.3383 | 122.58 | 62.1643 | 60.2097
3659.125 | 0.030518 | 0.39948 | -0.76691 | -0.22324 | 0.11429 | -0.26169 | -0.18478 | 60.2234 | -61.9766 | 0.018311 | -62.2513 | 60.2005 | 62.1964 | 62.1735 | 0.061035 | -0.10361 | 0.05661 | 0.27985 | -0.14526 | -0.17197 | 0 | 0.027466 | -62.384 | 60.1089 | 60.0815 | 62.2238 | 62.3657 | 122.5525 | 62.2375 | 60.1685
3660.8281 | 0.030518 | 0.392 | -0.77652 | -0.23605 | 0.1207 | -0.24246 | -0.18265 | 60.1639 | -62.0865 | -0.068665 | -62.3154 | 60.2463 | 62.2238 | 62.1918 | 0.030518 | -0.10147 | 0.048065 | 0.28198 | -0.13138 | -0.1741 | -0.068665 | -0.091553 | -62.4802 | 60.1364 | 60.1135 | 62.2421 | 62.3795 | 122.5388 | 62.1826 | 60.1913
3662.5156 | 0.030518 | 0.41122 | -0.77652 | -0.22217 | 0.11643 | -0.27023 | -0.18692 | 60.2371 | -61.9492 | 0.064087 | -62.2513 | 60.1593 | 62.2147 | 62.1689 | 0.015259 | -0.10788 | 0.055542 | 0.27237 | -0.14954 | -0.1741 | 0.032043 | 0.064087 | -62.3749 | 60.0861 | 60.0677 | 62.2284 | 62.352 | 122.493 | 62.2284 | 60.228
3664.1875 | 0.045776 | 0.41763 | -0.78186 | -0.22644 | 0.12176 | -0.27771 | -0.19012 | 60.2097 | -61.9904 | 0.041199 | -62.2833 | 60.1639 | 62.2238 | 62.1872 | 0.061035 | -0.11322 | 0.050201 | 0.28839 | -0.15381 | -0.16876 | 0.027466 | 0.068665 | -62.4161 | 60.0998 | 60.0769 | 62.2192 | 62.3703 | 122.4884 | 62.233 | 60.1913
3665.8594 | 0.061035 | 0.3952 | -0.77866 | -0.24674 | 0.13031 | -0.26596 | -0.19333 | 60.2371 | -61.9583 | 0.050354 | -62.2559 | 60.1547 | 62.1964 | 62.1552 | 0.045776 | -0.11215 | 0.057678 | 0.27237 | -0.1474 | -0.18265 | 0.027466 | 0.073242 | -62.3703 | 60.0906 | 60.0586 | 62.2284 | 62.3474 | 122.5113 | 62.2421 | 60.2188
3667.5469 | 0.045776 | 0.39734 | -0.77438 | -0.22003 | 0.13138 | -0.25207 | -0.17624 | 60.2005 | -62.0544 | -0.054932 | -62.3062 | 60.2325 | 62.2192 | 62.1872 | 0.061035 | -0.11429 | 0.048065 | 0.28091 | -0.13672 | -0.18478 | -0.027466 | -0.050354 | -62.439 | 60.1318 | 60.0952 | 62.233 | 62.3566 | 122.5525 | 62.2375 | 60.2097
3669.2188 | 0.045776 | 0.40161 | -0.76584 | -0.23712 | 0.11643 | -0.25421 | -0.17838 | 60.1868 | -62.0636 | -0.054932 | -62.3108 | 60.2325 | 62.2421 | 62.233 | 0.045776 | -0.091858 | 0.058746 | 0.28091 | -0.13458 | -0.17197 | -0.068665 | -0.073242 | -62.4756 | 60.1547 | 60.1227 | 62.2375 | 62.3795 | 122.5525 | 62.2147 | 60.1913
3670.8906 | 0.061035 | 0.37918 | -0.76584 | -0.22217 | 0.12283 | -0.24674 | -0.1741 | 60.1913 | -62.0865 | -0.059509 | -62.3108 | 60.2417 | 62.2147 | 62.1964 | 0.030518 | -0.087585 | 0.053406 | 0.27344 | -0.14847 | -0.17303 | -0.082397 | -0.10529 | -62.5076 | 60.1868 | 60.173 | 62.2284 | 62.3932 | 122.5388 | 62.2147 | 60.228
3672.5781 | 0.061035 | 0.39307 | -0.77972 | -0.24033 | 0.11856 | -0.25955 | -0.18906 | 60.1868 | -62.0728 | -0.059509 | -62.3199 | 60.2188 | 62.2375 | 62.2238 | 0.030518 | -0.09613 | 0.049133 | 0.28519 | -0.1506 | -0.17731 | -0.059509 | -0.073242 | -62.4664 | 60.1685 | 60.1273 | 62.2192 | 62.3566 | 122.5479 | 62.2375 | 60.228
3674.25 | 0.030518 | 0.38559 | -0.77331 | -0.26276 | 0.12711 | -0.26489 | -0.18478 | 60.1593 | -62.0407 | 0.045776 | -62.2925 | 60.2554 | 62.2101 | 62.2055 | 0.091553 | -0.11215 | 0.066223 | 0.28305 | -0.16876 | -0.18158 | 0.036621 | 0.091553 | -62.471 | 60.1822 | 60.173 | 62.2147 | 62.3474 | 122.6303 | 62.1506 | 60.2005
3675.9062 | 0.045776 | 0.40482 | -0.77331 | -0.22324 | 0.11856 | -0.25635 | -0.17731 | 60.1776 | -62.0819 | -0.059509 | -62.3154 | 60.2417 | 62.1918 | 62.1918 | 0.061035 | -0.099335 | 0.048065 | 0.27985 | -0.14206 | -0.17517 | -0.073242 | -0.064087 | -62.4664 | 60.1547 | 60.1135 | 62.2284 | 62.3703 | 122.5525 | 62.2192 | 60.2142
3677.5625 | 0.061035 | 0.38132 | -0.77866 | -0.25848 | 0.12497 | -0.26382 | -0.18372 | 60.1868 | -62.0544 | 0.059509 | -62.2879 | 60.2646 | 62.2009 | 62.1826 | 0.030518 | -0.097198 | 0.063019 | 0.28305 | -0.16876 | -0.16983 | 0.022888 | 0.091553 | -62.4527 | 60.1685 | 60.1868 | 62.2147 | 62.3611 | 122.6257 | 62.1643 | 60.2097
3679.2344 | 0.045776 | 0.41336 | -0.79147 | -0.23498 | 0.1207 | -0.29587 | -0.18478 | 60.173 | -62.0224 | 0.041199 | -62.2879 | 60.1822 | 62.2147 | 62.1826 | 0.061035 | -0.12283 | 0.048065 | 0.28305 | -0.16235 | -0.17303 | 0.022888 | 0.082397 | -62.4069 | 60.0998 | 60.0815 | 62.2192 | 62.3428 | 122.5342 | 62.2192 | 60.1685
3680.9062 | 0.076294 | 0.40909 | -0.77972 | -0.22644 | 0.13138 | -0.26169 | -0.17838 | 60.1868 | -62.0682 | -0.054932 | -62.3062 | 60.228 | 62.2238 | 62.1735 | 0.030518 | -0.095062 | 0.05127 | 0.28625 | -0.14206 | -0.19226 | -0.064087 | -0.059509 | -62.4527 | 60.1364 | 60.0952 | 62.233 | 62.3566 | 122.5525 | 62.2192 | 60.2097
3682.5781 | 0.061035 | 0.38986 | -0.77759 | -0.25314 | 0.12924 | -0.25528 | -0.17944 | 60.1913 | -62.0636 | 0.041199 | -62.2833 | 60.2234 | 62.2055 | 62.1918 | 0.061035 | -0.092926 | 0.068359 | 0.28412 | -0.15808 | -0.19012 | 0.013733 | 0.07782 | -62.4481 | 60.1822 | 60.1868 | 62.2375 | 62.3383 | 122.644 | 62.146 | 60.1822
3684.2812 | 0.061035 | 0.39307 | -0.77972 | -0.25207 | 0.1239 | -0.28198 | -0.19867 | 60.2554 | -61.9125 | 0.16937 | -62.2284 | 60.2005 | 62.1918 | 62.1689 | 0.045776 | -0.11215 | 0.052338 | 0.27985 | -0.16235 | -0.17731 | 0.1236 | 0.25635 | -62.3566 | 60.0769 | 60.0769 | 62.2055 | 62.3428 | 122.5891 | 62.1368 | 60.1685
3685.9375 | 0.045776 | 0.39948 | -0.77331 | -0.2243 | 0.11643 | -0.25528 | -0.18906 | 60.1868 | -62.0773 | -0.068665 | -62.3062 | 60.2509 | 62.2284 | 62.2147 | 0.061035 | -0.10254 | 0.038452 | 0.28519 | -0.13672 | -0.18265 | -0.082397 | -0.10071 | -62.4756 | 60.1273 | 60.1181 | 62.233 | 62.3657 | 122.5433 | 62.2284 | 60.2142
3687.625 | 0.045776 | 0.38132 | -0.77866 | -0.23178 | 0.1239 | -0.24567 | -0.17944 | 60.2554 | -61.9858 | 0.059509 | -62.2513 | 60.228 | 62.2101 | 62.1689 | 0.061035 | -0.09079 | 0.054474 | 0.27878 | -0.14313 | -0.1741 | 0.032043 | 0.054932 | -62.4344 | 60.173 | 60.1456 | 62.1964 | 62.352 | 122.5983 | 62.1552 | 60.1959
3689.2969 | 0.045776 | 0.38452 | -0.77545 | -0.25421 | 0.12817 | -0.2713 | -0.18692 | 60.1776 | -62.0544 | 0.041199 | -62.2787 | 60.2554 | 62.2284 | 62.2101 | 0.030518 | -0.10574 | 0.072632 | 0.29266 | -0.15915 | -0.17517 | 0.018311 | 0.09613 | -62.4573 | 60.1776 | 60.1776 | 62.2421 | 62.3337 | 122.6257 | 62.146 | 60.1868
3690.9688 | 0.030518 | 0.40268 | -0.78079 | -0.25101 | 0.12711 | -0.28625 | -0.19546 | 60.1959 | -61.9949 | 0.041199 | -62.2925 | 60.1868 | 62.2009 | 62.1597 | 0.030518 | -0.11749 | 0.05661 | 0.27344 | -0.16129 | -0.16983 | 0.022888 | 0.082397 | -62.4023 | 60.0906 | 60.1089 | 62.2147 | 62.3566 | 122.5021 | 62.2375 | 60.1822
3692.6562 | 0.045776 | 0.42084 | -0.80429 | -0.2211 | 0.12817 | -0.28519 | -0.19546 | 60.1822 | -62.0224 | 0.041199 | -62.2742 | 60.1639 | 62.2055 | 62.1735 | 0.061035 | -0.1207 | 0.041656 | 0.28198 | -0.16556 | -0.17303 | 0.013733 | 0.07782 | -62.4115 | 60.0998 | 60.1044 | 62.2375 | 62.3566 | 122.525 | 62.2147 | 60.2005
3694.3281 | 0.030518 | 0.40054 | -0.76691 | -0.23926 | 0.11429 | -0.24674 | -0.19012 | 60.2325 | -62.0224 | 0.054932 | -62.2513 | 60.2325 | 62.2055 | 62.178 | 0.045776 | -0.084381 | 0.048065 | 0.28519 | -0.13992 | -0.19119 | 0.018311 | 0.086975 | -62.4252 | 60.1822 | 60.1547 | 62.2238 | 62.3566 | 122.6303 | 62.1414 | 60.1868
3696 | 0.076294 | 0.40161 | -0.76904 | -0.23712 | 0.12924 | -0.24994 | -0.17624 | 60.1959 | -62.0636 | -0.045776 | -62.3062 | 60.2051 | 62.2147 | 62.2101 | 0.045776 | -0.093994 | 0.063019 | 0.28305 | -0.13138 | -0.18906 | -0.032043 | -0.041199 | -62.4435 | 60.1318 | 60.0952 | 62.2421 | 62.3657 | 122.5662 | 62.2147 | 60.1959
3697.6719 | 0.061035 | 0.39414 | -0.77545 | -0.25421 | 0.11856 | -0.28732 | -0.1976 | 60.26 | -61.9171 | 0.16022 | -62.2375 | 60.1685 | 62.2009 | 62.1826 | 0.045776 | -0.12283 | 0.054474 | 0.27985 | -0.16556 | -0.17944 | 0.13733 | 0.2655 | -62.3566 | 60.0952 | 60.1089 | 62.2147 | 62.3291 | 122.5937 | 62.1643 | 60.1868
3699.3438 | 0.061035 | 0.39841 | -0.76904 | -0.23178 | 0.13138 | -0.25314 | -0.18692 | 60.173 | -62.0819 | -0.041199 | -62.2971 | 60.26 | 62.233 | 62.2238 | 0.045776 | -0.088654 | 0.050201 | 0.28732 | -0.13565 | -0.18158 | -0.082397 | -0.086975 | -62.4847 | 60.1456 | 60.173 | 62.2284 | 62.3703 | 122.5571 | 62.2101 | 60.2097
3701.0156 | 0.061035 | 0.38559 | -0.76263 | -0.23178 | 0.14206 | -0.24567 | -0.17838 | 60.2463 | -61.9995 | 0.073242 | -62.2559 | 60.2509 | 62.2147 | 62.1735 | 0.045776 | -0.093994 | 0.066223 | 0.29694 | -0.14526 | -0.18372 | 0.032043 | 0.068665 | -62.4115 | 60.1547 | 60.1501 | 62.233 | 62.3428 | 122.6257 | 62.1643 | 60.1959
3702.6875 | 0.061035 | 0.38773 | -0.77225 | -0.23712 | 0.12176 | -0.25635 | -0.19012 | 60.2234 | -62.0087 | 0.068665 | -62.2467 | 60.2463 | 62.2055 | 62.1735 | 0.045776 | -0.099335 | 0.057678 | 0.28839 | -0.13565 | -0.18585 | 0.027466 | 0.091553 | -62.4207 | 60.1822 | 60.1822 | 62.2055 | 62.3703 | 122.6303 | 62.146 | 60.2097
3704.4219 | 0.030518 | 0.40482 | -0.78507 | -0.24139 | 0.1239 | -0.29053 | -0.17624 | 60.1868 | -61.9675 | 0.1236 | -62.2513 | 60.2234 | 62.2147 | 62.1735 | 0.030518 | -0.11536 | 0.061951 | 0.27664 | -0.16449 | -0.1741 | 0.045776 | 0.15106 | -62.439 | 60.173 | 60.1776 | 62.2467 | 62.3566 | 122.5708 | 62.1323 | 60.1913
3706.0938 | 0.030518 | 0.38986 | -0.77331 | -0.2211 | 0.13138 | -0.27237 | -0.17944 | 60.2142 | -61.9904 | 0.018311 | -62.2742 | 60.2188 | 62.2101 | 62.1964 | 0.076294 | -0.10895 | 0.052338 | 0.28946 | -0.14206 | -0.18265 | 0 | 0.041199 | -62.3795 | 60.1044 | 60.0815 | 62.2284 | 62.3337 | 122.5525 | 62.2101 | 60.1913
3707.7969 | 0.045776 | 0.37918 | -0.77331 | -0.22217 | 0.13565 | -0.24994 | -0.19119 | 60.173 | -62.059 | -0.054932 | -62.3016 | 60.2371 | 62.2055 | 62.2147 | 0.061035 | -0.098267 | 0.05661 | 0.27878 | -0.1506 | -0.17838 | -0.068665 | -0.068665 | -62.4481 | 60.1547 | 60.1318 | 62.2192 | 62.3566 | 122.5433 | 62.1826 | 60.1868
3709.5156 | 0.030518 | 0.40802 | -0.78186 | -0.2478 | 0.11749 | -0.28946 | -0.19333 | 60.1776 | -61.9858 | 0.032043 | -62.2742 | 60.1685 | 62.2055 | 62.1964 | 0.076294 | -0.12497 | 0.050201 | 0.27344 | -0.16769 | -0.17303 | 0.022888 | 0.07782 | -62.3886 | 60.0952 | 60.1044 | 62.2284 | 62.3749 | 122.5067 | 62.233 | 60.1685
3711.1875 | 0.045776 | 0.40161 | -0.77866 | -0.24674 | 0.1239 | -0.27557 | -0.18906 | 60.2554 | -61.8851 | 0.15564 | -62.2147 | 60.2005 | 62.1872 | 62.1826 | 0.030518 | -0.11643 | 0.053406 | 0.2713 | -0.16769 | -0.1741 | 0.13733 | 0.24719 | -62.3428 | 60.0861 | 60.1044 | 62.1872 | 62.3428 | 122.612 | 62.1506 | 60.173
3712.8594 | 0.030518 | 0.41122 | -0.78186 | -0.24246 | 0.11643 | -0.27344 | -0.19333 | 60.1913 | -61.9949 | 0.07782 | -62.2604 | 60.1913 | 62.1872 | 62.1826 | 0.030518 | -0.11963 | 0.050201 | 0.27878 | -0.16556 | -0.1741 | 0.09613 | 0.17853 | -62.352 | 60.1089 | 60.0815 | 62.1964 | 62.3474 | 122.6257 | 62.1597 | 60.1501
3714.5312 | 0.045776 | 0.40054 | -0.77866 | -0.22324 | 0.13245 | -0.25528 | -0.19119 | 60.2554 | -61.9492 | 0.059509 | -62.265 | 60.1913 | 62.2192 | 62.1735 | 0.045776 | -0.11215 | 0.043793 | 0.26596 | -0.14526 | -0.17731 | 0.050354 | 0.086975 | -62.3657 | 60.0906 | 60.0677 | 62.2147 | 62.3474 | 122.4976 | 62.2147 | 60.2142
3716.2188 | 0.045776 | 0.41016 | -0.78613 | -0.23926 | 0.13458 | -0.27023 | -0.19012 | 60.2783 | -61.8988 | 0.16937 | -62.2147 | 60.1913 | 62.1918 | 62.1918 | 0.061035 | -0.11749 | 0.048065 | 0.25528 | -0.16022 | -0.18158 | 0.15106 | 0.25635 | -62.3428 | 60.1044 | 60.0906 | 62.2055 | 62.3291 | 122.6074 | 62.1506 | 60.1822
3717.9531 | 0.076294 | 0.39307 | -0.78079 | -0.25314 | 0.11643 | -0.23605 | -0.18372 | 60.2463 | -62.027 | 0.050354 | -62.2467 | 60.2737 | 62.1964 | 62.1735 | 0.030518 | -0.088654 | 0.061951 | 0.28732 | -0.13138 | -0.20508 | 0.050354 | 0.086975 | -62.4344 | 60.1547 | 60.1547 | 62.2101 | 62.3383 | 122.6303 | 62.1368 | 60.2142
3719.625 | 0.045776 | 0.40375 | -0.77652 | -0.23819 | 0.1239 | -0.27771 | -0.18692 | 60.2051 | -61.9766 | 0.054932 | -62.2787 | 60.1685 | 62.2238 | 62.1735 | 0.061035 | -0.11856 | 0.063019 | 0.28412 | -0.15167 | -0.17624 | 0.041199 | 0.068665 | -62.3978 | 60.0998 | 60.0632 | 62.2009 | 62.3566 | 122.5021 | 62.2284 | 60.1959
3721.2969 | 0.045776 | 0.39307 | -0.78293 | -0.22751 | 0.11643 | -0.24887 | -0.17731 | 60.1822 | -62.0773 | -0.050354 | -62.3062 | 60.2371 | 62.2009 | 62.1918 | 0.061035 | -0.085449 | 0.044861 | 0.29053 | -0.12604 | -0.18372 | -0.068665 | -0.091553 | -62.4847 | 60.1822 | 60.141 | 62.2147 | 62.3428 | 122.525 | 62.2284 | 60.1959
3722.9688 | 0.061035 | 0.39307 | -0.78613 | -0.24674 | 0.11856 | -0.25742 | -0.18372 | 60.1913 | -62.0499 | 0.059509 | -62.2971 | 60.26 | 62.2284 | 62.2055 | 0.045776 | -0.095062 | 0.05661 | 0.28412 | -0.15701 | -0.18158 | 0.041199 | 0.086975 | -62.471 | 60.1776 | 60.1639 | 62.2055 | 62.3474 | 122.6257 | 62.1323 | 60.1913
3724.6406 | 0.061035 | 0.38345 | -0.76477 | -0.24353 | 0.13245 | -0.25528 | -0.18906 | 60.2371 | -61.9858 | 0.068665 | -62.2559 | 60.2142 | 62.2009 | 62.1872 | 0.045776 | -0.092926 | 0.068359 | 0.28412 | -0.13886 | -0.18478 | 0.041199 | 0.091553 | -62.4069 | 60.1639 | 60.1501 | 62.2147 | 62.3703 | 122.6257 | 62.1735 | 60.1776
3726.3125 | 0.045776 | 0.40588 | -0.78507 | -0.23926 | 0.13031 | -0.28625 | -0.18585 | 60.1456 | -62.0087 | 0.032043 | -62.2787 | 60.1776 | 62.1918 | 62.1872 | 0.076294 | -0.12176 | 0.055542 | 0.27664 | -0.1709 | -0.15381 | 0.027466 | 0.10529 | -62.3932 | 60.0998 | 60.0952 | 62.2284 | 62.3703 | 122.5342 | 62.1872 | 60.1868
3727.9844 | 0.061035 | 0.39414 | -0.77331 | -0.23071 | 0.11215 | -0.24567 | -0.17197 | 60.228 | -62.0224 | -0.004578 | -62.265 | 60.2371 | 62.2238 | 62.1826 | 0.045776 | -0.086517 | 0.058746 | 0.29266 | -0.13672 | -0.19226 | -0.050354 | -0.036621 | -62.4756 | 60.1593 | 60.1318 | 62.2421 | 62.3657 | 122.5067 | 62.2101 | 60.2142
3729.6719 | 0.061035 | 0.3952 | -0.77652 | -0.24246 | 0.11963 | -0.25955 | -0.17624 | 60.2097 | -62.0178 | 0.054932 | -62.2559 | 60.2371 | 62.2101 | 62.2101 | 0.061035 | -0.092926 | 0.065155 | 0.28732 | -0.1442 | -0.17944 | 0.027466 | 0.10529 | -62.4252 | 60.173 | 60.1639 | 62.2192 | 62.3383 | 122.6257 | 62.146 | 60.2005
3731.3438 | 0.030518 | 0.40161 | -0.78079 | -0.23926 | 0.1239 | -0.28839 | -0.19226 | 60.1822 | -61.9949 | 0.032043 | -62.2833 | 60.1639 | 62.2055 | 62.1643 | 0.045776 | -0.12924 | 0.058746 | 0.27985 | -0.16022 | -0.1709 | 0.018311 | 0.082397 | -62.4161 | 60.0861 | 60.0998 | 62.2467 | 62.3474 | 122.5021 | 62.2284 | 60.2142
3733.0312 | 0.045776 | 0.40375 | -0.76797 | -0.22217 | 0.11643 | -0.25848 | -0.17838 | 60.228 | -61.9446 | 0.059509 | -62.2421 | 60.1227 | 62.2009 | 62.1735 | 0.076294 | -0.10574 | 0.044861 | 0.28519 | -0.14206 | -0.17624 | 0.018311 | 0.073242 | -62.3703 | 60.0906 | 60.054 | 62.2375 | 62.3474 | 122.5204 | 62.2055 | 60.1822
3734.7031 | 0.045776 | 0.39734 | -0.784 | -0.24887 | 0.12497 | -0.28305 | -0.19546 | 60.2234 | -61.9171 | 0.17395 | -62.2238 | 60.173 | 62.2055 | 62.1689 | 0.045776 | -0.1207 | 0.057678 | 0.28198 | -0.16235 | -0.18585 | 0.13275 | 0.24719 | -62.3383 | 60.0861 | 60.1089 | 62.2238 | 62.3428 | 122.5754 | 62.1414 | 60.2142
3736.375 | 0.045776 | 0.39627 | -0.78507 | -0.21896 | 0.11963 | -0.25742 | -0.17731 | 60.2371 | -61.9949 | 0.009155 | -62.2467 | 60.1685 | 62.2192 | 62.1826 | 0.045776 | -0.10361 | 0.044861 | 0.27878 | -0.13672 | -0.17838 | 0.013733 | 0.022888 | -62.3886 | 60.1089 | 60.0998 | 62.2101 | 62.3566 | 122.5433 | 62.2101 | 60.2142
3738.0469 | 0.045776 | 0.36957 | -0.77331 | -0.25421 | 0.13031 | -0.25207 | -0.18158 | 60.2005 | -62.027 | 0.054932 | -62.2559 | 60.2554 | 62.2101 | 62.1872 | 0.061035 | -0.10468 | 0.065155 | 0.29053 | -0.14954 | -0.18692 | 0.041199 | 0.091553 | -62.4161 | 60.1822 | 60.1456 | 62.1964 | 62.3657 | 122.6532 | 62.1368 | 60.1913
3739.7031 | 0.076294 | 0.3952 | -0.79468 | -0.22537 | 0.12817 | -0.26916 | -0.18585 | 60.2417 | -61.9492 | 0.032043 | -62.2284 | 60.1547 | 62.1964 | 62.1872 | 0.015259 | -0.10788 | 0.054474 | 0.28839 | -0.15274 | -0.18478 | 0.027466 | 0.041199 | -62.3749 | 60.0952 | 60.0632 | 62.233 | 62.352 | 122.5296 | 62.2055 | 60.1868
3741.375 | 0.076294 | 0.38773 | -0.77652 | -0.24246 | 0.12604 | -0.25101 | -0.17838 | 60.2234 | -61.9904 | 0.073242 | -62.2513 | 60.2463 | 62.2147 | 62.1826 | 0.045776 | -0.09613 | 0.048065 | 0.27878 | -0.14099 | -0.18051 | 0.022888 | 0.07782 | -62.4298 | 60.1547 | 60.1456 | 62.2009 | 62.352 | 122.6212 | 62.1506 | 60.1868
3743.0469 | 0.076294 | 0.4187 | -0.77011 | -0.2446 | 0.11215 | -0.28625 | -0.17303 | 60.1868 | -61.9766 | 0.036621 | -62.2742 | 60.1593 | 62.1964 | 62.1872 | 0.045776 | -0.11856 | 0.058746 | 0.28091 | -0.16769 | -0.17303 | 0.013733 | 0.064087 | -62.4023 | 60.0998 | 60.0815 | 62.2009 | 62.3611 | 122.4884 | 62.2375 | 60.2097
3744.7188 | 0.076294 | 0.38238 | -0.77652 | -0.23071 | 0.11215 | -0.24674 | -0.17944 | 60.2234 | -62.0316 | 0.004578 | -62.2833 | 60.2509 | 62.2009 | 62.1689 | 0.045776 | -0.088654 | 0.060883 | 0.28839 | -0.13138 | -0.18692 | -0.045776 | -0.022888 | -62.4802 | 60.1547 | 60.1547 | 62.2192 | 62.3611 | 122.4976 | 62.1918 | 60.228
3746.4375 | 0.061035 | 0.40161 | -0.77972 | -0.23392 | 0.14099 | -0.27344 | -0.18051 | 60.2188 | -61.9583 | 0.036621 | -62.2238 | 60.1501 | 62.1918 | 62.1826 | 0.045776 | -0.11002 | 0.049133 | 0.27451 | -0.13779 | -0.18051 | 0.013733 | 0.054932 | -62.3657 | 60.0677 | 60.0861 | 62.2467 | 62.352 | 122.5388 | 62.2147 | 60.1822
3748.0938 | 0.045776 | 0.38559 | -0.7637 | -0.2478 | 0.10788 | -0.25421 | -0.17944 | 60.2051 | -62.0041 | 0.073242 | -62.2513 | 60.2463 | 62.2009 | 62.178 | 0.045776 | -0.09079 | 0.066223 | 0.28732 | -0.15167 | -0.18478 | 0.022888 | 0.091553 | -62.4115 | 60.1685 | 60.1685 | 62.2192 | 62.3611 | 122.6212 | 62.1506 | 60.1776
3749.75 | 0.045776 | 0.40909 | -0.77759 | -0.23285 | 0.12924 | -0.26489 | -0.18372 | 60.2188 | -61.9354 | 0.041199 | -62.2421 | 60.1364 | 62.2192 | 62.178 | 0.045776 | -0.11322 | 0.052338 | 0.27878 | -0.14633 | -0.18372 | 0.027466 | 0.068665 | -62.3611 | 60.0677 | 60.0952 | 62.2192 | 62.3749 | 122.4884 | 62.2101 | 60.1776
3751.4844 | 0.061035 | 0.40695 | -0.76797 | -0.23498 | 0.12283 | -0.27985 | -0.1976 | 60.2005 | -61.9812 | 0.032043 | -62.2604 | 60.173 | 62.1964 | 62.178 | 0.061035 | -0.10468 | 0.045929 | 0.27237 | -0.16769 | -0.16876 | 0.018311 | 0.064087 | -62.4023 | 60.0952 | 60.1227 | 62.2192 | 62.3566 | 122.493 | 62.1918 | 60.2005
3753.1562 | 0.076294 | 0.37918 | -0.76477 | -0.22537 | 0.11856 | -0.24887 | -0.18478 | 60.1822 | -62.0499 | -0.032043 | -62.2925 | 60.2234 | 62.2147 | 62.1964 | 0.045776 | -0.086517 | 0.049133 | 0.28412 | -0.12497 | -0.17731 | -0.086975 | -0.068665 | -62.4985 | 60.1547 | 60.1639 | 62.2375 | 62.3566 | 122.4976 | 62.1872 | 60.2142
3754.8281 | 0.045776 | 0.38986 | -0.77225 | -0.26596 | 0.1239 | -0.27557 | -0.17838 | 60.1593 | -62.027 | 0.064087 | -62.2879 | 60.1959 | 62.2284 | 62.2284 | 0.045776 | -0.1004 | 0.066223 | 0.28305 | -0.16876 | -0.17731 | 0.045776 | 0.11902 | -62.4481 | 60.1959 | 60.1547 | 62.233 | 62.3291 | 122.58 | 62.1506 | 60.2097
3756.5 | 0.045776 | 0.41122 | -0.77331 | -0.22537 | 0.11429 | -0.2713 | -0.18051 | 60.2371 | -61.972 | 0.022888 | -62.2375 | 60.2097 | 62.2147 | 62.1689 | 0.061035 | -0.095062 | 0.050201 | 0.28519 | -0.1442 | -0.18158 | 0.013733 | 0.027466 | -62.3795 | 60.0952 | 60.0952 | 62.2375 | 62.3703 | 122.5388 | 62.2101 | 60.1868
3758.1719 | 0.061035 | 0.39307 | -0.77438 | -0.24994 | 0.12176 | -0.25421 | -0.18051 | 60.1822 | -62.0499 | 0.032043 | -62.2742 | 60.2325 | 62.2055 | 62.2009 | 0.061035 | -0.091858 | 0.05661 | 0.28519 | -0.1506 | -0.18585 | 0.027466 | 0.086975 | -62.4252 | 60.1822 | 60.1868 | 62.2192 | 62.3703 | 122.6349 | 62.1506 | 60.1913
3759.875 | 0.061035 | 0.38345 | -0.77438 | -0.21683 | 0.11856 | -0.25207 | -0.1709 | 60.2142 | -62.0041 | 0.009155 | -62.2787 | 60.2509 | 62.2009 | 62.1689 | 0.045776 | -0.087585 | 0.054474 | 0.27664 | -0.12711 | -0.18585 | -0.045776 | -0.018311 | -62.4756 | 60.1364 | 60.1364 | 62.2284 | 62.3611 | 122.493 | 62.178 | 60.2051
3761.5469 | 0.061035 | 0.38986 | -0.77545 | -0.25421 | 0.1207 | -0.29266 | -0.19226 | 60.2142 | -61.9125 | 0.17853 | -62.2192 | 60.1456 | 62.1964 | 62.1643 | 0.045776 | -0.11856 | 0.05661 | 0.28305 | -0.16663 | -0.17838 | 0.11444 | 0.24261 | -62.352 | 60.1135 | 60.0861 | 62.2055 | 62.3291 | 122.5845 | 62.1506 | 60.1822
3763.2188 | 0.061035 | 0.41657 | -0.77972 | -0.2243 | 0.12497 | -0.28946 | -0.18906 | 60.1868 | -61.9812 | 0.036621 | -62.2833 | 60.1639 | 62.1872 | 62.178 | 0.030518 | -0.11536 | 0.050201 | 0.27878 | -0.16876 | -0.17197 | 0.022888 | 0.082397 | -62.4069 | 60.0998 | 60.1227 | 62.2055 | 62.3566 | 122.493 | 62.1964 | 60.1913
3764.9062 | 0.015259 | 0.39841 | -0.77972 | -0.24567 | 0.13351 | -0.26596 | -0.19119 | 60.2005 | -61.9812 | 0.11902 | -62.2467 | 60.2188 | 62.1964 | 62.2009 | 0.061035 | -0.10361 | 0.053406 | 0.29159 | -0.16983 | -0.18051 | 0.054932 | 0.1236 | -62.4298 | 60.1685 | 60.1364 | 62.2513 | 62.3657 | 122.5983 | 62.1414 | 60.2051
3766.5781 | 0.061035 | 0.40482 | -0.78507 | -0.21576 | 0.12176 | -0.26062 | -0.17838 | 60.2417 | -61.9629 | 0.045776 | -62.2467 | 60.173 | 62.2101 | 62.1552 | 0.061035 | -0.11536 | 0.046997 | 0.26916 | -0.14206 | -0.18478 | 0.027466 | 0.064087 | -62.3749 | 60.0632 | 60.0998 | 62.2238 | 62.3291 | 122.5021 | 62.2192 | 60.1822
3768.25 | 0.061035 | 0.38773 | -0.78507 | -0.23071 | 0.12176 | -0.24887 | -0.1944 | 60.1776 | -62.0819 | -0.054932 | -62.3062 | 60.2325 | 62.2192 | 62.1964 | 0.076294 | -0.1004 | 0.052338 | 0.28625 | -0.13138 | -0.18265 | -0.082397 | -0.11902 | -62.4939 | 60.173 | 60.1318 | 62.2284 | 62.3657 | 122.5159 | 62.1918 | 60.2097
3769.9219 | 0.030518 | 0.3952 | -0.76691 | -0.26169 | 0.11215 | -0.29587 | -0.1944 | 60.228 | -61.9217 | 0.16479 | -62.2101 | 60.1822 | 62.178 | 62.1689 | 0.045776 | -0.11322 | 0.054474 | 0.2713 | -0.15915 | -0.18051 | 0.11444 | 0.23346 | -62.3566 | 60.1227 | 60.1181 | 62.2147 | 62.3474 | 122.58 | 62.1506 | 60.2142
3771.625 | 0.061035 | 0.392 | -0.77866 | -0.22537 | 0.11749 | -0.24033 | -0.17838 | 60.173 | -62.0865 | -0.073242 | -62.3062 | 60.2692 | 62.2009 | 62.1918 | 0.061035 | -0.089722 | 0.046997 | 0.28732 | -0.1442 | -0.17517 | -0.086975 | -0.091553 | -62.471 | 60.1547 | 60.1685 | 62.2421 | 62.3611 | 122.4884 | 62.1918 | 60.2051
3773.3125 | 0.045776 | 0.40802 | -0.77972 | -0.2211 | 0.12924 | -0.24887 | -0.18372 | 60.1776 | -62.0453 | -0.073242 | -62.2925 | 60.2325 | 62.1918 | 62.2009 | 0.076294 | -0.097198 | 0.053406 | 0.29159 | -0.14633 | -0.18051 | -0.054932 | -0.054932 | -62.4435 | 60.1318 | 60.1181 | 62.2147 | 62.384 | 122.5479 | 62.1918 | 60.1822
3774.9844 | 0.045776 | 0.40268 | -0.77438 | -0.24887 | 0.12176 | -0.27985 | -0.19119 | 60.1685 | -62.027 | 0.086975 | -62.2696 | 60.2142 | 62.1826 | 62.1918 | 0.076294 | -0.10254 | 0.067291 | 0.28305 | -0.15488 | -0.16876 | 0.045776 | 0.13733 | -62.4435 | 60.1685 | 60.173 | 62.2147 | 62.3566 | 122.58 | 62.1689 | 60.1959
3776.6719 | 0.030518 | 0.3952 | -0.78507 | -0.24887 | 0.11963 | -0.27771 | -0.19226 | 60.1593 | -62.0361 | 0.050354 | -62.2879 | 60.2692 | 62.1918 | 62.178 | 0.061035 | -0.10361 | 0.058746 | 0.28091 | -0.1709 | -0.17731 | 0.018311 | 0.11444 | -62.4435 | 60.1822 | 60.1868 | 62.233 | 62.3703 | 122.5891 | 62.146 | 60.1822
3778.3594 | 0.045776 | 0.3952 | -0.78293 | -0.25528 | 0.12176 | -0.27344 | -0.19333 | 60.1776 | -61.9995 | 0.091553 | -62.2787 | 60.2371 | 62.2238 | 62.1689 | 0.030518 | -0.11856 | 0.059814 | 0.27878 | -0.16235 | -0.1741 | 0.036621 | 0.12817 | -62.4298 | 60.1593 | 60.1456 | 62.2467 | 62.3474 | 122.58 | 62.1689 | 60.1776
3780.0156 | 0.030518 | 0.3952 | -0.77972 | -0.23392 | 0.11643 | -0.26596 | -0.17838 | 60.228 | -61.9492 | 0.045776 | -62.2238 | 60.1593 | 62.2009 | 62.1643 | 0.045776 | -0.10468 | 0.044861 | 0.27664 | -0.13672 | -0.17838 | 0.013733 | 0.045776 | -62.3611 | 60.0815 | 60.0998 | 62.233 | 62.3474 | 122.5204 | 62.2101 | 60.173
3781.6875 | 0.045776 | 0.38879 | -0.76797 | -0.22964 | 0.11643 | -0.25742 | -0.16983 | 60.1913 | -62.0224 | -0.036621 | -62.2787 | 60.2142 | 62.2009 | 62.1964 | 0.045776 | -0.099335 | 0.03952 | 0.28412 | -0.14313 | -0.18372 | -0.032043 | -0.022888 | -62.4069 | 60.0998 | 60.0906 | 62.2101 | 62.3383 | 122.5204 | 62.2192 | 60.2051
3783.4062 | 0.045776 | 0.392 | -0.78079 | -0.26489 | 0.1239 | -0.28839 | -0.1944 | 60.2417 | -61.8988 | 0.16479 | -62.2238 | 60.1685 | 62.1964 | 62.1506 | 0.045776 | -0.11108 | 0.050201 | 0.27771 | -0.16983 | -0.16983 | 0.14648 | 0.26093 | -62.3428 | 60.0815 | 60.1227 | 62.178 | 62.3383 | 122.5708 | 62.1643 | 60.1685
3785.0781 | 0.030518 | 0.39414 | -0.77652 | -0.22751 | 0.11429 | -0.24567 | -0.18158 | 60.1913 | -62.0682 | -0.027466 | -62.2925 | 60.2371 | 62.2238 | 62.1735 | 0.045776 | -0.09079 | 0.05127 | 0.28732 | -0.13245 | -0.18585 | -0.091553 | -0.059509 | -62.4847 | 60.1868 | 60.1456 | 62.2421 | 62.3657 | 122.4838 | 62.1826 | 60.2463
3786.75 | 0.091553 | 0.40588 | -0.77438 | -0.24994 | 0.1207 | -0.28839 | -0.19012 | 60.2234 | -61.8988 | 0.16937 | -62.2238 | 60.1868 | 62.1735 | 62.1231 | 0.045776 | -0.12283 | 0.05127 | 0.27344 | -0.1709 | -0.18051 | 0.13733 | 0.23804 | -62.3291 | 60.0998 | 60.1089 | 62.1964 | 62.352 | 122.6028 | 62.1368 | 60.1593
3788.4844 | 0.045776 | 0.40054 | -0.78507 | -0.25742 | 0.11536 | -0.27344 | -0.19012 | 60.2371 | -61.94 | 0.16022 | -62.2238 | 60.1776 | 62.1872 | 62.1689 | 0.045776 | -0.11108 | 0.061951 | 0.2713 | -0.16342 | -0.18906 | 0.1236 | 0.23804 | -62.3611 | 60.1318 | 60.1089 | 62.2055 | 62.3611 | 122.58 | 62.146 | 60.2097
3790.1562 | 0.076294 | 0.40268 | -0.77866 | -0.21149 | 0.12711 | -0.26703 | -0.19546 | 60.2417 | -61.972 | 0.054932 | -62.2421 | 60.1501 | 62.2192 | 62.1689 | 0.030518 | -0.10147 | 0.049133 | 0.28412 | -0.1442 | -0.18906 | 0.036621 | 0.07782 | -62.3566 | 60.0952 | 60.1089 | 62.2009 | 62.352 | 122.4838 | 62.2238 | 60.1913
3791.8281 | 0.045776 | 0.40588 | -0.77438 | -0.23605 | 0.12176 | -0.27985 | -0.18478 | 60.1913 | -61.972 | 0.050354 | -62.2696 | 60.1364 | 62.2238 | 62.178 | 0.045776 | -0.11429 | 0.05127 | 0.27985 | -0.16235 | -0.17303 | 0.009155 | 0.086975 | -62.3978 | 60.0815 | 60.0677 | 62.2238 | 62.3611 | 122.4792 | 62.2238 | 60.2051
3793.5312 | 0.045776 | 0.40588 | -0.77866 | -0.23498 | 0.12604 | -0.26382 | -0.18906 | 60.228 | -61.9492 | 0.050354 | -62.2559 | 60.1822 | 62.2147 | 62.178 | 0.076294 | -0.10788 | 0.05661 | 0.27664 | -0.15274 | -0.18265 | 0.041199 | 0.068665 | -62.3886 | 60.0677 | 60.0586 | 62.2375 | 62.3795 | 122.4701 | 62.2192 | 60.1868
3795.2031 | 0.076294 | 0.38452 | -0.76477 | -0.22751 | 0.13245 | -0.23498 | -0.17517 | 60.1685 | -62.1094 | -0.064087 | -62.3154 | 60.26 | 62.2009 | 62.1964 | 0.030518 | -0.084381 | 0.05661 | 0.28305 | -0.12817 | -0.18372 | -0.064087 | -0.10529 | -62.4847 | 60.1639 | 60.1593 | 62.2467 | 62.3703 | 122.5067 | 62.2101 | 60.2051
3796.875 | 0.076294 | 0.39841 | -0.77759 | -0.22964 | 0.1239 | -0.2478 | -0.18051 | 60.2188 | -61.9995 | 0.059509 | -62.2375 | 60.26 | 62.2147 | 62.1964 | 0.030518 | -0.088654 | 0.059814 | 0.27664 | -0.14633 | -0.18692 | 0.041199 | 0.082397 | -62.439 | 60.173 | 60.1639 | 62.2147 | 62.3428 | 122.6074 | 62.1323 | 60.2188
3798.5469 | 0.030518 | 0.37491 | -0.76904 | -0.25207 | 0.11643 | -0.26703 | -0.18906 | 60.1685 | -62.0453 | 0.045776 | -62.2696 | 60.2371 | 62.2147 | 62.1872 | 0.045776 | -0.1004 | 0.066223 | 0.27878 | -0.15915 | -0.18051 | 0.022888 | 0.082397 | -62.4344 | 60.1868 | 60.1593 | 62.2101 | 62.3566 | 122.6349 | 62.1414 | 60.1822
3800.2031 | 0.061035 | 0.42084 | -0.77652 | -0.23071 | 0.11856 | -0.29266 | -0.19226 | 60.1639 | -61.9904 | 0.032043 | -62.2696 | 60.1547 | 62.2009 | 62.1826 | 0.045776 | -0.11429 | 0.045929 | 0.28625 | -0.14954 | -0.1741 | 0.022888 | 0.086975 | -62.3932 | 60.0723 | 60.1135 | 62.2192 | 62.3703 | 122.5067 | 62.1735 | 60.1868
3801.875 | 0.045776 | 0.37598 | -0.77438 | -0.23178 | 0.12711 | -0.2446 | -0.18265 | 60.1685 | -62.0865 | -0.054932 | -62.3016 | 60.26 | 62.2192 | 62.1735 | 0.030518 | -0.091858 | 0.054474 | 0.27344 | -0.13779 | -0.18478 | -0.082397 | -0.073242 | -62.4939 | 60.1364 | 60.173 | 62.2238 | 62.3703 | 122.4976 | 62.1826 | 60.2142
3803.5469 | 0.061035 | 0.38238 | -0.77011 | -0.26276 | 0.12283 | -0.26596 | -0.18906 | 60.1822 | -62.0316 | 0.045776 | -62.2513 | 60.2463 | 62.2009 | 62.178 | 0.030518 | -0.091858 | 0.054474 | 0.27771 | -0.15381 | -0.17838 | 0.022888 | 0.091553 | -62.4344 | 60.1959 | 60.1685 | 62.2009 | 62.3428 | 122.6349 | 62.1414 | 60.1776
3805.2344 | 0.045776 | 0.40054 | -0.77972 | -0.25101 | 0.1207 | -0.29373 | -0.19333 | 60.2142 | -61.9125 | 0.1236 | -62.2147 | 60.1685 | 62.1826 | 62.1506 | 0.045776 | -0.13245 | 0.067291 | 0.27985 | -0.18265 | -0.17197 | 0.12817 | 0.23346 | -62.3199 | 60.1135 | 60.0861 | 62.2055 | 62.352 | 122.612 | 62.1506 | 60.173
3806.9688 | 0.061035 | 0.39734 | -0.77972 | -0.23285 | 0.12176 | -0.27451 | -0.18692 | 60.2325 | -61.908 | 0.16022 | -62.2101 | 60.1776 | 62.1735 | 62.1643 | 0.061035 | -0.12497 | 0.043793 | 0.27771 | -0.15595 | -0.18372 | 0.13275 | 0.26093 | -62.3428 | 60.1273 | 60.0906 | 62.233 | 62.3291 | 122.5708 | 62.1414 | 60.173
3808.6406 | 0.045776 | 0.43366 | -0.79041 | -0.21362 | 0.12604 | -0.26062 | -0.18906 | 60.2005 | -61.972 | 0.022888 | -62.265 | 60.173 | 62.1964 | 62.178 | 0.030518 | -0.10788 | 0.041656 | 0.27771 | -0.1442 | -0.18372 | 0.032043 | 0.07782 | -62.3795 | 60.0998 | 60.1044 | 62.2284 | 62.3474 | 122.4838 | 62.1918 | 60.1868
3810.3125 | 0.030518 | 0.38025 | -0.77545 | -0.22751 | 0.11322 | -0.23392 | -0.17731 | 60.1639 | -62.1094 | -0.054932 | -62.3108 | 60.2509 | 62.2101 | 62.2055 | 0.045776 | -0.087585 | 0.053406 | 0.29159 | -0.13886 | -0.19119 | -0.086975 | -0.10986 | -62.4756 | 60.1456 | 60.1685 | 62.2147 | 62.3749 | 122.4976 | 62.2009 | 60.2051
3811.9844 | 0.045776 | 0.39627 | -0.77225 | -0.24246 | 0.10468 | -0.29053 | -0.18799 | 60.1776 | -61.9949 | 0.041199 | -62.2787 | 60.1685 | 62.1872 | 62.1826 | 0.061035 | -0.11963 | 0.058746 | 0.28412 | -0.16129 | -0.17838 | 0.013733 | 0.068665 | -62.4023 | 60.0861 | 60.0998 | 62.2147 | 62.3703 | 122.5021 | 62.2009 | 60.1959
3813.6562 | 0.045776 | 0.38345 | -0.77438 | -0.22644 | 0.1239 | -0.23819 | -0.17624 | 60.2097 | -62.027 | 0.004578 | -62.265 | 60.2509 | 62.1826 | 62.1826 | 0.045776 | -0.09079 | 0.040588 | 0.28091 | -0.12497 | -0.19012 | -0.050354 | -0.036621 | -62.4802 | 60.1776 | 60.1501 | 62.2284 | 62.3703 | 122.4747 | 62.2101 | 60.2097
3815.3594 | 0.045776 | 0.39093 | -0.76691 | -0.22751 | 0.12711 | -0.25101 | -0.17624 | 60.1868 | -62.0544 | -0.045776 | -62.2879 | 60.2188 | 62.1872 | 62.178 | 0.045776 | -0.10254 | 0.060883 | 0.29053 | -0.14099 | -0.17624 | -0.045776 | -0.041199 | -62.4344 | 60.1273 | 60.1181 | 62.2375 | 62.3428 | 122.5204 | 62.2055 | 60.1959
3817.0312 | 0.061035 | 0.37918 | -0.77225 | -0.23071 | 0.10895 | -0.24994 | -0.18051 | 60.1547 | -62.0865 | -0.041199 | -62.3016 | 60.2417 | 62.2238 | 62.1964 | 0.030518 | -0.087585 | 0.052338 | 0.29053 | -0.13031 | -0.18372 | -0.086975 | -0.082397 | -62.4985 | 60.1456 | 60.1593 | 62.2375 | 62.3657 | 122.5021 | 62.1964 | 60.2051
3818.6875 | 0.045776 | 0.39841 | -0.77759 | -0.25314 | 0.12817 | -0.30014 | -0.18692 | 60.2051 | -61.9125 | 0.1236 | -62.2284 | 60.1822 | 62.1918 | 62.1735 | 0.061035 | -0.11749 | 0.057678 | 0.27771 | -0.16983 | -0.17517 | 0.12817 | 0.22888 | -62.3245 | 60.0815 | 60.0906 | 62.2192 | 62.352 | 122.5937 | 62.1506 | 60.1639
3820.4062 | 0.030518 | 0.39093 | -0.77331 | -0.25207 | 0.11856 | -0.2713 | -0.19012 | 60.1868 | -62.0041 | 0.10071 | -62.2604 | 60.228 | 62.1918 | 62.178 | 0.061035 | -0.093994 | 0.066223 | 0.29694 | -0.16235 | -0.16876 | 0.041199 | 0.13275 | -62.4435 | 60.1547 | 60.1685 | 62.2513 | 62.352 | 122.5616 | 62.1506 | 60.2142
3822.0781 | 0.045776 | 0.4155 | -0.78827 | -0.21683 | 0.11215 | -0.27771 | -0.19226 | 60.2005 | -61.9766 | 0.041199 | -62.2833 | 60.173 | 62.2055 | 62.1689 | 0.061035 | -0.1207 | 0.029907 | 0.27237 | -0.15167 | -0.17731 | 0.027466 | 0.073242 | -62.4069 | 60.1089 | 60.0906 | 62.2284 | 62.3795 | 122.4976 | 62.1872 | 60.1822
3823.75 | 0.061035 | 0.39414 | -0.77118 | -0.21255 | 0.12283 | -0.25421 | -0.18799 | 60.2188 | -62.0178 | -0.022888 | -62.2696 | 60.2142 | 62.2009 | 62.2055 | 0.045776 | -0.11215 | 0.03952 | 0.27771 | -0.13565 | -0.17624 | 0.009155 | 0.018311 | -62.3749 | 60.0952 | 60.0998 | 62.1964 | 62.3291 | 122.5479 | 62.1872 | 60.1822
3825.4844 | 0.061035 | 0.39841 | -0.77438 | -0.23498 | 0.10895 | -0.27237 | -0.18692 | 60.2097 | -61.9812 | 0.041199 | -62.2742 | 60.1639 | 62.1964 | 62.1597 | 0.045776 | -0.10468 | 0.054474 | 0.27344 | -0.16663 | -0.16769 | 0.027466 | 0.059509 | -62.3795 | 60.0952 | 60.1089 | 62.2147 | 62.3749 | 122.4838 | 62.2238 | 60.2005
3827.1562 | 0.045776 | 0.38345 | -0.784 | -0.21896 | 0.12711 | -0.23498 | -0.18478 | 60.2234 | -62.027 | 0 | -62.2833 | 60.2509 | 62.2238 | 62.1918 | 0.061035 | -0.10574 | 0.05127 | 0.28091 | -0.13779 | -0.18906 | -0.064087 | -0.032043 | -62.4847 | 60.1501 | 60.1501 | 62.2238 | 62.352 | 122.4976 | 62.2009 | 60.2051
3828.8438 | 0.091553 | 0.38559 | -0.76904 | -0.24353 | 0.11856 | -0.25101 | -0.18585 | 60.228 | -61.9904 | 0.045776 | -62.2604 | 60.228 | 62.1918 | 62.1826 | 0.030518 | -0.098267 | 0.066223 | 0.28946 | -0.14526 | -0.18692 | 0 | 0.004578 | -62.439 | 60.1456 | 60.1456 | 62.2192 | 62.3474 | 122.5021 | 62.1597 | 60.2371
3830.5312 | 0.061035 | 0.40482 | -0.77759 | -0.22217 | 0.1239 | -0.27557 | -0.18478 | 60.2005 | -61.9446 | 0.059509 | -62.2284 | 60.1364 | 62.2147 | 62.1735 | 0.030518 | -0.11002 | 0.042725 | 0.27237 | -0.15915 | -0.18478 | 0.036621 | 0.082397 | -62.3566 | 60.0723 | 60.0998 | 62.2238 | 62.3428 | 122.4976 | 62.1872 | 60.2188
3832.2031 | 0.045776 | 0.41122 | -0.77972 | -0.23392 | 0.12283 | -0.27557 | -0.18372 | 60.2417 | -61.9675 | 0.032043 | -62.233 | 60.1685 | 62.178 | 62.178 | 0.061035 | -0.10788 | 0.03952 | 0.28946 | -0.14954 | -0.18692 | 0.013733 | 0.064087 | -62.3566 | 60.0632 | 60.0906 | 62.2284 | 62.3337 | 122.5296 | 62.1964 | 60.173
3833.875 | 0 | 0.38345 | -0.77652 | -0.26703 | 0.12176 | -0.25742 | -0.18906 | 60.1593 | -62.0316 | 0.054932 | -62.2696 | 60.2646 | 62.178 | 62.1918 | 0.061035 | -0.099335 | 0.066223 | 0.29266 | -0.16022 | -0.17944 | 0.022888 | 0.082397 | -62.4527 | 60.1776 | 60.1639 | 62.2421 | 62.3611 | 122.612 | 62.1323 | 60.173
3835.5625 | 0.061035 | 0.40268 | -0.78507 | -0.24353 | 0.1207 | -0.27878 | -0.18158 | 60.1868 | -61.972 | 0.050354 | -62.265 | 60.1639 | 62.1964 | 62.1597 | 0.061035 | -0.12711 | 0.060883 | 0.27878 | -0.16022 | -0.16876 | 0.032043 | 0.082397 | -62.3932 | 60.1044 | 60.0723 | 62.2238 | 62.3703 | 122.4792 | 62.2055 | 60.1868
3837.2344 | 0.061035 | 0.41229 | -0.77652 | -0.2243 | 0.11749 | -0.26276 | -0.18478 | 60.2325 | -61.9446 | 0.036621 | -62.233 | 60.1685 | 62.2009 | 62.1597 | 0.061035 | -0.10147 | 0.03952 | 0.27557 | -0.14954 | -0.18692 | 0.018311 | 0.045776 | -62.3703 | 60.0861 | 60.0677 | 62.233 | 62.3291 | 122.5159 | 62.1826 | 60.1959
3838.9062 | 0.061035 | 0.40695 | -0.78507 | -0.22324 | 0.1207 | -0.26916 | -0.18051 | 60.228 | -61.9446 | 0.041199 | -62.2375 | 60.1685 | 62.1735 | 62.178 | 0.030518 | -0.11322 | 0.036316 | 0.27771 | -0.14206 | -0.17624 | 0.036621 | 0.073242 | -62.3749 | 60.0723 | 60.0906 | 62.233 | 62.3749 | 122.4747 | 62.2009 | 60.2188
3840.5781 | 0.076294 | 0.38986 | -0.76691 | -0.23498 | 0.13458 | -0.25528 | -0.18158 | 60.1868 | -62.0407 | -0.059509 | -62.2925 | 60.2509 | 62.1872 | 62.1735 | 0.045776 | -0.1004 | 0.054474 | 0.27878 | -0.13458 | -0.18158 | -0.050354 | -0.068665 | -62.4435 | 60.1364 | 60.1501 | 62.2467 | 62.3566 | 122.5296 | 62.2101 | 60.2142
3842.25 | 0.061035 | 0.38986 | -0.76904 | -0.22644 | 0.11429 | -0.23605 | -0.18158 | 60.2097 | -62.0087 | 0.027466 | -62.265 | 60.2005 | 62.2055 | 62.1735 | 0.076294 | -0.09613 | 0.05661 | 0.28305 | -0.13779 | -0.19333 | -0.041199 | -0.018311 | -62.4664 | 60.1456 | 60.1639 | 62.2421 | 62.3703 | 122.4884 | 62.1918 | 60.2097
3843.9062 | 0.045776 | 0.40695 | -0.78293 | -0.24994 | 0.10895 | -0.29587 | -0.19653 | 60.1959 | -61.9171 | 0.12817 | -62.2238 | 60.1639 | 62.178 | 62.1735 | 0.061035 | -0.1207 | 0.055542 | 0.28091 | -0.16022 | -0.18265 | 0.12817 | 0.22888 | -62.3154 | 60.0861 | 60.0677 | 62.2238 | 62.3337 | 122.6166 | 62.146 | 60.141
3845.5938 | 0.061035 | 0.40482 | -0.77545 | -0.23285 | 0.12924 | -0.25314 | -0.18372 | 60.2051 | -61.9629 | 0.022888 | -62.233 | 60.1868 | 62.1826 | 62.1964 | 0.045776 | -0.10254 | 0.050201 | 0.27771 | -0.13245 | -0.19226 | 0.009155 | 0.036621 | -62.3566 | 60.0952 | 60.0494 | 62.2101 | 62.3337 | 122.525 | 62.1872 | 60.1868
3847.2656 | 0.061035 | 0.38238 | -0.77011 | -0.23926 | 0.12604 | -0.24353 | -0.17838 | 60.2417 | -61.972 | 0.054932 | -62.2421 | 60.2554 | 62.1826 | 62.178 | 0.045776 | -0.089722 | 0.053406 | 0.28198 | -0.13992 | -0.19226 | 0.027466 | 0.041199 | -62.4161 | 60.1547 | 60.1593 | 62.2101 | 62.3703 | 122.5708 | 62.1368 | 60.2005
3848.9688 | 0.045776 | 0.38452 | -0.77118 | -0.25421 | 0.13351 | -0.25528 | -0.19012 | 60.1639 | -62.0407 | 0.050354 | -62.2559 | 60.2234 | 62.2192 | 62.1872 | 0.045776 | -0.099335 | 0.05661 | 0.28305 | -0.15595 | -0.19012 | 0.013733 | 0.10071 | -62.4161 | 60.1685 | 60.1822 | 62.2238 | 62.3428 | 122.6257 | 62.1185 | 60.173
3850.6406 | 0.030518 | 0.4155 | -0.77972 | -0.22964 | 0.11536 | -0.28732 | -0.1944 | 60.141 | -61.9858 | 0.027466 | -62.2696 | 60.1547 | 62.1964 | 62.1918 | 0.076294 | -0.12283 | 0.048065 | 0.27237 | -0.16342 | -0.16556 | 0.022888 | 0.09613 | -62.3932 | 60.0906 | 60.0632 | 62.2375 | 62.3611 | 122.5067 | 62.1918 | 60.1913
3852.3125 | 0.076294 | 0.38238 | -0.77438 | -0.22964 | 0.11963 | -0.23498 | -0.18372 | 60.1685 | -62.059 | -0.064087 | -62.2787 | 60.2371 | 62.1918 | 62.1918 | 0.045776 | -0.086517 | 0.050201 | 0.28412 | -0.14313 | -0.19119 | -0.082397 | -0.07782 | -62.471 | 60.1685 | 60.141 | 62.233 | 62.3428 | 122.5296 | 62.2055 | 60.2005
3853.9844 | 0.045776 | 0.41229 | -0.77545 | -0.24994 | 0.1239 | -0.29587 | -0.18051 | 60.1364 | -61.9904 | 0.045776 | -62.2604 | 60.1639 | 62.1964 | 62.2055 | 0.076294 | -0.12176 | 0.057678 | 0.27985 | -0.1741 | -0.17838 | 0.009155 | 0.10986 | -62.3886 | 60.0906 | 60.0952 | 62.2421 | 62.3611 | 122.5159 | 62.178 | 60.1868
3855.6562 | 0.045776 | 0.38666 | -0.7637 | -0.22537 | 0.10681 | -0.25421 | -0.18585 | 60.2417 | -61.9904 | 0.045776 | -62.2421 | 60.228 | 62.1964 | 62.1506 | 0.045776 | -0.088654 | 0.053406 | 0.28519 | -0.1239 | -0.18372 | -0.004578 | 0.018311 | -62.4252 | 60.1318 | 60.141 | 62.2238 | 62.3428 | 122.4976 | 62.1506 | 60.2051
3857.3281 | 0.030518 | 0.37598 | -0.77866 | -0.26062 | 0.13565 | -0.26276 | -0.18158 | 60.1456 | -62.0453 | 0.050354 | -62.2833 | 60.2509 | 62.2101 | 62.1826 | 0.061035 | -0.10895 | 0.064087 | 0.27557 | -0.15595 | -0.18158 | 0.027466 | 0.082397 | -62.4573 | 60.1868 | 60.1547 | 62.2192 | 62.3383 | 122.6074 | 62.1185 | 60.1593
3859 | 0.045776 | 0.40161 | -0.78507 | -0.25101 | 0.11536 | -0.28625 | -0.18906 | 60.1593 | -61.9675 | 0.041199 | -62.2604 | 60.1501 | 62.2009 | 62.1552 | 0.030518 | -0.11215 | 0.050201 | 0.28412 | -0.16876 | -0.16663 | 0.013733 | 0.086975 | -62.3932 | 60.0952 | 60.0723 | 62.233 | 62.3474 | 122.4655 | 62.1826 | 60.173
3860.6719 | 0.045776 | 0.39627 | -0.77438 | -0.2179 | 0.1207 | -0.24353 | -0.17944 | 60.2188 | -61.9949 | 0.045776 | -62.2604 | 60.228 | 62.1918 | 62.1735 | 0.076294 | -0.087585 | 0.05127 | 0.28198 | -0.13245 | -0.19012 | -0.013733 | 0.009155 | -62.4435 | 60.1547 | 60.1318 | 62.2238 | 62.3337 | 122.5021 | 62.1689 | 60.2005
3862.3438 | 0.061035 | 0.38025 | -0.77225 | -0.24674 | 0.12176 | -0.25955 | -0.18585 | 60.1913 | -61.9995 | 0.054932 | -62.2238 | 60.2646 | 62.2147 | 62.2009 | 0.045776 | -0.10468 | 0.044861 | 0.27664 | -0.15274 | -0.18906 | 0.032043 | 0.086975 | -62.4023 | 60.1547 | 60.1593 | 62.2284 | 62.3703 | 122.5937 | 62.1231 | 60.1868
3864 | 0.045776 | 0.42191 | -0.78079 | -0.22003 | 0.10254 | -0.2713 | -0.18051 | 60.1913 | -61.9308 | 0.045776 | -62.2467 | 60.1089 | 62.1872 | 62.1735 | 0.045776 | -0.11749 | 0.05127 | 0.27771 | -0.15274 | -0.18158 | 0.022888 | 0.082397 | -62.3703 | 60.0952 | 60.0769 | 62.2375 | 62.3703 | 122.4838 | 62.1964 | 60.1959
3865.6875 | 0.045776 | 0.38879 | -0.77118 | -0.24139 | 0.12176 | -0.2478 | -0.18478 | 60.2234 | -61.9675 | 0.073242 | -62.233 | 60.228 | 62.1964 | 62.1735 | 0.061035 | -0.082245 | 0.061951 | 0.29266 | -0.13565 | -0.1741 | 0.036621 | 0.064087 | -62.4115 | 60.1639 | 60.1501 | 62.1964 | 62.3428 | 122.5662 | 62.1277 | 60.1868
3867.4375 | 0.030518 | 0.3952 | -0.76157 | -0.22858 | 0.11536 | -0.26169 | -0.17624 | 60.1593 | -62.0407 | -0.045776 | -62.2971 | 60.2005 | 62.1964 | 62.1918 | 0.045776 | -0.10468 | 0.049133 | 0.28732 | -0.13672 | -0.17303 | -0.036621 | -0.018311 | -62.4161 | 60.1181 | 60.1135 | 62.2192 | 62.3383 | 122.5296 | 62.1826 | 60.1685
3869.1094 | 0.045776 | 0.38132 | -0.77331 | -0.23285 | 0.11643 | -0.24994 | -0.18478 | 60.1959 | -62.0178 | -0.009155 | -62.265 | 60.228 | 62.1964 | 62.2009 | 0.061035 | -0.09613 | 0.046997 | 0.28946 | -0.12817 | -0.1741 | -0.073242 | -0.027466 | -62.471 | 60.1547 | 60.141 | 62.2192 | 62.3749 | 122.4838 | 62.1872 | 60.228
3870.8125 | 0.045776 | 0.37918 | -0.77866 | -0.22644 | 0.11643 | -0.24887 | -0.17838 | 60.1364 | -62.0636 | -0.07782 | -62.2971 | 60.2417 | 62.2192 | 62.2009 | 0.045776 | -0.099335 | 0.043793 | 0.29266 | -0.14206 | -0.16983 | -0.086975 | -0.091553 | -62.4664 | 60.1593 | 60.1685 | 62.2101 | 62.352 | 122.5159 | 62.1918 | 60.2051
3872.5 | 0.045776 | 0.37598 | -0.77972 | -0.2478 | 0.12176 | -0.25421 | -0.17197 | 60.1318 | -62.0682 | -0.036621 | -62.2833 | 60.2417 | 62.178 | 62.1689 | 0.045776 | -0.097198 | 0.061951 | 0.27985 | -0.14099 | -0.17731 | -0.10986 | -0.068665 | -62.4893 | 60.141 | 60.1776 | 62.2192 | 62.4023 | 122.4518 | 62.1964 | 60.2051
3874.1719 | 0.045776 | 0.40054 | -0.78079 | -0.25207 | 0.1239 | -0.298 | -0.18478 | 60.2188 | -61.8942 | 0.17395 | -62.2009 | 60.1776 | 62.1643 | 62.146 | 0.045776 | -0.13138 | 0.064087 | 0.27878 | -0.16769 | -0.1709 | 0.11902 | 0.2655 | -62.3108 | 60.0861 | 60.0906 | 62.2284 | 62.3291 | 122.5891 | 62.146 | 60.1685
3875.8594 | 0.061035 | 0.38773 | -0.77545 | -0.22964 | 0.12176 | -0.25421 | -0.18478 | 60.1547 | -62.0316 | -0.036621 | -62.2742 | 60.2142 | 62.2192 | 62.1918 | 0.045776 | -0.10468 | 0.048065 | 0.27878 | -0.14206 | -0.17624 | -0.032043 | -0.013733 | -62.3978 | 60.1227 | 60.0861 | 62.2421 | 62.3749 | 122.5204 | 62.2009 | 60.1685
3877.5625 | 0.045776 | 0.3952 | -0.77118 | -0.22217 | 0.12497 | -0.26062 | -0.18158 | 60.1868 | -61.9858 | 0.013733 | -62.2513 | 60.1959 | 62.1918 | 62.1643 | 0.030518 | -0.10895 | 0.054474 | 0.27771 | -0.1442 | -0.17624 | 0 | 0.036621 | -62.3703 | 60.1044 | 60.0586 | 62.2147 | 62.352 | 122.5296 | 62.1964 | 60.1593
3879.25 | 0.030518 | 0.40268 | -0.78507 | -0.25101 | 0.11856 | -0.29159 | -0.19012 | 60.1959 | -61.9446 | 0.13733 | -62.2147 | 60.1868 | 62.1872 | 62.1552 | 0.076294 | -0.10468 | 0.052338 | 0.27985 | -0.16129 | -0.17944 | 0.07782 | 0.18768 | -62.384 | 60.1547 | 60.1639 | 62.1964 | 62.3474 | 122.5525 | 62.1323 | 60.1822
3880.9062 | 0.061035 | 0.41657 | -0.77438 | -0.24033 | 0.13138 | -0.2948 | -0.19867 | 60.1639 | -61.972 | 0.073242 | -62.2421 | 60.1959 | 62.1826 | 62.1735 | 0.061035 | -0.11749 | 0.057678 | 0.28305 | -0.16342 | -0.18692 | 0.07782 | 0.16479 | -62.3474 | 60.0952 | 60.1135 | 62.2101 | 62.3474 | 122.5845 | 62.1552 | 60.1273
3882.5781 | 0.061035 | 0.42297 | -0.78507 | -0.23712 | 0.10574 | -0.28732 | -0.19333 | 60.1685 | -61.9812 | 0.036621 | -62.2421 | 60.2142 | 62.1964 | 62.1643 | 0.061035 | -0.1239 | 0.046997 | 0.27664 | -0.16556 | -0.1741 | 0.073242 | 0.12817 | -62.3566 | 60.0998 | 60.1135 | 62.2192 | 62.3291 | 122.5754 | 62.1506 | 60.1547
3884.2344 | 0.030518 | 0.3952 | -0.78934 | -0.23712 | 0.11643 | -0.24674 | -0.17944 | 60.1913 | -62.0544 | -0.068665 | -62.2879 | 60.228 | 62.2009 | 62.1689 | 0.061035 | -0.088654 | 0.057678 | 0.29159 | -0.13779 | -0.18585 | -0.032043 | -0.050354 | -62.4252 | 60.1273 | 60.0861 | 62.233 | 62.3337 | 122.525 | 62.2009 | 60.173
3885.9062 | 0.045776 | 0.40054 | -0.78827 | -0.25528 | 0.12176 | -0.26169 | -0.19119 | 60.2097 | -61.9949 | 0.11444 | -62.2467 | 60.2142 | 62.178 | 62.1643 | 0.045776 | -0.11429 | 0.064087 | 0.27557 | -0.16235 | -0.18692 | 0.041199 | 0.12817 | -62.4252 | 60.1318 | 60.173 | 62.2009 | 62.3611 | 122.5525 | 62.1368 | 60.2142
3887.6094 | 0.045776 | 0.40482 | -0.77545 | -0.24887 | 0.1207 | -0.28625 | -0.18692 | 60.2463 | -61.9034 | 0.15564 | -62.2055 | 60.1822 | 62.178 | 62.1506 | 0.045776 | -0.12176 | 0.05127 | 0.27664 | -0.16342 | -0.18692 | 0.14191 | 0.24719 | -62.3154 | 60.0769 | 60.0952 | 62.2238 | 62.3291 | 122.5983 | 62.1414 | 60.1547
3889.2969 | 0.030518 | 0.40695 | -0.77545 | -0.22964 | 0.11322 | -0.2478 | -0.19012 | 60.1913 | -61.9995 | -0.027466 | -62.2879 | 60.2142 | 62.2101 | 62.1552 | 0.045776 | -0.098267 | 0.053406 | 0.28732 | -0.14526 | -0.18799 | -0.004578 | -0.004578 | -62.3886 | 60.0952 | 60.0723 | 62.2421 | 62.3428 | 122.5204 | 62.2055 | 60.1776
3890.9688 | 0.045776 | 0.39093 | -0.77972 | -0.22751 | 0.13779 | -0.24994 | -0.18158 | 60.1776 | -62.0544 | -0.073242 | -62.3016 | 60.2097 | 62.2101 | 62.1964 | 0.030518 | -0.092926 | 0.044861 | 0.298 | -0.14099 | -0.18585 | -0.073242 | -0.091553 | -62.4756 | 60.1547 | 60.1456 | 62.2238 | 62.3703 | 122.5159 | 62.1735 | 60.173
3892.6562 | 0.061035 | 0.39093 | -0.77331 | -0.25101 | 0.12283 | -0.28198 | -0.19226 | 60.1913 | -61.9492 | 0.13733 | -62.2238 | 60.2051 | 62.2009 | 62.1689 | 0.061035 | -0.10895 | 0.058746 | 0.28198 | -0.15701 | -0.17838 | 0.073242 | 0.17853 | -62.4069 | 60.1456 | 60.1501 | 62.2238 | 62.3337 | 122.5525 | 62.1597 | 60.2097
3894.375 | 0.061035 | 0.41657 | -0.77438 | -0.22217 | 0.12924 | -0.27344 | -0.18692 | 60.2188 | -61.9308 | 0.059509 | -62.2421 | 60.1547 | 62.1964 | 62.1689 | 0.076294 | -0.10788 | 0.042725 | 0.27664 | -0.15274 | -0.17517 | 0.041199 | 0.082397 | -62.3611 | 60.0586 | 60.0723 | 62.2192 | 62.3566 | 122.4655 | 62.1918 | 60.173
3896.0312 | 0.061035 | 0.37918 | -0.77545 | -0.24567 | 0.11643 | -0.2478 | -0.17838 | 60.1868 | -61.9858 | 0.059509 | -62.2375 | 60.2234 | 62.178 | 62.1643 | 0.045776 | -0.10361 | 0.059814 | 0.29159 | -0.1474 | -0.19226 | 0.032043 | 0.091553 | -62.3978 | 60.173 | 60.1593 | 62.1964 | 62.3245 | 122.6166 | 62.1277 | 60.1822
3897.7031 | 0.030518 | 0.39841 | -0.77118 | -0.2478 | 0.11963 | -0.28198 | -0.18799 | 60.1639 | -61.9766 | 0.041199 | -62.2696 | 60.1776 | 62.2009 | 62.1597 | 0.061035 | -0.12283 | 0.068359 | 0.29266 | -0.1741 | -0.18158 | 0.018311 | 0.086975 | -62.3703 | 60.0861 | 60.0952 | 62.2147 | 62.3474 | 122.4655 | 62.2147 | 60.1868
3899.4062 | 0.045776 | 0.37811 | -0.76477 | -0.23392 | 0.1239 | -0.23285 | -0.17624 | 60.1959 | -61.9812 | 0.018311 | -62.2696 | 60.2417 | 62.1735 | 62.1735 | 0.061035 | -0.088654 | 0.043793 | 0.28732 | -0.12924 | -0.18692 | -0.018311 | -0.018311 | -62.4619 | 60.1593 | 60.1227 | 62.2284 | 62.3611 | 122.4884 | 62.2009 | 60.1913
3901.0781 | 0.045776 | 0.41977 | -0.784 | -0.23605 | 0.11322 | -0.2948 | -0.18906 | 60.1135 | -61.9675 | 0.054932 | -62.2559 | 60.1776 | 62.178 | 62.178 | 0.045776 | -0.11856 | 0.042725 | 0.27878 | -0.16556 | -0.17838 | 0.054932 | 0.12817 | -62.352 | 60.0861 | 60.0723 | 62.1918 | 62.352 | 122.5571 | 62.1643 | 60.1593
3902.7656 | 0.061035 | 0.38879 | -0.76797 | -0.22751 | 0.12497 | -0.23819 | -0.16663 | 60.1822 | -62.027 | -0.022888 | -62.2742 | 60.228 | 62.2238 | 62.1872 | 0.015259 | -0.091858 | 0.046997 | 0.28305 | -0.12711 | -0.18372 | -0.068665 | -0.045776 | -62.4619 | 60.173 | 60.1547 | 62.2055 | 62.3795 | 122.4792 | 62.2192 | 60.2188
3904.4844 | 0.030518 | 0.38559 | -0.77011 | -0.24246 | 0.12176 | -0.25314 | -0.18478 | 60.2234 | -61.9492 | 0.054932 | -62.2421 | 60.228 | 62.1964 | 62.1826 | 0.045776 | -0.1004 | 0.054474 | 0.29266 | -0.13458 | -0.18799 | 0.013733 | 0.045776 | -62.4298 | 60.1318 | 60.1318 | 62.2238 | 62.3428 | 122.5067 | 62.1552 | 60.1913
3906.1562 | 0.030518 | 0.392 | -0.784 | -0.24139 | 0.12497 | -0.28732 | -0.17944 | 60.1822 | -61.9125 | 0.16022 | -62.2101 | 60.1959 | 62.1735 | 62.1552 | 0.061035 | -0.11002 | 0.05661 | 0.26916 | -0.15595 | -0.18478 | 0.07782 | 0.20142 | -62.3749 | 60.1547 | 60.1089 | 62.2467 | 62.3337 | 122.5616 | 62.1323 | 60.1776
3907.8438 | 0.045776 | 0.42191 | -0.78507 | -0.2211 | 0.11322 | -0.28946 | -0.18799 | 60.1547 | -61.9675 | 0.027466 | -62.2696 | 60.1593 | 62.2055 | 62.1964 | 0.045776 | -0.1207 | 0.037384 | 0.27344 | -0.15701 | -0.16342 | 0.022888 | 0.086975 | -62.3886 | 60.0998 | 60.0677 | 62.2009 | 62.3383 | 122.4747 | 62.2147 | 60.1776
3909.5156 | 0.045776 | 0.40054 | -0.77331 | -0.23285 | 0.12604 | -0.26596 | -0.18906 | 60.173 | -62.0361 | -0.050354 | -62.2833 | 60.228 | 62.2147 | 62.1872 | 0.061035 | -0.1004 | 0.049133 | 0.27878 | -0.13138 | -0.19012 | -0.041199 | -0.036621 | -62.4023 | 60.1181 | 60.1089 | 62.2238 | 62.3245 | 122.5204 | 62.1735 | 60.1547
3911.1875 | 0.061035 | 0.38773 | -0.76263 | -0.23712 | 0.11429 | -0.23926 | -0.18051 | 60.2005 | -62.0132 | 0.013733 | -62.2604 | 60.2142 | 62.1826 | 62.1643 | 0.045776 | -0.085449 | 0.05661 | 0.28946 | -0.13779 | -0.19653 | -0.059509 | -0.032043 | -62.4435 | 60.1685 | 60.1501 | 62.2284 | 62.3566 | 122.4792 | 62.2055 | 60.1959
3912.8594 | 0.045776 | 0.41229 | -0.77438 | -0.24567 | 0.11536 | -0.298 | -0.18051 | 60.141 | -61.9812 | 0.059509 | -62.2467 | 60.1593 | 62.2192 | 62.1735 | 0.030518 | -0.12924 | 0.049133 | 0.28198 | -0.16129 | -0.17197 | 0.059509 | 0.15106 | -62.3428 | 60.0861 | 60.0677 | 62.2238 | 62.3566 | 122.58 | 62.1368 | 60.1501
3914.5469 | 0.030518 | 0.39093 | -0.78079 | -0.23605 | 0.12176 | -0.24567 | -0.18051 | 60.1593 | -62.0773 | -0.068665 | -62.2971 | 60.2463 | 62.1964 | 62.1918 | 0.061035 | -0.086517 | 0.057678 | 0.29266 | -0.13031 | -0.17838 | -0.086975 | -0.091553 | -62.471 | 60.1501 | 60.1273 | 62.2101 | 62.3611 | 122.4976 | 62.2101 | 60.2097
3916.2188 | 0.061035 | 0.37384 | -0.77225 | -0.25207 | 0.12817 | -0.25528 | -0.17944 | 60.1913 | -61.9904 | 0.059509 | -62.233 | 60.2554 | 62.1918 | 62.1689 | 0.076294 | -0.09613 | 0.065155 | 0.27451 | -0.14313 | -0.19333 | 0.032043 | 0.086975 | -62.3932 | 60.1593 | 60.141 | 62.2375 | 62.3566 | 122.6074 | 62.1323 | 60.1639
3917.8906 | 0.030518 | 0.4155 | -0.78827 | -0.24033 | 0.12176 | -0.28839 | -0.19119 | 60.1501 | -61.972 | 0.036621 | -62.2696 | 60.1776 | 62.1826 | 62.1735 | 0.045776 | -0.11536 | 0.043793 | 0.28839 | -0.15381 | -0.1741 | 0.004578 | 0.07782 | -62.3886 | 60.0769 | 60.0815 | 62.233 | 62.3428 | 122.4655 | 62.2055 | 60.1685
3919.5938 | 0.045776 | 0.39841 | -0.78079 | -0.24994 | 0.1207 | -0.27771 | -0.18692 | 60.228 | -61.8988 | 0.16022 | -62.2238 | 60.173 | 62.1918 | 62.1826 | 0.030518 | -0.10788 | 0.040588 | 0.28732 | -0.17303 | -0.18585 | 0.14648 | 0.27466 | -62.3016 | 60.0952 | 60.0952 | 62.2009 | 62.3291 | 122.5571 | 62.146 | 60.1456
3921.2656 | 0.076294 | 0.38986 | -0.77545 | -0.23605 | 0.13031 | -0.25421 | -0.18692 | 60.2142 | -61.9354 | 0.054932 | -62.2238 | 60.1593 | 62.2055 | 62.1597 | 0.045776 | -0.11215 | 0.05127 | 0.27451 | -0.14206 | -0.18478 | 0.022888 | 0.054932 | -62.352 | 60.0723 | 60.0449 | 62.2421 | 62.3611 | 122.4976 | 62.1964 | 60.1822
3922.9375 | 0.061035 | 0.37598 | -0.76691 | -0.24887 | 0.12283 | -0.24994 | -0.18265 | 60.173 | -62.0316 | 0.036621 | -62.2559 | 60.2509 | 62.2101 | 62.1964 | 0.045776 | -0.085449 | 0.052338 | 0.28732 | -0.15274 | -0.1944 | 0.018311 | 0.082397 | -62.4161 | 60.1822 | 60.1822 | 62.2421 | 62.3428 | 122.6074 | 62.114 | 60.1776
3924.6406 | 0.045776 | 0.39627 | -0.77011 | -0.2446 | 0.12497 | -0.28305 | -0.19012 | 60.2188 | -61.9034 | 0.16479 | -62.2055 | 60.173 | 62.1643 | 62.1506 | 0.061035 | -0.11215 | 0.044861 | 0.27557 | -0.15274 | -0.17624 | 0.13275 | 0.25635 | -62.3154 | 60.0952 | 60.0723 | 62.1964 | 62.3383 | 122.5388 | 62.1414 | 60.1822
3926.3594 | 0.030518 | 0.40375 | -0.78934 | -0.25101 | 0.11856 | -0.29587 | -0.20187 | 60.1685 | -61.972 | 0.086975 | -62.233 | 60.173 | 62.1872 | 62.1552 | 0.061035 | -0.12283 | 0.048065 | 0.28091 | -0.15274 | -0.17303 | 0.091553 | 0.17853 | -62.3245 | 60.1044 | 60.0952 | 62.2055 | 62.3383 | 122.6028 | 62.1277 | 60.1593
3928.0312 | 0.045776 | 0.40375 | -0.76904 | -0.23712 | 0.13672 | -0.23605 | -0.18692 | 60.1868 | -62.027 | 0.045776 | -62.2421 | 60.26 | 62.2009 | 62.1643 | 0.045776 | -0.091858 | 0.05127 | 0.28198 | -0.14206 | -0.20187 | 0.022888 | 0.086975 | -62.4115 | 60.1868 | 60.1685 | 62.2101 | 62.3337 | 122.6212 | 62.1277 | 60.1959
3929.7031 | 0.061035 | 0.38879 | -0.77866 | -0.25955 | 0.11215 | -0.26276 | -0.19546 | 60.228 | -61.8988 | 0.17395 | -62.2101 | 60.173 | 62.1689 | 62.1735 | 0.061035 | -0.11536 | 0.054474 | 0.26916 | -0.15701 | -0.17838 | 0.13733 | 0.24719 | -62.3337 | 60.0815 | 60.1135 | 62.1918 | 62.3428 | 122.5433 | 62.1323 | 60.1822
3931.4219 | 0.045776 | 0.40268 | -0.78613 | -0.22751 | 0.12604 | -0.25955 | -0.18051 | 60.2142 | -61.9446 | 0.059509 | -62.2238 | 60.1593 | 62.178 | 62.1643 | 0.061035 | -0.11536 | 0.053406 | 0.28198 | -0.14206 | -0.17303 | 0.036621 | 0.059509 | -62.3795 | 60.0815 | 60.0403 | 62.233 | 62.3566 | 122.4426 | 62.2009 | 60.1822
3933.1094 | 0.045776 | 0.40695 | -0.78507 | -0.23605 | 0.10895 | -0.27664 | -0.20401 | 60.1868 | -61.9629 | 0.086975 | -62.2284 | 60.1685 | 62.1552 | 62.1597 | 0.061035 | -0.11108 | 0.046997 | 0.28412 | -0.15274 | -0.18265 | 0.11902 | 0.19684 | -62.3245 | 60.1135 | 60.1089 | 62.1964 | 62.3291 | 122.5937 | 62.1277 | 60.1456
3934.7812 | 0.045776 | 0.39414 | -0.77438 | -0.21896 | 0.12176 | -0.24567 | -0.17624 | 60.1959 | -62.0224 | -0.045776 | -62.2742 | 60.1822 | 62.1826 | 62.1826 | 0.061035 | -0.10468 | 0.049133 | 0.27985 | -0.13565 | -0.19974 | -0.022888 | -0.027466 | -62.4115 | 60.1318 | 60.0998 | 62.2055 | 62.3428 | 122.5159 | 62.1964 | 60.1822
3936.5 | 0.030518 | 0.39093 | -0.77652 | -0.23178 | 0.12924 | -0.24887 | -0.18265 | 60.1639 | -62.0178 | 0.045776 | -62.2467 | 60.2417 | 62.2055 | 62.1872 | 0.045776 | -0.099335 | 0.042725 | 0.28839 | -0.14206 | -0.19119 | 0.027466 | 0.091553 | -62.4069 | 60.1868 | 60.1364 | 62.2375 | 62.3657 | 122.6166 | 62.114 | 60.1547
3938.1719 | 0.061035 | 0.4187 | -0.7872 | -0.23712 | 0.1239 | -0.29053 | -0.1944 | 60.228 | -61.8713 | 0.16937 | -62.2055 | 60.1685 | 62.1964 | 62.1597 | 0.045776 | -0.11536 | 0.043793 | 0.25955 | -0.15381 | -0.17944 | 0.15106 | 0.2655 | -62.3108 | 60.0861 | 60.0677 | 62.2147 | 62.352 | 122.5891 | 62.114 | 60.1456
3939.8281 | 0.045776 | 0.38879 | -0.77331 | -0.23392 | 0.11322 | -0.23712 | -0.18051 | 60.1776 | -62.0316 | -0.027466 | -62.2742 | 60.2371 | 62.1826 | 62.1918 | 0.045776 | -0.084381 | 0.048065 | 0.28519 | -0.12283 | -0.19119 | -0.07782 | -0.059509 | -62.471 | 60.1822 | 60.1501 | 62.2238 | 62.384 | 122.4747 | 62.2192 | 60.228
3941.5 | 0.030518 | 0.38345 | -0.77652 | -0.23605 | 0.11429 | -0.25528 | -0.17944 | 60.1639 | -62.0453 | -0.032043 | -62.2833 | 60.228 | 62.1964 | 62.178 | 0.045776 | -0.095062 | 0.044861 | 0.27878 | -0.13458 | -0.18478 | -0.10986 | -0.068665 | -62.4619 | 60.1639 | 60.1501 | 62.2192 | 62.3657 | 122.4609 | 62.1826 | 60.2188
3943.1719 | 0.030518 | 0.3952 | -0.77438 | -0.25742 | 0.1239 | -0.27557 | -0.18906 | 60.1318 | -62.0041 | 0.059509 | -62.2696 | 60.228 | 62.2055 | 62.178 | 0.030518 | -0.10788 | 0.063019 | 0.28412 | -0.16449 | -0.17731 | 0.036621 | 0.10986 | -62.4207 | 60.173 | 60.1501 | 62.2192 | 62.3245 | 122.5616 | 62.1597 | 60.1776
3944.8438 | 0.030518 | 0.37811 | -0.76904 | -0.25635 | 0.12604 | -0.24887 | -0.18051 | 60.1868 | -61.9858 | 0.064087 | -62.233 | 60.26 | 62.2238 | 62.1735 | 0.061035 | -0.099335 | 0.065155 | 0.2948 | -0.14954 | -0.18478 | 0.032043 | 0.086975 | -62.4069 | 60.1547 | 60.1593 | 62.2055 | 62.3383 | 122.5983 | 62.1368 | 60.1593
3946.5312 | 0.045776 | 0.39627 | -0.77438 | -0.23926 | 0.11002 | -0.2948 | -0.17624 | 60.2188 | -61.8942 | 0.16937 | -62.2238 | 60.1822 | 62.1735 | 62.1552 | 0.030518 | -0.11643 | 0.052338 | 0.27344 | -0.17197 | -0.18158 | 0.1236 | 0.27924 | -62.3062 | 60.0723 | 60.0861 | 62.2192 | 62.3337 | 122.58 | 62.1597 | 60.1593
3948.2031 | 0.045776 | 0.38986 | -0.77652 | -0.22324 | 0.11215 | -0.2478 | -0.18799 | 60.1868 | -62.0178 | -0.018311 | -62.265 | 60.1822 | 62.1918 | 62.1872 | 0.061035 | -0.09613 | 0.048065 | 0.27451 | -0.13886 | -0.18799 | -0.009155 | 0.032043 | -62.3657 | 60.1044 | 60.0861 | 62.2284 | 62.3062 | 122.525 | 62.1964 | 60.173
3949.9062 | 0.061035 | 0.39414 | -0.78079 | -0.23071 | 0.12497 | -0.26382 | -0.18051 | 60.2188 | -61.9308 | 0.027466 | -62.2009 | 60.1639 | 62.1918 | 62.1689 | 0.061035 | -0.11322 | 0.044861 | 0.27771 | -0.14099 | -0.18051 | 0.013733 | 0.045776 | -62.3383 | 60.0906 | 60.0632 | 62.2238 | 62.352 | 122.5021 | 62.1964 | 60.1685
3951.5938 | 0.061035 | 0.392 | -0.76797 | -0.23178 | 0.13245 | -0.25528 | -0.18585 | 60.1776 | -62.0041 | -0.022888 | -62.2513 | 60.2188 | 62.2009 | 62.178 | 0.061035 | -0.1004 | 0.043793 | 0.27878 | -0.14206 | -0.17944 | -0.013733 | 0.013733 | -62.3566 | 60.1181 | 60.1044 | 62.2604 | 62.3245 | 122.5067 | 62.1872 | 60.1547
3953.2656 | 0.030518 | 0.40375 | -0.77652 | -0.25314 | 0.11749 | -0.26596 | -0.18372 | 60.2097 | -61.9217 | 0.15106 | -62.2055 | 60.1593 | 62.1872 | 62.146 | 0.061035 | -0.10895 | 0.049133 | 0.28198 | -0.16769 | -0.18372 | 0.09613 | 0.19684 | -62.3703 | 60.141 | 60.1547 | 62.2101 | 62.352 | 122.5479 | 62.1323 | 60.1868
3954.9375 | 0.076294 | 0.38666 | -0.76904 | -0.23178 | 0.12283 | -0.25101 | -0.18692 | 60.1456 | -62.0178 | -0.050354 | -62.2971 | 60.2051 | 62.1918 | 62.1918 | 0.061035 | -0.085449 | 0.052338 | 0.28732 | -0.13992 | -0.19226 | -0.041199 | -0.050354 | -62.4298 | 60.1456 | 60.0998 | 62.233 | 62.3657 | 122.5113 | 62.1735 | 60.1639
3956.6094 | 0.045776 | 0.37598 | -0.7605 | -0.2446 | 0.11643 | -0.2478 | -0.18265 | 60.2142 | -61.9583 | 0.068665 | -62.2238 | 60.2325 | 62.1872 | 62.1414 | 0.076294 | -0.11215 | 0.057678 | 0.28091 | -0.1442 | -0.18906 | 0.045776 | 0.059509 | -62.4115 | 60.1456 | 60.1273 | 62.2009 | 62.3474 | 122.5708 | 62.146 | 60.1822
3958.3125 | 0.061035 | 0.39627 | -0.77866 | -0.22964 | 0.12283 | -0.25955 | -0.18051 | 60.1273 | -62.0361 | -0.064087 | -62.2787 | 60.2188 | 62.2101 | 62.178 | 0.045776 | -0.10254 | 0.050201 | 0.29266 | -0.13886 | -0.16663 | -0.059509 | -0.064087 | -62.4069 | 60.1089 | 60.1089 | 62.2238 | 62.352 | 122.5021 | 62.1826 | 60.1593
3960 | 0.045776 | 0.38986 | -0.76904 | -0.26703 | 0.13672 | -0.28625 | -0.18478 | 60.1868 | -61.9034 | 0.15564 | -62.2055 | 60.1685 | 62.1872 | 62.1597 | 0.045776 | -0.11963 | 0.055542 | 0.2713 | -0.17517 | -0.18372 | 0.082397 | 0.23346 | -62.352 | 60.1273 | 60.1273 | 62.2009 | 62.3383 | 122.5342 | 62.1323 | 60.173
3961.6719 | 0.045776 | 0.37491 | -0.77118 | -0.25314 | 0.12711 | -0.25848 | -0.19333 | 60.1776 | -61.9766 | 0.050354 | -62.2238 | 60.2554 | 62.1964 | 62.1826 | 0.061035 | -0.095062 | 0.060883 | 0.28091 | -0.14313 | -0.18585 | 0.050354 | 0.086975 | -62.4069 | 60.1547 | 60.1364 | 62.2284 | 62.3795 | 122.6028 | 62.1552 | 60.1685
3963.3438 | 0.045776 | 0.39841 | -0.78293 | -0.26062 | 0.12176 | -0.29373 | -0.20828 | 60.1868 | -61.8988 | 0.12817 | -62.2101 | 60.1776 | 62.1964 | 62.1368 | 0.061035 | -0.13351 | 0.058746 | 0.27023 | -0.1709 | -0.17838 | 0.14191 | 0.23804 | -62.2971 | 60.0906 | 60.0769 | 62.2238 | 62.3245 | 122.5937 | 62.1231 | 60.1501
3965.0312 | 0.030518 | 0.41443 | -0.77972 | -0.2243 | 0.13031 | -0.28091 | -0.18799 | 60.173 | -61.9354 | 0.032043 | -62.2604 | 60.1364 | 62.2055 | 62.1872 | 0.076294 | -0.11215 | 0.054474 | 0.27771 | -0.14847 | -0.18051 | 0.027466 | 0.068665 | -62.3749 | 60.1044 | 60.0677 | 62.2238 | 62.3749 | 122.4289 | 62.1826 | 60.1639
3966.7031 | 0.030518 | 0.38879 | -0.77118 | -0.22537 | 0.1239 | -0.24246 | -0.18799 | 60.2142 | -61.9675 | 0.059509 | -62.2192 | 60.2463 | 62.1826 | 62.1872 | 0.045776 | -0.093994 | 0.045929 | 0.29159 | -0.1442 | -0.19119 | 0.041199 | 0.082397 | -62.3932 | 60.1639 | 60.1501 | 62.2101 | 62.3428 | 122.5662 | 62.1506 | 60.1822
3968.375 | 0.076294 | 0.37705 | -0.77011 | -0.24033 | 0.11963 | -0.24674 | -0.18478 | 60.1456 | -62.0773 | -0.041199 | -62.2787 | 60.228 | 62.2009 | 62.1918 | 0.061035 | -0.1004 | 0.061951 | 0.28732 | -0.13886 | -0.18799 | -0.09613 | -0.10071 | -62.4802 | 60.1501 | 60.141 | 62.2238 | 62.3474 | 122.4564 | 62.178 | 60.2097
3970.0312 | 0.061035 | 0.40054 | -0.77011 | -0.25848 | 0.10574 | -0.30014 | -0.19012 | 60.2051 | -61.9034 | 0.14191 | -62.2147 | 60.1685 | 62.178 | 62.1689 | 0.045776 | -0.1207 | 0.052338 | 0.26596 | -0.1709 | -0.17303 | 0.13733 | 0.24719 | -62.3016 | 60.0906 | 60.0861 | 62.2101 | 62.3199 | 122.5754 | 62.1323 | 60.1273
3971.7031 | 0.030518 | 0.40909 | -0.77866 | -0.22964 | 0.13138 | -0.26169 | -0.17517 | 60.2142 | -61.9263 | 0.032043 | -62.2192 | 60.173 | 62.1918 | 62.1597 | 0.030518 | -0.10147 | 0.057678 | 0.27985 | -0.13565 | -0.18051 | 0.009155 | 0.036621 | -62.3428 | 60.0861 | 60.0723 | 62.233 | 62.3566 | 122.5113 | 62.1964 | 60.1685
3973.3906 | 0.061035 | 0.38559 | -0.77011 | -0.2478 | 0.11322 | -0.24353 | -0.1741 | 60.173 | -62.0316 | -0.009155 | -62.265 | 60.2188 | 62.1964 | 62.1918 | 0.045776 | -0.095062 | 0.053406 | 0.28839 | -0.13031 | -0.18585 | -0.073242 | -0.054932 | -62.4802 | 60.1593 | 60.141 | 62.233 | 62.3703 | 122.4747 | 62.1918 | 60.2005
3975.0625 | 0.045776 | 0.39307 | -0.78507 | -0.26596 | 0.11215 | -0.28839 | -0.18158 | 60.2005 | -61.908 | 0.16022 | -62.2055 | 60.1959 | 62.1597 | 62.1643 | 0.061035 | -0.12176 | 0.057678 | 0.26703 | -0.16449 | -0.17624 | 0.11902 | 0.24719 | -62.3383 | 60.1089 | 60.1135 | 62.1872 | 62.3199 | 122.5204 | 62.1231 | 60.1822
3976.7344 | 0.045776 | 0.392 | -0.77118 | -0.25742 | 0.1207 | -0.27451 | -0.19974 | 60.2142 | -61.8942 | 0.15106 | -62.2055 | 60.1685 | 62.1689 | 62.1643 | 0.061035 | -0.12283 | 0.05661 | 0.27878 | -0.16342 | -0.17944 | 0.13733 | 0.26093 | -62.3016 | 60.0952 | 60.0861 | 62.1826 | 62.352 | 122.5571 | 62.1231 | 60.173
3978.4062 | 0.045776 | 0.392 | -0.75943 | -0.2211 | 0.11643 | -0.25207 | -0.18158 | 60.2142 | -61.972 | 0 | -62.2421 | 60.1685 | 62.178 | 62.178 | 0.045776 | -0.095062 | 0.043793 | 0.27985 | -0.14099 | -0.18478 | 0.009155 | 0.041199 | -62.3566 | 60.0998 | 60.1044 | 62.2284 | 62.3154 | 122.5067 | 62.1918 | 60.1868
3980.0781 | 0.030518 | 0.36743 | -0.78507 | -0.25742 | 0.11856 | -0.26276 | -0.19653 | 60.1547 | -62.0178 | 0.054932 | -62.265 | 60.26 | 62.1964 | 62.1643 | 0.061035 | -0.10681 | 0.059814 | 0.27985 | -0.14954 | -0.18478 | 0.032043 | 0.091553 | -62.4435 | 60.1822 | 60.1639 | 62.2284 | 62.352 | 122.5754 | 62.1231 | 60.1822
3981.75 | 0.061035 | 0.38879 | -0.77011 | -0.23392 | 0.11536 | -0.27237 | -0.17838 | 60.173 | -61.9858 | -0.004578 | -62.2513 | 60.1959 | 62.1689 | 62.1872 | 0.045776 | -0.11749 | 0.05661 | 0.28198 | -0.13672 | -0.17197 | 0.009155 | 0.045776 | -62.3611 | 60.0677 | 60.0632 | 62.2238 | 62.3611 | 122.5113 | 62.1735 | 60.1593
3983.4844 | 0.061035 | 0.38666 | -0.76691 | -0.21896 | 0.11536 | -0.23605 | -0.18478 | 60.1913 | -61.9949 | 0.004578 | -62.265 | 60.2325 | 62.1964 | 62.1872 | 0.045776 | -0.084381 | 0.045929 | 0.27664 | -0.13031 | -0.18372 | -0.050354 | -0.045776 | -62.4619 | 60.1685 | 60.141 | 62.2375 | 62.3428 | 122.4655 | 62.1918 | 60.1959
3985.1562 | 0.045776 | 0.38345 | -0.77545 | -0.25421 | 0.11536 | -0.26596 | -0.19333 | 60.1318 | -62.0132 | 0.054932 | -62.265 | 60.2417 | 62.1918 | 62.1826 | 0.045776 | -0.10468 | 0.066223 | 0.28305 | -0.15381 | -0.17303 | 0.022888 | 0.091553 | -62.4344 | 60.1822 | 60.1868 | 62.2009 | 62.3566 | 122.6028 | 62.146 | 60.1822
3986.8438 | 0.091553 | 0.3952 | -0.76584 | -0.23178 | 0.10574 | -0.24674 | -0.17731 | 60.1318 | -62.059 | -0.073242 | -62.2833 | 60.2509 | 62.2101 | 62.178 | 0.045776 | -0.09613 | 0.057678 | 0.298 | -0.13886 | -0.18372 | -0.091553 | -0.10986 | -62.4619 | 60.1593 | 60.1456 | 62.233 | 62.3749 | 122.5021 | 62.178 | 60.1959
3988.5156 | 0.030518 | 0.41977 | -0.78293 | -0.23178 | 0.10574 | -0.29053 | -0.18799 | 60.1547 | -61.94 | 0.027466 | -62.2559 | 60.1639 | 62.1597 | 62.178 | 0.045776 | -0.11643 | 0.045929 | 0.27344 | -0.15595 | -0.17731 | 0.027466 | 0.086975 | -62.3795 | 60.0906 | 60.0632 | 62.2101 | 62.3703 | 122.4472 | 62.2009 | 60.1685
3990.1719 | 0.045776 | 0.38559 | -0.76263 | -0.23926 | 0.12604 | -0.24887 | -0.1741 | 60.1364 | -62.0636 | -0.068665 | -62.2925 | 60.2417 | 62.2284 | 62.1735 | 0.045776 | -0.1004 | 0.045929 | 0.28305 | -0.14099 | -0.18265 | -0.07782 | -0.082397 | -62.4619 | 60.141 | 60.1273 | 62.2284 | 62.3749 | 122.5021 | 62.1964 | 60.1639
3991.8281 | 0.045776 | 0.39307 | -0.77438 | -0.25742 | 0.12497 | -0.29266 | -0.19867 | 60.2142 | -61.853 | 0.15106 | -62.1872 | 60.1501 | 62.1735 | 62.1735 | 0.061035 | -0.11963 | 0.055542 | 0.27557 | -0.16769 | -0.18906 | 0.14191 | 0.25635 | -62.3062 | 60.0677 | 60.0815 | 62.2009 | 62.3337 | 122.5525 | 62.146 | 60.1318
3993.5156 | 0.030518 | 0.38986 | -0.76904 | -0.22003 | 0.11536 | -0.25421 | -0.18692 | 60.141 | -62.0636 | -0.082397 | -62.2879 | 60.228 | 62.2147 | 62.1735 | 0.045776 | -0.1004 | 0.045929 | 0.28519 | -0.13565 | -0.18051 | -0.091553 | -0.082397 | -62.4527 | 60.1593 | 60.1456 | 62.2467 | 62.352 | 122.4976 | 62.1826 | 60.173
3995.1875 | 0.030518 | 0.37064 | -0.77545 | -0.23819 | 0.12604 | -0.25101 | -0.17838 | 60.1593 | -62.0224 | -0.041199 | -62.265 | 60.1959 | 62.2147 | 62.1918 | 0.030518 | -0.10468 | 0.054474 | 0.28305 | -0.14847 | -0.18906 | -0.013733 | -0.013733 | -62.3795 | 60.0952 | 60.1227 | 62.2009 | 62.3337 | 122.5159 | 62.1964 | 60.1501
3996.8594 | 0.045776 | 0.38666 | -0.76157 | -0.24567 | 0.11322 | -0.25314 | -0.18051 | 60.1593 | -62.0636 | -0.068665 | -62.2787 | 60.2325 | 62.1964 | 62.1826 | 0.045776 | -0.091858 | 0.067291 | 0.28519 | -0.13565 | -0.18265 | -0.10071 | -0.10529 | -62.4435 | 60.1456 | 60.141 | 62.2101 | 62.3611 | 122.5113 | 62.1872 | 60.1776
3998.5625 | 0.045776 | 0.39948 | -0.77011 | -0.24567 | 0.1239 | -0.28519 | -0.19546 | 60.2051 | -61.8942 | 0.15564 | -62.2055 | 60.1639 | 62.1872 | 62.1414 | 0.076294 | -0.11429 | 0.059814 | 0.28625 | -0.16235 | -0.17838 | 0.10529 | 0.21057 | -62.3611 | 60.1135 | 60.1227 | 62.2101 | 62.3337 | 122.5342 | 62.1414 | 60.173
4000.2344 | 0.045776 | 0.40695 | -0.77118 | -0.2446 | 0.11215 | -0.29694 | -0.1944 | 60.2234 | -61.853 | 0.14648 | -62.1826 | 60.1822 | 62.1597 | 62.1506 | 0.045776 | -0.1239 | 0.049133 | 0.27451 | -0.15808 | -0.17731 | 0.13733 | 0.26093 | -62.3154 | 60.0769 | 60.0586 | 62.2009 | 62.3428 | 122.5662 | 62.1277 | 60.1456
4001.9062 | 0.076294 | 0.39734 | -0.784 | -0.2179 | 0.11429 | -0.25314 | -0.18585 | 60.2142 | -61.94 | 0.018311 | -62.2375 | 60.1959 | 62.2147 | 62.1643 | 0.045776 | -0.10468 | 0.041656 | 0.28091 | -0.13672 | -0.18585 | 0.018311 | 0.054932 | -62.3566 | 60.0998 | 60.0906 | 62.2055 | 62.352 | 122.5113 | 62.1964 | 60.1776
4003.5781 | 0.061035 | 0.37811 | -0.77866 | -0.22537 | 0.1207 | -0.24994 | -0.18265 | 60.1593 | -62.0499 | -0.073242 | -62.3016 | 60.228 | 62.2238 | 62.1964 | 0.045776 | -0.10147 | 0.041656 | 0.28839 | -0.13351 | -0.17944 | -0.07782 | -0.07782 | -62.4527 | 60.1593 | 60.1456 | 62.233 | 62.3474 | 122.493 | 62.1872 | 60.1547
4005.2656 | 0.061035 | 0.38559 | -0.77972 | -0.24246 | 0.11963 | -0.26596 | -0.18692 | 60.173 | -62.0224 | 0.050354 | -62.2513 | 60.2463 | 62.1826 | 62.1918 | 0.030518 | -0.09613 | 0.05127 | 0.29053 | -0.15808 | -0.17944 | 0.004578 | 0.086975 | -62.4298 | 60.1776 | 60.1593 | 62.2009 | 62.3428 | 122.6028 | 62.114 | 60.1822
4006.9531 | 0.030518 | 0.40588 | -0.77118 | -0.25955 | 0.10895 | -0.27985 | -0.18906 | 60.2188 | -61.9034 | 0.15106 | -62.2192 | 60.1868 | 62.1643 | 62.1506 | 0.030518 | -0.12817 | 0.05127 | 0.27771 | -0.16876 | -0.17624 | 0.14191 | 0.25177 | -62.2742 | 60.1089 | 60.0815 | 62.1826 | 62.3428 | 122.5891 | 62.1323 | 60.1227
4008.625 | 0.045776 | 0.38559 | -0.77225 | -0.22644 | 0.11215 | -0.23712 | -0.18478 | 60.1547 | -62.0819 | -0.082397 | -62.2879 | 60.2234 | 62.1872 | 62.1918 | 0.076294 | -0.086517 | 0.045929 | 0.29587 | -0.14206 | -0.1944 | -0.10071 | -0.091553 | -62.471 | 60.1501 | 60.1456 | 62.1964 | 62.352 | 122.4792 | 62.178 | 60.1959
4010.2969 | 0.030518 | 0.40695 | -0.78293 | -0.23392 | 0.11322 | -0.29159 | -0.18692 | 60.1547 | -61.9995 | 0.036621 | -62.2604 | 60.1593 | 62.1872 | 62.1826 | 0.030518 | -0.11856 | 0.050201 | 0.27344 | -0.15915 | -0.17838 | 0.022888 | 0.09613 | -62.3749 | 60.0952 | 60.1089 | 62.1872 | 62.3566 | 122.4792 | 62.1826 | 60.1868
4011.9688 | 0.061035 | 0.38452 | -0.77331 | -0.23498 | 0.10468 | -0.24887 | -0.19226 | 60.2234 | -62.0087 | 0.068665 | -62.2421 | 60.2371 | 62.1826 | 62.1826 | 0.030518 | -0.086517 | 0.045929 | 0.28625 | -0.13565 | -0.17624 | 0.041199 | 0.082397 | -62.3886 | 60.1547 | 60.141 | 62.2192 | 62.3383 | 122.5845 | 62.1231 | 60.1822
4013.6406 | 0.061035 | 0.39734 | -0.77866 | -0.25742 | 0.11749 | -0.27985 | -0.1976 | 60.2325 | -61.8851 | 0.16479 | -62.1964 | 60.1685 | 62.1964 | 62.1597 | 0.076294 | -0.1239 | 0.05127 | 0.28305 | -0.16876 | -0.16876 | 0.14191 | 0.24261 | -62.2787 | 60.0861 | 60.0723 | 62.1964 | 62.3337 | 122.5616 | 62.1231 | 60.1501
4015.3125 | 0.076294 | 0.38879 | -0.77225 | -0.23178 | 0.12497 | -0.24353 | -0.18906 | 60.1639 | -62.0544 | -0.059509 | -62.2787 | 60.2463 | 62.2009 | 62.1964 | 0.045776 | -0.1004 | 0.048065 | 0.28732 | -0.13351 | -0.19012 | -0.050354 | -0.07782 | -62.4435 | 60.1364 | 60.1318 | 62.2238 | 62.3474 | 122.5159 | 62.1918 | 60.1959
4016.9844 | 0.061035 | 0.39841 | -0.77331 | -0.24139 | 0.11856 | -0.26703 | -0.18478 | 60.1456 | -62.0041 | 0.073242 | -62.2742 | 60.2234 | 62.2101 | 62.1872 | 0.076294 | -0.095062 | 0.049133 | 0.28625 | -0.16342 | -0.19012 | 0.041199 | 0.10986 | -62.4252 | 60.1685 | 60.1685 | 62.2101 | 62.3566 | 122.5479 | 62.1414 | 60.1868
4018.6562 | 0.061035 | 0.38345 | -0.78613 | -0.2478 | 0.12176 | -0.26916 | -0.19012 | 60.2188 | -61.9171 | 0.14648 | -62.1964 | 60.1639 | 62.1872 | 62.1735 | 0.045776 | -0.11643 | 0.054474 | 0.27985 | -0.15381 | -0.17944 | 0.11444 | 0.22888 | -62.3428 | 60.1364 | 60.1318 | 62.2101 | 62.3291 | 122.5296 | 62.1506 | 60.1822
4020.3438 | 0.045776 | 0.3952 | -0.77331 | -0.22217 | 0.1207 | -0.24887 | -0.17838 | 60.2005 | -61.9583 | 0.004578 | -62.2421 | 60.1822 | 62.178 | 62.178 | 0.045776 | -0.11215 | 0.037384 | 0.28412 | -0.13886 | -0.19226 | 0.018311 | 0.032043 | -62.3566 | 60.0815 | 60.0815 | 62.2147 | 62.3245 | 122.5021 | 62.2009 | 60.1822
4022.0312 | 0.076294 | 0.3952 | -0.78293 | -0.25314 | 0.11749 | -0.27878 | -0.19867 | 60.2097 | -61.9125 | 0.17395 | -62.1964 | 60.1547 | 62.1735 | 62.1414 | 0.030518 | -0.11429 | 0.05127 | 0.27237 | -0.16983 | -0.18799 | 0.12817 | 0.25177 | -62.3291 | 60.0998 | 60.1135 | 62.1826 | 62.3291 | 122.5342 | 62.1323 | 60.1776
4023.7031 | 0.061035 | 0.40482 | -0.77225 | -0.22644 | 0.12176 | -0.27344 | -0.19119 | 60.2097 | -61.9217 | 0.059509 | -62.233 | 60.1593 | 62.1826 | 62.1689 | 0.030518 | -0.12497 | 0.038452 | 0.26489 | -0.15488 | -0.19012 | 0.022888 | 0.068665 | -62.3657 | 60.0815 | 60.0494 | 62.2147 | 62.3383 | 122.4472 | 62.1872 | 60.1822
4025.3906 | 0.061035 | 0.38345 | -0.78079 | -0.23498 | 0.11963 | -0.25314 | -0.18478 | 60.2234 | -61.9308 | 0.036621 | -62.2101 | 60.1822 | 62.1872 | 62.1689 | 0.045776 | -0.10147 | 0.048065 | 0.27237 | -0.14206 | -0.18478 | 0.027466 | 0.027466 | -62.3566 | 60.0906 | 60.0632 | 62.2284 | 62.3611 | 122.4884 | 62.178 | 60.1913
4027.0781 | 0.045776 | 0.37705 | -0.78079 | -0.23392 | 0.11429 | -0.2446 | -0.17624 | 60.173 | -62.0224 | -0.041199 | -62.265 | 60.2097 | 62.2101 | 62.2009 | 0.045776 | -0.10147 | 0.046997 | 0.28198 | -0.13992 | -0.17731 | -0.032043 | -0.045776 | -62.4115 | 60.1089 | 60.1089 | 62.2238 | 62.3566 | 122.5113 | 62.2009 | 60.141
4028.75 | 0.076294 | 0.40054 | -0.77759 | -0.26062 | 0.11749 | -0.27023 | -0.18692 | 60.1547 | -62.0178 | 0.054932 | -62.2559 | 60.2509 | 62.1964 | 62.1826 | 0.061035 | -0.091858 | 0.048065 | 0.28305 | -0.15701 | -0.18051 | 0.027466 | 0.091553 | -62.4344 | 60.1685 | 60.1501 | 62.2009 | 62.3337 | 122.5708 | 62.1185 | 60.1913
4030.4219 | 0.030518 | 0.4155 | -0.78293 | -0.23392 | 0.11749 | -0.2948 | -0.18265 | 60.1456 | -61.9766 | 0.059509 | -62.2421 | 60.1868 | 62.178 | 62.1597 | 0.030518 | -0.13138 | 0.048065 | 0.27771 | -0.16129 | -0.17731 | 0.064087 | 0.13733 | -62.3428 | 60.0677 | 60.0861 | 62.1872 | 62.3474 | 122.5433 | 62.1735 | 60.173
4032.0938 | 0.061035 | 0.39841 | -0.77331 | -0.22751 | 0.12817 | -0.24674 | -0.1741 | 60.1822 | -62.0132 | -0.045776 | -62.2696 | 60.2097 | 62.1964 | 62.1918 | 0.045776 | -0.076904 | 0.043793 | 0.29266 | -0.13672 | -0.18906 | -0.009155 | -0.013733 | -62.3886 | 60.1318 | 60.0998 | 62.2192 | 62.3383 | 122.493 | 62.1964 | 60.1685
4033.7656 | 0.030518 | 0.392 | -0.77438 | -0.26382 | 0.11215 | -0.28091 | -0.19012 | 60.2371 | -61.8942 | 0.13275 | -62.2101 | 60.1639 | 62.1872 | 62.146 | 0.061035 | -0.11429 | 0.057678 | 0.28732 | -0.17303 | -0.17197 | 0.16022 | 0.24719 | -62.2879 | 60.0677 | 60.0906 | 62.1872 | 62.3337 | 122.5616 | 62.1231 | 60.1501
4035.5 | 0.045776 | 0.39093 | -0.76584 | -0.24994 | 0.12283 | -0.2446 | -0.18265 | 60.2371 | -61.972 | 0.07782 | -62.233 | 60.2554 | 62.1872 | 62.1506 | 0.015259 | -0.093994 | 0.05661 | 0.2948 | -0.13565 | -0.19974 | 0.054932 | 0.082397 | -62.3978 | 60.1501 | 60.1456 | 62.2055 | 62.352 | 122.5662 | 62.1368 | 60.173
4037.1562 | 0.045776 | 0.40695 | -0.78079 | -0.25101 | 0.13672 | -0.29266 | -0.1944 | 60.2051 | -61.8851 | 0.13733 | -62.2055 | 60.1776 | 62.1735 | 62.1735 | 0.045776 | -0.12604 | 0.049133 | 0.27878 | -0.16022 | -0.17731 | 0.16022 | 0.23804 | -62.3016 | 60.0815 | 60.0677 | 62.2192 | 62.3474 | 122.5891 | 62.146 | 60.1181
4038.8281 | 0.061035 | 0.39627 | -0.77438 | -0.22003 | 0.11536 | -0.25848 | -0.19119 | 60.2051 | -61.9217 | 0.036621 | -62.2147 | 60.1639 | 62.1872 | 62.1597 | 0.061035 | -0.11749 | 0.045929 | 0.27664 | -0.14099 | -0.18372 | 0.032043 | 0.054932 | -62.3383 | 60.0723 | 60.0403 | 62.2192 | 62.3474 | 122.4564 | 62.1735 | 60.1547
4040.5312 | 0.030518 | 0.41763 | -0.78079 | -0.22751 | 0.098267 | -0.27344 | -0.1976 | 60.2005 | -61.9354 | 0.036621 | -62.2467 | 60.1501 | 62.1735 | 62.1506 | 0.045776 | -0.10895 | 0.049133 | 0.28198 | -0.15274 | -0.17731 | 0.041199 | 0.07782 | -62.3703 | 60.0815 | 60.0586 | 62.2009 | 62.3291 | 122.438 | 62.2055 | 60.2051
4042.2031 | 0.030518 | 0.392 | -0.77225 | -0.22751 | 0.11215 | -0.25207 | -0.18906 | 60.2051 | -61.972 | -0.004578 | -62.2375 | 60.1868 | 62.2101 | 62.178 | 0.045776 | -0.092926 | 0.044861 | 0.2948 | -0.13779 | -0.18158 | 0.004578 | 0.022888 | -62.352 | 60.1273 | 60.0906 | 62.2284 | 62.3291 | 122.5021 | 62.2055 | 60.1547
4043.8906 | 0.045776 | 0.41763 | -0.76584 | -0.22964 | 0.11536 | -0.23178 | -0.17838 | 60.1593 | -62.0636 | -0.045776 | -62.2787 | 60.2325 | 62.2192 | 62.1689 | 0.045776 | -0.088654 | 0.046997 | 0.28839 | -0.13886 | -0.18478 | -0.07782 | -0.068665 | -62.4847 | 60.1685 | 60.1593 | 62.233 | 62.3383 | 122.4564 | 62.1872 | 60.1959
4045.5625 | 0.045776 | 0.41657 | -0.75089 | -0.24033 | 0.13565 | -0.2446 | -0.18158 | 60.1547 | -62.0407 | -0.022888 | -62.2696 | 60.2234 | 62.1918 | 62.2192 | 0.061035 | -0.098267 | 0.048065 | 0.28839 | -0.13886 | -0.17838 | -0.086975 | -0.064087 | -62.4527 | 60.1776 | 60.1456 | 62.233 | 62.3703 | 122.4426 | 62.1689 | 60.2005
4047.2344 | 0.061035 | 0.40588 | -0.784 | -0.26489 | 0.11215 | -0.28519 | -0.17838 | 60.2142 | -61.8896 | 0.16937 | -62.2009 | 60.1593 | 62.1872 | 62.1735 | 0.030518 | -0.12604 | 0.05127 | 0.28305 | -0.16342 | -0.17838 | 0.13733 | 0.26093 | -62.3154 | 60.0769 | 60.0906 | 62.2192 | 62.3337 | 122.5525 | 62.146 | 60.1639
4048.9062 | 0.045776 | 0.37384 | -0.7872 | -0.24246 | 0.13245 | -0.28625 | -0.1944 | 60.1318 | -61.9904 | 0.045776 | -62.2375 | 60.1547 | 62.1918 | 62.1735 | 0.030518 | -0.11429 | 0.043793 | 0.27664 | -0.15701 | -0.17838 | 0.018311 | 0.09613 | -62.384 | 60.0861 | 60.1044 | 62.2009 | 62.3428 | 122.4838 | 62.1826 | 60.173
4050.5781 | 0.061035 | 0.38773 | -0.77652 | -0.23178 | 0.11963 | -0.24674 | -0.1944 | 60.1868 | -62.0041 | -0.032043 | -62.2559 | 60.2097 | 62.2009 | 62.1826 | 0.061035 | -0.10681 | 0.041656 | 0.28091 | -0.14526 | -0.1944 | 0.004578 | 0.018311 | -62.384 | 60.1089 | 60.0815 | 62.2009 | 62.3016 | 122.5021 | 62.1918 | 60.1685
4052.25 | 0.045776 | 0.40161 | -0.76263 | -0.24674 | 0.11536 | -0.25528 | -0.18585 | 60.1456 | -62.059 | -0.064087 | -62.2787 | 60.2463 | 62.1872 | 62.178 | 0.061035 | -0.097198 | 0.059814 | 0.28519 | -0.15381 | -0.18265 | -0.07782 | -0.086975 | -62.4344 | 60.1639 | 60.1135 | 62.233 | 62.3611 | 122.4976 | 62.2055 | 60.1776
4053.9219 | 0.061035 | 0.40695 | -0.77331 | -0.25635 | 0.11322 | -0.25848 | -0.18585 | 60.1364 | -61.9904 | 0.068665 | -62.2696 | 60.2051 | 62.1964 | 62.1735 | 0.061035 | -0.11536 | 0.05127 | 0.28091 | -0.16022 | -0.18051 | 0.041199 | 0.12817 | -62.4069 | 60.1822 | 60.1456 | 62.2375 | 62.3428 | 122.5525 | 62.1552 | 60.2005
4055.6094 | 0.061035 | 0.40802 | -0.77866 | -0.25101 | 0.11322 | -0.26489 | -0.18478 | 60.1364 | -61.9995 | 0.054932 | -62.2696 | 60.2463 | 62.1826 | 62.1964 | 0.045776 | -0.11643 | 0.055542 | 0.27771 | -0.15167 | -0.18158 | 0.032043 | 0.12817 | -62.4252 | 60.1822 | 60.1364 | 62.1964 | 62.3428 | 122.5479 | 62.1506 | 60.1501
4057.2812 | 0.030518 | 0.41443 | -0.76797 | -0.26276 | 0.13031 | -0.25635 | -0.19012 | 60.1593 | -62.027 | 0.041199 | -62.2604 | 60.2692 | 62.2055 | 62.1918 | 0.045776 | -0.098267 | 0.061951 | 0.29266 | -0.15595 | -0.1976 | 0.022888 | 0.10071 | -62.4252 | 60.1639 | 60.1547 | 62.1918 | 62.3337 | 122.5845 | 62.1277 | 60.1547
4058.9531 | 0.045776 | 0.40054 | -0.77011 | -0.22537 | 0.12711 | -0.24674 | -0.18051 | 60.1364 | -62.0499 | -0.068665 | -62.2879 | 60.2509 | 62.2055 | 62.178 | 0.030518 | -0.095062 | 0.03952 | 0.28305 | -0.12924 | -0.17517 | -0.082397 | -0.091553 | -62.4481 | 60.1364 | 60.1501 | 62.2238 | 62.3337 | 122.4838 | 62.1872 | 60.1959
4060.6406 | 0.030518 | 0.41016 | -0.77545 | -0.23819 | 0.11002 | -0.27023 | -0.1741 | 60.1639 | -62.0041 | 0.050354 | -62.2375 | 60.228 | 62.1918 | 62.1918 | 0.045776 | -0.098267 | 0.059814 | 0.29159 | -0.14633 | -0.17944 | 0.032043 | 0.10071 | -62.4023 | 60.1776 | 60.1547 | 62.2055 | 62.3474 | 122.5983 | 62.1323 | 60.1685
4062.3125 | 0.045776 | 0.4187 | -0.77972 | -0.26062 | 0.11856 | -0.29053 | -0.1944 | 60.1593 | -61.9583 | 0.091553 | -62.2559 | 60.2005 | 62.1918 | 62.1597 | 0.030518 | -0.11963 | 0.049133 | 0.27664 | -0.16342 | -0.17944 | 0.050354 | 0.14648 | -62.4069 | 60.1639 | 60.141 | 62.2467 | 62.3428 | 122.5296 | 62.1506 | 60.1776
4063.9844 | 0.061035 | 0.392 | -0.78079 | -0.24139 | 0.10147 | -0.28412 | -0.19546 | 60.141 | -61.9537 | 0.036621 | -62.265 | 60.1776 | 62.1918 | 62.1414 | 0.045776 | -0.12711 | 0.052338 | 0.27771 | -0.16022 | -0.17838 | 0.013733 | 0.07782 | -62.3611 | 60.0906 | 60.0632 | 62.2284 | 62.3566 | 122.4472 | 62.2192 | 60.1776
4065.6562 | 0.061035 | 0.38452 | -0.76584 | -0.22964 | 0.11215 | -0.26489 | -0.18265 | 60.2097 | -61.9263 | 0.022888 | -62.2192 | 60.1639 | 62.2147 | 62.1643 | 0.045776 | -0.11322 | 0.045929 | 0.27664 | -0.13779 | -0.18478 | 0.018311 | 0.036621 | -62.3428 | 60.0586 | 60.0815 | 62.2055 | 62.3337 | 122.5067 | 62.178 | 60.1913
4067.3281 | 0.045776 | 0.39841 | -0.77118 | -0.2211 | 0.12176 | -0.25848 | -0.19333 | 60.1547 | -62.0178 | -0.045776 | -62.2742 | 60.228 | 62.2055 | 62.1918 | 0.045776 | -0.10895 | 0.046997 | 0.2681 | -0.13458 | -0.17517 | -0.036621 | -0.018311 | -62.3886 | 60.1135 | 60.0998 | 62.233 | 62.3337 | 122.5067 | 62.1826 | 60.1547
4069 | 0.061035 | 0.41657 | -0.76904 | -0.25207 | 0.11215 | -0.24994 | -0.18585 | 60.2005 | -61.9858 | 0.068665 | -62.233 | 60.2371 | 62.1872 | 62.1552 | 0.045776 | -0.10254 | 0.048065 | 0.28412 | -0.1506 | -0.19226 | 0.041199 | 0.07782 | -62.3886 | 60.1685 | 60.1501 | 62.1964 | 62.3703 | 122.5891 | 62.1414 | 60.1685
4070.6719 | 0.045776 | 0.38452 | -0.79468 | -0.22537 | 0.10574 | -0.29373 | -0.1944 | 60.1456 | -61.9583 | 0.041199 | -62.2559 | 60.1822 | 62.1597 | 62.178 | 0.045776 | -0.11856 | 0.049133 | 0.27878 | -0.17197 | -0.17624 | 0.022888 | 0.068665 | -62.3886 | 60.0952 | 60.1044 | 62.2284 | 62.3566 | 122.4655 | 62.1918 | 60.1913
4072.3438 | 0.045776 | 0.39734 | -0.784 | -0.24567 | 0.12817 | -0.28305 | -0.19119 | 60.2234 | -61.8851 | 0.17395 | -62.2055 | 60.1456 | 62.1643 | 62.1552 | 0.061035 | -0.11749 | 0.048065 | 0.2713 | -0.14954 | -0.18692 | 0.13733 | 0.25635 | -62.3154 | 60.0906 | 60.0998 | 62.1918 | 62.3245 | 122.5342 | 62.1277 | 60.1868
4074.0156 | 0.030518 | 0.41657 | -0.7637 | -0.23605 | 0.12604 | -0.24246 | -0.18906 | 60.2371 | -61.9629 | 0.050354 | -62.2238 | 60.228 | 62.1735 | 62.178 | 0.030518 | -0.095062 | 0.049133 | 0.29159 | -0.13351 | -0.19119 | 0.013733 | 0.041199 | -62.3978 | 60.1456 | 60.141 | 62.2055 | 62.3474 | 122.493 | 62.1643 | 60.2097
4075.7031 | 0.061035 | 0.42191 | -0.75729 | -0.2478 | 0.11856 | -0.26062 | -0.18265 | 60.173 | -62.0178 | 0.054932 | -62.2375 | 60.2554 | 62.1872 | 62.1872 | 0.061035 | -0.093994 | 0.05661 | 0.28732 | -0.14206 | -0.18692 | 0.036621 | 0.07782 | -62.3978 | 60.1822 | 60.1593 | 62.2101 | 62.352 | 122.6074 | 62.1002 | 60.1913
4077.4375 | 0.061035 | 0.38025 | -0.77225 | -0.23071 | 0.10681 | -0.28732 | -0.20187 | 60.1685 | -61.9629 | 0.036621 | -62.265 | 60.1639 | 62.1689 | 62.1918 | 0.061035 | -0.12817 | 0.040588 | 0.28091 | -0.15808 | -0.17838 | 0.022888 | 0.091553 | -62.3611 | 60.0861 | 60.1089 | 62.2055 | 62.3383 | 122.438 | 62.1872 | 60.1685
4079.1094 | 0.045776 | 0.40695 | -0.77759 | -0.23498 | 0.11215 | -0.25421 | -0.18051 | 60.2142 | -61.9675 | 0.064087 | -62.2238 | 60.2509 | 62.1872 | 62.146 | 0.076294 | -0.091858 | 0.044861 | 0.28305 | -0.13992 | -0.18906 | 0.032043 | 0.082397 | -62.3932 | 60.1593 | 60.1456 | 62.1918 | 62.3474 | 122.5708 | 62.1414 | 60.1913
4080.8125 | 0.076294 | 0.38879 | -0.76584 | -0.22217 | 0.12283 | -0.26596 | -0.18265 | 60.1776 | -62.0041 | -0.018311 | -62.2696 | 60.1913 | 62.1826 | 62.1689 | 0.030518 | -0.11002 | 0.036316 | 0.27985 | -0.13992 | -0.17944 | -0.009155 | 0.013733 | -62.3703 | 60.1044 | 60.1089 | 62.2147 | 62.3154 | 122.5159 | 62.1918 | 60.1547
4082.5156 | 0.045776 | 0.40375 | -0.76263 | -0.22751 | 0.11749 | -0.24994 | -0.18692 | 60.1639 | -62.0499 | -0.059509 | -62.2925 | 60.2371 | 62.1872 | 62.2147 | 0.045776 | -0.10254 | 0.040588 | 0.28519 | -0.13672 | -0.17731 | -0.07782 | -0.068665 | -62.4435 | 60.1547 | 60.1685 | 62.2101 | 62.3474 | 122.493 | 62.178 | 60.1913
4084.1875 | 0.076294 | 0.4187 | -0.75943 | -0.26062 | 0.12283 | -0.27344 | -0.18051 | 60.141 | -62.0361 | 0.027466 | -62.2696 | 60.26 | 62.1872 | 62.1597 | 0.061035 | -0.095062 | 0.071564 | 0.28946 | -0.14847 | -0.18265 | 0.027466 | 0.082397 | -62.4207 | 60.1501 | 60.1547 | 62.2238 | 62.3337 | 122.5891 | 62.1185 | 60.1593
4085.8594 | 0.061035 | 0.38773 | -0.78186 | -0.24994 | 0.1207 | -0.28519 | -0.20294 | 60.2142 | -61.8668 | 0.16479 | -62.2009 | 60.173 | 62.146 | 62.1368 | 0.061035 | -0.1207 | 0.050201 | 0.27344 | -0.16983 | -0.17731 | 0.13733 | 0.27008 | -62.2925 | 60.0861 | 60.0815 | 62.178 | 62.3154 | 122.5662 | 62.1506 | 60.1547
4087.5625 | 0.061035 | 0.38238 | -0.79041 | -0.24887 | 0.11002 | -0.298 | -0.1976 | 60.141 | -61.9904 | 0.022888 | -62.2467 | 60.1913 | 62.2009 | 62.1552 | 0.045776 | -0.12817 | 0.05127 | 0.28412 | -0.1506 | -0.17838 | 0.027466 | 0.10071 | -62.3566 | 60.0998 | 60.1044 | 62.2284 | 62.3428 | 122.4792 | 62.1506 | 60.1593
4089.2344 | 0.030518 | 0.39734 | -0.76797 | -0.22217 | 0.13458 | -0.24033 | -0.18585 | 60.1456 | -62.0682 | -0.036621 | -62.2879 | 60.2234 | 62.1918 | 62.1735 | 0.045776 | -0.099335 | 0.041656 | 0.29373 | -0.11963 | -0.1944 | -0.086975 | -0.10071 | -62.4802 | 60.1776 | 60.1227 | 62.2559 | 62.3383 | 122.4701 | 62.2009 | 60.1959
4090.9062 | 0.030518 | 0.40482 | -0.77011 | -0.23071 | 0.1207 | -0.2446 | -0.18265 | 60.1273 | -62.0911 | -0.068665 | -62.2833 | 60.2325 | 62.2192 | 62.1872 | 0.045776 | -0.098267 | 0.042725 | 0.28305 | -0.13458 | -0.17731 | -0.09613 | -0.10071 | -62.4664 | 60.1547 | 60.173 | 62.2284 | 62.3749 | 122.4655 | 62.1826 | 60.2051
4092.5781 | 0.061035 | 0.38452 | -0.77866 | -0.24994 | 0.10788 | -0.30121 | -0.1976 | 60.1776 | -61.9308 | 0.091553 | -62.2192 | 60.1776 | 62.1689 | 62.1597 | 0.045776 | -0.12176 | 0.050201 | 0.27557 | -0.16235 | -0.1741 | 0.10071 | 0.19684 | -62.3108 | 60.0861 | 60.0769 | 62.2101 | 62.3337 | 122.5754 | 62.1277 | 60.141
4094.25 | 0.061035 | 0.37918 | -0.79788 | -0.23178 | 0.10468 | -0.28519 | -0.20508 | 60.1685 | -61.9537 | 0.032043 | -62.2559 | 60.1593 | 62.1918 | 62.1368 | 0.030518 | -0.1207 | 0.033112 | 0.28412 | -0.14847 | -0.18372 | 0.022888 | 0.059509 | -62.384 | 60.0952 | 60.0998 | 62.2238 | 62.3611 | 122.4518 | 62.1872 | 60.1868
4095.9062 | 0.045776 | 0.41122 | -0.7637 | -0.24033 | 0.10468 | -0.23498 | -0.17838 | 60.2325 | -61.9766 | 0.064087 | -62.2375 | 60.2692 | 62.1872 | 62.1826 | 0.061035 | -0.091858 | 0.057678 | 0.27985 | -0.1442 | -0.19546 | 0.041199 | 0.068665 | -62.4023 | 60.173 | 60.1456 | 62.2101 | 62.3383 | 122.5891 | 62.1277 | 60.2097
4097.5781 | 0.045776 | 0.38773 | -0.77438 | -0.26489 | 0.11963 | -0.2948 | -0.19333 | 60.1776 | -61.9263 | 0.10986 | -62.2101 | 60.1639 | 62.1918 | 62.1323 | 0.030518 | -0.11749 | 0.049133 | 0.27237 | -0.1709 | -0.18372 | 0.1236 | 0.21973 | -62.3108 | 60.0861 | 60.0723 | 62.2147 | 62.3428 | 122.58 | 62.1323 | 60.1593
4099.2969 | 0.061035 | 0.40482 | -0.7637 | -0.23071 | 0.11429 | -0.23605 | -0.18158 | 60.1913 | -61.9904 | 0.004578 | -62.2604 | 60.2188 | 62.2055 | 62.178 | 0.061035 | -0.098267 | 0.049133 | 0.28732 | -0.1239 | -0.18692 | -0.041199 | -0.050354 | -62.4619 | 60.1501 | 60.1273 | 62.2375 | 62.3474 | 122.4518 | 62.1826 | 60.1959
4100.9688 | 0.030518 | 0.39841 | -0.784 | -0.25848 | 0.11749 | -0.26596 | -0.18799 | 60.1501 | -61.9812 | 0.07782 | -62.2559 | 60.2234 | 62.2009 | 62.1735 | 0.045776 | -0.10895 | 0.05661 | 0.27557 | -0.15808 | -0.19012 | 0.064087 | 0.14648 | -62.4069 | 60.173 | 60.1685 | 62.2238 | 62.3337 | 122.5296 | 62.1323 | 60.1868
4102.6719 | 0.045776 | 0.3952 | -0.77652 | -0.23926 | 0.10361 | -0.27771 | -0.19653 | 60.1685 | -61.9446 | 0.036621 | -62.2604 | 60.173 | 62.178 | 62.1689 | 0.045776 | -0.12604 | 0.042725 | 0.28091 | -0.15915 | -0.1741 | 0.050354 | 0.091553 | -62.3703 | 60.0769 | 60.0906 | 62.1964 | 62.3428 | 122.4518 | 62.178 | 60.1822
4104.3438 | 0.061035 | 0.38879 | -0.76691 | -0.22324 | 0.11856 | -0.23819 | -0.18585 | 60.1547 | -62.0407 | -0.050354 | -62.2971 | 60.2371 | 62.1872 | 62.1918 | 0.045776 | -0.098267 | 0.05661 | 0.29159 | -0.1442 | -0.18478 | -0.068665 | -0.086975 | -62.4527 | 60.1364 | 60.141 | 62.2238 | 62.3474 | 122.493 | 62.1918 | 60.1822
4106 | 0.030518 | 0.41763 | -0.77545 | -0.2681 | 0.12604 | -0.27023 | -0.18692 | 60.1547 | -62.0041 | 0.045776 | -62.2604 | 60.2325 | 62.1826 | 62.178 | 0.045776 | -0.10361 | 0.066223 | 0.28198 | -0.16342 | -0.17838 | 0.027466 | 0.091553 | -62.4207 | 60.173 | 60.1318 | 62.2192 | 62.3337 | 122.5754 | 62.146 | 60.1456
4107.6875 | 0.061035 | 0.39414 | -0.77331 | -0.22751 | 0.1239 | -0.26489 | -0.16876 | 60.1547 | -62.0178 | -0.054932 | -62.2787 | 60.2097 | 62.178 | 62.1872 | 0.061035 | -0.11002 | 0.048065 | 0.28519 | -0.14313 | -0.18372 | -0.018311 | -0.027466 | -62.3795 | 60.0952 | 60.0906 | 62.1964 | 62.3337 | 122.4838 | 62.2055 | 60.1593
4109.4062 | 0.030518 | 0.39093 | -0.77866 | -0.23392 | 0.10361 | -0.25955 | -0.18692 | 60.1639 | -61.9995 | -0.027466 | -62.2604 | 60.1959 | 62.1826 | 62.178 | 0.061035 | -0.10361 | 0.053406 | 0.29266 | -0.14099 | -0.18585 | 0.004578 | 0.018311 | -62.3566 | 60.0861 | 60.0998 | 62.2009 | 62.3291 | 122.493 | 62.1964 | 60.1593
4111.0781 | 0.045776 | 0.41122 | -0.76584 | -0.24674 | 0.11749 | -0.25848 | -0.18372 | 60.1501 | -62.0087 | 0.036621 | -62.2559 | 60.2371 | 62.2101 | 62.1964 | 0.061035 | -0.09613 | 0.050201 | 0.28198 | -0.1474 | -0.18265 | 0.032043 | 0.07782 | -62.4252 | 60.1685 | 60.1959 | 62.2284 | 62.3337 | 122.58 | 62.1368 | 60.173
4112.7656 | 0.045776 | 0.38345 | -0.77652 | -0.22324 | 0.1239 | -0.25742 | -0.18265 | 60.1547 | -61.9995 | -0.041199 | -62.265 | 60.1868 | 62.1872 | 62.1597 | 0.030518 | -0.10895 | 0.043793 | 0.27771 | -0.14526 | -0.17197 | -0.013733 | 0.009155 | -62.3474 | 60.1044 | 60.0952 | 62.1826 | 62.3337 | 122.5021 | 62.1918 | 60.1547
4114.4844 | 0.030518 | 0.40909 | -0.77759 | -0.24994 | 0.12711 | -0.27771 | -0.18478 | 60.1273 | -61.9995 | 0.064087 | -62.2559 | 60.2417 | 62.1964 | 62.1597 | 0.045776 | -0.11963 | 0.055542 | 0.27344 | -0.1474 | -0.17944 | 0.032043 | 0.11902 | -62.4115 | 60.1822 | 60.141 | 62.2284 | 62.352 | 122.5433 | 62.1368 | 60.1685
4116.1562 | 0.061035 | 0.41016 | -0.7605 | -0.25635 | 0.1239 | -0.26489 | -0.18692 | 60.1364 | -62.0087 | 0.032043 | -62.2559 | 60.26 | 62.1918 | 62.178 | 0.061035 | -0.099335 | 0.064087 | 0.28198 | -0.16129 | -0.18265 | 0.022888 | 0.086975 | -62.4344 | 60.1547 | 60.1364 | 62.2421 | 62.3703 | 122.5891 | 62.1185 | 60.1547
4117.8438 | 0.045776 | 0.392 | -0.78186 | -0.25528 | 0.1239 | -0.29053 | -0.1976 | 60.1913 | -61.8851 | 0.15106 | -62.2101 | 60.1913 | 62.1643 | 62.1506 | 0.030518 | -0.12924 | 0.040588 | 0.2713 | -0.16769 | -0.1741 | 0.15106 | 0.24261 | -62.2879 | 60.0769 | 60.0861 | 62.1964 | 62.3245 | 122.5845 | 62.1277 | 60.1456
4119.5156 | 0.061035 | 0.38879 | -0.77118 | -0.2243 | 0.11643 | -0.26169 | -0.18585 | 60.1501 | -62.0316 | -0.073242 | -62.2879 | 60.2097 | 62.1826 | 62.178 | 0.045776 | -0.095062 | 0.042725 | 0.28091 | -0.14313 | -0.18906 | -0.059509 | -0.068665 | -62.4252 | 60.1318 | 60.1181 | 62.2192 | 62.3383 | 122.4976 | 62.178 | 60.1822
4121.2031 | 0.045776 | 0.39734 | -0.77438 | -0.25848 | 0.1207 | -0.28198 | -0.19333 | 60.2097 | -61.9034 | 0.15106 | -62.2101 | 60.1547 | 62.2009 | 62.1643 | 0.030518 | -0.11856 | 0.059814 | 0.27985 | -0.16449 | -0.18051 | 0.12817 | 0.24261 | -62.3245 | 60.1181 | 60.1089 | 62.2055 | 62.3383 | 122.5204 | 62.1277 | 60.1776
4122.875 | 0.045776 | 0.392 | -0.77118 | -0.27237 | 0.11856 | -0.28305 | -0.19119 | 60.2097 | -61.8851 | 0.14191 | -62.2101 | 60.1822 | 62.1872 | 62.1643 | 0.045776 | -0.11429 | 0.050201 | 0.28091 | -0.16876 | -0.18906 | 0.14648 | 0.23346 | -62.2787 | 60.0769 | 60.0723 | 62.1964 | 62.3428 | 122.5708 | 62.1506 | 60.141
4124.5625 | 0.045776 | 0.40482 | -0.77438 | -0.2446 | 0.12497 | -0.2713 | -0.19119 | 60.1913 | -61.9034 | 0.13275 | -62.2101 | 60.2188 | 62.1918 | 62.1552 | 0.045776 | -0.11536 | 0.037384 | 0.27557 | -0.14954 | -0.18799 | 0.091553 | 0.17853 | -62.3932 | 60.173 | 60.1273 | 62.2147 | 62.3337 | 122.5342 | 62.1323 | 60.1593
4126.2344 | 0.061035 | 0.38773 | -0.77438 | -0.22644 | 0.11749 | -0.26169 | -0.18051 | 60.2097 | -61.9217 | 0.041199 | -62.2147 | 60.1593 | 62.1872 | 62.1643 | 0.061035 | -0.12176 | 0.036316 | 0.27557 | -0.1506 | -0.19333 | 0.050354 | 0.086975 | -62.3383 | 60.0815 | 60.0677 | 62.2101 | 62.3337 | 122.4152 | 62.1872 | 60.1776
4127.9375 | 0.045776 | 0.38132 | -0.78079 | -0.22644 | 0.10574 | -0.26596 | -0.18051 | 60.2188 | -61.9171 | 0.036621 | -62.2101 | 60.1501 | 62.1964 | 62.1643 | 0.061035 | -0.10147 | 0.050201 | 0.27344 | -0.14206 | -0.18051 | 0.032043 | 0.064087 | -62.3383 | 60.054 | 60.0677 | 62.2192 | 62.3245 | 122.4472 | 62.1826 | 60.1318
4129.6094 | 0.030518 | 0.392 | -0.76691 | -0.22217 | 0.11002 | -0.2478 | -0.18478 | 60.1593 | -62.0728 | -0.064087 | -62.2971 | 60.2325 | 62.2147 | 62.178 | 0.030518 | -0.095062 | 0.044861 | 0.27664 | -0.13245 | -0.19333 | -0.068665 | -0.10529 | -62.4756 | 60.173 | 60.1639 | 62.2284 | 62.3291 | 122.4655 | 62.1872 | 60.1959
4131.2812 | 0.030518 | 0.38879 | -0.78293 | -0.25101 | 0.11108 | -0.27771 | -0.19119 | 60.2051 | -61.9263 | 0.1236 | -62.2192 | 60.2097 | 62.1826 | 62.146 | 0.045776 | -0.10468 | 0.044861 | 0.28519 | -0.15381 | -0.18158 | 0.082397 | 0.17853 | -62.3749 | 60.1501 | 60.1501 | 62.1964 | 62.3428 | 122.525 | 62.1323 | 60.1959
4132.9531 | 0.030518 | 0.3717 | -0.77972 | -0.24139 | 0.12176 | -0.2681 | -0.18372 | 60.2005 | -61.9171 | 0.064087 | -62.2238 | 60.1547 | 62.1918 | 62.1735 | 0.045776 | -0.12497 | 0.048065 | 0.29053 | -0.1474 | -0.18478 | 0.041199 | 0.09613 | -62.3337 | 60.0906 | 60.0952 | 62.2238 | 62.3474 | 122.4564 | 62.1872 | 60.1593
4134.6562 | 0.061035 | 0.38452 | -0.784 | -0.23926 | 0.11215 | -0.28198 | -0.17731 | 60.1639 | -61.9583 | 0.041199 | -62.2513 | 60.2005 | 62.178 | 62.1643 | 0.061035 | -0.1239 | 0.055542 | 0.28198 | -0.15915 | -0.1944 | 0.032043 | 0.073242 | -62.3795 | 60.0998 | 60.0632 | 62.1964 | 62.3566 | 122.4335 | 62.1964 | 60.1685
4136.3281 | 0.045776 | 0.38666 | -0.77118 | -0.22537 | 0.10574 | -0.24139 | -0.18158 | 60.1868 | -61.9995 | -0.041199 | -62.2513 | 60.1959 | 62.1826 | 62.1689 | 0.045776 | -0.10468 | 0.048065 | 0.29159 | -0.13458 | -0.1976 | 0.009155 | 0.018311 | -62.3703 | 60.1135 | 60.0861 | 62.1964 | 62.3245 | 122.5067 | 62.1826 | 60.1456
4137.9844 | 0.045776 | 0.40695 | -0.75623 | -0.24674 | 0.11536 | -0.24994 | -0.19119 | 60.1639 | -62.0087 | 0.054932 | -62.2421 | 60.26 | 62.2009 | 62.1826 | 0.061035 | -0.093994 | 0.058746 | 0.28091 | -0.15167 | -0.1976 | 0.032043 | 0.10529 | -62.4069 | 60.1822 | 60.1685 | 62.2055 | 62.3108 | 122.58 | 62.1231 | 60.141
4139.6719 | 0.015259 | 0.39307 | -0.77972 | -0.23178 | 0.10361 | -0.24674 | -0.17731 | 60.1456 | -62.0453 | -0.068665 | -62.2833 | 60.2325 | 62.2055 | 62.1872 | 0.076294 | -0.092926 | 0.05661 | 0.29053 | -0.14206 | -0.18799 | -0.045776 | -0.054932 | -62.4298 | 60.1181 | 60.1364 | 62.2238 | 62.3566 | 122.493 | 62.1735 | 60.1822
4141.3438 | 0.045776 | 0.38773 | -0.78934 | -0.2478 | 0.1207 | -0.28839 | -0.17303 | 60.1913 | -61.9308 | 0.13733 | -62.2055 | 60.2051 | 62.178 | 62.1506 | 0.045776 | -0.11002 | 0.061951 | 0.27344 | -0.16769 | -0.17838 | 0.073242 | 0.1831 | -62.3749 | 60.1501 | 60.1364 | 62.2147 | 62.3474 | 122.5296 | 62.1323 | 60.1776
4143.0156 | 0.030518 | 0.38132 | -0.78827 | -0.24246 | 0.12711 | -0.28412 | -0.19546 | 60.1501 | -61.9537 | 0.032043 | -62.2421 | 60.1822 | 62.1826 | 62.1414 | 0.045776 | -0.12283 | 0.05127 | 0.27344 | -0.15488 | -0.17944 | 0.022888 | 0.086975 | -62.3749 | 60.054 | 60.0906 | 62.233 | 62.3657 | 122.4564 | 62.1689 | 60.1456
4144.6875 | 0.061035 | 0.39734 | -0.75943 | -0.23285 | 0.12176 | -0.24139 | -0.18158 | 60.1547 | -62.0407 | -0.07782 | -62.2833 | 60.2371 | 62.2147 | 62.1872 | 0.076294 | -0.1004 | 0.05661 | 0.28305 | -0.13992 | -0.18692 | -0.068665 | -0.091553 | -62.439 | 60.1685 | 60.1364 | 62.2009 | 62.3383 | 122.4747 | 62.1643 | 60.1685
4146.4062 | 0.030518 | 0.39414 | -0.76584 | -0.24139 | 0.10895 | -0.2478 | -0.18158 | 60.1181 | -62.059 | -0.036621 | -62.2833 | 60.2234 | 62.2055 | 62.1918 | 0.045776 | -0.097198 | 0.053406 | 0.27985 | -0.13672 | -0.19012 | -0.091553 | -0.07782 | -62.4756 | 60.1547 | 60.1593 | 62.2467 | 62.3657 | 122.4518 | 62.1826 | 60.1913
4148.0781 | 0.030518 | 0.41336 | -0.7637 | -0.25207 | 0.11322 | -0.27237 | -0.19546 | 60.1227 | -61.9675 | 0.082397 | -62.2513 | 60.1959 | 62.1918 | 62.1689 | 0.061035 | -0.11322 | 0.063019 | 0.28305 | -0.16769 | -0.17944 | 0.045776 | 0.13275 | -62.4115 | 60.173 | 60.1456 | 62.2375 | 62.3611 | 122.5342 | 62.1414 | 60.1685
4149.75 | 0.061035 | 0.39307 | -0.76584 | -0.23498 | 0.10468 | -0.24994 | -0.18692 | 60.1364 | -62.0361 | -0.073242 | -62.2879 | 60.2417 | 62.2009 | 62.178 | 0.045776 | -0.10361 | 0.05127 | 0.29159 | -0.13992 | -0.18692 | -0.073242 | -0.068665 | -62.4344 | 60.1547 | 60.1501 | 62.2238 | 62.3428 | 122.5021 | 62.178 | 60.1685
4151.4688 | 0.061035 | 0.41122 | -0.75729 | -0.25207 | 0.11108 | -0.25314 | -0.17838 | 60.1822 | -61.9766 | 0.082397 | -62.2375 | 60.228 | 62.1689 | 62.1872 | 0.030518 | -0.10254 | 0.049133 | 0.27664 | -0.1506 | -0.19119 | 0.032043 | 0.07782 | -62.3932 | 60.1776 | 60.1547 | 62.1964 | 62.3383 | 122.5845 | 62.1231 | 60.1822
4153.1406 | 0.045776 | 0.37598 | -0.77331 | -0.26276 | 0.11429 | -0.2948 | -0.19653 | 60.1181 | -61.9812 | 0.032043 | -62.2513 | 60.1685 | 62.1964 | 62.1826 | 0.030518 | -0.11856 | 0.057678 | 0.27664 | -0.17197 | -0.17944 | 0.027466 | 0.10071 | -62.3703 | 60.0815 | 60.0998 | 62.2101 | 62.3703 | 122.4701 | 62.1918 | 60.173
4154.8281 | 0.061035 | 0.41122 | -0.77972 | -0.24033 | 0.11643 | -0.25955 | -0.18799 | 60.1593 | -62.0041 | 0.045776 | -62.2559 | 60.2554 | 62.1735 | 62.1964 | 0.015259 | -0.11002 | 0.049133 | 0.28946 | -0.14633 | -0.17731 | 0.018311 | 0.09613 | -62.4207 | 60.1959 | 60.1685 | 62.2055 | 62.3337 | 122.5662 | 62.1506 | 60.1639
4156.5312 | 0.061035 | 0.38345 | -0.77011 | -0.2179 | 0.11536 | -0.27023 | -0.18799 | 60.2051 | -61.9263 | 0.045776 | -62.2238 | 60.1685 | 62.1826 | 62.1506 | 0.061035 | -0.11108 | 0.043793 | 0.28839 | -0.14847 | -0.18692 | 0.027466 | 0.09613 | -62.3383 | 60.0586 | 60.0998 | 62.2192 | 62.3245 | 122.4518 | 62.1826 | 60.1913
4158.2031 | 0.061035 | 0.40695 | -0.75729 | -0.23926 | 0.12497 | -0.24033 | -0.18585 | 60.2188 | -61.9583 | 0.064087 | -62.2192 | 60.2463 | 62.1735 | 62.1735 | 0.061035 | -0.093994 | 0.055542 | 0.28732 | -0.14526 | -0.18906 | 0.032043 | 0.059509 | -62.4023 | 60.1547 | 60.1547 | 62.2238 | 62.3291 | 122.5525 | 62.1414 | 60.1776
4159.875 | 0.061035 | 0.41443 | -0.75729 | -0.24674 | 0.11002 | -0.2478 | -0.18478 | 60.2188 | -61.9492 | 0.054932 | -62.233 | 60.228 | 62.178 | 62.1918 | 0.030518 | -0.10574 | 0.064087 | 0.29053 | -0.13886 | -0.19226 | 0.036621 | 0.082397 | -62.3886 | 60.1685 | 60.1318 | 62.2147 | 62.3383 | 122.5479 | 62.1735 | 60.173
4161.5625 | 0.061035 | 0.38666 | -0.77225 | -0.26489 | 0.10574 | -0.30014 | -0.19012 | 60.1135 | -61.9583 | 0.073242 | -62.233 | 60.1868 | 62.1872 | 62.1735 | 0.061035 | -0.12817 | 0.055542 | 0.28412 | -0.16342 | -0.18265 | 0.082397 | 0.16022 | -62.3154 | 60.0906 | 60.054 | 62.2238 | 62.3428 | 122.5571 | 62.1323 | 60.1685
4163.2344 | 0.045776 | 0.38452 | -0.78613 | -0.22964 | 0.11749 | -0.27237 | -0.1976 | 60.2005 | -61.9171 | 0.041199 | -62.2238 | 60.1547 | 62.1552 | 62.1506 | 0.061035 | -0.11749 | 0.040588 | 0.28412 | -0.14313 | -0.18478 | 0.036621 | 0.10071 | -62.3337 | 60.0952 | 60.0632 | 62.2192 | 62.3383 | 122.4243 | 62.1735 | 60.1685
4164.9219 | 0.015259 | 0.40161 | -0.76797 | -0.22964 | 0.11215 | -0.24674 | -0.19546 | 60.1501 | -62.0544 | -0.07782 | -62.2787 | 60.2371 | 62.178 | 62.1872 | 0.045776 | -0.093994 | 0.053406 | 0.28519 | -0.12817 | -0.18372 | -0.082397 | -0.10529 | -62.4619 | 60.1822 | 60.1593 | 62.233 | 62.3428 | 122.4655 | 62.1643 | 60.1913
4166.5938 | 0.030518 | 0.3952 | -0.76263 | -0.24353 | 0.11429 | -0.25101 | -0.18158 | 60.2005 | -61.972 | 0.036621 | -62.2375 | 60.2371 | 62.1689 | 62.1643 | 0.045776 | -0.088654 | 0.064087 | 0.27985 | -0.14206 | -0.18799 | -0.004578 | 0 | -62.4298 | 60.1501 | 60.1501 | 62.2009 | 62.352 | 122.4701 | 62.1735 | 60.2051
4168.2969 | 0.030518 | 0.38345 | -0.77545 | -0.26703 | 0.11429 | -0.30014 | -0.20081 | 60.1456 | -61.94 | 0.09613 | -62.2375 | 60.173 | 62.1918 | 62.1552 | 0.061035 | -0.12711 | 0.045929 | 0.27664 | -0.17731 | -0.17731 | 0.10529 | 0.20142 | -62.3016 | 60.0815 | 60.0906 | 62.2192 | 62.3337 | 122.5708 | 62.1185 | 60.141
4169.9688 | 0.061035 | 0.392 | -0.77331 | -0.23712 | 0.11429 | -0.26276 | -0.18372 | 60.1593 | -62.0132 | 0.041199 | -62.2604 | 60.2417 | 62.2009 | 62.178 | 0.030518 | -0.10574 | 0.054474 | 0.28946 | -0.14847 | -0.19119 | 0.013733 | 0.091553 | -62.4161 | 60.1822 | 60.173 | 62.1964 | 62.3337 | 122.5983 | 62.1048 | 60.1593
4171.6406 | 0.061035 | 0.40588 | -0.76584 | -0.25314 | 0.12176 | -0.26169 | -0.19653 | 60.1318 | -62.0132 | 0.050354 | -62.2559 | 60.2646 | 62.1872 | 62.178 | 0.061035 | -0.10788 | 0.058746 | 0.28946 | -0.1506 | -0.17624 | 0.027466 | 0.091553 | -62.4115 | 60.173 | 60.1593 | 62.2147 | 62.3657 | 122.5891 | 62.1002 | 60.141
4173.3125 | 0.061035 | 0.38879 | -0.78827 | -0.26596 | 0.1239 | -0.29587 | -0.19546 | 60.1776 | -61.8851 | 0.13275 | -62.2055 | 60.1547 | 62.1597 | 62.1506 | 0.045776 | -0.1207 | 0.050201 | 0.27237 | -0.17197 | -0.1741 | 0.15106 | 0.23804 | -62.2787 | 60.0906 | 60.0906 | 62.2055 | 62.3428 | 122.5754 | 62.146 | 60.1456
4174.9844 | 0.030518 | 0.39307 | -0.77866 | -0.22324 | 0.11963 | -0.2478 | -0.19012 | 60.1501 | -62.0224 | -0.059509 | -62.2879 | 60.2188 | 62.2147 | 62.1918 | 0.045776 | -0.093994 | 0.050201 | 0.27878 | -0.13992 | -0.19653 | -0.050354 | -0.073242 | -62.4298 | 60.1364 | 60.1181 | 62.2284 | 62.352 | 122.4838 | 62.1826 | 60.1639
4176.6875 | 0.030518 | 0.38666 | -0.75836 | -0.22858 | 0.11856 | -0.22751 | -0.18265 | 60.1273 | -62.0087 | -0.022888 | -62.2604 | 60.2005 | 62.2055 | 62.1689 | 0.076294 | -0.086517 | 0.053406 | 0.28198 | -0.13138 | -0.18585 | -0.068665 | -0.054932 | -62.4619 | 60.1776 | 60.1227 | 62.2284 | 62.3749 | 122.4426 | 62.1826 | 60.1822
4178.4062 | 0.045776 | 0.41336 | -0.76263 | -0.24353 | 0.1207 | -0.25207 | -0.18585 | 60.1913 | -61.9492 | 0.073242 | -62.2147 | 60.2234 | 62.1597 | 62.178 | 0.061035 | -0.097198 | 0.059814 | 0.28091 | -0.14526 | -0.18478 | 0.027466 | 0.068665 | -62.384 | 60.1547 | 60.1227 | 62.2238 | 62.3337 | 122.5342 | 62.146 | 60.1456
4180.0625 | 0.045776 | 0.40054 | -0.78934 | -0.25101 | 0.10681 | -0.29053 | -0.18799 | 60.173 | -61.8759 | 0.15106 | -62.1964 | 60.1822 | 62.1826 | 62.1552 | 0.045776 | -0.12604 | 0.049133 | 0.26489 | -0.16342 | -0.17624 | 0.1236 | 0.24719 | -62.3154 | 60.1364 | 60.1044 | 62.2192 | 62.3337 | 122.5388 | 62.1323 | 60.1868
4181.7344 | 0.045776 | 0.40802 | -0.76263 | -0.27451 | 0.11749 | -0.2713 | -0.19119 | 60.1181 | -61.9675 | 0.07782 | -62.2513 | 60.2234 | 62.1964 | 62.1643 | 0.045776 | -0.12176 | 0.065155 | 0.27557 | -0.16342 | -0.19119 | 0.045776 | 0.12817 | -62.4069 | 60.1547 | 60.1273 | 62.2467 | 62.3474 | 122.525 | 62.1231 | 60.1868
4183.4531 | 0.030518 | 0.39734 | -0.77118 | -0.27023 | 0.10788 | -0.2713 | -0.19867 | 60.1822 | -61.908 | 0.14648 | -62.1964 | 60.2097 | 62.1872 | 62.1597 | 0.076294 | -0.11002 | 0.060883 | 0.2681 | -0.16235 | -0.18692 | 0.10529 | 0.20599 | -62.3703 | 60.1364 | 60.1089 | 62.2055 | 62.3245 | 122.5204 | 62.1323 | 60.1639
4185.125 | 0.045776 | 0.37811 | -0.77545 | -0.24033 | 0.11429 | -0.26489 | -0.19119 | 60.1776 | -61.9308 | 0.064087 | -62.2284 | 60.1639 | 62.2055 | 62.1414 | 0.045776 | -0.11536 | 0.046997 | 0.28412 | -0.13565 | -0.19119 | 0.041199 | 0.10071 | -62.3337 | 60.0769 | 60.0769 | 62.2009 | 62.3749 | 122.4289 | 62.1826 | 60.1868
4186.8281 | 0.045776 | 0.39093 | -0.784 | -0.25421 | 0.11643 | -0.28946 | -0.19333 | 60.1181 | -61.9629 | 0.050354 | -62.2467 | 60.1868 | 62.178 | 62.1735 | 0.061035 | -0.12176 | 0.052338 | 0.28091 | -0.16983 | -0.18372 | 0.064087 | 0.14191 | -62.3383 | 60.1181 | 60.0723 | 62.2009 | 62.3199 | 122.5388 | 62.1689 | 60.1501
4188.5156 | 0.045776 | 0.38345 | -0.77759 | -0.24674 | 0.11215 | -0.28198 | -0.1944 | 60.2188 | -61.8576 | 0.14648 | -62.1964 | 60.173 | 62.1735 | 62.1643 | 0.045776 | -0.1207 | 0.037384 | 0.27771 | -0.15488 | -0.18265 | 0.14191 | 0.26093 | -62.2925 | 60.0952 | 60.0769 | 62.2055 | 62.3199 | 122.5616 | 62.114 | 60.1456
4190.1875 | 0.030518 | 0.38132 | -0.78507 | -0.23178 | 0.11215 | -0.28091 | -0.1944 | 60.1456 | -61.9766 | 0.027466 | -62.2604 | 60.1547 | 62.1735 | 62.1964 | 0.045776 | -0.11643 | 0.043793 | 0.27344 | -0.15701 | -0.18158 | 0.018311 | 0.086975 | -62.3795 | 60.0906 | 60.0998 | 62.2147 | 62.3566 | 122.4609 | 62.1735 | 60.1776
4191.8594 | 0.045776 | 0.3685 | -0.77438 | -0.23071 | 0.10681 | -0.26703 | -0.18585 | 60.2188 | -61.9125 | 0.041199 | -62.2192 | 60.1547 | 62.2009 | 62.1643 | 0.045776 | -0.11002 | 0.054474 | 0.27237 | -0.13779 | -0.19974 | 0.032043 | 0.068665 | -62.3611 | 60.0815 | 60.0723 | 62.2238 | 62.3611 | 122.4426 | 62.1964 | 60.1913
4193.5312 | 0.045776 | 0.392 | -0.78613 | -0.2179 | 0.10788 | -0.24994 | -0.19226 | 60.2234 | -61.9583 | 0.004578 | -62.2375 | 60.1913 | 62.1826 | 62.1735 | 0.015259 | -0.095062 | 0.045929 | 0.28091 | -0.13779 | -0.18692 | 0.022888 | 0.050354 | -62.3383 | 60.1089 | 60.0998 | 62.2101 | 62.3016 | 122.4976 | 62.1918 | 60.1776
4195.2188 | 0.061035 | 0.38345 | -0.76797 | -0.22644 | 0.11108 | -0.25207 | -0.17517 | 60.1639 | -62.0224 | -0.068665 | -62.2925 | 60.2234 | 62.1918 | 62.178 | 0.045776 | -0.092926 | 0.042725 | 0.28519 | -0.12604 | -0.18478 | -0.045776 | -0.073242 | -62.4298 | 60.141 | 60.1273 | 62.2238 | 62.3611 | 122.493 | 62.1872 | 60.1913
4196.8906 | 0.076294 | 0.39307 | -0.76157 | -0.22858 | 0.09613 | -0.25207 | -0.17838 | 60.1547 | -62.0132 | -0.064087 | -62.265 | 60.2142 | 62.2009 | 62.178 | 0.030518 | -0.10574 | 0.03952 | 0.28305 | -0.12817 | -0.18692 | -0.032043 | -0.036621 | -62.4069 | 60.1089 | 60.1227 | 62.2604 | 62.3383 | 122.4976 | 62.1964 | 60.1547
4198.5781 | 0.045776 | 0.38345 | -0.77972 | -0.26916 | 0.12176 | -0.28946 | -0.19867 | 60.2051 | -61.8759 | 0.15564 | -62.1918 | 60.1776 | 62.146 | 62.1323 | 0.076294 | -0.11536 | 0.054474 | 0.2681 | -0.16235 | -0.18265 | 0.15564 | 0.24261 | -62.3016 | 60.0998 | 60.0952 | 62.1964 | 62.3428 | 122.5479 | 62.1048 | 60.1364
4200.25 | 0.061035 | 0.38238 | -0.77331 | -0.23071 | 0.11536 | -0.25101 | -0.19012 | 60.228 | -61.9354 | 0.032043 | -62.2101 | 60.1547 | 62.178 | 62.1506 | 0.045776 | -0.10788 | 0.037384 | 0.27557 | -0.13458 | -0.18158 | 0.032043 | 0.068665 | -62.352 | 60.0632 | 60.0632 | 62.2009 | 62.3428 | 122.4838 | 62.1826 | 60.1913
4201.9219 | 0.045776 | 0.40695 | -0.76797 | -0.2211 | 0.11108 | -0.24887 | -0.18585 | 60.1593 | -62.0407 | -0.022888 | -62.2787 | 60.2417 | 62.1918 | 62.1689 | 0.030518 | -0.095062 | 0.053406 | 0.28305 | -0.12924 | -0.19226 | -0.07782 | -0.064087 | -62.4619 | 60.1868 | 60.1364 | 62.2192 | 62.3703 | 122.4426 | 62.1826 | 60.1868
4203.5938 | 0.030518 | 0.39734 | -0.76904 | -0.26276 | 0.11536 | -0.28412 | -0.18265 | 60.1959 | -61.8805 | 0.15564 | -62.2055 | 60.173 | 62.1689 | 62.1689 | 0.061035 | -0.12497 | 0.042725 | 0.27878 | -0.16876 | -0.17624 | 0.13275 | 0.2655 | -62.3337 | 60.1044 | 60.141 | 62.2009 | 62.3337 | 122.5433 | 62.1414 | 60.1547
4205.2656 | 0.045776 | 0.392 | -0.79788 | -0.24674 | 0.11322 | -0.28412 | -0.1944 | 60.2005 | -61.8713 | 0.13275 | -62.2009 | 60.1868 | 62.1964 | 62.1552 | 0.030518 | -0.1239 | 0.048065 | 0.28091 | -0.15381 | -0.17838 | 0.15106 | 0.23804 | -62.2833 | 60.0861 | 60.0906 | 62.1918 | 62.3154 | 122.5708 | 62.114 | 60.1456
4206.9219 | 0.045776 | 0.38559 | -0.77011 | -0.24567 | 0.11963 | -0.24994 | -0.19974 | 60.1822 | -61.9858 | -0.022888 | -62.2559 | 60.1913 | 62.1826 | 62.146 | 0.045776 | -0.10361 | 0.046997 | 0.27878 | -0.13351 | -0.19226 | 0.013733 | 0.027466 | -62.352 | 60.1044 | 60.1089 | 62.2147 | 62.3291 | 122.5113 | 62.1918 | 60.1639
4208.6406 | 0.045776 | 0.40161 | -0.77545 | -0.23392 | 0.11856 | -0.2446 | -0.18372 | 60.2188 | -61.9537 | 0.036621 | -62.2375 | 60.2371 | 62.2055 | 62.1506 | 0.061035 | -0.092926 | 0.048065 | 0.28305 | -0.13565 | -0.1944 | -0.013733 | 0.018311 | -62.4252 | 60.1547 | 60.1593 | 62.1918 | 62.352 | 122.4655 | 62.1643 | 60.1959
4210.2969 | 0.061035 | 0.40054 | -0.77866 | -0.2681 | 0.11002 | -0.28091 | -0.19226 | 60.1822 | -61.9125 | 0.12817 | -62.2009 | 60.1913 | 62.1826 | 62.1872 | 0.045776 | -0.1207 | 0.066223 | 0.27664 | -0.15595 | -0.17838 | 0.073242 | 0.17853 | -62.3566 | 60.1776 | 60.1318 | 62.2055 | 62.3383 | 122.5159 | 62.1368 | 60.1776
4211.9844 | 0.045776 | 0.40375 | -0.77118 | -0.26276 | 0.13031 | -0.27344 | -0.18799 | 60.1456 | -61.9812 | 0.086975 | -62.2559 | 60.2325 | 62.2009 | 62.1735 | 0.045776 | -0.11749 | 0.060883 | 0.28305 | -0.1709 | -0.18906 | 0.059509 | 0.1236 | -62.4115 | 60.173 | 60.1227 | 62.2055 | 62.352 | 122.5342 | 62.1185 | 60.1685
4213.6562 | 0.045776 | 0.37811 | -0.78507 | -0.23712 | 0.1004 | -0.27557 | -0.19546 | 60.1776 | -61.9217 | 0.027466 | -62.233 | 60.1685 | 62.1964 | 62.1826 | 0.045776 | -0.11749 | 0.050201 | 0.27664 | -0.1474 | -0.17944 | 0.045776 | 0.07782 | -62.3611 | 60.0723 | 60.0677 | 62.2055 | 62.3566 | 122.4197 | 62.1918 | 60.173
4215.3281 | 0.045776 | 0.39841 | -0.77118 | -0.23071 | 0.12817 | -0.24994 | -0.17517 | 60.1547 | -62.027 | -0.054932 | -62.2833 | 60.2463 | 62.2055 | 62.1506 | 0.045776 | -0.095062 | 0.037384 | 0.27985 | -0.13138 | -0.19119 | -0.032043 | -0.050354 | -62.3932 | 60.1501 | 60.1135 | 62.2192 | 62.3611 | 122.4976 | 62.1689 | 60.1913
4216.9844 | 0.015259 | 0.40588 | -0.75516 | -0.25207 | 0.11856 | -0.25528 | -0.19226 | 60.1593 | -62.0178 | 0.059509 | -62.2375 | 60.2463 | 62.1964 | 62.1689 | 0.061035 | -0.095062 | 0.055542 | 0.28412 | -0.15274 | -0.1944 | 0.027466 | 0.091553 | -62.3886 | 60.1776 | 60.1913 | 62.1964 | 62.3383 | 122.5891 | 62.114 | 60.2005
4218.6719 | 0.045776 | 0.38345 | -0.78079 | -0.24353 | 0.10468 | -0.27985 | -0.19226 | 60.1913 | -61.9308 | 0.041199 | -62.2375 | 60.1364 | 62.1826 | 62.1735 | 0.045776 | -0.12283 | 0.048065 | 0.27664 | -0.15167 | -0.18051 | 0.036621 | 0.086975 | -62.3474 | 60.0861 | 60.0815 | 62.2101 | 62.3383 | 122.4197 | 62.1826 | 60.1685
4220.3438 | 0.045776 | 0.37598 | -0.78293 | -0.23285 | 0.097198 | -0.2446 | -0.19333 | 60.1639 | -62.027 | -0.041199 | -62.2604 | 60.2325 | 62.1918 | 62.1826 | 0.061035 | -0.10147 | 0.03952 | 0.29266 | -0.14847 | -0.19012 | -0.036621 | -0.027466 | -62.3932 | 60.0998 | 60.1135 | 62.2467 | 62.3199 | 122.4976 | 62.1826 | 60.1685
4222 | 0.015259 | 0.41336 | -0.76584 | -0.2478 | 0.10895 | -0.25955 | -0.18585 | 60.141 | -61.9995 | 0.050354 | -62.2467 | 60.2371 | 62.1735 | 62.1735 | 0.045776 | -0.099335 | 0.052338 | 0.28198 | -0.16449 | -0.19119 | 0.032043 | 0.11444 | -62.4069 | 60.173 | 60.1822 | 62.233 | 62.3749 | 122.5754 | 62.114 | 60.1593
4223.6719 | 0.061035 | 0.39414 | -0.76691 | -0.26062 | 0.10574 | -0.29907 | -0.18585 | 60.1639 | -61.9263 | 0.086975 | -62.2055 | 60.1776 | 62.178 | 62.1597 | 0.061035 | -0.1207 | 0.050201 | 0.27878 | -0.16983 | -0.17944 | 0.10529 | 0.21515 | -62.3016 | 60.0952 | 60.0906 | 62.2055 | 62.3474 | 122.5616 | 62.1368 | 60.1364
4225.375 | 0.045776 | 0.392 | -0.77652 | -0.26916 | 0.11643 | -0.28091 | -0.19974 | 60.2005 | -61.8851 | 0.17395 | -62.1964 | 60.1776 | 62.1597 | 62.1552 | 0.045776 | -0.11643 | 0.05127 | 0.27664 | -0.1506 | -0.19119 | 0.13733 | 0.2655 | -62.3199 | 60.0906 | 60.1044 | 62.2375 | 62.3428 | 122.525 | 62.1185 | 60.1547
4227.0625 | 0.045776 | 0.40054 | -0.7637 | -0.2211 | 0.11749 | -0.2478 | -0.18692 | 60.2325 | -61.9583 | 0.050354 | -62.2284 | 60.2554 | 62.1918 | 62.1735 | 0.030518 | -0.095062 | 0.049133 | 0.27985 | -0.13138 | -0.19653 | 0.027466 | 0.032043 | -62.4115 | 60.173 | 60.141 | 62.2009 | 62.3474 | 122.4884 | 62.1597 | 60.1639
4228.75 | 0.061035 | 0.37384 | -0.79041 | -0.23819 | 0.11215 | -0.27771 | -0.19333 | 60.1547 | -61.9354 | 0.045776 | -62.2375 | 60.1868 | 62.1918 | 62.1689 | 0.061035 | -0.1207 | 0.037384 | 0.27771 | -0.15595 | -0.18372 | 0.027466 | 0.07782 | -62.3611 | 60.1135 | 60.0861 | 62.2101 | 62.352 | 122.438 | 62.1964 | 60.1776
4230.4844 | 0.045776 | 0.38025 | -0.78827 | -0.24353 | 0.11002 | -0.29053 | -0.19012 | 60.1639 | -61.9629 | 0.032043 | -62.2559 | 60.1685 | 62.1872 | 62.1506 | 0.061035 | -0.12283 | 0.044861 | 0.27985 | -0.1474 | -0.18478 | 0.027466 | 0.086975 | -62.3703 | 60.1044 | 60.1181 | 62.2147 | 62.352 | 122.4335 | 62.1964 | 60.173
4232.1562 | 0.045776 | 0.38452 | -0.77866 | -0.2179 | 0.12924 | -0.24567 | -0.19119 | 60.2142 | -61.9629 | -0.013733 | -62.233 | 60.1593 | 62.1964 | 62.1597 | 0.030518 | -0.10681 | 0.048065 | 0.28732 | -0.13992 | -0.1944 | 0.018311 | 0.022888 | -62.3337 | 60.1044 | 60.1089 | 62.2284 | 62.3383 | 122.4701 | 62.2055 | 60.1822
4233.8281 | 0.045776 | 0.40054 | -0.77331 | -0.26169 | 0.12283 | -0.27451 | -0.19653 | 60.2051 | -61.8942 | 0.16022 | -62.2009 | 60.1822 | 62.1826 | 62.1414 | 0.061035 | -0.11856 | 0.053406 | 0.27878 | -0.16342 | -0.17838 | 0.13733 | 0.25635 | -62.3108 | 60.1089 | 60.1135 | 62.2009 | 62.3245 | 122.525 | 62.1231 | 60.1822
4235.5 | 0.061035 | 0.40695 | -0.74875 | -0.24674 | 0.11429 | -0.24567 | -0.19226 | 60.2234 | -61.9537 | 0.068665 | -62.2238 | 60.2325 | 62.1872 | 62.1597 | 0.030518 | -0.09613 | 0.058746 | 0.27878 | -0.13992 | -0.19226 | 0.041199 | 0.054932 | -62.3978 | 60.1776 | 60.1501 | 62.178 | 62.3428 | 122.5113 | 62.1277 | 60.1776
4237.2188 | 0.061035 | 0.39093 | -0.76584 | -0.22751 | 0.11215 | -0.24887 | -0.18799 | 60.1456 | -61.9949 | -0.041199 | -62.2787 | 60.2142 | 62.2238 | 62.178 | 0.076294 | -0.10574 | 0.067291 | 0.29373 | -0.13458 | -0.19012 | -0.027466 | -0.027466 | -62.3886 | 60.1135 | 60.1181 | 62.2101 | 62.3291 | 122.4976 | 62.1872 | 60.1593
4238.8906 | 0.061035 | 0.37705 | -0.77652 | -0.22644 | 0.11322 | -0.27344 | -0.19226 | 60.2051 | -61.9125 | 0.045776 | -62.2147 | 60.1181 | 62.1918 | 62.1506 | 0.061035 | -0.11322 | 0.05127 | 0.27451 | -0.1474 | -0.17838 | 0.045776 | 0.082397 | -62.3245 | 60.0677 | 60.0769 | 62.2101 | 62.3657 | 122.4335 | 62.2055 | 60.1959
4240.5625 | 0.030518 | 0.39414 | -0.77225 | -0.21896 | 0.1004 | -0.25421 | -0.18158 | 60.141 | -62.0453 | -0.082397 | -62.2742 | 60.2142 | 62.1826 | 62.1689 | 0.045776 | -0.088654 | 0.043793 | 0.28305 | -0.13458 | -0.18585 | -0.073242 | -0.068665 | -62.4344 | 60.1547 | 60.1181 | 62.2147 | 62.3474 | 122.4701 | 62.178 | 60.1685
4242.2344 | 0.061035 | 0.39414 | -0.76584 | -0.23392 | 0.10895 | -0.25207 | -0.18265 | 60.1273 | -62.0773 | -0.064087 | -62.2833 | 60.2554 | 62.1964 | 62.178 | 0.045776 | -0.10788 | 0.046997 | 0.27771 | -0.14099 | -0.18478 | -0.082397 | -0.07782 | -62.4619 | 60.1639 | 60.1639 | 62.233 | 62.3611 | 122.4472 | 62.1689 | 60.1868
4243.9062 | 0.045776 | 0.38559 | -0.76584 | -0.24994 | 0.11429 | -0.26062 | -0.17624 | 60.1547 | -62.0041 | -0.004578 | -62.2467 | 60.2188 | 62.1918 | 62.1735 | 0.061035 | -0.10681 | 0.063019 | 0.28305 | -0.13992 | -0.18906 | -0.059509 | -0.045776 | -62.4527 | 60.1501 | 60.1593 | 62.2101 | 62.3611 | 122.4472 | 62.1689 | 60.2097
4245.5625 | 0.030518 | 0.3717 | -0.77866 | -0.26489 | 0.11536 | -0.27451 | -0.20081 | 60.1227 | -61.9583 | 0.10071 | -62.2284 | 60.2188 | 62.1826 | 62.1597 | 0.076294 | -0.11002 | 0.055542 | 0.28305 | -0.16983 | -0.19012 | 0.041199 | 0.13733 | -62.4069 | 60.1547 | 60.1639 | 62.2559 | 62.3566 | 122.525 | 62.1368 | 60.1913
4247.2344 | 0.22888 | 0.41977 | -0.77652 | -0.26276 | 0.11108 | -0.26703 | -0.19226 | 60.1181 | -61.9904 | 0.050354 | -62.2513 | 60.228 | 62.178 | 62.178 | 0.045776 | -0.10574 | 0.063019 | 0.2948 | -0.16663 | -0.19012 | 0.036621 | 0.10529 | -62.4023 | 60.2188 | 60.2051 | 62.2833 | 62.4023 | 122.5662 | 62.1185 | 60.173
4248.9062 | 0.19836 | 0.41977 | -0.78293 | -0.2681 | 0.10788 | -0.27878 | -0.19226 | 60.1135 | -61.9858 | 0.054932 | -62.2604 | 60.2325 | 62.1735 | 62.1735 | 0.061035 | -0.10468 | 0.060883 | 0.29266 | -0.15488 | -0.18906 | 0.050354 | 0.13733 | -62.4115 | 60.1547 | 60.1547 | 62.2421 | 62.3474 | 122.5433 | 62.1277 | 60.1456
4250.5781 | 0.10681 | 0.36743 | -0.77011 | -0.23605 | 0.11963 | -0.29694 | -0.19974 | 60.1089 | -61.9583 | 0.018311 | -62.2513 | 60.2142 | 62.1643 | 62.1552 | 0.030518 | -0.12176 | 0.035248 | 0.2713 | -0.15701 | -0.1741 | 0.013733 | 0.11444 | -62.3566 | 60.0952 | 60.0952 | 62.1918 | 62.3795 | 122.4701 | 62.1552 | 60.1822
4252.2656 | 0.16785 | 0.36529 | -0.75729 | -0.22751 | 0.13138 | -0.27557 | -0.19333 | 60.1822 | -61.9217 | 0.032043 | -62.2238 | 60.1547 | 62.1918 | 62.1414 | 0.045776 | -0.11749 | 0.036316 | 0.2948 | -0.13031 | -0.1741 | 0.068665 | 0.11444 | -62.3062 | 60.1227 | 60.1227 | 62.2513 | 62.3703 | 122.4472 | 62.1872 | 60.1593
4253.9375 | 0.076294 | 0.42831 | -0.76584 | -0.24033 | 0.1239 | -0.24139 | -0.18372 | 60.1913 | -61.9629 | 0.032043 | -62.2421 | 60.2463 | 62.1826 | 62.1872 | 0.045776 | -0.10681 | 0.042725 | 0.28732 | -0.13138 | -0.18478 | -0.018311 | 0.004578 | -62.4115 | 60.1913 | 60.1593 | 62.2238 | 62.3154 | 122.4609 | 62.1597 | 60.1959
4255.6094 | 0.16785 | 0.41763 | -0.77545 | -0.25528 | 0.11643 | -0.25848 | -0.19546 | 60.1364 | -62.0224 | 0.027466 | -62.2421 | 60.2417 | 62.2009 | 62.1964 | 0.030518 | -0.092926 | 0.046997 | 0.27771 | -0.14847 | -0.17838 | 0.022888 | 0.09613 | -62.4161 | 60.2142 | 60.1639 | 62.2101 | 62.3474 | 122.5891 | 62.114 | 60.1776
4257.2812 | 0.045776 | 0.38345 | -0.77545 | -0.2681 | 0.11215 | -0.28091 | -0.18906 | 60.2005 | -61.8713 | 0.16479 | -62.2055 | 60.1685 | 62.1689 | 62.146 | 0.045776 | -0.12497 | 0.052338 | 0.26916 | -0.16022 | -0.19012 | 0.13275 | 0.25635 | -62.3199 | 60.1181 | 60.0906 | 62.2192 | 62.3291 | 122.5433 | 62.1277 | 60.1364
4258.9531 | 0.15259 | 0.43259 | -0.78613 | -0.28625 | 0.11322 | -0.26703 | -0.18906 | 60.1273 | -61.9904 | 0.064087 | -62.265 | 60.2371 | 62.2055 | 62.1689 | 0.061035 | -0.11749 | 0.068359 | 0.27878 | -0.14954 | -0.18692 | 0.032043 | 0.1236 | -62.4069 | 60.1776 | 60.1685 | 62.233 | 62.3703 | 122.5296 | 62.1277 | 60.1913
4260.625 | 0.15259 | 0.38345 | -0.76584 | -0.22751 | 0.11215 | -0.28305 | -0.18799 | 60.1364 | -61.9492 | 0.018311 | -62.2604 | 60.1593 | 62.1872 | 62.146 | 0.061035 | -0.11215 | 0.036316 | 0.28305 | -0.1506 | -0.17731 | 0.045776 | 0.086975 | -62.352 | 60.0906 | 60.1181 | 62.2192 | 62.3428 | 122.438 | 62.178 | 60.1685
4262.2969 | 0.076294 | 0.4155 | -0.76477 | -0.23712 | 0.11108 | -0.24353 | -0.19012 | 60.2188 | -61.9583 | 0.045776 | -62.2192 | 60.2417 | 62.1918 | 62.1506 | 0.045776 | -0.095062 | 0.059814 | 0.28839 | -0.12711 | -0.19012 | 0 | 0.032043 | -62.4069 | 60.1456 | 60.173 | 62.2009 | 62.3657 | 122.4701 | 62.1368 | 60.2142
4263.9688 | 0.10681 | 0.42511 | -0.7605 | -0.24674 | 0.11215 | -0.25101 | -0.19012 | 60.173 | -61.9492 | 0.054932 | -62.2284 | 60.2234 | 62.1735 | 62.1689 | 0.045776 | -0.10254 | 0.052338 | 0.28519 | -0.14099 | -0.18478 | 0.041199 | 0.091553 | -62.3795 | 60.1639 | 60.1501 | 62.2055 | 62.3428 | 122.5708 | 62.1094 | 60.1593
4265.6719 | 0.030518 | 0.40268 | -0.77118 | -0.21683 | 0.10468 | -0.25528 | -0.18585 | 60.1181 | -62.0178 | -0.059509 | -62.2696 | 60.2188 | 62.1643 | 62.1597 | 0.061035 | -0.11002 | 0.05127 | 0.28412 | -0.13565 | -0.16983 | -0.050354 | -0.041199 | -62.3886 | 60.1547 | 60.1318 | 62.2238 | 62.3566 | 122.493 | 62.1872 | 60.1776
4267.3594 | 0.045776 | 0.37918 | -0.78186 | -0.24994 | 0.10681 | -0.298 | -0.19012 | 60.1135 | -61.9675 | 0.041199 | -62.2421 | 60.173 | 62.178 | 62.1506 | 0.030518 | -0.12817 | 0.05661 | 0.27771 | -0.15701 | -0.18799 | 0.013733 | 0.10071 | -62.3611 | 60.1044 | 60.1318 | 62.2055 | 62.3566 | 122.4701 | 62.1689 | 60.1456
4269.0312 | 0.045776 | 0.37705 | -0.75836 | -0.21255 | 0.12817 | -0.2681 | -0.19119 | 60.228 | -61.9217 | 0.022888 | -62.2055 | 60.1822 | 62.1872 | 62.1689 | 0.061035 | -0.10788 | 0.043793 | 0.27878 | -0.13138 | -0.18799 | 0.022888 | 0.073242 | -62.3337 | 60.0861 | 60.0861 | 62.2101 | 62.3474 | 122.4609 | 62.1964 | 60.1776
4270.6875 | 0.076294 | 0.41443 | -0.77011 | -0.2681 | 0.10788 | -0.24887 | -0.18799 | 60.1501 | -61.9949 | 0.041199 | -62.2375 | 60.2371 | 62.1964 | 62.1552 | 0.045776 | -0.10574 | 0.052338 | 0.2713 | -0.15808 | -0.19119 | 0.018311 | 0.082397 | -62.3795 | 60.1959 | 60.1547 | 62.2147 | 62.3657 | 122.58 | 62.1231 | 60.1639
4272.4062 | 0.061035 | 0.42404 | -0.76477 | -0.24246 | 0.11108 | -0.25635 | -0.18372 | 60.1913 | -61.9537 | 0.022888 | -62.233 | 60.2142 | 62.178 | 62.1643 | 0.045776 | -0.099335 | 0.046997 | 0.29159 | -0.13351 | -0.19653 | -0.004578 | 0.009155 | -62.4207 | 60.141 | 60.1318 | 62.2055 | 62.352 | 122.4564 | 62.1597 | 60.1776
4274.0781 | 0.061035 | 0.42404 | -0.77011 | -0.26596 | 0.11002 | -0.2681 | -0.19333 | 60.1135 | -61.9904 | 0.050354 | -62.2513 | 60.2417 | 62.1826 | 62.178 | 0.045776 | -0.099335 | 0.060883 | 0.28625 | -0.15701 | -0.17624 | 0.013733 | 0.086975 | -62.4252 | 60.1822 | 60.1685 | 62.233 | 62.3566 | 122.5754 | 62.1414 | 60.1822
4275.75 | 0.045776 | 0.37064 | -0.79041 | -0.23926 | 0.11856 | -0.30014 | -0.19867 | 60.1227 | -61.9217 | 0.07782 | -62.2147 | 60.1913 | 62.1735 | 62.178 | 0.030518 | -0.12604 | 0.050201 | 0.2713 | -0.16129 | -0.18585 | 0.10071 | 0.18768 | -62.3062 | 60.0861 | 60.1089 | 62.2147 | 62.352 | 122.5571 | 62.1323 | 60.1776
4277.4844 | 0.045776 | 0.41977 | -0.76477 | -0.21683 | 0.11108 | -0.2446 | -0.1741 | 60.0998 | -62.059 | -0.073242 | -62.2879 | 60.2325 | 62.1964 | 62.1872 | 0.045776 | -0.097198 | 0.055542 | 0.28839 | -0.12176 | -0.19333 | -0.09613 | -0.10071 | -62.4619 | 60.1639 | 60.141 | 62.2513 | 62.3428 | 122.4655 | 62.178 | 60.1913
4279.1719 | 0.045776 | 0.38238 | -0.77759 | -0.23178 | 0.11963 | -0.27878 | -0.17303 | 60.1959 | -61.9217 | 0.022888 | -62.1918 | 60.1776 | 62.1918 | 62.1643 | 0.030518 | -0.10895 | 0.038452 | 0.28198 | -0.14526 | -0.18906 | 0.013733 | 0.045776 | -62.3428 | 60.0861 | 60.0723 | 62.233 | 62.3337 | 122.4701 | 62.2101 | 60.1776
4280.8438 | 0.091553 | 0.42618 | -0.76904 | -0.24353 | 0.10788 | -0.25848 | -0.18478 | 60.1822 | -61.972 | 0.050354 | -62.233 | 60.2234 | 62.1643 | 62.1506 | 0.045776 | -0.1004 | 0.05127 | 0.28625 | -0.1442 | -0.19653 | 0.027466 | 0.086975 | -62.3932 | 60.1639 | 60.1639 | 62.2009 | 62.3291 | 122.5571 | 62.1277 | 60.1501
4282.5156 | 0.030518 | 0.43579 | -0.77545 | -0.2713 | 0.10788 | -0.27344 | -0.18478 | 60.1227 | -62.0087 | 0.041199 | -62.2375 | 60.2097 | 62.1826 | 62.1506 | 0.045776 | -0.10788 | 0.061951 | 0.2681 | -0.15274 | -0.18265 | 0.013733 | 0.091553 | -62.4161 | 60.2005 | 60.1822 | 62.2101 | 62.3383 | 122.5754 | 62.1231 | 60.1547
4284.2031 | 0.045776 | 0.40909 | -0.77438 | -0.24674 | 0.10468 | -0.24567 | -0.17838 | 60.1089 | -62.0316 | -0.054932 | -62.265 | 60.2142 | 62.1826 | 62.178 | 0.045776 | -0.10788 | 0.050201 | 0.298 | -0.13779 | -0.18585 | -0.10071 | -0.073242 | -62.4664 | 60.173 | 60.1364 | 62.2467 | 62.3703 | 122.4472 | 62.1826 | 60.2005
4285.875 | 0.076294 | 0.36102 | -0.78079 | -0.26276 | 0.12497 | -0.2948 | -0.20828 | 60.1364 | -61.8851 | 0.1236 | -62.2101 | 60.1776 | 62.1689 | 62.1552 | 0.045776 | -0.12497 | 0.048065 | 0.28625 | -0.16769 | -0.18372 | 0.12817 | 0.23804 | -62.2696 | 60.0952 | 60.0952 | 62.2192 | 62.3245 | 122.5754 | 62.1323 | 60.1135
4287.5469 | 0.030518 | 0.39627 | -0.77866 | -0.26596 | 0.11322 | -0.28519 | -0.19226 | 60.1822 | -61.8759 | 0.16022 | -62.1964 | 60.1593 | 62.1552 | 62.1094 | 0.061035 | -0.11429 | 0.043793 | 0.27451 | -0.15488 | -0.17838 | 0.11444 | 0.23804 | -62.3245 | 60.1318 | 60.0952 | 62.2101 | 62.3291 | 122.5296 | 62.1323 | 60.1547
4289.2188 | 0.10681 | 0.35355 | -0.77331 | -0.24567 | 0.1004 | -0.27557 | -0.19653 | 60.173 | -61.9034 | 0.045776 | -62.2238 | 60.1639 | 62.1689 | 62.1368 | 0.045776 | -0.12176 | 0.040588 | 0.27878 | -0.1506 | -0.17838 | 0.027466 | 0.082397 | -62.3337 | 60.0815 | 60.0632 | 62.2101 | 62.3566 | 122.4335 | 62.2055 | 60.1776
4290.8906 | 0.045776 | 0.39093 | -0.77011 | -0.22217 | 0.11429 | -0.25742 | -0.19974 | 60.1547 | -61.9858 | -0.041199 | -62.2696 | 60.2234 | 62.1964 | 62.1643 | 0.045776 | -0.10895 | 0.033112 | 0.28091 | -0.14099 | -0.18799 | -0.009155 | 0 | -62.3657 | 60.1227 | 60.0815 | 62.2101 | 62.3337 | 122.5021 | 62.1826 | 60.1456
4292.5938 | 0.076294 | 0.43579 | -0.77652 | -0.25207 | 0.11963 | -0.25314 | -0.18478 | 60.1364 | -61.9766 | 0.064087 | -62.233 | 60.2371 | 62.178 | 62.1735 | 0.045776 | -0.10147 | 0.061951 | 0.27557 | -0.14206 | -0.19546 | 0.032043 | 0.07782 | -62.3932 | 60.1776 | 60.1547 | 62.2147 | 62.3474 | 122.5754 | 62.1231 | 60.1456
4294.2656 | 0.061035 | 0.37384 | -0.78293 | -0.25528 | 0.1207 | -0.27557 | -0.19546 | 60.173 | -61.8713 | 0.16022 | -62.2009 | 60.173 | 62.1597 | 62.1552 | 0.045776 | -0.1239 | 0.05661 | 0.27023 | -0.16556 | -0.18799 | 0.14648 | 0.2655 | -62.2971 | 60.1044 | 60.0861 | 62.1964 | 62.3245 | 122.5479 | 62.1231 | 60.1639
4295.9219 | 0.045776 | 0.40375 | -0.76904 | -0.22858 | 0.11108 | -0.24353 | -0.18799 | 60.1318 | -62.0316 | -0.082397 | -62.2742 | 60.2692 | 62.2009 | 62.1826 | 0.045776 | -0.09613 | 0.041656 | 0.28625 | -0.12924 | -0.18051 | -0.054932 | -0.09613 | -62.4435 | 60.1639 | 60.173 | 62.233 | 62.3566 | 122.4884 | 62.1735 | 60.1547
4297.5938 | 0.061035 | 0.41122 | -0.77866 | -0.26062 | 0.12604 | -0.2713 | -0.19012 | 60.1273 | -61.9766 | 0.073242 | -62.2604 | 60.2325 | 62.1826 | 62.1735 | 0.045776 | -0.10468 | 0.057678 | 0.2713 | -0.15488 | -0.1976 | 0.036621 | 0.11444 | -62.4023 | 60.173 | 60.1639 | 62.2192 | 62.3611 | 122.5159 | 62.1368 | 60.1868
4299.2812 | 0.030518 | 0.392 | -0.77438 | -0.26916 | 0.12283 | -0.27451 | -0.1944 | 60.1776 | -61.9263 | 0.12817 | -62.2101 | 60.2097 | 62.1826 | 62.1414 | 0.045776 | -0.10895 | 0.060883 | 0.28091 | -0.17517 | -0.18692 | 0.07782 | 0.16022 | -62.3795 | 60.1685 | 60.1685 | 62.2147 | 62.3291 | 122.525 | 62.1185 | 60.1776
4300.9531 | 0.091553 | 0.345 | -0.76584 | -0.2446 | 0.11002 | -0.27237 | -0.17838 | 60.1776 | -61.908 | 0.045776 | -62.2147 | 60.1181 | 62.1918 | 62.1506 | 0.061035 | -0.11749 | 0.049133 | 0.27878 | -0.1442 | -0.18478 | 0.041199 | 0.086975 | -62.3337 | 60.0906 | 60.0815 | 62.2055 | 62.3245 | 122.438 | 62.178 | 60.1593
4302.625 | 0.061035 | 0.4187 | -0.76157 | -0.25421 | 0.11643 | -0.23392 | -0.18692 | 60.2051 | -61.9446 | 0.054932 | -62.2192 | 60.2417 | 62.1689 | 62.1597 | 0.045776 | -0.092926 | 0.058746 | 0.27985 | -0.14526 | -0.1976 | 0.036621 | 0.054932 | -62.3932 | 60.1593 | 60.1501 | 62.233 | 62.3245 | 122.5342 | 62.1506 | 60.1776
4304.2969 | 0.076294 | 0.41016 | -0.78507 | -0.25101 | 0.11749 | -0.27557 | -0.20615 | 60.0998 | -61.9904 | 0.050354 | -62.2604 | 60.2417 | 62.1826 | 62.178 | 0.076294 | -0.11322 | 0.061951 | 0.28305 | -0.15274 | -0.18051 | 0.013733 | 0.09613 | -62.4207 | 60.2051 | 60.1685 | 62.2375 | 62.3383 | 122.5662 | 62.1048 | 60.1639
4305.9688 | 0.045776 | 0.36102 | -0.75943 | -0.22964 | 0.11536 | -0.2681 | -0.17517 | 60.173 | -61.908 | 0.027466 | -62.1964 | 60.1547 | 62.1918 | 62.178 | 0.076294 | -0.10788 | 0.045929 | 0.2681 | -0.13992 | -0.17944 | 0.027466 | 0.064087 | -62.3428 | 60.1044 | 60.0769 | 62.2284 | 62.3291 | 122.4655 | 62.1964 | 60.1685
4307.6406 | 0.061035 | 0.42191 | -0.7637 | -0.23178 | 0.11429 | -0.24887 | -0.18265 | 60.1181 | -62.0453 | -0.068665 | -62.2833 | 60.2509 | 62.1826 | 62.1643 | 0.061035 | -0.097198 | 0.042725 | 0.27664 | -0.14206 | -0.18906 | -0.07782 | -0.082397 | -62.4573 | 60.1593 | 60.1776 | 62.2284 | 62.3566 | 122.4518 | 62.1964 | 60.1959
4309.3125 | 0.076294 | 0.43579 | -0.76584 | -0.2478 | 0.11002 | -0.25848 | -0.18478 | 60.1913 | -61.9492 | 0.073242 | -62.2284 | 60.2325 | 62.178 | 62.1597 | 0.061035 | -0.10895 | 0.046997 | 0.27985 | -0.14099 | -0.18692 | 0.036621 | 0.07782 | -62.3795 | 60.1456 | 60.1593 | 62.2009 | 62.3657 | 122.5616 | 62.1231 | 60.1639
4310.9844 | 0.061035 | 0.40161 | -0.77972 | -0.27451 | 0.12604 | -0.28519 | -0.1976 | 60.1685 | -61.8713 | 0.15564 | -62.1872 | 60.1685 | 62.178 | 62.1231 | 0.030518 | -0.11536 | 0.052338 | 0.27771 | -0.16342 | -0.1944 | 0.09613 | 0.23804 | -62.3337 | 60.1364 | 60.1364 | 62.2238 | 62.3108 | 122.5296 | 62.1094 | 60.173
4312.6562 | 0.045776 | 0.38025 | -0.76477 | -0.23498 | 0.11856 | -0.26703 | -0.18585 | 60.1501 | -61.9949 | -0.032043 | -62.2696 | 60.2005 | 62.1826 | 62.1552 | 0.045776 | -0.11215 | 0.050201 | 0.27878 | -0.13672 | -0.19012 | -0.004578 | 0.022888 | -62.3611 | 60.1044 | 60.1227 | 62.2192 | 62.3428 | 122.5021 | 62.178 | 60.1685
4314.3281 | 0.045776 | 0.38452 | -0.77118 | -0.2211 | 0.11749 | -0.26382 | -0.17624 | 60.1456 | -61.9949 | -0.036621 | -62.2604 | 60.1913 | 62.1689 | 62.1552 | 0.061035 | -0.10788 | 0.050201 | 0.27557 | -0.13672 | -0.17838 | -0.022888 | 0.009155 | -62.3611 | 60.1135 | 60.1044 | 62.2238 | 62.3428 | 122.493 | 62.1735 | 60.1456
4315.9844 | 0.091553 | 0.42938 | -0.76584 | -0.24887 | 0.11002 | -0.25421 | -0.19226 | 60.1501 | -62.0224 | 0.032043 | -62.2421 | 60.2463 | 62.1643 | 62.1643 | 0.045776 | -0.10361 | 0.069427 | 0.2948 | -0.14633 | -0.18585 | 0.018311 | 0.10071 | -62.3886 | 60.1639 | 60.1913 | 62.2147 | 62.3428 | 122.58 | 62.114 | 60.1868
4317.6562 | 0.10681 | 0.4187 | -0.75516 | -0.25955 | 0.11108 | -0.25955 | -0.18478 | 60.1776 | -61.9629 | 0.064087 | -62.2192 | 60.228 | 62.1918 | 62.1597 | 0.045776 | -0.098267 | 0.055542 | 0.28625 | -0.1474 | -0.19119 | 0.032043 | 0.082397 | -62.384 | 60.1639 | 60.1593 | 62.2101 | 62.3199 | 122.5708 | 62.114 | 60.1822
4319.3281 | 0.061035 | 0.38559 | -0.77652 | -0.26703 | 0.11963 | -0.28732 | -0.18265 | 60.1639 | -61.8896 | 0.15106 | -62.2055 | 60.1959 | 62.1689 | 62.1323 | 0.061035 | -0.13458 | 0.054474 | 0.27985 | -0.15808 | -0.1741 | 0.11444 | 0.23804 | -62.3337 | 60.1181 | 60.1135 | 62.2101 | 62.3245 | 122.5113 | 62.1643 | 60.1639
4321 | 0.015259 | 0.3685 | -0.77972 | -0.26062 | 0.11108 | -0.28305 | -0.20294 | 60.1089 | -61.9446 | 0.068665 | -62.2375 | 60.173 | 62.1735 | 62.1323 | 0.061035 | -0.12604 | 0.037384 | 0.28091 | -0.15808 | -0.18585 | 0.068665 | 0.16937 | -62.3199 | 60.0952 | 60.1273 | 62.2147 | 62.3428 | 122.5479 | 62.1689 | 60.1456
4322.6719 | 0.030518 | 0.40161 | -0.75943 | -0.22751 | 0.11749 | -0.24246 | -0.19012 | 60.141 | -62.0316 | -0.068665 | -62.2742 | 60.2371 | 62.2055 | 62.1826 | 0.045776 | -0.1004 | 0.03952 | 0.28625 | -0.14526 | -0.18478 | -0.064087 | -0.091553 | -62.4252 | 60.173 | 60.141 | 62.2513 | 62.3474 | 122.4792 | 62.1826 | 60.173
4324.3438 | 0.030518 | 0.40054 | -0.78186 | -0.25848 | 0.11002 | -0.27023 | -0.19226 | 60.173 | -61.908 | 0.13733 | -62.2147 | 60.1822 | 62.178 | 62.1643 | 0.045776 | -0.11749 | 0.052338 | 0.27771 | -0.16556 | -0.17838 | 0.091553 | 0.19226 | -62.3795 | 60.1456 | 60.1639 | 62.2238 | 62.3566 | 122.5113 | 62.1277 | 60.173
4326.0156 | 0.076294 | 0.35782 | -0.77972 | -0.22324 | 0.095062 | -0.26916 | -0.19546 | 60.1776 | -61.9217 | 0.032043 | -62.2375 | 60.173 | 62.1597 | 62.1597 | 0.061035 | -0.11536 | 0.043793 | 0.28625 | -0.14099 | -0.19119 | 0.050354 | 0.068665 | -62.3611 | 60.0815 | 60.0906 | 62.2101 | 62.3566 | 122.4243 | 62.1918 | 60.1593
4327.6719 | 0.045776 | 0.4155 | -0.76157 | -0.22964 | 0.11856 | -0.24674 | -0.18372 | 60.1547 | -62.059 | -0.07782 | -62.265 | 60.2463 | 62.2055 | 62.1597 | 0.061035 | -0.10254 | 0.044861 | 0.28625 | -0.12817 | -0.18478 | -0.07782 | -0.10986 | -62.4481 | 60.1913 | 60.1547 | 62.2147 | 62.3657 | 122.4792 | 62.2009 | 60.2005
4329.3438 | 0.030518 | 0.43045 | -0.77331 | -0.23178 | 0.11215 | -0.24674 | -0.18265 | 60.1959 | -61.9812 | 0.018311 | -62.2467 | 60.2188 | 62.1918 | 62.178 | 0.030518 | -0.095062 | 0.044861 | 0.27557 | -0.13458 | -0.18372 | -0.032043 | -0.013733 | -62.439 | 60.1547 | 60.1639 | 62.2284 | 62.3474 | 122.4564 | 62.1918 | 60.2234
4331.0156 | 0.030518 | 0.41763 | -0.75836 | -0.22858 | 0.12604 | -0.25314 | -0.18372 | 60.1227 | -62.0728 | -0.050354 | -62.2833 | 60.2325 | 62.2009 | 62.1964 | 0.045776 | -0.10361 | 0.048065 | 0.28519 | -0.13886 | -0.17838 | -0.091553 | -0.09613 | -62.4435 | 60.1456 | 60.1593 | 62.2238 | 62.3474 | 122.4564 | 62.1689 | 60.2051
4332.7344 | 0.061035 | 0.42404 | -0.75836 | -0.25314 | 0.10788 | -0.26703 | -0.1709 | 60.1868 | -61.9537 | 0.050354 | -62.2467 | 60.2463 | 62.1872 | 62.1689 | 0.030518 | -0.098267 | 0.053406 | 0.28732 | -0.13779 | -0.18478 | -0.013733 | 0.013733 | -62.4298 | 60.141 | 60.1639 | 62.233 | 62.3611 | 122.4564 | 62.178 | 60.1959
4334.4531 | 0.061035 | 0.39734 | -0.78186 | -0.25955 | 0.099335 | -0.29694 | -0.19333 | 60.1593 | -61.8576 | 0.19684 | -62.1872 | 60.1639 | 62.178 | 62.1597 | 0.030518 | -0.12604 | 0.052338 | 0.26703 | -0.15381 | -0.17944 | 0.12817 | 0.25177 | -62.3016 | 60.0998 | 60.0998 | 62.2192 | 62.3291 | 122.5204 | 62.114 | 60.173
4336.125 | 0.061035 | 0.38025 | -0.76904 | -0.22964 | 0.11856 | -0.27023 | -0.18692 | 60.1959 | -61.9217 | 0.036621 | -62.1964 | 60.1685 | 62.1826 | 62.1414 | 0.061035 | -0.11215 | 0.038452 | 0.28305 | -0.14206 | -0.17944 | -0.009155 | 0.064087 | -62.3383 | 60.0723 | 60.0952 | 62.2421 | 62.3337 | 122.4792 | 62.1643 | 60.173
4337.8125 | 0.015259 | 0.41122 | -0.75836 | -0.23285 | 0.11322 | -0.25635 | -0.18585 | 60.1181 | -62.0544 | -0.054932 | -62.2925 | 60.2325 | 62.1964 | 62.1826 | 0.061035 | -0.097198 | 0.054474 | 0.27771 | -0.14847 | -0.18799 | -0.091553 | -0.09613 | -62.4619 | 60.1456 | 60.1501 | 62.2192 | 62.3749 | 122.4609 | 62.1826 | 60.1776
4339.5 | 0.045776 | 0.42191 | -0.76904 | -0.27451 | 0.11856 | -0.2713 | -0.20081 | 60.1227 | -61.9904 | 0.036621 | -62.2604 | 60.2554 | 62.1552 | 62.1597 | 0.030518 | -0.11536 | 0.058746 | 0.28839 | -0.15701 | -0.18265 | 0.022888 | 0.10529 | -62.4207 | 60.1868 | 60.2051 | 62.2375 | 62.3566 | 122.5754 | 62.1185 | 60.1685
4341.1719 | 0.045776 | 0.36957 | -0.77759 | -0.26703 | 0.10681 | -0.29159 | -0.18692 | 60.1227 | -61.9354 | 0.082397 | -62.2192 | 60.173 | 62.1964 | 62.1368 | 0.030518 | -0.13672 | 0.060883 | 0.28091 | -0.16876 | -0.18585 | 0.082397 | 0.17853 | -62.2971 | 60.0906 | 60.1318 | 62.2147 | 62.3199 | 122.5662 | 62.1414 | 60.1456
4342.8594 | 0.076294 | 0.40909 | -0.75516 | -0.26382 | 0.10361 | -0.24567 | -0.18372 | 60.2005 | -61.94 | 0.059509 | -62.2192 | 60.2371 | 62.1643 | 62.1506 | 0.061035 | -0.11215 | 0.057678 | 0.27985 | -0.13992 | -0.19867 | 0.050354 | 0.068665 | -62.3886 | 60.1547 | 60.1181 | 62.233 | 62.3611 | 122.5342 | 62.1323 | 60.1685
4344.5312 | 0.076294 | 0.3685 | -0.77545 | -0.23819 | 0.11322 | -0.28198 | -0.18585 | 60.1456 | -61.9354 | 0.041199 | -62.2421 | 60.1639 | 62.1918 | 62.1552 | 0.061035 | -0.12176 | 0.043793 | 0.27237 | -0.15167 | -0.17731 | 0.022888 | 0.086975 | -62.3474 | 60.0952 | 60.0998 | 62.2238 | 62.3428 | 122.4289 | 62.2147 | 60.173
4346.2031 | 0.061035 | 0.42618 | -0.7637 | -0.2446 | 0.10574 | -0.24994 | -0.18372 | 60.1639 | -61.9812 | 0 | -62.2467 | 60.2463 | 62.1872 | 62.1826 | 0.030518 | -0.093994 | 0.046997 | 0.28198 | -0.13779 | -0.19226 | -0.073242 | -0.041199 | -62.4664 | 60.173 | 60.1776 | 62.2238 | 62.3703 | 122.4426 | 62.1597 | 60.2097
4347.8906 | 0.030518 | 0.42618 | -0.76691 | -0.22858 | 0.10895 | -0.23819 | -0.18906 | 60.1913 | -61.9675 | 0.032043 | -62.2375 | 60.2097 | 62.1872 | 62.1735 | 0.030518 | -0.099335 | 0.052338 | 0.28091 | -0.14206 | -0.18692 | -0.027466 | 0.009155 | -62.4207 | 60.1318 | 60.1318 | 62.2513 | 62.3474 | 122.4518 | 62.146 | 60.2005
4349.5625 | 0.015259 | 0.40054 | -0.77331 | -0.24353 | 0.10147 | -0.26489 | -0.19119 | 60.1227 | -62.027 | -0.059509 | -62.2833 | 60.228 | 62.1964 | 62.2009 | 0.030518 | -0.11643 | 0.052338 | 0.28412 | -0.14206 | -0.18799 | -0.059509 | -0.054932 | -62.4069 | 60.1135 | 60.1089 | 62.2696 | 62.3337 | 122.493 | 62.1918 | 60.1501
4351.25 | 0.076294 | 0.42511 | -0.77972 | -0.24353 | 0.11108 | -0.26703 | -0.17517 | 60.173 | -61.9629 | 0.068665 | -62.2238 | 60.2234 | 62.1735 | 62.1506 | 0.045776 | -0.10574 | 0.053406 | 0.27451 | -0.14313 | -0.18478 | 0.013733 | 0.091553 | -62.3795 | 60.1364 | 60.1685 | 62.2147 | 62.3428 | 122.5571 | 62.1231 | 60.173
4352.9375 | 0.10681 | 0.42297 | -0.76691 | -0.26062 | 0.11536 | -0.25955 | -0.18158 | 60.1501 | -61.9858 | 0.041199 | -62.2147 | 60.26 | 62.1918 | 62.1506 | 0.045776 | -0.11002 | 0.059814 | 0.29159 | -0.16022 | -0.18372 | 0.032043 | 0.091553 | -62.3886 | 60.1822 | 60.1868 | 62.2009 | 62.3383 | 122.58 | 62.1185 | 60.2051
4354.6094 | 0.076294 | 0.42084 | -0.77866 | -0.24246 | 0.11215 | -0.25314 | -0.17838 | 60.1685 | -61.9492 | 0.064087 | -62.2101 | 60.2509 | 62.1689 | 62.1597 | 0.061035 | -0.10895 | 0.057678 | 0.28519 | -0.14847 | -0.19012 | 0.036621 | 0.091553 | -62.3749 | 60.1685 | 60.1685 | 62.2147 | 62.3428 | 122.5662 | 62.1323 | 60.1776
4356.2656 | 0.045776 | 0.40482 | -0.78934 | -0.26276 | 0.11536 | -0.28412 | -0.1944 | 60.1273 | -61.9446 | 0.07782 | -62.2284 | 60.2142 | 62.1964 | 62.1735 | 0.045776 | -0.11108 | 0.058746 | 0.27878 | -0.16022 | -0.17731 | 0.032043 | 0.13275 | -62.3932 | 60.1822 | 60.141 | 62.2467 | 62.3566 | 122.5296 | 62.1231 | 60.1685
4357.9375 | 0.030518 | 0.39841 | -0.75516 | -0.23285 | 0.10254 | -0.26703 | -0.18906 | 60.1273 | -61.9949 | -0.036621 | -62.2696 | 60.228 | 62.1872 | 62.1552 | 0.030518 | -0.11215 | 0.049133 | 0.27771 | -0.13565 | -0.18265 | -0.041199 | -0.022888 | -62.3749 | 60.0906 | 60.1181 | 62.233 | 62.3383 | 122.493 | 62.1872 | 60.1501
4359.6094 | 0.030518 | 0.40802 | -0.75409 | -0.22644 | 0.11643 | -0.25848 | -0.18692 | 60.1135 | -62.0407 | -0.073242 | -62.2787 | 60.2417 | 62.2009 | 62.1735 | 0.061035 | -0.1004 | 0.048065 | 0.29159 | -0.13779 | -0.18478 | -0.09613 | -0.09613 | -62.4252 | 60.1547 | 60.1639 | 62.2192 | 62.3703 | 122.4792 | 62.178 | 60.1685
4361.2969 | 0.045776 | 0.38025 | -0.77759 | -0.26276 | 0.11963 | -0.2948 | -0.19119 | 60.1776 | -61.8759 | 0.14648 | -62.2009 | 60.173 | 62.1872 | 62.1552 | 0.030518 | -0.13138 | 0.050201 | 0.26916 | -0.17624 | -0.18265 | 0.13733 | 0.24261 | -62.2787 | 60.0906 | 60.0861 | 62.1872 | 62.3428 | 122.5845 | 62.1323 | 60.1593
4362.9844 | 0.045776 | 0.4187 | -0.77118 | -0.24674 | 0.11963 | -0.23712 | -0.18372 | 60.1913 | -61.9766 | 0.022888 | -62.233 | 60.2463 | 62.1689 | 62.1597 | 0.045776 | -0.10468 | 0.049133 | 0.27771 | -0.12604 | -0.19974 | -0.027466 | -0.004578 | -62.4207 | 60.1822 | 60.1593 | 62.2192 | 62.3383 | 122.438 | 62.1918 | 60.1959
4364.6562 | 0.15259 | 0.42725 | -0.77225 | -0.26169 | 0.11002 | -0.25314 | -0.19119 | 60.1685 | -61.9766 | 0.050354 | -62.2238 | 60.26 | 62.1964 | 62.1689 | 0.045776 | -0.11429 | 0.066223 | 0.28519 | -0.1506 | -0.20401 | 0.032043 | 0.082397 | -62.384 | 60.1501 | 60.1593 | 62.2284 | 62.3611 | 122.5845 | 62.1094 | 60.1868
4366.3281 | 0.045776 | 0.36957 | -0.77545 | -0.25314 | 0.12176 | -0.29694 | -0.19653 | 60.1959 | -61.8439 | 0.14191 | -62.1826 | 60.173 | 62.1368 | 62.1414 | 0.061035 | -0.13458 | 0.046997 | 0.27664 | -0.16983 | -0.18585 | 0.12817 | 0.2655 | -62.2971 | 60.1044 | 60.1044 | 62.2009 | 62.3383 | 122.5525 | 62.1323 | 60.1364
4368 | 0.061035 | 0.42191 | -0.76691 | -0.23071 | 0.1207 | -0.23605 | -0.18265 | 60.1273 | -62.0407 | -0.054932 | -62.2696 | 60.2554 | 62.2192 | 62.1964 | 0.045776 | -0.11108 | 0.045929 | 0.27878 | -0.13031 | -0.19867 | -0.073242 | -0.086975 | -62.471 | 60.173 | 60.1456 | 62.2147 | 62.3474 | 122.4518 | 62.1918 | 60.2142
4369.6719 | 0.076294 | 0.44006 | -0.75516 | -0.23819 | 0.10254 | -0.25635 | -0.18906 | 60.1822 | -61.9492 | 0.050354 | -62.2284 | 60.2234 | 62.1872 | 62.1735 | 0.030518 | -0.09079 | 0.043793 | 0.29053 | -0.13992 | -0.19226 | 0.004578 | 0.050354 | -62.384 | 60.1456 | 60.1685 | 62.2009 | 62.3611 | 122.5113 | 62.1552 | 60.173
4371.3594 | 0.030518 | 0.42297 | -0.75943 | -0.23178 | 0.11429 | -0.25207 | -0.19226 | 60.0952 | -62.0773 | -0.064087 | -62.2833 | 60.2325 | 62.2147 | 62.1872 | 0.015259 | -0.11002 | 0.044861 | 0.28946 | -0.13565 | -0.18051 | -0.10071 | -0.10529 | -62.4298 | 60.1685 | 60.173 | 62.2284 | 62.3474 | 122.4701 | 62.1689 | 60.1959
4373.0469 | 0.061035 | 0.41122 | -0.74768 | -0.22537 | 0.1207 | -0.25528 | -0.19119 | 60.1181 | -62.0499 | -0.068665 | -62.2604 | 60.2463 | 62.1872 | 62.178 | 0.045776 | -0.10574 | 0.036316 | 0.28412 | -0.13565 | -0.18478 | -0.086975 | -0.10071 | -62.4344 | 60.1456 | 60.1685 | 62.233 | 62.3337 | 122.4701 | 62.1826 | 60.2005
4374.7656 | 0.061035 | 0.39841 | -0.75409 | -0.24353 | 0.10788 | -0.26062 | -0.18372 | 60.1273 | -62.0041 | -0.054932 | -62.2742 | 60.2051 | 62.1826 | 62.2009 | 0.061035 | -0.1207 | 0.048065 | 0.28946 | -0.14206 | -0.18692 | -0.059509 | -0.041199 | -62.3932 | 60.1593 | 60.1501 | 62.233 | 62.3428 | 122.4884 | 62.1597 | 60.1501
4376.4219 | 0.061035 | 0.42511 | -0.76584 | -0.25101 | 0.10361 | -0.25314 | -0.19012 | 60.1456 | -61.9766 | 0.027466 | -62.2513 | 60.1959 | 62.1643 | 62.1826 | 0.045776 | -0.1004 | 0.060883 | 0.28732 | -0.15167 | -0.18158 | -0.054932 | -0.018311 | -62.4344 | 60.1685 | 60.1593 | 62.2467 | 62.3566 | 122.4518 | 62.178 | 60.2005
4378.1094 | 0.10681 | 0.36636 | -0.784 | -0.25101 | 0.12283 | -0.29159 | -0.19333 | 60.1227 | -61.9492 | 0.032043 | -62.2513 | 60.1776 | 62.1643 | 62.1643 | 0.045776 | -0.13779 | 0.041656 | 0.26916 | -0.16235 | -0.17197 | 0.009155 | 0.064087 | -62.3566 | 60.0861 | 60.1273 | 62.233 | 62.3657 | 122.4564 | 62.1826 | 60.1593
4379.7969 | 0.045776 | 0.37811 | -0.77545 | -0.26062 | 0.11429 | -0.29907 | -0.20508 | 60.173 | -61.8851 | 0.13733 | -62.1918 | 60.1868 | 62.1964 | 62.1323 | 0.045776 | -0.13565 | 0.054474 | 0.28625 | -0.16449 | -0.18585 | 0.14191 | 0.23346 | -62.2971 | 60.0861 | 60.0906 | 62.2238 | 62.3108 | 122.5845 | 62.1277 | 60.1501
4381.4844 | 0.045776 | 0.38666 | -0.78507 | -0.25528 | 0.11322 | -0.27237 | -0.19119 | 60.1822 | -61.8988 | 0.16479 | -62.2009 | 60.1685 | 62.1643 | 62.146 | 0.045776 | -0.11963 | 0.061951 | 0.27023 | -0.16342 | -0.19119 | 0.11902 | 0.23346 | -62.3062 | 60.1044 | 60.0815 | 62.1964 | 62.3291 | 122.5159 | 62.1185 | 60.1547
4383.1562 | 0.076294 | 0.35782 | -0.75729 | -0.23926 | 0.098267 | -0.26703 | -0.18478 | 60.1913 | -61.9263 | 0.022888 | -62.2009 | 60.1639 | 62.1735 | 62.1689 | 0.030518 | -0.12604 | 0.050201 | 0.28091 | -0.14099 | -0.19653 | 0.022888 | 0.050354 | -62.3291 | 60.0677 | 60.0494 | 62.2375 | 62.3474 | 122.4518 | 62.1735 | 60.1593
4384.8438 | 0.061035 | 0.38452 | -0.77866 | -0.25528 | 0.11856 | -0.27985 | -0.18585 | 60.2234 | -61.8576 | 0.14191 | -62.1735 | 60.173 | 62.1872 | 62.1597 | 0.061035 | -0.11856 | 0.037384 | 0.27878 | -0.16129 | -0.18478 | 0.14648 | 0.25177 | -62.2925 | 60.0952 | 60.0998 | 62.1872 | 62.3291 | 122.5616 | 62.1552 | 60.1776
4386.5312 | 0.061035 | 0.42511 | -0.75516 | -0.24567 | 0.11643 | -0.23392 | -0.18692 | 60.2097 | -61.9583 | 0.013733 | -62.233 | 60.2371 | 62.1826 | 62.1597 | 0.045776 | -0.09613 | 0.059814 | 0.27771 | -0.13138 | -0.20081 | 0.009155 | 0 | -62.4161 | 60.1776 | 60.1547 | 62.233 | 62.3611 | 122.4472 | 62.1506 | 60.1868
4388.2031 | 0.030518 | 0.42511 | -0.77759 | -0.25955 | 0.10468 | -0.26596 | -0.19974 | 60.1181 | -61.9766 | 0.073242 | -62.2513 | 60.228 | 62.2284 | 62.1689 | 0.045776 | -0.10681 | 0.053406 | 0.28519 | -0.15701 | -0.18906 | 0.041199 | 0.11444 | -62.4069 | 60.2097 | 60.1639 | 62.2284 | 62.3428 | 122.5388 | 62.1231 | 60.1685
4389.875 | 0.045776 | 0.38879 | -0.76263 | -0.24246 | 0.11002 | -0.25742 | -0.19546 | 60.1227 | -62.0132 | -0.064087 | -62.2696 | 60.228 | 62.1964 | 62.178 | 0.045776 | -0.11002 | 0.05127 | 0.28412 | -0.1474 | -0.19012 | -0.032043 | -0.059509 | -62.4115 | 60.1089 | 60.1089 | 62.2238 | 62.3566 | 122.493 | 62.178 | 60.1639
4391.5469 | 0.10681 | 0.4187 | -0.7637 | -0.24994 | 0.11429 | -0.25314 | -0.18478 | 60.1364 | -61.9949 | 0.036621 | -62.2467 | 60.2554 | 62.178 | 62.178 | 0.061035 | -0.11322 | 0.042725 | 0.28305 | -0.15167 | -0.19119 | 0.032043 | 0.10529 | -62.4023 | 60.1913 | 60.2005 | 62.1964 | 62.3566 | 122.5845 | 62.114 | 60.173
4393.25 | 0.076294 | 0.38559 | -0.79681 | -0.24139 | 0.11536 | -0.30014 | -0.19867 | 60.0906 | -61.9629 | 0.036621 | -62.2513 | 60.1913 | 62.1872 | 62.1826 | 0.061035 | -0.13245 | 0.043793 | 0.27451 | -0.16022 | -0.17197 | 0.050354 | 0.11902 | -62.352 | 60.0861 | 60.1227 | 62.2147 | 62.3474 | 122.5021 | 62.1597 | 60.1685
4394.9219 | 0.030518 | 0.38345 | -0.78613 | -0.26062 | 0.11749 | -0.28625 | -0.19546 | 60.1959 | -61.8668 | 0.16022 | -62.1872 | 60.1593 | 62.1689 | 62.1643 | 0.061035 | -0.11429 | 0.050201 | 0.26916 | -0.15701 | -0.18692 | 0.14191 | 0.24719 | -62.2879 | 60.0952 | 60.0998 | 62.2147 | 62.3108 | 122.5616 | 62.1414 | 60.1456
4396.5938 | 0.030518 | 0.39948 | -0.784 | -0.25528 | 0.10681 | -0.26169 | -0.1976 | 60.1501 | -61.9308 | 0.09613 | -62.2192 | 60.2051 | 62.146 | 62.1735 | 0.061035 | -0.10574 | 0.048065 | 0.28732 | -0.16235 | -0.19974 | 0.059509 | 0.13275 | -62.3932 | 60.1685 | 60.1547 | 62.233 | 62.3474 | 122.5204 | 62.1323 | 60.1685
4398.2969 | 0.061035 | 0.38025 | -0.76797 | -0.22751 | 0.10681 | -0.24887 | -0.17624 | 60.1913 | -61.9171 | 0.022888 | -62.2147 | 60.1547 | 62.1872 | 62.1826 | 0.076294 | -0.11215 | 0.046997 | 0.27344 | -0.13779 | -0.18799 | 0.022888 | 0.054932 | -62.3337 | 60.0769 | 60.0769 | 62.2284 | 62.3474 | 122.4609 | 62.1964 | 60.141
4399.9688 | 0.030518 | 0.40695 | -0.7637 | -0.22751 | 0.10254 | -0.23605 | -0.18051 | 60.2142 | -61.94 | 0.041199 | -62.2284 | 60.2417 | 62.1918 | 62.1872 | 0.061035 | -0.092926 | 0.050201 | 0.28946 | -0.13245 | -0.19653 | 0.022888 | 0.036621 | -62.4069 | 60.1639 | 60.1456 | 62.2055 | 62.3383 | 122.4838 | 62.1506 | 60.173
4401.6406 | 0.045776 | 0.39414 | -0.76584 | -0.2713 | 0.1207 | -0.27344 | -0.18051 | 60.1593 | -61.9583 | 0.11444 | -62.2284 | 60.2051 | 62.1689 | 62.146 | 0.061035 | -0.10574 | 0.052338 | 0.27878 | -0.16235 | -0.18799 | 0.050354 | 0.13733 | -62.4069 | 60.1776 | 60.1639 | 62.2192 | 62.3337 | 122.5296 | 62.1185 | 60.1776
4403.3438 | 0.030518 | 0.38345 | -0.78507 | -0.25528 | 0.11429 | -0.29053 | -0.19653 | 60.1135 | -61.9629 | 0.041199 | -62.2421 | 60.1822 | 62.1826 | 62.1689 | 0.045776 | -0.11963 | 0.046997 | 0.27344 | -0.17197 | -0.18585 | 0.050354 | 0.1236 | -62.3428 | 60.1273 | 60.0906 | 62.2009 | 62.352 | 122.5067 | 62.1643 | 60.141
4405.0156 | 0.045776 | 0.39093 | -0.76584 | -0.2211 | 0.11643 | -0.25207 | -0.19012 | 60.1639 | -61.9629 | -0.018311 | -62.2421 | 60.1639 | 62.1918 | 62.146 | 0.061035 | -0.10361 | 0.03952 | 0.2713 | -0.13886 | -0.19867 | 0 | 0.022888 | -62.352 | 60.0861 | 60.0906 | 62.2009 | 62.3245 | 122.4884 | 62.1872 | 60.1776
4406.6875 | 0.045776 | 0.42618 | -0.76584 | -0.22964 | 0.11749 | -0.24887 | -0.19119 | 60.1959 | -61.9308 | 0.059509 | -62.2147 | 60.2417 | 62.1826 | 62.1735 | 0.061035 | -0.10254 | 0.053406 | 0.27985 | -0.12817 | -0.1944 | 0.045776 | 0.082397 | -62.384 | 60.1639 | 60.1456 | 62.2101 | 62.3657 | 122.5525 | 62.1231 | 60.1685
4408.4062 | 0.061035 | 0.41229 | -0.7637 | -0.23819 | 0.10895 | -0.25207 | -0.18158 | 60.1868 | -61.9308 | 0.032043 | -62.2284 | 60.2142 | 62.1918 | 62.1597 | 0.045776 | -0.10574 | 0.057678 | 0.27023 | -0.14099 | -0.19226 | -0.018311 | 0.036621 | -62.4344 | 60.1456 | 60.1456 | 62.2284 | 62.3474 | 122.4838 | 62.1689 | 60.1959
4410.0781 | 0.045776 | 0.4187 | -0.75089 | -0.25528 | 0.1207 | -0.24674 | -0.17944 | 60.1868 | -61.9446 | 0.064087 | -62.2147 | 60.2646 | 62.1597 | 62.178 | 0.045776 | -0.099335 | 0.069427 | 0.28839 | -0.1506 | -0.19012 | 0.009155 | 0.036621 | -62.4069 | 60.173 | 60.1318 | 62.2375 | 62.3291 | 122.4747 | 62.1552 | 60.1868
4411.7344 | 0.045776 | 0.37598 | -0.784 | -0.25742 | 0.099335 | -0.2948 | -0.18372 | 60.0861 | -61.9446 | 0.045776 | -62.2375 | 60.1822 | 62.1918 | 62.1643 | 0.045776 | -0.12711 | 0.043793 | 0.27344 | -0.16556 | -0.18051 | 0.054932 | 0.16479 | -62.3245 | 60.1089 | 60.1135 | 62.2055 | 62.3611 | 122.5525 | 62.146 | 60.1364
4413.4531 | 0.045776 | 0.38986 | -0.7637 | -0.22858 | 0.11963 | -0.24139 | -0.18585 | 60.1364 | -61.9766 | 0 | -62.2421 | 60.2417 | 62.1918 | 62.1735 | 0.076294 | -0.10361 | 0.03952 | 0.28625 | -0.13031 | -0.19333 | -0.045776 | -0.027466 | -62.439 | 60.1639 | 60.1364 | 62.2147 | 62.3566 | 122.4426 | 62.178 | 60.2325
4415.125 | 0.030518 | 0.40802 | -0.75089 | -0.23178 | 0.11536 | -0.25742 | -0.18265 | 60.1593 | -61.9675 | 0.059509 | -62.2101 | 60.2325 | 62.2101 | 62.1735 | 0.045776 | -0.10254 | 0.045929 | 0.28519 | -0.1442 | -0.18478 | 0.027466 | 0.091553 | -62.384 | 60.1273 | 60.1593 | 62.2192 | 62.3291 | 122.5845 | 62.1231 | 60.173
4416.7969 | 0.045776 | 0.392 | -0.76691 | -0.26596 | 0.098267 | -0.28839 | -0.19119 | 60.1822 | -61.8484 | 0.14648 | -62.1689 | 60.1868 | 62.1506 | 62.1414 | 0.076294 | -0.1239 | 0.048065 | 0.28625 | -0.16663 | -0.18692 | 0.14191 | 0.2655 | -62.2925 | 60.1273 | 60.0769 | 62.2009 | 62.3199 | 122.5571 | 62.1414 | 60.1273
4418.4688 | 0.061035 | 0.37384 | -0.79147 | -0.24139 | 0.10574 | -0.29266 | -0.20828 | 60.1135 | -61.9675 | 0.045776 | -62.2284 | 60.1776 | 62.2009 | 62.1735 | 0.045776 | -0.12176 | 0.035248 | 0.27451 | -0.15274 | -0.18051 | 0.041199 | 0.13733 | -62.3337 | 60.1089 | 60.0815 | 62.2467 | 62.3428 | 122.5159 | 62.1506 | 60.1639
4420.1562 | 0.045776 | 0.40482 | -0.76157 | -0.22644 | 0.10254 | -0.24674 | -0.18906 | 60.2188 | -61.9492 | 0.041199 | -62.2284 | 60.2417 | 62.1872 | 62.1506 | 0.061035 | -0.091858 | 0.046997 | 0.29266 | -0.13031 | -0.19226 | 0.013733 | 0.041199 | -62.4069 | 60.1547 | 60.1685 | 62.2375 | 62.3566 | 122.4976 | 62.1506 | 60.1959
4421.8438 | 0.030518 | 0.36636 | -0.77438 | -0.25314 | 0.11215 | -0.28946 | -0.1976 | 60.1273 | -61.9629 | 0.027466 | -62.2375 | 60.1593 | 62.1735 | 62.1552 | 0.045776 | -0.12817 | 0.048065 | 0.27878 | -0.16449 | -0.17944 | 0.022888 | 0.068665 | -62.3566 | 60.0906 | 60.0998 | 62.233 | 62.3428 | 122.4609 | 62.1643 | 60.1822
4423.5312 | 0.045776 | 0.37491 | -0.77225 | -0.24246 | 0.099335 | -0.26596 | -0.19226 | 60.1547 | -61.9308 | 0.036621 | -62.2467 | 60.1593 | 62.1689 | 62.1689 | 0.076294 | -0.11643 | 0.036316 | 0.27451 | -0.14847 | -0.18585 | 0.027466 | 0.082397 | -62.352 | 60.0952 | 60.0906 | 62.2147 | 62.3428 | 122.4426 | 62.1826 | 60.173
4425.2031 | 0.061035 | 0.42297 | -0.77011 | -0.22537 | 0.10895 | -0.23712 | -0.20187 | 60.2325 | -61.94 | 0.050354 | -62.233 | 60.2509 | 62.1689 | 62.1597 | 0.045776 | -0.093994 | 0.049133 | 0.29266 | -0.13138 | -0.1944 | 0.013733 | 0.027466 | -62.4161 | 60.1685 | 60.1547 | 62.2375 | 62.3611 | 122.4655 | 62.146 | 60.2005
4426.8906 | 0.045776 | 0.43472 | -0.77225 | -0.24353 | 0.11856 | -0.24887 | -0.19546 | 60.1913 | -61.9263 | 0.054932 | -62.2055 | 60.2509 | 62.1826 | 62.1552 | 0.061035 | -0.10574 | 0.041656 | 0.27237 | -0.14099 | -0.19226 | 0.045776 | 0.068665 | -62.384 | 60.1685 | 60.1456 | 62.233 | 62.3245 | 122.5479 | 62.1323 | 60.1593
4428.5625 | 0.076294 | 0.42938 | -0.76157 | -0.2681 | 0.12176 | -0.2681 | -0.18158 | 60.1501 | -61.9583 | 0.059509 | -62.2055 | 60.2554 | 62.1918 | 62.1643 | 0.045776 | -0.10574 | 0.063019 | 0.28625 | -0.15595 | -0.18692 | 0.032043 | 0.09613 | -62.3749 | 60.173 | 60.1501 | 62.2284 | 62.3657 | 122.58 | 62.1323 | 60.1273
4430.2344 | 0.030518 | 0.36636 | -0.77866 | -0.25955 | 0.098267 | -0.2948 | -0.19653 | 60.173 | -61.8439 | 0.14648 | -62.1918 | 60.1639 | 62.1414 | 62.1414 | 0.045776 | -0.13779 | 0.049133 | 0.2681 | -0.17517 | -0.18372 | 0.15106 | 0.25177 | -62.2879 | 60.0861 | 60.1044 | 62.2009 | 62.3291 | 122.5525 | 62.1506 | 60.1318
4431.9062 | 0.091553 | 0.37277 | -0.78613 | -0.23178 | 0.11643 | -0.28839 | -0.18906 | 60.1456 | -61.9629 | 0.018311 | -62.233 | 60.1639 | 62.1643 | 62.1826 | 0.045776 | -0.11322 | 0.033112 | 0.27557 | -0.15808 | -0.17624 | 0.032043 | 0.07782 | -62.352 | 60.1227 | 60.1318 | 62.2192 | 62.3428 | 122.438 | 62.1735 | 60.1776
4433.5781 | 0.10681 | 0.35782 | -0.784 | -0.24674 | 0.11002 | -0.27023 | -0.19226 | 60.1501 | -61.9583 | 0.032043 | -62.2421 | 60.1868 | 62.178 | 62.1826 | 0.030518 | -0.12924 | 0.055542 | 0.27985 | -0.15915 | -0.18799 | 0.032043 | 0.068665 | -62.3611 | 60.0952 | 60.0723 | 62.2284 | 62.3657 | 122.438 | 62.1964 | 60.173
4435.2812 | 0.045776 | 0.38559 | -0.76157 | -0.2243 | 0.10468 | -0.24887 | -0.18799 | 60.1501 | -62.0132 | -0.059509 | -62.2742 | 60.2417 | 62.1964 | 62.1552 | 0.045776 | -0.097198 | 0.038452 | 0.28839 | -0.13245 | -0.18585 | -0.050354 | -0.059509 | -62.4161 | 60.1364 | 60.1273 | 62.2421 | 62.3428 | 122.4747 | 62.1826 | 60.141
4436.9531 | 0.045776 | 0.36636 | -0.77972 | -0.24994 | 0.095062 | -0.28412 | -0.19653 | 60.1089 | -61.9675 | 0.041199 | -62.233 | 60.173 | 62.1964 | 62.1643 | 0.045776 | -0.1239 | 0.035248 | 0.26916 | -0.15381 | -0.18692 | 0.050354 | 0.1236 | -62.3428 | 60.0998 | 60.1089 | 62.2055 | 62.3337 | 122.4838 | 62.1506 | 60.1776
4438.625 | 0.061035 | 0.41229 | -0.75302 | -0.23071 | 0.10574 | -0.23392 | -0.19119 | 60.1364 | -62.059 | -0.059509 | -62.2925 | 60.2783 | 62.1918 | 62.1918 | 0.045776 | -0.095062 | 0.038452 | 0.28625 | -0.13672 | -0.19867 | -0.068665 | -0.10986 | -62.4619 | 60.1868 | 60.1593 | 62.2421 | 62.3474 | 122.4747 | 62.1735 | 60.2051
4440.2969 | 0.045776 | 0.41977 | -0.75302 | -0.25314 | 0.11963 | -0.24353 | -0.18372 | 60.1776 | -61.9629 | 0.068665 | -62.2238 | 60.2509 | 62.1918 | 62.1826 | 0.045776 | -0.10254 | 0.05661 | 0.27771 | -0.14206 | -0.18906 | 0.036621 | 0.07782 | -62.3703 | 60.1685 | 60.1547 | 62.2238 | 62.3383 | 122.5616 | 62.1094 | 60.1822
4441.9531 | 0.045776 | 0.37064 | -0.79041 | -0.25101 | 0.10681 | -0.28305 | -0.19012 | 60.1181 | -61.9537 | 0.041199 | -62.233 | 60.1868 | 62.178 | 62.1597 | 0.061035 | -0.1239 | 0.053406 | 0.27878 | -0.15915 | -0.17731 | 0.059509 | 0.1236 | -62.3291 | 60.0815 | 60.0769 | 62.2147 | 62.3657 | 122.5021 | 62.1552 | 60.173
4443.625 | 0.045776 | 0.37598 | -0.79361 | -0.2478 | 0.11429 | -0.27237 | -0.19974 | 60.2005 | -61.8622 | 0.14648 | -62.1918 | 60.1685 | 62.1689 | 62.1368 | 0.015259 | -0.1207 | 0.037384 | 0.2713 | -0.14954 | -0.19119 | 0.14191 | 0.2655 | -62.2696 | 60.0998 | 60.0815 | 62.2055 | 62.3154 | 122.5708 | 62.1323 | 60.1547
4445.2969 | 0.045776 | 0.37064 | -0.76691 | -0.22324 | 0.10895 | -0.25742 | -0.19653 | 60.2005 | -61.908 | 0.050354 | -62.2192 | 60.1547 | 62.1872 | 62.1597 | 0.030518 | -0.11536 | 0.041656 | 0.27664 | -0.13992 | -0.19119 | 0.032043 | 0.07782 | -62.3383 | 60.0952 | 60.0403 | 62.2192 | 62.352 | 122.4609 | 62.1964 | 60.1501
4446.9844 | 0.030518 | 0.41122 | -0.77118 | -0.22217 | 0.10788 | -0.24139 | -0.18478 | 60.1364 | -62.0224 | -0.091553 | -62.265 | 60.2371 | 62.2101 | 62.178 | 0.076294 | -0.10681 | 0.042725 | 0.28305 | -0.13138 | -0.18906 | -0.068665 | -0.09613 | -62.4435 | 60.1593 | 60.1501 | 62.233 | 62.3474 | 122.4792 | 62.1964 | 60.1868
4448.6562 | 0.045776 | 0.41977 | -0.75943 | -0.22858 | 0.11215 | -0.2446 | -0.17624 | 60.1593 | -61.9995 | 0.009155 | -62.2559 | 60.2234 | 62.2055 | 62.1689 | 0.045776 | -0.09079 | 0.058746 | 0.28198 | -0.14633 | -0.19333 | -0.059509 | -0.036621 | -62.4435 | 60.1501 | 60.1181 | 62.2513 | 62.3795 | 122.4472 | 62.1872 | 60.1776
4450.3281 | 0.045776 | 0.40909 | -0.77759 | -0.26916 | 0.10468 | -0.25955 | -0.18906 | 60.1181 | -61.9858 | 0.036621 | -62.2513 | 60.2371 | 62.2101 | 62.1689 | 0.030518 | -0.098267 | 0.060883 | 0.27985 | -0.14954 | -0.18478 | 0.036621 | 0.091553 | -62.3932 | 60.2051 | 60.1501 | 62.233 | 62.3566 | 122.58 | 62.1277 | 60.1639
4452 | 0.045776 | 0.36957 | -0.77866 | -0.26276 | 0.11002 | -0.29159 | -0.20081 | 60.0998 | -61.9629 | 0.022888 | -62.2467 | 60.1685 | 62.1735 | 62.1597 | 0.015259 | -0.12711 | 0.043793 | 0.27878 | -0.1741 | -0.18265 | 0.027466 | 0.10986 | -62.352 | 60.0861 | 60.1089 | 62.2375 | 62.352 | 122.4747 | 62.1597 | 60.1456
4453.6875 | 0.045776 | 0.37811 | -0.77225 | -0.23071 | 0.12283 | -0.26062 | -0.18051 | 60.1593 | -61.9766 | -0.013733 | -62.2421 | 60.2051 | 62.1826 | 62.1918 | 0.061035 | -0.1004 | 0.040588 | 0.28198 | -0.13138 | -0.18692 | 0 | 0.027466 | -62.352 | 60.141 | 60.1181 | 62.2147 | 62.3108 | 122.5021 | 62.1735 | 60.1639
4455.4062 | 0.045776 | 0.37064 | -0.78613 | -0.23712 | 0.099335 | -0.27664 | -0.20721 | 60.1501 | -61.9308 | 0.036621 | -62.2513 | 60.1776 | 62.1872 | 62.146 | 0.045776 | -0.11856 | 0.035248 | 0.27344 | -0.15595 | -0.18585 | 0.027466 | 0.07782 | -62.3657 | 60.0723 | 60.1364 | 62.1872 | 62.3474 | 122.438 | 62.1826 | 60.2051
4457.0781 | 0.030518 | 0.42725 | -0.76263 | -0.22644 | 0.11002 | -0.24567 | -0.18265 | 60.1456 | -62.027 | -0.036621 | -62.2696 | 60.228 | 62.1872 | 62.1643 | 0.030518 | -0.091858 | 0.049133 | 0.28305 | -0.13138 | -0.19653 | -0.082397 | -0.054932 | -62.4619 | 60.1776 | 60.1868 | 62.2467 | 62.3795 | 122.4472 | 62.178 | 60.2142
4458.75 | 0.061035 | 0.42831 | -0.7605 | -0.23712 | 0.1004 | -0.24353 | -0.18478 | 60.1868 | -61.94 | 0.054932 | -62.2101 | 60.2325 | 62.1872 | 62.1643 | 0.045776 | -0.095062 | 0.063019 | 0.27557 | -0.13992 | -0.18906 | 0.045776 | 0.086975 | -62.3795 | 60.173 | 60.1639 | 62.2192 | 62.3383 | 122.5754 | 62.1231 | 60.173
4460.4844 | 0.045776 | 0.37384 | -0.78507 | -0.25528 | 0.11002 | -0.30441 | -0.19333 | 60.1501 | -61.9034 | 0.11902 | -62.2147 | 60.1868 | 62.1643 | 62.1597 | 0.045776 | -0.13351 | 0.03952 | 0.28091 | -0.15595 | -0.18906 | 0.13733 | 0.21973 | -62.2787 | 60.1089 | 60.1135 | 62.2238 | 62.3337 | 122.5845 | 62.1323 | 60.1501
4462.1562 | 0.061035 | 0.36316 | -0.77972 | -0.23926 | 0.099335 | -0.27664 | -0.19974 | 60.173 | -61.9308 | 0.036621 | -62.2238 | 60.1364 | 62.1735 | 62.1414 | 0.015259 | -0.12497 | 0.035248 | 0.27237 | -0.15595 | -0.18478 | 0.032043 | 0.07782 | -62.3383 | 60.0952 | 60.0952 | 62.2238 | 62.352 | 122.438 | 62.1918 | 60.1639
4463.8281 | 0.061035 | 0.36957 | -0.78186 | -0.23605 | 0.10895 | -0.28519 | -0.19974 | 60.1318 | -61.9766 | 0.032043 | -62.2375 | 60.1685 | 62.1872 | 62.1689 | 0.061035 | -0.12497 | 0.043793 | 0.27451 | -0.16235 | -0.19226 | 0.022888 | 0.11902 | -62.3428 | 60.1227 | 60.1044 | 62.2421 | 62.3245 | 122.4792 | 62.1414 | 60.1639
4465.4844 | 0.045776 | 0.38773 | -0.76584 | -0.23285 | 0.11963 | -0.25314 | -0.18158 | 60.1913 | -62.0041 | -0.032043 | -62.2559 | 60.1822 | 62.2147 | 62.2101 | 0.045776 | -0.10681 | 0.03952 | 0.2681 | -0.13565 | -0.19974 | 0 | 0.004578 | -62.3566 | 60.1318 | 60.0952 | 62.233 | 62.3428 | 122.4976 | 62.178 | 60.141
4467.1562 | 0.061035 | 0.39841 | -0.78186 | -0.2446 | 0.11108 | -0.27237 | -0.20401 | 60.1501 | -61.9812 | 0.07782 | -62.2604 | 60.2234 | 62.2055 | 62.1735 | 0.045776 | -0.10254 | 0.052338 | 0.2713 | -0.15595 | -0.19012 | 0.064087 | 0.13275 | -62.4069 | 60.173 | 60.1822 | 62.2101 | 62.3428 | 122.525 | 62.1231 | 60.1868
4468.8438 | 0.030518 | 0.37491 | -0.78507 | -0.25742 | 0.10681 | -0.28519 | -0.19974 | 60.2005 | -61.8668 | 0.13733 | -62.1872 | 60.2005 | 62.1643 | 62.1506 | 0.045776 | -0.1239 | 0.043793 | 0.27878 | -0.16342 | -0.18585 | 0.15106 | 0.23804 | -62.2787 | 60.0723 | 60.1089 | 62.2147 | 62.352 | 122.5708 | 62.1231 | 60.1364
4470.5156 | 0.030518 | 0.37598 | -0.78827 | -0.25207 | 0.11856 | -0.28519 | -0.1944 | 60.2188 | -61.8576 | 0.14191 | -62.178 | 60.1822 | 62.1964 | 62.1414 | 0.030518 | -0.12924 | 0.049133 | 0.2713 | -0.15915 | -0.19333 | 0.15564 | 0.2655 | -62.2971 | 60.1089 | 60.0906 | 62.2284 | 62.3428 | 122.5388 | 62.1277 | 60.1547
4472.1719 | 0.030518 | 0.37384 | -0.77866 | -0.21683 | 0.11856 | -0.25314 | -0.18585 | 60.2188 | -61.9034 | 0.041199 | -62.2147 | 60.1639 | 62.2055 | 62.146 | 0.030518 | -0.10147 | 0.044861 | 0.27664 | -0.14633 | -0.20187 | 0.041199 | 0.068665 | -62.3428 | 60.0952 | 60.0632 | 62.2147 | 62.3566 | 122.4518 | 62.1872 | 60.1639
4473.8438 | 0.061035 | 0.42404 | -0.76157 | -0.25207 | 0.11749 | -0.2446 | -0.18906 | 60.1868 | -61.9812 | 0.045776 | -62.2147 | 60.2737 | 62.2055 | 62.1872 | 0.045776 | -0.10254 | 0.052338 | 0.28091 | -0.14954 | -0.20935 | 0.041199 | 0.086975 | -62.3795 | 60.1776 | 60.1639 | 62.2238 | 62.3383 | 122.5754 | 62.1231 | 60.1685
4475.5312 | 0.061035 | 0.37064 | -0.7872 | -0.24567 | 0.11322 | -0.28519 | -0.19333 | 60.1959 | -61.8622 | 0.14191 | -62.2009 | 60.1501 | 62.1689 | 62.1552 | 0.045776 | -0.1239 | 0.060883 | 0.26596 | -0.15808 | -0.18692 | 0.16022 | 0.27466 | -62.2742 | 60.0861 | 60.0723 | 62.2009 | 62.3199 | 122.5754 | 62.1094 | 60.1089
4477.2031 | 0.030518 | 0.37277 | -0.78507 | -0.22324 | 0.10681 | -0.25742 | -0.19226 | 60.1776 | -61.9675 | -0.009155 | -62.2467 | 60.1913 | 62.2101 | 62.178 | 0.030518 | -0.10468 | 0.048065 | 0.28198 | -0.14633 | -0.1944 | 0.018311 | 0.032043 | -62.3337 | 60.1318 | 60.0998 | 62.2101 | 62.3566 | 122.4884 | 62.178 | 60.1547
4478.8906 | 0.045776 | 0.3717 | -0.77331 | -0.23819 | 0.10788 | -0.27344 | -0.19012 | 60.1501 | -61.9492 | 0.032043 | -62.2559 | 60.2005 | 62.1597 | 62.1506 | 0.061035 | -0.11963 | 0.044861 | 0.27664 | -0.14847 | -0.19119 | 0.036621 | 0.082397 | -62.3703 | 60.0723 | 60.0815 | 62.1918 | 62.384 | 122.4472 | 62.1964 | 60.2097
4480.5781 | 0.061035 | 0.38986 | -0.78613 | -0.25528 | 0.11108 | -0.27344 | -0.18799 | 60.2188 | -61.8805 | 0.16022 | -62.1872 | 60.1822 | 62.1414 | 62.146 | 0.061035 | -0.11643 | 0.054474 | 0.27985 | -0.1506 | -0.1944 | 0.15564 | 0.23804 | -62.3108 | 60.1227 | 60.1044 | 62.2147 | 62.3337 | 122.525 | 62.1368 | 60.173
4482.25 | 0.045776 | 0.37918 | -0.76691 | -0.21896 | 0.11215 | -0.25635 | -0.18585 | 60.2051 | -61.9354 | 0 | -62.233 | 60.1959 | 62.178 | 62.178 | 0.045776 | -0.1004 | 0.03952 | 0.28198 | -0.13779 | -0.18265 | 0.022888 | 0.032043 | -62.3428 | 60.0952 | 60.1089 | 62.1872 | 62.3428 | 122.4884 | 62.1597 | 60.1913
4483.9219 | 0.061035 | 0.4187 | -0.76263 | -0.23605 | 0.11536 | -0.24567 | -0.19012 | 60.1181 | -62.0544 | -0.068665 | -62.2742 | 60.2417 | 62.1964 | 62.2055 | 0.061035 | -0.091858 | 0.03952 | 0.29053 | -0.14313 | -0.19653 | -0.082397 | -0.086975 | -62.4573 | 60.1776 | 60.1364 | 62.2238 | 62.3749 | 122.4609 | 62.2009 | 60.1776
4485.5938 | 0.076294 | 0.42297 | -0.77545 | -0.26382 | 0.11215 | -0.25314 | -0.18372 | 60.1685 | -61.9858 | 0.054932 | -62.2147 | 60.2554 | 62.178 | 62.1826 | 0.030518 | -0.10147 | 0.054474 | 0.28305 | -0.14206 | -0.1944 | 0.036621 | 0.07782 | -62.4023 | 60.173 | 60.1776 | 62.2101 | 62.3611 | 122.5845 | 62.1506 | 60.1501
4487.2656 | 0.045776 | 0.40054 | -0.77331 | -0.28091 | 0.11856 | -0.28519 | -0.18372 | 60.1868 | -61.8759 | 0.16022 | -62.1689 | 60.1593 | 62.1597 | 62.1597 | 0.045776 | -0.12283 | 0.048065 | 0.27771 | -0.16342 | -0.18906 | 0.11902 | 0.25635 | -62.3199 | 60.1089 | 60.0952 | 62.2009 | 62.3474 | 122.5296 | 62.1185 | 60.1776
4488.9375 | 0.061035 | 0.41657 | -0.78934 | -0.26596 | 0.11429 | -0.26382 | -0.18906 | 60.1227 | -61.972 | 0.054932 | -62.2375 | 60.2463 | 62.1964 | 62.1689 | 0.045776 | -0.10254 | 0.068359 | 0.27878 | -0.14847 | -0.19226 | 0.036621 | 0.11902 | -62.4069 | 60.1868 | 60.1639 | 62.2421 | 62.3611 | 122.5479 | 62.1048 | 60.1456
4490.6406 | 0.061035 | 0.42297 | -0.76157 | -0.24994 | 0.10361 | -0.23819 | -0.18906 | 60.2005 | -61.9446 | 0.036621 | -62.2238 | 60.2371 | 62.1735 | 62.1643 | 0.061035 | -0.10574 | 0.054474 | 0.27771 | -0.13351 | -0.18692 | 0.013733 | 0.032043 | -62.4023 | 60.1868 | 60.1547 | 62.2375 | 62.3566 | 122.4884 | 62.1506 | 60.1959
4492.3125 | 0.061035 | 0.38132 | -0.77011 | -0.25742 | 0.11536 | -0.29266 | -0.18799 | 60.1639 | -61.8713 | 0.14648 | -62.1964 | 60.1913 | 62.1872 | 62.1414 | 0.045776 | -0.1239 | 0.048065 | 0.26916 | -0.16342 | -0.18372 | 0.15564 | 0.24719 | -62.2604 | 60.1181 | 60.1044 | 62.2055 | 62.3291 | 122.5616 | 62.1323 | 60.1273
4494 | 0.13733 | 0.42191 | -0.76477 | -0.2478 | 0.12283 | -0.25314 | -0.18372 | 60.1547 | -61.9583 | 0.059509 | -62.2192 | 60.2692 | 62.1735 | 62.1872 | 0.045776 | -0.091858 | 0.052338 | 0.29373 | -0.14954 | -0.19333 | 0.045776 | 0.10071 | -62.384 | 60.1776 | 60.1456 | 62.2238 | 62.3428 | 122.5616 | 62.1231 | 60.173
4495.6875 | 0.030518 | 0.3952 | -0.75623 | -0.22858 | 0.11002 | -0.24567 | -0.17944 | 60.1273 | -62.0087 | -0.068665 | -62.2787 | 60.228 | 62.1964 | 62.1872 | 0.076294 | -0.11215 | 0.041656 | 0.27878 | -0.13779 | -0.17838 | -0.054932 | -0.064087 | -62.3978 | 60.1273 | 60.1227 | 62.2421 | 62.352 | 122.4792 | 62.1597 | 60.1501
4497.4219 | 0.061035 | 0.41229 | -0.74875 | -0.23498 | 0.11536 | -0.25421 | -0.19333 | 60.1135 | -62.0316 | -0.054932 | -62.2559 | 60.2692 | 62.2055 | 62.1643 | 0.045776 | -0.1004 | 0.045929 | 0.28946 | -0.13779 | -0.18692 | -0.09613 | -0.086975 | -62.4756 | 60.1868 | 60.173 | 62.2238 | 62.3611 | 122.438 | 62.1918 | 60.1868
4499.0938 | 0.045776 | 0.4187 | -0.78079 | -0.26596 | 0.10788 | -0.28412 | -0.18906 | 60.1501 | -61.9354 | 0.10529 | -62.2238 | 60.2097 | 62.1826 | 62.1643 | 0.061035 | -0.11643 | 0.048065 | 0.27771 | -0.15808 | -0.17731 | 0.036621 | 0.14648 | -62.384 | 60.1639 | 60.173 | 62.233 | 62.3428 | 122.5159 | 62.1231 | 60.1776
4500.7969 | 0.13733 | 0.37384 | -0.76157 | -0.2211 | 0.12176 | -0.26703 | -0.18372 | 60.1913 | -61.9171 | 0.045776 | -62.2101 | 60.1685 | 62.178 | 62.1735 | 0.030518 | -0.11536 | 0.033112 | 0.27985 | -0.14313 | -0.19226 | 0.054932 | 0.091553 | -62.2971 | 60.1089 | 60.1273 | 62.2559 | 62.3703 | 122.4701 | 62.1826 | 60.173
4502.5 | 0.030518 | 0.37918 | -0.78827 | -0.25101 | 0.10468 | -0.29694 | -0.1976 | 60.173 | -61.9034 | 0.1236 | -62.1964 | 60.2005 | 62.178 | 62.1689 | 0.061035 | -0.12711 | 0.046997 | 0.27878 | -0.16556 | -0.17624 | 0.14648 | 0.21515 | -62.2879 | 60.0906 | 60.0998 | 62.2055 | 62.3383 | 122.5571 | 62.1323 | 60.1364
4504.1719 | 0.030518 | 0.38132 | -0.76263 | -0.23071 | 0.11108 | -0.24353 | -0.18799 | 60.1685 | -62.0224 | -0.054932 | -62.2559 | 60.2005 | 62.178 | 62.1964 | 0.076294 | -0.10254 | 0.033112 | 0.28198 | -0.13992 | -0.18906 | -0.013733 | -0.009155 | -62.3703 | 60.1318 | 60.1135 | 62.2101 | 62.3383 | 122.4976 | 62.2009 | 60.1547
4505.8594 | 0.030518 | 0.38238 | -0.79147 | -0.25955 | 0.10895 | -0.28412 | -0.19974 | 60.2005 | -61.8668 | 0.16479 | -62.1918 | 60.1913 | 62.178 | 62.1414 | 0.030518 | -0.11536 | 0.042725 | 0.27771 | -0.14954 | -0.19012 | 0.13733 | 0.26093 | -62.3062 | 60.1273 | 60.1044 | 62.2147 | 62.3291 | 122.5342 | 62.1323 | 60.173
4507.5469 | 0.12207 | 0.42191 | -0.77118 | -0.24567 | 0.10574 | -0.24353 | -0.19333 | 60.2005 | -61.9629 | 0.064087 | -62.2055 | 60.2554 | 62.1826 | 62.1689 | 0.061035 | -0.10468 | 0.054474 | 0.28412 | -0.13992 | -0.20081 | 0.036621 | 0.082397 | -62.384 | 60.173 | 60.173 | 62.1918 | 62.3611 | 122.5754 | 62.1277 | 60.1593
4509.2344 | 0.045776 | 0.39948 | -0.77225 | -0.26382 | 0.10147 | -0.28625 | -0.1944 | 60.1913 | -61.8942 | 0.16937 | -62.178 | 60.1685 | 62.1506 | 62.1597 | 0.061035 | -0.12497 | 0.05127 | 0.27878 | -0.17197 | -0.19333 | 0.12817 | 0.24719 | -62.3291 | 60.1273 | 60.1364 | 62.1964 | 62.3383 | 122.525 | 62.1231 | 60.1547
4510.9531 | 0.045776 | 0.42404 | -0.76157 | -0.23178 | 0.097198 | -0.23392 | -0.18372 | 60.1318 | -62.0453 | -0.059509 | -62.2787 | 60.2509 | 62.1872 | 62.1964 | 0.030518 | -0.098267 | 0.061951 | 0.30014 | -0.13351 | -0.1944 | -0.07782 | -0.068665 | -62.4802 | 60.1822 | 60.1501 | 62.2238 | 62.3703 | 122.4518 | 62.1735 | 60.1913
4512.6562 | 0.030518 | 0.40802 | -0.79468 | -0.25635 | 0.13031 | -0.28198 | -0.1976 | 60.1776 | -61.8942 | 0.12817 | -62.1964 | 60.1822 | 62.1735 | 62.1597 | 0.045776 | -0.11963 | 0.050201 | 0.27664 | -0.15915 | -0.18372 | 0.082397 | 0.20599 | -62.352 | 60.1547 | 60.1501 | 62.2055 | 62.3291 | 122.5113 | 62.1185 | 60.1913
4514.3438 | 0.061035 | 0.36743 | -0.77225 | -0.24033 | 0.11856 | -0.28625 | -0.19546 | 60.1318 | -61.972 | 0.064087 | -62.2238 | 60.1868 | 62.2009 | 62.1735 | 0.061035 | -0.12283 | 0.045929 | 0.27023 | -0.15915 | -0.18478 | 0.059509 | 0.15106 | -62.3062 | 60.1181 | 60.1273 | 62.2284 | 62.3611 | 122.5525 | 62.1094 | 60.1593
4516.0469 | 0.061035 | 0.3717 | -0.79788 | -0.23712 | 0.10361 | -0.28305 | -0.21042 | 60.2234 | -61.8668 | 0.14648 | -62.2055 | 60.1776 | 62.1872 | 62.1414 | 0.061035 | -0.11856 | 0.03418 | 0.2681 | -0.16235 | -0.18585 | 0.14191 | 0.25177 | -62.2742 | 60.1089 | 60.1089 | 62.2147 | 62.3291 | 122.5571 | 62.1414 | 60.1318
4517.7188 | 0.045776 | 0.41122 | -0.76584 | -0.21255 | 0.12497 | -0.23285 | -0.19653 | 60.173 | -62.0224 | -0.036621 | -62.265 | 60.2417 | 62.1689 | 62.1552 | 0.061035 | -0.084381 | 0.048065 | 0.27557 | -0.12604 | -0.19867 | -0.073242 | -0.064087 | -62.4527 | 60.1822 | 60.173 | 62.2101 | 62.352 | 122.438 | 62.178 | 60.1959
4519.4531 | 0.045776 | 0.43579 | -0.75409 | -0.2478 | 0.095062 | -0.25314 | -0.18265 | 60.1639 | -62.027 | -0.036621 | -62.265 | 60.2371 | 62.1872 | 62.1872 | 0.045776 | -0.099335 | 0.048065 | 0.28625 | -0.13672 | -0.18906 | -0.10071 | -0.068665 | -62.471 | 60.173 | 60.1639 | 62.233 | 62.384 | 122.438 | 62.178 | 60.1822
4521.125 | 0.091553 | 0.42618 | -0.75836 | -0.25421 | 0.11429 | -0.25528 | -0.18585 | 60.1959 | -61.94 | 0.059509 | -62.2055 | 60.2417 | 62.1826 | 62.1826 | 0.045776 | -0.095062 | 0.059814 | 0.27664 | -0.14847 | -0.18585 | 0.032043 | 0.091553 | -62.3795 | 60.1318 | 60.173 | 62.2101 | 62.352 | 122.5754 | 62.1231 | 60.1776
4522.8125 | 0.030518 | 0.38773 | -0.77545 | -0.27451 | 0.11002 | -0.28198 | -0.19653 | 60.1959 | -61.8759 | 0.17853 | -62.1826 | 60.173 | 62.1872 | 62.1552 | 0.045776 | -0.12924 | 0.059814 | 0.27771 | -0.16022 | -0.18478 | 0.13275 | 0.25177 | -62.3016 | 60.1089 | 60.1044 | 62.1964 | 62.352 | 122.525 | 62.1185 | 60.1547
4524.5 | 0.045776 | 0.36423 | -0.77438 | -0.24139 | 0.11215 | -0.298 | -0.19974 | 60.1089 | -61.972 | 0.050354 | -62.2421 | 60.2051 | 62.1872 | 62.2009 | 0.045776 | -0.12497 | 0.03952 | 0.27344 | -0.15595 | -0.18906 | 0.045776 | 0.13275 | -62.3291 | 60.0952 | 60.1135 | 62.2192 | 62.3474 | 122.5204 | 62.1414 | 60.1822
4526.1719 | 0.10681 | 0.35996 | -0.78934 | -0.23605 | 0.10788 | -0.28519 | -0.20081 | 60.1456 | -61.9583 | 0.032043 | -62.2375 | 60.2051 | 62.1826 | 62.1918 | 0.045776 | -0.12924 | 0.035248 | 0.27451 | -0.15274 | -0.18799 | 0.022888 | 0.11444 | -62.3337 | 60.1318 | 60.1135 | 62.2055 | 62.3566 | 122.4884 | 62.1552 | 60.173
4527.8594 | 0.12207 | 0.36957 | -0.77972 | -0.23392 | 0.10361 | -0.2713 | -0.19119 | 60.173 | -61.9263 | 0.045776 | -62.2421 | 60.1639 | 62.178 | 62.1643 | 0.061035 | -0.11963 | 0.045929 | 0.27237 | -0.15274 | -0.18585 | 0.027466 | 0.086975 | -62.3611 | 60.1044 | 60.0952 | 62.2101 | 62.3337 | 122.438 | 62.178 | 60.1868
4529.5469 | 0.12207 | 0.36636 | -0.78507 | -0.24994 | 0.098267 | -0.27771 | -0.18372 | 60.1685 | -61.9446 | 0.036621 | -62.2559 | 60.1685 | 62.2055 | 62.1735 | 0.045776 | -0.12283 | 0.043793 | 0.26916 | -0.16235 | -0.19119 | 0.027466 | 0.07782 | -62.3611 | 60.1089 | 60.1089 | 62.2604 | 62.352 | 122.438 | 62.1826 | 60.173
4531.2188 | 0.030518 | 0.38345 | -0.76584 | -0.22858 | 0.11002 | -0.23712 | -0.19974 | 60.1822 | -61.9995 | -0.041199 | -62.2559 | 60.2234 | 62.1689 | 62.1826 | 0.045776 | -0.10254 | 0.033112 | 0.28412 | -0.13031 | -0.20508 | -0.004578 | -0.004578 | -62.3703 | 60.1135 | 60.1135 | 62.233 | 62.3474 | 122.4838 | 62.1689 | 60.1959
4532.8906 | 0.091553 | 0.36423 | -0.77972 | -0.23605 | 0.10788 | -0.28412 | -0.19012 | 60.1364 | -61.9812 | 0.032043 | -62.2559 | 60.1868 | 62.2101 | 62.1597 | 0.045776 | -0.1239 | 0.03952 | 0.27344 | -0.15915 | -0.18372 | 0.027466 | 0.09613 | -62.3474 | 60.1181 | 60.1181 | 62.2101 | 62.3566 | 122.5021 | 62.1872 | 60.1776
4534.5625 | 0.030518 | 0.36423 | -0.76263 | -0.22217 | 0.10895 | -0.2478 | -0.19226 | 60.228 | -61.9583 | -0.004578 | -62.2238 | 60.2097 | 62.1735 | 62.1414 | 0.061035 | -0.10468 | 0.038452 | 0.28305 | -0.13779 | -0.20187 | 0.022888 | 0.036621 | -62.3428 | 60.1089 | 60.1135 | 62.2147 | 62.3383 | 122.4884 | 62.1689 | 60.1776
4536.2344 | 0.12207 | 0.41229 | -0.76584 | -0.25421 | 0.12497 | -0.25421 | -0.18372 | 60.2005 | -61.9537 | 0.059509 | -62.2238 | 60.2371 | 62.1735 | 62.1826 | 0.030518 | -0.10574 | 0.046997 | 0.28839 | -0.13245 | -0.19546 | 0.045776 | 0.073242 | -62.384 | 60.1685 | 60.1456 | 62.1964 | 62.3474 | 122.58 | 62.1231 | 60.1639
4537.9062 | 0.045776 | 0.40482 | -0.78507 | -0.27344 | 0.11429 | -0.27023 | -0.19653 | 60.1913 | -61.8942 | 0.16479 | -62.1872 | 60.2005 | 62.1735 | 62.1552 | 0.061035 | -0.12283 | 0.049133 | 0.2713 | -0.16556 | -0.18478 | 0.12817 | 0.23346 | -62.3245 | 60.141 | 60.0906 | 62.2101 | 62.3291 | 122.5342 | 62.1094 | 60.1868
4539.5781 | 0.10681 | 0.41977 | -0.76263 | -0.25742 | 0.10788 | -0.24353 | -0.18158 | 60.1822 | -61.9537 | 0.059509 | -62.2192 | 60.2646 | 62.1964 | 62.1414 | 0.045776 | -0.099335 | 0.050201 | 0.2948 | -0.14099 | -0.1976 | 0.041199 | 0.082397 | -62.3749 | 60.1639 | 60.1593 | 62.2238 | 62.3428 | 122.5571 | 62.1323 | 60.1868
4541.25 | 0.045776 | 0.39093 | -0.78079 | -0.26916 | 0.11856 | -0.28305 | -0.18906 | 60.1593 | -61.8988 | 0.14191 | -62.1964 | 60.1959 | 62.178 | 62.1552 | 0.045776 | -0.12176 | 0.055542 | 0.27237 | -0.16449 | -0.19333 | 0.082397 | 0.18768 | -62.3657 | 60.1364 | 60.1456 | 62.2284 | 62.3474 | 122.5067 | 62.1094 | 60.1868
4542.9219 | 0.030518 | 0.3952 | -0.77545 | -0.2681 | 0.10147 | -0.27557 | -0.19012 | 60.1776 | -61.8896 | 0.14191 | -62.1964 | 60.1959 | 62.1643 | 62.1552 | 0.030518 | -0.12497 | 0.066223 | 0.27664 | -0.16449 | -0.19867 | 0.07782 | 0.18768 | -62.3611 | 60.1913 | 60.1456 | 62.2192 | 62.352 | 122.525 | 62.1048 | 60.1685
4544.6406 | 0.061035 | 0.40802 | -0.76263 | -0.24139 | 0.11108 | -0.24033 | -0.18585 | 60.1959 | -61.9537 | 0.036621 | -62.2238 | 60.2463 | 62.178 | 62.1597 | 0.061035 | -0.092926 | 0.042725 | 0.28412 | -0.11749 | -0.1976 | -0.004578 | 0.018311 | -62.4115 | 60.1456 | 60.1227 | 62.2192 | 62.3795 | 122.4609 | 62.1643 | 60.1593
4546.3281 | 0.045776 | 0.35996 | -0.77972 | -0.24887 | 0.11215 | -0.2948 | -0.18799 | 60.0861 | -61.9537 | 0.036621 | -62.2375 | 60.1959 | 62.178 | 62.1552 | 0.045776 | -0.13138 | 0.043793 | 0.2681 | -0.15808 | -0.18265 | 0.059509 | 0.14191 | -62.3245 | 60.1089 | 60.1089 | 62.233 | 62.3291 | 122.525 | 62.1368 | 60.1593
4548.0156 | 0.061035 | 0.37811 | -0.7637 | -0.23071 | 0.10681 | -0.27023 | -0.18265 | 60.2005 | -61.9263 | 0.045776 | -62.2284 | 60.1639 | 62.1735 | 62.1643 | 0.045776 | -0.11429 | 0.028839 | 0.27023 | -0.13779 | -0.18265 | 0.045776 | 0.082397 | -62.3154 | 60.0861 | 60.0769 | 62.2055 | 62.3291 | 122.4426 | 62.1826 | 60.1868
4549.6875 | 0.045776 | 0.37918 | -0.75409 | -0.2243 | 0.11536 | -0.26169 | -0.18799 | 60.1822 | -61.9446 | 0.009155 | -62.2192 | 60.2005 | 62.1689 | 62.1597 | 0.061035 | -0.10147 | 0.03418 | 0.25635 | -0.13031 | -0.18585 | 0.004578 | 0.032043 | -62.3383 | 60.1089 | 60.1089 | 62.2192 | 62.3154 | 122.4838 | 62.1643 | 60.1501
4551.3594 | 0.061035 | 0.37705 | -0.79575 | -0.26276 | 0.11108 | -0.28305 | -0.1944 | 60.228 | -61.8759 | 0.13275 | -62.2009 | 60.1593 | 62.1689 | 62.1689 | 0.045776 | -0.12924 | 0.049133 | 0.27023 | -0.16556 | -0.19546 | 0.16022 | 0.27008 | -62.265 | 60.0952 | 60.1227 | 62.1964 | 62.3199 | 122.5525 | 62.1414 | 60.1685
4553.0625 | 0.030518 | 0.39627 | -0.77438 | -0.2713 | 0.10468 | -0.26703 | -0.19546 | 60.1868 | -61.9171 | 0.1236 | -62.2055 | 60.228 | 62.1964 | 62.1735 | 0.045776 | -0.10361 | 0.059814 | 0.27771 | -0.1506 | -0.1976 | 0.064087 | 0.15564 | -62.384 | 60.1822 | 60.1547 | 62.2513 | 62.3657 | 122.5067 | 62.1048 | 60.173
4554.7344 | 0.061035 | 0.39307 | -0.77118 | -0.23926 | 0.1004 | -0.23605 | -0.18265 | 60.1364 | -62.0407 | -0.059509 | -62.2742 | 60.26 | 62.1964 | 62.178 | 0.045776 | -0.10788 | 0.050201 | 0.29266 | -0.13458 | -0.19867 | -0.064087 | -0.086975 | -62.4573 | 60.1822 | 60.1318 | 62.2559 | 62.3657 | 122.4609 | 62.1735 | 60.1868
4556.4375 | 0.030518 | 0.39841 | -0.77866 | -0.25742 | 0.12176 | -0.26916 | -0.19226 | 60.1547 | -61.9675 | 0.073242 | -62.2467 | 60.2417 | 62.2009 | 62.1735 | 0.045776 | -0.11749 | 0.046997 | 0.27023 | -0.1506 | -0.1944 | 0.050354 | 0.13275 | -62.3978 | 60.1685 | 60.1776 | 62.2421 | 62.3428 | 122.525 | 62.1185 | 60.1822
4558.125 | 0.045776 | 0.3685 | -0.7637 | -0.22858 | 0.11002 | -0.27237 | -0.19333 | 60.1959 | -61.908 | 0.059509 | -62.2284 | 60.1593 | 62.1643 | 62.1689 | 0.045776 | -0.12497 | 0.036316 | 0.27344 | -0.14847 | -0.18692 | 0.041199 | 0.09613 | -62.3199 | 60.0906 | 60.0906 | 62.2147 | 62.352 | 122.438 | 62.1643 | 60.1822
4559.8125 | 0.045776 | 0.42084 | -0.75836 | -0.24246 | 0.11536 | -0.24674 | -0.17944 | 60.2005 | -61.9537 | 0.036621 | -62.2284 | 60.2325 | 62.1643 | 62.1597 | 0.045776 | -0.088654 | 0.045929 | 0.28305 | -0.13138 | -0.19333 | -0.013733 | 0.022888 | -62.4069 | 60.1456 | 60.1639 | 62.2375 | 62.384 | 122.4655 | 62.1826 | 60.1868
4561.5 | 0.045776 | 0.38452 | -0.75729 | -0.23392 | 0.11215 | -0.25955 | -0.18692 | 60.1456 | -61.94 | -0.022888 | -62.2375 | 60.1959 | 62.1964 | 62.1826 | 0.030518 | -0.11215 | 0.046997 | 0.28091 | -0.1442 | -0.18372 | 0.013733 | 0.045776 | -62.3383 | 60.1227 | 60.0952 | 62.2375 | 62.3337 | 122.493 | 62.1826 | 60.1776
4563.1875 | 0.045776 | 0.35782 | -0.77972 | -0.26703 | 0.1239 | -0.29373 | -0.19226 | 60.1547 | -61.9354 | 0.086975 | -62.233 | 60.1913 | 62.1872 | 62.1826 | 0.030518 | -0.12497 | 0.05127 | 0.28519 | -0.17838 | -0.18906 | 0.10529 | 0.20142 | -62.2879 | 60.0998 | 60.1135 | 62.1964 | 62.3474 | 122.5708 | 62.1506 | 60.1593
4564.9062 | 0.045776 | 0.3952 | -0.77759 | -0.25314 | 0.10361 | -0.26169 | -0.19653 | 60.1364 | -61.972 | 0.073242 | -62.2467 | 60.2325 | 62.1597 | 62.1597 | 0.061035 | -0.099335 | 0.043793 | 0.28198 | -0.1474 | -0.19333 | 0.045776 | 0.12817 | -62.4023 | 60.1868 | 60.1776 | 62.2284 | 62.3383 | 122.525 | 62.1185 | 60.1547
4566.5938 | 0.045776 | 0.38986 | -0.75943 | -0.21683 | 0.11002 | -0.24887 | -0.19012 | 60.1318 | -62.0132 | -0.068665 | -62.2787 | 60.2417 | 62.2101 | 62.1872 | 0.030518 | -0.10147 | 0.050201 | 0.28839 | -0.13779 | -0.18585 | -0.054932 | -0.068665 | -62.4344 | 60.1593 | 60.1639 | 62.2467 | 62.3611 | 122.4884 | 62.1689 | 60.1868
4568.2969 | 0.061035 | 0.38773 | -0.76904 | -0.23285 | 0.10574 | -0.26062 | -0.18158 | 60.1959 | -61.9125 | 0.009155 | -62.2101 | 60.1822 | 62.1643 | 62.1643 | 0.061035 | -0.11749 | 0.050201 | 0.27237 | -0.14099 | -0.18585 | 0.018311 | 0.064087 | -62.3291 | 60.1044 | 60.0815 | 62.233 | 62.3428 | 122.493 | 62.1918 | 60.1501
4569.9844 | 0.061035 | 0.38559 | -0.77118 | -0.24674 | 0.10788 | -0.26596 | -0.17838 | 60.1959 | -61.9308 | 0.036621 | -62.2192 | 60.1685 | 62.178 | 62.146 | 0.045776 | -0.11749 | 0.046997 | 0.27557 | -0.13992 | -0.19226 | 0.009155 | 0.059509 | -62.3337 | 60.0952 | 60.0586 | 62.2101 | 62.3611 | 122.4792 | 62.178 | 60.1593
4571.6719 | 0.030518 | 0.36423 | -0.78934 | -0.26703 | 0.10574 | -0.28519 | -0.19012 | 60.2097 | -61.8576 | 0.15106 | -62.1689 | 60.1868 | 62.1597 | 62.1414 | 0.045776 | -0.12604 | 0.043793 | 0.27237 | -0.17303 | -0.18158 | 0.1236 | 0.25177 | -62.2925 | 60.1089 | 60.1227 | 62.2055 | 62.3199 | 122.5296 | 62.1414 | 60.1501
4573.4062 | 0.030518 | 0.39948 | -0.76904 | -0.24994 | 0.10681 | -0.25528 | -0.18906 | 60.1501 | -62.0544 | -0.07782 | -62.2925 | 60.2646 | 62.2009 | 62.2055 | 0.030518 | -0.10895 | 0.049133 | 0.28625 | -0.14099 | -0.19333 | -0.073242 | -0.09613 | -62.4344 | 60.1547 | 60.1547 | 62.2421 | 62.3611 | 122.4792 | 62.178 | 60.1913
4575.0938 | 0.061035 | 0.35889 | -0.77011 | -0.23071 | 0.10681 | -0.2681 | -0.18051 | 60.1822 | -61.8851 | 0.064087 | -62.2009 | 60.1639 | 62.178 | 62.1643 | 0.045776 | -0.12711 | 0.043793 | 0.27344 | -0.14099 | -0.18906 | 0.032043 | 0.09613 | -62.3337 | 60.0861 | 60.0815 | 62.2421 | 62.352 | 122.438 | 62.1689 | 60.1685
4576.7656 | 0.030518 | 0.40268 | -0.76691 | -0.26169 | 0.11002 | -0.26596 | -0.18906 | 60.1639 | -61.9354 | 0.10529 | -62.2147 | 60.2142 | 62.1552 | 62.1826 | 0.030518 | -0.10788 | 0.057678 | 0.28732 | -0.16556 | -0.19546 | 0.064087 | 0.13275 | -62.3932 | 60.1685 | 60.1456 | 62.233 | 62.3428 | 122.5204 | 62.1552 | 60.173
4578.5 | 0.061035 | 0.36529 | -0.77866 | -0.23712 | 0.11643 | -0.26916 | -0.18585 | 60.1913 | -61.9171 | 0.041199 | -62.2147 | 60.1501 | 62.1643 | 62.1826 | 0.030518 | -0.11536 | 0.040588 | 0.27451 | -0.13245 | -0.19226 | 0.050354 | 0.086975 | -62.3245 | 60.1089 | 60.0861 | 62.2101 | 62.352 | 122.4426 | 62.1826 | 60.1913
4580.1875 | 0.045776 | 0.36743 | -0.77118 | -0.24887 | 0.10681 | -0.27985 | -0.20294 | 60.1822 | -61.8896 | 0.10986 | -62.2147 | 60.1913 | 62.1872 | 62.1414 | 0.030518 | -0.13138 | 0.045929 | 0.28946 | -0.16449 | -0.18585 | 0.16022 | 0.24261 | -62.2833 | 60.0861 | 60.1044 | 62.2147 | 62.3566 | 122.5845 | 62.1277 | 60.1547
4581.875 | 0.030518 | 0.38025 | -0.75409 | -0.22324 | 0.10574 | -0.24674 | -0.18478 | 60.141 | -62.0041 | -0.068665 | -62.2879 | 60.2325 | 62.2055 | 62.1826 | 0.061035 | -0.093994 | 0.043793 | 0.28519 | -0.12924 | -0.19333 | -0.045776 | -0.064087 | -62.3978 | 60.1501 | 60.1227 | 62.233 | 62.3703 | 122.4838 | 62.2055 | 60.1593
4583.5625 | 0.061035 | 0.38025 | -0.75729 | -0.23178 | 0.11322 | -0.25742 | -0.18372 | 60.173 | -61.9263 | 0.013733 | -62.2101 | 60.1822 | 62.1826 | 62.1552 | 0.045776 | -0.10788 | 0.037384 | 0.27237 | -0.13351 | -0.18585 | 0.004578 | 0.045776 | -62.3428 | 60.1135 | 60.0998 | 62.2238 | 62.3291 | 122.493 | 62.1735 | 60.1685
4585.2344 | 0.061035 | 0.38238 | -0.77652 | -0.26489 | 0.11322 | -0.27771 | -0.19653 | 60.2005 | -61.8713 | 0.16479 | -62.1826 | 60.173 | 62.1689 | 62.1552 | 0.061035 | -0.12817 | 0.03952 | 0.27878 | -0.16022 | -0.19653 | 0.14648 | 0.26093 | -62.3154 | 60.0861 | 60.1089 | 62.2101 | 62.3383 | 122.5342 | 62.1094 | 60.1639
4586.9219 | 0.15259 | 0.36423 | -0.77438 | -0.23392 | 0.11749 | -0.27237 | -0.19867 | 60.2005 | -61.9171 | 0.064087 | -62.2192 | 60.1685 | 62.1964 | 62.1552 | 0.076294 | -0.1239 | 0.041656 | 0.27237 | -0.14954 | -0.18906 | 0.036621 | 0.07782 | -62.352 | 60.1318 | 60.141 | 62.2513 | 62.3703 | 122.4243 | 62.2055 | 60.1868
4588.6094 | 0.045776 | 0.39948 | -0.77972 | -0.27344 | 0.11108 | -0.26062 | -0.20081 | 60.1913 | -61.908 | 0.13733 | -62.1918 | 60.2005 | 62.178 | 62.1414 | 0.045776 | -0.11108 | 0.052338 | 0.27451 | -0.14633 | -0.20081 | 0.091553 | 0.18768 | -62.3566 | 60.1501 | 60.1318 | 62.2147 | 62.3245 | 122.5204 | 62.1048 | 60.2005
4590.2969 | 0.015259 | 0.38132 | -0.76904 | -0.23178 | 0.11643 | -0.2446 | -0.19333 | 60.1685 | -61.9812 | -0.018311 | -62.2513 | 60.2188 | 62.1872 | 62.178 | 0.076294 | -0.10147 | 0.040588 | 0.27023 | -0.13138 | -0.18799 | 0.004578 | 0.022888 | -62.352 | 60.1181 | 60.0723 | 62.2375 | 62.3383 | 122.5067 | 62.1918 | 60.1456
4592 | 0.16785 | 0.42297 | -0.784 | -0.25955 | 0.11749 | -0.2681 | -0.19867 | 60.1364 | -61.9766 | 0.059509 | -62.2467 | 60.2646 | 62.1918 | 62.146 | 0.030518 | -0.11856 | 0.041656 | 0.27664 | -0.15274 | -0.19226 | 0.036621 | 0.10986 | -62.4161 | 60.1913 | 60.173 | 62.2284 | 62.3383 | 122.5479 | 62.1002 | 60.1639
4593.6875 | 0.045776 | 0.41977 | -0.77331 | -0.22964 | 0.10361 | -0.24674 | -0.18265 | 60.1089 | -62.0087 | -0.050354 | -62.265 | 60.2554 | 62.1872 | 62.1964 | 0.030518 | -0.098267 | 0.058746 | 0.28839 | -0.12711 | -0.18692 | -0.10071 | -0.068665 | -62.471 | 60.1868 | 60.1227 | 62.2559 | 62.3795 | 122.4518 | 62.1826 | 60.1776
4595.4375 | 0.045776 | 0.439 | -0.76797 | -0.25421 | 0.11429 | -0.2478 | -0.17303 | 60.1593 | -61.9629 | 0 | -62.2604 | 60.2325 | 62.1872 | 62.178 | 0.076294 | -0.10468 | 0.049133 | 0.27664 | -0.13245 | -0.18372 | -0.050354 | -0.022888 | -62.4298 | 60.1501 | 60.1456 | 62.2421 | 62.3657 | 122.4609 | 62.178 | 60.1822
4597.1562 | 0.045776 | 0.42404 | -0.77118 | -0.25421 | 0.099335 | -0.2446 | -0.17944 | 60.1135 | -62.0224 | -0.018311 | -62.265 | 60.2417 | 62.1826 | 62.1826 | 0.030518 | -0.11429 | 0.059814 | 0.28198 | -0.13565 | -0.19546 | -0.09613 | -0.050354 | -62.4481 | 60.141 | 60.1501 | 62.2284 | 62.352 | 122.438 | 62.1826 | 60.1913
4598.8438 | 0.076294 | 0.36209 | -0.784 | -0.2681 | 0.10361 | -0.28732 | -0.19653 | 60.1685 | -61.8576 | 0.17395 | -62.1872 | 60.1913 | 62.1689 | 62.1506 | 0.045776 | -0.13031 | 0.040588 | 0.26382 | -0.17197 | -0.18051 | 0.13275 | 0.26093 | -62.2833 | 60.0952 | 60.0906 | 62.2147 | 62.3428 | 122.5662 | 62.1323 | 60.141
4600.5312 | 0.061035 | 0.38879 | -0.77011 | -0.24887 | 0.10361 | -0.25635 | -0.18051 | 60.1135 | -62.027 | -0.064087 | -62.2833 | 60.228 | 62.1964 | 62.1964 | 0.045776 | -0.10468 | 0.046997 | 0.27878 | -0.13779 | -0.19119 | -0.068665 | -0.064087 | -62.4115 | 60.1547 | 60.1364 | 62.2284 | 62.3703 | 122.4884 | 62.1918 | 60.1639
4602.2031 | 0.061035 | 0.38773 | -0.77759 | -0.26489 | 0.10895 | -0.29159 | -0.19546 | 60.1181 | -61.9217 | 0.082397 | -62.2284 | 60.1639 | 62.1872 | 62.1597 | 0.061035 | -0.1239 | 0.042725 | 0.26916 | -0.15274 | -0.18265 | 0.086975 | 0.1831 | -62.3108 | 60.1273 | 60.1044 | 62.2147 | 62.3428 | 122.5662 | 62.114 | 60.1593
4603.9062 | 0.21362 | 0.36102 | -0.75516 | -0.23926 | 0.10788 | -0.26703 | -0.18692 | 60.1868 | -61.9125 | 0.036621 | -62.2238 | 60.1501 | 62.1964 | 62.1643 | 0.045776 | -0.12176 | 0.03952 | 0.28091 | -0.14313 | -0.17517 | 0.059509 | 0.10986 | -62.2971 | 60.1181 | 60.0861 | 62.2787 | 62.3886 | 122.4518 | 62.1826 | 60.1685
4605.5938 | 0.1831 | 0.41657 | -0.784 | -0.27557 | 0.10254 | -0.25314 | -0.1976 | 60.1456 | -61.9904 | 0.059509 | -62.2604 | 60.26 | 62.1918 | 62.1872 | 0.045776 | -0.10254 | 0.048065 | 0.27344 | -0.16235 | -0.19974 | 0.041199 | 0.10529 | -62.4161 | 60.1959 | 60.1822 | 62.2238 | 62.3978 | 122.5571 | 62.114 | 60.1959
4607.2656 | 0.045776 | 0.4155 | -0.77972 | -0.23285 | 0.11536 | -0.24887 | -0.18906 | 60.1181 | -62.0224 | -0.064087 | -62.2742 | 60.2417 | 62.2009 | 62.1689 | 0.061035 | -0.10681 | 0.048065 | 0.29159 | -0.13565 | -0.19546 | -0.07782 | -0.10529 | -62.4435 | 60.173 | 60.141 | 62.265 | 62.3657 | 122.4701 | 62.1918 | 60.2005
4608.9375 | 0.045776 | 0.3717 | -0.77011 | -0.26276 | 0.11643 | -0.28839 | -0.19974 | 60.1593 | -61.908 | 0.10986 | -62.2192 | 60.1913 | 62.1735 | 62.1643 | 0.030518 | -0.12283 | 0.038452 | 0.27664 | -0.16235 | -0.17731 | 0.10986 | 0.21515 | -62.2925 | 60.1044 | 60.1089 | 62.2101 | 62.3566 | 122.5708 | 62.1414 | 60.1364
4610.6094 | 0.1831 | 0.41977 | -0.77331 | -0.25528 | 0.10147 | -0.25314 | -0.19119 | 60.1868 | -61.9812 | 0.064087 | -62.2284 | 60.2783 | 62.2147 | 62.1964 | 0.061035 | -0.093994 | 0.049133 | 0.298 | -0.14099 | -0.1944 | 0.022888 | 0.086975 | -62.3703 | 60.1639 | 60.1547 | 62.2192 | 62.3566 | 122.5662 | 62.1277 | 60.2234
4612.3125 | 0.061035 | 0.37277 | -0.77331 | -0.25528 | 0.10895 | -0.29266 | -0.19226 | 60.1273 | -61.9446 | 0.064087 | -62.2284 | 60.1822 | 62.1918 | 62.1689 | 0.045776 | -0.12497 | 0.059814 | 0.26916 | -0.16556 | -0.1944 | 0.082397 | 0.17395 | -62.3154 | 60.1135 | 60.0998 | 62.2147 | 62.3795 | 122.5571 | 62.1231 | 60.1501
4614.0156 | 0.030518 | 0.41443 | -0.76584 | -0.23819 | 0.11963 | -0.23605 | -0.19012 | 60.1318 | -62.0132 | -0.045776 | -62.2787 | 60.228 | 62.1826 | 62.178 | 0.045776 | -0.1004 | 0.048065 | 0.27344 | -0.13458 | -0.19546 | -0.10071 | -0.07782 | -62.4664 | 60.1776 | 60.1593 | 62.2421 | 62.3795 | 122.4426 | 62.1735 | 60.1959
4615.6875 | 0.076294 | 0.36209 | -0.78507 | -0.24994 | 0.11749 | -0.29694 | -0.19546 | 60.1044 | -61.9766 | 0.041199 | -62.2467 | 60.1959 | 62.1964 | 62.1689 | 0.030518 | -0.13779 | 0.042725 | 0.28198 | -0.16556 | -0.18372 | 0.041199 | 0.13733 | -62.3291 | 60.1273 | 60.1044 | 62.2238 | 62.3566 | 122.5021 | 62.1506 | 60.1547
4617.375 | 0.015259 | 0.42404 | -0.76477 | -0.24674 | 0.11536 | -0.24567 | -0.18158 | 60.1776 | -61.9812 | 0 | -62.2559 | 60.2325 | 62.1689 | 62.1735 | 0.030518 | -0.10895 | 0.041656 | 0.28519 | -0.13458 | -0.20187 | -0.059509 | -0.045776 | -62.439 | 60.1593 | 60.1547 | 62.2559 | 62.3566 | 122.4564 | 62.1689 | 60.2234
4619.0938 | 0.045776 | 0.42084 | -0.75836 | -0.24353 | 0.10361 | -0.25314 | -0.16983 | 60.1135 | -62.0224 | -0.064087 | -62.2879 | 60.2417 | 62.2238 | 62.1826 | 0.045776 | -0.10361 | 0.048065 | 0.28732 | -0.13138 | -0.18158 | -0.082397 | -0.068665 | -62.471 | 60.1685 | 60.1501 | 62.2421 | 62.352 | 122.4289 | 62.178 | 60.1822
4620.8125 | 0.045776 | 0.42191 | -0.77225 | -0.24994 | 0.11108 | -0.24674 | -0.18372 | 60.1273 | -62.0636 | -0.054932 | -62.2696 | 60.2554 | 62.2101 | 62.1918 | 0.045776 | -0.10895 | 0.054474 | 0.28625 | -0.14633 | -0.19226 | -0.10529 | -0.086975 | -62.4527 | 60.1639 | 60.1639 | 62.233 | 62.3383 | 122.4472 | 62.1368 | 60.1822
4622.4844 | 0.1831 | 0.3685 | -0.77118 | -0.24033 | 0.11108 | -0.29053 | -0.19012 | 60.1318 | -61.9354 | 0.041199 | -62.2375 | 60.1547 | 62.2238 | 62.1643 | 0.15259 | -0.11322 | 0.049133 | 0.27451 | -0.1506 | -0.17517 | 0.050354 | 0.10529 | -62.3245 | 60.1227 | 60.1227 | 62.2696 | 62.352 | 122.4472 | 62.1964 | 60.1547
4624.1719 | 0.030518 | 0.3717 | -0.77866 | -0.2681 | 0.10574 | -0.27664 | -0.1944 | 60.2051 | -61.8576 | 0.16937 | -62.1964 | 60.1913 | 62.146 | 62.178 | 0.045776 | -0.13672 | 0.055542 | 0.26382 | -0.15381 | -0.18692 | 0.13733 | 0.27924 | -62.2971 | 60.1227 | 60.1135 | 62.1918 | 62.3108 | 122.5296 | 62.1185 | 60.1456
4625.875 | 0.12207 | 0.42084 | -0.77225 | -0.24674 | 0.11429 | -0.25101 | -0.19333 | 60.1776 | -61.9583 | 0.050354 | -62.2238 | 60.2646 | 62.1597 | 62.1689 | 0.045776 | -0.097198 | 0.043793 | 0.2681 | -0.14206 | -0.19333 | 0.027466 | 0.091553 | -62.384 | 60.1822 | 60.1593 | 62.2147 | 62.3566 | 122.5662 | 62.1277 | 60.1593
4627.5625 | 0.13733 | 0.41229 | -0.75729 | -0.26062 | 0.11749 | -0.25314 | -0.19546 | 60.1364 | -61.9995 | 0.036621 | -62.2421 | 60.2646 | 62.2101 | 62.2009 | 0.030518 | -0.11002 | 0.054474 | 0.27664 | -0.15595 | -0.20294 | 0.009155 | 0.10986 | -62.384 | 60.1776 | 60.1913 | 62.2238 | 62.3291 | 122.5845 | 62.1094 | 60.1639
4629.2812 | 0.16785 | 0.3685 | -0.7637 | -0.2446 | 0.10361 | -0.29159 | -0.19012 | 60.141 | -61.9308 | 0.041199 | -62.2421 | 60.1685 | 62.1964 | 62.1414 | 0.061035 | -0.1239 | 0.048065 | 0.27985 | -0.15488 | -0.18265 | 0.018311 | 0.086975 | -62.3199 | 60.1273 | 60.1364 | 62.2604 | 62.3749 | 122.4197 | 62.2055 | 60.1868
4630.9844 | 0.091553 | 0.41336 | -0.76584 | -0.25421 | 0.11429 | -0.2478 | -0.18051 | 60.2051 | -61.9492 | 0.054932 | -62.2238 | 60.2463 | 62.1826 | 62.146 | 0.045776 | -0.097198 | 0.049133 | 0.29159 | -0.12817 | -0.19867 | 0.009155 | 0.045776 | -62.3886 | 60.1685 | 60.1685 | 62.2147 | 62.3108 | 122.5067 | 62.1689 | 60.1959
4632.6875 | 0.1831 | 0.41763 | -0.77438 | -0.25314 | 0.10681 | -0.2478 | -0.17944 | 60.1456 | -61.9675 | 0.045776 | -62.2009 | 60.2737 | 62.1689 | 62.1735 | 0.061035 | -0.11749 | 0.049133 | 0.27664 | -0.13992 | -0.19226 | 0.027466 | 0.091553 | -62.3703 | 60.1822 | 60.1547 | 62.2192 | 62.3337 | 122.58 | 62.1277 | 60.1547
4634.4531 | 0.12207 | 0.37384 | -0.76263 | -0.25421 | 0.10468 | -0.28839 | -0.20615 | 60.0998 | -61.9675 | 0.018311 | -62.2467 | 60.1685 | 62.1872 | 62.1826 | 0.030518 | -0.12497 | 0.042725 | 0.27557 | -0.1741 | -0.17838 | 0.013733 | 0.09613 | -62.352 | 60.1044 | 60.1181 | 62.2055 | 62.3428 | 122.4701 | 62.1735 | 60.1822
4636.1562 | 0.1831 | 0.3685 | -0.75409 | -0.23605 | 0.11429 | -0.26276 | -0.18799 | 60.2142 | -61.9217 | 0.027466 | -62.2101 | 60.1685 | 62.1826 | 62.1552 | 0.061035 | -0.11963 | 0.035248 | 0.28732 | -0.13245 | -0.18265 | 0.059509 | 0.07782 | -62.2925 | 60.1501 | 60.141 | 62.2559 | 62.3611 | 122.4701 | 62.1826 | 60.1685
4637.8281 | 0.1831 | 0.41336 | -0.77225 | -0.25421 | 0.12283 | -0.24139 | -0.19226 | 60.1959 | -61.9583 | 0.064087 | -62.2147 | 60.2646 | 62.1826 | 62.1872 | 0.045776 | -0.1004 | 0.041656 | 0.27771 | -0.1442 | -0.20508 | 0.036621 | 0.091553 | -62.3795 | 60.1593 | 60.1913 | 62.2147 | 62.3383 | 122.5845 | 62.1094 | 60.173
4639.5 | 0.045776 | 0.42084 | -0.76584 | -0.24567 | 0.11856 | -0.25742 | -0.19546 | 60.1547 | -62.0178 | -0.022888 | -62.2696 | 60.2097 | 62.2055 | 62.178 | 0.030518 | -0.11002 | 0.044861 | 0.28625 | -0.13886 | -0.19867 | -0.091553 | -0.054932 | -62.4573 | 60.1822 | 60.1776 | 62.2467 | 62.3383 | 122.4335 | 62.1597 | 60.2097
4641.1875 | 0.12207 | 0.36743 | -0.76797 | -0.25955 | 0.10895 | -0.29587 | -0.18372 | 60.1181 | -61.9858 | 0.032043 | -62.2513 | 60.1776 | 62.1826 | 62.178 | 0.045776 | -0.12924 | 0.045929 | 0.27557 | -0.16022 | -0.18799 | 0.022888 | 0.10986 | -62.3474 | 60.1181 | 60.1044 | 62.2467 | 62.3291 | 122.4792 | 62.1689 | 60.1501
4642.8594 | 0.21362 | 0.36636 | -0.75623 | -0.23712 | 0.11856 | -0.27237 | -0.18158 | 60.2188 | -61.9354 | 0.027466 | -62.2147 | 60.173 | 62.1826 | 62.1368 | 0.045776 | -0.11536 | 0.048065 | 0.27878 | -0.11643 | -0.17838 | 0.050354 | 0.10529 | -62.2925 | 60.1593 | 60.1639 | 62.2742 | 62.384 | 122.4747 | 62.1735 | 60.1639
4644.5469 | 0.19836 | 0.4187 | -0.77759 | -0.26169 | 0.10681 | -0.2681 | -0.19653 | 60.1273 | -62.0087 | 0.054932 | -62.2604 | 60.2463 | 62.1826 | 62.1826 | 0.030518 | -0.10361 | 0.058746 | 0.27985 | -0.1474 | -0.19867 | 0.022888 | 0.10986 | -62.4115 | 60.2142 | 60.2005 | 62.2787 | 62.3657 | 122.5616 | 62.0911 | 60.1639
4646.2188 | 0.015259 | 0.37918 | -0.78293 | -0.24887 | 0.097198 | -0.2948 | -0.20721 | 60.1685 | -61.8942 | 0.1236 | -62.2009 | 60.2097 | 62.1735 | 62.1643 | 0.061035 | -0.12283 | 0.036316 | 0.27664 | -0.15595 | -0.18372 | 0.11444 | 0.21515 | -62.2925 | 60.1181 | 60.1181 | 62.2238 | 62.3154 | 122.5708 | 62.1185 | 60.1593
4647.9219 | 0.045776 | 0.41977 | -0.76584 | -0.23392 | 0.11322 | -0.25101 | -0.1944 | 60.1181 | -62.0544 | -0.07782 | -62.2971 | 60.2325 | 62.1918 | 62.1964 | 0.061035 | -0.085449 | 0.048065 | 0.29266 | -0.13458 | -0.20508 | -0.082397 | -0.086975 | -62.4481 | 60.1639 | 60.1456 | 62.2559 | 62.3703 | 122.4655 | 62.1872 | 60.1868
4649.5938 | 0.076294 | 0.41763 | -0.77118 | -0.26062 | 0.12283 | -0.24033 | -0.19226 | 60.1959 | -61.9492 | 0.032043 | -62.233 | 60.2325 | 62.1826 | 62.1552 | 0.030518 | -0.10681 | 0.057678 | 0.27344 | -0.14313 | -0.19653 | -0.013733 | 0.036621 | -62.4115 | 60.1547 | 60.1547 | 62.233 | 62.352 | 122.4838 | 62.1826 | 60.1685
4651.2812 | 0.045776 | 0.37064 | -0.77545 | -0.26169 | 0.11429 | -0.28412 | -0.20081 | 60.1868 | -61.8622 | 0.14191 | -62.2238 | 60.1868 | 62.178 | 62.1689 | 0.030518 | -0.13138 | 0.054474 | 0.27878 | -0.16769 | -0.18585 | 0.13733 | 0.25635 | -62.2604 | 60.0861 | 60.1044 | 62.2238 | 62.3062 | 122.58 | 62.1323 | 60.1135
4652.9844 | 0.22888 | 0.4187 | -0.78827 | -0.26916 | 0.10895 | -0.26596 | -0.19653 | 60.1273 | -61.9812 | 0.041199 | -62.2604 | 60.2509 | 62.1872 | 62.1964 | 0.076294 | -0.099335 | 0.059814 | 0.28732 | -0.15808 | -0.18799 | 0.032043 | 0.09613 | -62.3749 | 60.2646 | 60.2234 | 62.2559 | 62.384 | 122.5708 | 62.1231 | 60.1685
4654.6562 | 0.030518 | 0.38452 | -0.78079 | -0.24353 | 0.10574 | -0.28412 | -0.18692 | 60.1913 | -61.8622 | 0.15564 | -62.1872 | 60.2005 | 62.1643 | 62.1368 | 0.045776 | -0.13031 | 0.041656 | 0.28198 | -0.14633 | -0.19226 | 0.14648 | 0.27924 | -62.2833 | 60.1135 | 60.1227 | 62.1964 | 62.3062 | 122.525 | 62.1048 | 60.1501
4656.3281 | 0.10681 | 0.37491 | -0.77225 | -0.23071 | 0.10254 | -0.27344 | -0.19226 | 60.1273 | -61.9629 | 0.018311 | -62.2604 | 60.1822 | 62.1826 | 62.1689 | 0.030518 | -0.13138 | 0.035248 | 0.27664 | -0.1474 | -0.17944 | 0.022888 | 0.10071 | -62.3474 | 60.1318 | 60.1364 | 62.2238 | 62.3611 | 122.4609 | 62.178 | 60.1822
4658 | 0.091553 | 0.41763 | -0.76584 | -0.25101 | 0.10895 | -0.23071 | -0.18265 | 60.2463 | -61.9583 | 0.041199 | -62.2147 | 60.2509 | 62.1826 | 62.1918 | 0.061035 | -0.099335 | 0.03418 | 0.27878 | -0.12497 | -0.19546 | 0.013733 | 0.041199 | -62.4161 | 60.1776 | 60.1639 | 62.2238 | 62.3566 | 122.5021 | 62.1597 | 60.2005
4659.6719 | 0.045776 | 0.37384 | -0.77438 | -0.27237 | 0.11429 | -0.28091 | -0.19226 | 60.1913 | -61.8759 | 0.16479 | -62.1826 | 60.1822 | 62.178 | 62.146 | 0.076294 | -0.12924 | 0.052338 | 0.26489 | -0.16876 | -0.18906 | 0.13275 | 0.26093 | -62.2971 | 60.1089 | 60.1135 | 62.2238 | 62.3108 | 122.5296 | 62.1323 | 60.1685
4661.4062 | 0.030518 | 0.36529 | -0.75623 | -0.23819 | 0.11963 | -0.25848 | -0.19333 | 60.1822 | -61.9354 | 0.009155 | -62.2147 | 60.1959 | 62.1872 | 62.1872 | 0.061035 | -0.11429 | 0.044861 | 0.28519 | -0.13565 | -0.19333 | 0.004578 | 0.045776 | -62.3245 | 60.0998 | 60.1135 | 62.2375 | 62.3199 | 122.4884 | 62.1689 | 60.1501
4663.1094 | 0.076294 | 0.37598 | -0.78186 | -0.23071 | 0.097198 | -0.28519 | -0.19012 | 60.1273 | -61.9675 | 0.032043 | -62.2604 | 60.1776 | 62.1735 | 62.1643 | 0.030518 | -0.1239 | 0.035248 | 0.27344 | -0.15381 | -0.17944 | 0.027466 | 0.10529 | -62.3474 | 60.0998 | 60.1181 | 62.2192 | 62.3337 | 122.493 | 62.1414 | 60.1639
4664.7812 | 0.1831 | 0.36529 | -0.76263 | -0.2243 | 0.098267 | -0.27023 | -0.19119 | 60.2005 | -61.908 | 0.045776 | -62.233 | 60.2005 | 62.2055 | 62.2055 | 0.16785 | -0.12176 | 0.037384 | 0.28732 | -0.13351 | -0.19012 | 0.091553 | 0.10986 | -62.3062 | 60.1181 | 60.141 | 62.2833 | 62.3886 | 122.4426 | 62.2101 | 60.1959
4666.4844 | 0.045776 | 0.40695 | -0.75943 | -0.24139 | 0.10254 | -0.24353 | -0.19226 | 60.1364 | -62.0361 | -0.068665 | -62.2833 | 60.2692 | 62.1964 | 62.1689 | 0.045776 | -0.10574 | 0.044861 | 0.28412 | -0.13031 | -0.18692 | -0.082397 | -0.086975 | -62.439 | 60.173 | 60.1364 | 62.2696 | 62.3383 | 122.493 | 62.178 | 60.1822
4668.1562 | 0.12207 | 0.40482 | -0.76797 | -0.27023 | 0.11643 | -0.23819 | -0.18799 | 60.1822 | -61.9629 | 0.073242 | -62.2238 | 60.2371 | 62.1643 | 62.1872 | 0.045776 | -0.1004 | 0.061951 | 0.28091 | -0.14954 | -0.19119 | 0.041199 | 0.091553 | -62.3795 | 60.1776 | 60.1685 | 62.2421 | 62.3474 | 122.5845 | 62.1231 | 60.1547
4669.8281 | 0.091553 | 0.40375 | -0.77011 | -0.27451 | 0.10681 | -0.24033 | -0.18158 | 60.173 | -61.9308 | 0.068665 | -62.233 | 60.2554 | 62.1506 | 62.1597 | 0.030518 | -0.09613 | 0.063019 | 0.28946 | -0.1474 | -0.19974 | 0.036621 | 0.10071 | -62.3886 | 60.2005 | 60.1364 | 62.2101 | 62.3291 | 122.5662 | 62.1277 | 60.1593
4671.5 | 0.19836 | 0.4187 | -0.77118 | -0.28091 | 0.10254 | -0.27664 | -0.1944 | 60.0952 | -61.9766 | 0.073242 | -62.2604 | 60.228 | 62.1872 | 62.1826 | 0.076294 | -0.12283 | 0.052338 | 0.27985 | -0.16876 | -0.18372 | 0.045776 | 0.13733 | -62.3978 | 60.1913 | 60.1593 | 62.2375 | 62.3474 | 122.5433 | 62.1185 | 60.1593
4673.1719 | 0.22888 | 0.41336 | -0.77866 | -0.27664 | 0.10681 | -0.26596 | -0.18478 | 60.1089 | -61.9904 | 0.041199 | -62.2513 | 60.2509 | 62.1826 | 62.1826 | 0.076294 | -0.10361 | 0.066223 | 0.28091 | -0.15595 | -0.1944 | 0.022888 | 0.10071 | -62.4207 | 60.2005 | 60.1639 | 62.2696 | 62.3886 | 122.5754 | 62.1231 | 60.1593
4674.8438 | 0.045776 | 0.37918 | -0.77331 | -0.26489 | 0.1207 | -0.27985 | -0.19653 | 60.1501 | -61.8439 | 0.16937 | -62.1872 | 60.1822 | 62.1506 | 62.1552 | 0.045776 | -0.13565 | 0.05127 | 0.27771 | -0.15915 | -0.19333 | 0.12817 | 0.24719 | -62.3016 | 60.1273 | 60.0861 | 62.2101 | 62.3154 | 122.5296 | 62.1048 | 60.1547
4676.5469 | 0.030518 | 0.42297 | -0.77438 | -0.23712 | 0.10147 | -0.24139 | -0.18265 | 60.1089 | -62.0041 | -0.032043 | -62.265 | 60.2646 | 62.2009 | 62.1964 | 0.045776 | -0.10147 | 0.053406 | 0.27985 | -0.14206 | -0.1976 | -0.086975 | -0.045776 | -62.4527 | 60.1776 | 60.1593 | 62.2192 | 62.3566 | 122.4289 | 62.1689 | 60.1868
4678.2344 | 0.19836 | 0.3685 | -0.75943 | -0.23605 | 0.10468 | -0.28091 | -0.19974 | 60.1501 | -61.908 | 0.050354 | -62.233 | 60.1593 | 62.2055 | 62.2101 | 0.16785 | -0.10788 | 0.040588 | 0.27985 | -0.13779 | -0.1741 | 0.054932 | 0.13275 | -62.2604 | 60.1089 | 60.1044 | 62.2696 | 62.3749 | 122.4472 | 62.1826 | 60.1547
4679.9375 | 0.045776 | 0.40268 | -0.75195 | -0.23712 | 0.10895 | -0.25314 | -0.18265 | 60.1135 | -62.0178 | -0.068665 | -62.2787 | 60.2554 | 62.2009 | 62.1918 | 0.030518 | -0.10254 | 0.040588 | 0.27771 | -0.13458 | -0.1976 | -0.07782 | -0.068665 | -62.4252 | 60.1685 | 60.1639 | 62.2467 | 62.352 | 122.493 | 62.1918 | 60.1593
4681.6406 | 0.030518 | 0.39841 | -0.78507 | -0.26062 | 0.12497 | -0.28732 | -0.18692 | 60.1547 | -61.8759 | 0.16022 | -62.1964 | 60.1776 | 62.1735 | 62.1918 | 0.045776 | -0.11963 | 0.055542 | 0.27557 | -0.16235 | -0.18799 | 0.10071 | 0.2243 | -62.3199 | 60.1547 | 60.1089 | 62.2009 | 62.3062 | 122.525 | 62.1414 | 60.1639
4683.3125 | 0.076294 | 0.35996 | -0.76157 | -0.24139 | 0.1004 | -0.2948 | -0.20508 | 60.1089 | -61.9492 | 0.059509 | -62.2284 | 60.2005 | 62.1506 | 62.1735 | 0.030518 | -0.1239 | 0.041656 | 0.27878 | -0.15488 | -0.18906 | 0.054932 | 0.16022 | -62.3291 | 60.0998 | 60.0861 | 62.2192 | 62.3337 | 122.5662 | 62.178 | 60.1456
4684.9844 | 0.015259 | 0.37811 | -0.76904 | -0.23498 | 0.11643 | -0.25742 | -0.18692 | 60.1501 | -61.9812 | -0.050354 | -62.265 | 60.228 | 62.1918 | 62.1918 | 0.030518 | -0.10361 | 0.043793 | 0.28091 | -0.14099 | -0.18906 | -0.018311 | 0 | -62.352 | 60.1227 | 60.1044 | 62.233 | 62.3657 | 122.4838 | 62.1964 | 60.1501
4686.6562 | 0.045776 | 0.3952 | -0.75943 | -0.23819 | 0.11963 | -0.24994 | -0.17731 | 60.1227 | -61.9995 | -0.050354 | -62.265 | 60.2325 | 62.1964 | 62.178 | 0.061035 | -0.09613 | 0.03952 | 0.27023 | -0.1442 | -0.1976 | -0.013733 | -0.022888 | -62.3657 | 60.1181 | 60.0998 | 62.2375 | 62.3886 | 122.4838 | 62.1964 | 60.1593
4688.3438 | 0.12207 | 0.36957 | -0.77652 | -0.2681 | 0.11002 | -0.29159 | -0.20187 | 60.1089 | -61.9675 | 0.032043 | -62.2467 | 60.2051 | 62.1918 | 62.1689 | 0.045776 | -0.12817 | 0.048065 | 0.27451 | -0.17197 | -0.17197 | 0.027466 | 0.11902 | -62.352 | 60.1181 | 60.1364 | 62.2101 | 62.3474 | 122.4884 | 62.1597 | 60.1593
4690.0156 | 0.091553 | 0.42191 | -0.7637 | -0.24887 | 0.10361 | -0.24246 | -0.18478 | 60.2005 | -61.9675 | 0.022888 | -62.2375 | 60.228 | 62.1826 | 62.1918 | 0.030518 | -0.098267 | 0.03418 | 0.28305 | -0.13138 | -0.19974 | 0 | 0.009155 | -62.4115 | 60.1501 | 60.173 | 62.2101 | 62.3291 | 122.4655 | 62.1735 | 60.2097
4691.7031 | 0.15259 | 0.41122 | -0.7637 | -0.26916 | 0.11322 | -0.25421 | -0.18158 | 60.1776 | -61.9446 | 0.073242 | -62.2192 | 60.2646 | 62.178 | 62.1552 | 0.061035 | -0.10574 | 0.063019 | 0.28519 | -0.1442 | -0.18051 | 0.045776 | 0.10071 | -62.384 | 60.1639 | 60.1456 | 62.233 | 62.3428 | 122.5754 | 62.1094 | 60.1547
4693.4375 | 0.030518 | 0.36209 | -0.76157 | -0.23498 | 0.11856 | -0.25635 | -0.19226 | 60.1547 | -61.9675 | -0.018311 | -62.2559 | 60.2051 | 62.1918 | 62.178 | 0.030518 | -0.11963 | 0.03952 | 0.28305 | -0.1474 | -0.19333 | -0.009155 | 0.027466 | -62.3474 | 60.0861 | 60.0998 | 62.2192 | 62.3428 | 122.5113 | 62.1872 | 60.1685
4695.1094 | 0.061035 | 0.41016 | -0.75195 | -0.23819 | 0.10681 | -0.2478 | -0.18372 | 60.0952 | -62.0636 | -0.068665 | -62.2971 | 60.2417 | 62.2055 | 62.1826 | 0.045776 | -0.10681 | 0.048065 | 0.28519 | -0.13565 | -0.18478 | -0.082397 | -0.10071 | -62.4527 | 60.1959 | 60.1868 | 62.2467 | 62.3611 | 122.4609 | 62.1918 | 60.1913
4696.7812 | 0.1831 | 0.42511 | -0.77866 | -0.25528 | 0.12924 | -0.25955 | -0.19012 | 60.173 | -61.9766 | 0.054932 | -62.2238 | 60.2371 | 62.2055 | 62.1826 | 0.030518 | -0.11108 | 0.060883 | 0.2713 | -0.1442 | -0.1976 | 0.027466 | 0.091553 | -62.3795 | 60.1868 | 60.173 | 62.2147 | 62.3337 | 122.5708 | 62.1323 | 60.1593
4698.4844 | 0.030518 | 0.39948 | -0.74768 | -0.22964 | 0.10681 | -0.27023 | -0.19119 | 60.1135 | -62.0087 | -0.059509 | -62.2833 | 60.26 | 62.1918 | 62.1918 | 0.061035 | -0.10788 | 0.048065 | 0.27985 | -0.13245 | -0.18799 | -0.068665 | -0.064087 | -62.4115 | 60.1547 | 60.141 | 62.233 | 62.3749 | 122.493 | 62.1597 | 60.1547
4700.1562 | 0.076294 | 0.4155 | -0.76157 | -0.26276 | 0.12497 | -0.24246 | -0.18906 | 60.1639 | -61.9675 | 0.045776 | -62.233 | 60.2325 | 62.1735 | 62.1964 | 0.030518 | -0.10361 | 0.052338 | 0.29053 | -0.1506 | -0.19653 | -0.032043 | 0.027466 | -62.4161 | 60.1776 | 60.1639 | 62.233 | 62.3566 | 122.4609 | 62.178 | 60.1685
4701.8281 | 0.10681 | 0.37384 | -0.77225 | -0.24674 | 0.099335 | -0.30548 | -0.19333 | 60.1181 | -61.972 | 0.027466 | -62.2513 | 60.1639 | 62.1872 | 62.146 | 0.030518 | -0.13992 | 0.035248 | 0.27878 | -0.15274 | -0.18372 | 0 | 0.10071 | -62.3337 | 60.1273 | 60.1318 | 62.2513 | 62.4161 | 122.4655 | 62.2055 | 60.1868
4703.5156 | 0.061035 | 0.39093 | -0.77225 | -0.26276 | 0.1207 | -0.29053 | -0.20081 | 60.1593 | -61.8851 | 0.15564 | -62.2009 | 60.2142 | 62.1506 | 62.1643 | 0.030518 | -0.1207 | 0.063019 | 0.27237 | -0.16235 | -0.19333 | 0.09613 | 0.2243 | -62.3245 | 60.1547 | 60.1364 | 62.2284 | 62.3337 | 122.525 | 62.1368 | 60.1913
4705.1875 | 0.12207 | 0.36102 | -0.77011 | -0.25314 | 0.11643 | -0.28625 | -0.19974 | 60.1181 | -61.9492 | 0.022888 | -62.2421 | 60.1776 | 62.1872 | 62.178 | 0.061035 | -0.13031 | 0.045929 | 0.28305 | -0.15274 | -0.19546 | 0.013733 | 0.07782 | -62.3657 | 60.1089 | 60.0906 | 62.2284 | 62.3657 | 122.4564 | 62.2055 | 60.1913
4706.8906 | 0.045776 | 0.40161 | -0.75836 | -0.23178 | 0.11322 | -0.24353 | -0.19226 | 60.1273 | -62.027 | -0.086975 | -62.2833 | 60.228 | 62.2101 | 62.2101 | 0.045776 | -0.10254 | 0.05127 | 0.28732 | -0.13565 | -0.19653 | -0.068665 | -0.082397 | -62.4252 | 60.1547 | 60.1456 | 62.2421 | 62.3795 | 122.4838 | 62.1872 | 60.1639
4708.5781 | 0.091553 | 0.37064 | -0.76477 | -0.24353 | 0.11322 | -0.28625 | -0.20294 | 60.1044 | -61.9675 | 0.041199 | -62.2559 | 60.2051 | 62.1964 | 62.1597 | 0.045776 | -0.12497 | 0.038452 | 0.26916 | -0.15808 | -0.18692 | 0.032043 | 0.14191 | -62.3245 | 60.0998 | 60.1227 | 62.2147 | 62.3474 | 122.5388 | 62.1689 | 60.1456
4710.25 | 0.16785 | 0.41443 | -0.7605 | -0.27023 | 0.11643 | -0.25101 | -0.19333 | 60.1456 | -62.0224 | 0.036621 | -62.2467 | 60.2509 | 62.1735 | 62.178 | 0.061035 | -0.10147 | 0.050201 | 0.27771 | -0.15381 | -0.20401 | 0.027466 | 0.10986 | -62.4069 | 60.1959 | 60.1822 | 62.2192 | 62.3337 | 122.58 | 62.1231 | 60.1868
4711.9375 | 0.061035 | 0.40802 | -0.75943 | -0.23819 | 0.11749 | -0.24139 | -0.18478 | 60.1181 | -62.0499 | -0.068665 | -62.2742 | 60.2737 | 62.1964 | 62.1872 | 0.045776 | -0.10895 | 0.040588 | 0.28519 | -0.13565 | -0.19333 | -0.086975 | -0.082397 | -62.4481 | 60.1868 | 60.1822 | 62.2284 | 62.3611 | 122.4472 | 62.1643 | 60.173
4713.6094 | 0.061035 | 0.41657 | -0.75623 | -0.25314 | 0.10681 | -0.24567 | -0.17731 | 60.173 | -61.9858 | 0.004578 | -62.2513 | 60.2554 | 62.2055 | 62.1918 | 0.061035 | -0.10788 | 0.05661 | 0.27985 | -0.13779 | -0.20508 | -0.054932 | -0.013733 | -62.4481 | 60.1501 | 60.1593 | 62.2375 | 62.352 | 122.4472 | 62.1552 | 60.2005
4715.3125 | 0.030518 | 0.38559 | -0.74234 | -0.25101 | 0.10788 | -0.26382 | -0.19546 | 60.1364 | -61.9583 | -0.018311 | -62.2513 | 60.2005 | 62.178 | 62.1597 | 0.045776 | -0.12176 | 0.03952 | 0.27985 | -0.14313 | -0.18799 | 0.036621 | 0.059509 | -62.3108 | 60.1685 | 60.141 | 62.2833 | 62.3703 | 122.4976 | 62.2055 | 60.1456
4716.9844 | 0.10681 | 0.41336 | -0.76584 | -0.24674 | 0.11963 | -0.25635 | -0.17838 | 60.1959 | -61.9446 | 0.045776 | -62.2284 | 60.2371 | 62.1918 | 62.1643 | 0.045776 | -0.097198 | 0.046997 | 0.27771 | -0.13138 | -0.18372 | -0.022888 | 0.032043 | -62.4115 | 60.1456 | 60.1685 | 62.2238 | 62.3383 | 122.4701 | 62.178 | 60.2051
4718.6719 | 0.045776 | 0.39734 | -0.784 | -0.25207 | 0.11856 | -0.29587 | -0.20081 | 60.1868 | -61.8759 | 0.15106 | -62.1918 | 60.1685 | 62.1735 | 62.1414 | 0.045776 | -0.14313 | 0.052338 | 0.27451 | -0.16022 | -0.19119 | 0.14191 | 0.27924 | -62.2925 | 60.0998 | 60.1273 | 62.2284 | 62.3199 | 122.5342 | 62.1323 | 60.1776
4720.375 | 0.061035 | 0.40375 | -0.76797 | -0.24033 | 0.11429 | -0.25421 | -0.19012 | 60.1227 | -62.0407 | -0.086975 | -62.2787 | 60.2554 | 62.2147 | 62.178 | 0.061035 | -0.10788 | 0.053406 | 0.28519 | -0.13031 | -0.19333 | -0.086975 | -0.07782 | -62.439 | 60.1639 | 60.1547 | 62.2604 | 62.3566 | 122.4701 | 62.1872 | 60.1776
4722.0469 | 0.045776 | 0.39841 | -0.78507 | -0.27344 | 0.11322 | -0.27557 | -0.1976 | 60.1547 | -61.908 | 0.11902 | -62.2147 | 60.2142 | 62.2009 | 62.1414 | 0.030518 | -0.11108 | 0.061951 | 0.27451 | -0.16769 | -0.19012 | 0.068665 | 0.16937 | -62.3749 | 60.1913 | 60.1593 | 62.2375 | 62.3383 | 122.525 | 62.1323 | 60.1776
4723.7344 | 0.045776 | 0.4187 | -0.76157 | -0.24246 | 0.10788 | -0.23926 | -0.18585 | 60.1593 | -61.9675 | 0.004578 | -62.2421 | 60.2371 | 62.1918 | 62.178 | 0.045776 | -0.1004 | 0.049133 | 0.29159 | -0.13245 | -0.19226 | -0.027466 | 0.004578 | -62.4344 | 60.1776 | 60.1685 | 62.2192 | 62.3657 | 122.4426 | 62.1735 | 60.2097
4725.4531 | 0.13733 | 0.36102 | -0.77438 | -0.2446 | 0.11002 | -0.298 | -0.18051 | 60.1089 | -61.9263 | 0.022888 | -62.265 | 60.1639 | 62.1872 | 62.1872 | 0.076294 | -0.12497 | 0.045929 | 0.27344 | -0.14526 | -0.17731 | 0.045776 | 0.09613 | -62.3199 | 60.1181 | 60.141 | 62.2559 | 62.3886 | 122.4518 | 62.1826 | 60.1639
4727.125 | 0.12207 | 0.37918 | -0.76797 | -0.23819 | 0.10468 | -0.28839 | -0.20401 | 60.1044 | -61.9675 | 0.032043 | -62.233 | 60.1776 | 62.178 | 62.1735 | 0.045776 | -0.13031 | 0.045929 | 0.27344 | -0.15915 | -0.18585 | 0.009155 | 0.09613 | -62.352 | 60.1318 | 60.1044 | 62.2238 | 62.3749 | 122.4838 | 62.178 | 60.173
4728.7969 | 0.030518 | 0.36743 | -0.76477 | -0.23392 | 0.10788 | -0.26276 | -0.18906 | 60.2051 | -61.9263 | 0.013733 | -62.2055 | 60.2005 | 62.1918 | 62.1643 | 0.030518 | -0.11536 | 0.042725 | 0.26596 | -0.12924 | -0.18906 | 0.054932 | 0.068665 | -62.3062 | 60.1547 | 60.1639 | 62.2787 | 62.3795 | 122.4976 | 62.1552 | 60.1685
4730.5 | 0.15259 | 0.38238 | -0.77331 | -0.2478 | 0.1004 | -0.26916 | -0.1976 | 60.1685 | -61.9537 | 0.054932 | -62.2101 | 60.2051 | 62.2238 | 62.1918 | 0.16785 | -0.11215 | 0.033112 | 0.28519 | -0.13779 | -0.18372 | 0.059509 | 0.10529 | -62.3383 | 60.1456 | 60.1547 | 62.2375 | 62.3749 | 122.4426 | 62.2055 | 60.1685
4732.1719 | 0.030518 | 0.41229 | -0.77652 | -0.25742 | 0.095062 | -0.23712 | -0.1944 | 60.1456 | -62.0544 | -0.054932 | -62.2696 | 60.2463 | 62.2147 | 62.1826 | 0.061035 | -0.097198 | 0.041656 | 0.28412 | -0.13565 | -0.19974 | -0.09613 | -0.09613 | -62.471 | 60.173 | 60.1868 | 62.265 | 62.3657 | 122.438 | 62.1597 | 60.2188
4733.8594 | 0.030518 | 0.36423 | -0.76691 | -0.24887 | 0.11322 | -0.28839 | -0.20187 | 60.1685 | -61.9308 | 0.07782 | -62.2147 | 60.2097 | 62.2009 | 62.1552 | 0.045776 | -0.1239 | 0.03418 | 0.27664 | -0.15915 | -0.18906 | 0.11902 | 0.21973 | -62.2879 | 60.1181 | 60.1364 | 62.2055 | 62.3428 | 122.5662 | 62.1368 | 60.1593
4735.5156 | 0.1831 | 0.3717 | -0.77225 | -0.23178 | 0.10895 | -0.27557 | -0.19653 | 60.2097 | -61.9034 | 0.054932 | -62.2192 | 60.1593 | 62.178 | 62.1597 | 0.16785 | -0.10895 | 0.03952 | 0.29159 | -0.13458 | -0.18799 | 0.059509 | 0.11902 | -62.2925 | 60.1501 | 60.1364 | 62.2696 | 62.3886 | 122.438 | 62.2192 | 60.2005
4737.1875 | 0.030518 | 0.39841 | -0.78186 | -0.24887 | 0.11322 | -0.27771 | -0.1944 | 60.2142 | -61.9034 | 0.15106 | -62.178 | 60.2051 | 62.1552 | 62.1735 | 0.061035 | -0.12283 | 0.036316 | 0.26489 | -0.15488 | -0.20721 | 0.12817 | 0.24719 | -62.3154 | 60.1364 | 60.1456 | 62.2101 | 62.352 | 122.5388 | 62.1231 | 60.1593
4738.8906 | 0.076294 | 0.42084 | -0.77011 | -0.2478 | 0.10895 | -0.24139 | -0.18051 | 60.2417 | -61.9492 | 0.050354 | -62.2375 | 60.2463 | 62.2009 | 62.1964 | 0.061035 | -0.10681 | 0.046997 | 0.27878 | -0.13779 | -0.20187 | 0.004578 | 0.032043 | -62.4023 | 60.173 | 60.1639 | 62.2467 | 62.3474 | 122.5021 | 62.1506 | 60.2005
4740.5781 | 0.045776 | 0.41977 | -0.78079 | -0.27557 | 0.10361 | -0.26916 | -0.1976 | 60.1456 | -61.9629 | 0.091553 | -62.265 | 60.26 | 62.178 | 62.1964 | 0.045776 | -0.11643 | 0.059814 | 0.27664 | -0.16769 | -0.19867 | 0.041199 | 0.13275 | -62.4023 | 60.1776 | 60.1547 | 62.2604 | 62.3566 | 122.5388 | 62.1323 | 60.1959
4742.2656 | 0.091553 | 0.39948 | -0.77652 | -0.24567 | 0.1004 | -0.24139 | -0.1976 | 60.2051 | -61.9446 | 0.041199 | -62.233 | 60.2325 | 62.1735 | 62.1872 | 0.061035 | -0.11215 | 0.053406 | 0.29266 | -0.1442 | -0.20294 | 0.009155 | 0.032043 | -62.4069 | 60.1639 | 60.1639 | 62.2421 | 62.3611 | 122.4792 | 62.1552 | 60.2005
4743.9844 | 0.076294 | 0.37277 | -0.78293 | -0.2681 | 0.11002 | -0.29159 | -0.19119 | 60.1227 | -61.9354 | 0.086975 | -62.2284 | 60.1776 | 62.1735 | 62.1506 | 0.061035 | -0.1442 | 0.049133 | 0.2681 | -0.16663 | -0.18799 | 0.09613 | 0.20142 | -62.3062 | 60.1135 | 60.0952 | 62.1964 | 62.3657 | 122.5708 | 62.1368 | 60.1456
4745.6875 | 0.045776 | 0.36529 | -0.77225 | -0.27344 | 0.10147 | -0.27878 | -0.20081 | 60.2097 | -61.8301 | 0.15564 | -62.1964 | 60.1959 | 62.1872 | 62.146 | 0.045776 | -0.13138 | 0.048065 | 0.27451 | -0.15915 | -0.1976 | 0.15106 | 0.26093 | -62.3016 | 60.0998 | 60.0906 | 62.2055 | 62.3383 | 122.5616 | 62.1414 | 60.1273
4747.4062 | 0.13733 | 0.36636 | -0.7637 | -0.24246 | 0.10681 | -0.27451 | -0.20187 | 60.1364 | -61.9446 | 0.022888 | -62.2559 | 60.2005 | 62.1735 | 62.1689 | 0.045776 | -0.1207 | 0.038452 | 0.27878 | -0.15595 | -0.18799 | 0.022888 | 0.07782 | -62.3611 | 60.1135 | 60.1089 | 62.233 | 62.3886 | 122.4564 | 62.1826 | 60.1501
4749.0781 | 0.19836 | 0.37064 | -0.76797 | -0.21683 | 0.11429 | -0.25742 | -0.18372 | 60.1913 | -61.9034 | 0.050354 | -62.2284 | 60.1593 | 62.1872 | 62.1643 | 0.15259 | -0.10468 | 0.052338 | 0.28625 | -0.12497 | -0.19119 | 0.073242 | 0.11902 | -62.2833 | 60.1547 | 60.1227 | 62.265 | 62.3795 | 122.438 | 62.1735 | 60.1822
4750.7656 | 0.19836 | 0.36957 | -0.75302 | -0.23712 | 0.11643 | -0.24246 | -0.18158 | 60.2005 | -61.9125 | 0.027466 | -62.2055 | 60.1822 | 62.1826 | 62.1597 | 0.061035 | -0.10147 | 0.045929 | 0.28412 | -0.11856 | -0.18372 | 0.068665 | 0.10986 | -62.2833 | 60.1456 | 60.1364 | 62.2742 | 62.3703 | 122.4838 | 62.1964 | 60.1685
4752.4844 | 0.045776 | 0.38879 | -0.77866 | -0.2713 | 0.099335 | -0.26489 | -0.18799 | 60.1822 | -61.8942 | 0.15106 | -62.2055 | 60.2097 | 62.1643 | 62.1735 | 0.061035 | -0.11963 | 0.044861 | 0.26703 | -0.15701 | -0.18692 | 0.09613 | 0.21515 | -62.3611 | 60.173 | 60.141 | 62.2467 | 62.3291 | 122.5342 | 62.1323 | 60.1868
4754.1719 | 0.030518 | 0.37918 | -0.77652 | -0.24033 | 0.11429 | -0.27451 | -0.19012 | 60.1776 | -61.8896 | 0.11902 | -62.2147 | 60.2234 | 62.1597 | 62.1552 | 0.030518 | -0.13031 | 0.043793 | 0.27557 | -0.15381 | -0.1944 | 0.14191 | 0.23804 | -62.2787 | 60.1181 | 60.0952 | 62.2284 | 62.352 | 122.5891 | 62.1414 | 60.1547
4755.8438 | 0.061035 | 0.38666 | -0.76904 | -0.23498 | 0.10681 | -0.24994 | -0.18478 | 60.1913 | -61.9995 | -0.041199 | -62.265 | 60.2371 | 62.2055 | 62.1826 | 0.030518 | -0.10468 | 0.036316 | 0.27344 | -0.13351 | -0.20401 | -0.004578 | 0.009155 | -62.3703 | 60.1501 | 60.0998 | 62.2055 | 62.3749 | 122.4976 | 62.1735 | 60.173
4757.5156 | 0.061035 | 0.41657 | -0.76584 | -0.2446 | 0.11108 | -0.23071 | -0.17303 | 60.173 | -61.9995 | -0.013733 | -62.2696 | 60.2463 | 62.1826 | 62.2055 | 0.045776 | -0.098267 | 0.046997 | 0.27771 | -0.12924 | -0.19974 | -0.059509 | -0.032043 | -62.4481 | 60.173 | 60.173 | 62.2375 | 62.3795 | 122.4655 | 62.1643 | 60.2142
4759.1875 | 0.16785 | 0.36636 | -0.77011 | -0.25101 | 0.095062 | -0.27023 | -0.1944 | 60.2005 | -61.908 | 0.041199 | -62.2375 | 60.173 | 62.1872 | 62.1689 | 0.045776 | -0.11536 | 0.057678 | 0.30441 | -0.14633 | -0.17303 | 0.068665 | 0.11902 | -62.3016 | 60.1456 | 60.1227 | 62.3016 | 62.3886 | 122.4426 | 62.1918 | 60.1822
4760.8594 | 0.030518 | 0.36102 | -0.784 | -0.26169 | 0.11215 | -0.27878 | -0.1944 | 60.173 | -61.8988 | 0.11444 | -62.2101 | 60.1959 | 62.1689 | 62.1643 | 0.030518 | -0.12604 | 0.03952 | 0.27985 | -0.16769 | -0.19333 | 0.14191 | 0.22888 | -62.2833 | 60.1227 | 60.1227 | 62.233 | 62.3428 | 122.5845 | 62.1552 | 60.1364
4762.5312 | 0.16785 | 0.35461 | -0.76263 | -0.24567 | 0.11002 | -0.27344 | -0.20187 | 60.2142 | -61.9125 | 0.045776 | -62.2284 | 60.1776 | 62.178 | 62.1597 | 0.061035 | -0.11963 | 0.03952 | 0.27344 | -0.13886 | -0.1709 | 0.068665 | 0.1236 | -62.3154 | 60.1273 | 60.1181 | 62.265 | 62.4207 | 122.4426 | 62.1735 | 60.1822
4764.2344 | 0.10681 | 0.37277 | -0.77011 | -0.25101 | 0.10147 | -0.28091 | -0.19333 | 60.1364 | -61.9949 | 0.027466 | -62.2604 | 60.2005 | 62.1918 | 62.1826 | 0.015259 | -0.13031 | 0.041656 | 0.27878 | -0.15167 | -0.19119 | 0.041199 | 0.11444 | -62.3611 | 60.1501 | 60.1089 | 62.233 | 62.3474 | 122.4884 | 62.1689 | 60.1593
4765.9062 | 0.22888 | 0.36636 | -0.75302 | -0.22964 | 0.11322 | -0.2446 | -0.19974 | 60.2142 | -61.9217 | 0.045776 | -62.2238 | 60.1593 | 62.2467 | 62.2192 | 0.21362 | -0.10788 | 0.041656 | 0.28839 | -0.1207 | -0.17624 | 0.07782 | 0.10071 | -62.2925 | 60.1593 | 60.1181 | 62.2879 | 62.384 | 122.4518 | 62.2009 | 60.1868
4767.5781 | 0.045776 | 0.37064 | -0.76904 | -0.25421 | 0.10468 | -0.28305 | -0.19226 | 60.1822 | -61.9034 | 0.11444 | -62.2101 | 60.2142 | 62.178 | 62.1872 | 0.045776 | -0.13351 | 0.043793 | 0.27344 | -0.15915 | -0.19119 | 0.1236 | 0.22888 | -62.2925 | 60.1318 | 60.0815 | 62.2055 | 62.3383 | 122.5891 | 62.1231 | 60.1776
4769.25 | 0.19836 | 0.36636 | -0.77545 | -0.2478 | 0.10681 | -0.25742 | -0.20721 | 60.1593 | -61.94 | 0.032043 | -62.2696 | 60.1685 | 62.1918 | 62.2009 | 0.030518 | -0.12817 | 0.040588 | 0.26382 | -0.15595 | -0.19653 | 0.045776 | 0.082397 | -62.3611 | 60.1227 | 60.0769 | 62.2375 | 62.3657 | 122.4518 | 62.1918 | 60.1685
4770.9219 | 0.061035 | 0.36957 | -0.77759 | -0.24567 | 0.10254 | -0.27237 | -0.19119 | 60.1685 | -61.9263 | 0.086975 | -62.2284 | 60.1959 | 62.1689 | 62.1597 | 0.076294 | -0.12817 | 0.038452 | 0.2681 | -0.15488 | -0.19226 | 0.10986 | 0.19684 | -62.3154 | 60.1547 | 60.0998 | 62.2238 | 62.3383 | 122.5754 | 62.1002 | 60.1456
4772.6094 | 0.21362 | 0.42404 | -0.7872 | -0.26169 | 0.10895 | -0.24887 | -0.19546 | 60.1501 | -61.9675 | 0.054932 | -62.265 | 60.26 | 62.2055 | 62.2147 | 0.076294 | -0.10895 | 0.048065 | 0.27771 | -0.1506 | -0.20828 | 0.059509 | 0.10986 | -62.4207 | 60.2051 | 60.1685 | 62.3108 | 62.3978 | 122.5433 | 62.1323 | 60.173
4774.3594 | 0.030518 | 0.37491 | -0.77759 | -0.24567 | 0.099335 | -0.27664 | -0.19653 | 60.1959 | -61.8393 | 0.15106 | -62.1964 | 60.2005 | 62.1735 | 62.1597 | 0.045776 | -0.13031 | 0.03952 | 0.2713 | -0.15701 | -0.19546 | 0.15564 | 0.25177 | -62.2742 | 60.0998 | 60.0769 | 62.2284 | 62.3611 | 122.5754 | 62.1231 | 60.141
4776.0469 | 0.22888 | 0.36423 | -0.75729 | -0.21149 | 0.10147 | -0.25528 | -0.18051 | 60.2005 | -61.8942 | 0.059509 | -62.2101 | 60.1547 | 62.1689 | 62.1643 | 0.030518 | -0.11643 | 0.048065 | 0.298 | -0.13458 | -0.18478 | 0.073242 | 0.11902 | -62.2879 | 60.1456 | 60.1181 | 62.2604 | 62.3795 | 122.4426 | 62.1826 | 60.2005
4777.8438 | 0.061035 | 0.41657 | -0.76477 | -0.23926 | 0.10788 | -0.22537 | -0.18692 | 60.141 | -62.027 | -0.041199 | -62.2696 | 60.2692 | 62.2055 | 62.1735 | 0.061035 | -0.09613 | 0.043793 | 0.28946 | -0.12497 | -0.1944 | -0.059509 | -0.059509 | -62.4619 | 60.1822 | 60.1776 | 62.2604 | 62.3474 | 122.4518 | 62.2009 | 60.1913
4779.6094 | 0.10681 | 0.37598 | -0.10895 | -0.24033 | 0.11108 | -0.28625 | -0.18585 | 60.1181 | -61.9583 | 0.027466 | -62.2604 | 60.1868 | 62.1826 | 62.1826 | 0.061035 | -0.12176 | 0.036316 | 0.27557 | -0.1506 | -0.18906 | 0.041199 | 0.12817 | -62.3291 | 60.1227 | 60.1089 | 62.233 | 62.3383 | 122.4976 | 62.1506 | 60.1776
4781.3906 | 0.22888 | 0.36636 | -0.75302 | -0.2211 | 0.11963 | -0.25742 | -0.18265 | 60.2051 | -61.8896 | 0.045776 | -62.2238 | 60.1776 | 62.1872 | 62.1597 | 0.1831 | -0.10895 | 0.048065 | 0.28198 | -0.12711 | -0.18906 | 0.073242 | 0.11902 | -62.2833 | 60.1456 | 60.1227 | 62.265 | 62.3886 | 122.4609 | 62.1872 | 60.2051
4783.1719 | 0.21362 | 0.40909 | -0.78293 | -0.2478 | 0.10574 | -0.25207 | -0.19226 | 60.1547 | -61.9995 | 0.041199 | -62.2604 | 60.2554 | 62.1735 | 62.1826 | 0.061035 | -0.1207 | 0.046997 | 0.27664 | -0.13351 | -0.19653 | 0.027466 | 0.10071 | -62.4207 | 60.2097 | 60.1639 | 62.2467 | 62.352 | 122.5891 | 62.1323 | 60.1822
4784.9375 | 0.1831 | 0.42297 | -0.76584 | -0.26382 | 0.12497 | -0.25742 | -0.19119 | 60.1685 | -61.9675 | 0.068665 | -62.2192 | 60.2829 | 62.2009 | 62.1643 | 0.061035 | -0.098267 | 0.046997 | 0.27344 | -0.14526 | -0.19012 | 0.041199 | 0.10529 | -62.384 | 60.1685 | 60.1822 | 62.2467 | 62.3566 | 122.5891 | 62.1094 | 60.1639
4786.9375 | 0.030518 | 0.42297 | -0.7637 | -0.2446 | 0.11429 | -0.24674 | -0.18692 | 60.1044 | -62.027 | -0.073242 | -62.2696 | 60.2509 | 62.2192 | 62.1872 | 0.030518 | -0.099335 | 0.048065 | 0.28519 | -0.13138 | -0.19974 | -0.07782 | -0.068665 | -62.4756 | 60.1593 | 60.1456 | 62.2604 | 62.3657 | 122.4518 | 62.1735 | 60.2005
4788.7031 | 0.21362 | 0.36423 | -0.76157 | -0.24246 | 0.097198 | -0.27771 | -0.18692 | 60.1685 | -61.9034 | 0.054932 | -62.2238 | 60.1593 | 62.1918 | 62.1735 | 0.045776 | -0.11856 | 0.045929 | 0.26916 | -0.14633 | -0.18692 | 0.07782 | 0.12817 | -62.2879 | 60.1547 | 60.1181 | 62.2925 | 62.3978 | 122.4426 | 62.2147 | 60.1868
4790.6719 | 0.13733 | 0.4155 | -0.77011 | -0.24674 | 0.091858 | -0.26382 | -0.17731 | 60.1639 | -61.9492 | 0.054932 | -62.2238 | 60.2692 | 62.1735 | 62.1735 | 0.076294 | -0.10681 | 0.03952 | 0.27985 | -0.13031 | -0.20935 | 0.032043 | 0.10071 | -62.3886 | 60.1776 | 60.1639 | 62.2513 | 62.352 | 122.5937 | 62.1277 | 60.1868
4793.0781 | 0.12207 | 0.41016 | -0.77011 | -0.25314 | 0.10788 | -0.24353 | -0.18265 | 60.1868 | -61.9492 | 0.068665 | -62.233 | 60.2234 | 62.1964 | 62.1918 | 0.030518 | -0.11002 | 0.042725 | 0.26916 | -0.13245 | -0.1944 | 0.032043 | 0.10529 | -62.384 | 60.1547 | 60.1685 | 62.2375 | 62.3383 | 122.5708 | 62.1277 | 60.173
4796.7656 | 0.061035 | 0.36743 | -0.78186 | -0.25314 | 0.10361 | -0.30121 | -0.19867 | 60.1364 | -61.9308 | 0.07782 | -62.2238 | 60.2142 | 62.1826 | 62.1872 | 0.061035 | -0.12604 | 0.040588 | 0.2681 | -0.16235 | -0.19653 | 0.10071 | 0.22888 | -62.2787 | 60.1089 | 60.1501 | 62.2284 | 62.3474 | 122.5754 | 62.1277 | 60.1639
4798.5469 | 0.10681 | 0.41016 | -0.77225 | -0.25421 | 0.11108 | -0.25101 | -0.19012 | 60.2097 | -61.9629 | 0.050354 | -62.2284 | 60.26 | 62.1918 | 62.1552 | 0.076294 | -0.10254 | 0.044861 | 0.27451 | -0.13031 | -0.20187 | 0.018311 | 0.091553 | -62.3795 | 60.2142 | 60.173 | 62.233 | 62.3611 | 122.5891 | 62.0911 | 60.1685
4801.1719 | 0.091553 | 0.40482 | -0.76584 | -0.25528 | 0.10895 | -0.2478 | -0.19012 | 60.2097 | -61.9354 | 0.036621 | -62.2284 | 60.26 | 62.1918 | 62.1826 | 0.015259 | -0.097198 | 0.046997 | 0.27985 | -0.13672 | -0.19867 | -0.009155 | 0.045776 | -62.4023 | 60.1776 | 60.1639 | 62.2513 | 62.3474 | 122.5021 | 62.1506 | 60.1822
4803.0156 | 0.12207 | 0.36209 | -0.77759 | -0.25421 | 0.11108 | -0.28198 | -0.20187 | 60.1273 | -61.9492 | 0.032043 | -62.2559 | 60.1776 | 62.1597 | 62.1597 | 0.045776 | -0.12711 | 0.048065 | 0.27344 | -0.16022 | -0.17944 | 0.013733 | 0.09613 | -62.3428 | 60.1044 | 60.1135 | 62.2467 | 62.3932 | 122.4747 | 62.1918 | 60.173
4804.8438 | 0.1831 | 0.42831 | -0.77972 | -0.27985 | 0.10574 | -0.2681 | -0.20401 | 60.1181 | -61.9995 | 0.045776 | -62.2604 | 60.2737 | 62.1918 | 62.1689 | 0.061035 | -0.11002 | 0.060883 | 0.28305 | -0.16022 | -0.19119 | 0.032043 | 0.11444 | -62.4023 | 60.2097 | 60.1868 | 62.2513 | 62.3886 | 122.5616 | 62.1552 | 60.1593
4806.7188 | 0.15259 | 0.34927 | -0.75409 | -0.24033 | 0.11215 | -0.26062 | -0.17838 | 60.1959 | -61.9308 | 0.041199 | -62.2101 | 60.1822 | 62.2055 | 62.1689 | 0.045776 | -0.11429 | 0.040588 | 0.28305 | -0.1474 | -0.19974 | 0.018311 | 0.11444 | -62.2879 | 60.1547 | 60.1501 | 62.3108 | 62.4069 | 122.4792 | 62.1826 | 60.173
4808.5 | 0.045776 | 0.40695 | -0.78079 | -0.24994 | 0.10681 | -0.24353 | -0.18265 | 60.1364 | -62.0132 | -0.036621 | -62.2696 | 60.2646 | 62.2055 | 62.1918 | 0.061035 | -0.1004 | 0.040588 | 0.28198 | -0.12497 | -0.18692 | -0.07782 | -0.059509 | -62.4481 | 60.173 | 60.1685 | 62.265 | 62.384 | 122.4518 | 62.1597 | 60.1822
4810.1719 | 0.030518 | 0.37384 | -0.77438 | -0.24033 | 0.10468 | -0.28519 | -0.20187 | 60.1456 | -61.9125 | 0.086975 | -62.2284 | 60.1776 | 62.1735 | 62.1826 | 0.045776 | -0.12497 | 0.03952 | 0.27023 | -0.16235 | -0.18265 | 0.11444 | 0.2243 | -62.3016 | 60.1227 | 60.1273 | 62.2192 | 62.3657 | 122.5616 | 62.1323 | 60.1364
4811.9531 | 0.1831 | 0.35461 | -0.75729 | -0.24353 | 0.11749 | -0.26703 | -0.18158 | 60.1959 | -61.9354 | 0.036621 | -62.2101 | 60.1685 | 62.1964 | 62.1414 | 0.045776 | -0.10788 | 0.044861 | 0.28198 | -0.1442 | -0.20294 | 0.013733 | 0.054932 | -62.3291 | 60.1318 | 60.1273 | 62.3016 | 62.3886 | 122.4747 | 62.1735 | 60.141
4813.7031 | 0.045776 | 0.38986 | -0.78293 | -0.25314 | 0.1207 | -0.27664 | -0.20721 | 60.2051 | -61.8896 | 0.16022 | -62.2009 | 60.2097 | 62.1643 | 62.1872 | 0.061035 | -0.11536 | 0.036316 | 0.27557 | -0.15595 | -0.20187 | 0.14191 | 0.24261 | -62.3062 | 60.1364 | 60.1044 | 62.2192 | 62.3474 | 122.5204 | 62.1231 | 60.1776
4815.4062 | 0.10681 | 0.41336 | -0.77652 | -0.25635 | 0.099335 | -0.24139 | -0.18478 | 60.2097 | -61.9492 | 0.054932 | -62.2421 | 60.2646 | 62.1918 | 62.1689 | 0.045776 | -0.10147 | 0.042725 | 0.27557 | -0.13672 | -0.20615 | 0.050354 | 0.073242 | -62.3749 | 60.1639 | 60.1822 | 62.2559 | 62.352 | 122.5571 | 62.1368 | 60.2005
4817.1562 | 0.061035 | 0.37918 | -0.76477 | -0.23819 | 0.11002 | -0.2478 | -0.18906 | 60.141 | -61.9858 | -0.045776 | -62.2787 | 60.2325 | 62.1964 | 62.1826 | 0.061035 | -0.11536 | 0.040588 | 0.28625 | -0.1442 | -0.1944 | -0.041199 | -0.018311 | -62.3611 | 60.1456 | 60.1135 | 62.2604 | 62.3703 | 122.5021 | 62.1826 | 60.173
4818.9062 | 0.1831 | 0.3717 | -0.7605 | -0.24246 | 0.097198 | -0.27237 | -0.17838 | 60.173 | -61.908 | 0.050354 | -62.233 | 60.2142 | 62.2467 | 62.2284 | 0.19836 | -0.11322 | 0.043793 | 0.28839 | -0.13031 | -0.17624 | 0.059509 | 0.1236 | -62.2925 | 60.141 | 60.1273 | 62.2787 | 62.4207 | 122.4564 | 62.1872 | 60.1776
4820.6406 | 0.061035 | 0.36636 | -0.78613 | -0.26489 | 0.10468 | -0.29373 | -0.20081 | 60.1227 | -61.9446 | 0.07782 | -62.233 | 60.2051 | 62.1826 | 62.1735 | 0.030518 | -0.13351 | 0.045929 | 0.27344 | -0.16449 | -0.19333 | 0.073242 | 0.16937 | -62.3062 | 60.1181 | 60.1227 | 62.2696 | 62.3566 | 122.5616 | 62.1414 | 60.1456
4822.3281 | 0.21362 | 0.36209 | -0.75943 | -0.25314 | 0.11429 | -0.26169 | -0.19012 | 60.1822 | -61.908 | 0.036621 | -62.2284 | 60.1685 | 62.1826 | 62.1872 | 0.030518 | -0.11963 | 0.046997 | 0.28091 | -0.14847 | -0.1976 | 0.036621 | 0.11902 | -62.2971 | 60.1456 | 60.1044 | 62.2742 | 62.384 | 122.4472 | 62.1872 | 60.1685
4824.7188 | 0.045776 | 0.41657 | -0.76477 | -0.24139 | 0.11322 | -0.24246 | -0.18906 | 60.141 | -62.0316 | -0.054932 | -62.2833 | 60.2737 | 62.2009 | 62.178 | 0.030518 | -0.098267 | 0.038452 | 0.28519 | -0.13672 | -0.21042 | -0.082397 | -0.091553 | -62.471 | 60.1913 | 60.1868 | 62.2467 | 62.3703 | 122.4564 | 62.178 | 60.2097
4827.3906 | 0.10681 | 0.42084 | -0.76477 | -0.25528 | 0.11002 | -0.2446 | -0.18906 | 60.2051 | -61.9217 | 0.054932 | -62.233 | 60.2692 | 62.1918 | 62.1597 | 0.061035 | -0.10468 | 0.05127 | 0.28519 | -0.12924 | -0.19974 | 0.018311 | 0.045776 | -62.4069 | 60.1685 | 60.1593 | 62.2421 | 62.3611 | 122.5159 | 62.1414 | 60.1822
4829.2031 | 0.076294 | 0.36423 | -0.76584 | -0.25848 | 0.10254 | -0.30121 | -0.19119 | 60.0998 | -61.9446 | 0.036621 | -62.2559 | 60.1822 | 62.1918 | 62.1964 | 0.030518 | -0.13992 | 0.038452 | 0.27344 | -0.16663 | -0.17731 | 0.018311 | 0.10071 | -62.3474 | 60.1181 | 60.1044 | 62.2696 | 62.352 | 122.4609 | 62.1826 | 60.173
4830.9844 | 0.12207 | 0.40909 | -0.77545 | -0.25635 | 0.10147 | -0.25207 | -0.18158 | 60.1685 | -61.9492 | 0.064087 | -62.233 | 60.2692 | 62.1872 | 62.178 | 0.030518 | -0.11002 | 0.057678 | 0.27664 | -0.14206 | -0.19974 | 0.022888 | 0.10529 | -62.3749 | 60.1959 | 60.1547 | 62.2467 | 62.3428 | 122.5708 | 62.1277 | 60.1639
4832.6875 | 0.1831 | 0.4155 | -0.77759 | -0.26276 | 0.10468 | -0.26062 | -0.19119 | 60.1227 | -61.9858 | 0.036621 | -62.2513 | 60.26 | 62.1872 | 62.1964 | 0.045776 | -0.11749 | 0.049133 | 0.29053 | -0.14847 | -0.19546 | 0.018311 | 0.10529 | -62.3932 | 60.1913 | 60.173 | 62.2009 | 62.352 | 122.5891 | 62.1231 | 60.1639
4834.4531 | 0.061035 | 0.41657 | -0.7605 | -0.23285 | 0.10254 | -0.2446 | -0.19333 | 60.1135 | -62.0407 | -0.068665 | -62.2696 | 60.26 | 62.2055 | 62.2009 | 0.045776 | -0.099335 | 0.045929 | 0.28091 | -0.13138 | -0.19333 | -0.073242 | -0.091553 | -62.4435 | 60.1822 | 60.1685 | 62.2604 | 62.384 | 122.4747 | 62.2009 | 60.2142
4836.3125 | 0.030518 | 0.42297 | -0.75943 | -0.2478 | 0.11643 | -0.2478 | -0.17838 | 60.1181 | -62.0041 | -0.054932 | -62.2696 | 60.2463 | 62.2101 | 62.1735 | 0.061035 | -0.10147 | 0.041656 | 0.27451 | -0.13031 | -0.19119 | -0.07782 | -0.050354 | -62.4435 | 60.1776 | 60.1822 | 62.2559 | 62.3703 | 122.4609 | 62.1689 | 60.2142
4838.0781 | -1.5411 | -0.10788 | -0.10895 | -0.23178 | 0.10895 | -0.29587 | -0.19012 | 60.1044 | -61.9492 | 0.045776 | -62.2513 | 60.2417 | 62.1964 | 62.1918 | 0.091553 | -0.1239 | 0.029907 | 0.2681 | -0.10788 | -0.17731 | 0.032043 | 0.13275 | -62.3245 | 60.1181 | 60.141 | 62.2604 | 62.3428 | 122.4976 | 62.1735 | 60.173
4841.2031 | 0.045776 | 0.40695 | -0.76797 | -0.25635 | 0.11536 | -0.23926 | -0.18478 | 60.1868 | -61.9766 | 0.018311 | -62.2467 | 60.2554 | 62.2147 | 62.1689 | 0.061035 | -0.10895 | 0.05661 | 0.28625 | -0.13992 | -0.20187 | -0.022888 | -0.013733 | -62.439 | 60.1593 | 60.1776 | 62.2421 | 62.3566 | 122.4609 | 62.1689 | 60.2325
4843.4062 | 0.030518 | 0.38238 | -0.77652 | -0.25848 | 0.09613 | -0.29159 | -0.20187 | 60.1913 | -61.8988 | 0.15564 | -62.2009 | 60.1822 | 62.1735 | 62.1735 | 0.045776 | -0.12924 | 0.03952 | 0.26916 | -0.15274 | -0.18906 | 0.10986 | 0.25177 | -62.3108 | 60.1273 | 60.1685 | 62.2284 | 62.3245 | 122.5159 | 62.1185 | 60.1822
4845.1562 | 0.21362 | 0.36316 | -0.74982 | -0.22324 | 0.098267 | -0.26382 | -0.1976 | 60.2051 | -61.9446 | 0.022888 | -62.2101 | 60.1822 | 62.1826 | 62.1506 | 0.061035 | -0.11215 | 0.037384 | 0.28198 | -0.1239 | -0.17731 | 0.045776 | 0.086975 | -62.2879 | 60.1685 | 60.1639 | 62.2879 | 62.3657 | 122.4976 | 62.178 | 60.1913
4846.8281 | 0.045776 | 0.37277 | -0.75943 | -0.25742 | 0.095062 | -0.24994 | -0.1944 | 60.1227 | -62.0224 | -0.073242 | -62.2879 | 60.2646 | 62.2055 | 62.1689 | 0.030518 | -0.10895 | 0.060883 | 0.27557 | -0.15488 | -0.19974 | -0.073242 | -0.082397 | -62.4252 | 60.1913 | 60.1547 | 62.2513 | 62.3749 | 122.4884 | 62.1735 | 60.1685
4848.5938 | 0.21362 | 0.40909 | -0.78079 | -0.26596 | 0.11536 | -0.27878 | -0.19546 | 60.1273 | -61.9858 | 0.050354 | -62.2604 | 60.2737 | 62.1826 | 62.1872 | 0.030518 | -0.11643 | 0.053406 | 0.28091 | -0.15488 | -0.19333 | 0.004578 | 0.082397 | -62.4115 | 60.1959 | 60.1913 | 62.2559 | 62.352 | 122.58 | 62.1277 | 60.1776
4850.3438 | 0.030518 | 0.4155 | -0.79147 | -0.25101 | 0.11215 | -0.2713 | -0.19012 | 60.1456 | -61.9537 | 0.086975 | -62.2559 | 60.2737 | 62.1872 | 62.1552 | 0.076294 | -0.11215 | 0.040588 | 0.27557 | -0.15274 | -0.18906 | 0.041199 | 0.13275 | -62.3886 | 60.2005 | 60.2097 | 62.2559 | 62.352 | 122.525 | 62.1368 | 60.1776
4852.4062 | 0.16785 | 0.35889 | -0.77225 | -0.23498 | 0.09613 | -0.28091 | -0.18265 | 60.1456 | -61.9263 | 0.041199 | -62.265 | 60.1639 | 62.1597 | 62.1872 | 0.030518 | -0.12924 | 0.03952 | 0.28625 | -0.12924 | -0.18478 | 0.045776 | 0.10986 | -62.3199 | 60.1273 | 60.1089 | 62.2925 | 62.3795 | 122.4564 | 62.2238 | 60.1868
4854.2656 | 0.030518 | 0.36209 | -0.75943 | -0.24994 | 0.1004 | -0.25421 | -0.18478 | 60.1364 | -62.0087 | -0.059509 | -62.2742 | 60.26 | 62.1964 | 62.1826 | 0.061035 | -0.10788 | 0.044861 | 0.27985 | -0.15167 | -0.20187 | -0.022888 | -0.036621 | -62.3886 | 60.1456 | 60.1364 | 62.2604 | 62.3611 | 122.493 | 62.178 | 60.1639
4856.0156 | 0.030518 | 0.40054 | -0.77011 | -0.22537 | 0.10468 | -0.25207 | -0.1944 | 60.1318 | -62.0316 | -0.07782 | -62.2787 | 60.2737 | 62.1872 | 62.2009 | 0.045776 | -0.10681 | 0.025635 | 0.27664 | -0.13351 | -0.19333 | -0.082397 | -0.091553 | -62.4435 | 60.1776 | 60.1776 | 62.2604 | 62.3795 | 122.4884 | 62.1918 | 60.2234
4859.1094 | 0.091553 | 0.3685 | -0.77438 | -0.24887 | 0.10895 | -0.2948 | -0.20828 | 60.0998 | -61.9675 | 0.050354 | -62.2604 | 60.2051 | 62.1964 | 62.1735 | 0.061035 | -0.13458 | 0.058746 | 0.27451 | -0.16769 | -0.19333 | 0.045776 | 0.13275 | -62.3291 | 60.1456 | 60.1181 | 62.2513 | 62.3428 | 122.5296 | 62.1643 | 60.1776
4860.7969 | 0.22888 | 0.36636 | -0.77225 | -0.25421 | 0.10574 | -0.27664 | -0.20081 | 60.1547 | -61.9537 | 0.036621 | -62.2375 | 60.2005 | 62.1735 | 62.1872 | 0.045776 | -0.13565 | 0.042725 | 0.28305 | -0.14526 | -0.18585 | 0.032043 | 0.068665 | -62.3474 | 60.1456 | 60.141 | 62.2559 | 62.384 | 122.438 | 62.1872 | 60.1685
4862.5469 | 0.061035 | 0.41122 | -0.75302 | -0.24567 | 0.10254 | -0.24139 | -0.18478 | 60.1639 | -62.0132 | -0.027466 | -62.2787 | 60.2646 | 62.1872 | 62.1826 | 0.045776 | -0.095062 | 0.045929 | 0.28732 | -0.13138 | -0.20401 | -0.068665 | -0.064087 | -62.4527 | 60.1913 | 60.173 | 62.265 | 62.3703 | 122.438 | 62.1826 | 60.2142
4864.5469 | 0.045776 | 0.3717 | -0.75302 | -0.22964 | 0.10681 | -0.25742 | -0.19333 | 60.1822 | -61.9583 | -0.004578 | -62.2467 | 60.1913 | 62.1735 | 62.1735 | 0.045776 | -0.11002 | 0.037384 | 0.28732 | -0.12924 | -0.18906 | 0.018311 | 0.032043 | -62.3062 | 60.1822 | 60.1364 | 62.2879 | 62.3703 | 122.5067 | 62.1964 | 60.1776
4866.3125 | 0.045776 | 0.40802 | -0.76157 | -0.24887 | 0.11215 | -0.24353 | -0.18372 | 60.1227 | -62.0316 | -0.045776 | -62.2742 | 60.2509 | 62.2055 | 62.178 | 0.030518 | -0.11322 | 0.050201 | 0.27771 | -0.13351 | -0.19974 | -0.10986 | -0.09613 | -62.4847 | 60.1868 | 60.173 | 62.2513 | 62.3795 | 122.4655 | 62.2055 | 60.2051
4868.3125 | 0.21362 | 0.42084 | -0.77759 | -0.26382 | 0.097198 | -0.26703 | -0.19546 | 60.1456 | -62.0178 | 0.045776 | -62.2513 | 60.2417 | 62.2101 | 62.1964 | 0.045776 | -0.10361 | 0.050201 | 0.28305 | -0.15488 | -0.18585 | 0.009155 | 0.09613 | -62.4161 | 60.2142 | 60.2051 | 62.2467 | 62.352 | 122.5937 | 62.0956 | 60.173
4870.1406 | 0.045776 | 0.37491 | -0.76797 | -0.25207 | 0.1004 | -0.25207 | -0.18692 | 60.1501 | -62.0132 | -0.050354 | -62.2879 | 60.2325 | 62.2101 | 62.1918 | 0.045776 | -0.10574 | 0.035248 | 0.28732 | -0.14313 | -0.1976 | -0.041199 | -0.022888 | -62.4023 | 60.1456 | 60.1364 | 62.2284 | 62.3657 | 122.5113 | 62.178 | 60.1776
4872.0781 | 0.061035 | 0.4155 | -0.77545 | -0.25848 | 0.11749 | -0.24674 | -0.18051 | 60.1318 | -62.0316 | -0.036621 | -62.2833 | 60.2509 | 62.2101 | 62.1964 | 0.091553 | -0.10681 | 0.053406 | 0.28519 | -0.14206 | -0.19012 | -0.11444 | -0.059509 | -62.4573 | 60.1776 | 60.1593 | 62.2742 | 62.3795 | 122.4426 | 62.1826 | 60.2051
4873.8125 | 0.030518 | 0.4155 | -0.7637 | -0.24674 | 0.11856 | -0.24887 | -0.18372 | 60.1593 | -61.9995 | -0.027466 | -62.2696 | 60.2463 | 62.1826 | 62.1643 | 0.061035 | -0.10895 | 0.044861 | 0.28305 | -0.14206 | -0.1944 | -0.073242 | -0.054932 | -62.4481 | 60.1776 | 60.2142 | 62.2604 | 62.3703 | 122.4472 | 62.178 | 60.2097
4875.625 | 0.1831 | 0.36102 | -0.75409 | -0.24567 | 0.11108 | -0.28732 | -0.20081 | 60.1639 | -61.9125 | 0.073242 | -62.2192 | 60.2234 | 62.2101 | 62.2055 | 0.1831 | -0.11322 | 0.054474 | 0.29053 | -0.12176 | -0.16342 | 0.073242 | 0.17853 | -62.3245 | 60.1273 | 60.1501 | 62.2925 | 62.3749 | 122.4289 | 62.1872 | 60.1913
4877.3125 | 0.061035 | 0.36102 | -0.77011 | -0.28305 | 0.11322 | -0.30121 | -0.20401 | 60.141 | -61.9492 | 0.091553 | -62.2467 | 60.2005 | 62.1735 | 62.1414 | 0.045776 | -0.13886 | 0.055542 | 0.27557 | -0.16663 | -0.18692 | 0.082397 | 0.18768 | -62.3016 | 60.1273 | 60.1181 | 62.2559 | 62.352 | 122.58 | 62.1506 | 60.1456
4879.0625 | 0.21362 | 0.36102 | -0.75409 | -0.24674 | 0.10147 | -0.25635 | -0.20401 | 60.2051 | -61.9171 | 0.036621 | -62.2238 | 60.1913 | 62.1918 | 62.1506 | 0.045776 | -0.11429 | 0.054474 | 0.28839 | -0.1442 | -0.17731 | 0.073242 | 0.1236 | -62.2787 | 60.1639 | 60.1364 | 62.2925 | 62.4023 | 122.4518 | 62.178 | 60.1639
4882.5156 | 0.1831 | 0.43152 | -0.78293 | -0.25101 | 0.11749 | -0.24567 | -0.18799 | 60.1685 | -61.9858 | 0.054932 | -62.2467 | 60.2783 | 62.1735 | 62.1643 | 0.061035 | -0.11002 | 0.05127 | 0.29159 | -0.14099 | -0.19867 | 0.013733 | 0.086975 | -62.384 | 60.2142 | 60.1685 | 62.2742 | 62.3474 | 122.58 | 62.1185 | 60.1593
4884.2656 | 0.045776 | 0.4155 | -0.784 | -0.25742 | 0.10895 | -0.26916 | -0.21362 | 60.1822 | -61.9125 | 0.14648 | -62.2192 | 60.2325 | 62.2147 | 62.146 | 0.015259 | -0.11749 | 0.038452 | 0.27237 | -0.14847 | -0.18478 | 0.09613 | 0.17853 | -62.352 | 60.173 | 60.1685 | 62.2421 | 62.3428 | 122.5204 | 62.1552 | 60.1913
4885.9531 | 0.061035 | 0.37384 | -0.75943 | -0.26276 | 0.11429 | -0.25635 | -0.18692 | 60.1547 | -62.0361 | -0.054932 | -62.2742 | 60.2371 | 62.2009 | 62.178 | 0.045776 | -0.11215 | 0.064087 | 0.28519 | -0.13672 | -0.1976 | -0.054932 | -0.036621 | -62.3932 | 60.1181 | 60.141 | 62.2559 | 62.3703 | 122.4884 | 62.1689 | 60.173
4887.7031 | 0.22888 | 0.41657 | -0.78186 | -0.26596 | 0.1004 | -0.25848 | -0.19867 | 60.1273 | -61.9949 | 0.045776 | -62.265 | 60.2554 | 62.2147 | 62.1552 | 0.045776 | -0.10895 | 0.059814 | 0.28412 | -0.14954 | -0.19012 | 0.022888 | 0.086975 | -62.4207 | 60.1913 | 60.173 | 62.2467 | 62.3932 | 122.5983 | 62.1231 | 60.1913
4889.4688 | 0.076294 | 0.3952 | -0.76157 | -0.23819 | 0.10574 | -0.25421 | -0.18051 | 60.1318 | -62.0132 | -0.064087 | -62.3016 | 60.2692 | 62.1918 | 62.2009 | 0.030518 | -0.1004 | 0.03952 | 0.29053 | -0.13779 | -0.18051 | -0.07782 | -0.073242 | -62.4298 | 60.1913 | 60.1593 | 62.2604 | 62.3657 | 122.4976 | 62.1826 | 60.173
4891.1562 | 0.076294 | 0.4187 | -0.77011 | -0.25314 | 0.10361 | -0.24674 | -0.19119 | 60.1822 | -61.9629 | 0.027466 | -62.2375 | 60.26 | 62.2055 | 62.1643 | 0.030518 | -0.10254 | 0.055542 | 0.29159 | -0.13672 | -0.1944 | -0.032043 | 0 | -62.4161 | 60.1776 | 60.1639 | 62.2375 | 62.3428 | 122.4564 | 62.178 | 60.2005
4892.8906 | 0.061035 | 0.41122 | -0.76263 | -0.24139 | 0.10468 | -0.25635 | -0.18692 | 60.1227 | -62.0316 | -0.059509 | -62.2787 | 60.2737 | 62.2147 | 62.2147 | 0.076294 | -0.10361 | 0.050201 | 0.27878 | -0.14313 | -0.18585 | -0.09613 | -0.091553 | -62.471 | 60.1776 | 60.1959 | 62.2559 | 62.3749 | 122.4472 | 62.1689 | 60.2234
4894.5781 | 0.061035 | 0.37491 | -0.75409 | -0.24246 | 0.10681 | -0.25848 | -0.18906 | 60.1547 | -61.9995 | -0.022888 | -62.2787 | 60.2234 | 62.2101 | 62.1735 | 0.061035 | -0.11215 | 0.038452 | 0.28198 | -0.13779 | -0.18906 | 0.018311 | 0.059509 | -62.2971 | 60.1776 | 60.1868 | 62.2742 | 62.4115 | 122.5021 | 62.1872 | 60.1776
4896.3281 | 0.045776 | 0.41657 | -0.78613 | -0.25528 | 0.12283 | -0.28519 | -0.20187 | 60.1593 | -61.9446 | 0.10986 | -62.233 | 60.2142 | 62.1918 | 62.1735 | 0.061035 | -0.11322 | 0.042725 | 0.27451 | -0.16449 | -0.18692 | 0.045776 | 0.15564 | -62.3886 | 60.1822 | 60.2005 | 62.265 | 62.3566 | 122.5342 | 62.1185 | 60.1959
4898.0156 | 0.15259 | 0.41122 | -0.77652 | -0.27878 | 0.1207 | -0.24567 | -0.19653 | 60.1868 | -61.9675 | 0.073242 | -62.233 | 60.26 | 62.1872 | 62.1689 | 0.045776 | -0.10468 | 0.057678 | 0.2948 | -0.13992 | -0.20187 | 0.045776 | 0.091553 | -62.384 | 60.1639 | 60.1868 | 62.233 | 62.3566 | 122.5754 | 62.1323 | 60.1639
4899.7656 | 0.045776 | 0.38238 | -0.75943 | -0.26169 | 0.10468 | -0.26382 | -0.19546 | 60.1181 | -62.0224 | -0.068665 | -62.2833 | 60.2509 | 62.1872 | 62.1918 | 0.045776 | -0.11215 | 0.046997 | 0.28625 | -0.13458 | -0.19974 | -0.068665 | -0.068665 | -62.4115 | 60.1547 | 60.1364 | 62.2604 | 62.384 | 122.493 | 62.146 | 60.1501
4901.5156 | 0.12207 | 0.37384 | -0.77011 | -0.24994 | 0.10788 | -0.29053 | -0.20615 | 60.1089 | -61.9675 | 0.032043 | -62.2604 | 60.2005 | 62.1918 | 62.1735 | 0.045776 | -0.12711 | 0.041656 | 0.27023 | -0.16129 | -0.18051 | 0.009155 | 0.09613 | -62.352 | 60.1089 | 60.1273 | 62.2559 | 62.3886 | 122.4609 | 62.1643 | 60.1822
4903.2031 | 0.061035 | 0.41763 | -0.76691 | -0.25101 | 0.10468 | -0.23819 | -0.18692 | 60.1456 | -62.0407 | -0.045776 | -62.2833 | 60.2463 | 62.2009 | 62.2055 | 0.045776 | -0.10254 | 0.044861 | 0.29373 | -0.12817 | -0.20081 | -0.10071 | -0.064087 | -62.4664 | 60.2097 | 60.1685 | 62.2742 | 62.3886 | 122.4564 | 62.1643 | 60.2097
4904.9531 | 0.19836 | 0.36102 | -0.74875 | -0.24033 | 0.11536 | -0.27237 | -0.18906 | 60.1868 | -61.8851 | 0.086975 | -62.1964 | 60.2051 | 62.2192 | 62.2101 | 0.16785 | -0.11108 | 0.042725 | 0.29159 | -0.12817 | -0.16663 | 0.059509 | 0.10986 | -62.2879 | 60.1456 | 60.1273 | 62.265 | 62.4207 | 122.4472 | 62.1872 | 60.1913
4906.6875 | 0.045776 | 0.37064 | -0.784 | -0.25421 | 0.11108 | -0.298 | -0.19653 | 60.2051 | -61.8622 | 0.15106 | -62.2147 | 60.2097 | 62.1872 | 62.1552 | 0.045776 | -0.13458 | 0.035248 | 0.27237 | -0.16769 | -0.18692 | 0.15564 | 0.27008 | -62.2696 | 60.1318 | 60.1456 | 62.2513 | 62.3474 | 122.5662 | 62.1094 | 60.1639
4908.4375 | 0.091553 | 0.40802 | -0.78293 | -0.27023 | 0.11215 | -0.23819 | -0.19119 | 60.2005 | -61.9537 | 0.073242 | -62.233 | 60.2646 | 62.178 | 62.1735 | 0.045776 | -0.12283 | 0.041656 | 0.28625 | -0.1506 | -0.19974 | 0.041199 | 0.091553 | -62.3795 | 60.1822 | 60.1501 | 62.2559 | 62.3566 | 122.5662 | 62.1277 | 60.1593
4910.125 | 0.061035 | 0.38666 | -0.77438 | -0.26382 | 0.11215 | -0.29053 | -0.20935 | 60.1959 | -61.8759 | 0.17395 | -62.2009 | 60.2005 | 62.1689 | 62.1597 | 0.030518 | -0.13138 | 0.046997 | 0.26703 | -0.15915 | -0.18906 | 0.12817 | 0.26093 | -62.2879 | 60.0952 | 60.1501 | 62.2284 | 62.3474 | 122.5433 | 62.1277 | 60.173
4912.1719 | 0.045776 | 0.35568 | -0.76797 | -0.25742 | 0.091858 | -0.28305 | -0.19867 | 60.2051 | -61.9171 | 0.10529 | -62.2147 | 60.1913 | 62.1918 | 62.1689 | 0.030518 | -0.11856 | 0.05127 | 0.27237 | -0.16022 | -0.1944 | 0.13275 | 0.21973 | -62.2833 | 60.1044 | 60.1593 | 62.2467 | 62.3383 | 122.5708 | 62.1368 | 60.1593
4913.9375 | 0.091553 | 0.35996 | -0.77118 | -0.25314 | 0.10468 | -0.27023 | -0.19546 | 60.1639 | -61.9675 | 0.018311 | -62.2559 | 60.1959 | 62.178 | 62.178 | 0.045776 | -0.12817 | 0.03952 | 0.27451 | -0.14954 | -0.19546 | 0.013733 | 0.068665 | -62.3611 | 60.1044 | 60.1181 | 62.2696 | 62.352 | 122.4564 | 62.178 | 60.2005
4915.6406 | 0.045776 | 0.38452 | -0.77225 | -0.23819 | 0.11108 | -0.2446 | -0.1944 | 60.173 | -62.0407 | -0.07782 | -62.2925 | 60.2646 | 62.2238 | 62.1964 | 0.030518 | -0.10254 | 0.036316 | 0.28305 | -0.13031 | -0.21255 | -0.059509 | -0.07782 | -62.4252 | 60.1685 | 60.1822 | 62.2513 | 62.3566 | 122.4884 | 62.178 | 60.2051
4917.5625 | 0.19836 | 0.36423 | -0.76797 | -0.24887 | 0.097198 | -0.27771 | -0.19653 | 60.173 | -61.9492 | 0.022888 | -62.2559 | 60.2005 | 62.1964 | 62.1643 | 0.015259 | -0.13138 | 0.038452 | 0.2681 | -0.13886 | -0.18585 | 0.050354 | 0.091553 | -62.3428 | 60.1456 | 60.1639 | 62.2559 | 62.3703 | 122.4564 | 62.1964 | 60.2097
4919.3125 | 0.030518 | 0.40054 | -0.78934 | -0.23605 | 0.10574 | -0.27985 | -0.20081 | 60.2188 | -61.8851 | 0.14191 | -62.2055 | 60.1913 | 62.1735 | 62.1552 | 0.015259 | -0.12924 | 0.038452 | 0.25955 | -0.14847 | -0.19546 | 0.14191 | 0.24261 | -62.3199 | 60.1456 | 60.1456 | 62.2192 | 62.3611 | 122.5342 | 62.1094 | 60.2097
4921 | 0.1831 | 0.36529 | -0.76477 | -0.23712 | 0.10254 | -0.27237 | -0.20081 | 60.2371 | -61.7798 | 0.045776 | -62.2147 | 60.2005 | 62.2055 | 62.2238 | 0.13733 | -0.11002 | 0.038452 | 0.28198 | -0.12711 | -0.18265 | 0.073242 | 0.091553 | -62.3199 | 60.1501 | 60.1501 | 62.265 | 62.384 | 122.4426 | 62.1918 | 60.1959
4922.7031 | 0.061035 | 0.36957 | -0.77866 | -0.25528 | 0.092926 | -0.27344 | -0.1976 | 60.2005 | -61.9492 | 0.10071 | -62.2284 | 60.1913 | 62.178 | 62.1643 | 0.045776 | -0.12924 | 0.044861 | 0.27023 | -0.16449 | -0.19867 | 0.11444 | 0.20599 | -62.3016 | 60.1501 | 60.1227 | 62.2055 | 62.3199 | 122.5891 | 62.1552 | 60.1639
4924.3906 | 0.1831 | 0.36316 | -0.75836 | -0.23712 | 0.10574 | -0.24246 | -0.19653 | 60.2417 | -61.9171 | 0.050354 | -62.233 | 60.1776 | 62.1964 | 62.1735 | 0.045776 | -0.12283 | 0.05127 | 0.28732 | -0.12497 | -0.1944 | 0.082397 | 0.10986 | -62.3108 | 60.1593 | 60.1364 | 62.2742 | 62.4069 | 122.4701 | 62.178 | 60.2005
4926.0938 | 0.045776 | 0.39734 | -0.77331 | -0.25848 | 0.10147 | -0.23926 | -0.19333 | 60.173 | -62.059 | -0.054932 | -62.2971 | 60.2875 | 62.178 | 62.2147 | 0.030518 | -0.099335 | 0.055542 | 0.27771 | -0.13886 | -0.19974 | -0.068665 | -0.09613 | -62.4527 | 60.2005 | 60.173 | 62.2879 | 62.3932 | 122.4884 | 62.1918 | 60.1868
4927.7656 | 0.015259 | 0.38025 | -0.76904 | -0.27237 | 0.1004 | -0.27664 | -0.18906 | 60.2005 | -61.8759 | 0.17395 | -62.2101 | 60.2097 | 62.1735 | 62.1872 | 0.030518 | -0.13245 | 0.053406 | 0.28305 | -0.16235 | -0.20187 | 0.14191 | 0.24719 | -62.3108 | 60.1273 | 60.1181 | 62.2604 | 62.3703 | 122.525 | 62.1277 | 60.173
4929.4531 | 0.19836 | 0.41763 | -0.77225 | -0.2681 | 0.10895 | -0.25314 | -0.19974 | 60.1318 | -61.9675 | 0.032043 | -62.2696 | 60.2646 | 62.1918 | 62.1964 | 0.015259 | -0.11002 | 0.054474 | 0.28519 | -0.15381 | -0.1976 | 0.032043 | 0.10071 | -62.4207 | 60.2417 | 60.1913 | 62.3062 | 62.4069 | 122.5845 | 62.1094 | 60.1822
4931.1406 | 0.12207 | 0.42297 | -0.76584 | -0.24033 | 0.10147 | -0.24353 | -0.19333 | 60.2188 | -61.908 | 0.059509 | -62.233 | 60.2371 | 62.1826 | 62.1597 | 0.030518 | -0.10574 | 0.045929 | 0.28091 | -0.12604 | -0.20294 | 0.050354 | 0.073242 | -62.3978 | 60.1913 | 60.1685 | 62.2513 | 62.3611 | 122.5433 | 62.1735 | 60.1776
4932.8438 | 0.22888 | 0.36316 | -0.75836 | -0.24674 | 0.1004 | -0.26703 | -0.18692 | 60.1776 | -61.9034 | 0.054932 | -62.2238 | 60.1685 | 62.1964 | 62.1689 | 0.10681 | -0.10895 | 0.049133 | 0.28412 | -0.13565 | -0.17838 | 0.07782 | 0.13275 | -62.2742 | 60.141 | 60.1227 | 62.265 | 62.3886 | 122.4609 | 62.2009 | 60.1639
4934.5469 | 0.16785 | 0.36316 | -0.76904 | -0.23712 | 0.10574 | -0.27557 | -0.18906 | 60.1685 | -61.9034 | 0.050354 | -62.2513 | 60.1822 | 62.178 | 62.1826 | 0.045776 | -0.13565 | 0.052338 | 0.28839 | -0.14099 | -0.16983 | 0.073242 | 0.11444 | -62.3245 | 60.141 | 60.1135 | 62.2833 | 62.4161 | 122.4197 | 62.2009 | 60.1593
4936.2344 | 0.19836 | 0.41977 | -0.784 | -0.2681 | 0.11749 | -0.26382 | -0.19653 | 60.1135 | -61.9812 | 0.068665 | -62.2833 | 60.26 | 62.1918 | 62.2009 | 0.045776 | -0.10681 | 0.048065 | 0.28305 | -0.14954 | -0.19333 | 0.050354 | 0.11902 | -62.3978 | 60.2005 | 60.1868 | 62.265 | 62.3657 | 122.5479 | 62.1231 | 60.1913
4937.9219 | 0.091553 | 0.41122 | -0.76477 | -0.24246 | 0.10468 | -0.24674 | -0.18478 | 60.2142 | -61.9263 | 0.054932 | -62.2375 | 60.26 | 62.1689 | 62.2055 | 0.061035 | -0.10681 | 0.043793 | 0.27557 | -0.12924 | -0.19653 | 0.013733 | 0.041199 | -62.4115 | 60.1547 | 60.1593 | 62.2604 | 62.3428 | 122.5021 | 62.1506 | 60.1913
4939.6094 | 0.12207 | 0.40909 | -0.77866 | -0.26276 | 0.10895 | -0.25314 | -0.18585 | 60.1913 | -61.9308 | 0.064087 | -62.2375 | 60.2783 | 62.1826 | 62.1643 | 0.061035 | -0.10468 | 0.055542 | 0.27985 | -0.13779 | -0.19653 | 0.022888 | 0.068665 | -62.3886 | 60.1959 | 60.1685 | 62.2513 | 62.352 | 122.5433 | 62.1277 | 60.1959
4941.3125 | 0.030518 | 0.392 | -0.75729 | -0.23712 | 0.11002 | -0.26169 | -0.18906 | 60.1227 | -62.0407 | -0.07782 | -62.2925 | 60.26 | 62.2147 | 62.2101 | 0.045776 | -0.11963 | 0.044861 | 0.28519 | -0.13779 | -0.18799 | -0.07782 | -0.086975 | -62.4344 | 60.1913 | 60.1685 | 62.2787 | 62.3795 | 122.4838 | 62.1689 | 60.1868
4942.9844 | 0.030518 | 0.36957 | -0.77545 | -0.26169 | 0.12283 | -0.30121 | -0.1944 | 60.1959 | -61.8668 | 0.16937 | -62.2055 | 60.2188 | 62.1735 | 62.1643 | 0.015259 | -0.13672 | 0.050201 | 0.27451 | -0.1741 | -0.19012 | 0.11444 | 0.2655 | -62.3016 | 60.1364 | 60.1318 | 62.2238 | 62.3428 | 122.5525 | 62.1368 | 60.1593
4944.6875 | 0.1831 | 0.41229 | -0.77545 | -0.23926 | 0.11002 | -0.24887 | -0.19119 | 60.1822 | -61.9812 | 0.073242 | -62.2192 | 60.2554 | 62.1964 | 62.178 | 0.045776 | -0.098267 | 0.041656 | 0.28946 | -0.14526 | -0.19974 | 0.022888 | 0.09613 | -62.3795 | 60.1822 | 60.1913 | 62.2284 | 62.3611 | 122.5845 | 62.1414 | 60.1639
4946.375 | 0.1831 | 0.43793 | -0.78293 | -0.24887 | 0.10574 | -0.27237 | -0.1944 | 60.1227 | -61.9766 | 0.059509 | -62.2604 | 60.2554 | 62.1872 | 62.1918 | 0.030518 | -0.11749 | 0.042725 | 0.27664 | -0.1474 | -0.1976 | 0.050354 | 0.13275 | -62.3886 | 60.2097 | 60.2005 | 62.2742 | 62.3703 | 122.5479 | 62.1323 | 60.173
4948.1094 | 0.12207 | 0.40375 | -0.77331 | -0.24887 | 0.10895 | -0.24674 | -0.19653 | 60.1959 | -61.9446 | 0.054932 | -62.233 | 60.2463 | 62.1826 | 62.1964 | 0.061035 | -0.11108 | 0.041656 | 0.27771 | -0.14099 | -0.19546 | 0.022888 | 0.045776 | -62.3978 | 60.1685 | 60.1776 | 62.2238 | 62.3611 | 122.5204 | 62.146 | 60.1685
4949.7812 | 0.045776 | 0.39627 | -0.75089 | -0.25314 | 0.10147 | -0.25848 | -0.20615 | 60.1227 | -62.0041 | -0.059509 | -62.2833 | 60.2417 | 62.2284 | 62.2055 | 0.045776 | -0.11215 | 0.044861 | 0.28305 | -0.12711 | -0.19333 | -0.059509 | -0.054932 | -62.4023 | 60.1501 | 60.1364 | 62.2833 | 62.3657 | 122.5067 | 62.1826 | 60.1822
4951.4688 | 0.21362 | 0.41016 | -0.78079 | -0.27557 | 0.10361 | -0.26596 | -0.20294 | 60.1181 | -62.0132 | 0.045776 | -62.265 | 60.2646 | 62.1964 | 62.1872 | 0.045776 | -0.11108 | 0.055542 | 0.29159 | -0.15915 | -0.19012 | 0 | 0.10071 | -62.4023 | 60.2142 | 60.2005 | 62.2421 | 62.3657 | 122.5845 | 62.1506 | 60.1547
4953.1562 | 0.045776 | 0.38132 | -0.76157 | -0.24353 | 0.11536 | -0.26489 | -0.19119 | 60.1181 | -62.0132 | -0.091553 | -62.2971 | 60.2692 | 62.2238 | 62.2009 | 0.045776 | -0.12283 | 0.041656 | 0.28412 | -0.1474 | -0.19012 | -0.07782 | -0.068665 | -62.4207 | 60.1685 | 60.1593 | 62.2742 | 62.3611 | 122.4976 | 62.1872 | 60.173
4954.8438 | 0.19836 | 0.41977 | -0.78507 | -0.2713 | 0.1004 | -0.25955 | -0.20401 | 60.1273 | -62.0132 | 0.041199 | -62.2604 | 60.2921 | 62.2192 | 62.2101 | 0.045776 | -0.11002 | 0.058746 | 0.28625 | -0.14954 | -0.19974 | 0.009155 | 0.10529 | -62.3795 | 60.1913 | 60.1868 | 62.2559 | 62.3566 | 122.6028 | 62.1231 | 60.1547
4956.5156 | 0.1831 | 0.35782 | -0.76157 | -0.23285 | 0.093994 | -0.27344 | -0.20187 | 60.1639 | -61.8851 | 0.050354 | -62.2421 | 60.1868 | 62.2055 | 62.1689 | 0.030518 | -0.13031 | 0.042725 | 0.27771 | -0.14313 | -0.17944 | 0.07782 | 0.10986 | -62.2879 | 60.1593 | 60.1456 | 62.3016 | 62.3932 | 122.4426 | 62.1872 | 60.1959
4958.2188 | 0.045776 | 0.40802 | -0.74875 | -0.23285 | 0.10788 | -0.2478 | -0.18692 | 60.1181 | -62.0178 | -0.064087 | -62.2833 | 60.2829 | 62.2192 | 62.2055 | 0.015259 | -0.10147 | 0.03418 | 0.27771 | -0.15274 | -0.18906 | -0.068665 | -0.07782 | -62.4069 | 60.1685 | 60.1547 | 62.2559 | 62.3474 | 122.4976 | 62.178 | 60.1822
4959.9062 | 0.045776 | 0.36636 | -0.77972 | -0.25421 | 0.10468 | -0.28198 | -0.20401 | 60.2005 | -61.8393 | 0.15106 | -62.2055 | 60.1959 | 62.1735 | 62.1506 | 0.061035 | -0.13779 | 0.042725 | 0.2681 | -0.16129 | -0.19546 | 0.1236 | 0.27924 | -62.2787 | 60.141 | 60.1364 | 62.2375 | 62.3611 | 122.5433 | 62.1552 | 60.1318
4961.6406 | 0.15259 | 0.35675 | -0.77652 | -0.24353 | 0.10681 | -0.28091 | -0.20401 | 60.1822 | -61.9125 | 0.036621 | -62.2559 | 60.1959 | 62.1689 | 62.178 | 0.045776 | -0.12497 | 0.033112 | 0.2681 | -0.12711 | -0.19119 | 0.064087 | 0.10986 | -62.3062 | 60.1547 | 60.1318 | 62.2879 | 62.4069 | 122.4106 | 62.1964 | 60.1776
4963.3281 | 0.030518 | 0.40482 | -0.77759 | -0.2713 | 0.11749 | -0.26276 | -0.20187 | 60.1501 | -61.9583 | 0.082397 | -62.2559 | 60.26 | 62.1964 | 62.2101 | 0.045776 | -0.11322 | 0.044861 | 0.28091 | -0.14526 | -0.20081 | 0.050354 | 0.12817 | -62.3932 | 60.2097 | 60.1913 | 62.2467 | 62.3703 | 122.5342 | 62.1231 | 60.2142
4965.0781 | 0.21362 | 0.42084 | -0.78293 | -0.26489 | 0.11215 | -0.26489 | -0.19546 | 60.1273 | -61.9812 | 0.045776 | -62.2742 | 60.2692 | 62.178 | 62.178 | 0.061035 | -0.11963 | 0.050201 | 0.27985 | -0.15381 | -0.19974 | 0.036621 | 0.10071 | -62.4069 | 60.2142 | 60.1868 | 62.2787 | 62.4252 | 122.5662 | 62.1277 | 60.1959
4966.7656 | 0.16785 | 0.36529 | -0.75089 | -0.2446 | 0.093994 | -0.25528 | -0.19226 | 60.1822 | -61.908 | 0.032043 | -62.2147 | 60.2188 | 62.1826 | 62.1735 | 0.061035 | -0.11536 | 0.038452 | 0.28198 | -0.11749 | -0.18692 | 0.054932 | 0.07782 | -62.2925 | 60.1593 | 60.1501 | 62.3245 | 62.3978 | 122.4976 | 62.1735 | 60.1822
4968.4375 | 0.1831 | 0.40909 | -0.77331 | -0.2681 | 0.10895 | -0.25421 | -0.19867 | 60.1318 | -61.9858 | 0.054932 | -62.2559 | 60.2737 | 62.2101 | 62.1735 | 0.030518 | -0.10895 | 0.050201 | 0.27664 | -0.14313 | -0.1976 | 0.022888 | 0.09613 | -62.4023 | 60.1959 | 60.1913 | 62.2375 | 62.3749 | 122.5983 | 62.0956 | 60.173
4970.125 | 0.045776 | 0.41229 | -0.76157 | -0.25314 | 0.11215 | -0.24887 | -0.18265 | 60.1456 | -61.9995 | -0.027466 | -62.2696 | 60.26 | 62.1826 | 62.1918 | 0.061035 | -0.10574 | 0.045929 | 0.29053 | -0.13779 | -0.19546 | -0.07782 | -0.059509 | -62.4481 | 60.1776 | 60.173 | 62.2696 | 62.3611 | 122.4472 | 62.1918 | 60.1959
4971.8125 | 0.045776 | 0.37064 | -0.76263 | -0.23498 | 0.10681 | -0.27557 | -0.18478 | 60.173 | -61.9263 | 0.004578 | -62.2238 | 60.2097 | 62.178 | 62.1918 | 0.045776 | -0.11108 | 0.038452 | 0.28839 | -0.11749 | -0.17624 | 0.050354 | 0.086975 | -62.2879 | 60.1456 | 60.1547 | 62.3245 | 62.3932 | 122.5021 | 62.2009 | 60.1685
4973.5 | 0.061035 | 0.39414 | -0.77331 | -0.26596 | 0.10468 | -0.29053 | -0.19974 | 60.1685 | -61.8759 | 0.16479 | -62.1964 | 60.1913 | 62.1872 | 62.1735 | 0.045776 | -0.11322 | 0.040588 | 0.27344 | -0.16342 | -0.19333 | 0.10986 | 0.25177 | -62.3199 | 60.1364 | 60.1501 | 62.2375 | 62.3428 | 122.5433 | 62.146 | 60.2005
4975.1875 | 0.045776 | 0.40268 | -0.7637 | -0.24033 | 0.093994 | -0.25421 | -0.18478 | 60.1318 | -62.0224 | -0.07782 | -62.2833 | 60.2737 | 62.2101 | 62.1918 | 0.061035 | -0.10254 | 0.043793 | 0.27771 | -0.13031 | -0.19333 | -0.068665 | -0.082397 | -62.4252 | 60.1685 | 60.1593 | 62.2604 | 62.3978 | 122.5113 | 62.1735 | 60.173
4976.875 | 0.10681 | 0.35782 | -0.76691 | -0.24674 | 0.091858 | -0.28305 | -0.20828 | 60.1181 | -61.9675 | 0.041199 | -62.265 | 60.2051 | 62.1964 | 62.1735 | 0.045776 | -0.14313 | 0.043793 | 0.27237 | -0.16022 | -0.18265 | 0.027466 | 0.10986 | -62.3428 | 60.1318 | 60.1273 | 62.2559 | 62.3795 | 122.493 | 62.1643 | 60.1456
4978.625 | 0.045776 | 0.39734 | -0.75195 | -0.2446 | 0.095062 | -0.23498 | -0.18585 | 60.141 | -62.027 | -0.045776 | -62.2787 | 60.2829 | 62.1826 | 62.2009 | 0.045776 | -0.095062 | 0.044861 | 0.28412 | -0.14099 | -0.21042 | -0.10071 | -0.054932 | -62.4619 | 60.1776 | 60.2005 | 62.2421 | 62.3657 | 122.4518 | 62.178 | 60.2097
4980.3125 | 0.13733 | 0.41229 | -0.77652 | -0.2478 | 0.11536 | -0.25314 | -0.18265 | 60.1776 | -61.9354 | 0.064087 | -62.2284 | 60.26 | 62.178 | 62.1552 | 0.030518 | -0.10895 | 0.044861 | 0.28305 | -0.14633 | -0.1976 | 0.018311 | 0.086975 | -62.3749 | 60.1959 | 60.1547 | 62.2513 | 62.3291 | 122.5616 | 62.1506 | 60.173
4981.9844 | 0.061035 | 0.39627 | -0.7637 | -0.24246 | 0.10468 | -0.25314 | -0.19867 | 60.1364 | -62.027 | -0.068665 | -62.2833 | 60.2509 | 62.1918 | 62.1597 | 0.030518 | -0.10788 | 0.044861 | 0.28519 | -0.13886 | -0.19867 | -0.086975 | -0.091553 | -62.4298 | 60.1822 | 60.1593 | 62.265 | 62.3978 | 122.4976 | 62.1826 | 60.2005
4983.6875 | 0.045776 | 0.41122 | -0.74982 | -0.24353 | 0.10468 | -0.25314 | -0.19012 | 60.0952 | -62.0407 | -0.064087 | -62.2833 | 60.2692 | 62.2238 | 62.1918 | 0.061035 | -0.1004 | 0.037384 | 0.28625 | -0.13351 | -0.18051 | -0.082397 | -0.09613 | -62.439 | 60.2097 | 60.2005 | 62.2879 | 62.3611 | 122.4701 | 62.178 | 60.2051
4985.375 | 0.030518 | 0.38773 | -0.77545 | -0.27451 | 0.11108 | -0.28946 | -0.19546 | 60.1868 | -61.8988 | 0.14648 | -62.2147 | 60.1959 | 62.1826 | 62.1597 | 0.045776 | -0.13351 | 0.050201 | 0.27557 | -0.16556 | -0.1976 | 0.082397 | 0.21973 | -62.3337 | 60.1593 | 60.1776 | 62.2238 | 62.3474 | 122.525 | 62.1277 | 60.2005
4987.0625 | 0.015259 | 0.40695 | -0.75623 | -0.25207 | 0.11429 | -0.23926 | -0.19226 | 60.1044 | -62.0636 | -0.068665 | -62.3108 | 60.2646 | 62.2147 | 62.1689 | 0.045776 | -0.10574 | 0.045929 | 0.2713 | -0.13779 | -0.1944 | -0.10071 | -0.09613 | -62.4435 | 60.1868 | 60.1913 | 62.2925 | 62.3749 | 122.4792 | 62.178 | 60.2142
4988.7656 | 0.045776 | 0.41336 | -0.76263 | -0.24567 | 0.11215 | -0.24353 | -0.19226 | 60.1547 | -61.9675 | 0.004578 | -62.2513 | 60.2646 | 62.1735 | 62.1689 | 0.030518 | -0.10895 | 0.046997 | 0.27771 | -0.13565 | -0.19653 | -0.032043 | -0.009155 | -62.4481 | 60.1776 | 60.1776 | 62.2742 | 62.3886 | 122.4472 | 62.1918 | 60.228
4990.4844 | 0.030518 | 0.38345 | -0.77866 | -0.26382 | 0.10254 | -0.30014 | -0.1944 | 60.1547 | -61.8805 | 0.16479 | -62.2055 | 60.1913 | 62.2009 | 62.146 | 0.030518 | -0.13138 | 0.042725 | 0.26169 | -0.15274 | -0.18372 | 0.11444 | 0.24261 | -62.3016 | 60.1456 | 60.1456 | 62.2604 | 62.3337 | 122.5296 | 62.1277 | 60.1822
4992.1719 | 0.091553 | 0.40375 | -0.78186 | -0.25848 | 0.10895 | -0.25207 | -0.19012 | 60.2051 | -61.9446 | 0.054932 | -62.2421 | 60.2829 | 62.2009 | 62.1826 | 0.061035 | -0.11429 | 0.045929 | 0.27985 | -0.13886 | -0.19333 | 0.013733 | 0.036621 | -62.3932 | 60.1685 | 60.1868 | 62.2467 | 62.3474 | 122.5342 | 62.1643 | 60.2097
4993.875 | 0.045776 | 0.41122 | -0.75729 | -0.23605 | 0.10254 | -0.25314 | -0.18799 | 60.1135 | -62.0316 | -0.073242 | -62.2833 | 60.2646 | 62.2238 | 62.2055 | 0.061035 | -0.10254 | 0.042725 | 0.29053 | -0.13779 | -0.18906 | -0.10071 | -0.09613 | -62.439 | 60.2005 | 60.1959 | 62.2971 | 62.352 | 122.4884 | 62.1918 | 60.2142
4995.6094 | 0.030518 | 0.37277 | -0.78079 | -0.25314 | 0.10468 | -0.29907 | -0.19012 | 60.1913 | -61.8668 | 0.16937 | -62.1872 | 60.2097 | 62.1872 | 62.1552 | 0.045776 | -0.13138 | 0.042725 | 0.26596 | -0.16769 | -0.18799 | 0.13275 | 0.2655 | -62.2971 | 60.1227 | 60.1135 | 62.2513 | 62.3383 | 122.5708 | 62.1277 | 60.1593
4997.2812 | 0.045776 | 0.41016 | -0.75729 | -0.24139 | 0.10361 | -0.24567 | -0.1976 | 60.141 | -62.0224 | -0.045776 | -62.2696 | 60.2737 | 62.2009 | 62.2055 | 0.045776 | -0.1004 | 0.045929 | 0.28305 | -0.13245 | -0.20294 | -0.091553 | -0.073242 | -62.4527 | 60.2097 | 60.1822 | 62.2787 | 62.384 | 122.4609 | 62.2192 | 60.2097
4998.9844 | 0.045776 | 0.36743 | -0.75516 | -0.2446 | 0.10361 | -0.26276 | -0.18692 | 60.141 | -61.9904 | -0.022888 | -62.2833 | 60.2234 | 62.2009 | 62.1826 | 0.030518 | -0.11536 | 0.045929 | 0.28198 | -0.14313 | -0.18906 | -0.027466 | 0.004578 | -62.3474 | 60.1318 | 60.1547 | 62.2375 | 62.352 | 122.5204 | 62.2055 | 60.1685
5000.6719 | 0.19836 | 0.40482 | -0.76691 | -0.26703 | 0.12283 | -0.25421 | -0.18692 | 60.1181 | -62.0087 | 0.054932 | -62.265 | 60.2829 | 62.1918 | 62.1689 | 0.061035 | -0.1207 | 0.057678 | 0.27878 | -0.15167 | -0.18478 | 0.013733 | 0.07782 | -62.4207 | 60.2097 | 60.1913 | 62.2696 | 62.352 | 122.5937 | 62.1185 | 60.1501
5002.375 | 0.030518 | 0.36423 | -0.77652 | -0.25635 | 0.099335 | -0.28946 | -0.20294 | 60.1639 | -61.8851 | 0.12817 | -62.1964 | 60.2188 | 62.1689 | 62.1826 | 0.045776 | -0.13886 | 0.05127 | 0.28091 | -0.16022 | -0.18799 | 0.13275 | 0.22888 | -62.2833 | 60.1181 | 60.1364 | 62.2604 | 62.3428 | 122.5845 | 62.146 | 60.1456
5004.0625 | 0.061035 | 0.40482 | -0.76263 | -0.27557 | 0.099335 | -0.23926 | -0.17517 | 60.2051 | -61.9675 | 0.041199 | -62.2467 | 60.2509 | 62.1872 | 62.1597 | 0.045776 | -0.10681 | 0.059814 | 0.28412 | -0.14099 | -0.21149 | -0.009155 | 0.009155 | -62.4069 | 60.1913 | 60.173 | 62.265 | 62.352 | 122.493 | 62.1826 | 60.2097
5005.7344 | 0.19836 | 0.34714 | -0.76691 | -0.22644 | 0.11108 | -0.27344 | -0.19974 | 60.1822 | -61.9171 | 0.032043 | -62.2192 | 60.1685 | 62.1826 | 62.1735 | 0.16785 | -0.10254 | 0.050201 | 0.29907 | -0.1207 | -0.17624 | 0.068665 | 0.10986 | -62.2833 | 60.1501 | 60.1501 | 62.3108 | 62.4023 | 122.4609 | 62.1872 | 60.1776
5007.4219 | 0.061035 | 0.38559 | -0.77652 | -0.26276 | 0.10788 | -0.29159 | -0.19867 | 60.1913 | -61.8942 | 0.16022 | -62.2101 | 60.228 | 62.1826 | 62.2009 | 0.061035 | -0.12604 | 0.032043 | 0.27023 | -0.17197 | -0.19546 | 0.12817 | 0.25177 | -62.3291 | 60.1227 | 60.1318 | 62.2284 | 62.352 | 122.5296 | 62.1231 | 60.2142
5009.1406 | 0.061035 | 0.41336 | -0.77011 | -0.23392 | 0.10895 | -0.23498 | -0.19226 | 60.1822 | -61.9629 | 0.013733 | -62.2559 | 60.2646 | 62.1826 | 62.1872 | 0.030518 | -0.10681 | 0.035248 | 0.28198 | -0.12497 | -0.1976 | -0.027466 | -0.013733 | -62.4298 | 60.2051 | 60.1639 | 62.2467 | 62.3703 | 122.4655 | 62.1735 | 60.2097
5010.8281 | 0.16785 | 0.34393 | -0.75089 | -0.24674 | 0.10254 | -0.26169 | -0.18906 | 60.2097 | -61.908 | 0.041199 | -62.2101 | 60.2005 | 62.1964 | 62.1872 | 0.015259 | -0.11749 | 0.045929 | 0.27344 | -0.1506 | -0.20187 | 0.050354 | 0.09613 | -62.2833 | 60.1547 | 60.1639 | 62.3016 | 62.4115 | 122.493 | 62.2055 | 60.1776
5012.5312 | 0.076294 | 0.40268 | -0.75195 | -0.25848 | 0.10468 | -0.2446 | -0.20508 | 60.2097 | -61.9675 | 0.022888 | -62.2421 | 60.2554 | 62.1872 | 62.178 | 0.061035 | -0.10361 | 0.063019 | 0.28946 | -0.14633 | -0.19867 | -0.018311 | 0.013733 | -62.4161 | 60.1913 | 60.2005 | 62.2421 | 62.3795 | 122.4792 | 62.1414 | 60.2417
5014.2188 | 0.076294 | 0.35248 | -0.77866 | -0.26062 | 0.10254 | -0.30228 | -0.1976 | 60.0998 | -61.9492 | 0.068665 | -62.2421 | 60.2188 | 62.2192 | 62.2009 | 0.045776 | -0.13992 | 0.03952 | 0.26596 | -0.15808 | -0.18906 | 0.041199 | 0.14191 | -62.3154 | 60.1044 | 60.141 | 62.2513 | 62.3657 | 122.5525 | 62.1597 | 60.1547
5015.9062 | 0.10681 | 0.41763 | -0.77011 | -0.25314 | 0.12924 | -0.2478 | -0.19546 | 60.2142 | -61.9354 | 0.054932 | -62.2284 | 60.2829 | 62.1872 | 62.2009 | 0.015259 | -0.1004 | 0.043793 | 0.28305 | -0.1474 | -0.20828 | 0.027466 | 0.086975 | -62.3932 | 60.1913 | 60.1639 | 62.233 | 62.3428 | 122.5616 | 62.1185 | 60.1959
5017.5938 | 0.045776 | 0.37918 | -0.78613 | -0.26382 | 0.09613 | -0.27985 | -0.20401 | 60.1868 | -61.8713 | 0.16937 | -62.2055 | 60.2051 | 62.1735 | 62.1597 | 0.061035 | -0.13031 | 0.038452 | 0.25635 | -0.15808 | -0.19653 | 0.11902 | 0.26093 | -62.3108 | 60.1135 | 60.1135 | 62.2513 | 62.3383 | 122.5342 | 62.1277 | 60.1639
5019.2969 | 0.030518 | 0.42297 | -0.75943 | -0.23392 | 0.099335 | -0.23392 | -0.19546 | 60.1593 | -61.9904 | -0.018311 | -62.2604 | 60.2737 | 62.2009 | 62.2009 | 0.030518 | -0.10468 | 0.036316 | 0.28305 | -0.12711 | -0.19653 | -0.073242 | -0.050354 | -62.439 | 60.173 | 60.1822 | 62.2604 | 62.3749 | 122.4564 | 62.178 | 60.2234
5020.9844 | 0.061035 | 0.3685 | -0.75943 | -0.24887 | 0.095062 | -0.26169 | -0.17838 | 60.173 | -61.9171 | 0.050354 | -62.2284 | 60.1639 | 62.1918 | 62.178 | 0.045776 | -0.1207 | 0.040588 | 0.27878 | -0.14313 | -0.19333 | 0.022888 | 0.064087 | -62.3199 | 60.1044 | 60.0952 | 62.2513 | 62.3474 | 122.4701 | 62.1872 | 60.1776
5022.7031 | 0.045776 | 0.36636 | -0.76797 | -0.25207 | 0.10147 | -0.2681 | -0.18158 | 60.1913 | -61.908 | 0.032043 | -62.2238 | 60.1913 | 62.2055 | 62.1826 | 0.045776 | -0.11963 | 0.040588 | 0.27023 | -0.13565 | -0.20187 | 0.004578 | 0.064087 | -62.3337 | 60.1181 | 60.1044 | 62.2604 | 62.3749 | 122.4792 | 62.1643 | 60.1547
5024.3906 | 0.045776 | 0.38025 | -0.78186 | -0.2713 | 0.10254 | -0.28946 | -0.20721 | 60.1868 | -61.8713 | 0.15564 | -62.2055 | 60.2142 | 62.1918 | 62.1643 | 0.045776 | -0.1207 | 0.043793 | 0.27023 | -0.15808 | -0.18692 | 0.11902 | 0.25177 | -62.3199 | 60.1273 | 60.1135 | 62.2513 | 62.3383 | 122.5388 | 62.1277 | 60.1913
5026.1094 | 0.030518 | 0.36102 | -0.79041 | -0.24994 | 0.09613 | -0.28946 | -0.19333 | 60.2097 | -61.8668 | 0.15564 | -62.1964 | 60.1822 | 62.1826 | 62.1689 | 0.030518 | -0.13138 | 0.02243 | 0.27023 | -0.15595 | -0.19653 | 0.13275 | 0.25635 | -62.2925 | 60.1227 | 60.1364 | 62.2696 | 62.3337 | 122.5891 | 62.146 | 60.141
5027.8438 | 0.030518 | 0.35996 | -0.75836 | -0.24674 | 0.10788 | -0.25207 | -0.20081 | 60.2051 | -61.9171 | 0.041199 | -62.233 | 60.1868 | 62.1918 | 62.1872 | 0.076294 | -0.13031 | 0.036316 | 0.28091 | -0.13992 | -0.19653 | 0.036621 | 0.07782 | -62.3291 | 60.1089 | 60.1135 | 62.2604 | 62.3795 | 122.4701 | 62.1552 | 60.1868
5029.6562 | 0.045776 | 0.39093 | -0.78613 | -0.25955 | 0.10788 | -0.26489 | -0.20081 | 60.1822 | -61.9308 | 0.11444 | -62.2284 | 60.2737 | 62.1964 | 62.1918 | 0.045776 | -0.12283 | 0.043793 | 0.27451 | -0.14847 | -0.1976 | 0.059509 | 0.14648 | -62.3886 | 60.2005 | 60.1822 | 62.2467 | 62.3749 | 122.525 | 62.114 | 60.2234
5031.4062 | 0.045776 | 0.37705 | -0.74341 | -0.25101 | 0.10361 | -0.26276 | -0.18478 | 60.2142 | -61.9125 | 0.041199 | -62.2284 | 60.1639 | 62.2055 | 62.178 | 0.045776 | -0.12604 | 0.049133 | 0.27451 | -0.14633 | -0.19546 | 0.022888 | 0.054932 | -62.3291 | 60.1227 | 60.0769 | 62.265 | 62.3611 | 122.4655 | 62.2147 | 60.1639
5033.1719 | 0.030518 | 0.35782 | -0.78079 | -0.26276 | 0.10147 | -0.27557 | -0.19974 | 60.2051 | -61.8668 | 0.17853 | -62.2009 | 60.2005 | 62.1689 | 62.1826 | 0.061035 | -0.12497 | 0.037384 | 0.26596 | -0.14954 | -0.1976 | 0.14191 | 0.26093 | -62.3154 | 60.1318 | 60.1089 | 62.2421 | 62.3703 | 122.5525 | 62.1277 | 60.1913
5034.875 | 0.045776 | 0.36636 | -0.77866 | -0.23819 | 0.10147 | -0.27878 | -0.20721 | 60.1685 | -61.9308 | 0.009155 | -62.2513 | 60.2005 | 62.1643 | 62.1872 | 0.045776 | -0.12924 | 0.03952 | 0.27557 | -0.14526 | -0.19119 | 0.032043 | 0.073242 | -62.3611 | 60.1227 | 60.1273 | 62.233 | 62.3657 | 122.4518 | 62.1964 | 60.2005
5036.6094 | 0.061035 | 0.37277 | -0.77545 | -0.26703 | 0.10254 | -0.2681 | -0.19974 | 60.2188 | -61.8942 | 0.11902 | -62.2147 | 60.2097 | 62.2284 | 62.1597 | 0.045776 | -0.11322 | 0.052338 | 0.27451 | -0.15595 | -0.18799 | 0.09613 | 0.19684 | -62.3245 | 60.1456 | 60.1227 | 62.2467 | 62.3566 | 122.5296 | 62.1231 | 60.1959
5038.375 | 0.045776 | 0.37811 | -0.78079 | -0.26276 | 0.10895 | -0.27344 | -0.20081 | 60.2051 | -61.8805 | 0.11444 | -62.2147 | 60.2097 | 62.2055 | 62.2009 | 0.045776 | -0.12497 | 0.050201 | 0.27664 | -0.1506 | -0.1976 | 0.09613 | 0.21515 | -62.3108 | 60.141 | 60.0998 | 62.2238 | 62.3474 | 122.525 | 62.1552 | 60.1547
5040.125 | 0.015259 | 0.35996 | -0.76263 | -0.24139 | 0.099335 | -0.27023 | -0.19012 | 60.2234 | -61.908 | 0.07782 | -62.233 | 60.2005 | 62.1872 | 62.1735 | 0.030518 | -0.11856 | 0.036316 | 0.27771 | -0.14633 | -0.20721 | 0.068665 | 0.09613 | -62.3611 | 60.1135 | 60.0815 | 62.2467 | 62.3474 | 122.4609 | 62.1918 | 60.1822
5041.8125 | 0.045776 | 0.39627 | -0.76904 | -0.26276 | 0.10574 | -0.25207 | -0.18799 | 60.1547 | -61.9949 | 0.022888 | -62.2879 | 60.2737 | 62.2055 | 62.2055 | 0.061035 | -0.10895 | 0.043793 | 0.27985 | -0.15701 | -0.20294 | 0.022888 | 0.091553 | -62.4115 | 60.2051 | 60.1822 | 62.2787 | 62.3749 | 122.5616 | 62.1277 | 60.173
5043.5781 | 0.045776 | 0.40695 | -0.77972 | -0.24246 | 0.10254 | -0.26169 | -0.18478 | 60.1547 | -61.9858 | 0.022888 | -62.2742 | 60.2737 | 62.1872 | 62.1964 | 0.030518 | -0.11002 | 0.044861 | 0.27878 | -0.14099 | -0.1976 | 0.004578 | 0.082397 | -62.4161 | 60.2097 | 60.228 | 62.265 | 62.3383 | 122.5525 | 62.1323 | 60.2097
5045.3281 | 0.045776 | 0.40802 | -0.77866 | -0.26703 | 0.10788 | -0.25528 | -0.18906 | 60.1456 | -61.9812 | 0.022888 | -62.2742 | 60.3012 | 62.2284 | 62.1872 | 0.030518 | -0.10788 | 0.05661 | 0.27878 | -0.1506 | -0.19974 | 0.009155 | 0.059509 | -62.4298 | 60.1959 | 60.1913 | 62.265 | 62.3703 | 122.58 | 62.1277 | 60.1913
5047.0625 | 0.045776 | 0.37064 | -0.77972 | -0.2478 | 0.089722 | -0.27664 | -0.19119 | 60.173 | -61.8851 | 0.10986 | -62.2192 | 60.1776 | 62.1826 | 62.1964 | 0.045776 | -0.12817 | 0.045929 | 0.27344 | -0.15808 | -0.18799 | 0.073242 | 0.22888 | -62.3199 | 60.1089 | 60.1181 | 62.2604 | 62.3383 | 122.5388 | 62.1643 | 60.1913
5048.7656 | 0.076294 | 0.42297 | -0.76157 | -0.24567 | 0.10681 | -0.22751 | -0.18906 | 60.2371 | -61.9263 | 0.082397 | -62.2284 | 60.2875 | 62.1826 | 62.178 | 0.045776 | -0.10254 | 0.043793 | 0.28839 | -0.13672 | -0.20935 | 0.032043 | 0.068665 | -62.4069 | 60.1593 | 60.2005 | 62.2467 | 62.3611 | 122.5021 | 62.1552 | 60.2234
5050.5156 | 0.045776 | 0.35782 | -0.77331 | -0.26382 | 0.10361 | -0.28732 | -0.19974 | 60.2051 | -61.8439 | 0.12817 | -62.2101 | 60.1913 | 62.2055 | 62.1643 | 0.030518 | -0.13245 | 0.053406 | 0.26703 | -0.15915 | -0.18478 | 0.09613 | 0.22888 | -62.2971 | 60.1181 | 60.0906 | 62.265 | 62.3886 | 122.5708 | 62.1231 | 60.1547
5052.2969 | 0.061035 | 0.38986 | -0.76157 | -0.26703 | 0.10895 | -0.25207 | -0.20187 | 60.1364 | -61.9766 | 0.018311 | -62.2787 | 60.2921 | 62.2055 | 62.1918 | 0.045776 | -0.10681 | 0.048065 | 0.28305 | -0.15488 | -0.18585 | 0 | 0.082397 | -62.4069 | 60.2097 | 60.2051 | 62.2696 | 62.3474 | 122.5708 | 62.1231 | 60.1868
5053.9688 | 0.045776 | 0.392 | -0.77118 | -0.22644 | 0.099335 | -0.24353 | -0.1944 | 60.1639 | -62.0041 | -0.022888 | -62.2742 | 60.2737 | 62.2101 | 62.1597 | 0.045776 | -0.093994 | 0.041656 | 0.29053 | -0.13779 | -0.19546 | -0.036621 | -0.050354 | -62.4298 | 60.1959 | 60.1822 | 62.2742 | 62.3611 | 122.4976 | 62.1643 | 60.2097
5055.6562 | 0.030518 | 0.3685 | -0.75729 | -0.24353 | 0.10468 | -0.26489 | -0.1741 | 60.2005 | -61.9125 | 0.068665 | -62.2055 | 60.1913 | 62.1918 | 62.178 | 0.045776 | -0.12604 | 0.03418 | 0.28732 | -0.14099 | -0.1944 | 0.041199 | 0.091553 | -62.3245 | 60.141 | 60.1044 | 62.2925 | 62.3383 | 122.493 | 62.1689 | 60.1685
5057.4062 | 0.030518 | 0.41229 | -0.75943 | -0.25421 | 0.093994 | -0.24246 | -0.18265 | 60.228 | -61.9308 | 0.073242 | -62.2147 | 60.2692 | 62.1918 | 62.1597 | 0.045776 | -0.10361 | 0.055542 | 0.27878 | -0.13992 | -0.19974 | 0.009155 | 0.054932 | -62.4023 | 60.2142 | 60.1913 | 62.2467 | 62.3566 | 122.493 | 62.1414 | 60.2005
5059.1406 | 0.076294 | 0.35782 | -0.77759 | -0.24674 | 0.10895 | -0.29159 | -0.20294 | 60.1227 | -61.9537 | 0.032043 | -62.265 | 60.1913 | 62.1918 | 62.1826 | 0.045776 | -0.13245 | 0.027771 | 0.2713 | -0.15915 | -0.1709 | 0.004578 | 0.082397 | -62.3611 | 60.0998 | 60.141 | 62.2604 | 62.3932 | 122.4838 | 62.1964 | 60.1868
5060.8906 | 0.045776 | 0.37811 | -0.76797 | -0.26596 | 0.10361 | -0.29587 | -0.20508 | 60.1959 | -61.8805 | 0.10986 | -62.2101 | 60.1959 | 62.2055 | 62.1689 | 0.045776 | -0.12711 | 0.049133 | 0.27237 | -0.16983 | -0.20401 | 0.10071 | 0.21515 | -62.3016 | 60.1227 | 60.1456 | 62.2925 | 62.3474 | 122.5616 | 62.1231 | 60.1639
5062.6562 | 0.061035 | 0.41122 | -0.76263 | -0.25421 | 0.1004 | -0.24353 | -0.1976 | 60.2234 | -61.9263 | 0.07782 | -62.2238 | 60.2921 | 62.1826 | 62.178 | 0.061035 | -0.1004 | 0.055542 | 0.28198 | -0.13245 | -0.20615 | 0.045776 | 0.07782 | -62.3795 | 60.2188 | 60.1776 | 62.233 | 62.3795 | 122.5433 | 62.1231 | 60.2051
5064.3438 | 0.045776 | 0.35889 | -0.77331 | -0.24139 | 0.098267 | -0.27771 | -0.1976 | 60.1913 | -61.8988 | 0.068665 | -62.2284 | 60.173 | 62.1964 | 62.1735 | 0.030518 | -0.13245 | 0.042725 | 0.28091 | -0.14313 | -0.19012 | 0.054932 | 0.10529 | -62.3245 | 60.1227 | 60.0769 | 62.2925 | 62.384 | 122.4426 | 62.1872 | 60.1959
5066.0781 | 0.030518 | 0.36423 | -0.75195 | -0.25207 | 0.097198 | -0.25848 | -0.19333 | 60.1868 | -61.9446 | 0.032043 | -62.2421 | 60.2234 | 62.2009 | 62.178 | 0.045776 | -0.11856 | 0.041656 | 0.27771 | -0.13886 | -0.21042 | 0.036621 | 0.064087 | -62.3337 | 60.173 | 60.1456 | 62.233 | 62.3474 | 122.5067 | 62.1826 | 60.1822
5067.8438 | 0.030518 | 0.42297 | -0.76904 | -0.25528 | 0.10574 | -0.24674 | -0.1944 | 60.173 | -61.9446 | 0.064087 | -62.2375 | 60.2966 | 62.1826 | 62.178 | 0.061035 | -0.1004 | 0.033112 | 0.27237 | -0.13565 | -0.19653 | 0.027466 | 0.10529 | -62.384 | 60.2005 | 60.1822 | 62.2604 | 62.3657 | 122.5891 | 62.1048 | 60.1822
5069.5469 | 0.061035 | 0.35996 | -0.76157 | -0.24567 | 0.11215 | -0.28305 | -0.19546 | 60.1959 | -61.8896 | 0.068665 | -62.2375 | 60.1685 | 62.178 | 62.1735 | 0.061035 | -0.11963 | 0.030975 | 0.27451 | -0.1474 | -0.19012 | 0.064087 | 0.10529 | -62.3291 | 60.1364 | 60.1089 | 62.2696 | 62.3657 | 122.438 | 62.2147 | 60.2097
5071.2812 | 0.045776 | 0.38345 | -0.78293 | -0.2681 | 0.10574 | -0.28732 | -0.19119 | 60.173 | -61.8851 | 0.11444 | -62.2238 | 60.173 | 62.2009 | 62.1826 | 0.045776 | -0.13031 | 0.036316 | 0.26916 | -0.14633 | -0.19119 | 0.082397 | 0.21057 | -62.3016 | 60.1181 | 60.1227 | 62.2559 | 62.3611 | 122.5388 | 62.1277 | 60.1685
5073.0156 | 0.045776 | 0.39093 | -0.77331 | -0.26916 | 0.097198 | -0.26169 | -0.20508 | 60.1318 | -61.9858 | 0.027466 | -62.2925 | 60.2829 | 62.1826 | 62.1689 | 0.045776 | -0.11536 | 0.044861 | 0.28198 | -0.15701 | -0.1944 | -0.004578 | 0.082397 | -62.4115 | 60.2188 | 60.2142 | 62.2833 | 62.3749 | 122.5754 | 62.1323 | 60.1913
5074.7812 | 0.045776 | 0.41657 | -0.76157 | -0.25207 | 0.11643 | -0.25101 | -0.19119 | 60.2097 | -61.9537 | 0.07782 | -62.2421 | 60.2875 | 62.1735 | 62.1735 | 0.045776 | -0.093994 | 0.044861 | 0.28305 | -0.13672 | -0.21576 | 0.027466 | 0.09613 | -62.3657 | 60.2188 | 60.1685 | 62.2742 | 62.352 | 122.5754 | 62.1094 | 60.173
5076.4688 | 0.045776 | 0.41977 | -0.75943 | -0.25528 | 0.093994 | -0.2446 | -0.18372 | 60.1822 | -61.9492 | 0.082397 | -62.2284 | 60.2829 | 62.1964 | 62.1826 | 0.061035 | -0.1207 | 0.046997 | 0.2948 | -0.13672 | -0.19546 | 0.050354 | 0.09613 | -62.384 | 60.2188 | 60.1776 | 62.2604 | 62.3795 | 122.5983 | 62.1048 | 60.2097
5078.2031 | 0.061035 | 0.36529 | -0.75623 | -0.23285 | 0.10468 | -0.26169 | -0.18372 | 60.1593 | -61.9858 | 0.004578 | -62.265 | 60.2325 | 62.178 | 62.2192 | 0.015259 | -0.12817 | 0.042725 | 0.28198 | -0.1474 | -0.1944 | 0.022888 | 0.050354 | -62.352 | 60.1318 | 60.1547 | 62.2559 | 62.3611 | 122.5159 | 62.1964 | 60.1639
5079.9688 | 0.015259 | 0.39627 | -0.76263 | -0.24567 | 0.11108 | -0.25955 | -0.18051 | 60.1501 | -62.0224 | -0.032043 | -62.2787 | 60.2737 | 62.1964 | 62.1964 | 0.045776 | -0.1004 | 0.037384 | 0.28625 | -0.14099 | -0.18478 | -0.050354 | -0.045776 | -62.4252 | 60.2097 | 60.2051 | 62.2467 | 62.4023 | 122.5067 | 62.1826 | 60.1868
5081.6562 | 0.061035 | 0.40802 | -0.75836 | -0.25207 | 0.10574 | -0.25421 | -0.18692 | 60.1959 | -61.9263 | 0.082397 | -62.233 | 60.2966 | 62.178 | 62.1689 | 0.045776 | -0.11429 | 0.052338 | 0.28412 | -0.13672 | -0.19546 | 0.041199 | 0.07782 | -62.3749 | 60.1913 | 60.2097 | 62.2559 | 62.3657 | 122.5433 | 62.1323 | 60.2188
5083.4062 | 0.015259 | 0.38666 | -0.75623 | -0.25207 | 0.095062 | -0.26703 | -0.19226 | 60.1364 | -62.0087 | -0.022888 | -62.2833 | 60.2875 | 62.2192 | 62.1872 | 0.030518 | -0.12176 | 0.046997 | 0.28412 | -0.13779 | -0.1944 | -0.036621 | -0.018311 | -62.4161 | 60.1822 | 60.1685 | 62.2421 | 62.3611 | 122.5067 | 62.178 | 60.173
5085.0938 | 0.045776 | 0.35889 | -0.77652 | -0.25955 | 0.10361 | -0.30228 | -0.20081 | 60.1685 | -61.8851 | 0.11444 | -62.2147 | 60.2005 | 62.1826 | 62.1872 | 0.045776 | -0.13779 | 0.044861 | 0.27237 | -0.17303 | -0.19012 | 0.082397 | 0.21057 | -62.2787 | 60.1227 | 60.0815 | 62.2559 | 62.3703 | 122.5708 | 62.146 | 60.1501
5086.8594 | 0.045776 | 0.34927 | -0.77652 | -0.25848 | 0.095062 | -0.27878 | -0.19867 | 60.1364 | -61.9446 | 0.032043 | -62.2787 | 60.1959 | 62.1964 | 62.1872 | 0 | -0.12711 | 0.041656 | 0.27023 | -0.15167 | -0.18692 | 0.022888 | 0.082397 | -62.3428 | 60.141 | 60.1181 | 62.2513 | 62.3749 | 122.4609 | 62.1918 | 60.1822
5088.5625 | 0.061035 | 0.35996 | -0.77011 | -0.25314 | 0.11215 | -0.26489 | -0.19546 | 60.1868 | -61.9034 | 0.059509 | -62.233 | 60.1959 | 62.178 | 62.1643 | 0.045776 | -0.12176 | 0.042725 | 0.28732 | -0.1474 | -0.19226 | 0.045776 | 0.073242 | -62.3611 | 60.1273 | 60.0815 | 62.265 | 62.3703 | 122.4426 | 62.2055 | 60.1776
5090.3125 | 0.045776 | 0.34714 | -0.77118 | -0.25955 | 0.10468 | -0.28091 | -0.19333 | 60.1089 | -61.9858 | 0.022888 | -62.2696 | 60.1959 | 62.2055 | 62.1964 | 0.061035 | -0.12604 | 0.046997 | 0.27451 | -0.15915 | -0.19653 | 0.032043 | 0.11444 | -62.3474 | 60.1364 | 60.1181 | 62.265 | 62.3703 | 122.5571 | 62.1964 | 60.1501
5092.0625 | 0.076294 | 0.392 | -0.44327 | -0.26916 | -0.20615 | -0.23498 | -0.1944 | 0.073242 | -0.068665 | -0.004578 | 0.018311 | 0.28839 | 0.032043 | 0.18768 | 0.030518 | -0.11749 | -0.27344 | -0.045929 | -0.13886 | -0.20401 | -0.013733 | -0.018311 | -0.086975 | 0.17395 | 0.15106 | 0.14191 | 0.18768 | -0.12817 | 0.091553 | 0.13733
5093.7656 | 0.030518 | 0.36423 | -0.47104 | -0.2446 | -0.20935 | -0.27878 | -0.1944 | 0.12817 | 0.10529 | 0.10986 | 0.068665 | 0.19226 | 0.050354 | 0.19226 | 0.045776 | -0.14526 | -0.29373 | -0.054474 | -0.16342 | -0.19974 | 0.09613 | 0.21057 | 0.022888 | 0.10529 | 0.11444 | 0.14191 | 0.19684 | 0.10529 | 0.059509 | 0.086975
5095.5156 | 0.045776 | 0.37918 | -0.45075 | -0.23285 | -0.21149 | -0.24674 | -0.19333 | 0.086975 | -0.032043 | -0.018311 | 0.013733 | 0.25635 | 0.036621 | 0.19684 | 0.015259 | -0.11108 | -0.2948 | -0.044861 | -0.13565 | -0.20721 | -0.013733 | -0.009155 | -0.054932 | 0.15106 | 0.1236 | 0.11902 | 0.17395 | 0.022888 | 0.091553 | 0.13733
5097.2656 | 0.10681 | 0.42191 | -0.46249 | -0.2446 | -0.20935 | -0.25207 | -0.19974 | 0.10529 | -0.009155 | 0.045776 | 0.050354 | 0.28381 | 0.045776 | 0.19226 | 0.045776 | -0.11429 | -0.28198 | -0.044861 | -0.13138 | -0.1976 | 0.013733 | 0.086975 | -0.036621 | 0.19226 | 0.16937 | 0.10986 | 0.1831 | 0.10071 | 0.022888 | 0.13275
5099.0312 | 0.045776 | 0.37277 | -0.45929 | -0.25101 | -0.20081 | -0.298 | -0.1976 | 0.054932 | 0 | 0.036621 | 0.036621 | 0.19684 | 0.068665 | 0.19226 | 0.045776 | -0.12924 | -0.29159 | -0.060883 | -0.16449 | -0.19653 | 0.022888 | 0.1236 | 0.018311 | 0.10986 | 0.091553 | 0.13275 | 0.18768 | 0.10071 | 0.050354 | 0.10071
5100.7812 | 0.030518 | 0.35889 | -0.45288 | -0.24246 | -0.20401 | -0.27344 | -0.19333 | 0.1236 | 0.054932 | 0.082397 | 0.059509 | 0.19684 | 0.045776 | 0.18768 | 0.045776 | -0.12924 | -0.28946 | -0.053406 | -0.14206 | -0.20294 | 0.036621 | 0.07782 | -0.013733 | 0.091553 | 0.068665 | 0.14191 | 0.18768 | -0.041199 | 0.11444 | 0.1236
5102.4688 | 0.061035 | 0.36743 | -0.46997 | -0.26916 | -0.20615 | -0.29159 | -0.1944 | 0.12817 | 0.09613 | 0.11444 | 0.086975 | 0.1831 | 0.050354 | 0.20142 | 0.045776 | -0.12604 | -0.29266 | -0.059814 | -0.15808 | -0.20401 | 0.068665 | 0.19684 | 0.027466 | 0.11444 | 0.086975 | 0.1236 | 0.19226 | 0.13275 | 0.045776 | 0.082397
5104.2188 | 0.061035 | 0.3685 | -0.46143 | -0.22644 | -0.19867 | -0.26916 | -0.1976 | 0.13275 | 0.068665 | 0.073242 | 0.059509 | 0.1831 | 0.041199 | 0.1831 | 0.061035 | -0.12283 | -0.298 | -0.050201 | -0.13779 | -0.1976 | 0.027466 | 0.07782 | -0.013733 | 0.091553 | 0.07782 | 0.1236 | 0.19684 | -0.009155 | 0.10986 | 0.12817
5105.9531 | 0.015259 | 0.37598 | -0.46463 | -0.26703 | -0.20294 | -0.27664 | -0.20187 | 0.12817 | 0.09613 | 0.11444 | 0.082397 | 0.18768 | 0.041199 | 0.19226 | 0.061035 | -0.1239 | -0.28732 | -0.05661 | -0.15167 | -0.20187 | 0.073242 | 0.19226 | 0.022888 | 0.11902 | 0.086975 | 0.12817 | 0.17853 | 0.091553 | 0.041199 | 0.10071
5107.6562 | 0.076294 | 0.42831 | -0.46036 | -0.24887 | -0.20615 | -0.25635 | -0.19653 | 0.086975 | -0.022888 | 0.013733 | 0.041199 | 0.25635 | 0.059509 | 0.1831 | 0.061035 | -0.10895 | -0.29266 | -0.054474 | -0.13138 | -0.20828 | -0.013733 | 0.086975 | -0.045776 | 0.17853 | 0.16022 | 0.11902 | 0.17395 | 0.14648 | 0.018311 | 0.11444
5109.4219 | 0.10681 | 0.41763 | -0.45609 | -0.24246 | -0.20187 | -0.24674 | -0.18158 | 0.10986 | 0.009155 | 0.059509 | 0.068665 | 0.28381 | 0.041199 | 0.19684 | 0.030518 | -0.10681 | -0.28946 | -0.05127 | -0.13458 | -0.19974 | 0 | 0.073242 | -0.032043 | 0.15564 | 0.15564 | 0.13733 | 0.17395 | 0.14191 | 0.027466 | 0.14648
5111.1719 | 0.045776 | 0.42511 | -0.44434 | -0.25314 | -0.21469 | -0.23926 | -0.18906 | 0.059509 | -0.091553 | -0.032043 | 0.009155 | 0.25177 | 0.054932 | 0.20142 | 0.061035 | -0.092926 | -0.29159 | -0.049133 | -0.13245 | -0.18906 | -0.068665 | -0.036621 | -0.091553 | 0.18768 | 0.16479 | 0.14191 | 0.17395 | 0.013733 | 0.082397 | 0.13733
5112.875 | 0 | 0.4187 | -0.46249 | -0.26382 | -0.20828 | -0.25955 | -0.19867 | 0.059509 | -0.036621 | 0.022888 | 0.032043 | 0.24719 | 0.064087 | 0.19226 | 0.030518 | -0.099335 | -0.27344 | -0.050201 | -0.15488 | -0.18585 | -0.041199 | 0.068665 | -0.068665 | 0.20142 | 0.16022 | 0.13275 | 0.20142 | 0.14191 | 0.027466 | 0.11444
5114.6406 | 0.045776 | 0.40375 | -0.47211 | -0.26382 | -0.19974 | -0.27878 | -0.20081 | 0.032043 | -0.032043 | 0.022888 | 0.022888 | 0.25635 | 0.064087 | 0.20142 | 0.061035 | -0.13138 | -0.28091 | -0.038452 | -0.1709 | -0.20081 | -0.022888 | 0.082397 | -0.064087 | 0.17395 | 0.15106 | 0.14191 | 0.18768 | 0.10071 | 0.045776 | 0.11902
5116.3281 | 0.045776 | 0.38773 | -0.4689 | -0.26062 | -0.21149 | -0.28519 | -0.20081 | 0.10529 | 0.064087 | 0.10529 | 0.082397 | 0.19226 | 0.050354 | 0.18768 | 0.030518 | -0.13672 | -0.28732 | -0.045929 | -0.16663 | -0.1976 | 0.009155 | 0.17853 | -0.004578 | 0.12817 | 0.10986 | 0.12817 | 0.18768 | 0.09613 | 0.041199 | 0.10529
5118.0625 | 0.045776 | 0.37598 | -0.47531 | -0.24567 | -0.20401 | -0.28625 | -0.20721 | 0.11444 | 0.082397 | 0.10529 | 0.07782 | 0.1831 | 0.059509 | 0.19226 | 0.061035 | -0.12497 | -0.30014 | -0.052338 | -0.14847 | -0.19867 | 0.059509 | 0.21515 | 0.032043 | 0.10529 | 0.086975 | 0.13275 | 0.1831 | 0.10529 | 0.045776 | 0.09613
5119.8125 | 0.091553 | 0.42084 | -0.46356 | -0.25314 | -0.20401 | -0.25635 | -0.20401 | 0.082397 | -0.045776 | 0.009155 | 0.032043 | 0.28381 | 0.050354 | 0.20142 | 0.045776 | -0.10361 | -0.28519 | -0.044861 | -0.14313 | -0.1976 | -0.032043 | 0.064087 | -0.064087 | 0.20142 | 0.15564 | 0.12817 | 0.17853 | 0.14191 | 0.027466 | 0.11902
5121.5 | 0.10681 | 0.4155 | -0.47424 | -0.25848 | -0.20081 | -0.25635 | -0.20508 | 0.073242 | -0.041199 | 0.009155 | 0.036621 | 0.2655 | 0.059509 | 0.20142 | 0.045776 | -0.11322 | -0.27557 | -0.055542 | -0.14847 | -0.19974 | -0.045776 | 0.064087 | -0.073242 | 0.1831 | 0.14648 | 0.14191 | 0.17853 | 0.12817 | 0.018311 | 0.10986
5123.2344 | 0.030518 | 0.41657 | -0.44968 | -0.24567 | -0.21149 | -0.2446 | -0.1944 | 0.1236 | 0.013733 | 0.054932 | 0.050354 | 0.24261 | 0.022888 | 0.18768 | 0.061035 | -0.11108 | -0.27771 | -0.041656 | -0.13992 | -0.18799 | -0.022888 | 0.022888 | -0.073242 | 0.16022 | 0.13733 | 0.10986 | 0.17395 | 0.032043 | 0.068665 | 0.14191
5125 | 0.030518 | 0.38559 | -0.47852 | -0.25742 | -0.19653 | -0.29266 | -0.20294 | 0.091553 | 0.086975 | 0.11902 | 0.086975 | 0.16937 | 0.050354 | 0.19684 | 0.061035 | -0.14313 | -0.27771 | -0.061951 | -0.15595 | -0.19226 | 0.036621 | 0.21057 | 0.036621 | 0.10071 | 0.086975 | 0.1236 | 0.17395 | 0.10071 | 0.041199 | 0.10071
5126.7031 | 0.045776 | 0.35034 | -0.46143 | -0.27664 | -0.21469 | -0.29694 | -0.19226 | 0.068665 | 0.032043 | 0.068665 | 0.059509 | 0.1831 | 0.050354 | 0.19684 | 0.045776 | -0.13138 | -0.29266 | -0.049133 | -0.16235 | -0.19333 | 0.045776 | 0.16937 | 0.045776 | 0.091553 | 0.068665 | 0.13275 | 0.18768 | 0.13733 | 0.054932 | 0.068665
5128.4688 | 0.076294 | 0.35782 | -0.47638 | -0.27023 | -0.21896 | -0.28946 | -0.19867 | 0.050354 | -0.013733 | 0.013733 | 0.027466 | 0.18768 | 0.064087 | 0.20599 | 0.061035 | -0.13138 | -0.28198 | -0.057678 | -0.16129 | -0.19546 | -0.018311 | 0.086975 | -0.009155 | 0.10529 | 0.073242 | 0.13275 | 0.19684 | 0.054932 | 0.091553 | 0.082397
5130.2188 | 0.076294 | 0.41336 | -0.45502 | -0.2446 | -0.20828 | -0.24246 | -0.19226 | 0.10986 | -0.013733 | 0.050354 | 0.082397 | 0.2655 | 0.036621 | 0.17395 | 0.030518 | -0.11002 | -0.28305 | -0.043793 | -0.13351 | -0.19546 | 0.013733 | 0.073242 | -0.036621 | 0.20142 | 0.16937 | 0.1236 | 0.17853 | 0.11902 | 0.018311 | 0.11902
5131.9688 | 0.061035 | 0.36316 | -0.45181 | -0.23605 | -0.20721 | -0.24353 | -0.19974 | 0.12817 | 0.054932 | 0.059509 | 0.07782 | 0.1831 | 0.041199 | 0.18768 | 0.045776 | -0.11749 | -0.28412 | -0.03952 | -0.14206 | -0.20187 | 0.004578 | 0.064087 | 0.009155 | 0.10529 | 0.082397 | 0.10986 | 0.17395 | 0.041199 | 0.09613 | 0.11444
5133.6562 | 0.045776 | 0.35889 | -0.46036 | -0.24139 | -0.20828 | -0.26382 | -0.19333 | 0.09613 | 0.064087 | 0.086975 | 0.068665 | 0.16022 | 0.041199 | 0.18768 | 0.015259 | -0.1239 | -0.28839 | -0.052338 | -0.14099 | -0.19226 | 0.018311 | 0.10529 | 0.027466 | 0.091553 | 0.073242 | 0.12817 | 0.17853 | 0 | 0.11902 | 0.091553
5135.4062 | 0.045776 | 0.36102 | -0.47104 | -0.25742 | -0.20401 | -0.28625 | -0.19653 | 0.022888 | -0.009155 | 0.004578 | 0.018311 | 0.18768 | 0.054932 | 0.21973 | 0.061035 | -0.14099 | -0.29587 | -0.045929 | -0.15915 | -0.18692 | -0.018311 | 0.082397 | -0.009155 | 0.10071 | 0.068665 | 0.14648 | 0.19226 | 0.064087 | 0.11444 | 0.082397
5137.1406 | 0.076294 | 0.34927 | -0.48065 | -0.25635 | -0.20508 | -0.27664 | -0.20081 | 0.064087 | 0.032043 | 0.036621 | 0.027466 | 0.17853 | 0.032043 | 0.20142 | 0.030518 | -0.13458 | -0.28091 | -0.048065 | -0.15381 | -0.20294 | -0.013733 | 0.068665 | -0.009155 | 0.10071 | 0.07782 | 0.1236 | 0.21515 | 0.004578 | 0.11902 | 0.11444
5138.8281 | 0.076294 | 0.41122 | -0.44434 | -0.24674 | -0.19867 | -0.23926 | -0.18799 | 0.064087 | -0.073242 | -0.004578 | 0.027466 | 0.26093 | 0.041199 | 0.19684 | 0.045776 | -0.11108 | -0.28198 | -0.040588 | -0.12711 | -0.20721 | -0.09613 | -0.050354 | -0.11444 | 0.17853 | 0.15564 | 0.11444 | 0.16937 | 0.013733 | 0.082397 | 0.14648
5140.5938 | 0.045776 | 0.3685 | -0.45822 | -0.2446 | -0.22858 | -0.27451 | -0.19974 | 0.10529 | 0.07782 | 0.059509 | 0.050354 | 0.16937 | 0.032043 | 0.19684 | 0.061035 | -0.13138 | -0.30014 | -0.042725 | -0.14954 | -0.19546 | 0.004578 | 0.082397 | -0.018311 | 0.082397 | 0.059509 | 0.1236 | 0.1831 | -0.013733 | 0.11444 | 0.10071
5142.2812 | 0.061035 | 0.36209 | -0.47638 | -0.25421 | -0.21042 | -0.298 | -0.21149 | 0.068665 | 0.064087 | 0.068665 | 0.068665 | 0.19684 | 0.045776 | 0.19226 | 0.030518 | -0.12497 | -0.28946 | -0.054474 | -0.16769 | -0.18906 | 0.064087 | 0.16479 | 0.041199 | 0.10071 | 0.064087 | 0.13275 | 0.19684 | 0.14191 | 0.045776 | 0.064087
5144.0156 | 0.061035 | 0.42084 | -0.44861 | -0.24139 | -0.1976 | -0.23926 | -0.18692 | 0.11902 | -0.027466 | 0.009155 | 0.032043 | 0.24719 | 0.027466 | 0.17395 | 0.045776 | -0.10574 | -0.29053 | -0.045929 | -0.12283 | -0.20294 | -0.064087 | -0.022888 | -0.10986 | 0.16937 | 0.14648 | 0.11902 | 0.17395 | 0 | 0.054932 | 0.15564
5145.7656 | 0.030518 | 0.40802 | -0.47745 | -0.25528 | -0.1944 | -0.2713 | -0.1944 | 0.059509 | -0.036621 | 0.018311 | 0.027466 | 0.25635 | 0.054932 | 0.20599 | 0.030518 | -0.11215 | -0.28732 | -0.05127 | -0.15274 | -0.19226 | -0.050354 | 0.068665 | -0.07782 | 0.1831 | 0.15106 | 0.15106 | 0.17853 | 0.12817 | 0.022888 | 0.12817
5147.4531 | 0.045776 | 0.41657 | -0.45609 | -0.24887 | -0.21149 | -0.24353 | -0.18585 | 0.14191 | 0.041199 | 0.068665 | 0.068665 | 0.25635 | 0.036621 | 0.16937 | 0.045776 | -0.10147 | -0.28732 | -0.05127 | -0.13565 | -0.20187 | 0.018311 | 0.082397 | -0.036621 | 0.16479 | 0.13733 | 0.09613 | 0.16937 | 0.091553 | 0.027466 | 0.11902
5149.2031 | 0.045776 | 0.392 | -0.46463 | -0.24033 | -0.20187 | -0.27878 | -0.1976 | 0.11444 | 0.091553 | 0.10529 | 0.086975 | 0.17853 | 0.050354 | 0.16479 | 0.030518 | -0.12497 | -0.30548 | -0.061951 | -0.15808 | -0.18478 | 0.041199 | 0.20142 | 0.032043 | 0.10986 | 0.082397 | 0.11902 | 0.17395 | 0.10529 | 0.036621 | 0.11902
5150.9531 | 0.076294 | 0.39414 | -0.44006 | -0.24139 | -0.21683 | -0.25742 | -0.1944 | 0.073242 | -0.059509 | -0.009155 | 0.013733 | 0.23804 | 0.045776 | 0.19226 | 0.030518 | -0.11215 | -0.28198 | -0.060883 | -0.13245 | -0.20081 | -0.050354 | -0.022888 | -0.068665 | 0.15106 | 0.14191 | 0.13275 | 0.17395 | 0.073242 | 0.07782 | 0.10986
5152.7031 | 0.091553 | 0.43259 | -0.46356 | -0.26916 | -0.20721 | -0.26596 | -0.20615 | 0.082397 | -0.032043 | 0.036621 | 0.059509 | 0.25635 | 0.036621 | 0.16937 | 0.045776 | -0.11108 | -0.27664 | -0.055542 | -0.15167 | -0.1976 | -0.032043 | 0.068665 | -0.032043 | 0.16022 | 0.16022 | 0.1236 | 0.16479 | 0.13733 | 0.027466 | 0.10986
5154.4062 | 0.091553 | 0.35889 | -0.46356 | -0.27344 | -0.21255 | -0.30121 | -0.20935 | 0.032043 | -0.022888 | 0.018311 | 0.041199 | 0.16479 | 0.045776 | 0.21057 | 0.061035 | -0.13351 | -0.28412 | -0.049133 | -0.1709 | -0.19226 | -0.027466 | 0.082397 | -0.009155 | 0.09613 | 0.064087 | 0.13733 | 0.19684 | 0.041199 | 0.09613 | 0.086975
5156.1406 | 0.061035 | 0.35889 | -0.47531 | -0.25101 | -0.21255 | -0.29373 | -0.21042 | 0.041199 | -0.032043 | 0.013733 | 0.036621 | 0.16937 | 0.050354 | 0.21057 | 0.045776 | -0.13565 | -0.298 | -0.05127 | -0.15167 | -0.19867 | -0.018311 | 0.10071 | 0.009155 | 0.10986 | 0.086975 | 0.14648 | 0.19684 | 0.082397 | 0.10529 | 0.086975
5157.8438 | 0.030518 | 0.38666 | -0.46463 | -0.26703 | -0.20615 | -0.27237 | -0.20508 | 0.11902 | 0.086975 | 0.10986 | 0.086975 | 0.17395 | 0.045776 | 0.17853 | 0.045776 | -0.13565 | -0.28519 | -0.046997 | -0.16129 | -0.20828 | 0.050354 | 0.18768 | 0.032043 | 0.091553 | 0.086975 | 0.11444 | 0.17395 | 0.11902 | 0.045776 | 0.086975
5159.6094 | 0.10681 | 0.35355 | -0.47958 | -0.2446 | -0.21576 | -0.27664 | -0.20721 | 0.07782 | 0.009155 | 0.027466 | 0.041199 | 0.17395 | 0.054932 | 0.17853 | 0.061035 | -0.11856 | -0.30014 | -0.054474 | -0.15381 | -0.19974 | -0.027466 | 0.068665 | -0.018311 | 0.082397 | 0.068665 | 0.13733 | 0.18768 | 0.004578 | 0.11902 | 0.091553
5161.2969 | 0.030518 | 0.40588 | -0.45395 | -0.24246 | -0.21362 | -0.22964 | -0.19546 | 0.09613 | -0.054932 | -0.027466 | 0.027466 | 0.25635 | 0.009155 | 0.1831 | 0.045776 | -0.11002 | -0.27237 | -0.05127 | -0.13565 | -0.21469 | -0.064087 | -0.059509 | -0.073242 | 0.16937 | 0.11444 | 0.11444 | 0.19226 | 0.045776 | 0.073242 | 0.14191
5163.0469 | 0.076294 | 0.41657 | -0.44861 | -0.25101 | -0.21255 | -0.24674 | -0.19226 | 0.13733 | 0.041199 | 0.082397 | 0.086975 | 0.23346 | 0.027466 | 0.15564 | 0.045776 | -0.11322 | -0.28625 | -0.046997 | -0.14206 | -0.20508 | 0.018311 | 0.086975 | -0.027466 | 0.16022 | 0.12817 | 0.10071 | 0.15106 | 0.11444 | 0.022888 | 0.10529
5164.8125 | 0.045776 | 0.41977 | -0.44861 | -0.25207 | -0.21255 | -0.24353 | -0.19119 | 0.07782 | -0.036621 | 0 | 0.041199 | 0.23804 | 0.032043 | 0.1831 | 0.061035 | -0.10895 | -0.28198 | -0.036316 | -0.13992 | -0.18906 | -0.09613 | -0.027466 | -0.11444 | 0.17853 | 0.16022 | 0.11902 | 0.17395 | 0.009155 | 0.068665 | 0.13733
5166.5156 | 0.045776 | 0.37277 | -0.45395 | -0.24139 | -0.20828 | -0.26169 | -0.19974 | 0.082397 | 0 | 0.027466 | 0.045776 | 0.21973 | 0.022888 | 0.17395 | 0.061035 | -0.12604 | -0.27771 | -0.046997 | -0.13886 | -0.18585 | -0.009155 | 0.045776 | 0 | 0.073242 | 0.082397 | 0.09613 | 0.15106 | 0.050354 | 0.091553 | 0.10529
5168.2656 | 0.030518 | 0.39627 | -0.48813 | -0.25635 | -0.20401 | -0.27557 | -0.1976 | 0.07782 | 0.027466 | 0.07782 | 0.064087 | 0.20599 | 0.045776 | 0.19684 | 0.030518 | -0.13351 | -0.28412 | -0.060883 | -0.15595 | -0.18585 | -0.013733 | 0.10071 | -0.054932 | 0.13733 | 0.13733 | 0.1236 | 0.1831 | 0.07782 | 0.032043 | 0.11444
5169.9375 | 0.045776 | 0.36423 | -0.45288 | -0.24246 | -0.19546 | -0.27023 | -0.19119 | 0.1236 | 0.059509 | 0.064087 | 0.091553 | 0.17395 | 0.018311 | 0.15564 | 0.045776 | -0.1207 | -0.28412 | -0.05661 | -0.14526 | -0.19226 | 0 | 0.082397 | 0.013733 | 0.091553 | 0.059509 | 0.09613 | 0.18768 | 0.041199 | 0.07782 | 0.07782
5171.6875 | 0.076294 | 0.42297 | -0.45715 | -0.24994 | -0.19333 | -0.25101 | -0.18692 | 0.13733 | 0.013733 | 0.07782 | 0.086975 | 0.23804 | 0.018311 | 0.17395 | 0.045776 | -0.10681 | -0.28519 | -0.045929 | -0.13779 | -0.20508 | 0.013733 | 0.082397 | -0.036621 | 0.16479 | 0.12817 | 0.091553 | 0.16479 | 0.10529 | 0.032043 | 0.13275
5173.375 | 0.076294 | 0.40482 | -0.45288 | -0.24674 | -0.19974 | -0.24887 | -0.19226 | 0.050354 | -0.091553 | -0.036621 | 0.022888 | 0.25635 | 0.013733 | 0.16937 | 0.030518 | -0.10468 | -0.2948 | -0.048065 | -0.13138 | -0.19226 | -0.07782 | -0.050354 | -0.10529 | 0.15564 | 0.15564 | 0.11444 | 0.17853 | 0 | 0.091553 | 0.13275
5175.125 | 0.076294 | 0.40161 | -0.4689 | -0.26596 | -0.20508 | -0.29694 | -0.20081 | 0.091553 | 0.054932 | 0.09613 | 0.068665 | 0.1831 | 0.036621 | 0.17395 | 0.045776 | -0.13565 | -0.27237 | -0.044861 | -0.16022 | -0.20187 | 0.004578 | 0.16479 | 0 | 0.11444 | 0.10071 | 0.1236 | 0.16937 | 0.09613 | 0.018311 | 0.11444
5176.8906 | 0.061035 | 0.40161 | -0.46249 | -0.24246 | -0.21362 | -0.25848 | -0.1944 | 0.054932 | -0.086975 | -0.032043 | 0.027466 | 0.25177 | 0.045776 | 0.17395 | 0.015259 | -0.11856 | -0.29159 | -0.036316 | -0.13672 | -0.20828 | -0.091553 | -0.054932 | -0.086975 | 0.17853 | 0.14648 | 0.11902 | 0.15106 | 0.013733 | 0.07782 | 0.13275
5178.5781 | 0.045776 | 0.36636 | -0.45715 | -0.23392 | -0.20187 | -0.2681 | -0.19546 | 0.13733 | 0.050354 | 0.073242 | 0.07782 | 0.16479 | 0.018311 | 0.18768 | 0.061035 | -0.12817 | -0.2948 | -0.057678 | -0.14526 | -0.20187 | 0.009155 | 0.10986 | 0.041199 | 0.073242 | 0.068665 | 0.1236 | 0.15106 | 0.027466 | 0.10529 | 0.082397
5180.3281 | 0.10681 | 0.42297 | -0.4689 | -0.24567 | -0.21362 | -0.26169 | -0.20187 | 0.10071 | 0 | 0.064087 | 0.068665 | 0.25177 | 0.032043 | 0.19226 | 0.030518 | -0.10574 | -0.28839 | -0.05661 | -0.14313 | -0.21042 | -0.013733 | 0.082397 | -0.041199 | 0.16479 | 0.15564 | 0.11444 | 0.16937 | 0.16022 | -0.009155 | 0.13275
5182.0625 | 0.045776 | 0.41443 | -0.47104 | -0.28198 | -0.21576 | -0.27557 | -0.20401 | 0.032043 | -0.027466 | 0.027466 | 0.027466 | 0.24719 | 0.050354 | 0.22888 | 0.061035 | -0.12283 | -0.2713 | -0.041656 | -0.15915 | -0.19867 | -0.036621 | 0.07782 | -0.054932 | 0.16937 | 0.16937 | 0.10529 | 0.16022 | 0.10529 | 0.027466 | 0.1236
5183.75 | 0.045776 | 0.41336 | -0.44434 | -0.26062 | -0.20187 | -0.25314 | -0.1976 | 0.10529 | 0.004578 | 0.050354 | 0.068665 | 0.24719 | 0.027466 | 0.16022 | 0.045776 | -0.10147 | -0.27771 | -0.049133 | -0.13992 | -0.19653 | -0.045776 | 0.009155 | -0.064087 | 0.14648 | 0.14191 | 0.11902 | 0.16479 | 0 | 0.073242 | 0.14648
5185.5 | 0.045776 | 0.40588 | -0.46997 | -0.26916 | -0.22217 | -0.27344 | -0.20081 | 0.050354 | -0.041199 | 0.013733 | 0.041199 | 0.26093 | 0.041199 | 0.19684 | 0.061035 | -0.11429 | -0.27771 | -0.05661 | -0.15488 | -0.19546 | -0.059509 | 0.059509 | -0.082397 | 0.16479 | 0.14191 | 0.12817 | 0.16937 | 0.13275 | 0.009155 | 0.10071
5187.2344 | 0.10681 | 0.41443 | -0.46249 | -0.27023 | -0.20721 | -0.26382 | -0.17838 | 0.073242 | -0.009155 | 0.032043 | 0.073242 | 0.25177 | 0.045776 | 0.17395 | 0.061035 | -0.11536 | -0.27451 | -0.03952 | -0.14099 | -0.19974 | -0.032043 | 0.082397 | -0.041199 | 0.18768 | 0.15564 | 0.09613 | 0.16022 | 0.14191 | 0.004578 | 0.10071
5188.9844 | 0.045776 | 0.39948 | -0.45502 | -0.24246 | -0.20935 | -0.24887 | -0.1944 | 0.059509 | -0.068665 | -0.018311 | 0.027466 | 0.24719 | 0.027466 | 0.16937 | 0.045776 | -0.10468 | -0.29159 | -0.048065 | -0.1442 | -0.20187 | -0.086975 | -0.050354 | -0.086975 | 0.17395 | 0.15564 | 0.1236 | 0.17395 | 0.036621 | 0.07782 | 0.13733
5190.75 | 0.091553 | 0.4187 | -0.44968 | -0.24353 | -0.21255 | -0.25101 | -0.1944 | 0.11444 | 0.018311 | 0.07782 | 0.073242 | 0.24719 | 0.013733 | 0.17853 | 0.045776 | -0.11322 | -0.29266 | -0.043793 | -0.13351 | -0.20187 | -0.004578 | 0.073242 | -0.032043 | 0.17853 | 0.15564 | 0.086975 | 0.16022 | 0.10529 | 0.009155 | 0.1236
5192.4531 | 0.030518 | 0.36743 | -0.45609 | -0.24994 | -0.22217 | -0.27985 | -0.19653 | 0.1236 | 0.045776 | 0.07782 | 0.082397 | 0.1831 | 0.041199 | 0.19226 | 0.076294 | -0.13458 | -0.29053 | -0.058746 | -0.15167 | -0.19974 | 0.009155 | 0.10986 | 0.032043 | 0.091553 | 0.07782 | 0.11902 | 0.17853 | 0 | 0.10529 | 0.11444
5194.2031 | 0.045776 | 0.38238 | -0.44754 | -0.25207 | -0.20187 | -0.26062 | -0.20187 | 0.073242 | -0.073242 | -0.022888 | 0.022888 | 0.24719 | 0.032043 | 0.17853 | 0.015259 | -0.11963 | -0.29694 | -0.054474 | -0.13886 | -0.20081 | -0.091553 | -0.045776 | -0.07782 | 0.16022 | 0.1236 | 0.11902 | 0.18768 | 0.041199 | 0.082397 | 0.10986
5195.9062 | 0.061035 | 0.34286 | -0.45822 | -0.26596 | -0.20721 | -0.28519 | -0.20508 | 0.091553 | 0.036621 | 0.041199 | 0.045776 | 0.16479 | 0.013733 | 0.19684 | 0.045776 | -0.13886 | -0.27878 | -0.050201 | -0.15915 | -0.19226 | -0.009155 | 0.073242 | 0.009155 | 0.073242 | 0.082397 | 0.12817 | 0.18768 | -0.004578 | 0.10986 | 0.10071
5197.6719 | 0.061035 | 0.36102 | -0.47745 | -0.27664 | -0.1976 | -0.29053 | -0.21362 | 0.064087 | 0.027466 | 0.059509 | 0.054932 | 0.17853 | 0.054932 | 0.18768 | 0.045776 | -0.12604 | -0.28091 | -0.065155 | -0.16663 | -0.19867 | 0.022888 | 0.16022 | 0.050354 | 0.10986 | 0.07782 | 0.13275 | 0.17853 | 0.13275 | 0.050354 | 0.059509
5199.375 | 0.045776 | 0.36316 | -0.46249 | -0.26276 | -0.21576 | -0.27878 | -0.21362 | 0.064087 | 0 | 0.018311 | 0.032043 | 0.17853 | 0.032043 | 0.1831 | 0.045776 | -0.12817 | -0.28519 | -0.049133 | -0.15274 | -0.19546 | -0.018311 | 0.059509 | -0.027466 | 0.082397 | 0.059509 | 0.11444 | 0.19226 | 0.022888 | 0.10071 | 0.10071
5201.125 | 0.045776 | 0.41657 | -0.45075 | -0.27557 | -0.20081 | -0.2478 | -0.20508 | 0.073242 | -0.027466 | 0.036621 | 0.059509 | 0.26093 | 0.041199 | 0.18768 | 0.045776 | -0.10681 | -0.27451 | -0.043793 | -0.14206 | -0.21362 | -0.027466 | 0.064087 | -0.041199 | 0.18768 | 0.17853 | 0.10529 | 0.16937 | 0.14191 | 0.032043 | 0.09613
5202.8594 | 0.061035 | 0.37705 | -0.45075 | -0.23712 | -0.21042 | -0.25528 | -0.20187 | 0.091553 | 0 | 0.022888 | 0.041199 | 0.20599 | 0.013733 | 0.1831 | 0.076294 | -0.11429 | -0.28839 | -0.040588 | -0.12604 | -0.19333 | 0 | 0.050354 | 0.009155 | 0.11902 | 0.086975 | 0.10986 | 0.14648 | 0.054932 | 0.10071 | 0.09613
5204.5625 | 0.045776 | 0.40054 | -0.48386 | -0.27451 | -0.19867 | -0.2681 | -0.19974 | 0.073242 | 0.018311 | 0.064087 | 0.054932 | 0.17853 | 0.032043 | 0.19684 | 0.061035 | -0.12176 | -0.27237 | -0.048065 | -0.16342 | -0.20081 | -0.032043 | 0.09613 | -0.064087 | 0.16022 | 0.1236 | 0.13275 | 0.17853 | 0.091553 | 0.027466 | 0.1236
5206.3125 | 0.076294 | 0.35568 | -0.47424 | -0.25314 | -0.20721 | -0.27344 | -0.20508 | 0.036621 | 0 | 0.018311 | 0.027466 | 0.1831 | 0.054932 | 0.20599 | 0.030518 | -0.13992 | -0.29587 | -0.046997 | -0.16022 | -0.19974 | -0.032043 | 0.064087 | -0.004578 | 0.09613 | 0.082397 | 0.1236 | 0.19684 | 0.045776 | 0.10529 | 0.082397
5208.0469 | 0.045776 | 0.39627 | -0.45288 | -0.25528 | -0.1976 | -0.24567 | -0.18372 | 0.11444 | 0.013733 | 0.059509 | 0.073242 | 0.25635 | 0.027466 | 0.19226 | 0.045776 | -0.10468 | -0.29053 | -0.044861 | -0.13245 | -0.20401 | -0.013733 | 0.073242 | -0.036621 | 0.16937 | 0.12817 | 0.1236 | 0.17395 | 0.13275 | 0.004578 | 0.13275
5209.7969 | 0.045776 | 0.36102 | -0.48279 | -0.26062 | -0.2211 | -0.27985 | -0.19546 | 0.050354 | 0.009155 | 0.013733 | 0.018311 | 0.16479 | 0.032043 | 0.20142 | 0.061035 | -0.13992 | -0.29373 | -0.057678 | -0.16235 | -0.18158 | -0.045776 | 0.054932 | -0.022888 | 0.091553 | 0.059509 | 0.13275 | 0.18768 | 0.027466 | 0.09613 | 0.091553
5211.5625 | 0 | 0.37384 | -0.44861 | -0.23605 | -0.21683 | -0.26596 | -0.19226 | 0.13275 | 0.064087 | 0.064087 | 0.068665 | 0.16937 | 0.036621 | 0.15564 | 0.045776 | -0.11643 | -0.298 | -0.055542 | -0.14313 | -0.1976 | 0.013733 | 0.09613 | 0.022888 | 0.082397 | 0.068665 | 0.11902 | 0.17395 | 0.004578 | 0.11444 | 0.10986
5213.25 | 0.045776 | 0.40482 | -0.4422 | -0.26703 | -0.20828 | -0.24674 | -0.19226 | 0.13733 | 0.018311 | 0.07782 | 0.073242 | 0.24261 | 0.009155 | 0.18768 | 0.061035 | -0.11322 | -0.26276 | -0.060883 | -0.13779 | -0.19974 | -0.022888 | 0.045776 | -0.07782 | 0.15564 | 0.1236 | 0.10529 | 0.16937 | 0.027466 | 0.059509 | 0.1236
5215.0156 | 0.030518 | 0.35782 | -0.45929 | -0.23712 | -0.21255 | -0.27771 | -0.19333 | 0.11902 | 0.068665 | 0.073242 | 0.068665 | 0.16479 | 0.041199 | 0.1831 | 0.045776 | -0.13565 | -0.298 | -0.044861 | -0.15274 | -0.20615 | 0.013733 | 0.091553 | 0.013733 | 0.068665 | 0.050354 | 0.13733 | 0.17395 | -0.027466 | 0.091553 | 0.10071
5216.7188 | 0.015259 | 0.42618 | -0.4422 | -0.23819 | -0.20828 | -0.23926 | -0.19226 | 0.10071 | -0.013733 | 0.041199 | 0.050354 | 0.25177 | 0.018311 | 0.16937 | 0.030518 | -0.097198 | -0.29373 | -0.045929 | -0.14099 | -0.20081 | -0.07782 | -0.036621 | -0.10071 | 0.16022 | 0.14191 | 0.10529 | 0.16022 | 0.004578 | 0.082397 | 0.14648
5218.4844 | 0.076294 | 0.37277 | -0.4657 | -0.24887 | -0.20294 | -0.28732 | -0.18478 | 0.068665 | 0.032043 | 0.036621 | 0.032043 | 0.16479 | 0.045776 | 0.17853 | 0.045776 | -0.13565 | -0.30121 | -0.05661 | -0.15595 | -0.18585 | -0.013733 | 0.073242 | -0.009155 | 0.064087 | 0.068665 | 0.10986 | 0.16479 | 0.004578 | 0.10529 | 0.10071
5220.1719 | 0.10681 | 0.36209 | -0.4689 | -0.26916 | -0.21469 | -0.27878 | -0.20401 | 0.082397 | 0.022888 | 0.041199 | 0.032043 | 0.16479 | 0.054932 | 0.19226 | 0.045776 | -0.13351 | -0.28305 | -0.057678 | -0.16769 | -0.18906 | -0.009155 | 0.073242 | -0.013733 | 0.10529 | 0.050354 | 0.12817 | 0.16022 | 0.009155 | 0.11444 | 0.082397
5221.9375 | 0.045776 | 0.35675 | -0.46143 | -0.25848 | -0.21362 | -0.28519 | -0.20508 | 0.045776 | -0.004578 | 0.022888 | 0.050354 | 0.1831 | 0.045776 | 0.18768 | 0.045776 | -0.13031 | -0.28946 | -0.057678 | -0.15488 | -0.20081 | 0 | 0.11444 | 0 | 0.10529 | 0.091553 | 0.11902 | 0.1831 | 0.09613 | 0.059509 | 0.073242
5223.6875 | 0.045776 | 0.38025 | -0.45075 | -0.23926 | -0.20401 | -0.23819 | -0.19119 | 0.07782 | -0.050354 | -0.027466 | 0.027466 | 0.23804 | 0.032043 | 0.19226 | 0.045776 | -0.10895 | -0.28091 | -0.037384 | -0.13779 | -0.21042 | -0.07782 | -0.045776 | -0.07782 | 0.17853 | 0.13733 | 0.091553 | 0.17853 | 0.045776 | 0.091553 | 0.10071
5225.3906 | 0.030518 | 0.36423 | -0.4657 | -0.24674 | -0.1976 | -0.26382 | -0.18478 | 0.12817 | 0.050354 | 0.059509 | 0.10071 | 0.18768 | 0.022888 | 0.17853 | 0.061035 | -0.11536 | -0.29587 | -0.046997 | -0.14099 | -0.20615 | 0.018311 | 0.059509 | 0.009155 | 0.10071 | 0.068665 | 0.10529 | 0.15564 | 0.054932 | 0.07782 | 0.10529
5227.1406 | 0.061035 | 0.36636 | -0.4689 | -0.23819 | -0.20508 | -0.26062 | -0.19546 | 0.10986 | 0.07782 | 0.07782 | 0.086975 | 0.15106 | 0.022888 | 0.15564 | 0.030518 | -0.12711 | -0.28091 | -0.052338 | -0.13351 | -0.19653 | 0.022888 | 0.09613 | 0.022888 | 0.086975 | 0.041199 | 0.10529 | 0.15564 | 0.045776 | 0.10529 | 0.054932
5228.8281 | 0.091553 | 0.35996 | -0.46356 | -0.25848 | -0.21042 | -0.2713 | -0.20508 | 0.068665 | 0.041199 | 0.041199 | 0.054932 | 0.14648 | 0.027466 | 0.17395 | 0.030518 | -0.13565 | -0.28519 | -0.05127 | -0.15274 | -0.19333 | -0.009155 | 0.07782 | -0.018311 | 0.07782 | 0.064087 | 0.1236 | 0.16937 | 0.009155 | 0.10986 | 0.091553
5230.5938 | 0.076294 | 0.41016 | -0.45075 | -0.25314 | -0.21255 | -0.23605 | -0.19333 | 0.10986 | 0.013733 | 0.041199 | 0.073242 | 0.22888 | 0.027466 | 0.16479 | 0.061035 | -0.11215 | -0.27771 | -0.046997 | -0.1239 | -0.20294 | -0.050354 | 0.004578 | -0.086975 | 0.16022 | 0.1236 | 0.09613 | 0.15564 | 0.004578 | 0.064087 | 0.14648
5232.3438 | 0.015259 | 0.35782 | -0.46356 | -0.25421 | -0.21149 | -0.30014 | -0.21683 | 0.07782 | 0.041199 | 0.064087 | 0.068665 | 0.17395 | 0.032043 | 0.19226 | 0.045776 | -0.13672 | -0.28625 | -0.05127 | -0.16769 | -0.20081 | 0.054932 | 0.17395 | 0.041199 | 0.091553 | 0.07782 | 0.10986 | 0.17395 | 0.15106 | 0.045776 | 0.059509
5234.0156 | 0.045776 | 0.3685 | -0.47424 | -0.27557 | -0.19119 | -0.27664 | -0.19333 | 0.11444 | 0.10071 | 0.1236 | 0.086975 | 0.1831 | 0.041199 | 0.17395 | 0.045776 | -0.13138 | -0.28305 | -0.059814 | -0.16876 | -0.19546 | 0.050354 | 0.20142 | 0.022888 | 0.10071 | 0.07782 | 0.11444 | 0.16022 | 0.091553 | 0.041199 | 0.09613
5235.7812 | 0 | 0.38132 | -0.48065 | -0.25421 | -0.20294 | -0.28519 | -0.19546 | 0.045776 | -0.009155 | 0.022888 | 0.036621 | 0.16937 | 0.064087 | 0.19226 | 0.061035 | -0.12497 | -0.29373 | -0.052338 | -0.15595 | -0.19012 | -0.013733 | 0.10071 | 0 | 0.086975 | 0.086975 | 0.14191 | 0.1831 | 0.086975 | 0.073242 | 0.064087
5237.5312 | 0.061035 | 0.36423 | -0.4689 | -0.25635 | -0.20935 | -0.26489 | -0.20294 | 0.07782 | 0.013733 | 0.022888 | 0.036621 | 0.14648 | 0.036621 | 0.19226 | 0.030518 | -0.13031 | -0.28305 | -0.058746 | -0.14313 | -0.19974 | -0.004578 | 0.059509 | -0.022888 | 0.09613 | 0.068665 | 0.12817 | 0.16937 | 0.018311 | 0.09613 | 0.082397
5239.2188 | 0.045776 | 0.40054 | -0.45822 | -0.26276 | -0.20828 | -0.2478 | -0.20935 | 0.082397 | -0.036621 | 0.018311 | 0.050354 | 0.24261 | 0.027466 | 0.1831 | 0.045776 | -0.10681 | -0.28946 | -0.048065 | -0.14313 | -0.21255 | -0.032043 | 0.064087 | -0.07782 | 0.17395 | 0.14191 | 0.10529 | 0.1831 | 0.15564 | 0.018311 | 0.11444
5240.9219 | 0.061035 | 0.42511 | -0.46356 | -0.27344 | -0.21255 | -0.26062 | -0.20401 | 0.050354 | -0.018311 | 0.027466 | 0.036621 | 0.24261 | 0.036621 | 0.17853 | 0.015259 | -0.11963 | -0.28305 | -0.050201 | -0.16022 | -0.19546 | -0.022888 | 0.082397 | -0.054932 | 0.16937 | 0.14648 | 0.11444 | 0.17395 | 0.086975 | 0.018311 | 0.11444
5242.6719 | 0.061035 | 0.36957 | -0.44647 | -0.23605 | -0.19333 | -0.25528 | -0.1944 | 0.10529 | 0 | 0.013733 | 0.064087 | 0.21515 | 0.032043 | 0.15564 | 0.061035 | -0.11108 | -0.28946 | -0.033112 | -0.13992 | -0.20401 | 0.009155 | 0.059509 | -0.004578 | 0.09613 | 0.068665 | 0.091553 | 0.14648 | 0.059509 | 0.09613 | 0.091553
5244.3594 | 0.061035 | 0.36209 | -0.44647 | -0.24033 | -0.20935 | -0.24994 | -0.18478 | 0.13275 | 0.036621 | 0.050354 | 0.07782 | 0.19226 | 0.032043 | 0.16022 | 0.030518 | -0.10574 | -0.2948 | -0.057678 | -0.13458 | -0.20721 | 0.022888 | 0.068665 | 0.018311 | 0.086975 | 0.1236 | 0.11902 | 0.19226 | 0.068665 | 0.086975 | 0.10071
5246.125 | 0.045776 | 0.40054 | -0.44434 | -0.24246 | -0.19867 | -0.25955 | -0.19333 | 0.054932 | -0.050354 | -0.022888 | 0.027466 | 0.25177 | 0.032043 | 0.16479 | 0.030518 | -0.10254 | -0.28198 | -0.037384 | -0.13031 | -0.19546 | -0.064087 | -0.059509 | -0.086975 | 0.16479 | 0.13733 | 0.11444 | 0.16479 | 0.041199 | 0.091553 | 0.11444
5247.8125 | 0.030518 | 0.4155 | -0.46249 | -0.25207 | -0.19867 | -0.2478 | -0.18692 | 0.10071 | 0.013733 | 0.041199 | 0.064087 | 0.21515 | 0.018311 | 0.17395 | 0.045776 | -0.10147 | -0.28625 | -0.038452 | -0.13886 | -0.19974 | -0.050354 | -0.004578 | -0.07782 | 0.16022 | 0.13275 | 0.10529 | 0.16479 | 0.009155 | 0.045776 | 0.14191
5249.5625 | 0.1831 | 0.41229 | -0.4657 | -0.26276 | -0.20508 | -0.28519 | -0.20401 | 0.041199 | -0.013733 | 0.027466 | 0.009155 | 0.23804 | 0.045776 | 0.18768 | 0.030518 | -0.12497 | -0.27664 | -0.046997 | -0.15274 | -0.20187 | -0.041199 | 0.073242 | -0.059509 | 0.17395 | 0.15564 | 0.10986 | 0.17395 | 0.12817 | 0.032043 | 0.1236
5251.3125 | 0.13733 | 0.36316 | -0.46997 | -0.24353 | -0.21469 | -0.29907 | -0.19546 | 0.064087 | 0.022888 | 0.022888 | 0.032043 | 0.17853 | 0.041199 | 0.19226 | 0.091553 | -0.13245 | -0.30334 | -0.049133 | -0.16769 | -0.19226 | -0.032043 | 0.073242 | -0.004578 | 0.073242 | 0.086975 | 0.12817 | 0.19684 | -0.004578 | 0.11902 | 0.086975
5253.0781 | 0.091553 | 0.34286 | -0.46677 | -0.26062 | -0.20828 | -0.28732 | -0.21362 | 0.045776 | -0.018311 | 0.009155 | 0.027466 | 0.16937 | 0.045776 | 0.17853 | 0.045776 | -0.12817 | -0.28625 | -0.046997 | -0.15488 | -0.19546 | -0.045776 | 0.073242 | -0.013733 | 0.086975 | 0.082397 | 0.15106 | 0.17853 | 0.041199 | 0.086975 | 0.064087
5254.8438 | 0.045776 | 0.36957 | -0.45502 | -0.25742 | -0.21469 | -0.25314 | -0.19867 | 0.091553 | -0.018311 | 0.022888 | 0.041199 | 0.20599 | 0.022888 | 0.16937 | 0.061035 | -0.11002 | -0.27771 | -0.03952 | -0.1442 | -0.20935 | -0.013733 | 0.022888 | -0.009155 | 0.11902 | 0.082397 | 0.091553 | 0.16937 | 0.050354 | 0.07782 | 0.091553
5256.5312 | 0.045776 | 0.36102 | -0.46677 | -0.25742 | -0.22003 | -0.28412 | -0.19974 | 0.073242 | 0.027466 | 0.059509 | 0.054932 | 0.1831 | 0.022888 | 0.17853 | 0.045776 | -0.13672 | -0.28091 | -0.043793 | -0.16663 | -0.20721 | 0.032043 | 0.14648 | 0.027466 | 0.086975 | 0.073242 | 0.13733 | 0.18768 | 0.13275 | 0.045776 | 0.068665
5258.2812 | 0.045776 | 0.40802 | -0.48386 | -0.25421 | -0.21576 | -0.25848 | -0.20081 | 0.086975 | 0.009155 | 0.054932 | 0.059509 | 0.21057 | 0.041199 | 0.16937 | 0.030518 | -0.10681 | -0.298 | -0.049133 | -0.15595 | -0.19653 | -0.022888 | 0.07782 | -0.064087 | 0.14648 | 0.1236 | 0.12817 | 0.16937 | 0.086975 | 0.036621 | 0.10529
5259.9844 | 0.30518 | 0.41122 | -0.47852 | -0.26169 | -0.20935 | -0.24674 | -0.1976 | 0.07782 | -0.027466 | 0.018311 | 0.041199 | 0.24261 | 0.027466 | 0.18768 | 0.015259 | -0.11215 | -0.27023 | -0.044861 | -0.15167 | -0.19226 | -0.045776 | 0.050354 | -0.07782 | 0.1831 | 0.13275 | 0.11444 | 0.17853 | 0.17395 | 0.018311 | 0.10529
5261.7344 | 0.12207 | 0.35141 | -0.46356 | -0.24887 | -0.21683 | -0.28732 | -0.20081 | 0.022888 | 0 | 0.013733 | 0.036621 | 0.18768 | 0.036621 | 0.19684 | 0.045776 | -0.13779 | -0.28198 | -0.053406 | -0.16129 | -0.19119 | -0.013733 | 0.091553 | 0.004578 | 0.10986 | 0.064087 | 0.13733 | 0.1831 | 0.09613 | 0.09613 | 0.059509
5263.4219 | 0.045776 | 0.35461 | -0.46677 | -0.26169 | -0.21149 | -0.2713 | -0.20615 | 0.073242 | 0.041199 | 0.050354 | 0.059509 | 0.17395 | 0.036621 | 0.19226 | 0.030518 | -0.12817 | -0.28412 | -0.054474 | -0.16342 | -0.19546 | 0.041199 | 0.16022 | 0.036621 | 0.091553 | 0.073242 | 0.1236 | 0.17853 | 0.13733 | 0.045776 | 0.068665
5265.1562 | 0.045776 | 0.36209 | -0.46143 | -0.26916 | -0.20615 | -0.28198 | -0.20935 | 0.12817 | 0.086975 | 0.11902 | 0.07782 | 0.16479 | 0.022888 | 0.19226 | 0.045776 | -0.12817 | -0.28625 | -0.054474 | -0.16022 | -0.20187 | 0.054932 | 0.20142 | 0.032043 | 0.09613 | 0.045776 | 0.12817 | 0.15564 | 0.10529 | 0.073242 | 0.086975
5266.8594 | 0.1831 | 0.35355 | -0.45288 | -0.22858 | -0.2179 | -0.25848 | -0.21149 | 0.11444 | 0.059509 | 0.064087 | 0.068665 | 0.14648 | 0.032043 | 0.17853 | 0.045776 | -0.12283 | -0.28412 | -0.044861 | -0.13992 | -0.21896 | 0.059509 | 0.12817 | 0.054932 | 0.10986 | 0.073242 | 0.15106 | 0.19226 | 0.018311 | 0.10529 | 0.10071
5268.6406 | 0.091553 | 0.41336 | -0.46249 | -0.24674 | -0.1976 | -0.24139 | -0.1976 | 0.12817 | 0.045776 | 0.059509 | 0.073242 | 0.24719 | 0.032043 | 0.16479 | 0.045776 | -0.11322 | -0.29694 | -0.042725 | -0.12817 | -0.20721 | 0.022888 | 0.091553 | -0.036621 | 0.16479 | 0.11902 | 0.10071 | 0.16479 | 0.1236 | 0.022888 | 0.11444
5270.3281 | 0.030518 | 0.41977 | -0.46997 | -0.26169 | -0.21255 | -0.26703 | -0.18906 | 0.059509 | 0.009155 | 0.036621 | 0.036621 | 0.20599 | 0.050354 | 0.19684 | 0.045776 | -0.12176 | -0.28091 | -0.054474 | -0.15595 | -0.21149 | 0 | 0.091553 | -0.059509 | 0.14648 | 0.13275 | 0.1236 | 0.18768 | 0.091553 | 0.032043 | 0.11444
5272.0156 | 0.19836 | 0.36423 | -0.4454 | -0.2446 | -0.21255 | -0.26169 | -0.1944 | 0.13275 | 0.064087 | 0.054932 | 0.086975 | 0.16022 | -0.009155 | 0.19226 | 0.015259 | -0.10681 | -0.30228 | -0.03418 | -0.12497 | -0.17838 | 0.059509 | 0.12817 | 0.073242 | 0.1236 | 0.10986 | 0.16937 | 0.20142 | 0.036621 | 0.091553 | 0.086975
5273.7812 | 0.061035 | 0.36957 | -0.46143 | -0.24246 | -0.1976 | -0.25314 | -0.19333 | 0.12817 | 0.041199 | 0.045776 | 0.086975 | 0.17853 | 0.013733 | 0.16937 | 0.045776 | -0.11536 | -0.28946 | -0.049133 | -0.14847 | -0.20081 | -0.004578 | 0.068665 | 0.004578 | 0.082397 | 0.11444 | 0.15106 | 0.19226 | 0.059509 | 0.082397 | 0.091553
5275.4844 | 0.1831 | 0.36316 | -0.4657 | -0.25528 | -0.22003 | -0.27878 | -0.19653 | 0.09613 | 0.045776 | 0.041199 | 0.050354 | 0.1236 | 0.050354 | 0.18768 | 0.030518 | -0.13351 | -0.29053 | -0.052338 | -0.15808 | -0.1944 | 0.022888 | 0.09613 | 0.022888 | 0.11902 | 0.082397 | 0.15564 | 0.20599 | 0 | 0.10986 | 0.073242
5277.2344 | 0.045776 | 0.35889 | -0.45609 | -0.25635 | -0.21362 | -0.28839 | -0.19333 | 0.064087 | 0.041199 | 0.032043 | 0.068665 | 0.17395 | 0.027466 | 0.17853 | 0.030518 | -0.12604 | -0.29587 | -0.066223 | -0.15595 | -0.19333 | 0 | 0.13733 | 0.032043 | 0.10529 | 0.068665 | 0.11444 | 0.17395 | 0.13275 | 0.059509 | 0.050354
5279 | 0.045776 | 0.40054 | -0.45288 | -0.26169 | -0.21042 | -0.23285 | -0.19333 | 0.12817 | -0.009155 | 0.050354 | 0.064087 | 0.24261 | 0.027466 | 0.16022 | 0.030518 | -0.099335 | -0.28198 | -0.041656 | -0.1239 | -0.21042 | -0.013733 | 0.013733 | -0.073242 | 0.15564 | 0.13275 | 0.1236 | 0.16022 | 0.022888 | 0.073242 | 0.12817
5280.75 | 0.045776 | 0.41336 | -0.47958 | -0.25742 | -0.21255 | -0.26489 | -0.19867 | 0.086975 | 0.018311 | 0.032043 | 0.045776 | 0.21515 | 0.036621 | 0.17395 | 0.045776 | -0.1239 | -0.28519 | -0.052338 | -0.15274 | -0.19333 | -0.036621 | 0.10071 | -0.050354 | 0.15564 | 0.1236 | 0.11902 | 0.17395 | 0.07782 | 0.036621 | 0.10986
5282.4375 | 0.21362 | 0.42404 | -0.48172 | -0.25848 | -0.21683 | -0.26382 | -0.20401 | 0.059509 | -0.036621 | 0.022888 | 0.027466 | 0.23804 | 0.032043 | 0.19226 | 0.030518 | -0.10468 | -0.28732 | -0.050201 | -0.14847 | -0.20721 | -0.045776 | 0.050354 | -0.068665 | 0.16937 | 0.13275 | 0.11444 | 0.15564 | 0.16022 | 0.027466 | 0.10986
5284.1875 | 0.1831 | 0.4187 | -0.46677 | -0.2681 | -0.20081 | -0.26703 | -0.19974 | 0.050354 | -0.027466 | 0.027466 | 0.032043 | 0.25177 | 0.045776 | 0.16022 | 0.045776 | -0.11643 | -0.28946 | -0.050201 | -0.15274 | -0.19119 | -0.045776 | 0.07782 | -0.059509 | 0.17853 | 0.16479 | 0.16479 | 0.20142 | 0.1236 | 0.018311 | 0.1236
5285.9531 | 0.030518 | 0.36636 | -0.4657 | -0.26276 | -0.20081 | -0.29159 | -0.21255 | 0.086975 | 0.068665 | 0.054932 | 0.064087 | 0.16479 | 0.041199 | 0.17395 | 0.045776 | -0.14206 | -0.27344 | -0.060883 | -0.16449 | -0.1976 | 0.050354 | 0.19684 | 0.059509 | 0.086975 | 0.059509 | 0.11444 | 0.1831 | 0.14191 | 0.041199 | 0.054932
5287.7188 | 0.22888 | 0.35889 | -0.44327 | -0.23712 | -0.21469 | -0.26489 | -0.19333 | 0.10529 | 0.07782 | 0.082397 | 0.082397 | 0.16479 | 0.027466 | 0.19226 | 0.061035 | -0.12283 | -0.28946 | -0.048065 | -0.14526 | -0.21362 | 0.050354 | 0.12817 | 0.068665 | 0.11444 | 0.07782 | 0.14191 | 0.19684 | 0.004578 | 0.10529 | 0.082397
5289.4062 | 0.16785 | 0.36423 | -0.4657 | -0.24353 | -0.21042 | -0.28091 | -0.20294 | 0.073242 | 0.041199 | 0.027466 | 0.036621 | 0.16479 | 0.036621 | 0.19226 | 0.061035 | -0.11749 | -0.30548 | -0.048065 | -0.15167 | -0.19333 | -0.013733 | 0.064087 | -0.027466 | 0.091553 | 0.064087 | 0.11444 | 0.19226 | 0 | 0.11902 | 0.091553
5291.1406 | 0.076294 | 0.38025 | -0.46249 | -0.26062 | -0.20828 | -0.28091 | -0.20187 | 0.1236 | 0.082397 | 0.10986 | 0.086975 | 0.16937 | 0.036621 | 0.19226 | 0.061035 | -0.12283 | -0.29587 | -0.058746 | -0.15167 | -0.21255 | 0.050354 | 0.19684 | 0.045776 | 0.086975 | 0.064087 | 0.11444 | 0.1831 | 0.14191 | 0.041199 | 0.068665
5292.8281 | 0.076294 | 0.37064 | -0.46143 | -0.2446 | -0.22537 | -0.27985 | -0.1976 | 0.073242 | 0.004578 | 0.018311 | 0.036621 | 0.16022 | 0.032043 | 0.17853 | 0.015259 | -0.12604 | -0.29907 | -0.064087 | -0.15595 | -0.20401 | 0.018311 | 0.11444 | 0.009155 | 0.086975 | 0.059509 | 0.13275 | 0.16479 | 0.11902 | 0.054932 | 0.059509
5294.5781 | 0.13733 | 0.36529 | -0.45929 | -0.23498 | -0.21576 | -0.27237 | -0.19333 | 0.14191 | 0.045776 | 0.045776 | 0.050354 | 0.15564 | 0.036621 | 0.17395 | 0.19836 | -0.11536 | -0.29053 | -0.040588 | -0.13351 | -0.19546 | 0.022888 | 0.10071 | 0.018311 | 0.10529 | 0.073242 | 0.16479 | 0.21515 | 0 | 0.11444 | 0.068665
5296.3125 | 0.10681 | 0.40375 | -0.45929 | -0.25528 | -0.20828 | -0.22644 | -0.1944 | 0.16479 | 0.018311 | 0.059509 | 0.082397 | 0.24261 | 0.022888 | 0.17395 | 0.030518 | -0.09613 | -0.28625 | -0.041656 | -0.13672 | -0.22003 | 0.032043 | 0.086975 | -0.032043 | 0.15564 | 0.13733 | 0.091553 | 0.16937 | 0.12817 | 0.004578 | 0.10529
5298 | 0.21362 | 0.40375 | -0.46677 | -0.26276 | -0.20615 | -0.25101 | -0.19974 | 0.068665 | -0.036621 | 0.013733 | 0.041199 | 0.25177 | 0.045776 | 0.17395 | 0.045776 | -0.10788 | -0.28305 | -0.043793 | -0.15808 | -0.1976 | -0.032043 | 0.059509 | -0.073242 | 0.15564 | 0.14191 | 0.1236 | 0.16937 | 0.15106 | 0.013733 | 0.091553
5299.75 | 0.030518 | 0.34714 | -0.46249 | -0.26703 | -0.20294 | -0.28198 | -0.20401 | 0.064087 | 0.041199 | 0.054932 | 0.054932 | 0.15564 | 0.027466 | 0.16479 | 0.045776 | -0.14526 | -0.27985 | -0.060883 | -0.16235 | -0.19333 | 0.027466 | 0.16937 | 0.041199 | 0.082397 | 0.059509 | 0.11902 | 0.17853 | 0.13733 | 0.045776 | 0.059509
5301.4531 | 0.045776 | 0.40909 | -0.44327 | -0.25742 | -0.21255 | -0.23712 | -0.18158 | 0.10986 | 0.009155 | 0.045776 | 0.064087 | 0.22888 | 0.032043 | 0.16479 | 0.045776 | -0.10254 | -0.28305 | -0.053406 | -0.13992 | -0.20508 | -0.050354 | 0.004578 | -0.091553 | 0.15564 | 0.13733 | 0.10529 | 0.16022 | 0.004578 | 0.091553 | 0.13275
5303.125 | 0.076294 | 0.36209 | -0.47318 | -0.25101 | -0.19546 | -0.29159 | -0.19867 | 0.036621 | 0.027466 | 0.032043 | 0.059509 | 0.17853 | 0.054932 | 0.17853 | 0.015259 | -0.13351 | -0.29266 | -0.060883 | -0.16769 | -0.19333 | 0 | 0.13275 | 0.009155 | 0.082397 | 0.054932 | 0.11444 | 0.17395 | 0.12817 | 0.07782 | 0.054932
5304.8906 | 0.22888 | 0.41122 | -0.47852 | -0.25635 | -0.20508 | -0.26596 | -0.19119 | 0.064087 | -0.027466 | 0.018311 | 0.032043 | 0.25635 | 0.041199 | 0.19684 | 0.061035 | -0.10254 | -0.28732 | -0.043793 | -0.1474 | -0.20935 | -0.032043 | 0.050354 | -0.073242 | 0.17853 | 0.14648 | 0.11444 | 0.17395 | 0.14191 | 0.013733 | 0.11444
5306.6562 | 0.076294 | 0.35782 | -0.46036 | -0.26489 | -0.20294 | -0.28091 | -0.1976 | 0.059509 | 0.022888 | 0.050354 | 0.050354 | 0.17853 | 0.041199 | 0.17395 | 0.030518 | -0.12924 | -0.29266 | -0.061951 | -0.16983 | -0.20294 | 0.018311 | 0.14191 | 0.004578 | 0.082397 | 0.073242 | 0.1236 | 0.1831 | 0.11902 | 0.045776 | 0.059509
5308.3438 | 0.15259 | 0.36423 | -0.46783 | -0.2446 | -0.20508 | -0.26382 | -0.1976 | 0.091553 | 0.064087 | 0.054932 | 0.054932 | 0.16022 | 0.027466 | 0.19226 | 0.030518 | -0.13031 | -0.29587 | -0.054474 | -0.15381 | -0.19974 | 0.018311 | 0.10071 | 0.032043 | 0.10529 | 0.10071 | 0.16022 | 0.21973 | 0.013733 | 0.10986 | 0.10529
5310.1094 | 0.10681 | 0.41229 | -0.44968 | -0.26382 | -0.20508 | -0.23712 | -0.19867 | 0.14648 | 0.054932 | 0.086975 | 0.07782 | 0.24261 | 0.013733 | 0.15106 | 0.030518 | -0.10361 | -0.27451 | -0.045929 | -0.13351 | -0.21255 | 0.009155 | 0.064087 | -0.050354 | 0.15564 | 0.13733 | 0.091553 | 0.15564 | 0.073242 | 0.045776 | 0.1236
5311.8125 | 0.076294 | 0.40375 | -0.45929 | -0.25101 | -0.2179 | -0.2446 | -0.19012 | 0.11902 | 0.022888 | 0.041199 | 0.054932 | 0.22888 | 0.045776 | 0.17853 | 0.045776 | -0.1207 | -0.27771 | -0.029907 | -0.13458 | -0.20721 | -0.036621 | 0.018311 | -0.073242 | 0.14648 | 0.13733 | 0.09613 | 0.14191 | 0.018311 | 0.059509 | 0.14191
5313.5625 | 0.21362 | 0.41229 | -0.46677 | -0.27664 | -0.21149 | -0.26703 | -0.19333 | 0.050354 | -0.018311 | 0.027466 | 0.050354 | 0.23346 | 0.032043 | 0.19226 | 0.030518 | -0.11749 | -0.28946 | -0.049133 | -0.13992 | -0.20828 | -0.064087 | 0.073242 | -0.073242 | 0.16479 | 0.13275 | 0.11902 | 0.16479 | 0.13733 | 0.022888 | 0.10529
5315.3125 | 0.045776 | 0.36529 | -0.46249 | -0.24674 | -0.20828 | -0.30228 | -0.20615 | 0.082397 | 0.082397 | 0.082397 | 0.073242 | 0.16022 | 0.022888 | 0.18768 | 0.030518 | -0.1442 | -0.2948 | -0.052338 | -0.16342 | -0.1944 | 0.068665 | 0.19684 | 0.041199 | 0.07782 | 0.068665 | 0.10071 | 0.17853 | 0.14191 | 0.050354 | 0.064087
5317.0156 | 0.19836 | 0.35248 | -0.46143 | -0.22858 | -0.20935 | -0.26703 | -0.19653 | 0.13733 | 0.050354 | 0.068665 | 0.086975 | 0.14648 | 0.018311 | 0.17853 | 0.1831 | -0.11108 | -0.29159 | -0.036316 | -0.12711 | -0.19226 | 0.045776 | 0.13275 | 0.064087 | 0.1236 | 0.086975 | 0.15106 | 0.19684 | 0.004578 | 0.091553 | 0.073242
5318.7656 | 0.045776 | 0.37064 | -0.4689 | -0.26062 | -0.21469 | -0.29266 | -0.21149 | 0.12817 | 0.082397 | 0.10986 | 0.082397 | 0.15106 | 0.027466 | 0.1831 | 0.045776 | -0.12711 | -0.29694 | -0.046997 | -0.15915 | -0.19653 | 0.045776 | 0.20599 | 0.036621 | 0.086975 | 0.073242 | 0.10529 | 0.14648 | 0.1236 | 0.041199 | 0.073242
5320.5156 | 0.015259 | 0.35568 | -0.45822 | -0.25101 | -0.19119 | -0.24994 | -0.1944 | 0.13275 | 0.036621 | 0.064087 | 0.07782 | 0.19226 | 0.013733 | 0.15564 | 0.045776 | -0.11643 | -0.28946 | -0.049133 | -0.1474 | -0.21042 | 0.018311 | 0.073242 | 0.022888 | 0.09613 | 0.059509 | 0.10986 | 0.15564 | 0.059509 | 0.10071 | 0.082397
5322.2812 | 0.12207 | 0.41229 | -0.46143 | -0.25955 | -0.21042 | -0.24353 | -0.20187 | 0.13275 | 0.041199 | 0.10071 | 0.073242 | 0.24719 | 0.032043 | 0.17853 | 0.045776 | -0.10254 | -0.26276 | -0.048065 | -0.13886 | -0.21255 | 0.009155 | 0.10071 | -0.032043 | 0.15564 | 0.13733 | 0.082397 | 0.14191 | 0.11902 | 0.027466 | 0.091553
5323.9688 | 0.10681 | 0.35248 | -0.47318 | -0.2446 | -0.20187 | -0.28625 | -0.19867 | 0.041199 | 0 | 0.018311 | 0.045776 | 0.16937 | 0.027466 | 0.1831 | 0.061035 | -0.13031 | -0.2948 | -0.05661 | -0.16235 | -0.19333 | -0.041199 | 0.07782 | -0.022888 | 0.086975 | 0.064087 | 0.1236 | 0.18768 | 0.004578 | 0.10529 | 0.09613
5325.7188 | 0.045776 | 0.41122 | -0.46036 | -0.23605 | -0.21362 | -0.24674 | -0.19226 | 0.073242 | -0.068665 | -0.013733 | 0.027466 | 0.24261 | 0.018311 | 0.17395 | 0.030518 | -0.1004 | -0.28625 | -0.03952 | -0.13886 | -0.20187 | -0.086975 | -0.041199 | -0.10071 | 0.16937 | 0.13733 | 0.10986 | 0.16022 | 0.013733 | 0.064087 | 0.13275
5327.4844 | 0.15259 | 0.3717 | -0.4689 | -0.23819 | -0.20294 | -0.29053 | -0.20508 | 0.091553 | 0.013733 | 0.036621 | 0.032043 | 0.16479 | 0.050354 | 0.20142 | 0.16785 | -0.11322 | -0.2713 | -0.057678 | -0.14206 | -0.18478 | 0.009155 | 0.09613 | 0.013733 | 0.10529 | 0.07782 | 0.14648 | 0.18768 | 0.004578 | 0.09613 | 0.073242
5329.1719 | 0.1831 | 0.40802 | -0.47531 | -0.27878 | -0.20935 | -0.26062 | -0.19974 | 0.068665 | -0.027466 | 0.041199 | 0.041199 | 0.23346 | 0.027466 | 0.18768 | 0.045776 | -0.11643 | -0.27664 | -0.044861 | -0.1442 | -0.21255 | -0.032043 | 0.073242 | -0.050354 | 0.16479 | 0.13275 | 0.10529 | 0.17853 | 0.14648 | 0.004578 | 0.086975
5330.9219 | 0.21362 | 0.41122 | -0.4689 | -0.27878 | -0.20615 | -0.26489 | -0.1976 | 0.050354 | -0.022888 | -0.004578 | 0.054932 | 0.24261 | 0.036621 | 0.1831 | 0.061035 | -0.11322 | -0.27878 | -0.048065 | -0.15274 | -0.20508 | -0.050354 | 0.036621 | -0.073242 | 0.1831 | 0.16479 | 0.14191 | 0.20599 | 0.14191 | 0.018311 | 0.1236
5332.6719 | 0.061035 | 0.40588 | -0.46997 | -0.25742 | -0.21362 | -0.24139 | -0.19226 | 0.11902 | 0.013733 | 0.050354 | 0.059509 | 0.21515 | 0.013733 | 0.17853 | 0.030518 | -0.11108 | -0.27985 | -0.055542 | -0.13245 | -0.20615 | -0.041199 | 0.022888 | -0.073242 | 0.15564 | 0.12817 | 0.10071 | 0.14648 | 0.013733 | 0.064087 | 0.1236
5334.3594 | 0.015259 | 0.37064 | -0.47104 | -0.25528 | -0.22324 | -0.29373 | -0.21576 | 0.086975 | 0.050354 | 0.09613 | 0.073242 | 0.15564 | 0.041199 | 0.16479 | 0.030518 | -0.12924 | -0.29053 | -0.057678 | -0.16663 | -0.18585 | 0.050354 | 0.18768 | 0.050354 | 0.07782 | 0.059509 | 0.11444 | 0.16479 | 0.15564 | 0.054932 | 0.045776
5336.1094 | 0.030518 | 0.38986 | -0.46356 | -0.26703 | -0.20615 | -0.27237 | -0.19653 | 0.1236 | 0.054932 | 0.086975 | 0.09613 | 0.16479 | 0.018311 | 0.16479 | 0.045776 | -0.12711 | -0.28732 | -0.05661 | -0.16983 | -0.19546 | 0.009155 | 0.16937 | -0.009155 | 0.11902 | 0.091553 | 0.10529 | 0.1831 | 0.086975 | 0.059509 | 0.10071
5337.8906 | 0.045776 | 0.40161 | -0.46036 | -0.25101 | -0.20721 | -0.23392 | -0.18265 | 0.10986 | -0.013733 | 0.027466 | 0.050354 | 0.23804 | 0.013733 | 0.16937 | 0.061035 | -0.10361 | -0.28519 | -0.03952 | -0.14099 | -0.20615 | -0.064087 | -0.009155 | -0.086975 | 0.15106 | 0.12817 | 0.10529 | 0.16022 | 0.018311 | 0.064087 | 0.13275
5339.5938 | 0.091553 | 0.36316 | -0.47531 | -0.24139 | -0.21683 | -0.28839 | -0.19974 | 0.013733 | -0.009155 | -0.004578 | 0.041199 | 0.15564 | 0.032043 | 0.18768 | 0.045776 | -0.13992 | -0.29266 | -0.063019 | -0.16022 | -0.1976 | -0.022888 | 0.10529 | 0.004578 | 0.073242 | 0.054932 | 0.11444 | 0.18768 | 0.073242 | 0.086975 | 0.073242
5341.3281 | 0.061035 | 0.37491 | -0.47318 | -0.25955 | -0.21896 | -0.28091 | -0.20508 | 0.073242 | 0.041199 | 0.068665 | 0.059509 | 0.16479 | 0.041199 | 0.1831 | 0.030518 | -0.12924 | -0.29587 | -0.068359 | -0.16556 | -0.19333 | 0.045776 | 0.16022 | 0.054932 | 0.082397 | 0.064087 | 0.10986 | 0.17395 | 0.14648 | 0.050354 | 0.068665
5343.0938 | 0.076294 | 0.37064 | -0.46677 | -0.26062 | -0.20935 | -0.28519 | -0.20081 | 0.07782 | 0.013733 | 0.050354 | 0.059509 | 0.17853 | 0.032043 | 0.1831 | 0.045776 | -0.12817 | -0.27664 | -0.048065 | -0.16129 | -0.19974 | 0.032043 | 0.13733 | 0.032043 | 0.086975 | 0.073242 | 0.11444 | 0.17853 | 0.13733 | 0.068665 | 0.054932
5344.8594 | 0.21362 | 0.36316 | -0.45822 | -0.24139 | -0.19867 | -0.25101 | -0.19974 | 0.14191 | 0.064087 | 0.064087 | 0.07782 | 0.15564 | 0.018311 | 0.16022 | 0.045776 | -0.11429 | -0.298 | -0.048065 | -0.13458 | -0.18478 | 0.064087 | 0.11444 | 0.054932 | 0.13275 | 0.082397 | 0.14191 | 0.1831 | 0.009155 | 0.10986 | 0.082397
5346.5625 | 0.045776 | 0.38666 | -0.4689 | -0.2446 | -0.21683 | -0.27664 | -0.19867 | 0.14648 | 0.082397 | 0.11902 | 0.07782 | 0.16937 | 0.009155 | 0.17853 | 0.030518 | -0.13245 | -0.30762 | -0.055542 | -0.16129 | -0.1976 | 0.050354 | 0.21057 | 0.027466 | 0.086975 | 0.059509 | 0.09613 | 0.14648 | 0.10529 | 0.036621 | 0.09613
5348.3125 | 0.045776 | 0.37491 | -0.45502 | -0.25314 | -0.21149 | -0.23178 | -0.1976 | 0.086975 | -0.022888 | 0 | 0.041199 | 0.2243 | 0.041199 | 0.17853 | 0.015259 | -0.11429 | -0.28625 | -0.05127 | -0.13992 | -0.21255 | -0.036621 | -0.018311 | -0.050354 | 0.15106 | 0.10071 | 0.09613 | 0.16022 | 0.036621 | 0.086975 | 0.10071
5350.0469 | 0.091553 | 0.36423 | -0.10681 | -0.2446 | -0.21149 | -0.28519 | -0.1976 | 0.041199 | 0.004578 | 0.036621 | 0.059509 | 0.17395 | 0.041199 | 0.19684 | 0.030518 | -0.13672 | -0.30228 | -0.05661 | -0.14526 | -0.18265 | 0 | 0.13733 | 0.004578 | 0.07782 | 0.054932 | 0.11902 | 0.16937 | 0.11902 | 0.068665 | 0.068665
5351.8125 | 0.19836 | 0.42297 | -0.48065 | -0.27023 | -0.20508 | -0.24567 | -0.20401 | 0.07782 | -0.018311 | 0.027466 | 0.032043 | 0.24261 | 0.036621 | 0.18768 | 0.045776 | -0.11108 | -0.28519 | -0.043793 | -0.14313 | -0.21362 | -0.036621 | 0.068665 | -0.064087 | 0.16479 | 0.14191 | 0.10986 | 0.16479 | 0.15564 | 0.027466 | 0.082397
5353.5156 | 0.061035 | 0.42938 | -0.47424 | -0.25848 | -0.20081 | -0.27023 | -0.19974 | 0.059509 | 0 | 0.036621 | 0.041199 | 0.21515 | 0.027466 | 0.17853 | 0.030518 | -0.11108 | -0.29159 | -0.049133 | -0.15381 | -0.20294 | -0.036621 | 0.086975 | -0.064087 | 0.16479 | 0.14191 | 0.11902 | 0.1831 | 0.086975 | 0.022888 | 0.11902
5355.2656 | 0.076294 | 0.39307 | -0.46036 | -0.26276 | -0.19974 | -0.24033 | -0.18692 | 0.1236 | 0.009155 | 0.068665 | 0.059509 | 0.21057 | 0.022888 | 0.17395 | 0.030518 | -0.11108 | -0.27344 | -0.054474 | -0.13458 | -0.21576 | -0.045776 | 0.013733 | -0.07782 | 0.15106 | 0.12817 | 0.10071 | 0.16022 | 0.013733 | 0.073242 | 0.13733
5357.0312 | 0.045776 | 0.35782 | -0.47531 | -0.26062 | -0.21255 | -0.28519 | -0.20508 | 0.054932 | 0.050354 | 0.059509 | 0.068665 | 0.17395 | 0.032043 | 0.16479 | 0.045776 | -0.14206 | -0.28625 | -0.05661 | -0.16342 | -0.1976 | 0.036621 | 0.18768 | 0.032043 | 0.086975 | 0.045776 | 0.10071 | 0.16937 | 0.14191 | 0.054932 | 0.073242
5358.7188 | 0.061035 | 0.39948 | -0.45181 | -0.24887 | -0.20187 | -0.2446 | -0.17517 | 0.045776 | -0.054932 | -0.027466 | 0.022888 | 0.23804 | 0.027466 | 0.1831 | 0.061035 | -0.099335 | -0.28732 | -0.03418 | -0.13245 | -0.20508 | -0.07782 | -0.041199 | -0.10071 | 0.15564 | 0.13275 | 0.09613 | 0.16937 | 0 | 0.068665 | 0.11444
5360.4688 | 0.10681 | 0.35996 | -0.48599 | -0.24994 | -0.21896 | -0.2948 | -0.19867 | 0.009155 | 0.004578 | 0.009155 | 0.041199 | 0.15564 | 0.041199 | 0.1831 | 0.045776 | -0.13245 | -0.29266 | -0.044861 | -0.15488 | -0.19653 | -0.018311 | 0.10986 | 0.009155 | 0.086975 | 0.059509 | 0.12817 | 0.19684 | 0.082397 | 0.091553 | 0.07782
5362.2031 | 0.076294 | 0.35889 | -0.47318 | -0.25955 | -0.21896 | -0.28305 | -0.21149 | 0.09613 | 0.082397 | 0.068665 | 0.059509 | 0.16479 | 0.050354 | 0.16479 | 0.045776 | -0.12817 | -0.29587 | -0.061951 | -0.16342 | -0.20187 | 0.068665 | 0.17853 | 0.050354 | 0.068665 | 0.036621 | 0.11902 | 0.16022 | 0.13275 | 0.050354 | 0.059509
5363.9531 | 0.061035 | 0.4155 | -0.46036 | -0.25528 | -0.20615 | -0.23498 | -0.19119 | 0.11902 | 0.027466 | 0.041199 | 0.068665 | 0.24261 | 0.018311 | 0.16479 | 0.061035 | -0.10681 | -0.27557 | -0.049133 | -0.13351 | -0.20721 | -0.032043 | 0.018311 | -0.07782 | 0.15106 | 0.11902 | 0.10529 | 0.15564 | 0.009155 | 0.07782 | 0.14191
5365.7031 | 0.045776 | 0.37918 | -0.45609 | -0.25421 | -0.20615 | -0.25528 | -0.18265 | 0.045776 | -0.032043 | -0.018311 | 0.027466 | 0.2243 | 0.027466 | 0.17853 | 0.045776 | -0.10788 | -0.28625 | -0.048065 | -0.14206 | -0.20508 | -0.068665 | -0.036621 | -0.073242 | 0.14648 | 0.10986 | 0.10529 | 0.16937 | 0.054932 | 0.082397 | 0.07782
5367.4688 | 0.21362 | 0.36957 | -0.45822 | -0.23071 | -0.20721 | -0.27985 | -0.1944 | 0.10071 | 0.10071 | 0.082397 | 0.073242 | 0.16022 | 0.032043 | 0.16022 | 0.015259 | -0.1239 | -0.28946 | -0.041656 | -0.13245 | -0.18478 | 0.032043 | 0.11902 | 0.041199 | 0.10986 | 0.09613 | 0.15564 | 0.19684 | -0.018311 | 0.09613 | 0.07782
5369.1406 | 0.045776 | 0.41336 | -0.48386 | -0.28091 | -0.19653 | -0.26062 | -0.20615 | 0.041199 | -0.009155 | 0.027466 | 0.032043 | 0.22888 | 0.041199 | 0.17853 | 0.030518 | -0.12604 | -0.27771 | -0.040588 | -0.15595 | -0.19653 | -0.018311 | 0.073242 | -0.054932 | 0.15106 | 0.11902 | 0.12817 | 0.17395 | 0.086975 | 0.027466 | 0.10071
5370.8906 | 0.015259 | 0.37384 | -0.45715 | -0.26062 | -0.19653 | -0.27771 | -0.20294 | 0.082397 | 0.10071 | 0.10986 | 0.091553 | 0.16937 | 0.036621 | 0.17395 | 0.045776 | -0.12283 | -0.2948 | -0.067291 | -0.15701 | -0.20081 | 0.032043 | 0.18768 | 0.022888 | 0.11902 | 0.082397 | 0.10071 | 0.14648 | 0.09613 | 0.036621 | 0.09613
5372.6406 | 0.10681 | 0.41336 | -0.45502 | -0.23712 | -0.20508 | -0.2446 | -0.1944 | 0.11444 | 0.054932 | 0.068665 | 0.073242 | 0.23346 | 0 | 0.17395 | 0.061035 | -0.093994 | -0.28732 | -0.046997 | -0.13672 | -0.20294 | 0.004578 | 0.082397 | -0.036621 | 0.15106 | 0.13733 | 0.091553 | 0.14648 | 0.11902 | 0.022888 | 0.10529
5374.3906 | 0.030518 | 0.39627 | -0.46036 | -0.25207 | -0.20615 | -0.26382 | -0.19119 | 0.045776 | -0.054932 | -0.013733 | 0.018311 | 0.24261 | 0.009155 | 0.1831 | 0.061035 | -0.10361 | -0.28946 | -0.046997 | -0.13351 | -0.20187 | -0.073242 | -0.059509 | -0.09613 | 0.14191 | 0.14191 | 0.11444 | 0.17395 | 0.004578 | 0.082397 | 0.14191
5376.0781 | 0.22888 | 0.42511 | -0.47424 | -0.27237 | -0.19012 | -0.27557 | -0.20401 | 0.041199 | -0.032043 | 0.004578 | 0.041199 | 0.23804 | 0.045776 | 0.19226 | 0.045776 | -0.10574 | -0.28198 | -0.043793 | -0.15595 | -0.18692 | -0.050354 | 0.059509 | -0.07782 | 0.16022 | 0.13275 | 0.10529 | 0.1831 | 0.13733 | 0.009155 | 0.11902
5377.8281 | 0.045776 | 0.40482 | -0.46463 | -0.25742 | -0.2179 | -0.25207 | -0.18692 | 0.11444 | 0.009155 | 0.041199 | 0.059509 | 0.22888 | 0.009155 | 0.17395 | 0.030518 | -0.11108 | -0.27664 | -0.050201 | -0.13138 | -0.20081 | -0.050354 | 0.018311 | -0.07782 | 0.16479 | 0.14191 | 0.09613 | 0.15564 | 0.027466 | 0.073242 | 0.12817
5379.5781 | 0.061035 | 0.36423 | -0.44113 | -0.24033 | -0.18799 | -0.26596 | -0.19119 | 0.09613 | 0.018311 | 0.045776 | 0.068665 | 0.1831 | 0.009155 | 0.17853 | 0.061035 | -0.11536 | -0.29373 | -0.044861 | -0.13992 | -0.1976 | -0.018311 | 0.068665 | 0.022888 | 0.10986 | 0.11444 | 0.14191 | 0.19226 | 0.059509 | 0.086975 | 0.091553
5381.2656 | 0.091553 | 0.39948 | -0.44968 | -0.27344 | -0.21683 | -0.24674 | -0.18585 | 0.1236 | -0.004578 | 0.07782 | 0.068665 | 0.21973 | 0.013733 | 0.1831 | 0.045776 | -0.11002 | -0.26703 | -0.046997 | -0.14847 | -0.20508 | -0.050354 | 0.032043 | -0.064087 | 0.13733 | 0.11902 | 0.10986 | 0.16022 | 0.018311 | 0.050354 | 0.13275
5383 | 0.15259 | 0.36423 | -0.45288 | -0.24674 | -0.21896 | -0.27985 | -0.19653 | 0.082397 | 0.013733 | 0.045776 | 0.041199 | 0.14191 | 0.054932 | 0.20599 | 0.15259 | -0.12497 | -0.27557 | -0.035248 | -0.13886 | -0.1741 | 0.009155 | 0.10529 | 0.027466 | 0.10529 | 0.09613 | 0.13733 | 0.20142 | 0 | 0.11444 | 0.10071
5384.75 | 0.045776 | 0.41657 | -0.43793 | -0.24353 | -0.21469 | -0.25314 | -0.18906 | 0.045776 | -0.091553 | -0.022888 | 0.004578 | 0.24719 | 0.018311 | 0.1831 | 0.061035 | -0.10147 | -0.28839 | -0.049133 | -0.12711 | -0.20081 | -0.091553 | -0.064087 | -0.09613 | 0.14648 | 0.13733 | 0.10071 | 0.15106 | 0.018311 | 0.091553 | 0.1236
5386.4375 | 0.19836 | 0.40802 | -0.47424 | -0.26703 | -0.20401 | -0.25314 | -0.19974 | 0.050354 | -0.027466 | 0.013733 | 0.050354 | 0.22888 | 0.036621 | 0.18768 | 0.030518 | -0.11002 | -0.29373 | -0.048065 | -0.13779 | -0.20828 | -0.054932 | 0.068665 | -0.059509 | 0.14648 | 0.15106 | 0.10529 | 0.16479 | 0.14191 | 0.009155 | 0.10071
5388.2031 | 0.061035 | 0.3952 | -0.46997 | -0.26062 | -0.20294 | -0.28305 | -0.19333 | 0.091553 | 0.050354 | 0.082397 | 0.073242 | 0.17853 | 0.027466 | 0.17853 | 0.030518 | -0.13565 | -0.27985 | -0.043793 | -0.16556 | -0.19974 | -0.004578 | 0.13733 | -0.018311 | 0.10986 | 0.10071 | 0.09613 | 0.15106 | 0.09613 | 0.036621 | 0.086975
5389.9688 | 0.12207 | 0.40909 | -0.46249 | -0.25314 | -0.20294 | -0.2446 | -0.19974 | 0.11902 | 0.022888 | 0.07782 | 0.073242 | 0.23804 | 0.013733 | 0.16022 | 0.045776 | -0.11536 | -0.29159 | -0.054474 | -0.14526 | -0.21255 | 0.004578 | 0.10071 | -0.032043 | 0.14648 | 0.12817 | 0.10986 | 0.14191 | 0.1236 | 0.022888 | 0.091553
5391.6719 | 0.12207 | 0.37277 | -0.46677 | -0.25421 | -0.21149 | -0.29053 | -0.20401 | 0.036621 | 0.004578 | 0.022888 | 0.050354 | 0.15564 | 0.045776 | 0.17853 | 0.045776 | -0.13031 | -0.29266 | -0.052338 | -0.16449 | -0.19867 | -0.032043 | 0.086975 | 0.009155 | 0.082397 | 0.073242 | 0.13733 | 0.1831 | 0.013733 | 0.09613 | 0.091553
5393.4219 | 0.076294 | 0.36743 | -0.47104 | -0.24994 | -0.21255 | -0.29159 | -0.21255 | 0.041199 | 0 | 0.036621 | 0.054932 | 0.16937 | 0.032043 | 0.17853 | 0.045776 | -0.12817 | -0.29373 | -0.058746 | -0.15488 | -0.19653 | -0.004578 | 0.11444 | 0.013733 | 0.068665 | 0.07782 | 0.09613 | 0.16937 | 0.13275 | 0.059509 | 0.059509
5395.1719 | 0.030518 | 0.38559 | -0.46997 | -0.28198 | -0.20721 | -0.26916 | -0.21042 | 0.10986 | 0.050354 | 0.10529 | 0.07782 | 0.16937 | 0.036621 | 0.16022 | 0.030518 | -0.12604 | -0.28091 | -0.054474 | -0.16022 | -0.20615 | 0.018311 | 0.14191 | -0.013733 | 0.10986 | 0.1236 | 0.1236 | 0.17853 | 0.09613 | 0.045776 | 0.10986
5396.875 | 0.061035 | 0.37277 | -0.4689 | -0.25955 | -0.21576 | -0.27878 | -0.1976 | 0.14191 | 0.10071 | 0.11902 | 0.091553 | 0.16479 | 0.045776 | 0.1831 | 0.045776 | -0.12924 | -0.2948 | -0.05661 | -0.15595 | -0.19867 | 0.054932 | 0.21515 | 0.032043 | 0.068665 | 0.059509 | 0.09613 | 0.16479 | 0.14191 | 0.054932 | 0.064087
5398.6406 | 0.045776 | 0.37811 | -0.45929 | -0.27023 | -0.21469 | -0.26062 | -0.20508 | 0.11902 | 0.054932 | 0.082397 | 0.073242 | 0.17853 | 0.032043 | 0.17853 | 0.030518 | -0.12604 | -0.27344 | -0.050201 | -0.14954 | -0.20615 | 0.009155 | 0.13733 | -0.027466 | 0.12817 | 0.10986 | 0.11902 | 0.16479 | 0.082397 | 0.045776 | 0.086975
5400.3281 | 0.030518 | 0.40268 | -0.44861 | -0.23926 | -0.21469 | -0.24353 | -0.1944 | 0.068665 | -0.045776 | -0.018311 | 0.027466 | 0.23804 | 0.018311 | 0.1831 | 0.030518 | -0.10895 | -0.28091 | -0.040588 | -0.13565 | -0.21576 | -0.073242 | -0.064087 | -0.10529 | 0.15564 | 0.1236 | 0.11902 | 0.15564 | 0.032043 | 0.091553 | 0.12817
5402.0781 | 0.061035 | 0.38879 | -0.47211 | -0.26169 | -0.1976 | -0.27985 | -0.20508 | 0.10529 | 0.086975 | 0.10986 | 0.091553 | 0.16937 | 0.018311 | 0.15564 | 0.045776 | -0.13138 | -0.29266 | -0.058746 | -0.15488 | -0.19974 | 0.032043 | 0.1831 | 0.009155 | 0.09613 | 0.07782 | 0.1236 | 0.17395 | 0.091553 | 0.045776 | 0.09613
5403.8281 | 0.030518 | 0.37064 | -0.46677 | -0.25848 | -0.20828 | -0.27985 | -0.20828 | 0.11444 | 0.11444 | 0.11902 | 0.082397 | 0.15564 | 0.032043 | 0.16479 | 0.045776 | -0.13031 | -0.28198 | -0.05661 | -0.16449 | -0.20294 | 0.068665 | 0.20142 | 0.036621 | 0.086975 | 0.050354 | 0.086975 | 0.16937 | 0.15106 | 0.045776 | 0.064087
5405.5781 | 0.10681 | 0.40802 | -0.45288 | -0.25314 | -0.20401 | -0.23926 | -0.19653 | 0.13275 | 0.018311 | 0.073242 | 0.073242 | 0.22888 | 0.027466 | 0.1831 | 0.045776 | -0.10147 | -0.28412 | -0.042725 | -0.13138 | -0.21042 | 0.013733 | 0.082397 | -0.027466 | 0.16022 | 0.12817 | 0.11902 | 0.16479 | 0.1236 | 0.018311 | 0.10529
5407.2656 | 0.15259 | 0.345 | -0.44327 | -0.23819 | -0.21149 | -0.25848 | -0.18692 | 0.12817 | 0.064087 | 0.082397 | 0.10071 | 0.17395 | 0.013733 | 0.16479 | 0.061035 | -0.12497 | -0.27878 | -0.042725 | -0.1474 | -0.20935 | 0.013733 | 0.12817 | 0.082397 | 0.11902 | 0.09613 | 0.15564 | 0.2243 | 0.045776 | 0.09613 | 0.10071
5409.0156 | 0.030518 | 0.34607 | -0.45929 | -0.23178 | -0.20828 | -0.25528 | -0.20401 | 0.1236 | 0.054932 | 0.059509 | 0.082397 | 0.17853 | 0.018311 | 0.15564 | 0.045776 | -0.11643 | -0.27878 | -0.05127 | -0.14099 | -0.20615 | 0.013733 | 0.086975 | 0.013733 | 0.11902 | 0.09613 | 0.13733 | 0.20599 | 0.045776 | 0.07782 | 0.068665
5410.7656 | 0.15259 | 0.40909 | -0.47104 | -0.24674 | -0.19974 | -0.26169 | -0.19333 | 0.068665 | -0.032043 | 0.022888 | 0.045776 | 0.2243 | 0.013733 | 0.17853 | 0.045776 | -0.11002 | -0.28732 | -0.046997 | -0.14313 | -0.20081 | -0.027466 | 0.082397 | -0.041199 | 0.15106 | 0.1236 | 0.073242 | 0.15106 | 0.15106 | 0.009155 | 0.10071
5412.5156 | 0.076294 | 0.41336 | -0.45715 | -0.2446 | -0.1976 | -0.25955 | -0.19546 | 0.09613 | -0.018311 | 0.027466 | 0.041199 | 0.23804 | 0.036621 | 0.16937 | 0.045776 | -0.10681 | -0.27451 | -0.058746 | -0.13031 | -0.20615 | -0.068665 | -0.013733 | -0.10529 | 0.15106 | 0.1236 | 0.10986 | 0.14648 | 0.009155 | 0.07782 | 0.14648
5414.1875 | 0.13733 | 0.37598 | -0.46783 | -0.24887 | -0.20721 | -0.30014 | -0.19012 | 0.068665 | 0.027466 | 0.032043 | 0.073242 | 0.1831 | 0.073242 | 0.21973 | 0.12207 | -0.11429 | -0.29587 | -0.05661 | -0.15595 | -0.18372 | -0.009155 | 0.09613 | 0.027466 | 0.091553 | 0.09613 | 0.13275 | 0.20142 | -0.009155 | 0.12817 | 0.07782
5415.9375 | 0.19836 | 0.41122 | -0.47638 | -0.27023 | -0.20401 | -0.27023 | -0.20508 | 0.045776 | -0.013733 | 0.027466 | 0.027466 | 0.23804 | 0.041199 | 0.17853 | 0.030518 | -0.11963 | -0.28519 | -0.05127 | -0.16022 | -0.20081 | -0.027466 | 0.073242 | -0.064087 | 0.17395 | 0.14191 | 0.1236 | 0.16022 | 0.11444 | 0.045776 | 0.10071
5417.7031 | 0.076294 | 0.35675 | -0.45929 | -0.26382 | -0.21042 | -0.28519 | -0.20508 | 0.013733 | 0.018311 | 0.036621 | 0.045776 | 0.17395 | 0.027466 | 0.20599 | 0.045776 | -0.13992 | -0.28625 | -0.05127 | -0.17197 | -0.20294 | -0.009155 | 0.10986 | 0.009155 | 0.091553 | 0.059509 | 0.1236 | 0.17853 | 0.12817 | 0.059509 | 0.059509
5419.3906 | 0.19836 | 0.35996 | -0.46036 | -0.24567 | -0.20828 | -0.25528 | -0.19546 | 0.11444 | 0.07782 | 0.068665 | 0.073242 | 0.15106 | 0.027466 | 0.1831 | 0.045776 | -0.12497 | -0.28625 | -0.048065 | -0.1474 | -0.20401 | 0.018311 | 0.13733 | 0.054932 | 0.091553 | 0.082397 | 0.14191 | 0.19226 | 0.013733 | 0.11902 | 0.073242
5421.1406 | 0.16785 | 0.36957 | -0.4422 | -0.22964 | -0.21149 | -0.25742 | -0.19333 | 0.13275 | 0.082397 | 0.068665 | 0.086975 | 0.16022 | 0.018311 | 0.16022 | 0.15259 | -0.11643 | -0.28519 | -0.038452 | -0.12176 | -0.18799 | 0.050354 | 0.13733 | 0.068665 | 0.13275 | 0.091553 | 0.1831 | 0.19684 | 0.041199 | 0.082397 | 0.082397
5422.8281 | 0.091553 | 0.36209 | -0.47104 | -0.24567 | -0.20187 | -0.28946 | -0.20615 | 0.022888 | 0.004578 | 0.022888 | 0.018311 | 0.15564 | 0.045776 | 0.18768 | 0.030518 | -0.12711 | -0.28839 | -0.048065 | -0.15701 | -0.20294 | -0.036621 | 0.068665 | -0.018311 | 0.10071 | 0.064087 | 0.12817 | 0.16479 | 0.032043 | 0.09613 | 0.07782
5424.5781 | 0.030518 | 0.41657 | -0.45181 | -0.23392 | -0.20935 | -0.22858 | -0.19012 | 0.086975 | -0.045776 | -0.004578 | 0.036621 | 0.23346 | 0.018311 | 0.19684 | 0.030518 | -0.097198 | -0.29373 | -0.043793 | -0.13351 | -0.20294 | -0.091553 | -0.041199 | -0.10986 | 0.16937 | 0.12817 | 0.10986 | 0.16479 | -0.004578 | 0.073242 | 0.12817
5426.3281 | 0.15259 | 0.35568 | -0.45288 | -0.23819 | -0.21683 | -0.26276 | -0.18692 | 0.11444 | 0.07782 | 0.068665 | 0.091553 | 0.16937 | 0.013733 | 0.14648 | 0.030518 | -0.12497 | -0.28732 | -0.049133 | -0.13565 | -0.20187 | 0.004578 | 0.068665 | 0.004578 | 0.073242 | 0.10529 | 0.16022 | 0.17853 | 0.032043 | 0.082397 | 0.082397
5428.0625 | 0.12207 | 0.40802 | -0.46249 | -0.26382 | -0.20294 | -0.25528 | -0.19226 | 0.10071 | 0.022888 | 0.07782 | 0.068665 | 0.22888 | 0.018311 | 0.17395 | 0.045776 | -0.10254 | -0.26703 | -0.03952 | -0.14847 | -0.20935 | 0.004578 | 0.082397 | -0.032043 | 0.15564 | 0.1236 | 0.09613 | 0.16022 | 0.12817 | 0.013733 | 0.10529
5429.8281 | 0.076294 | 0.41763 | -0.45288 | -0.26276 | -0.19974 | -0.25207 | -0.18799 | 0.1236 | 0.045776 | 0.073242 | 0.068665 | 0.2243 | 0.018311 | 0.16022 | 0.045776 | -0.10788 | -0.29266 | -0.050201 | -0.13565 | -0.20721 | 0.009155 | 0.082397 | -0.032043 | 0.13733 | 0.1236 | 0.091553 | 0.13275 | 0.09613 | 0.018311 | 0.1236
5431.5156 | 0.030518 | 0.41016 | -0.47852 | -0.2713 | -0.19867 | -0.29053 | -0.20187 | 0.068665 | 0.022888 | 0.073242 | 0.068665 | 0.21057 | 0.059509 | 0.18768 | 0.045776 | -0.12924 | -0.28198 | -0.048065 | -0.16556 | -0.19653 | -0.036621 | 0.09613 | -0.050354 | 0.13275 | 0.1236 | 0.1236 | 0.17853 | 0.082397 | 0.036621 | 0.11444
5433.2656 | 0.030518 | 0.41443 | -0.4892 | -0.26489 | -0.21469 | -0.27451 | -0.19867 | 0.045776 | 0 | 0.032043 | 0.032043 | 0.21973 | 0.027466 | 0.16479 | 0.030518 | -0.12497 | -0.28732 | -0.046997 | -0.16022 | -0.20187 | -0.045776 | 0.091553 | -0.059509 | 0.15564 | 0.11902 | 0.11444 | 0.16937 | 0.10529 | 0.018311 | 0.10071
5435.0156 | 0.045776 | 0.40375 | -0.45288 | -0.25635 | -0.21576 | -0.25314 | -0.18585 | 0.054932 | -0.054932 | -0.009155 | 0.032043 | 0.22888 | 0.022888 | 0.1831 | 0.045776 | -0.11108 | -0.28198 | -0.03418 | -0.13779 | -0.20615 | -0.086975 | -0.050354 | -0.082397 | 0.16022 | 0.13733 | 0.091553 | 0.17395 | 0.032043 | 0.10071 | 0.12817
5436.7812 | 0.045776 | 0.40909 | -0.47424 | -0.27771 | -0.21576 | -0.27878 | -0.20081 | 0.054932 | 0.009155 | 0.041199 | 0.032043 | 0.22888 | 0.041199 | 0.16937 | 0.076294 | -0.11856 | -0.29053 | -0.060883 | -0.15274 | -0.19867 | -0.032043 | 0.091553 | -0.073242 | 0.16022 | 0.12817 | 0.13733 | 0.1831 | 0.10071 | 0.045776 | 0.10529
5438.4688 | 0.15259 | 0.41977 | -0.46463 | -0.26703 | -0.19974 | -0.25528 | -0.19546 | 0.11444 | 0.018311 | 0.068665 | 0.082397 | 0.23804 | 0.018311 | 0.16479 | 0.045776 | -0.11429 | -0.27771 | -0.041656 | -0.13672 | -0.20401 | -0.013733 | 0.086975 | -0.018311 | 0.15106 | 0.12817 | 0.10986 | 0.14648 | 0.11902 | 0.004578 | 0.10986
5440.2188 | 0.10681 | 0.41443 | -0.47211 | -0.26276 | -0.20721 | -0.2478 | -0.19974 | 0.10529 | 0.036621 | 0.082397 | 0.082397 | 0.22888 | 0.013733 | 0.16937 | 0.045776 | -0.11002 | -0.27985 | -0.044861 | -0.14526 | -0.20721 | 0 | 0.09613 | -0.018311 | 0.14191 | 0.14648 | 0.09613 | 0.14648 | 0.12817 | 0.018311 | 0.10071
5441.9219 | 0.030518 | 0.41443 | -0.46249 | -0.25848 | -0.21896 | -0.2478 | -0.19653 | 0.041199 | -0.054932 | -0.004578 | 0.041199 | 0.21515 | 0.027466 | 0.15106 | 0.061035 | -0.10895 | -0.26703 | -0.043793 | -0.1474 | -0.20187 | -0.10529 | -0.050354 | -0.09613 | 0.15106 | 0.14191 | 0.1236 | 0.15564 | 0 | 0.073242 | 0.14191
5443.6719 | 0.15259 | 0.40482 | -0.46997 | -0.26382 | -0.21042 | -0.25848 | -0.18799 | 0.10071 | 0.013733 | 0.064087 | 0.073242 | 0.23346 | 0.032043 | 0.1831 | 0.015259 | -0.10361 | -0.27985 | -0.05661 | -0.13245 | -0.19974 | -0.027466 | 0.091553 | -0.027466 | 0.15106 | 0.1236 | 0.07782 | 0.14648 | 0.12817 | 0.013733 | 0.09613
5445.4219 | 0.076294 | 0.36423 | -0.44754 | -0.25101 | -0.20294 | -0.26916 | -0.20615 | 0.07782 | 0.013733 | 0.022888 | 0.041199 | 0.19226 | 0.018311 | 0.16479 | 0.030518 | -0.11963 | -0.28519 | -0.052338 | -0.14099 | -0.19653 | -0.009155 | 0.064087 | 0 | 0.10071 | 0.10986 | 0.13275 | 0.18768 | 0.045776 | 0.082397 | 0.07782
5447.1719 | 0.19836 | 0.40482 | -0.47424 | -0.28732 | -0.21149 | -0.25528 | -0.20187 | 0.045776 | -0.036621 | 0.027466 | 0.041199 | 0.23804 | 0.027466 | 0.17395 | 0.045776 | -0.12176 | -0.27771 | -0.041656 | -0.14847 | -0.20081 | -0.059509 | 0.050354 | -0.068665 | 0.15564 | 0.14191 | 0.10986 | 0.15106 | 0.13733 | 0.032043 | 0.09613
5448.875 | 0.045776 | 0.40482 | -0.45609 | -0.24033 | -0.20721 | -0.25528 | -0.19226 | 0.041199 | -0.064087 | -0.018311 | 0.018311 | 0.2243 | 0.018311 | 0.16937 | 0.045776 | -0.10895 | -0.28198 | -0.038452 | -0.1506 | -0.1976 | -0.086975 | -0.059509 | -0.091553 | 0.15564 | 0.1236 | 0.10986 | 0.15564 | 0.009155 | 0.073242 | 0.1236
5450.625 | 0.21362 | 0.42404 | -0.47424 | -0.26596 | -0.21255 | -0.27023 | -0.1976 | 0.027466 | -0.027466 | 0.022888 | 0.027466 | 0.23346 | 0.027466 | 0.1831 | 0.030518 | -0.11643 | -0.28946 | -0.043793 | -0.15915 | -0.1976 | -0.059509 | 0.054932 | -0.068665 | 0.16937 | 0.13733 | 0.10986 | 0.16022 | 0.13275 | 0.004578 | 0.10986
5452.375 | 0.16785 | 0.41443 | -0.48172 | -0.26703 | -0.20721 | -0.27771 | -0.19226 | 0.036621 | -0.027466 | 0.027466 | 0.018311 | 0.22888 | 0.045776 | 0.17853 | 0.030518 | -0.11749 | -0.28412 | -0.043793 | -0.17303 | -0.19546 | -0.054932 | 0.07782 | -0.068665 | 0.17395 | 0.15564 | 0.11902 | 0.17853 | 0.10071 | 0.036621 | 0.10529
5454.0625 | 0.030518 | 0.40268 | -0.45609 | -0.25528 | -0.21362 | -0.25421 | -0.19226 | 0.032043 | -0.064087 | 0.004578 | 0.036621 | 0.24261 | 0.032043 | 0.16937 | 0.045776 | -0.099335 | -0.2713 | -0.045929 | -0.14099 | -0.20615 | -0.11444 | -0.064087 | -0.1236 | 0.13733 | 0.13275 | 0.091553 | 0.15564 | -0.009155 | 0.086975 | 0.1236
5455.8125 | 0.045776 | 0.41122 | -0.49027 | -0.25207 | -0.20721 | -0.27878 | -0.19974 | 0.064087 | 0.045776 | 0.07782 | 0.07782 | 0.16479 | 0.027466 | 0.19226 | 0.030518 | -0.12176 | -0.29266 | -0.059814 | -0.15595 | -0.19119 | -0.032043 | 0.12817 | -0.036621 | 0.12817 | 0.11902 | 0.12817 | 0.15106 | 0.091553 | 0.032043 | 0.091553
5457.5781 | 0.12207 | 0.35889 | -0.46997 | -0.24567 | -0.20401 | -0.29053 | -0.21042 | 0.027466 | -0.018311 | 0.018311 | 0.032043 | 0.14191 | 0.027466 | 0.16937 | 0.045776 | -0.12711 | -0.29053 | -0.045929 | -0.16983 | -0.19653 | -0.036621 | 0.082397 | 0 | 0.07782 | 0.091553 | 0.11444 | 0.16937 | 0.054932 | 0.082397 | 0.068665
5459.3281 | 0.061035 | 0.37918 | -0.45502 | -0.23178 | -0.2179 | -0.24674 | -0.20615 | 0.09613 | -0.050354 | -0.004578 | 0.036621 | 0.22888 | 0.022888 | 0.17395 | 0.045776 | -0.11429 | -0.27985 | -0.046997 | -0.13565 | -0.20615 | -0.059509 | -0.018311 | -0.032043 | 0.10986 | 0.10529 | 0.10071 | 0.15564 | 0.059509 | 0.064087 | 0.11444
5461.0312 | 0.030518 | 0.37598 | -0.47104 | -0.25314 | -0.21576 | -0.28839 | -0.20615 | 0.10529 | 0.07782 | 0.10986 | 0.091553 | 0.15106 | 0.032043 | 0.15564 | 0.030518 | -0.12604 | -0.28305 | -0.057678 | -0.15595 | -0.20187 | 0.045776 | 0.21057 | 0.050354 | 0.07782 | 0.073242 | 0.10529 | 0.15564 | 0.09613 | 0.022888 | 0.086975
5462.7969 | 0.061035 | 0.35675 | -0.46463 | -0.25742 | -0.21896 | -0.29907 | -0.21896 | 0.032043 | 0.018311 | 0.032043 | 0.050354 | 0.16479 | 0.032043 | 0.18768 | 0.045776 | -0.11963 | -0.28839 | -0.054474 | -0.16769 | -0.1976 | -0.009155 | 0.1236 | 0.013733 | 0.082397 | 0.054932 | 0.10986 | 0.16479 | 0.10986 | 0.059509 | 0.059509
5464.5 | 0.015259 | 0.35889 | -0.47318 | -0.27023 | -0.20187 | -0.27985 | -0.20508 | 0.1236 | 0.091553 | 0.09613 | 0.09613 | 0.16022 | 0.036621 | 0.16479 | 0.061035 | -0.1239 | -0.28412 | -0.053406 | -0.16663 | -0.21149 | 0.041199 | 0.19226 | 0.045776 | 0.091553 | 0.045776 | 0.10529 | 0.15564 | 0.1236 | 0.054932 | 0.054932
5466.2344 | 0.045776 | 0.3717 | -0.47531 | -0.2478 | -0.20401 | -0.28732 | -0.20615 | 0.09613 | 0.036621 | 0.068665 | 0.064087 | 0.16937 | 0.027466 | 0.17853 | 0.045776 | -0.12497 | -0.30014 | -0.05661 | -0.15167 | -0.20615 | 0.050354 | 0.15106 | 0.027466 | 0.073242 | 0.050354 | 0.1236 | 0.16937 | 0.13733 | 0.050354 | 0.059509
5467.9219 | 0.030518 | 0.38238 | -0.47638 | -0.25635 | -0.20081 | -0.26489 | -0.19867 | 0.12817 | 0.07782 | 0.11444 | 0.07782 | 0.17853 | 0 | 0.16937 | 0.045776 | -0.12283 | -0.27878 | -0.061951 | -0.15274 | -0.20508 | 0.054932 | 0.1831 | 0.022888 | 0.091553 | 0.086975 | 0.11902 | 0.16022 | 0.086975 | 0.054932 | 0.09613
5469.6875 | 0.16785 | 0.42297 | -0.47531 | -0.27023 | -0.20935 | -0.26276 | -0.19974 | 0.073242 | -0.032043 | 0.022888 | 0.022888 | 0.2243 | 0.041199 | 0.1831 | 0.030518 | -0.11536 | -0.28305 | -0.05127 | -0.15488 | -0.21896 | -0.027466 | 0.082397 | -0.073242 | 0.15564 | 0.12817 | 0.1236 | 0.16479 | 0.10071 | 0.032043 | 0.10071
5471.4375 | 0.21362 | 0.36209 | -0.44647 | -0.22324 | -0.20508 | -0.24887 | -0.1976 | 0.15564 | 0.032043 | 0.073242 | 0.082397 | 0.16022 | 0.054932 | 0.2243 | 0.21362 | -0.11108 | -0.28519 | -0.028839 | -0.1207 | -0.18906 | 0.068665 | 0.11902 | 0.054932 | 0.12817 | 0.10071 | 0.14191 | 0.19684 | 0.027466 | 0.10529 | 0.082397
5473.125 | 0.091553 | 0.35996 | -0.46997 | -0.25101 | -0.20615 | -0.28519 | -0.20081 | 0.064087 | -0.027466 | 0.009155 | 0.032043 | 0.16479 | 0.050354 | 0.21057 | 0.061035 | -0.1239 | -0.28519 | -0.054474 | -0.16129 | -0.20401 | -0.036621 | 0.086975 | -0.013733 | 0.086975 | 0.059509 | 0.11902 | 0.18768 | 0.064087 | 0.086975 | 0.068665
5474.875 | 0.045776 | 0.3717 | -0.47318 | -0.25635 | -0.21576 | -0.27878 | -0.20615 | 0.086975 | 0.045776 | 0.073242 | 0.073242 | 0.16022 | 0.022888 | 0.17853 | 0.061035 | -0.13031 | -0.29694 | -0.042725 | -0.15915 | -0.20508 | 0.054932 | 0.17395 | 0.032043 | 0.09613 | 0.050354 | 0.11444 | 0.15564 | 0.14648 | 0.036621 | 0.068665
5476.5625 | 0.12207 | 0.40588 | -0.45609 | -0.26276 | -0.20508 | -0.23392 | -0.18906 | 0.17395 | 0.045776 | 0.086975 | 0.09613 | 0.23346 | 0.022888 | 0.16479 | 0.015259 | -0.099335 | -0.27023 | -0.043793 | -0.12711 | -0.21683 | 0.009155 | 0.064087 | -0.045776 | 0.14191 | 0.11444 | 0.10071 | 0.15106 | 0.09613 | 0.032043 | 0.10986
5478.3125 | 0.076294 | 0.38986 | -0.46036 | -0.25421 | -0.20294 | -0.23605 | -0.20294 | 0.13733 | 0.059509 | 0.059509 | 0.050354 | 0.22888 | 0 | 0.16022 | 0.045776 | -0.1004 | -0.26916 | -0.044861 | -0.13138 | -0.20935 | -0.009155 | 0.045776 | -0.073242 | 0.13733 | 0.10986 | 0.10071 | 0.16022 | 0.041199 | 0.054932 | 0.11444
5480.0625 | 0.091553 | 0.41763 | -0.44968 | -0.26169 | -0.20935 | -0.25421 | -0.18478 | 0.11444 | 0.022888 | 0.045776 | 0.064087 | 0.2243 | 0.013733 | 0.15564 | 0.045776 | -0.10147 | -0.27878 | -0.038452 | -0.14206 | -0.20721 | -0.041199 | 0.018311 | -0.082397 | 0.13733 | 0.13275 | 0.091553 | 0.15106 | 0.009155 | 0.082397 | 0.12817
5481.75 | 0.045776 | 0.41657 | -0.44434 | -0.24139 | -0.20935 | -0.25528 | -0.18158 | 0.064087 | -0.068665 | -0.013733 | 0.027466 | 0.24719 | 0.018311 | 0.16479 | 0.045776 | -0.10254 | -0.28732 | -0.045929 | -0.14313 | -0.20615 | -0.10071 | -0.032043 | -0.09613 | 0.15106 | 0.14191 | 0.10071 | 0.17395 | 0 | 0.082397 | 0.1236
5483.5 | 0.16785 | 0.40802 | -0.45502 | -0.26169 | -0.21042 | -0.26703 | -0.19867 | 0.091553 | 0.013733 | 0.050354 | 0.082397 | 0.23804 | 0.009155 | 0.16479 | 0.030518 | -0.10681 | -0.28839 | -0.050201 | -0.14847 | -0.19226 | -0.041199 | 0.10071 | -0.032043 | 0.14191 | 0.1236 | 0.10529 | 0.15106 | 0.1236 | 0 | 0.11902
5485.1875 | 0.076294 | 0.37064 | -0.4689 | -0.24887 | -0.22537 | -0.29373 | -0.19653 | 0.041199 | 0 | 0.027466 | 0.045776 | 0.14648 | 0.036621 | 0.17395 | 0.076294 | -0.13672 | -0.28625 | -0.067291 | -0.16876 | -0.19653 | -0.009155 | 0.12817 | 0.018311 | 0.086975 | 0.068665 | 0.10986 | 0.16479 | 0.11444 | 0.054932 | 0.054932
5486.9531 | 0.045776 | 0.35141 | -0.47318 | -0.25314 | -0.21149 | -0.29694 | -0.21042 | 0.09613 | 0.054932 | 0.07782 | 0.07782 | 0.16479 | 0.036621 | 0.1831 | 0.045776 | -0.12711 | -0.28091 | -0.045929 | -0.16235 | -0.19226 | 0.041199 | 0.21057 | 0.032043 | 0.064087 | 0.032043 | 0.10986 | 0.16022 | 0.13275 | 0.041199 | 0.064087
5488.7031 | 0.13733 | 0.40161 | -0.45929 | -0.24353 | -0.22217 | -0.24567 | -0.19867 | 0.13275 | 0.013733 | 0.064087 | 0.07782 | 0.22888 | 0.004578 | 0.17853 | 0.030518 | -0.10788 | -0.28839 | -0.058746 | -0.13779 | -0.21362 | -0.004578 | 0.09613 | -0.027466 | 0.14648 | 0.13733 | 0.091553 | 0.14191 | 0.12817 | 0.036621 | 0.082397
5490.3906 | 0.030518 | 0.36957 | -0.46783 | -0.24994 | -0.19546 | -0.28839 | -0.20508 | 0.11902 | 0.068665 | 0.11444 | 0.10529 | 0.15564 | 0.018311 | 0.15564 | 0.030518 | -0.12604 | -0.28946 | -0.057678 | -0.14954 | -0.19867 | 0.045776 | 0.19684 | 0.027466 | 0.091553 | 0.068665 | 0.082397 | 0.1236 | 0.091553 | 0.036621 | 0.082397
5492.1406 | 0.030518 | 0.37918 | -0.45609 | -0.23605 | -0.20935 | -0.25207 | -0.18799 | 0.086975 | -0.07782 | -0.036621 | 0.013733 | 0.21515 | 0.013733 | 0.17853 | 0.030518 | -0.11322 | -0.29053 | -0.048065 | -0.13672 | -0.20508 | -0.086975 | -0.054932 | -0.068665 | 0.15106 | 0.1236 | 0.11902 | 0.15564 | 0.068665 | 0.082397 | 0.10529
5493.8906 | 0.10681 | 0.42084 | -0.46356 | -0.24567 | -0.20828 | -0.2478 | -0.20828 | 0.11444 | 0.022888 | 0.073242 | 0.07782 | 0.23804 | 0.027466 | 0.18768 | 0.045776 | -0.10468 | -0.28732 | -0.05127 | -0.13992 | -0.20081 | -0.013733 | 0.086975 | -0.045776 | 0.15564 | 0.1236 | 0.11902 | 0.16022 | 0.13275 | 0.036621 | 0.10986
5495.6406 | 0.045776 | 0.37384 | -0.40802 | -0.26276 | -0.22003 | -0.29266 | -0.19653 | 0.045776 | 0.041199 | 0.050354 | 0.045776 | 0.16022 | 0.036621 | 0.16937 | 0.045776 | -0.13565 | -0.28412 | -0.064087 | -0.15701 | -0.19867 | -0.004578 | 0.14648 | 0.032043 | 0.064087 | 0.059509 | 0.1236 | 0.16022 | 0.13733 | 0.041199 | 0.050354
5497.3906 | 0.16785 | 0.35461 | -0.46356 | -0.2478 | -0.21149 | -0.27451 | -0.1944 | 0.10071 | 0.022888 | 0.045776 | 0.041199 | 0.12817 | 0.036621 | 0.17853 | 0.061035 | -0.11429 | -0.28198 | -0.048065 | -0.13779 | -0.18585 | 0.009155 | 0.10071 | 0.018311 | 0.10529 | 0.073242 | 0.14648 | 0.18768 | 0.009155 | 0.12817 | 0.091553
5499.0781 | 0.10681 | 0.36316 | -0.47745 | -0.25635 | -0.19867 | -0.27664 | -0.21255 | 0.054932 | -0.027466 | 0.009155 | 0.032043 | 0.16022 | 0.027466 | 0.1831 | 0.076294 | -0.12711 | -0.29587 | -0.061951 | -0.1474 | -0.19012 | -0.041199 | 0.068665 | -0.022888 | 0.068665 | 0.064087 | 0.13733 | 0.16937 | 0.036621 | 0.10071 | 0.082397
5500.8281 | 0.10681 | 0.37491 | -0.46783 | -0.26062 | -0.20401 | -0.28839 | -0.1944 | 0.082397 | 0 | 0.027466 | 0.036621 | 0.16937 | 0.050354 | 0.17853 | 0.045776 | -0.13138 | -0.28946 | -0.069427 | -0.1506 | -0.1976 | -0.032043 | 0.059509 | -0.027466 | 0.091553 | 0.064087 | 0.11902 | 0.1831 | 0.027466 | 0.086975 | 0.086975
5502.5781 | 0.045776 | 0.40588 | -0.45929 | -0.25207 | -0.21255 | -0.23819 | -0.20294 | 0.082397 | -0.059509 | -0.013733 | 0.041199 | 0.24261 | 0 | 0.16937 | 0.045776 | -0.093994 | -0.28198 | -0.03952 | -0.13886 | -0.20935 | -0.07782 | -0.068665 | -0.10071 | 0.16479 | 0.13733 | 0.10071 | 0.16479 | 0.018311 | 0.064087 | 0.11902
5504.2812 | 0.015259 | 0.38238 | -0.47211 | -0.24887 | -0.20615 | -0.28091 | -0.20294 | 0.10529 | 0.11444 | 0.10071 | 0.07782 | 0.15106 | 0.013733 | 0.1831 | 0.061035 | -0.14206 | -0.28625 | -0.053406 | -0.15381 | -0.20935 | 0.041199 | 0.20599 | 0.041199 | 0.07782 | 0.059509 | 0.09613 | 0.15564 | 0.1236 | 0.054932 | 0.050354
5506.0156 | 0.030518 | 0.36423 | -0.47104 | -0.27237 | -0.20721 | -0.27771 | -0.21255 | 0.12817 | 0.086975 | 0.11444 | 0.082397 | 0.14191 | 0.018311 | 0.16937 | 0.045776 | -0.13672 | -0.29266 | -0.064087 | -0.15274 | -0.21042 | 0.059509 | 0.21973 | 0.022888 | 0.073242 | 0.054932 | 0.10529 | 0.16022 | 0.11902 | 0.032043 | 0.059509
5507.7656 | 0.061035 | 0.38452 | -0.45929 | -0.24994 | -0.20187 | -0.24567 | -0.18906 | 0.086975 | -0.054932 | -0.022888 | 0.018311 | 0.24719 | 0.027466 | 0.16479 | 0.045776 | -0.10574 | -0.28625 | -0.035248 | -0.12817 | -0.21042 | -0.064087 | -0.045776 | -0.09613 | 0.14191 | 0.11902 | 0.10529 | 0.16479 | 0.041199 | 0.07782 | 0.1236
5509.5312 | 0.030518 | 0.39948 | -0.44968 | -0.25742 | -0.2211 | -0.2478 | -0.18585 | 0.07782 | -0.054932 | -0.013733 | 0.022888 | 0.22888 | 0.027466 | 0.16937 | 0.061035 | -0.10254 | -0.28946 | -0.045929 | -0.13886 | -0.18799 | -0.068665 | -0.050354 | -0.07782 | 0.13733 | 0.11444 | 0.11902 | 0.16937 | 0.032043 | 0.086975 | 0.10071
5511.2188 | 0.061035 | 0.37277 | -0.44861 | -0.25421 | -0.22003 | -0.25635 | -0.18372 | 0.082397 | 0.009155 | 0.032043 | 0.045776 | 0.20599 | 0.009155 | 0.17395 | 0.045776 | -0.11749 | -0.29907 | -0.044861 | -0.13565 | -0.18799 | 0.018311 | 0.09613 | 0.045776 | 0.1236 | 0.10986 | 0.13275 | 0.16479 | 0.059509 | 0.082397 | 0.068665
5512.9844 | 0.045776 | 0.39841 | -0.45075 | -0.25101 | -0.20721 | -0.24674 | -0.1976 | 0.054932 | -0.041199 | -0.018311 | 0.045776 | 0.23346 | 0.032043 | 0.1831 | 0.045776 | -0.11536 | -0.27985 | -0.05127 | -0.12604 | -0.19119 | -0.086975 | -0.032043 | -0.07782 | 0.13733 | 0.10529 | 0.11902 | 0.16479 | 0.059509 | 0.086975 | 0.091553
5514.6875 | 0.076294 | 0.40802 | -0.45822 | -0.27023 | -0.20615 | -0.25207 | -0.18692 | 0.086975 | 0.032043 | 0.054932 | 0.041199 | 0.20599 | 0.018311 | 0.15564 | 0.045776 | -0.10788 | -0.27451 | -0.041656 | -0.13886 | -0.20721 | -0.041199 | 0.013733 | -0.086975 | 0.15564 | 0.1236 | 0.09613 | 0.13733 | 0.009155 | 0.068665 | 0.1236
5516.4375 | 0 | 0.35355 | -0.46997 | -0.27771 | -0.2211 | -0.30121 | -0.20828 | 0.050354 | 0.073242 | 0.068665 | 0.068665 | 0.16022 | 0.022888 | 0.17853 | 0.045776 | -0.13886 | -0.27771 | -0.066223 | -0.17303 | -0.19867 | 0.027466 | 0.17853 | 0.041199 | 0.082397 | 0.068665 | 0.10986 | 0.16479 | 0.13733 | 0.045776 | 0.036621
5518.1406 | 0.1831 | 0.42404 | -0.48172 | -0.27344 | -0.20508 | -0.26596 | -0.19546 | 0.022888 | -0.018311 | 0.022888 | 0.036621 | 0.23346 | 0.027466 | 0.19226 | 0.061035 | -0.11108 | -0.28091 | -0.036316 | -0.15915 | -0.21255 | -0.045776 | 0.073242 | -0.073242 | 0.17395 | 0.14191 | 0.16937 | 0.21057 | 0.11444 | 0.018311 | 0.10071
5519.9062 | 0.13733 | 0.36316 | -0.4689 | -0.25101 | -0.19546 | -0.27985 | -0.20401 | 0.036621 | 0.013733 | 0.032043 | 0.050354 | 0.15106 | 0.041199 | 0.18768 | 0.030518 | -0.12711 | -0.28091 | -0.05127 | -0.16876 | -0.1976 | -0.036621 | 0.073242 | -0.022888 | 0.073242 | 0.054932 | 0.11902 | 0.1831 | 0.018311 | 0.11902 | 0.068665
5521.6719 | 0.091553 | 0.35675 | -0.45929 | -0.26276 | -0.20081 | -0.28946 | -0.20721 | 0.013733 | 0.004578 | 0.036621 | 0.032043 | 0.17395 | 0.050354 | 0.16937 | 0.061035 | -0.12497 | -0.27878 | -0.048065 | -0.16022 | -0.20401 | -0.004578 | 0.10529 | 0.004578 | 0.10529 | 0.064087 | 0.10986 | 0.17395 | 0.10071 | 0.068665 | 0.050354
5523.3594 | 0.15259 | 0.35889 | -0.47424 | -0.24353 | -0.21149 | -0.27664 | -0.20508 | 0.082397 | 0.022888 | 0.027466 | 0.036621 | 0.15564 | 0.032043 | 0.16937 | 0.045776 | -0.11963 | -0.28732 | -0.053406 | -0.14847 | -0.20401 | -0.009155 | 0.068665 | 0.004578 | 0.11444 | 0.073242 | 0.14191 | 0.18768 | -0.004578 | 0.10529 | 0.07782
5525.125 | 0.1831 | 0.36209 | -0.45715 | -0.23712 | -0.21255 | -0.26062 | -0.19333 | 0.13275 | 0.059509 | 0.073242 | 0.091553 | 0.16937 | 0.018311 | 0.16022 | 0.045776 | -0.11536 | -0.29159 | -0.053406 | -0.14206 | -0.19119 | 0.064087 | 0.13733 | 0.050354 | 0.12817 | 0.086975 | 0.15564 | 0.21973 | 0.022888 | 0.10071 | 0.059509
5526.8125 | 0.030518 | 0.37384 | -0.47104 | -0.26703 | -0.20508 | -0.27557 | -0.20294 | 0.1236 | 0.11902 | 0.11902 | 0.07782 | 0.16022 | 0.027466 | 0.17853 | 0.030518 | -0.12604 | -0.2713 | -0.045929 | -0.15808 | -0.20401 | 0.050354 | 0.21057 | 0.032043 | 0.086975 | 0.045776 | 0.11444 | 0.16022 | 0.14648 | 0.059509 | 0.068665
5528.5625 | 0.030518 | 0.37811 | -0.46036 | -0.27557 | -0.20828 | -0.27344 | -0.19974 | 0.1236 | 0.10986 | 0.091553 | 0.082397 | 0.13733 | 0.032043 | 0.17853 | 0.061035 | -0.13031 | -0.28412 | -0.052338 | -0.15381 | -0.21469 | 0.054932 | 0.20599 | 0.036621 | 0.086975 | 0.059509 | 0.10529 | 0.16022 | 0.10986 | 0.045776 | 0.086975
5530.3281 | 0.045776 | 0.40588 | -0.46783 | -0.24674 | -0.19974 | -0.23819 | -0.18906 | 0.073242 | -0.059509 | -0.009155 | 0.045776 | 0.22888 | 0 | 0.17395 | 0.030518 | -0.10147 | -0.28305 | -0.048065 | -0.13138 | -0.20828 | -0.07782 | -0.045776 | -0.10071 | 0.15106 | 0.12817 | 0.10071 | 0.16937 | 0.032043 | 0.082397 | 0.13733
5532.0156 | 0.10681 | 0.40161 | -0.45181 | -0.26062 | -0.20508 | -0.2446 | -0.18478 | 0.14648 | 0.064087 | 0.082397 | 0.068665 | 0.21057 | 0.013733 | 0.16937 | 0.030518 | -0.10574 | -0.29373 | -0.042725 | -0.13886 | -0.19546 | 0.004578 | 0.082397 | -0.045776 | 0.13275 | 0.12817 | 0.086975 | 0.14648 | 0.082397 | 0.022888 | 0.1236
5533.7656 | 0.12207 | 0.40268 | -0.45715 | -0.26382 | -0.19867 | -0.25314 | -0.18692 | 0.1236 | 0.027466 | 0.082397 | 0.07782 | 0.21057 | 0.022888 | 0.15564 | 0.030518 | -0.11322 | -0.27985 | -0.052338 | -0.13565 | -0.20508 | 0.018311 | 0.082397 | -0.045776 | 0.15106 | 0.12817 | 0.082397 | 0.13275 | 0.11902 | 0.032043 | 0.10071
5535.5156 | 0.045776 | 0.37277 | -0.44968 | -0.24353 | -0.21683 | -0.26169 | -0.1944 | 0.086975 | 0 | 0.027466 | 0.050354 | 0.19684 | 0.018311 | 0.16022 | 0.061035 | -0.12176 | -0.298 | -0.05127 | -0.14633 | -0.19867 | -0.013733 | 0.064087 | 0 | 0.082397 | 0.086975 | 0.10986 | 0.18768 | 0.054932 | 0.091553 | 0.082397
5537.2188 | 0.15259 | 0.36102 | -0.45288 | -0.2446 | -0.20935 | -0.27237 | -0.18906 | 0.12817 | 0.054932 | 0.086975 | 0.091553 | 0.16937 | -0.004578 | 0.15106 | 0.045776 | -0.1207 | -0.27344 | -0.042725 | -0.14954 | -0.18906 | 0.009155 | 0.091553 | 0.004578 | 0.12817 | 0.10071 | 0.14648 | 0.19684 | 0.045776 | 0.086975 | 0.086975
5538.9844 | 0.045776 | 0.3952 | -0.48065 | -0.2713 | -0.20721 | -0.27557 | -0.20294 | 0.068665 | 0.050354 | 0.073242 | 0.064087 | 0.18768 | 0.041199 | 0.1831 | 0.045776 | -0.12817 | -0.28091 | -0.048065 | -0.16022 | -0.19119 | -0.032043 | 0.11902 | -0.036621 | 0.13733 | 0.10529 | 0.10529 | 0.17395 | 0.082397 | 0.050354 | 0.10986
5540.7344 | 0.22888 | 0.34714 | -0.44754 | -0.24674 | -0.20828 | -0.27023 | -0.1944 | 0.1236 | 0.064087 | 0.068665 | 0.086975 | 0.14648 | 0.009155 | 0.15106 | 0.061035 | -0.12283 | -0.29694 | -0.040588 | -0.1506 | -0.19333 | 0.045776 | 0.13275 | 0.059509 | 0.13275 | 0.10071 | 0.16479 | 0.21057 | 0.032043 | 0.10071 | 0.073242
5542.5 | 0.015259 | 0.40695 | -0.46249 | -0.25101 | -0.22537 | -0.24994 | -0.19226 | 0.045776 | -0.045776 | -0.013733 | 0.045776 | 0.24261 | 0.018311 | 0.18768 | 0.061035 | -0.10788 | -0.27985 | -0.041656 | -0.13672 | -0.19867 | -0.086975 | -0.045776 | -0.082397 | 0.14648 | 0.12817 | 0.086975 | 0.15106 | 0.027466 | 0.082397 | 0.1236
5544.1875 | 0.045776 | 0.37491 | -0.45395 | -0.23285 | -0.20721 | -0.26703 | -0.18692 | 0.054932 | -0.022888 | -0.004578 | 0.027466 | 0.19226 | 0.018311 | 0.17853 | 0.045776 | -0.10574 | -0.29266 | -0.044861 | -0.1442 | -0.18799 | -0.050354 | -0.004578 | -0.027466 | 0.11444 | 0.082397 | 0.086975 | 0.15564 | 0.045776 | 0.082397 | 0.086975
5545.9375 | 0.16785 | 0.35461 | -0.46997 | -0.23605 | -0.21469 | -0.28091 | -0.20081 | 0.082397 | 0.064087 | 0.045776 | 0.050354 | 0.13275 | 0.018311 | 0.17853 | 0.045776 | -0.11536 | -0.28091 | -0.061951 | -0.16556 | -0.18692 | 0.018311 | 0.10529 | 0.032043 | 0.09613 | 0.068665 | 0.15106 | 0.21515 | 0.004578 | 0.10529 | 0.068665
5547.625 | 0.16785 | 0.37064 | -0.47104 | -0.24246 | -0.20401 | -0.27878 | -0.20187 | 0.054932 | 0.050354 | 0.032043 | 0.032043 | 0.12817 | 0.036621 | 0.17853 | 0.045776 | -0.12604 | -0.29373 | -0.058746 | -0.15915 | -0.19653 | -0.027466 | 0.091553 | -0.004578 | 0.10529 | 0.07782 | 0.13275 | 0.19684 | 0.004578 | 0.11902 | 0.091553
5549.375 | 0.16785 | 0.36102 | -0.46677 | -0.24353 | -0.21683 | -0.27237 | -0.20187 | 0.054932 | 0.004578 | 0.018311 | 0.045776 | 0.1831 | 0.045776 | 0.14648 | 0.015259 | -0.12497 | -0.298 | -0.048065 | -0.16342 | -0.20187 | -0.027466 | 0.068665 | -0.013733 | 0.07782 | 0.054932 | 0.12817 | 0.17395 | 0 | 0.10986 | 0.091553
5551.1094 | 0.030518 | 0.3717 | -0.4689 | -0.24567 | -0.21255 | -0.28305 | -0.21042 | 0.1236 | 0.086975 | 0.07782 | 0.086975 | 0.1831 | 0.027466 | 0.17853 | 0.045776 | -0.11643 | -0.29587 | -0.060883 | -0.16342 | -0.21042 | 0.068665 | 0.19684 | 0.059509 | 0.064087 | 0.073242 | 0.086975 | 0.16022 | 0.12817 | 0.050354 | 0.050354
5552.8594 | 0.030518 | 0.36209 | -0.45822 | -0.24994 | -0.2211 | -0.27023 | -0.20935 | 0.10071 | 0.054932 | 0.073242 | 0.073242 | 0.14648 | 0.032043 | 0.17395 | 0.061035 | -0.1207 | -0.298 | -0.060883 | -0.15701 | -0.20828 | 0.050354 | 0.17395 | 0.050354 | 0.068665 | 0.068665 | 0.10071 | 0.16937 | 0.13733 | 0.050354 | 0.059509
5554.625 | 0.045776 | 0.40802 | -0.46249 | -0.24994 | -0.20187 | -0.23605 | -0.19226 | 0.09613 | -0.032043 | -0.013733 | 0.032043 | 0.22888 | 0.013733 | 0.17853 | 0.061035 | -0.10788 | -0.28519 | -0.03952 | -0.13351 | -0.21362 | -0.091553 | -0.041199 | -0.1236 | 0.14648 | 0.11902 | 0.091553 | 0.16022 | 0 | 0.073242 | 0.10986
5556.375 | 0.061035 | 0.39414 | -0.48172 | -0.26596 | -0.20615 | -0.26382 | -0.19974 | 0.10071 | 0.054932 | 0.073242 | 0.07782 | 0.16937 | 0.032043 | 0.17395 | 0.045776 | -0.11643 | -0.28305 | -0.052338 | -0.16663 | -0.19867 | -0.004578 | 0.13275 | -0.036621 | 0.11444 | 0.091553 | 0.10986 | 0.16022 | 0.09613 | 0.050354 | 0.10529
5558.0625 | 0.045776 | 0.38773 | -0.47424 | -0.25528 | -0.21362 | -0.27985 | -0.1944 | 0.13275 | 0.09613 | 0.091553 | 0.086975 | 0.15564 | 0.022888 | 0.17395 | 0.045776 | -0.13245 | -0.29159 | -0.058746 | -0.15274 | -0.18692 | 0.054932 | 0.20599 | 0.041199 | 0.086975 | 0.041199 | 0.10529 | 0.16937 | 0.12817 | 0.054932 | 0.059509
5559.8281 | 0.12207 | 0.4155 | -0.4689 | -0.24887 | -0.19974 | -0.24887 | -0.19653 | 0.12817 | 0.018311 | 0.059509 | 0.068665 | 0.21515 | 0.022888 | 0.16479 | 0.045776 | -0.10574 | -0.28625 | -0.040588 | -0.12924 | -0.22003 | -0.013733 | 0.07782 | -0.045776 | 0.15106 | 0.12817 | 0.10071 | 0.13275 | 0.13733 | 0.013733 | 0.11444
5561.5156 | 0.015259 | 0.41657 | -0.4689 | -0.26382 | -0.20401 | -0.27557 | -0.20615 | 0.068665 | -0.013733 | 0.036621 | 0.027466 | 0.21057 | 0.036621 | 0.17853 | 0.045776 | -0.11429 | -0.27344 | -0.053406 | -0.15488 | -0.19226 | -0.032043 | 0.082397 | -0.064087 | 0.14191 | 0.11444 | 0.11444 | 0.17853 | 0.086975 | 0.036621 | 0.091553
5563.2656 | 0.030518 | 0.38025 | -0.47852 | -0.25421 | -0.2179 | -0.28625 | -0.19974 | 0.12817 | 0.11444 | 0.11444 | 0.086975 | 0.15106 | 0.027466 | 0.16479 | 0.045776 | -0.13565 | -0.30441 | -0.064087 | -0.15595 | -0.19867 | 0.054932 | 0.2243 | 0.041199 | 0.082397 | 0.045776 | 0.10529 | 0.14191 | 0.14191 | 0.022888 | 0.054932
5564.9688 | 0.045776 | 0.36957 | -0.45609 | -0.24246 | -0.19653 | -0.25848 | -0.1944 | 0.1236 | 0.013733 | 0.022888 | 0.064087 | 0.20142 | 0.022888 | 0.16937 | 0.045776 | -0.11429 | -0.28519 | -0.050201 | -0.14313 | -0.19226 | 0 | 0.068665 | 0.004578 | 0.073242 | 0.064087 | 0.07782 | 0.19226 | 0.059509 | 0.07782 | 0.073242
5566.7188 | 0.15259 | 0.4187 | -0.46997 | -0.26062 | -0.19974 | -0.25421 | -0.19226 | 0.07782 | -0.032043 | 0.022888 | 0.041199 | 0.22888 | 0.027466 | 0.18768 | 0.045776 | -0.10361 | -0.28412 | -0.052338 | -0.13992 | -0.20935 | -0.036621 | 0.068665 | -0.068665 | 0.15564 | 0.13733 | 0.10529 | 0.15564 | 0.16937 | 0.022888 | 0.10529
5568.4688 | 0.091553 | 0.41657 | -0.44647 | -0.25528 | -0.19653 | -0.24994 | -0.18906 | 0.15564 | 0.022888 | 0.059509 | 0.054932 | 0.2243 | 0.027466 | 0.16479 | 0.061035 | -0.1004 | -0.28412 | -0.05127 | -0.13565 | -0.19653 | -0.045776 | 0.036621 | -0.068665 | 0.13733 | 0.11444 | 0.10071 | 0.14191 | 0.022888 | 0.050354 | 0.1236
5570.1562 | 0.030518 | 0.36957 | -0.45822 | -0.25635 | -0.19974 | -0.26276 | -0.19546 | 0.059509 | -0.027466 | -0.004578 | 0.032043 | 0.21057 | 0.032043 | 0.15564 | 0.045776 | -0.10788 | -0.27344 | -0.046997 | -0.14206 | -0.1976 | -0.041199 | 0.018311 | -0.022888 | 0.1236 | 0.082397 | 0.10529 | 0.13275 | 0.054932 | 0.09613 | 0.073242
5571.9062 | 0.045776 | 0.41016 | -0.46677 | -0.25528 | -0.20081 | -0.25848 | -0.19974 | 0.068665 | -0.032043 | 0.018311 | 0.041199 | 0.23804 | 0.009155 | 0.16022 | 0.061035 | -0.095062 | -0.28091 | -0.050201 | -0.13886 | -0.19974 | -0.09613 | -0.027466 | -0.086975 | 0.15106 | 0.13733 | 0.10071 | 0.16479 | 0.009155 | 0.064087 | 0.12817
5573.5938 | 0.19836 | 0.41229 | -0.46249 | -0.27878 | -0.20508 | -0.28305 | -0.20081 | 0.032043 | -0.027466 | 0.027466 | 0.022888 | 0.23346 | 0.041199 | 0.18768 | 0.045776 | -0.11215 | -0.27237 | -0.040588 | -0.15167 | -0.19546 | -0.064087 | 0.073242 | -0.07782 | 0.17853 | 0.15106 | 0.10071 | 0.1831 | 0.11444 | 0.027466 | 0.11902
5575.3594 | 0.030518 | 0.36957 | -0.46997 | -0.26489 | -0.20721 | -0.2948 | -0.20508 | 0.09613 | 0.082397 | 0.10529 | 0.09613 | 0.15106 | 0.018311 | 0.17395 | 0.015259 | -0.13138 | -0.28839 | -0.053406 | -0.16663 | -0.18692 | 0.036621 | 0.21973 | 0.045776 | 0.054932 | 0.050354 | 0.10529 | 0.16022 | 0.12817 | 0.054932 | 0.064087
5577.0625 | 0.1831 | 0.42511 | -0.48172 | -0.25528 | -0.21362 | -0.25635 | -0.20294 | 0.07782 | -0.032043 | 0.018311 | 0.041199 | 0.2243 | 0.027466 | 0.18768 | 0.045776 | -0.10788 | -0.28839 | -0.044861 | -0.13565 | -0.20721 | -0.045776 | 0.086975 | -0.059509 | 0.15106 | 0.11444 | 0.11902 | 0.15564 | 0.14191 | 0.013733 | 0.09613
5578.8281 | 0.061035 | 0.40054 | -0.44968 | -0.2478 | -0.21362 | -0.24567 | -0.19333 | 0.07782 | -0.07782 | -0.004578 | 0.036621 | 0.24719 | 0.036621 | 0.18768 | 0 | -0.10895 | -0.28305 | -0.041656 | -0.1442 | -0.20935 | -0.086975 | -0.059509 | -0.082397 | 0.14191 | 0.12817 | 0.09613 | 0.16479 | 0.018311 | 0.091553 | 0.12817
5580.5156 | 0.19836 | 0.42831 | -0.47318 | -0.25742 | -0.20615 | -0.26703 | -0.1976 | 0.059509 | -0.045776 | 0.018311 | 0.032043 | 0.23804 | 0.041199 | 0.1831 | 0.030518 | -0.11108 | -0.27878 | -0.057678 | -0.14206 | -0.19653 | -0.054932 | 0.059509 | -0.059509 | 0.15106 | 0.13733 | 0.10986 | 0.16937 | 0.14191 | 0.027466 | 0.10986
5582.2969 | 0.10681 | 0.35782 | -0.48279 | -0.24887 | -0.20828 | -0.30014 | -0.20721 | 0.027466 | 0.013733 | 0.027466 | 0.036621 | 0.15106 | 0.036621 | 0.19226 | 0.045776 | -0.13138 | -0.28091 | -0.050201 | -0.16983 | -0.19333 | -0.013733 | 0.11444 | 0.022888 | 0.10071 | 0.073242 | 0.13275 | 0.15106 | 0.11902 | 0.07782 | 0.054932
5583.9844 | 0.10681 | 0.4155 | -0.47211 | -0.25207 | -0.20828 | -0.24139 | -0.20615 | 0.13733 | 0.041199 | 0.068665 | 0.082397 | 0.23346 | 0.009155 | 0.15564 | 0.045776 | -0.10254 | -0.28839 | -0.03952 | -0.12711 | -0.21362 | 0.009155 | 0.073242 | -0.036621 | 0.14648 | 0.11444 | 0.10071 | 0.15564 | 0.091553 | 0.022888 | 0.11444
5585.7344 | 0.1831 | 0.41122 | -0.47424 | -0.25848 | -0.21255 | -0.26596 | -0.20508 | 0.050354 | -0.036621 | 0.032043 | 0.045776 | 0.20599 | 0.027466 | 0.16022 | 0.030518 | -0.10788 | -0.2713 | -0.03952 | -0.1474 | -0.1976 | -0.059509 | 0.07782 | -0.059509 | 0.15106 | 0.13275 | 0.091553 | 0.14648 | 0.13275 | 0.009155 | 0.082397
5587.4844 | 0.13733 | 0.36316 | -0.46783 | -0.23392 | -0.21469 | -0.29373 | -0.20828 | 0.036621 | -0.013733 | 0.009155 | 0.041199 | 0.16479 | 0.032043 | 0.17395 | 0.061035 | -0.12711 | -0.27557 | -0.048065 | -0.16876 | -0.20081 | -0.036621 | 0.064087 | -0.022888 | 0.07782 | 0.054932 | 0.11902 | 0.17395 | 0.027466 | 0.086975 | 0.091553
5589.1875 | 0.22888 | 0.36316 | -0.44754 | -0.25101 | -0.21362 | -0.27237 | -0.19653 | 0.10986 | 0.073242 | 0.086975 | 0.091553 | 0.13733 | 0.004578 | 0.1831 | 0.061035 | -0.11749 | -0.28519 | -0.049133 | -0.14206 | -0.1944 | 0.045776 | 0.1236 | 0.050354 | 0.10986 | 0.07782 | 0.14191 | 0.21057 | 0.013733 | 0.1236 | 0.091553
5590.9531 | 0.045776 | 0.35248 | -0.46463 | -0.26382 | -0.20615 | -0.28305 | -0.20615 | 0.11902 | 0.082397 | 0.10986 | 0.082397 | 0.15106 | 0.022888 | 0.17395 | 0.045776 | -0.13886 | -0.28732 | -0.055542 | -0.16769 | -0.20401 | 0.054932 | 0.18768 | 0.036621 | 0.082397 | 0.041199 | 0.09613 | 0.16022 | 0.11444 | 0.050354 | 0.054932
5592.6562 | 0.045776 | 0.39948 | -0.47852 | -0.25955 | -0.20615 | -0.2713 | -0.20294 | 0.09613 | 0.032043 | 0.082397 | 0.073242 | 0.16937 | 0.027466 | 0.17853 | 0.061035 | -0.10468 | -0.27985 | -0.057678 | -0.16449 | -0.21469 | -0.018311 | 0.10529 | -0.041199 | 0.13733 | 0.10986 | 0.09613 | 0.16022 | 0.073242 | 0.027466 | 0.09613
5594.4219 | 0.061035 | 0.36102 | -0.48172 | -0.2478 | -0.21042 | -0.2948 | -0.20721 | 0.059509 | 0.013733 | 0.027466 | 0.059509 | 0.16022 | 0.045776 | 0.17395 | 0.061035 | -0.12711 | -0.30121 | -0.049133 | -0.1506 | -0.21255 | 0 | 0.10986 | 0.018311 | 0.073242 | 0.059509 | 0.11444 | 0.16937 | 0.11444 | 0.050354 | 0.064087
5596.1094 | 0.19836 | 0.35568 | -0.44647 | -0.24139 | -0.20721 | -0.24567 | -0.20187 | 0.12817 | 0.054932 | 0.073242 | 0.091553 | 0.16479 | 0.027466 | 0.16479 | 0.061035 | -0.11108 | -0.28732 | -0.050201 | -0.13138 | -0.21362 | 0.013733 | 0.068665 | -0.009155 | 0.059509 | 0.10071 | 0.15106 | 0.21057 | 0.041199 | 0.082397 | 0.064087
5597.8594 | 0.12207 | 0.41443 | -0.46249 | -0.24887 | -0.20187 | -0.24033 | -0.19974 | 0.1236 | 0.036621 | 0.068665 | 0.07782 | 0.23346 | 0.018311 | 0.1831 | 0.061035 | -0.10681 | -0.28091 | -0.046997 | -0.13565 | -0.21149 | 0.004578 | 0.086975 | -0.032043 | 0.15564 | 0.13275 | 0.091553 | 0.13733 | 0.13733 | 0.013733 | 0.091553
5599.5625 | 0.045776 | 0.36423 | -0.47852 | -0.24887 | -0.20401 | -0.28091 | -0.19546 | 0.11444 | 0.10071 | 0.091553 | 0.073242 | 0.15564 | 0.032043 | 0.17395 | 0.061035 | -0.13031 | -0.28519 | -0.060883 | -0.16769 | -0.19867 | 0.07782 | 0.21057 | 0.068665 | 0.073242 | 0.041199 | 0.09613 | 0.15564 | 0.15106 | 0.045776 | 0.045776
5601.3125 | 0.045776 | 0.40588 | -0.47424 | -0.25421 | -0.21469 | -0.26382 | -0.20401 | 0.091553 | 0.059509 | 0.073242 | 0.082397 | 0.19226 | 0.022888 | 0.16937 | 0.045776 | -0.11536 | -0.2948 | -0.058746 | -0.14954 | -0.19653 | 0.013733 | 0.13733 | -0.032043 | 0.12817 | 0.09613 | 0.11902 | 0.15564 | 0.10986 | 0.036621 | 0.09613
5603.0625 | 0.061035 | 0.41122 | -0.46356 | -0.23712 | -0.20508 | -0.24033 | -0.18906 | 0.11902 | 0.004578 | 0.022888 | 0.059509 | 0.2243 | 0.013733 | 0.16937 | 0.045776 | -0.095062 | -0.28305 | -0.045929 | -0.1207 | -0.20828 | -0.050354 | 0.009155 | -0.082397 | 0.14648 | 0.13733 | 0.091553 | 0.16022 | 0.018311 | 0.07782 | 0.12817
5604.7656 | 0.13733 | 0.4155 | -0.46463 | -0.25742 | -0.19012 | -0.25314 | -0.20081 | 0.091553 | 0.032043 | 0.059509 | 0.07782 | 0.2243 | 0.022888 | 0.16479 | 0.045776 | -0.099335 | -0.27344 | -0.052338 | -0.15167 | -0.20615 | 0 | 0.073242 | -0.027466 | 0.13733 | 0.14648 | 0.09613 | 0.14648 | 0.13275 | 0.009155 | 0.10071
5606.5 | 0.16785 | 0.35996 | -0.44968 | -0.24994 | -0.21469 | -0.27023 | -0.18585 | 0.11444 | 0.073242 | 0.07782 | 0.082397 | 0.16022 | 0.009155 | 0.15564 | 0.015259 | -0.11002 | -0.28091 | -0.054474 | -0.14633 | -0.19012 | 0.009155 | 0.073242 | 0.064087 | 0.10986 | 0.10529 | 0.14191 | 0.1831 | 0.050354 | 0.068665 | 0.073242
5608.25 | 0.061035 | 0.40482 | -0.45395 | -0.26703 | -0.20828 | -0.24887 | -0.18265 | 0.086975 | 0.013733 | 0.059509 | 0.059509 | 0.20599 | 0.018311 | 0.16022 | 0.045776 | -0.10254 | -0.26169 | -0.043793 | -0.1474 | -0.21042 | -0.050354 | 0.009155 | -0.07782 | 0.14648 | 0.1236 | 0.1236 | 0.14191 | 0.009155 | 0.086975 | 0.13733
5609.9531 | 0.045776 | 0.39841 | -0.46036 | -0.25314 | -0.20721 | -0.24674 | -0.19867 | 0.036621 | -0.068665 | -0.022888 | 0.032043 | 0.23346 | 0.013733 | 0.17395 | 0.030518 | -0.09613 | -0.27557 | -0.044861 | -0.14847 | -0.1944 | -0.082397 | -0.050354 | -0.09613 | 0.14648 | 0.14648 | 0.11444 | 0.14648 | 0.022888 | 0.059509 | 0.11902
5611.6875 | 0.045776 | 0.38025 | -0.47104 | -0.24567 | -0.19653 | -0.29159 | -0.19226 | 0.10529 | 0.10986 | 0.13275 | 0.10071 | 0.15106 | 0.009155 | 0.1831 | 0.076294 | -0.13672 | -0.298 | -0.066223 | -0.15274 | -0.20081 | 0.041199 | 0.21973 | 0.059509 | 0.082397 | 0.050354 | 0.09613 | 0.15564 | 0.1236 | 0.041199 | 0.064087
5613.375 | 0.045776 | 0.36529 | -0.46997 | -0.26382 | -0.21576 | -0.29266 | -0.21362 | 0.059509 | 0.027466 | 0.050354 | 0.050354 | 0.16479 | 0.032043 | 0.17395 | 0.045776 | -0.13351 | -0.29373 | -0.055542 | -0.16342 | -0.19546 | 0.009155 | 0.15106 | 0.027466 | 0.068665 | 0.064087 | 0.10986 | 0.16022 | 0.12817 | 0.054932 | 0.041199
5615.125 | 0.061035 | 0.36529 | -0.46783 | -0.27237 | -0.21576 | -0.30014 | -0.20187 | 0.068665 | 0.013733 | 0.032043 | 0.059509 | 0.16937 | 0.050354 | 0.17395 | 0.030518 | -0.12497 | -0.27771 | -0.065155 | -0.17197 | -0.20615 | -0.009155 | 0.12817 | 0.022888 | 0.086975 | 0.054932 | 0.1236 | 0.16937 | 0.13733 | 0.059509 | 0.054932
5616.8125 | 0.22888 | 0.35141 | -0.45502 | -0.23926 | -0.20187 | -0.26703 | -0.20294 | 0.13733 | 0.059509 | 0.064087 | 0.082397 | 0.13275 | 0.013733 | 0.16022 | 0.030518 | -0.13031 | -0.29373 | -0.045929 | -0.13672 | -0.19867 | 0.050354 | 0.10529 | 0.045776 | 0.10986 | 0.082397 | 0.14191 | 0.18768 | -0.004578 | 0.10529 | 0.091553
5618.5625 | 0.045776 | 0.41122 | -0.46036 | -0.24246 | -0.20615 | -0.24033 | -0.19333 | 0.15564 | 0.027466 | 0.064087 | 0.064087 | 0.20599 | 0.009155 | 0.15564 | 0.030518 | -0.10147 | -0.27237 | -0.040588 | -0.11749 | -0.21683 | -0.027466 | 0.032043 | -0.054932 | 0.13275 | 0.11444 | 0.10071 | 0.15564 | 0.027466 | 0.064087 | 0.13275
5620.3281 | 0.21362 | 0.36636 | -0.45181 | -0.24353 | -0.20721 | -0.26382 | -0.1976 | 0.12817 | 0.068665 | 0.073242 | 0.082397 | 0.15564 | 0.064087 | 0.21057 | 0.21362 | -0.10254 | -0.27557 | -0.03418 | -0.12817 | -0.19333 | 0.059509 | 0.14648 | 0.059509 | 0.10071 | 0.10529 | 0.14191 | 0.19684 | 0.013733 | 0.10529 | 0.068665
5622.0312 | 0.19836 | 0.345 | -0.4454 | -0.23926 | -0.20721 | -0.25848 | -0.19546 | 0.1236 | 0.041199 | 0.07782 | 0.10529 | 0.16022 | 0.004578 | 0.16479 | 0.045776 | -0.11536 | -0.28412 | -0.049133 | -0.15274 | -0.1944 | 0.054932 | 0.1236 | 0.045776 | 0.11902 | 0.082397 | 0.16479 | 0.19226 | 0.027466 | 0.068665 | 0.07782
5623.7812 | 0.061035 | 0.35889 | -0.46783 | -0.26062 | -0.19974 | -0.29587 | -0.19012 | 0.082397 | 0.059509 | 0.073242 | 0.073242 | 0.15564 | 0.032043 | 0.18768 | 0.061035 | -0.13245 | -0.28839 | -0.055542 | -0.16983 | -0.19546 | 0.041199 | 0.19226 | 0.045776 | 0.064087 | 0.036621 | 0.10986 | 0.17395 | 0.14191 | 0.045776 | 0.045776
5625.4844 | 0.045776 | 0.39307 | -0.48172 | -0.25848 | -0.20721 | -0.26596 | -0.21255 | 0.11444 | 0.041199 | 0.086975 | 0.082397 | 0.17395 | 0.054932 | 0.17853 | 0.045776 | -0.11536 | -0.29373 | -0.052338 | -0.16022 | -0.20935 | 0 | 0.1236 | -0.041199 | 0.10071 | 0.11902 | 0.11902 | 0.16022 | 0.082397 | 0.041199 | 0.10071
5627.2344 | 0.1831 | 0.36209 | -0.46677 | -0.24353 | -0.21255 | -0.27344 | -0.20081 | 0.082397 | 0.036621 | 0.032043 | 0.036621 | 0.1236 | 0.041199 | 0.18768 | 0.045776 | -0.12604 | -0.30334 | -0.050201 | -0.15381 | -0.18372 | 0.018311 | 0.09613 | 0 | 0.09613 | 0.091553 | 0.1236 | 0.17853 | 0.004578 | 0.14191 | 0.086975
5628.9844 | 0.030518 | 0.41229 | -0.46356 | -0.24246 | -0.20828 | -0.22324 | -0.19546 | 0.082397 | -0.027466 | 0.004578 | 0.050354 | 0.23804 | 0.004578 | 0.17395 | 0.015259 | -0.10681 | -0.28091 | -0.042725 | -0.1239 | -0.21255 | -0.082397 | -0.022888 | -0.10071 | 0.14648 | 0.13275 | 0.10986 | 0.17395 | 0 | 0.068665 | 0.13275
5630.6719 | 0.045776 | 0.37491 | -0.44968 | -0.24246 | -0.19546 | -0.25528 | -0.18906 | 0.064087 | -0.022888 | 0 | 0.027466 | 0.21057 | 0.013733 | 0.17395 | 0.045776 | -0.10361 | -0.27771 | -0.044861 | -0.13779 | -0.18799 | -0.041199 | -0.022888 | -0.050354 | 0.11444 | 0.082397 | 0.10071 | 0.14191 | 0.050354 | 0.091553 | 0.09613
5632.4219 | 0.16785 | 0.36102 | -0.45715 | -0.24567 | -0.20615 | -0.27451 | -0.19546 | 0.10071 | 0.073242 | 0.068665 | 0.068665 | 0.14648 | 0.018311 | 0.16022 | 0.061035 | -0.12283 | -0.28412 | -0.05661 | -0.1506 | -0.17517 | 0.054932 | 0.10071 | 0.027466 | 0.11902 | 0.11444 | 0.14191 | 0.21057 | -0.013733 | 0.11444 | 0.10529
5634.1094 | 0.13733 | 0.36636 | -0.45929 | -0.24246 | -0.21362 | -0.2681 | -0.20401 | 0.091553 | 0.050354 | 0.045776 | 0.050354 | 0.13733 | 0.032043 | 0.16937 | 0.061035 | -0.11108 | -0.28305 | -0.05661 | -0.14847 | -0.19119 | 0.027466 | 0.10986 | 0.022888 | 0.07782 | 0.091553 | 0.16479 | 0.20599 | -0.004578 | 0.10071 | 0.073242
5635.8594 | 0.030518 | 0.37277 | -0.46356 | -0.26169 | -0.21469 | -0.27985 | -0.20828 | 0.13275 | 0.11444 | 0.10986 | 0.07782 | 0.15106 | 0.013733 | 0.17395 | 0.045776 | -0.13031 | -0.29053 | -0.03952 | -0.16876 | -0.20294 | 0.059509 | 0.21515 | 0.050354 | 0.059509 | 0.036621 | 0.10071 | 0.13733 | 0.13275 | 0.041199 | 0.086975
5637.6094 | 0.045776 | 0.3717 | -0.79147 | -0.25955 | 0.11429 | -0.27451 | -0.20508 | 60.498 | -62.1735 | 0.10986 | -62.5305 | 60.466 | 62.5763 | 62.5076 | 0.030518 | -0.11322 | 0.058746 | 0.29373 | -0.15381 | -0.19974 | 0.064087 | 0.21515 | -62.6175 | 60.3745 | 60.3607 | 62.6083 | 62.6404 | 123.1796 | 62.4298 | 60.4248
5639.3125 | 0.13733 | 0.40268 | -0.784 | -0.26169 | 0.11322 | -0.23392 | -0.18692 | 60.553 | -62.2238 | 0.07782 | -62.5168 | 60.553 | 62.5031 | 62.4893 | 0.045776 | -0.081177 | 0.070496 | 0.30334 | -0.13565 | -0.20081 | 0.022888 | 0.054932 | -62.6862 | 60.4614 | 60.4477 | 62.5397 | 62.645 | 123.1567 | 62.4435 | 60.4889
5641.0781 | 0.091553 | 0.41977 | -0.78507 | -0.24994 | 0.11856 | -0.23926 | -0.19012 | 60.5347 | -62.1964 | 0.082397 | -62.5076 | 60.5255 | 62.4847 | 62.4664 | 0.045776 | -0.091858 | 0.061951 | 0.30334 | -0.12604 | -0.21042 | 0.018311 | 0.082397 | -62.6678 | 60.466 | 60.4385 | 62.5351 | 62.6358 | 123.1338 | 62.4344 | 60.4706
5642.7812 | 0.015259 | 0.39841 | -0.78507 | -0.25635 | 0.1004 | -0.25421 | -0.18051 | 60.434 | -62.3062 | -0.018311 | -62.5488 | 60.5255 | 62.471 | 62.4985 | 0.045776 | -0.085449 | 0.060883 | 0.29587 | -0.13351 | -0.18799 | -0.059509 | -0.050354 | -62.7136 | 60.4523 | 60.4523 | 62.5442 | 62.6358 | 123.0789 | 62.4893 | 60.4752
5644.5312 | 0.15259 | 0.43152 | -0.79681 | -0.2713 | 0.11856 | -0.27344 | -0.19333 | 60.3973 | -62.2604 | 0.013733 | -62.5534 | 60.4843 | 62.4939 | 62.4939 | 0.045776 | -0.10574 | 0.064087 | 0.30334 | -0.16449 | -0.19974 | -0.004578 | 0.10071 | -62.6999 | 60.4477 | 60.434 | 62.5488 | 62.6129 | 123.1247 | 62.4344 | 60.4477
5646.2812 | 0.045776 | 0.39734 | -0.80215 | -0.26169 | 0.12817 | -0.28946 | -0.19119 | 60.4706 | -62.1735 | 0.10071 | -62.4847 | 60.4385 | 62.4527 | 62.4573 | 0.045776 | -0.12176 | 0.066223 | 0.28412 | -0.16022 | -0.19333 | 0.059509 | 0.19684 | -62.6358 | 60.3882 | 60.4019 | 62.5122 | 62.6221 | 123.0972 | 62.4298 | 60.4385
5648.0156 | 0.045776 | 0.39948 | -0.76904 | -0.24887 | 0.11215 | -0.24353 | -0.18692 | 60.4248 | -62.2971 | -0.018311 | -62.5397 | 60.5255 | 62.4985 | 62.439 | 0.045776 | -0.10254 | 0.05127 | 0.29159 | -0.13672 | -0.19974 | -0.032043 | -0.041199 | -62.709 | 60.4385 | 60.4248 | 62.5168 | 62.6221 | 123.056 | 62.4664 | 60.4385
5649.7031 | 0.091553 | 0.40482 | -0.77545 | -0.25955 | 0.11429 | -0.2446 | -0.18372 | 60.4935 | -62.1964 | 0.059509 | -62.5076 | 60.498 | 62.4527 | 62.4344 | 0.061035 | -0.093994 | 0.069427 | 0.30121 | -0.13138 | -0.19119 | 0.022888 | 0.068665 | -62.6862 | 60.4248 | 60.4248 | 62.4985 | 62.5763 | 123.0286 | 62.4344 | 60.4752
5651.4531 | 0.045776 | 0.35141 | -0.78934 | -0.2681 | 0.10681 | -0.28519 | -0.21042 | 60.466 | -62.1414 | 0.10986 | -62.4847 | 60.4385 | 62.4619 | 62.4435 | 0.061035 | -0.11643 | 0.060883 | 0.28946 | -0.15701 | -0.1944 | 0.09613 | 0.2243 | -62.5442 | 60.3561 | 60.3699 | 62.4802 | 62.6083 | 123.1201 | 62.4252 | 60.3973
5653.2031 | 0.045776 | 0.40482 | -0.77652 | -0.26169 | 0.12497 | -0.24567 | -0.18906 | 60.4431 | -62.233 | 0.041199 | -62.5168 | 60.5209 | 62.4481 | 62.4298 | 0.015259 | -0.10254 | 0.071564 | 0.29907 | -0.13138 | -0.20721 | -0.022888 | 0.004578 | -62.709 | 60.4294 | 60.4019 | 62.4939 | 62.5946 | 123.0103 | 62.4344 | 60.4614
5654.9062 | 0.045776 | 0.38345 | -0.80322 | -0.26062 | 0.11963 | -0.28305 | -0.19546 | 60.434 | -62.1552 | 0.10071 | -62.4664 | 60.4294 | 62.4573 | 62.4252 | 0.045776 | -0.11856 | 0.066223 | 0.27985 | -0.16342 | -0.19119 | 0.036621 | 0.1831 | -62.6175 | 60.3699 | 60.4019 | 62.4847 | 62.6129 | 123.0743 | 62.4161 | 60.434
5656.6719 | 0.030518 | 0.37277 | -0.77972 | -0.27023 | 0.11749 | -0.28732 | -0.20508 | 60.4614 | -62.1506 | 0.09613 | -62.4939 | 60.4431 | 62.4527 | 62.439 | 0.061035 | -0.12604 | 0.053406 | 0.28519 | -0.15595 | -0.1944 | 0.10529 | 0.20599 | -62.558 | 60.3561 | 60.3745 | 62.4893 | 62.59 | 123.1201 | 62.3886 | 60.3836
5658.375 | 0.030518 | 0.41336 | -0.77438 | -0.25207 | 0.10254 | -0.24353 | -0.18158 | 60.4706 | -62.2467 | 0.032043 | -62.5076 | 60.5072 | 62.4527 | 62.4252 | 0.061035 | -0.09079 | 0.059814 | 0.29907 | -0.13458 | -0.21149 | -0.041199 | -0.018311 | -62.6999 | 60.4568 | 60.4385 | 62.4985 | 62.5763 | 122.9919 | 62.439 | 60.4706
5660.1406 | 0.24414 | 0.35568 | -0.77331 | -0.24246 | 0.11856 | -0.27878 | -0.18906 | 60.4477 | -62.178 | 0.07782 | -62.4847 | 60.3882 | 62.4435 | 62.4207 | 0.061035 | -0.10895 | 0.048065 | 0.29266 | -0.14954 | -0.18478 | 0.091553 | 0.14191 | -62.5534 | 60.3836 | 60.379 | 62.5214 | 62.6312 | 122.9645 | 62.4664 | 60.4385
5661.8281 | 0.045776 | 0.36957 | -0.7872 | -0.2478 | 0.092926 | -0.28732 | -0.20721 | 60.3973 | -62.2009 | 0.050354 | -62.4985 | 60.4431 | 62.4527 | 62.4435 | 0.045776 | -0.11536 | 0.072632 | 0.28839 | -0.15915 | -0.18799 | 0.064087 | 0.17395 | -62.5717 | 60.3287 | 60.3561 | 62.5031 | 62.5763 | 123.0789 | 62.4161 | 60.3836
5663.5625 | 0.21362 | 0.42404 | -0.79681 | -0.25955 | 0.10574 | -0.25528 | -0.19867 | 60.4065 | -62.2421 | 0.009155 | -62.5214 | 60.5072 | 62.4527 | 62.439 | 0.030518 | -0.098267 | 0.055542 | 0.28946 | -0.15274 | -0.21042 | 0 | 0.082397 | -62.677 | 60.4477 | 60.434 | 62.5351 | 62.6175 | 123.0881 | 62.3795 | 60.4111
5665.3125 | 0.030518 | 0.36529 | -0.78293 | -0.2478 | 0.11963 | -0.28839 | -0.20187 | 60.4431 | -62.0956 | 0.10986 | -62.4802 | 60.4294 | 62.4161 | 62.4069 | 0.061035 | -0.12817 | 0.054474 | 0.29159 | -0.15915 | -0.20508 | 0.11444 | 0.21515 | -62.5442 | 60.347 | 60.3333 | 62.4847 | 62.5763 | 123.0789 | 62.4023 | 60.3882
5667 | 0.21362 | 0.4187 | -0.47211 | -0.26916 | -0.20081 | -0.26382 | -0.19012 | 0.059509 | -0.036621 | 0.059509 | 0.018311 | 0.24719 | 0.022888 | 0.20142 | 0.030518 | -0.11002 | -0.27344 | -0.05127 | -0.15488 | -0.19546 | 0.10529 | 0.16479 | -0.091553 | 0.17853 | 0.13275 | 0.11902 | 0.16479 | 0.073242 | 0.045776 | 0.10529
5668.7344 | 0.16785 | 0.41336 | -0.46036 | -0.25528 | -0.19974 | -0.23392 | -0.20294 | 0.16022 | 0.032043 | 0.07782 | 0.073242 | 0.24261 | 0.004578 | 0.17853 | 0.061035 | -0.10147 | -0.27557 | -0.03952 | -0.1442 | -0.20828 | 0.032043 | 0.07782 | -0.059509 | 0.15106 | 0.14191 | 0.086975 | 0.14648 | 0.036621 | 0.041199 | 0.1236
5670.4531 | 0.19836 | 0.35889 | -0.46249 | -0.22964 | -0.22003 | -0.28732 | -0.19974 | 0.068665 | 0.018311 | 0.041199 | 0.027466 | 0.15564 | 0.032043 | 0.17853 | 0.045776 | -0.13245 | -0.27664 | -0.03418 | -0.14954 | -0.18158 | 0.045776 | 0.11444 | 0.013733 | 0.11902 | 0.086975 | 0.14648 | 0.19226 | -0.045776 | 0.1236 | 0.07782
5672.2031 | 0.045776 | 0.35675 | -0.46783 | -0.26276 | -0.21469 | -0.27878 | -0.20187 | 0.073242 | 0.032043 | 0.068665 | 0.068665 | 0.17853 | 0.036621 | 0.18768 | 0.045776 | -0.12176 | -0.29373 | -0.055542 | -0.16663 | -0.20081 | 0.068665 | 0.17853 | 0.036621 | 0.091553 | 0.059509 | 0.12817 | 0.16937 | 0.11444 | 0.064087 | 0.045776
5673.9531 | 0.030518 | 0.35996 | -0.46997 | -0.25528 | -0.20081 | -0.27985 | -0.20828 | 0.10986 | 0.082397 | 0.086975 | 0.064087 | 0.16479 | 0.032043 | 0.17395 | 0.045776 | -0.13138 | -0.29587 | -0.054474 | -0.16556 | -0.20294 | 0.09613 | 0.20142 | 0.059509 | 0.091553 | 0.050354 | 0.10529 | 0.14191 | 0.11902 | 0.050354 | 0.064087
5675.7031 | 0.061035 | 0.39093 | -0.47104 | -0.25528 | -0.20615 | -0.24674 | -0.18906 | 0.07782 | -0.050354 | -0.013733 | 0.032043 | 0.24719 | 0.013733 | 0.17853 | 0.045776 | -0.10147 | -0.28732 | -0.03952 | -0.13245 | -0.20294 | -0.045776 | -0.064087 | -0.10529 | 0.16022 | 0.1236 | 0.11444 | 0.15106 | 0.009155 | 0.07782 | 0.12817
5677.4688 | 0.16785 | 0.41229 | -0.47211 | -0.25848 | -0.20187 | -0.25101 | -0.19867 | 0.082397 | 0.004578 | 0.032043 | 0.082397 | 0.24261 | 0.027466 | 0.16479 | 0.061035 | -0.11215 | -0.27344 | -0.046997 | -0.13886 | -0.20508 | 0.004578 | 0.082397 | -0.050354 | 0.17853 | 0.13275 | 0.09613 | 0.12817 | 0.10986 | 0.013733 | 0.086975
5679.2188 | 0.1831 | 0.36743 | -0.44968 | -0.23712 | -0.20721 | -0.26276 | -0.18478 | 0.11902 | 0.054932 | 0.059509 | 0.07782 | 0.17395 | 0.009155 | 0.17395 | 0.061035 | -0.11429 | -0.28198 | -0.042725 | -0.13458 | -0.20828 | 0.073242 | 0.11902 | 0.045776 | 0.11902 | 0.1236 | 0.13275 | 0.17395 | 0.036621 | 0.068665 | 0.09613
5680.9219 | 0.061035 | 0.4155 | -0.45502 | -0.24674 | -0.21149 | -0.25101 | -0.18051 | 0.09613 | -0.004578 | 0.032043 | 0.050354 | 0.24261 | 0.013733 | 0.17395 | 0.045776 | -0.095062 | -0.28839 | -0.058746 | -0.13351 | -0.20187 | -0.041199 | -0.013733 | -0.09613 | 0.15106 | 0.1236 | 0.10529 | 0.15106 | -0.009155 | 0.068665 | 0.13275
5682.6719 | 0.15259 | 0.37811 | -0.45929 | -0.24674 | -0.20294 | -0.28091 | -0.18906 | 0.07782 | 0.068665 | 0.050354 | 0.036621 | 0.19684 | 0.068665 | 0.25177 | 0.12207 | -0.11429 | -0.28198 | -0.044861 | -0.13351 | -0.18158 | 0.036621 | 0.11444 | 0.027466 | 0.11444 | 0.068665 | 0.14648 | 0.18768 | -0.009155 | 0.10071 | 0.082397
5684.4375 | 0.16785 | 0.36423 | -0.46143 | -0.25742 | -0.21255 | -0.27664 | -0.20508 | 0.07782 | 0.059509 | 0.050354 | 0.045776 | 0.14191 | 0.018311 | 0.15564 | 0.030518 | -0.12283 | -0.29053 | -0.044861 | -0.15808 | -0.19974 | 0.022888 | 0.13275 | 0.027466 | 0.11444 | 0.086975 | 0.17853 | 0.20142 | 0 | 0.10529 | 0.091553
5686.125 | 0.15259 | 0.3685 | -0.46356 | -0.24887 | -0.22003 | -0.27878 | -0.19974 | 0.09613 | 0.041199 | 0.041199 | 0.045776 | 0.14648 | 0.013733 | 0.17853 | 0.030518 | -0.12924 | -0.29266 | -0.042725 | -0.14847 | -0.18158 | 0.050354 | 0.10071 | 0.009155 | 0.11444 | 0.086975 | 0.14191 | 0.1831 | 0 | 0.11444 | 0.068665
5687.875 | 0.045776 | 0.40161 | -0.46356 | -0.24674 | -0.21149 | -0.24567 | -0.19546 | 0.059509 | -0.068665 | -0.004578 | 0.032043 | 0.25177 | 0.018311 | 0.1831 | 0.030518 | -0.091858 | -0.28839 | -0.03418 | -0.13031 | -0.19974 | -0.073242 | -0.045776 | -0.10071 | 0.16022 | 0.14191 | 0.11444 | 0.15564 | 0.004578 | 0.068665 | 0.12817
5689.625 | 0.030518 | 0.38879 | -0.47958 | -0.25955 | -0.20828 | -0.28091 | -0.19546 | 0.1236 | 0.10071 | 0.11902 | 0.082397 | 0.16937 | 0.027466 | 0.15564 | 0.045776 | -0.1239 | -0.29159 | -0.063019 | -0.15488 | -0.18906 | 0.059509 | 0.21057 | 0.022888 | 0.073242 | 0.073242 | 0.09613 | 0.14648 | 0.082397 | 0.036621 | 0.091553
5691.3281 | 0.21362 | 0.41443 | -0.47745 | -0.26169 | -0.1976 | -0.26703 | -0.19974 | 0.059509 | -0.018311 | 0.004578 | 0.036621 | 0.25635 | 0.036621 | 0.20599 | 0.045776 | -0.10254 | -0.28519 | -0.050201 | -0.14526 | -0.20615 | -0.027466 | 0.054932 | -0.082397 | 0.16937 | 0.15106 | 0.1236 | 0.14648 | 0.14191 | 0.004578 | 0.11902
5693.0781 | 0.015259 | 0.37384 | -0.47424 | -0.25314 | -0.20508 | -0.29053 | -0.20935 | 0.13275 | 0.10071 | 0.10529 | 0.086975 | 0.16022 | 0.022888 | 0.16937 | 0.045776 | -0.11643 | -0.29373 | -0.054474 | -0.15488 | -0.1976 | 0.073242 | 0.21973 | 0.041199 | 0.082397 | 0.064087 | 0.10529 | 0.13275 | 0.13275 | 0.050354 | 0.082397
5694.8281 | 0.045776 | 0.39734 | -0.47638 | -0.26062 | -0.20508 | -0.28198 | -0.20508 | 0.10071 | 0.07782 | 0.10529 | 0.086975 | 0.17395 | 0.032043 | 0.17395 | 0.030518 | -0.11963 | -0.28625 | -0.050201 | -0.16022 | -0.20615 | 0.032043 | 0.16022 | 0 | 0.10986 | 0.10071 | 0.11444 | 0.15106 | 0.091553 | 0.032043 | 0.10529
5696.5156 | 0.19836 | 0.41336 | -0.47958 | -0.2478 | -0.20508 | -0.24567 | -0.18906 | 0.073242 | -0.041199 | 0.032043 | 0.050354 | 0.24261 | 0.041199 | 0.17853 | 0.030518 | -0.10147 | -0.27771 | -0.048065 | -0.14847 | -0.20935 | -0.027466 | 0.091553 | -0.068665 | 0.1831 | 0.1236 | 0.10986 | 0.15106 | 0.14191 | 0.018311 | 0.07782
5698.2812 | 0.045776 | 0.38986 | -0.45075 | -0.2478 | -0.19333 | -0.2446 | -0.18265 | 0.068665 | -0.068665 | -0.009155 | 0.041199 | 0.24261 | 0.036621 | 0.1831 | 0.061035 | -0.10254 | -0.26382 | -0.041656 | -0.13672 | -0.19867 | -0.07782 | -0.059509 | -0.11444 | 0.14648 | 0.13733 | 0.10986 | 0.14191 | 0.013733 | 0.09613 | 0.13275
5700.0312 | 0.19836 | 0.40375 | -0.47531 | -0.27344 | -0.21149 | -0.26596 | -0.1976 | 0.041199 | -0.032043 | 0.004578 | 0.027466 | 0.24261 | 0.027466 | 0.1831 | 0.045776 | -0.10468 | -0.28198 | -0.044861 | -0.1474 | -0.20401 | -0.032043 | 0.068665 | -0.064087 | 0.16937 | 0.11902 | 0.10986 | 0.13733 | 0.13275 | 0.013733 | 0.09613
5701.7344 | 0.061035 | 0.41229 | -0.46783 | -0.24674 | -0.20935 | -0.24887 | -0.19226 | 0.018311 | -0.07782 | -0.013733 | 0.022888 | 0.23346 | 0.022888 | 0.16022 | 0.045776 | -0.097198 | -0.27451 | -0.042725 | -0.12924 | -0.20081 | -0.064087 | -0.050354 | -0.091553 | 0.16479 | 0.11444 | 0.11444 | 0.15106 | 0.013733 | 0.073242 | 0.11444
5703.5 | 0.061035 | 0.4155 | -0.45075 | -0.25421 | -0.20828 | -0.25207 | -0.19119 | 0.027466 | -0.059509 | -0.004578 | 0.027466 | 0.23346 | 0.032043 | 0.16479 | 0.030518 | -0.091858 | -0.27878 | -0.044861 | -0.14313 | -0.19653 | -0.068665 | -0.054932 | -0.07782 | 0.13733 | 0.13275 | 0.10986 | 0.16022 | 0.027466 | 0.064087 | 0.1236
5705.25 | 0.045776 | 0.38879 | -0.45181 | -0.25421 | -0.20187 | -0.2478 | -0.1944 | 0.041199 | -0.045776 | -0.018311 | 0.022888 | 0.22888 | 0.022888 | 0.16937 | 0.030518 | -0.10468 | -0.27344 | -0.033112 | -0.1442 | -0.19333 | -0.068665 | -0.050354 | -0.068665 | 0.15106 | 0.11444 | 0.11444 | 0.14648 | 0.050354 | 0.064087 | 0.10529
5706.9531 | 0.061035 | 0.39841 | -0.48172 | -0.26703 | -0.21576 | -0.28625 | -0.20187 | 0.064087 | 0.041199 | 0.082397 | 0.064087 | 0.1831 | 0.032043 | 0.17853 | 0.045776 | -0.11643 | -0.27878 | -0.045929 | -0.16235 | -0.20508 | -0.013733 | 0.11444 | -0.054932 | 0.15106 | 0.11444 | 0.10071 | 0.15564 | 0.10071 | 0.032043 | 0.09613
5708.6406 | 0.19836 | 0.37064 | -0.46677 | -0.26276 | -0.21042 | -0.29694 | -0.20615 | 0.041199 | 0.041199 | 0.027466 | 0.041199 | 0.13733 | 0.027466 | 0.17395 | 0.045776 | -0.13672 | -0.28198 | -0.049133 | -0.15595 | -0.18585 | -0.018311 | 0.073242 | -0.004578 | 0.086975 | 0.050354 | 0.1236 | 0.15564 | 0 | 0.10986 | 0.073242
5710.4062 | 0.045776 | 0.36102 | -0.46463 | -0.25742 | -0.21255 | -0.28732 | -0.21042 | 0.032043 | 0.027466 | 0.050354 | 0.054932 | 0.16937 | 0.032043 | 0.17853 | 0.045776 | -0.13138 | -0.28946 | -0.05661 | -0.1709 | -0.19867 | 0.032043 | 0.14648 | 0.027466 | 0.07782 | 0.064087 | 0.11902 | 0.14648 | 0.13275 | 0.059509 | 0.064087
5712.1719 | 0.045776 | 0.40375 | -0.46356 | -0.23178 | -0.20828 | -0.24139 | -0.18692 | 0.064087 | -0.068665 | -0.032043 | 0.027466 | 0.2243 | 0.027466 | 0.16937 | 0.030518 | -0.087585 | -0.28946 | -0.046997 | -0.1207 | -0.20935 | -0.068665 | -0.059509 | -0.09613 | 0.15564 | 0.11902 | 0.09613 | 0.1236 | 0 | 0.068665 | 0.12817
5713.8594 | 0.10681 | 0.37491 | -0.47745 | -0.24246 | -0.20294 | -0.27451 | -0.20721 | 0.050354 | 0.009155 | 0.032043 | 0.050354 | 0.16022 | 0.022888 | 0.17853 | 0.045776 | -0.11643 | -0.29587 | -0.043793 | -0.16769 | -0.19974 | -0.009155 | 0.059509 | -0.013733 | 0.10071 | 0.082397 | 0.14648 | 0.16937 | 0.022888 | 0.091553 | 0.09613
5715.6094 | 0.045776 | 0.36957 | -0.45715 | -0.24033 | -0.21576 | -0.24887 | -0.19333 | 0.086975 | -0.022888 | 0.022888 | 0.050354 | 0.21973 | 0.013733 | 0.16022 | 0.030518 | -0.11536 | -0.2948 | -0.049133 | -0.13992 | -0.20508 | -0.013733 | 0.027466 | -0.013733 | 0.07782 | 0.064087 | 0.10529 | 0.12817 | 0.050354 | 0.091553 | 0.07782
5717.2969 | 0.16785 | 0.42938 | -0.47104 | -0.28091 | -0.20294 | -0.26382 | -0.20294 | 0.022888 | -0.009155 | 0.032043 | 0.022888 | 0.21973 | 0.022888 | 0.19226 | 0.030518 | -0.10788 | -0.27344 | -0.05127 | -0.15701 | -0.19653 | -0.032043 | 0.068665 | -0.07782 | 0.16022 | 0.14191 | 0.10986 | 0.14191 | 0.1236 | 0.036621 | 0.10986
5719.0469 | 0.061035 | 0.41122 | -0.45715 | -0.25101 | -0.21362 | -0.24246 | -0.19226 | 0.027466 | -0.054932 | -0.022888 | 0.036621 | 0.23346 | 0.018311 | 0.17853 | 0.030518 | -0.099335 | -0.27771 | -0.037384 | -0.13351 | -0.19974 | -0.068665 | -0.054932 | -0.09613 | 0.13733 | 0.12817 | 0.082397 | 0.15106 | 0.027466 | 0.054932 | 0.10529
5720.7969 | 0.16785 | 0.35889 | -0.46783 | -0.24674 | -0.20508 | -0.27557 | -0.19333 | 0.07782 | 0.068665 | 0.054932 | 0.054932 | 0.14648 | 0.041199 | 0.16479 | 0.061035 | -0.12497 | -0.27557 | -0.033112 | -0.12283 | -0.17303 | 0.036621 | 0.11902 | 0.022888 | 0.09613 | 0.086975 | 0.15106 | 0.17853 | -0.004578 | 0.11902 | 0.086975
5722.5781 | 0.030518 | 0.41229 | -0.4892 | -0.27878 | -0.19119 | -0.27237 | -0.20187 | 0.054932 | 0.036621 | 0.068665 | 0.050354 | 0.20599 | 0.032043 | 0.17395 | 0.030518 | -0.11429 | -0.27664 | -0.057678 | -0.15274 | -0.20187 | -0.018311 | 0.10071 | -0.059509 | 0.14191 | 0.11902 | 0.11902 | 0.15564 | 0.07782 | 0.036621 | 0.10986
5724.2656 | 0.091553 | 0.40802 | -0.45395 | -0.27237 | -0.1976 | -0.2478 | -0.18478 | 0.10529 | 0.032043 | 0.07782 | 0.091553 | 0.22888 | 0.022888 | 0.16022 | 0.030518 | -0.091858 | -0.27664 | -0.050201 | -0.13565 | -0.19974 | 0.027466 | 0.09613 | -0.027466 | 0.14648 | 0.11444 | 0.082397 | 0.13275 | 0.13275 | 0.032043 | 0.086975
5726.0156 | 0.1831 | 0.41763 | -0.46036 | -0.2681 | -0.20081 | -0.27557 | -0.20508 | 0.027466 | -0.027466 | 0.022888 | 0.045776 | 0.21973 | 0.027466 | 0.19684 | 0.045776 | -0.10361 | -0.27451 | -0.049133 | -0.1442 | -0.20828 | -0.032043 | 0.07782 | -0.064087 | 0.15564 | 0.12817 | 0.09613 | 0.13275 | 0.13733 | 0.022888 | 0.10986
5727.7656 | 0.13733 | 0.40909 | -0.45609 | -0.25101 | -0.20401 | -0.24674 | -0.19226 | 0.09613 | 0.050354 | 0.091553 | 0.082397 | 0.22888 | 0.004578 | 0.14648 | 0.061035 | -0.10788 | -0.27557 | -0.042725 | -0.13992 | -0.20401 | 0.018311 | 0.086975 | -0.032043 | 0.14191 | 0.12817 | 0.091553 | 0.13275 | 0.10529 | 0.009155 | 0.10986
5729.4688 | 0.15259 | 0.37491 | -0.46677 | -0.24994 | -0.21683 | -0.28946 | -0.20401 | 0.036621 | 0.027466 | 0.027466 | 0.032043 | 0.15564 | 0.027466 | 0.17853 | 0.030518 | -0.1207 | -0.28519 | -0.049133 | -0.16983 | -0.19546 | -0.022888 | 0.07782 | -0.013733 | 0.082397 | 0.082397 | 0.12817 | 0.16022 | 0.013733 | 0.10986 | 0.073242
5731.2188 | 0.13733 | 0.41229 | -0.46463 | -0.26169 | -0.1976 | -0.2446 | -0.1976 | 0.14648 | 0.036621 | 0.07782 | 0.09613 | 0.24719 | 0 | 0.16022 | 0.030518 | -0.092926 | -0.28625 | -0.049133 | -0.14206 | -0.20294 | 0.013733 | 0.064087 | -0.050354 | 0.14648 | 0.12817 | 0.07782 | 0.11902 | 0.082397 | 0.041199 | 0.11902
5732.9688 | 0.076294 | 0.40375 | -0.47104 | -0.25955 | -0.20721 | -0.28732 | -0.1976 | 0.086975 | 0.059509 | 0.086975 | 0.07782 | 0.17853 | 0.022888 | 0.16479 | 0.045776 | -0.11963 | -0.2713 | -0.060883 | -0.16235 | -0.19974 | 0.009155 | 0.15564 | -0.013733 | 0.11444 | 0.10529 | 0.10071 | 0.15106 | 0.091553 | 0.032043 | 0.091553
5734.7031 | 0.10681 | 0.40588 | -0.4689 | -0.26382 | -0.20615 | -0.2446 | -0.19546 | 0.11902 | 0 | 0.064087 | 0.086975 | 0.23804 | 0.027466 | 0.17853 | 0.015259 | -0.099335 | -0.27023 | -0.048065 | -0.12924 | -0.19333 | 0.004578 | 0.082397 | -0.009155 | 0.15106 | 0.12817 | 0.09613 | 0.1236 | 0.13733 | 0.013733 | 0.10986
5736.4062 | 0.030518 | 0.35568 | -0.4689 | -0.2478 | -0.21255 | -0.30548 | -0.19653 | 0.082397 | 0.050354 | 0.068665 | 0.068665 | 0.16937 | 0.054932 | 0.17395 | 0.045776 | -0.12711 | -0.28091 | -0.053406 | -0.17197 | -0.18692 | 0.050354 | 0.17853 | 0.050354 | 0.073242 | 0.054932 | 0.1236 | 0.13733 | 0.15106 | 0.050354 | 0.064087
5738.1562 | 0.045776 | 0.40054 | -0.4657 | -0.24994 | -0.21149 | -0.24994 | -0.1944 | 0.045776 | -0.09613 | -0.009155 | 0.018311 | 0.23804 | 0 | 0.18768 | 0.061035 | -0.087585 | -0.27451 | -0.035248 | -0.12497 | -0.20401 | -0.073242 | -0.054932 | -0.09613 | 0.1831 | 0.13733 | 0.10529 | 0.12817 | 0.009155 | 0.086975 | 0.10986
5739.9062 | 0.030518 | 0.37384 | -0.45288 | -0.23392 | -0.20401 | -0.26382 | -0.19119 | 0.07782 | -0.022888 | 0.009155 | 0.059509 | 0.20599 | 0.018311 | 0.15106 | 0.061035 | -0.10681 | -0.28412 | -0.037384 | -0.13992 | -0.19333 | -0.027466 | 0.013733 | 0 | 0.11902 | 0.073242 | 0.091553 | 0.12817 | 0.059509 | 0.068665 | 0.073242
5741.6562 | 0.045776 | 0.40802 | -0.45395 | -0.25314 | -0.20935 | -0.26062 | -0.19546 | 0.059509 | -0.064087 | 0 | 0.036621 | 0.23804 | 0.018311 | 0.15106 | 0.061035 | -0.091858 | -0.27771 | -0.048065 | -0.14313 | -0.21362 | -0.07782 | -0.054932 | -0.091553 | 0.17395 | 0.14191 | 0.091553 | 0.16022 | 0.004578 | 0.068665 | 0.10529
5743.3594 | 0.091553 | 0.36209 | -0.47424 | -0.26596 | -0.20508 | -0.29587 | -0.19119 | 0.036621 | 0 | 0.018311 | 0.059509 | 0.16022 | 0.022888 | 0.16937 | 0.061035 | -0.13565 | -0.27451 | -0.049133 | -0.16876 | -0.19333 | -0.041199 | 0.064087 | -0.022888 | 0.073242 | 0.054932 | 0.1236 | 0.16479 | 0.027466 | 0.10071 | 0.09613
5745.1094 | 0.10681 | 0.40054 | -0.44968 | -0.26596 | -0.20721 | -0.25101 | -0.20187 | 0.15106 | 0.045776 | 0.059509 | 0.07782 | 0.20599 | 0 | 0.15106 | 0.061035 | -0.095062 | -0.2713 | -0.03418 | -0.14313 | -0.22003 | 0 | 0.045776 | -0.054932 | 0.14648 | 0.12817 | 0.10071 | 0.12817 | 0.050354 | 0.041199 | 0.13275
5746.8594 | 0.045776 | 0.40054 | -0.47531 | -0.2681 | -0.1944 | -0.28732 | -0.20935 | 0.064087 | 0.050354 | 0.064087 | 0.068665 | 0.17853 | 0.036621 | 0.19226 | 0.045776 | -0.11108 | -0.27878 | -0.048065 | -0.15381 | -0.18799 | -0.004578 | 0.11902 | -0.036621 | 0.13275 | 0.10529 | 0.12817 | 0.14191 | 0.091553 | 0.013733 | 0.10071
5748.625 | 0.21362 | 0.35675 | -0.46143 | -0.25314 | -0.20615 | -0.27023 | -0.20081 | 0.086975 | 0.068665 | 0.068665 | 0.091553 | 0.14191 | 0.009155 | 0.16022 | 0.030518 | -0.12711 | -0.28412 | -0.048065 | -0.13779 | -0.18585 | 0.054932 | 0.11902 | 0.064087 | 0.09613 | 0.09613 | 0.13275 | 0.17395 | -0.004578 | 0.10986 | 0.086975
5750.3906 | 0.22888 | 0.35034 | -0.4454 | -0.23071 | -0.20935 | -0.25848 | -0.18478 | 0.10529 | 0.082397 | 0.086975 | 0.086975 | 0.15106 | 0.004578 | 0.17395 | 0.045776 | -0.11429 | -0.27451 | -0.048065 | -0.14313 | -0.18906 | 0.068665 | 0.12817 | 0.050354 | 0.11444 | 0.073242 | 0.15106 | 0.18768 | 0.009155 | 0.10986 | 0.064087
5752.1562 | 0.045776 | 0.37705 | -0.48172 | -0.2681 | -0.21255 | -0.28625 | -0.19974 | 0.086975 | 0.09613 | 0.10071 | 0.091553 | 0.15106 | 0.018311 | 0.17395 | 0.045776 | -0.12176 | -0.28412 | -0.05127 | -0.15915 | -0.1976 | 0.064087 | 0.20599 | 0.022888 | 0.082397 | 0.073242 | 0.091553 | 0.13733 | 0.091553 | 0.045776 | 0.07782
5753.8281 | 0.061035 | 0.36636 | -0.48172 | -0.24567 | -0.20615 | -0.27878 | -0.19333 | 0.12817 | 0.10071 | 0.091553 | 0.091553 | 0.15564 | 0.027466 | 0.15564 | 0.030518 | -0.1239 | -0.29373 | -0.057678 | -0.15808 | -0.19653 | 0.082397 | 0.20142 | 0.082397 | 0.07782 | 0.045776 | 0.09613 | 0.14191 | 0.15106 | 0.045776 | 0.050354
5755.5938 | 0.061035 | 0.41443 | -0.46249 | -0.24246 | -0.20401 | -0.24246 | -0.1976 | 0.07782 | -0.050354 | -0.027466 | 0.041199 | 0.23346 | 0.013733 | 0.15564 | 0.045776 | -0.093994 | -0.28412 | -0.038452 | -0.13245 | -0.21149 | -0.059509 | -0.068665 | -0.10529 | 0.14648 | 0.1236 | 0.10986 | 0.13733 | 0.036621 | 0.07782 | 0.1236
5757.3438 | 0.061035 | 0.41443 | -0.47211 | -0.26489 | -0.19974 | -0.23285 | -0.18799 | 0.10071 | 0.032043 | 0.045776 | 0.050354 | 0.20599 | 0.004578 | 0.16479 | 0.045776 | -0.10254 | -0.28412 | -0.046997 | -0.13458 | -0.21255 | -0.013733 | 0.022888 | -0.068665 | 0.13733 | 0.1236 | 0.11444 | 0.14648 | 0.018311 | 0.041199 | 0.10529
5759.0312 | 0.22888 | 0.35568 | -0.45502 | -0.25101 | -0.19653 | -0.2713 | -0.20294 | 0.086975 | 0.091553 | 0.064087 | 0.068665 | 0.12817 | 0.032043 | 0.16022 | 0.030518 | -0.12711 | -0.27451 | -0.033112 | -0.13565 | -0.18372 | 0.045776 | 0.13733 | 0.064087 | 0.09613 | 0.086975 | 0.15106 | 0.18768 | 0.013733 | 0.10986 | 0.068665
5760.7812 | 0.061035 | 0.35675 | -0.4657 | -0.27344 | -0.20935 | -0.30121 | -0.20294 | 0.013733 | 0.013733 | 0.018311 | 0.041199 | 0.16022 | 0.045776 | 0.16937 | 0.045776 | -0.12283 | -0.27985 | -0.042725 | -0.16556 | -0.19653 | 0 | 0.10986 | 0.013733 | 0.07782 | 0.050354 | 0.09613 | 0.13275 | 0.10071 | 0.068665 | 0.059509
5762.5781 | 0.045776 | 0.39307 | -0.45075 | -0.2446 | -0.19974 | -0.24887 | -0.18585 | 0.054932 | -0.054932 | -0.009155 | 0.041199 | 0.25177 | 0.018311 | 0.16937 | 0.045776 | -0.09613 | -0.29373 | -0.046997 | -0.14847 | -0.19974 | -0.054932 | -0.045776 | -0.10071 | 0.12817 | 0.13275 | 0.091553 | 0.15106 | 0.054932 | 0.07782 | 0.09613
5764.3281 | 0.10681 | 0.41977 | -0.46356 | -0.25528 | -0.20081 | -0.26062 | -0.19867 | 0.12817 | 0.027466 | 0.050354 | 0.073242 | 0.20142 | 0.022888 | 0.13275 | 0.045776 | -0.097198 | -0.28732 | -0.040588 | -0.13458 | -0.20935 | 0.013733 | 0.086975 | -0.018311 | 0.15564 | 0.11902 | 0.09613 | 0.13275 | 0.1236 | 0.013733 | 0.086975
5766.0156 | 0.045776 | 0.36529 | -0.4689 | -0.25955 | -0.21896 | -0.30868 | -0.21042 | 0.045776 | 0.032043 | 0.054932 | 0.064087 | 0.15106 | 0.022888 | 0.17853 | 0.045776 | -0.11963 | -0.28839 | -0.05661 | -0.16556 | -0.1976 | 0.027466 | 0.15106 | 0.032043 | 0.086975 | 0.059509 | 0.10986 | 0.16479 | 0.1236 | 0.045776 | 0.059509
5767.7812 | 0.16785 | 0.35782 | -0.46249 | -0.24994 | -0.20508 | -0.25955 | -0.19226 | 0.11444 | 0.054932 | 0.064087 | 0.091553 | 0.16937 | 0.018311 | 0.15106 | 0.045776 | -0.11749 | -0.28519 | -0.053406 | -0.1442 | -0.20508 | 0.027466 | 0.11444 | 0.068665 | 0.11444 | 0.09613 | 0.16022 | 0.17395 | 0.054932 | 0.091553 | 0.068665
5769.5469 | 0.10681 | 0.35675 | -0.46249 | -0.26596 | -0.21042 | -0.29159 | -0.20935 | 0.050354 | 0.022888 | 0.036621 | 0.045776 | 0.15106 | 0.013733 | 0.19226 | 0.015259 | -0.13031 | -0.28625 | -0.058746 | -0.15488 | -0.19546 | 0 | 0.068665 | -0.009155 | 0.059509 | 0.073242 | 0.12817 | 0.16022 | 0.009155 | 0.10986 | 0.073242
5771.2344 | 0.045776 | 0.38879 | -0.45288 | -0.24567 | -0.21042 | -0.24994 | -0.20294 | 0.059509 | -0.027466 | -0.022888 | 0.027466 | 0.23346 | 0.022888 | 0.17853 | 0.015259 | -0.098267 | -0.27878 | -0.046997 | -0.13458 | -0.1944 | -0.050354 | -0.045776 | -0.064087 | 0.13733 | 0.10071 | 0.11444 | 0.15564 | 0.050354 | 0.086975 | 0.09613
5773 | 0.19836 | 0.41657 | -0.47424 | -0.28839 | -0.20081 | -0.26062 | -0.20081 | 0.054932 | -0.036621 | 0.013733 | 0.009155 | 0.2243 | 0.036621 | 0.1831 | 0.030518 | -0.10681 | -0.27878 | -0.041656 | -0.16556 | -0.18906 | -0.022888 | 0.073242 | -0.082397 | 0.21515 | 0.1831 | 0.15106 | 0.18768 | 0.1236 | 0.027466 | 0.10986
5774.6875 | 0.030518 | 0.42191 | -0.48386 | -0.26062 | -0.19653 | -0.27344 | -0.20615 | 0.041199 | 0.004578 | 0.036621 | 0.045776 | 0.21973 | 0.018311 | 0.17395 | 0.061035 | -0.11002 | -0.27878 | -0.05127 | -0.14847 | -0.20401 | 0 | 0.073242 | -0.054932 | 0.13733 | 0.14191 | 0.10986 | 0.16022 | 0.10071 | 0.032043 | 0.11444
5776.4531 | 0.13733 | 0.35996 | -0.4657 | -0.2446 | -0.20721 | -0.28946 | -0.1976 | 0.036621 | 0.004578 | 0.018311 | 0.036621 | 0.15106 | 0.036621 | 0.16022 | 0.030518 | -0.1207 | -0.28412 | -0.053406 | -0.16342 | -0.19546 | -0.018311 | 0.059509 | -0.013733 | 0.086975 | 0.073242 | 0.11902 | 0.15106 | 0.009155 | 0.10986 | 0.082397
5778.1562 | 0.061035 | 0.37811 | -0.47211 | -0.2446 | -0.20401 | -0.26596 | -0.20401 | 0.1236 | 0.082397 | 0.091553 | 0.09613 | 0.15564 | 0.027466 | 0.1831 | 0.045776 | -0.12176 | -0.29373 | -0.054474 | -0.15701 | -0.20187 | 0.068665 | 0.21515 | 0.041199 | 0.068665 | 0.059509 | 0.086975 | 0.1236 | 0.12817 | 0.041199 | 0.064087
5779.9219 | 0.045776 | 0.38986 | -0.47104 | -0.2478 | -0.21042 | -0.24567 | -0.18158 | 0.064087 | -0.036621 | -0.018311 | 0.027466 | 0.2243 | 0.027466 | 0.16022 | 0.061035 | -0.11749 | -0.28946 | -0.05127 | -0.13672 | -0.20615 | -0.045776 | -0.027466 | -0.07782 | 0.13733 | 0.10071 | 0.086975 | 0.15106 | 0.045776 | 0.082397 | 0.09613
5781.6562 | 0.19836 | 0.42404 | -0.47211 | -0.25955 | -0.19974 | -0.26062 | -0.19867 | 0.059509 | -0.022888 | 0.013733 | 0.041199 | 0.21515 | 0.036621 | 0.16479 | 0.061035 | -0.1004 | -0.28839 | -0.042725 | -0.14313 | -0.1976 | -0.018311 | 0.068665 | -0.054932 | 0.15564 | 0.1236 | 0.10071 | 0.13733 | 0.15564 | 0.009155 | 0.086975
5783.3594 | 0.030518 | 0.41229 | -0.4657 | -0.25207 | -0.20508 | -0.25101 | -0.18799 | 0.11444 | -0.013733 | 0.027466 | 0.054932 | 0.21973 | 0.013733 | 0.15564 | 0.061035 | -0.087585 | -0.28198 | -0.046997 | -0.13351 | -0.20615 | -0.064087 | -0.009155 | -0.091553 | 0.15564 | 0.1236 | 0.09613 | 0.13275 | 0.013733 | 0.073242 | 0.13733
5785.1094 | 0.076294 | 0.40268 | -0.4657 | -0.26276 | -0.20935 | -0.25742 | -0.18906 | 0.11444 | 0.059509 | 0.07782 | 0.086975 | 0.23804 | 0.004578 | 0.17395 | 0.061035 | -0.10361 | -0.27771 | -0.03952 | -0.14206 | -0.19974 | 0.018311 | 0.082397 | -0.041199 | 0.14648 | 0.10529 | 0.082397 | 0.10529 | 0.09613 | 0.041199 | 0.10071
5786.8125 | 0.13733 | 0.40375 | -0.45395 | -0.26489 | -0.20401 | -0.25528 | -0.19012 | 0.086975 | 0.018311 | 0.073242 | 0.07782 | 0.21057 | 0.009155 | 0.15106 | 0.045776 | -0.10254 | -0.29053 | -0.050201 | -0.13992 | -0.20187 | 0.009155 | 0.082397 | -0.032043 | 0.15564 | 0.1236 | 0.10986 | 0.13275 | 0.11902 | 0.022888 | 0.10529
5788.5625 | 0.16785 | 0.42084 | -0.47638 | -0.26062 | -0.20935 | -0.27771 | -0.21576 | 0.041199 | -0.013733 | 0.045776 | 0.027466 | 0.21973 | 0.050354 | 0.1831 | 0.030518 | -0.10895 | -0.27771 | -0.043793 | -0.16022 | -0.20294 | -0.032043 | 0.07782 | -0.059509 | 0.13275 | 0.13275 | 0.10529 | 0.15106 | 0.11902 | 0.022888 | 0.10529
5790.3281 | 0.19836 | 0.42511 | -0.46997 | -0.25207 | -0.21149 | -0.26596 | -0.20401 | 0.050354 | -0.050354 | 0.013733 | 0.041199 | 0.23346 | 0.013733 | 0.16937 | 0.030518 | -0.10574 | -0.28519 | -0.043793 | -0.14633 | -0.19974 | -0.045776 | 0.059509 | -0.07782 | 0.15564 | 0.13733 | 0.10986 | 0.15106 | 0.13733 | 0.022888 | 0.11444
5792.0938 | 0.091553 | 0.36102 | -0.47958 | -0.24674 | -0.20187 | -0.28519 | -0.20294 | 0.041199 | -0.009155 | 0.013733 | 0.032043 | 0.15564 | 0.036621 | 0.16937 | 0.061035 | -0.11643 | -0.28519 | -0.059814 | -0.15701 | -0.18906 | -0.027466 | 0.07782 | -0.013733 | 0.091553 | 0.073242 | 0.12817 | 0.16022 | 0.022888 | 0.10071 | 0.073242
5793.7812 | 0.030518 | 0.39948 | -0.45395 | -0.25955 | -0.21683 | -0.25421 | -0.20294 | 0.068665 | -0.054932 | -0.013733 | 0.032043 | 0.22888 | 0.018311 | 0.17395 | 0.045776 | -0.10468 | -0.27451 | -0.032043 | -0.14847 | -0.19867 | -0.073242 | -0.064087 | -0.09613 | 0.16022 | 0.11444 | 0.10071 | 0.14648 | 0.018311 | 0.068665 | 0.1236
5795.5469 | 0.13733 | 0.41336 | -0.4689 | -0.24674 | -0.20828 | -0.25207 | -0.1944 | 0.10529 | 0.018311 | 0.064087 | 0.091553 | 0.21515 | 0.027466 | 0.16022 | 0.061035 | -0.095062 | -0.28412 | -0.041656 | -0.14099 | -0.21042 | 0.018311 | 0.086975 | -0.041199 | 0.15564 | 0.1236 | 0.086975 | 0.12817 | 0.1236 | 0.022888 | 0.091553
5797.2344 | 0.030518 | 0.37598 | -0.45609 | -0.25101 | -0.21149 | -0.25955 | -0.19546 | 0.054932 | -0.050354 | -0.027466 | 0.018311 | 0.20599 | 0.027466 | 0.16022 | 0.015259 | -0.10468 | -0.27878 | -0.043793 | -0.13351 | -0.19012 | -0.045776 | -0.022888 | -0.045776 | 0.13275 | 0.10986 | 0.11444 | 0.12817 | 0.045776 | 0.086975 | 0.082397
5799 | 0.091553 | 0.4155 | -0.46677 | -0.2478 | -0.20508 | -0.25207 | -0.18478 | 0.13275 | 0.027466 | 0.064087 | 0.082397 | 0.22888 | 0.027466 | 0.16022 | 0.030518 | -0.10574 | -0.28091 | -0.041656 | -0.13779 | -0.21149 | -0.009155 | 0.050354 | -0.050354 | 0.13733 | 0.14191 | 0.10071 | 0.12817 | 0.054932 | 0.036621 | 0.10986
5800.75 | 0.045776 | 0.40482 | -0.4454 | -0.23392 | -0.19867 | -0.25421 | -0.19974 | 0.027466 | -0.050354 | -0.013733 | 0.041199 | 0.2243 | 0.036621 | 0.18768 | 0.045776 | -0.10895 | -0.27023 | -0.044861 | -0.13672 | -0.19546 | -0.07782 | -0.064087 | -0.09613 | 0.16022 | 0.13275 | 0.10071 | 0.13275 | 0.027466 | 0.091553 | 0.1236
5802.4531 | 0.045776 | 0.42191 | -0.46677 | -0.24674 | -0.19546 | -0.26169 | -0.18585 | 0.036621 | -0.064087 | -0.009155 | 0.041199 | 0.23804 | 0.027466 | 0.17395 | 0.045776 | -0.10895 | -0.28732 | -0.035248 | -0.14206 | -0.19546 | -0.073242 | -0.045776 | -0.07782 | 0.15106 | 0.13733 | 0.091553 | 0.14191 | 0.004578 | 0.082397 | 0.10986
5804.2031 | 0.030518 | 0.36529 | -0.45609 | -0.25207 | -0.20508 | -0.26169 | -0.19974 | 0.091553 | 0.027466 | 0.036621 | 0.086975 | 0.16937 | 0 | 0.14648 | 0.030518 | -0.11749 | -0.27557 | -0.042725 | -0.1474 | -0.19226 | -0.004578 | 0.059509 | 0.013733 | 0.11902 | 0.09613 | 0.13275 | 0.17853 | 0.059509 | 0.086975 | 0.07782
5805.9688 | 0.1831 | 0.36423 | -0.44861 | -0.2478 | -0.20187 | -0.28412 | -0.1976 | 0.082397 | 0.07782 | 0.082397 | 0.068665 | 0.13275 | 0.009155 | 0.16022 | 0.030518 | -0.11215 | -0.29159 | -0.044861 | -0.14206 | -0.17517 | 0.041199 | 0.11902 | 0.041199 | 0.10071 | 0.086975 | 0.13733 | 0.18768 | -0.013733 | 0.10529 | 0.082397
5807.7344 | 0.1831 | 0.40161 | -0.48386 | -0.27664 | -0.21149 | -0.25955 | -0.20187 | 0.054932 | -0.036621 | 0.022888 | 0.059509 | 0.2243 | 0.018311 | 0.17853 | 0.061035 | -0.10361 | -0.28412 | -0.045929 | -0.14313 | -0.21149 | -0.041199 | 0.073242 | -0.041199 | 0.16022 | 0.11902 | 0.091553 | 0.12817 | 0.15564 | 0.036621 | 0.07782
5809.5 | 0.1831 | 0.35355 | -0.4657 | -0.2446 | -0.19974 | -0.28412 | -0.19974 | 0.059509 | 0.018311 | 0.013733 | 0.041199 | 0.15106 | 0.036621 | 0.17395 | 0.061035 | -0.12924 | -0.28732 | -0.060883 | -0.16129 | -0.19653 | -0.027466 | 0.091553 | -0.004578 | 0.086975 | 0.082397 | 0.10529 | 0.16937 | 0.009155 | 0.10986 | 0.073242
5811.25 | 0.21362 | 0.34714 | -0.46783 | -0.23285 | -0.20401 | -0.2681 | -0.20508 | 0.1236 | 0.059509 | 0.07782 | 0.086975 | 0.15106 | 0.013733 | 0.13733 | 0.061035 | -0.11749 | -0.28305 | -0.044861 | -0.13458 | -0.19119 | 0.054932 | 0.13275 | 0.073242 | 0.10071 | 0.086975 | 0.16479 | 0.17853 | 0.013733 | 0.10529 | 0.054932
5812.9531 | 0.061035 | 0.37384 | -0.45929 | -0.24033 | -0.20828 | -0.25742 | -0.20615 | 0.068665 | -0.022888 | 0 | 0.041199 | 0.21515 | 0.018311 | 0.15564 | 0.061035 | -0.10681 | -0.27664 | -0.052338 | -0.14206 | -0.21149 | -0.027466 | -0.004578 | -0.041199 | 0.10529 | 0.082397 | 0.10986 | 0.12817 | 0.064087 | 0.082397 | 0.07782
5814.7188 | 0.045776 | 0.41016 | -0.45822 | -0.24033 | -0.21149 | -0.24887 | -0.1944 | 0.082397 | -0.036621 | 0.018311 | 0.045776 | 0.21057 | 0.027466 | 0.16479 | 0.030518 | -0.098267 | -0.29159 | -0.037384 | -0.13351 | -0.20828 | -0.073242 | -0.036621 | -0.10529 | 0.15564 | 0.1236 | 0.09613 | 0.13275 | 0.013733 | 0.086975 | 0.13733
5816.4219 | 0.091553 | 0.42404 | -0.45288 | -0.26062 | -0.21255 | -0.25528 | -0.19333 | 0.13275 | 0.022888 | 0.073242 | 0.082397 | 0.22888 | 0.009155 | 0.15564 | 0.030518 | -0.088654 | -0.28091 | -0.040588 | -0.13565 | -0.20187 | -0.013733 | 0.050354 | -0.050354 | 0.13733 | 0.11444 | 0.086975 | 0.11902 | 0.050354 | 0.050354 | 0.10986
5818.1719 | 0.030518 | -0.57999 | -0.41229 | -0.11002 | -0.20294 | -0.42831 | -0.10788 | 0.032043 | -0.013733 | 0.022888 | 0.054932 | 0.15564 | -0.013733 | 0.16479 | 0.045776 | 0.20187 | -0.097198 | -0.086517 | -0.10895 | -0.10788 | -0.082397 | 0.018311 | -0.032043 | 0.073242 | 0.068665 | 0.07782 | 0.09613 | -0.1236 | -9.1599 | -8.812
5819.8594 | 0.045776 | 0.001068 | -0.001068 | 0.007477 | -0.024567 | 0.012817 | 0.004272 | 11.1649 | 9.8282 | 11.9476 | 16.8274 | 0.022888 | 0.013733 | 0.013733 | 0.061035 | 0.008545 | -0.005341 | 0.002136 | 0.009613 | -0.10788 | 10.7529 | 12.2314 | 10.6339 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 13.3163 | 0.022888 | 0.018311
5821.6094 | 0.061035 | 0 | 0.003204 | 0.012817 | -0.024567 | 0.014954 | 0.010681 | -8.2764 | -21.2265 | -5.0674 | 7.8003 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.007477 | -0.001068 | 0.001068 | 0.013885 | 0.009613 | -22.0139 | -19.455 | -8.3588 | 0.004578 | 0.018311 | 0.013733 | 0.009155 | 11.3022 | 0.022888 | 0.018311
5823.3125 | 0.030518 | 0.001068 | 0.001068 | 0.006409 | -0.011749 | 0.010681 | 0.009613 | 4.3167 | -16.3513 | -13.6963 | -0.054932 | 0.013733 | 0.004578 | 0.013733 | 0.030518 | 0.005341 | 0 | 0.004272 | 0.011749 | 0.011749 | -16.6489 | -16.832 | -16.6718 | 0.013733 | 0.004578 | 0.013733 | 0.013733 | 8.0978 | 0.018311 | 0.018311
5825 | 0.030518 | 0.002136 | 0.002136 | 0.005341 | -0.006409 | 0.008545 | 0.008545 | 9.0683 | -14.1174 | -13.0096 | -4.5822 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0.010681 | 0.011749 | -14.4196 | -14.5706 | -14.4882 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 6.2073 | 0.022888 | 0.022888
5826.75 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0 | 0.005341 | 0.006409 | 10.8765 | -13.0508 | -11.0413 | -6.0196 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.001068 | 0.001068 | 0.008545 | 0.009613 | -11.9156 | -13.5086 | -13.4354 | 0.013733 | 0.009155 | 0.018311 | 0.009155 | 4.8065 | 0.022888 | 0.018311
5828.4531 | 0.045776 | 0.003204 | 0 | 0.002136 | -0.001068 | 0.005341 | 0.006409 | 11.3846 | -12.3367 | -9.4162 | -5.3925 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.008545 | 0.010681 | -3.1677 | -12.9227 | -12.8723 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 3.9047 | 0.022888 | 0.018311
5830.2031 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.005341 | 11.261 | -9.9564 | -7.4707 | -4.5273 | 0.013733 | 0.022888 | 0.009155 | 0.045776 | 0.004272 | 0.003204 | 0.001068 | 0.005341 | 0.007477 | 3.4515 | -12.5153 | -12.5153 | 0.009155 | 0.004578 | 0.018311 | 0.013733 | 3.1128 | 0.022888 | 0.018311
5831.8906 | 0.030518 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.003204 | 0.004272 | 10.6934 | -7.1182 | -5.6396 | -3.6987 | 0.013733 | 0.009155 | 0.018311 | 0.030518 | 0.004272 | 0 | 0.003204 | 0.004272 | 0.009613 | 9.8099 | -10.5789 | -12.2589 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 2.4811 | 0.022888 | 0.013733
5833.6719 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | 10.1807 | -4.2938 | -4.0878 | -2.9251 | 0.009155 | 0.009155 | 0.004578 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.007477 | 13.7878 | -5.7358 | -12.0438 | 0.004578 | 0.004578 | 0.013733 | 0.013733 | 1.9547 | 0.022888 | 0.009155
5835.3594 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | 9.3658 | -2.1698 | -2.9114 | -2.2659 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.005341 | 14.4241 | -2.3483 | -11.7874 | 0 | 0.013733 | 0.013733 | 0.009155 | 1.5198 | 0.022888 | 0.009155
5837.125 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0.002136 | 0 | 0.002136 | 8.6929 | -0.48065 | -2.005 | -1.7349 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.006409 | 14.4379 | 0.54474 | -10.7574 | 0.004578 | 0.009155 | 0.013733 | 0.018311 | 1.3 | 0.013733 | 0.009155
5838.875 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 8.0292 | 0.90637 | -1.181 | -1.236 | 0.009155 | 0.013733 | 0.009155 | 0.015259 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.005341 | 14.3875 | 3.8269 | -8.2031 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 1.1261 | 0.018311 | 0.018311
5840.6406 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 7.3151 | 1.8814 | -0.66376 | -0.81482 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.004272 | 14.3372 | 7.608 | -5.2597 | 0.009155 | 0.009155 | 0.009155 | 0.009155 | 1.1124 | 0.018311 | 0.018311
5842.4062 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 6.6193 | 2.6001 | -0.082397 | -0.38452 | 0.018311 | 0.022888 | 0.013733 | 0.030518 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.004272 | 14.2593 | 10.8994 | -2.5223 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.8194 | 0.013733 | 0.018311
5844.0938 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 5.928 | 3.1174 | 0.31128 | -0.027466 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | 14.1678 | 12.2406 | -0.56305 | 0.013733 | 0.013733 | 0.022888 | 0.013733 | 1.1444 | 0.018311 | 0.018311
5845.8438 | 0.045776 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 5.0262 | 3.4058 | 0.61798 | 0.27466 | 0.022888 | 0.009155 | 0.004578 | 0.076294 | 0.002136 | 0.005341 | 0.001068 | 0.002136 | 0.003204 | 14.0259 | 12.9227 | 1.1581 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.69122 | 0.009155 | 0.027466
5847.6406 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 4.184 | 3.566 | 0.7782 | 0.43488 | 0.004578 | 0.004578 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 13.7054 | 13.3575 | 3.9139 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.1032 | 0.018311 | 0.022888
5849.3281 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 3.3966 | 3.6026 | 0.81024 | 0.55389 | 0.009155 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0 | 0.002136 | 0.002136 | 0.003204 | 13.1195 | 13.4903 | 6.0196 | 0.018311 | 0.013733 | 0.013733 | 0.004578 | 0.65918 | 0.013733 | 0.018311
5851.0781 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.001068 | 2.5681 | 3.5934 | 0.82855 | 0.55847 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0 | 0.001068 | 12.4786 | 13.623 | 7.8049 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.8194 | 0.018311 | 0.018311
5852.8438 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 1.8402 | 3.5568 | 0.80109 | 0.54474 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 11.8378 | 13.4995 | 8.5602 | 0.004578 | 0.013733 | 0.009155 | 0.009155 | 0.70496 | 0.013733 | 0.013733
5854.6094 | 0.076294 | 0.005341 | 0.002136 | 0.001068 | 0.003204 | 0.004272 | 0.001068 | 1.1719 | 3.4103 | 0.67291 | 0.43945 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 11.1374 | 13.2019 | 9.1553 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 1.2177 | 0.013733 | 0.022888
5856.2969 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.6958 | 3.3279 | 0.59052 | 0.33875 | 0.018311 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 10.1578 | 13.0142 | 10.2539 | 0.009155 | 0.009155 | 0.013733 | 0.013733 | 0.85144 | 0.018311 | 0.013733
5858.0469 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0 | -0.001068 | 0.32959 | 3.2135 | 0.44861 | 0.15564 | 0.018311 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 9.3887 | 12.6297 | 10.4874 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.70496 | 0.022888 | 0.013733
5859.7344 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.068665 | 3.1677 | 0.37994 | 0.022888 | 0.004578 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 8.7112 | 12.2498 | 10.7162 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.54474 | 0.013733 | 0.022888
5861.5 | 0.045776 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.001068 | 0.002136 | -0.14648 | 3.1311 | 0.32501 | -0.10986 | 0.009155 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 8.0429 | 11.7691 | 10.7574 | 0.018311 | 0.018311 | 0.009155 | 0.013733 | 0.45776 | 0.022888 | 0.009155
5863.1875 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | -0.32959 | 3.0167 | 0.24719 | -0.26093 | 0.018311 | 0.013733 | 0.009155 | 0.030518 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 7.4387 | 11.2839 | 10.7437 | 0.018311 | 0.009155 | 0.004578 | 0.013733 | 0.41657 | 0.018311 | 0.022888
5864.9531 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.001068 | -0.41657 | 2.9663 | 0.1831 | -0.39825 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0 | 0.001068 | 6.8985 | 10.7758 | 10.6018 | 0.018311 | 0.009155 | 0.009155 | 0.013733 | 0.52185 | 0.013733 | 0.018311
5866.6406 | 0.030518 | 0.003204 | 0.001068 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.49439 | 2.9022 | 0.11902 | -0.5127 | 0.009155 | 0.013733 | 0.018311 | 0.030518 | 0.004272 | 0.003204 | 0.005341 | 0.001068 | 0.002136 | 6.395 | 10.2951 | 10.4645 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.40283 | 0.018311 | 0.013733
5868.4062 | 0.045776 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.002136 | -0.52185 | 2.8702 | 0.1236 | -0.58136 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 5.9326 | 9.7961 | 10.2585 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | 0.37994 | 0.009155 | 0.018311
5870.1562 | 0.045776 | 0.002136 | 0 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.53101 | 2.8107 | 0.082397 | -0.67749 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 5.5298 | 9.3246 | 9.993 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | 0.46234 | 0.018311 | 0.022888
5871.8438 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0 | 0.003204 | -0.56305 | 2.774 | 0.11902 | -0.70038 | 0.013733 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 5.1361 | 8.9081 | 9.7916 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.24719 | 0.022888 | 0.018311
5873.625 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | -0.55847 | 2.7237 | 0.10529 | -0.76446 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 4.7836 | 8.4412 | 9.4528 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 0.52185 | 0.013733 | 0.018311
5875.3281 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.55847 | 2.6733 | 0.1236 | -0.79193 | 0.013733 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 4.4632 | 8.075 | 9.1965 | 0.018311 | 0.004578 | 0.018311 | 0.004578 | 0.47607 | 0.027466 | 0.022888
5877.0781 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.54932 | 2.6413 | 0.13275 | -0.82855 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 4.1473 | 7.663 | 8.8577 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.48523 | 0.018311 | 0.022888
5878.7812 | 0.030518 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | -0.56305 | 2.5864 | 0.17853 | -0.80566 | 0.009155 | 0.004578 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 3.8589 | 7.3059 | 8.5922 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.39368 | 0.009155 | 0.013733
5880.5312 | 0.015259 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | -0.56763 | 2.5589 | 0.17395 | -0.83313 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 3.5934 | 6.9397 | 8.2443 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.42572 | 0.009155 | 0.022888
5882.2188 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.5722 | 2.4948 | 0.18768 | -0.84228 | 0.013733 | 0.004578 | 0.013733 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 3.3371 | 6.6376 | 7.9788 | 0.009155 | 0.018311 | 0.013733 | 0.009155 | 0.41199 | 0.018311 | 0.018311
5883.9844 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.55847 | 2.449 | 0.24261 | -0.8194 | 0.013733 | 0.004578 | 0.009155 | 0.030518 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 3.0991 | 6.3126 | 7.663 | 0.018311 | 0.013733 | 0.022888 | 0.022888 | 0.14191 | 0.018311 | 0.027466
5885.7344 | 0.030518 | 0.006409 | 0.002136 | 0.003204 | 0 | 0 | 0.003204 | -0.54016 | 2.4353 | 0.28839 | -0.78735 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 2.8748 | 6.0333 | 7.3975 | 0.013733 | 0.018311 | 0.018311 | 0.004578 | 0.16022 | 0.013733 | 0.027466
5887.5 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.52185 | 2.3804 | 0.32044 | -0.75531 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 2.6825 | 5.7587 | 7.1045 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.2655 | 0.022888 | 0.018311
5889.2031 | 0.045776 | 0.004272 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0 | -0.51727 | 2.3346 | 0.33875 | -0.75073 | 0.018311 | 0.018311 | 0.004578 | 0.030518 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 2.4902 | 5.4977 | 6.8436 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.24261 | 0.013733 | 0.018311
5890.9688 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.001068 | -0.48065 | 2.3026 | 0.36163 | -0.75073 | 0.018311 | 0.013733 | 0.004578 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 2.3392 | 5.2322 | 6.5506 | 0.004578 | 0.013733 | 0.013733 | 0.013733 | 0.35706 | 0.018311 | 0.018311
5892.7188 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.001068 | 0.004272 | 0.001068 | -0.48981 | 2.2797 | 0.41657 | -0.6958 | 0.013733 | 0.009155 | 0.009155 | 0.030518 | 0.003204 | 0.004272 | 0.004272 | 0.001068 | 0.002136 | 2.1698 | 5.0125 | 6.3309 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.09613 | 0.018311 | 0.022888
5894.4219 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.48981 | 2.2476 | 0.44403 | -0.68665 | 0.018311 | 0.018311 | 0.009155 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 2.0187 | 4.7836 | 6.0974 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.33875 | 0.018311 | 0.018311
5896.1875 | 0.015259 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.48981 | 2.1927 | 0.46692 | -0.6546 | 0.013733 | 0.013733 | 0.004578 | 0.030518 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 1.8723 | 4.5502 | 5.8319 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.19226 | 0.013733 | 0.018311
5897.9375 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.47607 | 2.1652 | 0.52185 | -0.60425 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 1.7349 | 4.3488 | 5.6259 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.12817 | 0.022888 | 0.004578
5899.6406 | 0.045776 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | -0.4715 | 2.124 | 0.55389 | -0.56763 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 1.6022 | 4.1245 | 5.4016 | 0.022888 | 0.013733 | 0.004578 | 0.009155 | 0.16937 | 0.027466 | 0.018311
5901.3906 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | -0.44861 | 2.0828 | 0.54474 | -0.56763 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 1.5015 | 3.9001 | 5.1682 | 0.018311 | 0.009155 | 0.013733 | 0.022888 | 0.45319 | 0.022888 | 0.013733
5903.1406 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.42572 | 2.0554 | 0.56763 | -0.54016 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 1.4191 | 3.7399 | 4.9667 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.4303 | 0.022888 | 0.018311
5904.8281 | 0.045776 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.42572 | 2.0416 | 0.60883 | -0.48523 | 0.004578 | 0.009155 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 1.3184 | 3.5706 | 4.8019 | 0.018311 | 0.018311 | 0.018311 | 0.009155 | 0.40741 | 0.018311 | 0.018311
5906.5781 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.003204 | -0.43945 | 1.9958 | 0.63629 | -0.45776 | 0.013733 | 0.013733 | 0.022888 | 0.030518 | 0.003204 | 0.002136 | 0.004272 | 0.001068 | 0.001068 | 1.2131 | 3.3875 | 4.5959 | 0.013733 | 0.009155 | 0.009155 | 0.018311 | 0.35706 | 0.013733 | 0.018311
5908.2812 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | -0.42114 | 1.9272 | 0.63629 | -0.43945 | 0.009155 | 0.013733 | 0.018311 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 1.1261 | 3.1952 | 4.3991 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.3067 | 0.018311 | 0.022888
5910.0312 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0 | 0.003204 | -0.42572 | 1.9043 | 0.64545 | -0.42114 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 1.0712 | 3.0396 | 4.1931 | 0.018311 | 0.018311 | 0.009155 | 0.009155 | 0.29297 | 0.022888 | 0.013733
5911.7812 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.40283 | 1.9043 | 0.68665 | -0.37537 | 0.018311 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 1.0162 | 2.8976 | 4.0329 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 0.23804 | 0.022888 | 0.018311
5913.5469 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0 | -0.40283 | 1.8539 | 0.6958 | -0.33875 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.9613 | 2.7557 | 3.8589 | 0.013733 | 0.009155 | 0.009155 | 0.013733 | 0.21515 | 0.013733 | 0.018311
5915.2344 | 0.045776 | 0.004272 | 0.001068 | 0 | 0.001068 | 0.001068 | 0.002136 | -0.36621 | 1.8631 | 0.70038 | -0.32501 | 0.013733 | 0.013733 | 0.022888 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.9201 | 2.6276 | 3.6942 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.19684 | 0.013733 | 0.022888
5916.9844 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.004272 | -0.35706 | 1.8036 | 0.70953 | -0.31586 | 0.009155 | 0.009155 | 0.009155 | 0.030518 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.88348 | 2.4994 | 3.5019 | 0.009155 | 0.009155 | 0.013733 | 0.009155 | 0.40283 | 0.013733 | 0.009155
5918.6875 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.23804 | 1.8219 | 2.3987 | 0.32501 | 0.009155 | 0.009155 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 1.9821 | 4.7379 | 3.2593 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.32501 | 0.018311 | 0.022888
5920.4375 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.21515 | 1.8585 | 1.5518 | 0.27008 | 0.013733 | 0.009155 | 0.004578 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.87433 | 3.2822 | 3.3966 | 0.027466 | 0.018311 | 0.013733 | 0.004578 | 0.24261 | 0.018311 | 0.013733
5922.2031 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0 | -0.28839 | 1.7807 | 1.387 | 0.25635 | 0.013733 | 0.018311 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.004272 | 0.80109 | 2.8519 | 3.2364 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | -0.42114 | 0.018311 | 0.009155
5923.8906 | 0.076294 | 0.004272 | 0.001068 | 0.001068 | 0 | 0 | 0.002136 | -0.27924 | 1.7349 | 1.1124 | 0.15106 | 0.009155 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.059509 | 1.9089 | 2.6505 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.036621 | 0.013733 | 0.018311
5925.6562 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.26093 | 1.7761 | 0.98419 | 0.059509 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.48523 | 2.0462 | 2.9572 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | 0.2243 | 0.018311 | 0.018311
5927.3594 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.2655 | 1.7532 | 0.94757 | 0.050354 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.89722 | 2.3346 | 2.536 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | 0.16022 | 0.018311 | 0.013733
5929.125 | 0.045776 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.27924 | 1.7029 | 0.92926 | -0.022888 | 0.018311 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.71411 | 2.1378 | 2.4399 | 0.013733 | 0.018311 | 0.009155 | 0.013733 | 0.58136 | 0.013733 | 0.013733
5930.8125 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0 | 0.002136 | -0.27466 | 1.6754 | 0.88806 | -0.022888 | 0.018311 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.64087 | 1.9638 | 2.3026 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.44861 | 0.013733 | 0.022888
5932.5625 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.30212 | 1.6479 | 0.91095 | -0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.60425 | 2.2018 | 2.6367 | 0.022888 | 0.013733 | 0.013733 | 0.013733 | 0.48523 | 0.009155 | 0.018311
5934.3125 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0 | -0.30212 | 1.6296 | 0.82855 | -0.032043 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.8194 | 1.6571 | 1.8768 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.53558 | 0.013733 | 0.018311
5936.0469 | 0.030518 | 0.003204 | 0 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.3479 | 1.5701 | 0.88348 | -0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.65002 | 1.7532 | 1.886 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.48981 | 0.018311 | 0.022888
5937.7344 | 0.030518 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.004272 | 0.003204 | -0.33417 | 1.561 | 0.83313 | -0.009155 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.51727 | 1.7349 | 2.0187 | 0.009155 | 0.022888 | 0.009155 | 0.009155 | 0.42114 | 0.027466 | 0.018311
5939.4844 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.003204 | -0.34332 | 1.5152 | 0.86975 | 0.013733 | 0.013733 | 0.009155 | 0.022888 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.31586 | 1.6571 | 2.3209 | 0.018311 | 0.013733 | 0.018311 | 0.004578 | 0.31586 | 0.022888 | 0.018311
5941.1719 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0 | -0.34332 | 1.4969 | 0.82855 | -0.009155 | 0.009155 | 0.022888 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.10071 | 1.2177 | 1.7944 | 0.009155 | 0.013733 | 0.009155 | 0.018311 | 0.6134 | 0.018311 | 0.022888
5942.9219 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.35248 | 1.474 | 0.86517 | -0.004578 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.054932 | 0.6958 | 1.1353 | 0.022888 | 0.009155 | 0.018311 | 0.013733 | 0.37537 | 0.018311 | 0.013733
5944.625 | 0.015259 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.33875 | 1.4603 | 0.73242 | -0.032043 | 0.009155 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.34332 | 1.3138 | 1.2451 | 0.009155 | 0.009155 | 0.013733 | 0.004578 | 0.55847 | 0.022888 | 0.018311
5946.3906 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.32501 | 1.4282 | 0.74616 | -0.059509 | 0.018311 | 0.004578 | 0.013733 | 0.061035 | 0.003204 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.37537 | 1.3138 | 1.3367 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 0.52185 | 0.013733 | 0.018311
5948.1406 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.31586 | 1.4282 | 0.76904 | -0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | 0.38452 | 1.268 | 1.2268 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.29297 | 0.018311 | 0.018311
5949.8906 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.32501 | 1.3779 | 0.72327 | -0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | 0.40283 | 1.2726 | 1.4923 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.42572 | 0.013733 | 0.022888
5951.6406 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.32959 | 1.5335 | 0.75989 | -0.064087 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 2.0325 | 3.4561 | 1.4832 | 0.022888 | 0.018311 | 0.013733 | 0.013733 | 0.46234 | 0.013733 | 0.018311
5953.3438 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.19684 | 1.4832 | 0.80109 | 0.018311 | 0.022888 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | 0.20142 | 0.91553 | -1.4236 | 0.009155 | 0.004578 | 0.018311 | 0.009155 | 0.54016 | 0.018311 | 0.018311
5955.0938 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.19226 | 1.3962 | 0.81482 | 0.032043 | 0.018311 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.93384 | 1.4786 | -0.29755 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 0.40283 | 0.013733 | 0.013733
5956.8438 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | -0.21515 | 1.355 | 0.83771 | 0.068665 | 0.013733 | 0.009155 | 0.018311 | 0 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 1.0849 | 1.8723 | 0.70038 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.48523 | 0.013733 | 0.013733
5958.5469 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.23346 | 1.3824 | 0.93842 | -0.022888 | 0.018311 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 1.7029 | 5.3925 | 6.1707 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.31128 | 0.022888 | 0.022888
5960.3125 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.20142 | 1.181 | 0.79651 | 0.064087 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 1.0574 | 3.0075 | 2.4765 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 0.46692 | 0.013733 | 0.018311
5962.0625 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.21973 | 1.3779 | 0.80109 | 0.068665 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.086975 | 0.95673 | -1.0803 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.37079 | 0.022888 | 0.022888
5963.75 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.26093 | 1.2863 | 0.80566 | 0.091553 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.68665 | 1.3458 | -0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 0.37994 | 0.009155 | 0.022888
5965.5156 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.29297 | 1.2222 | 0.77362 | 0.07782 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.94299 | 1.68 | 0.73242 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.3479 | 0.013733 | 0.022888
5967.2812 | 0.045776 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0 | -0.3067 | 1.1856 | 0.74158 | 0.068665 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.90637 | 1.8768 | 1.2543 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.55389 | 0.018311 | 0.022888
5969.0156 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | -0.002136 | 0.002136 | 0.001068 | -0.31128 | 1.1444 | 0.74158 | 0.073242 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.79651 | 1.9135 | 1.6159 | 0.018311 | 0.013733 | 0.009155 | 0.009155 | 0.42114 | 0.013733 | 0.022888
5970.7656 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | 1.1536 | 0.70953 | 0.073242 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.5722 | 1.7029 | 1.6434 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.55389 | 0.013733 | 0.018311
5972.4531 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.40283 | 1.0574 | 0.62256 | 0.022888 | 0.004578 | 0.013733 | 0.009155 | 0.015259 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.49439 | 0.027466 | 0.58594 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.45319 | 0.022888 | 0.022888
5974.2031 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.37079 | 1.2177 | 0.70496 | 0.050354 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0 | -0.27924 | 0.94299 | -0.59052 | 0.018311 | 0.018311 | 0.004578 | 0.013733 | 0.71869 | 0.013733 | 0.018311
5975.9375 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | -0.001068 | 0 | 0.001068 | -0.25635 | 1.0803 | 0.74616 | 0.11902 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.001068 | 0.3479 | 1.0025 | -0.30212 | 0.004578 | 0.013733 | 0.004578 | 0.018311 | 0.48523 | 0.018311 | 0.022888
5977.7031 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0 | -0.30212 | 0.97504 | 0.68665 | 0.036621 | 0.013733 | 0.009155 | 0.022888 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 1.0941 | -0.71411 | -2.4857 | 0.009155 | 0.013733 | 0.009155 | 0.022888 | 0.6546 | 0.018311 | 0.022888
5979.4688 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.37079 | 1.4099 | 1.1215 | 0.25177 | 0.018311 | 0.009155 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | -0.93842 | 0.97961 | -0.34332 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 0.72784 | 0.018311 | 0.013733
5981.2344 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.28839 | 1.0345 | 1.2589 | 0.37079 | 0.018311 | 0.009155 | 0.022888 | 0.061035 | 0.001068 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.70038 | 1.5701 | 0.98419 | 0.018311 | 0.013733 | 0.009155 | 0.009155 | 0.38452 | 0.018311 | 0.018311
5982.9844 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.14191 | 1.1673 | 0.65918 | 0.21515 | 0.022888 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.15564 | 0.15106 | -2.3392 | 0.013733 | 0.018311 | 0.022888 | 0.013733 | 0.54016 | 0.013733 | 0.022888
5984.6875 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.12817 | 1.0941 | 0.65918 | 0.15106 | 0.018311 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.46234 | -0.027466 | -2.536 | 0.009155 | 0.009155 | 0.013733 | 0.018311 | 0.29297 | 0.022888 | 0.004578
5986.4375 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | -0.18768 | 1.0208 | 0.66376 | 0.11902 | 0.009155 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.001068 | 0.004272 | 0.002136 | 0.002136 | -0.073242 | 0.42114 | -1.3504 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.27924 | 0.022888 | 0.013733
5988.125 | 0.045776 | 0.003204 | 0 | 0.001068 | 0.001068 | 0.003204 | 0.003204 | -0.21515 | 0.98419 | 0.62714 | 0.091553 | 0.018311 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | 0.003204 | -1.0071 | 0.73242 | -0.92926 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 0.55389 | 0.018311 | 0.022888
5989.8906 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0 | 0 | 0 | 0.22888 | 0.95673 | 0.68665 | 0.14191 | 0.018311 | 0.009155 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -1.2863 | 1.1307 | -0.20142 | 0.009155 | 0.004578 | 0.009155 | 0.009155 | 0.5127 | 0.018311 | 0.018311
5991.6562 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.11444 | 1.03 | 0.91553 | 0.10071 | 0.018311 | 0.013733 | 0.004578 | 0.015259 | 0.002136 | 0.002136 | 0.001068 | 0 | 0.002136 | -1.1124 | -0.52185 | -1.5244 | 0.013733 | 0.018311 | 0.004578 | 0.013733 | 0.65918 | 0.013733 | 0.018311
5993.3438 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.28839 | 0.95215 | 0.75073 | 0.091553 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 1.0895 | -0.94757 | -1.2817 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.50354 | 0.009155 | 0.018311
5995.1094 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.48065 | 0.94299 | 0.17395 | -0.14191 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | -0.39368 | 1.3733 | 3.2547 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.60883 | 0.018311 | 0.018311
5996.8594 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.48065 | 0.84228 | 0.40741 | -0.15106 | 0.013733 | 0.009155 | 0.018311 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.50812 | 0.49896 | 2.6001 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | 0.54932 | 0.022888 | 0.018311
5998.6094 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.5127 | 0.8194 | 0.40283 | -0.1236 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.48523 | 0.004578 | 2.0416 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 0.56763 | 0.013733 | 0.022888
6000.3125 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.001068 | -0.50812 | 0.79651 | 0.37994 | -0.1236 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.42114 | -0.24261 | 1.5656 | 0.013733 | 0.018311 | 0.009155 | 0.009155 | 0.35248 | 0.018311 | 0.018311
6002.0625 | 0.015259 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.48523 | 0.78735 | 0.34332 | -0.16479 | 0.004578 | 0.013733 | 0.018311 | 0.045776 | 0 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.31586 | -0.33875 | 1.1627 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.57678 | 0.022888 | 0.018311
6003.8281 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.45776 | 0.79651 | 0.33875 | -0.17395 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.23346 | -0.32501 | 0.88806 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | 0.54932 | 0.018311 | 0.018311
6005.5312 | 0.045776 | 0.004272 | 0 | 0 | 0 | 0.002136 | 0.002136 | -0.4303 | 0.80109 | 0.31128 | -0.2243 | 0.013733 | 0.013733 | 0.004578 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | -0.17853 | -0.29297 | 0.67291 | 0.022888 | 0.013733 | 0.009155 | 0.009155 | 0.83771 | 0.009155 | 0.013733
6007.2812 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.41199 | 0.81024 | 0.29755 | -0.24719 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | -0.1236 | -0.23346 | 0.5127 | 0.018311 | 0.013733 | 0.009155 | 0.009155 | 0.76904 | 0.022888 | 0.018311
6009.0156 | 0.030518 | 0.003204 | 0.002136 | 0 | 0 | 0.002136 | 0.002136 | -0.39825 | 0.80109 | 0.28381 | -0.26093 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.091553 | -0.16937 | 0.40741 | 0.009155 | 0 | 0.018311 | 0.013733 | 0.6958 | 0.018311 | 0.018311
6010.7812 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.39825 | 0.77362 | 0.27008 | -0.30212 | 0.018311 | 0.018311 | 0.009155 | 0.030518 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | -0.068665 | -0.11444 | 0.31586 | 0.004578 | 0.004578 | 0.013733 | 0.018311 | 0.80109 | 0.018311 | 0.018311
6012.4688 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.39825 | 0.75531 | 0.27466 | -0.30212 | 0.018311 | 0.009155 | 0.018311 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.068665 | -0.064087 | 0.27008 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 0.54932 | 0.022888 | 0.013733
6014.2031 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.39368 | 0.74158 | 0.24261 | -0.34332 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.086975 | -0.041199 | 0.20142 | 0.009155 | 0.018311 | 0.009155 | 0.018311 | 0.47607 | 0.022888 | 0.013733
6015.8906 | 0.015259 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.3891 | 0.73242 | 0.21515 | -0.37537 | 0.013733 | 0.018311 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.07782 | -0.009155 | 0.13275 | 0.004578 | 0.018311 | 0.013733 | 0.013733 | 0.70953 | 0.013733 | 0.022888
6017.6562 | 0.045776 | 0.005341 | 0 | 0.002136 | -0.002136 | 0 | 0.003204 | -0.3891 | 0.70953 | 0.20599 | -0.37537 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.073242 | 0.018311 | 0.10986 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.53558 | 0.018311 | 0.013733
6019.3438 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.40283 | 0.70953 | 0.20142 | -0.3891 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.068665 | 0.054932 | 0.068665 | 0.013733 | 0.009155 | 0.009155 | 0.013733 | 0.54474 | 0.018311 | 0.018311
6021.1094 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.39825 | 0.68665 | 0.17853 | -0.42114 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.004272 | 0 | 0.003204 | 0.002136 | 0.004272 | -0.073242 | 0.064087 | 0.041199 | 0.022888 | 0.009155 | 0.018311 | 0.013733 | 0.61798 | 0.018311 | 0.018311
6022.7969 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.39368 | 0.69122 | 0.1831 | -0.42114 | 0.013733 | 0.027466 | 0.009155 | 0.045776 | 0.001068 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.064087 | 0.09613 | 0.036621 | 0.018311 | 0.018311 | 0.009155 | 0.013733 | 0.49896 | 0.013733 | 0.022888
6024.5625 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.3891 | 0.66376 | 0.16479 | -0.43488 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | -0.07782 | 0.11444 | 0 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.40283 | 0.018311 | 0.018311
6026.3281 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.3891 | 0.66834 | 0.14648 | -0.44861 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.068665 | 0.13275 | -0.009155 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | 0.43488 | 0.013733 | 0.022888
6028.0156 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.36163 | 0.66834 | 0.12817 | -0.4715 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -0.050354 | 0.14191 | -0.027466 | 0.022888 | 0.022888 | 0.018311 | 0.018311 | 0.49439 | 0.018311 | 0.022888
6029.7812 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | -0.001068 | 0.003204 | 0.003204 | -0.3479 | 0.67291 | 0.1236 | -0.48523 | 0.009155 | 0.009155 | 0.013733 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -0.041199 | 0.16479 | -0.022888 | 0.009155 | 0.013733 | 0.009155 | 0.009155 | 0.74158 | 0.009155 | 0.022888
6031.4688 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.43488 | 0.62714 | 0.20142 | -0.4303 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.091553 | 0.21057 | 0.004578 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 0.37079 | 0.022888 | 0.018311
6033.2188 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.43488 | 0.59967 | 0.09613 | -0.49896 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.10986 | 0.16937 | 0.036621 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.29297 | 0.018311 | 0.013733
6034.9688 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.4303 | 0.60425 | 0.10529 | -0.48981 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.10071 | 0.1831 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.26093 | 0.022888 | 0.018311
6036.7188 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.43488 | 0.59052 | 0.086975 | -0.48981 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.11444 | 0.16022 | -0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.28381 | 0.018311 | 0.018311
6038.4688 | 0.030518 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.41657 | 0.59052 | 0.068665 | -0.51727 | 0.013733 | 0.009155 | 0.018311 | 0.076294 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.11444 | 0.15564 | -0.041199 | 0.013733 | 0.009155 | 0.004578 | 0.013733 | 0.33875 | 0.022888 | 0.009155
6040.2188 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.40283 | 0.59052 | 0.068665 | -0.54016 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.09613 | 0.15564 | -0.064087 | 0.013733 | 0.013733 | 0.018311 | 0.022888 | 0.46692 | 0.018311 | 0.013733
6041.9062 | 0.061035 | 0.002136 | 0.001068 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.40741 | 0.56763 | 0.059509 | -0.54474 | 0.004578 | 0.013733 | 0.009155 | 0.015259 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.09613 | 0.17853 | -0.054932 | 0.004578 | 0.018311 | 0.009155 | 0.018311 | 0.40283 | 0.022888 | 0.018311
6043.6562 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.37994 | 0.58136 | 0.073242 | -0.52185 | 0.018311 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.10529 | 0.19226 | -0.045776 | 0.018311 | 0.018311 | 0.018311 | 0.009155 | 0.27466 | 0.027466 | 0.018311
6045.4219 | 0.030518 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.004272 | 0.002136 | -0.38452 | 0.58136 | 0.059509 | -0.54474 | 0.018311 | 0.018311 | 0.018311 | 0.030518 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.001068 | -0.086975 | 0.1831 | -0.068665 | 0.013733 | 0.022888 | 0.009155 | 0.013733 | 0.60425 | 0.013733 | 0.018311
6047.1719 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.37079 | 0.55389 | 0.050354 | -0.55389 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.082397 | 0.19226 | -0.068665 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.58136 | 0.022888 | 0.018311
6048.8594 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.39368 | 0.55847 | 0.064087 | -0.54474 | 0.018311 | 0.018311 | 0.013733 | 0.030518 | 0.002136 | 0.004272 | 0.002136 | 0.004272 | 0.001068 | -0.091553 | 0.20142 | -0.045776 | 0.013733 | 0.004578 | 0.013733 | 0.004578 | 0.39825 | 0.022888 | 0.018311
6050.625 | 0.045776 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | -0.38452 | 0.54932 | 0.027466 | -0.56305 | 0 | 0.009155 | 0.018311 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.091553 | 0.19684 | -0.059509 | 0.013733 | 0.013733 | 0.009155 | 0.022888 | 0.72327 | 0.013733 | 0.018311
6052.3906 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.37079 | 0.55389 | 0.036621 | -0.56763 | 0.004578 | 0.009155 | 0.013733 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.073242 | 0.21057 | -0.041199 | 0.013733 | 0.013733 | 0.009155 | 0.009155 | 0.68207 | 0.022888 | 0.013733
6054.125 | 0.015259 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.40283 | 0.55389 | 0.059509 | -0.54932 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.086975 | 0.23346 | -0.022888 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 0.43945 | 0.022888 | 0.018311
6055.8281 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.39825 | 0.51727 | 0.022888 | -0.58136 | 0.004578 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.086975 | 0.21515 | -0.045776 | 0.009155 | 0.009155 | 0.018311 | 0.009155 | 0.64545 | 0.018311 | 0.013733
6057.5938 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.002136 | 0 | -0.38452 | 0.51727 | 0.022888 | -0.58136 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | -0.091553 | 0.2243 | -0.041199 | 0.009155 | 0.009155 | 0.018311 | 0.009155 | 0.55389 | 0.022888 | 0.009155
6059.3594 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.001068 | 0 | -0.3891 | 0.52185 | 0.004578 | -0.59052 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.082397 | 0.22888 | -0.027466 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.58136 | 0.018311 | 0.022888
6061.1094 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.40283 | 0.52185 | 0.018311 | -0.57678 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.09613 | 0.23346 | -0.022888 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.68207 | 0.013733 | 0.013733
6062.8125 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.41199 | 0.50354 | -0.009155 | -0.60425 | 0.009155 | 0.013733 | 0.004578 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.11444 | 0.21057 | -0.036621 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.6546 | 0.009155 | 0.018311
6064.5781 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.40283 | 0.48065 | -0.004578 | -0.59967 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -0.10529 | 0.22888 | -0.018311 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.5722 | 0.018311 | 0.013733
6066.3438 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.42114 | 0.47607 | -0.013733 | -0.60883 | 0.013733 | 0.013733 | 0.009155 | 0.076294 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.11902 | 0.21515 | -0.032043 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 0.48065 | 0.018311 | 0.018311
6068.0938 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.42114 | 0.48065 | -0.036621 | -0.63171 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.1236 | 0.19684 | -0.054932 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | 0.73242 | 0.013733 | 0.013733
6069.7812 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.4303 | 0.46234 | -0.045776 | -0.65002 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.13733 | 0.19226 | -0.059509 | 0.018311 | 0.009155 | 0.018311 | 0.018311 | 0.6546 | 0.018311 | 0.013733
6071.5469 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | -0.42572 | 0.44403 | -0.045776 | -0.63629 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.13733 | 0.18768 | -0.054932 | 0.013733 | 0.009155 | 0.022888 | 0.009155 | 0.48065 | 0.018311 | 0.018311
6073.2969 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | -0.41657 | 0.45776 | -0.041199 | -0.64087 | 0.009155 | 0.018311 | 0.004578 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.14191 | 0.17853 | -0.059509 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.51727 | 0.013733 | 0.027466
6075.0312 | 0.015259 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.44403 | 0.43945 | -0.068665 | -0.66376 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -0.13733 | 0.16022 | -0.073242 | 0.018311 | 0.009155 | 0.009155 | 0.013733 | 0.63171 | 0.018311 | 0.018311
6076.7344 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | -0.44861 | 0.42572 | -0.073242 | -0.66376 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | -0.15564 | 0.15564 | -0.082397 | 0.018311 | 0.022888 | 0.013733 | 0.009155 | 0.74158 | 0.018311 | 0.013733
6078.5 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.44861 | 0.42114 | -0.091553 | -0.67749 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.14191 | 0.15564 | -0.082397 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.64087 | 0.018311 | 0.018311
6080.25 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.44403 | 0.41199 | -0.09613 | -0.68665 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.15106 | 0.14191 | -0.091553 | 0.022888 | 0.009155 | 0.009155 | 0.018311 | 0.52643 | 0.027466 | 0.018311
6081.9375 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.4303 | 0.3891 | -0.10071 | -0.70038 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.15564 | 0.14191 | -0.10071 | 0.018311 | 0.013733 | 0.009155 | 0.027466 | 0.54016 | 0.018311 | 0.027466
6083.6875 | 0.061035 | 0.004272 | 0 | 0 | -0.001068 | 0.002136 | 0.002136 | -0.4303 | 0.41199 | -0.09613 | -0.6958 | 0.009155 | 0.004578 | 0.009155 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.15564 | 0.14191 | -0.09613 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.48523 | 0.018311 | 0.013733
6085.4531 | 0.045776 | 0.005341 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.4303 | 0.39825 | -0.10986 | -0.71869 | 0.004578 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | -0.15106 | 0.1236 | -0.1236 | 0.013733 | 0.022888 | 0.013733 | 0.013733 | 0.70953 | 0.013733 | 0.022888
6087.2031 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.4303 | 0.39825 | -0.10986 | -0.71411 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.15564 | 0.12817 | -0.11444 | 0.013733 | 0.013733 | 0.018311 | 0.004578 | 0.67291 | 0.022888 | 0.018311
6088.9531 | 0.015259 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.001068 | 0 | -0.43488 | 0.37994 | -0.13733 | -0.72784 | 0.004578 | 0.013733 | 0.022888 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.15106 | 0.1236 | -0.1236 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 0.60883 | 0.027466 | 0.018311
6090.6406 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | -0.002136 | 0.002136 | 0 | -0.45776 | 0.38452 | -0.13733 | -0.72327 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.003204 | -0.15106 | 0.12817 | -0.10529 | 0.013733 | 0.022888 | 0.018311 | 0.009155 | 0.58136 | 0.018311 | 0.018311
6092.4062 | 0.030518 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.46692 | 0.35248 | -0.12817 | -0.72784 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.16479 | 0.13275 | -0.11902 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.39368 | 0.018311 | 0.022888
6094.1562 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.44861 | 0.37537 | -0.14191 | -0.72784 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -0.16937 | 0.11902 | -0.13275 | 0.013733 | 0.009155 | 0.013733 | 0.009155 | 0.59509 | 0.013733 | 0.022888
6095.875 | 0.045776 | 0.006409 | 0.001068 | 0.001068 | 0 | 0.002136 | 0.001068 | -0.44403 | 0.36163 | -0.14648 | -0.74616 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.16937 | 0.10071 | -0.13275 | 0.009155 | 0.013733 | 0.022888 | 0.009155 | 0.59509 | 0.018311 | 0.018311
6097.6406 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0.001068 | -0.42572 | 0.37537 | -0.14648 | -0.75073 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.005341 | 0.002136 | -0.15564 | 0.09613 | -0.13733 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.67749 | 0.013733 | 0.018311
6099.4062 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.44403 | 0.36163 | -0.18768 | -0.77362 | 0.004578 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.16022 | 0.11444 | -0.15564 | 0.018311 | 0.018311 | 0.013733 | 0.009155 | 0.56763 | 0.022888 | 0.022888
6101.0938 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | -0.001068 | 0.001068 | 0.001068 | -0.41657 | 0.35248 | -0.19684 | -0.80109 | 0.013733 | 0.013733 | 0.004578 | 0.061035 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.17395 | 0.082397 | -0.19226 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | 0.79651 | 0.013733 | 0.022888
6102.8594 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.43488 | 0.35248 | -0.1831 | -0.76904 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.16022 | 0.091553 | -0.19226 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.65918 | 0.018311 | 0.018311
6104.625 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.45776 | 0.31586 | -0.17853 | -0.77362 | 0.009155 | 0.004578 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | -0.17853 | 0.091553 | -0.16479 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 0.55389 | 0.027466 | 0.009155
6106.3281 | 0.045776 | 0.005341 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.48065 | 0.3067 | -0.19226 | -0.7782 | 0.009155 | 0.013733 | 0.022888 | 0.045776 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.19226 | 0.07782 | -0.16479 | 0.004578 | 0.013733 | 0.018311 | 0.013733 | 0.64545 | 0.022888 | 0.018311
6108.0625 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.55389 | 0.14191 | -0.37537 | -0.82855 | 0.018311 | 0.013733 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -1.3733 | -0.48523 | 0.25177 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.53101 | 0.018311 | 0.018311
6109.7656 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.48065 | 0.32044 | -0.20142 | -0.84686 | 0.013733 | 0.004578 | 0.018311 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.92468 | -0.009155 | -1.4099 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 0.85602 | 0.022888 | 0.013733
6111.5312 | 0.061035 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.45319 | 0.33417 | -0.21057 | -0.82398 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.81482 | 0.47607 | -0.82398 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 0.62256 | 0.018311 | 0.013733
6113.2812 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.43488 | 0.31586 | -0.23346 | -0.80566 | 0.004578 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.737 | 0.79651 | -0.34332 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.68665 | 0.022888 | 0.013733
6115.0312 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.46234 | 0.28381 | -0.14191 | -0.79193 | 0.013733 | 0.018311 | 0.004578 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | 0.64087 | 0.85144 | -0.032043 | 0.009155 | 0.018311 | 0.013733 | 0.009155 | 0.72327 | 0.013733 | 0.022888
6116.7344 | 0.030518 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.48523 | 0.27008 | -0.064087 | -0.737 | 0.004578 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.58136 | 0.94299 | 0.36163 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.54474 | 0.018311 | 0.018311
6118.5 | 0.015259 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.004272 | -0.47607 | 0.24719 | -0.27924 | -0.79193 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.25635 | 0.89264 | 0.27008 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.62714 | 0.013733 | 0.013733
6120.1875 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | -0.001068 | 0.003204 | 0 | -0.4715 | 0.25635 | -0.23346 | -0.81024 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.17853 | 0.80566 | 0.3891 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.70038 | 0.018311 | 0.013733
6121.9375 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.48065 | 0.24261 | -0.20599 | -0.81482 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.064087 | 0.71411 | 0.4303 | 0.013733 | 0.022888 | 0.018311 | 0.013733 | 0.6546 | 0.018311 | 0.022888
6123.6875 | 0.045776 | 0.004272 | 0.004272 | 0.003204 | -0.001068 | 0.002136 | 0.001068 | -0.46234 | 0.25177 | -0.24261 | -0.8194 | 0.004578 | 0.009155 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.036621 | 0.61798 | 0.39368 | 0.009155 | 0.013733 | 0.009155 | 0.009155 | 0.6958 | 0.022888 | 0.009155
6125.375 | 0.045776 | 0.003204 | 0 | 0.001068 | 0 | 0.003204 | 0.001068 | -0.47607 | 0.24261 | -0.24261 | -0.8194 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.13275 | 0.49896 | 0.3479 | 0.004578 | 0.022888 | 0.013733 | 0.018311 | 0.75073 | 0.018311 | 0.018311
6127.1406 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.003204 | -0.50812 | 0.21057 | -0.27924 | -0.85602 | 0.004578 | 0.022888 | 0.013733 | 0.076294 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.21973 | 0.37079 | 0.25635 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.9613 | 0.018311 | 0.018311
6128.9062 | 0.030518 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.50812 | 0.21057 | -0.27924 | -0.86517 | 0.013733 | 0.013733 | 0 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | -0.2655 | 0.27924 | 0.16937 | 0.013733 | 0.009155 | 0.009155 | 0.013733 | 0.91095 | 0.022888 | 0.022888
6130.6094 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.51727 | 0.18768 | -0.28839 | -0.85602 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | 0.19226 | 0.09613 | 0.004578 | 0.009155 | 0.022888 | 0.009155 | 0.75989 | 0.018311 | 0.013733
6132.3906 | 0.045776 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.003204 | 0.003204 | -0.49896 | 0.18768 | -0.32501 | -0.88806 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.32501 | 0.10071 | -0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.88348 | 0.013733 | 0.018311
6134.1406 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.47607 | 0.19684 | -0.31586 | -0.90179 | 0.009155 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.32044 | 0.059509 | -0.064087 | 0.009155 | 0.022888 | 0.013733 | 0.022888 | 0.89722 | 0.022888 | 0.022888
6135.9062 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.48523 | 0.21515 | -0.29297 | -0.87433 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | -0.32501 | 0.022888 | -0.086975 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 0.65918 | 0.022888 | 0.018311
6137.6719 | 0.061035 | 0.004272 | 0 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.49896 | 0.19226 | -0.3067 | -0.88348 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.005341 | 0.002136 | -0.33875 | -0.027466 | -0.15106 | 0.013733 | 0.022888 | 0.009155 | 0.018311 | 0.76904 | 0.009155 | 0.018311
6139.4375 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.49896 | 0.17395 | -0.33417 | -0.91553 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.33875 | -0.064087 | -0.20142 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.78735 | 0.018311 | 0.013733
6141.125 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.5127 | 0.17853 | -0.32501 | -0.89722 | 0.013733 | 0.018311 | 0.018311 | 0.015259 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.34332 | -0.082397 | -0.22888 | 0.013733 | 0.009155 | 0.009155 | 0.009155 | 0.66834 | 0.013733 | 0.018311
6142.8906 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.52185 | 0.16022 | -0.36163 | -0.92926 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0 | 0.001068 | -0.33417 | -0.11444 | -0.30212 | 0.018311 | 0.013733 | 0.004578 | 0.013733 | 0.85602 | 0.018311 | 0.013733
6144.5938 | 0.030518 | 0.005341 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | -0.49439 | 0.16937 | -0.36621 | -0.93842 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.32501 | -0.12817 | -0.3067 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.97961 | 0.013733 | 0.018311
6146.3438 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.49896 | 0.16937 | -0.33417 | -0.90637 | 0.009155 | 0.018311 | 0.009155 | 0.10681 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | -0.32959 | -0.12817 | -0.31586 | 0.009155 | 0.009155 | 0.013733 | 0.009155 | 0.76446 | 0.022888 | 0.022888
6148.0312 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.5127 | 0.15106 | -0.34332 | -0.91095 | 0.018311 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.001068 | -0.33417 | -0.15106 | -0.35248 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.71869 | 0.022888 | 0.022888
6149.7969 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.51727 | 0.15106 | -0.36621 | -0.93842 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.33875 | -0.17853 | -0.38452 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 0.79193 | 0.022888 | 0.022888
6151.5 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.50812 | 0.14191 | -0.39368 | -0.96588 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0 | -0.3067 | -0.1831 | -0.41657 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.83313 | 0.013733 | 0.022888
6153.2344 | 0.061035 | 0.005341 | 0.003204 | 0 | 0.001068 | 0.003204 | 0.002136 | -0.50354 | 0.15564 | -0.37079 | -0.94299 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | -0.31128 | -0.17395 | -0.41657 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.64545 | 0.018311 | 0.022888
6154.9844 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.51727 | 0.15106 | -0.37537 | -0.94757 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.31586 | -0.17853 | -0.4303 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.84228 | 0.018311 | 0.018311
6156.7344 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.51727 | 0.14191 | -0.3891 | -0.9613 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.31586 | -0.19226 | -0.44861 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.0208 | 0.022888 | 0.018311
6158.4219 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.51727 | 0.1236 | -0.38452 | -0.95215 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.31586 | -0.17395 | -0.45319 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.68207 | 0.013733 | 0.027466
6160.1719 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | -0.52185 | 0.10986 | -0.39825 | -0.95673 | 0.013733 | 0.009155 | 0.009155 | 0.076294 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.31128 | -0.19684 | -0.46234 | 0.009155 | 0.004578 | 0.022888 | 0.013733 | 0.68207 | 0.018311 | 0.013733
6161.875 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0 | 0.003204 | 0.001068 | -0.52185 | 0.12817 | -0.3891 | -0.95215 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.3067 | -0.19684 | -0.45776 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.64545 | 0.018311 | 0.018311
6163.6406 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | -0.51727 | 0.1236 | -0.41199 | -0.97046 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.29755 | -0.20142 | -0.49439 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.70496 | 0.018311 | 0.022888
6165.3906 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.50812 | 0.11444 | -0.41657 | -0.98877 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.28839 | -0.18768 | -0.50354 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 0.94757 | 0.013733 | 0.022888
6167.1562 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0 | -0.50812 | 0.10529 | -0.42114 | -0.98419 | 0.009155 | 0.013733 | 0.009155 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | -0.28381 | -0.1831 | -0.48523 | 0.013733 | 0.004578 | 0.018311 | 0.018311 | 0.75531 | 0.018311 | 0.013733
6168.8594 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.52643 | 0.10986 | -0.40283 | -0.97961 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.29297 | -0.17395 | -0.4715 | 0.009155 | 0.004578 | 0.013733 | 0.013733 | 0.70038 | 0.013733 | 0.018311
6170.6094 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | -0.001068 | 0.004272 | 0.002136 | -0.51727 | 0.09613 | -0.43945 | -1.0071 | 0.018311 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | -0.28839 | -0.19226 | -0.50354 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.80109 | 0.013733 | 0.018311
6172.375 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | -0.001068 | 0.001068 | 0.003204 | -0.52185 | 0.10071 | -0.44403 | -1.0071 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.27466 | -0.17395 | -0.50354 | 0.013733 | 0.009155 | 0.009155 | 0.009155 | 0.95215 | 0.022888 | 0.022888
6174.125 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.53558 | 0.09613 | -0.41657 | -0.97961 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | -0.27466 | -0.16479 | -0.47607 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.6134 | 0.018311 | 0.018311
6175.8125 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0 | 0 | 0.001068 | -0.52643 | 0.082397 | -0.4303 | -0.99792 | 0.009155 | 0.009155 | 0.009155 | 0.015259 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | -0.29755 | -0.16479 | -0.48065 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.69122 | 0.018311 | 0.022888
6177.5781 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.51727 | 0.10529 | -0.4303 | -1.0025 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.002136 | -0.29755 | -0.1831 | -0.48523 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 0.74158 | 0.022888 | 0.018311
6179.3438 | 0.076294 | 0.003204 | 0.003204 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.53558 | 0.068665 | -0.45319 | -1.0162 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.29755 | -0.19226 | -0.49439 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.76904 | 0.022888 | 0.022888
6181.0938 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.53101 | 0.086975 | -0.44403 | -1.0208 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | -0.29297 | -0.1831 | -0.50812 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 0.89722 | 0.018311 | 0.018311
6182.7812 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.53101 | 0.068665 | -0.46234 | -1.0391 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.28839 | -0.19226 | -0.5127 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 0.91095 | 0.018311 | 0.009155
6184.5312 | 0.045776 | 0.003204 | 0.001068 | 0.001068 | 0 | 0.001068 | 0 | -0.51727 | 0.073242 | -0.44861 | -1.0208 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.003204 | -0.27924 | -0.16937 | -0.50354 | 0.004578 | 0.009155 | 0.013733 | 0.009155 | 0.80566 | 0.018311 | 0.013733
6186.2188 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0 | 0 | 0.001068 | -0.52643 | 0.086975 | -0.45776 | -1.03 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | -0.28839 | -0.17395 | -0.50354 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.86517 | 0.018311 | 0.018311
6187.9219 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | -0.001068 | 0.002136 | 0.003204 | -0.52185 | 0.059509 | -0.4715 | -1.0483 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.003204 | 0.001068 | 0.003204 | 0 | 0.003204 | -0.28839 | -0.1831 | -0.51727 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 0.95673 | 0.013733 | 0.022888
6189.6875 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | -0.52643 | 0.064087 | -0.45776 | -1.0345 | 0.004578 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.27466 | -0.17395 | -0.49439 | 0.018311 | 0.018311 | 0.004578 | 0.018311 | 0.82855 | 0.022888 | 0.022888
6191.3906 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.53101 | 0.059509 | -0.46234 | -1.0345 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | 0.001068 | -0.29755 | -0.17395 | -0.49896 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.62714 | 0.022888 | 0.018311
6193.1406 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.52643 | 0.064087 | -0.48065 | -1.0574 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.29297 | -0.19226 | -0.51727 | 0.018311 | 0.013733 | 0.009155 | 0.009155 | 0.94757 | 0.013733 | 0.018311
6194.8906 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.54474 | 0.036621 | -0.48981 | -1.0574 | 0.009155 | 0.022888 | 0.022888 | 0.045776 | 0.002136 | 0.001068 | 0.004272 | 0.004272 | 0.002136 | -0.27924 | -0.19226 | -0.5127 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 1.0162 | 0.013733 | 0.018311
6196.5938 | 0.030518 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.54932 | 0.041199 | -0.4715 | -1.03 | 0.022888 | 0.018311 | 0.022888 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.28839 | -0.1831 | -0.50354 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.70953 | 0.013733 | 0.022888
6198.3594 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0 | 0.002136 | -0.53558 | 0.045776 | -0.47607 | -1.0437 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.29297 | -0.18768 | -0.50354 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.72327 | 0.018311 | 0.018311
6200.1094 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.52643 | 0.036621 | -0.49896 | -1.0666 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | -0.27924 | -0.19684 | -0.5127 | 0.022888 | 0.022888 | 0.009155 | 0.013733 | 0.89722 | 0.018311 | 0.018311
6201.7969 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.54932 | 0.045776 | -0.48523 | -1.0437 | 0.018311 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.28839 | -0.17395 | -0.50354 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.85602 | 0.013733 | 0.022888
6203.5625 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.55847 | 0.027466 | -0.49896 | -1.062 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0 | 0.002136 | -0.29297 | -0.18768 | -0.50812 | 0.009155 | 0.022888 | 0.018311 | 0.018311 | 0.79651 | 0.018311 | 0.013733
6205.25 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0 | -0.5722 | 0.009155 | -0.52185 | -1.0712 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.28839 | -0.19684 | -0.51727 | 0.009155 | 0.013733 | 0.009155 | 0.018311 | 0.83313 | 0.022888 | 0.018311
6207 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.55847 | 0.027466 | -0.49896 | -1.0666 | 0.009155 | 0.022888 | 0.022888 | 0.045776 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.28839 | -0.18768 | -0.50812 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | 0.88806 | 0.013733 | 0.018311
6208.7656 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.001068 | -0.55389 | 0.018311 | -0.5127 | -1.0849 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.3067 | -0.21057 | -0.52185 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.0666 | 0.022888 | 0.022888
6210.5156 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.55847 | 0.013733 | -0.52185 | -1.0849 | 0.009155 | 0.009155 | 0.013733 | 0.030518 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.29297 | -0.21057 | -0.53101 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.0117 | 0.013733 | 0.013733
6212.1875 | 0.045776 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.002136 | 0.003204 | -0.56763 | -0.009155 | -0.5127 | -1.0712 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | -0.31128 | -0.19684 | -0.50812 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.75531 | 0.009155 | 0.018311
6213.9531 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.55847 | 0.004578 | -0.51727 | -1.0757 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.31128 | -0.21515 | -0.51727 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.85144 | 0.022888 | 0.018311
6215.6406 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.55389 | 0 | -0.54474 | -1.1032 | 0.022888 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.29297 | -0.21973 | -0.54932 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 1.0071 | 0.022888 | 0.009155
6217.4062 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.56305 | 0.004578 | -0.51727 | -1.0803 | 0.018311 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -0.31586 | -0.23346 | -0.52185 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | 0.75073 | 0.018311 | 0.018311
6219.1406 | 0.045776 | 0.006409 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.55389 | -0.022888 | -0.54932 | -1.0986 | 0.018311 | 0.004578 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.31128 | -0.23804 | -0.55389 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.88806 | 0.022888 | 0.022888
6220.8438 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.55389 | -0.009155 | -0.54932 | -1.1124 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.28839 | -0.23804 | -0.55389 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.98419 | 0.022888 | 0.009155
6222.5938 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.54016 | -0.009155 | -0.54932 | -1.1124 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.29297 | -0.2243 | -0.55389 | 0.009155 | 0.022888 | 0.013733 | 0.013733 | 0.94757 | 0.018311 | 0.018311
6224.3438 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.56763 | -0.022888 | -0.54474 | -1.1078 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | -0.3067 | -0.21973 | -0.54016 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.77362 | 0.022888 | 0.013733
6226.0156 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -0.54932 | -0.004578 | -0.53558 | -1.0986 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.3067 | -0.2243 | -0.53558 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 0.90637 | 0.022888 | 0.009155
6227.7812 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.003204 | -0.56763 | -0.009155 | -0.54016 | -1.0895 | 0.009155 | 0.009155 | 0.013733 | 0.061035 | 0.001068 | 0 | 0 | 0.002136 | 0.004272 | -0.31586 | -0.22888 | -0.54016 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.75531 | 0.013733 | 0.013733
6229.5469 | 0.061035 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.5722 | -0.041199 | -0.56763 | -1.1215 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0 | 0.003204 | 0.003204 | 0.003204 | -0.30212 | -0.24261 | -0.5722 | 0.009155 | 0.009155 | 0.018311 | 0.013733 | 0.93842 | 0.022888 | 0.018311
6231.2969 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.56763 | -0.027466 | -0.56763 | -1.1215 | 0.018311 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.30212 | -0.23804 | -0.56763 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.0941 | 0.018311 | 0.013733
6233 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.56305 | -0.045776 | -0.56305 | -1.1124 | 0.009155 | 0.018311 | 0.022888 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | -0.29755 | -0.2243 | -0.55389 | 0.022888 | 0.009155 | 0.009155 | 0.013733 | 0.76446 | 0.018311 | 0.018311
6234.75 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.55389 | -0.041199 | -0.55389 | -1.1078 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.3067 | -0.24261 | -0.55389 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 0.79193 | 0.013733 | 0.018311
6236.4375 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.54932 | -0.009155 | -0.54932 | -1.1078 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.31128 | -0.23804 | -0.54474 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.9613 | 0.018311 | 0.013733
6238.125 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | -0.001068 | 0 | 0.001068 | -0.55389 | -0.027466 | -0.56763 | -1.1124 | 0.018311 | 0.018311 | 0.013733 | 0.030518 | 0 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | -0.32044 | -0.24719 | -0.55389 | 0.009155 | 0.018311 | 0.009155 | 0.018311 | 1.0254 | 0.018311 | 0.027466
6239.8125 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0 | 0.001068 | -0.55847 | -0.027466 | -0.55847 | -1.1124 | 0.018311 | 0.022888 | 0.022888 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.32501 | -0.2655 | -0.57678 | 0.004578 | 0.018311 | 0.013733 | 0.018311 | 0.79651 | 0.022888 | 0.009155
6241.5625 | 0.076294 | 0.004272 | 0.001068 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | -0.54932 | -0.045776 | -0.5722 | -1.1261 | 0.013733 | 0.013733 | 0.022888 | 0.076294 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.31586 | -0.27924 | -0.59052 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.93842 | 0.022888 | 0.013733
6243.3125 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | -0.002136 | 0.001068 | 0.003204 | -0.58136 | -0.054932 | -0.5722 | -1.1261 | 0.009155 | 0.013733 | 0.022888 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.32044 | -0.27008 | -0.59052 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.89722 | 0.018311 | 0.022888
6245.0156 | 0.045776 | 0.006409 | 0 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.57678 | -0.050354 | -0.59052 | -1.1444 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.32044 | -0.27924 | -0.60425 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 1.0025 | 0.027466 | 0.013733
6246.7812 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.003204 | -0.58594 | -0.054932 | -0.56763 | -1.1261 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.32501 | -0.2655 | -0.59052 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.79651 | 0.013733 | 0.013733
6248.5469 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.58594 | -0.054932 | -0.60883 | -1.1673 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.32044 | -0.27924 | -0.61798 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.1398 | 0.018311 | 0.013733
6250.2969 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.59509 | -0.059509 | -0.58136 | -1.1398 | 0.004578 | 0.004578 | 0.009155 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.32501 | -0.27466 | -0.59967 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.90179 | 0.022888 | 0.018311
6251.9844 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.59052 | -0.082397 | -0.60883 | -1.1536 | 0.009155 | 0.009155 | 0.018311 | 0.061035 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.32501 | -0.28839 | -0.61798 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.85602 | 0.018311 | 0.013733
6253.7344 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.57678 | -0.07782 | -0.62256 | -1.1719 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.32044 | -0.29297 | -0.62714 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 0.90179 | 0.013733 | 0.013733
6255.5 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | -0.58594 | -0.07782 | -0.61798 | -1.1719 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | -0.30212 | -0.63629 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 0.98877 | 0.022888 | 0.018311
6257.25 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.59052 | -0.068665 | -0.62256 | -1.1673 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.31586 | -0.28839 | -0.61798 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 0.9201 | 0.018311 | 0.022888
6258.9688 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.58594 | -0.073242 | -0.6134 | -1.149 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.33417 | -0.28839 | -0.60883 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.70038 | 0.013733 | 0.013733
6260.7031 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.59052 | -0.082397 | -0.63171 | -1.181 | 0.013733 | 0.009155 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | -0.32959 | -0.3067 | -0.63629 | 0.013733 | 0.009155 | 0.022888 | 0.013733 | 0.84686 | 0.018311 | 0.018311
6262.4531 | 0.045776 | 0.003204 | 0.002136 | 0.005341 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.10071 | -0.63171 | -1.181 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | -0.32959 | -0.30212 | -0.64087 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.93842 | 0.022888 | 0.013733
6264.2031 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0 | -0.57678 | -0.09613 | -0.63629 | -1.1993 | 0.013733 | 0.004578 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | -0.32959 | -0.3067 | -0.65002 | 0.013733 | 0.018311 | 0.009155 | 0.022888 | 1.0529 | 0.013733 | 0.018311
6265.9062 | 0.061035 | 0.005341 | 0.001068 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.59509 | -0.082397 | -0.61798 | -1.1765 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | -0.3479 | -0.31128 | -0.63171 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | 0.84686 | 0.022888 | 0.013733
6267.6719 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | -0.001068 | 0.002136 | 0 | -0.59509 | -0.09613 | -0.64087 | -1.1765 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.35706 | -0.31586 | -0.65002 | 0.022888 | 0.013733 | 0.009155 | 0.018311 | 0.93384 | 0.018311 | 0.018311
6269.4375 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.10529 | -0.64087 | -1.1765 | 0.009155 | 0.009155 | 0.018311 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.002136 | -0.33875 | -0.32044 | -0.65002 | 0.009155 | 0.009155 | 0.018311 | 0.013733 | 0.87891 | 0.009155 | 0.022888
6271.1875 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | -0.60425 | -0.10071 | -0.65002 | -1.181 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | -0.34332 | -0.32501 | -0.66376 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.72327 | 0.013733 | 0.018311
6272.875 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.59509 | -0.10529 | -0.64545 | -1.1856 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.33417 | -0.32501 | -0.65918 | 0.009155 | 0.022888 | 0.009155 | 0.018311 | 0.78735 | 0.013733 | 0.022888
6274.5781 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0 | -0.59509 | -0.10529 | -0.6546 | -1.2085 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.33417 | -0.33417 | -0.67749 | 0.018311 | 0.022888 | 0.004578 | 0.018311 | 1.03 | 0.022888 | 0.022888
6276.3438 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.001068 | 0 | -0.59967 | -0.1236 | -0.64545 | -1.1856 | 0.018311 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.33417 | -0.31586 | -0.6546 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.90179 | 0.018311 | 0.022888
6278.1094 | 0.030518 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | -0.56763 | -0.10071 | -0.6546 | -1.1993 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.32501 | -0.31586 | -0.67291 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.97504 | 0.022888 | 0.022888
6279.7969 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.56763 | -0.10071 | -0.63171 | -1.1856 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.33417 | -0.32044 | -0.65918 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 0.76904 | 0.013733 | 0.022888
6281.5469 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.5722 | -0.09613 | -0.64087 | -1.1765 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.003204 | -0.33875 | -0.32044 | -0.6546 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.76904 | 0.009155 | 0.018311
6283.2344 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.003204 | -0.56763 | -0.10071 | -0.64087 | -1.1856 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.34332 | -0.33875 | -0.67291 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 0.95673 | 0.018311 | 0.018311
6284.9375 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.56763 | -0.11444 | -0.65918 | -1.1993 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | -0.3479 | -0.35706 | -0.70038 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.94757 | 0.013733 | 0.018311
6286.625 | 0.045776 | 0.006409 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.58136 | -0.11902 | -0.6546 | -1.1993 | 0.013733 | 0.022888 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | -0.34332 | -0.3479 | -0.69122 | 0.022888 | 0.013733 | 0.009155 | 0.009155 | 0.94757 | 0.018311 | 0.022888
6288.375 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.59967 | -0.11902 | -0.65918 | -1.2039 | 0.022888 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.3479 | -0.3479 | -0.70953 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 1.0345 | 0.018311 | 0.018311
6290.0625 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.59967 | -0.13733 | -0.67749 | -1.2085 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.33417 | -0.35706 | -0.71411 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.97504 | 0.022888 | 0.018311
6291.75 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.60425 | -0.11902 | -0.65002 | -1.2039 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.34332 | -0.33875 | -0.69122 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | 0.78735 | 0.018311 | 0.022888
6293.4531 | 0.045776 | 0.004272 | 0 | 0.003204 | -0.001068 | 0.002136 | 0.002136 | -0.60425 | -0.13733 | -0.66834 | -1.2222 | 0.009155 | 0.009155 | 0.009155 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.34332 | -0.35706 | -0.70496 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.97046 | 0.018311 | 0.013733
6295.2031 | 0.045776 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.59967 | -0.13275 | -0.6546 | -1.1993 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.34332 | -0.33875 | -0.68665 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | 0.83313 | 0.018311 | 0.018311
6296.9062 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.58594 | -0.13275 | -0.67749 | -1.2131 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.34332 | -0.35248 | -0.69122 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 1.0757 | 0.013733 | 0.013733
6298.6875 | 0.061035 | 0.005341 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.5722 | -0.1236 | -0.67749 | -1.2085 | 0.013733 | 0.009155 | 0.018311 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.33417 | -0.35248 | -0.70038 | 0.004578 | 0.018311 | 0.013733 | 0.009155 | 0.97046 | 0.022888 | 0.022888
6300.4531 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.002136 | 0 | -0.60883 | -0.14191 | -0.69122 | -1.2222 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.33875 | -0.36163 | -0.71411 | 0.018311 | 0.022888 | 0.013733 | 0.018311 | 0.88348 | 0.018311 | 0.018311
6302.1406 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.6134 | -0.14648 | -0.67291 | -1.2085 | 0.009155 | 0.009155 | 0.018311 | 0.030518 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.34332 | -0.34332 | -0.70038 | 0.027466 | 0.004578 | 0.018311 | 0.009155 | 0.8194 | 0.022888 | 0.022888
6303.8281 | 0.045776 | 0.003204 | 0.001068 | 0 | 0.001068 | 0 | 0.003204 | -0.59509 | -0.15106 | -0.69122 | -1.2314 | 0.018311 | 0.013733 | 0.013733 | 0.076294 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | -0.34332 | -0.35706 | -0.70496 | 0.009155 | 0.018311 | 0.022888 | 0.018311 | 0.88806 | 0.018311 | 0.022888
6305.5781 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.60425 | -0.15106 | -0.6958 | -1.236 | 0.013733 | 0.022888 | 0.009155 | 0.061035 | 0 | 0.003204 | 0.005341 | 0.003204 | 0.002136 | -0.34332 | -0.35706 | -0.70953 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.93842 | 0.013733 | 0.013733
6307.25 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.60883 | -0.14191 | -0.67291 | -1.2085 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.36163 | -0.35706 | -0.69122 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.81024 | 0.022888 | 0.013733
6308.9531 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.59967 | -0.15564 | -0.70496 | -1.2314 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.36163 | -0.37994 | -0.73242 | 0.004578 | 0.013733 | 0.013733 | 0.009155 | 0.92468 | 0.018311 | 0.018311
6310.7188 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.59509 | -0.14648 | -0.67291 | -1.2222 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.004272 | 0.001068 | -0.36163 | -0.37537 | -0.71869 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 0.92468 | 0.013733 | 0.018311
6312.4688 | 0.045776 | 0.005341 | 0 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.59052 | -0.14191 | -0.69122 | -1.2222 | 0.018311 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | -0.36621 | -0.37537 | -0.737 | 0.018311 | 0.013733 | 0.027466 | 0.013733 | 0.94299 | 0.013733 | 0.022888
6314.1562 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.59052 | -0.15106 | -0.70038 | -1.236 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.001068 | 0.004272 | 0.002136 | 0.003204 | -0.35248 | -0.3891 | -0.74616 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.97046 | 0.022888 | 0.018311
6315.8438 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.6134 | -0.15564 | -0.70038 | -1.2405 | 0.004578 | 0.009155 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.35248 | -0.3891 | -0.74158 | 0.013733 | 0.009155 | 0.022888 | 0.018311 | 1.0483 | 0.027466 | 0.027466
6317.6094 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.60425 | -0.15564 | -0.68207 | -1.236 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | -0.002136 | 0.002136 | -0.35248 | -0.3891 | -0.737 | 0.009155 | 0.009155 | 0.018311 | 0.013733 | 0.90179 | 0.022888 | 0.022888
6319.3906 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.62256 | -0.16937 | -0.70038 | -1.236 | 0.009155 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | -0.35706 | -0.39825 | -0.75073 | 0.013733 | 0.013733 | 0.013733 | 0.004578 | 0.78735 | 0.013733 | 0.022888
6321.0781 | 0.030518 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.60425 | -0.17853 | -0.70496 | -1.2543 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.36163 | -0.41199 | -0.7782 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.83771 | 0.013733 | 0.018311
6322.7656 | 0.030518 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | -0.60425 | -0.16937 | -0.71869 | -1.2634 | 0.004578 | 0.009155 | 0.022888 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.004272 | -0.3479 | -0.40741 | -0.7782 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.97046 | 0.013733 | 0.018311
6324.5312 | 0.030518 | 0.005341 | 0.001068 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.17395 | -0.72327 | -1.2497 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.35248 | -0.40741 | -0.7782 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.97504 | 0.018311 | 0.022888
6326.2031 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0.003204 | 0.003204 | -0.6134 | -0.16479 | -0.6958 | -1.236 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.35248 | -0.38452 | -0.75073 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.82855 | 0.022888 | 0.013733
6327.9062 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0 | 0.003204 | -0.6134 | -0.18768 | -0.71869 | -1.2543 | 0.013733 | 0.027466 | 0.018311 | 0.030518 | 0 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.35248 | -0.40741 | -0.7782 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.85144 | 0.018311 | 0.013733
6329.6719 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.001068 | 0 | -0.59967 | -0.16937 | -0.71411 | -1.2451 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.004272 | -0.35706 | -0.39825 | -0.76904 | 0.013733 | 0.009155 | 0.022888 | 0.009155 | 0.81024 | 0.022888 | 0.018311
6331.3594 | 0.076294 | 0.005341 | 0.002136 | 0.002136 | -0.002136 | 0 | 0.002136 | -0.60883 | -0.16937 | -0.70496 | -1.2314 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.35706 | -0.40283 | -0.75531 | 0.009155 | 0.022888 | 0.013733 | 0.018311 | 0.70038 | 0.013733 | 0.018311
6333.0469 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.18768 | -0.72327 | -1.2497 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.36621 | -0.40741 | -0.78278 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.8606 | 0.022888 | 0.018311
6334.7344 | 0.030518 | 0.005341 | 0.001068 | 0.004272 | -0.001068 | 0.002136 | 0 | -0.60425 | -0.19226 | -0.73242 | -1.2634 | 0.018311 | 0.013733 | 0.009155 | 0.061035 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.35248 | -0.40741 | -0.7782 | 0.013733 | 0.013733 | 0.022888 | 0.013733 | 0.98419 | 0.018311 | 0.018311
6336.4844 | 0.045776 | 0.004272 | 0.001068 | 0 | 0 | 0.001068 | 0 | -0.60883 | -0.17395 | -0.70953 | -1.2405 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.004272 | -0.3479 | -0.39368 | -0.75531 | 0.009155 | 0.013733 | 0.018311 | 0.009155 | 0.85602 | 0.018311 | 0.018311
6338.2344 | 0.030518 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.59509 | -0.19684 | -0.737 | -1.2589 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | -0.34332 | -0.40283 | -0.77362 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 0.91553 | 0.018311 | 0.022888
6339.9375 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.59967 | -0.16937 | -0.70953 | -1.2497 | 0.022888 | 0.013733 | 0.013733 | 0.030518 | 0.001068 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | -0.34332 | -0.38452 | -0.75531 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 1.0025 | 0.018311 | 0.018311
6341.7031 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.59509 | -0.17853 | -0.71411 | -1.2405 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.3479 | -0.37994 | -0.75531 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.93842 | 0.022888 | 0.018311
6343.4688 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | -0.6134 | -0.20142 | -0.737 | -1.2726 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.001068 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | -0.33875 | -0.39825 | -0.76904 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | 0.96588 | 0.018311 | 0.018311
6345.2188 | 0.061035 | 0.006409 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.59509 | -0.1831 | -0.70953 | -1.2451 | 0.018311 | 0.009155 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.34332 | -0.37994 | -0.75073 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.78735 | 0.018311 | 0.022888
6346.9219 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.62256 | -0.18768 | -0.70953 | -1.2451 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.3479 | -0.39368 | -0.75531 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.8194 | 0.022888 | 0.022888
6348.6875 | 0.015259 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.60425 | -0.18768 | -0.72784 | -1.2726 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -0.35706 | -0.40741 | -0.76904 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.88348 | 0.022888 | 0.022888
6350.4531 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.20142 | -0.72784 | -1.2543 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.005341 | -0.34332 | -0.3891 | -0.76446 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.81482 | 0.022888 | 0.022888
6352.2188 | 0.045776 | 0.003204 | 0.003204 | 0 | 0 | 0.001068 | 0.001068 | -0.60883 | -0.18768 | -0.73242 | -1.2497 | 0.009155 | 0.009155 | 0.013733 | 0.076294 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.3479 | -0.39825 | -0.76446 | 0.018311 | 0.022888 | 0.013733 | 0.009155 | 0.94299 | 0.018311 | 0.027466
6353.9219 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.60425 | -0.16937 | -0.73242 | -1.2543 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.35248 | -0.39825 | -0.77362 | 0.018311 | 0.018311 | 0.013733 | 0.009155 | 1.0162 | 0.018311 | 0.018311
6355.6719 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.001068 | -0.6134 | -0.19226 | -0.73242 | -1.2634 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.36163 | -0.40283 | -0.77362 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.92468 | 0.027466 | 0.022888
6357.3594 | 0.061035 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.003204 | -0.57678 | -0.17853 | -0.75531 | -1.3 | 0.018311 | 0.018311 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.32959 | -0.40741 | -0.79651 | 0.027466 | 0.013733 | 0.022888 | 0.013733 | 1.0986 | 0.022888 | 0.027466
6359.1562 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.59509 | -0.17395 | -0.71869 | -1.2543 | 0.009155 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.005341 | 0.002136 | -0.30212 | -0.37994 | -0.75073 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | 0.76904 | 0.013733 | 0.013733
6360.8594 | 0.076294 | 0.005341 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -1.8768 | -0.37537 | -1.3824 | -3.035 | 0.013733 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 3.7857 | 5.2826 | 1.6525 | 0.013733 | 0.004578 | 0.018311 | 0.013733 | 0.94757 | 0.013733 | 0.022888
6362.625 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.001068 | 0.78735 | 0.79193 | 1.8082 | 2.243 | 0.013733 | 0.022888 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -2.7878 | -0.59509 | -1.5839 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.95673 | 0.018311 | 0.027466
6364.375 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0 | 0 | -0.23804 | 0.28839 | 0.32044 | 2.0554 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -2.1515 | 1.5518 | 0.86975 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.79193 | 0.013733 | 0.018311
6366.125 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.48523 | 0.059509 | -0.20599 | 0.55389 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -1.1398 | 1.4282 | 1.8951 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.87433 | 0.018311 | 0.018311
6367.8281 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0 | 0.001068 | -0.2655 | 0.082397 | -0.30212 | -0.23346 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -1.0712 | 1.0529 | 1.6159 | 0.022888 | 0.009155 | 0.013733 | 0.004578 | 0.86975 | 0.018311 | 0.018311
6369.5312 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | 1.8677 | 2.5543 | -0.98877 | 0.059509 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 2.0691 | 1.1719 | -0.95673 | 0.018311 | 0.018311 | 0.013733 | 0.009155 | 0.79651 | 0.013733 | 0.022888
6371.2812 | 0.076294 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | 0.059509 | 0.22888 | 1.8585 | -0.027466 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.58594 | -0.94299 | -1.3641 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 1.1169 | 0.018311 | 0.022888
6373.0312 | 0.061035 | 0.002136 | 0.001068 | 0.004272 | 0.001068 | 0.001068 | 0.003204 | -1.5335 | -1.0162 | 1.6067 | -0.55389 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | -1.0025 | -0.59967 | -2.8564 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 1.3 | 0.018311 | 0.022888
6374.7344 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | 1.1353 | 0.97504 | 0.39825 | 1.973 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -1.1673 | 0.64545 | -1.2817 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.1261 | 0.018311 | 0.027466
6376.5 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | 0.33875 | 1.181 | -0.62714 | -0.14648 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | -0.87433 | -0.21057 | -0.83313 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 1.03 | 0.027466 | 0.018311
6378.25 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0 | -0.027466 | 0.24261 | 2.1011 | -0.054932 | 0.018311 | 0.013733 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -1.5976 | 2.5909 | 1.2772 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 0.88806 | 0.013733 | 0.013733
6379.9375 | 0.030518 | 0.003204 | 0.004272 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.009155 | 0.28839 | 0.97504 | -0.33875 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -1.7715 | 0.46234 | 1.4145 | 0.013733 | 0.004578 | 0.013733 | 0.018311 | 0.66376 | 0.009155 | 0.022888
6381.7031 | 0.030518 | 0.004272 | 0.001068 | 0.003204 | 0 | 0 | 0.001068 | -0.44403 | 0.09613 | 0.33417 | -0.28839 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | -1.2314 | -0.10986 | 1.4511 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.54474 | 0.022888 | 0.018311
6383.4531 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.001068 | -0.61798 | 0.009155 | -0.11902 | -0.48065 | 0.018311 | 0.013733 | 0.009155 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.97046 | -0.41199 | 1.2589 | 0.013733 | 0.022888 | 0.013733 | 0.018311 | 0.62714 | 0.022888 | 0.018311
6385.2188 | 0.030518 | 0.002136 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -0.67291 | -0.027466 | -0.37079 | -0.66376 | 0.009155 | 0.009155 | 0.013733 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.78735 | -0.55847 | 1.0254 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.71411 | 0.018311 | 0.013733
6386.9375 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.001068 | 0.001068 | 0.003204 | -0.68207 | -0.027466 | -0.52185 | -0.8194 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -0.66376 | -0.59052 | 0.80566 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | 0.82398 | 0.018311 | 0.022888
6388.7031 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.72327 | -0.032043 | -0.54932 | -0.91095 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.20599 | -0.19684 | 1.2405 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.8194 | 0.022888 | 0.018311
6390.4688 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.95673 | -0.1831 | -0.68207 | -1.0849 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.39368 | -0.26093 | 0.91095 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 1.2405 | 0.018311 | 0.013733
6392.1562 | 0.061035 | 0.003204 | 0.004272 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.9201 | -0.1831 | -0.86517 | -1.1581 | 0.009155 | 0.013733 | 0.009155 | 0.030518 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.63629 | 0.35706 | 1.3046 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 1.3367 | 0.022888 | 0.018311
6393.8438 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.95673 | -0.19684 | -0.82855 | -1.4053 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.16937 | 0.42114 | 1.0849 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 1.2085 | 0.018311 | 0.018311
6395.5312 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.45319 | -0.004578 | -0.68665 | -1.3824 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.63171 | 0.65918 | 2.1698 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | 1.3458 | 0.018311 | 0.018311
6397.2812 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -0.67749 | 0.10529 | -0.55847 | -1.355 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | 0.10986 | 0.07782 | -0.68665 | 0.018311 | 0.018311 | 0.004578 | 0.018311 | 1.0757 | 0.013733 | 0.013733
6398.9844 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | 0.001068 | -0.70953 | -0.15564 | -0.65002 | -1.2543 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.32501 | 0.32044 | -0.16479 | 0.004578 | 0.018311 | 0.009155 | 0.018311 | 0.82855 | 0.022888 | 0.013733
6400.75 | 0.061035 | 0.006409 | 0.004272 | 0.001068 | -0.001068 | 0.002136 | 0.002136 | -0.74616 | -0.19226 | -0.70953 | -1.2131 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.27466 | 0.46234 | 0.18768 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 0.39368 | 0.013733 | 0.018311
6402.5 | 0.061035 | 0.006409 | 0.003204 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.72327 | -0.19684 | -0.75989 | -1.2222 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.12817 | 0.46692 | 0.36163 | 0.027466 | 0.013733 | 0.018311 | 0.018311 | 0.63629 | 0.018311 | 0.018311
6404.25 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.72784 | -0.21057 | -0.78735 | -1.2497 | 0.013733 | 0.018311 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.036621 | 0.3891 | 0.41199 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.67291 | 0.018311 | 0.013733
6405.9375 | 0.061035 | 0.007477 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.70496 | -0.22888 | -0.80109 | -1.2634 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.1831 | 0.2655 | 0.37994 | 0.009155 | 0.018311 | 0.009155 | 0.009155 | 0.72784 | 0.018311 | 0.013733
6407.6875 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0 | -0.68665 | -0.21973 | -0.78735 | -1.2634 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0.005341 | -0.31128 | 0.14191 | 0.31128 | 0.022888 | 0.022888 | 0.018311 | 0.013733 | 0.74616 | 0.018311 | 0.013733
6409.375 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.68207 | -0.2243 | -0.78735 | -1.2772 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.40741 | -0.004578 | 0.20599 | 0.004578 | 0.013733 | 0.009155 | 0.013733 | 0.87433 | 0.027466 | 0.018311
6411.125 | 0.030518 | 0.004272 | 0.001068 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.67291 | -0.23346 | -0.79651 | -1.2863 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.003204 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | -0.48065 | -0.14191 | 0.07782 | 0.009155 | 0.013733 | 0.018311 | 0.022888 | 0.94757 | 0.009155 | 0.018311
6412.8125 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | -0.6546 | -0.2243 | -0.80109 | -1.3 | 0.009155 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.51727 | -0.25635 | -0.068665 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | 1.1536 | 0.018311 | 0.027466
6414.5625 | 0.030518 | 0.006409 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.63629 | -0.21057 | -0.76904 | -1.2817 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.53558 | -0.34332 | -0.17395 | 0.013733 | 0.022888 | 0.013733 | 0.018311 | 0.97961 | 0.009155 | 0.022888
6416.3281 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.63171 | -0.2243 | -0.77362 | -1.2955 | 0.013733 | 0.013733 | 0.022888 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.5722 | -0.4303 | -0.28381 | 0.009155 | 0.018311 | 0.013733 | 0.009155 | 1.062 | 0.027466 | 0.018311
6418.0156 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | -0.002136 | 0.003204 | 0.003204 | -0.64545 | -0.24719 | -0.79193 | -1.3092 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | -0.58136 | -0.50812 | -0.41657 | 0.009155 | 0.018311 | 0.009155 | 0.022888 | 1.149 | 0.013733 | 0.018311
6419.7812 | 0.076294 | 0.006409 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.2243 | -0.76446 | -1.2909 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.56763 | -0.54932 | -0.49896 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.92926 | 0.018311 | 0.018311
6421.5469 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.62256 | -0.23346 | -0.75989 | -1.2772 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.5722 | -0.59052 | -0.5722 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.81482 | 0.009155 | 0.018311
6423.2344 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.62714 | -0.23346 | -0.76446 | -1.3 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.56305 | -0.63171 | -0.66376 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | 1.0666 | 0.013733 | 0.022888
6424.9375 | 0.030518 | 0.005341 | 0.001068 | 0.002136 | -0.001068 | 0.003204 | 0.002136 | -0.61798 | -0.24261 | -0.77362 | -1.2772 | 0.013733 | 0.013733 | 0.004578 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.55389 | -0.6546 | -0.71411 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.78735 | 0.022888 | 0.018311
6426.6875 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.63629 | -0.23804 | -0.75073 | -1.2726 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.53558 | -0.65918 | -0.76446 | 0.013733 | 0.004578 | 0.022888 | 0.013733 | 0.82398 | 0.018311 | 0.018311
6428.4375 | 0.030518 | 0.007477 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.002136 | -0.62714 | -0.24261 | -0.76446 | -1.2817 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -0.52185 | -0.67749 | -0.81024 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 1.0574 | 0.013733 | 0.022888
6430.2031 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.001068 | -0.62256 | -0.24719 | -0.75989 | -1.2634 | 0.018311 | 0.018311 | 0.009155 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.49896 | -0.65918 | -0.84686 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 0.95673 | 0.018311 | 0.018311
6431.9219 | 0.045776 | 0.005341 | 0.001068 | 0 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.2655 | -0.77362 | -1.2726 | 0.009155 | 0.018311 | 0.009155 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.004272 | -0.48065 | -0.66834 | -0.86517 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 0.93384 | 0.018311 | 0.018311
6433.6875 | 0.045776 | 0.006409 | 0.001068 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.62256 | -0.25177 | -0.75531 | -1.268 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.4715 | -0.66376 | -0.89264 | 0.013733 | 0.018311 | 0.009155 | 0.013733 | 0.94757 | 0.022888 | 0.013733
6435.375 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.61798 | -0.26093 | -0.76446 | -1.268 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.45319 | -0.65918 | -0.90637 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.88348 | 0.022888 | 0.022888
6437.125 | 0.061035 | 0.006409 | 0.002136 | 0.003204 | 0 | 0.002136 | -0.001068 | -0.61798 | -0.26093 | -0.78278 | -1.2955 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | -0.44403 | -0.65918 | -0.94757 | 0.018311 | 0.022888 | 0.009155 | 0.018311 | 1.0986 | 0.018311 | 0.013733
6438.8281 | 0.061035 | 0.008545 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.61798 | -0.27466 | -0.77362 | -1.2772 | 0.004578 | 0.004578 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.4303 | -0.63629 | -0.93384 | 0.009155 | 0.018311 | 0.009155 | 0.009155 | 0.85602 | 0.018311 | 0.013733
6440.5156 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | -0.001068 | 0.005341 | 0 | -0.60425 | -0.25177 | -0.76446 | -1.2634 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -0.42114 | -0.61798 | -0.92926 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.85144 | 0.018311 | 0.018311
6442.2812 | 0.045776 | 0.006409 | 0.002136 | 0.004272 | -0.001068 | 0.001068 | 0.002136 | -0.62256 | -0.26093 | -0.76904 | -1.2772 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.40741 | -0.6134 | -0.93842 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.0254 | 0.027466 | 0.022888
6443.9844 | 0.030518 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0 | -0.6134 | -0.27008 | -0.75989 | -1.268 | 0.013733 | 0.009155 | 0.013733 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.40741 | -0.60425 | -0.93842 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 0.94757 | 0.018311 | 0.013733
6445.75 | 0.061035 | 0.006409 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.61798 | -0.2655 | -0.75531 | -1.2634 | 0.013733 | 0.013733 | 0.004578 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | -0.40741 | -0.60883 | -0.93842 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 0.87891 | 0.013733 | 0.018311
6447.5156 | 0.030518 | 0.006409 | 0.002136 | 0.004272 | 0 | 0.003204 | 0.002136 | -0.61798 | -0.27008 | -0.78735 | -1.2863 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.003204 | 0.001068 | 0.004272 | 0.004272 | -0.39368 | -0.59967 | -0.9613 | 0.004578 | 0.013733 | 0.013733 | 0.013733 | 1.1124 | 0.018311 | 0.027466
6449.2812 | 0.061035 | 0.007477 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | -0.63629 | -0.28381 | -0.76904 | -1.268 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -0.39368 | -0.5722 | -0.94757 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.77362 | 0.018311 | 0.018311
6450.9688 | 0.076294 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.62714 | -0.28381 | -0.79651 | -1.2955 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.37994 | -0.5722 | -0.95215 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.0391 | 0.018311 | 0.018311
6452.7188 | 0.061035 | 0.007477 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.61798 | -0.27924 | -0.76446 | -1.2634 | 0.009155 | 0.004578 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | -0.36621 | -0.53558 | -0.92468 | 0.004578 | 0.013733 | 0.013733 | 0.022888 | 0.83313 | 0.022888 | 0.018311
6454.4688 | 0.061035 | 0.006409 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.64545 | -0.30212 | -0.81024 | -1.2955 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | 0.003204 | -0.35706 | -0.54932 | -0.93384 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 1.0117 | 0.013733 | 0.018311
6456.2188 | 0.045776 | 0.005341 | 0.002136 | 0 | 0 | 0.002136 | 0.003204 | -0.63629 | -0.29297 | -0.80566 | -1.3046 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.35248 | -0.53558 | -0.92926 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.0071 | 0.013733 | 0.018311
6457.9062 | 0.045776 | 0.006409 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0.003204 | -0.64545 | -0.28381 | -0.7782 | -1.2772 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.35706 | -0.50354 | -0.89264 | 0.009155 | 0.022888 | 0.013733 | 0.018311 | 0.99335 | 0.018311 | 0.022888
6459.6562 | 0.061035 | 0.007477 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.64545 | -0.29755 | -0.80109 | -1.2955 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | -0.36621 | -0.52185 | -0.90637 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 1.03 | 0.018311 | 0.013733
6461.3438 | 0.061035 | 0.006409 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.64087 | -0.30212 | -0.78278 | -1.2726 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.36621 | -0.50354 | -0.89264 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.79651 | 0.027466 | 0.018311
6463.0312 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.63171 | -0.28381 | -0.80109 | -1.2955 | 0.009155 | 0.009155 | 0.013733 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | -0.37079 | -0.5127 | -0.90179 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.9613 | 0.027466 | 0.018311
6464.7812 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.63629 | -0.30212 | -0.80566 | -1.3 | 0.004578 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.37537 | -0.52185 | -0.90179 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 1.0025 | 0.013733 | 0.013733
6466.5469 | 0.030518 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.63171 | -0.3067 | -0.79651 | -1.3 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.35248 | -0.50354 | -0.89722 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.79193 | 0.018311 | 0.018311
6468.2969 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.63171 | -0.28839 | -0.78735 | -1.2817 | 0.004578 | 0.009155 | 0.022888 | 0.061035 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.35706 | -0.49439 | -0.87433 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.76904 | 0.022888 | 0.018311
6469.9844 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | 0.001068 | 0.001068 | -0.63171 | -0.28839 | -0.78735 | -1.2817 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.37079 | -0.50354 | -0.87433 | 0.004578 | 0.004578 | 0.022888 | 0.013733 | 0.8606 | 0.018311 | 0.022888
6471.7656 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.63171 | -0.28381 | -0.81482 | -1.3092 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | -0.35248 | -0.5127 | -0.90179 | 0.009155 | 0.018311 | 0.009155 | 0.022888 | 0.99792 | 0.018311 | 0.013733
6473.5156 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.62256 | -0.29755 | -0.81024 | -1.3092 | 0.013733 | 0.009155 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | -0.3479 | -0.50354 | -0.89722 | 0.013733 | 0.018311 | 0.022888 | 0.018311 | 0.99792 | 0.013733 | 0.027466
6475.2812 | 0.030518 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.30212 | -0.81482 | -1.3138 | 0.013733 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.35248 | -0.49439 | -0.88348 | 0.013733 | 0.009155 | 0.004578 | 0.018311 | 1.0574 | 0.022888 | 0.013733
6476.9844 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.28381 | -0.78278 | -1.2909 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.36163 | -0.48065 | -0.86517 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.90179 | 0.013733 | 0.018311
6478.6875 | 0.030518 | 0.005341 | 0.002136 | 0.003204 | -0.002136 | 0.002136 | 0.001068 | -0.63629 | -0.30212 | -0.81024 | -1.3229 | 0.018311 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.37994 | -0.50812 | -0.89722 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 1.062 | 0.022888 | 0.018311
6480.375 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.61798 | -0.28839 | -0.79651 | -1.3 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.35706 | -0.49896 | -0.88348 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 1.0529 | 0.018311 | 0.013733
6482.0625 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | -0.6134 | -0.28839 | -0.7782 | -1.2863 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.36621 | -0.48523 | -0.86975 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 0.77362 | 0.018311 | 0.018311
6483.75 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.3067 | -0.81024 | -1.3092 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.35248 | -0.49896 | -0.88806 | 0.022888 | 0.013733 | 0.004578 | 0.013733 | 0.9201 | 0.018311 | 0.022888
6485.5 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.63171 | -0.32501 | -0.80109 | -1.2817 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.35248 | -0.48523 | -0.86517 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.9613 | 0.022888 | 0.009155
6487.25 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.61798 | -0.29297 | -0.79193 | -1.2817 | 0.013733 | 0.013733 | 0.004578 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | -0.3479 | -0.47607 | -0.85144 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.92926 | 0.022888 | 0.013733
6488.9531 | 0.076294 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.62714 | -0.32959 | -0.81024 | -1.3 | 0.009155 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.34332 | -0.46692 | -0.85602 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.95673 | 0.018311 | 0.022888
6490.6562 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.62714 | -0.3067 | -0.78735 | -1.268 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.35248 | -0.46234 | -0.83313 | 0.013733 | 0.022888 | 0.013733 | 0.009155 | 0.84228 | 0.013733 | 0.018311
6492.4062 | 0.045776 | 0.005341 | 0.005341 | 0.004272 | 0 | 0.001068 | 0.001068 | -0.61798 | -0.29297 | -0.81024 | -1.3 | 0.018311 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.3479 | -0.47607 | -0.84686 | 0.013733 | 0.009155 | 0.018311 | 0.009155 | 1.1353 | 0.013733 | 0.018311
6494.0938 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.62256 | -0.29297 | -0.77362 | -1.2817 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | -0.31586 | -0.46692 | -0.83313 | 0.009155 | 0.022888 | 0.013733 | 0.013733 | 1.1169 | 0.018311 | 0.022888
6495.7812 | 0.045776 | 0.006409 | 0.003204 | 0.001068 | -0.001068 | 0.001068 | 0.003204 | -0.61798 | -0.31586 | -0.80109 | -1.2909 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.001068 | 0 | 0.002136 | 0.003204 | -0.3479 | -0.4715 | -0.84686 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 1.0208 | 0.027466 | 0.022888
6497.4688 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0 | 0.002136 | -0.62256 | -0.32044 | -0.80109 | -1.2955 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.32501 | -0.46692 | -0.85602 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 1.03 | 0.013733 | 0.022888
6499.1562 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | -0.001068 | 0.001068 | 0.001068 | -0.62714 | -0.3067 | -0.80109 | -1.3 | 0.013733 | 0.009155 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | -0.45776 | -0.85602 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 1.3367 | 0.013733 | 0.022888
6500.8594 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.29755 | -0.79651 | -1.2863 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.001068 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -0.32501 | -0.45776 | -0.84228 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.0483 | 0.018311 | 0.022888
6502.6094 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.64087 | -0.29297 | -0.7782 | -1.2817 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.31128 | -0.45776 | -0.84228 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 1.3 | 0.022888 | 0.018311
6504.375 | 0.045776 | 0.003204 | 0.005341 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.64087 | -0.31586 | -0.78278 | -1.2772 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.32044 | -0.44403 | -0.83771 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.0849 | 0.013733 | 0.013733
6506.1406 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -0.63171 | -0.31128 | -0.74158 | -1.2405 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.33875 | -0.44403 | -0.82855 | 0.013733 | 0.022888 | 0.018311 | 0.013733 | 1.3687 | 0.027466 | 0.013733
6507.8281 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 1.2405 | 0.27924 | 1.8768 | 3.36 | 0.018311 | 0.018311 | 0.013733 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -1.4511 | -2.243 | -1.9501 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 1.2634 | 0.018311 | 0.018311
6509.5781 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | -0.001068 | 0.003204 | 0.001068 | 0.33875 | 0.022888 | 0.19226 | 1.387 | 0.018311 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | -0.12817 | -1.6571 | -2.4719 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.4282 | 0.009155 | 0.022888
6511.3438 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0.002136 | 0 | 0 | -2.9205 | -1.5244 | -1.268 | -4.184 | 0.018311 | 0.009155 | 0.009155 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.054932 | 0.032043 | -0.41657 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 1.0437 | 0.018311 | 0.022888
6513.0312 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.001068 | 0.001068 | -1.5106 | -0.32501 | -0.94299 | -2.8061 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 1.0986 | 0.72327 | 0.29297 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.2955 | 0.022888 | 0.013733
6514.7812 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | -0.001068 | 0 | 0.002136 | -0.80566 | -0.43945 | -1.0437 | -2.2293 | 0.022888 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.001068 | 0.001068 | 2.1332 | 1.268 | 2.5681 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 1.181 | 0.027466 | 0.018311
6516.5469 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.43488 | -0.24261 | -0.88806 | -1.9409 | 0.013733 | 0.013733 | 0.013733 | 0.015259 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 1.6708 | 1.886 | 2.0187 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 1.268 | 0.013733 | 0.018311
6518.3125 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.43488 | -0.35248 | -0.85602 | -1.7899 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 1.0895 | 1.2497 | 0.1831 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 1.0666 | 0.018311 | 0.018311
6520 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.38452 | -0.21057 | -0.74158 | -1.6663 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.10986 | -0.40283 | -2.3026 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 1.387 | 0.018311 | 0.022888
6521.7031 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.32959 | -0.22888 | -0.69122 | -1.561 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.009155 | -0.27466 | -1.355 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.1627 | 0.013733 | 0.013733
6523.4531 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.35706 | -0.26093 | -0.69122 | -1.4877 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.054932 | -0.27924 | -0.93384 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.1627 | 0.018311 | 0.009155
6525.2031 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | -0.001068 | 0.003204 | 0.001068 | -0.41199 | -0.28381 | -0.68665 | -1.4374 | 0.022888 | 0.018311 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.10071 | -0.28381 | -0.70953 | 0.022888 | 0.013733 | 0.009155 | 0.013733 | 1.2039 | 0.022888 | 0.018311
6526.9062 | 0.061035 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.45319 | -0.29297 | -0.70496 | -1.3962 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.004272 | 0.003204 | 0.002136 | -0.15106 | -0.30212 | -0.62256 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.2039 | 0.018311 | 0.018311
6528.6562 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0 | 0.001068 | -0.47607 | -0.30212 | -0.71411 | -1.3687 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | 0.001068 | -0.18768 | -0.3067 | -0.5722 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.3229 | 0.018311 | 0.009155
6530.3438 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.50812 | -0.28381 | -0.71411 | -1.3458 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.21057 | -0.32501 | -0.55389 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 1.3046 | 0.018311 | 0.013733
6532.0938 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.004272 | 0.003204 | -0.53558 | -0.3067 | -0.72327 | -1.3412 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.23804 | -0.3479 | -0.56763 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | 1.4465 | 0.018311 | 0.022888
6533.7812 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | -0.55847 | -0.29297 | -0.71869 | -1.3 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.24261 | -0.34332 | -0.55389 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 1.1353 | 0.013733 | 0.018311
6535.5312 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.003204 | -0.56763 | -0.30212 | -0.74616 | -1.3138 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | -0.26093 | -0.35706 | -0.58594 | 0.018311 | 0.013733 | 0.022888 | 0.022888 | 1.2817 | 0.018311 | 0.018311
6537.2969 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.55389 | -0.29755 | -0.737 | -1.2955 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.27466 | -0.36163 | -0.59509 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 1.2085 | 0.018311 | 0.022888
6539 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | -0.002136 | 0.002136 | 0.002136 | -0.5722 | -0.31128 | -0.77362 | -1.3184 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.28381 | -0.37994 | -0.62714 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.3275 | 0.022888 | 0.013733
6540.7656 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | -0.57678 | -0.29755 | -0.77362 | -1.3138 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.28839 | -0.38452 | -0.65002 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.2634 | 0.022888 | 0.022888
6542.4688 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | -0.001068 | 0.001068 | 0.003204 | -0.57678 | -0.29755 | -0.75531 | -1.3046 | 0.018311 | 0.009155 | 0.013733 | 0.015259 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.28381 | -0.37537 | -0.64545 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.3092 | 0.013733 | 0.022888
6544.1719 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.57678 | -0.28839 | -0.75073 | -1.2772 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.30212 | -0.37994 | -0.63629 | 0.013733 | 0.009155 | 0.009155 | 0.013733 | 1.1307 | 0.022888 | 0.022888
6545.875 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | -0.59052 | -0.3067 | -0.75989 | -1.2817 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | -0.3067 | -0.39825 | -0.65918 | 0.022888 | 0.018311 | 0.013733 | 0.018311 | 1.1536 | 0.022888 | 0.018311
6547.5781 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.58594 | -0.29297 | -0.77362 | -1.3 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | -0.30212 | -0.41199 | -0.69122 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | 1.3 | 0.013733 | 0.022888
6549.2969 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.59509 | -0.31586 | -0.76904 | -1.2955 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.30212 | -0.40283 | -0.69122 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | 1.0345 | 0.013733 | 0.009155
6550.9844 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.004272 | 0.003204 | -0.60883 | -0.31586 | -0.78735 | -1.2909 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0 | -0.31128 | -0.40283 | -0.70038 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.1536 | 0.022888 | 0.013733
6552.7344 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.59967 | -0.31128 | -0.79651 | -1.3092 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.31586 | -0.42114 | -0.71869 | 0.013733 | 0.009155 | 0.022888 | 0.022888 | 1.3275 | 0.018311 | 0.027466
6554.4219 | 0.091553 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | -0.61798 | -0.32044 | -0.78735 | -1.3046 | 0.018311 | 0.013733 | 0.009155 | 0.015259 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.30212 | -0.40283 | -0.72784 | 0.022888 | 0.018311 | 0.013733 | 0.013733 | 1.3367 | 0.018311 | 0.022888
6556.1094 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.62256 | -0.31128 | -0.80109 | -1.3046 | 0.013733 | 0.009155 | 0.013733 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.30212 | -0.41199 | -0.72784 | 0.009155 | 0.013733 | 0.009155 | 0.022888 | 1.3412 | 0.022888 | 0.013733
6557.7969 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.6134 | -0.30212 | -0.78735 | -1.2863 | 0.013733 | 0.027466 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.31586 | -0.40283 | -0.71411 | 0.013733 | 0.013733 | 0.022888 | 0.022888 | 1.0666 | 0.018311 | 0.022888
6559.5312 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | -0.001068 | 0.003204 | 0.003204 | -0.64545 | -0.32501 | -0.79651 | -1.2955 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.32501 | -0.41657 | -0.72327 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 1.062 | 0.022888 | 0.022888
6561.2188 | 0.076294 | 0.005341 | 0.004272 | 0.004272 | 0.001068 | 0.004272 | 0.003204 | -0.62714 | -0.31128 | -0.80566 | -1.3 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.001068 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | -0.32959 | -0.43488 | -0.74158 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 1.2131 | 0.018311 | 0.018311
6562.9844 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.63171 | -0.32501 | -0.81482 | -1.3046 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.004272 | 0.003204 | -0.32959 | -0.43945 | -0.75989 | 0.018311 | 0.022888 | 0.013733 | 0.018311 | 1.062 | 0.009155 | 0.022888
6564.6719 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.003204 | -0.001068 | -0.62256 | -0.32959 | -0.82398 | -1.3138 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.31586 | -0.44403 | -0.78278 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.3916 | 0.027466 | 0.022888
6566.4062 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | -0.001068 | 0.001068 | 0.001068 | -0.63171 | -0.32501 | -0.81024 | -1.2955 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.005341 | 0.002136 | 0.003204 | 0.004272 | -0.32501 | -0.4303 | -0.75531 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.2222 | 0.022888 | 0.013733
6568.1094 | 0 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0 | 0.002136 | -0.63171 | -0.33417 | -0.82398 | -1.3 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.32959 | -0.44403 | -0.77362 | 0.018311 | 0.009155 | 0.013733 | 0.022888 | 1.0895 | 0.022888 | 0.013733
6569.7969 | 0.076294 | 0.006409 | 0.003204 | 0.004272 | 0 | 0.001068 | 0.002136 | -0.61798 | -0.32959 | -0.8194 | -1.3092 | 0.009155 | 0.013733 | 0.022888 | 0.030518 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -0.32959 | -0.44861 | -0.7782 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 1.1032 | 0.027466 | 0.022888
6571.5469 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.62256 | -0.3067 | -0.80566 | -1.3 | 0.009155 | 0.018311 | 0.018311 | 0.015259 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.32959 | -0.45319 | -0.76904 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 1.0574 | 0.022888 | 0.022888
6573.2969 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.62256 | -0.32044 | -0.81482 | -1.3 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.32959 | -0.45776 | -0.79193 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | 0.90179 | 0.027466 | 0.018311
6574.9844 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.63171 | -0.31586 | -0.8194 | -1.3 | 0.013733 | 0.013733 | 0.022888 | 0.045776 | 0.002136 | 0.005341 | 0.002136 | 0.004272 | 0.002136 | -0.33417 | -0.45319 | -0.78735 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.0712 | 0.022888 | 0.018311
6576.6875 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | -0.60425 | -0.3067 | -0.8194 | -1.3046 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -0.32959 | -0.45776 | -0.79651 | 0.022888 | 0.013733 | 0.018311 | 0.009155 | 1.1856 | 0.027466 | 0.018311
6578.375 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.62256 | -0.31586 | -0.81482 | -1.3046 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.32959 | -0.45776 | -0.80109 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 1.2039 | 0.022888 | 0.022888
6580.0625 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.61798 | -0.32501 | -0.82855 | -1.3229 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.31128 | -0.46692 | -0.82855 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.3412 | 0.022888 | 0.022888
6581.7656 | 0.061035 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.001068 | 0.002136 | -0.63629 | -0.33417 | -0.82855 | -1.3092 | 0.018311 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.31586 | -0.4303 | -0.7782 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.3046 | 0.027466 | 0.013733
6583.5156 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | 0 | 0 | 0.003204 | -0.6546 | -0.35706 | -0.80566 | -1.3184 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.3067 | -0.44403 | -0.79193 | 0.018311 | 0.013733 | 0.009155 | 0.018311 | 1.6708 | 0.022888 | 0.018311
6585.2812 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0 | 0 | -0.65002 | -0.36163 | -0.84686 | -1.3092 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | -0.34332 | -0.46234 | -0.80109 | 0.009155 | 0.013733 | 0.013733 | 0.009155 | 2.2156 | 0.018311 | 0.018311
6586.9844 | 0.061035 | 0.004272 | 0.002136 | 0 | 0 | 0.003204 | 0.001068 | -0.6546 | -0.35248 | -0.82855 | -1.3046 | 0.004578 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.005341 | 0.002136 | -0.35248 | -0.46692 | -0.79651 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 1.767 | 0.018311 | 0.013733
6588.75 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | -0.001068 | 0.001068 | 0.001068 | -0.6546 | -0.36163 | -0.85602 | -1.3321 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.35248 | -0.49896 | -0.83313 | 0.018311 | 0.013733 | 0.013733 | 0.004578 | 2.0187 | 0.022888 | 0.018311
6590.5 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.64545 | -0.36163 | -0.82855 | -1.2955 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.3479 | -0.48523 | -0.82398 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 1.474 | 0.022888 | 0.022888
6592.25 | 0.030518 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.004272 | 0.001068 | -0.61798 | -0.35706 | -0.83771 | -1.3138 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0 | -0.34332 | -0.49896 | -0.86517 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | 1.1307 | 0.018311 | 0.022888
6593.9375 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.60883 | -0.32959 | -0.8606 | -1.3504 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.33417 | -0.48981 | -0.84686 | 0.004578 | 0.013733 | 0.013733 | 0.022888 | 1.561 | 0.013733 | 0.018311
6595.6875 | 0.076294 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.33417 | -0.85602 | -1.355 | 0.013733 | 0.013733 | 0.013733 | 0.015259 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.32044 | -0.48523 | -0.84228 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 2.7466 | 0.013733 | 0.022888
6597.3906 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.32501 | -0.82855 | -1.3275 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | -0.31586 | -0.46234 | -0.82398 | 0.013733 | 0.013733 | 0.022888 | 0.013733 | 1.5839 | 0.018311 | 0.018311
6599.1562 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | -0.001068 | 0.001068 | 0.002136 | -0.62714 | -0.34332 | -0.83313 | -1.3229 | 0.013733 | 0.013733 | 0.018311 | 0.076294 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.33417 | -0.46692 | -0.82855 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 1.0117 | 0.022888 | 0.022888
6600.8594 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | -0.63629 | -0.32044 | -0.84228 | -1.3458 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.32959 | -0.48065 | -0.83771 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.3275 | 0.022888 | 0.018311
6602.6094 | 0.061035 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.62714 | -0.32501 | -0.82855 | -1.3275 | 0.013733 | 0.022888 | 0.018311 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | -0.32959 | -0.48065 | -0.84228 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 1.3687 | 0.013733 | 0.018311
6604.375 | 0.076294 | 0.003204 | 0.002136 | 0 | -0.001068 | 0.003204 | 0.002136 | -0.63171 | -0.3479 | -0.85602 | -1.3458 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.31586 | -0.47607 | -0.85144 | 0.009155 | 0.018311 | 0.018311 | 0.022888 | 1.5472 | 0.013733 | 0.022888
6606.125 | 0.061035 | 0.006409 | 0.004272 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.63629 | -0.3479 | -0.80109 | -1.2726 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.32501 | -0.46234 | -0.83313 | 0.004578 | 0.022888 | 0.013733 | 0.009155 | 1.2405 | 0.022888 | 0.022888
6607.8281 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -0.60425 | -0.33875 | -0.83771 | -1.3275 | 0.013733 | 0.022888 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | -0.34332 | -0.46692 | -0.84228 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | 1.6022 | 0.018311 | 0.022888
6609.5938 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.63629 | -0.33417 | -0.83313 | -1.3367 | 0.004578 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.31586 | -0.46234 | -0.84686 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 1.3046 | 0.022888 | 0.018311
6611.2812 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0 | 0 | 0.003204 | -0.62256 | -0.31586 | -0.84686 | -1.3412 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.29755 | -0.44403 | -0.75073 | 0.022888 | 0.018311 | 0.018311 | 0.018311 | 0.60883 | 0.022888 | 0.018311
6612.9844 | 0.076294 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.71411 | -0.42572 | -0.9201 | -1.3779 | 0.009155 | 0.009155 | 0.009155 | 0.045776 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | -0.31586 | -0.50354 | -0.75531 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.60425 | 0.018311 | 0.018311
6614.7344 | 0.030518 | 0.004272 | 0 | 0.003204 | 0.001068 | 0 | 0.003204 | -0.70038 | -0.40283 | -0.90637 | -1.387 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.31586 | -0.47607 | -0.80566 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 0.89264 | 0.013733 | 0.018311
6616.4219 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0 | -0.69122 | -0.3891 | -0.9201 | -1.3962 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.31586 | -0.48523 | -0.82398 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | -0.032043 | 0.018311 | 0.018311
6618.1875 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.003204 | 0.003204 | -0.65002 | -0.36621 | -0.88806 | -1.3687 | 0.013733 | 0.018311 | 0.009155 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.32501 | -0.46692 | -0.8194 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 0.97504 | 0.018311 | 0.022888
6619.8906 | 0.030518 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.63629 | -0.36621 | -0.89722 | -1.387 | 0.013733 | 0.022888 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | -0.33875 | -0.49896 | -0.85144 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | 1.3229 | 0.009155 | 0.018311
6621.6406 | 0.076294 | 0.004272 | 0.003204 | 0.001068 | -0.001068 | 0.003204 | 0.001068 | -0.63171 | -0.36163 | -0.87891 | -1.3733 | 0.009155 | 0.013733 | 0.018311 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.3479 | -0.50812 | -0.85602 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.3046 | 0.018311 | 0.018311
6623.4062 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0 | -0.64087 | -0.37079 | -0.88348 | -1.3641 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | -0.35248 | -0.50812 | -0.85602 | 0.018311 | 0.013733 | 0.013733 | 0.009155 | 1.149 | 0.018311 | 0.013733
6625.1562 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.64087 | -0.3479 | -0.87433 | -1.3687 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | -0.34332 | -0.49896 | -0.84686 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 1.5015 | 0.022888 | 0.018311
6626.8594 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.63629 | -0.35706 | -0.87433 | -1.3641 | 0.018311 | 0.018311 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.35248 | -0.5127 | -0.86975 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.2634 | 0.013733 | 0.018311
6628.625 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.62714 | -0.35706 | -0.87433 | -1.3779 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.34332 | -0.52643 | -0.89264 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.4282 | 0.013733 | 0.022888
6630.3125 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.004272 | 0.003204 | -0.6134 | -0.33875 | -0.83771 | -1.355 | 0.009155 | 0.027466 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.34332 | -0.49896 | -0.8606 | 0.022888 | 0.013733 | 0.013733 | 0.018311 | 1.3962 | 0.022888 | 0.018311
6632 | 0.030518 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.59967 | -0.33417 | -0.83771 | -1.3504 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.34332 | -0.50812 | -0.86975 | 0.013733 | 0.027466 | 0.018311 | 0.018311 | 1.2268 | 0.013733 | 0.013733
6633.7656 | 0.030518 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | -0.60883 | -0.35706 | -0.85144 | -1.3596 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | 0.003204 | -0.34332 | -0.52643 | -0.90637 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 1.712 | 0.013733 | 0.022888
6635.4688 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0 | -0.60425 | -0.32959 | -0.82398 | -1.3458 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.32044 | -0.5127 | -0.90179 | 0.009155 | 0.013733 | 0.022888 | 0.013733 | 1.886 | 0.013733 | 0.013733
6637.1562 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.003204 | 0.003204 | -0.63629 | -0.36621 | -0.81024 | -1.3138 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.34332 | -0.50812 | -0.91095 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | 1.7029 | 0.022888 | 0.022888
6638.8594 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.84686 | -0.65002 | -2.4948 | -3.1311 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.35706 | -0.52185 | -0.89264 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.7899 | 0.022888 | 0.022888
6640.6094 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.54474 | -0.27008 | -0.21515 | -0.86975 | 0.013733 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.38452 | -0.55389 | -0.92468 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.7029 | 0.022888 | 0.022888
6642.2969 | 0.076294 | 0.004272 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.80109 | -0.16022 | -0.11902 | -0.45776 | 0.013733 | 0.022888 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.32501 | -0.50354 | -0.75531 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 1.6846 | 0.022888 | 0.018311
6644 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.48065 | -0.32501 | 0.63171 | 0.15564 | 0.013733 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.091553 | -0.39368 | -0.42114 | 0.018311 | 0.009155 | 0.018311 | 0.022888 | 1.8356 | 0.018311 | 0.018311
6645.75 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | -0.53558 | -0.42572 | 0.045776 | -0.13275 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.091553 | -0.31586 | -0.46234 | 0.018311 | 0.004578 | 0.022888 | 0.022888 | 1.7166 | 0.013733 | 0.018311
6647.5156 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.40741 | -0.20599 | 0.082397 | 0.018311 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.004272 | -0.073242 | -0.26093 | -0.41199 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.4603 | 0.013733 | 0.018311
6649.2031 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | -0.50354 | -0.31586 | -0.10071 | -0.3891 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | -0.23346 | -0.32044 | -0.61798 | 0.009155 | 0.013733 | 0.013733 | 0.013733 | 0.84228 | 0.018311 | 0.022888
6650.8906 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.57678 | -0.35248 | -0.13275 | -0.36621 | 0.022888 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.24261 | -0.36163 | -0.70038 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 0.67749 | 0.013733 | 0.018311
6652.6406 | 0.061035 | 0.004272 | 0.003204 | 0 | 0 | 0.002136 | 0.002136 | -0.56305 | -0.30212 | -0.4303 | -0.59509 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.23804 | -0.3891 | -0.74158 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 0.88806 | 0.013733 | 0.027466
6654.3906 | 0.061035 | 0.004272 | 0.004272 | 0.001068 | -0.001068 | 0.002136 | 0.004272 | -0.58136 | -0.32501 | -0.70038 | -0.92926 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.25635 | -0.45319 | -0.75989 | 0.022888 | 0.018311 | 0.022888 | 0.009155 | 0.85602 | 0.013733 | 0.018311
6656.0781 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.56305 | -0.3067 | -0.737 | -0.97504 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.25177 | -0.37994 | -0.81482 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | 0.99792 | 0.018311 | 0.027466
6657.7812 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.45319 | -0.23346 | -0.52185 | -0.8606 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -0.21057 | -0.19226 | -0.75073 | 0.013733 | 0.022888 | 0.013733 | 0.018311 | 1.4969 | 0.018311 | 0.018311
6659.5469 | 0.030518 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.3891 | -0.25177 | -0.56763 | -1.062 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | -0.28839 | -0.23804 | -0.76446 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.8082 | 0.022888 | 0.018311
6661.3125 | 0.061035 | 0.006409 | 0.002136 | 0 | -0.002136 | 0.001068 | 0.001068 | -0.70953 | -0.43488 | -0.9201 | -1.2634 | 0.013733 | 0.018311 | 0.018311 | 0.015259 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | -0.29297 | -0.43945 | -0.75531 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | 2.1561 | 0.022888 | 0.022888
6663.0156 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | -0.003204 | 0.002136 | 0.001068 | -0.66376 | -0.37537 | -0.90179 | -1.3138 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | -0.2655 | -0.42114 | -0.7782 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 2.1149 | 0.018311 | 0.013733
6664.7656 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.64087 | -0.36163 | -0.90179 | -1.3504 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.26093 | -0.42114 | -0.80109 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.8814 | 0.022888 | 0.027466
6666.5156 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.65918 | -0.37079 | -1.0712 | -1.5656 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -0.25177 | -0.39825 | -0.7782 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 1.6251 | 0.018311 | 0.022888
6668.2188 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | 0 | 0.001068 | 0 | -0.64087 | -0.38452 | -1.0803 | -1.6251 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.005341 | 0.004272 | -0.27466 | -0.41657 | -0.80566 | 0.013733 | 0.004578 | 0.027466 | 0.018311 | 1.6983 | 0.022888 | 0.022888
6669.9062 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.003204 | 0.002136 | -0.85144 | -0.45776 | -2.2842 | -3.035 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.001068 | 0.004272 | 0.001068 | -0.26093 | -0.40283 | -0.78735 | 0.009155 | 0.013733 | 0.018311 | 0.009155 | 1.6754 | 0.013733 | 0.013733
6671.6562 | 0.061035 | 0.003204 | 0.004272 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.68207 | -0.36163 | -1.1124 | -1.8631 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.27466 | -0.39368 | -0.78278 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.6022 | 0.022888 | 0.018311
6673.375 | 0.030518 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.53558 | -0.29755 | -0.34332 | -1.03 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.25635 | -0.39825 | -0.78735 | 0.009155 | 0.022888 | 0.013733 | 0.009155 | 1.4374 | 0.013733 | 0.018311
6675.1406 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.66376 | -0.41657 | -0.69122 | -1.1902 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.25635 | -0.39825 | -0.77362 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.4511 | 0.018311 | 0.018311
6676.8438 | 0.076294 | 0.007477 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -0.70953 | -0.41657 | -1.4328 | -2.0233 | 0.009155 | 0.013733 | 0.009155 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.27008 | -0.39368 | -0.78278 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | 1.5976 | 0.018311 | 0.013733
6678.6094 | 0.045776 | 0.004272 | 0.001068 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.68207 | -0.25177 | -0.67291 | -0.70953 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.28839 | -0.3891 | -0.75531 | 0.009155 | 0.013733 | 0.027466 | 0.013733 | 1.3092 | 0.009155 | 0.013733
6680.375 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.37537 | -0.22888 | 0.62256 | 0.38452 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.27924 | -0.39368 | -0.76446 | 0.013733 | 0.004578 | 0.013733 | 0.009155 | 1.2497 | 0.013733 | 0.013733
6682.1406 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.49896 | -0.29297 | 0.11444 | 0.11902 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -0.27008 | -0.39368 | -0.75531 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 1.3458 | 0.018311 | 0.018311
6683.8281 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.005341 | 0.003204 | -0.53101 | -0.3067 | -0.20599 | -0.19684 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | -0.25635 | -0.39368 | -0.76904 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 1.4328 | 0.013733 | 0.018311
6685.5781 | 0.061035 | 0.006409 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.58594 | -0.30212 | -0.48065 | -0.52643 | 0.013733 | 0.022888 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.28381 | -0.3891 | -0.75073 | 0.022888 | 0.013733 | 0.022888 | 0.018311 | 1.506 | 0.009155 | 0.022888
6687.3281 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.59967 | -0.31586 | -0.61798 | -0.76446 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | -0.28381 | -0.3891 | -0.74158 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 1.387 | 0.018311 | 0.022888
6689.0312 | 0.061035 | 0.004272 | 0.001068 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.60883 | -0.33875 | -0.70496 | -0.92926 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | -0.28839 | -0.40741 | -0.76446 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 1.5381 | 0.018311 | 0.018311
6690.7812 | 0.030518 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | -0.6134 | -0.32501 | -0.72784 | -1.03 | 0.004578 | 0.009155 | 0.018311 | 0.076294 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.27924 | -0.39368 | -0.75073 | 0.013733 | 0.009155 | 0.013733 | 0.004578 | 1.442 | 0.018311 | 0.013733
6692.5312 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.63629 | -0.35248 | -0.82398 | -1.1581 | 0.013733 | 0.009155 | 0.013733 | 0.076294 | 0.002136 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | -0.29297 | -0.40283 | -0.75989 | 0.022888 | 0.018311 | 0.013733 | 0.009155 | 1.3046 | 0.013733 | 0.022888
6694.2344 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.6958 | -0.40741 | -0.9201 | -1.1307 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.28381 | -0.40283 | -0.75989 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | 1.4557 | 0.013733 | 0.013733
6695.9844 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0 | 0.004272 | -0.70038 | -0.37994 | -0.8606 | -1.1765 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.3067 | -0.42114 | -0.75073 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.5793 | 0.018311 | 0.009155
6697.6719 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | -0.001068 | 0.002136 | 0.001068 | -0.71411 | -0.37994 | -0.86975 | -1.2405 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | -0.29755 | -0.42114 | -0.75531 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.4511 | 0.022888 | 0.018311
6699.3906 | 0.061035 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.70953 | -0.39368 | -0.92926 | -1.3733 | 0.018311 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.32959 | -0.44403 | -0.76904 | 0.018311 | 0.009155 | 0.022888 | 0.013733 | 1.6296 | 0.022888 | 0.018311
6701.0781 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | -1.3275 | -0.66834 | -1.7578 | -1.9455 | 0.004578 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | -0.33417 | -0.44403 | -0.76446 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.3184 | 0.022888 | 0.018311
6702.7656 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.43488 | -0.42572 | -1.0025 | -1.7441 | 0.022888 | 0.013733 | 0.022888 | 0.061035 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.35706 | -0.48523 | -0.79651 | 0.013733 | 0.018311 | 0.018311 | 0.009155 | 1.3733 | 0.022888 | 0.018311
6704.5312 | 0.061035 | 0.005341 | 0.004272 | 0 | 0.001068 | 0.002136 | 0.002136 | -1.8585 | -0.69122 | -1.8631 | -3.6301 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | -0.46234 | -0.53558 | -0.78735 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | 1.4374 | 0.022888 | 0.018311
6706.2188 | 0.045776 | 0.005341 | 0.001068 | 0.004272 | 0 | 0.004272 | 0.003204 | -0.38452 | -0.23346 | -1.0117 | -3.067 | 0.009155 | 0.013733 | 0.022888 | 0.045776 | 0.001068 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -0.5722 | -0.6546 | -0.87891 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.2909 | 0.022888 | 0.018311
6707.9062 | 0.030518 | 0.007477 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.001068 | 3.9368 | 1.9867 | 3.7216 | -0.9613 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | -0.54474 | -0.737 | -0.98419 | 0.018311 | 0.018311 | 0.022888 | 0.013733 | 1.4374 | 0.022888 | 0.018311
6709.6719 | 0.061035 | 0.007477 | 0.004272 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | 1.5152 | 0.16479 | 2.861 | 3.511 | 0.022888 | 0.004578 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.49896 | -0.74158 | -1.0345 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.5564 | 0.018311 | 0.013733
6711.3594 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | 0.29755 | 0.064087 | 1.7441 | 2.5497 | 0.013733 | 0.013733 | 0.018311 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.4303 | -0.72784 | -1.0803 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 1.5472 | 0.018311 | 0.022888
6713.1094 | 0.061035 | 0.006409 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.003204 | -3.6163 | -1.9043 | -1.9592 | -0.14191 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.38452 | -0.71869 | -1.0895 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 1.5244 | 0.018311 | 0.022888
6714.8125 | 0.076294 | 0.006409 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | 0.20142 | 0.56763 | 2.1149 | 1.3596 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | -0.35706 | -0.67749 | -1.0941 | 0.022888 | 0.018311 | 0.013733 | 0.022888 | 1.5701 | 0.018311 | 0.018311
6716.5625 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.46692 | -3.0212 | -4.5822 | -1.9821 | 0.018311 | 0.018311 | 0.018311 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.21057 | -0.58136 | -1.0345 | 0.004578 | 0.018311 | 0.013733 | 0.013733 | 1.3 | 0.018311 | 0.022888
6718.3281 | 0.045776 | 0.004272 | 0.004272 | 0.003204 | -0.001068 | 0.001068 | 0.002136 | -2.298 | 0.84228 | -1.9501 | -5.159 | 0.013733 | 0.009155 | 0.013733 | 0.015259 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.62714 | -0.6134 | -0.85602 | 0.022888 | 0.018311 | 0.018311 | 0.013733 | 2.4536 | 0.018311 | 0.022888
6720.0156 | 0.045776 | 0.004272 | 0.001068 | 0.004272 | -0.001068 | 0.001068 | 0.003204 | -0.97961 | -0.95215 | -0.18768 | -2.7832 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | -1.0254 | -1.0208 | -1.1353 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.90179 | 0.018311 | 0.013733
6721.7812 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.1831 | -1.268 | 0.5127 | -1.8539 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -1.1215 | -1.3 | -1.3916 | 0.013733 | 0.013733 | 0.009155 | 0.009155 | 0.77362 | 0.018311 | 0.018311
6723.5469 | 0.045776 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.20142 | -1.0941 | 1.0757 | -1.0803 | 0.013733 | 0.009155 | 0.022888 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -1.0849 | -1.4786 | -1.6067 | 0.013733 | 0.022888 | 0.009155 | 0.018311 | 1.1169 | 0.013733 | 0.022888
6725.3125 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.005341 | 0.36163 | -0.87891 | 1.506 | -0.30212 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | -1.0117 | -1.5289 | -1.7441 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.97961 | 0.009155 | 0.027466
6727 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | -0.001068 | 0.003204 | 0.002136 | 0.42114 | -0.69122 | 1.7899 | 0.44861 | 0.022888 | 0.013733 | 0.018311 | 0.076294 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.89722 | -1.5289 | -1.8219 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.99335 | 0.013733 | 0.013733
6728.7656 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.004272 | 0.64087 | -0.37079 | 2.6917 | 1.9455 | 0.022888 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0 | 0.002136 | -0.80566 | -1.4969 | -1.8677 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.2314 | 0.018311 | 0.022888
6730.4688 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.001068 | 0.23346 | -0.55847 | 1.3092 | 1.1353 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -0.64545 | -1.3596 | -1.8448 | 0.013733 | 0.022888 | 0.013733 | 0.018311 | 1.1536 | 0.018311 | 0.018311
6732.2188 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.004272 | 0.002136 | 0.32044 | -0.4303 | 1.2817 | 1.355 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | -2.3346 | -0.09613 | -0.87891 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.3412 | 0.018311 | 0.018311
6733.9688 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.003204 | 0.001068 | 0.13275 | -0.60883 | 0.90637 | 1.5335 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -3.2364 | -0.4303 | -0.6134 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.4191 | 0.013733 | 0.018311
6735.6562 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | -0.001068 | 0.001068 | 0.002136 | -0.3479 | -0.7782 | 0.87891 | 1.6113 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -2.9846 | -0.94757 | -0.66834 | 0.018311 | 0.004578 | 0.018311 | 0.009155 | 1.5289 | 0.018311 | 0.018311
6737.4219 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.45319 | -0.70038 | 1.1673 | 1.8311 | 0.013733 | 0.022888 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -2.623 | -1.2405 | -0.68207 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 1.4694 | 0.022888 | 0.022888
6739.125 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.52185 | -0.737 | 1.2497 | 1.9867 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -2.7237 | -1.5747 | -1.1856 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | 1.4786 | 0.022888 | 0.018311
6740.8281 | 0.076294 | 0.006409 | 0.001068 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.62256 | -0.75989 | 0.60425 | 1.8448 | 0.018311 | 0.013733 | 0.009155 | 0.045776 | 0.001068 | 0.003204 | 0.005341 | 0.003204 | 0.001068 | -2.3209 | -1.6891 | -1.2039 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.4557 | 0.022888 | 0.018311
6742.5938 | 0.045776 | 0.005341 | 0.004272 | 0.001068 | -0.001068 | 0.002136 | 0.003204 | -0.53558 | -0.68665 | 0.24719 | 1.4923 | 0.022888 | 0.018311 | 0.013733 | 0.076294 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -1.9089 | -1.7899 | -1.3321 | 0.022888 | 0.009155 | 0.018311 | 0.018311 | 1.5427 | 0.013733 | 0.018311
6744.2969 | 0.015259 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.29755 | -0.48065 | 0.2655 | 1.2634 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.004272 | -2.7237 | -2.2568 | -1.7075 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | 1.6846 | 0.022888 | 0.022888
6745.9844 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.44861 | -0.48065 | 0.24719 | 1.1627 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | -3.3829 | -2.9388 | -2.2842 | 0.009155 | 0.022888 | 0.013733 | 0.018311 | 1.4557 | 0.018311 | 0.009155
6747.7344 | 0.061035 | 0.006409 | 0.005341 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | -0.24719 | -0.20142 | 0.62714 | 1.387 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.005341 | 0.003204 | 0.002136 | 0.003204 | -0.27008 | -1.9455 | -2.0508 | 0.018311 | 0.013733 | 0.004578 | 0.013733 | 1.3321 | 0.022888 | 0.022888
6749.5156 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.55389 | -0.35706 | 0.5127 | 1.3229 | 0.018311 | 0.018311 | 0.009155 | 0.030518 | 0.001068 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.82398 | -0.61798 | -0.89264 | 0.036621 | 0.013733 | 0.013733 | 0.013733 | 1.5976 | 0.018311 | 0.022888
6751.2031 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.002136 | 0 | -0.11902 | 0.1236 | 0.050354 | 1.0757 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.41199 | -0.4303 | -1.3779 | 0.022888 | 0.009155 | 0.013733 | 0.013733 | 1.4603 | 0.022888 | 0.022888
6752.9688 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | -0.002136 | 0.002136 | 0 | 0.082397 | 0.3891 | 0.52643 | 1.1032 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.054932 | -0.41199 | -1.3824 | 0.018311 | 0.018311 | 0.022888 | 0.004578 | 1.2222 | 0.022888 | 0.018311
6754.7344 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.3479 | 0.51727 | 0.64087 | 1.1215 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -0.19684 | -0.47607 | -1.2726 | 0.018311 | 0.018311 | 0.027466 | 0.018311 | 1.1169 | 0.027466 | 0.022888
6756.5 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.39368 | 0.4303 | 0.86975 | 1.2634 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.36621 | -0.57678 | -1.2039 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 1.3046 | 0.022888 | 0.027466
6758.1875 | 0.076294 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.002136 | 0.31586 | 0.32044 | 1.0391 | 1.4557 | 0.009155 | 0.009155 | 0.018311 | 0.015259 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.45319 | -0.6546 | -1.1124 | 0.022888 | 0.013733 | 0.013733 | 0.018311 | 1.1673 | 0.013733 | 0.018311
6759.8906 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.14648 | 0.15564 | 1.0757 | 1.5701 | 0.027466 | 0.018311 | 0.022888 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0 | 0.002136 | -0.48523 | -0.72327 | -1.0941 | 0.013733 | 0.018311 | 0.022888 | 0.013733 | 1.2863 | 0.018311 | 0.018311
6761.6406 | 0.076294 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.004578 | 0.036621 | 1.062 | 1.6251 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.4715 | -0.737 | -1.0712 | 0.009155 | 0.009155 | 0.013733 | 0.013733 | 1.4328 | 0.018311 | 0.018311
6763.3906 | 0.061035 | 0.003204 | 0.004272 | 0.001068 | 0 | 0.003204 | 0.002136 | 0.013733 | 0.086975 | 1.3687 | 1.9135 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.41199 | -0.74158 | -1.0208 | 0.013733 | 0.009155 | 0.022888 | 0.004578 | 1.4145 | 0.018311 | 0.018311
6765.0938 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.27924 | -0.20142 | 1.062 | 1.8311 | 0.009155 | 0.009155 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.79193 | -0.91553 | -1.3321 | 0.004578 | 0.018311 | 0.013733 | 0.009155 | 1.1719 | 0.018311 | 0.018311
6766.7969 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.42572 | -0.21515 | 0.85602 | 1.6891 | 0.009155 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.89722 | -0.95215 | -1.8311 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.85144 | 0.018311 | 0.018311
6768.5781 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.63171 | -0.47607 | 0.49896 | 1.4786 | 0.022888 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.59509 | -0.93842 | -1.5244 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.5722 | 0.022888 | 0.009155
6770.3438 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.001068 | -0.59967 | -0.40741 | 0.2243 | 1.1169 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.48065 | -0.91553 | -1.3275 | 0.022888 | 0.018311 | 0.009155 | 0.013733 | 1.0391 | 0.013733 | 0.018311
6772.1094 | 0.045776 | 0.005341 | 0.001068 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.56305 | -0.37537 | 0.69122 | 1.5472 | 0.009155 | 0.009155 | 0.022888 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.12817 | -0.65918 | -1.1719 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.81482 | 0.013733 | 0.022888
6773.7969 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.66376 | -0.44861 | -0.004578 | 0.79193 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.001068 | 0.004272 | 0.002136 | 0.001068 | 0.004272 | -0.15106 | -0.54932 | -1.0208 | 0.013733 | 0.013733 | 0.018311 | 0.027466 | 0.88348 | 0.022888 | 0.009155
6775.5469 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.65002 | -0.44861 | -0.022888 | 0.67749 | 0.013733 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.15106 | -0.48523 | -0.9201 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.0849 | 0.022888 | 0.013733
6777.3125 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.65918 | -0.45319 | -0.082397 | 0.55847 | 0.018311 | 0.022888 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.14648 | -0.44403 | -0.84686 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | 1.2955 | 0.022888 | 0.018311
6779.0156 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.65002 | -0.45319 | -0.13275 | 0.48065 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.14648 | -0.37994 | -0.77362 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | 1.2589 | 0.022888 | 0.018311
6780.7656 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.004272 | -0.63629 | -0.41199 | -0.1831 | 0.40741 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | -0.14648 | -0.35706 | -0.71411 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | 1.3275 | 0.013733 | 0.022888
6782.5156 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.001068 | -0.61798 | -0.41199 | -0.24719 | 0.27924 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.13275 | -0.32501 | -0.69122 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.3275 | 0.027466 | 0.013733
6784.2188 | 0.061035 | 0.006409 | 0.002136 | 0.001068 | 0 | 0.002136 | 0 | -0.63171 | -0.42114 | -0.29297 | 0.19226 | 0.018311 | 0.009155 | 0.018311 | 0.061035 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | -0.13733 | -0.29755 | -0.65002 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.268 | 0.018311 | 0.009155
6785.9531 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | -0.001068 | 0.003204 | 0.001068 | -0.62714 | -0.42572 | -0.35706 | 0.082397 | 0.018311 | 0.022888 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.005341 | 0.003204 | -0.13275 | -0.29297 | -0.64087 | 0.018311 | 0.013733 | 0.009155 | 0.013733 | 1.387 | 0.018311 | 0.018311
6787.7031 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.65002 | -0.39368 | -0.54932 | -0.16937 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.14648 | -0.27008 | -0.60883 | 0.018311 | 0.013733 | 0.013733 | 0.022888 | 1.3504 | 0.018311 | 0.022888
6789.4688 | 0.030518 | 0.004272 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.73242 | -0.54932 | -0.41199 | 0.14648 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | 0.001068 | -0.19226 | -0.28839 | -0.60425 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.3229 | 0.018311 | 0.022888
6791.2188 | 0.045776 | 0.007477 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.79651 | -0.55389 | -0.82855 | -0.32044 | 0.004578 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.31586 | -0.30212 | -0.55847 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 1.355 | 0.018311 | 0.027466
6792.9062 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.76904 | -0.46692 | -0.71411 | -0.4715 | 0.018311 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -11.6135 | 11.1328 | 6.3217 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.4145 | 0.018311 | 0.022888
6794.6094 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.5722 | -0.26093 | -0.43488 | -0.46234 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.002136 | 0.003204 | 0.005341 | 0.001068 | 0.002136 | -11.6272 | 8.8943 | 8.6746 | 0.027466 | 0.013733 | 0.013733 | 0.013733 | 1.4053 | 0.013733 | 0.018311
6796.3594 | 0.030518 | 0.006409 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.001068 | -0.52185 | -0.24261 | 0.073242 | 0.14191 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -11.5677 | 5.6442 | 7.814 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.2955 | 0.013733 | 0.013733
6798.125 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.83771 | -0.40741 | 0.17853 | 0.97046 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -11.3388 | 3.3508 | 6.9626 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 1.4008 | 0.022888 | 0.022888
6799.8125 | 0.030518 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.41199 | -0.24719 | -0.97961 | -0.97046 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -10.7483 | 1.3458 | 5.9555 | 0.009155 | 0.013733 | 0.018311 | 0.009155 | 1.0895 | 0.022888 | 0.013733
6801.5781 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.6958 | -0.71411 | -1.0529 | -0.98877 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | -9.8557 | -1.7624 | 4.2435 | 0.013733 | 0.013733 | 0.013733 | 0.009155 | 1.2955 | 0.022888 | 0.013733
6803.3438 | 0.045776 | 0.006409 | 0 | 0.002136 | -0.002136 | 0.001068 | 0.002136 | -0.97046 | -0.42572 | -0.82855 | -0.94757 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | -7.8735 | -1.8539 | 3.8223 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 1.2131 | 0.018311 | 0.022888
6805.1406 | 0.061035 | 0.006409 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.56305 | -0.14648 | -0.65918 | -0.89722 | 0.013733 | 0.009155 | 0.022888 | 0.061035 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -8.0338 | -4.1931 | 2.3804 | 0.009155 | 0.018311 | 0.009155 | 0.009155 | 1.1444 | 0.027466 | 0.018311
6806.8438 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0 | 0.001068 | 0.001068 | -0.3479 | -0.09613 | -0.47607 | -0.80109 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -6.5231 | -5.0537 | 1.1627 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | 1.1581 | 0.022888 | 0.022888
6808.5469 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.15106 | -0.045776 | -0.43945 | -0.70038 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -5.6076 | -5.2094 | -0.004578 | 0.022888 | 0.013733 | 0.018311 | 0.013733 | 1.387 | 0.022888 | 0.018311
6810.3125 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.12817 | -0.13275 | -0.37079 | -0.62714 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -4.7653 | -5.0766 | -0.93384 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 1.1215 | 0.022888 | 0.018311
6812 | 0.061035 | 0.005341 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.3479 | -0.1831 | -0.32959 | -0.5127 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -4.985 | -5.2185 | -1.7441 | 0.013733 | 0.018311 | 0.009155 | 0.022888 | 1.1169 | 0.018311 | 0.018311
6813.75 | 0.061035 | 0.007477 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.41199 | -0.2655 | -0.3891 | -0.56763 | 0.013733 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | -4.5685 | -5.6351 | -2.7649 | 0.022888 | 0.013733 | 0.013733 | 0.013733 | 1.3046 | 0.022888 | 0.022888
6815.5312 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.001068 | -0.3891 | -0.1831 | -0.24261 | -0.48065 | 0.018311 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -3.8773 | -5.2048 | -3.3371 | 0.018311 | 0.009155 | 0.004578 | 0.018311 | 1.3184 | 0.022888 | 0.013733
6817.2969 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.003204 | 0.001068 | -0.41657 | -0.34332 | -0.045776 | -0.32959 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -4.8019 | -4.3121 | -3.2227 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.2268 | 0.022888 | 0.018311
6819 | 0.030518 | 0.004272 | 0.002136 | 0.004272 | -0.001068 | 0.003204 | 0.002136 | -0.50354 | -0.20599 | -0.15564 | -0.32044 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -2.9343 | -3.9688 | -3.2181 | 0.009155 | 0.013733 | 0.022888 | 0.009155 | 1.2589 | 0.009155 | 0.022888
6820.75 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.47607 | -0.13733 | 0.35248 | -0.086975 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -3.2959 | -4.1656 | -3.479 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.1444 | 0.013733 | 0.022888
6822.5156 | 0.015259 | 0.004272 | 0.003204 | 0 | 0.001068 | 0.003204 | 0.002136 | -0.30212 | -0.086975 | 0.14648 | -0.059509 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -3.1265 | -4.2847 | -3.7125 | 0.009155 | 0.013733 | 0.022888 | 0.013733 | 1.1124 | 0.013733 | 0.022888
6824.2969 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.003204 | -0.001068 | -0.19684 | 0.009155 | 0.14191 | 0.009155 | 0.009155 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -2.8519 | -4.2252 | -3.8589 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.1169 | 0.013733 | 0.022888
6826 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.30212 | -0.1236 | 0.064087 | 0.027466 | 0.022888 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -2.5864 | -4.1245 | -3.9505 | 0.018311 | 0.018311 | 0.009155 | 0.013733 | 1.2451 | 0.013733 | 0.018311
6827.75 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.41657 | -0.31586 | 0.07782 | 0.18768 | 0.013733 | 0.022888 | 0.022888 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -2.536 | -4.1702 | -4.0466 | 0.013733 | 0.009155 | 0.018311 | 0.022888 | 1.3275 | 0.018311 | 0.018311
6829.4688 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | -0.78278 | -0.52643 | -0.26093 | -0.24261 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -2.2614 | -3.8177 | -4.0924 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.2039 | 0.018311 | 0.018311
6831.2344 | 0.030518 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.001068 | 0.002136 | -0.49439 | -0.22888 | -0.073242 | -0.15564 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -1.9043 | -3.6575 | -4.0054 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | 1.2817 | 0.013733 | 0.018311
6833.8438 | 0.091553 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.31586 | -0.34332 | -0.29755 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -1.6159 | -3.3463 | -3.7628 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.3046 | 0.022888 | 0.022888
6837.0938 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | -0.4715 | -0.30212 | -0.40283 | -0.48523 | 0.018311 | 0.009155 | 0.013733 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.041199 | -2.5177 | -3.3691 | 0.022888 | 0.022888 | 0.004578 | 0.018311 | 1.2909 | 0.022888 | 0.027466
6840.7812 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.43488 | -0.24719 | -0.16937 | -0.35248 | 0.022888 | 0.009155 | 0.013733 | 0.061035 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.56305 | -2.449 | -3.2364 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.3458 | 0.018311 | 0.018311
6846.3125 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.45319 | -0.2655 | -0.29297 | -0.42114 | 0.013733 | 0.022888 | 0.009155 | 0.045776 | 0.004272 | 0.003204 | 0.005341 | 0.001068 | 0.004272 | -0.79193 | -2.3117 | -3.2135 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 0.60425 | 0.018311 | 0.013733
6848 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.48981 | -0.25635 | -0.33875 | -0.41657 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -0.89264 | -2.4536 | -3.3508 | 0.022888 | 0.018311 | 0.013733 | 0.018311 | 0.71411 | 0.013733 | 0.013733
6849.7656 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | 0 | 0.003204 | -0.53101 | -0.27924 | -0.29297 | -0.3891 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.91095 | -2.4765 | -3.4149 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 0.87891 | 0.022888 | 0.013733
6851.5312 | 0.076294 | 0.005341 | 0.004272 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.54474 | -0.27924 | -0.3479 | -0.4303 | 0.013733 | 0.013733 | 0.022888 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.89264 | -2.449 | -3.4149 | 0.009155 | 0.013733 | 0.009155 | 0.018311 | 1.1948 | 0.022888 | 0.022888
6853.2969 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.004272 | 0.001068 | -0.56763 | -0.3067 | -0.34332 | -0.4303 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.005341 | 0.002136 | 0.003204 | 0.003204 | -0.8606 | -2.3575 | -3.3371 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 1.1536 | 0.018311 | 0.018311
6854.9844 | 0.045776 | 0.006409 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.58594 | -0.30212 | -0.37079 | -0.45776 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.82398 | -2.2705 | -3.2776 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 1.2314 | 0.022888 | 0.013733
6856.75 | 0.091553 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.33875 | -0.41657 | -0.51727 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.7782 | -2.1927 | -3.2272 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.4145 | 0.022888 | 0.022888
6858.4531 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.60883 | -0.34332 | -0.4303 | -0.52643 | 0.013733 | 0.018311 | 0.018311 | 0.030518 | 0 | 0.003204 | 0.005341 | 0.003204 | 0.002136 | -0.72784 | -2.092 | -3.1448 | 0.004578 | 0.013733 | 0.022888 | 0.009155 | 1.4053 | 0.018311 | 0.022888
6860.2188 | 0.030518 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0 | -0.62714 | -0.35248 | -0.45319 | -0.55847 | 0.018311 | 0.009155 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.69122 | -1.9867 | -3.0396 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.3824 | 0.013733 | 0.018311
6861.9844 | 0.076294 | 0.006409 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.60883 | -0.36621 | -0.50812 | -0.62256 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.65002 | -1.886 | -2.9572 | 0.013733 | 0.018311 | 0.022888 | 0.013733 | 1.4053 | 0.018311 | 0.027466
6863.7344 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.001068 | -0.63629 | -0.37994 | -0.3479 | -0.50812 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | -0.6134 | -1.7532 | -2.7374 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 2.2156 | 0.009155 | 0.018311
6865.5 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.63629 | -0.36163 | -0.26093 | -0.40283 | 0.018311 | 0.022888 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | -0.32959 | -1.5518 | -2.5085 | 0.013733 | 0.018311 | 0.022888 | 0.013733 | 2.3209 | 0.022888 | 0.009155
6867.2656 | 0.076294 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.70038 | -0.3891 | -0.28381 | -0.2655 | 0.018311 | 0.022888 | 0.022888 | 0.061035 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.39368 | -1.4832 | -2.4811 | 0.013733 | 0.018311 | 0.022888 | 0.018311 | 1.9775 | 0.018311 | 0.022888
6868.9688 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.002136 | -0.69122 | -0.40741 | -0.62256 | -0.67291 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | -0.46692 | -1.4648 | -2.449 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 1.6663 | 0.018311 | 0.018311
6870.7188 | 0.076294 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.003204 | 0.002136 | -0.66834 | -0.37079 | -0.72327 | -0.81482 | 0.013733 | 0.018311 | 0.027466 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -2.4536 | -1.0345 | -2.211 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.5289 | 0.022888 | 0.022888
6872.4844 | 0.076294 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.59052 | -0.32501 | -0.63629 | -0.84228 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -3.8132 | -0.68207 | -1.7487 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 1.4236 | 0.022888 | 0.022888
6874.25 | 0.030518 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.003204 | 0.002136 | -0.48065 | -0.30212 | -0.53101 | -0.81024 | 0.018311 | 0.022888 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -2.5314 | -1.1902 | -1.7441 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.3046 | 0.009155 | 0.013733
6876 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.001068 | -0.30212 | -0.1831 | -0.47607 | -1.5793 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -1.9226 | -1.3229 | -1.7899 | 0.009155 | 0.022888 | 0.018311 | 0.013733 | 1.3687 | 0.022888 | 0.018311
6877.7031 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.70953 | -0.37537 | -0.60425 | -0.65918 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -1.6342 | -1.4099 | -1.8448 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 1.5747 | 0.027466 | 0.018311
6879.4531 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.50354 | -0.33875 | -0.73242 | -0.76446 | 0.009155 | 0.018311 | 0.013733 | 0.076294 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | 0.004272 | -1.2405 | -1.387 | -1.8219 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.2955 | 0.013733 | 0.022888
6881.1562 | 0.045776 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.72327 | -0.42572 | -0.86975 | -0.86975 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.004272 | 0.002136 | -11.7233 | 12.1719 | 6.0883 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | 1.4236 | 0.022888 | 0.013733
6882.9219 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | -0.001068 | 0.004272 | 0.003204 | -0.76446 | -0.4303 | -0.62714 | -0.87433 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.005341 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -11.7371 | 13.3804 | 11.2885 | 0.027466 | 0.013733 | 0.009155 | 0.022888 | 1.5106 | 0.018311 | 0.022888
6884.6719 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.60883 | -0.35706 | -0.50812 | -0.84686 | 0.013733 | 0.009155 | 0.018311 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | -11.7142 | 8.931 | 10.2631 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.4648 | 0.022888 | 0.018311
6886.4219 | 0.045776 | 0.005341 | 0.004272 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.5722 | -0.32044 | -0.53101 | -0.8194 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -11.6867 | 5.3513 | 8.9493 | 0.022888 | 0.018311 | 0.013733 | 0.013733 | 1.4145 | 0.018311 | 0.022888
6888.1094 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.52643 | -0.28381 | -0.52185 | -0.81024 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | -11.6409 | 2.7191 | 7.5302 | 0.022888 | 0.018311 | 0.009155 | 0.009155 | 1.2726 | 0.013733 | 0.022888
6889.7969 | 0.030518 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.004272 | 0.002136 | -0.48523 | -0.29297 | -0.5722 | -0.85144 | 0.022888 | 0.009155 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -11.5402 | 0.054932 | 6.1707 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.5701 | 0.013733 | 0.022888
6891.5625 | 0.061035 | 0.005341 | 0.002136 | 0 | 0.001068 | 0.003204 | 0.002136 | -0.51727 | -0.28839 | -0.54016 | -0.83771 | 0.022888 | 0.018311 | 0.022888 | 0.030518 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -11.1008 | -2.8015 | 4.4724 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.5884 | 0.018311 | 0.022888
6893.3281 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.43488 | -0.24719 | -0.4715 | -0.78735 | 0.018311 | 0.013733 | 0.022888 | 0.045776 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.001068 | -10.1624 | -5.2139 | 2.9022 | 0.022888 | 0.018311 | 0.022888 | 0.018311 | 1.5198 | 0.022888 | 0.018311
6895.0156 | 0.045776 | 0.006409 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.003204 | -0.40283 | -0.22888 | -0.40741 | -0.72784 | 0.013733 | 0.013733 | 0.009155 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | -9.1187 | -6.4178 | 1.5289 | 0.022888 | 0.013733 | 0.013733 | 0.018311 | 1.2131 | 0.018311 | 0.022888
6896.7656 | 0.061035 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.3891 | -0.21973 | -0.35248 | -0.67291 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -8.0795 | -6.6833 | 0.23804 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.2085 | 0.022888 | 0.018311
6898.5156 | 0.045776 | 0.005341 | 0.001068 | 0 | 0 | 0.002136 | 0.003204 | -0.38452 | -0.21973 | -0.34332 | -0.64545 | 0.018311 | 0.022888 | 0.022888 | 0.076294 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -7.1869 | -6.7703 | -1.0483 | 0.018311 | 0.022888 | 0.022888 | 0.013733 | 1.4008 | 0.022888 | 0.022888
6900.2812 | 0.030518 | 0.006409 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.33417 | -0.17395 | -0.27466 | -0.60425 | 0.013733 | 0.013733 | 0.018311 | 0.091553 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -6.395 | -6.752 | -2.2842 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | 1.5106 | 0.018311 | 0.027466
6901.9688 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.38452 | -0.22888 | -0.26093 | -0.53558 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -5.7678 | -6.6833 | -3.2959 | 0.013733 | 0.022888 | 0.013733 | 0.018311 | 1.6479 | 0.018311 | 0.022888
6903.7344 | 0.030518 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.35706 | -0.19226 | -0.20142 | -0.4715 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -5.1636 | -6.4865 | -4.0649 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | 1.5472 | 0.013733 | 0.022888
6905.5 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.42572 | -0.27466 | -0.20599 | -0.45319 | 0.013733 | 0.018311 | 0.009155 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | -4.6783 | -6.34 | -4.66 | 0.009155 | 0.013733 | 0.022888 | 0.009155 | 1.3596 | 0.013733 | 0.018311
6907.2656 | 0.076294 | 0.006409 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.37537 | -0.22888 | -0.21973 | -0.46692 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | -4.184 | -6.0974 | -4.9347 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 1.2543 | 0.022888 | 0.018311
6908.9531 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.004272 | 0.003204 | -0.41199 | -0.25177 | -0.24261 | -0.49896 | 0.022888 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -3.7811 | -5.8731 | -5.1315 | 0.018311 | 0.013733 | 0.018311 | 0.009155 | 1.4603 | 0.018311 | 0.022888
6910.7188 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.35248 | -0.2243 | -0.09613 | -0.33417 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -3.4287 | -5.6351 | -5.2322 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 1.6296 | 0.022888 | 0.022888
6912.4844 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.32501 | -0.22888 | 0.14648 | -0.041199 | 0.022888 | 0.009155 | 0.013733 | 0.091553 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | -3.1036 | -5.3833 | -5.2689 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 1.4374 | 0.022888 | 0.022888
6914.2344 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.4303 | -0.27008 | -0.35706 | -0.45776 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.005341 | 0.003204 | 0.004272 | 0.005341 | -2.8656 | -5.1636 | -5.2826 | 0.018311 | 0.018311 | 0.009155 | 0.013733 | 1.236 | 0.013733 | 0.013733
6915.9219 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.44403 | -0.28381 | -0.28839 | -0.45319 | 0.022888 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.004272 | 0.005341 | -2.623 | -4.9667 | -5.2963 | 0.022888 | 0.018311 | 0.018311 | 0.018311 | 1.3229 | 0.022888 | 0.022888
6917.6719 | 0.061035 | 0.005341 | 0.004272 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.44861 | -0.28839 | -0.26093 | -0.43945 | 0.022888 | 0.022888 | 0.022888 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | -2.3849 | -4.7287 | -5.2414 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 1.5564 | 0.013733 | 0.022888
6919.4219 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.4715 | -0.31128 | -0.24719 | -0.41657 | 0.009155 | 0.018311 | 0.009155 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -2.1698 | -4.5136 | -5.1727 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 1.5793 | 0.018311 | 0.027466
6921.1719 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.004272 | -0.49896 | -0.33417 | -0.23804 | -0.39368 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -1.9958 | -4.2984 | -5.0766 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.442 | 0.022888 | 0.027466
6922.875 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.49439 | -0.32959 | -0.25635 | -0.39825 | 0.018311 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -1.8265 | -4.1153 | -4.9988 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 1.5335 | 0.022888 | 0.022888
6924.6406 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0 | -0.5127 | -0.33875 | -0.27008 | -0.38452 | 0.022888 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -1.6663 | -3.9047 | -4.8752 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | 1.3779 | 0.022888 | 0.022888
6926.4062 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.53101 | -0.33875 | -0.28381 | -0.38452 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | -1.5335 | -3.7216 | -4.7607 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.5701 | 0.022888 | 0.036621
6928.1562 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0 | 0.002136 | -0.52643 | -0.36163 | -0.31128 | -0.41199 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -1.4145 | -3.5522 | -4.6463 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 1.5152 | 0.022888 | 0.018311
6929.8438 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0 | -0.54474 | -0.36163 | -0.30212 | -0.3891 | 0.022888 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -1.3046 | -3.3783 | -4.5181 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | 1.3046 | 0.018311 | 0.018311
6931.6094 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.55847 | -0.37537 | -0.33417 | -0.41657 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -1.2039 | -3.2135 | -4.3808 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.3824 | 0.022888 | 0.018311
6933.3125 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.55389 | -0.37994 | -0.37994 | -0.46234 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | 0.004272 | -1.1032 | -3.0808 | -4.303 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.593 | 0.013733 | 0.027466
6935 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.54932 | -0.3891 | -0.37994 | -0.46692 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -1.0162 | -2.8976 | -4.1656 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 1.4511 | 0.022888 | 0.013733
6936.7656 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.55847 | -0.40283 | -0.41657 | -0.49439 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | -0.93842 | -2.7603 | -4.0329 | 0.009155 | 0.013733 | 0.009155 | 0.018311 | 1.474 | 0.022888 | 0.018311
6938.5469 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.5722 | -0.39825 | -0.40741 | -0.49896 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.87891 | -2.6093 | -3.8864 | 0.009155 | 0.013733 | 0.022888 | 0.013733 | 1.4511 | 0.018311 | 0.018311
6940.3125 | 0.076294 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.001068 | -0.57678 | -0.40741 | -0.43945 | -0.53558 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | -0.82398 | -2.4765 | -3.7674 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | 1.5564 | 0.022888 | 0.018311
6942 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0 | 0.001068 | -0.5722 | -0.3891 | -0.4715 | -0.56305 | 0.009155 | 0.013733 | 0.013733 | 0.030518 | 0.004272 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | -0.76904 | -2.3666 | -3.6667 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 1.5701 | 0.018311 | 0.022888
6943.7031 | 0.030518 | 0.004272 | 0.001068 | 0.003204 | -0.001068 | 0.003204 | 0.001068 | -0.58136 | -0.39825 | -0.49439 | -0.59509 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.71411 | -2.2385 | -3.5385 | 0.013733 | 0.013733 | 0.018311 | 0.022888 | 1.4557 | 0.018311 | 0.022888
6945.4062 | 0.045776 | 0.006409 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.59052 | -0.41657 | -0.52185 | -0.62256 | 0.013733 | 0.018311 | 0.022888 | 0.076294 | 0.002136 | 0 | 0.004272 | 0.002136 | 0.001068 | -0.67749 | -2.1194 | -3.4332 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | 1.561 | 0.022888 | 0.018311
6947.1562 | 0.045776 | 0.005341 | 0.005341 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.60425 | -0.43488 | -0.53558 | -0.64087 | 0.013733 | 0.022888 | 0.018311 | 0.091553 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.63629 | -1.9958 | -3.3051 | 0.013733 | 0.004578 | 0.018311 | 0.018311 | 1.2909 | 0.018311 | 0.022888
6948.8594 | 0.091553 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.60883 | -0.43488 | -0.56763 | -0.69122 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.004272 | -0.62256 | -1.8997 | -3.1723 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.2909 | 0.018311 | 0.022888
6950.6406 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.58594 | -0.40741 | -0.50812 | -0.65002 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.58136 | -1.8265 | -3.0991 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | 1.5839 | 0.022888 | 0.022888
6952.3438 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.45319 | -0.59509 | -0.71869 | 0.009155 | 0.013733 | 0.009155 | 0.030518 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | -0.53558 | -1.6983 | -2.9755 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 1.4145 | 0.018311 | 0.022888
6954.0938 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.6134 | -0.45776 | -0.60425 | -0.737 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | -0.52185 | -1.6388 | -2.8702 | 0.013733 | 0.022888 | 0.018311 | 0.013733 | 1.4557 | 0.022888 | 0.022888
6955.8281 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.001068 | 0 | -0.60883 | -0.42114 | -0.6134 | -0.76446 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.50354 | -1.5335 | -2.7512 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.387 | 0.018311 | 0.018311
6957.5938 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.59967 | -0.44403 | -0.64087 | -0.80109 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.46692 | -1.4557 | -2.6871 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 1.6067 | 0.027466 | 0.018311
6959.3594 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.59052 | -0.42572 | -0.64087 | -0.80566 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.006409 | 0.003204 | -0.46234 | -1.3641 | -2.5452 | 0.013733 | 0.018311 | 0.009155 | 0.013733 | 1.5152 | 0.018311 | 0.032043
6961.0469 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.59509 | -0.40741 | -0.60883 | -0.79651 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.42572 | -1.3 | -2.4582 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | 1.4465 | 0.022888 | 0.027466
6962.75 | 0.091553 | 0.005341 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.001068 | -0.60425 | -0.42114 | -0.64087 | -0.82855 | 0.013733 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.003204 | -0.43488 | -1.236 | -2.3712 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | 1.3733 | 0.022888 | 0.018311
6964.5156 | 0.030518 | 0.005341 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.59967 | -0.4303 | -0.66376 | -0.85602 | 0.009155 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.006409 | 0.004272 | 0.003204 | -0.4303 | -1.2039 | -2.2842 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 1.2817 | 0.018311 | 0.013733
6966.2812 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.002136 | 0.001068 | -0.59967 | -0.40283 | -0.6546 | -0.86517 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 0.001068 | -0.39368 | -1.149 | -2.2293 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.2405 | 0.018311 | 0.018311
6967.9688 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | -0.59052 | -0.42114 | -0.6546 | -0.87891 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.4303 | -1.1124 | -2.1515 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.3229 | 0.018311 | 0.027466
6969.7344 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.58136 | -0.41199 | -0.66834 | -0.89264 | 0.009155 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.40741 | -1.0712 | -2.0782 | 0.018311 | 0.018311 | 0.009155 | 0.027466 | 1.236 | 0.018311 | 0.027466
6971.4375 | 0.061035 | 0.006409 | 0 | 0.002136 | -0.001068 | 0.001068 | 0.003204 | -0.58136 | -0.42572 | -0.70496 | -0.93842 | 0.022888 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.39368 | -1.0437 | -2.0416 | 0.018311 | 0.018311 | 0.018311 | 0.009155 | 1.4969 | 0.013733 | 0.018311
6973.2031 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.59509 | -0.4303 | -0.70496 | -0.94757 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.37537 | -0.99335 | -1.9501 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 1.268 | 0.022888 | 0.013733
6974.9062 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.004272 | -0.59052 | -0.4303 | -0.71411 | -0.98419 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.005341 | -0.36621 | -0.94757 | -1.886 | 0.009155 | 0.027466 | 0.027466 | 0.018311 | 1.506 | 0.013733 | 0.022888
6976.6719 | 0.061035 | 0.005341 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.61798 | -0.42572 | -0.71411 | -0.96588 | 0.022888 | 0.018311 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.36621 | -0.91553 | -1.8127 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 1.3458 | 0.018311 | 0.009155
6978.4219 | 0.061035 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.001068 | 0.001068 | -0.6134 | -0.45319 | -0.74158 | -1.0071 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.37079 | -0.89722 | -1.7761 | 0.009155 | 0.022888 | 0.013733 | 0.018311 | 1.474 | 0.018311 | 0.022888
6980.1719 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0 | 0.004272 | 0.002136 | -0.60425 | -0.44403 | -0.74158 | -1.0208 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | -0.37079 | -0.86517 | -1.7166 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.4191 | 0.018311 | 0.018311
6981.8594 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.59967 | -0.44403 | -0.77362 | -1.0529 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.37537 | -0.85602 | -1.6937 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.4465 | 0.018311 | 0.018311
6983.625 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.61798 | -0.43488 | -0.74616 | -1.0437 | 0.018311 | 0.013733 | 0.013733 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.37079 | -0.82398 | -1.6296 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 1.3046 | 0.022888 | 0.022888
6985.375 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.6134 | -0.43488 | -0.76904 | -1.0712 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -0.37079 | -0.8194 | -1.6022 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 1.4603 | 0.018311 | 0.027466
6987.0625 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.59509 | -0.43488 | -0.7782 | -1.0895 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.35706 | -0.81024 | -1.5701 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | 1.4923 | 0.022888 | 0.018311
6988.7656 | 0.030518 | 0.004272 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.002136 | -0.59052 | -0.43945 | -0.76904 | -1.1032 | 0.009155 | 0.018311 | 0.004578 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | 0.001068 | -0.35706 | -0.78735 | -1.5289 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 1.4145 | 0.022888 | 0.013733
6990.5156 | 0.076294 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.60425 | -0.40741 | -0.78278 | -1.1124 | 0.013733 | 0.018311 | 0.022888 | 0.076294 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.3479 | -0.74616 | -1.4832 | 0.013733 | 0.018311 | 0.013733 | 0.027466 | 1.4328 | 0.013733 | 0.022888
6992.2031 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.59967 | -0.39825 | -0.78735 | -1.1307 | 0.013733 | 0.013733 | 0.022888 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.004272 | -0.60883 | -0.86975 | -1.6342 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | 0.67749 | 0.022888 | 0.013733
6993.8906 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.004272 | 0.001068 | -0.56763 | -0.41657 | -0.80109 | -1.1353 | 0.018311 | 0.018311 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.48523 | -0.83313 | -1.7349 | 0.013733 | 0.027466 | 0.022888 | 0.013733 | -0.086975 | 0.013733 | 0.018311
6995.6562 | 0.061035 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.001068 | 0.002136 | -0.54474 | -0.43488 | -0.82855 | -1.1353 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.5127 | -0.87433 | -1.5747 | 0.013733 | 0.013733 | 0.022888 | 0.022888 | 0.66376 | 0.027466 | 0.022888
6997.4219 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.54474 | -0.42114 | -0.84686 | -1.1856 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | -0.45319 | -0.87433 | -1.561 | 0.013733 | 0.009155 | 0.013733 | 0.013733 | 0.86517 | 0.018311 | 0.022888
6999.1094 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.003204 | -0.58136 | -0.41199 | -0.74158 | -1.1032 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.41199 | -0.81024 | -1.474 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.85144 | 0.018311 | 0.018311
7000.8281 | 0.045776 | 0.005341 | 0.001068 | 0.004272 | -0.001068 | 0.001068 | 0.002136 | -0.59509 | -0.43945 | -0.79651 | -1.1536 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.40283 | -0.81482 | -1.4465 | 0.018311 | 0.013733 | 0.009155 | 0.022888 | 0.97046 | 0.013733 | 0.018311
7002.5938 | 0.061035 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.46234 | -0.77362 | -1.1307 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.37994 | -0.76446 | -1.3779 | 0.013733 | 0.013733 | 0.004578 | 0.013733 | -0.004578 | 0.022888 | 0.013733
7004.3594 | 0.030518 | 0.006409 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.001068 | -0.63171 | -0.45319 | -0.81482 | -1.1673 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.005341 | 0.002136 | 0.005341 | 0.004272 | 0.003204 | -0.41657 | -0.8194 | -1.4465 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 0.89264 | 0.018311 | 0.022888
7006.125 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.003204 | 0.001068 | -0.62714 | -0.42114 | -0.7782 | -1.1398 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.42572 | -0.80109 | -1.4053 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.95215 | 0.018311 | 0.022888
7007.8125 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.45319 | -0.81482 | -1.1765 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -0.42572 | -0.80566 | -1.3916 | 0.018311 | 0.009155 | 0.013733 | 0.013733 | 0.86517 | 0.022888 | 0.018311
7009.5781 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.001068 | -0.63171 | -0.43945 | -0.82398 | -1.1902 | 0.018311 | 0.018311 | 0.009155 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.4303 | -0.80109 | -1.3596 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | 0.8606 | 0.009155 | 0.022888
7011.3281 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.61798 | -0.4303 | -0.81024 | -1.1948 | 0.022888 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.41199 | -0.78735 | -1.3412 | 0.013733 | 0.009155 | 0.022888 | 0.009155 | 0.9613 | 0.022888 | 0.013733
7013.0156 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.004272 | 0.002136 | -0.63629 | -0.45319 | -0.82398 | -1.2085 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | -0.39825 | -0.76904 | -1.3229 | 0.009155 | 0.013733 | 0.009155 | 0.013733 | 0.92468 | 0.022888 | 0.018311
7014.7656 | 0.045776 | 0.006409 | 0.003204 | 0.003204 | -0.002136 | 0.004272 | 0.002136 | -0.61798 | -0.42572 | -0.82398 | -1.2085 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.39368 | -0.75989 | -1.3092 | 0.018311 | 0.018311 | 0.013733 | 0.027466 | 0.93842 | 0.018311 | 0.018311
7016.5156 | 0.061035 | 0.005341 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | -0.60883 | -0.44403 | -0.84228 | -1.2451 | 0.013733 | 0.013733 | 0.022888 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.37079 | -0.75989 | -1.3092 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.0986 | 0.027466 | 0.022888
7018.2188 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.004272 | 0.002136 | -0.60425 | -0.4303 | -0.84228 | -1.2405 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.36163 | -0.73242 | -1.2955 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 1.3229 | 0.018311 | 0.009155
7019.9688 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.60425 | -0.43488 | -0.84686 | -1.2405 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | -0.33875 | -0.70953 | -1.2772 | 0.022888 | 0.018311 | 0.018311 | 0.013733 | 1.181 | 0.013733 | 0.027466
7021.7188 | 0.045776 | 0.006409 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.62256 | -0.43945 | -0.84228 | -1.236 | 0.018311 | 0.013733 | 0.009155 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.33417 | -0.68207 | -1.2543 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 1.3733 | 0.018311 | 0.018311
7023.4844 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0 | 0.001068 | -0.63629 | -0.4303 | -0.79193 | -1.181 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.33417 | -0.65918 | -1.2039 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 1.3184 | 0.018311 | 0.022888
7025.2656 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.59509 | -0.43488 | -0.9613 | -1.3 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | -0.37079 | -0.70496 | -1.1765 | 0.018311 | 0.022888 | 0.013733 | 0.018311 | 1.4465 | 0.018311 | 0.018311
7026.9531 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.60425 | -0.43945 | -0.89722 | -1.2772 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.38452 | -0.66376 | -1.1261 | 0.013733 | 0.022888 | 0.013733 | 0.022888 | 1.3962 | 0.018311 | 0.022888
7028.7188 | 0.030518 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.6134 | -0.44403 | -0.86975 | -1.2817 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.36163 | -0.67291 | -1.1581 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 1.6708 | 0.022888 | 0.018311
7030.4844 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.60425 | -0.44403 | -0.89264 | -1.3046 | 0.018311 | 0.018311 | 0.022888 | 0.076294 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | -0.36621 | -0.67749 | -1.1536 | 0.013733 | 0.018311 | 0.004578 | 0.022888 | 2.2751 | 0.022888 | 0.018311
7032.2344 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.49896 | -0.39825 | -0.86975 | -1.3092 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.37079 | -0.60425 | -1.062 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | 1.3458 | 0.013733 | 0.022888
7033.9219 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.54932 | -0.39825 | -0.82398 | -1.2451 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | -0.35248 | -0.60425 | -1.1032 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.4282 | 0.018311 | 0.027466
7035.625 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.5722 | -0.41199 | -0.83771 | -1.2451 | 0.013733 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.39825 | -0.59967 | -1.0986 | 0.013733 | 0.022888 | 0.013733 | 0.009155 | 1.4832 | 0.018311 | 0.013733
7037.3906 | 0.076294 | 0.005341 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.001068 | -0.61798 | -0.4303 | -0.80566 | -1.2405 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.35706 | -0.59509 | -1.1398 | 0.009155 | 0.018311 | 0.013733 | 0.013733 | 1.5244 | 0.022888 | 0.013733
7039.1406 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.61798 | -0.41199 | -0.80566 | -1.2177 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.34332 | -0.60425 | -1.1078 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.4603 | 0.022888 | 0.018311
7040.8438 | 0.061035 | 0.005341 | 0.005341 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.67291 | -0.45776 | -0.66376 | -1.1398 | 0.009155 | 0.013733 | 0.022888 | 0.061035 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.42572 | -0.73242 | -1.149 | 0.018311 | 0.027466 | 0.013733 | 0.013733 | 1.1993 | 0.022888 | 0.022888
7042.625 | 0.045776 | 0.006409 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.66834 | -0.44403 | -0.74616 | -1.1536 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.35706 | -0.6958 | -1.1536 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.1307 | 0.018311 | 0.018311
7044.3281 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.66834 | -0.46692 | -0.80109 | -1.1948 | 0.013733 | 0.022888 | 0.022888 | 0.045776 | 0.004272 | 0.002136 | 0.005341 | 0.003204 | 0.004272 | -0.36163 | -0.68207 | -1.1444 | 0.013733 | 0.022888 | 0.018311 | 0.009155 | 1.3412 | 0.022888 | 0.027466
7046.0156 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.63629 | -0.43488 | -0.81024 | -1.2222 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.35248 | -0.66376 | -1.1124 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 1.4465 | 0.027466 | 0.022888
7047.7812 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.43488 | -0.83313 | -1.2634 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.004272 | 0.002136 | -0.34332 | -0.67291 | -1.1169 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.7532 | 0.022888 | 0.018311
7049.5 | 0.045776 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.001068 | -0.63629 | -0.43488 | -0.84686 | -1.2909 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.34332 | -0.6546 | -1.1169 | 0.013733 | 0.018311 | 0.013733 | 0.009155 | 1.8036 | 0.027466 | 0.018311
7051.25 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.63171 | -0.45776 | -0.84686 | -1.2863 | 0.022888 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | -0.32501 | -0.63629 | -1.1078 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | 1.7303 | 0.027466 | 0.018311
7052.9531 | 0.061035 | 0.006409 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.003204 | -0.63629 | -0.43945 | -0.82855 | -1.2497 | 0.013733 | 0.009155 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0 | 0.004272 | -0.32959 | -0.61798 | -1.0712 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 1.6479 | 0.018311 | 0.022888
7054.7188 | 0.076294 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | -0.62256 | -0.42572 | -0.82398 | -1.2451 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -0.34332 | -0.6134 | -1.0529 | 0.018311 | 0.018311 | 0.009155 | 0.022888 | 1.5793 | 0.018311 | 0.018311
7056.4219 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.61798 | -0.4303 | -0.83313 | -1.2589 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.34332 | -0.61798 | -1.0529 | 0.022888 | 0.013733 | 0.018311 | 0.013733 | 1.5289 | 0.013733 | 0.022888
7058.1875 | 0.091553 | 0.004272 | 0.004272 | 0.002136 | -0.001068 | 0.002136 | 0.001068 | -0.60883 | -0.42572 | -0.84228 | -1.2726 | 0.018311 | 0.013733 | 0.022888 | 0.076294 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | -0.32959 | -0.62714 | -1.0666 | 0.018311 | 0.009155 | 0.018311 | 0.022888 | 1.6342 | 0.018311 | 0.022888
7059.8906 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.61798 | -0.43488 | -0.84228 | -1.2589 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.003204 | 0.005341 | 0.002136 | -0.32044 | -0.61798 | -1.0437 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | 1.4694 | 0.018311 | 0.018311
7061.6719 | 0.030518 | 0.006409 | 0.003204 | 0.003204 | -0.001068 | 0.002136 | 0.002136 | -0.62256 | -0.44403 | -0.85602 | -1.2955 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.32044 | -0.62256 | -1.0529 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | 1.6663 | 0.018311 | 0.018311
7063.4219 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.6134 | -0.43945 | -0.8606 | -1.2909 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.3067 | -0.58594 | -1.0437 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | 1.5244 | 0.022888 | 0.018311
7065.1094 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.61798 | -0.42572 | -0.84228 | -1.2772 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.3067 | -0.57678 | -1.0208 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | 1.4969 | 0.013733 | 0.022888
7066.8125 | 0.045776 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.001068 | -0.62256 | -0.44403 | -0.86517 | -1.2955 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.32501 | -0.58136 | -1.0254 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | 1.5564 | 0.022888 | 0.018311
7068.5781 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.003204 | -0.63629 | -0.42572 | -0.83313 | -1.2726 | 0.022888 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.32044 | -0.56305 | -1.0025 | 0.013733 | 0.022888 | 0.022888 | 0.018311 | 1.4145 | 0.027466 | 0.018311
7070.2812 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.63629 | -0.45319 | -0.8606 | -1.2909 | 0.027466 | 0.027466 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.32959 | -0.58136 | -1.0162 | 0.022888 | 0.018311 | 0.013733 | 0.022888 | 1.3504 | 0.022888 | 0.018311
7071.9688 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0 | 0.004272 | 0.001068 | -0.63171 | -0.43488 | -0.85602 | -1.2955 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.33417 | -0.58136 | -1.0025 | 0.018311 | 0.009155 | 0.013733 | 0.022888 | 1.4053 | 0.018311 | 0.018311
7073.7188 | 0.076294 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.003204 | 0.002136 | -0.65002 | -0.46234 | -0.86975 | -1.3046 | 0.013733 | 0.013733 | 0.009155 | 0.045776 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.33875 | -0.58136 | -1.0025 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.3824 | 0.027466 | 0.018311
7075.4219 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0 | -0.65918 | -0.45776 | -0.85602 | -1.2817 | 0.027466 | 0.022888 | 0.009155 | 0.076294 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.34332 | -0.5722 | -0.99792 | 0.013733 | 0.022888 | 0.022888 | 0.018311 | 1.2131 | 0.027466 | 0.013733
7077.1875 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.004272 | 0.002136 | -0.64545 | -0.42114 | -0.85144 | -1.2909 | 0.018311 | 0.022888 | 0.022888 | 0.076294 | 0.003204 | 0.003204 | 0.005341 | 0.003204 | 0.001068 | -0.36621 | -0.59967 | -0.99792 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.2268 | 0.022888 | 0.022888
7078.875 | 0.045776 | 0.006409 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.63171 | -0.45776 | -0.86975 | -1.3046 | 0.013733 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.35706 | -0.62256 | -1.0208 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 1.3229 | 0.022888 | 0.022888
7080.6406 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.65002 | -0.45319 | -0.86975 | -1.3 | 0.009155 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.36621 | -0.61798 | -1.0162 | 0.022888 | 0.018311 | 0.013733 | 0.022888 | 1.1856 | 0.022888 | 0.013733
7082.4062 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.63629 | -0.45776 | -0.87433 | -1.3092 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.001068 | 0.005341 | 0.004272 | 0.003204 | 0.002136 | -0.35706 | -0.62714 | -1.03 | 0.022888 | 0.018311 | 0.013733 | 0.018311 | 1.1902 | 0.022888 | 0.013733
7084.1562 | 0.045776 | 0.005341 | 0.004272 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.64545 | -0.45776 | -0.86975 | -1.3138 | 0.018311 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.36163 | -0.62714 | -1.0345 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | 1.1581 | 0.018311 | 0.022888
7085.8594 | 0.091553 | 0.003204 | 0.002136 | 0.001068 | 0 | 0.004272 | 0.002136 | -0.64087 | -0.45776 | -0.87891 | -1.3184 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -0.3479 | -0.6134 | -1.0437 | 0.013733 | 0.022888 | 0.022888 | 0.013733 | 1.1215 | 0.018311 | 0.018311
7087.625 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.64545 | -0.45776 | -0.90179 | -1.3275 | 0.022888 | 0.018311 | 0.013733 | 0.076294 | 0.001068 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | -0.3479 | -0.63171 | -1.0574 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.3596 | 0.013733 | 0.018311
7089.3906 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.64087 | -0.45776 | -0.89264 | -1.3275 | 0.004578 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.33875 | -0.6134 | -1.03 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 1.4694 | 0.018311 | 0.022888
7091.0781 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | -0.001068 | 0.003204 | 0 | -0.64545 | -0.46692 | -0.89264 | -1.3229 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.005341 | 0.003204 | 0.003204 | -0.33875 | -0.59967 | -1.0117 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.1673 | 0.027466 | 0.018311
7092.7812 | 0.076294 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.64087 | -0.44861 | -0.89264 | -1.3321 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.33417 | -0.59052 | -1.0117 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 1.2405 | 0.018311 | 0.022888
7094.5469 | 0.076294 | 0.005341 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.6546 | -0.46692 | -0.88806 | -1.3275 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.35248 | -0.60425 | -1.0208 | 0.013733 | 0.013733 | 0.027466 | 0.022888 | 1.1673 | 0.027466 | 0.022888
7096.3125 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.64087 | -0.46692 | -0.89722 | -1.3458 | 0.022888 | 0.013733 | 0.009155 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.004272 | 0.004272 | -0.35248 | -0.60883 | -1.0254 | 0.009155 | 0.009155 | 0.022888 | 0.018311 | 1.1581 | 0.022888 | 0.018311
7098 | 0.076294 | 0.006409 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.62714 | -0.44403 | -0.88348 | -1.3412 | 0.022888 | 0.022888 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.34332 | -0.59052 | -1.0162 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 1.3367 | 0.018311 | 0.022888
7099.75 | 0.045776 | 0.006409 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.005341 | -0.63629 | -0.44861 | -0.86517 | -1.3092 | 0.022888 | 0.022888 | 0.018311 | 0.076294 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.33875 | -0.58136 | -0.98419 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.0941 | 0.022888 | 0.022888
7101.5156 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | -0.65002 | -0.46692 | -0.87433 | -1.3184 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.35706 | -0.60425 | -1.0025 | 0.022888 | 0.013733 | 0.018311 | 0.013733 | 1.181 | 0.018311 | 0.018311
7103.2031 | 0.076294 | 0.006409 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | -0.64087 | -0.49439 | -0.90179 | -1.3367 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.34332 | -0.6134 | -1.0345 | 0.013733 | 0.018311 | 0.009155 | 0.013733 | 1.3962 | 0.018311 | 0.022888
7104.9062 | 0.076294 | 0.004272 | 0.002136 | 0.001068 | -0.001068 | 0.003204 | 0.003204 | -0.62256 | -0.43945 | -0.87433 | -1.3275 | 0.009155 | 0.018311 | 0.009155 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -0.32044 | -0.60425 | -1.0162 | 0.018311 | 0.013733 | 0.009155 | 0.022888 | 1.2955 | 0.018311 | 0.018311
7106.6094 | 0.045776 | 0.006409 | 0.003204 | 0.001068 | 0.001068 | 0.001068 | 0.002136 | -0.6134 | -0.46234 | -0.86517 | -1.3184 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.32959 | -0.59052 | -0.98419 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.0803 | 0.013733 | 0.018311
7108.3594 | 0.061035 | 0.004272 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | 0.001068 | -0.61798 | -0.46692 | -0.86975 | -1.3138 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.33875 | -0.60425 | -1.0117 | 0.018311 | 0.009155 | 0.018311 | 0.018311 | 1.2543 | 0.018311 | 0.013733
7110.1094 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.62714 | -0.4715 | -0.88806 | -1.3275 | 0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.32501 | -0.60425 | -1.0117 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 1.355 | 0.022888 | 0.027466
7111.8125 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.63171 | -0.45319 | -0.87433 | -1.3 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.004272 | -0.33875 | -0.58136 | -0.99335 | 0.009155 | 0.009155 | 0.022888 | 0.022888 | 1.2177 | 0.018311 | 0.013733
7113.5781 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0 | 0.003204 | -0.61798 | -0.4715 | -0.88348 | -1.3229 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.004272 | 0.004272 | 0.001068 | -0.33875 | -0.59509 | -0.99792 | 0.009155 | 0.013733 | 0.018311 | 0.013733 | 1.2497 | 0.018311 | 0.022888
7115.3438 | 0.045776 | 0.006409 | 0.004272 | 0 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.45319 | -0.86975 | -1.3 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.002136 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | -0.33875 | -0.60425 | -0.99335 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | 1.2634 | 0.022888 | 0.022888
7117.0312 | 0.045776 | 0.004272 | 0.002136 | 0.005341 | 0.001068 | 0.003204 | 0.002136 | -0.62256 | -0.45776 | -0.87433 | -1.3229 | 0.013733 | 0.009155 | 0.013733 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.34332 | -0.60425 | -1.0025 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.4465 | 0.018311 | 0.022888
7118.7344 | 0.061035 | 0.004272 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.63629 | -0.45319 | -0.85144 | -1.2909 | 0.009155 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | -0.34332 | -0.59052 | -0.97961 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | 1.1902 | 0.018311 | 0.022888
7120.5 | 0.030518 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | -0.63629 | -0.47607 | -0.88348 | -1.3184 | 0.018311 | 0.013733 | 0.009155 | 0.030518 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.3479 | -0.6134 | -1.0071 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 1.387 | 0.022888 | 0.018311
7122.1875 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0 | 0.004272 | 0.001068 | -0.64545 | -0.4715 | -0.87433 | -1.3 | 0.013733 | 0.022888 | 0.009155 | 0.045776 | 0.001068 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | -0.35248 | -0.59509 | -0.99335 | 0.013733 | 0.018311 | 0.013733 | 0.022888 | 1.1307 | 0.018311 | 0.018311
7123.8906 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.62256 | -0.44403 | -0.87433 | -1.3184 | 0.018311 | 0.013733 | 0.009155 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | -0.3479 | -0.59967 | -0.99792 | 0.018311 | 0.013733 | 0.027466 | 0.013733 | 1.4328 | 0.022888 | 0.013733
7125.6562 | 0.061035 | 0.006409 | 0.004272 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.61798 | -0.45319 | -0.87433 | -1.3138 | 0.009155 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -0.34332 | -0.60883 | -1.0071 | 0.013733 | 0.022888 | 0.022888 | 0.013733 | 1.2634 | 0.022888 | 0.022888
7127.3594 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.003204 | 0.001068 | -0.63629 | -0.46692 | -0.87891 | -1.3138 | 0.018311 | 0.013733 | 0.013733 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.33875 | -0.59052 | -1.0071 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | 1.2863 | 0.022888 | 0.022888
7129.0469 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.003204 | 0.001068 | -0.63629 | -0.47607 | -0.87433 | -1.3184 | 0.018311 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | -0.33417 | -0.59052 | -1.0025 | 0.022888 | 0.009155 | 0.013733 | 0.009155 | 1.2497 | 0.022888 | 0.018311
7130.75 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.63629 | -0.47607 | -0.88348 | -1.3229 | 0.013733 | 0.013733 | 0.018311 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.32044 | -0.59052 | -0.99792 | 0.022888 | 0.009155 | 0.013733 | 0.018311 | 1.3641 | 0.022888 | 0.022888
7132.5156 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.003204 | 0.002136 | -0.61798 | -0.46234 | -0.87433 | -1.3184 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.001068 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | -0.31586 | -0.58136 | -0.98419 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 1.3916 | 0.018311 | 0.018311
7134.2812 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.003204 | -0.64087 | -0.48981 | -0.89264 | -1.3275 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.32044 | -0.57678 | -0.98419 | 0.013733 | 0.009155 | 0.013733 | 0.018311 | 1.4648 | 0.018311 | 0.018311
7135.9688 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.63171 | -0.4715 | -0.87891 | -1.3229 | 0.022888 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.32959 | -0.57678 | -0.97046 | 0.009155 | 0.022888 | 0.018311 | 0.018311 | -0.65002 | 0.018311 | 0.027466
7137.7188 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.62256 | -0.46234 | -0.87433 | -1.3229 | 0.022888 | 0.013733 | 0.004578 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.31586 | -0.56305 | -0.9613 | 0.018311 | 0.018311 | 0.013733 | 0.027466 | -0.54932 | 0.022888 | 0.018311
7139.4844 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.003204 | 0 | 0.002136 | -0.63171 | -0.4715 | -0.8606 | -1.3184 | 0.018311 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.33875 | -0.55389 | -0.94757 | 0.018311 | 0.013733 | 0.022888 | 0.013733 | -0.72327 | 0.018311 | 0.022888
7141.2344 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.62256 | -0.4715 | -0.89264 | -1.3321 | 0.018311 | 0.022888 | 0.018311 | 0.076294 | 0.004272 | 0.002136 | 0.006409 | 0.005341 | 0.003204 | -0.32959 | -0.57678 | -0.96588 | 0.018311 | 0.013733 | 0.009155 | 0.018311 | -0.57678 | 0.018311 | 0.022888
7142.9375 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.62256 | -0.46234 | -0.8606 | -1.3046 | 0.004578 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.32959 | -0.56305 | -0.94757 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | -0.72784 | 0.022888 | 0.022888
7144.7188 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.62256 | -0.46234 | -0.88348 | -1.3367 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.004272 | 0.002136 | 0.004272 | 0.004272 | -0.32501 | -0.58594 | -0.97046 | 0.009155 | 0.013733 | 0.018311 | 0.022888 | -0.52643 | 0.018311 | 0.013733
7146.4844 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.62714 | -0.46692 | -0.88806 | -1.3321 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | -0.32501 | -0.58136 | -0.97504 | 0.013733 | 0.013733 | 0.009155 | 0.022888 | -0.62256 | 0.018311 | 0.027466
7148.1719 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.005341 | -0.63629 | -0.47607 | -0.88348 | -1.3321 | 0.022888 | 0.022888 | 0.013733 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.32501 | -0.5722 | -0.96588 | 0.022888 | 0.018311 | 0.018311 | 0.018311 | -0.64545 | 0.018311 | 0.013733
7149.9375 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | 0.002136 | -0.61798 | -0.46234 | -0.87433 | -1.3092 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | -0.32959 | -0.5722 | -0.97046 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -0.78278 | 0.022888 | 0.018311
7151.7031 | 0.061035 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.62256 | -0.46692 | -0.88348 | -1.3138 | 0.009155 | 0.013733 | 0.018311 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | -0.32501 | -0.57678 | -0.97961 | 0.018311 | 0.022888 | 0.013733 | 0.018311 | -0.6546 | 0.022888 | 0.022888
7153.4531 | 0.045776 | 0.005341 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.62714 | -0.4715 | -0.87891 | -1.3046 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | -0.32501 | -0.58136 | -0.97504 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -0.6134 | 0.022888 | 0.027466
7155.2031 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0.002136 | 0.004272 | 0.003204 | -0.62714 | -0.47607 | -0.86975 | -1.2909 | 0.009155 | 0.018311 | 0.004578 | 0.045776 | 0.001068 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | -0.32044 | -0.56763 | -0.97046 | 0.018311 | 0.013733 | 0.027466 | 0.018311 | -0.71411 | 0.013733 | 0.018311
7156.9062 | 0.061035 | 0.005341 | 0 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.45776 | -0.85144 | -1.2817 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.32959 | -0.55389 | -0.93842 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | -0.88806 | 0.018311 | 0.018311
7158.6875 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.45776 | -0.86975 | -1.3 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.001068 | -0.33875 | -0.57678 | -0.96588 | 0.013733 | 0.022888 | 0.013733 | 0.013733 | -0.65918 | 0.018311 | 0.013733
7160.4531 | 0.061035 | 0.006409 | 0.003204 | 0.004272 | -0.001068 | 0.003204 | 0.001068 | -0.63629 | -0.46692 | -0.84686 | -1.268 | 0.013733 | 0.013733 | 0.022888 | 0.030518 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | 0.004272 | -0.34332 | -0.57678 | -0.94757 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | -0.89722 | 0.013733 | 0.009155
7162.2031 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.004272 | -0.6134 | -0.45319 | -0.86975 | -1.3 | 0.018311 | 0.009155 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -0.34332 | -0.59052 | -0.98419 | 0.013733 | 0.018311 | 0.022888 | 0.018311 | -0.75989 | 0.018311 | 0.022888
7163.9219 | 0.061035 | 0.006409 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.60883 | -0.43945 | -0.85602 | -1.2772 | 0.018311 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -0.33417 | -0.57678 | -0.9613 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.75989 | 0.018311 | 0.018311
7165.6875 | 0.061035 | 0.005341 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.61798 | -0.45776 | -0.84686 | -1.2772 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.004272 | 0.004272 | 0.004272 | -0.33875 | -0.59052 | -0.97046 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | -0.75989 | 0.022888 | 0.018311
7167.4531 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.003204 | -0.60425 | -0.46692 | -0.86975 | -1.2955 | 0.022888 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.001068 | 0.004272 | 0.002136 | 0.002136 | -0.33417 | -0.59509 | -0.97504 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -0.81024 | 0.022888 | 0.022888
7169.2031 | 0.045776 | 0.004272 | 0.001068 | 0.002136 | 0 | 0.001068 | 0.003204 | -0.61798 | -0.45776 | -0.85602 | -1.3046 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | -0.32959 | -0.59052 | -0.97504 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -0.71411 | 0.018311 | 0.018311
7170.9062 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.6134 | -0.43488 | -0.84228 | -1.2863 | 0.013733 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.005341 | 0.002136 | 0.003204 | 0.003204 | -0.33417 | -0.57678 | -0.96588 | 0.009155 | 0.018311 | 0.013733 | 0.018311 | -0.72784 | 0.018311 | 0.018311
7172.6719 | 0.076294 | 0.004272 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.001068 | -0.62714 | -0.44403 | -0.83771 | -1.2589 | 0.013733 | 0.018311 | 0.004578 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.32959 | -0.56763 | -0.94299 | 0.022888 | 0.018311 | 0.018311 | 0.022888 | -0.82855 | 0.022888 | 0.018311
7174.4375 | 0.045776 | 0.007477 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -0.61798 | -0.4715 | -0.85602 | -1.2863 | 0.018311 | 0.013733 | 0.013733 | 0.076294 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.001068 | -0.32959 | -0.58136 | -0.97504 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | -0.86517 | 0.018311 | 0.018311
7176.1875 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.62256 | -0.46234 | -0.85602 | -1.2817 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | -0.32044 | -0.57678 | -0.94757 | 0.018311 | 0.018311 | 0.022888 | 0.013733 | -0.97961 | 0.013733 | 0.022888
7177.8906 | 0.045776 | 0.005341 | 0.004272 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.6134 | -0.44403 | -0.83313 | -1.2726 | 0.027466 | 0.013733 | 0.018311 | 0.091553 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | -0.32044 | -0.56763 | -0.93842 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | -0.86975 | 0.018311 | 0.018311
7179.6562 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.60883 | -0.45776 | -0.84228 | -1.268 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | -0.32044 | -0.56763 | -0.95215 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | -0.89264 | 0.009155 | 0.022888
7181.4219 | 0.061035 | 0.004272 | 0.001068 | 0.004272 | 0.001068 | 0.003204 | 0.004272 | -0.59509 | -0.43945 | -0.82398 | -1.268 | 0.022888 | 0.022888 | 0.018311 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.32501 | -0.5722 | -0.93842 | 0.013733 | 0.009155 | 0.018311 | 0.013733 | -0.88806 | 0.022888 | 0.022888
7183.1094 | 0.076294 | 0.006409 | 0.001068 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.59052 | -0.4303 | -0.84228 | -1.2863 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -0.31128 | -0.56305 | -0.95673 | 0.013733 | 0.013733 | 0.027466 | 0.018311 | -0.76904 | 0.027466 | 0.018311
7184.875 | 0.030518 | 0.006409 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.59509 | -0.43488 | -0.82398 | -1.2589 | 0.013733 | 0.009155 | 0.013733 | 0.061035 | 0.005341 | 0.001068 | 0.004272 | 0.003204 | 0.004272 | -0.31586 | -0.55847 | -0.93384 | 0.013733 | 0.022888 | 0.022888 | 0.022888 | -0.91553 | 0.018311 | 0.022888
7186.5625 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -0.59052 | -0.42114 | -0.84228 | -1.2772 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.31586 | -0.55847 | -0.95215 | 0.022888 | 0.018311 | 0.027466 | 0.018311 | -0.60883 | 0.018311 | 0.013733
7188.3281 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.60883 | -0.43488 | -0.81482 | -1.2497 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.003204 | -0.3067 | -0.54932 | -0.92926 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | -0.78278 | 0.018311 | 0.013733
7190.0156 | 0.030518 | 0.007477 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.59509 | -0.43488 | -0.84686 | -1.2817 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.001068 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | -0.3067 | -0.56305 | -0.95215 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.6958 | 0.022888 | 0.027466
7191.7812 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.003204 | -0.59052 | -0.42572 | -0.82855 | -1.2589 | 0.009155 | 0.022888 | 0.022888 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | -0.30212 | -0.54932 | -0.92926 | 0.022888 | 0.018311 | 0.022888 | 0.018311 | -0.75531 | 0.013733 | 0.027466
7193.5469 | 0.030518 | 0.005341 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | -0.60425 | -0.43488 | -0.82398 | -1.2405 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.004272 | -0.31586 | -0.54932 | -0.91553 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | -0.92926 | 0.022888 | 0.022888
7195.3125 | 0.061035 | 0.006409 | 0.002136 | 0 | 0.001068 | 0.003204 | 0.002136 | -0.60425 | -0.43945 | -0.82855 | -1.2543 | 0.013733 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | -0.31586 | -0.55847 | -0.93384 | 0.013733 | 0.013733 | 0.022888 | 0.009155 | -0.91095 | 0.013733 | 0.022888
7197 | 0.076294 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.61798 | -0.44403 | -0.82855 | -1.2543 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.001068 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.32501 | -0.55389 | -0.92468 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | -0.96588 | 0.013733 | 0.018311
7198.7656 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -0.59509 | -0.44403 | -0.85144 | -1.2863 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | 0.005341 | 0.003204 | -0.31586 | -0.5722 | -0.95673 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | -0.79651 | 0.018311 | 0.018311
7200.5469 | 0.061035 | 0.003204 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | -0.59052 | -0.4303 | -0.83313 | -1.2772 | 0.018311 | 0.027466 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | -0.31128 | -0.54932 | -0.93384 | 0.018311 | 0.013733 | 0.013733 | 0.022888 | -0.7782 | 0.018311 | 0.018311
7202.3125 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.61798 | -0.43488 | -0.82398 | -1.2634 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.30212 | -0.53558 | -0.91095 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | -0.97961 | 0.018311 | 0.022888
7203.9844 | 0.045776 | 0.006409 | 0.002136 | 0.004272 | -0.001068 | 0.002136 | 0.002136 | -0.60883 | -0.43945 | -0.85144 | -1.2863 | 0.013733 | 0.022888 | 0.018311 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.3067 | -0.55389 | -0.92926 | 0.009155 | 0.013733 | 0.018311 | 0.009155 | -0.71869 | 0.022888 | 0.027466
7205.75 | 0.045776 | 0.007477 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.62256 | -0.45776 | -0.84228 | -1.2772 | 0.009155 | 0.022888 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.30212 | -0.53558 | -0.91095 | 0.013733 | 0.018311 | 0.022888 | 0.018311 | -0.93384 | 0.022888 | 0.013733
7207.4375 | 0.045776 | 0.006409 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.63171 | -0.46234 | -0.8606 | -1.2817 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.30212 | -0.54474 | -0.92468 | 0.013733 | 0.022888 | 0.022888 | 0.018311 | -0.67749 | 0.018311 | 0.022888
7209.1719 | 0.061035 | 0.006409 | 0.002136 | 0.004272 | 0 | 0.001068 | 0.004272 | -0.63171 | -0.44403 | -0.82398 | -1.2634 | 0.013733 | 0.018311 | 0.022888 | 0.030518 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | 0.004272 | -0.29755 | -0.52185 | -0.90637 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | -0.86517 | 0.022888 | 0.018311
7210.875 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.004272 | -0.62714 | -0.45319 | -0.84228 | -1.2772 | 0.013733 | 0.009155 | 0.018311 | 0.091553 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.31128 | -0.54016 | -0.9201 | 0.013733 | 0.013733 | 0.027466 | 0.013733 | -0.9201 | 0.018311 | 0.018311
7212.6406 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.61798 | -0.45776 | -0.84686 | -1.2726 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.31128 | -0.54474 | -0.91553 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | -0.97046 | 0.018311 | 0.013733
7214.4062 | 0.091553 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.6134 | -0.44861 | -0.85602 | -1.2955 | 0.009155 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.004272 | -0.3067 | -0.54474 | -0.92468 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.74158 | 0.018311 | 0.022888
7216.1562 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.6134 | -0.44861 | -0.85144 | -1.3046 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | -0.29755 | -0.54474 | -0.93384 | 0.009155 | 0.018311 | 0.018311 | 0.013733 | -0.75073 | 0.018311 | 0.018311
7217.8594 | 0.061035 | 0.006409 | 0.005341 | 0.001068 | 0 | 0.003204 | 0.001068 | -0.62256 | -0.45319 | -0.82398 | -1.2634 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | -0.29755 | -0.51727 | -0.89722 | 0.013733 | 0.013733 | 0.018311 | 0.013733 | -0.93384 | 0.018311 | 0.022888
7219.625 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | -0.001068 | 0.003204 | 0.002136 | -0.60883 | -0.44861 | -0.84228 | -1.2817 | 0.018311 | 0.013733 | 0.022888 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | -0.30212 | -0.54016 | -0.9201 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | -0.81024 | 0.022888 | 0.018311
7221.3906 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.004272 | -0.60425 | -0.44403 | -0.85602 | -1.2909 | 0.018311 | 0.022888 | 0.018311 | 0.076294 | 0.002136 | 0.004272 | 0.004272 | 0.002136 | 0.004272 | -0.29755 | -0.53558 | -0.91553 | 0.018311 | 0.009155 | 0.013733 | 0.009155 | -0.77362 | 0.013733 | 0.013733
7223.125 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.004272 | 0.002136 | -0.62256 | -0.45776 | -0.85144 | -1.2726 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.3067 | -0.52643 | -0.89264 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.82398 | 0.018311 | 0.022888
7224.8281 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.46234 | -0.86517 | -1.2909 | 0.022888 | 0.018311 | 0.013733 | 0.015259 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.004272 | -0.31128 | -0.53101 | -0.91095 | 0.018311 | 0.013733 | 0.009155 | 0.022888 | -0.77362 | 0.018311 | 0.022888
7226.6094 | 0.045776 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.62714 | -0.46692 | -0.86975 | -1.3 | 0.009155 | 0.018311 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | -0.31128 | -0.54016 | -0.91095 | 0.013733 | 0.004578 | 0.022888 | 0.018311 | -0.8606 | 0.018311 | 0.009155
7228.375 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.004272 | -0.62256 | -0.45319 | -0.8606 | -1.3092 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.001068 | -0.31128 | -0.52643 | -0.90637 | 0.018311 | 0.009155 | 0.013733 | 0.018311 | -0.84228 | 0.018311 | 0.022888
7230.125 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.61798 | -0.43945 | -0.85602 | -1.3046 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.29297 | -0.51727 | -0.88806 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | -0.83313 | 0.022888 | 0.018311
7231.8281 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.62714 | -0.44861 | -0.86975 | -1.3138 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.3067 | -0.52643 | -0.90637 | 0.018311 | 0.013733 | 0.009155 | 0.027466 | -0.78278 | 0.022888 | 0.027466
7233.6094 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.63629 | -0.47607 | -0.86975 | -1.3046 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.004272 | 0.005341 | 0.003204 | 0.002136 | -0.3067 | -0.52643 | -0.89722 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -0.94757 | 0.018311 | 0.018311
7235.2969 | 0.061035 | 0.006409 | 0.004272 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.64545 | -0.47607 | -0.87433 | -1.3046 | 0.018311 | 0.009155 | 0.013733 | 0.030518 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.30212 | -0.52185 | -0.88806 | 0.022888 | 0.018311 | 0.022888 | 0.018311 | -0.90637 | 0.022888 | 0.018311
7237.0625 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | -0.61798 | -0.44861 | -0.8606 | -1.2863 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.005341 | 0.002136 | 0.003204 | -0.31128 | -0.53101 | -0.88348 | 0.004578 | 0.022888 | 0.018311 | 0.013733 | -0.98877 | 0.018311 | 0.022888
7238.7656 | 0.076294 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | 0.002136 | -0.62714 | -0.46234 | -0.88806 | -1.3184 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | -0.54474 | -0.91553 | 0.018311 | 0.022888 | 0.027466 | 0.022888 | -0.76446 | 0.018311 | 0.018311
7240.5312 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | -0.60425 | -0.44403 | -0.85602 | -1.2955 | 0.013733 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.002136 | -0.3067 | -0.53558 | -0.89722 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | -0.78735 | 0.018311 | 0.022888
7242.2969 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | 0.004272 | -0.60425 | -0.44861 | -0.8606 | -1.3 | 0.022888 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.31586 | -0.53558 | -0.89722 | 0.013733 | 0.027466 | 0.013733 | 0.018311 | -0.67291 | 0.013733 | 0.022888
7244 | 0.045776 | 0.005341 | 0.002136 | 0.001068 | -0.001068 | 0.003204 | 0.003204 | -0.62714 | -0.44861 | -0.84228 | -1.2772 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | -0.31128 | -0.52185 | -0.87433 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | -0.95215 | 0.022888 | 0.022888
7245.75 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0 | 0.003204 | -0.63629 | -0.46234 | -0.85144 | -1.2863 | 0.022888 | 0.013733 | 0.022888 | 0.030518 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.32501 | -0.54016 | -0.89722 | 0.013733 | 0.013733 | 0.013733 | 0.022888 | -0.97504 | 0.018311 | 0.018311
7247.5156 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.63171 | -0.45776 | -0.87433 | -1.3184 | 0.013733 | 0.009155 | 0.022888 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.32044 | -0.56305 | -0.92926 | 0.018311 | 0.018311 | 0.009155 | 0.018311 | -0.72784 | 0.018311 | 0.022888
7249.2812 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.002136 | -0.62256 | -0.46692 | -0.86975 | -1.3138 | 0.013733 | 0.004578 | 0.013733 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -0.30212 | -0.54474 | -0.92468 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -0.84686 | 0.018311 | 0.022888
7251.0625 | 0.076294 | 0.005341 | 0.001068 | 0.004272 | 0.001068 | 0.003204 | 0.001068 | -0.61798 | -0.45776 | -0.84228 | -1.2863 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.31586 | -0.54016 | -0.90179 | 0.018311 | 0.022888 | 0.018311 | 0.009155 | -0.92926 | 0.022888 | 0.022888
7252.75 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.62256 | -0.46692 | -0.86975 | -1.3 | 0.022888 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | -0.32501 | -0.55389 | -0.91095 | 0.009155 | 0.018311 | 0.009155 | 0.013733 | -0.82398 | 0.013733 | 0.022888
7254.5156 | 0.061035 | 0.005341 | 0.004272 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.60883 | -0.45319 | -0.8606 | -1.3046 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.32044 | -0.55389 | -0.92468 | 0.013733 | 0.009155 | 0.018311 | 0.022888 | -0.74616 | 0.013733 | 0.022888
7256.2812 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.003204 | 0.004272 | -0.61798 | -0.45776 | -0.85602 | -1.3 | 0.018311 | 0.022888 | 0.013733 | 0.015259 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | -0.32044 | -0.54932 | -0.91553 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.87433 | 0.022888 | 0.027466
7257.9688 | 0.076294 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.43945 | -0.84228 | -1.2955 | 0.018311 | 0.022888 | 0.022888 | 0.030518 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.32044 | -0.54016 | -0.89722 | 0.022888 | 0.022888 | 0.018311 | 0.013733 | -0.87891 | 0.018311 | 0.018311
7259.7344 | 0.030518 | 0.005341 | 0.001068 | 0.006409 | 0.001068 | 0.002136 | 0.002136 | -0.60425 | -0.44403 | -0.87433 | -1.3229 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.32044 | -0.56763 | -0.93384 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.63171 | 0.018311 | 0.027466
7261.5156 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.61798 | -0.45776 | -0.84228 | -1.2955 | 0.013733 | 0.027466 | 0.022888 | 0.076294 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.004272 | -0.31586 | -0.54474 | -0.91553 | 0.013733 | 0.022888 | 0.022888 | 0.022888 | -0.94299 | 0.027466 | 0.022888
7263.2656 | 0.061035 | 0.006409 | 0.002136 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | -0.62256 | -0.45319 | -0.86517 | -1.3138 | 0.013733 | 0.022888 | 0.022888 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.005341 | -0.32959 | -0.57678 | -0.94299 | 0.013733 | 0.018311 | 0.022888 | 0.013733 | -0.70496 | 0.022888 | 0.022888
7265.0156 | 0.076294 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | 0.004272 | 0.003204 | -0.61798 | -0.46234 | -0.85602 | -1.2955 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -0.32044 | -0.56763 | -0.93384 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | -0.99335 | 0.013733 | 0.018311
7266.7188 | 0.030518 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.62714 | -0.45319 | -0.85144 | -1.2909 | 0.018311 | 0.018311 | 0.013733 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | -0.33417 | -0.56763 | -0.9201 | 0.013733 | 0.009155 | 0.022888 | 0.018311 | -0.9201 | 0.022888 | 0.022888
7268.4688 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.64545 | -0.4715 | -0.88806 | -1.3184 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.33417 | -0.58136 | -0.95215 | 0.022888 | 0.018311 | 0.022888 | 0.013733 | -0.70038 | 0.018311 | 0.018311
7270.1562 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0.001068 | 0.002136 | 0.001068 | -0.65002 | -0.48065 | -0.87433 | -1.3229 | 0.018311 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | -0.32959 | -0.58136 | -0.95673 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -0.78278 | 0.018311 | 0.022888
7271.9219 | 0.015259 | 0.003204 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.63171 | -0.45776 | -0.8606 | -1.2955 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.32501 | -0.5722 | -0.92926 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | -0.90637 | 0.013733 | 0.022888
7273.6875 | 0.061035 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.62714 | -0.46234 | -0.88806 | -1.3367 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.33417 | -0.58136 | -0.95215 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | -0.81482 | 0.022888 | 0.013733
7275.4531 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -0.62256 | -0.45319 | -0.86517 | -1.3138 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.32501 | -0.56305 | -0.93384 | 0.013733 | 0.027466 | 0.022888 | 0.013733 | -0.64545 | 0.022888 | 0.022888
7277.1406 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.62256 | -0.45319 | -0.85144 | -1.2955 | 0.018311 | 0.013733 | 0.013733 | 0.045776 | 0.002136 | 0.002136 | 0.003204 | 0.003204 | 0.004272 | -0.32501 | -0.55847 | -0.91095 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | -0.94757 | 0.027466 | 0.027466
7278.9062 | 0.045776 | 0.005341 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -0.61798 | -0.45776 | -0.84686 | -1.2955 | 0.018311 | 0.004578 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.004272 | -0.32959 | -0.56763 | -0.92926 | 0.018311 | 0.018311 | 0.022888 | 0.027466 | -0.75531 | 0.027466 | 0.027466
7280.6719 | 0.030518 | 0.006409 | 0.001068 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.6134 | -0.46234 | -0.85144 | -1.3 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | 0.003204 | -0.33875 | -0.5722 | -0.93842 | 0.013733 | 0.018311 | 0.009155 | 0.013733 | -0.85602 | 0.022888 | 0.022888
7282.4375 | 0.061035 | 0.005341 | 0.005341 | 0.004272 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.44861 | -0.86517 | -1.3046 | 0.022888 | 0.013733 | 0.009155 | 0.076294 | 0.002136 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | -0.32501 | -0.5722 | -0.95215 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.7782 | 0.022888 | 0.013733
7284.1875 | 0.030518 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.001068 | 0.002136 | -0.60425 | -0.4303 | -0.8606 | -1.3046 | 0.013733 | 0.013733 | 0.013733 | 0.015259 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.32044 | -0.57678 | -0.95215 | 0.022888 | 0.018311 | 0.013733 | 0.018311 | -0.62256 | 0.018311 | 0.022888
7285.8906 | 0.076294 | 0.005341 | 0.004272 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.44403 | -0.86517 | -1.3092 | 0.018311 | 0.009155 | 0.027466 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.002136 | -0.31128 | -0.5722 | -0.95215 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | -0.75531 | 0.018311 | 0.022888
7287.6719 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | -0.001068 | 0.003204 | 0.003204 | -0.59967 | -0.43488 | -0.83771 | -1.2726 | 0.009155 | 0.013733 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.3067 | -0.54932 | -0.92926 | 0.018311 | 0.018311 | 0.013733 | 0.018311 | -0.87433 | 0.018311 | 0.022888
7289.4375 | 0.045776 | 0.005341 | 0.003204 | 0.001068 | 0 | 0.002136 | 0.003204 | -0.59052 | -0.44861 | -0.86517 | -1.3 | 0.018311 | 0.018311 | 0.009155 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.31128 | -0.55847 | -0.9613 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | -0.83313 | 0.022888 | 0.013733
7291.1875 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.59052 | -0.44861 | -0.85602 | -1.3 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.004272 | -0.29755 | -0.55389 | -0.95673 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | -0.66376 | 0.013733 | 0.013733
7292.8906 | 0.061035 | 0.006409 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.59052 | -0.44861 | -0.82398 | -1.2589 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -0.30212 | -0.54474 | -0.91553 | 0.022888 | 0.018311 | 0.013733 | 0.009155 | -0.98877 | 0.022888 | 0.027466
7294.6562 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.59509 | -0.43488 | -0.83313 | -1.2726 | 0.013733 | 0.022888 | 0.018311 | 0.076294 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.31586 | -0.54932 | -0.9201 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | -0.75531 | 0.027466 | 0.022888
7296.4062 | 0.076294 | 0.005341 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.59509 | -0.42114 | -0.83313 | -1.268 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.001068 | -0.31128 | -0.55389 | -0.9201 | 0.018311 | 0.022888 | 0.013733 | 0.013733 | -0.75531 | 0.022888 | 0.032043
7298.0938 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.001068 | 0.003204 | -0.59509 | -0.43488 | -0.81482 | -1.2451 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | -0.32044 | -0.54474 | -0.91553 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.94757 | 0.027466 | 0.018311
7299.8281 | 0.061035 | 0.005341 | 0.004272 | 0.004272 | 0 | 0.003204 | 0.004272 | -0.61798 | -0.45776 | -0.84228 | -1.268 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | -0.32501 | -0.56305 | -0.92926 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.89722 | 0.018311 | 0.018311
7301.5938 | 0.045776 | 0.006409 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.001068 | -0.62256 | -0.44861 | -0.85602 | -1.2817 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | -0.32044 | -0.5722 | -0.95215 | 0.009155 | 0.018311 | 0.022888 | 0.018311 | -0.79651 | 0.018311 | 0.018311
7303.3594 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | -0.6134 | -0.45776 | -0.86517 | -1.2863 | 0.013733 | 0.027466 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.005341 | 0.002136 | -0.31128 | -0.56763 | -0.95673 | 0.009155 | 0.013733 | 0.013733 | 0.018311 | -0.78735 | 0.018311 | 0.013733
7305.125 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.63171 | -0.45319 | -0.85602 | -1.2863 | 0.022888 | 0.018311 | 0.018311 | 0.091553 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | -0.30212 | -0.55847 | -0.94299 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | -0.76446 | 0.018311 | 0.018311
7306.8438 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.004272 | 0.002136 | -0.63171 | -0.4715 | -0.84686 | -1.268 | 0.018311 | 0.022888 | 0.027466 | 0.045776 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | -0.30212 | -0.53558 | -0.91553 | 0.013733 | 0.013733 | 0.018311 | 0.009155 | -0.89722 | 0.018311 | 0.018311
7308.6094 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.63629 | -0.4715 | -0.83313 | -1.268 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.002136 | 0.004272 | 0.005341 | 0.001068 | 0.002136 | -0.31586 | -0.54016 | -0.91553 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.98419 | 0.027466 | 0.018311
7310.3594 | 0.045776 | 0.006409 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.62256 | -0.43488 | -0.83313 | -1.2817 | 0.022888 | 0.013733 | 0.018311 | 0.061035 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.003204 | -0.31128 | -0.54474 | -0.91095 | 0.018311 | 0.018311 | 0.018311 | 0.013733 | -0.84228 | 0.013733 | 0.027466
7312.125 | 0.061035 | 0.004272 | 0.002136 | 0.005341 | 0.002136 | 0.001068 | 0.003204 | -0.6134 | -0.43945 | -0.84228 | -1.2817 | 0.013733 | 0.022888 | 0.013733 | 0.015259 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | -0.32959 | -0.55847 | -0.9201 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -0.97961 | 0.027466 | 0.018311
7313.8281 | 0.030518 | 0.006409 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.61798 | -0.44861 | -0.86975 | -1.3092 | 0.013733 | 0.013733 | 0.022888 | 0.091553 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.31586 | -0.5722 | -0.94299 | 0.009155 | 0.018311 | 0.018311 | 0.009155 | -0.71869 | 0.022888 | 0.022888
7315.5938 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.002136 | -0.62256 | -0.43945 | -0.84686 | -1.2772 | 0.009155 | 0.013733 | 0.018311 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.32501 | -0.55389 | -0.9201 | 0.022888 | 0.027466 | 0.018311 | 0.018311 | -0.78278 | 0.022888 | 0.022888
7317.3438 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.004272 | -0.60425 | -0.43945 | -0.85602 | -1.2955 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | -0.32501 | -0.56305 | -0.92468 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.91095 | 0.027466 | 0.018311
7319.0469 | 0.076294 | 0.005341 | 0.004272 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.61798 | -0.44861 | -0.8606 | -1.3 | 0.009155 | 0.013733 | 0.009155 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.32959 | -0.5722 | -0.93384 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | -0.9201 | 0.022888 | 0.022888
7320.8125 | 0.076294 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.6134 | -0.45776 | -0.87891 | -1.3184 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.32959 | -0.59052 | -0.9613 | 0.018311 | 0.018311 | 0.022888 | 0.022888 | -0.85144 | 0.018311 | 0.018311
7322.5781 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.61798 | -0.45319 | -0.85144 | -1.3046 | 0.018311 | 0.009155 | 0.013733 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -0.31586 | -0.56305 | -0.92926 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | -0.8194 | 0.009155 | 0.022888
7324.3281 | 0.091553 | 0.004272 | 0.004272 | 0.003204 | 0 | 0.002136 | 0.002136 | -0.59967 | -0.43945 | -0.86517 | -1.3046 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.002136 | 0.003204 | 0.004272 | 0.004272 | -0.31586 | -0.56763 | -0.94299 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | -0.70496 | 0.018311 | 0.022888
7326.0156 | 0.061035 | 0.006409 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.60425 | -0.44861 | -0.8606 | -1.3092 | 0.018311 | 0.022888 | 0.027466 | 0.091553 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | -0.32044 | -0.56305 | -0.93842 | 0.022888 | 0.018311 | 0.022888 | 0.018311 | -0.85602 | 0.022888 | 0.022888
7327.7812 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | -0.62714 | -0.46234 | -0.88806 | -1.3412 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.31128 | -0.58136 | -0.95673 | 0.013733 | 0.018311 | 0.009155 | 0.018311 | -0.65002 | 0.022888 | 0.018311
7329.5469 | 0.030518 | 0.004272 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.6134 | -0.45776 | -0.86517 | -1.3229 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -0.31128 | -0.56305 | -0.94299 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.67291 | 0.018311 | 0.022888
7331.3125 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | -0.6134 | -0.45776 | -0.85144 | -1.3 | 0.013733 | 0.013733 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.31128 | -0.54474 | -0.91553 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | -0.99335 | 0.022888 | 0.018311
7333.0156 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.001068 | 0.002136 | -0.61798 | -0.46234 | -0.86517 | -1.3184 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | -0.31128 | -0.55847 | -0.91553 | 0.013733 | 0.013733 | 0.018311 | 0.022888 | -0.72327 | 0.018311 | 0.022888
7334.7812 | 0.045776 | 0.004272 | 0.001068 | 0.003204 | -0.001068 | 0.002136 | 0.004272 | -0.60425 | -0.45319 | -0.83771 | -1.2726 | 0.009155 | 0.018311 | 0.027466 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | 0.001068 | -0.30212 | -0.54016 | -0.89264 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | -0.92926 | 0.018311 | 0.018311
7336.4688 | 0.076294 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.001068 | 0.003204 | -0.59967 | -0.44861 | -0.8606 | -1.3046 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | -0.32044 | -0.55847 | -0.92926 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.76446 | 0.013733 | 0.022888
7338.2344 | 0.061035 | 0.006409 | 0.003204 | 0.004272 | 0.001068 | 0.001068 | 0.002136 | -0.59509 | -0.43945 | -0.85144 | -1.2955 | 0.018311 | 0.013733 | 0.022888 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | -0.31586 | -0.56305 | -0.9201 | 0.022888 | 0.022888 | 0.018311 | 0.013733 | -0.68665 | 0.022888 | 0.013733
7339.9375 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.60883 | -0.46692 | -0.8606 | -1.3 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -0.30212 | -0.55847 | -0.93384 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | -0.74616 | 0.018311 | 0.022888
7341.7031 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.004272 | 0.001068 | -0.59509 | -0.43945 | -0.83313 | -1.268 | 0.018311 | 0.009155 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -0.31586 | -0.54474 | -0.91095 | 0.013733 | 0.022888 | 0.013733 | 0.022888 | -0.84686 | 0.018311 | 0.013733
7343.4062 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.60883 | -0.46692 | -0.85144 | -1.2863 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | -0.31128 | -0.55389 | -0.93384 | 0.027466 | 0.013733 | 0.013733 | 0.018311 | -0.79651 | 0.018311 | 0.022888
7345.1562 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | -0.001068 | 0.001068 | 0.002136 | -0.60425 | -0.44403 | -0.83771 | -1.2772 | 0.013733 | 0.018311 | 0.009155 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | -0.3067 | -0.55389 | -0.93384 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | -0.77362 | 0.018311 | 0.018311
7346.8594 | 0.076294 | 0.005341 | 0.002136 | 0.001068 | 0.001068 | 0.003204 | 0.003204 | -0.59052 | -0.4303 | -0.84228 | -1.2726 | 0.018311 | 0.027466 | 0.018311 | 0.061035 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | -0.31128 | -0.54932 | -0.92468 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | -0.7782 | 0.022888 | 0.022888
7348.625 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.004272 | -0.60883 | -0.45776 | -0.85144 | -1.2817 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | -0.3067 | -0.55847 | -0.93384 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | -0.84686 | 0.018311 | 0.022888
7350.375 | 0.045776 | 0.006409 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.004272 | -0.60883 | -0.45776 | -0.84228 | -1.2863 | 0.022888 | 0.013733 | 0.018311 | 0.030518 | 0.001068 | 0.004272 | 0.003204 | 0.004272 | 0.004272 | -0.29755 | -0.54474 | -0.9201 | 0.018311 | 0.022888 | 0.018311 | 0.022888 | -0.81482 | 0.013733 | 0.027466
7352.125 | 0.061035 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.005341 | 0.001068 | -0.6134 | -0.44403 | -0.84686 | -1.2817 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.29755 | -0.52185 | -0.89264 | 0.018311 | 0.018311 | 0.013733 | 0.013733 | -0.76446 | 0.018311 | 0.018311
7353.8281 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0 | 0.003204 | 0.002136 | -0.6134 | -0.44403 | -0.83313 | -1.2863 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.30212 | -0.52185 | -0.88348 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | -0.94757 | 0.018311 | 0.018311
7355.5938 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | -0.62714 | -0.46234 | -0.85144 | -1.2863 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -0.29755 | -0.54016 | -0.91095 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | -0.6546 | 0.027466 | 0.022888
7357.3438 | 0.076294 | 0.005341 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | -0.62256 | -0.44403 | -0.84228 | -1.2772 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | -0.29297 | -0.52185 | -0.89264 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | -0.89722 | 0.022888 | 0.022888
7359.1094 | 0.061035 | 0.005341 | 0.003204 | 0.001068 | 0.001068 | 0.003204 | 0.002136 | -0.63171 | -0.45776 | -0.85144 | -1.3 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | 0.003204 | -0.29755 | -0.53558 | -0.90179 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | -0.70038 | 0.022888 | 0.022888
7360.8125 | 0.061035 | 0.007477 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.61798 | -0.46692 | -0.84228 | -1.2909 | 0.018311 | 0.018311 | 0.022888 | 0.076294 | 0.003204 | 0.005341 | 0.002136 | 0.003204 | 0.003204 | -0.28839 | -0.5127 | -0.89264 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | -0.90637 | 0.022888 | 0.018311
7362.5781 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.6958 | -0.48981 | -0.72327 | -1.1719 | 0.027466 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.004272 | -0.18768 | -0.4715 | -0.8606 | 0.018311 | 0.009155 | 0.018311 | 0.013733 | -0.17395 | 0.022888 | 0.018311
7364.2656 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.004272 | -0.67291 | -0.49896 | -0.67291 | -1.0437 | 0.013733 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.005341 | 0.002136 | 0.004272 | -0.10529 | -0.3067 | -0.85144 | 0.022888 | 0.018311 | 0.022888 | 0.027466 | 1.1353 | 0.022888 | 0.022888
7366.0312 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.003204 | -0.67291 | -0.50354 | -0.81024 | -1.2222 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.005341 | 0.004272 | 0.003204 | 0.004272 | -0.33875 | -0.4715 | -0.7782 | 0.013733 | 0.027466 | 0.013733 | 0.022888 | 0.737 | 0.022888 | 0.022888
7367.7969 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | -0.001068 | 0.002136 | 0.002136 | 3.1586 | 0.47607 | 3.5889 | 7.1548 | 0.018311 | 0.018311 | 0.013733 | 0.045776 | 0.001068 | 0.002136 | 0.005341 | 0.004272 | 0.003204 | -0.091553 | -0.46234 | -0.89722 | 0.013733 | 0.013733 | 0.004578 | 0.018311 | -0.21973 | 0.022888 | 0.018311
7369.4844 | 0.030518 | 0.008545 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | 0.004272 | 0.78735 | -0.66834 | -0.89722 | 5.1544 | 0.022888 | 0.013733 | 0.013733 | 0.030518 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | 0.41657 | -0.10071 | -0.78278 | 0.018311 | 0.022888 | 0.013733 | 0.009155 | -1.1169 | 0.018311 | 0.018311
7371.2344 | 0.076294 | 0.005341 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.002136 | -1.7395 | 0.19684 | -3.1494 | -0.53558 | 0.018311 | 0.022888 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.79651 | 0.39825 | -0.42572 | 0.009155 | 0.018311 | 0.009155 | 0.018311 | -1.2863 | 0.022888 | 0.022888
7373 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -4.2389 | -0.45776 | -3.7079 | -1.2131 | 0.009155 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.91553 | 0.75073 | -0.054932 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | -1.3184 | 0.013733 | 0.022888
7374.75 | 0.045776 | 0.002136 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -3.1998 | 1.0666 | 0.71869 | -0.66376 | 0.004578 | 0.027466 | 0.022888 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | 0.84686 | 0.97504 | 0.25177 | 0.009155 | 0.027466 | 0.022888 | 0.022888 | -1.7166 | 0.018311 | 0.022888
7376.4375 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -2.0782 | 0.10529 | -0.77362 | -1.9226 | 0.009155 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.72327 | 1.0437 | 0.48523 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -1.8356 | 0.022888 | 0.013733
7378.1875 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 3.0808 | -2.1103 | 2.742 | 6.2439 | 0.027466 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | 0.72327 | 1.0941 | 0.65918 | 0.009155 | 0.027466 | 0.018311 | 0.018311 | -1.7532 | 0.022888 | 0.018311
7379.8906 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -6.2347 | -4.9667 | -10.7803 | -5.191 | 0.009155 | 0.018311 | 0.013733 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.8194 | 1.2222 | 0.82398 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | -1.442 | 0.018311 | 0.013733
7381.6562 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 1.149 | 2.1881 | -1.5427 | 4.3579 | 0.022888 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.91095 | 1.3504 | 1.03 | 0.022888 | 0.018311 | 0.009155 | 0.022888 | -1.2085 | 0.022888 | 0.032043
7383.3594 | 0.045776 | 0.004272 | 0.004272 | 0.002136 | 0 | 0.004272 | 0.004272 | -1.2268 | 0.55847 | -4.0421 | 1.9775 | 0.013733 | 0.009155 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.93384 | 1.4694 | 1.181 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | -1.181 | 0.022888 | 0.018311
7385.1094 | 0.045776 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.004272 | -2.4307 | 1.4191 | -5.1361 | -2.2293 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.90637 | 1.5152 | 1.2955 | 0.018311 | 0.013733 | 0.022888 | 0.022888 | -0.94299 | 0.022888 | 0.022888
7386.875 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -2.504 | -0.39368 | -2.9755 | -1.2726 | 0.018311 | 0.018311 | 0.013733 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.88348 | 1.5198 | 1.3321 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | -1.0941 | 0.018311 | 0.022888
7388.5781 | 0.061035 | 0.005341 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | -2.3117 | -0.56763 | -5.6442 | -3.598 | 0.013733 | 0.018311 | 0.013733 | 0.076294 | 0.003204 | 0.003204 | 0.005341 | 0.003204 | 0.004272 | 0.91553 | 1.6022 | 1.4786 | 0.018311 | 0.013733 | 0.013733 | 0.022888 | -1.0574 | 0.027466 | 0.013733
7390.3281 | 0.061035 | 0.006409 | 0.004272 | 0.002136 | 0 | 0.003204 | 0.001068 | -4.7974 | -1.5289 | -7.7042 | -8.5327 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.8194 | 1.5839 | 1.5244 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -1.1581 | 0.022888 | 0.022888
7392.0781 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.003204 | -2.504 | -0.37537 | -3.4607 | -5.7724 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | 0.65918 | 1.561 | 1.6113 | 0.022888 | 0.013733 | 0.018311 | 0.022888 | -1.5198 | 0.013733 | 0.022888
7393.7812 | 0.045776 | 0.005341 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 1.0529 | 0.07782 | 1.0666 | 1.3321 | 0.022888 | 0.018311 | 0.018311 | 0.076294 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | 0.004272 | 0.54932 | 1.4603 | 1.6022 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | -1.4786 | 0.018311 | 0.027466
7395.5312 | 0.061035 | 0.005341 | 0.002136 | 0.004272 | -0.001068 | 0.003204 | 0.002136 | 0.4303 | 0.34332 | 1.0391 | 2.0279 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.002136 | 0.004272 | 0.004272 | 0.003204 | 0.004272 | 0.48065 | 1.3687 | 1.5884 | 0.018311 | 0.018311 | 0.022888 | 0.022888 | -1.5381 | 0.027466 | 0.018311
7397.2969 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.002136 | -0.63171 | -0.46234 | -2.5864 | -1.149 | 0.018311 | 0.022888 | 0.013733 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.40741 | 1.2955 | 1.5564 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | -1.6251 | 0.018311 | 0.022888
7399.0625 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.001068 | -0.75989 | -0.018311 | -1.3229 | -1.3092 | 0.018311 | 0.018311 | 0.018311 | 0.091553 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 0.36621 | 1.1902 | 1.4923 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | -1.5152 | 0.018311 | 0.022888
7400.7656 | 0.045776 | 0.005341 | 0.001068 | 0.004272 | 0 | 0.004272 | 0.003204 | -0.81482 | -0.15564 | -2.1332 | -2.3987 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | 0.33417 | 1.1398 | 1.4648 | 0.018311 | 0.018311 | 0.013733 | 0.022888 | -1.6571 | 0.022888 | 0.022888
7402.5312 | 0.076294 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.737 | -0.3891 | -2.6917 | -3.7079 | 0.013733 | 0.018311 | 0.022888 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.27924 | 1.0666 | 1.4236 | 0.018311 | 0.022888 | 0.018311 | 0.013733 | -1.4511 | 0.022888 | 0.032043
7404.2969 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | -0.001068 | 0.002136 | 0.003204 | -0.73242 | -0.62714 | -2.8152 | -3.9917 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.22888 | 0.97961 | 1.3367 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | -1.236 | 0.022888 | 0.013733
7405.9844 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.002136 | -0.2655 | -0.086975 | 1.7899 | 0.32501 | 0.018311 | 0.018311 | 0.022888 | 0.030518 | 0.003204 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.24719 | 0.92926 | 1.2955 | 0.018311 | 0.018311 | 0.013733 | 0.027466 | -1.0895 | 0.022888 | 0.018311
7407.7344 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | 0.002136 | -1.0208 | -0.61798 | -3.2227 | -3.3371 | 0.013733 | 0.013733 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.2243 | 0.87891 | 1.2405 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -1.0437 | 0.018311 | 0.013733
7409.4219 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -2.8931 | -0.94299 | -3.479 | -5.6625 | 0.013733 | 0.009155 | 0.009155 | 0.076294 | 0.002136 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.15106 | 0.84228 | 1.2131 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | -1.2589 | 0.027466 | 0.022888
7411.2031 | 0.045776 | 0.006409 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | 0.003204 | -1.4145 | -0.6546 | -2.092 | -4.5776 | 0.022888 | 0.027466 | 0.022888 | 0.045776 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.041199 | 0.70038 | 1.1124 | 0.013733 | 0.013733 | 0.013733 | 0.013733 | 0.42114 | 0.018311 | 0.013733
7412.9688 | 0.045776 | 0.005341 | 0.005341 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | -0.70038 | -0.53101 | -0.59967 | -3.4515 | 0.018311 | 0.018311 | 0.022888 | 0.076294 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | -0.013733 | 0.59967 | 1.0162 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.94299 | 0.018311 | 0.027466
7414.6719 | 0.045776 | 0.006409 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | -0.59967 | -0.48065 | -0.6546 | -3.3234 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.004272 | 0.002136 | -0.068665 | 0.50354 | 0.95215 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | 0.90637 | 0.018311 | 0.013733
7416.4219 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -1.1719 | -0.93842 | -3.1128 | -5.2094 | 0.013733 | 0.022888 | 0.013733 | 0.045776 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.005341 | -0.11444 | 0.40283 | 0.82855 | 0.018311 | 0.013733 | 0.027466 | 0.022888 | 0.75073 | 0.022888 | 0.018311
7418.1094 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.002136 | 0.003204 | -0.12817 | -0.013733 | -0.40741 | -3.8406 | 0.022888 | 0.018311 | 0.018311 | 0.076294 | 0.002136 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | -0.13733 | 0.30212 | 0.68665 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | 0.76904 | 0.027466 | 0.032043
7419.875 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.69122 | -0.62256 | -0.35248 | -2.2705 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | -0.09613 | 0.28839 | 0.62256 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | 0.84686 | 0.018311 | 0.022888
7421.6406 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | -0.002136 | 0.002136 | 0.004272 | 0.22888 | 0.41199 | 6.5918 | 3.035 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.005341 | 0.002136 | 0.002136 | -0.24261 | 0.1831 | 0.52185 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | 0.4715 | 0.022888 | 0.018311
7423.4062 | 0.076294 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 1.1032 | -0.63629 | -1.2405 | 1.5335 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.24261 | 0.059509 | 0.3891 | 0.013733 | 0.013733 | 0.022888 | 0.018311 | 0.6958 | 0.022888 | 0.018311
7425.1094 | 0.076294 | 0.004272 | 0.004272 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | 3.1174 | 1.2772 | -2.1469 | 2.8427 | 0.013733 | 0.013733 | 0.013733 | 0.045776 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.003204 | -0.09613 | 0.032043 | 0.32501 | 0.018311 | 0.022888 | 0.022888 | 0.022888 | 0.41199 | 0.027466 | 0.022888
7426.875 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 1.2405 | 0.39825 | -3.2501 | 1.2039 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.001068 | 0.004272 | 0.050354 | 0.16022 | 0.34332 | 0.022888 | 0.018311 | 0.018311 | 0.022888 | 0.32501 | 0.022888 | 0.022888
7428.5781 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | 0.33875 | 0.16937 | -4.8843 | -0.53101 | 0.013733 | 0.009155 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | 0.1236 | 0.2655 | 0.39368 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 0.53101 | 0.018311 | 0.027466
7430.3281 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | 0.001068 | 0.002136 | 0.003204 | -0.10529 | 0.041199 | -5.4565 | -2.3804 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | 0.15564 | 0.34332 | 0.45776 | 0.009155 | 0.013733 | 0.018311 | 0.018311 | 0.49439 | 0.022888 | 0.027466
7432.0938 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.34332 | -0.086975 | -5.3925 | -3.9871 | 0.027466 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.002136 | 0.004272 | 0.13733 | 0.39368 | 0.49439 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | 0.32959 | 0.027466 | 0.027466
7433.7969 | 0.030518 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.001068 | 0.002136 | -2.1835 | -0.86975 | -6.9168 | -6.9077 | 0.009155 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.005341 | -0.1236 | 0.32959 | 0.37994 | 0.018311 | 0.013733 | 0.013733 | 0.018311 | -0.29297 | 0.022888 | 0.022888
7435.5625 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0 | 0.004272 | 0.001068 | -1.5884 | -0.58136 | -5.7632 | -7.196 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -0.018311 | 0.26093 | 0.52185 | 0.022888 | 0.027466 | 0.018311 | 0.022888 | -0.56763 | 0.018311 | 0.013733
7437.3125 | 0.061035 | 0.005341 | 0.005341 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.97046 | -0.71869 | -4.4083 | -5.8594 | 0.013733 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.004272 | -0.036621 | 0.18768 | 0.39825 | 0.018311 | 0.013733 | 0.018311 | 0.013733 | -0.6134 | 0.022888 | 0.018311
7439.0156 | 0.076294 | 0.004272 | 0.003204 | 0.003204 | 0 | 0.003204 | 0.003204 | -0.6958 | -0.52643 | -3.5294 | -5.3055 | 0.013733 | 0.018311 | 0.018311 | 0.076294 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.032043 | 0.23804 | 0.39825 | 0.013733 | 0.013733 | 0.009155 | 0.018311 | -0.67749 | 0.022888 | 0.018311
7440.7812 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.003204 | -0.64545 | -0.39825 | -3.4744 | -5.278 | 0.018311 | 0.022888 | 0.013733 | 0.076294 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | 0.013733 | 0.19226 | 0.3067 | 0.018311 | 0.022888 | 0.018311 | 0.018311 | -0.59967 | 0.022888 | 0.022888
7442.4688 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.64087 | -0.40283 | -3.5522 | -5.365 | 0.013733 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.018311 | 0.21973 | 0.24261 | 0.022888 | 0.018311 | 0.018311 | 0.009155 | 1.5472 | 0.022888 | 0.022888
7444.2188 | 0.076294 | 0.006409 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | -0.5722 | -0.27466 | -2.7283 | -4.7516 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.005341 | 0.003204 | 0.003204 | 0.041199 | 0.22888 | 0.27924 | 0.022888 | 0.018311 | 0.022888 | 0.009155 | 1.7578 | 0.018311 | 0.022888
7445.9688 | 0.061035 | 0.005341 | 0.002136 | 0.004272 | 0.001068 | 0.004272 | 0.003204 | -0.51727 | 0.09613 | -2.5864 | -4.6783 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.005341 | 0.002136 | 0.004272 | 0.003204 | 0.064087 | 0.22888 | 0.27924 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 1.6846 | 0.018311 | 0.022888
7447.6719 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.46234 | -0.42572 | -2.5131 | -4.5456 | 0.009155 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.004272 | 0.002136 | 0.004272 | 0.002136 | 0.10529 | 0.27466 | 0.33875 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 1.2222 | 0.022888 | 0.022888
7449.4375 | 0.030518 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.42572 | -0.29297 | -2.0737 | -4.1931 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | 0.005341 | 0.10529 | 0.28381 | 0.34332 | 0.013733 | 0.013733 | 0.009155 | 0.013733 | 1.1169 | 0.032043 | 0.022888
7451.1875 | 0.091553 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.003204 | -0.41657 | 0.39825 | -1.7944 | -4.0054 | 0.018311 | 0.022888 | 0.018311 | 0.061035 | 0.004272 | 0.005341 | 0.003204 | 0.003204 | 0.002136 | 0.10986 | 0.30212 | 0.37994 | 0.027466 | 0.022888 | 0.013733 | 0.018311 | 0.27466 | 0.027466 | 0.022888
7452.875 | 0.091553 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | 0 | -0.42114 | -0.35706 | -2.0782 | -4.0878 | 0.013733 | 0.018311 | 0.018311 | 0.076294 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.10986 | 0.30212 | 0.38452 | 0.018311 | 0.018311 | 0.022888 | 0.018311 | 0.17853 | 0.018311 | 0.018311
7454.6562 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.002136 | -0.39368 | -0.47607 | -1.8631 | -3.8635 | 0.013733 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | 0.086975 | 0.30212 | 0.37537 | 0.022888 | 0.013733 | 0.022888 | 0.018311 | 0.35706 | 0.013733 | 0.027466
7456.3594 | 0.076294 | 0.005341 | 0.002136 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | -0.32501 | -0.23804 | -1.5106 | -3.5889 | 0.018311 | 0.009155 | 0.022888 | 0.030518 | 0.004272 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | 0.022888 | 0.32501 | 0.25635 | 0.022888 | 0.018311 | 0.018311 | 0.013733 | 0.3479 | 0.022888 | 0.022888
7458.125 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.37537 | -0.42114 | -1.5152 | -3.4882 | 0.022888 | 0.018311 | 0.027466 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.002136 | 0.004272 | 0.11444 | 0.32044 | 0.40283 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.35248 | 0.022888 | 0.027466
7459.8281 | 0.076294 | 0.005341 | 0.001068 | 0.002136 | 0.001068 | 0.005341 | 0.001068 | -0.38452 | -0.39368 | -1.4282 | -3.3646 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.004272 | 0.002136 | 0.004272 | 0.004272 | 0.10071 | 0.31586 | 0.3891 | 0.009155 | 0.018311 | 0.018311 | 0.018311 | 0.48981 | 0.027466 | 0.018311
7461.5938 | 0.076294 | 0.004272 | 0.004272 | 0.004272 | 0 | 0.004272 | 0.003204 | -0.38452 | -0.3891 | -1.2909 | -3.1952 | 0.022888 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.10071 | 0.3067 | 0.40283 | 0.013733 | 0.018311 | 0.018311 | 0.013733 | -0.018311 | 0.027466 | 0.022888
7463.2812 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -0.39368 | -0.41657 | -1.2039 | -3.0487 | 0.009155 | 0.018311 | 0.018311 | 0.045776 | 0.002136 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.064087 | 0.30212 | 0.39825 | 0.013733 | 0.027466 | 0.013733 | 0.018311 | 0.42114 | 0.018311 | 0.022888
7465.0469 | 0.061035 | 0.004272 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | -0.38452 | -0.37994 | -1.1261 | -2.9022 | 0.009155 | 0.022888 | 0.018311 | 0.045776 | 0.003204 | 0.003204 | 0.005341 | 0.002136 | 0.003204 | 0.041199 | 0.28839 | 0.39825 | 0.018311 | 0.018311 | 0.018311 | 0.018311 | 0.52185 | 0.018311 | 0.018311
7466.7969 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.37994 | -0.38452 | -1.0071 | -2.7512 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.005341 | 0.003204 | 0.004272 | 0.003204 | 0.004578 | 0.25177 | 0.36621 | 0.013733 | 0.022888 | 0.022888 | 0.009155 | 0.78278 | 0.022888 | 0.022888
7468.5625 | 0.061035 | 0.004272 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | 0.003204 | -0.3891 | -0.40283 | -1.0025 | -2.655 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -0.018311 | 0.23346 | 0.32044 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.77362 | 0.018311 | 0.022888
7470.2656 | 0.061035 | 0.003204 | 0.002136 | 0.003204 | -0.001068 | 0.002136 | 0.004272 | -0.41657 | -0.39825 | -0.93384 | -2.536 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | -0.018311 | 0.2243 | 0.33417 | 0.009155 | 0.018311 | 0.022888 | 0.018311 | 0.54932 | 0.027466 | 0.027466
7472 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0 | 0.003204 | 0.004272 | -0.42572 | -0.42572 | -0.9201 | -2.4673 | 0.018311 | 0.013733 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.001068 | 0.002136 | -0.036621 | 0.17395 | 0.27924 | 0.022888 | 0.013733 | 0.022888 | 0.018311 | 0.70038 | 0.018311 | 0.022888
7473.75 | 0.076294 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | 0.004272 | 0.004272 | -0.41657 | -0.42572 | -0.85602 | -2.3666 | 0.018311 | 0.022888 | 0.018311 | 0.091553 | 0.003204 | 0.004272 | 0.004272 | 0.005341 | 0.003204 | -0.050354 | 0.15106 | 0.25635 | 0.018311 | 0.018311 | 0.022888 | 0.027466 | 0.59967 | 0.018311 | 0.027466
7475.4531 | 0.076294 | 0.004272 | 0.004272 | 0.003204 | 0 | 0.004272 | 0.003204 | -0.42572 | -0.39825 | -0.80566 | -2.2568 | 0.018311 | 0.022888 | 0.013733 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.004272 | 0.004272 | -0.059509 | 0.14191 | 0.23804 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | 0.35248 | 0.032043 | 0.022888
7477.2188 | 0.061035 | 0.004272 | 0.002136 | 0.005341 | -0.001068 | 0.003204 | 0.002136 | -0.43945 | -0.40741 | -0.82855 | -2.2064 | 0.009155 | 0.013733 | 0.013733 | 0.061035 | 0.002136 | 0.004272 | 0.004272 | 0.004272 | 0.004272 | -0.082397 | 0.091553 | 0.17853 | 0.018311 | 0.018311 | 0.027466 | 0.022888 | 0.36621 | 0.022888 | 0.022888
7478.9844 | 0.061035 | 0.005341 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.002136 | -0.43945 | -0.66834 | -0.79193 | -2.0874 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.005341 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | -0.10986 | 0.068665 | 0.16479 | 0.013733 | 0.018311 | 0.013733 | 0.013733 | 0.10986 | 0.018311 | 0.018311
7480.7344 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.001068 | 0.002136 | -0.43945 | -0.55389 | -1.1353 | -2.2888 | 0.018311 | 0.013733 | 0.018311 | 0.076294 | 0.002136 | 0.001068 | 0.004272 | 0.004272 | 0.003204 | -0.10529 | 0.086975 | 0.09613 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | -2.7603 | 0.018311 | 0.018311
7482.4844 | 0.045776 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.001068 | 0.002136 | -0.43488 | -0.43945 | -1.0391 | -2.2568 | 0.018311 | 0.009155 | 0.022888 | 0.076294 | 0.004272 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -0.13733 | 0.036621 | 0.064087 | 0.018311 | 0.013733 | 0.018311 | 0.022888 | -0.87433 | 0.022888 | 0.018311
7484.25 | 0.061035 | 0.005341 | 0.002136 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | -0.40741 | -0.44403 | -0.45319 | -1.799 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.005341 | 0.004272 | -0.14648 | 0.009155 | 0.045776 | 0.013733 | 0.022888 | 0.027466 | 0.018311 | -0.52185 | 0.018311 | 0.018311
7485.9531 | 0.076294 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.004272 | 0.005341 | -0.44861 | -0.29755 | -0.79193 | -1.9089 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | -0.14648 | -0.032043 | -0.004578 | 0.022888 | 0.013733 | 0.022888 | 0.022888 | -0.33875 | 0.018311 | 0.027466
7487.7188 | 0.076294 | 0.005341 | 0.004272 | 0.003204 | 0 | 0.004272 | 0.003204 | -0.46692 | -0.82398 | -0.85144 | -1.8585 | 0.013733 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.004272 | 0.002136 | 0.005341 | 0.003204 | -0.15106 | -0.036621 | -0.027466 | 0.022888 | 0.018311 | 0.018311 | 0.013733 | -0.26093 | 0.018311 | 0.018311
7489.4219 | 0.076294 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.004272 | -0.46234 | -0.53558 | -0.78735 | -1.799 | 0.013733 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0.002136 | 0.002136 | 0.004272 | 0.003204 | -0.15106 | -0.041199 | -0.009155 | 0.013733 | 0.022888 | 0.013733 | 0.022888 | -0.4303 | 0.022888 | 0.027466
7491.1875 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.50812 | 0.032043 | -0.3479 | -1.5152 | 0.022888 | 0.022888 | 0.018311 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.004272 | -0.21515 | -0.091553 | -0.082397 | 0.013733 | 0.018311 | 0.027466 | 0.018311 | -0.16022 | 0.018311 | 0.022888
7492.9531 | 0.10681 | 0.005341 | 0.002136 | 0.003204 | 0 | 0.002136 | 0.003204 | -0.61798 | -0.70038 | -1.2268 | -2.0508 | 0.013733 | 0.013733 | 0.018311 | 0.091553 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | -0.20599 | -0.1236 | -0.068665 | 0.013733 | 0.013733 | 0.018311 | 0.018311 | -0.13733 | 0.022888 | 0.022888
7494.6562 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.003204 | 0.003204 | -0.50354 | -0.44403 | -0.65002 | -1.6891 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | 0.004272 | -0.32501 | -0.20599 | -0.10071 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 0.1236 | 0.018311 | 0.027466
7496.4062 | 0.076294 | 0.005341 | 0.004272 | 0.003204 | 0.001068 | 0.002136 | 0.004272 | -0.51727 | -0.48065 | -0.66834 | -1.6342 | 0.027466 | 0.018311 | 0.018311 | 0.061035 | 0.001068 | 0.004272 | 0.003204 | 0.005341 | 0.003204 | -0.27466 | -0.24719 | -0.19684 | 0.018311 | 0.022888 | 0.022888 | 0.013733 | 0.10071 | 0.018311 | 0.022888
7498.0938 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -0.50354 | -0.42572 | -0.64545 | -1.561 | 0.018311 | 0.018311 | 0.009155 | 0.091553 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.005341 | -0.25177 | -0.24261 | -0.23346 | 0.022888 | 0.018311 | 0.018311 | 0.013733 | 0.036621 | 0.022888 | 0.018311
7499.875 | 0.076294 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.004272 | -0.47607 | -0.36163 | -0.57678 | -1.4694 | 0.013733 | 0.018311 | 0.022888 | 0.030518 | 0.003204 | 0.004272 | 0.004272 | 0.002136 | 0.003204 | -0.22888 | -0.25177 | -0.26093 | 0.022888 | 0.013733 | 0.027466 | 0.022888 | -0.20142 | 0.022888 | 0.018311
7501.5625 | 0.061035 | 0.004272 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -0.4715 | -0.40741 | -0.64087 | -1.4786 | 0.013733 | 0.027466 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.005341 | 0.002136 | 0.004272 | -0.22888 | -0.2655 | -0.28839 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | -0.3067 | 0.022888 | 0.018311
7503.3281 | 0.061035 | 0.006409 | 0.004272 | 0.002136 | 0.002136 | 0.003204 | 0.002136 | -0.37994 | -0.31128 | -0.69122 | -1.561 | 0.018311 | 0.022888 | 0.022888 | 0.030518 | 0.003204 | 0.003204 | 0.004272 | 0.004272 | 0.003204 | -0.16937 | -0.29755 | -0.39368 | 0.018311 | 0.018311 | 0.018311 | 0.022888 | 0.40741 | 0.027466 | 0.013733
7505.0938 | 0.076294 | 0.50095 | -0.4924 | -0.19653 | -0.098267 | -0.27344 | -0.16449 | 0.09613 | 0.009155 | 0.073242 | 0.036621 | -0.15106 | -0.15106 | -0.064087 | 0.091553 | 0.001068 | -0.22858 | -0.058746 | -0.18158 | -0.10254 | 0.050354 | 0.086975 | 0.027466 | -0.14648 | -0.15106 | -0.12817 | -0.073242 | 0.83313 | 0.018311 | 0.027466
7506.8594 | 0.030518 | 0.4924 | -0.48599 | -0.20081 | -0.13351 | -0.28519 | -0.1709 | 0.10529 | 0.068665 | 0.14191 | 0.073242 | -0.11444 | -0.18768 | -0.10071 | 0.076294 | -0.033112 | -0.23498 | -0.042725 | -0.18051 | -0.13031 | 0.086975 | 0.1236 | 0.082397 | -0.10986 | -0.10986 | -0.15106 | -0.086975 | -0.65918 | 0.022888 | 0.022888
7508.5625 | 0.061035 | 0.50201 | -0.48065 | -0.18692 | -0.14633 | -0.25528 | -0.17731 | 0.018311 | -0.064087 | 0.09613 | -0.004578 | -0.07782 | -0.14191 | -0.054932 | 0.061035 | -0.03418 | -0.23392 | -0.046997 | -0.16022 | -0.13138 | 0.009155 | 0.082397 | -0.073242 | -0.059509 | -0.064087 | -0.13275 | -0.073242 | -0.78278 | 0.018311 | 0.027466
7510.3281 | 0.061035 | 0.49347 | -0.47852 | -0.18585 | -0.13779 | -0.26703 | -0.15488 | 0.10529 | 0.032043 | 0.054932 | 0.045776 | -0.16022 | -0.15106 | -0.054932 | 0.045776 | -0.041656 | -0.22644 | -0.049133 | -0.1709 | -0.14206 | 0.045776 | 0.091553 | 0.022888 | -0.15106 | -0.11902 | -0.13733 | -0.091553 | -0.89264 | 0.018311 | 0.022888
7512.0781 | 0.045776 | 0.46143 | -0.46997 | -0.21042 | -0.14633 | -0.23819 | -0.16769 | 0 | -0.13275 | -0.027466 | -0.027466 | -0.10071 | -0.12817 | -0.013733 | 0.076294 | -0.028839 | -0.23071 | -0.03418 | -0.16342 | -0.13245 | -0.009155 | -0.004578 | -0.12817 | -0.10529 | -0.091553 | -0.09613 | -0.022888 | -0.16479 | 0.018311 | 0.018311
7513.8281 | 0.061035 | 0.47745 | -0.47638 | -0.20401 | -0.14099 | -0.25742 | -0.17303 | 0.032043 | -0.050354 | 0.10529 | 0.004578 | -0.073242 | -0.16022 | -0.032043 | 0.061035 | -0.036316 | -0.23498 | -0.035248 | -0.15488 | -0.13779 | 0.009155 | 0.050354 | -0.082397 | -0.064087 | -0.050354 | -0.12817 | -0.082397 | -0.27466 | 0.013733 | 0.018311
7515.5938 | 0.076294 | 0.4924 | -0.47531 | -0.19119 | -0.14954 | -0.25635 | -0.15274 | 0.032043 | -0.013733 | 0.027466 | 0.018311 | -0.1236 | -0.16022 | -0.068665 | 0.061035 | -0.05661 | -0.24139 | -0.049133 | -0.15915 | -0.13245 | 0.059509 | 0.11444 | 0 | -0.10986 | -0.10529 | -0.15564 | -0.082397 | 0.10986 | 0.036621 | -0.091553
7517.2812 | 0.061035 | 0.48492 | -0.47852 | -0.19546 | -0.15488 | -0.28091 | -0.16556 | 0.1236 | 0.10071 | 0.19226 | 0.10529 | -0.091553 | -0.19684 | -0.09613 | 0.076294 | -0.05661 | -0.24033 | -0.048065 | -0.16449 | -0.1442 | 0.086975 | 0.16022 | 0.073242 | -0.11902 | -0.09613 | -0.16937 | -0.11444 | -0.018311 | 0.036621 | -0.027466
7519.0469 | 0.045776 | 0.48492 | -0.45822 | -0.18692 | -0.1442 | -0.24246 | -0.16663 | -0.013733 | -0.11902 | -0.032043 | -0.022888 | -0.11444 | -0.11902 | -0.036621 | 0.045776 | -0.045929 | -0.23285 | -0.032043 | -0.15488 | -0.13565 | -0.004578 | 0.027466 | -0.10071 | -0.10529 | -0.086975 | -0.10986 | -0.050354 | 0.09613 | 0.027466 | -0.09613
7520.75 | 0.061035 | 0.47531 | -0.47424 | -0.18799 | -0.13245 | -0.24994 | -0.15595 | 0.036621 | -0.041199 | 0.10529 | -0.004578 | -0.11902 | -0.10529 | -0.032043 | 0.045776 | -0.032043 | -0.23712 | -0.037384 | -0.16342 | -0.13992 | 0.041199 | 0.07782 | -0.10529 | -0.10986 | -0.1236 | -0.10071 | -0.041199 | 0.045776 | 0.036621 | -0.11444
7522.5 | 0.061035 | 0.4689 | -0.48492 | -0.20615 | -0.14847 | -0.27557 | -0.16556 | 0.027466 | -0.045776 | 0.11902 | -0.009155 | -0.086975 | -0.14191 | -0.041199 | 0.061035 | -0.053406 | -0.24353 | -0.041656 | -0.16556 | -0.12817 | 0.004578 | 0.041199 | -0.050354 | -0.050354 | -0.064087 | -0.12817 | -0.064087 | -0.022888 | 0.041199 | -0.064087
7524.2656 | 0.045776 | 0.47958 | -0.46677 | -0.19546 | -0.15167 | -0.26169 | -0.15381 | 0.09613 | 0.018311 | 0.073242 | 0.059509 | -0.1236 | -0.16937 | -0.086975 | 0.061035 | -0.061951 | -0.24246 | -0.049133 | -0.1506 | -0.1506 | 0.050354 | 0.11902 | 0.032043 | -0.13275 | -0.13733 | -0.13733 | -0.10071 | 0.073242 | 0.032043 | -0.082397
7526.0156 | 0.061035 | 0.4924 | -0.47424 | -0.19653 | -0.15167 | -0.28305 | -0.16876 | 0.064087 | 0.013733 | 0.041199 | 0.054932 | -0.07782 | -0.20142 | -0.10071 | 0.061035 | -0.060883 | -0.25207 | -0.03952 | -0.1709 | -0.13779 | -0.013733 | 0.036621 | 0.018311 | -0.082397 | -0.07782 | -0.16937 | -0.10529 | -0.032043 | 0.022888 | -0.018311
7527.7656 | 0.061035 | 0.47424 | -0.48172 | -0.20721 | -0.14099 | -0.25742 | -0.18585 | 0.10529 | 0.064087 | 0.1831 | 0.07782 | -0.10529 | -0.19226 | -0.082397 | 0.061035 | -0.048065 | -0.23819 | -0.045929 | -0.17517 | -0.14099 | 0.054932 | 0.1236 | 0.036621 | -0.10071 | -0.091553 | -0.15106 | -0.091553 | -0.059509 | 0.054932 | -0.050354
7529.4531 | 0.061035 | 0.45929 | -0.45929 | -0.20294 | -0.15381 | -0.2446 | -0.1741 | 0.022888 | -0.10986 | -0.022888 | -0.027466 | -0.10071 | -0.13275 | -0.027466 | 0.045776 | -0.046997 | -0.24887 | -0.037384 | -0.15488 | -0.14954 | -0.004578 | 0.032043 | -0.07782 | -0.10529 | -0.09613 | -0.11444 | -0.045776 | 0.1236 | 0.013733 | -0.091553
7531.2188 | 0.061035 | 0.4657 | -0.46783 | -0.18692 | -0.1506 | -0.23926 | -0.16022 | 0.041199 | -0.054932 | 0.11444 | 0.009155 | -0.1236 | -0.1236 | -0.004578 | 0.045776 | -0.043793 | -0.23819 | -0.050201 | -0.15595 | -0.13779 | 0.073242 | 0.11444 | -0.068665 | -0.10986 | -0.09613 | -0.09613 | -0.022888 | 0.086975 | 0.041199 | -0.10529
7532.9844 | 0.045776 | 0.46783 | -0.45929 | -0.19653 | -0.14954 | -0.26489 | -0.17517 | 0.013733 | -0.054932 | 0.10986 | 0 | -0.064087 | -0.16022 | -0.050354 | 0.061035 | -0.055542 | -0.23605 | -0.040588 | -0.17197 | -0.1442 | 0.009155 | 0.045776 | -0.068665 | -0.073242 | -0.032043 | -0.10986 | -0.059509 | -0.027466 | 0.054932 | -0.054932
7534.6875 | 0.076294 | 0.45715 | -0.46783 | -0.21042 | -0.13886 | -0.25207 | -0.16342 | 0.013733 | -0.064087 | 0.10071 | -0.018311 | -0.068665 | -0.14191 | -0.036621 | 0.061035 | -0.05661 | -0.23285 | -0.036316 | -0.18051 | -0.13672 | 0 | 0.032043 | -0.082397 | -0.064087 | -0.068665 | -0.1236 | -0.068665 | 0.013733 | 0.041199 | -0.091553
7536.4375 | 0.061035 | 0.46783 | -0.47958 | -0.1976 | -0.14526 | -0.27557 | -0.16449 | 0.11902 | 0.064087 | 0.18768 | 0.086975 | -0.091553 | -0.19226 | -0.10071 | 0.061035 | -0.059814 | -0.24887 | -0.045929 | -0.16876 | -0.12924 | 0.064087 | 0.14648 | 0.073242 | -0.11444 | -0.10529 | -0.17853 | -0.10071 | -0.036621 | 0.036621 | -0.036621
7538.1875 | 0.076294 | 0.46143 | -0.46997 | -0.19653 | -0.1442 | -0.27451 | -0.16769 | 0.10071 | 0.050354 | 0.18768 | 0.082397 | -0.10071 | -0.17395 | -0.086975 | 0.076294 | -0.061951 | -0.24246 | -0.049133 | -0.16022 | -0.1442 | 0.068665 | 0.11902 | 0.027466 | -0.086975 | -0.064087 | -0.14191 | -0.09613 | -0.068665 | 0.059509 | -0.036621
7539.9375 | 0.061035 | 0.48386 | -0.49027 | -0.19012 | -0.13565 | -0.25635 | -0.17303 | 0.009155 | -0.054932 | 0.09613 | -0.009155 | -0.068665 | -0.12817 | -0.041199 | 0.061035 | -0.050201 | -0.24567 | -0.049133 | -0.15915 | -0.1474 | 0.013733 | 0.054932 | -0.073242 | -0.059509 | -0.064087 | -0.11902 | -0.054932 | -0.013733 | 0.064087 | -0.045776
7541.625 | 0.061035 | 0.50522 | -0.49027 | -0.17944 | -0.13565 | -0.27237 | -0.1741 | 0.09613 | 0.050354 | 0.09613 | 0.07782 | -0.086975 | -0.19226 | -0.10071 | 0.091553 | -0.060883 | -0.2478 | -0.032043 | -0.16663 | -0.13779 | 0.036621 | 0.12817 | 0.086975 | -0.086975 | -0.073242 | -0.17395 | -0.11444 | 0.009155 | 0.027466 | -0.032043
7543.3906 | 0.045776 | 0.46356 | -0.4689 | -0.18585 | -0.14099 | -0.26489 | -0.16235 | 0.1236 | 0.050354 | 0.059509 | 0.059509 | -0.11902 | -0.17853 | -0.086975 | 0.076294 | -0.054474 | -0.2478 | -0.05127 | -0.15274 | -0.15915 | 0.045776 | 0.11444 | 0.032043 | -0.15106 | -0.12817 | -0.15106 | -0.082397 | 0.064087 | 0.018311 | -0.059509
7545.0938 | 0.061035 | 0.46036 | -0.47852 | -0.19333 | -0.14633 | -0.25528 | -0.17197 | 0.045776 | -0.004578 | 0.12817 | 0.004578 | -0.073242 | -0.15106 | -0.059509 | 0.061035 | -0.050201 | -0.24353 | -0.054474 | -0.16235 | -0.1506 | 0.004578 | 0.050354 | -0.041199 | -0.059509 | -0.050354 | -0.11902 | -0.068665 | -0.032043 | 0.050354 | -0.041199
7546.8594 | 0.045776 | 0.46783 | -0.48386 | -0.19867 | -0.13992 | -0.27771 | -0.16129 | 0.073242 | 0.018311 | 0.054932 | 0.045776 | -0.082397 | -0.18768 | -0.082397 | 0.061035 | -0.066223 | -0.24674 | -0.046997 | -0.17197 | -0.13565 | 0.013733 | 0.059509 | 0.036621 | -0.09613 | -0.082397 | -0.17853 | -0.10986 | -0.004578 | 0.018311 | -0.027466
7548.625 | 0.030518 | 0.47638 | -0.48279 | -0.20935 | -0.16235 | -0.27344 | -0.16663 | 0.12817 | 0.086975 | 0.13733 | 0.091553 | -0.082397 | -0.19684 | -0.086975 | 0.061035 | -0.057678 | -0.24033 | -0.048065 | -0.17303 | -0.15488 | 0.086975 | 0.1236 | 0.086975 | -0.091553 | -0.082397 | -0.17395 | -0.11902 | 0.027466 | 0.045776 | -0.032043
7550.3281 | 0.061035 | 0.47211 | -0.47318 | -0.19119 | -0.13458 | -0.25421 | -0.15488 | 0.11902 | 0.032043 | 0.054932 | 0.064087 | -0.13275 | -0.16937 | -0.073242 | 0.061035 | -0.049133 | -0.23926 | -0.042725 | -0.15488 | -0.15595 | 0.059509 | 0.10529 | 0.027466 | -0.13733 | -0.12817 | -0.14648 | -0.082397 | 0.07782 | 0.009155 | -0.07782
7552.0781 | 0.061035 | 0.46356 | -0.46997 | -0.21255 | -0.15701 | -0.2681 | -0.17197 | 0.10529 | 0.032043 | 0.16022 | 0.059509 | -0.09613 | -0.16937 | -0.086975 | 0.030518 | -0.054474 | -0.25314 | -0.036316 | -0.16449 | -0.1506 | 0.018311 | 0.059509 | -0.027466 | -0.07782 | -0.068665 | -0.1236 | -0.064087 | -0.036621 | 0.050354 | -0.050354
7553.7812 | 0.076294 | 0.46677 | -0.47958 | -0.19974 | -0.15381 | -0.26703 | -0.16342 | 0.018311 | -0.068665 | 0.10529 | -0.013733 | -0.064087 | -0.14191 | -0.050354 | 0.061035 | -0.044861 | -0.23392 | -0.050201 | -0.16449 | -0.14313 | 0.009155 | 0.059509 | -0.091553 | -0.054932 | -0.059509 | -0.10986 | -0.045776 | 0.004578 | 0.045776 | -0.073242
7555.5469 | 0.061035 | 0.46143 | -0.46997 | -0.21149 | -0.14633 | -0.24567 | -0.15915 | 0.018311 | -0.082397 | 0.10071 | -0.004578 | -0.064087 | -0.13275 | -0.027466 | 0.061035 | -0.041656 | -0.23392 | -0.037384 | -0.16769 | -0.1442 | 0.009155 | 0.064087 | -0.091553 | -0.073242 | -0.050354 | -0.1236 | -0.050354 | 0.068665 | 0.022888 | -0.10071
7557.3125 | 0.061035 | 0.46036 | -0.78827 | -0.19867 | 0.16449 | -0.24567 | -0.16556 | 60.7727 | -62.5809 | 0.10529 | -62.7869 | 60.4431 | 62.7869 | 62.6266 | 0.061035 | -0.040588 | 0.11643 | 0.31616 | -0.14954 | -0.13886 | 0.054932 | 0.10529 | -62.9745 | 60.4111 | 60.4156 | 62.5488 | 62.7411 | 123.587 | 62.6633 | 60.5209
7559.0625 | 0.061035 | 0.45822 | -0.78507 | -0.19226 | 0.16129 | -0.24994 | -0.15595 | 60.6812 | -62.6495 | 0.027466 | -62.8326 | 60.4111 | 62.7365 | 62.6541 | 0.076294 | -0.026703 | 0.11215 | 0.3215 | -0.15808 | -0.14847 | 0 | 0.036621 | -63.0203 | 60.4294 | 60.4385 | 62.5214 | 62.7045 | 123.5504 | 62.6724 | 60.498
7560.8281 | 0.061035 | 0.46249 | -0.79147 | -0.1944 | 0.18265 | -0.27985 | -0.16022 | 60.7773 | -62.4619 | 0.054932 | -62.7182 | 60.3607 | 62.6175 | 62.5351 | 0.045776 | -0.063019 | 0.11322 | 0.31189 | -0.16342 | -0.13031 | 0.045776 | 0.11444 | -62.8464 | 60.379 | 60.3745 | 62.4435 | 62.6541 | 123.4726 | 62.6633 | 60.5713
7562.5156 | 0.045776 | 0.47852 | -0.79254 | -0.19867 | 0.18265 | -0.26489 | -0.16449 | 60.7544 | -62.4893 | 0.032043 | -62.7365 | 60.4156 | 62.5717 | 62.5031 | 0.030518 | -0.050201 | 0.10895 | 0.2948 | -0.16983 | -0.13672 | 0.022888 | 0.073242 | -62.8601 | 60.434 | 60.434 | 62.3886 | 62.6266 | 123.4222 | 62.6724 | 60.5713
7564.2812 | 0.061035 | 0.46783 | -0.79041 | -0.19012 | 0.1741 | -0.27664 | -0.16876 | 60.8185 | -62.3978 | 0.18768 | -62.6587 | 60.4111 | 62.5763 | 62.4664 | 0.061035 | -0.069427 | 0.098267 | 0.298 | -0.16449 | -0.14099 | 0.10071 | 0.16022 | -62.8006 | 60.4065 | 60.4019 | 62.3978 | 62.6129 | 123.4314 | 62.6541 | 60.5804
7566.0469 | 0.045776 | 0.46036 | -0.7872 | -0.21469 | 0.16876 | -0.2681 | -0.1709 | 60.8047 | -62.4298 | 0.18768 | -62.6633 | 60.4111 | 62.5488 | 62.4573 | 0.045776 | -0.068359 | 0.10895 | 0.31296 | -0.17838 | -0.14099 | 0.082397 | 0.15564 | -62.8098 | 60.3973 | 60.4065 | 62.4023 | 62.6221 | 123.3856 | 62.6404 | 60.5621
7567.75 | 0.061035 | 0.45822 | -0.79895 | -0.20187 | 0.16449 | -0.24994 | -0.17303 | 60.6949 | -62.5626 | 0.086975 | -62.7502 | 60.4477 | 62.6083 | 62.5168 | 0.076294 | -0.05127 | 0.11002 | 0.30762 | -0.16235 | -0.13992 | 0.032043 | 0.045776 | -62.9562 | 60.434 | 60.4248 | 62.439 | 62.6266 | 123.4222 | 62.6678 | 60.5255
7569.5156 | 0.030518 | 0.46249 | -0.79681 | -0.20615 | 0.18478 | -0.27237 | -0.16663 | 60.7864 | -62.4298 | 0.12817 | -62.645 | 60.4248 | 62.5351 | 62.4344 | 0.045776 | -0.066223 | 0.11643 | 0.30228 | -0.16129 | -0.14633 | 0.091553 | 0.13275 | -62.7914 | 60.4019 | 60.3973 | 62.3657 | 62.5854 | 123.3994 | 62.6404 | 60.553
7571.2969 | 0.061035 | 0.45395 | -0.78827 | -0.19012 | 0.16556 | -0.23285 | -0.16342 | 60.6491 | -62.6266 | -0.032043 | -62.796 | 60.4202 | 62.6221 | 62.4985 | 0.076294 | -0.043793 | 0.11108 | 0.31296 | -0.15488 | -0.14526 | 0 | 0.009155 | -62.9837 | 60.3973 | 60.3882 | 62.4527 | 62.6587 | 123.4634 | 62.6266 | 60.4935
7572.9844 | 0.061035 | 0.47852 | -0.79147 | -0.17838 | 0.1709 | -0.25314 | -0.16663 | 60.7407 | -62.4481 | 0.068665 | -62.6816 | 60.3699 | 62.5717 | 62.4573 | 0.076294 | -0.055542 | 0.093994 | 0.29907 | -0.15915 | -0.14847 | 0.07782 | 0.1236 | -62.8235 | 60.3287 | 60.3561 | 62.3657 | 62.59 | 123.4085 | 62.6221 | 60.5392
7574.75 | 0.061035 | 0.44861 | -0.784 | -0.17838 | 0.18051 | -0.23285 | -0.1474 | 60.7086 | -62.5397 | 0.091553 | -62.7411 | 60.3699 | 62.5946 | 62.5031 | 0.061035 | -0.03952 | 0.10147 | 0.30014 | -0.14099 | -0.14526 | 0.064087 | 0.09613 | -62.9654 | 60.3836 | 60.3561 | 62.439 | 62.6541 | 123.4085 | 62.6266 | 60.4935
7576.4531 | 0.061035 | 0.46463 | -0.79041 | -0.19546 | 0.17197 | -0.25101 | -0.14847 | 60.6583 | -62.5259 | 0.10529 | -62.7136 | 60.4019 | 62.6083 | 62.4802 | 0.076294 | -0.053406 | 0.10254 | 0.30868 | -0.15915 | -0.14526 | 0.064087 | 0.10071 | -62.9196 | 60.4019 | 60.379 | 62.4115 | 62.6587 | 123.436 | 62.6083 | 60.4889
7578.2188 | 0.061035 | 0.44647 | -0.78827 | -0.19546 | 0.17517 | -0.25742 | -0.16235 | 60.6308 | -62.59 | -0.032043 | -62.7594 | 60.3928 | 62.5946 | 62.4847 | 0.061035 | -0.049133 | 0.10574 | 0.31723 | -0.15808 | -0.13351 | 0.013733 | 0.027466 | -62.9379 | 60.3745 | 60.3561 | 62.4023 | 62.6358 | 123.4451 | 62.5854 | 60.466
7579.9062 | 0.076294 | 0.45609 | -0.79575 | -0.20721 | 0.17517 | -0.27557 | -0.16235 | 60.7361 | -62.3886 | 0.19226 | -62.6266 | 60.3745 | 62.5122 | 62.4161 | 0.045776 | -0.061951 | 0.093994 | 0.298 | -0.17197 | -0.14206 | 0.086975 | 0.15564 | -62.8006 | 60.3607 | 60.4019 | 62.352 | 62.558 | 123.2986 | 62.6129 | 60.5347
7581.6719 | 0.045776 | 0.45288 | -0.77225 | -0.20401 | 0.18051 | -0.23926 | -0.16022 | 60.6766 | -62.5351 | 0.1236 | -62.7182 | 60.3745 | 62.5763 | 62.4985 | 0.061035 | -0.038452 | 0.11643 | 0.32364 | -0.15701 | -0.15167 | 0.064087 | 0.10529 | -62.9013 | 60.3699 | 60.3745 | 62.4115 | 62.6129 | 123.436 | 62.5946 | 60.4385
7583.4531 | 0.061035 | 0.4657 | -0.79041 | -0.1976 | 0.16342 | -0.27557 | -0.16556 | 60.7269 | -62.4115 | 0.16937 | -62.6541 | 60.3745 | 62.5305 | 62.4252 | 0.091553 | -0.060883 | 0.10468 | 0.30868 | -0.17303 | -0.14954 | 0.059509 | 0.10071 | -62.8464 | 60.379 | 60.4202 | 62.3566 | 62.5854 | 123.2758 | 62.6129 | 60.5164
7585.2188 | 0.061035 | 0.48813 | -0.78827 | -0.19012 | 0.16129 | -0.27664 | -0.17197 | 60.7086 | -62.4527 | 0.036621 | -62.6587 | 60.3699 | 62.4847 | 62.4115 | 0.045776 | -0.060883 | 0.10574 | 0.30334 | -0.16983 | -0.13672 | 0.032043 | 0.073242 | -62.8189 | 60.3699 | 60.3836 | 62.3428 | 62.5626 | 123.2758 | 62.6175 | 60.5347
7586.9219 | 0.076294 | 0.47211 | -0.79361 | -0.18478 | 0.16556 | -0.26382 | -0.17197 | 60.7178 | -62.4207 | 0.054932 | -62.6633 | 60.3241 | 62.5168 | 62.4207 | 0.045776 | -0.067291 | 0.095062 | 0.31189 | -0.16983 | -0.13565 | 0.082397 | 0.09613 | -62.7869 | 60.3516 | 60.3561 | 62.3749 | 62.5534 | 123.2849 | 62.6129 | 60.5347
7588.6719 | 0.076294 | 0.42725 | -0.78827 | -0.20935 | 0.16556 | -0.24353 | -0.16449 | 60.672 | -62.5214 | 0.12817 | -62.6862 | 60.3928 | 62.5626 | 62.4847 | 0.061035 | -0.040588 | 0.10574 | 0.30762 | -0.15381 | -0.14954 | 0.10071 | 0.13275 | -62.883 | 60.3561 | 60.379 | 62.4023 | 62.6129 | 123.3902 | 62.5946 | 60.434
7590.4375 | 0.061035 | 0.45822 | -0.79788 | -0.20401 | 0.18265 | -0.27771 | -0.16342 | 60.7407 | -62.3657 | 0.19226 | -62.6038 | 60.3882 | 62.5076 | 62.3932 | 0.061035 | -0.067291 | 0.091858 | 0.30228 | -0.15595 | -0.13245 | 0.10529 | 0.15564 | -62.764 | 60.3607 | 60.3561 | 62.3199 | 62.5534 | 123.262 | 62.59 | 60.553
7592.2031 | 0.045776 | 0.46356 | -0.78934 | -0.19546 | 0.17303 | -0.25742 | -0.17517 | 60.7361 | -62.3611 | 0.20142 | -62.5992 | 60.3699 | 62.4847 | 62.3749 | 0.061035 | -0.064087 | 0.098267 | 0.30014 | -0.16022 | -0.15488 | 0.10986 | 0.16479 | -62.7594 | 60.3516 | 60.3287 | 62.3428 | 62.5397 | 123.2529 | 62.59 | 60.5484
7593.9219 | 0.061035 | 0.45609 | -0.7872 | -0.20615 | 0.16129 | -0.25955 | -0.16983 | 60.7132 | -62.4207 | 0.16479 | -62.6495 | 60.3607 | 62.5214 | 62.4115 | 0.061035 | -0.061951 | 0.098267 | 0.30334 | -0.15915 | -0.13351 | 0.059509 | 0.073242 | -62.8235 | 60.3607 | 60.3424 | 62.3703 | 62.5809 | 123.262 | 62.6038 | 60.5392
7595.6875 | 0.045776 | 0.44861 | -0.784 | -0.1944 | 0.1741 | -0.23498 | -0.16235 | 60.6537 | -62.4939 | 0.11444 | -62.6953 | 60.3653 | 62.5763 | 62.471 | 0.061035 | -0.040588 | 0.095062 | 0.29694 | -0.14633 | -0.14633 | 0.09613 | 0.1236 | -62.8876 | 60.3516 | 60.3058 | 62.3978 | 62.6358 | 123.3627 | 62.5809 | 60.434
7597.4531 | 0.045776 | 0.47531 | -0.78934 | -0.18906 | 0.16342 | -0.28198 | -0.16663 | 60.6857 | -62.4023 | 0.036621 | -62.6404 | 60.3699 | 62.4893 | 62.3932 | 0.061035 | -0.060883 | 0.087585 | 0.28946 | -0.16769 | -0.13565 | 0.041199 | 0.068665 | -62.796 | 60.3424 | 60.347 | 62.3016 | 62.5488 | 123.2483 | 62.59 | 60.5392
7599.1406 | 0.061035 | 0.45181 | -0.79361 | -0.20401 | 0.17197 | -0.27344 | -0.16235 | 60.672 | -62.4252 | 0.14648 | -62.6495 | 60.3699 | 62.5305 | 62.4435 | 0.045776 | -0.065155 | 0.10574 | 0.298 | -0.16876 | -0.13565 | 0.054932 | 0.07782 | -62.8326 | 60.3424 | 60.3699 | 62.352 | 62.5717 | 123.2346 | 62.59 | 60.5164
7600.9219 | 0.061035 | 0.47104 | -0.80322 | -0.20828 | 0.16342 | -0.24567 | -0.17197 | 60.6171 | -62.5076 | 0.10071 | -62.6953 | 60.4065 | 62.5122 | 62.4298 | 0.045776 | -0.064087 | 0.11002 | 0.30868 | -0.16342 | -0.1442 | 0.036621 | 0.064087 | -62.8967 | 60.3745 | 60.379 | 62.3703 | 62.5946 | 123.2941 | 62.5809 | 60.4568
7602.6875 | 0.061035 | 0.43793 | -0.78293 | -0.20401 | 0.17624 | -0.23605 | -0.16983 | 60.6354 | -62.471 | 0.12817 | -62.6816 | 60.3745 | 62.5488 | 62.4664 | 0.045776 | -0.055542 | 0.10681 | 0.30655 | -0.15488 | -0.14313 | 0.10071 | 0.10986 | -62.8647 | 60.3424 | 60.3287 | 62.3657 | 62.6404 | 123.3673 | 62.5626 | 60.4385
7604.4531 | 0.091553 | 0.4689 | -0.79788 | -0.20081 | 0.15488 | -0.27771 | -0.16342 | 60.6445 | -62.4023 | 0.064087 | -62.6221 | 60.3653 | 62.4847 | 62.4023 | 0.061035 | -0.079041 | 0.083313 | 0.28946 | -0.1709 | -0.13992 | 0.050354 | 0.086975 | -62.7411 | 60.3745 | 60.3516 | 62.2925 | 62.5351 | 123.2758 | 62.5626 | 60.5255
7606.1562 | 0.061035 | 0.45288 | -0.77652 | -0.20935 | 0.16342 | -0.27451 | -0.16769 | 60.7407 | -62.3245 | 0.1831 | -62.5854 | 60.3378 | 62.4802 | 62.3795 | 0.061035 | -0.063019 | 0.097198 | 0.30121 | -0.16769 | -0.15915 | 0.10529 | 0.17395 | -62.7136 | 60.3378 | 60.3653 | 62.3016 | 62.5305 | 123.2529 | 62.5626 | 60.498
7607.9219 | 0.091553 | 0.45395 | -0.79254 | -0.1976 | 0.15701 | -0.2681 | -0.16663 | 60.7407 | -62.3337 | 0.1831 | -62.59 | 60.3607 | 62.4893 | 62.3932 | 0.061035 | -0.063019 | 0.098267 | 0.30975 | -0.16342 | -0.15595 | 0.11444 | 0.15564 | -62.7228 | 60.3287 | 60.3607 | 62.2925 | 62.5168 | 123.2437 | 62.5442 | 60.498
7609.6875 | 0.030518 | 0.44754 | -0.78079 | -0.21255 | 0.1741 | -0.26382 | -0.16449 | 60.7132 | -62.384 | 0.17853 | -62.6038 | 60.3378 | 62.4893 | 62.3795 | 0.076294 | -0.067291 | 0.10468 | 0.298 | -0.15915 | -0.14633 | 0.09613 | 0.12817 | -62.7731 | 60.3333 | 60.3333 | 62.3337 | 62.5534 | 123.2025 | 62.59 | 60.5164
7611.4219 | 0.076294 | 0.45609 | -0.79041 | -0.19012 | 0.16876 | -0.25207 | -0.17303 | 60.6171 | -62.4847 | 0.10986 | -62.6816 | 60.379 | 62.5351 | 62.4344 | 0.091553 | -0.055542 | 0.092926 | 0.30334 | -0.16022 | -0.14954 | 0.027466 | 0.045776 | -62.8738 | 60.3882 | 60.3699 | 62.352 | 62.5763 | 123.2437 | 62.5717 | 60.498
7613.1719 | 0.030518 | 0.46356 | -0.79254 | -0.19333 | 0.17517 | -0.27771 | -0.16556 | 60.7315 | -62.3337 | 0.15564 | -62.59 | 60.3653 | 62.4756 | 62.3795 | 0.061035 | -0.071564 | 0.092926 | 0.29907 | -0.16769 | -0.14633 | 0.13275 | 0.16479 | -62.6907 | 60.347 | 60.3058 | 62.2971 | 62.5351 | 123.2758 | 62.5626 | 60.498
7614.875 | 0.091553 | 0.44006 | -0.77866 | -0.19867 | 0.16769 | -0.23605 | -0.15488 | 60.5942 | -62.5214 | 0.050354 | -62.7274 | 60.3699 | 62.5626 | 62.4435 | 0.061035 | -0.036316 | 0.093994 | 0.3183 | -0.15167 | -0.1506 | 0.036621 | 0.041199 | -62.9333 | 60.3516 | 60.3149 | 62.3749 | 62.5946 | 123.262 | 62.5763 | 60.4477
7616.6406 | 0.091553 | 0.45181 | -0.79254 | -0.20081 | 0.16769 | -0.26382 | -0.16769 | 60.7132 | -62.3154 | 0.1831 | -62.5717 | 60.3378 | 62.4527 | 62.3795 | 0.091553 | -0.065155 | 0.088654 | 0.29373 | -0.16235 | -0.14633 | 0.10986 | 0.16022 | -62.7045 | 60.347 | 60.3149 | 62.2879 | 62.5168 | 123.23 | 62.5442 | 60.5072
7618.4062 | 0.061035 | 0.46356 | -0.79147 | -0.18906 | 0.16769 | -0.24674 | -0.16129 | 60.6628 | -62.3978 | 0.050354 | -62.6083 | 60.3195 | 62.4985 | 62.3978 | 0.045776 | -0.059814 | 0.087585 | 0.30762 | -0.15167 | -0.14954 | 0.07782 | 0.12817 | -62.7777 | 60.3104 | 60.2692 | 62.3337 | 62.5763 | 123.3261 | 62.5214 | 60.4477
7620.1719 | 0.076294 | 0.44861 | -0.784 | -0.19867 | 0.18051 | -0.25742 | -0.16129 | 60.6812 | -62.3383 | 0.18768 | -62.5946 | 60.3241 | 62.4939 | 62.3886 | 0.061035 | -0.060883 | 0.085449 | 0.28946 | -0.16769 | -0.14313 | 0.10071 | 0.15564 | -62.764 | 60.347 | 60.3012 | 62.3199 | 62.5626 | 123.1796 | 62.5534 | 60.5026
7621.9219 | 0.061035 | 0.44861 | -0.78613 | -0.20294 | 0.17303 | -0.26596 | -0.16556 | 60.672 | -62.3978 | 0.050354 | -62.6175 | 60.3607 | 62.471 | 62.3749 | 0.061035 | -0.072632 | 0.1004 | 0.30975 | -0.16663 | -0.15274 | 0.059509 | 0.082397 | -62.764 | 60.3195 | 60.3241 | 62.2971 | 62.5351 | 123.1934 | 62.5488 | 60.5026
7623.6406 | 0.076294 | 0.45075 | -0.78613 | -0.19867 | 0.16449 | -0.25314 | -0.16449 | 60.6079 | -62.4893 | 0.09613 | -62.677 | 60.3882 | 62.4847 | 62.4298 | 0.061035 | -0.042725 | 0.10468 | 0.30228 | -0.16449 | -0.14954 | 0.036621 | 0.068665 | -62.8693 | 60.3745 | 60.3699 | 62.3611 | 62.5717 | 123.2346 | 62.5763 | 60.4706
7625.4062 | 0.061035 | 0.45395 | -0.77759 | -0.1944 | 0.17624 | -0.24246 | -0.15701 | 60.585 | -62.5031 | 0.10529 | -62.6816 | 60.3699 | 62.5351 | 62.4435 | 0.061035 | -0.042725 | 0.098267 | 0.30441 | -0.15167 | -0.12924 | 0.054932 | 0.086975 | -62.8647 | 60.3516 | 60.3195 | 62.3657 | 62.5809 | 123.317 | 62.5397 | 60.4385
7627.1719 | 0.061035 | 0.44861 | -0.78186 | -0.20187 | 0.17517 | -0.24033 | -0.16449 | 60.585 | -62.4985 | 0.09613 | -62.6541 | 60.379 | 62.5305 | 62.4252 | 0.061035 | -0.058746 | 0.09613 | 0.29907 | -0.1709 | -0.13992 | 0.050354 | 0.082397 | -62.8601 | 60.3699 | 60.3378 | 62.3657 | 62.5717 | 123.3078 | 62.558 | 60.4431
7628.8906 | 0.045776 | 0.46143 | -0.79361 | -0.1944 | 0.15808 | -0.26916 | -0.16663 | 60.6354 | -62.4069 | 0.036621 | -62.6129 | 60.3424 | 62.4756 | 62.3657 | 0.061035 | -0.070496 | 0.098267 | 0.30121 | -0.16449 | -0.13992 | 0.027466 | 0.059509 | -62.7594 | 60.3195 | 60.3516 | 62.2696 | 62.5168 | 123.2208 | 62.558 | 60.5255
7630.6406 | 0.061035 | 0.44968 | -0.78079 | -0.20721 | 0.15595 | -0.24994 | -0.16129 | 60.5896 | -62.4939 | 0.11444 | -62.6541 | 60.379 | 62.5351 | 62.4298 | 0.076294 | -0.055542 | 0.092926 | 0.31082 | -0.15381 | -0.14526 | 0.050354 | 0.086975 | -62.851 | 60.3378 | 60.3012 | 62.352 | 62.5809 | 123.3307 | 62.5168 | 60.4477
7632.3438 | 0.061035 | 0.44754 | -0.78507 | -0.21683 | 0.17197 | -0.27023 | -0.16022 | 60.6995 | -62.3291 | 0.20142 | -62.5717 | 60.3287 | 62.4664 | 62.3474 | 0.061035 | -0.067291 | 0.091858 | 0.30014 | -0.1709 | -0.15595 | 0.10986 | 0.16022 | -62.7182 | 60.3195 | 60.3287 | 62.3108 | 62.5442 | 123.1979 | 62.5809 | 60.4797
7634.0938 | 0.061035 | 0.45075 | -0.7872 | -0.21255 | 0.16769 | -0.25955 | -0.16769 | 60.585 | -62.4756 | 0.10071 | -62.6633 | 60.3561 | 62.5259 | 62.4252 | 0.045776 | -0.042725 | 0.10147 | 0.29587 | -0.15488 | -0.15274 | 0.022888 | 0.050354 | -62.851 | 60.3607 | 60.3333 | 62.3749 | 62.5717 | 123.2208 | 62.5305 | 60.466
7635.7969 | 0.076294 | 0.45822 | -0.79147 | -0.19333 | 0.16022 | -0.27878 | -0.16235 | 60.6354 | -62.3978 | 0.027466 | -62.6129 | 60.3424 | 62.471 | 62.384 | 0.061035 | -0.0737 | 0.091858 | 0.28305 | -0.15701 | -0.14313 | 0.036621 | 0.073242 | -62.7548 | 60.3287 | 60.3424 | 62.3199 | 62.5305 | 123.1613 | 62.5488 | 60.4889
7637.5625 | 0.061035 | 0.44754 | -0.77652 | -0.19546 | 0.18478 | -0.24246 | -0.16663 | 60.6079 | -62.4435 | 0.1236 | -62.6633 | 60.3516 | 62.5076 | 62.4344 | 0.061035 | -0.049133 | 0.088654 | 0.31509 | -0.14954 | -0.1506 | 0.091553 | 0.11902 | -62.8418 | 60.3241 | 60.3195 | 62.3703 | 62.5992 | 123.2849 | 62.5351 | 60.4065
7639.3281 | 0.061035 | 0.46356 | -0.78613 | -0.20187 | 0.15488 | -0.29373 | -0.16769 | 60.6354 | -62.3886 | 0.050354 | -62.5992 | 60.3378 | 62.4527 | 62.352 | 0.045776 | -0.064087 | 0.097198 | 0.29587 | -0.17731 | -0.14954 | 0.054932 | 0.086975 | -62.7274 | 60.3104 | 60.3424 | 62.2971 | 62.5031 | 123.2071 | 62.5259 | 60.4752
7641.0312 | 0.061035 | 0.45929 | -0.77972 | -0.19333 | 0.16556 | -0.23285 | -0.15915 | 60.5392 | -62.5351 | 0.009155 | -62.6907 | 60.3241 | 62.5397 | 62.4481 | 0.061035 | -0.048065 | 0.095062 | 0.28946 | -0.13779 | -0.14954 | 0.004578 | 0.036621 | -62.9196 | 60.3241 | 60.3104 | 62.384 | 62.5946 | 123.2483 | 62.5488 | 60.4385
7642.7969 | 0.076294 | 0.45715 | -0.77438 | -0.18265 | 0.18051 | -0.24353 | -0.16449 | 60.5392 | -62.5122 | 0.018311 | -62.6724 | 60.3378 | 62.5442 | 62.4481 | 0.061035 | -0.049133 | 0.092926 | 0.30334 | -0.15381 | -0.13672 | -0.004578 | 0.041199 | -62.9196 | 60.3149 | 60.3104 | 62.3886 | 62.6038 | 123.23 | 62.5488 | 60.4156
7644.5625 | 0.061035 | 0.45609 | -0.78079 | -0.20828 | 0.15381 | -0.26062 | -0.16129 | 60.5713 | -62.471 | 0.10986 | -62.6495 | 60.3424 | 62.5076 | 62.4527 | 0.061035 | -0.049133 | 0.099335 | 0.30334 | -0.16342 | -0.15167 | 0.064087 | 0.11902 | -62.851 | 60.3012 | 60.3241 | 62.3657 | 62.5717 | 123.2895 | 62.5259 | 60.4019
7646.3281 | 0.045776 | 0.46143 | -0.77759 | -0.19974 | 0.16663 | -0.25528 | -0.15274 | 60.6125 | -62.4298 | 0.013733 | -62.6266 | 60.3104 | 62.471 | 62.4023 | 0.076294 | -0.069427 | 0.09613 | 0.30655 | -0.15701 | -0.1506 | 0.064087 | 0.12817 | -62.7548 | 60.3012 | 60.2783 | 62.3291 | 62.5351 | 123.2849 | 62.5214 | 60.4248
7648.0312 | 0.061035 | 0.45929 | -0.78507 | -0.19119 | 0.17197 | -0.25955 | -0.16235 | 60.5759 | -62.471 | 0 | -62.6587 | 60.3333 | 62.5214 | 62.4115 | 0.076294 | -0.057678 | 0.086517 | 0.30868 | -0.15808 | -0.13672 | 0.054932 | 0.086975 | -62.7869 | 60.2875 | 60.3058 | 62.3383 | 62.5305 | 123.2803 | 62.5351 | 60.4156
7649.7969 | 0.076294 | 0.44861 | -0.78079 | -0.19333 | 0.17731 | -0.24567 | -0.16022 | 60.5255 | -62.5442 | -0.009155 | -62.6907 | 60.3149 | 62.5122 | 62.4298 | 0.076294 | -0.048065 | 0.099335 | 0.30762 | -0.14526 | -0.14099 | 0.004578 | 0.032043 | -62.8967 | 60.3195 | 60.3424 | 62.384 | 62.5854 | 123.2391 | 62.5534 | 60.3836
7651.5 | 0.061035 | 0.44968 | -0.78827 | -0.21149 | 0.16022 | -0.27664 | -0.16449 | 60.6308 | -62.3566 | 0.17853 | -62.59 | 60.3149 | 62.4573 | 62.3566 | 0.061035 | -0.0737 | 0.092926 | 0.28839 | -0.17517 | -0.13779 | 0.054932 | 0.10071 | -62.7777 | 60.3241 | 60.3149 | 62.3337 | 62.5442 | 123.1476 | 62.5259 | 60.4706
7653.25 | 0.091553 | 0.46249 | -0.78293 | -0.19119 | 0.17624 | -0.26169 | -0.16342 | 60.6491 | -62.3703 | 0.054932 | -62.5763 | 60.2737 | 62.4481 | 62.3703 | 0.045776 | -0.061951 | 0.080109 | 0.29907 | -0.1474 | -0.14206 | 0.07782 | 0.11902 | -62.7274 | 60.2783 | 60.26 | 62.3154 | 62.5214 | 123.2529 | 62.5122 | 60.4568
7654.9531 | 0.061035 | 0.46036 | -0.79361 | -0.21255 | 0.17197 | -0.28091 | -0.15808 | 60.6537 | -62.3337 | 0.1831 | -62.558 | 60.3287 | 62.4481 | 62.3703 | 0.045776 | -0.0737 | 0.093994 | 0.28946 | -0.16342 | -0.15701 | 0.086975 | 0.13275 | -62.7365 | 60.3241 | 60.3012 | 62.2971 | 62.5259 | 123.1293 | 62.5351 | 60.4614
7656.75 | 0.061035 | 0.4454 | -0.78186 | -0.21362 | 0.15915 | -0.26489 | -0.15915 | 60.5713 | -62.439 | 0.11902 | -62.6404 | 60.3653 | 62.4847 | 62.4207 | 0.061035 | -0.053406 | 0.091858 | 0.29907 | -0.16022 | -0.14526 | 0.022888 | 0.050354 | -62.8235 | 60.347 | 60.3378 | 62.3611 | 62.5488 | 123.1613 | 62.5305 | 60.466
7658.5156 | 0.045776 | 0.44968 | -0.784 | -0.20294 | 0.17303 | -0.26916 | -0.16556 | 60.6812 | -62.2971 | 0.19226 | -62.5534 | 60.3287 | 62.4252 | 62.3291 | 0.030518 | -0.075836 | 0.081177 | 0.29373 | -0.16663 | -0.15167 | 0.10986 | 0.15564 | -62.6862 | 60.3104 | 60.2829 | 62.2925 | 62.5214 | 123.143 | 62.5305 | 60.4935
7660.2031 | 0.061035 | 0.46997 | -0.80109 | -0.20081 | 0.16235 | -0.27985 | -0.16769 | 60.6125 | -62.3657 | 0.045776 | -62.5946 | 60.3149 | 62.439 | 62.3749 | 0.061035 | -0.082245 | 0.072632 | 0.2713 | -0.16769 | -0.14954 | 0.013733 | 0.059509 | -62.7457 | 60.3104 | 60.3058 | 62.2833 | 62.4939 | 123.1293 | 62.5259 | 60.4889
7661.9531 | 0.061035 | 0.46783 | -0.784 | -0.18372 | 0.15381 | -0.25101 | -0.16556 | 60.6537 | -62.3428 | 0.054932 | -62.5717 | 60.3012 | 62.4939 | 62.3795 | 0.061035 | -0.064087 | 0.087585 | 0.2948 | -0.15167 | -0.14847 | 0.086975 | 0.11444 | -62.7182 | 60.2737 | 60.2554 | 62.3428 | 62.5305 | 123.2254 | 62.5168 | 60.4385
7663.7031 | 0.045776 | 0.45395 | -0.78827 | -0.20294 | 0.16022 | -0.26703 | -0.16556 | 60.6491 | -62.3337 | 0.1831 | -62.5488 | 60.2829 | 62.4573 | 62.3703 | 0.045776 | -0.075836 | 0.095062 | 0.28946 | -0.16556 | -0.15701 | 0.09613 | 0.11902 | -62.7411 | 60.3287 | 60.3104 | 62.3062 | 62.5305 | 123.1155 | 62.5305 | 60.466
7665.4219 | 0.076294 | 0.46249 | -0.78613 | -0.19867 | 0.16129 | -0.27451 | -0.16449 | 60.6308 | -62.3611 | 0.050354 | -62.59 | 60.3287 | 62.4527 | 62.3474 | 0.061035 | -0.063019 | 0.080109 | 0.29373 | -0.16129 | -0.13351 | 0.032043 | 0.045776 | -62.7502 | 60.3149 | 60.3149 | 62.2787 | 62.4893 | 123.1476 | 62.5214 | 60.4797
7667.1875 | 0.061035 | 0.46249 | -0.79788 | -0.18585 | 0.14847 | -0.26703 | -0.17197 | 60.6445 | -62.3566 | 0.032043 | -62.5854 | 60.3149 | 62.4664 | 62.3474 | 0.061035 | -0.067291 | 0.084381 | 0.29053 | -0.15915 | -0.14847 | 0.064087 | 0.068665 | -62.7365 | 60.3104 | 60.3058 | 62.2971 | 62.4939 | 123.1338 | 62.5214 | 60.5026
7668.8906 | 0.076294 | 0.45929 | -0.77652 | -0.20508 | 0.15595 | -0.2681 | -0.1741 | 60.6171 | -62.3703 | 0.050354 | -62.5763 | 60.347 | 62.439 | 62.3428 | 0.061035 | -0.0737 | 0.089722 | 0.29159 | -0.16449 | -0.1506 | 0.054932 | 0.054932 | -62.7411 | 60.3287 | 60.2875 | 62.3108 | 62.5305 | 123.1659 | 62.4893 | 60.498
7670.6406 | 0.045776 | 0.45609 | -0.78186 | -0.19546 | 0.16983 | -0.23498 | -0.15701 | 60.5209 | -62.5305 | -0.027466 | -62.6678 | 60.3241 | 62.5076 | 62.4069 | 0.045776 | -0.040588 | 0.099335 | 0.29907 | -0.13992 | -0.15381 | 0.018311 | 0.022888 | -62.8922 | 60.3287 | 60.2783 | 62.3703 | 62.5534 | 123.2208 | 62.5214 | 60.4202
7672.3438 | 0.061035 | 0.45609 | -0.78293 | -0.19119 | 0.16022 | -0.23712 | -0.15167 | 60.5896 | -62.4023 | 0.10986 | -62.6175 | 60.3149 | 62.5122 | 62.4069 | 0.061035 | -0.050201 | 0.085449 | 0.298 | -0.13886 | -0.1442 | 0.10071 | 0.11444 | -62.8189 | 60.2829 | 60.2692 | 62.3383 | 62.5442 | 123.2346 | 62.5442 | 60.379
7674.1094 | 0.061035 | 0.45288 | -0.784 | -0.20828 | 0.17944 | -0.28519 | -0.16449 | 60.672 | -62.2467 | 0.17395 | -62.5168 | 60.3012 | 62.4344 | 62.3245 | 0.061035 | -0.076904 | 0.084381 | 0.28625 | -0.17303 | -0.13672 | 0.10529 | 0.16479 | -62.6404 | 60.2829 | 60.2737 | 62.2787 | 62.4985 | 123.1567 | 62.4847 | 60.498
7675.875 | 0.076294 | 0.46356 | -0.78934 | -0.21469 | 0.15167 | -0.27557 | -0.16235 | 60.6079 | -62.3474 | 0.064087 | -62.5717 | 60.347 | 62.4207 | 62.3108 | 0.045776 | -0.066223 | 0.087585 | 0.29907 | -0.16769 | -0.14954 | 0.041199 | 0.086975 | -62.7274 | 60.3012 | 60.3058 | 62.2742 | 62.4756 | 123.1338 | 62.4939 | 60.466
7677.5781 | 0.076294 | 0.46036 | -0.77225 | -0.1976 | 0.15274 | -0.23605 | -0.16342 | 60.5759 | -62.4252 | 0.082397 | -62.6266 | 60.3012 | 62.4985 | 62.4252 | 0.045776 | -0.036316 | 0.089722 | 0.30014 | -0.1506 | -0.16022 | 0.068665 | 0.091553 | -62.796 | 60.3104 | 60.2737 | 62.3428 | 62.5626 | 123.23 | 62.4847 | 60.3745
7679.3594 | 0.045776 | 0.45075 | -0.77866 | -0.19119 | 0.1709 | -0.24033 | -0.15808 | 60.5484 | -62.4435 | 0.064087 | -62.6221 | 60.2921 | 62.5076 | 62.4344 | 0.061035 | -0.057678 | 0.085449 | 0.29053 | -0.1474 | -0.15274 | 0.032043 | 0.07782 | -62.8143 | 60.3058 | 60.2875 | 62.3474 | 62.5717 | 123.2391 | 62.4985 | 60.3882
7681.125 | 0.061035 | 0.45502 | -0.77438 | -0.19867 | 0.16769 | -0.26169 | -0.15274 | 60.5392 | -62.4298 | 0.009155 | -62.6266 | 60.3195 | 62.4847 | 62.4023 | 0.076294 | -0.055542 | 0.097198 | 0.2948 | -0.15701 | -0.14206 | 0.082397 | 0.10986 | -62.7869 | 60.2875 | 60.3012 | 62.2971 | 62.5305 | 123.262 | 62.5076 | 60.3973
7682.8281 | 0.091553 | 0.4454 | -0.78293 | -0.21255 | 0.16876 | -0.25955 | -0.15595 | 60.5209 | -62.4619 | 0.041199 | -62.6541 | 60.3012 | 62.5168 | 62.4115 | 0.045776 | -0.057678 | 0.1004 | 0.30655 | -0.15701 | -0.14313 | -0.022888 | 0.018311 | -62.8418 | 60.3241 | 60.3149 | 62.3337 | 62.558 | 123.1888 | 62.5168 | 60.3928
7684.5938 | 0.030518 | 0.45075 | -0.79254 | -0.20401 | 0.15915 | -0.27344 | -0.16235 | 60.585 | -62.352 | 0.082397 | -62.5626 | 60.3149 | 62.4115 | 62.3337 | 0.076294 | -0.082245 | 0.085449 | 0.29587 | -0.16556 | -0.14206 | 0.073242 | 0.09613 | -62.7228 | 60.2783 | 60.2966 | 62.2604 | 62.4893 | 123.111 | 62.5031 | 60.4706
7686.3594 | 0.061035 | 0.45929 | -0.78827 | -0.21255 | 0.16449 | -0.25528 | -0.17838 | 60.6079 | -62.3428 | 0.14191 | -62.5626 | 60.2875 | 62.4344 | 62.3611 | 0.061035 | -0.064087 | 0.09613 | 0.29266 | -0.16663 | -0.14633 | 0.018311 | 0.064087 | -62.7502 | 60.2921 | 60.2966 | 62.3291 | 62.5351 | 123.1064 | 62.5305 | 60.4706
7688.0469 | 0.045776 | 0.43686 | -0.79147 | -0.20615 | 0.15595 | -0.24887 | -0.16022 | 60.5347 | -62.4481 | 0.050354 | -62.6221 | 60.3424 | 62.4802 | 62.4023 | 0.061035 | -0.066223 | 0.095062 | 0.29053 | -0.15595 | -0.15595 | -0.004578 | 0.013733 | -62.8372 | 60.3287 | 60.2966 | 62.3474 | 62.558 | 123.2025 | 62.5168 | 60.3882
7689.75 | 0.061035 | 0.45075 | -0.78079 | -0.19653 | 0.15274 | -0.25207 | -0.16022 | 60.553 | -62.4115 | 0.082397 | -62.6175 | 60.2966 | 62.4893 | 62.4069 | 0.076294 | -0.044861 | 0.093994 | 0.30014 | -0.14206 | -0.1506 | 0.059509 | 0.09613 | -62.8006 | 60.3012 | 60.2646 | 62.3566 | 62.5717 | 123.23 | 62.4756 | 60.3836
7691.5156 | 0.061035 | 0.45181 | -0.78613 | -0.21042 | 0.16556 | -0.28412 | -0.17303 | 60.6445 | -62.2604 | 0.15564 | -62.5259 | 60.2921 | 62.4207 | 62.3291 | 0.061035 | -0.072632 | 0.082245 | 0.29053 | -0.17197 | -0.14313 | 0.10071 | 0.15106 | -62.6541 | 60.26 | 60.2875 | 62.2604 | 62.4893 | 123.1338 | 62.4985 | 60.4248
7693.2656 | 0.061035 | 0.43045 | -0.77438 | -0.19119 | 0.16663 | -0.2446 | -0.15701 | 60.553 | -62.4298 | 0.064087 | -62.6221 | 60.3241 | 62.5168 | 62.4161 | 0.091553 | -0.059814 | 0.092926 | 0.30334 | -0.15915 | -0.1442 | 0.07782 | 0.091553 | -62.8052 | 60.2829 | 60.2783 | 62.3428 | 62.5626 | 123.2162 | 62.4664 | 60.3699
7695.0312 | 0.061035 | 0.46249 | -0.78079 | -0.19333 | 0.16769 | -0.26382 | -0.15701 | 60.5759 | -62.3795 | 0.073242 | -62.5854 | 60.3058 | 62.4619 | 62.3749 | 0.061035 | -0.063019 | 0.080109 | 0.29694 | -0.15595 | -0.14954 | 0.10986 | 0.16479 | -62.709 | 60.26 | 60.2875 | 62.2696 | 62.4939 | 123.2254 | 62.4573 | 60.3973
7696.75 | 0.076294 | 0.46249 | -0.78186 | -0.18906 | 0.16556 | -0.27237 | -0.16449 | 60.6262 | -62.2971 | 0.10529 | -62.5534 | 60.2737 | 62.4207 | 62.3474 | 0.061035 | -0.071564 | 0.0737 | 0.29373 | -0.15915 | -0.14633 | 0.13733 | 0.16937 | -62.6907 | 60.26 | 60.2783 | 62.2604 | 62.5076 | 123.0881 | 62.4985 | 60.4568
7698.4688 | 0.061035 | 0.46783 | -0.78827 | -0.20935 | 0.14954 | -0.27985 | -0.17731 | 60.585 | -62.3154 | 0.082397 | -62.5442 | 60.3195 | 62.4344 | 62.3383 | 0.076294 | -0.0737 | 0.086517 | 0.28839 | -0.16449 | -0.14313 | 0.054932 | 0.11444 | -62.677 | 60.3104 | 60.2829 | 62.2879 | 62.4939 | 123.1338 | 62.4527 | 60.4385
7700.1875 | 0.061035 | 0.44113 | -0.77972 | -0.19653 | 0.1709 | -0.24139 | -0.16449 | 60.5576 | -62.4252 | 0.059509 | -62.6083 | 60.3012 | 62.4893 | 62.4023 | 0.045776 | -0.046997 | 0.087585 | 0.29587 | -0.1474 | -0.15915 | 0.064087 | 0.07782 | -62.8098 | 60.3012 | 60.2921 | 62.3566 | 62.5534 | 123.2025 | 62.4985 | 60.3653
7701.8594 | 0.061035 | 0.46143 | -0.77866 | -0.19333 | 0.15274 | -0.24567 | -0.15701 | 60.5072 | -62.4619 | -0.022888 | -62.6404 | 60.3241 | 62.4847 | 62.3886 | 0.061035 | -0.061951 | 0.082245 | 0.298 | -0.14954 | -0.14847 | 0.018311 | 0.054932 | -62.8326 | 60.3149 | 60.2875 | 62.3566 | 62.558 | 123.2117 | 62.4802 | 60.3973
7703.625 | 0.076294 | 0.45395 | -0.77866 | -0.19653 | 0.15274 | -0.26703 | -0.1474 | 60.5255 | -62.4298 | 0.013733 | -62.6266 | 60.3195 | 62.4664 | 62.3611 | 0.061035 | -0.053406 | 0.093994 | 0.30014 | -0.15701 | -0.14206 | 0.068665 | 0.082397 | -62.7823 | 60.2737 | 60.2921 | 62.3199 | 62.5122 | 123.2391 | 62.4527 | 60.4065
7705.3125 | 0.045776 | 0.43152 | -0.76691 | -0.22324 | 0.16769 | -0.2446 | -0.15488 | 60.5576 | -62.4069 | 0.091553 | -62.6083 | 60.2783 | 62.5214 | 62.4161 | 0.061035 | -0.050201 | 0.095062 | 0.30441 | -0.16129 | -0.15488 | 0.073242 | 0.10986 | -62.7731 | 60.2371 | 60.2692 | 62.3337 | 62.5626 | 123.2025 | 62.4985 | 60.3607
7707 | 0.061035 | 0.46249 | -0.78507 | -0.21255 | 0.16022 | -0.29266 | -0.1741 | 60.5759 | -62.3245 | 0.09613 | -62.5214 | 60.3012 | 62.4115 | 62.3383 | 0.045776 | -0.083313 | 0.083313 | 0.2948 | -0.18158 | -0.13886 | 0.059509 | 0.11444 | -62.6633 | 60.2829 | 60.2783 | 62.2696 | 62.4756 | 123.111 | 62.4756 | 60.4385
7708.6875 | 0.061035 | 0.4454 | -0.77438 | -0.20294 | 0.15595 | -0.25207 | -0.16983 | 60.5164 | -62.4573 | 0.036621 | -62.6175 | 60.3333 | 62.4756 | 62.3886 | 0.076294 | -0.044861 | 0.091858 | 0.29587 | -0.16769 | -0.15167 | -0.013733 | 0.013733 | -62.8143 | 60.2966 | 60.2966 | 62.3383 | 62.5259 | 123.1705 | 62.4985 | 60.3516
7710.375 | 0.045776 | 0.45181 | -0.77331 | -0.20615 | 0.16556 | -0.24674 | -0.16769 | 60.4889 | -62.4847 | -0.004578 | -62.6358 | 60.3287 | 62.4664 | 62.3978 | 0.045776 | -0.05661 | 0.095062 | 0.29159 | -0.14633 | -0.14526 | 0.009155 | 0.022888 | -62.8784 | 60.3058 | 60.3058 | 62.3337 | 62.5442 | 123.1659 | 62.4893 | 60.3928
7712.0938 | 0.061035 | 0.4422 | -0.784 | -0.18799 | 0.16342 | -0.24994 | -0.16022 | 60.5026 | -62.4847 | -0.022888 | -62.6312 | 60.3058 | 62.4802 | 62.3795 | 0.061035 | -0.066223 | 0.09079 | 0.28519 | -0.14847 | -0.14954 | 0.032043 | 0.045776 | -62.8235 | 60.2921 | 60.2921 | 62.3199 | 62.5351 | 123.2025 | 62.4847 | 60.3745
7713.7812 | 0.061035 | 0.45075 | -0.78293 | -0.22751 | 0.16449 | -0.28412 | -0.16769 | 60.6171 | -62.2742 | 0.16022 | -62.5214 | 60.2829 | 62.4207 | 62.3337 | 0.045776 | -0.0737 | 0.09613 | 0.28946 | -0.18478 | -0.14099 | 0.082397 | 0.15106 | -62.6587 | 60.2646 | 60.3058 | 62.2696 | 62.4847 | 123.0835 | 62.4847 | 60.4202
7715.5 | 0.076294 | 0.4689 | -0.78827 | -0.1976 | 0.16342 | -0.25742 | -0.17197 | 60.6125 | -62.3154 | 0.10986 | -62.5259 | 60.2966 | 62.4344 | 62.3154 | 0.061035 | -0.068359 | 0.082245 | 0.30121 | -0.13779 | -0.14847 | 0.1236 | 0.1831 | -62.677 | 60.2829 | 60.2509 | 62.2787 | 62.4893 | 123.1796 | 62.4573 | 60.4156
7717.1719 | 0.061035 | 0.44647 | -0.77652 | -0.2179 | 0.16129 | -0.25207 | -0.17303 | 60.5209 | -62.4161 | 0.07782 | -62.6083 | 60.3104 | 62.4527 | 62.3703 | 0.045776 | -0.064087 | 0.095062 | 0.29373 | -0.1709 | -0.15274 | -0.009155 | 0 | -62.796 | 60.3104 | 60.3195 | 62.3245 | 62.5168 | 123.0652 | 62.5122 | 60.4156
7718.8906 | 0.045776 | 0.44861 | -0.77545 | -0.18585 | 0.15808 | -0.24246 | -0.15915 | 60.5621 | -62.4069 | 0.07782 | -62.5763 | 60.2966 | 62.4756 | 62.4115 | 0.076294 | -0.049133 | 0.081177 | 0.30548 | -0.15381 | -0.13992 | 0.054932 | 0.068665 | -62.7823 | 60.26 | 60.2692 | 62.3245 | 62.5717 | 123.1888 | 62.4527 | 60.3653
7720.625 | 0.061035 | 0.44113 | -0.78293 | -0.20401 | 0.16022 | -0.24994 | -0.16342 | 60.5576 | -62.3932 | 0.091553 | -62.6038 | 60.2875 | 62.4802 | 62.3978 | 0.045776 | -0.045929 | 0.10254 | 0.30121 | -0.14313 | -0.13565 | 0.050354 | 0.068665 | -62.8006 | 60.2646 | 60.2692 | 62.3611 | 62.5534 | 123.1384 | 62.5031 | 60.3928
7722.3125 | 0.061035 | 0.46249 | -0.77972 | -0.19653 | 0.15808 | -0.2681 | -0.16876 | 60.5759 | -62.3291 | 0.09613 | -62.5305 | 60.2966 | 62.4344 | 62.3428 | 0.091553 | -0.072632 | 0.086517 | 0.298 | -0.15274 | -0.1506 | 0.11902 | 0.1831 | -62.6862 | 60.2509 | 60.2417 | 62.2971 | 62.4893 | 123.1796 | 62.4756 | 60.4065
7724 | 0.061035 | 0.45929 | -0.7872 | -0.21362 | 0.15701 | -0.28732 | -0.16769 | 60.5804 | -62.3337 | 0.07782 | -62.5442 | 60.3287 | 62.3932 | 62.3108 | 0.061035 | -0.077972 | 0.084381 | 0.28519 | -0.18372 | -0.14099 | 0.045776 | 0.091553 | -62.6953 | 60.2966 | 60.3104 | 62.2833 | 62.4893 | 123.056 | 62.4802 | 60.4477
7725.7031 | 0.076294 | 0.46997 | -0.79041 | -0.18692 | 0.16022 | -0.27237 | -0.18478 | 60.5988 | -62.2879 | 0.10071 | -62.5259 | 60.2783 | 62.3749 | 62.2925 | 0.061035 | -0.072632 | 0.074768 | 0.29373 | -0.1741 | -0.14206 | 0.11444 | 0.13275 | -62.6907 | 60.26 | 60.2325 | 62.265 | 62.4664 | 123.0606 | 62.4985 | 60.4752
7727.375 | 0.076294 | 0.43579 | -0.76691 | -0.21896 | 0.16556 | -0.25421 | -0.16876 | 60.5026 | -62.4527 | 0.050354 | -62.6175 | 60.3378 | 62.4619 | 62.384 | 0.061035 | -0.043793 | 0.095062 | 0.2948 | -0.15915 | -0.15808 | 0 | 0.022888 | -62.796 | 60.3104 | 60.2875 | 62.3337 | 62.5351 | 123.1705 | 62.4619 | 60.3653
7729.1094 | 0.061035 | 0.43579 | -0.78079 | -0.18158 | 0.16876 | -0.24567 | -0.16769 | 60.4797 | -62.471 | -0.004578 | -62.6358 | 60.3378 | 62.471 | 62.384 | 0.061035 | -0.055542 | 0.09079 | 0.29694 | -0.1474 | -0.1474 | 0.004578 | 0.032043 | -62.8326 | 60.2829 | 60.2737 | 62.3291 | 62.5397 | 123.1338 | 62.471 | 60.3882
7730.7969 | 0.061035 | 0.45609 | -0.7872 | -0.21469 | 0.16342 | -0.28198 | -0.17624 | 60.5621 | -62.3337 | 0.064087 | -62.5259 | 60.3149 | 62.3978 | 62.3062 | 0.061035 | -0.077972 | 0.087585 | 0.28625 | -0.16983 | -0.13351 | 0.045776 | 0.082397 | -62.6907 | 60.2921 | 60.3104 | 62.2559 | 62.4893 | 123.0606 | 62.4847 | 60.434
7732.5625 | 0.061035 | 0.45715 | -0.77652 | -0.21255 | 0.14526 | -0.26382 | -0.16769 | 60.585 | -62.3428 | 0.068665 | -62.5442 | 60.3104 | 62.3978 | 62.3016 | 0.061035 | -0.072632 | 0.091858 | 0.28839 | -0.17731 | -0.15488 | 0.059509 | 0.086975 | -62.6862 | 60.3012 | 60.3058 | 62.2421 | 62.4802 | 123.0698 | 62.4802 | 60.4385
7734.25 | 0.061035 | 0.43472 | -0.76691 | -0.20401 | 0.16235 | -0.23498 | -0.16449 | 60.553 | -62.3978 | 0.086975 | -62.5992 | 60.2737 | 62.4847 | 62.4023 | 0.045776 | -0.048065 | 0.082245 | 0.31296 | -0.15274 | -0.16022 | 0.086975 | 0.086975 | -62.7914 | 60.2509 | 60.26 | 62.3383 | 62.5534 | 123.143 | 62.4847 | 60.3287
7735.9375 | 0.061035 | 0.46249 | -0.79254 | -0.19546 | 0.15915 | -0.28625 | -0.16876 | 60.553 | -62.3154 | 0.073242 | -62.5259 | 60.3195 | 62.3932 | 62.3154 | 0.045776 | -0.076904 | 0.079041 | 0.29907 | -0.16663 | -0.14099 | 0.054932 | 0.09613 | -62.6862 | 60.2875 | 60.2966 | 62.2742 | 62.471 | 123.056 | 62.4802 | 60.4614
7737.6406 | 0.061035 | 0.45609 | -0.77545 | -0.18051 | 0.16235 | -0.24994 | -0.16876 | 60.4843 | -62.4481 | -0.022888 | -62.6038 | 60.3058 | 62.471 | 62.3611 | 0.061035 | -0.049133 | 0.083313 | 0.29907 | -0.14847 | -0.1442 | 0.032043 | 0.032043 | -62.8281 | 60.2921 | 60.2783 | 62.3154 | 62.5351 | 123.1659 | 62.4527 | 60.3836
7739.3281 | 0.061035 | 0.45395 | -0.78507 | -0.20615 | 0.15167 | -0.27664 | -0.16769 | 60.6125 | -62.233 | 0.17395 | -62.5031 | 60.2783 | 62.3932 | 62.3108 | 0.091553 | -0.070496 | 0.089722 | 0.29053 | -0.16663 | -0.14633 | 0.10986 | 0.13733 | -62.6266 | 60.2554 | 60.26 | 62.2604 | 62.4939 | 123.0652 | 62.4619 | 60.4156
7741.0156 | 0.045776 | 0.45609 | -0.78613 | -0.18478 | 0.16663 | -0.24567 | -0.16129 | 60.5759 | -62.2925 | 0.082397 | -62.5259 | 60.3104 | 62.4207 | 62.3245 | 0.061035 | -0.067291 | 0.075836 | 0.28839 | -0.1506 | -0.1474 | 0.13275 | 0.1831 | -62.6724 | 60.2463 | 60.2463 | 62.2833 | 62.4527 | 123.1705 | 62.4344 | 60.379
7742.7188 | 0.061035 | 0.45502 | -0.78186 | -0.22324 | 0.16022 | -0.24567 | -0.17624 | 60.4935 | -62.4252 | 0.036621 | -62.6083 | 60.3149 | 62.4527 | 62.352 | 0.061035 | -0.054474 | 0.079041 | 0.30121 | -0.16235 | -0.13458 | 0 | 0.018311 | -62.7914 | 60.2875 | 60.3012 | 62.3291 | 62.5031 | 123.111 | 62.4893 | 60.3699
7744.4062 | 0.061035 | 0.44327 | -0.78186 | -0.19226 | 0.1506 | -0.24994 | -0.16022 | 60.5255 | -62.3749 | 0.07782 | -62.5763 | 60.2921 | 62.4573 | 62.3337 | 0.030518 | -0.050201 | 0.084381 | 0.30121 | -0.15488 | -0.14206 | 0.050354 | 0.07782 | -62.7914 | 60.2509 | 60.2463 | 62.3245 | 62.5351 | 123.1018 | 62.471 | 60.379
7746.0938 | 0.045776 | 0.4657 | -0.78827 | -0.20294 | 0.15274 | -0.27237 | -0.16876 | 60.5576 | -62.2879 | 0.07782 | -62.5259 | 60.2875 | 62.384 | 62.2787 | 0.061035 | -0.09079 | 0.077972 | 0.28946 | -0.15915 | -0.13886 | 0.064087 | 0.10529 | -62.6953 | 60.26 | 60.2692 | 62.2513 | 62.4664 | 123.024 | 62.4527 | 60.4431
7747.7656 | 0.061035 | 0.44861 | -0.78613 | -0.22003 | 0.15701 | -0.27878 | -0.17838 | 60.553 | -62.3199 | 0.073242 | -62.5259 | 60.3104 | 62.3703 | 62.2833 | 0.061035 | -0.076904 | 0.085449 | 0.29159 | -0.17731 | -0.15488 | 0.045776 | 0.091553 | -62.677 | 60.2417 | 60.2921 | 62.265 | 62.4573 | 123.0927 | 62.439 | 60.434
7749.4531 | 0.045776 | 0.43259 | -0.77759 | -0.20187 | 0.1506 | -0.24994 | -0.16663 | 60.5301 | -62.384 | 0.082397 | -62.5717 | 60.2554 | 62.4619 | 62.3978 | 0.061035 | -0.054474 | 0.089722 | 0.31616 | -0.15167 | -0.16342 | 0.073242 | 0.09613 | -62.7731 | 60.26 | 60.2509 | 62.3383 | 62.5214 | 123.1247 | 62.4573 | 60.3241
7751.125 | 0.045776 | 0.46143 | -0.79895 | -0.20508 | 0.16129 | -0.2713 | -0.16235 | 60.5667 | -62.2879 | 0.07782 | -62.5259 | 60.2783 | 62.3978 | 62.2971 | 0.061035 | -0.071564 | 0.081177 | 0.29159 | -0.16556 | -0.13886 | 0.059509 | 0.10071 | -62.677 | 60.2692 | 60.2783 | 62.2787 | 62.4527 | 123.0148 | 62.4802 | 60.4248
7752.8125 | 0.061035 | 0.45822 | -0.77972 | -0.20828 | 0.15595 | -0.27771 | -0.16769 | 60.5576 | -62.2971 | 0.07782 | -62.5122 | 60.3241 | 62.4161 | 62.3337 | 0.061035 | -0.074768 | 0.079041 | 0.28732 | -0.16342 | -0.1474 | 0.068665 | 0.10986 | -62.6495 | 60.2737 | 60.2737 | 62.2513 | 62.4252 | 123.0789 | 62.4527 | 60.3882
7754.5469 | 0.076294 | 0.43472 | -0.77759 | -0.19653 | 0.15274 | -0.23819 | -0.16235 | 60.5347 | -62.384 | 0.082397 | -62.5809 | 60.2692 | 62.4344 | 62.3795 | 0.061035 | -0.05661 | 0.084381 | 0.30334 | -0.14526 | -0.1474 | 0.064087 | 0.091553 | -62.7731 | 60.2737 | 60.2554 | 62.3154 | 62.5305 | 123.1293 | 62.4619 | 60.3516
7756.2344 | 0.076294 | 0.44434 | -0.78186 | -0.18372 | 0.1506 | -0.25101 | -0.1741 | 60.553 | -62.3337 | 0.059509 | -62.5442 | 60.2921 | 62.4161 | 62.3199 | 0.061035 | -0.057678 | 0.082245 | 0.29159 | -0.15701 | -0.14954 | 0.1236 | 0.16479 | -62.6816 | 60.2737 | 60.2234 | 62.3016 | 62.4756 | 123.1522 | 62.4481 | 60.3745
7757.9219 | 0.076294 | 0.45181 | -0.77972 | -0.21469 | 0.15595 | -0.26703 | -0.16876 | 60.5759 | -62.2696 | 0.13275 | -62.4847 | 60.2921 | 62.3795 | 62.2925 | 0.061035 | -0.080109 | 0.091858 | 0.29373 | -0.16983 | -0.15595 | 0.10529 | 0.13733 | -62.6312 | 60.2646 | 60.2554 | 62.2559 | 62.471 | 123.0606 | 62.439 | 60.4019
7759.6406 | 0.061035 | 0.45609 | -0.77866 | -0.19653 | 0.16556 | -0.25101 | -0.15701 | 60.5301 | -62.3657 | 0.041199 | -62.5442 | 60.3104 | 62.4252 | 62.3291 | 0.076294 | -0.05661 | 0.075836 | 0.29587 | -0.1474 | -0.15488 | 0.10986 | 0.15564 | -62.6999 | 60.2692 | 60.2234 | 62.2696 | 62.4756 | 123.1476 | 62.4344 | 60.3699
7761.3125 | 0.045776 | 0.43472 | -0.78293 | -0.21469 | 0.15595 | -0.26062 | -0.16449 | 60.5118 | -62.3749 | 0.086975 | -62.5717 | 60.2737 | 62.4252 | 62.352 | 0.061035 | -0.058746 | 0.097198 | 0.29587 | -0.16983 | -0.1506 | 0.004578 | 0.009155 | -62.764 | 60.2737 | 60.2875 | 62.3154 | 62.5351 | 123.0194 | 62.471 | 60.3882
7763 | 0.091553 | 0.44434 | -0.78507 | -0.1944 | 0.1474 | -0.24567 | -0.16235 | 60.4385 | -62.4619 | -0.004578 | -62.6221 | 60.2966 | 62.4527 | 62.3703 | 0.045776 | -0.055542 | 0.088654 | 0.2948 | -0.14954 | -0.14847 | 0.022888 | 0.032043 | -62.8235 | 60.2646 | 60.2509 | 62.3245 | 62.5305 | 123.111 | 62.4435 | 60.379
7764.7031 | 0.045776 | 0.44434 | -0.78293 | -0.20187 | 0.15915 | -0.26062 | -0.1506 | 60.5759 | -62.2742 | 0.1236 | -62.5031 | 60.2509 | 62.4069 | 62.3016 | 0.076294 | -0.0737 | 0.082245 | 0.29159 | -0.16235 | -0.1442 | 0.1236 | 0.18768 | -62.6495 | 60.2463 | 60.2371 | 62.2742 | 62.4527 | 123.0835 | 62.4527 | 60.4019
7766.3906 | 0.061035 | 0.44861 | -0.77759 | -0.22324 | 0.16022 | -0.27557 | -0.1741 | 60.6125 | -62.2238 | 0.16937 | -62.4756 | 60.2921 | 62.3932 | 62.3016 | 0.061035 | -0.079041 | 0.087585 | 0.28198 | -0.16769 | -0.14954 | 0.10071 | 0.15106 | -62.6129 | 60.2371 | 60.26 | 62.2559 | 62.471 | 123.0286 | 62.4573 | 60.4111
7768.0938 | 0.061035 | 0.45288 | -0.79575 | -0.1976 | 0.16769 | -0.2713 | -0.16449 | 60.5896 | -62.2375 | 0.16022 | -62.4985 | 60.2737 | 62.3886 | 62.3062 | 0.045776 | -0.072632 | 0.086517 | 0.27985 | -0.16129 | -0.14954 | 0.07782 | 0.12817 | -62.6312 | 60.2463 | 60.2188 | 62.2696 | 62.4802 | 123.0011 | 62.4802 | 60.3928
7769.7656 | 0.076294 | 0.43152 | -0.76691 | -0.20294 | 0.17303 | -0.23712 | -0.16663 | 60.4935 | -62.384 | 0.059509 | -62.5717 | 60.2921 | 62.4664 | 62.3703 | 0.030518 | -0.050201 | 0.095062 | 0.29053 | -0.15381 | -0.15274 | 0.054932 | 0.068665 | -62.7548 | 60.2875 | 60.26 | 62.3199 | 62.5168 | 123.1384 | 62.439 | 60.3378
7771.4531 | 0.076294 | 0.45502 | -0.77331 | -0.21255 | 0.14847 | -0.28198 | -0.17197 | 60.5804 | -62.2421 | 0.11902 | -62.471 | 60.2875 | 62.3795 | 62.3108 | 0.061035 | -0.074768 | 0.085449 | 0.29159 | -0.17731 | -0.14847 | 0.10071 | 0.13275 | -62.5946 | 60.2509 | 60.2463 | 62.2467 | 62.4573 | 123.056 | 62.4527 | 60.4111
7773.1562 | 0.045776 | 0.42831 | -0.77331 | -0.20401 | 0.15274 | -0.24887 | -0.16876 | 60.5164 | -62.3703 | 0.082397 | -62.5671 | 60.2875 | 62.471 | 62.3795 | 0.076294 | -0.053406 | 0.10788 | 0.30014 | -0.1506 | -0.1506 | 0.054932 | 0.086975 | -62.7548 | 60.2417 | 60.2325 | 62.3428 | 62.5122 | 123.1293 | 62.4527 | 60.3561
7774.8594 | 0.045776 | 0.43579 | -0.78079 | -0.21042 | 0.13672 | -0.25635 | -0.17517 | 60.466 | -62.3886 | 0.064087 | -62.5854 | 60.2829 | 62.4527 | 62.3749 | 0.061035 | -0.059814 | 0.082245 | 0.29159 | -0.16769 | -0.14847 | 0 | 0.018311 | -62.7686 | 60.2692 | 60.2737 | 62.3291 | 62.5168 | 123.0286 | 62.4847 | 60.3699
7776.6406 | 0.076294 | 0.45715 | -0.77866 | -0.20721 | 0.1442 | -0.27344 | -0.16769 | 60.6079 | -62.1918 | 0.16479 | -62.4619 | 60.2646 | 62.3795 | 62.2879 | 0.076294 | -0.076904 | 0.079041 | 0.29053 | -0.16449 | -0.1442 | 0.086975 | 0.16479 | -62.5992 | 60.2554 | 60.2417 | 62.2467 | 62.4435 | 123.0286 | 62.4435 | 60.3882
7778.3281 | 0.076294 | 0.45075 | -0.77225 | -0.20508 | 0.15488 | -0.2478 | -0.1709 | 60.4797 | -62.3886 | 0.045776 | -62.5763 | 60.3058 | 62.4619 | 62.3886 | 0.076294 | -0.058746 | 0.076904 | 0.29907 | -0.15701 | -0.15274 | -0.004578 | 0.041199 | -62.7777 | 60.2829 | 60.2646 | 62.3245 | 62.5305 | 123.1384 | 62.4481 | 60.3287
7780.0312 | 0.045776 | 0.44968 | -0.79254 | -0.20294 | 0.14847 | -0.27344 | -0.17197 | 60.585 | -62.2513 | 0.10986 | -62.5076 | 60.26 | 62.384 | 62.2971 | 0.061035 | -0.069427 | 0.069427 | 0.29159 | -0.15915 | -0.15274 | 0.1236 | 0.16022 | -62.6266 | 60.228 | 60.2371 | 62.2513 | 62.4435 | 123.0194 | 62.4481 | 60.3882
7781.7188 | 0.091553 | 0.44434 | -0.77331 | -0.20508 | 0.15595 | -0.24033 | -0.17197 | 60.498 | -62.3474 | 0.082397 | -62.5763 | 60.2829 | 62.4207 | 62.3657 | 0.076294 | -0.053406 | 0.0737 | 0.29053 | -0.14847 | -0.14954 | 0.041199 | 0.064087 | -62.7869 | 60.2509 | 60.2234 | 62.3474 | 62.5351 | 123.0835 | 62.4527 | 60.3378
7783.4375 | 0.076294 | 0.43366 | -0.77759 | -0.19974 | 0.14847 | -0.25207 | -0.16876 | 60.4889 | -62.3474 | 0.082397 | -62.558 | 60.2692 | 62.4664 | 62.352 | 0.045776 | -0.058746 | 0.085449 | 0.29053 | -0.15274 | -0.14313 | 0.068665 | 0.09613 | -62.7411 | 60.2325 | 60.2142 | 62.3337 | 62.5031 | 123.0881 | 62.4619 | 60.3287
7785.1094 | 0.061035 | 0.46036 | -0.78934 | -0.20935 | 0.15274 | -0.298 | -0.16449 | 60.5301 | -62.2787 | 0.073242 | -62.5214 | 60.2509 | 62.384 | 62.3016 | 0.076294 | -0.074768 | 0.079041 | 0.28625 | -0.16022 | -0.12924 | 0.059509 | 0.10529 | -62.6587 | 60.2509 | 60.2509 | 62.2467 | 62.4619 | 122.9874 | 62.4664 | 60.4248
7786.7969 | 0.045776 | 0.45395 | -0.78186 | -0.21683 | 0.15167 | -0.2681 | -0.16449 | 60.498 | -62.3154 | 0.09613 | -62.5214 | 60.2646 | 62.4115 | 62.3291 | 0.076294 | -0.071564 | 0.075836 | 0.2948 | -0.16876 | -0.13992 | -0.004578 | 0.018311 | -62.7457 | 60.2692 | 60.26 | 62.3062 | 62.5214 | 122.9874 | 62.4893 | 60.379
7788.5 | 0.030518 | 0.43472 | -0.77331 | -0.20721 | 0.16129 | -0.25207 | -0.16769 | 60.4752 | -62.3795 | 0.068665 | -62.5488 | 60.2875 | 62.4435 | 62.3657 | 0.061035 | -0.054474 | 0.091858 | 0.30441 | -0.14313 | -0.16342 | 0.022888 | 0.059509 | -62.7365 | 60.2692 | 60.2463 | 62.3108 | 62.5397 | 123.1018 | 62.4344 | 60.3287
7790.1875 | 0.030518 | 0.4422 | -0.78827 | -0.21255 | 0.15381 | -0.27237 | -0.16876 | 60.5026 | -62.3154 | 0.10529 | -62.5214 | 60.2692 | 62.4069 | 62.3199 | 0.061035 | -0.072632 | 0.095062 | 0.29159 | -0.16769 | -0.1506 | -0.004578 | 0.032043 | -62.7365 | 60.2692 | 60.2554 | 62.2742 | 62.4985 | 122.9828 | 62.4756 | 60.3882
7791.8594 | 0.076294 | 0.43686 | -0.77545 | -0.19119 | 0.15915 | -0.24674 | -0.16556 | 60.4752 | -62.3886 | 0.036621 | -62.59 | 60.2509 | 62.4481 | 62.3657 | 0.091553 | -0.053406 | 0.085449 | 0.29053 | -0.1506 | -0.16235 | 0.022888 | 0.045776 | -62.7869 | 60.2509 | 60.2371 | 62.3245 | 62.4939 | 123.0652 | 62.4435 | 60.3516
7793.5469 | 0.045776 | 0.4454 | -0.77972 | -0.21149 | 0.15808 | -0.27344 | -0.17303 | 60.5072 | -62.2971 | 0.11902 | -62.5122 | 60.2875 | 62.4069 | 62.3383 | 0.061035 | -0.057678 | 0.084381 | 0.29159 | -0.16769 | -0.13992 | 0 | 0.041199 | -62.7182 | 60.2417 | 60.2783 | 62.2787 | 62.5031 | 122.9874 | 62.4527 | 60.3699
7795.25 | 0.045776 | 0.44861 | -0.78293 | -0.1976 | 0.15595 | -0.25955 | -0.16449 | 60.5347 | -62.2787 | 0.073242 | -62.5031 | 60.2646 | 62.3932 | 62.3016 | 0.045776 | -0.066223 | 0.086517 | 0.29159 | -0.14954 | -0.14633 | 0.13733 | 0.15106 | -62.6541 | 60.2371 | 60.2371 | 62.265 | 62.4527 | 123.1064 | 62.4161 | 60.3561
7796.9688 | 0.076294 | 0.4422 | -0.77972 | -0.19974 | 0.16129 | -0.25101 | -0.15701 | 60.434 | -62.4115 | -0.013733 | -62.59 | 60.2783 | 62.4207 | 62.3383 | 0.061035 | -0.063019 | 0.077972 | 0.29694 | -0.1442 | -0.13992 | 0.036621 | 0.032043 | -62.7686 | 60.2783 | 60.2325 | 62.3108 | 62.5259 | 123.1018 | 62.4298 | 60.3653
7798.6719 | 0.091553 | 0.43686 | -0.78186 | -0.19546 | 0.16556 | -0.25314 | -0.16769 | 60.4385 | -62.4069 | 0.009155 | -62.59 | 60.2875 | 62.4435 | 62.3703 | 0.076294 | -0.054474 | 0.077972 | 0.29373 | -0.15488 | -0.13886 | -0.009155 | 0.041199 | -62.8006 | 60.2463 | 60.2554 | 62.3474 | 62.5259 | 123.0515 | 62.4161 | 60.379
7800.3594 | 0.030518 | 0.45502 | -0.79254 | -0.2179 | 0.16129 | -0.29587 | -0.16876 | 60.4843 | -62.2879 | 0.054932 | -62.5122 | 60.2875 | 62.3611 | 62.3199 | 0.076294 | -0.081177 | 0.079041 | 0.28519 | -0.17731 | -0.14313 | 0.032043 | 0.091553 | -62.6495 | 60.2692 | 60.2463 | 62.2375 | 62.4435 | 122.9965 | 62.4161 | 60.4202
7802.0469 | 0.061035 | 0.41122 | -0.77225 | -0.21683 | 0.15167 | -0.24674 | -0.16983 | 60.5026 | -62.3657 | 0.073242 | -62.5442 | 60.2966 | 62.4435 | 62.3428 | 0.061035 | -0.059814 | 0.085449 | 0.29266 | -0.16769 | -0.16022 | 0.045776 | 0.073242 | -62.7411 | 60.2417 | 60.2509 | 62.3199 | 62.5076 | 123.1064 | 62.4069 | 60.3012
7803.7656 | 0.061035 | 0.45288 | -0.78613 | -0.21255 | 0.15381 | -0.29373 | -0.16449 | 60.585 | -62.2009 | 0.14648 | -62.4573 | 60.2463 | 62.3703 | 62.2833 | 0.045776 | -0.076904 | 0.077972 | 0.29694 | -0.1741 | -0.1442 | 0.091553 | 0.13733 | -62.5809 | 60.2325 | 60.2692 | 62.2421 | 62.4161 | 122.9828 | 62.4344 | 60.3653
7805.4844 | 0.061035 | 0.44434 | -0.77652 | -0.20401 | 0.14847 | -0.26596 | -0.17944 | 60.4935 | -62.3154 | 0.064087 | -62.5214 | 60.26 | 62.3978 | 62.3291 | 0.061035 | -0.065155 | 0.081177 | 0.29159 | -0.15915 | -0.15701 | -0.004578 | 0.013733 | -62.7319 | 60.26 | 60.2509 | 62.2787 | 62.4847 | 122.9599 | 62.4619 | 60.3607
7807.1719 | 0.061035 | 0.43152 | -0.77652 | -0.18906 | 0.16022 | -0.24567 | -0.16235 | 60.4385 | -62.4069 | -0.009155 | -62.5763 | 60.2646 | 62.4435 | 62.3383 | 0.045776 | -0.058746 | 0.080109 | 0.29053 | -0.14954 | -0.15488 | 0.027466 | 0.036621 | -62.7823 | 60.2554 | 60.2417 | 62.2925 | 62.5397 | 123.0743 | 62.4298 | 60.3561
7808.875 | 0.045776 | 0.45395 | -0.77759 | -0.20294 | 0.16449 | -0.27557 | -0.16449 | 60.5118 | -62.2421 | 0.14191 | -62.4939 | 60.26 | 62.3932 | 62.3199 | 0.061035 | -0.065155 | 0.088654 | 0.28946 | -0.16983 | -0.14847 | 0.027466 | 0.054932 | -62.6724 | 60.2509 | 60.2417 | 62.2833 | 62.4756 | 122.9599 | 62.439 | 60.3973
7810.625 | 0.076294 | 0.44113 | -0.7872 | -0.21255 | 0.15701 | -0.25421 | -0.18158 | 60.5072 | -62.3108 | 0.10986 | -62.4664 | 60.2875 | 62.4069 | 62.3337 | 0.076294 | -0.069427 | 0.1004 | 0.29266 | -0.16663 | -0.14633 | 0.059509 | 0.13733 | -62.7411 | 60.2463 | 60.2509 | 62.3108 | 62.5351 | 123.0881 | 62.4481 | 60.3973
7812.3125 | 0.061035 | 0.46036 | -0.78293 | -0.18906 | 0.15808 | -0.27771 | -0.17303 | 60.553 | -62.265 | 0.14648 | -62.3154 | 60.2875 | 62.3566 | 62.2787 | 0.045776 | -0.079041 | 0.081177 | 0.29159 | -0.15808 | -0.14954 | 0.23804 | 0.2243 | -62.6358 | 60.2509 | 60.2325 | 62.233 | 62.4619 | 123.3124 | 62.4298 | 60.4111
7813.9844 | 0.045776 | 0.44647 | -0.78186 | -0.21362 | 0.1506 | -0.27451 | -0.18051 | 60.6171 | -62.2192 | 0.21057 | -62.2421 | 60.2646 | 62.3932 | 62.2925 | 0.061035 | -0.068359 | 0.087585 | 0.29159 | -0.16235 | -0.15595 | 0.26093 | 0.55389 | -62.5671 | 60.2234 | 60.2417 | 62.2513 | 62.4985 | 123.2117 | 62.4344 | 60.4065
7815.6719 | 0.061035 | 0.43472 | -0.77545 | -0.21576 | 0.15274 | -0.25314 | -0.17838 | 60.5209 | -62.3154 | 0.11444 | -62.2833 | 60.2875 | 62.3795 | 62.3383 | 0.045776 | -0.058746 | 0.083313 | 0.2948 | -0.16983 | -0.14954 | 0.22888 | 0.60883 | -62.6633 | 60.2463 | 60.2554 | 62.3016 | 62.4893 | 123.3307 | 62.4573 | 60.3653
7817.3438 | 0.061035 | 0.44968 | -0.77759 | -0.18265 | 0.16449 | -0.24567 | -0.16769 | 60.4431 | -62.3932 | -0.009155 | -62.5671 | 60.2966 | 62.4161 | 62.352 | 0.061035 | -0.054474 | 0.085449 | 0.28839 | -0.14206 | -0.15167 | 0.041199 | 0.059509 | -62.7502 | 60.2646 | 60.2417 | 62.2833 | 62.5076 | 123.1064 | 62.4069 | 60.3378
7819.0312 | 0.045776 | 0.44113 | -0.79041 | -0.20935 | 0.15595 | -0.27451 | -0.16342 | 60.5621 | -62.2101 | 0.17395 | -62.471 | 60.2554 | 62.3474 | 62.2971 | 0.045776 | -0.074768 | 0.082245 | 0.29053 | -0.16876 | -0.15274 | 0.091553 | 0.12817 | -62.6175 | 60.2005 | 60.2142 | 62.2375 | 62.4619 | 122.9599 | 62.4481 | 60.3699
7820.7344 | 0.045776 | 0.45502 | -0.77866 | -0.20721 | 0.16022 | -0.28412 | -0.17624 | 60.5621 | -62.1918 | 0.15106 | -62.4527 | 60.2692 | 62.3245 | 62.2742 | 0.076294 | -0.069427 | 0.074768 | 0.298 | -0.1709 | -0.15488 | 0.1236 | 0.14648 | -62.5717 | 60.2234 | 60.2188 | 62.2375 | 62.439 | 123.0194 | 62.4115 | 60.3699
7822.4062 | 0.030518 | 0.43472 | -0.78293 | -0.19546 | 0.1474 | -0.23498 | -0.16769 | 60.5164 | -62.3337 | 0.07782 | -62.5442 | 60.2463 | 62.4435 | 62.3474 | 0.061035 | -0.055542 | 0.089722 | 0.30014 | -0.15915 | -0.15915 | 0.07782 | 0.10071 | -62.7274 | 60.228 | 60.2325 | 62.3062 | 62.5397 | 123.0423 | 62.4298 | 60.3287
7824.0781 | 0.076294 | 0.47531 | -0.79147 | -0.18906 | 0.15808 | -0.27451 | -0.16449 | 60.498 | -62.2421 | 0.082397 | -62.4802 | 60.2692 | 62.352 | 62.2833 | 0.076294 | -0.091858 | 0.063019 | 0.28839 | -0.15488 | -0.13886 | 0.064087 | 0.082397 | -62.6266 | 60.26 | 60.2646 | 62.2421 | 62.439 | 122.9736 | 62.4344 | 60.4111
7825.75 | 0.061035 | 0.44434 | -0.78186 | -0.22003 | 0.15701 | -0.26276 | -0.17517 | 60.5026 | -62.3062 | 0.086975 | -62.5214 | 60.2783 | 62.3886 | 62.3108 | 0.045776 | -0.057678 | 0.071564 | 0.28946 | -0.16129 | -0.15488 | -0.004578 | 0.013733 | -62.7136 | 60.2692 | 60.2737 | 62.2971 | 62.4939 | 122.9462 | 62.4573 | 60.3653
7827.4375 | 0.076294 | 0.42938 | -0.77118 | -0.19974 | 0.1474 | -0.23819 | -0.16663 | 60.498 | -62.3108 | 0.07782 | -62.5488 | 60.2692 | 62.4115 | 62.3245 | 0.061035 | -0.045929 | 0.087585 | 0.298 | -0.15381 | -0.14847 | 0.064087 | 0.09613 | -62.7319 | 60.2188 | 60.2005 | 62.2971 | 62.4985 | 123.0377 | 62.4207 | 60.3287
7829.125 | 0.076294 | 0.439 | -0.77652 | -0.22644 | 0.16022 | -0.25848 | -0.16556 | 60.4248 | -62.352 | 0.050354 | -62.5488 | 60.2829 | 62.4207 | 62.3337 | 0.045776 | -0.060883 | 0.09079 | 0.29373 | -0.16129 | -0.14099 | -0.013733 | 0.022888 | -62.7594 | 60.2463 | 60.2554 | 62.3062 | 62.5076 | 122.9965 | 62.4619 | 60.3424
7830.7969 | 0.061035 | 0.45929 | -0.78186 | -0.19012 | 0.14526 | -0.27237 | -0.16556 | 60.5301 | -62.2055 | 0.11902 | -62.471 | 60.2188 | 62.4023 | 62.2833 | 0.076294 | -0.068359 | 0.072632 | 0.28839 | -0.14954 | -0.1506 | 0.11444 | 0.16479 | -62.6038 | 60.2325 | 60.2005 | 62.2559 | 62.4664 | 122.9828 | 62.4023 | 60.4019
7832.4688 | 0.061035 | 0.43045 | -0.79254 | -0.19653 | 0.14954 | -0.27023 | -0.17197 | 60.4385 | -62.3657 | 0.059509 | -62.5626 | 60.2692 | 62.4252 | 62.3291 | 0.076294 | -0.05661 | 0.086517 | 0.29053 | -0.16342 | -0.14526 | -0.009155 | 0 | -62.7457 | 60.2829 | 60.2509 | 62.3062 | 62.5305 | 122.9782 | 62.4344 | 60.3149
7834.1562 | 0.061035 | 0.44113 | -0.77972 | -0.19119 | 0.15488 | -0.26703 | -0.16663 | 60.5438 | -62.2284 | 0.10986 | -62.471 | 60.2554 | 62.3657 | 62.2879 | 0.030518 | -0.0737 | 0.082245 | 0.27557 | -0.1474 | -0.15167 | 0.1236 | 0.16937 | -62.5946 | 60.2005 | 60.2097 | 62.2238 | 62.439 | 123.0286 | 62.4115 | 60.3882
7835.8906 | 0.061035 | 0.43152 | -0.77972 | -0.19012 | 0.15808 | -0.25101 | -0.16556 | 60.434 | -62.3886 | 0.018311 | -62.558 | 60.2554 | 62.4298 | 62.3657 | 0.061035 | -0.040588 | 0.074768 | 0.29587 | -0.1506 | -0.15488 | 0.009155 | 0.041199 | -62.7731 | 60.26 | 60.2371 | 62.3062 | 62.5259 | 123.0331 | 62.4298 | 60.3378
7837.6406 | 0.045776 | 0.43259 | -0.77545 | -0.22003 | 0.15167 | -0.25635 | -0.16449 | 60.4248 | -62.3657 | 0.050354 | -62.5442 | 60.26 | 62.4207 | 62.3108 | 0.076294 | -0.053406 | 0.083313 | 0.30441 | -0.16449 | -0.1506 | 0 | 0.009155 | -62.7411 | 60.2737 | 60.2646 | 62.2833 | 62.5076 | 122.9965 | 62.4207 | 60.3424
7839.3438 | 0.076294 | 0.44754 | -0.78186 | -0.20721 | 0.13565 | -0.28625 | -0.1741 | 60.5026 | -62.2421 | 0.07782 | -62.4664 | 60.2554 | 62.3154 | 62.2421 | 0.061035 | -0.076904 | 0.083313 | 0.28412 | -0.16129 | -0.13886 | 0.064087 | 0.10071 | -62.6221 | 60.2234 | 60.2325 | 62.2467 | 62.4344 | 122.9187 | 62.4207 | 60.4202
7841.0469 | 0.045776 | 0.46677 | -0.77866 | -0.17944 | 0.16022 | -0.27023 | -0.16983 | 60.553 | -62.2284 | 0.11902 | -62.4619 | 60.228 | 62.352 | 62.265 | 0.076294 | -0.075836 | 0.079041 | 0.28305 | -0.15274 | -0.15274 | 0.1236 | 0.16937 | -62.6038 | 60.2188 | 60.1959 | 62.2513 | 62.4527 | 122.9645 | 62.4252 | 60.379
7842.7344 | 0.076294 | 0.42191 | -0.78827 | -0.22003 | 0.15808 | -0.2713 | -0.17944 | 60.5118 | -62.2421 | 0.1236 | -62.4802 | 60.2234 | 62.352 | 62.3108 | 0.045776 | -0.057678 | 0.068359 | 0.28839 | -0.1741 | -0.15488 | 0.018311 | 0.064087 | -62.6724 | 60.26 | 60.228 | 62.265 | 62.4893 | 122.905 | 62.4115 | 60.3516
7844.4219 | 0.076294 | 0.45075 | -0.77545 | -0.21255 | 0.15701 | -0.2446 | -0.16342 | 60.4706 | -62.3245 | 0.022888 | -62.5214 | 60.2692 | 62.3932 | 62.2879 | 0.061035 | -0.067291 | 0.072632 | 0.28305 | -0.14313 | -0.14954 | 0.10071 | 0.13275 | -62.6587 | 60.2509 | 60.1822 | 62.2604 | 62.4619 | 123.0606 | 62.4023 | 60.347
7846.1094 | 0.061035 | 0.43686 | -0.77545 | -0.20294 | 0.15274 | -0.24246 | -0.15808 | 60.4202 | -62.3703 | 0.041199 | -62.5671 | 60.2417 | 62.4298 | 62.3337 | 0.061035 | -0.05661 | 0.081177 | 0.30014 | -0.14633 | -0.14954 | 0.032043 | 0.050354 | -62.764 | 60.2463 | 60.2097 | 62.3154 | 62.5351 | 122.9965 | 62.4207 | 60.3241
7847.7969 | 0.076294 | 0.4454 | -0.78934 | -0.22858 | 0.14847 | -0.28412 | -0.16663 | 60.5255 | -62.1964 | 0.12817 | -62.4298 | 60.2646 | 62.3383 | 62.265 | 0.045776 | -0.079041 | 0.082245 | 0.28732 | -0.17303 | -0.15274 | 0.09613 | 0.1236 | -62.5717 | 60.2142 | 60.2463 | 62.2284 | 62.4481 | 122.9828 | 62.3886 | 60.379
7849.4844 | 0.076294 | 0.43793 | -0.77652 | -0.20294 | 0.16022 | -0.23712 | -0.16342 | 60.4889 | -62.3154 | 0.086975 | -62.5259 | 60.2646 | 62.4023 | 62.3428 | 0.045776 | -0.061951 | 0.074768 | 0.28519 | -0.14954 | -0.14954 | 0.068665 | 0.082397 | -62.7182 | 60.2234 | 60.2097 | 62.3016 | 62.4985 | 123.024 | 62.4207 | 60.2966
7851.1875 | 0.076294 | 0.42511 | -0.77972 | -0.20294 | 0.16129 | -0.25848 | -0.15488 | 60.4156 | -62.3428 | 0.054932 | -62.5214 | 60.2417 | 62.3978 | 62.3291 | 0.061035 | -0.068359 | 0.088654 | 0.28946 | -0.15488 | -0.14633 | 0.022888 | 0.059509 | -62.7045 | 60.228 | 60.1959 | 62.2971 | 62.4985 | 123.0652 | 62.4161 | 60.3012
7852.875 | 0.076294 | 0.43366 | -0.78186 | -0.21042 | 0.15488 | -0.24994 | -0.16663 | 60.4477 | -62.3245 | 0.068665 | -62.5214 | 60.2417 | 62.3932 | 62.3291 | 0.061035 | -0.053406 | 0.083313 | 0.2948 | -0.15274 | -0.14847 | 0.032043 | 0.064087 | -62.7457 | 60.2371 | 60.2188 | 62.3016 | 62.5351 | 123.0103 | 62.3932 | 60.3333
7854.6094 | 0.076294 | 0.42084 | -0.77545 | -0.21576 | 0.17197 | -0.24567 | -0.1709 | 60.4477 | -62.3062 | 0.082397 | -62.5168 | 60.2371 | 62.4252 | 62.3428 | 0.061035 | -0.053406 | 0.092926 | 0.29587 | -0.15167 | -0.15488 | 0.050354 | 0.10986 | -62.6907 | 60.2097 | 60.1685 | 62.3383 | 62.5259 | 123.0194 | 62.4115 | 60.3058
7856.3281 | 0.045776 | 0.43686 | -0.77331 | -0.19333 | 0.15595 | -0.28625 | -0.16129 | 60.5072 | -62.2101 | 0.10529 | -62.4435 | 60.2142 | 62.3291 | 62.2559 | 0.061035 | -0.082245 | 0.074768 | 0.29587 | -0.16769 | -0.14099 | 0.11444 | 0.17853 | -62.59 | 60.1913 | 60.2234 | 62.2192 | 62.439 | 122.9645 | 62.4023 | 60.3928
7858.0156 | 0.061035 | 0.45395 | -0.78507 | -0.21896 | 0.14954 | -0.27771 | -0.16876 | 60.4843 | -62.2513 | 0.07782 | -62.471 | 60.2692 | 62.3062 | 62.2696 | 0.061035 | -0.072632 | 0.077972 | 0.28305 | -0.18265 | -0.14847 | 0.041199 | 0.086975 | -62.6038 | 60.2325 | 60.2371 | 62.2101 | 62.4298 | 122.9233 | 62.3978 | 60.4111
7859.7188 | 0.076294 | 0.44434 | -0.78293 | -0.19012 | 0.15808 | -0.25101 | -0.16235 | 60.5164 | -62.2604 | 0.07782 | -62.4619 | 60.2325 | 62.3657 | 62.2879 | 0.076294 | -0.060883 | 0.0737 | 0.29373 | -0.14847 | -0.16342 | 0.11444 | 0.15564 | -62.6083 | 60.2142 | 60.2188 | 62.2284 | 62.4481 | 123.0469 | 62.3932 | 60.3241
7861.4219 | 0.061035 | 0.42618 | -0.76157 | -0.20401 | 0.15381 | -0.24674 | -0.17197 | 60.434 | -62.3383 | 0.054932 | -62.5168 | 60.2509 | 62.3978 | 62.3291 | 0.045776 | -0.05127 | 0.076904 | 0.29907 | -0.15381 | -0.15488 | 0.036621 | 0.064087 | -62.7274 | 60.2325 | 60.2005 | 62.2742 | 62.5259 | 123.0423 | 62.4252 | 60.2921
7863.125 | 0.061035 | 0.43152 | -0.77759 | -0.19226 | 0.15488 | -0.26276 | -0.16663 | 60.466 | -62.3108 | 0.045776 | -62.4939 | 60.2463 | 62.3795 | 62.2971 | 0.091553 | -0.065155 | 0.072632 | 0.28412 | -0.15808 | -0.15381 | 0.10529 | 0.15106 | -62.6221 | 60.2051 | 60.1913 | 62.2421 | 62.4527 | 123.056 | 62.3657 | 60.3287
7864.8281 | 0.045776 | 0.44327 | -0.78507 | -0.22217 | 0.14954 | -0.27878 | -0.16556 | 60.4889 | -62.2604 | 0.07782 | -62.4619 | 60.2509 | 62.3245 | 62.2467 | 0.076294 | -0.083313 | 0.084381 | 0.27878 | -0.16129 | -0.14313 | 0.050354 | 0.086975 | -62.6266 | 60.2509 | 60.2554 | 62.2192 | 62.4435 | 122.9462 | 62.3932 | 60.3928
7866.5781 | 0.076294 | 0.44434 | -0.79147 | -0.21149 | 0.1506 | -0.28198 | -0.17624 | 60.5347 | -62.1735 | 0.13275 | -62.4252 | 60.228 | 62.3428 | 62.2696 | 0.061035 | -0.081177 | 0.085449 | 0.29587 | -0.16769 | -0.15701 | 0.11902 | 0.13275 | -62.5534 | 60.2097 | 60.2051 | 62.1918 | 62.4298 | 122.9782 | 62.4069 | 60.379
7868.3594 | 0.045776 | 0.44647 | -0.78827 | -0.20401 | 0.15274 | -0.26062 | -0.15488 | 60.434 | -62.3566 | -0.018311 | -62.5488 | 60.2921 | 62.3749 | 62.2971 | 0.076294 | -0.05127 | 0.0737 | 0.28839 | -0.1442 | -0.15381 | 0.068665 | 0.059509 | -62.7136 | 60.26 | 60.2234 | 62.2604 | 62.4664 | 123.0423 | 62.384 | 60.3104
7870.0469 | 0.076294 | 0.44647 | -0.78827 | -0.20508 | 0.15381 | -0.27557 | -0.17517 | 60.5347 | -62.1689 | 0.17395 | -62.4298 | 60.2142 | 62.3428 | 62.2559 | 0.045776 | -0.079041 | 0.079041 | 0.29373 | -0.15808 | -0.13992 | 0.07782 | 0.16022 | -62.5671 | 60.1959 | 60.1913 | 62.2055 | 62.439 | 122.9324 | 62.4115 | 60.3653
7871.7656 | 0.061035 | 0.44968 | -0.77438 | -0.20508 | 0.15167 | -0.24033 | -0.16663 | 60.434 | -62.3566 | -0.013733 | -62.5442 | 60.2646 | 62.3886 | 62.3337 | 0.045776 | -0.05127 | 0.071564 | 0.29694 | -0.13672 | -0.15488 | 0.045776 | 0.054932 | -62.7274 | 60.2417 | 60.2554 | 62.265 | 62.4802 | 123.0423 | 62.384 | 60.3287
7873.5312 | 0.045776 | 0.45395 | -0.77866 | -0.20935 | 0.1506 | -0.26703 | -0.16449 | 60.5026 | -62.2238 | 0.14648 | -62.4481 | 60.2142 | 62.3474 | 62.2696 | 0.045776 | -0.069427 | 0.089722 | 0.28732 | -0.16556 | -0.1474 | 0.036621 | 0.086975 | -62.645 | 60.2051 | 60.2051 | 62.2604 | 62.4481 | 122.8775 | 62.3932 | 60.3195
7875.25 | 0.045776 | 0.43259 | -0.77652 | -0.21683 | 0.15167 | -0.25742 | -0.1709 | 60.4202 | -62.3383 | 0.050354 | -62.5397 | 60.26 | 62.3932 | 62.3291 | 0.061035 | -0.066223 | 0.087585 | 0.30121 | -0.15915 | -0.14847 | 0.004578 | 0.009155 | -62.7228 | 60.2463 | 60.228 | 62.3062 | 62.4893 | 122.9828 | 62.3932 | 60.3287
7877 | 0.045776 | 0.46783 | -0.79575 | -0.19012 | 0.16129 | -0.27771 | -0.17303 | 60.4797 | -62.2192 | 0.064087 | -62.4573 | 60.2646 | 62.3154 | 62.2238 | 0.076294 | -0.081177 | 0.059814 | 0.29053 | -0.15701 | -0.14633 | 0.054932 | 0.10071 | -62.6175 | 60.2142 | 60.2371 | 62.2192 | 62.4527 | 122.9004 | 62.3932 | 60.3882
7878.7031 | 0.076294 | 0.44113 | -0.78079 | -0.21362 | 0.14633 | -0.26169 | -0.17197 | 60.4156 | -62.3383 | 0.045776 | -62.5351 | 60.2692 | 62.3749 | 62.3199 | 0.045776 | -0.057678 | 0.085449 | 0.29694 | -0.15808 | -0.15595 | -0.009155 | 0.009155 | -62.7228 | 60.2692 | 60.2325 | 62.2604 | 62.4847 | 122.9095 | 62.4115 | 60.3195
7880.4062 | 0.061035 | 0.43366 | -0.78507 | -0.20828 | 0.15488 | -0.2681 | -0.17731 | 60.5438 | -62.1689 | 0.16479 | -62.4207 | 60.26 | 62.3383 | 62.2559 | 0.045776 | -0.066223 | 0.081177 | 0.27771 | -0.15808 | -0.14847 | 0.073242 | 0.14648 | -62.5626 | 60.2142 | 60.1913 | 62.2101 | 62.4435 | 122.9095 | 62.3978 | 60.3653
7882.1094 | 0.076294 | 0.45288 | -0.77759 | -0.1944 | 0.1506 | -0.25101 | -0.16449 | 60.5347 | -62.2238 | 0.10529 | -62.4252 | 60.2234 | 62.3337 | 62.2559 | 0.061035 | -0.061951 | 0.081177 | 0.28198 | -0.15488 | -0.15701 | 0.12817 | 0.1831 | -62.5763 | 60.2097 | 60.2051 | 62.2192 | 62.4207 | 122.9919 | 62.3795 | 60.3516
7883.8125 | 0.061035 | 0.4454 | -0.784 | -0.21362 | 0.15167 | -0.26489 | -0.18051 | 60.498 | -62.2284 | 0.082397 | -62.4481 | 60.2646 | 62.3291 | 62.2467 | 0.061035 | -0.074768 | 0.077972 | 0.28412 | -0.16556 | -0.14954 | 0.082397 | 0.11444 | -62.5626 | 60.228 | 60.2097 | 62.2101 | 62.4069 | 122.9279 | 62.3749 | 60.3561
7885.5781 | 0.061035 | 0.46036 | -0.78934 | -0.20615 | 0.15595 | -0.26596 | -0.16769 | 60.4935 | -62.2284 | 0.073242 | -62.439 | 60.2554 | 62.3428 | 62.2375 | 0.061035 | -0.082245 | 0.074768 | 0.28091 | -0.16235 | -0.14633 | 0.045776 | 0.082397 | -62.59 | 60.2142 | 60.2188 | 62.2147 | 62.4298 | 122.9233 | 62.3932 | 60.3973
7887.2812 | 0.045776 | 0.44434 | -0.78186 | -0.20721 | 0.16129 | -0.26382 | -0.16983 | 60.5118 | -62.2192 | 0.068665 | -62.4527 | 60.2325 | 62.3474 | 62.2375 | 0.061035 | -0.0737 | 0.075836 | 0.28519 | -0.15274 | -0.16022 | 0.10071 | 0.10986 | -62.6083 | 60.2417 | 60.2051 | 62.2192 | 62.4619 | 122.8912 | 62.4115 | 60.3928
7888.9844 | 0.045776 | 0.43793 | -0.77759 | -0.20401 | 0.15167 | -0.25101 | -0.17197 | 60.4294 | -62.3245 | 0.036621 | -62.5259 | 60.2921 | 62.3978 | 62.2971 | 0.091553 | -0.057678 | 0.076904 | 0.29053 | -0.14633 | -0.15381 | 0 | 0.018311 | -62.7136 | 60.2509 | 60.2325 | 62.2833 | 62.4664 | 122.9599 | 62.4161 | 60.3058
7890.7188 | 0.061035 | 0.46249 | -0.7872 | -0.20187 | 0.15595 | -0.27557 | -0.1741 | 60.498 | -62.233 | 0.068665 | -62.439 | 60.2142 | 62.3383 | 62.2375 | 0.045776 | -0.066223 | 0.064087 | 0.28305 | -0.15167 | -0.14633 | 0.064087 | 0.10071 | -62.5992 | 60.2142 | 60.2188 | 62.2101 | 62.4207 | 122.8912 | 62.384 | 60.3516
7892.4219 | 0.045776 | 0.43152 | -0.76584 | -0.20615 | 0.15381 | -0.24887 | -0.17517 | 60.466 | -62.3199 | 0.004578 | -62.5168 | 60.26 | 62.3566 | 62.2742 | 0.076294 | -0.05661 | 0.0737 | 0.2948 | -0.1442 | -0.15274 | 0.09613 | 0.11444 | -62.6541 | 60.2371 | 60.1822 | 62.2696 | 62.4481 | 123.0423 | 62.352 | 60.3149
7894.1562 | 0.061035 | 0.44968 | -0.77972 | -0.19974 | 0.16129 | -0.25421 | -0.16022 | 60.4797 | -62.233 | 0.064087 | -62.4527 | 60.2325 | 62.352 | 62.2604 | 0.061035 | -0.064087 | 0.071564 | 0.29053 | -0.1442 | -0.14954 | 0.12817 | 0.15106 | -62.6083 | 60.2005 | 60.1593 | 62.2559 | 62.4435 | 123.0103 | 62.3703 | 60.3195
7895.875 | 0.061035 | 0.4454 | -0.77972 | -0.21149 | 0.15488 | -0.26596 | -0.18265 | 60.4843 | -62.2147 | 0.082397 | -62.4664 | 60.2188 | 62.2971 | 62.2513 | 0.091553 | -0.079041 | 0.076904 | 0.29373 | -0.16342 | -0.13672 | 0.07782 | 0.11444 | -62.5946 | 60.2325 | 60.2051 | 62.2192 | 62.4298 | 122.8729 | 62.384 | 60.3882
7897.6719 | 0.045776 | 0.45502 | -0.784 | -0.22324 | 0.14954 | -0.27771 | -0.17731 | 60.5392 | -62.1643 | 0.14191 | -62.4115 | 60.228 | 62.3291 | 62.2513 | 0.030518 | -0.082245 | 0.084381 | 0.28839 | -0.17624 | -0.15381 | 0.11902 | 0.15564 | -62.5305 | 60.2051 | 60.1547 | 62.2101 | 62.4252 | 122.9324 | 62.4023 | 60.347
7899.4062 | 0.076294 | 0.45715 | -0.77759 | -0.19226 | 0.14206 | -0.25207 | -0.17517 | 60.5255 | -62.1826 | 0.10986 | -62.439 | 60.2234 | 62.3428 | 62.2696 | 0.076294 | -0.070496 | 0.068359 | 0.2948 | -0.14526 | -0.16342 | 0.13733 | 0.1831 | -62.5671 | 60.2005 | 60.173 | 62.233 | 62.4207 | 122.9279 | 62.3795 | 60.3607
7901.125 | 0.045776 | 0.44006 | -0.784 | -0.19653 | 0.15167 | -0.24139 | -0.15808 | 60.5026 | -62.2147 | 0.10986 | -62.4435 | 60.2325 | 62.3337 | 62.2421 | 0.061035 | -0.064087 | 0.072632 | 0.28839 | -0.1474 | -0.16342 | 0.12817 | 0.16479 | -62.5854 | 60.1868 | 60.1959 | 62.2238 | 62.4298 | 123.0011 | 62.352 | 60.3149
7902.8281 | 0.045776 | 0.4422 | -0.78507 | -0.22964 | 0.14526 | -0.27878 | -0.1709 | 60.4706 | -62.2284 | 0.073242 | -62.4344 | 60.2509 | 62.3245 | 62.233 | 0.091553 | -0.067291 | 0.077972 | 0.28625 | -0.16663 | -0.16129 | 0.059509 | 0.091553 | -62.59 | 60.1913 | 60.2142 | 62.1964 | 62.4161 | 122.9233 | 62.3657 | 60.3561
7904.5625 | 0.076294 | 0.46249 | -0.78613 | -0.19974 | 0.15274 | -0.26703 | -0.17517 | 60.4889 | -62.2009 | 0.082397 | -62.439 | 60.2509 | 62.3154 | 62.2421 | 0.061035 | -0.082245 | 0.074768 | 0.28198 | -0.15488 | -0.15167 | 0.09613 | 0.10986 | -62.5534 | 60.2097 | 60.2142 | 62.1964 | 62.4298 | 122.9279 | 62.3657 | 60.347
7906.2812 | 0.061035 | 0.43152 | -0.77866 | -0.21362 | 0.1474 | -0.25742 | -0.17731 | 60.4385 | -62.3062 | 0.059509 | -62.5076 | 60.2554 | 62.3657 | 62.3062 | 0.061035 | -0.059814 | 0.077972 | 0.29694 | -0.15167 | -0.16129 | 0.009155 | 0.009155 | -62.6999 | 60.2188 | 60.1913 | 62.2696 | 62.4893 | 122.8821 | 62.4069 | 60.3378
7907.9844 | 0.030518 | 0.45181 | -0.77011 | -0.20294 | 0.16663 | -0.24246 | -0.17197 | 60.4111 | -62.3154 | 0.050354 | -62.4893 | 60.2417 | 62.3795 | 62.3108 | 0.061035 | -0.055542 | 0.070496 | 0.28946 | -0.1506 | -0.16022 | 0.027466 | 0.045776 | -62.6862 | 60.2188 | 60.1868 | 62.2833 | 62.4939 | 123.0103 | 62.3978 | 60.3104
7909.6875 | 0.076294 | 0.4454 | -0.77866 | -0.18372 | 0.14313 | -0.26276 | -0.16022 | 60.4431 | -62.2513 | 0.050354 | -62.4802 | 60.2417 | 62.3566 | 62.2696 | 0.076294 | -0.070496 | 0.072632 | 0.28946 | -0.1506 | -0.14206 | 0.10986 | 0.16022 | -62.6129 | 60.2142 | 60.1685 | 62.2238 | 62.4527 | 123.0148 | 62.3703 | 60.3104
7911.3906 | 0.061035 | 0.43366 | -0.77866 | -0.21255 | 0.14954 | -0.2713 | -0.1741 | 60.5484 | -62.1094 | 0.16479 | -62.3978 | 60.2097 | 62.3154 | 62.2009 | 0.061035 | -0.082245 | 0.076904 | 0.28732 | -0.15808 | -0.15167 | 0.09613 | 0.16479 | -62.5488 | 60.2051 | 60.1959 | 62.1872 | 62.4069 | 122.9004 | 62.3749 | 60.3333
7913.0781 | 0.061035 | 0.43686 | -0.77866 | -0.19974 | 0.1474 | -0.23392 | -0.16769 | 60.4065 | -62.3337 | 0.009155 | -62.5259 | 60.2463 | 62.3932 | 62.3291 | 0.061035 | -0.063019 | 0.084381 | 0.2948 | -0.15167 | -0.15595 | 0 | 0.036621 | -62.7457 | 60.2142 | 60.2051 | 62.2696 | 62.4939 | 122.9416 | 62.3795 | 60.3195
7914.7656 | 0.045776 | 0.45609 | -0.78293 | -0.21683 | 0.13886 | -0.28091 | -0.17303 | 60.5026 | -62.1597 | 0.091553 | -62.4435 | 60.2051 | 62.2925 | 62.2009 | 0.061035 | -0.086517 | 0.081177 | 0.28625 | -0.16235 | -0.14633 | 0.091553 | 0.14191 | -62.5717 | 60.2097 | 60.2325 | 62.2055 | 62.3978 | 122.8729 | 62.3566 | 60.3836
7916.4531 | 0.076294 | 0.42831 | -0.77759 | -0.22324 | 0.14847 | -0.24994 | -0.16769 | 60.3928 | -62.3291 | 0.045776 | -62.5122 | 60.2325 | 62.3657 | 62.3062 | 0.076294 | -0.054474 | 0.084381 | 0.2948 | -0.1506 | -0.15808 | -0.013733 | 0.018311 | -62.7045 | 60.228 | 60.228 | 62.265 | 62.471 | 122.9599 | 62.3886 | 60.2829
7918.1719 | 0.061035 | 0.44647 | -0.78079 | -0.20828 | 0.16235 | -0.28305 | -0.17517 | 60.5209 | -62.1277 | 0.16479 | -62.3932 | 60.1959 | 62.3108 | 62.2467 | 0.045776 | -0.081177 | 0.077972 | 0.27344 | -0.16342 | -0.14847 | 0.09613 | 0.16022 | -62.5031 | 60.1959 | 60.173 | 62.2192 | 62.4069 | 122.9095 | 62.3703 | 60.3287
7919.8594 | 0.045776 | 0.42725 | -0.78186 | -0.21042 | 0.15274 | -0.24887 | -0.1741 | 60.4065 | -62.3245 | 0.027466 | -62.4985 | 60.2417 | 62.3749 | 62.2971 | 0.076294 | -0.052338 | 0.086517 | 0.29266 | -0.15915 | -0.16129 | -0.004578 | 0.022888 | -62.6953 | 60.2234 | 60.2051 | 62.2833 | 62.4939 | 122.9828 | 62.4023 | 60.2875
7921.6406 | 0.045776 | 0.43472 | -0.7872 | -0.21896 | 0.15808 | -0.27451 | -0.16342 | 60.4797 | -62.1826 | 0.15564 | -62.4161 | 60.228 | 62.3245 | 62.2375 | 0.045776 | -0.0737 | 0.086517 | 0.28946 | -0.16022 | -0.14633 | 0.059509 | 0.10986 | -62.5854 | 60.1868 | 60.1822 | 62.233 | 62.4619 | 122.8409 | 62.4069 | 60.3699
7923.4219 | 0.076294 | 0.43152 | -0.78613 | -0.22324 | 0.15274 | -0.26169 | -0.17303 | 60.3836 | -62.3154 | 0.036621 | -62.5031 | 60.2692 | 62.3886 | 62.2971 | 0.061035 | -0.05661 | 0.086517 | 0.2948 | -0.15808 | -0.15167 | -0.009155 | 0.009155 | -62.709 | 60.2188 | 60.1822 | 62.2696 | 62.4985 | 122.937 | 62.3886 | 60.3104
7925.2031 | 0.045776 | 0.42297 | -0.78934 | -0.19119 | 0.1474 | -0.23926 | -0.16235 | 60.379 | -62.3383 | -0.013733 | -62.5259 | 60.228 | 62.352 | 62.2879 | 0.061035 | -0.058746 | 0.084381 | 0.30121 | -0.1442 | -0.15381 | 0.009155 | 0.032043 | -62.7411 | 60.228 | 60.2051 | 62.2787 | 62.4893 | 122.9462 | 62.3749 | 60.2829
7926.9375 | 0.045776 | 0.45502 | -0.78186 | -0.20721 | 0.15808 | -0.27771 | -0.17303 | 60.4477 | -62.1964 | 0.091553 | -62.4435 | 60.2234 | 62.3291 | 62.2238 | 0.091553 | -0.085449 | 0.069427 | 0.28305 | -0.16235 | -0.14206 | 0.068665 | 0.10986 | -62.5671 | 60.1913 | 60.1959 | 62.2147 | 62.3886 | 122.8546 | 62.3611 | 60.3607
7928.7188 | 0.061035 | 0.43579 | -0.77972 | -0.20081 | 0.13886 | -0.23712 | -0.16129 | 60.4156 | -62.3108 | 0.018311 | -62.5031 | 60.2234 | 62.3886 | 62.3108 | 0.076294 | -0.050201 | 0.077972 | 0.29159 | -0.14313 | -0.15595 | 0.013733 | 0.064087 | -62.7274 | 60.2234 | 60.2005 | 62.265 | 62.4893 | 122.9279 | 62.384 | 60.3012
7930.5156 | 0.061035 | 0.4422 | -0.78293 | -0.22858 | 0.15167 | -0.27023 | -0.16663 | 60.5072 | -62.1277 | 0.16937 | -62.4161 | 60.2097 | 62.2971 | 62.2375 | 0.061035 | -0.069427 | 0.077972 | 0.29266 | -0.17303 | -0.1474 | 0.09613 | 0.13275 | -62.5488 | 60.1913 | 60.1959 | 62.2009 | 62.3978 | 122.8455 | 62.3795 | 60.3424
7932.2969 | 0.061035 | 0.4422 | -0.78827 | -0.20935 | 0.1474 | -0.28732 | -0.16876 | 60.5255 | -62.1231 | 0.15564 | -62.3978 | 60.2188 | 62.3108 | 62.2421 | 0.061035 | -0.081177 | 0.082245 | 0.27664 | -0.16129 | -0.15701 | 0.10529 | 0.15106 | -62.4939 | 60.1776 | 60.1639 | 62.2055 | 62.4115 | 122.9004 | 62.3749 | 60.3149
7934 | 0.061035 | 0.45715 | -0.77652 | -0.20401 | 0.16022 | -0.25848 | -0.1709 | 60.5118 | -62.2238 | 0.07782 | -62.4161 | 60.2142 | 62.3383 | 62.265 | 0.076294 | -0.065155 | 0.072632 | 0.28519 | -0.14954 | -0.15488 | 0.13275 | 0.16022 | -62.5763 | 60.1959 | 60.173 | 62.2147 | 62.3978 | 122.9828 | 62.3245 | 60.3058
7935.7812 | 0.091553 | 0.42831 | -0.77545 | -0.20401 | 0.16235 | -0.23605 | -0.17731 | 60.4248 | -62.2833 | 0.059509 | -62.4847 | 60.2554 | 62.352 | 62.3108 | 0.061035 | -0.043793 | 0.083313 | 0.30014 | -0.15381 | -0.16022 | 0.032043 | 0.054932 | -62.709 | 60.1776 | 60.1868 | 62.2559 | 62.4985 | 122.9462 | 62.3657 | 60.2783
7937.5469 | 0.045776 | 0.45288 | -0.77652 | -0.20615 | 0.15701 | -0.25848 | -0.15701 | 60.4477 | -62.2467 | 0.036621 | -62.4664 | 60.228 | 62.3474 | 62.2559 | 0.076294 | -0.067291 | 0.080109 | 0.28625 | -0.14633 | -0.15381 | 0.11444 | 0.13733 | -62.59 | 60.1776 | 60.2188 | 62.2375 | 62.4298 | 122.9691 | 62.3337 | 60.2966
7939.25 | 0.045776 | 0.47638 | -0.79254 | -0.20508 | 0.15701 | -0.28946 | -0.17731 | 60.4477 | -62.1964 | 0.07782 | -62.4344 | 60.2371 | 62.3245 | 62.2375 | 0.076294 | -0.084381 | 0.067291 | 0.27985 | -0.16342 | -0.14526 | 0.050354 | 0.09613 | -62.558 | 60.2234 | 60.2097 | 62.2055 | 62.4069 | 122.8821 | 62.3611 | 60.3607
7941.0312 | 0.061035 | 0.44861 | -0.77866 | -0.20294 | 0.15488 | -0.26062 | -0.16769 | 60.5118 | -62.1735 | 0.10529 | -62.4115 | 60.2234 | 62.2925 | 62.2421 | 0.061035 | -0.075836 | 0.077972 | 0.29587 | -0.15808 | -0.15167 | 0.11902 | 0.17853 | -62.5534 | 60.1959 | 60.2097 | 62.2101 | 62.4344 | 122.8912 | 62.352 | 60.3287
7942.8125 | 0.045776 | 0.43152 | -0.77331 | -0.19012 | 0.16022 | -0.23605 | -0.16983 | 60.3882 | -62.3337 | -0.041199 | -62.5122 | 60.2554 | 62.3703 | 62.2925 | 0.045776 | -0.041656 | 0.075836 | 0.30014 | -0.15167 | -0.1506 | 0.022888 | 0.045776 | -62.6999 | 60.2142 | 60.2051 | 62.2101 | 62.4573 | 122.9599 | 62.3428 | 60.3058
7944.5312 | 0.076294 | 0.42938 | -0.77118 | -0.21149 | 0.15488 | -0.23819 | -0.1506 | 60.4248 | -62.2696 | 0.064087 | -62.4802 | 60.2005 | 62.384 | 62.2925 | 0.061035 | -0.068359 | 0.082245 | 0.29694 | -0.15274 | -0.15381 | 0.068665 | 0.086975 | -62.6633 | 60.1776 | 60.2005 | 62.2513 | 62.4664 | 122.9599 | 62.3932 | 60.2509
7946.2344 | 0.061035 | 0.44006 | -0.77225 | -0.19974 | 0.14847 | -0.26596 | -0.17624 | 60.4568 | -62.2421 | 0.059509 | -62.4527 | 60.2097 | 62.352 | 62.2513 | 0.076294 | -0.066223 | 0.069427 | 0.29907 | -0.15701 | -0.15381 | 0.11444 | 0.14191 | -62.5671 | 60.1868 | 60.2188 | 62.2192 | 62.4344 | 122.9645 | 62.3474 | 60.3012
7947.9375 | 0.061035 | 0.44434 | -0.78186 | -0.19546 | 0.15595 | -0.28091 | -0.16983 | 60.4935 | -62.1689 | 0.10529 | -62.3932 | 60.2005 | 62.3062 | 62.233 | 0.045776 | -0.067291 | 0.079041 | 0.28625 | -0.13992 | -0.15274 | 0.11444 | 0.17395 | -62.558 | 60.1822 | 60.1685 | 62.2009 | 62.4207 | 122.9462 | 62.3337 | 60.3195
7949.7031 | 0.061035 | 0.4454 | -0.78934 | -0.23392 | 0.14633 | -0.28732 | -0.17624 | 60.5026 | -62.1506 | 0.15106 | -62.3932 | 60.2417 | 62.2879 | 62.2055 | 0.045776 | -0.081177 | 0.079041 | 0.28732 | -0.17624 | -0.15488 | 0.10529 | 0.14648 | -62.5305 | 60.1547 | 60.1868 | 62.1918 | 62.3932 | 122.8912 | 62.352 | 60.3287
7951.4219 | 0.061035 | 0.44327 | -0.78827 | -0.20187 | 0.15915 | -0.26596 | -0.17303 | 60.5118 | -62.178 | 0.10986 | -62.3932 | 60.1913 | 62.2833 | 62.2055 | 0.061035 | -0.059814 | 0.075836 | 0.28946 | -0.15381 | -0.15274 | 0.12817 | 0.17853 | -62.5442 | 60.1639 | 60.1822 | 62.2055 | 62.4069 | 122.8958 | 62.3383 | 60.3058
7953.1875 | 0.076294 | 0.45929 | -0.78186 | -0.20187 | 0.1474 | -0.25635 | -0.16449 | 60.5072 | -62.1506 | 0.10986 | -62.4252 | 60.1959 | 62.3016 | 62.2238 | 0.061035 | -0.066223 | 0.076904 | 0.28305 | -0.14954 | -0.15701 | 0.1236 | 0.15106 | -62.5442 | 60.1868 | 60.1501 | 62.1918 | 62.4069 | 122.8363 | 62.3657 | 60.3699
7954.9375 | 0.076294 | 0.44113 | -0.79147 | -0.21255 | 0.1474 | -0.26276 | -0.18372 | 60.3745 | -62.2879 | 0.041199 | -62.4985 | 60.2463 | 62.3611 | 62.2925 | 0.045776 | -0.053406 | 0.075836 | 0.28198 | -0.15701 | -0.15915 | -0.013733 | 0 | -62.6907 | 60.2234 | 60.1868 | 62.2742 | 62.4619 | 122.8958 | 62.3932 | 60.2875
7956.6719 | 0.061035 | 0.44006 | -0.78827 | -0.21683 | 0.1506 | -0.25848 | -0.16876 | 60.3745 | -62.2971 | 0.041199 | -62.5031 | 60.2646 | 62.3611 | 62.2742 | 0.061035 | -0.064087 | 0.075836 | 0.28519 | -0.15808 | -0.14526 | -0.004578 | -0.009155 | -62.6999 | 60.228 | 60.1776 | 62.265 | 62.471 | 122.8775 | 62.3749 | 60.3149
7958.4531 | 0.045776 | 0.439 | -0.78613 | -0.2211 | 0.15488 | -0.25207 | -0.18906 | 60.3607 | -62.2742 | 0.036621 | -62.4847 | 60.2234 | 62.3749 | 62.2971 | 0.061035 | -0.069427 | 0.082245 | 0.28198 | -0.1506 | -0.15595 | -0.018311 | -0.004578 | -62.6907 | 60.2142 | 60.2005 | 62.2787 | 62.471 | 122.8638 | 62.3795 | 60.2966
7960.2188 | 0.045776 | 0.45288 | -0.78934 | -0.20294 | 0.15595 | -0.27344 | -0.17303 | 60.4797 | -62.1506 | 0.091553 | -62.4023 | 60.2005 | 62.2971 | 62.2284 | 0.030518 | -0.074768 | 0.079041 | 0.28198 | -0.16022 | -0.13992 | 0.11902 | 0.15106 | -62.5534 | 60.173 | 60.1822 | 62.178 | 62.4069 | 122.8271 | 62.3245 | 60.3424
7961.9375 | 0.076294 | 0.43686 | -0.77011 | -0.21896 | 0.15488 | -0.28198 | -0.17944 | 60.4431 | -62.1735 | 0.086975 | -62.4115 | 60.2371 | 62.2787 | 62.2055 | 0.061035 | -0.075836 | 0.079041 | 0.28412 | -0.17838 | -0.16235 | 0.091553 | 0.1236 | -62.5305 | 60.2234 | 60.173 | 62.1964 | 62.3749 | 122.8592 | 62.3428 | 60.3424
7963.7188 | 0.076294 | 0.45822 | -0.78079 | -0.20721 | 0.15488 | -0.26703 | -0.1709 | 60.498 | -62.1506 | 0.1236 | -62.3932 | 60.2051 | 62.2971 | 62.2238 | 0.061035 | -0.071564 | 0.0737 | 0.29694 | -0.16449 | -0.16235 | 0.12817 | 0.16479 | -62.5351 | 60.1685 | 60.1593 | 62.1872 | 62.3978 | 122.85 | 62.3657 | 60.347
7965.5 | 0.045776 | 0.41657 | -0.78186 | -0.1944 | 0.14954 | -0.24353 | -0.16663 | 60.4202 | -62.2604 | 0.064087 | -62.4756 | 60.2188 | 62.3657 | 62.3016 | 0.061035 | -0.046997 | 0.084381 | 0.28839 | -0.13458 | -0.15488 | 0.068665 | 0.082397 | -62.6587 | 60.173 | 60.1639 | 62.2604 | 62.4847 | 122.9187 | 62.3566 | 60.2463
7967.2812 | 0.091553 | 0.43366 | -0.77011 | -0.19653 | 0.14954 | -0.24567 | -0.16663 | 60.4065 | -62.265 | 0.009155 | -62.4802 | 60.2417 | 62.3245 | 62.2467 | 0.061035 | -0.055542 | 0.086517 | 0.28732 | -0.15595 | -0.15488 | 0.10071 | 0.11444 | -62.6129 | 60.1868 | 60.1776 | 62.2421 | 62.4435 | 122.9645 | 62.3245 | 60.2921
7969.0469 | 0.045776 | 0.43472 | -0.77225 | -0.2243 | 0.1442 | -0.26382 | -0.16983 | 60.3653 | -62.2696 | 0.050354 | -62.4939 | 60.2234 | 62.3474 | 62.3016 | 0.091553 | -0.057678 | 0.089722 | 0.28198 | -0.17517 | -0.1506 | -0.009155 | -0.004578 | -62.6678 | 60.2142 | 60.1959 | 62.2559 | 62.4527 | 122.8363 | 62.3932 | 60.3058
7970.7656 | 0.061035 | 0.42831 | -0.77118 | -0.20508 | 0.16342 | -0.24353 | -0.17197 | 60.3973 | -62.2559 | 0.064087 | -62.4756 | 60.2234 | 62.3566 | 62.2879 | 0.061035 | -0.044861 | 0.074768 | 0.28946 | -0.14099 | -0.14954 | 0.045776 | 0.068665 | -62.6816 | 60.2051 | 60.1776 | 62.2604 | 62.4527 | 122.9095 | 62.3703 | 60.2692
7972.5312 | 0.061035 | 0.42831 | -0.77225 | -0.20508 | 0.15274 | -0.25421 | -0.1709 | 60.3516 | -62.2787 | 0.050354 | -62.4756 | 60.2142 | 62.3566 | 62.2971 | 0.076294 | -0.059814 | 0.087585 | 0.29053 | -0.16235 | -0.15595 | 0 | 0.054932 | -62.6587 | 60.1913 | 60.1776 | 62.2421 | 62.4573 | 122.937 | 62.352 | 60.2554
7974.3125 | 0.091553 | 0.42297 | -0.77118 | -0.20935 | 0.14313 | -0.24994 | -0.16663 | 60.3882 | -62.2559 | 0.07782 | -62.4802 | 60.1959 | 62.3795 | 62.2925 | 0.061035 | -0.058746 | 0.0737 | 0.30121 | -0.16342 | -0.1506 | 0.032043 | 0.086975 | -62.6495 | 60.1639 | 60.1593 | 62.2559 | 62.4664 | 122.9462 | 62.3428 | 60.2417
7976.0156 | 0.076294 | 0.44006 | -0.78293 | -0.20721 | 0.14206 | -0.25742 | -0.16235 | 60.4065 | -62.2513 | 0.064087 | -62.471 | 60.1776 | 62.3749 | 62.3016 | 0.061035 | -0.053406 | 0.084381 | 0.29373 | -0.16449 | -0.14847 | 0.054932 | 0.09613 | -62.6541 | 60.1593 | 60.1593 | 62.2833 | 62.439 | 122.9095 | 62.3657 | 60.2325
7977.7969 | 0.045776 | 0.43259 | -0.77438 | -0.21362 | 0.1709 | -0.25314 | -0.16022 | 60.3516 | -62.3199 | 0.009155 | -62.4939 | 60.1822 | 62.3657 | 62.2833 | 0.061035 | -0.052338 | 0.083313 | 0.29587 | -0.15167 | -0.14099 | 0 | 0.045776 | -62.6862 | 60.1913 | 60.1959 | 62.2467 | 62.4893 | 122.9004 | 62.3657 | 60.2463
7979.5781 | 0.076294 | 0.43686 | -0.78507 | -0.20828 | 0.14954 | -0.25421 | -0.17624 | 60.3745 | -62.2467 | 0.064087 | -62.471 | 60.1913 | 62.3566 | 62.2742 | 0.061035 | -0.059814 | 0.075836 | 0.29694 | -0.14633 | -0.14313 | 0.027466 | 0.10071 | -62.6404 | 60.1593 | 60.1593 | 62.265 | 62.4664 | 122.9324 | 62.3428 | 60.2417
7981.3125 | 0.045776 | 0.44006 | -0.77438 | -0.22858 | 0.15381 | -0.28946 | -0.18051 | 60.3287 | -62.2971 | 0.041199 | -62.4939 | 60.2051 | 62.3383 | 62.2696 | 0.061035 | -0.069427 | 0.089722 | 0.28305 | -0.16556 | -0.15381 | -0.022888 | 0 | -62.6633 | 60.1959 | 60.1913 | 62.2421 | 62.4481 | 122.8409 | 62.3932 | 60.2921
7983.0781 | 0.061035 | 0.45715 | -0.7872 | -0.18692 | 0.15701 | -0.28198 | -0.1741 | 60.4568 | -62.1414 | 0.10529 | -62.3932 | 60.1913 | 62.2787 | 62.2009 | 0.061035 | -0.065155 | 0.069427 | 0.28625 | -0.16129 | -0.1442 | 0.11444 | 0.14648 | -62.5351 | 60.1868 | 60.1913 | 62.178 | 62.384 | 122.8317 | 62.3611 | 60.3195
7984.7969 | 0.045776 | 0.44647 | -0.78613 | -0.21576 | 0.14954 | -0.28625 | -0.18372 | 60.434 | -62.2055 | 0.064087 | -62.4115 | 60.2417 | 62.265 | 62.2192 | 0.076294 | -0.081177 | 0.066223 | 0.28091 | -0.17197 | -0.14633 | 0.032043 | 0.073242 | -62.5397 | 60.2051 | 60.2188 | 62.1872 | 62.3886 | 122.8363 | 62.3657 | 60.3699
7986.5625 | 0.061035 | 0.44861 | -0.78293 | -0.21469 | 0.16556 | -0.28091 | -0.1944 | 60.5026 | -62.1368 | 0.14191 | -62.3749 | 60.2097 | 62.2833 | 62.2192 | 0.061035 | -0.064087 | 0.072632 | 0.2948 | -0.18372 | -0.1474 | 0.1236 | 0.14648 | -62.4756 | 60.2005 | 60.1639 | 62.1826 | 62.3932 | 122.8546 | 62.3566 | 60.3149
7988.2812 | 0.061035 | 0.40375 | -0.77759 | -0.19867 | 0.16235 | -0.23819 | -0.18158 | 60.3836 | -62.2879 | 0.054932 | -62.4664 | 60.2234 | 62.3566 | 62.265 | 0.091553 | -0.059814 | 0.087585 | 0.29266 | -0.14099 | -0.15701 | 0.013733 | 0.054932 | -62.6541 | 60.2051 | 60.1547 | 62.2604 | 62.4664 | 122.9416 | 62.3474 | 60.2463
7990.0469 | 0.061035 | 0.43472 | -0.77331 | -0.1944 | 0.15915 | -0.24139 | -0.16769 | 60.3424 | -62.3428 | -0.018311 | -62.5214 | 60.2234 | 62.3474 | 62.2787 | 0.076294 | -0.053406 | 0.082245 | 0.30014 | -0.14526 | -0.16022 | 0.013733 | 0.036621 | -62.7045 | 60.2188 | 60.1776 | 62.2604 | 62.4344 | 122.9004 | 62.3657 | 60.2737
7991.8281 | 0.061035 | 0.43793 | -0.78827 | -0.21469 | 0.14526 | -0.28198 | -0.16556 | 60.4797 | -62.1231 | 0.15106 | -62.384 | 60.1822 | 62.2742 | 62.2101 | 0.061035 | -0.077972 | 0.074768 | 0.27878 | -0.15701 | -0.14954 | 0.07782 | 0.12817 | -62.5214 | 60.1685 | 60.1913 | 62.2101 | 62.4023 | 122.7997 | 62.3474 | 60.2875
7993.6094 | 0.076294 | 0.43366 | -0.78613 | -0.20615 | 0.1442 | -0.26276 | -0.16769 | 60.3699 | -62.2879 | 0.032043 | -62.471 | 60.2417 | 62.3428 | 62.2513 | 0.061035 | -0.052338 | 0.077972 | 0.28519 | -0.15915 | -0.15915 | -0.022888 | 0.009155 | -62.6678 | 60.2142 | 60.2234 | 62.2467 | 62.4344 | 122.8271 | 62.3703 | 60.2692
7995.3281 | 0.076294 | 0.43366 | -0.78934 | -0.20187 | 0.15808 | -0.24994 | -0.17303 | 60.3928 | -62.2879 | 0 | -62.471 | 60.2188 | 62.3245 | 62.2559 | 0.045776 | -0.055542 | 0.079041 | 0.29907 | -0.15488 | -0.14313 | 0.073242 | 0.09613 | -62.6312 | 60.1822 | 60.2005 | 62.2421 | 62.4252 | 122.9599 | 62.3291 | 60.2737
7997.0312 | 0.045776 | 0.4454 | -0.79575 | -0.20828 | 0.15167 | -0.2713 | -0.17303 | 60.4385 | -62.1643 | 0.07782 | -62.4069 | 60.2005 | 62.2925 | 62.1918 | 0.061035 | -0.074768 | 0.076904 | 0.29159 | -0.17303 | -0.1506 | 0.064087 | 0.10071 | -62.5442 | 60.1959 | 60.2051 | 62.1689 | 62.3795 | 122.7997 | 62.3245 | 60.3424
7998.8125 | 0.061035 | 0.45502 | -0.78934 | -0.20615 | 0.15701 | -0.27557 | -0.1741 | 60.4385 | -62.1826 | 0.068665 | -62.4161 | 60.2188 | 62.2925 | 62.2055 | 0.061035 | -0.074768 | 0.069427 | 0.28839 | -0.16235 | -0.1506 | 0.054932 | 0.09613 | -62.558 | 60.2051 | 60.1822 | 62.178 | 62.3749 | 122.8043 | 62.3337 | 60.3378
8000.5938 | 0.045776 | 0.42191 | -0.75729 | -0.21683 | 0.1506 | -0.24353 | -0.16769 | 60.3561 | -62.3199 | -0.009155 | -62.5031 | 60.2371 | 62.352 | 62.2971 | 0.045776 | -0.055542 | 0.085449 | 0.29159 | -0.1474 | -0.16663 | 0.041199 | 0.022888 | -62.7136 | 60.2051 | 60.2051 | 62.2375 | 62.4619 | 122.9004 | 62.3245 | 60.2829
8002.3594 | 0.076294 | 0.44327 | -0.784 | -0.1944 | 0.14526 | -0.25955 | -0.17517 | 60.3653 | -62.2604 | 0.018311 | -62.4573 | 60.1913 | 62.3291 | 62.2559 | 0.061035 | -0.068359 | 0.077972 | 0.2948 | -0.1506 | -0.15167 | 0.091553 | 0.10986 | -62.6038 | 60.1868 | 60.1501 | 62.2192 | 62.4298 | 122.9599 | 62.3108 | 60.2692
8004.125 | 0.061035 | 0.42618 | -0.7872 | -0.20721 | 0.14206 | -0.2446 | -0.15701 | 60.3745 | -62.2467 | 0.054932 | -62.4619 | 60.1913 | 62.3383 | 62.2833 | 0.076294 | -0.05127 | 0.082245 | 0.2948 | -0.1442 | -0.15808 | 0.041199 | 0.068665 | -62.6907 | 60.1501 | 60.1456 | 62.2421 | 62.4573 | 122.8683 | 62.3337 | 60.2646
8005.8438 | 0.076294 | 0.43579 | -0.784 | -0.22537 | 0.16556 | -0.2681 | -0.17731 | 60.4477 | -62.1277 | 0.16022 | -62.3978 | 60.1822 | 62.2879 | 62.1964 | 0.076294 | -0.084381 | 0.071564 | 0.2948 | -0.16876 | -0.15701 | 0.050354 | 0.11902 | -62.5442 | 60.1593 | 60.1822 | 62.2055 | 62.3978 | 122.7722 | 62.3611 | 60.3058
8007.6406 | 0.061035 | 0.45288 | -0.77866 | -0.20828 | 0.15381 | -0.27771 | -0.17517 | 60.4385 | -62.1552 | 0.073242 | -62.4069 | 60.2234 | 62.2879 | 62.1735 | 0.076294 | -0.069427 | 0.074768 | 0.28732 | -0.16769 | -0.14847 | 0.073242 | 0.11902 | -62.5397 | 60.1959 | 60.1868 | 62.1735 | 62.3932 | 122.7905 | 62.3566 | 60.3378
8009.3594 | 0.061035 | 0.43686 | -0.77011 | -0.20081 | 0.1474 | -0.24567 | -0.17197 | 60.3882 | -62.3108 | -0.022888 | -62.4802 | 60.2371 | 62.3383 | 62.2696 | 0.045776 | -0.055542 | 0.077972 | 0.29907 | -0.15274 | -0.15595 | 0.036621 | 0.041199 | -62.677 | 60.1959 | 60.2005 | 62.2513 | 62.4573 | 122.9141 | 62.3291 | 60.2829
8011.1094 | 0.045776 | 0.45502 | -0.784 | -0.20721 | 0.15274 | -0.28732 | -0.16876 | 60.4431 | -62.1552 | 0.091553 | -62.3932 | 60.2051 | 62.2696 | 62.2101 | 0.061035 | -0.079041 | 0.063019 | 0.27664 | -0.16983 | -0.14954 | 0.050354 | 0.09613 | -62.5442 | 60.1959 | 60.1822 | 62.1689 | 62.3978 | 122.7997 | 62.3566 | 60.3241
8012.8906 | 0.076294 | 0.44861 | -0.78507 | -0.22003 | 0.15381 | -0.27451 | -0.17517 | 60.4935 | -62.1002 | 0.15564 | -62.3611 | 60.1822 | 62.2742 | 62.1918 | 0.061035 | -0.079041 | 0.082245 | 0.27344 | -0.1709 | -0.16342 | 0.11444 | 0.15564 | -62.4985 | 60.1822 | 60.1639 | 62.2147 | 62.3886 | 122.8226 | 62.3291 | 60.3241
8014.6719 | 0.061035 | 0.43686 | -0.77438 | -0.21042 | 0.13886 | -0.25955 | -0.17944 | 60.466 | -62.146 | 0.09613 | -62.384 | 60.1868 | 62.3016 | 62.1964 | 0.061035 | -0.075836 | 0.079041 | 0.28412 | -0.15915 | -0.15381 | 0.1236 | 0.15106 | -62.5259 | 60.173 | 60.1501 | 62.1735 | 62.3932 | 122.7859 | 62.3428 | 60.3378
8016.4531 | 0.061035 | 0.44113 | -0.78079 | -0.20187 | 0.14847 | -0.26596 | -0.18265 | 60.4614 | -62.1368 | 0.14648 | -62.3703 | 60.1913 | 62.2925 | 62.2375 | 0.076294 | -0.0737 | 0.086517 | 0.28519 | -0.15595 | -0.16022 | 0.059509 | 0.11444 | -62.5442 | 60.1685 | 60.173 | 62.2238 | 62.3978 | 122.7722 | 62.3611 | 60.3149
8018.2344 | 0.076294 | 0.4187 | -0.77438 | -0.19333 | 0.16022 | -0.24887 | -0.16769 | 60.3241 | -62.3291 | -0.013733 | -62.4893 | 60.228 | 62.352 | 62.265 | 0.076294 | -0.064087 | 0.085449 | 0.29373 | -0.14313 | -0.15808 | 0.027466 | 0.032043 | -62.6907 | 60.2051 | 60.1639 | 62.2559 | 62.4664 | 122.8683 | 62.3291 | 60.2966
8020 | 0.061035 | 0.44968 | -0.77866 | -0.20828 | 0.16022 | -0.27023 | -0.16556 | 60.4614 | -62.1185 | 0.10071 | -62.3932 | 60.173 | 62.2925 | 62.1964 | 0.076294 | -0.074768 | 0.076904 | 0.28091 | -0.15595 | -0.1474 | 0.12817 | 0.14191 | -62.5168 | 60.173 | 60.1593 | 62.1414 | 62.3749 | 122.7768 | 62.3474 | 60.3149
8021.7188 | 0.076294 | 0.45929 | -0.78507 | -0.2179 | 0.14847 | -0.26916 | -0.17944 | 60.4248 | -62.1506 | 0.068665 | -62.384 | 60.2234 | 62.2742 | 62.1964 | 0.030518 | -0.072632 | 0.071564 | 0.28198 | -0.16556 | -0.15381 | 0.050354 | 0.082397 | -62.5442 | 60.1913 | 60.2142 | 62.1597 | 62.3978 | 122.7997 | 62.3199 | 60.3333
8023.4844 | 0.076294 | 0.44647 | -0.77972 | -0.20508 | 0.15595 | -0.25955 | -0.17838 | 60.466 | -62.1368 | 0.10529 | -62.3886 | 60.2005 | 62.2787 | 62.1918 | 0.061035 | -0.065155 | 0.061951 | 0.28732 | -0.15381 | -0.16235 | 0.10071 | 0.13275 | -62.5442 | 60.1639 | 60.1593 | 62.1689 | 62.3978 | 122.7631 | 62.352 | 60.3378
8025.1875 | 0.061035 | 0.44113 | -0.78079 | -0.20508 | 0.1506 | -0.2446 | -0.16769 | 60.347 | -62.3062 | 0.004578 | -62.4756 | 60.2325 | 62.3245 | 62.2559 | 0.061035 | -0.053406 | 0.082245 | 0.28946 | -0.13886 | -0.15701 | 0.027466 | 0.036621 | -62.6907 | 60.2051 | 60.1593 | 62.233 | 62.4664 | 122.8867 | 62.2925 | 60.2783
8026.9688 | 0.061035 | 0.439 | -0.78079 | -0.21683 | 0.15701 | -0.27771 | -0.16876 | 60.4752 | -62.0728 | 0.13275 | -62.3611 | 60.1868 | 62.2559 | 62.1964 | 0.091553 | -0.076904 | 0.086517 | 0.27771 | -0.17624 | -0.15701 | 0.11444 | 0.15564 | -62.4527 | 60.1776 | 60.1501 | 62.1872 | 62.3886 | 122.8363 | 62.3383 | 60.3149
8028.7344 | 0.091553 | 0.45288 | -0.77759 | -0.20401 | 0.15488 | -0.28091 | -0.18051 | 60.4294 | -62.1414 | 0.086975 | -62.3749 | 60.1868 | 62.2742 | 62.2009 | 0.061035 | -0.082245 | 0.0737 | 0.2948 | -0.16342 | -0.16769 | 0.09613 | 0.11902 | -62.4939 | 60.1959 | 60.1776 | 62.1368 | 62.3657 | 122.8088 | 62.3245 | 60.3195
8030.4531 | 0.061035 | 0.44968 | -0.78507 | -0.18799 | 0.14526 | -0.25421 | -0.16983 | 60.4706 | -62.1231 | 0.11444 | -62.3749 | 60.1868 | 62.265 | 62.2192 | 0.061035 | -0.071564 | 0.064087 | 0.28946 | -0.14313 | -0.15915 | 0.1236 | 0.16479 | -62.5122 | 60.1501 | 60.1227 | 62.1872 | 62.3795 | 122.8134 | 62.3245 | 60.3241
8032.2188 | 0.061035 | 0.43793 | -0.77545 | -0.20721 | 0.1474 | -0.22858 | -0.16556 | 60.3287 | -62.3016 | -0.013733 | -62.4802 | 60.2142 | 62.3474 | 62.265 | 0.076294 | -0.052338 | 0.074768 | 0.298 | -0.1506 | -0.16556 | 0.032043 | 0.027466 | -62.6816 | 60.1959 | 60.1318 | 62.2375 | 62.4252 | 122.8592 | 62.3199 | 60.26
8033.9844 | 0.076294 | 0.43686 | -0.78186 | -0.20187 | 0.15167 | -0.24567 | -0.16876 | 60.4294 | -62.1414 | 0.07782 | -62.384 | 60.2005 | 62.3199 | 62.2101 | 0.061035 | -0.065155 | 0.068359 | 0.28625 | -0.15274 | -0.15595 | 0.13275 | 0.17853 | -62.5259 | 60.1639 | 60.1135 | 62.1872 | 62.3932 | 122.9004 | 62.2925 | 60.2783
8035.75 | 0.061035 | 0.44754 | -0.80109 | -0.22964 | 0.15488 | -0.28198 | -0.17731 | 60.4523 | -62.1231 | 0.10071 | -62.3657 | 60.2234 | 62.2787 | 62.1689 | 0.061035 | -0.068359 | 0.074768 | 0.28519 | -0.16129 | -0.14633 | 0.10071 | 0.12817 | -62.4802 | 60.173 | 60.1868 | 62.1506 | 62.352 | 122.8134 | 62.3108 | 60.3149
8037.5312 | 0.061035 | 0.43045 | -0.78613 | -0.22003 | 0.15915 | -0.27664 | -0.16876 | 60.4889 | -62.0956 | 0.16479 | -62.352 | 60.2097 | 62.2787 | 62.1918 | 0.091553 | -0.069427 | 0.09079 | 0.30121 | -0.16769 | -0.15808 | 0.10529 | 0.13733 | -62.4664 | 60.141 | 60.1456 | 62.1689 | 62.3657 | 122.8043 | 62.3062 | 60.2692
8039.2344 | 0.061035 | 0.44006 | -0.78827 | -0.21683 | 0.15595 | -0.25955 | -0.18265 | 60.3653 | -62.2375 | 0.036621 | -62.4527 | 60.2234 | 62.3245 | 62.2604 | 0.061035 | -0.058746 | 0.080109 | 0.28946 | -0.14633 | -0.15274 | 0 | 0.022888 | -62.645 | 60.1868 | 60.1501 | 62.2238 | 62.4252 | 122.818 | 62.3199 | 60.2509
8041.0312 | 0.061035 | 0.44113 | -0.79147 | -0.20828 | 0.14313 | -0.26276 | -0.16663 | 60.4431 | -62.1323 | 0.12817 | -62.3795 | 60.1776 | 62.2879 | 62.2101 | 0.061035 | -0.080109 | 0.069427 | 0.28519 | -0.1506 | -0.15595 | 0.041199 | 0.082397 | -62.5717 | 60.1593 | 60.1501 | 62.2192 | 62.4207 | 122.7585 | 62.3611 | 60.3149
8042.8281 | 0.076294 | 0.43259 | -0.78613 | -0.21255 | 0.15915 | -0.27344 | -0.17517 | 60.466 | -62.1002 | 0.12817 | -62.3611 | 60.228 | 62.2559 | 62.2055 | 0.076294 | -0.065155 | 0.072632 | 0.28519 | -0.16876 | -0.15701 | 0.09613 | 0.12817 | -62.4847 | 60.1913 | 60.1593 | 62.1552 | 62.3703 | 122.8226 | 62.3154 | 60.3058
8044.5469 | 0.061035 | 0.43686 | -0.784 | -0.20828 | 0.15915 | -0.25635 | -0.17731 | 60.466 | -62.1002 | 0.16479 | -62.352 | 60.1685 | 62.2787 | 62.2009 | 0.076294 | -0.070496 | 0.074768 | 0.28839 | -0.15915 | -0.15701 | 0.086975 | 0.12817 | -62.5076 | 60.1822 | 60.1273 | 62.1872 | 62.4069 | 122.7631 | 62.3291 | 60.3058
8046.3281 | 0.061035 | 0.45075 | -0.78507 | -0.2179 | 0.14847 | -0.25314 | -0.16769 | 60.4706 | -62.1185 | 0.1236 | -62.3703 | 60.1868 | 62.2879 | 62.2101 | 0.061035 | -0.077972 | 0.070496 | 0.2948 | -0.15808 | -0.16663 | 0.1236 | 0.17395 | -62.5076 | 60.1547 | 60.1273 | 62.1964 | 62.3932 | 122.8363 | 62.3016 | 60.3012
8048.1094 | 0.061035 | 0.44968 | -0.77866 | -0.21149 | 0.13565 | -0.27237 | -0.1709 | 60.4614 | -62.0956 | 0.1236 | -62.3474 | 60.2142 | 62.2513 | 62.1872 | 0.045776 | -0.079041 | 0.067291 | 0.28412 | -0.16556 | -0.15167 | 0.11444 | 0.13275 | -62.4619 | 60.1593 | 60.1501 | 62.1689 | 62.3566 | 122.8226 | 62.3108 | 60.2966
8049.8125 | 0.030518 | 0.41443 | -0.76157 | -0.21576 | 0.15488 | -0.23285 | -0.16235 | 60.4065 | -62.2147 | 0.09613 | -62.4344 | 60.1776 | 62.352 | 62.2696 | 0.030518 | -0.045929 | 0.076904 | 0.30228 | -0.14847 | -0.16022 | 0.07782 | 0.086975 | -62.6175 | 60.141 | 60.0723 | 62.2421 | 62.4527 | 122.85 | 62.3199 | 60.2325
8051.5938 | 0.061035 | 0.41122 | -0.77866 | -0.20401 | 0.14526 | -0.23605 | -0.15701 | 60.3287 | -62.2604 | 0.036621 | -62.4756 | 60.2005 | 62.3611 | 62.265 | 0.061035 | -0.064087 | 0.077972 | 0.298 | -0.14206 | -0.15808 | 0.018311 | 0.059509 | -62.6587 | 60.1685 | 60.1364 | 62.2604 | 62.4481 | 122.8409 | 62.3428 | 60.2646
8053.375 | 0.045776 | 0.43686 | -0.78934 | -0.20615 | 0.15274 | -0.25955 | -0.15701 | 60.4065 | -62.1597 | 0.082397 | -62.384 | 60.2005 | 62.3154 | 62.2009 | 0.061035 | -0.064087 | 0.066223 | 0.29266 | -0.15274 | -0.14633 | 0.12817 | 0.16022 | -62.5122 | 60.1685 | 60.1364 | 62.1872 | 62.384 | 122.8912 | 62.2833 | 60.2737
8055.1562 | 0.061035 | 0.43366 | -0.78079 | -0.2211 | 0.14206 | -0.25207 | -0.16022 | 60.3195 | -62.2421 | 0.059509 | -62.4619 | 60.2234 | 62.3154 | 62.2513 | 0.061035 | -0.071564 | 0.080109 | 0.28305 | -0.16129 | -0.1474 | -0.004578 | 0.041199 | -62.6358 | 60.1868 | 60.1639 | 62.2375 | 62.439 | 122.8638 | 62.3108 | 60.2463
8056.875 | 0.061035 | 0.45609 | -0.79041 | -0.22644 | 0.14526 | -0.29053 | -0.16983 | 60.3882 | -62.146 | 0.059509 | -62.384 | 60.2142 | 62.2604 | 62.1918 | 0.061035 | -0.0737 | 0.080109 | 0.28946 | -0.16769 | -0.1442 | 0.045776 | 0.091553 | -62.5305 | 60.173 | 60.1639 | 62.1368 | 62.3932 | 122.7997 | 62.3154 | 60.3149
8058.6562 | 0.091553 | 0.43152 | -0.77652 | -0.20081 | 0.14954 | -0.2478 | -0.16022 | 60.3333 | -62.2513 | 0.022888 | -62.4664 | 60.1776 | 62.3154 | 62.2833 | 0.061035 | -0.03952 | 0.065155 | 0.30228 | -0.13886 | -0.15808 | 0.022888 | 0.054932 | -62.6678 | 60.1868 | 60.1593 | 62.2421 | 62.4527 | 122.8546 | 62.3016 | 60.2875
8060.4375 | 0.076294 | 0.4422 | -0.77331 | -0.21576 | 0.15595 | -0.25742 | -0.16876 | 60.3699 | -62.2284 | 0.032043 | -62.4252 | 60.2188 | 62.3154 | 62.2192 | 0.045776 | -0.067291 | 0.066223 | 0.28091 | -0.15808 | -0.15595 | 0.091553 | 0.11902 | -62.5534 | 60.1501 | 60.1685 | 62.1826 | 62.3795 | 122.8958 | 62.2787 | 60.2463
8062.1875 | 0.061035 | 0.43793 | -0.78507 | -0.22964 | 0.15274 | -0.28412 | -0.18372 | 60.4477 | -62.1048 | 0.1236 | -62.3428 | 60.2051 | 62.2513 | 62.178 | 0.091553 | -0.088654 | 0.077972 | 0.29266 | -0.1709 | -0.15701 | 0.086975 | 0.13275 | -62.4619 | 60.1639 | 60.1593 | 62.1414 | 62.3749 | 122.7905 | 62.3245 | 60.2783
8063.9219 | 0.061035 | 0.43152 | -0.784 | -0.21576 | 0.15167 | -0.27023 | -0.17944 | 60.379 | -62.2101 | 0.07782 | -62.4252 | 60.1868 | 62.3016 | 62.2421 | 0.045776 | -0.072632 | 0.089722 | 0.29266 | -0.15915 | -0.1506 | 0.004578 | 0.022888 | -62.6083 | 60.2005 | 60.1593 | 62.2101 | 62.4527 | 122.7448 | 62.352 | 60.2829
8065.7031 | 0.076294 | 0.44113 | -0.80856 | -0.2243 | 0.14099 | -0.27878 | -0.18372 | 60.4568 | -62.0636 | 0.14191 | -62.3428 | 60.1639 | 62.2513 | 62.178 | 0.061035 | -0.084381 | 0.071564 | 0.27878 | -0.17517 | -0.15274 | 0.10071 | 0.15106 | -62.4481 | 60.1639 | 60.1135 | 62.1826 | 62.3566 | 122.7997 | 62.3062 | 60.2966
8067.4844 | 0.076294 | 0.44327 | -0.77225 | -0.20721 | 0.15488 | -0.25955 | -0.16876 | 60.466 | -62.1185 | 0.11444 | -62.3657 | 60.1593 | 62.2467 | 62.1735 | 0.061035 | -0.061951 | 0.066223 | 0.29053 | -0.15381 | -0.16022 | 0.12817 | 0.16479 | -62.4847 | 60.1501 | 60.1227 | 62.1597 | 62.3795 | 122.8317 | 62.2787 | 60.2966
8069.25 | 0.061035 | 0.41763 | -0.77225 | -0.22217 | 0.1506 | -0.25955 | -0.16876 | 60.4385 | -62.1735 | 0.086975 | -62.3749 | 60.1776 | 62.2742 | 62.2009 | 0.076294 | -0.075836 | 0.081177 | 0.29373 | -0.14206 | -0.15915 | 0.13733 | 0.15564 | -62.5351 | 60.1593 | 60.1227 | 62.1826 | 62.3611 | 122.8775 | 62.2879 | 60.2783
8070.9531 | 0.091553 | 0.43259 | -0.78293 | -0.21255 | 0.1474 | -0.27557 | -0.17838 | 60.4385 | -62.0911 | 0.11444 | -62.3474 | 60.2234 | 62.2559 | 62.1964 | 0.076294 | -0.080109 | 0.074768 | 0.29159 | -0.16449 | -0.15488 | 0.086975 | 0.11902 | -62.471 | 60.173 | 60.1501 | 62.1414 | 62.3566 | 122.8043 | 62.2925 | 60.3058
8072.7188 | 0.076294 | 0.44861 | -0.77652 | -0.2179 | 0.14847 | -0.27451 | -0.18692 | 60.4065 | -62.1552 | 0.082397 | -62.3795 | 60.2234 | 62.2375 | 62.1826 | 0.076294 | -0.066223 | 0.072632 | 0.29266 | -0.16769 | -0.15274 | 0.059509 | 0.10529 | -62.5397 | 60.1913 | 60.1776 | 62.178 | 62.3611 | 122.7493 | 62.3108 | 60.3149
8074.5 | 0.061035 | 0.42618 | -0.78507 | -0.2179 | 0.14954 | -0.25207 | -0.16876 | 60.3745 | -62.233 | 0.068665 | -62.4619 | 60.2097 | 62.3016 | 62.2421 | 0.045776 | -0.052338 | 0.068359 | 0.28839 | -0.15701 | -0.16663 | 0 | 0.022888 | -62.6129 | 60.1913 | 60.1685 | 62.2284 | 62.439 | 122.7448 | 62.3383 | 60.2646
8076.2188 | 0.061035 | 0.44434 | -0.7872 | -0.2211 | 0.15701 | -0.26489 | -0.18158 | 60.4568 | -62.0819 | 0.16022 | -62.3474 | 60.1685 | 62.2467 | 62.1826 | 0.076294 | -0.075836 | 0.074768 | 0.27985 | -0.15915 | -0.16342 | 0.073242 | 0.14648 | -62.4847 | 60.1501 | 60.0998 | 62.1735 | 62.3795 | 122.7356 | 62.3062 | 60.2966
8078.0156 | 0.061035 | 0.43579 | -0.77652 | -0.20401 | 0.14847 | -0.26062 | -0.16983 | 60.4523 | -62.0911 | 0.10529 | -62.352 | 60.173 | 62.2787 | 62.2009 | 0.061035 | -0.079041 | 0.05661 | 0.28091 | -0.16022 | -0.14954 | 0.11902 | 0.15564 | -62.4939 | 60.1501 | 60.1135 | 62.1643 | 62.3474 | 122.7676 | 62.2879 | 60.3149
8079.7344 | 0.061035 | 0.44861 | -0.79041 | -0.20935 | 0.14847 | -0.26276 | -0.17303 | 60.4431 | -62.0636 | 0.16479 | -62.3657 | 60.1822 | 62.2604 | 62.1872 | 0.045776 | -0.076904 | 0.0737 | 0.27557 | -0.16022 | -0.1506 | 0.07782 | 0.13733 | -62.4985 | 60.141 | 60.1227 | 62.1643 | 62.3657 | 122.7493 | 62.3245 | 60.2829
8081.5156 | 0.076294 | 0.43793 | -0.76797 | -0.20081 | 0.14206 | -0.23712 | -0.17517 | 60.3378 | -62.265 | 0 | -62.4664 | 60.2142 | 62.3291 | 62.233 | 0.061035 | -0.059814 | 0.081177 | 0.29587 | -0.13672 | -0.16449 | 0.004578 | 0.032043 | -62.677 | 60.1822 | 60.1501 | 62.2284 | 62.4527 | 122.8271 | 62.3062 | 60.2554
8083.2812 | 0.076294 | 0.46143 | -0.78934 | -0.21149 | 0.14526 | -0.28519 | -0.1741 | 60.3973 | -62.1231 | 0.073242 | -62.3703 | 60.2097 | 62.2513 | 62.178 | 0.030518 | -0.079041 | 0.066223 | 0.28198 | -0.16022 | -0.14954 | 0.054932 | 0.09613 | -62.4939 | 60.1593 | 60.1685 | 62.1414 | 62.352 | 122.7539 | 62.2925 | 60.3287
8084.9844 | 0.061035 | 0.44861 | -0.79361 | -0.21896 | 0.15808 | -0.27878 | -0.17624 | 60.3973 | -62.1323 | 0.082397 | -62.3749 | 60.2097 | 62.2559 | 62.178 | 0.076294 | -0.072632 | 0.069427 | 0.28946 | -0.1741 | -0.14313 | 0.059509 | 0.10071 | -62.5031 | 60.1822 | 60.1501 | 62.1368 | 62.3566 | 122.7676 | 62.3062 | 60.2921
8086.7812 | 0.076294 | 0.44327 | -0.78613 | -0.2179 | 0.1506 | -0.2713 | -0.17303 | 60.4752 | -62.0911 | 0.12817 | -62.3383 | 60.1913 | 62.2238 | 62.1506 | 0.045776 | -0.074768 | 0.070496 | 0.29053 | -0.16129 | -0.15274 | 0.10529 | 0.13275 | -62.4756 | 60.1685 | 60.173 | 62.1597 | 62.3611 | 122.7859 | 62.2971 | 60.3012
8088.5781 | 0.076294 | 0.43259 | -0.76477 | -0.20401 | 0.15381 | -0.24994 | -0.1741 | 60.4385 | -62.1735 | 0.073242 | -62.3795 | 60.1639 | 62.2787 | 62.2009 | 0.076294 | -0.057678 | 0.067291 | 0.29694 | -0.15274 | -0.17517 | 0.13275 | 0.15564 | -62.5031 | 60.1593 | 60.141 | 62.178 | 62.3566 | 122.8729 | 62.2879 | 60.2509
8090.2969 | 0.076294 | 0.43686 | -0.78186 | -0.21362 | 0.14847 | -0.24567 | -0.16449 | 60.3378 | -62.2467 | 0.045776 | -62.4298 | 60.2097 | 62.3199 | 62.2467 | 0.045776 | -0.05127 | 0.081177 | 0.28946 | -0.15488 | -0.16663 | 0.013733 | 0.022888 | -62.6266 | 60.1959 | 60.1364 | 62.2559 | 62.4298 | 122.8363 | 62.3154 | 60.2371
8092.0469 | 0.076294 | 0.40268 | -0.7872 | -0.20508 | 0.15488 | -0.2446 | -0.16876 | 60.3287 | -62.2696 | -0.013733 | -62.4481 | 60.1868 | 62.3291 | 62.2375 | 0.076294 | -0.058746 | 0.09079 | 0.29373 | -0.14313 | -0.15595 | 0.022888 | 0.050354 | -62.6633 | 60.173 | 60.141 | 62.2192 | 62.4252 | 122.85 | 62.3199 | 60.2371
8093.7656 | 0.045776 | 0.45075 | -0.77972 | -0.21255 | 0.15274 | -0.28519 | -0.17303 | 60.466 | -62.0407 | 0.14648 | -62.3245 | 60.1776 | 62.2192 | 62.1689 | 0.061035 | -0.087585 | 0.072632 | 0.27985 | -0.17517 | -0.15701 | 0.086975 | 0.16022 | -62.4619 | 60.1456 | 60.1181 | 62.1552 | 62.3749 | 122.7585 | 62.3108 | 60.2829
8095.5469 | 0.061035 | 0.44006 | -0.79254 | -0.21576 | 0.15915 | -0.27664 | -0.17624 | 60.4523 | -62.0544 | 0.15106 | -62.3337 | 60.173 | 62.2375 | 62.1689 | 0.061035 | -0.087585 | 0.079041 | 0.28519 | -0.17303 | -0.1506 | 0.10986 | 0.16479 | -62.439 | 60.1181 | 60.1364 | 62.1506 | 62.3657 | 122.7859 | 62.2925 | 60.2737
8097.3281 | 0.061035 | 0.4187 | -0.79041 | -0.2211 | 0.15595 | -0.26596 | -0.1709 | 60.3241 | -62.2147 | 0.045776 | -62.4344 | 60.2005 | 62.3199 | 62.2284 | 0.030518 | -0.072632 | 0.0737 | 0.27451 | -0.15167 | -0.15915 | -0.009155 | 0.009155 | -62.5992 | 60.1913 | 60.1318 | 62.233 | 62.4023 | 122.7448 | 62.3199 | 60.3149
8099.0312 | 0.076294 | 0.44327 | -0.79041 | -0.19653 | 0.14954 | -0.23178 | -0.16663 | 60.3195 | -62.2513 | -0.022888 | -62.4481 | 60.2417 | 62.3016 | 62.2467 | 0.045776 | -0.05661 | 0.063019 | 0.28519 | -0.13992 | -0.1506 | 0.050354 | 0.064087 | -62.6266 | 60.1685 | 60.1135 | 62.2055 | 62.4069 | 122.8638 | 62.265 | 60.2463
8100.8125 | 0.061035 | 0.41977 | -0.78827 | -0.21576 | 0.14526 | -0.25314 | -0.16769 | 60.3104 | -62.2421 | 0.045776 | -62.4344 | 60.1959 | 62.3062 | 62.233 | 0.045776 | -0.059814 | 0.070496 | 0.2948 | -0.16235 | -0.1506 | 0 | 0.004578 | -62.6175 | 60.1776 | 60.1501 | 62.2055 | 62.4115 | 122.7951 | 62.3062 | 60.228
8102.5781 | 0.091553 | 0.43259 | -0.77331 | -0.20615 | 0.1506 | -0.25742 | -0.16342 | 60.2966 | -62.2559 | -0.009155 | -62.4573 | 60.1959 | 62.3199 | 62.233 | 0.091553 | -0.057678 | 0.069427 | 0.29053 | -0.14099 | -0.15488 | 0.027466 | 0.041199 | -62.645 | 60.1593 | 60.1318 | 62.2192 | 62.4435 | 122.8317 | 62.2971 | 60.2142
8104.3594 | 0.076294 | 0.40802 | -0.76904 | -0.20615 | 0.15488 | -0.24246 | -0.16663 | 60.347 | -62.1964 | 0.091553 | -62.4435 | 60.1593 | 62.3245 | 62.2604 | 0.076294 | -0.058746 | 0.077972 | 0.298 | -0.15274 | -0.15701 | 0.073242 | 0.09613 | -62.59 | 60.1227 | 60.1318 | 62.2284 | 62.4207 | 122.8363 | 62.3291 | 60.2051
8106.125 | 0.061035 | 0.42297 | -0.784 | -0.22644 | 0.14847 | -0.28625 | -0.16876 | 60.4202 | -62.0819 | 0.15564 | -62.3428 | 60.1547 | 62.2559 | 62.1735 | 0.061035 | -0.071564 | 0.079041 | 0.28839 | -0.17303 | -0.1506 | 0.07782 | 0.13275 | -62.4893 | 60.1273 | 60.141 | 62.1643 | 62.3611 | 122.7264 | 62.3108 | 60.2737
8107.8281 | 0.061035 | 0.42191 | -0.78186 | -0.21149 | 0.15701 | -0.25635 | -0.16449 | 60.347 | -62.1964 | 0.086975 | -62.4115 | 60.1913 | 62.3291 | 62.2147 | 0.091553 | -0.058746 | 0.075836 | 0.28732 | -0.1474 | -0.15808 | 0.041199 | 0.091553 | -62.5854 | 60.1318 | 60.1089 | 62.233 | 62.4252 | 122.8455 | 62.3016 | 60.2188
8109.6094 | 0.061035 | 0.4155 | -0.77652 | -0.20828 | 0.16556 | -0.25101 | -0.16663 | 60.347 | -62.2055 | 0.068665 | -62.4207 | 60.1776 | 62.3108 | 62.265 | 0.061035 | -0.064087 | 0.075836 | 0.30762 | -0.14954 | -0.15915 | 0.050354 | 0.07782 | -62.59 | 60.1593 | 60.1181 | 62.2375 | 62.4252 | 122.8409 | 62.2833 | 60.2005
8111.3906 | 0.061035 | 0.43045 | -0.77652 | -0.20508 | 0.15381 | -0.25421 | -0.16235 | 60.2966 | -62.2513 | 0 | -62.4481 | 60.1913 | 62.3245 | 62.233 | 0.045776 | -0.058746 | 0.079041 | 0.29907 | -0.14847 | -0.14847 | -0.009155 | 0.041199 | -62.6404 | 60.1547 | 60.1913 | 62.233 | 62.3978 | 122.7997 | 62.3154 | 60.228
8113.1562 | 0.061035 | 0.44113 | -0.78186 | -0.20081 | 0.15488 | -0.27878 | -0.1741 | 60.3195 | -62.1735 | 0.068665 | -62.4207 | 60.1639 | 62.2925 | 62.2101 | 0.076294 | -0.076904 | 0.074768 | 0.28519 | -0.15488 | -0.15915 | -0.013733 | 0.022888 | -62.5854 | 60.1685 | 60.1685 | 62.2238 | 62.3886 | 122.7127 | 62.3245 | 60.2783
8114.8906 | 0.061035 | 0.43472 | -0.77438 | -0.21896 | 0.15274 | -0.27451 | -0.17624 | 60.3287 | -62.1964 | 0.059509 | -62.4115 | 60.2051 | 62.2742 | 62.2147 | 0.091553 | -0.054474 | 0.074768 | 0.28839 | -0.17517 | -0.14633 | -0.018311 | 0.009155 | -62.6038 | 60.1685 | 60.1685 | 62.2147 | 62.4023 | 122.7173 | 62.3383 | 60.26
8116.6875 | 0.061035 | 0.43152 | -0.78934 | -0.22003 | 0.15915 | -0.27664 | -0.17838 | 60.4431 | -62.059 | 0.14648 | -62.3337 | 60.1822 | 62.2284 | 62.1368 | 0.045776 | -0.084381 | 0.067291 | 0.28625 | -0.17838 | -0.15274 | 0.10986 | 0.16479 | -62.4207 | 60.1547 | 60.1501 | 62.1597 | 62.3291 | 122.7585 | 62.3062 | 60.2554
8118.4062 | 0.045776 | 0.4422 | -0.78507 | -0.20294 | 0.16129 | -0.27451 | -0.18265 | 60.4111 | -62.1185 | 0.086975 | -62.3703 | 60.173 | 62.2101 | 62.1597 | 0.045776 | -0.080109 | 0.055542 | 0.28732 | -0.15808 | -0.16022 | 0.07782 | 0.13275 | -62.5076 | 60.1547 | 60.1547 | 62.1506 | 62.3428 | 122.7173 | 62.2833 | 60.3104
8120.1719 | 0.061035 | 0.43686 | -0.78079 | -0.21469 | 0.15381 | -0.27237 | -0.17731 | 60.4431 | -62.0911 | 0.16937 | -62.3337 | 60.1822 | 62.2375 | 62.1826 | 0.076294 | -0.064087 | 0.0737 | 0.28732 | -0.17517 | -0.16556 | 0.073242 | 0.1236 | -62.4756 | 60.1639 | 60.1273 | 62.1689 | 62.352 | 122.7127 | 62.3016 | 60.2554
8121.9531 | 0.030518 | 0.41336 | -0.77759 | -0.20935 | 0.13779 | -0.24033 | -0.16769 | 60.3561 | -62.1964 | 0.086975 | -62.4161 | 60.1868 | 62.3199 | 62.2375 | 0.061035 | -0.058746 | 0.084381 | 0.29159 | -0.1474 | -0.16235 | 0.068665 | 0.086975 | -62.5946 | 60.141 | 60.1181 | 62.2284 | 62.4298 | 122.8226 | 62.3016 | 60.2051
8123.7188 | 0.061035 | 0.42297 | -0.78079 | -0.20081 | 0.1506 | -0.24887 | -0.16022 | 60.347 | -62.1826 | 0.027466 | -62.3978 | 60.1822 | 62.2925 | 62.1964 | 0.061035 | -0.071564 | 0.076904 | 0.28946 | -0.14954 | -0.15701 | 0.09613 | 0.12817 | -62.5351 | 60.1501 | 60.1044 | 62.1918 | 62.3566 | 122.8363 | 62.2787 | 60.2371
8125.4375 | 0.061035 | 0.42084 | -0.76904 | -0.21042 | 0.14633 | -0.24674 | -0.15915 | 60.347 | -62.1918 | 0.068665 | -62.4252 | 60.1547 | 62.3291 | 62.2238 | 0.061035 | -0.057678 | 0.074768 | 0.29694 | -0.15808 | -0.1506 | 0.050354 | 0.073242 | -62.6266 | 60.1273 | 60.1501 | 62.1964 | 62.4252 | 122.7905 | 62.2971 | 60.2554
8127.1875 | 0.061035 | 0.45822 | -0.78934 | -0.21149 | 0.14526 | -0.28625 | -0.16983 | 60.3928 | -62.1048 | 0.091553 | -62.3566 | 60.1776 | 62.2513 | 62.146 | 0.061035 | -0.091858 | 0.074768 | 0.29266 | -0.16876 | -0.16022 | 0.07782 | 0.11902 | -62.4939 | 60.1501 | 60.1547 | 62.1414 | 62.3474 | 122.7127 | 62.2971 | 60.2966
8128.9844 | 0.061035 | 0.45075 | -0.78293 | -0.21469 | 0.14526 | -0.28732 | -0.17517 | 60.3973 | -62.114 | 0.082397 | -62.352 | 60.1456 | 62.2009 | 62.1689 | 0.076294 | -0.080109 | 0.082245 | 0.27878 | -0.16449 | -0.15595 | 0.082397 | 0.10529 | -62.5122 | 60.1501 | 60.141 | 62.146 | 62.3611 | 122.7219 | 62.3016 | 60.3287
8130.7031 | 0.061035 | 0.41657 | -0.784 | -0.23071 | 0.1474 | -0.26382 | -0.16769 | 60.4202 | -62.0911 | 0.10071 | -62.3383 | 60.173 | 62.2513 | 62.1597 | 0.076294 | -0.070496 | 0.081177 | 0.29159 | -0.16022 | -0.16449 | 0.1236 | 0.16479 | -62.4619 | 60.0998 | 60.0998 | 62.1506 | 62.3703 | 122.7402 | 62.2833 | 60.3058
8132.4844 | 0.030518 | 0.43366 | -0.77331 | -0.20508 | 0.13886 | -0.2478 | -0.17731 | 60.4156 | -62.1048 | 0.091553 | -62.3383 | 60.1456 | 62.2696 | 62.1689 | 0.061035 | -0.069427 | 0.075836 | 0.28519 | -0.1442 | -0.16876 | 0.14191 | 0.16937 | -62.4847 | 60.141 | 60.0906 | 62.1735 | 62.3428 | 122.8409 | 62.2742 | 60.2646
8134.2656 | 0.076294 | 0.47104 | -0.77866 | -0.1976 | 0.14954 | -0.28091 | -0.17838 | 60.4202 | -62.0682 | 0.11902 | -62.3291 | 60.1776 | 62.2238 | 62.1506 | 0.061035 | -0.080109 | 0.064087 | 0.29159 | -0.16129 | -0.1506 | 0.10071 | 0.11902 | -62.4435 | 60.1501 | 60.1456 | 62.146 | 62.3291 | 122.7493 | 62.2833 | 60.2783
8135.9688 | 0.061035 | 0.41016 | -0.78293 | -0.23178 | 0.14954 | -0.25635 | -0.17624 | 60.3378 | -62.1689 | 0.068665 | -62.3978 | 60.2005 | 62.2879 | 62.2192 | 0.061035 | -0.067291 | 0.080109 | 0.29266 | -0.16983 | -0.16983 | -0.013733 | 0 | -62.5992 | 60.1868 | 60.1364 | 62.2192 | 62.3749 | 122.7173 | 62.3062 | 60.2921
8137.7344 | 0.076294 | 0.41977 | -0.77545 | -0.18799 | 0.14954 | -0.23926 | -0.16449 | 60.3561 | -62.178 | 0.07782 | -62.4115 | 60.1501 | 62.3016 | 62.2604 | 0.045776 | -0.052338 | 0.074768 | 0.29053 | -0.14526 | -0.15167 | 0.073242 | 0.086975 | -62.5946 | 60.1364 | 60.0998 | 62.2009 | 62.4161 | 122.8088 | 62.3154 | 60.1822
8139.5156 | 0.076294 | 0.45075 | -0.78827 | -0.22003 | 0.14206 | -0.2948 | -0.1741 | 60.4111 | -62.0499 | 0.1236 | -62.3199 | 60.1868 | 62.2375 | 62.146 | 0.076294 | -0.075836 | 0.0737 | 0.28519 | -0.16449 | -0.15701 | 0.09613 | 0.13733 | -62.4435 | 60.1181 | 60.1318 | 62.1414 | 62.3474 | 122.7539 | 62.2559 | 60.2646
8141.2344 | 0.061035 | 0.42725 | -0.78079 | -0.19867 | 0.15381 | -0.24033 | -0.17731 | 60.3058 | -62.2467 | -0.027466 | -62.4435 | 60.2005 | 62.2925 | 62.2375 | 0.061035 | -0.054474 | 0.068359 | 0.28519 | -0.15701 | -0.14526 | 0.045776 | 0.036621 | -62.6129 | 60.1456 | 60.141 | 62.1964 | 62.4023 | 122.8226 | 62.2787 | 60.2325
8143.0156 | 0.045776 | 0.42511 | -0.79788 | -0.2243 | 0.14633 | -0.27344 | -0.18158 | 60.3699 | -62.1094 | 0.1236 | -62.352 | 60.1639 | 62.2467 | 62.1735 | 0.091553 | -0.076904 | 0.075836 | 0.27878 | -0.1709 | -0.14847 | 0.018311 | 0.07782 | -62.5488 | 60.1501 | 60.1364 | 62.178 | 62.3932 | 122.6898 | 62.3199 | 60.2783
8144.7969 | 0.061035 | 0.42831 | -0.76904 | -0.21362 | 0.1442 | -0.24674 | -0.16556 | 60.3149 | -62.2559 | 0.004578 | -62.4435 | 60.173 | 62.3062 | 62.233 | 0.061035 | -0.066223 | 0.076904 | 0.298 | -0.1506 | -0.15274 | 0.013733 | 0.032043 | -62.6633 | 60.141 | 60.1364 | 62.2009 | 62.4115 | 122.7631 | 62.2925 | 60.228
8146.5938 | 0.076294 | 0.44006 | -0.79361 | -0.2179 | 0.13886 | -0.28091 | -0.18478 | 60.3928 | -62.0911 | 0.10529 | -62.3337 | 60.1822 | 62.233 | 62.1506 | 0.061035 | -0.081177 | 0.068359 | 0.29159 | -0.16556 | -0.16129 | 0.082397 | 0.13733 | -62.4481 | 60.1547 | 60.1456 | 62.1277 | 62.3383 | 122.7631 | 62.2879 | 60.2783
8148.375 | 0.076294 | 0.43793 | -0.78079 | -0.22751 | 0.14954 | -0.28412 | -0.16663 | 60.3745 | -62.1094 | 0.086975 | -62.3245 | 60.1959 | 62.2192 | 62.1597 | 0.045776 | -0.079041 | 0.070496 | 0.27771 | -0.1709 | -0.15381 | 0.082397 | 0.1236 | -62.439 | 60.1456 | 60.141 | 62.1368 | 62.3474 | 122.7631 | 62.2833 | 60.2692
8150.0781 | 0.045776 | 0.45395 | -0.78507 | -0.21362 | 0.15274 | -0.27878 | -0.1709 | 60.379 | -62.1277 | 0.064087 | -62.3566 | 60.2005 | 62.2055 | 62.1552 | 0.061035 | -0.086517 | 0.066223 | 0.27985 | -0.15274 | -0.15488 | 0.068665 | 0.086975 | -62.4893 | 60.1639 | 60.141 | 62.1414 | 62.3566 | 122.7356 | 62.2971 | 60.2692
8151.8438 | 0.076294 | 0.44861 | -0.784 | -0.21362 | 0.15381 | -0.26276 | -0.16983 | 60.4294 | -62.0544 | 0.11444 | -62.3474 | 60.1547 | 62.2238 | 62.1323 | 0.061035 | -0.074768 | 0.071564 | 0.28839 | -0.14313 | -0.16129 | 0.12817 | 0.16937 | -62.4619 | 60.1273 | 60.1044 | 62.1552 | 62.3611 | 122.7264 | 62.2879 | 60.2875
8153.625 | 0.061035 | 0.42084 | -0.77011 | -0.22964 | 0.13992 | -0.25101 | -0.17517 | 60.3287 | -62.2192 | 0.045776 | -62.4252 | 60.2005 | 62.2833 | 62.233 | 0.045776 | -0.053406 | 0.070496 | 0.28305 | -0.14526 | -0.17197 | 0.004578 | 0.036621 | -62.6083 | 60.1868 | 60.1135 | 62.2192 | 62.4069 | 122.8134 | 62.265 | 60.2234
8155.3281 | 0.076294 | 0.44647 | -0.78079 | -0.20294 | 0.1506 | -0.26276 | -0.16556 | 60.4248 | -62.0728 | 0.10986 | -62.3199 | 60.1456 | 62.2284 | 62.1643 | 0.061035 | -0.068359 | 0.061951 | 0.29694 | -0.15381 | -0.16342 | 0.13733 | 0.1831 | -62.4847 | 60.1364 | 60.0998 | 62.146 | 62.3474 | 122.7859 | 62.2833 | 60.2692
8157.0938 | 0.045776 | 0.42938 | -0.77652 | -0.23605 | 0.1506 | -0.27344 | -0.18051 | 60.4477 | -62.0544 | 0.16022 | -62.3108 | 60.1639 | 62.2147 | 62.1506 | 0.045776 | -0.070496 | 0.064087 | 0.28839 | -0.17731 | -0.15915 | 0.12817 | 0.16479 | -62.4298 | 60.1273 | 60.141 | 62.146 | 62.3566 | 122.7219 | 62.2925 | 60.2783
8158.8906 | 0.076294 | 0.44968 | -0.77545 | -0.20081 | 0.1474 | -0.26916 | -0.18051 | 60.3928 | -62.1002 | 0.11902 | -62.3611 | 60.1547 | 62.2604 | 62.1918 | 0.076294 | -0.057678 | 0.070496 | 0.28625 | -0.16022 | -0.16022 | 0.022888 | 0.059509 | -62.5488 | 60.1501 | 60.141 | 62.1826 | 62.3886 | 122.6807 | 62.3245 | 60.2692
8160.5938 | 0.045776 | 0.43366 | -0.784 | -0.19333 | 0.1506 | -0.24246 | -0.16235 | 60.3149 | -62.2284 | -0.013733 | -62.4207 | 60.1959 | 62.2971 | 62.2101 | 0.076294 | -0.057678 | 0.065155 | 0.29266 | -0.14313 | -0.16022 | 0.054932 | 0.054932 | -62.6083 | 60.173 | 60.1181 | 62.1964 | 62.4069 | 122.818 | 62.2559 | 60.2051
8162.3594 | 0.076294 | 0.43366 | -0.77331 | -0.20935 | 0.14954 | -0.2478 | -0.17303 | 60.2966 | -62.265 | -0.013733 | -62.4435 | 60.1913 | 62.2879 | 62.2238 | 0.061035 | -0.063019 | 0.083313 | 0.28839 | -0.15167 | -0.14633 | 0.013733 | 0.041199 | -62.6404 | 60.1501 | 60.1318 | 62.2055 | 62.4298 | 122.7814 | 62.2879 | 60.2097
8164.1562 | 0.076294 | 0.41443 | -0.784 | -0.20828 | 0.14954 | -0.25528 | -0.1709 | 60.3287 | -62.1597 | 0.082397 | -62.4115 | 60.1593 | 62.3016 | 62.2421 | 0.061035 | -0.063019 | 0.082245 | 0.29373 | -0.15701 | -0.16129 | 0.068665 | 0.091553 | -62.5763 | 60.1135 | 60.1227 | 62.2192 | 62.3932 | 122.8134 | 62.2742 | 60.2005
8165.875 | 0.061035 | 0.4155 | -0.77438 | -0.23071 | 0.13351 | -0.27451 | -0.16342 | 60.4111 | -62.0865 | 0.10529 | -62.3291 | 60.1456 | 62.2467 | 62.1643 | 0.091553 | -0.077972 | 0.080109 | 0.27878 | -0.15274 | -0.15167 | 0.1236 | 0.17395 | -62.4619 | 60.1181 | 60.1089 | 62.1414 | 62.3428 | 122.7676 | 62.2513 | 60.2737
8167.6562 | 0.076294 | 0.43045 | -0.77011 | -0.1976 | 0.14954 | -0.2446 | -0.16129 | 60.2921 | -62.2467 | 0.013733 | -62.4252 | 60.1776 | 62.3016 | 62.2238 | 0.076294 | -0.05661 | 0.072632 | 0.30228 | -0.14526 | -0.14954 | 0.004578 | 0.032043 | -62.6358 | 60.1639 | 60.1501 | 62.2147 | 62.3932 | 122.7631 | 62.2971 | 60.2051
8169.375 | 0.061035 | 0.43045 | -0.78934 | -0.22644 | 0.14633 | -0.28305 | -0.16663 | 60.4019 | -62.0819 | 0.10986 | -62.3383 | 60.141 | 62.2192 | 62.146 | 0.061035 | -0.082245 | 0.069427 | 0.28519 | -0.1741 | -0.15808 | 0.11902 | 0.15106 | -62.4573 | 60.1227 | 60.1456 | 62.1277 | 62.3245 | 122.6898 | 62.2787 | 60.2829
8171.1406 | 0.045776 | 0.41336 | -0.78186 | -0.2211 | 0.13779 | -0.24887 | -0.18051 | 60.2966 | -62.2284 | 0.036621 | -62.4207 | 60.1913 | 62.2833 | 62.2055 | 0.076294 | -0.065155 | 0.079041 | 0.30441 | -0.15701 | -0.16235 | -0.004578 | 0 | -62.5992 | 60.1639 | 60.1593 | 62.2101 | 62.3932 | 122.7493 | 62.3108 | 60.2097
8172.9219 | 0.061035 | 0.43472 | -0.77331 | -0.20294 | 0.13779 | -0.24994 | -0.17624 | 60.2921 | -62.2604 | -0.022888 | -62.4344 | 60.2051 | 62.2787 | 62.2055 | 0.076294 | -0.05661 | 0.082245 | 0.29907 | -0.15274 | -0.16449 | 0.027466 | 0.045776 | -62.6221 | 60.1547 | 60.1547 | 62.2238 | 62.4161 | 122.7905 | 62.2833 | 60.2097
8174.7031 | 0.061035 | 0.42511 | -0.7872 | -0.21469 | 0.14954 | -0.28412 | -0.18265 | 60.4111 | -62.0682 | 0.16479 | -62.3154 | 60.173 | 62.2375 | 62.1414 | 0.061035 | -0.075836 | 0.074768 | 0.2948 | -0.16556 | -0.15701 | 0.073242 | 0.1236 | -62.4619 | 60.1364 | 60.1364 | 62.1277 | 62.3566 | 122.6807 | 62.2925 | 60.2692
8176.4219 | 0.076294 | 0.43152 | -0.78827 | -0.20081 | 0.14954 | -0.25635 | -0.17303 | 60.3012 | -62.2421 | -0.027466 | -62.4298 | 60.1685 | 62.3016 | 62.2284 | 0.061035 | -0.058746 | 0.074768 | 0.29053 | -0.14526 | -0.15595 | 0.027466 | 0.054932 | -62.6221 | 60.1639 | 60.1318 | 62.2009 | 62.4115 | 122.7997 | 62.265 | 60.2188
8178.1875 | 0.030518 | 0.45822 | -0.78079 | -0.22217 | 0.16129 | -0.28946 | -0.17838 | 60.3607 | -62.1231 | 0.064087 | -62.3337 | 60.1776 | 62.2192 | 62.146 | 0.076294 | -0.083313 | 0.067291 | 0.28732 | -0.17731 | -0.15595 | 0.045776 | 0.10071 | -62.4756 | 60.1547 | 60.1501 | 62.1277 | 62.352 | 122.7081 | 62.2696 | 60.2875
8179.9688 | 0.091553 | 0.42404 | -0.77331 | -0.21042 | 0.14954 | -0.24994 | -0.18051 | 60.3058 | -62.2055 | 0.045776 | -62.4252 | 60.1685 | 62.2971 | 62.2375 | 0.061035 | -0.05661 | 0.077972 | 0.28732 | -0.15167 | -0.16235 | 0.004578 | 0.036621 | -62.59 | 60.1639 | 60.1273 | 62.2055 | 62.3886 | 122.7814 | 62.2925 | 60.1959
8181.6875 | 0.061035 | 0.44113 | -0.78507 | -0.22217 | 0.13351 | -0.28305 | -0.17944 | 60.3973 | -62.0865 | 0.10986 | -62.3199 | 60.1593 | 62.2238 | 62.1368 | 0.076294 | -0.087585 | 0.072632 | 0.29266 | -0.18158 | -0.15808 | 0.073242 | 0.12817 | -62.4298 | 60.1181 | 60.1547 | 62.146 | 62.352 | 122.7264 | 62.265 | 60.2692
8183.4531 | 0.045776 | 0.44861 | -0.78613 | -0.20615 | 0.13031 | -0.27237 | -0.18692 | 60.3745 | -62.0911 | 0.091553 | -62.3383 | 60.173 | 62.2147 | 62.1414 | 0.045776 | -0.0737 | 0.066223 | 0.29053 | -0.15701 | -0.16342 | 0.07782 | 0.09613 | -62.4893 | 60.1547 | 60.1456 | 62.1506 | 62.3474 | 122.6761 | 62.2833 | 60.2829
8185.2188 | 0.061035 | 0.43579 | -0.77972 | -0.19546 | 0.1474 | -0.2478 | -0.18265 | 60.4111 | -62.0865 | 0.091553 | -62.3154 | 60.1318 | 62.2559 | 62.1689 | 0.076294 | -0.070496 | 0.063019 | 0.29053 | -0.1442 | -0.15381 | 0.13275 | 0.17395 | -62.4802 | 60.1227 | 60.0952 | 62.1826 | 62.3566 | 122.7951 | 62.2559 | 60.2325
8187 | 0.061035 | 0.43045 | -0.78079 | -0.22751 | 0.13992 | -0.26276 | -0.17944 | 60.4065 | -62.1002 | 0.082397 | -62.3337 | 60.1822 | 62.2101 | 62.1323 | 0.061035 | -0.0737 | 0.083313 | 0.28091 | -0.16235 | -0.15701 | 0.091553 | 0.12817 | -62.4802 | 60.1456 | 60.1273 | 62.1277 | 62.3383 | 122.6715 | 62.2879 | 60.2692
8188.7812 | 0.045776 | 0.41977 | -0.784 | -0.20935 | 0.1474 | -0.23178 | -0.17838 | 60.3561 | -62.1918 | 0.059509 | -62.4023 | 60.1501 | 62.2925 | 62.2284 | 0.045776 | -0.043793 | 0.082245 | 0.28732 | -0.14099 | -0.16983 | 0.07782 | 0.10986 | -62.5809 | 60.1227 | 60.1044 | 62.2055 | 62.3932 | 122.7676 | 62.2833 | 60.1959
8190.5625 | 0.061035 | 0.43366 | -0.77225 | -0.21255 | 0.14954 | -0.25314 | -0.17197 | 60.3378 | -62.178 | 0.041199 | -62.3886 | 60.1685 | 62.2421 | 62.2238 | 0.061035 | -0.065155 | 0.074768 | 0.30014 | -0.16022 | -0.16022 | 0.10986 | 0.13733 | -62.5168 | 60.1501 | 60.141 | 62.1597 | 62.3474 | 122.818 | 62.2559 | 60.2234
8192.2812 | 0.076294 | 0.43579 | -0.77866 | -0.21362 | 0.15915 | -0.25314 | -0.17838 | 60.3333 | -62.2055 | 0.027466 | -62.3978 | 60.1547 | 62.2513 | 62.1918 | 0.061035 | -0.052338 | 0.069427 | 0.2948 | -0.15595 | -0.14954 | 0.07782 | 0.10986 | -62.5305 | 60.1318 | 60.1227 | 62.1597 | 62.3566 | 122.8363 | 62.2559 | 60.2371
8194.0781 | 0.061035 | 0.41763 | -0.76584 | -0.23605 | 0.14633 | -0.26489 | -0.1709 | 60.2966 | -62.1872 | 0.045776 | -62.3978 | 60.1639 | 62.2925 | 62.2192 | 0.076294 | -0.048065 | 0.084381 | 0.28946 | -0.16663 | -0.15701 | 0.022888 | 0.064087 | -62.5854 | 60.1227 | 60.1456 | 62.1918 | 62.4069 | 122.7951 | 62.2696 | 60.1822
8195.7969 | 0.045776 | 0.42831 | -0.77545 | -0.2243 | 0.14954 | -0.2948 | -0.17517 | 60.379 | -62.1048 | 0.10529 | -62.3245 | 60.173 | 62.2101 | 62.146 | 0.030518 | -0.084381 | 0.071564 | 0.27664 | -0.17517 | -0.14847 | 0.091553 | 0.13733 | -62.4344 | 60.141 | 60.1639 | 62.146 | 62.3199 | 122.7219 | 62.2696 | 60.2554
8197.5781 | 0.061035 | 0.42084 | -0.79575 | -0.22217 | 0.15167 | -0.25848 | -0.17731 | 60.379 | -62.0911 | 0.13733 | -62.3383 | 60.1318 | 62.2375 | 62.1872 | 0.045776 | -0.086517 | 0.075836 | 0.28625 | -0.16449 | -0.15595 | 0.041199 | 0.086975 | -62.4893 | 60.1135 | 60.1364 | 62.1964 | 62.3566 | 122.6578 | 62.2971 | 60.2783
8199.2812 | 0.061035 | 0.44327 | -0.78827 | -0.21576 | 0.15274 | -0.28198 | -0.18051 | 60.4111 | -62.0407 | 0.14191 | -62.3062 | 60.1776 | 62.1964 | 62.1597 | 0.045776 | -0.072632 | 0.065155 | 0.28732 | -0.1709 | -0.15915 | 0.11444 | 0.14648 | -62.4161 | 60.1044 | 60.1364 | 62.1231 | 62.3154 | 122.731 | 62.265 | 60.2417
8201.0625 | 0.061035 | 0.4155 | -0.76584 | -0.21469 | 0.14954 | -0.24139 | -0.17197 | 60.3241 | -62.1689 | 0.073242 | -62.3795 | 60.1501 | 62.2879 | 62.233 | 0.061035 | -0.05661 | 0.081177 | 0.28839 | -0.14847 | -0.1506 | 0.068665 | 0.068665 | -62.5626 | 60.1318 | 60.0952 | 62.1964 | 62.4207 | 122.8088 | 62.2787 | 60.1959
8202.8281 | 0.061035 | 0.4187 | -0.78293 | -0.21896 | 0.1474 | -0.27237 | -0.17624 | 60.3378 | -62.1368 | 0.082397 | -62.3703 | 60.1685 | 62.2742 | 62.1918 | 0.061035 | -0.067291 | 0.061951 | 0.29159 | -0.15167 | -0.16022 | 0.009155 | 0.022888 | -62.5626 | 60.1593 | 60.141 | 62.1826 | 62.3703 | 122.6669 | 62.2879 | 60.2646
8204.6094 | 0.076294 | 0.43045 | -0.77866 | -0.20401 | 0.15381 | -0.24567 | -0.16556 | 60.3333 | -62.178 | 0.064087 | -62.3749 | 60.1501 | 62.2971 | 62.2284 | 0.076294 | -0.046997 | 0.068359 | 0.29587 | -0.13458 | -0.15167 | 0.073242 | 0.082397 | -62.5717 | 60.1318 | 60.1181 | 62.2101 | 62.4207 | 122.8043 | 62.265 | 60.1913
8206.3125 | 0.076294 | 0.4155 | -0.78079 | -0.21896 | 0.14526 | -0.25742 | -0.17303 | 60.3058 | -62.1689 | 0.07782 | -62.3749 | 60.1547 | 62.2696 | 62.2421 | 0.061035 | -0.066223 | 0.080109 | 0.29159 | -0.1506 | -0.15274 | 0.036621 | 0.07782 | -62.5626 | 60.1227 | 60.1044 | 62.1918 | 62.3795 | 122.7951 | 62.2604 | 60.1776
8208.0781 | 0.045776 | 0.40802 | -0.77438 | -0.24246 | 0.1474 | -0.24994 | -0.1741 | 60.3012 | -62.1689 | 0.091553 | -62.3886 | 60.1593 | 62.3016 | 62.2284 | 0.045776 | -0.067291 | 0.095062 | 0.298 | -0.16342 | -0.16129 | 0.059509 | 0.091553 | -62.5488 | 60.0998 | 60.1044 | 62.1872 | 62.3932 | 122.7859 | 62.2879 | 60.2005
8209.8594 | 0.076294 | 0.43793 | -0.78934 | -0.22537 | 0.1474 | -0.29587 | -0.17838 | 60.3882 | -62.0132 | 0.15106 | -62.3016 | 60.1501 | 62.2009 | 62.1277 | 0.061035 | -0.09079 | 0.072632 | 0.28091 | -0.17303 | -0.15274 | 0.09613 | 0.16022 | -62.3932 | 60.1318 | 60.1181 | 62.1414 | 62.3428 | 122.7127 | 62.2742 | 60.2509
8211.625 | 0.061035 | 0.41763 | -0.77652 | -0.22217 | 0.13672 | -0.26596 | -0.17731 | 60.2783 | -62.1689 | 0.050354 | -62.3932 | 60.1639 | 62.2833 | 62.178 | 0.061035 | -0.068359 | 0.079041 | 0.28625 | -0.15701 | -0.15488 | -0.013733 | 0.013733 | -62.5671 | 60.1501 | 60.1547 | 62.2055 | 62.3703 | 122.6715 | 62.3016 | 60.2554
8213.3281 | 0.045776 | 0.41763 | -0.78507 | -0.2243 | 0.14954 | -0.25101 | -0.17303 | 60.3058 | -62.178 | 0.064087 | -62.3932 | 60.1501 | 62.3108 | 62.2101 | 0.076294 | -0.058746 | 0.072632 | 0.29159 | -0.15915 | -0.16022 | 0.036621 | 0.082397 | -62.5534 | 60.1181 | 60.1318 | 62.2192 | 62.3795 | 122.7905 | 62.2696 | 60.1639
8215.1094 | 0.061035 | 0.42511 | -0.77972 | -0.22324 | 0.14954 | -0.26703 | -0.18051 | 60.2921 | -62.2009 | 0.022888 | -62.4115 | 60.1822 | 62.2742 | 62.2192 | 0.045776 | -0.059814 | 0.069427 | 0.28839 | -0.15701 | -0.15488 | 0 | 0.018311 | -62.5809 | 60.1639 | 60.1639 | 62.2009 | 62.384 | 122.7127 | 62.2787 | 60.2188
8216.9062 | 0.076294 | 0.43366 | -0.76904 | -0.23178 | 0.1506 | -0.28519 | -0.17517 | 60.379 | -62.0636 | 0.15564 | -62.3154 | 60.1593 | 62.2192 | 62.1506 | 0.061035 | -0.087585 | 0.091858 | 0.28839 | -0.16983 | -0.14313 | 0.073242 | 0.13733 | -62.4481 | 60.0998 | 60.1044 | 62.1552 | 62.3611 | 122.6532 | 62.2833 | 60.2692
8218.6875 | 0.061035 | 0.44861 | -0.7872 | -0.20508 | 0.14099 | -0.26276 | -0.16876 | 60.3516 | -62.1002 | 0.086975 | -62.3154 | 60.1456 | 62.2284 | 62.1643 | 0.091553 | -0.0737 | 0.068359 | 0.29053 | -0.1474 | -0.16022 | 0.1236 | 0.16937 | -62.4527 | 60.0952 | 60.0952 | 62.1506 | 62.3337 | 122.7905 | 62.2513 | 60.2325
8220.4688 | 0.045776 | 0.43579 | -0.76797 | -0.19333 | 0.14099 | -0.26062 | -0.17731 | 60.2692 | -62.2284 | -0.018311 | -62.4207 | 60.1776 | 62.265 | 62.2238 | 0.061035 | -0.058746 | 0.083313 | 0.28732 | -0.1474 | -0.14954 | 0.045776 | 0.050354 | -62.59 | 60.141 | 60.1273 | 62.1643 | 62.4069 | 122.7905 | 62.2559 | 60.2188
8222.25 | 0.045776 | 0.43793 | -0.77972 | -0.19867 | 0.12711 | -0.26916 | -0.16983 | 60.379 | -62.0682 | 0.091553 | -62.3245 | 60.1501 | 62.233 | 62.1506 | 0.061035 | -0.081177 | 0.067291 | 0.27985 | -0.14847 | -0.1474 | 0.11902 | 0.16937 | -62.4527 | 60.1089 | 60.0723 | 62.1506 | 62.3383 | 122.7814 | 62.2284 | 60.228
8223.9688 | 0.045776 | 0.43152 | -0.78613 | -0.22751 | 0.14633 | -0.29587 | -0.18265 | 60.347 | -62.1002 | 0.091553 | -62.3245 | 60.1776 | 62.2284 | 62.146 | 0.061035 | -0.083313 | 0.080109 | 0.27557 | -0.17731 | -0.15274 | 0.073242 | 0.10986 | -62.439 | 60.1318 | 60.1501 | 62.1277 | 62.3337 | 122.7173 | 62.265 | 60.2554
8225.75 | 0.076294 | 0.43472 | -0.77972 | -0.20081 | 0.15167 | -0.25101 | -0.1709 | 60.2966 | -62.2009 | -0.009155 | -62.3932 | 60.1868 | 62.2787 | 62.2147 | 0.061035 | -0.059814 | 0.081177 | 0.28519 | -0.15274 | -0.15488 | 0.045776 | 0.064087 | -62.5717 | 60.1456 | 60.1135 | 62.1964 | 62.3795 | 122.7814 | 62.2513 | 60.228
8227.5312 | 0.076294 | 0.42831 | -0.784 | -0.23285 | 0.13565 | -0.27664 | -0.16983 | 60.3973 | -62.027 | 0.17853 | -62.3016 | 60.1318 | 62.2009 | 62.1689 | 0.076294 | -0.080109 | 0.069427 | 0.27771 | -0.16342 | -0.15488 | 0.07782 | 0.14648 | -62.4527 | 60.0952 | 60.1044 | 62.146 | 62.3474 | 122.6532 | 62.2604 | 60.26
8229.2344 | 0.061035 | 0.42938 | -0.79681 | -0.21576 | 0.13992 | -0.26703 | -0.16876 | 60.4019 | -62.059 | 0.10071 | -62.3016 | 60.1501 | 62.2467 | 62.1597 | 0.076294 | -0.077972 | 0.069427 | 0.28839 | -0.14954 | -0.16556 | 0.12817 | 0.17395 | -62.4619 | 60.0952 | 60.1044 | 62.1277 | 62.352 | 122.7585 | 62.233 | 60.228
8231.0156 | 0.061035 | 0.41122 | -0.77118 | -0.21469 | 0.13886 | -0.24033 | -0.16769 | 60.3195 | -62.1414 | 0.082397 | -62.3795 | 60.1639 | 62.2787 | 62.2192 | 0.091553 | -0.064087 | 0.081177 | 0.28946 | -0.1474 | -0.1709 | 0.054932 | 0.073242 | -62.558 | 60.1135 | 60.1089 | 62.1918 | 62.3978 | 122.7676 | 62.2513 | 60.1822
8232.7969 | 0.061035 | 0.42618 | -0.77331 | -0.20935 | 0.1506 | -0.24887 | -0.16769 | 60.3287 | -62.1552 | 0.073242 | -62.3886 | 60.1273 | 62.2833 | 62.2055 | 0.061035 | -0.061951 | 0.0737 | 0.28946 | -0.1506 | -0.16449 | 0.050354 | 0.082397 | -62.5854 | 60.1227 | 60.1181 | 62.2101 | 62.3886 | 122.7356 | 62.2742 | 60.1913
8234.5781 | 0.061035 | 0.45075 | -0.77438 | -0.23285 | 0.14847 | -0.28412 | -0.19012 | 60.3424 | -62.0819 | 0.07782 | -62.3291 | 60.1776 | 62.233 | 62.1231 | 0.045776 | -0.085449 | 0.067291 | 0.28839 | -0.16235 | -0.14954 | 0.054932 | 0.10071 | -62.4802 | 60.1044 | 60.1456 | 62.1231 | 62.3199 | 122.6395 | 62.2787 | 60.26
8236.3594 | 0.045776 | 0.43152 | -0.78934 | -0.22751 | 0.14526 | -0.27344 | -0.1709 | 60.3745 | -62.0453 | 0.16479 | -62.3108 | 60.1181 | 62.2238 | 62.1414 | 0.061035 | -0.071564 | 0.064087 | 0.28625 | -0.15808 | -0.16556 | 0.059509 | 0.11902 | -62.4527 | 60.1089 | 60.1044 | 62.1506 | 62.3245 | 122.644 | 62.2696 | 60.2325
8238.0625 | 0.061035 | 0.40268 | -0.77331 | -0.22537 | 0.14313 | -0.23819 | -0.16769 | 60.2692 | -62.233 | 0.018311 | -62.4115 | 60.1593 | 62.2925 | 62.1918 | 0.061035 | -0.060883 | 0.084381 | 0.29694 | -0.14633 | -0.15701 | 0.009155 | 0.032043 | -62.6266 | 60.1501 | 60.0998 | 62.2101 | 62.3932 | 122.7402 | 62.2742 | 60.228
8239.8438 | 0.061035 | 0.42831 | -0.77866 | -0.20508 | 0.15381 | -0.25421 | -0.16556 | 60.3104 | -62.1323 | 0.091553 | -62.3749 | 60.141 | 62.2879 | 62.2192 | 0.045776 | -0.058746 | 0.076904 | 0.298 | -0.13779 | -0.16129 | 0.07782 | 0.10071 | -62.5626 | 60.0998 | 60.0815 | 62.1964 | 62.4069 | 122.7631 | 62.2742 | 60.1639
8241.6406 | 0.061035 | 0.43045 | -0.79041 | -0.22537 | 0.14099 | -0.29373 | -0.18051 | 60.347 | -62.0773 | 0.11444 | -62.3062 | 60.1364 | 62.2055 | 62.1368 | 0.076294 | -0.076904 | 0.0737 | 0.28091 | -0.1709 | -0.15381 | 0.068665 | 0.1236 | -62.4161 | 60.1227 | 60.1318 | 62.0956 | 62.3154 | 122.7036 | 62.2421 | 60.2646
8243.3438 | 0.076294 | 0.45395 | -0.77438 | -0.19867 | 0.13779 | -0.27344 | -0.16983 | 60.3836 | -62.0453 | 0.10529 | -62.3108 | 60.1318 | 62.2101 | 62.1414 | 0.061035 | -0.068359 | 0.060883 | 0.28305 | -0.15274 | -0.16449 | 0.12817 | 0.16479 | -62.4527 | 60.0815 | 60.0952 | 62.1414 | 62.3337 | 122.7081 | 62.2375 | 60.26
8245.1094 | 0.061035 | 0.44434 | -0.79361 | -0.20615 | 0.14206 | -0.26703 | -0.17838 | 60.3745 | -62.0544 | 0.10986 | -62.3108 | 60.1181 | 62.2101 | 62.1414 | 0.076294 | -0.067291 | 0.065155 | 0.29053 | -0.1442 | -0.16129 | 0.11444 | 0.16479 | -62.4435 | 60.1044 | 60.1089 | 62.146 | 62.3199 | 122.6852 | 62.2421 | 60.2509
8246.8906 | 0.076294 | 0.42831 | -0.78934 | -0.21042 | 0.14099 | -0.24674 | -0.16876 | 60.2966 | -62.2284 | -0.022888 | -62.4069 | 60.1822 | 62.265 | 62.2238 | 0.061035 | -0.064087 | 0.069427 | 0.29053 | -0.14633 | -0.1442 | 0.032043 | 0.054932 | -62.5946 | 60.1547 | 60.1227 | 62.1964 | 62.3932 | 122.7585 | 62.2467 | 60.2234
8248.6719 | 0.030518 | 0.42191 | -0.77652 | -0.23712 | 0.15915 | -0.26703 | -0.17517 | 60.3653 | -62.0819 | 0.12817 | -62.3108 | 60.1456 | 62.2375 | 62.1735 | 0.061035 | -0.074768 | 0.081177 | 0.28305 | -0.1709 | -0.15808 | 0.018311 | 0.068665 | -62.4939 | 60.1456 | 60.141 | 62.1552 | 62.3657 | 122.6212 | 62.2604 | 60.2692
8250.4531 | 0.076294 | 0.43579 | -0.77866 | -0.20508 | 0.13565 | -0.24353 | -0.17624 | 60.2921 | -62.1964 | 0.004578 | -62.3886 | 60.1776 | 62.2604 | 62.2009 | 0.061035 | -0.068359 | 0.080109 | 0.28412 | -0.14526 | -0.1474 | 0.068665 | 0.073242 | -62.558 | 60.141 | 60.1135 | 62.1735 | 62.3566 | 122.7905 | 62.2467 | 60.1959
8252.1562 | 0.091553 | 0.43579 | -0.77225 | -0.21469 | 0.1474 | -0.24994 | -0.17517 | 60.2829 | -62.2192 | -0.013733 | -62.4115 | 60.1822 | 62.2742 | 62.2192 | 0.061035 | -0.057678 | 0.079041 | 0.29266 | -0.15274 | -0.16342 | 0.041199 | 0.059509 | -62.5763 | 60.1364 | 60.1318 | 62.1643 | 62.4023 | 122.7722 | 62.2559 | 60.2097
8253.9219 | 0.061035 | 0.44327 | -0.77972 | -0.21469 | 0.13992 | -0.26489 | -0.16769 | 60.3561 | -62.0682 | 0.086975 | -62.3199 | 60.1501 | 62.2147 | 62.146 | 0.076294 | -0.075836 | 0.069427 | 0.29159 | -0.16129 | -0.16235 | 0.13733 | 0.16937 | -62.4481 | 60.1089 | 60.0769 | 62.1277 | 62.3108 | 122.7722 | 62.2421 | 60.2325
8255.7031 | 0.045776 | 0.42725 | -0.78507 | -0.22751 | 0.14313 | -0.28305 | -0.17624 | 60.3561 | -62.1002 | 0.064087 | -62.3199 | 60.1547 | 62.1826 | 62.1231 | 0.061035 | -0.081177 | 0.076904 | 0.29053 | -0.16449 | -0.16342 | 0.041199 | 0.091553 | -62.4756 | 60.1547 | 60.1501 | 62.114 | 62.2925 | 122.6669 | 62.2467 | 60.2737
8257.4219 | 0.045776 | 0.44006 | -0.78293 | -0.2211 | 0.15701 | -0.26916 | -0.18478 | 60.3699 | -62.0407 | 0.14648 | -62.3016 | 60.1501 | 62.2192 | 62.1506 | 0.061035 | -0.083313 | 0.074768 | 0.28305 | -0.15274 | -0.15701 | 0.064087 | 0.10529 | -62.4573 | 60.1273 | 60.0906 | 62.1552 | 62.3383 | 122.6166 | 62.2833 | 60.2509
8259.2031 | 0.061035 | 0.42725 | -0.77866 | -0.21149 | 0.14526 | -0.2478 | -0.16663 | 60.3012 | -62.1735 | 0.004578 | -62.3657 | 60.1639 | 62.2604 | 62.1552 | 0.076294 | -0.070496 | 0.058746 | 0.27878 | -0.14099 | -0.16129 | 0.086975 | 0.11902 | -62.5076 | 60.1227 | 60.0952 | 62.1597 | 62.3474 | 122.7814 | 62.2513 | 60.2005
8260.9844 | 0.076294 | 0.41122 | -0.77652 | -0.21255 | 0.15595 | -0.25207 | -0.17303 | 60.26 | -62.1735 | 0.045776 | -62.3795 | 60.1822 | 62.2604 | 62.2055 | 0.061035 | -0.060883 | 0.082245 | 0.29694 | -0.16129 | -0.14954 | -0.004578 | 0.027466 | -62.5763 | 60.1273 | 60.0815 | 62.2192 | 62.3886 | 122.7585 | 62.2513 | 60.1959
8262.7031 | 0.076294 | 0.41977 | -0.77972 | -0.2179 | 0.14313 | -0.25207 | -0.16876 | 60.2646 | -62.2284 | -0.018311 | -62.4069 | 60.1593 | 62.2467 | 62.1918 | 0.061035 | -0.072632 | 0.076904 | 0.30121 | -0.1506 | -0.15701 | 0.041199 | 0.054932 | -62.5992 | 60.1181 | 60.1227 | 62.2192 | 62.3886 | 122.7493 | 62.2467 | 60.1959
8264.5 | 0.045776 | 0.41657 | -0.77331 | -0.21042 | 0.14099 | -0.25207 | -0.16983 | 60.3058 | -62.1368 | 0.064087 | -62.3657 | 60.1364 | 62.2833 | 62.2238 | 0.076294 | -0.05661 | 0.070496 | 0.29373 | -0.1442 | -0.16129 | 0.059509 | 0.09613 | -62.5626 | 60.0815 | 60.0815 | 62.2101 | 62.4115 | 122.7493 | 62.2513 | 60.1868
8266.2812 | 0.045776 | 0.43579 | -0.77866 | -0.21576 | 0.14206 | -0.27878 | -0.15701 | 60.347 | -62.0407 | 0.09613 | -62.3154 | 60.1273 | 62.1964 | 62.1323 | 0.045776 | -0.0737 | 0.076904 | 0.28412 | -0.17303 | -0.1474 | 0.12817 | 0.15106 | -62.439 | 60.1089 | 60.0952 | 62.1094 | 62.3199 | 122.6486 | 62.2742 | 60.2692
8268.0469 | 0.061035 | 0.42938 | -0.77011 | -0.21683 | 0.15488 | -0.23498 | -0.17624 | 60.2646 | -62.2238 | 0.004578 | -62.4023 | 60.1593 | 62.2879 | 62.2238 | 0.10681 | -0.061951 | 0.070496 | 0.29587 | -0.15808 | -0.15274 | 0 | 0.036621 | -62.6312 | 60.1364 | 60.1364 | 62.2055 | 62.3886 | 122.7173 | 62.265 | 60.2188
8269.8281 | 0.061035 | 0.43366 | -0.78079 | -0.20935 | 0.13992 | -0.26596 | -0.17197 | 60.3561 | -62.0819 | 0.064087 | -62.3154 | 60.1364 | 62.2101 | 62.1597 | 0.061035 | -0.076904 | 0.079041 | 0.28839 | -0.14099 | -0.15915 | 0.11902 | 0.17395 | -62.4527 | 60.1135 | 60.1044 | 62.1414 | 62.3062 | 122.7722 | 62.2238 | 60.1959
8271.5469 | 0.061035 | 0.44968 | -0.79041 | -0.21683 | 0.1442 | -0.28946 | -0.19226 | 60.3241 | -62.1002 | 0.050354 | -62.3245 | 60.1685 | 62.2101 | 62.1414 | 0.076294 | -0.083313 | 0.076904 | 0.28519 | -0.16449 | -0.15915 | 0.050354 | 0.10071 | -62.4619 | 60.1227 | 60.1227 | 62.114 | 62.3199 | 122.6349 | 62.2559 | 60.2463
8273.3125 | 0.076294 | 0.439 | -0.78827 | -0.19867 | 0.14313 | -0.25314 | -0.17303 | 60.2829 | -62.1735 | -0.004578 | -62.3795 | 60.1868 | 62.2559 | 62.1826 | 0.061035 | -0.070496 | 0.064087 | 0.28732 | -0.14847 | -0.16129 | 0.073242 | 0.091553 | -62.5259 | 60.1227 | 60.0906 | 62.1506 | 62.3337 | 122.7905 | 62.2421 | 60.1959
8275.0156 | 0.045776 | 0.439 | -0.78613 | -0.2211 | 0.13779 | -0.28519 | -0.17944 | 60.4019 | -61.9995 | 0.17853 | -62.2787 | 60.1318 | 62.2101 | 62.146 | 0.061035 | -0.075836 | 0.061951 | 0.26169 | -0.16129 | -0.16876 | 0.09613 | 0.15106 | -62.4115 | 60.0952 | 60.0998 | 62.1094 | 62.3291 | 122.6669 | 62.2559 | 60.26
8276.8125 | 0.061035 | 0.42938 | -0.77866 | -0.23178 | 0.14206 | -0.28305 | -0.19546 | 60.3928 | -62.0178 | 0.16022 | -62.2925 | 60.1456 | 62.2101 | 62.1506 | 0.076294 | -0.079041 | 0.075836 | 0.28839 | -0.17517 | -0.16235 | 0.082397 | 0.12817 | -62.4252 | 60.0906 | 60.1089 | 62.1368 | 62.3199 | 122.6212 | 62.2787 | 60.2463
8278.5938 | 0.061035 | 0.439 | -0.79361 | -0.20828 | 0.1474 | -0.2681 | -0.17624 | 60.2692 | -62.1964 | 0.032043 | -62.3886 | 60.173 | 62.2696 | 62.1918 | 0.076294 | -0.068359 | 0.080109 | 0.29266 | -0.15381 | -0.16449 | 0 | -0.004578 | -62.5809 | 60.1501 | 60.1181 | 62.1872 | 62.3886 | 122.6852 | 62.2787 | 60.2051
8280.375 | 0.061035 | 0.41977 | -0.77331 | -0.2211 | 0.1506 | -0.24994 | -0.16663 | 60.3241 | -62.1414 | 0.086975 | -62.352 | 60.1593 | 62.2879 | 62.1918 | 0.061035 | -0.05127 | 0.079041 | 0.30441 | -0.15701 | -0.16663 | 0.054932 | 0.091553 | -62.558 | 60.0998 | 60.1044 | 62.1872 | 62.3932 | 122.7585 | 62.233 | 60.1685
8282.0938 | 0.061035 | 0.42831 | -0.78827 | -0.2243 | 0.13779 | -0.28198 | -0.17303 | 60.3928 | -61.9766 | 0.16937 | -62.2787 | 60.1547 | 62.2055 | 62.1277 | 0.061035 | -0.083313 | 0.068359 | 0.28839 | -0.16983 | -0.14954 | 0.091553 | 0.16022 | -62.4069 | 60.0861 | 60.1044 | 62.1414 | 62.3199 | 122.6486 | 62.2696 | 60.2692
8283.875 | 0.045776 | 0.42404 | -0.78293 | -0.20721 | 0.1442 | -0.26489 | -0.17197 | 60.3699 | -62.0682 | 0.09613 | -62.2925 | 60.1089 | 62.1964 | 62.1552 | 0.061035 | -0.077972 | 0.061951 | 0.28305 | -0.14526 | -0.16769 | 0.1236 | 0.16479 | -62.4481 | 60.0906 | 60.0677 | 62.1231 | 62.3383 | 122.7493 | 62.2192 | 60.2142
8285.5938 | 0.061035 | 0.42297 | -0.78827 | -0.23178 | 0.14099 | -0.27985 | -0.17517 | 60.3836 | -61.9904 | 0.16479 | -62.2879 | 60.1501 | 62.1964 | 62.1414 | 0.061035 | -0.080109 | 0.065155 | 0.27664 | -0.16449 | -0.15701 | 0.086975 | 0.16022 | -62.4069 | 60.1181 | 60.0632 | 62.146 | 62.3291 | 122.6532 | 62.2375 | 60.2509
8287.375 | 0.061035 | 0.42618 | -0.77652 | -0.23285 | 0.15701 | -0.2681 | -0.18051 | 60.3928 | -61.9904 | 0.16937 | -62.2833 | 60.1501 | 62.2009 | 62.1323 | 0.061035 | -0.077972 | 0.069427 | 0.27237 | -0.15808 | -0.16663 | 0.09613 | 0.15106 | -62.4115 | 60.0998 | 60.0952 | 62.1231 | 62.3474 | 122.6395 | 62.2467 | 60.2371
8289.1719 | 0.076294 | 0.41443 | -0.77438 | -0.22751 | 0.13886 | -0.24887 | -0.18585 | 60.2875 | -62.1872 | 0.032043 | -62.3749 | 60.1776 | 62.265 | 62.1826 | 0.091553 | -0.05127 | 0.074768 | 0.30228 | -0.14847 | -0.16769 | 0 | 0.004578 | -62.5809 | 60.141 | 60.141 | 62.178 | 62.3703 | 122.731 | 62.2467 | 60.1868
8290.8906 | 0.045776 | 0.42725 | -0.78293 | -0.21683 | 0.15701 | -0.28091 | -0.17197 | 60.3973 | -61.9995 | 0.15564 | -62.2742 | 60.1364 | 62.2009 | 62.1231 | 0.061035 | -0.084381 | 0.070496 | 0.28732 | -0.16235 | -0.1709 | 0.086975 | 0.16022 | -62.3886 | 60.1181 | 60.0998 | 62.114 | 62.2971 | 122.6578 | 62.2604 | 60.2509
8292.6875 | 0.061035 | 0.42618 | -0.78507 | -0.1976 | 0.14526 | -0.23926 | -0.16876 | 60.2737 | -62.2147 | -0.018311 | -62.4023 | 60.1776 | 62.265 | 62.1918 | 0.061035 | -0.059814 | 0.070496 | 0.30228 | -0.1442 | -0.16235 | 0.050354 | 0.045776 | -62.5854 | 60.1273 | 60.1089 | 62.1872 | 62.3749 | 122.7631 | 62.2467 | 60.2005
8294.4062 | 0.076294 | 0.43686 | -0.79468 | -0.23178 | 0.14099 | -0.27985 | -0.1709 | 60.3287 | -62.0682 | 0.07782 | -62.3062 | 60.1639 | 62.2147 | 62.1552 | 0.061035 | -0.084381 | 0.081177 | 0.28412 | -0.17197 | -0.16129 | 0.068665 | 0.11902 | -62.4435 | 60.1227 | 60.1135 | 62.1002 | 62.3199 | 122.6715 | 62.2375 | 60.26
8296.1875 | 0.045776 | 0.43366 | -0.77866 | -0.21576 | 0.13886 | -0.27023 | -0.18158 | 60.4111 | -61.9766 | 0.16022 | -62.265 | 60.1364 | 62.2192 | 62.1414 | 0.061035 | -0.065155 | 0.067291 | 0.29053 | -0.16663 | -0.16342 | 0.073242 | 0.15106 | -62.4161 | 60.1181 | 60.1089 | 62.1185 | 62.3199 | 122.6486 | 62.2421 | 60.2188
8297.9531 | 0.076294 | 0.4155 | -0.78079 | -0.23071 | 0.15274 | -0.24139 | -0.17944 | 60.2783 | -62.1826 | 0.041199 | -62.3749 | 60.1685 | 62.2833 | 62.1964 | 0.061035 | -0.057678 | 0.074768 | 0.29159 | -0.16449 | -0.16556 | 0.009155 | 0.054932 | -62.5671 | 60.1318 | 60.1044 | 62.2101 | 62.3978 | 122.7768 | 62.233 | 60.1593
8299.6719 | 0.076294 | 0.44006 | -0.77759 | -0.22217 | 0.15274 | -0.27237 | -0.17303 | 60.3333 | -62.059 | 0.064087 | -62.3108 | 60.1639 | 62.2055 | 62.1048 | 0.061035 | -0.079041 | 0.074768 | 0.29587 | -0.16663 | -0.15808 | 0.068665 | 0.091553 | -62.4573 | 60.1273 | 60.1044 | 62.1094 | 62.3291 | 122.6257 | 62.2284 | 60.2554
8301.4531 | 0.030518 | 0.43579 | -0.77225 | -0.20081 | 0.15381 | -0.26062 | -0.18158 | 60.3973 | -62.027 | 0.10986 | -62.3062 | 60.1318 | 62.2055 | 62.1277 | 0.045776 | -0.0737 | 0.068359 | 0.29587 | -0.15167 | -0.16556 | 0.12817 | 0.16022 | -62.4252 | 60.1089 | 60.0952 | 62.1231 | 62.3428 | 122.6532 | 62.2513 | 60.2646
8303.2344 | 0.045776 | 0.43045 | -0.78934 | -0.19653 | 0.14313 | -0.2478 | -0.16983 | 60.3378 | -62.1185 | 0.041199 | -62.3474 | 60.1547 | 62.2192 | 62.178 | 0.076294 | -0.069427 | 0.061951 | 0.29053 | -0.12817 | -0.15488 | 0.12817 | 0.16022 | -62.4664 | 60.1227 | 60.0632 | 62.1597 | 62.3199 | 122.7631 | 62.233 | 60.2234
8305.0156 | 0.061035 | 0.42725 | -0.77652 | -0.21362 | 0.12711 | -0.24139 | -0.18051 | 60.3104 | -62.1552 | 0.068665 | -62.3566 | 60.1181 | 62.2787 | 62.2192 | 0.076294 | -0.054474 | 0.070496 | 0.298 | -0.1474 | -0.16983 | 0.073242 | 0.10071 | -62.5534 | 60.0952 | 60.0632 | 62.1872 | 62.4298 | 122.7493 | 62.2421 | 60.1685
8306.7969 | 0.030518 | 0.44861 | -0.78827 | -0.21576 | 0.13779 | -0.29053 | -0.1741 | 60.3195 | -62.0773 | 0.059509 | -62.3154 | 60.1776 | 62.2009 | 62.1323 | 0.076294 | -0.089722 | 0.065155 | 0.27451 | -0.16449 | -0.14206 | 0.041199 | 0.10071 | -62.4435 | 60.141 | 60.1318 | 62.1185 | 62.2879 | 122.6578 | 62.2421 | 60.2966
8308.5 | 0.045776 | 0.39307 | -0.77438 | -0.2211 | 0.14099 | -0.23819 | -0.16556 | 60.2371 | -62.2192 | 0 | -62.4115 | 60.1639 | 62.2696 | 62.2284 | 0.091553 | -0.061951 | 0.087585 | 0.29587 | -0.14633 | -0.17303 | 0.032043 | 0.041199 | -62.6038 | 60.1501 | 60.0998 | 62.2055 | 62.3749 | 122.7448 | 62.2467 | 60.1868
8310.2812 | 0.045776 | 0.43045 | -0.78079 | -0.23178 | 0.14633 | -0.27878 | -0.16769 | 60.3195 | -62.0728 | 0.10071 | -62.3291 | 60.1501 | 62.2421 | 62.178 | 0.076294 | -0.080109 | 0.083313 | 0.29159 | -0.16022 | -0.15488 | 0.018311 | 0.050354 | -62.5214 | 60.1181 | 60.1044 | 62.1552 | 62.3566 | 122.6212 | 62.2696 | 60.2371
8312.0625 | 0.061035 | 0.40802 | -0.77011 | -0.22751 | 0.14313 | -0.24353 | -0.16983 | 60.26 | -62.1735 | 0.059509 | -62.3611 | 60.1501 | 62.2742 | 62.1826 | 0.076294 | -0.060883 | 0.084381 | 0.28732 | -0.15167 | -0.16556 | 0.009155 | 0.050354 | -62.558 | 60.1227 | 60.0906 | 62.1826 | 62.3886 | 122.7493 | 62.2559 | 60.1822
8313.8438 | 0.091553 | 0.42404 | -0.77972 | -0.20615 | 0.13351 | -0.24994 | -0.16449 | 60.2097 | -62.2101 | -0.013733 | -62.4069 | 60.1593 | 62.265 | 62.2009 | 0.076294 | -0.066223 | 0.066223 | 0.29053 | -0.14099 | -0.1474 | 0 | 0.041199 | -62.59 | 60.1089 | 60.0952 | 62.178 | 62.3611 | 122.7173 | 62.2284 | 60.1959
8315.6094 | 0.076294 | 0.43366 | -0.78293 | -0.2179 | 0.14954 | -0.27557 | -0.16663 | 60.3424 | -62.0316 | 0.10529 | -62.2925 | 60.1273 | 62.2147 | 62.1414 | 0.061035 | -0.085449 | 0.068359 | 0.28946 | -0.14313 | -0.15808 | 0.11902 | 0.17395 | -62.4344 | 60.0632 | 60.054 | 62.1368 | 62.3337 | 122.7127 | 62.233 | 60.2371
8317.3281 | 0.061035 | 0.40909 | -0.77225 | -0.2243 | 0.15274 | -0.24033 | -0.16449 | 60.2966 | -62.1414 | 0.07782 | -62.3795 | 60.1456 | 62.2833 | 62.1872 | 0.045776 | -0.063019 | 0.071564 | 0.29907 | -0.15915 | -0.16235 | 0.059509 | 0.082397 | -62.5488 | 60.1089 | 60.0769 | 62.1918 | 62.3703 | 122.7036 | 62.265 | 60.1868
8319.1094 | 0.030518 | 0.43045 | -0.7872 | -0.23178 | 0.14847 | -0.28091 | -0.17838 | 60.3607 | -61.9904 | 0.15106 | -62.2833 | 60.1364 | 62.2009 | 62.1277 | 0.061035 | -0.083313 | 0.077972 | 0.28839 | -0.16876 | -0.15595 | 0.091553 | 0.15106 | -62.384 | 60.0906 | 60.1181 | 62.1277 | 62.2833 | 122.644 | 62.2559 | 60.2371
8320.8281 | 0.061035 | 0.43152 | -0.77225 | -0.22003 | 0.13565 | -0.28412 | -0.17838 | 60.3561 | -62.0544 | 0.086975 | -62.3108 | 60.1456 | 62.178 | 62.1323 | 0.061035 | -0.082245 | 0.068359 | 0.28839 | -0.15701 | -0.16449 | 0.09613 | 0.13733 | -62.4298 | 60.1227 | 60.1181 | 62.1094 | 62.3016 | 122.612 | 62.233 | 60.26
8322.6094 | 0.061035 | 0.41122 | -0.77331 | -0.20935 | 0.14206 | -0.24246 | -0.16663 | 60.3104 | -62.1368 | 0.086975 | -62.3566 | 60.1364 | 62.2787 | 62.178 | 0.076294 | -0.063019 | 0.077972 | 0.28732 | -0.13886 | -0.16342 | 0.054932 | 0.086975 | -62.5397 | 60.1089 | 60.0677 | 62.1735 | 62.3886 | 122.7493 | 62.2421 | 60.173
8324.375 | 0.076294 | 0.43045 | -0.79895 | -0.21683 | 0.15167 | -0.28412 | -0.17944 | 60.3058 | -62.0728 | 0.059509 | -62.3154 | 60.1593 | 62.1918 | 62.1185 | 0.030518 | -0.074768 | 0.082245 | 0.27451 | -0.1709 | -0.15808 | 0.050354 | 0.091553 | -62.4481 | 60.1364 | 60.1181 | 62.1231 | 62.3016 | 122.644 | 62.2375 | 60.26
8326.0938 | 0.061035 | 0.42725 | -0.77118 | -0.20935 | 0.1474 | -0.25421 | -0.17731 | 60.3745 | -62.0453 | 0.10071 | -62.2879 | 60.1273 | 62.2147 | 62.1323 | 0.061035 | -0.081177 | 0.066223 | 0.28732 | -0.1506 | -0.16129 | 0.12817 | 0.18768 | -62.4344 | 60.0861 | 60.054 | 62.1368 | 62.3199 | 122.7081 | 62.2238 | 60.1959
8327.875 | 0.061035 | 0.43472 | -0.79254 | -0.20401 | 0.14099 | -0.2681 | -0.16876 | 60.3699 | -62.0453 | 0.10986 | -62.2833 | 60.1273 | 62.1964 | 62.1231 | 0.045776 | -0.077972 | 0.061951 | 0.27664 | -0.14633 | -0.16449 | 0.12817 | 0.16937 | -62.4252 | 60.0998 | 60.0723 | 62.1231 | 62.3245 | 122.6761 | 62.2238 | 60.2325
8329.6719 | 0.061035 | 0.42084 | -0.76904 | -0.20721 | 0.13886 | -0.24139 | -0.16342 | 60.2554 | -62.1643 | 0.050354 | -62.384 | 60.1364 | 62.2742 | 62.2101 | 0.045776 | -0.061951 | 0.072632 | 0.29266 | -0.13672 | -0.16235 | 0.032043 | 0.054932 | -62.5671 | 60.1273 | 60.0815 | 62.1918 | 62.3978 | 122.6852 | 62.2284 | 60.2005
8331.4531 | 0.076294 | 0.4155 | -0.78079 | -0.21896 | 0.15595 | -0.24674 | -0.1709 | 60.2509 | -62.178 | 0.041199 | -62.4023 | 60.1181 | 62.2787 | 62.1918 | 0.061035 | -0.079041 | 0.072632 | 0.28946 | -0.1442 | -0.14206 | 0.032043 | 0.064087 | -62.59 | 60.1318 | 60.0998 | 62.2101 | 62.3886 | 122.6944 | 62.2604 | 60.1822
8333.1719 | 0.045776 | 0.42618 | -0.76904 | -0.22858 | 0.13672 | -0.25742 | -0.1741 | 60.2463 | -62.1597 | 0.036621 | -62.3749 | 60.1685 | 62.2513 | 62.1918 | 0.061035 | -0.064087 | 0.082245 | 0.28839 | -0.16449 | -0.15808 | -0.009155 | 0.032043 | -62.5534 | 60.1364 | 60.0998 | 62.1918 | 62.3566 | 122.7539 | 62.2147 | 60.173
8334.9531 | 0.061035 | 0.43579 | -0.79147 | -0.22537 | 0.13458 | -0.28946 | -0.18799 | 60.3516 | -62.0041 | 0.13275 | -62.2696 | 60.1456 | 62.178 | 62.1094 | 0.076294 | -0.083313 | 0.064087 | 0.28091 | -0.17944 | -0.15701 | 0.091553 | 0.14191 | -62.3886 | 60.0952 | 60.0952 | 62.1185 | 62.3016 | 122.6669 | 62.2375 | 60.2188
8336.6719 | 0.045776 | 0.44968 | -0.78293 | -0.2211 | 0.13886 | -0.27664 | -0.19653 | 60.3104 | -62.0636 | 0.064087 | -62.2925 | 60.1547 | 62.1918 | 62.1231 | 0.061035 | -0.093994 | 0.058746 | 0.2713 | -0.15808 | -0.1506 | 0.050354 | 0.086975 | -62.4481 | 60.1227 | 60.1044 | 62.1414 | 62.3383 | 122.6349 | 62.2513 | 60.2417
8338.4375 | 0.076294 | 0.42618 | -0.75836 | -0.21683 | 0.14954 | -0.25101 | -0.17197 | 60.2829 | -62.178 | 0.009155 | -62.3795 | 60.1822 | 62.2513 | 62.2147 | 0.045776 | -0.061951 | 0.070496 | 0.29587 | -0.14633 | -0.15915 | 0.07782 | 0.082397 | -62.5397 | 60.1547 | 60.0952 | 62.1506 | 62.3795 | 122.7493 | 62.2101 | 60.1868
8340.2188 | 0.076294 | 0.41763 | -0.77759 | -0.20615 | 0.14206 | -0.23926 | -0.16449 | 60.2463 | -62.2101 | 0 | -62.3795 | 60.1685 | 62.2421 | 62.2101 | 0.045776 | -0.065155 | 0.069427 | 0.2948 | -0.14313 | -0.16129 | 0 | 0.032043 | -62.6038 | 60.1318 | 60.0952 | 62.178 | 62.3703 | 122.699 | 62.2147 | 60.1959
8342.0156 | 0.030518 | 0.42404 | -0.78186 | -0.22644 | 0.14526 | -0.2681 | -0.17197 | 60.2417 | -62.1506 | 0.045776 | -62.3886 | 60.1501 | 62.2513 | 62.2009 | 0.061035 | -0.069427 | 0.067291 | 0.29373 | -0.16342 | -0.1474 | -0.004578 | 0.004578 | -62.558 | 60.1547 | 60.1227 | 62.178 | 62.3703 | 122.6715 | 62.2513 | 60.173
8343.75 | 0.076294 | 0.43793 | -0.77331 | -0.21255 | 0.14633 | -0.26169 | -0.16769 | 60.2554 | -62.1689 | -0.009155 | -62.3749 | 60.1776 | 62.2375 | 62.2101 | 0.076294 | -0.071564 | 0.081177 | 0.298 | -0.14313 | -0.15488 | 0.036621 | 0.059509 | -62.5442 | 60.1181 | 60.0998 | 62.1735 | 62.3611 | 122.7356 | 62.2147 | 60.2051
8345.5156 | 0.061035 | 0.42191 | -0.76904 | -0.2211 | 0.13672 | -0.24353 | -0.15915 | 60.2554 | -62.1964 | 0.009155 | -62.3978 | 60.1273 | 62.2742 | 62.2055 | 0.091553 | -0.069427 | 0.081177 | 0.28839 | -0.16022 | -0.15488 | 0.004578 | 0.064087 | -62.59 | 60.1364 | 60.1044 | 62.1872 | 62.3886 | 122.6715 | 62.2559 | 60.1868
8347.2969 | 0.076294 | 0.42938 | -0.78934 | -0.21576 | 0.1442 | -0.28091 | -0.17731 | 60.3424 | -62.0407 | 0.082397 | -62.3016 | 60.1227 | 62.1597 | 62.1185 | 0.091553 | -0.09079 | 0.058746 | 0.28412 | -0.16556 | -0.15274 | 0.07782 | 0.12817 | -62.439 | 60.1044 | 60.1089 | 62.1185 | 62.3016 | 122.6028 | 62.2375 | 60.2646
8349.0781 | 0.076294 | 0.43472 | -0.77866 | -0.22964 | 0.14526 | -0.28519 | -0.17197 | 60.3195 | -62.0544 | 0.064087 | -62.2971 | 60.1639 | 62.1826 | 62.1048 | 0.061035 | -0.068359 | 0.060883 | 0.27985 | -0.16983 | -0.15808 | 0.068665 | 0.10071 | -62.4527 | 60.1135 | 60.1135 | 62.1231 | 62.2971 | 122.5937 | 62.2513 | 60.2646
8350.7969 | 0.091553 | 0.43045 | -0.77652 | -0.20828 | 0.13992 | -0.25101 | -0.17838 | 60.2142 | -62.2284 | -0.004578 | -62.4023 | 60.1685 | 62.2467 | 62.1735 | 0.030518 | -0.065155 | 0.063019 | 0.27985 | -0.13886 | -0.16983 | 0.036621 | 0.027466 | -62.5763 | 60.0998 | 60.1089 | 62.1735 | 62.3795 | 122.7173 | 62.2238 | 60.1639
8352.5781 | 0.076294 | 0.43152 | -0.79254 | -0.22217 | 0.1474 | -0.27664 | -0.18906 | 60.3195 | -62.0682 | 0.059509 | -62.3154 | 60.1318 | 62.1735 | 62.1323 | 0.076294 | -0.095062 | 0.075836 | 0.27023 | -0.17731 | -0.15915 | 0.064087 | 0.086975 | -62.4344 | 60.1227 | 60.1044 | 62.1231 | 62.3199 | 122.6028 | 62.233 | 60.26
8354.3594 | 0.091553 | 0.42618 | -0.78293 | -0.21469 | 0.14099 | -0.24887 | -0.16983 | 60.3058 | -62.114 | 0.032043 | -62.3291 | 60.1685 | 62.2238 | 62.146 | 0.076294 | -0.071564 | 0.072632 | 0.29587 | -0.15488 | -0.16449 | 0.10529 | 0.14191 | -62.4527 | 60.1089 | 60.0861 | 62.1414 | 62.3245 | 122.7448 | 62.2147 | 60.2142
8356.0625 | 0.061035 | 0.44647 | -0.79575 | -0.21469 | 0.13565 | -0.28091 | -0.18478 | 60.3653 | -61.9858 | 0.13275 | -62.265 | 60.141 | 62.178 | 62.1185 | 0.076294 | -0.091858 | 0.052338 | 0.28625 | -0.16235 | -0.16342 | 0.11444 | 0.14648 | -62.3795 | 60.1089 | 60.0998 | 62.1368 | 62.3291 | 122.6715 | 62.2284 | 60.2554
8357.8438 | 0.045776 | 0.4155 | -0.78079 | -0.22858 | 0.13779 | -0.24246 | -0.18158 | 60.2509 | -62.1552 | 0.027466 | -62.3795 | 60.1776 | 62.2375 | 62.1964 | 0.061035 | -0.070496 | 0.077972 | 0.2948 | -0.16022 | -0.16129 | -0.004578 | 0.004578 | -62.5626 | 60.1547 | 60.0861 | 62.1826 | 62.3703 | 122.6578 | 62.2559 | 60.2005
8359.5469 | 0.061035 | 0.45822 | -0.78934 | -0.21896 | 0.12924 | -0.27878 | -0.18265 | 60.3287 | -62.0636 | 0.07782 | -62.2971 | 60.2005 | 62.1826 | 62.1231 | 0.061035 | -0.0737 | 0.064087 | 0.28198 | -0.16129 | -0.16556 | 0.059509 | 0.086975 | -62.4527 | 60.1135 | 60.1227 | 62.0865 | 62.2925 | 122.6257 | 62.2284 | 60.2554
8361.3125 | 0.061035 | 0.42725 | -0.77545 | -0.20508 | 0.13458 | -0.26276 | -0.16876 | 60.3058 | -62.1506 | 0.022888 | -62.3657 | 60.1593 | 62.2513 | 62.1552 | 0.061035 | -0.063019 | 0.049133 | 0.28625 | -0.14526 | -0.16556 | 0.10529 | 0.1236 | -62.4756 | 60.1227 | 60.0861 | 62.146 | 62.3337 | 122.7448 | 62.2375 | 60.1913
8363.0312 | 0.061035 | 0.42404 | -0.77759 | -0.22003 | 0.13886 | -0.2446 | -0.1741 | 60.2737 | -62.2055 | -0.018311 | -62.3886 | 60.1593 | 62.2513 | 62.1964 | 0.061035 | -0.065155 | 0.075836 | 0.29053 | -0.15701 | -0.16449 | 0.050354 | 0.041199 | -62.5626 | 60.1318 | 60.1364 | 62.1735 | 62.3611 | 122.7356 | 62.2238 | 60.1776
8364.8125 | 0.045776 | 0.44006 | -0.77652 | -0.22324 | 0.15381 | -0.27771 | -0.18585 | 60.347 | -62.0316 | 0.10986 | -62.2879 | 60.1181 | 62.1918 | 62.1277 | 0.030518 | -0.074768 | 0.065155 | 0.29373 | -0.1709 | -0.15808 | 0.1236 | 0.16022 | -62.4115 | 60.0861 | 60.0998 | 62.0911 | 62.2833 | 122.6074 | 62.2238 | 60.2234
8366.5156 | 0.045776 | 0.4454 | -0.79361 | -0.21469 | 0.13992 | -0.28839 | -0.18051 | 60.3149 | -62.0636 | 0.082397 | -62.2925 | 60.1501 | 62.178 | 62.1002 | 0.061035 | -0.095062 | 0.064087 | 0.28625 | -0.15808 | -0.15808 | 0.07782 | 0.11902 | -62.4161 | 60.1089 | 60.0952 | 62.1094 | 62.2787 | 122.6532 | 62.2421 | 60.2371
8368.2969 | 0.061035 | 0.43259 | -0.78827 | -0.21683 | 0.13672 | -0.26489 | -0.18372 | 60.3287 | -62.0499 | 0.12817 | -62.2879 | 60.1318 | 62.2147 | 62.1597 | 0.061035 | -0.080109 | 0.0737 | 0.29587 | -0.15488 | -0.16983 | 0.027466 | 0.059509 | -62.5031 | 60.1135 | 60.0815 | 62.1735 | 62.3291 | 122.5754 | 62.2604 | 60.2417
8370.0625 | 0.061035 | 0.45288 | -0.78507 | -0.20615 | 0.13031 | -0.26916 | -0.17838 | 60.3287 | -62.0316 | 0.073242 | -62.2971 | 60.1501 | 62.1552 | 62.1094 | 0.076294 | -0.070496 | 0.054474 | 0.29159 | -0.15274 | -0.16129 | 0.082397 | 0.10071 | -62.439 | 60.1227 | 60.1089 | 62.1002 | 62.3062 | 122.5983 | 62.2513 | 60.2463
8371.8438 | 0.061035 | 0.43045 | -0.78293 | -0.2243 | 0.14206 | -0.26703 | -0.17517 | 60.3287 | -62.059 | 0.050354 | -62.3108 | 60.1685 | 62.1826 | 62.1231 | 0.076294 | -0.072632 | 0.066223 | 0.27664 | -0.16769 | -0.1741 | 0.068665 | 0.07782 | -62.4481 | 60.1273 | 60.1227 | 62.1002 | 62.2971 | 122.6486 | 62.2238 | 60.2371
8373.6406 | 0.061035 | 0.41763 | -0.76691 | -0.20828 | 0.1474 | -0.23178 | -0.17517 | 60.2646 | -62.1872 | -0.032043 | -62.3657 | 60.1685 | 62.2513 | 62.1735 | 0.076294 | -0.058746 | 0.070496 | 0.29587 | -0.1442 | -0.16876 | 0.064087 | 0.064087 | -62.558 | 60.1318 | 60.1044 | 62.1414 | 62.3428 | 122.7219 | 62.2101 | 60.1547
8375.3594 | 0.061035 | 0.42618 | -0.77759 | -0.20508 | 0.14847 | -0.25635 | -0.16769 | 60.3607 | -62.0224 | 0.09613 | -62.2742 | 60.141 | 62.2009 | 62.1506 | 0.061035 | -0.066223 | 0.070496 | 0.28519 | -0.13779 | -0.16876 | 0.14191 | 0.16937 | -62.4161 | 60.0723 | 60.0494 | 62.1277 | 62.3199 | 122.7127 | 62.233 | 60.2097
8377.1406 | 0.045776 | 0.4187 | -0.77972 | -0.21362 | 0.13886 | -0.25421 | -0.16663 | 60.2692 | -62.1552 | -0.009155 | -62.3795 | 60.1593 | 62.233 | 62.1735 | 0.061035 | -0.063019 | 0.068359 | 0.29053 | -0.15381 | -0.16129 | 0.073242 | 0.086975 | -62.5305 | 60.0998 | 60.0723 | 62.1597 | 62.3611 | 122.7539 | 62.2192 | 60.173
8378.875 | 0.045776 | 0.43259 | -0.79361 | -0.23285 | 0.13565 | -0.27771 | -0.18051 | 60.3607 | -62.0178 | 0.11444 | -62.2513 | 60.173 | 62.1826 | 62.1185 | 0.061035 | -0.079041 | 0.066223 | 0.28625 | -0.16449 | -0.15595 | 0.086975 | 0.13275 | -62.3886 | 60.1044 | 60.0906 | 62.1048 | 62.3016 | 122.6349 | 62.2055 | 60.228
8380.6406 | 0.061035 | 0.439 | -0.77972 | -0.22217 | 0.13886 | -0.27664 | -0.18799 | 60.3653 | -62.0041 | 0.10986 | -62.265 | 60.1501 | 62.1735 | 62.1277 | 0.061035 | -0.079041 | 0.061951 | 0.29159 | -0.16235 | -0.16556 | 0.10071 | 0.13733 | -62.3886 | 60.1227 | 60.1044 | 62.1094 | 62.2787 | 122.6532 | 62.2467 | 60.2234
8382.4219 | 0.076294 | 0.41763 | -0.77118 | -0.2243 | 0.15274 | -0.26169 | -0.1741 | 60.2692 | -62.1597 | 0.045776 | -62.3795 | 60.1685 | 62.2513 | 62.178 | 0.076294 | -0.064087 | 0.076904 | 0.29373 | -0.15274 | -0.16235 | -0.009155 | 0.004578 | -62.5534 | 60.141 | 60.1089 | 62.2009 | 62.3657 | 122.6303 | 62.2742 | 60.173
8384.2031 | 0.076294 | 0.43152 | -0.78186 | -0.22003 | 0.13031 | -0.27237 | -0.17303 | 60.3928 | -61.972 | 0.15106 | -62.2696 | 60.1364 | 62.1872 | 62.1277 | 0.061035 | -0.079041 | 0.066223 | 0.28198 | -0.16449 | -0.16876 | 0.13275 | 0.16937 | -62.3657 | 60.1089 | 60.0632 | 62.1002 | 62.3016 | 122.6303 | 62.2421 | 60.2188
8385.9688 | 0.061035 | 0.44006 | -0.77972 | -0.21576 | 0.12817 | -0.26596 | -0.18478 | 60.3836 | -61.972 | 0.14648 | -62.2513 | 60.1318 | 62.1826 | 62.1231 | 0.061035 | -0.089722 | 0.061951 | 0.27985 | -0.16876 | -0.15808 | 0.11902 | 0.16022 | -62.3703 | 60.0815 | 60.0769 | 62.1323 | 62.2879 | 122.6257 | 62.2421 | 60.2463
8387.7031 | 0.091553 | 0.43686 | -0.79041 | -0.21149 | 0.1474 | -0.27023 | -0.17944 | 60.3653 | -62.0224 | 0.10071 | -62.2971 | 60.1456 | 62.1597 | 62.0956 | 0.061035 | -0.0737 | 0.057678 | 0.27878 | -0.14847 | -0.16235 | 0.09613 | 0.14191 | -62.439 | 60.1181 | 60.0998 | 62.0773 | 62.3154 | 122.5983 | 62.2421 | 60.2417
8389.4688 | 0.061035 | 0.44754 | -0.7872 | -0.22217 | 0.13245 | -0.27451 | -0.17731 | 60.3836 | -61.9858 | 0.13733 | -62.2467 | 60.1273 | 62.178 | 62.1368 | 0.061035 | -0.080109 | 0.064087 | 0.27664 | -0.15274 | -0.15808 | 0.12817 | 0.16937 | -62.384 | 60.1089 | 60.0677 | 62.1368 | 62.2879 | 122.6395 | 62.2238 | 60.2463
8391.2344 | 0.045776 | 0.44006 | -0.79041 | -0.2179 | 0.14847 | -0.27344 | -0.18158 | 60.347 | -62.027 | 0.09613 | -62.2787 | 60.1501 | 62.2009 | 62.1368 | 0.045776 | -0.085449 | 0.076904 | 0.27344 | -0.16663 | -0.16556 | 0.091553 | 0.13733 | -62.3978 | 60.0998 | 60.0861 | 62.0956 | 62.3016 | 122.6578 | 62.2101 | 60.2325
8393.0312 | 0.061035 | 0.41763 | -0.77759 | -0.21469 | 0.13992 | -0.25528 | -0.16876 | 60.3516 | -62.027 | 0.11902 | -62.2925 | 60.141 | 62.2284 | 62.1506 | 0.045776 | -0.069427 | 0.068359 | 0.28625 | -0.16022 | -0.18051 | 0.045776 | 0.073242 | -62.4802 | 60.1089 | 60.0906 | 62.1414 | 62.3245 | 122.5754 | 62.2696 | 60.228
8394.75 | 0.076294 | 0.43579 | -0.77438 | -0.21042 | 0.14526 | -0.26703 | -0.17197 | 60.3653 | -62.0178 | 0.11902 | -62.2604 | 60.1227 | 62.1872 | 62.1277 | 0.076294 | -0.076904 | 0.064087 | 0.28732 | -0.1506 | -0.16556 | 0.15564 | 0.17853 | -62.4207 | 60.0998 | 60.0449 | 62.1277 | 62.3199 | 122.6669 | 62.2375 | 60.228
8396.5156 | 0.076294 | 0.43259 | -0.77759 | -0.21576 | 0.13351 | -0.25528 | -0.17517 | 60.347 | -62.0453 | 0.064087 | -62.2833 | 60.1593 | 62.2009 | 62.1414 | 0.076294 | -0.064087 | 0.074768 | 0.29373 | -0.14206 | -0.16022 | 0.13733 | 0.16937 | -62.4252 | 60.0861 | 60.0769 | 62.1368 | 62.3154 | 122.7081 | 62.2009 | 60.2097
8398.3125 | 0.061035 | 0.42831 | -0.7872 | -0.21896 | 0.13672 | -0.25848 | -0.17517 | 60.3561 | -62.0132 | 0.10529 | -62.2833 | 60.1227 | 62.1689 | 62.1094 | 0.045776 | -0.086517 | 0.058746 | 0.28412 | -0.16022 | -0.15808 | 0.13275 | 0.14191 | -62.4298 | 60.0952 | 60.0677 | 62.0956 | 62.3245 | 122.5891 | 62.2238 | 60.2737
8400.0312 | 0.061035 | 0.43152 | -0.77972 | -0.21042 | 0.12497 | -0.26916 | -0.18265 | 60.3149 | -62.0453 | 0.07782 | -62.2971 | 60.1501 | 62.178 | 62.114 | 0.076294 | -0.080109 | 0.070496 | 0.28091 | -0.15488 | -0.16556 | 0.068665 | 0.091553 | -62.4344 | 60.1044 | 60.0906 | 62.1277 | 62.2971 | 122.6074 | 62.2192 | 60.26
8401.8281 | 0.061035 | 0.41229 | -0.77118 | -0.2243 | 0.14954 | -0.23605 | -0.16876 | 60.2783 | -62.1231 | 0.032043 | -62.3383 | 60.1593 | 62.2604 | 62.1872 | 0.045776 | -0.060883 | 0.079041 | 0.30655 | -0.15595 | -0.17303 | 0.041199 | 0.064087 | -62.5305 | 60.0906 | 60.0632 | 62.1643 | 62.3657 | 122.7036 | 62.2238 | 60.1456
8403.5938 | 0.076294 | 0.44113 | -0.78079 | -0.20828 | 0.14633 | -0.26382 | -0.16449 | 60.3333 | -61.9995 | 0.09613 | -62.265 | 60.1181 | 62.178 | 62.114 | 0.045776 | -0.082245 | 0.070496 | 0.28732 | -0.15488 | -0.16235 | 0.12817 | 0.1831 | -62.4023 | 60.0815 | 60.0311 | 62.1506 | 62.3199 | 122.6669 | 62.233 | 60.2325
8405.375 | 0.061035 | 0.42725 | -0.76904 | -0.21469 | 0.14847 | -0.26062 | -0.18265 | 60.3561 | -62.0087 | 0.10986 | -62.2742 | 60.1135 | 62.178 | 62.1094 | 0.061035 | -0.077972 | 0.069427 | 0.28839 | -0.15595 | -0.16235 | 0.13275 | 0.16022 | -62.4115 | 60.0861 | 60.0632 | 62.0956 | 62.3291 | 122.612 | 62.2284 | 60.2509
8407.0938 | 0.061035 | 0.43045 | -0.77759 | -0.20187 | 0.14847 | -0.25421 | -0.17197 | 60.3058 | -62.1048 | 0.041199 | -62.3337 | 60.1364 | 62.2192 | 62.1597 | 0.061035 | -0.071564 | 0.060883 | 0.28839 | -0.13672 | -0.16129 | 0.10986 | 0.15564 | -62.4573 | 60.0998 | 60.054 | 62.1506 | 62.3291 | 122.7264 | 62.2101 | 60.1822
8408.875 | 0.061035 | 0.41336 | -0.78079 | -0.23392 | 0.13779 | -0.25955 | -0.1709 | 60.3058 | -62.0407 | 0.10529 | -62.2971 | 60.1318 | 62.2101 | 62.1323 | 0.076294 | -0.069427 | 0.075836 | 0.28198 | -0.16129 | -0.16983 | 0.032043 | 0.064087 | -62.4847 | 60.1181 | 60.0861 | 62.1552 | 62.3383 | 122.5845 | 62.2513 | 60.2417
8410.6406 | 0.030518 | 0.41122 | -0.76477 | -0.22751 | 0.1442 | -0.24353 | -0.16663 | 60.2692 | -62.0956 | 0.068665 | -62.3383 | 60.1456 | 62.2604 | 62.2009 | 0.091553 | -0.063019 | 0.086517 | 0.29159 | -0.13992 | -0.16556 | 0.054932 | 0.073242 | -62.5259 | 60.1135 | 60.0632 | 62.1735 | 62.3795 | 122.731 | 62.233 | 60.1593
8412.3438 | 0.076294 | 0.43366 | -0.77118 | -0.21576 | 0.14099 | -0.25742 | -0.17838 | 60.2646 | -62.1368 | 0.009155 | -62.3566 | 60.1456 | 62.2375 | 62.1735 | 0.076294 | -0.065155 | 0.069427 | 0.29053 | -0.16022 | -0.1506 | 0.073242 | 0.10071 | -62.4802 | 60.1135 | 60.1044 | 62.1277 | 62.3291 | 122.731 | 62.1964 | 60.1776
8414.1406 | 0.061035 | 0.43366 | -0.77331 | -0.21149 | 0.14526 | -0.27557 | -0.1741 | 60.3333 | -62.0178 | 0.10986 | -62.2879 | 60.0952 | 62.1918 | 62.1094 | 0.061035 | -0.083313 | 0.060883 | 0.28625 | -0.1506 | -0.16235 | 0.1236 | 0.17853 | -62.4069 | 60.0677 | 60.0494 | 62.114 | 62.3108 | 122.644 | 62.2101 | 60.2234
8415.8594 | 0.061035 | 0.43793 | -0.7872 | -0.22217 | 0.13565 | -0.28519 | -0.18051 | 60.3333 | -62.0178 | 0.09613 | -62.2833 | 60.1273 | 62.1552 | 62.1094 | 0.061035 | -0.080109 | 0.0737 | 0.28946 | -0.16342 | -0.16342 | 0.091553 | 0.13733 | -62.4161 | 60.0906 | 60.0677 | 62.0819 | 62.2971 | 122.58 | 62.2559 | 60.26
8417.6406 | 0.076294 | 0.40909 | -0.78613 | -0.22751 | 0.13672 | -0.23819 | -0.1741 | 60.2325 | -62.146 | 0.045776 | -62.3474 | 60.1364 | 62.2604 | 62.2009 | 0.061035 | -0.061951 | 0.0737 | 0.28519 | -0.1474 | -0.17197 | 0.013733 | 0.041199 | -62.5397 | 60.1227 | 60.0815 | 62.178 | 62.3749 | 122.7081 | 62.2055 | 60.1547
8419.3594 | 0.045776 | 0.42084 | -0.784 | -0.23178 | 0.13779 | -0.28305 | -0.19012 | 60.2966 | -62.0224 | 0.082397 | -62.2879 | 60.1364 | 62.1826 | 62.1185 | 0.061035 | -0.081177 | 0.074768 | 0.28198 | -0.16876 | -0.16022 | 0.086975 | 0.11444 | -62.3886 | 60.1089 | 60.0906 | 62.0956 | 62.3199 | 122.6395 | 62.2192 | 60.2371
8421.1406 | 0.076294 | 0.42084 | -0.77225 | -0.20401 | 0.13031 | -0.25742 | -0.17197 | 60.2188 | -62.2055 | -0.041199 | -62.3932 | 60.1501 | 62.2559 | 62.1826 | 0.045776 | -0.048065 | 0.0737 | 0.30441 | -0.15595 | -0.16129 | 0.032043 | 0.032043 | -62.5717 | 60.1135 | 60.0815 | 62.1597 | 62.3611 | 122.6852 | 62.2192 | 60.173
8422.9219 | 0.045776 | 0.4155 | -0.79147 | -0.22537 | 0.13672 | -0.27237 | -0.17944 | 60.3241 | -62.0132 | 0.14648 | -62.2787 | 60.1181 | 62.2101 | 62.1231 | 0.045776 | -0.080109 | 0.063019 | 0.28305 | -0.16342 | -0.16129 | 0.036621 | 0.10071 | -62.4573 | 60.0952 | 60.0861 | 62.1277 | 62.352 | 122.5754 | 62.2696 | 60.2188
8424.7031 | 0.030518 | 0.43472 | -0.77866 | -0.21683 | 0.13565 | -0.26596 | -0.18478 | 60.3378 | -62.0132 | 0.091553 | -62.2833 | 60.1089 | 62.2055 | 62.114 | 0.076294 | -0.083313 | 0.059814 | 0.29907 | -0.16342 | -0.16663 | 0.12817 | 0.16022 | -62.4115 | 60.0677 | 60.0952 | 62.1231 | 62.3154 | 122.5983 | 62.2467 | 60.2097
8426.4062 | 0.076294 | 0.44006 | -0.77331 | -0.22751 | 0.13992 | -0.27878 | -0.16876 | 60.3561 | -62.0041 | 0.11902 | -62.2375 | 60.1547 | 62.1918 | 62.1048 | 0.045776 | -0.087585 | 0.070496 | 0.28732 | -0.17944 | -0.15488 | 0.10071 | 0.13733 | -62.3703 | 60.1227 | 60.0815 | 62.0956 | 62.2971 | 122.6303 | 62.2009 | 60.2234
8428.1719 | 0.045776 | 0.4155 | -0.78507 | -0.22324 | 0.13779 | -0.26169 | -0.18906 | 60.2463 | -62.1185 | 0.045776 | -62.3566 | 60.173 | 62.2375 | 62.1735 | 0.061035 | -0.072632 | 0.0737 | 0.29266 | -0.15808 | -0.16449 | 0.009155 | 0 | -62.5305 | 60.1318 | 60.0861 | 62.1826 | 62.384 | 122.5983 | 62.2375 | 60.1959
8429.9375 | 0.061035 | 0.45929 | -0.77972 | -0.21149 | 0.1442 | -0.27664 | -0.18585 | 60.3607 | -61.9675 | 0.14191 | -62.2604 | 60.1318 | 62.1689 | 62.1048 | 0.061035 | -0.088654 | 0.065155 | 0.28091 | -0.16342 | -0.14954 | 0.13275 | 0.16479 | -62.352 | 60.0998 | 60.0769 | 62.1185 | 62.3062 | 122.6303 | 62.2101 | 60.2188
8431.6562 | 0.076294 | 0.43045 | -0.78186 | -0.22751 | 0.13992 | -0.28198 | -0.18372 | 60.3653 | -61.9766 | 0.14191 | -62.265 | 60.1456 | 62.1872 | 62.1414 | 0.061035 | -0.083313 | 0.061951 | 0.27985 | -0.16556 | -0.16235 | 0.13275 | 0.15106 | -62.3749 | 60.1089 | 60.0815 | 62.0956 | 62.2925 | 122.6257 | 62.2147 | 60.228
8433.4219 | 0.061035 | 0.42831 | -0.7872 | -0.23605 | 0.1474 | -0.2713 | -0.18692 | 60.3104 | -62.0499 | 0.10071 | -62.3245 | 60.1227 | 62.2284 | 62.1506 | 0.061035 | -0.0737 | 0.071564 | 0.27878 | -0.15595 | -0.16556 | 0.032043 | 0.041199 | -62.4893 | 60.1227 | 60.0723 | 62.1643 | 62.3428 | 122.5708 | 62.2604 | 60.2142
8435.1406 | 0.061035 | 0.41122 | -0.76263 | -0.20935 | 0.12711 | -0.23712 | -0.16663 | 60.2875 | -62.1094 | 0.07782 | -62.3428 | 60.1593 | 62.2375 | 62.178 | 0.061035 | -0.059814 | 0.060883 | 0.30121 | -0.14206 | -0.16876 | 0.068665 | 0.091553 | -62.5076 | 60.0815 | 60.0677 | 62.1735 | 62.3657 | 122.699 | 62.2192 | 60.1639
8436.9219 | 0.061035 | 0.44434 | -0.77331 | -0.22537 | 0.1442 | -0.27237 | -0.16342 | 60.3333 | -62.0087 | 0.091553 | -62.2787 | 60.1364 | 62.1689 | 62.1048 | 0.061035 | -0.09613 | 0.068359 | 0.29907 | -0.15595 | -0.15488 | 0.10071 | 0.13733 | -62.4252 | 60.1044 | 60.0906 | 62.114 | 62.2925 | 122.5891 | 62.233 | 60.2554
8438.7031 | 0.061035 | 0.42938 | -0.77118 | -0.22537 | 0.15167 | -0.28305 | -0.16983 | 60.3333 | -61.9949 | 0.14648 | -62.2559 | 60.1135 | 62.1918 | 62.114 | 0.076294 | -0.077972 | 0.079041 | 0.29266 | -0.16235 | -0.16769 | 0.068665 | 0.1236 | -62.4023 | 60.0906 | 60.0403 | 62.1277 | 62.3108 | 122.5662 | 62.2513 | 60.2234
8440.4219 | 0.061035 | 0.41443 | -0.76157 | -0.19974 | 0.13351 | -0.23712 | -0.16129 | 60.2921 | -62.1002 | 0.082397 | -62.3474 | 60.1273 | 62.2559 | 62.1597 | 0.045776 | -0.066223 | 0.075836 | 0.29587 | -0.13886 | -0.16983 | 0.068665 | 0.09613 | -62.5397 | 60.0998 | 60.0403 | 62.1597 | 62.3703 | 122.6578 | 62.2101 | 60.173
8442.2031 | 0.061035 | 0.42831 | -0.77866 | -0.22003 | 0.13351 | -0.28305 | -0.18372 | 60.2783 | -62.0178 | 0.054932 | -62.2925 | 60.1501 | 62.178 | 62.1231 | 0.061035 | -0.088654 | 0.072632 | 0.28625 | -0.16556 | -0.15915 | 0.054932 | 0.09613 | -62.4161 | 60.1135 | 60.0861 | 62.0911 | 62.3108 | 122.5845 | 62.2009 | 60.2509
8443.9844 | 0.061035 | 0.43259 | -0.78827 | -0.20721 | 0.1442 | -0.26596 | -0.16876 | 60.3378 | -61.9995 | 0.10071 | -62.2787 | 60.1318 | 62.1689 | 62.114 | 0.076294 | -0.077972 | 0.061951 | 0.28946 | -0.14954 | -0.16129 | 0.12817 | 0.13733 | -62.4069 | 60.0998 | 60.0769 | 62.0911 | 62.2879 | 122.5937 | 62.2284 | 60.2646
8445.7656 | 0.030518 | 0.42297 | -0.77225 | -0.2243 | 0.13565 | -0.24674 | -0.16769 | 60.2509 | -62.1643 | 0 | -62.3657 | 60.141 | 62.233 | 62.1643 | 0.076294 | -0.065155 | 0.068359 | 0.28625 | -0.15701 | -0.17624 | 0.059509 | 0.054932 | -62.5214 | 60.1181 | 60.1044 | 62.1414 | 62.3383 | 122.7264 | 62.2147 | 60.1959
8447.5312 | 0.061035 | 0.41016 | -0.76904 | -0.21469 | 0.15381 | -0.24139 | -0.16876 | 60.2554 | -62.1094 | 0.07782 | -62.3474 | 60.1135 | 62.2375 | 62.1872 | 0.076294 | -0.064087 | 0.080109 | 0.28732 | -0.14954 | -0.16342 | 0.082397 | 0.11902 | -62.5214 | 60.0723 | 60.0769 | 62.1689 | 62.384 | 122.6807 | 62.2421 | 60.1593
8449.3438 | 0.045776 | 0.42404 | -0.77545 | -0.24567 | 0.13458 | -0.27344 | -0.18051 | 60.2554 | -62.0819 | 0.086975 | -62.3337 | 60.1501 | 62.2238 | 62.1368 | 0.061035 | -0.086517 | 0.082245 | 0.28198 | -0.16556 | -0.1506 | 0.009155 | 0.022888 | -62.5122 | 60.1273 | 60.0998 | 62.1597 | 62.3428 | 122.5525 | 62.2467 | 60.2142
8451.0469 | 0.045776 | 0.41763 | -0.784 | -0.22644 | 0.13031 | -0.26062 | -0.17944 | 60.2234 | -62.146 | 0.022888 | -62.3611 | 60.1501 | 62.2513 | 62.1872 | 0.061035 | -0.066223 | 0.079041 | 0.29266 | -0.15808 | -0.16663 | -0.013733 | 0.009155 | -62.5397 | 60.1273 | 60.1044 | 62.1643 | 62.3474 | 122.6166 | 62.233 | 60.1868
8452.8281 | 0.061035 | 0.44861 | -0.78079 | -0.2243 | 0.12604 | -0.28305 | -0.18265 | 60.2966 | -62.0453 | 0.054932 | -62.2833 | 60.1273 | 62.1506 | 62.0956 | 0.045776 | -0.085449 | 0.064087 | 0.28839 | -0.1709 | -0.16022 | 0.059509 | 0.10071 | -62.4344 | 60.1181 | 60.1135 | 62.1002 | 62.2971 | 122.5754 | 62.2192 | 60.2371
8454.5312 | 0.061035 | 0.40909 | -0.78079 | -0.22751 | 0.13886 | -0.26703 | -0.17731 | 60.3287 | -61.9904 | 0.13733 | -62.2559 | 60.1227 | 62.178 | 62.1048 | 0.061035 | -0.09079 | 0.064087 | 0.28519 | -0.16663 | -0.1709 | 0.059509 | 0.12817 | -62.4069 | 60.0861 | 60.0677 | 62.1506 | 62.352 | 122.5525 | 62.2192 | 60.2371
8456.2969 | 0.076294 | 0.41657 | -0.78293 | -0.21896 | 0.12924 | -0.25528 | -0.18478 | 60.2371 | -62.146 | 0.036621 | -62.3611 | 60.173 | 62.2147 | 62.1964 | 0.061035 | -0.070496 | 0.069427 | 0.29266 | -0.15595 | -0.16663 | -0.004578 | 0.027466 | -62.5397 | 60.1273 | 60.1273 | 62.1506 | 62.3703 | 122.6395 | 62.2421 | 60.1685
8458.0625 | 0.045776 | 0.45395 | -0.79041 | -0.20081 | 0.11749 | -0.27771 | -0.18051 | 60.3333 | -62.0087 | 0.091553 | -62.265 | 60.1456 | 62.1597 | 62.114 | 0.045776 | -0.09613 | 0.057678 | 0.27771 | -0.15167 | -0.15274 | 0.09613 | 0.13275 | -62.3795 | 60.1135 | 60.0723 | 62.0865 | 62.2879 | 122.6303 | 62.2192 | 60.228
8459.8438 | 0.061035 | 0.42831 | -0.79147 | -0.23392 | 0.12817 | -0.27664 | -0.18265 | 60.347 | -61.9812 | 0.1236 | -62.2696 | 60.141 | 62.1643 | 62.114 | 0.061035 | -0.082245 | 0.060883 | 0.28198 | -0.15808 | -0.16129 | 0.1236 | 0.13275 | -62.3657 | 60.0769 | 60.0815 | 62.0865 | 62.2742 | 122.6166 | 62.233 | 60.2188
8461.625 | 0.061035 | 0.44861 | -0.7872 | -0.2179 | 0.13565 | -0.26062 | -0.16769 | 60.3561 | -61.9904 | 0.09613 | -62.2787 | 60.1044 | 62.1918 | 62.1185 | 0.091553 | -0.09079 | 0.065155 | 0.28198 | -0.15488 | -0.16556 | 0.12817 | 0.15564 | -62.3978 | 60.0906 | 60.0632 | 62.1185 | 62.3199 | 122.58 | 62.2238 | 60.2371
8463.4062 | 0.076294 | 0.42404 | -0.79147 | -0.23498 | 0.14313 | -0.26382 | -0.18799 | 60.3561 | -61.9858 | 0.16479 | -62.2513 | 60.1273 | 62.2009 | 62.1231 | 0.076294 | -0.085449 | 0.085449 | 0.29053 | -0.16129 | -0.16235 | 0.086975 | 0.14191 | -62.3978 | 60.0906 | 60.054 | 62.114 | 62.3154 | 122.58 | 62.2559 | 60.2371
8465.125 | 0.045776 | 0.40802 | -0.77011 | -0.22644 | 0.1442 | -0.23285 | -0.17197 | 60.2829 | -62.1277 | 0.068665 | -62.3474 | 60.141 | 62.2559 | 62.1872 | 0.061035 | -0.057678 | 0.070496 | 0.30014 | -0.13245 | -0.18265 | 0.054932 | 0.059509 | -62.5534 | 60.1227 | 60.0586 | 62.1826 | 62.3795 | 122.6578 | 62.2192 | 60.1776
8466.9062 | 0.076294 | 0.42191 | -0.77331 | -0.23178 | 0.13886 | -0.27344 | -0.18158 | 60.3241 | -61.9904 | 0.15106 | -62.2604 | 60.1227 | 62.1826 | 62.1277 | 0.045776 | -0.081177 | 0.080109 | 0.28732 | -0.16876 | -0.16342 | 0.07782 | 0.12817 | -62.4161 | 60.0769 | 60.0815 | 62.1094 | 62.3199 | 122.5616 | 62.2467 | 60.2417
8468.6719 | 0.061035 | 0.43152 | -0.77545 | -0.22324 | 0.14099 | -0.25848 | -0.17624 | 60.2371 | -62.1277 | 0.032043 | -62.352 | 60.1685 | 62.2513 | 62.1689 | 0.076294 | -0.060883 | 0.071564 | 0.29694 | -0.1442 | -0.16022 | 0.004578 | 0.004578 | -62.5534 | 60.1318 | 60.1089 | 62.1643 | 62.3428 | 122.5845 | 62.2467 | 60.1868
8470.3906 | 0.061035 | 0.42191 | -0.78293 | -0.21576 | 0.13672 | -0.27451 | -0.17944 | 60.3287 | -61.9263 | 0.12817 | -62.2467 | 60.1318 | 62.178 | 62.0911 | 0.061035 | -0.09079 | 0.068359 | 0.27985 | -0.16022 | -0.15701 | 0.1236 | 0.15106 | -62.3611 | 60.0906 | 60.0632 | 62.0865 | 62.3108 | 122.6257 | 62.1872 | 60.2234
8472.1719 | 0.076294 | 0.42511 | -0.77972 | -0.22537 | 0.13779 | -0.25635 | -0.17838 | 60.228 | -62.114 | 0.041199 | -62.3566 | 60.1593 | 62.2238 | 62.1643 | 0.061035 | -0.074768 | 0.072632 | 0.27771 | -0.15595 | -0.16449 | -0.013733 | 0.018311 | -62.5168 | 60.0998 | 60.0906 | 62.178 | 62.3611 | 122.5891 | 62.2284 | 60.228
8473.9531 | 0.061035 | 0.43152 | -0.77225 | -0.22964 | 0.14526 | -0.26916 | -0.17838 | 60.3149 | -62.0132 | 0.09613 | -62.2879 | 60.141 | 62.1689 | 62.1048 | 0.061035 | -0.084381 | 0.070496 | 0.29159 | -0.16769 | -0.16449 | 0.086975 | 0.1236 | -62.3978 | 60.1044 | 60.0815 | 62.1048 | 62.3199 | 122.5708 | 62.233 | 60.2463
8475.6562 | 0.061035 | 0.41229 | -0.79681 | -0.2211 | 0.13992 | -0.24887 | -0.17731 | 60.228 | -62.114 | 0.036621 | -62.352 | 60.1776 | 62.233 | 62.1735 | 0.091553 | -0.069427 | 0.067291 | 0.27985 | -0.16129 | -0.16235 | -0.004578 | 0.009155 | -62.5397 | 60.1273 | 60.0861 | 62.1643 | 62.3566 | 122.6257 | 62.2375 | 60.1776
8477.4375 | 0.045776 | 0.43579 | -0.78934 | -0.23178 | 0.14206 | -0.28732 | -0.18051 | 60.3149 | -61.972 | 0.11902 | -62.2559 | 60.1547 | 62.178 | 62.1048 | 0.076294 | -0.089722 | 0.067291 | 0.28091 | -0.16769 | -0.16876 | 0.10071 | 0.13275 | -62.3566 | 60.0861 | 60.0723 | 62.1002 | 62.3062 | 122.6212 | 62.2009 | 60.2325
8479.1562 | 0.030518 | 0.41763 | -0.77545 | -0.21683 | 0.13458 | -0.24567 | -0.1741 | 60.2554 | -62.1094 | 0 | -62.3474 | 60.1547 | 62.2284 | 62.146 | 0.061035 | -0.074768 | 0.068359 | 0.26916 | -0.13458 | -0.16022 | 0.10071 | 0.10529 | -62.4893 | 60.1318 | 60.054 | 62.146 | 62.3199 | 122.7219 | 62.1826 | 60.1822
8480.9219 | 0.076294 | 0.4454 | -0.78827 | -0.21469 | 0.1442 | -0.2681 | -0.18051 | 60.3195 | -61.972 | 0.10986 | -62.2742 | 60.0906 | 62.1964 | 62.1002 | 0.061035 | -0.065155 | 0.052338 | 0.28091 | -0.1506 | -0.15488 | 0.11444 | 0.16022 | -62.3886 | 60.0815 | 60.0632 | 62.0956 | 62.2879 | 122.5891 | 62.1918 | 60.2234
8482.7031 | 0.061035 | 0.42618 | -0.77972 | -0.20081 | 0.13779 | -0.26169 | -0.17944 | 60.3333 | -61.9995 | 0.10071 | -62.2604 | 60.1227 | 62.1597 | 62.0819 | 0.061035 | -0.082245 | 0.052338 | 0.28412 | -0.16342 | -0.16983 | 0.11902 | 0.1831 | -62.3886 | 60.0861 | 60.0357 | 62.1002 | 62.2925 | 122.6028 | 62.1964 | 60.228
8484.4844 | 0.061035 | 0.40695 | -0.77759 | -0.23605 | 0.14526 | -0.26169 | -0.16876 | 60.2417 | -62.1414 | 0.045776 | -62.352 | 60.1639 | 62.2192 | 62.2009 | 0.091553 | -0.064087 | 0.0737 | 0.28198 | -0.15167 | -0.16556 | 0.004578 | 0.027466 | -62.5351 | 60.1318 | 60.0769 | 62.1597 | 62.3566 | 122.6761 | 62.2192 | 60.1501
8486.25 | 0.061035 | 0.40909 | -0.78507 | -0.24674 | 0.14206 | -0.26703 | -0.17517 | 60.2234 | -62.1414 | 0.041199 | -62.352 | 60.1593 | 62.2009 | 62.1826 | 0.061035 | -0.068359 | 0.068359 | 0.298 | -0.15808 | -0.16449 | -0.009155 | 0.004578 | -62.5351 | 60.1089 | 60.1089 | 62.1689 | 62.3657 | 122.612 | 62.2055 | 60.1776
8488.0156 | 0.045776 | 0.4187 | -0.79041 | -0.21255 | 0.13351 | -0.26489 | -0.17517 | 60.228 | -62.114 | 0.050354 | -62.352 | 60.1593 | 62.2467 | 62.1689 | 0.061035 | -0.075836 | 0.069427 | 0.28732 | -0.16129 | -0.15595 | 0 | 0 | -62.5259 | 60.1135 | 60.0952 | 62.1552 | 62.3611 | 122.5754 | 62.2467 | 60.1822
8489.7656 | 0.045776 | 0.41977 | -0.77866 | -0.2211 | 0.14099 | -0.27985 | -0.17624 | 60.26 | -62.0728 | 0.07782 | -62.3108 | 60.141 | 62.2192 | 62.1414 | 0.045776 | -0.067291 | 0.058746 | 0.28839 | -0.16342 | -0.16769 | 0 | 0.018311 | -62.4985 | 60.0998 | 60.0815 | 62.1689 | 62.3337 | 122.5616 | 62.2467 | 60.1959
8491.5469 | 0.061035 | 0.45181 | -0.79681 | -0.22324 | 0.13458 | -0.29053 | -0.17944 | 60.2921 | -62.0316 | 0.068665 | -62.2696 | 60.1501 | 62.1552 | 62.0911 | 0.076294 | -0.088654 | 0.057678 | 0.28625 | -0.16235 | -0.15488 | 0.059509 | 0.12817 | -62.4023 | 60.0906 | 60.0906 | 62.0682 | 62.2925 | 122.612 | 62.2055 | 60.2097
8493.3125 | 0.045776 | 0.42831 | -0.79254 | -0.22217 | 0.12817 | -0.28091 | -0.17624 | 60.3836 | -61.9354 | 0.16479 | -62.2421 | 60.1318 | 62.1597 | 62.1094 | 0.061035 | -0.088654 | 0.055542 | 0.27985 | -0.15915 | -0.17197 | 0.11444 | 0.15106 | -62.3749 | 60.0906 | 60.0769 | 62.0956 | 62.2925 | 122.6028 | 62.2055 | 60.2234
8495.0156 | 0.061035 | 0.41443 | -0.77225 | -0.20294 | 0.1474 | -0.23819 | -0.1741 | 60.2829 | -62.0956 | 0.073242 | -62.3383 | 60.1273 | 62.2467 | 62.1918 | 0.045776 | -0.070496 | 0.071564 | 0.30334 | -0.13779 | -0.16449 | 0.082397 | 0.082397 | -62.5122 | 60.0861 | 60.0494 | 62.1826 | 62.3611 | 122.6807 | 62.2101 | 60.1593
8496.8281 | 0.061035 | 0.43259 | -0.79041 | -0.21149 | 0.14099 | -0.25101 | -0.17197 | 60.2554 | -62.1277 | 0.018311 | -62.3291 | 60.1318 | 62.2101 | 62.1552 | 0.061035 | -0.085449 | 0.067291 | 0.28625 | -0.1506 | -0.17517 | 0.091553 | 0.10071 | -62.4847 | 60.0769 | 60.0494 | 62.1597 | 62.3337 | 122.7036 | 62.2147 | 60.1959
8498.625 | 0.045776 | 0.44006 | -0.77545 | -0.21683 | 0.14313 | -0.28839 | -0.16129 | 60.3287 | -61.9995 | 0.10071 | -62.2833 | 60.0906 | 62.2009 | 62.1277 | 0.061035 | -0.085449 | 0.060883 | 0.28625 | -0.15808 | -0.15381 | 0.1236 | 0.16022 | -62.3932 | 60.1044 | 60.0815 | 62.1048 | 62.3154 | 122.5662 | 62.2147 | 60.2417
8500.75 | 0.061035 | 0.4155 | -0.78934 | -0.23071 | 0.13351 | -0.27237 | -0.17303 | 60.2463 | -62.1048 | 0.054932 | -62.3199 | 60.141 | 62.2101 | 62.1506 | 0.061035 | -0.075836 | 0.074768 | 0.27557 | -0.16769 | -0.16449 | -0.004578 | 0.022888 | -62.5168 | 60.1227 | 60.0906 | 62.1735 | 62.3428 | 122.5708 | 62.2467 | 60.2142
8502.5469 | 0.045776 | 0.41977 | -0.76904 | -0.22644 | 0.14099 | -0.2478 | -0.17624 | 60.2371 | -62.1231 | 0.054932 | -62.3245 | 60.141 | 62.2421 | 62.1826 | 0.045776 | -0.058746 | 0.069427 | 0.28519 | -0.15488 | -0.16663 | 0.050354 | 0.07782 | -62.5168 | 60.0998 | 60.0815 | 62.1506 | 62.3703 | 122.699 | 62.1689 | 60.141
8504.4688 | 0.061035 | 0.40802 | -0.77011 | -0.22964 | 0.13886 | -0.27557 | -0.16876 | 60.228 | -62.1185 | 0.064087 | -62.3428 | 60.1501 | 62.2192 | 62.1552 | 0.076294 | -0.079041 | 0.071564 | 0.28625 | -0.15915 | -0.15167 | 0.009155 | 0.022888 | -62.5076 | 60.1135 | 60.0906 | 62.1643 | 62.3611 | 122.5571 | 62.2559 | 60.1913
8508.8594 | 0.061035 | 0.43152 | -0.78186 | -0.23178 | 0.13779 | -0.27344 | -0.18051 | 60.3378 | -61.9629 | 0.16479 | -62.2513 | 60.1181 | 62.178 | 62.1231 | 0.061035 | -0.091858 | 0.063019 | 0.28625 | -0.17197 | -0.16342 | 0.086975 | 0.15564 | -62.3657 | 60.0677 | 60.0769 | 62.1094 | 62.3016 | 122.5708 | 62.2009 | 60.1913
8510.9062 | 0.076294 | 0.41336 | -0.78079 | -0.22644 | 0.14206 | -0.28198 | -0.18158 | 60.2875 | -62.0499 | 0.07782 | -62.2833 | 60.1456 | 62.1643 | 62.1048 | 0.045776 | -0.084381 | 0.070496 | 0.27344 | -0.16983 | -0.16876 | 0.054932 | 0.09613 | -62.3978 | 60.1181 | 60.1135 | 62.0956 | 62.3062 | 122.5983 | 62.1964 | 60.2188
8512.6875 | 0.061035 | 0.42084 | -0.76797 | -0.21042 | 0.13779 | -0.23285 | -0.17303 | 60.2417 | -62.1414 | 0 | -62.3474 | 60.1364 | 62.233 | 62.1689 | 0.076294 | -0.059814 | 0.070496 | 0.30334 | -0.15701 | -0.17303 | 0.073242 | 0.059509 | -62.4985 | 60.0952 | 60.0861 | 62.146 | 62.352 | 122.7081 | 62.1826 | 60.173
8514.4375 | 0.061035 | 0.42831 | -0.78613 | -0.22858 | 0.13672 | -0.27771 | -0.17624 | 60.3745 | -61.9446 | 0.14648 | -62.2467 | 60.1181 | 62.1689 | 62.1002 | 0.076294 | -0.076904 | 0.066223 | 0.26916 | -0.15915 | -0.1442 | 0.10071 | 0.16479 | -62.352 | 60.0815 | 60.0769 | 62.1231 | 62.2879 | 122.58 | 62.2238 | 60.2097
8516.375 | 0.076294 | 0.42084 | -0.78186 | -0.20508 | 0.13458 | -0.24887 | -0.1709 | 60.2097 | -62.1735 | -0.018311 | -62.3749 | 60.1456 | 62.2192 | 62.1643 | 0.030518 | -0.064087 | 0.075836 | 0.28732 | -0.13672 | -0.16769 | 0.041199 | 0.036621 | -62.558 | 60.1181 | 60.0586 | 62.178 | 62.3657 | 122.644 | 62.2192 | 60.1868
8518.875 | 0.061035 | 0.41977 | -0.77011 | -0.2179 | 0.13672 | -0.2446 | -0.1741 | 60.1913 | -62.178 | -0.018311 | -62.3703 | 60.1685 | 62.2421 | 62.1918 | 0.045776 | -0.070496 | 0.074768 | 0.28732 | -0.13672 | -0.16022 | 0.041199 | 0.045776 | -62.5671 | 60.1135 | 60.0769 | 62.178 | 62.384 | 122.6669 | 62.2238 | 60.1685
8520.6562 | 0.045776 | 0.45822 | -0.78934 | -0.21683 | 0.1442 | -0.29694 | -0.17731 | 60.2829 | -62.0178 | 0.073242 | -62.2787 | 60.1273 | 62.146 | 62.0956 | 0.061035 | -0.081177 | 0.072632 | 0.27985 | -0.16342 | -0.15167 | 0.054932 | 0.10529 | -62.4115 | 60.0906 | 60.0861 | 62.0911 | 62.2787 | 122.5525 | 62.2192 | 60.228
8522.5781 | 0.061035 | 0.42191 | -0.78079 | -0.2211 | 0.1442 | -0.24139 | -0.17731 | 60.2005 | -62.2009 | -0.004578 | -62.3703 | 60.1318 | 62.2375 | 62.178 | 0.076294 | -0.059814 | 0.075836 | 0.2948 | -0.13886 | -0.15808 | 0.041199 | 0.050354 | -62.5626 | 60.1044 | 60.0815 | 62.1597 | 62.3657 | 122.644 | 62.2101 | 60.1776
8524.4062 | 0.045776 | 0.39948 | -0.77225 | -0.23285 | 0.13245 | -0.24674 | -0.16556 | 60.2325 | -62.0865 | 0.073242 | -62.3245 | 60.1181 | 62.2238 | 62.178 | 0.076294 | -0.068359 | 0.067291 | 0.2948 | -0.1506 | -0.16663 | 0.064087 | 0.09613 | -62.5031 | 60.0906 | 60.0632 | 62.1735 | 62.3749 | 122.6624 | 62.2009 | 60.1685
8526.2812 | 0.061035 | 0.41122 | -0.77118 | -0.23498 | 0.13565 | -0.28091 | -0.17624 | 60.2966 | -61.9904 | 0.14191 | -62.2696 | 60.1089 | 62.1735 | 62.1185 | 0.076294 | -0.0737 | 0.0737 | 0.28519 | -0.17944 | -0.15167 | 0.036621 | 0.10071 | -62.4435 | 60.0906 | 60.0815 | 62.1323 | 62.3337 | 122.525 | 62.2238 | 60.2005
8528.0938 | 0.076294 | 0.42511 | -0.77652 | -0.21149 | 0.1442 | -0.24674 | -0.17197 | 60.1913 | -62.1735 | 0.004578 | -62.352 | 60.1593 | 62.2238 | 62.1964 | 0.061035 | -0.072632 | 0.069427 | 0.27985 | -0.14526 | -0.1741 | 0.004578 | 0.041199 | -62.5717 | 60.1135 | 60.1135 | 62.1735 | 62.3611 | 122.6257 | 62.2238 | 60.1547
8529.9062 | 0.061035 | 0.42831 | -0.78079 | -0.22537 | 0.14313 | -0.27985 | -0.18478 | 60.2966 | -61.9904 | 0.16937 | -62.2604 | 60.1181 | 62.1872 | 62.1277 | 0.061035 | -0.087585 | 0.068359 | 0.27878 | -0.17303 | -0.15488 | 0.050354 | 0.11444 | -62.439 | 60.0906 | 60.0815 | 62.1048 | 62.3108 | 122.5342 | 62.2101 | 60.2234
8531.625 | 0.061035 | 0.42084 | -0.77438 | -0.22537 | 0.13992 | -0.28198 | -0.18799 | 60.3149 | -61.9904 | 0.14648 | -62.2513 | 60.1135 | 62.1826 | 62.1094 | 0.061035 | -0.084381 | 0.072632 | 0.29373 | -0.17624 | -0.16235 | 0.050354 | 0.12817 | -62.3932 | 60.0769 | 60.0998 | 62.1094 | 62.3245 | 122.5433 | 62.2375 | 60.2005
8533.3438 | 0.061035 | 0.42404 | -0.78186 | -0.22324 | 0.1474 | -0.29159 | -0.18478 | 60.2875 | -62.0407 | 0.073242 | -62.265 | 60.1593 | 62.146 | 62.0773 | 0.030518 | -0.09079 | 0.057678 | 0.28305 | -0.17197 | -0.16342 | 0.064087 | 0.10071 | -62.3978 | 60.0769 | 60.1181 | 62.0956 | 62.3016 | 122.5845 | 62.2147 | 60.2005
8535.0625 | 0.076294 | 0.40268 | -0.77118 | -0.22644 | 0.13245 | -0.24887 | -0.18372 | 60.2509 | -62.1414 | 0.054932 | -62.3245 | 60.1639 | 62.265 | 62.1872 | 0.061035 | -0.055542 | 0.072632 | 0.29694 | -0.1474 | -0.17731 | 0.041199 | 0.068665 | -62.5168 | 60.1044 | 60.0769 | 62.1735 | 62.352 | 122.6852 | 62.2147 | 60.141
8536.8906 | 0.045776 | 0.44647 | -0.7872 | -0.20828 | 0.13672 | -0.28091 | -0.17944 | 60.347 | -61.9492 | 0.14191 | -62.2375 | 60.1089 | 62.1597 | 62.1002 | 0.076294 | -0.086517 | 0.049133 | 0.29266 | -0.15274 | -0.15808 | 0.10071 | 0.14191 | -62.3566 | 60.0723 | 60.1227 | 62.0728 | 62.3154 | 122.5845 | 62.2101 | 60.1776
8538.6562 | 0.076294 | 0.439 | -0.78293 | -0.22003 | 0.14099 | -0.28519 | -0.18692 | 60.3287 | -62.0224 | 0.10071 | -62.2604 | 60.1364 | 62.1735 | 62.1231 | 0.061035 | -0.083313 | 0.063019 | 0.29159 | -0.1741 | -0.16449 | 0.091553 | 0.13733 | -62.352 | 60.1089 | 60.1135 | 62.1094 | 62.2696 | 122.612 | 62.178 | 60.2051
8540.375 | 0.061035 | 0.4155 | -0.77331 | -0.20828 | 0.13779 | -0.26382 | -0.18265 | 60.3516 | -61.9949 | 0.10529 | -62.2559 | 60.1135 | 62.1826 | 62.1231 | 0.061035 | -0.071564 | 0.067291 | 0.28198 | -0.1474 | -0.16556 | 0.15564 | 0.16022 | -62.3932 | 60.0815 | 60.0632 | 62.1048 | 62.3154 | 122.6349 | 62.1964 | 60.2005
8542.1562 | 0.061035 | 0.4155 | -0.77866 | -0.21255 | 0.14099 | -0.25314 | -0.17517 | 60.2509 | -62.1231 | -0.004578 | -62.3383 | 60.1593 | 62.1964 | 62.1826 | 0.061035 | -0.068359 | 0.063019 | 0.29694 | -0.13886 | -0.16449 | 0.082397 | 0.091553 | -62.4664 | 60.0998 | 60.0815 | 62.1323 | 62.3383 | 122.7036 | 62.2009 | 60.1868
8543.875 | 0.076294 | 0.42511 | -0.76584 | -0.20935 | 0.13779 | -0.25314 | -0.17197 | 60.2325 | -62.1277 | 0.004578 | -62.3337 | 60.141 | 62.2055 | 62.1506 | 0.076294 | -0.069427 | 0.065155 | 0.30121 | -0.15488 | -0.15488 | 0.082397 | 0.082397 | -62.4893 | 60.1044 | 60.0906 | 62.1323 | 62.3291 | 122.7036 | 62.178 | 60.1639
8545.6562 | 0.076294 | 0.4187 | -0.7872 | -0.21042 | 0.13351 | -0.26382 | -0.1741 | 60.26 | -62.1185 | 0.004578 | -62.3474 | 60.1456 | 62.2238 | 62.146 | 0.076294 | -0.069427 | 0.066223 | 0.28519 | -0.14633 | -0.15915 | 0.091553 | 0.10529 | -62.471 | 60.1044 | 60.0906 | 62.1094 | 62.3337 | 122.6944 | 62.1918 | 60.1639
8547.3906 | 0.061035 | 0.43686 | -0.78079 | -0.21576 | 0.11963 | -0.28519 | -0.18265 | 60.2783 | -62.027 | 0.054932 | -62.265 | 60.1227 | 62.1414 | 62.1002 | 0.076294 | -0.089722 | 0.054474 | 0.27344 | -0.15274 | -0.15381 | 0.068665 | 0.10071 | -62.4115 | 60.0815 | 60.1044 | 62.0956 | 62.2971 | 122.5571 | 62.2009 | 60.2188
8549.1562 | 0.061035 | 0.44113 | -0.77866 | -0.21683 | 0.13458 | -0.28305 | -0.19012 | 60.2921 | -62.027 | 0.068665 | -62.2787 | 60.141 | 62.1323 | 62.0911 | 0.045776 | -0.084381 | 0.057678 | 0.29159 | -0.16449 | -0.16235 | 0.054932 | 0.10071 | -62.3978 | 60.1135 | 60.0998 | 62.0956 | 62.3062 | 122.5433 | 62.1918 | 60.2325
8550.9375 | 0.061035 | 0.42831 | -0.77225 | -0.21362 | 0.13458 | -0.25635 | -0.18799 | 60.2463 | -62.0728 | 0.073242 | -62.3108 | 60.1593 | 62.2101 | 62.146 | 0.061035 | -0.0737 | 0.076904 | 0.28519 | -0.15808 | -0.16022 | -0.009155 | 0.013733 | -62.5031 | 60.1227 | 60.0677 | 62.1689 | 62.3291 | 122.5342 | 62.2147 | 60.2325
8552.6562 | 0.045776 | 0.4187 | -0.77438 | -0.22858 | 0.13138 | -0.24887 | -0.17731 | 60.2509 | -62.146 | -0.004578 | -62.3474 | 60.1593 | 62.2238 | 62.1735 | 0.061035 | -0.067291 | 0.059814 | 0.29694 | -0.14206 | -0.16342 | 0.050354 | 0.068665 | -62.5168 | 60.0906 | 60.0952 | 62.1735 | 62.352 | 122.6807 | 62.1735 | 60.1501
8554.3906 | 0.061035 | 0.41122 | -0.77972 | -0.23819 | 0.13672 | -0.27664 | -0.17838 | 60.3012 | -62.0087 | 0.12817 | -62.2604 | 60.1135 | 62.178 | 62.1368 | 0.045776 | -0.081177 | 0.070496 | 0.28839 | -0.1506 | -0.15595 | 0.050354 | 0.086975 | -62.4481 | 60.0998 | 60.0861 | 62.1323 | 62.3108 | 122.5067 | 62.2284 | 60.228
8556.1562 | 0.030518 | 0.44434 | -0.78186 | -0.23071 | 0.14099 | -0.28625 | -0.18692 | 60.2875 | -62.0407 | 0.07782 | -62.2833 | 60.1456 | 62.146 | 62.0773 | 0.061035 | -0.092926 | 0.060883 | 0.28946 | -0.16769 | -0.16663 | 0.059509 | 0.086975 | -62.4069 | 60.1044 | 60.0906 | 62.0819 | 62.2833 | 122.5616 | 62.1964 | 60.2371
8557.8594 | 0.076294 | 0.40802 | -0.77331 | -0.23926 | 0.12924 | -0.24246 | -0.17624 | 60.2371 | -62.1368 | 0.041199 | -62.3245 | 60.1501 | 62.2192 | 62.1689 | 0.076294 | -0.060883 | 0.070496 | 0.28946 | -0.1506 | -0.16022 | 0.009155 | 0.032043 | -62.5259 | 60.1089 | 60.054 | 62.1643 | 62.3611 | 122.6669 | 62.1872 | 60.1547
8559.625 | 0.045776 | 0.4155 | -0.77331 | -0.22003 | 0.14206 | -0.25101 | -0.16129 | 60.2234 | -62.1735 | -0.022888 | -62.3474 | 60.1501 | 62.2238 | 62.1735 | 0.061035 | -0.070496 | 0.071564 | 0.29266 | -0.14313 | -0.16022 | 0.045776 | 0.036621 | -62.5351 | 60.0952 | 60.0906 | 62.1597 | 62.3474 | 122.6669 | 62.2147 | 60.2005
8561.4219 | 0.045776 | 0.42618 | -0.77866 | -0.21896 | 0.12817 | -0.28305 | -0.18051 | 60.26 | -62.0636 | 0.07782 | -62.3062 | 60.1135 | 62.2147 | 62.1414 | 0.045776 | -0.086517 | 0.076904 | 0.28946 | -0.16663 | -0.16449 | -0.013733 | 0.013733 | -62.4985 | 60.1089 | 60.1089 | 62.1368 | 62.3383 | 122.525 | 62.2284 | 60.2097
8563.2031 | 0.076294 | 0.41657 | -0.76797 | -0.2211 | 0.14847 | -0.24353 | -0.16342 | 60.2692 | -62.0911 | 0.073242 | -62.3291 | 60.1501 | 62.2238 | 62.1689 | 0.061035 | -0.065155 | 0.072632 | 0.29694 | -0.15381 | -0.15915 | 0.073242 | 0.091553 | -62.4939 | 60.0723 | 60.0677 | 62.146 | 62.384 | 122.6669 | 62.1964 | 60.1318
8564.9844 | 0.045776 | 0.42725 | -0.77225 | -0.20508 | 0.13992 | -0.27237 | -0.16663 | 60.3058 | -62.0178 | 0.10071 | -62.2559 | 60.1044 | 62.1643 | 62.1231 | 0.061035 | -0.083313 | 0.059814 | 0.28839 | -0.1506 | -0.16663 | 0.13275 | 0.16479 | -62.3978 | 60.0449 | 60.0861 | 62.0956 | 62.2925 | 122.6624 | 62.1826 | 60.1639
8566.7031 | 0.076294 | 0.42618 | -0.7872 | -0.2211 | 0.12817 | -0.27451 | -0.18372 | 60.3058 | -61.9949 | 0.16479 | -62.2467 | 60.0952 | 62.1826 | 62.1094 | 0.045776 | -0.097198 | 0.072632 | 0.28305 | -0.15595 | -0.15915 | 0.068665 | 0.1236 | -62.4023 | 60.0677 | 60.0586 | 62.114 | 62.3016 | 122.5296 | 62.2101 | 60.2234
8568.4375 | 0.076294 | 0.42618 | -0.78934 | -0.23392 | 0.13779 | -0.27771 | -0.18585 | 60.3149 | -61.9858 | 0.1236 | -62.2375 | 60.1364 | 62.1552 | 62.0956 | 0.061035 | -0.091858 | 0.069427 | 0.27878 | -0.17517 | -0.15808 | 0.11902 | 0.14648 | -62.352 | 60.0723 | 60.0677 | 62.114 | 62.2879 | 122.5983 | 62.2238 | 60.2188
8570.2031 | 0.061035 | 0.44434 | -0.7872 | -0.22751 | 0.13138 | -0.27023 | -0.19119 | 60.2966 | -62.027 | 0.07782 | -62.2742 | 60.1456 | 62.1323 | 62.0819 | 0.076294 | -0.086517 | 0.061951 | 0.27985 | -0.15595 | -0.16663 | 0.064087 | 0.09613 | -62.3978 | 60.1044 | 60.0861 | 62.0819 | 62.2833 | 122.5479 | 62.1964 | 60.2463
8572 | 0.076294 | 0.42084 | -0.77011 | -0.22537 | 0.13138 | -0.24033 | -0.16876 | 60.2417 | -62.1185 | 0.032043 | -62.3474 | 60.1181 | 62.2284 | 62.1826 | 0.061035 | -0.066223 | 0.067291 | 0.28305 | -0.14526 | -0.16983 | 0.045776 | 0.064087 | -62.5534 | 60.0815 | 60.0494 | 62.1918 | 62.3795 | 122.644 | 62.2055 | 60.1685
8573.7031 | 0.045776 | 0.42938 | -0.76691 | -0.21576 | 0.13245 | -0.2478 | -0.16342 | 60.1913 | -62.1597 | -0.013733 | -62.3566 | 60.1456 | 62.2375 | 62.1872 | 0.045776 | -0.061951 | 0.075836 | 0.29159 | -0.1474 | -0.16022 | 0.032043 | 0.036621 | -62.5397 | 60.1135 | 60.0815 | 62.178 | 62.3383 | 122.644 | 62.2055 | 60.1456
8575.4844 | 0.061035 | 0.41763 | -0.77972 | -0.23178 | 0.13886 | -0.2478 | -0.17517 | 60.26 | -62.0819 | 0.07782 | -62.3291 | 60.1089 | 62.2284 | 62.1689 | 0.045776 | -0.069427 | 0.066223 | 0.298 | -0.15274 | -0.16556 | 0.054932 | 0.09613 | -62.5076 | 60.0677 | 60.0769 | 62.1689 | 62.352 | 122.6349 | 62.178 | 60.1547
8577.25 | 0.061035 | 0.45075 | -0.784 | -0.22003 | 0.13245 | -0.28091 | -0.17944 | 60.2966 | -61.9949 | 0.073242 | -62.2787 | 60.1273 | 62.1323 | 62.1002 | 0.045776 | -0.093994 | 0.057678 | 0.27878 | -0.15808 | -0.15167 | 0.086975 | 0.11902 | -62.3932 | 60.0952 | 60.0815 | 62.114 | 62.2925 | 122.5204 | 62.2009 | 60.2325
8579.8906 | 0.061035 | 0.44006 | -0.78934 | -0.21683 | 0.14847 | -0.27878 | -0.18158 | 60.3104 | -61.9766 | 0.10071 | -62.2604 | 60.1135 | 62.1552 | 62.0956 | 0.045776 | -0.088654 | 0.060883 | 0.28198 | -0.15488 | -0.16449 | 0.11902 | 0.13733 | -62.4023 | 60.0906 | 60.1135 | 62.0956 | 62.2787 | 122.5342 | 62.178 | 60.2188
8582.0938 | 0.045776 | 0.43793 | -0.78827 | -0.22003 | 0.13565 | -0.27344 | -0.18906 | 60.2692 | -62.0316 | 0.091553 | -62.2833 | 60.1273 | 62.1689 | 62.146 | 0.061035 | -0.083313 | 0.067291 | 0.28412 | -0.16129 | -0.15808 | 0.027466 | 0.027466 | -62.4573 | 60.141 | 60.0952 | 62.1735 | 62.3291 | 122.5296 | 62.2101 | 60.2051
8584.4688 | 0.045776 | 0.41016 | -0.77972 | -0.2211 | 0.13458 | -0.24994 | -0.18051 | 60.2142 | -62.1231 | 0.041199 | -62.3199 | 60.1364 | 62.233 | 62.1643 | 0.061035 | -0.076904 | 0.072632 | 0.29159 | -0.15701 | -0.16342 | 0.032043 | 0.059509 | -62.4985 | 60.1044 | 60.0906 | 62.1735 | 62.352 | 122.6624 | 62.1872 | 60.1364
8586.7656 | 0.045776 | 0.42618 | -0.78186 | -0.2211 | 0.13351 | -0.27023 | -0.16876 | 60.3241 | -61.9949 | 0.10529 | -62.2513 | 60.1181 | 62.1872 | 62.1094 | 0.061035 | -0.088654 | 0.070496 | 0.29373 | -0.16663 | -0.16342 | 0.1236 | 0.16937 | -62.3795 | 60.1135 | 60.0861 | 62.1094 | 62.2833 | 122.612 | 62.1872 | 60.2097
8588.8281 | 0.030518 | 0.41657 | -0.77225 | -0.23285 | 0.13672 | -0.27451 | -0.1741 | 60.3058 | -61.9858 | 0.14648 | -62.2513 | 60.1181 | 62.1689 | 62.114 | 0.061035 | -0.072632 | 0.066223 | 0.298 | -0.17624 | -0.15381 | 0.059509 | 0.11444 | -62.3978 | 60.0998 | 60.0586 | 62.1323 | 62.3154 | 122.525 | 62.2055 | 60.2097
8591.1406 | 0.045776 | 0.41443 | -0.76477 | -0.2243 | 0.13565 | -0.24246 | -0.1709 | 60.2646 | -62.0911 | 0.068665 | -62.3291 | 60.1273 | 62.233 | 62.1964 | 0.061035 | -0.061951 | 0.070496 | 0.2948 | -0.1442 | -0.16769 | 0.068665 | 0.082397 | -62.5305 | 60.0861 | 60.0815 | 62.1735 | 62.3749 | 122.6257 | 62.2101 | 60.1501
8592.9375 | 0.045776 | 0.41443 | -0.77118 | -0.22324 | 0.14206 | -0.25207 | -0.17731 | 60.2142 | -62.1414 | -0.018311 | -62.3428 | 60.1685 | 62.2147 | 62.1414 | 0.091553 | -0.079041 | 0.070496 | 0.30121 | -0.13992 | -0.16129 | 0.045776 | 0.064087 | -62.5122 | 60.1089 | 60.0906 | 62.1735 | 62.3474 | 122.6761 | 62.1643 | 60.1776
8595.0625 | 0.061035 | 0.44113 | -0.784 | -0.22751 | 0.13458 | -0.2948 | -0.18906 | 60.2692 | -62.0087 | 0.064087 | -62.2604 | 60.1135 | 62.1689 | 62.1094 | 0.076294 | -0.09613 | 0.059814 | 0.27878 | -0.16342 | -0.16342 | 0.073242 | 0.091553 | -62.4023 | 60.1227 | 60.0998 | 62.0956 | 62.2833 | 122.5525 | 62.1826 | 60.2509
8598.0625 | 0.076294 | 0.45609 | -0.78827 | -0.22537 | 0.12924 | -0.28839 | -0.18585 | 60.2829 | -62.027 | 0.068665 | -62.2559 | 60.1547 | 62.1506 | 62.0773 | 0.045776 | -0.093994 | 0.057678 | 0.28839 | -0.15915 | -0.16449 | 0.045776 | 0.10071 | -62.3978 | 60.1227 | 60.1135 | 62.0956 | 62.2833 | 122.5754 | 62.1964 | 60.2234
8600.125 | 0.030518 | 0.41443 | -0.78293 | -0.23605 | 0.12817 | -0.26276 | -0.19012 | 60.3104 | -61.9949 | 0.11902 | -62.2604 | 60.1181 | 62.2147 | 62.1277 | 0.045776 | -0.072632 | 0.068359 | 0.27664 | -0.15274 | -0.16769 | 0.032043 | 0.068665 | -62.4527 | 60.1181 | 60.0815 | 62.1414 | 62.3428 | 122.5021 | 62.2147 | 60.1868
8602.1094 | 0.061035 | 0.42831 | -0.76691 | -0.21683 | 0.13565 | -0.25314 | -0.18051 | 60.347 | -62.0041 | 0.11444 | -62.2467 | 60.1044 | 62.1597 | 62.1048 | 0.076294 | -0.076904 | 0.063019 | 0.28732 | -0.15274 | -0.16556 | 0.14191 | 0.18768 | -62.384 | 60.0677 | 60.054 | 62.0956 | 62.2742 | 122.6028 | 62.1964 | 60.1913
8604.1406 | 0.045776 | 0.41443 | -0.77118 | -0.20187 | 0.13565 | -0.24246 | -0.17731 | 60.2554 | -62.1094 | 0.050354 | -62.3474 | 60.1181 | 62.2375 | 62.1643 | 0.045776 | -0.066223 | 0.072632 | 0.30014 | -0.13779 | -0.18051 | 0.041199 | 0.064087 | -62.5214 | 60.0906 | 60.0632 | 62.178 | 62.3749 | 122.6028 | 62.2147 | 60.1547
8606.3594 | 0.061035 | 0.43259 | -0.77545 | -0.23285 | 0.13992 | -0.27451 | -0.18265 | 60.3195 | -61.972 | 0.15564 | -62.2467 | 60.1135 | 62.1597 | 62.1048 | 0.076294 | -0.091858 | 0.061951 | 0.27557 | -0.16342 | -0.16022 | 0.064087 | 0.1236 | -62.4023 | 60.0998 | 60.0952 | 62.146 | 62.3154 | 122.5342 | 62.2055 | 60.2325
8608.2812 | 0.045776 | 0.41336 | -0.77331 | -0.22644 | 0.14526 | -0.25955 | -0.17944 | 60.2234 | -62.1277 | 0.041199 | -62.3199 | 60.141 | 62.2009 | 62.178 | 0.045776 | -0.070496 | 0.059814 | 0.28305 | -0.15595 | -0.16449 | 0.018311 | 0.045776 | -62.4985 | 60.1044 | 60.0815 | 62.1689 | 62.3611 | 122.644 | 62.2009 | 60.1547
8610 | 0.045776 | 0.40482 | -0.76904 | -0.21469 | 0.14633 | -0.24994 | -0.16983 | 60.2646 | -62.0865 | 0.07782 | -62.3154 | 60.1227 | 62.2192 | 62.1414 | 0.076294 | -0.071564 | 0.075836 | 0.29266 | -0.14633 | -0.16556 | 0.059509 | 0.086975 | -62.4847 | 60.0815 | 60.0586 | 62.1735 | 62.3474 | 122.644 | 62.1872 | 60.1273
8611.7812 | 0.076294 | 0.41336 | -0.78186 | -0.22217 | 0.13672 | -0.25421 | -0.17944 | 60.2051 | -62.1643 | -0.013733 | -62.352 | 60.1501 | 62.2147 | 62.1826 | 0.076294 | -0.068359 | 0.064087 | 0.29587 | -0.1474 | -0.15915 | 0.036621 | 0.045776 | -62.5351 | 60.0952 | 60.0998 | 62.1689 | 62.3566 | 122.6395 | 62.178 | 60.1822
8613.5156 | 0.061035 | 0.43152 | -0.79041 | -0.23392 | 0.12604 | -0.28519 | -0.18478 | 60.3149 | -61.9766 | 0.1236 | -62.2375 | 60.1456 | 62.1368 | 62.0865 | 0.061035 | -0.09613 | 0.064087 | 0.28305 | -0.16556 | -0.14633 | 0.10986 | 0.12817 | -62.3291 | 60.0952 | 60.0815 | 62.0956 | 62.3016 | 122.5891 | 62.1918 | 60.2097
8615.2812 | 0.061035 | 0.4422 | -0.79147 | -0.20615 | 0.13672 | -0.28946 | -0.19012 | 60.2783 | -62.0178 | 0.050354 | -62.2696 | 60.1318 | 62.1414 | 62.0773 | 0.061035 | -0.10254 | 0.064087 | 0.29266 | -0.16342 | -0.16342 | 0.068665 | 0.10071 | -62.3886 | 60.0769 | 60.0861 | 62.0956 | 62.2742 | 122.5342 | 62.2101 | 60.2371
8617.0469 | 0.045776 | 0.42725 | -0.77866 | -0.2211 | 0.13458 | -0.28198 | -0.19226 | 60.3149 | -61.9537 | 0.11444 | -62.233 | 60.1456 | 62.146 | 62.0956 | 0.076294 | -0.086517 | 0.067291 | 0.27344 | -0.16876 | -0.16449 | 0.10071 | 0.13275 | -62.3428 | 60.1044 | 60.0494 | 62.1002 | 62.2879 | 122.5891 | 62.2009 | 60.2051
8618.7656 | 0.076294 | 0.42084 | -0.77866 | -0.21683 | 0.12817 | -0.24139 | -0.18265 | 60.2371 | -62.0819 | 0.054932 | -62.3016 | 60.1318 | 62.2284 | 62.1689 | 0.061035 | -0.068359 | 0.067291 | 0.27878 | -0.14847 | -0.17944 | 0.064087 | 0.07782 | -62.4756 | 60.0998 | 60.0586 | 62.1689 | 62.3474 | 122.6761 | 62.2055 | 60.1547
8620.5625 | 0.076294 | 0.42725 | -0.78827 | -0.22858 | 0.13779 | -0.27451 | -0.18478 | 60.3195 | -61.9629 | 0.16479 | -62.2375 | 60.0998 | 62.1552 | 62.0865 | 0.061035 | -0.083313 | 0.064087 | 0.28625 | -0.16983 | -0.16663 | 0.082397 | 0.15106 | -62.3886 | 60.054 | 60.0815 | 62.1002 | 62.2742 | 122.5342 | 62.1964 | 60.2051
8622.2812 | 0.061035 | 0.40268 | -0.77652 | -0.21149 | 0.12817 | -0.24139 | -0.16235 | 60.2097 | -62.1552 | 0.004578 | -62.3657 | 60.1318 | 62.2238 | 62.1597 | 0.061035 | -0.066223 | 0.064087 | 0.29053 | -0.1442 | -0.16235 | 0.013733 | 0.041199 | -62.5671 | 60.1364 | 60.1044 | 62.1643 | 62.3566 | 122.612 | 62.2055 | 60.1593
8624.2812 | 0.045776 | 0.42511 | -0.77545 | -0.2179 | 0.13672 | -0.28732 | -0.17944 | 60.3287 | -61.9354 | 0.14648 | -62.2238 | 60.1089 | 62.1231 | 62.1185 | 0.045776 | -0.10361 | 0.065155 | 0.28732 | -0.16983 | -0.16129 | 0.12817 | 0.16937 | -62.3199 | 60.0815 | 60.0815 | 62.0911 | 62.2787 | 122.5662 | 62.178 | 60.2142
8626.25 | 0.061035 | 0.38452 | -0.79147 | -0.23498 | 0.14633 | -0.23498 | -0.16663 | 60.26 | -62.0819 | 0.073242 | -62.3154 | 60.1273 | 62.2192 | 62.1735 | 0.076294 | -0.067291 | 0.069427 | 0.27557 | -0.14847 | -0.17517 | 0.091553 | 0.091553 | -62.4756 | 60.0723 | 60.0494 | 62.1597 | 62.3749 | 122.6212 | 62.1826 | 60.1318
8628.4844 | 0.061035 | 0.38666 | -0.77438 | -0.23392 | 0.14847 | -0.25421 | -0.17838 | 60.26 | -62.0728 | 0.086975 | -62.3154 | 60.1318 | 62.2101 | 62.1735 | 0.061035 | -0.065155 | 0.071564 | 0.30228 | -0.14954 | -0.1741 | 0.07782 | 0.086975 | -62.5031 | 60.0861 | 60.0677 | 62.178 | 62.352 | 122.6257 | 62.2055 | 60.1273
8630.6875 | 0.076294 | 0.40909 | -0.78186 | -0.23712 | 0.12604 | -0.27237 | -0.18158 | 60.2097 | -62.114 | 0.041199 | -62.3383 | 60.141 | 62.2238 | 62.1552 | 0.045776 | -0.076904 | 0.074768 | 0.28519 | -0.16129 | -0.16769 | 0 | 0.022888 | -62.5168 | 60.0998 | 60.0952 | 62.1597 | 62.352 | 122.5891 | 62.2101 | 60.1639
8632.9531 | 0.061035 | 0.41229 | -0.76904 | -0.21149 | 0.13138 | -0.25207 | -0.17838 | 60.1959 | -62.1643 | -0.018311 | -62.352 | 60.1318 | 62.2147 | 62.1506 | 0.045776 | -0.0737 | 0.070496 | 0.2948 | -0.16022 | -0.15595 | 0.036621 | 0.054932 | -62.5259 | 60.0998 | 60.0952 | 62.1506 | 62.3474 | 122.6532 | 62.146 | 60.173
8635.4688 | 0.045776 | 0.42191 | -0.77438 | -0.22003 | 0.13458 | -0.28412 | -0.18478 | 60.2921 | -61.9812 | 0.10071 | -62.265 | 60.1273 | 62.1414 | 62.1002 | 0.076294 | -0.09613 | 0.067291 | 0.28839 | -0.16342 | -0.16129 | 0.10071 | 0.12817 | -62.3978 | 60.1089 | 60.0952 | 62.0956 | 62.2833 | 122.5388 | 62.2055 | 60.2371
8637.3906 | 0.061035 | 0.42191 | -0.77545 | -0.2179 | 0.16342 | -0.28412 | -0.17838 | 60.2554 | -62.0041 | 0.073242 | -62.265 | 60.1501 | 62.1323 | 62.0728 | 0.061035 | -0.092926 | 0.068359 | 0.27344 | -0.16876 | -0.16556 | 0.068665 | 0.09613 | -62.3932 | 60.0906 | 60.0861 | 62.1002 | 62.2925 | 122.5525 | 62.2055 | 60.2554
8639.4062 | 0.061035 | 0.44113 | -0.77011 | -0.21896 | 0.14313 | -0.2713 | -0.19012 | 60.3241 | -61.9812 | 0.10529 | -62.2696 | 60.1181 | 62.1735 | 62.1414 | 0.045776 | -0.082245 | 0.054474 | 0.2948 | -0.15808 | -0.16769 | 0.13733 | 0.15106 | -62.3749 | 60.0906 | 60.0357 | 62.0819 | 62.3154 | 122.5525 | 62.2101 | 60.2142
8641.3438 | 0.061035 | 0.40588 | -0.76797 | -0.2211 | 0.11856 | -0.24674 | -0.18372 | 60.2234 | -62.1231 | 0.027466 | -62.3291 | 60.1501 | 62.2147 | 62.1597 | 0.061035 | -0.069427 | 0.064087 | 0.29053 | -0.1506 | -0.17197 | 0.018311 | 0.032043 | -62.5168 | 60.1044 | 60.0952 | 62.1735 | 62.3474 | 122.6624 | 62.1918 | 60.1456
8643.2188 | 0.061035 | 0.42725 | -0.76797 | -0.22751 | 0.13351 | -0.25848 | -0.17197 | 60.2188 | -62.1323 | -0.022888 | -62.3291 | 60.1593 | 62.1918 | 62.146 | 0.045776 | -0.070496 | 0.0737 | 0.29907 | -0.14633 | -0.16556 | 0.059509 | 0.064087 | -62.5076 | 60.1227 | 60.0677 | 62.1414 | 62.3337 | 122.6807 | 62.1872 | 60.1593
8644.9375 | 0.076294 | 0.40482 | -0.77225 | -0.22644 | 0.13565 | -0.26916 | -0.16983 | 60.3149 | -61.9812 | 0.10529 | -62.2421 | 60.0815 | 62.1597 | 62.114 | 0.061035 | -0.077972 | 0.063019 | 0.28732 | -0.15701 | -0.16449 | 0.12817 | 0.18768 | -62.3611 | 60.0677 | 60.054 | 62.114 | 62.2971 | 122.612 | 62.1689 | 60.1959
8646.7188 | 0.061035 | 0.41336 | -0.77866 | -0.21576 | 0.13031 | -0.27451 | -0.17731 | 60.3104 | -61.9629 | 0.10071 | -62.2513 | 60.0906 | 62.1414 | 62.1094 | 0.076294 | -0.082245 | 0.064087 | 0.28519 | -0.14847 | -0.1506 | 0.12817 | 0.15564 | -62.3749 | 60.0815 | 60.0769 | 62.1048 | 62.2742 | 122.58 | 62.1689 | 60.2325
8648.5625 | 0.061035 | 0.43472 | -0.78507 | -0.21576 | 0.13672 | -0.27985 | -0.17944 | 60.3058 | -61.972 | 0.09613 | -62.2604 | 60.1181 | 62.1506 | 62.0956 | 0.045776 | -0.092926 | 0.057678 | 0.29266 | -0.15808 | -0.15595 | 0.11902 | 0.15564 | -62.3703 | 60.0815 | 60.0815 | 62.1048 | 62.2696 | 122.5342 | 62.1918 | 60.2463
8651.3906 | 0.061035 | 0.439 | -0.79041 | -0.20187 | 0.13992 | -0.26916 | -0.18158 | 60.3333 | -61.9675 | 0.10529 | -62.2467 | 60.1318 | 62.1552 | 62.114 | 0.076294 | -0.077972 | 0.059814 | 0.27985 | -0.1474 | -0.15808 | 0.13275 | 0.14648 | -62.3795 | 60.0769 | 60.0586 | 62.1002 | 62.2925 | 122.5204 | 62.178 | 60.228
8653.75 | 0.045776 | 0.41977 | -0.77438 | -0.22003 | 0.13565 | -0.25848 | -0.18051 | 60.2829 | -62.059 | 0.041199 | -62.2833 | 60.1501 | 62.1643 | 62.146 | 0.045776 | -0.0737 | 0.069427 | 0.28198 | -0.14954 | -0.15808 | 0.11902 | 0.16937 | -62.4161 | 60.0723 | 60.054 | 62.1048 | 62.3062 | 122.6578 | 62.1552 | 60.1776
8655.6719 | 0.061035 | 0.41122 | -0.76904 | -0.21683 | 0.12497 | -0.25101 | -0.1709 | 60.2554 | -62.0865 | 0.032043 | -62.2971 | 60.1227 | 62.1872 | 62.1277 | 0.061035 | -0.082245 | 0.063019 | 0.28625 | -0.15274 | -0.16022 | 0.12817 | 0.13733 | -62.4298 | 60.0998 | 60.0632 | 62.1231 | 62.3108 | 122.6669 | 62.1735 | 60.173
8657.3906 | 0.076294 | 0.42404 | -0.77759 | -0.24139 | 0.12604 | -0.28198 | -0.18585 | 60.3195 | -61.9537 | 0.14191 | -62.2375 | 60.1273 | 62.146 | 62.0773 | 0.091553 | -0.09613 | 0.072632 | 0.27771 | -0.16022 | -0.15274 | 0.10071 | 0.14648 | -62.3337 | 60.0677 | 60.0677 | 62.0911 | 62.2604 | 122.5708 | 62.2147 | 60.1959
8659.2812 | 0.076294 | 0.44113 | -0.77225 | -0.2211 | 0.13245 | -0.27237 | -0.17944 | 60.2875 | -62.0132 | 0.068665 | -62.2513 | 60.1456 | 62.1552 | 62.0911 | 0.045776 | -0.095062 | 0.058746 | 0.27451 | -0.16663 | -0.15915 | 0.054932 | 0.082397 | -62.3978 | 60.0998 | 60.0769 | 62.0911 | 62.2833 | 122.5433 | 62.1964 | 60.2417
8661.0469 | 0.061035 | 0.42084 | -0.78507 | -0.23178 | 0.13672 | -0.26382 | -0.18585 | 60.3653 | -61.9217 | 0.14191 | -62.2238 | 60.1135 | 62.1368 | 62.1048 | 0.045776 | -0.087585 | 0.066223 | 0.28519 | -0.16342 | -0.16983 | 0.10986 | 0.15106 | -62.352 | 60.0952 | 60.054 | 62.0911 | 62.2879 | 122.5479 | 62.2055 | 60.1868
8662.8438 | 0.076294 | 0.4187 | -0.78186 | -0.22003 | 0.12604 | -0.24246 | -0.17517 | 60.2371 | -62.1414 | -0.013733 | -62.3291 | 60.1639 | 62.1826 | 62.1689 | 0.061035 | -0.060883 | 0.068359 | 0.29373 | -0.14633 | -0.17303 | 0.059509 | 0.041199 | -62.5214 | 60.1089 | 60.0861 | 62.1597 | 62.3566 | 122.644 | 62.1918 | 60.1273
8664.7188 | 0.045776 | 0.4187 | -0.77225 | -0.23392 | 0.12711 | -0.28091 | -0.17838 | 60.2646 | -62.0087 | 0.10529 | -62.2742 | 60.141 | 62.1964 | 62.1323 | 0.076294 | -0.084381 | 0.075836 | 0.27344 | -0.16663 | -0.15701 | 0.032043 | 0.027466 | -62.4619 | 60.1273 | 60.0632 | 62.1643 | 62.3337 | 122.5113 | 62.2284 | 60.2142
8667.2969 | 0.076294 | 0.43152 | -0.78613 | -0.23605 | 0.14313 | -0.27985 | -0.18478 | 60.3516 | -61.9171 | 0.13275 | -62.2284 | 60.1273 | 62.1414 | 62.0956 | 0.061035 | -0.076904 | 0.060883 | 0.29053 | -0.17944 | -0.17838 | 0.14648 | 0.17395 | -62.3199 | 60.0723 | 60.0769 | 62.0956 | 62.2879 | 122.5754 | 62.1872 | 60.2097
8669.0781 | 0.061035 | 0.43366 | -0.79361 | -0.21149 | 0.12497 | -0.26916 | -0.19012 | 60.3012 | -61.9904 | 0.073242 | -62.265 | 60.1456 | 62.1552 | 62.0773 | 0.061035 | -0.077972 | 0.061951 | 0.28412 | -0.15381 | -0.16769 | 0.10071 | 0.10986 | -62.3978 | 60.0906 | 60.0998 | 62.0773 | 62.2833 | 122.525 | 62.1918 | 60.2371
8670.9688 | 0.061035 | 0.43259 | -0.78934 | -0.21896 | 0.14206 | -0.2713 | -0.18158 | 60.3012 | -62.0178 | 0.073242 | -62.2513 | 60.1364 | 62.1735 | 62.0728 | 0.076294 | -0.082245 | 0.05127 | 0.28198 | -0.14954 | -0.15915 | 0.073242 | 0.07782 | -62.3795 | 60.1044 | 60.0906 | 62.1048 | 62.2696 | 122.5525 | 62.178 | 60.2371
8672.8125 | 0.045776 | 0.40802 | -0.78507 | -0.23071 | 0.12711 | -0.26489 | -0.17197 | 60.2234 | -62.0682 | 0.045776 | -62.3154 | 60.1639 | 62.2147 | 62.1735 | 0.045776 | -0.069427 | 0.072632 | 0.28625 | -0.15274 | -0.17624 | 0 | 0.018311 | -62.5076 | 60.1318 | 60.0769 | 62.1826 | 62.3291 | 122.5525 | 62.2055 | 60.1959
8674.5312 | 0.061035 | 0.40588 | -0.77652 | -0.23285 | 0.13672 | -0.2681 | -0.17731 | 60.2234 | -62.0773 | 0.032043 | -62.3245 | 60.1501 | 62.2147 | 62.1643 | 0.061035 | -0.075836 | 0.064087 | 0.29053 | -0.16983 | -0.17624 | -0.004578 | 0.009155 | -62.4802 | 60.1273 | 60.1044 | 62.1506 | 62.3154 | 122.5388 | 62.2192 | 60.2005
8676.25 | 0.076294 | 0.41229 | -0.77438 | -0.23178 | 0.11856 | -0.25848 | -0.17944 | 60.2097 | -62.0773 | 0.050354 | -62.3245 | 60.1685 | 62.1964 | 62.146 | 0.061035 | -0.079041 | 0.083313 | 0.29159 | -0.16022 | -0.16983 | 0.013733 | 0.022888 | -62.4939 | 60.1364 | 60.0861 | 62.146 | 62.3383 | 122.5433 | 62.2009 | 60.1822
8677.9844 | 0.030518 | 0.41443 | -0.76584 | -0.20935 | 0.13351 | -0.2478 | -0.17303 | 60.2325 | -62.0773 | 0.064087 | -62.2971 | 60.1364 | 62.2284 | 62.1689 | 0.076294 | -0.068359 | 0.065155 | 0.2948 | -0.1442 | -0.17731 | 0.054932 | 0.09613 | -62.4893 | 60.0632 | 60.054 | 62.1643 | 62.352 | 122.6532 | 62.1918 | 60.1273
8679.8438 | 0.076294 | 0.41336 | -0.77011 | -0.20935 | 0.13351 | -0.24994 | -0.16342 | 60.173 | -62.1552 | -0.018311 | -62.3566 | 60.1273 | 62.233 | 62.1506 | 0.076294 | -0.074768 | 0.066223 | 0.29373 | -0.1442 | -0.15915 | 0.032043 | 0.054932 | -62.5397 | 60.0952 | 60.0906 | 62.178 | 62.3657 | 122.6166 | 62.1918 | 60.173
8681.6406 | 0.076294 | 0.40482 | -0.76691 | -0.21683 | 0.13351 | -0.25421 | -0.17303 | 60.2234 | -62.0544 | 0.073242 | -62.3016 | 60.1456 | 62.2147 | 62.1643 | 0.045776 | -0.079041 | 0.067291 | 0.27557 | -0.13458 | -0.16022 | 0.091553 | 0.11902 | -62.471 | 60.0952 | 60.0449 | 62.1643 | 62.3657 | 122.6349 | 62.1643 | 60.1501
8683.375 | 0.061035 | 0.43472 | -0.7872 | -0.23285 | 0.12176 | -0.29373 | -0.1741 | 60.3012 | -61.9308 | 0.12817 | -62.2147 | 60.1318 | 62.1414 | 62.1048 | 0.076294 | -0.088654 | 0.072632 | 0.28305 | -0.17517 | -0.15595 | 0.1236 | 0.16479 | -62.3154 | 60.0632 | 60.0677 | 62.1002 | 62.2833 | 122.5891 | 62.1735 | 60.2051
8685.1562 | 0.061035 | 0.41443 | -0.77652 | -0.23712 | 0.12924 | -0.27771 | -0.18158 | 60.2829 | -61.9583 | 0.15106 | -62.2284 | 60.1135 | 62.146 | 62.0911 | 0.061035 | -0.076904 | 0.074768 | 0.28305 | -0.17303 | -0.16556 | 0.059509 | 0.11902 | -62.3886 | 60.0906 | 60.0494 | 62.114 | 62.2925 | 122.5159 | 62.1826 | 60.2188
8686.9375 | 0.061035 | 0.40268 | -0.77866 | -0.23285 | 0.13138 | -0.27023 | -0.19226 | 60.2097 | -62.0682 | 0.054932 | -62.3337 | 60.1593 | 62.2055 | 62.1506 | 0.061035 | -0.076904 | 0.069427 | 0.29907 | -0.16235 | -0.16983 | -0.004578 | 0.004578 | -62.471 | 60.0952 | 60.0998 | 62.1597 | 62.3566 | 122.5342 | 62.2192 | 60.1868
8688.6562 | 0.061035 | 0.41443 | -0.784 | -0.2179 | 0.12711 | -0.27557 | -0.17731 | 60.3012 | -61.9583 | 0.07782 | -62.2559 | 60.0998 | 62.1323 | 62.0911 | 0.076294 | -0.086517 | 0.059814 | 0.27878 | -0.15488 | -0.16449 | 0.10986 | 0.13733 | -62.3703 | 60.0998 | 60.0357 | 62.1002 | 62.2696 | 122.525 | 62.1689 | 60.2463
8690.4531 | 0.061035 | 0.42084 | -0.7872 | -0.23071 | 0.13672 | -0.27985 | -0.18478 | 60.3149 | -61.908 | 0.14648 | -62.2147 | 60.141 | 62.1506 | 62.0911 | 0.045776 | -0.092926 | 0.060883 | 0.28412 | -0.14954 | -0.16449 | 0.086975 | 0.15564 | -62.3245 | 60.0769 | 60.0449 | 62.0956 | 62.2742 | 122.5342 | 62.178 | 60.2142
8692.2188 | 0.061035 | 0.40802 | -0.77545 | -0.22217 | 0.1207 | -0.25528 | -0.18265 | 60.2005 | -62.1002 | 0.027466 | -62.3108 | 60.1593 | 62.2055 | 62.1643 | 0.061035 | -0.074768 | 0.069427 | 0.28412 | -0.15595 | -0.16769 | 0.004578 | 0.027466 | -62.4939 | 60.1227 | 60.0815 | 62.1689 | 62.3428 | 122.5983 | 62.2009 | 60.1776
8694 | 0.076294 | 0.42084 | -0.77118 | -0.21576 | 0.13779 | -0.2446 | -0.16556 | 60.2371 | -62.114 | 0.009155 | -62.3383 | 60.1364 | 62.2101 | 62.178 | 0.061035 | -0.063019 | 0.061951 | 0.298 | -0.13779 | -0.16663 | 0.041199 | 0.059509 | -62.5076 | 60.1181 | 60.0586 | 62.146 | 62.3657 | 122.6074 | 62.1918 | 60.1776
8695.7969 | 0.045776 | 0.43045 | -0.78934 | -0.20401 | 0.13458 | -0.26596 | -0.16769 | 60.3058 | -61.9629 | 0.10529 | -62.233 | 60.1044 | 62.1414 | 62.0773 | 0.076294 | -0.084381 | 0.055542 | 0.29266 | -0.1506 | -0.15808 | 0.13733 | 0.1831 | -62.3611 | 60.0677 | 60.054 | 62.0819 | 62.2925 | 122.5937 | 62.1597 | 60.2142
8697.5781 | 0.061035 | 0.40695 | -0.77331 | -0.23712 | 0.14633 | -0.25314 | -0.1741 | 60.1685 | -62.1506 | -0.032043 | -62.3428 | 60.1501 | 62.2101 | 62.1735 | 0.061035 | -0.068359 | 0.076904 | 0.29159 | -0.15488 | -0.16235 | 0.041199 | 0.041199 | -62.5259 | 60.1044 | 60.0998 | 62.1597 | 62.3566 | 122.6349 | 62.1689 | 60.1776
8699.2812 | 0.076294 | 0.43045 | -0.77545 | -0.24246 | 0.12817 | -0.28198 | -0.18051 | 60.2737 | -61.972 | 0.086975 | -62.2284 | 60.1685 | 62.1277 | 62.0728 | 0.061035 | -0.098267 | 0.069427 | 0.28412 | -0.17838 | -0.1506 | 0.09613 | 0.1236 | -62.3291 | 60.0952 | 60.0815 | 62.0865 | 62.265 | 122.5571 | 62.178 | 60.2097
8701.0781 | 0.061035 | 0.39307 | -0.77972 | -0.21896 | 0.13351 | -0.23712 | -0.1741 | 60.2097 | -62.114 | 0.009155 | -62.3245 | 60.1364 | 62.2238 | 62.1689 | 0.045776 | -0.060883 | 0.067291 | 0.29373 | -0.15274 | -0.1741 | 0.036621 | 0.041199 | -62.5259 | 60.0952 | 60.054 | 62.1414 | 62.3337 | 122.612 | 62.1735 | 60.141
8702.875 | 0.076294 | 0.42191 | -0.7872 | -0.22644 | 0.12924 | -0.28412 | -0.18692 | 60.2554 | -61.9904 | 0.068665 | -62.2375 | 60.1685 | 62.1185 | 62.0865 | 0.061035 | -0.099335 | 0.061951 | 0.28519 | -0.16556 | -0.15595 | 0.050354 | 0.091553 | -62.3566 | 60.1044 | 60.0906 | 62.0773 | 62.2559 | 122.5388 | 62.1826 | 60.228
8704.5938 | 0.061035 | 0.43152 | -0.77118 | -0.20187 | 0.12817 | -0.26596 | -0.18265 | 60.2829 | -61.9949 | 0.059509 | -62.2375 | 60.1364 | 62.1643 | 62.1048 | 0.061035 | -0.091858 | 0.061951 | 0.28732 | -0.13886 | -0.17517 | 0.13275 | 0.16479 | -62.3703 | 60.0815 | 60.0403 | 62.0819 | 62.2742 | 122.6486 | 62.1643 | 60.1959
8706.3125 | 0.076294 | 0.43045 | -0.77545 | -0.23605 | 0.13992 | -0.2713 | -0.19333 | 60.2737 | -62.0087 | 0.064087 | -62.2559 | 60.1501 | 62.1277 | 62.0682 | 0.061035 | -0.087585 | 0.067291 | 0.29159 | -0.16556 | -0.16663 | 0.068665 | 0.10529 | -62.3749 | 60.1181 | 60.0998 | 62.0911 | 62.2742 | 122.5388 | 62.1872 | 60.2417
8708.0156 | 0.061035 | 0.40268 | -0.77545 | -0.21683 | 0.11963 | -0.2446 | -0.17944 | 60.26 | -62.0544 | 0.07782 | -62.3016 | 60.1273 | 62.2055 | 62.146 | 0.061035 | -0.061951 | 0.065155 | 0.2948 | -0.13779 | -0.17303 | 0.073242 | 0.07782 | -62.4802 | 60.1044 | 60.0403 | 62.1597 | 62.352 | 122.6532 | 62.1643 | 60.1501
8709.8125 | 0.061035 | 0.41229 | -0.77438 | -0.22751 | 0.13779 | -0.25848 | -0.17197 | 60.2417 | -62.0819 | 0.045776 | -62.3108 | 60.1501 | 62.2101 | 62.1597 | 0.076294 | -0.070496 | 0.072632 | 0.298 | -0.15488 | -0.16769 | 0.045776 | 0.086975 | -62.4527 | 60.1273 | 60.0998 | 62.1552 | 62.352 | 122.6532 | 62.1506 | 60.1639
8711.6094 | 0.061035 | 0.41977 | -0.77545 | -0.22964 | 0.12711 | -0.2713 | -0.17838 | 60.2097 | -62.0865 | 0.032043 | -62.3108 | 60.1364 | 62.2192 | 62.1277 | 0.061035 | -0.085449 | 0.074768 | 0.28732 | -0.15808 | -0.16769 | 0 | 0.027466 | -62.4985 | 60.1273 | 60.0952 | 62.1552 | 62.3062 | 122.6166 | 62.1643 | 60.1685
8713.4062 | 0.061035 | 0.42725 | -0.78507 | -0.23819 | 0.14313 | -0.28412 | -0.17303 | 60.2875 | -61.9995 | 0.064087 | -62.2513 | 60.1685 | 62.1414 | 62.0728 | 0.061035 | -0.093994 | 0.072632 | 0.29373 | -0.17731 | -0.16129 | 0.07782 | 0.10986 | -62.3703 | 60.1044 | 60.0906 | 62.0728 | 62.2375 | 122.5159 | 62.146 | 60.2371
8715.1875 | 0.061035 | 0.4155 | -0.784 | -0.23392 | 0.13565 | -0.27771 | -0.18265 | 60.3195 | -61.9446 | 0.13733 | -62.2147 | 60.1364 | 62.146 | 62.0819 | 0.076294 | -0.087585 | 0.070496 | 0.27557 | -0.16129 | -0.17197 | 0.054932 | 0.10071 | -62.384 | 60.1181 | 60.0861 | 62.1414 | 62.265 | 122.5021 | 62.1918 | 60.2234
8716.9688 | 0.076294 | 0.42297 | -0.77331 | -0.22217 | 0.14206 | -0.26916 | -0.18478 | 60.3333 | -61.94 | 0.10529 | -62.233 | 60.1135 | 62.1231 | 62.059 | 0.091553 | -0.093994 | 0.066223 | 0.29159 | -0.15381 | -0.17303 | 0.13275 | 0.16937 | -62.352 | 60.1044 | 60.0861 | 62.0911 | 62.2513 | 122.5479 | 62.1597 | 60.2554
8718.7031 | 0.061035 | 0.41657 | -0.76904 | -0.2179 | 0.11963 | -0.25528 | -0.16663 | 60.3012 | -62.0087 | 0.073242 | -62.233 | 60.1501 | 62.1597 | 62.1094 | 0.045776 | -0.080109 | 0.066223 | 0.29053 | -0.15167 | -0.16983 | 0.14191 | 0.17395 | -62.3657 | 60.1135 | 60.0632 | 62.0956 | 62.265 | 122.6532 | 62.1277 | 60.1776
8720.5 | 0.076294 | 0.40802 | -0.77652 | -0.23071 | 0.13672 | -0.25528 | -0.17303 | 60.2737 | -62.0453 | 0.068665 | -62.2787 | 60.1593 | 62.2009 | 62.1277 | 0.045776 | -0.066223 | 0.058746 | 0.30228 | -0.15595 | -0.17303 | 0.059509 | 0.086975 | -62.4664 | 60.0952 | 60.0723 | 62.1368 | 62.352 | 122.644 | 62.178 | 60.1501
8722.2969 | 0.061035 | 0.41016 | -0.77972 | -0.22324 | 0.12604 | -0.2681 | -0.18051 | 60.2188 | -62.0819 | 0.036621 | -62.2971 | 60.1547 | 62.2009 | 62.1552 | 0.061035 | -0.0737 | 0.060883 | 0.28625 | -0.1474 | -0.16235 | 0.004578 | 0.041199 | -62.471 | 60.1089 | 60.0952 | 62.1277 | 62.352 | 122.6532 | 62.1552 | 60.1685
8724.0781 | 0.061035 | 0.44006 | -0.7872 | -0.21576 | 0.13138 | -0.28412 | -0.17197 | 60.2921 | -61.972 | 0.068665 | -62.2284 | 60.1501 | 62.1185 | 62.0499 | 0.076294 | -0.092926 | 0.054474 | 0.27771 | -0.14954 | -0.15808 | 0.10071 | 0.11444 | -62.3428 | 60.1135 | 60.1227 | 62.0544 | 62.233 | 122.5204 | 62.1414 | 60.2554
8725.875 | 0.061035 | 0.42297 | -0.77972 | -0.2446 | 0.13245 | -0.27771 | -0.18372 | 60.2875 | -61.9812 | 0.059509 | -62.2375 | 60.1776 | 62.1094 | 62.0682 | 0.061035 | -0.086517 | 0.069427 | 0.28412 | -0.17197 | -0.16983 | 0.073242 | 0.10529 | -62.3657 | 60.141 | 60.1089 | 62.0728 | 62.2467 | 122.5204 | 62.146 | 60.2417
8727.6094 | 0.076294 | 0.42191 | -0.78507 | -0.24139 | 0.13351 | -0.27344 | -0.18799 | 60.3516 | -61.9034 | 0.15564 | -62.1872 | 60.1593 | 62.1094 | 62.0819 | 0.061035 | -0.095062 | 0.069427 | 0.28412 | -0.17303 | -0.17197 | 0.11444 | 0.15106 | -62.3108 | 60.1089 | 60.0952 | 62.0728 | 62.233 | 122.5388 | 62.178 | 60.2417
8729.3906 | 0.061035 | 0.43366 | -0.78079 | -0.19653 | 0.12711 | -0.25314 | -0.18692 | 60.3516 | -61.94 | 0.10986 | -62.2284 | 60.1273 | 62.114 | 62.0544 | 0.076294 | -0.089722 | 0.058746 | 0.29053 | -0.15915 | -0.16663 | 0.14191 | 0.15106 | -62.3383 | 60.1181 | 60.0952 | 62.0773 | 62.265 | 122.5479 | 62.1597 | 60.2371
8731.0938 | 0.061035 | 0.42191 | -0.78613 | -0.20935 | 0.13565 | -0.2478 | -0.16983 | 60.2554 | -62.0682 | -0.004578 | -62.2971 | 60.1913 | 62.1552 | 62.1414 | 0.061035 | -0.074768 | 0.068359 | 0.29907 | -0.13779 | -0.16876 | 0.086975 | 0.073242 | -62.4435 | 60.1547 | 60.1044 | 62.1002 | 62.2696 | 122.6624 | 62.1231 | 60.1776
8732.8906 | 0.076294 | 0.39414 | -0.77011 | -0.22217 | 0.13779 | -0.24674 | -0.16449 | 60.2692 | -62.0499 | 0.082397 | -62.2604 | 60.141 | 62.1643 | 62.146 | 0.061035 | -0.071564 | 0.063019 | 0.29373 | -0.1506 | -0.16769 | 0.068665 | 0.10071 | -62.4481 | 60.1181 | 60.1044 | 62.146 | 62.3016 | 122.644 | 62.1368 | 60.1593
8734.5938 | 0.061035 | 0.44006 | -0.77866 | -0.23498 | 0.1442 | -0.29694 | -0.18372 | 60.3195 | -61.9629 | 0.073242 | -62.2238 | 60.1639 | 62.1002 | 62.0453 | 0.091553 | -0.087585 | 0.060883 | 0.28305 | -0.16876 | -0.15381 | 0.10529 | 0.11444 | -62.352 | 60.1089 | 60.1456 | 62.0728 | 62.2238 | 122.5113 | 62.146 | 60.2554
8736.375 | 0.076294 | 0.41336 | -0.7872 | -0.21255 | 0.1442 | -0.25742 | -0.18478 | 60.2463 | -62.0544 | -0.004578 | -62.2787 | 60.1913 | 62.1277 | 62.1231 | 0.061035 | -0.075836 | 0.059814 | 0.30014 | -0.14526 | -0.16876 | 0.068665 | 0.091553 | -62.439 | 60.1181 | 60.1044 | 62.0911 | 62.2833 | 122.6624 | 62.114 | 60.2005
8738.1406 | 0.076294 | 0.44434 | -0.79041 | -0.21149 | 0.13886 | -0.28839 | -0.1741 | 60.3012 | -61.9308 | 0.091553 | -62.1918 | 60.1868 | 62.1002 | 62.0361 | 0.076294 | -0.093994 | 0.055542 | 0.27771 | -0.1709 | -0.16022 | 0.10071 | 0.12817 | -62.3062 | 60.1181 | 60.1318 | 62.0407 | 62.2513 | 122.5662 | 62.1323 | 60.2417
8739.9219 | 0.061035 | 0.40375 | -0.7637 | -0.23285 | 0.13992 | -0.24139 | -0.1709 | 60.3058 | -62.0316 | 0.082397 | -62.2604 | 60.1593 | 62.1643 | 62.1277 | 0.076294 | -0.066223 | 0.075836 | 0.28732 | -0.15701 | -0.1741 | 0.054932 | 0.07782 | -62.4344 | 60.1273 | 60.0906 | 62.1323 | 62.3291 | 122.6349 | 62.1368 | 60.2097
8741.6406 | 0.045776 | 0.40375 | -0.76263 | -0.22858 | 0.13992 | -0.24994 | -0.17731 | 60.2783 | -62.0361 | 0.064087 | -62.265 | 60.173 | 62.1964 | 62.1323 | 0.061035 | -0.076904 | 0.080109 | 0.2948 | -0.15595 | -0.16556 | 0.045776 | 0.091553 | -62.4344 | 60.1273 | 60.1273 | 62.1323 | 62.3062 | 122.6532 | 62.1231 | 60.1593
8743.4219 | 0.030518 | 0.41122 | -0.76477 | -0.20401 | 0.14099 | -0.25848 | -0.17731 | 60.2417 | -62.0865 | -0.009155 | -62.2833 | 60.1913 | 62.1506 | 62.1368 | 0.076294 | -0.068359 | 0.060883 | 0.28946 | -0.16342 | -0.15915 | 0.059509 | 0.073242 | -62.4481 | 60.1364 | 60.1456 | 62.1185 | 62.2971 | 122.644 | 62.1231 | 60.2097
8745.125 | 0.076294 | 0.41443 | -0.784 | -0.2179 | 0.13672 | -0.25314 | -0.16983 | 60.2188 | -62.0911 | -0.022888 | -62.2971 | 60.1685 | 62.1597 | 62.146 | 0.076294 | -0.068359 | 0.065155 | 0.29266 | -0.1474 | -0.1474 | 0.041199 | 0.064087 | -62.471 | 60.1456 | 60.1181 | 62.1094 | 62.3062 | 122.6349 | 62.1185 | 60.2325
8746.9219 | 0.076294 | 0.40909 | -0.78079 | -0.22537 | 0.11002 | -0.26276 | -0.16235 | 60.2142 | -62.1002 | -0.013733 | -62.3016 | 60.1822 | 62.1552 | 62.1414 | 0.076294 | -0.080109 | 0.077972 | 0.29159 | -0.1474 | -0.16556 | 0.027466 | 0.041199 | -62.471 | 60.1364 | 60.1364 | 62.1231 | 62.2879 | 122.6303 | 62.1368 | 60.2097
8748.7031 | 0.061035 | 0.43366 | -0.77331 | -0.22644 | 0.13245 | -0.29373 | -0.18585 | 60.2783 | -61.9492 | 0.068665 | -62.2147 | 60.2051 | 62.1094 | 62.0316 | 0.030518 | -0.10468 | 0.058746 | 0.29266 | -0.17731 | -0.14847 | 0.054932 | 0.10986 | -62.3154 | 60.1227 | 60.1501 | 62.0865 | 62.2421 | 122.5662 | 62.1368 | 60.2646
8750.4844 | 0.045776 | 0.40482 | -0.77438 | -0.24353 | 0.14206 | -0.26703 | -0.18585 | 60.2966 | -61.9217 | 0.12817 | -62.1872 | 60.1639 | 62.1231 | 62.059 | 0.045776 | -0.086517 | 0.077972 | 0.28519 | -0.16449 | -0.1709 | 0.050354 | 0.091553 | -62.3703 | 60.1273 | 60.1227 | 62.0956 | 62.2879 | 122.4884 | 62.1689 | 60.2646
8752.2656 | 0.076294 | 0.44434 | -0.78827 | -0.21042 | 0.14206 | -0.27985 | -0.18585 | 60.3287 | -61.908 | 0.086975 | -62.1918 | 60.1547 | 62.0636 | 62.0361 | 0.045776 | -0.09079 | 0.057678 | 0.29373 | -0.15488 | -0.15488 | 0.10529 | 0.13275 | -62.3245 | 60.1593 | 60.1364 | 62.0728 | 62.2467 | 122.5113 | 62.1506 | 60.2966
8753.9688 | 0.045776 | 0.41763 | -0.78293 | -0.21469 | 0.12176 | -0.24887 | -0.18372 | 60.26 | -62.0224 | 0.022888 | -62.2467 | 60.1913 | 62.1552 | 62.0728 | 0.061035 | -0.074768 | 0.061951 | 0.28839 | -0.14099 | -0.16983 | 0.10529 | 0.11444 | -62.3611 | 60.1547 | 60.0906 | 62.0636 | 62.233 | 122.6669 | 62.1094 | 60.2188
8755.7656 | 0.045776 | 0.41443 | -0.78186 | -0.22644 | 0.14206 | -0.25742 | -0.16342 | 60.2737 | -62.0178 | 0.073242 | -62.2375 | 60.1913 | 62.1552 | 62.1094 | 0.045776 | -0.077972 | 0.061951 | 0.29159 | -0.14099 | -0.17303 | 0.059509 | 0.082397 | -62.4115 | 60.1547 | 60.1227 | 62.0956 | 62.3199 | 122.6303 | 62.1231 | 60.1959
8757.5781 | 0.076294 | 0.42404 | -0.784 | -0.23926 | 0.13138 | -0.28198 | -0.17731 | 60.3516 | -61.8668 | 0.16937 | -62.1597 | 60.2005 | 62.0865 | 62.0316 | 0.061035 | -0.089722 | 0.074768 | 0.28625 | -0.1709 | -0.17197 | 0.10071 | 0.16022 | -62.2833 | 60.1273 | 60.1089 | 62.0316 | 62.2238 | 122.5342 | 62.1277 | 60.2646
8759.2969 | 0.061035 | 0.42725 | -0.77652 | -0.2179 | 0.1442 | -0.25742 | -0.16663 | 60.3149 | -61.9766 | 0.050354 | -62.2284 | 60.1959 | 62.1048 | 62.059 | 0.091553 | -0.080109 | 0.068359 | 0.27771 | -0.14313 | -0.1741 | 0.13275 | 0.15106 | -62.3428 | 60.1501 | 60.1227 | 62.0499 | 62.2375 | 122.6532 | 62.0911 | 60.2234
8761.0625 | 0.045776 | 0.43259 | -0.77545 | -0.21255 | 0.13458 | -0.28198 | -0.18799 | 60.3561 | -61.8896 | 0.10529 | -62.178 | 60.2005 | 62.0819 | 62.0178 | 0.061035 | -0.097198 | 0.066223 | 0.27985 | -0.15915 | -0.14954 | 0.10986 | 0.13275 | -62.3154 | 60.1547 | 60.1501 | 62.0316 | 62.2284 | 122.5021 | 62.114 | 60.3149
8762.875 | 0.030518 | 0.41336 | -0.79575 | -0.23178 | 0.13886 | -0.27878 | -0.17838 | 60.379 | -61.8668 | 0.13733 | -62.1368 | 60.2097 | 62.0865 | 62.0224 | 0.030518 | -0.095062 | 0.075836 | 0.28625 | -0.18265 | -0.16769 | 0.13733 | 0.15564 | -62.2421 | 60.1547 | 60.1135 | 62.0132 | 62.1918 | 122.5525 | 62.0911 | 60.2417
8764.5938 | 0.061035 | 0.40695 | -0.77331 | -0.21042 | 0.12711 | -0.24674 | -0.18051 | 60.2966 | -62.0087 | 0.073242 | -62.233 | 60.2234 | 62.1368 | 62.0865 | 0.045776 | -0.072632 | 0.053406 | 0.28732 | -0.13672 | -0.18478 | 0.054932 | 0.064087 | -62.4069 | 60.1501 | 60.1135 | 62.0865 | 62.2604 | 122.6303 | 62.1185 | 60.2005
8766.375 | 0.091553 | 0.40588 | -0.77438 | -0.21576 | 0.13992 | -0.25421 | -0.1709 | 60.2554 | -62.0316 | -0.013733 | -62.2467 | 60.2234 | 62.146 | 62.0682 | 0.076294 | -0.080109 | 0.060883 | 0.27985 | -0.1474 | -0.15595 | 0.064087 | 0.050354 | -62.4298 | 60.173 | 60.141 | 62.0728 | 62.2421 | 122.6578 | 62.0911 | 60.2417
8768.1562 | 0.061035 | 0.42404 | -0.784 | -0.22324 | 0.12497 | -0.28091 | -0.17517 | 60.3882 | -61.7981 | 0.16479 | -62.1185 | 60.1913 | 62.0636 | 62.0132 | 0.061035 | -0.095062 | 0.059814 | 0.28519 | -0.16769 | -0.15701 | 0.09613 | 0.16479 | -62.2559 | 60.1501 | 60.141 | 62.0224 | 62.2101 | 122.5433 | 62.1048 | 60.2829
8769.875 | 0.061035 | 0.41657 | -0.77545 | -0.22537 | 0.12283 | -0.25421 | -0.17731 | 60.26 | -62.0407 | -0.009155 | -62.2604 | 60.2325 | 62.1231 | 62.0636 | 0.045776 | -0.079041 | 0.063019 | 0.28198 | -0.14313 | -0.16556 | 0.036621 | 0.059509 | -62.4161 | 60.1913 | 60.1593 | 62.0682 | 62.2421 | 122.6532 | 62.0636 | 60.2371
8771.6562 | 0.061035 | 0.39307 | -0.77438 | -0.21576 | 0.14206 | -0.25101 | -0.16769 | 60.2692 | -62.0132 | 0.018311 | -62.2421 | 60.2234 | 62.1231 | 62.0773 | 0.061035 | -0.067291 | 0.059814 | 0.27771 | -0.13992 | -0.16876 | 0.027466 | 0.050354 | -62.4435 | 60.2005 | 60.1456 | 62.0636 | 62.2742 | 122.6028 | 62.0773 | 60.2554
8773.4375 | 0.015259 | 0.40482 | -0.77866 | -0.22644 | 0.14099 | -0.25635 | -0.17197 | 60.2966 | -61.9629 | 0.07782 | -62.2009 | 60.228 | 62.1323 | 62.0682 | 0.061035 | -0.076904 | 0.070496 | 0.28412 | -0.14847 | -0.16449 | 0.036621 | 0.09613 | -62.3703 | 60.2051 | 60.1501 | 62.0728 | 62.2742 | 122.6486 | 62.0865 | 60.2142
8775.1562 | 0.076294 | 0.41016 | -0.78079 | -0.25101 | 0.13138 | -0.26916 | -0.18585 | 60.2692 | -61.9995 | 0.054932 | -62.2055 | 60.2371 | 62.1094 | 62.0682 | 0.061035 | -0.069427 | 0.0737 | 0.29159 | -0.15808 | -0.15701 | 0.004578 | 0.036621 | -62.4069 | 60.1639 | 60.1822 | 62.0682 | 62.233 | 122.6349 | 62.0728 | 60.228
8776.9375 | 0.045776 | 0.41016 | -0.76477 | -0.24674 | 0.13138 | -0.29587 | -0.19333 | 60.3561 | -61.8759 | 0.10529 | -62.1231 | 60.2554 | 62.0178 | 61.9949 | 0.045776 | -0.10468 | 0.064087 | 0.298 | -0.17517 | -0.16235 | 0.086975 | 0.13733 | -62.2467 | 60.1822 | 60.1868 | 61.9583 | 62.1643 | 122.5616 | 62.0453 | 60.3241
8778.6719 | 0.061035 | 0.40802 | -0.78293 | -0.24033 | 0.12711 | -0.27557 | -0.18372 | 60.4111 | -61.7889 | 0.16479 | -62.0956 | 60.2371 | 62.0544 | 61.9812 | 0.061035 | -0.089722 | 0.067291 | 0.28305 | -0.17517 | -0.18478 | 0.10529 | 0.16937 | -62.2284 | 60.1913 | 60.173 | 61.9858 | 62.1689 | 122.5525 | 62.0911 | 60.2829
8780.4688 | 0.061035 | 0.41977 | -0.76904 | -0.21149 | 0.12817 | -0.26489 | -0.17838 | 60.4294 | -61.8622 | 0.11444 | -62.1323 | 60.2234 | 62.0178 | 61.9904 | 0.045776 | -0.0737 | 0.057678 | 0.28625 | -0.15167 | -0.18051 | 0.16022 | 0.18768 | -62.2559 | 60.1913 | 60.1639 | 62.0224 | 62.178 | 122.6074 | 62.1002 | 60.2875
8782.1875 | 0.061035 | 0.40588 | -0.76584 | -0.22537 | 0.12924 | -0.25101 | -0.17303 | 60.2875 | -61.972 | 0.045776 | -62.2147 | 60.2692 | 62.0911 | 62.0636 | 0.045776 | -0.068359 | 0.071564 | 0.27771 | -0.14526 | -0.1709 | 0.018311 | 0.022888 | -62.4069 | 60.2371 | 60.1913 | 62.0544 | 62.2238 | 122.6028 | 62.0773 | 60.2554
8783.9688 | 0.076294 | 0.40909 | -0.77438 | -0.22537 | 0.12497 | -0.27771 | -0.18478 | 60.3973 | -61.8347 | 0.11444 | -62.114 | 60.2234 | 62.0361 | 61.9812 | 0.045776 | -0.089722 | 0.065155 | 0.28091 | -0.14847 | -0.16663 | 0.14191 | 0.16937 | -62.2604 | 60.1776 | 60.1959 | 61.9675 | 62.178 | 122.5204 | 62.0911 | 60.3333
8785.7656 | 0.061035 | 0.41657 | -0.78507 | -0.20081 | 0.13351 | -0.24567 | -0.17303 | 60.2921 | -62.0178 | 0.013733 | -62.2238 | 60.2737 | 62.0911 | 62.027 | 0.045776 | -0.065155 | 0.067291 | 0.29694 | -0.13886 | -0.16983 | 0.032043 | 0.050354 | -62.4344 | 60.2325 | 60.1868 | 62.0178 | 62.2147 | 122.5983 | 62.0499 | 60.2783
8787.5781 | 0.045776 | 0.41977 | -0.76691 | -0.21683 | 0.14099 | -0.25848 | -0.16556 | 60.3149 | -61.9537 | 0 | -62.1872 | 60.2646 | 62.0773 | 62.0316 | 0.045776 | -0.081177 | 0.069427 | 0.28305 | -0.1506 | -0.16769 | 0.091553 | 0.10071 | -62.3199 | 60.2142 | 60.173 | 61.9949 | 62.178 | 122.6669 | 62.0224 | 60.2921
8789.2812 | 0.045776 | 0.44327 | -0.78827 | -0.21896 | 0.12604 | -0.29907 | -0.18585 | 60.3607 | -61.8668 | 0.073242 | -62.1094 | 60.2783 | 62.0087 | 61.9492 | 0.061035 | -0.088654 | 0.058746 | 0.27771 | -0.16983 | -0.16449 | 0.054932 | 0.11902 | -62.2467 | 60.2142 | 60.228 | 61.9583 | 62.1506 | 122.5571 | 62.0224 | 60.347
8791.0625 | 0.076294 | 0.42511 | -0.78079 | -0.23819 | 0.13992 | -0.26596 | -0.18585 | 60.4248 | -61.8073 | 0.15564 | -62.0911 | 60.2921 | 61.9766 | 61.9537 | 0.061035 | -0.089722 | 0.067291 | 0.29266 | -0.16876 | -0.1709 | 0.07782 | 0.11902 | -62.2375 | 60.2417 | 60.2142 | 61.9537 | 62.1277 | 122.4884 | 62.0361 | 60.3424
8792.875 | 0.045776 | 0.40375 | -0.76797 | -0.2243 | 0.14206 | -0.23605 | -0.17197 | 60.3973 | -61.9034 | 0.09613 | -62.1597 | 60.2783 | 62.0728 | 62.0132 | 0.076294 | -0.069427 | 0.075836 | 0.298 | -0.15167 | -0.17517 | 0.086975 | 0.11444 | -62.3245 | 60.2417 | 60.2142 | 62.0178 | 62.1689 | 122.5937 | 62.0316 | 60.2692
8794.6562 | 0.076294 | 0.41229 | -0.78186 | -0.22964 | 0.12817 | -0.27023 | -0.18158 | 60.4431 | -61.8027 | 0.10986 | -62.0956 | 60.2692 | 62.0041 | 61.9263 | 0.061035 | -0.095062 | 0.059814 | 0.2948 | -0.16663 | -0.17303 | 0.13733 | 0.15564 | -62.1964 | 60.228 | 60.2005 | 61.9354 | 62.1414 | 122.5388 | 62.0224 | 60.3882
8796.4531 | 0.061035 | 0.4187 | -0.78186 | -0.21469 | 0.13031 | -0.2446 | -0.17624 | 60.3333 | -61.9675 | -0.022888 | -62.1872 | 60.3195 | 62.027 | 61.9995 | 0.061035 | -0.076904 | 0.05661 | 0.28839 | -0.13886 | -0.17303 | 0.045776 | 0.036621 | -62.3703 | 60.2554 | 60.2325 | 62.0041 | 62.178 | 122.6212 | 62.027 | 60.3058
8798.2344 | 0.061035 | 0.40802 | -0.77545 | -0.24246 | 0.13031 | -0.27557 | -0.18372 | 60.379 | -61.8851 | 0.068665 | -62.1506 | 60.3516 | 62.0087 | 61.9766 | 0.061035 | -0.084381 | 0.081177 | 0.28946 | -0.16235 | -0.17517 | 0.004578 | 0.032043 | -62.3108 | 60.2875 | 60.3195 | 61.9949 | 62.1231 | 122.5433 | 62.0178 | 60.3516
8799.9375 | 0.061035 | 0.40375 | -0.76797 | -0.22003 | 0.12497 | -0.25421 | -0.17517 | 60.3653 | -61.9354 | -0.018311 | -62.1414 | 60.3378 | 61.9949 | 61.9446 | 0.076294 | -0.070496 | 0.068359 | 0.29694 | -0.13672 | -0.16449 | 0.045776 | 0.050354 | -62.3383 | 60.2921 | 60.2783 | 61.972 | 62.1597 | 122.5891 | 61.9949 | 60.3653
8801.7344 | 0.045776 | 0.41016 | -0.77545 | -0.21683 | 0.14206 | -0.25635 | -0.17517 | 60.3973 | -61.8622 | 0.064087 | -62.1002 | 60.3424 | 61.9949 | 61.972 | 0.076294 | -0.079041 | 0.059814 | 0.29159 | -0.14633 | -0.16556 | 0.050354 | 0.07782 | -62.265 | 60.3104 | 60.2692 | 61.9492 | 62.1231 | 122.6349 | 61.9492 | 60.3561
8803.4688 | 0.061035 | 0.42297 | -0.77866 | -0.23926 | 0.12711 | -0.30228 | -0.18692 | 60.4752 | -61.7432 | 0.10071 | -62.0224 | 60.3378 | 61.908 | 61.8896 | 0.045776 | -0.09613 | 0.066223 | 0.28946 | -0.17731 | -0.16022 | 0.10071 | 0.15106 | -62.1048 | 60.3104 | 60.3195 | 61.8759 | 62.059 | 122.5525 | 61.9446 | 60.4431
8805.2344 | 0.061035 | 0.38238 | -0.76157 | -0.24994 | 0.1207 | -0.2446 | -0.17197 | 60.4202 | -61.8942 | -0.022888 | -62.1002 | 60.3653 | 61.972 | 61.9354 | 0.061035 | -0.0737 | 0.069427 | 0.30868 | -0.15808 | -0.17517 | 0.068665 | 0.064087 | -62.2421 | 60.3333 | 60.2966 | 61.9308 | 62.1048 | 122.6349 | 61.9308 | 60.3928
8807.0312 | 0.076294 | 0.43259 | -0.77118 | -0.20828 | 0.13458 | -0.27451 | -0.1741 | 60.498 | -61.7249 | 0.10071 | -62.0041 | 60.347 | 61.9308 | 61.8576 | 0.061035 | -0.088654 | 0.055542 | 0.27985 | -0.1474 | -0.15488 | 0.11444 | 0.15106 | -62.1414 | 60.3149 | 60.2737 | 61.8759 | 62.0407 | 122.5159 | 61.94 | 60.4614
8808.75 | 0.045776 | 0.43152 | -0.78934 | -0.21576 | 0.12924 | -0.29587 | -0.18692 | 60.5072 | -61.7294 | 0.09613 | -61.9904 | 60.3745 | 61.908 | 61.8439 | 0.076294 | -0.1004 | 0.059814 | 0.28091 | -0.16449 | -0.16663 | 0.10529 | 0.12817 | -62.0956 | 60.3287 | 60.3241 | 61.853 | 62.0407 | 122.5571 | 61.908 | 60.4294
8810.5469 | 0.045776 | 0.4187 | -0.79041 | -0.23071 | 0.13138 | -0.28412 | -0.18799 | 60.5438 | -61.7111 | 0.15106 | -61.972 | 60.4019 | 61.8713 | 61.821 | 0.061035 | -0.091858 | 0.063019 | 0.27771 | -0.16769 | -0.16663 | 0.11902 | 0.13733 | -62.0773 | 60.3149 | 60.3104 | 61.8393 | 62.0361 | 122.5708 | 61.9125 | 60.434
8812.2656 | 0.061035 | 0.40268 | -0.76904 | -0.2211 | 0.12817 | -0.23285 | -0.16235 | 60.434 | -61.8896 | 0 | -62.0773 | 60.4156 | 61.9583 | 61.9217 | 0.045776 | -0.066223 | 0.076904 | 0.29159 | -0.14206 | -0.17944 | 0.018311 | 0.018311 | -62.2971 | 60.3745 | 60.2875 | 61.9217 | 62.0956 | 122.5891 | 61.9217 | 60.3928
8814.0625 | 0.045776 | 0.41336 | -0.77118 | -0.25635 | 0.12817 | -0.26596 | -0.17303 | 60.4477 | -61.8164 | 0.082397 | -62.0361 | 60.4156 | 61.9537 | 61.8851 | 0.045776 | -0.069427 | 0.079041 | 0.28839 | -0.16556 | -0.16983 | 0.013733 | 0.022888 | -62.2238 | 60.3699 | 60.3424 | 61.8896 | 62.0728 | 122.58 | 61.9263 | 60.434
8815.7812 | 0.061035 | 0.42084 | -0.77438 | -0.22964 | 0.12711 | -0.28091 | -0.18478 | 60.5576 | -61.6516 | 0.15564 | -61.9354 | 60.4156 | 61.8759 | 61.8164 | 0.076294 | -0.095062 | 0.069427 | 0.28091 | -0.16876 | -0.16876 | 0.11444 | 0.15564 | -62.0453 | 60.3653 | 60.3378 | 61.8118 | 61.9904 | 122.5616 | 61.8851 | 60.4752
8817.5781 | 0.061035 | 0.40375 | -0.77118 | -0.21683 | 0.12924 | -0.23178 | -0.16556 | 60.5209 | -61.7661 | 0.091553 | -62.0224 | 60.3973 | 61.9217 | 61.8851 | 0.076294 | -0.067291 | 0.070496 | 0.29159 | -0.13458 | -0.17197 | 0.09613 | 0.10986 | -62.1918 | 60.3607 | 60.3333 | 61.8576 | 62.0499 | 122.5891 | 61.9034 | 60.4111
8819.2969 | 0.076294 | 0.40695 | -0.77972 | -0.22751 | 0.13031 | -0.2681 | -0.17731 | 60.466 | -61.7889 | 0.050354 | -62.0316 | 60.4523 | 61.9125 | 61.8759 | 0.061035 | -0.072632 | 0.080109 | 0.28519 | -0.14526 | -0.16769 | 0.032043 | 0.027466 | -62.2055 | 60.4065 | 60.3653 | 61.8759 | 62.0544 | 122.5983 | 61.908 | 60.4523
8821.0781 | 0.030518 | 0.40482 | -0.77438 | -0.22003 | 0.12924 | -0.23926 | -0.17197 | 60.5392 | -61.7569 | 0.086975 | -61.9949 | 60.4614 | 61.908 | 61.8347 | 0.045776 | -0.070496 | 0.063019 | 0.29053 | -0.14206 | -0.16769 | 0.073242 | 0.091553 | -62.1918 | 60.3928 | 60.3973 | 61.8393 | 62.0224 | 122.5937 | 61.8896 | 60.4431
8822.875 | 0.091553 | 0.40695 | -0.76584 | -0.24033 | 0.13779 | -0.25848 | -0.18051 | 60.498 | -61.7569 | 0.07782 | -61.9675 | 60.4889 | 61.8713 | 61.821 | 0.076294 | -0.076904 | 0.076904 | 0.27771 | -0.16129 | -0.15915 | 0.004578 | 0.050354 | -62.1506 | 60.4065 | 60.4248 | 61.8393 | 61.9904 | 122.6303 | 61.8301 | 60.4797
8824.6719 | 0.061035 | 0.40588 | -0.77545 | -0.21896 | 0.1442 | -0.25848 | -0.16769 | 60.4889 | -61.7935 | 0.009155 | -62.0041 | 60.4752 | 61.8713 | 61.821 | 0.030518 | -0.074768 | 0.057678 | 0.28625 | -0.13779 | -0.15915 | -0.013733 | 0.036621 | -62.1872 | 60.4568 | 60.4202 | 61.8164 | 62.027 | 122.58 | 61.8484 | 60.5118
8826.4688 | 0.076294 | 0.40054 | -0.77759 | -0.20935 | 0.13245 | -0.2681 | -0.17197 | 60.5896 | -61.6882 | 0.091553 | -61.94 | 60.4752 | 61.8622 | 61.8118 | 0.061035 | -0.070496 | 0.059814 | 0.28732 | -0.14954 | -0.16235 | 0.064087 | 0.091553 | -62.114 | 60.4477 | 60.434 | 61.7935 | 61.9766 | 122.6028 | 61.8118 | 60.5301
8828.1875 | 0.061035 | 0.40909 | -0.77545 | -0.2243 | 0.12924 | -0.26169 | -0.16983 | 60.5896 | -61.6745 | 0.086975 | -61.9263 | 60.5301 | 61.8118 | 61.7798 | 0.061035 | -0.072632 | 0.065155 | 0.29694 | -0.14847 | -0.16556 | 0.068665 | 0.09613 | -62.1048 | 60.466 | 60.466 | 61.7889 | 61.9537 | 122.5983 | 61.7844 | 60.5209
8829.9688 | 0.061035 | 0.41443 | -0.77652 | -0.25101 | 0.13245 | -0.28732 | -0.18051 | 60.6354 | -61.5921 | 0.12817 | -61.8439 | 60.5209 | 61.7706 | 61.7249 | 0.061035 | -0.098267 | 0.074768 | 0.28946 | -0.17838 | -0.16022 | 0.018311 | 0.073242 | -62.027 | 60.498 | 60.4843 | 61.7249 | 61.8988 | 122.4884 | 61.7889 | 60.5988
8831.75 | 0.030518 | 0.43686 | -0.77866 | -0.23926 | 0.13458 | -0.30014 | -0.18478 | 60.6949 | -61.528 | 0.15564 | -61.7935 | 60.5484 | 61.702 | 61.6791 | 0.061035 | -0.10574 | 0.068359 | 0.28839 | -0.17731 | -0.15595 | 0.11902 | 0.15564 | -61.8942 | 60.5026 | 60.5164 | 61.6653 | 61.8668 | 122.5479 | 61.7477 | 60.6171
8833.5312 | 0.076294 | 0.42404 | -0.79147 | -0.22324 | 0.12711 | -0.28091 | -0.19119 | 60.6857 | -61.5509 | 0.10986 | -61.7981 | 60.5759 | 61.7065 | 61.6745 | 0.061035 | -0.10574 | 0.057678 | 0.27878 | -0.15915 | -0.16663 | 0.086975 | 0.14648 | -61.9034 | 60.5301 | 60.5072 | 61.647 | 61.8439 | 122.5616 | 61.7523 | 60.6445
8835.3125 | 0.076294 | 0.42725 | -0.79147 | -0.23285 | 0.1442 | -0.27771 | -0.1944 | 60.7636 | -61.4594 | 0.1831 | -61.7569 | 60.5759 | 61.6928 | 61.6287 | 0.076294 | -0.095062 | 0.059814 | 0.27771 | -0.16129 | -0.1709 | 0.11444 | 0.16022 | -61.8805 | 60.5118 | 60.5072 | 61.6425 | 61.8164 | 122.5342 | 61.7294 | 60.6445
8837.0938 | 0.076294 | 0.39414 | -0.77118 | -0.2211 | 0.14313 | -0.24353 | -0.18372 | 60.6766 | -61.6333 | 0.10071 | -61.8256 | 60.6033 | 61.7523 | 61.7157 | 0.045776 | -0.068359 | 0.072632 | 0.29159 | -0.14954 | -0.17944 | 0.073242 | 0.073242 | -62.0132 | 60.5576 | 60.5255 | 61.6974 | 61.8851 | 122.6257 | 61.7249 | 60.5804
8838.875 | 0.061035 | 0.41657 | -0.78613 | -0.21042 | 0.13458 | -0.28519 | -0.17838 | 60.7544 | -61.5143 | 0.082397 | -61.7798 | 60.6216 | 61.6699 | 61.6196 | 0.076294 | -0.09079 | 0.071564 | 0.28305 | -0.16342 | -0.15381 | 0.059509 | 0.10986 | -61.9034 | 60.5576 | 60.5713 | 61.6333 | 61.7844 | 122.5113 | 61.7157 | 60.6995
8840.6719 | 0.061035 | 0.41016 | -0.78934 | -0.21576 | 0.13565 | -0.24139 | -0.17944 | 60.7315 | -61.5738 | 0.10986 | -61.8301 | 60.585 | 61.7157 | 61.6974 | 0.061035 | -0.068359 | 0.066223 | 0.28412 | -0.13779 | -0.1741 | 0.073242 | 0.10529 | -61.9995 | 60.5576 | 60.5438 | 61.6699 | 61.8622 | 122.6028 | 61.6837 | 60.6354
8842.4531 | 0.061035 | 0.44113 | -0.77759 | -0.24033 | 0.14099 | -0.28625 | -0.18692 | 60.7727 | -61.4639 | 0.15106 | -61.7386 | 60.6308 | 61.6425 | 61.5967 | 0.061035 | -0.099335 | 0.070496 | 0.27878 | -0.16769 | -0.16449 | 0.11444 | 0.14648 | -61.8393 | 60.553 | 60.5804 | 61.615 | 61.7706 | 122.5616 | 61.6699 | 60.704
8844.1562 | 0.076294 | 0.40695 | -0.76904 | -0.23285 | 0.13351 | -0.25101 | -0.16876 | 60.7361 | -61.5509 | 0.10529 | -61.7981 | 60.6537 | 61.7157 | 61.6653 | 0.045776 | -0.080109 | 0.0737 | 0.28732 | -0.14526 | -0.17731 | 0.07782 | 0.086975 | -61.9537 | 60.6033 | 60.5484 | 61.6608 | 61.8256 | 122.6349 | 61.6791 | 60.6491
8845.9375 | 0.045776 | 0.42938 | -0.78293 | -0.23605 | 0.12283 | -0.28519 | -0.18051 | 60.8276 | -61.3998 | 0.19684 | -61.6745 | 60.6445 | 61.615 | 61.5784 | 0.061035 | -0.10681 | 0.069427 | 0.27771 | -0.16983 | -0.16235 | 0.13275 | 0.15106 | -61.8027 | 60.5896 | 60.585 | 61.5692 | 61.7523 | 122.5479 | 61.6562 | 60.7132
8847.7188 | 0.045776 | 0.41977 | -0.75943 | -0.2243 | 0.13458 | -0.24994 | -0.17944 | 60.7544 | -61.5646 | 0.018311 | -61.7844 | 60.6812 | 61.6379 | 61.647 | 0.076294 | -0.071564 | 0.067291 | 0.29694 | -0.1506 | -0.16342 | 0.086975 | 0.091553 | -61.9217 | 60.6354 | 60.6033 | 61.6104 | 61.7661 | 122.6532 | 61.6104 | 60.6766
8849.5156 | 0.030518 | 0.43579 | -0.77652 | -0.2179 | 0.13565 | -0.26276 | -0.17197 | 60.8505 | -61.3907 | 0.12817 | -61.6516 | 60.6537 | 61.5829 | 61.5372 | 0.076294 | -0.089722 | 0.064087 | 0.29159 | -0.14633 | -0.16876 | 0.15564 | 0.18768 | -61.7844 | 60.6354 | 60.6216 | 61.5555 | 61.7661 | 122.5891 | 61.6013 | 60.7498
8851.2969 | 0.061035 | 0.40161 | -0.78186 | -0.22324 | 0.11429 | -0.24353 | -0.17624 | 60.7086 | -61.5875 | 0 | -61.7798 | 60.704 | 61.6425 | 61.5921 | 0.061035 | -0.066223 | 0.077972 | 0.27985 | -0.13886 | -0.16663 | 0.041199 | 0.050354 | -61.9812 | 60.6583 | 60.6171 | 61.6058 | 61.8027 | 122.6074 | 61.5967 | 60.7361
8853.0781 | 0.076294 | 0.40695 | -0.78186 | -0.24994 | 0.13031 | -0.27985 | -0.18372 | 60.8597 | -61.3266 | 0.20142 | -61.647 | 60.6995 | 61.5509 | 61.5326 | 0.061035 | -0.089722 | 0.076904 | 0.29053 | -0.16449 | -0.16342 | 0.10529 | 0.17395 | -61.7615 | 60.6491 | 60.6491 | 61.5509 | 61.6974 | 122.5067 | 61.6058 | 60.7773
8854.875 | 0.061035 | 0.40054 | -0.77545 | -0.22217 | 0.13031 | -0.26276 | -0.18051 | 60.7452 | -61.5051 | 0.054932 | -61.7386 | 60.7224 | 61.6104 | 61.6013 | 0.045776 | -0.077972 | 0.072632 | 0.28412 | -0.15488 | -0.17517 | 0.009155 | 0.050354 | -61.9171 | 60.6766 | 60.6354 | 61.6104 | 61.7844 | 122.6532 | 61.6058 | 60.6995
8856.6719 | 0.061035 | 0.4155 | -0.75409 | -0.21042 | 0.13138 | -0.25421 | -0.18051 | 60.7269 | -61.5601 | -0.036621 | -61.7615 | 60.7269 | 61.6196 | 61.5829 | 0.061035 | -0.074768 | 0.0737 | 0.29373 | -0.13779 | -0.14633 | 0.022888 | 0.050354 | -61.9354 | 60.6995 | 60.6674 | 61.5784 | 61.7706 | 122.6028 | 61.5829 | 60.7452
8858.4531 | 0.061035 | 0.41443 | -0.76797 | -0.23285 | 0.13779 | -0.28091 | -0.19653 | 60.8276 | -61.3953 | 0.073242 | -61.6608 | 60.7407 | 61.5784 | 61.5189 | 0.030518 | -0.089722 | 0.063019 | 0.27878 | -0.16449 | -0.16022 | 0 | 0.004578 | -61.8439 | 60.6857 | 60.704 | 61.5326 | 61.7432 | 122.5021 | 61.615 | 60.7864
8860.1562 | 0.045776 | 0.40802 | -0.78186 | -0.21896 | 0.12604 | -0.25742 | -0.18158 | 60.791 | -61.5189 | -0.032043 | -61.7386 | 60.7636 | 61.6241 | 61.5372 | 0.061035 | -0.085449 | 0.061951 | 0.29373 | -0.14633 | -0.16556 | 0.054932 | 0.054932 | -61.9034 | 60.6857 | 60.704 | 61.528 | 61.7477 | 122.644 | 61.5692 | 60.7727
8861.9531 | 0.076294 | 0.40909 | -0.77866 | -0.23819 | 0.14099 | -0.26916 | -0.18158 | 60.8002 | -61.4731 | -0.009155 | -61.7111 | 60.759 | 61.5829 | 61.5417 | 0.061035 | -0.074768 | 0.060883 | 0.27878 | -0.15488 | -0.15595 | -0.018311 | -0.013733 | -61.8896 | 60.7224 | 60.7224 | 61.5555 | 61.7157 | 122.5708 | 61.5967 | 60.7819
8863.7344 | 0.045776 | 0.43686 | -0.78079 | -0.22858 | 0.13245 | -0.28839 | -0.18906 | 60.9146 | -61.3174 | 0.12817 | -61.5738 | 60.7819 | 61.4822 | 61.4594 | 0.061035 | -0.092926 | 0.055542 | 0.28412 | -0.17197 | -0.15701 | 0.09613 | 0.16022 | -61.6974 | 60.7361 | 60.7086 | 61.4456 | 61.6241 | 122.5067 | 61.528 | 60.8551
8865.4531 | 0.061035 | 0.40909 | -0.77011 | -0.21576 | 0.1474 | -0.25421 | -0.18692 | 60.8093 | -61.4685 | -0.018311 | -61.7065 | 60.7773 | 61.5784 | 61.5234 | 0.045776 | -0.070496 | 0.054474 | 0.28839 | -0.15488 | -0.17197 | -0.018311 | -0.018311 | -61.8622 | 60.7269 | 60.7086 | 61.5463 | 61.7157 | 122.5342 | 61.5738 | 60.791
8867.2344 | 0.061035 | 0.40268 | -0.76477 | -0.21149 | 0.12924 | -0.23926 | -0.17624 | 60.8139 | -61.5051 | 0.009155 | -61.7203 | 60.7452 | 61.6013 | 61.5646 | 0.061035 | -0.072632 | 0.065155 | 0.29266 | -0.13992 | -0.16769 | 0.018311 | 0.041199 | -61.9034 | 60.7086 | 60.7544 | 61.5692 | 61.7432 | 122.5983 | 61.528 | 60.7819
8869.0312 | 0.061035 | 0.40375 | -0.7637 | -0.23819 | 0.13138 | -0.26382 | -0.17624 | 60.8322 | -61.4319 | 0 | -61.6562 | 60.791 | 61.5829 | 61.5097 | 0.061035 | -0.072632 | 0.075836 | 0.28946 | -0.15808 | -0.15915 | 0.004578 | 0.045776 | -61.8301 | 60.759 | 60.7224 | 61.5097 | 61.6791 | 122.5204 | 61.528 | 60.7864
8870.7656 | 0.061035 | 0.41763 | -0.78293 | -0.21576 | 0.1239 | -0.26703 | -0.17944 | 60.8688 | -61.4227 | 0.018311 | -61.6196 | 60.8047 | 61.4914 | 61.4548 | 0.076294 | -0.081177 | 0.057678 | 0.28946 | -0.14313 | -0.15808 | 0.11444 | 0.1236 | -61.7477 | 60.7681 | 60.791 | 61.4365 | 61.6104 | 122.6578 | 61.4456 | 60.8688
8872.5 | 0.061035 | 0.4155 | -0.78079 | -0.22217 | 0.13351 | -0.29907 | -0.20187 | 61.0153 | -61.2259 | 0.16479 | -61.528 | 60.8276 | 61.441 | 61.3815 | 0.076294 | -0.091858 | 0.064087 | 0.27985 | -0.16449 | -0.16342 | 0.09613 | 0.16479 | -61.6287 | 60.7819 | 60.8139 | 61.3998 | 61.5601 | 122.5296 | 61.4685 | 60.8826
8874.2812 | 0.061035 | 0.4155 | -0.79254 | -0.24033 | 0.12497 | -0.27878 | -0.18372 | 60.9924 | -61.2488 | 0.14191 | -61.4868 | 60.8871 | 61.3998 | 61.3358 | 0.061035 | -0.10361 | 0.063019 | 0.28839 | -0.1741 | -0.16449 | 0.091553 | 0.13733 | -61.5738 | 60.8276 | 60.8322 | 61.3449 | 61.5463 | 122.5433 | 61.4273 | 60.9512
8876 | 0.061035 | 0.41229 | -0.77331 | -0.20615 | 0.12711 | -0.24033 | -0.17838 | 60.9329 | -61.3815 | 0.009155 | -61.5875 | 60.8871 | 61.4639 | 61.3998 | 0.045776 | -0.072632 | 0.058746 | 0.28519 | -0.13672 | -0.16769 | 0.027466 | 0.032043 | -61.7981 | 60.8505 | 60.8505 | 61.441 | 61.6058 | 122.58 | 61.4594 | 60.8826
8877.7969 | 0.061035 | 0.39627 | -0.76904 | -0.21576 | 0.13992 | -0.24033 | -0.17197 | 60.9604 | -61.3266 | 0.027466 | -61.5601 | 60.91 | 61.441 | 61.3953 | 0.091553 | -0.072632 | 0.059814 | 0.2948 | -0.14099 | -0.16876 | 0.022888 | 0.064087 | -61.7569 | 60.878 | 60.8688 | 61.3678 | 61.5601 | 122.5754 | 61.4182 | 60.9238
8879.5312 | 0.061035 | 0.41336 | -0.77118 | -0.22003 | 0.13245 | -0.24353 | -0.17517 | 61.0199 | -61.3037 | -0.032043 | -61.5143 | 61.0107 | 61.3815 | 61.3266 | 0.076294 | -0.072632 | 0.052338 | 0.29587 | -0.1506 | -0.16769 | 0.022888 | 0.022888 | -61.6837 | 60.9283 | 60.9421 | 61.3312 | 61.4822 | 122.6074 | 61.3541 | 60.9924
8881.3125 | 0.045776 | 0.43045 | -0.77972 | -0.23392 | 0.11108 | -0.29159 | -0.18585 | 61.1618 | -61.0474 | 0.16937 | -61.3541 | 60.9787 | 61.2854 | 61.2488 | 0.076294 | -0.11108 | 0.054474 | 0.27344 | -0.16556 | -0.16342 | 0.10071 | 0.16479 | -61.4731 | 60.9512 | 60.9467 | 61.2488 | 61.3815 | 122.5296 | 61.3495 | 61.0703
8883.0312 | 0.061035 | 0.42511 | -0.78079 | -0.23178 | 0.13138 | -0.28946 | -0.18906 | 61.0291 | -61.2305 | 0.054932 | -61.4685 | 60.9375 | 61.3266 | 61.2991 | 0.030518 | -0.095062 | 0.055542 | 0.27664 | -0.16769 | -0.16342 | 0.027466 | 0.073242 | -61.6013 | 60.8734 | 60.8826 | 61.3358 | 61.4914 | 122.5296 | 61.3724 | 61.0062
8884.8281 | 0.061035 | 0.40588 | -0.784 | -0.24139 | 0.13138 | -0.26916 | -0.19226 | 61.084 | -61.1572 | 0.17395 | -61.4136 | 60.9055 | 61.3632 | 61.3266 | 0.061035 | -0.095062 | 0.074768 | 0.29159 | -0.17303 | -0.17517 | 0.086975 | 0.15106 | -61.5601 | 60.878 | 60.8688 | 61.29 | 61.4868 | 122.4792 | 61.4044 | 60.997
8886.5469 | 0.061035 | 0.43579 | -0.77972 | -0.23819 | 0.13031 | -0.28946 | -0.18906 | 61.0977 | -61.171 | 0.059509 | -61.4182 | 60.9695 | 61.2991 | 61.2625 | 0.076294 | -0.093994 | 0.061951 | 0.28625 | -0.16556 | -0.17944 | 0.073242 | 0.073242 | -61.5646 | 60.9192 | 60.9055 | 61.2808 | 61.4639 | 122.5067 | 61.3586 | 61.0336
8888.3281 | 0.045776 | 0.39948 | -0.77866 | -0.22858 | 0.11963 | -0.2478 | -0.19012 | 61.0336 | -61.2717 | 0.07782 | -61.4639 | 60.997 | 61.3495 | 61.322 | 0.061035 | -0.087585 | 0.067291 | 0.29053 | -0.14847 | -0.18799 | 0.054932 | 0.07782 | -61.6653 | 60.9695 | 60.9146 | 61.3403 | 61.5097 | 122.6166 | 61.3495 | 60.965
8890.125 | 0.045776 | 0.40054 | -0.77331 | -0.23712 | 0.15167 | -0.25528 | -0.17731 | 61.0565 | -61.2534 | 0.086975 | -61.4594 | 60.9787 | 61.3449 | 61.3266 | 0.061035 | -0.0737 | 0.066223 | 0.29373 | -0.15701 | -0.1741 | 0.054932 | 0.064087 | -61.6608 | 60.965 | 60.9238 | 61.3037 | 61.5189 | 122.6028 | 61.3358 | 60.9833
8891.9062 | 0.045776 | 0.41657 | -0.76904 | -0.22858 | 0.12817 | -0.27771 | -0.18906 | 61.1206 | -61.1252 | 0.064087 | -61.3953 | 60.9512 | 61.2991 | 61.2305 | 0.061035 | -0.10788 | 0.063019 | 0.29159 | -0.15915 | -0.17303 | 0.10986 | 0.11902 | -61.5143 | 60.9238 | 60.9421 | 61.2488 | 61.3998 | 122.493 | 61.3266 | 61.0611
8893.7031 | 0.045776 | 0.40909 | -0.75623 | -0.21362 | 0.12497 | -0.24994 | -0.17838 | 61.0336 | -61.2717 | -0.022888 | -61.4685 | 61.0245 | 61.3312 | 61.2946 | 0.030518 | -0.080109 | 0.074768 | 0.30121 | -0.13245 | -0.17624 | 0.050354 | 0.041199 | -61.6699 | 60.9695 | 60.9604 | 61.29 | 61.4914 | 122.5845 | 61.322 | 61.0107
8895.5 | 0.076294 | 0.44113 | -0.7637 | -0.2243 | 0.13992 | -0.2681 | -0.17624 | 61.1481 | -61.0886 | 0.068665 | -61.3586 | 60.9695 | 61.2854 | 61.2396 | 0.091553 | -0.097198 | 0.061951 | 0.29266 | -0.1506 | -0.16983 | 0.12817 | 0.16937 | -61.5005 | 60.9283 | 60.8963 | 61.2396 | 61.4365 | 122.5983 | 61.3129 | 61.0565
8897.2031 | 0.061035 | 0.43366 | -0.78186 | -0.2243 | 0.12283 | -0.27878 | -0.18265 | 61.1252 | -61.0794 | 0.036621 | -61.3678 | 61.0199 | 61.235 | 61.2076 | 0.076294 | -0.088654 | 0.058746 | 0.28198 | -0.15701 | -0.15915 | 0.068665 | 0.073242 | -61.4731 | 61.0016 | 60.9833 | 61.2167 | 61.3861 | 122.493 | 61.2717 | 61.1298
8899 | 0.076294 | 0.41122 | -0.77011 | -0.21362 | 0.1207 | -0.24887 | -0.17197 | 61.1572 | -61.1069 | 0.013733 | -61.3678 | 61.0474 | 61.2808 | 61.2213 | 0.061035 | -0.086517 | 0.058746 | 0.28519 | -0.14313 | -0.18051 | 0.10986 | 0.14648 | -61.4914 | 60.9879 | 60.9558 | 61.2076 | 61.3678 | 122.6303 | 61.2259 | 61.0886
8900.7812 | 0.061035 | 0.40375 | -0.77225 | -0.22324 | 0.13565 | -0.25314 | -0.17944 | 61.1481 | -61.1389 | -0.027466 | -61.3678 | 61.1069 | 61.235 | 61.2076 | 0.076294 | -0.085449 | 0.066223 | 0.28412 | -0.1442 | -0.16235 | 0.054932 | 0.054932 | -61.528 | 61.0382 | 61.0199 | 61.1984 | 61.3678 | 122.6532 | 61.1847 | 61.116
8902.5 | 0.045776 | 0.42084 | -0.78507 | -0.21149 | 0.12283 | -0.27237 | -0.18478 | 61.2305 | -61.0016 | 0.073242 | -61.2717 | 61.0519 | 61.1938 | 61.1572 | 0.076294 | -0.087585 | 0.05127 | 0.27771 | -0.15167 | -0.1709 | 0.091553 | 0.15106 | -61.3998 | 61.0016 | 60.997 | 61.1481 | 61.3449 | 122.5891 | 61.2076 | 61.1343
8904.2812 | 0.045776 | 0.44006 | -0.67505 | -0.22964 | 0.13351 | -0.27985 | -0.18692 | 61.2534 | -60.965 | 0.064087 | -61.2122 | 61.1389 | 61.1206 | 61.084 | 0.045776 | -0.092926 | 0.045929 | 0.27771 | -0.16876 | -0.16449 | 0.059509 | 0.091553 | -61.3449 | 61.116 | 61.084 | 61.0519 | 61.2717 | 122.5342 | 61.171 | 61.2305
8906 | 0.061035 | 0.40161 | -0.77438 | -0.22537 | 0.13031 | -0.25848 | -0.18478 | 61.2717 | -60.9741 | 0.050354 | -61.2442 | 61.1389 | 61.1435 | 61.0931 | 0.030518 | -0.072632 | 0.046997 | 0.28091 | -0.14526 | -0.17197 | 0.10986 | 0.14648 | -61.3678 | 61.0931 | 61.0474 | 61.1206 | 61.2762 | 122.6212 | 61.1343 | 61.1847
8907.7812 | 0.061035 | 0.41977 | -0.77652 | -0.2211 | 0.13992 | -0.24674 | -0.17517 | 61.3495 | -60.91 | 0.07782 | -61.1664 | 61.1755 | 61.084 | 61.0519 | 0.061035 | -0.084381 | 0.070496 | 0.28519 | -0.14526 | -0.16769 | 0.11444 | 0.14648 | -61.3266 | 61.1435 | 61.0977 | 61.0565 | 61.2396 | 122.5983 | 61.0931 | 61.2442
8909.5 | 0.061035 | 0.40695 | -0.76797 | -0.22858 | 0.12711 | -0.2478 | -0.17517 | 61.2946 | -60.9695 | 0.11902 | -61.1847 | 61.2442 | 61.0703 | 61.0382 | 0.061035 | -0.076904 | 0.067291 | 0.27237 | -0.15274 | -0.16556 | 0.086975 | 0.11444 | -61.3541 | 61.2076 | 61.171 | 61.0382 | 61.2396 | 122.6257 | 61.0565 | 61.2579
8911.2969 | 0.061035 | 0.42297 | -0.77866 | -0.23926 | 0.13672 | -0.26489 | -0.18158 | 61.3632 | -60.8322 | 0.16479 | -61.1206 | 61.2396 | 61.0519 | 61.0016 | 0.061035 | -0.091858 | 0.0737 | 0.28198 | -0.16663 | -0.16876 | 0.086975 | 0.11444 | -61.3083 | 61.2213 | 61.1847 | 61.0062 | 61.2076 | 122.4838 | 61.0703 | 61.3174
8913.0312 | 0.076294 | 0.42191 | -0.77866 | -0.23819 | 0.12924 | -0.25635 | -0.18158 | 61.3449 | -60.9238 | 0.10529 | -61.1435 | 61.322 | 61.0336 | 61.0107 | 0.045776 | -0.081177 | 0.067291 | 0.30121 | -0.16129 | -0.17303 | 0.082397 | 0.064087 | -61.322 | 61.2717 | 61.2579 | 61.0016 | 61.1572 | 122.6074 | 61.0565 | 61.29
8914.8125 | 0.061035 | 0.41016 | -0.77011 | -0.23071 | 0.13886 | -0.25207 | -0.17624 | 61.3266 | -60.9512 | 0.027466 | -61.1572 | 61.3129 | 61.0428 | 61.0016 | 0.061035 | -0.063019 | 0.066223 | 0.28839 | -0.14847 | -0.16876 | 0.050354 | 0.050354 | -61.3678 | 61.2579 | 61.2213 | 61.0153 | 61.1893 | 122.5754 | 61.0336 | 61.322
8916.5938 | 0.076294 | 0.41336 | -0.77545 | -0.22537 | 0.13245 | -0.26169 | -0.17624 | 61.3403 | -60.9238 | -0.013733 | -61.1526 | 61.2946 | 61.0291 | 60.9787 | 0.030518 | -0.09079 | 0.066223 | 0.29373 | -0.15915 | -0.16983 | 0.073242 | 0.082397 | -61.2854 | 61.2442 | 61.2167 | 60.9924 | 61.1343 | 122.6532 | 61.0016 | 61.2991
8918.3125 | 0.076294 | 0.41657 | -0.77438 | -0.23285 | 0.11856 | -0.29053 | -0.19119 | 61.4273 | -60.7636 | 0.064087 | -61.0565 | 61.3449 | 60.9329 | 60.878 | 0.061035 | -0.09613 | 0.055542 | 0.27557 | -0.17517 | -0.16769 | 0.050354 | 0.09613 | -61.1526 | 61.322 | 61.2808 | 60.878 | 61.0748 | 122.5342 | 60.9467 | 61.409
8920.0938 | 0.076294 | 0.42084 | -0.77759 | -0.23819 | 0.13779 | -0.28946 | -0.18158 | 61.5417 | -60.6583 | 0.15564 | -60.965 | 61.3632 | 60.8963 | 60.8505 | 0.030518 | -0.097198 | 0.065155 | 0.28839 | -0.17731 | -0.17517 | 0.14191 | 0.16937 | -61.0519 | 61.3129 | 61.3037 | 60.8551 | 61.0291 | 122.5433 | 60.9146 | 61.4548
8921.8281 | 0.061035 | 0.41977 | -0.76584 | -0.22003 | 0.12604 | -0.26276 | -0.16769 | 61.5829 | -60.6857 | 0.059509 | -60.9512 | 61.3815 | 60.878 | 60.8185 | 0.076294 | -0.085449 | 0.061951 | 0.29694 | -0.15701 | -0.17944 | 0.11902 | 0.14648 | -61.084 | 61.3586 | 61.3266 | 60.8414 | 61.0107 | 122.5845 | 60.878 | 61.4822
8923.6094 | 0.076294 | 0.40482 | -0.78186 | -0.22751 | 0.13138 | -0.25635 | -0.1709 | 61.5784 | -60.7086 | 0.091553 | -60.9467 | 61.5372 | 60.8414 | 60.8093 | 0.061035 | -0.077972 | 0.064087 | 0.27664 | -0.15167 | -0.17838 | 0.059509 | 0.082397 | -61.1206 | 61.4914 | 61.441 | 60.7956 | 60.9604 | 122.5983 | 60.8002 | 61.5189
8925.3906 | 0.061035 | 0.40161 | -0.77225 | -0.2446 | 0.12711 | -0.2713 | -0.18265 | 61.5967 | -60.6628 | 0.11444 | -60.9009 | 61.5372 | 60.7864 | 60.7544 | 0.045776 | -0.083313 | 0.0737 | 0.28732 | -0.16342 | -0.16342 | 0.068665 | 0.068665 | -61.0794 | 61.5005 | 61.4731 | 60.7727 | 60.9421 | 122.4884 | 60.8047 | 61.5738
8927.1562 | 0.076294 | 0.40268 | -0.77438 | -0.24674 | 0.13886 | -0.26276 | -0.17838 | 61.6058 | -60.6491 | 0.091553 | -60.9192 | 61.5417 | 60.8093 | 60.7407 | 0.045776 | -0.099335 | 0.079041 | 0.29694 | -0.1741 | -0.17838 | 0.059509 | 0.073242 | -61.0748 | 61.4822 | 61.4639 | 60.759 | 60.9512 | 122.5021 | 60.8002 | 61.5738
8928.875 | 0.045776 | 0.41336 | -0.76477 | -0.21469 | 0.13245 | -0.24994 | -0.18158 | 61.5967 | -60.6812 | -0.032043 | -60.9055 | 61.5692 | 60.8002 | 60.7224 | 0.045776 | -0.0737 | 0.063019 | 0.30121 | -0.14206 | -0.1741 | 0.036621 | 0.027466 | -61.0794 | 61.5326 | 61.5005 | 60.7178 | 60.9146 | 122.5937 | 60.7636 | 61.5875
8930.6562 | 0.061035 | 0.40375 | -0.76477 | -0.23071 | 0.1239 | -0.25314 | -0.16449 | 61.7249 | -60.5713 | 0.032043 | -60.8047 | 61.647 | 60.672 | 60.6308 | 0.045776 | -0.071564 | 0.071564 | 0.2948 | -0.15381 | -0.16556 | 0.073242 | 0.082397 | -60.9833 | 61.6241 | 61.5967 | 60.6354 | 60.8139 | 122.5662 | 60.6628 | 61.6699
8932.4375 | 0.061035 | 0.39948 | -0.76904 | -0.25314 | 0.13031 | -0.2681 | -0.18478 | 61.7981 | -60.4752 | 0.091553 | -60.6995 | 61.7752 | 60.5896 | 60.5392 | 0.045776 | -0.087585 | 0.071564 | 0.30121 | -0.15488 | -0.16769 | 0.068665 | 0.10071 | -60.878 | 61.7249 | 61.7157 | 60.5438 | 60.7361 | 122.5937 | 60.5621 | 61.7432
8934.2188 | 0.061035 | 0.40909 | -0.77331 | -0.2243 | 0.13031 | -0.25955 | -0.17624 | 61.7798 | -60.466 | 0.11902 | -60.6903 | 61.7798 | 60.5896 | 60.553 | 0.076294 | -0.071564 | 0.068359 | 0.29373 | -0.15595 | -0.16342 | 0.09613 | 0.12817 | -60.8643 | 61.702 | 61.7065 | 60.5667 | 60.7498 | 122.6257 | 60.585 | 61.7569
8935.9688 | 0.045776 | 0.41443 | -0.79254 | -0.22858 | 0.12283 | -0.27451 | -0.18585 | 61.853 | -60.3973 | 0.10986 | -60.6445 | 61.8256 | 60.498 | 60.4706 | 0.061035 | -0.074768 | 0.076904 | 0.29373 | -0.16449 | -0.16342 | 0.054932 | 0.082397 | -60.8231 | 61.7889 | 61.7706 | 60.4889 | 60.6445 | 122.5479 | 60.5255 | 61.8256
8937.7656 | 0.061035 | 0.42084 | -0.7637 | -0.22537 | 0.13458 | -0.27557 | -0.18692 | 61.9308 | -60.3104 | 0.14191 | -60.5804 | 61.8622 | 60.4523 | 60.434 | 0.076294 | -0.091858 | 0.065155 | 0.28732 | -0.16769 | -0.16663 | 0.064087 | 0.073242 | -60.7498 | 61.8393 | 61.8073 | 60.4523 | 60.5988 | 122.4976 | 60.5026 | 61.8851
8939.5625 | 0.045776 | 0.40588 | -0.77118 | -0.24994 | 0.13672 | -0.29266 | -0.18692 | 62.027 | -60.1639 | 0.19226 | -60.466 | 61.8851 | 60.4019 | 60.3607 | 0.061035 | -0.11322 | 0.057678 | 0.27878 | -0.17197 | -0.16449 | 0.1236 | 0.17395 | -60.5759 | 61.8027 | 61.821 | 60.3882 | 60.5484 | 122.5159 | 60.4431 | 61.9217
8941.2812 | 0.045776 | 0.43259 | -0.79254 | -0.21362 | 0.12604 | -0.28839 | -0.19119 | 61.9492 | -60.2829 | 0.068665 | -60.5347 | 61.8622 | 60.434 | 60.3516 | 0.061035 | -0.09613 | 0.050201 | 0.28412 | -0.15274 | -0.17303 | 0.045776 | 0.059509 | -60.6583 | 61.821 | 61.8073 | 60.3882 | 60.5759 | 122.5113 | 60.466 | 61.972
8943.0781 | 0.061035 | 0.41763 | -0.77225 | -0.24033 | 0.12924 | -0.28839 | -0.19653 | 62.0361 | -60.1822 | 0.07782 | -60.4431 | 61.9446 | 60.347 | 60.3149 | 0.045776 | -0.099335 | 0.065155 | 0.28091 | -0.16449 | -0.17624 | 0.059509 | 0.086975 | -60.5667 | 61.9034 | 61.8668 | 60.3104 | 60.4797 | 122.5388 | 60.3745 | 62.0087
8944.8594 | 0.061035 | 0.41016 | -0.75836 | -0.22003 | 0.11856 | -0.2446 | -0.17838 | 62.0316 | -60.2554 | -0.009155 | -60.498 | 62.027 | 60.3333 | 60.3333 | 0.061035 | -0.070496 | 0.064087 | 0.30762 | -0.14954 | -0.1709 | 0.068665 | 0.050354 | -60.6537 | 61.9583 | 61.9263 | 60.3012 | 60.4752 | 122.644 | 60.3195 | 61.9858
8946.6562 | 0.061035 | 0.40909 | -0.77225 | -0.2179 | 0.13458 | -0.24139 | -0.17944 | 62.0178 | -60.2875 | 0 | -60.4843 | 62.027 | 60.347 | 60.3104 | 0.091553 | -0.076904 | 0.067291 | 0.28519 | -0.13779 | -0.17303 | 0.045776 | 0.041199 | -60.6674 | 61.9858 | 61.9125 | 60.3241 | 60.4797 | 122.5891 | 60.3195 | 62.0087
8948.4375 | 0.061035 | 0.40588 | -0.76691 | -0.23498 | 0.14206 | -0.25528 | -0.1709 | 62.1185 | -60.141 | 0.12817 | -60.3928 | 62.027 | 60.3149 | 60.2783 | 0.045776 | -0.082245 | 0.063019 | 0.28305 | -0.14847 | -0.16983 | 0.10986 | 0.12817 | -60.5621 | 61.9904 | 61.972 | 60.2692 | 60.434 | 122.6303 | 60.2921 | 62.0132
8950.1406 | 0.076294 | 0.40802 | -0.77011 | -0.22217 | 0.13992 | -0.25314 | -0.17517 | 62.1231 | -60.141 | 0.086975 | -60.4019 | 62.0453 | 60.2829 | 60.2417 | 0.076294 | -0.077972 | 0.068359 | 0.30228 | -0.1442 | -0.16663 | 0.07782 | 0.091553 | -60.5942 | 61.9995 | 62.0178 | 60.2509 | 60.4431 | 122.58 | 60.2646 | 62.0453
8951.9375 | 0.045776 | 0.4155 | -0.76477 | -0.22003 | 0.12711 | -0.26596 | -0.16769 | 62.1506 | -60.0906 | 0.13275 | -60.3607 | 62.059 | 60.26 | 60.2005 | 0.061035 | -0.074768 | 0.072632 | 0.28732 | -0.1474 | -0.16769 | 0.13275 | 0.14191 | -60.5255 | 61.9904 | 62.0041 | 60.2417 | 60.4065 | 122.58 | 60.2646 | 62.0636
8953.7344 | 0.061035 | 0.39841 | -0.77011 | -0.23178 | 0.13138 | -0.25848 | -0.17197 | 62.2192 | -60.0311 | 0.068665 | -60.2783 | 62.1597 | 60.1593 | 60.1135 | 0.061035 | -0.067291 | 0.064087 | 0.29053 | -0.13779 | -0.16663 | 0.068665 | 0.086975 | -60.4706 | 62.1552 | 62.1231 | 60.1135 | 60.3149 | 122.5754 | 60.1364 | 62.1872
8955.4531 | 0.061035 | 0.40482 | -0.77118 | -0.23712 | 0.13351 | -0.27664 | -0.18051 | 62.2971 | -59.9075 | 0.11902 | -60.1593 | 62.2787 | 60.0403 | 60.0357 | 0.061035 | -0.079041 | 0.079041 | 0.27664 | -0.16022 | -0.15808 | 0.054932 | 0.082397 | -60.3424 | 62.2742 | 62.2467 | 60.0266 | 60.2051 | 122.5754 | 60.0403 | 62.2925
8957.2344 | 0.061035 | 0.41016 | -0.77331 | -0.23392 | 0.1442 | -0.27344 | -0.17731 | 62.3016 | -59.9304 | -0.027466 | -60.1776 | 62.3062 | 60.0311 | 60.0037 | 0.076294 | -0.069427 | 0.050201 | 0.29373 | -0.15595 | -0.16022 | 0.045776 | 0.059509 | -60.3287 | 62.2696 | 62.2284 | 60.0082 | 60.1868 | 122.6349 | 60.022 | 62.3199
8958.9688 | 0.061035 | 0.42297 | -0.75836 | -0.24139 | 0.12711 | -0.26703 | -0.18799 | 62.352 | -59.903 | 0.004578 | -60.1364 | 62.3062 | 59.9991 | 59.9579 | 0.030518 | -0.076904 | 0.061951 | 0.28839 | -0.15595 | -0.16129 | 0.082397 | 0.09613 | -60.26 | 62.2604 | 62.2513 | 59.9487 | 60.1364 | 122.644 | 59.9945 | 62.3337
8960.7656 | 0.045776 | 0.41122 | -0.76797 | -0.2179 | 0.13245 | -0.25955 | -0.19333 | 62.3566 | -59.8984 | 0.013733 | -60.1181 | 62.3474 | 59.9762 | 59.935 | 0.045776 | -0.09079 | 0.068359 | 0.30548 | -0.14633 | -0.16129 | 0.027466 | 0.041199 | -60.3333 | 62.3154 | 62.3062 | 59.9213 | 60.1273 | 122.5754 | 59.9579 | 62.3932
8962.5625 | 0.045776 | 0.42084 | -0.77759 | -0.24353 | 0.13886 | -0.30762 | -0.19119 | 62.4115 | -59.7519 | 0.12817 | -60.0494 | 62.2879 | 59.967 | 59.9213 | 0.045776 | -0.10361 | 0.075836 | 0.27664 | -0.1741 | -0.15488 | 0.11444 | 0.13733 | -60.1685 | 62.2421 | 62.2421 | 59.9442 | 60.1227 | 122.5433 | 60.022 | 62.3703
8964.3594 | 0.030518 | 0.39307 | -0.77118 | -0.23712 | 0.13351 | -0.26062 | -0.18478 | 62.4619 | -59.7656 | 0.10986 | -59.9945 | 62.4298 | 59.9121 | 59.8755 | 0.076294 | -0.080109 | 0.0737 | 0.28946 | -0.15381 | -0.16876 | 0.10071 | 0.11902 | -60.1822 | 62.3795 | 62.352 | 59.8801 | 60.054 | 122.6257 | 59.8663 | 62.4252
8966.0625 | 0.045776 | 0.41443 | -0.76691 | -0.2179 | 0.14099 | -0.25848 | -0.18051 | 62.4664 | -59.7473 | 0.059509 | -60.0311 | 62.3474 | 59.9258 | 59.8709 | 0.061035 | -0.099335 | 0.064087 | 0.28625 | -0.14847 | -0.1709 | 0.1236 | 0.14191 | -60.1639 | 62.3016 | 62.2787 | 59.8846 | 60.054 | 122.612 | 59.9213 | 62.384
8967.8438 | 0.061035 | 0.40482 | -0.7872 | -0.23819 | 0.13245 | -0.28519 | -0.18692 | 62.6175 | -59.5459 | 0.19684 | -59.8709 | 62.4619 | 59.7794 | 59.7427 | 0.030518 | -0.1004 | 0.064087 | 0.27878 | -0.16022 | -0.16876 | 0.14191 | 0.16937 | -59.9945 | 62.4252 | 62.4069 | 59.7382 | 59.9487 | 122.5021 | 59.8251 | 62.5351
8969.6406 | 0.061035 | 0.4187 | -0.7637 | -0.24246 | 0.12283 | -0.28625 | -0.18265 | 62.5854 | -59.6237 | 0.086975 | -59.8801 | 62.5305 | 59.7794 | 59.729 | 0.076294 | -0.10361 | 0.060883 | 0.28732 | -0.17197 | -0.1741 | 0.086975 | 0.09613 | -59.9945 | 62.4573 | 62.471 | 59.7198 | 59.8938 | 122.5388 | 59.8114 | 62.5809
8971.3594 | 0.045776 | 0.4155 | -0.7637 | -0.21255 | 0.12604 | -0.26169 | -0.17944 | 62.7045 | -59.5413 | 0.07782 | -59.8068 | 62.5351 | 59.7427 | 59.6878 | 0.030518 | -0.083313 | 0.061951 | 0.29266 | -0.14954 | -0.18158 | 0.12817 | 0.13275 | -59.9716 | 62.4664 | 62.439 | 59.729 | 59.8434 | 122.612 | 59.7565 | 62.5763
8973.1562 | 0.061035 | 0.40588 | -0.78186 | -0.24567 | 0.12817 | -0.28732 | -0.18799 | 62.7319 | -59.4269 | 0.21973 | -59.7702 | 62.5351 | 59.7015 | 59.6741 | 0.061035 | -0.10574 | 0.067291 | 0.28519 | -0.16342 | -0.18158 | 0.16022 | 0.19684 | -59.8938 | 62.4985 | 62.4893 | 59.6649 | 59.8343 | 122.5204 | 59.729 | 62.6129
8974.9531 | 0.061035 | 0.40695 | -0.77759 | -0.2179 | 0.11536 | -0.26382 | -0.16983 | 62.764 | -59.4177 | 0.09613 | -59.7244 | 62.5992 | 59.6512 | 59.6146 | 0.061035 | -0.089722 | 0.064087 | 0.28732 | -0.15808 | -0.17838 | 0.14191 | 0.14191 | -59.8663 | 62.5717 | 62.5397 | 59.6146 | 59.7931 | 122.5021 | 59.6695 | 62.7365
8976.6875 | 0.045776 | 0.42404 | -0.77118 | -0.21683 | 0.1239 | -0.25742 | -0.1741 | 62.7731 | -59.4452 | 0.064087 | -59.7427 | 62.59 | 59.7015 | 59.6146 | 0.061035 | -0.083313 | 0.059814 | 0.27985 | -0.13992 | -0.1709 | 0.1236 | 0.13275 | -59.8755 | 62.5442 | 62.5031 | 59.6329 | 59.8068 | 122.5891 | 59.6832 | 62.6404
8978.4844 | 0.061035 | 0.39948 | -0.77652 | -0.22003 | 0.12711 | -0.23819 | -0.18158 | 62.8555 | -59.3536 | 0.10986 | -59.6603 | 62.7686 | 59.5551 | 59.5413 | 0.045776 | -0.066223 | 0.066223 | 0.28091 | -0.1474 | -0.17838 | 0.13733 | 0.12817 | -59.8663 | 62.7182 | 62.6907 | 59.5505 | 59.7061 | 122.58 | 59.523 | 62.7914
8980.2656 | 0.045776 | 0.43686 | -0.79254 | -0.21576 | 0.11643 | -0.29694 | -0.17624 | 62.9196 | -59.2346 | 0.050354 | -59.5505 | 62.851 | 59.4315 | 59.3765 | 0.061035 | -0.10147 | 0.052338 | 0.29159 | -0.16876 | -0.16556 | 0.054932 | 0.082397 | -59.6832 | 62.8235 | 62.8006 | 59.3811 | 59.5917 | 122.525 | 59.436 | 62.9425
8982.0625 | 0.061035 | 0.38559 | -0.76691 | -0.23926 | 0.12817 | -0.24033 | -0.18906 | 62.8235 | -59.436 | -0.009155 | -59.6924 | 62.8281 | 59.5413 | 59.523 | 0.061035 | -0.065155 | 0.074768 | 0.28946 | -0.15381 | -0.1709 | 0.068665 | 0.032043 | -59.8572 | 62.796 | 62.7274 | 59.5093 | 59.6832 | 122.5983 | 59.5139 | 62.8189
8983.7812 | 0.061035 | 0.40695 | -0.77866 | -0.24246 | 0.13245 | -0.26382 | -0.19226 | 62.9883 | -59.1751 | 0.19684 | -59.5001 | 62.8784 | 59.4315 | 59.3948 | 0.061035 | -0.09613 | 0.069427 | 0.29053 | -0.16556 | -0.16449 | 0.11902 | 0.12817 | -59.6786 | 62.8601 | 62.8372 | 59.3765 | 59.5642 | 122.4609 | 59.4406 | 62.9562
8985.5781 | 0.076294 | 0.41443 | -0.77438 | -0.23071 | 0.12817 | -0.27237 | -0.18906 | 63.1393 | -59.0332 | 0.16937 | -59.3582 | 63.0249 | 59.2758 | 59.2255 | 0.061035 | -0.09079 | 0.05127 | 0.28198 | -0.15701 | -0.16876 | 0.091553 | 0.086975 | -59.5505 | 63.0066 | 63.0112 | 59.2392 | 59.4177 | 122.5021 | 59.2804 | 63.121
8987.375 | 0.045776 | 0.42618 | -0.78934 | -0.23178 | 0.14206 | -0.27985 | -0.18799 | 63.089 | -59.0607 | 0.086975 | -59.3719 | 63.0249 | 59.2667 | 59.2117 | 0.061035 | -0.10361 | 0.05127 | 0.28412 | -0.16556 | -0.16663 | 0.091553 | 0.10529 | -59.4727 | 62.9654 | 62.9654 | 59.2529 | 59.3857 | 122.5342 | 59.3262 | 63.1027
8989.1719 | 0.061035 | 0.39841 | -0.77972 | -0.21683 | 0.14633 | -0.23392 | -0.1709 | 63.1531 | -59.0698 | 0.068665 | -59.3628 | 63.1256 | 59.2346 | 59.2163 | 0.045776 | -0.070496 | 0.05127 | 0.298 | -0.14313 | -0.17197 | 0.091553 | 0.073242 | -59.5505 | 63.0798 | 63.0478 | 59.1705 | 59.3994 | 122.5662 | 59.2117 | 63.1119
8990.9062 | 0.091553 | 0.43259 | -0.78186 | -0.2446 | 0.13458 | -0.28412 | -0.18585 | 63.2996 | -58.8501 | 0.17853 | -59.2072 | 63.1439 | 59.1431 | 59.0973 | 0.030518 | -0.10468 | 0.058746 | 0.28198 | -0.17517 | -0.16342 | 0.16937 | 0.17395 | -59.2896 | 63.0615 | 63.0707 | 59.1019 | 59.2575 | 122.5342 | 59.166 | 63.2217
8992.6875 | 0.061035 | 0.40695 | -0.77225 | -0.21469 | 0.13138 | -0.2446 | -0.18692 | 63.2904 | -58.9005 | 0.12817 | -59.2072 | 63.2538 | 59.079 | 59.0652 | 0.061035 | -0.0737 | 0.0737 | 0.298 | -0.15381 | -0.17197 | 0.14648 | 0.11444 | -59.3857 | 63.2034 | 63.176 | 59.0698 | 59.2346 | 122.6166 | 59.079 | 63.2263
8994.4688 | 0.061035 | 0.40909 | -0.77972 | -0.24353 | 0.13992 | -0.29373 | -0.16876 | 63.3591 | -58.7494 | 0.21057 | -59.1202 | 63.2217 | 59.0424 | 59.0195 | 0.061035 | -0.10468 | 0.067291 | 0.29159 | -0.17303 | -0.16449 | 0.16479 | 0.1831 | -59.2529 | 63.1943 | 63.1668 | 59.0286 | 59.1934 | 122.4838 | 59.0836 | 63.2904
8996.1719 | 0.045776 | 0.39948 | -0.77545 | -0.23605 | 0.14206 | -0.26916 | -0.17731 | 63.2996 | -58.8318 | 0.20142 | -59.166 | 63.1851 | 59.111 | 59.0698 | 0.030518 | -0.092926 | 0.061951 | 0.28305 | -0.1506 | -0.1741 | 0.13733 | 0.15106 | -59.3536 | 63.1302 | 63.0936 | 59.0881 | 59.2621 | 122.4747 | 59.1614 | 63.2492
8997.9531 | 0.061035 | 0.40909 | -0.77118 | -0.23605 | 0.1239 | -0.26382 | -0.18265 | 63.3774 | -58.7311 | 0.19684 | -59.0881 | 63.2858 | 59.0332 | 58.9645 | 0.076294 | -0.077972 | 0.081177 | 0.28839 | -0.16769 | -0.17197 | 0.12817 | 0.11902 | -59.285 | 63.2492 | 63.2217 | 59.0149 | 59.1522 | 122.4655 | 59.0515 | 63.3453
8999.75 | 0.045776 | 0.40695 | -0.76797 | -0.21683 | 0.13138 | -0.25101 | -0.17303 | 63.3224 | -58.8547 | 0.10986 | -59.1568 | 63.3133 | 59.024 | 59.0103 | 0.076294 | -0.079041 | 0.063019 | 0.29587 | -0.1474 | -0.16983 | 0.13275 | 0.10071 | -59.3308 | 63.2355 | 63.2309 | 59.0195 | 59.1934 | 122.6028 | 59.0378 | 63.2492
9001.4844 | 0.076294 | 0.4187 | -0.79147 | -0.21896 | 0.13031 | -0.27985 | -0.18906 | 63.4872 | -58.6166 | 0.22888 | -59.0103 | 63.3499 | 58.9417 | 58.8867 | 0.061035 | -0.09613 | 0.054474 | 0.28091 | -0.15808 | -0.16449 | 0.16479 | 0.16937 | -59.1156 | 63.3224 | 63.2904 | 58.905 | 59.0652 | 122.4792 | 58.9966 | 63.4094
9003.2969 | 0.076294 | 0.42618 | -0.77545 | -0.22537 | 0.12604 | -0.27878 | -0.18158 | 63.4552 | -58.6945 | 0.11902 | -59.0469 | 63.3408 | 58.9096 | 58.905 | 0.061035 | -0.086517 | 0.050201 | 0.27664 | -0.16449 | -0.18051 | 0.086975 | 0.086975 | -59.1705 | 63.295 | 63.295 | 58.8776 | 59.0652 | 122.4976 | 58.9645 | 63.414
9005.0156 | 0.045776 | 0.42084 | -0.76263 | -0.21683 | 0.13031 | -0.27451 | -0.18265 | 63.5101 | -58.6349 | 0.16022 | -58.992 | 63.3545 | 58.8959 | 58.8684 | 0.076294 | -0.089722 | 0.061951 | 0.27344 | -0.15595 | -0.16983 | 0.14648 | 0.14191 | -59.1156 | 63.2858 | 63.2858 | 58.8959 | 59.0286 | 122.525 | 58.9279 | 63.4277
9006.7969 | 0.076294 | 0.42511 | -0.77011 | -0.22964 | 0.11429 | -0.26703 | -0.17303 | 63.6154 | -58.548 | 0.14648 | -58.9188 | 63.4415 | 58.8409 | 58.7677 | 0.076294 | -0.1004 | 0.065155 | 0.28198 | -0.14847 | -0.17838 | 0.15564 | 0.13275 | -59.0378 | 63.4048 | 63.3316 | 58.7997 | 58.9691 | 122.5983 | 58.7952 | 63.5147
9008.5938 | 0.061035 | 0.41229 | -0.784 | -0.2211 | 0.1239 | -0.26703 | -0.18585 | 63.6749 | -58.4656 | 0.16937 | -58.8181 | 63.5056 | 58.7631 | 58.699 | 0.045776 | -0.091858 | 0.068359 | 0.28412 | -0.14954 | -0.16876 | 0.14648 | 0.15564 | -58.9737 | 63.4872 | 63.3911 | 58.7448 | 58.8776 | 122.5937 | 58.7357 | 63.6063
9010.375 | 0.045776 | 0.41443 | -0.77866 | -0.23285 | 0.12817 | -0.27557 | -0.17944 | 63.652 | -58.4473 | 0.2655 | -58.8593 | 63.4964 | 58.7677 | 58.7357 | 0.061035 | -0.097198 | 0.061951 | 0.27664 | -0.15167 | -0.17517 | 0.17395 | 0.1831 | -58.9828 | 63.4369 | 63.4369 | 58.754 | 58.9279 | 122.4884 | 58.8455 | 63.5925
9012.1562 | 0.061035 | 0.39841 | -0.77972 | -0.24139 | 0.13031 | -0.27451 | -0.18799 | 63.6795 | -58.4839 | 0.18768 | -58.8455 | 63.6108 | 58.7402 | 58.6853 | 0.061035 | -0.09079 | 0.061951 | 0.28946 | -0.16235 | -0.16663 | 0.10986 | 0.068665 | -59.0057 | 63.5788 | 63.5468 | 58.6899 | 58.8638 | 122.493 | 58.7219 | 63.6566
9013.875 | 0.045776 | 0.41657 | -0.77759 | -0.23392 | 0.13245 | -0.28305 | -0.18265 | 63.7894 | -58.3008 | 0.20142 | -58.699 | 63.6887 | 58.6121 | 58.5663 | 0.061035 | -0.095062 | 0.066223 | 0.28412 | -0.16342 | -0.16876 | 0.16022 | 0.13733 | -58.7906 | 63.6017 | 63.5788 | 58.5617 | 58.7494 | 122.5342 | 58.6395 | 63.7115
9015.6719 | 0.061035 | 0.41229 | -0.77759 | -0.24246 | 0.13779 | -0.25421 | -0.1741 | 63.7985 | -58.3694 | 0.16937 | -58.7219 | 63.7665 | 58.5983 | 58.5617 | 0.091553 | -0.072632 | 0.059814 | 0.28412 | -0.14847 | -0.18372 | 0.1236 | 0.07782 | -58.9005 | 63.707 | 63.6795 | 58.5526 | 58.7219 | 122.5616 | 58.5846 | 63.7344
9017.4688 | 0.061035 | 0.392 | -0.78079 | -0.22537 | 0.12817 | -0.23498 | -0.18158 | 63.9221 | -58.2138 | 0.17853 | -58.5846 | 63.8535 | 58.5159 | 58.4793 | 0.045776 | -0.074768 | 0.068359 | 0.28625 | -0.13565 | -0.18158 | 0.1831 | 0.13733 | -58.7585 | 63.7619 | 63.7527 | 58.4656 | 58.6533 | 122.612 | 58.4702 | 63.8214
9019.25 | 0.045776 | 0.43579 | -0.78507 | -0.21576 | 0.1239 | -0.28946 | -0.18692 | 64.0457 | -57.9941 | 0.27466 | -58.4473 | 63.8901 | 58.4106 | 58.342 | 0.045776 | -0.10681 | 0.055542 | 0.27878 | -0.15274 | -0.16342 | 0.1831 | 0.18768 | -58.5754 | 63.8351 | 63.8168 | 58.3511 | 58.5159 | 122.525 | 58.4106 | 63.945
9020.9688 | 0.030518 | 0.39948 | -0.77972 | -0.22858 | 0.13138 | -0.26596 | -0.19226 | 63.9999 | -58.0902 | 0.19684 | -58.4885 | 63.9862 | 58.3878 | 58.342 | 0.045776 | -0.084381 | 0.061951 | 0.28305 | -0.15274 | -0.16983 | 0.1236 | 0.07782 | -58.6716 | 63.9221 | 63.8763 | 58.3969 | 58.5434 | 122.4884 | 58.4106 | 63.9999
9022.7812 | 0.045776 | 0.40375 | -0.77011 | -0.22858 | 0.14099 | -0.25421 | -0.17197 | 64.1144 | -57.9758 | 0.21515 | -58.3832 | 64.0366 | 58.2779 | 58.2458 | 0.045776 | -0.077972 | 0.074768 | 0.2948 | -0.13458 | -0.17944 | 0.20142 | 0.14191 | -58.5434 | 64.0091 | 63.9542 | 58.2687 | 58.4427 | 122.6212 | 58.2733 | 64.0549
9024.5 | 0.061035 | 0.40268 | -0.78079 | -0.24994 | 0.12924 | -0.28412 | -0.18051 | 64.357 | -57.6874 | 0.32044 | -58.136 | 64.2014 | 58.0307 | 58.0078 | 0.045776 | -0.098267 | 0.071564 | 0.27878 | -0.17517 | -0.1709 | 0.19684 | 0.1831 | -58.2596 | 64.1602 | 64.183 | 58.0215 | 58.2047 | 122.4792 | 58.0811 | 64.2929
9026.2812 | 0.061035 | 0.41336 | -0.76477 | -0.22644 | 0.12176 | -0.2446 | -0.17303 | 64.5035 | -57.6004 | 0.21515 | -58.0124 | 64.4531 | 57.9025 | 57.8705 | 0.061035 | -0.076904 | 0.060883 | 0.29694 | -0.14526 | -0.1709 | 0.18768 | 0.11902 | -58.2047 | 64.3936 | 64.3387 | 57.8751 | 58.0399 | 122.58 | 57.8934 | 64.4394
9028.0938 | 0.076294 | 0.41229 | -0.77972 | -0.20081 | 0.13886 | -0.27664 | -0.18372 | 64.6545 | -57.3807 | 0.20142 | -57.8293 | 64.5218 | 57.7377 | 57.6599 | 0.076294 | -0.097198 | 0.052338 | 0.28839 | -0.14954 | -0.16769 | 0.17853 | 0.15564 | -57.9529 | 64.4714 | 64.4669 | 57.7332 | 57.8842 | 122.5571 | 57.7515 | 64.6042
9029.8125 | 0.061035 | 0.40802 | -0.78079 | -0.23178 | 0.12711 | -0.26596 | -0.17624 | 64.7141 | -57.3578 | 0.19684 | -57.7698 | 64.7232 | 57.6508 | 57.5958 | 0.045776 | -0.077972 | 0.072632 | 0.28625 | -0.15808 | -0.16876 | 0.14191 | 0.07782 | -57.9437 | 64.7003 | 64.65 | 57.6187 | 57.7789 | 122.5616 | 57.6279 | 64.7278
9031.5938 | 0.076294 | 0.43152 | -0.77331 | -0.23498 | 0.1239 | -0.28091 | -0.17624 | 64.8285 | -57.2113 | 0.17853 | -57.6553 | 64.7369 | 57.5226 | 57.4997 | 0.030518 | -0.098267 | 0.058746 | 0.28625 | -0.17624 | -0.16235 | 0.12817 | 0.064087 | -57.7789 | 64.6729 | 64.6912 | 57.4997 | 57.6874 | 122.4884 | 57.5729 | 64.8376
9033.375 | 0.061035 | 0.41336 | -0.76904 | -0.20187 | 0.11429 | -0.25528 | -0.17731 | 64.9338 | -57.1472 | 0.2243 | -57.5592 | 64.8285 | 57.4539 | 57.4356 | 0.030518 | -0.069427 | 0.052338 | 0.28625 | -0.14526 | -0.1709 | 0.19684 | 0.11902 | -57.7011 | 64.7644 | 64.7461 | 57.4356 | 57.5912 | 122.6212 | 57.4448 | 64.856
9035.0938 | 0.076294 | 0.39841 | -0.77652 | -0.2446 | 0.13672 | -0.26596 | -0.18585 | 65.0253 | -57.0145 | 0.27924 | -57.4539 | 64.975 | 57.3532 | 57.3166 | 0.045776 | -0.084381 | 0.070496 | 0.28625 | -0.16342 | -0.16556 | 0.14648 | 0.073242 | -57.6416 | 64.9429 | 64.9017 | 57.3395 | 57.4951 | 122.4976 | 57.4036 | 65.0391
9036.8906 | 0.045776 | 0.42404 | -0.77866 | -0.2446 | 0.13031 | -0.28412 | -0.19226 | 65.3412 | -56.694 | 0.32959 | -57.1609 | 65.1627 | 57.0877 | 57.0602 | 0.061035 | -0.092926 | 0.065155 | 0.28412 | -0.15915 | -0.1709 | 0.20142 | 0.18768 | -57.2937 | 65.1215 | 65.1123 | 57.0694 | 57.2479 | 122.4976 | 57.106 | 65.2679
9038.625 | 0.061035 | 0.41336 | -0.78613 | -0.22964 | 0.13458 | -0.27344 | -0.18799 | 65.3778 | -56.6391 | 0.32501 | -57.1106 | 65.2359 | 57.0374 | 57.019 | 0.061035 | -0.10254 | 0.058746 | 0.27557 | -0.15381 | -0.16663 | 0.20142 | 0.16022 | -57.2662 | 65.2084 | 65.1855 | 57.0236 | 57.193 | 122.4884 | 57.0831 | 65.3229
9040.4062 | 0.061035 | 0.38666 | -0.76584 | -0.22751 | 0.1239 | -0.23926 | -0.18158 | 65.4648 | -56.5979 | 0.21973 | -57.0419 | 65.4053 | 56.987 | 56.9275 | 0.061035 | -0.077972 | 0.068359 | 0.29053 | -0.13672 | -0.1741 | 0.22888 | 0.14648 | -57.2433 | 65.3229 | 65.2634 | 56.9412 | 57.1152 | 122.612 | 56.9183 | 65.387
9042.125 | 0.061035 | 0.42297 | -0.79147 | -0.23071 | 0.14633 | -0.28625 | -0.18051 | 65.5563 | -56.4285 | 0.16479 | -56.9229 | 65.4739 | 56.8268 | 56.7673 | 0.061035 | -0.10147 | 0.053406 | 0.28412 | -0.16129 | -0.15915 | 0.15106 | 0.086975 | -57.0648 | 65.4099 | 65.3641 | 56.7856 | 56.9595 | 122.493 | 56.8497 | 65.5518
9043.9219 | 0.061035 | 0.43045 | -0.77545 | -0.21255 | 0.14313 | -0.26062 | -0.1709 | 65.6662 | -56.3324 | 0.11902 | -56.8222 | 65.4968 | 56.7444 | 56.7215 | 0.045776 | -0.088654 | 0.061951 | 0.28412 | -0.1506 | -0.16663 | 0.19684 | 0.13275 | -56.9824 | 65.4556 | 65.4327 | 56.7261 | 56.8954 | 122.6074 | 56.781 | 65.5655
9045.7188 | 0.045776 | 0.41016 | -0.77118 | -0.20615 | 0.12283 | -0.24353 | -0.17731 | 65.5975 | -56.4331 | 0.009155 | -56.8726 | 65.6296 | 56.7398 | 56.7261 | 0.091553 | -0.079041 | 0.064087 | 0.27664 | -0.13458 | -0.17303 | 0.13733 | 0.045776 | -57.1014 | 65.5655 | 65.506 | 56.7215 | 56.8817 | 122.5708 | 56.7169 | 65.6021
9047.5 | 0.091553 | 0.40054 | -0.78507 | -0.23712 | 0.13886 | -0.26596 | -0.17944 | 65.7715 | -56.1951 | 0.07782 | -56.694 | 65.7761 | 56.5704 | 56.5613 | 0.061035 | -0.09079 | 0.069427 | 0.27878 | -0.15915 | -0.17197 | 0.14191 | 0.054932 | -56.8817 | 65.7532 | 65.6891 | 56.543 | 56.7261 | 122.5342 | 56.575 | 65.8081
9049.2031 | 0.061035 | 0.40909 | -0.77118 | -0.21683 | 0.12711 | -0.25101 | -0.16983 | 65.7623 | -56.2317 | -0.036621 | -56.7169 | 65.7761 | 56.5887 | 56.5475 | 0.076294 | -0.075836 | 0.059814 | 0.28946 | -0.14099 | -0.16983 | 0.11902 | 0.041199 | -56.9183 | 65.7303 | 65.7028 | 56.543 | 56.7535 | 122.5891 | 56.5613 | 65.7852
9050.9844 | 0.030518 | 0.39093 | -0.76584 | -0.24353 | 0.1207 | -0.24994 | -0.17303 | 66.0141 | -55.9525 | 0.059509 | -56.4514 | 65.9775 | 56.3644 | 56.3507 | 0.061035 | -0.066223 | 0.067291 | 0.28839 | -0.14954 | -0.16129 | 0.21057 | 0.10986 | -56.6528 | 65.9042 | 65.863 | 56.3782 | 56.5155 | 122.6166 | 56.337 | 65.9546
9052.7812 | 0.061035 | 0.43686 | -0.77011 | -0.21469 | 0.12176 | -0.28412 | -0.18158 | 66.1331 | -55.7602 | 0.027466 | -56.3278 | 65.9958 | 56.2454 | 56.2088 | 0.076294 | -0.099335 | 0.050201 | 0.28946 | -0.17517 | -0.16235 | 0.16937 | 0.064087 | -56.4743 | 65.9546 | 65.9546 | 56.2225 | 56.3782 | 122.4884 | 56.2729 | 66.1011
9054.5469 | 0.061035 | 0.4187 | -0.77759 | -0.23926 | 0.1239 | -0.28732 | -0.18372 | 66.3116 | -55.5862 | 0.091553 | -56.163 | 66.1743 | 56.0898 | 56.0623 | 0.045776 | -0.10681 | 0.061951 | 0.28839 | -0.17197 | -0.16663 | 0.21973 | 0.14191 | -56.3095 | 66.124 | 66.0828 | 56.1081 | 56.25 | 122.493 | 56.131 | 66.2521
9056.3281 | 0.061035 | 0.40909 | -0.77438 | -0.24033 | 0.12283 | -0.26276 | -0.17303 | 66.3437 | -55.5908 | -0.022888 | -56.1218 | 66.3528 | 56.0257 | 55.9845 | 0.076294 | -0.077972 | 0.082245 | 0.28732 | -0.15595 | -0.1741 | 0.16022 | 0.073242 | -56.3232 | 66.2888 | 66.2521 | 56.0074 | 56.1584 | 122.5937 | 56.0028 | 66.3025
9058.1406 | 0.061035 | 0.39414 | -0.76263 | -0.22217 | 0.12497 | -0.23605 | -0.17731 | 66.3986 | -55.5222 | -0.086975 | -56.0761 | 66.3757 | 55.9753 | 55.925 | 0.061035 | -0.075836 | 0.074768 | 0.29373 | -0.14206 | -0.17731 | 0.14648 | 0.064087 | -56.2775 | 66.3437 | 66.3071 | 55.9341 | 56.1264 | 122.5662 | 55.9479 | 66.3712
9059.8594 | 0.076294 | 0.41016 | -0.76904 | -0.24033 | 0.12711 | -0.28412 | -0.17731 | 66.774 | -55.0781 | 0.11444 | -55.7007 | 66.6412 | 55.6229 | 55.6183 | 0.061035 | -0.099335 | 0.057678 | 0.28839 | -0.16663 | -0.17624 | 0.2243 | 0.1831 | -55.8517 | 66.5863 | 66.6092 | 55.6229 | 55.7648 | 122.5021 | 55.6732 | 66.7053
9061.6406 | 0.030518 | 0.41977 | -0.76691 | -0.22003 | 0.13031 | -0.26276 | -0.18692 | 66.8243 | -55.0644 | -0.045776 | -55.6503 | 66.7419 | 55.5496 | 55.5359 | 0.030518 | -0.086517 | 0.064087 | 0.28946 | -0.14954 | -0.18158 | 0.20599 | 0.14648 | -55.7968 | 66.687 | 66.6641 | 55.5313 | 55.6824 | 122.612 | 55.5588 | 66.7419
9063.4375 | 0.045776 | 0.40588 | -0.76904 | -0.2243 | 0.13779 | -0.27451 | -0.17838 | 67.0807 | -54.7943 | 0.013733 | -55.4306 | 66.9205 | 55.3299 | 55.2704 | 0.076294 | -0.092926 | 0.072632 | 0.29053 | -0.16342 | -0.17838 | 0.17853 | 0.1236 | -55.5634 | 66.8838 | 66.8518 | 55.3024 | 55.5038 | 122.5159 | 55.3757 | 67.0074
9065.1562 | 0.045776 | 0.40588 | -0.77331 | -0.23498 | 0.13458 | -0.2446 | -0.18478 | 67.0532 | -54.8309 | -0.022888 | -55.4489 | 67.012 | 55.3391 | 55.3024 | 0.030518 | -0.077972 | 0.064087 | 0.29587 | -0.13779 | -0.18265 | 0.16937 | 0.10529 | -55.6686 | 66.9571 | 66.9113 | 55.3116 | 55.4993 | 122.58 | 55.3207 | 66.9983
9066.9375 | 0.061035 | 0.39841 | -0.77972 | -0.23178 | 0.13886 | -0.27557 | -0.18478 | 67.2455 | -54.5288 | 0.10529 | -55.2063 | 67.1539 | 55.1239 | 55.0735 | 0.061035 | -0.10361 | 0.070496 | 0.28839 | -0.16022 | -0.1741 | 0.20142 | 0.17853 | -55.3711 | 67.1036 | 67.0944 | 55.0964 | 55.2658 | 122.4701 | 55.1605 | 67.2318
9068.7344 | 0.076294 | 0.41016 | -0.76584 | -0.21469 | 0.14313 | -0.24994 | -0.17944 | 67.2684 | -54.6066 | 0.013733 | -55.2109 | 67.2089 | 55.1651 | 55.1102 | 0.061035 | -0.076904 | 0.055542 | 0.28305 | -0.14633 | -0.16769 | 0.20599 | 0.13733 | -55.4214 | 67.1722 | 67.1219 | 55.1056 | 55.2933 | 122.58 | 55.1239 | 67.1997
9070.5312 | 0.045776 | 0.43259 | -0.77759 | -0.2243 | 0.11963 | -0.28625 | -0.18158 | 67.2638 | -54.5334 | 0.032043 | -55.2109 | 67.1402 | 55.0919 | 55.0964 | 0.061035 | -0.10254 | 0.042725 | 0.27557 | -0.16235 | -0.15488 | 0.14191 | 0.10071 | -55.3528 | 67.1082 | 67.1219 | 55.069 | 55.2475 | 122.4884 | 55.1697 | 67.2409
9072.2344 | 0.045776 | 0.42511 | -0.77331 | -0.23712 | 0.13779 | -0.29266 | -0.18906 | 67.4103 | -54.3732 | 0.16937 | -55.0644 | 67.3141 | 54.9866 | 54.9408 | 0.045776 | -0.11429 | 0.054474 | 0.27344 | -0.16129 | -0.15915 | 0.16937 | 0.1236 | -55.1834 | 67.2272 | 67.2409 | 54.95 | 55.1147 | 122.5342 | 55.014 | 67.3874
9074.0156 | 0.076294 | 0.40588 | -0.76477 | -0.23392 | 0.13351 | -0.23712 | -0.18265 | 67.4286 | -54.4281 | 0.018311 | -55.0735 | 67.3691 | 54.9866 | 54.9728 | 0.045776 | -0.080109 | 0.070496 | 0.29053 | -0.1474 | -0.18478 | 0.20142 | 0.10529 | -55.275 | 67.2867 | 67.2913 | 54.9957 | 55.1376 | 122.6028 | 54.9637 | 67.3279
9075.8125 | 0.061035 | 0.4187 | -0.77972 | -0.23605 | 0.12283 | -0.29053 | -0.18585 | 67.6941 | -54.0665 | 0.14191 | -54.7806 | 67.543 | 54.7119 | 54.6753 | 0.045776 | -0.1004 | 0.060883 | 0.28091 | -0.16556 | -0.16449 | 0.17395 | 0.12817 | -54.9271 | 67.5201 | 67.4835 | 54.6982 | 54.8584 | 122.5159 | 54.7485 | 67.6117
9077.6094 | 0.061035 | 0.41763 | -0.7637 | -0.23071 | 0.12924 | -0.26062 | -0.17944 | 67.9092 | -53.9246 | -0.013733 | -54.5746 | 67.8452 | 54.4785 | 54.4464 | 0.061035 | -0.075836 | 0.0737 | 0.30334 | -0.14847 | -0.16983 | 0.14648 | 0.086975 | -54.7028 | 67.7902 | 67.7536 | 54.4601 | 54.5929 | 122.612 | 54.4739 | 67.8497
9079.3281 | 0.045776 | 0.4187 | -0.77866 | -0.23498 | 0.13992 | -0.2713 | -0.19119 | 67.9962 | -53.7506 | 0.19226 | -54.4739 | 67.8864 | 54.3915 | 54.3823 | 0.076294 | -0.080109 | 0.066223 | 0.28412 | -0.16449 | -0.18265 | 0.13733 | 0.041199 | -54.6753 | 67.8497 | 67.8314 | 54.4052 | 54.5563 | 122.4564 | 54.4281 | 67.9413
9081.125 | 0.076294 | 0.41443 | -0.77759 | -0.22644 | 0.12497 | -0.28305 | -0.18692 | 67.7948 | -53.9749 | 0.073242 | -54.689 | 67.6941 | 54.5929 | 54.5425 | 0.076294 | -0.10254 | 0.05661 | 0.28946 | -0.15274 | -0.16876 | 0.091553 | -0.013733 | -54.8447 | 67.6437 | 67.662 | 54.5425 | 54.7485 | 122.4701 | 54.6433 | 67.7628
9082.9219 | 0.045776 | 0.40909 | -0.77545 | -0.24246 | 0.12924 | -0.27878 | -0.18478 | 68.0557 | -53.627 | 0.28839 | -54.4052 | 67.923 | 54.364 | 54.3091 | 0.045776 | -0.099335 | 0.067291 | 0.28946 | -0.16983 | -0.18372 | 0.13275 | 0.068665 | -54.5883 | 67.8818 | 67.868 | 54.3182 | 54.4922 | 122.4655 | 54.3961 | 68.0099
9084.7188 | 0.045776 | 0.40161 | -0.7637 | -0.21362 | 0.11643 | -0.23392 | -0.18692 | 68.129 | -53.6133 | 0.25635 | -54.3549 | 68.0603 | 54.2816 | 54.277 | 0.045776 | -0.064087 | 0.055542 | 0.30121 | -0.13245 | -0.16663 | 0.13733 | 0.050354 | -54.5609 | 68.0008 | 67.9825 | 54.2725 | 54.4235 | 122.5937 | 54.2679 | 68.042
9086.5 | 0.061035 | 0.40482 | -0.77118 | -0.23926 | 0.13245 | -0.26489 | -0.18585 | 68.66 | -53.0411 | 0.2655 | -53.7781 | 68.692 | 53.6957 | 53.6453 | 0.045776 | -0.0737 | 0.070496 | 0.29053 | -0.15488 | -0.17197 | 0.009155 | -0.032043 | -53.9886 | 68.6325 | 68.6005 | 53.6591 | 53.8147 | 122.5754 | 53.6682 | 68.6691
9088.2188 | 0.061035 | 0.39414 | -0.77545 | -0.23926 | 0.13351 | -0.27344 | -0.17303 | 68.8934 | -52.7573 | 0.29297 | -53.54 | 68.9392 | 53.4393 | 53.3981 | 0.061035 | -0.079041 | 0.068359 | 0.29266 | -0.16022 | -0.16663 | -0.004578 | 0 | -53.7552 | 68.8751 | 68.8477 | 53.4348 | 53.5675 | 122.5296 | 53.4531 | 68.9438
9090 | 0.030518 | 0.43366 | -0.78613 | -0.22751 | 0.13245 | -0.28625 | -0.18372 | 68.6096 | -53.0136 | 0.27924 | -53.8467 | 68.5181 | 53.7231 | 53.7048 | 0.076294 | -0.10361 | 0.054474 | 0.28946 | -0.16342 | -0.17303 | -0.032043 | -0.045776 | -53.9932 | 68.4814 | 68.4677 | 53.714 | 53.8742 | 122.4792 | 53.7735 | 68.6325
9091.7656 | 0.045776 | 0.4155 | -0.78079 | -0.22858 | 0.13138 | -0.27023 | -0.18158 | 68.866 | -52.7756 | 0.49439 | -53.5812 | 68.7195 | 53.5492 | 53.5172 | 0.061035 | -0.089722 | 0.064087 | 0.28198 | -0.15701 | -0.1741 | 0.036621 | 0.045776 | -53.7781 | 68.7149 | 68.692 | 53.5126 | 53.6682 | 122.4792 | 53.5675 | 68.8339
9093.5625 | 0.061035 | 0.39841 | -0.77118 | -0.22858 | 0.13245 | -0.24139 | -0.17731 | 69.1498 | -52.533 | 0.4303 | -53.3203 | 69.1269 | 53.2196 | 53.1967 | 0.091553 | -0.069427 | 0.058746 | 0.29373 | -0.15274 | -0.16983 | 0.004578 | -0.032043 | -53.5263 | 69.0674 | 69.0628 | 53.2059 | 53.3569 | 122.6028 | 53.1967 | 69.104
9095.3438 | 0.061035 | 0.41122 | -0.77545 | -0.2179 | 0.1207 | -0.25207 | -0.18051 | 69.3192 | -52.3636 | 0.43488 | -53.1509 | 69.2825 | 53.0365 | 53.0045 | 0.061035 | -0.071564 | 0.060883 | 0.29159 | -0.15167 | -0.16235 | -0.027466 | -0.13733 | -53.3295 | 69.2459 | 69.2093 | 53.0136 | 53.1555 | 122.6303 | 53.0182 | 69.2825
9097.0469 | 0.045776 | 0.42725 | -0.77118 | -0.21042 | 0.13138 | -0.27237 | -0.17197 | 69.722 | -51.8875 | 0.6546 | -52.7481 | 69.5938 | 52.6611 | 52.6474 | 0.076294 | -0.097198 | 0.055542 | 0.28091 | -0.15595 | -0.17197 | 0.07782 | 0.10071 | -52.9129 | 69.5343 | 69.5114 | 52.6703 | 52.803 | 122.5296 | 52.7115 | 69.6762
9098.8281 | 0.061035 | 0.41977 | -0.78079 | -0.23819 | 0.13565 | -0.28625 | -0.18799 | 70.0287 | -51.5625 | 0.93384 | -52.4368 | 69.8868 | 52.359 | 52.359 | 0.045776 | -0.10254 | 0.058746 | 0.28305 | -0.15915 | -0.1709 | 0.13275 | 0.10529 | -52.6062 | 69.8135 | 69.7952 | 52.3727 | 52.5513 | 122.5021 | 52.4414 | 69.9738
9100.625 | 0.045776 | 0.4187 | -0.78613 | -0.24033 | 0.12817 | -0.26596 | -0.19867 | 69.7861 | -51.8188 | 0.87433 | -52.6657 | 69.7311 | 52.597 | 52.5787 | 0.061035 | -0.070496 | 0.067291 | 0.28198 | -0.16876 | -0.17838 | 0.068665 | 0.018311 | -52.9037 | 69.7083 | 69.6259 | 52.6108 | 52.771 | 122.4701 | 52.6245 | 69.7906
9102.4062 | 0.045776 | 0.41763 | -0.77545 | -0.21149 | 0.12711 | -0.24246 | -0.17197 | 70.0333 | -51.6174 | 0.78278 | -52.4094 | 70.0378 | 52.3132 | 52.2766 | 0.061035 | -0.076904 | 0.071564 | 0.29159 | -0.1442 | -0.17197 | 0.036621 | 0 | -52.6428 | 70.0104 | 69.9509 | 52.2949 | 52.4643 | 122.6212 | 52.2858 | 70.0607
9104.1406 | 0.061035 | 0.42831 | -0.78186 | -0.22644 | 0.13245 | -0.27664 | -0.19546 | 70.4086 | -51.1368 | 1.0162 | -52.0294 | 70.3354 | 51.9196 | 51.8875 | 0.061035 | -0.092926 | 0.061951 | 0.27664 | -0.15595 | -0.16983 | 0.009155 | 0.018311 | -52.1942 | 70.3171 | 70.2896 | 51.9333 | 52.066 | 122.493 | 51.9836 | 70.4178
9105.9375 | 0.061035 | 0.41336 | -0.7872 | -0.23926 | 0.12817 | -0.27344 | -0.18906 | 70.7199 | -50.7935 | 1.0391 | -51.6998 | 70.6421 | 51.6495 | 51.5991 | 0.061035 | -0.086517 | 0.068359 | 0.27557 | -0.17303 | -0.17624 | 0.018311 | -0.009155 | -51.86 | 70.578 | 70.5414 | 51.6083 | 51.7914 | 122.5525 | 51.6861 | 70.7062
9107.7344 | 0.061035 | 0.40588 | -0.77866 | -0.22537 | 0.12817 | -0.23178 | -0.1709 | 71.0037 | -50.6012 | 0.97961 | -51.4664 | 70.9579 | 51.3748 | 51.329 | 0.061035 | -0.065155 | 0.058746 | 0.28625 | -0.14526 | -0.18158 | -0.036621 | -0.082397 | -51.7136 | 70.9396 | 70.8755 | 51.384 | 51.5259 | 122.5662 | 51.3702 | 71.0083
9109.5156 | 0.045776 | 0.38238 | -0.78079 | -0.23926 | 0.1207 | -0.25207 | -0.17624 | 71.3562 | -50.2167 | 0.98877 | -51.0727 | 71.3791 | 50.9949 | 50.9766 | 0.061035 | -0.075836 | 0.069427 | 0.28519 | -0.1506 | -0.16983 | -0.032043 | 0.1236 | -51.3016 | 71.3058 | 71.2509 | 50.9949 | 51.1414 | 122.5983 | 50.9628 | 71.3425
9111.2969 | 0.061035 | 0.43366 | -0.78507 | -0.22217 | 0.12817 | -0.2948 | -0.17944 | 71.9238 | -49.53 | 0.99335 | -50.4593 | 71.8872 | 50.386 | 50.3952 | 0.045776 | -0.10254 | 0.063019 | 0.27771 | -0.17303 | -0.16449 | -0.004578 | 0.11902 | -50.6149 | 71.8369 | 71.814 | 50.354 | 50.5325 | 122.5204 | 50.4044 | 71.9513
9113.0938 | 0.061035 | 0.40802 | -0.77866 | -0.22217 | 0.13031 | -0.24246 | -0.16983 | 72.4045 | -49.173 | 0.86517 | -50.0381 | 72.4411 | 49.9283 | 49.9191 | 0.061035 | -0.083313 | 0.070496 | 0.29373 | -0.14206 | -0.16663 | -0.10529 | -0.027466 | -50.3036 | 72.377 | 72.3175 | 49.9191 | 50.0702 | 122.5571 | 49.9054 | 72.4319
9114.8125 | 0.076294 | 0.43152 | -0.76797 | -0.23819 | 0.13031 | -0.27878 | -0.17731 | 72.7341 | -48.761 | 1.0895 | -49.7131 | 72.6151 | 49.6353 | 49.6445 | 0.045776 | -0.095062 | 0.045929 | 0.28519 | -0.16449 | -0.17517 | -0.009155 | -0.10071 | -49.8825 | 72.5693 | 72.5418 | 49.617 | 49.7772 | 122.5021 | 49.6811 | 72.6974
9116.5938 | 0.061035 | 0.42191 | -0.78186 | -0.21683 | 0.14313 | -0.26703 | -0.18478 | 73.1369 | -48.3765 | 1.1032 | -49.2874 | 73.1735 | 49.1959 | 49.1821 | 0.045776 | -0.081177 | 0.067291 | 0.28839 | -0.15167 | -0.1709 | -0.09613 | 0.091553 | -49.5346 | 73.1277 | 73.0682 | 49.1776 | 49.3378 | 122.5571 | 49.2096 | 73.1461
9118.3125 | 0.061035 | 0.39948 | -0.77866 | -0.22537 | 0.13138 | -0.2446 | -0.18692 | 73.5718 | -47.9874 | 1.3458 | -48.8983 | 73.5214 | 48.8342 | 48.8068 | 0.061035 | -0.081177 | 0.052338 | 0.28519 | -0.1474 | -0.17197 | -0.068665 | 0.07782 | -49.1318 | 73.4711 | 73.4528 | 48.793 | 48.967 | 122.5708 | 48.8022 | 73.4711
9120.1094 | 0.061035 | 0.41977 | -0.78827 | -0.22751 | 0.13245 | -0.28625 | -0.18265 | 74.1394 | -47.319 | 1.4328 | -48.2666 | 74.1165 | 48.1567 | 48.1567 | 0.091553 | -0.098267 | 0.05661 | 0.28198 | -0.1709 | -0.16129 | -0.18768 | -0.004578 | -48.4451 | 74.0845 | 74.0707 | 48.143 | 48.3124 | 122.525 | 48.2071 | 74.1943
9121.8906 | 0.045776 | 0.41122 | -0.78079 | -0.25101 | 0.13245 | -0.2681 | -0.18906 | 74.7025 | -46.7514 | 1.5015 | -47.7356 | 74.6201 | 47.6624 | 47.6532 | 0.061035 | -0.09079 | 0.057678 | 0.28412 | -0.16876 | -0.16983 | -0.15106 | -0.073242 | -47.9553 | 74.6063 | 74.5514 | 47.6761 | 47.7859 | 122.4518 | 47.7356 | 74.7025
9123.625 | 0.045776 | 0.42191 | -0.77225 | -0.24033 | 0.13672 | -0.28946 | -0.18051 | 74.4049 | -47.0673 | 1.2817 | -48.0286 | 74.3774 | 47.9507 | 47.9324 | 0.061035 | -0.097198 | 0.065155 | 0.27664 | -0.17197 | -0.18372 | -0.30212 | -0.14191 | -48.2025 | 74.3042 | 74.295 | 47.9279 | 48.0972 | 122.5113 | 47.9645 | 74.4232
9125.4219 | 0.061035 | 0.40482 | -0.78934 | -0.22964 | 0.12283 | -0.25635 | -0.17303 | 74.025 | -47.4747 | 1.2497 | -48.4085 | 74.0616 | 48.3307 | 48.3078 | 0.061035 | -0.087585 | 0.066223 | 0.29159 | -0.1474 | -0.17303 | -0.31586 | -0.2243 | -48.6465 | 74.025 | 73.9609 | 48.3261 | 48.4543 | 122.525 | 48.3261 | 74.0616
9127.2031 | 0.061035 | 0.40375 | -0.77438 | -0.21683 | 0.12604 | -0.26062 | -0.16876 | 73.6404 | -47.7951 | 1.3046 | -48.8113 | 73.5168 | 48.7793 | 48.7473 | 0.061035 | -0.09079 | 0.057678 | 0.29159 | -0.14313 | -0.17731 | -0.32044 | -0.25177 | -49.0219 | 73.4528 | 73.4802 | 48.761 | 48.912 | 122.5616 | 48.7885 | 73.5535
9128.9375 | 0.061035 | 0.40482 | -0.77225 | -0.22964 | 0.1239 | -0.24246 | -0.16769 | 74.5193 | -46.962 | 1.1124 | -47.905 | 74.5468 | 47.8043 | 47.7951 | 0.061035 | -0.084381 | 0.067291 | 0.28732 | -0.14206 | -0.18265 | -0.43488 | -0.39368 | -48.1705 | 74.4965 | 74.4873 | 47.7997 | 47.9645 | 122.5845 | 47.7585 | 74.5468
9130.7344 | 0.045776 | 0.38879 | -0.77652 | -0.21362 | 0.13138 | -0.2478 | -0.1709 | 74.8901 | -46.5546 | 1.0712 | -47.5708 | 74.8581 | 47.4701 | 47.4701 | 0.076294 | -0.0737 | 0.067291 | 0.2948 | -0.13031 | -0.16876 | -0.52643 | -0.3891 | -47.8455 | 74.8306 | 74.8077 | 47.4747 | 47.6303 | 122.5525 | 47.4655 | 74.8764
9132.4531 | 0.045776 | 0.41443 | -0.77545 | -0.2243 | 0.1239 | -0.26703 | -0.1741 | 74.7986 | -46.6599 | 1.149 | -47.6624 | 74.675 | 47.5891 | 47.5845 | 0.061035 | -0.079041 | 0.076904 | 0.28946 | -0.1474 | -0.17838 | -0.62714 | -0.20142 | -47.8775 | 74.6292 | 74.6017 | 47.5754 | 47.7448 | 122.6074 | 47.612 | 74.7299
9134.25 | 0.045776 | 0.38773 | -0.77438 | -0.21042 | 0.14099 | -0.24353 | -0.16876 | 75.1602 | -46.3028 | 0.95673 | -47.2641 | 75.1465 | 47.1725 | 47.1588 | 0.076294 | -0.077972 | 0.063019 | 0.28732 | -0.14313 | -0.16983 | -0.86517 | -0.49439 | -47.5479 | 75.1602 | 75.1099 | 47.1771 | 47.3236 | 122.5479 | 47.1771 | 75.1877
9136.0469 | 0.061035 | 0.43579 | -0.77972 | -0.22964 | 0.13245 | -0.29373 | -0.18692 | 75.6454 | -45.694 | 1.1444 | -46.788 | 75.531 | 46.7331 | 46.7422 | 0.076294 | -0.10895 | 0.058746 | 0.27771 | -0.15167 | -0.15595 | -0.79651 | -0.39825 | -46.9711 | 75.4852 | 75.4486 | 46.7148 | 46.8658 | 122.4976 | 46.7926 | 75.6088
9137.7656 | 0.076294 | 0.41336 | -0.77652 | -0.2243 | 0.13031 | -0.25421 | -0.17517 | 75.7507 | -45.6482 | 1.03 | -46.669 | 75.7095 | 46.5683 | 46.582 | 0.045776 | -0.088654 | 0.054474 | 0.28625 | -0.12924 | -0.16983 | -1.03 | -0.97961 | -46.8704 | 75.6409 | 75.5951 | 46.5912 | 46.7285 | 122.6074 | 46.6141 | 75.7324
9139.5469 | 0.061035 | 0.39734 | -0.77011 | -0.22964 | 0.11215 | -0.25101 | -0.1741 | 75.8972 | -45.5246 | 1.0574 | -46.5317 | 75.8972 | 46.4767 | 46.4584 | 0.061035 | -0.088654 | 0.070496 | 0.28305 | -0.15701 | -0.17303 | -1.0025 | -0.737 | -46.7697 | 75.824 | 75.7828 | 46.4722 | 46.6278 | 122.6074 | 46.4355 | 75.8698
9141.3281 | 0.061035 | 0.42297 | -0.78827 | -0.22537 | 0.12497 | -0.28198 | -0.18692 | 76.1307 | -45.2316 | 1.0574 | -46.3303 | 76.0208 | 46.2341 | 46.225 | 0.045776 | -0.087585 | 0.054474 | 0.28198 | -0.16235 | -0.16235 | -1.1581 | -1.0529 | -46.5042 | 76.0071 | 75.9796 | 46.2296 | 46.3898 | 122.4655 | 46.2982 | 76.1078
9143.0469 | 0.045776 | 0.41763 | -0.79361 | -0.23071 | 0.11322 | -0.27771 | -0.18799 | 76.3458 | -44.9844 | 1.1032 | -46.0739 | 76.2451 | 46.0098 | 46.0144 | 0.061035 | -0.10468 | 0.058746 | 0.27985 | -0.16342 | -0.16663 | -1.2451 | -1.0666 | -46.2708 | 76.2268 | 76.1902 | 46.019 | 46.1517 | 122.4701 | 46.051 | 76.3275
9144.8438 | 0.076294 | 0.42191 | -0.79041 | -0.23605 | 0.12497 | -0.27878 | -0.18372 | 75.3845 | -45.9091 | 0.88348 | -46.994 | 75.3845 | 46.9208 | 46.9025 | 0.061035 | -0.10681 | 0.075836 | 0.27023 | -0.17303 | -0.17838 | -1.4191 | -1.4511 | -47.2137 | 75.3067 | 75.3113 | 46.9162 | 47.0718 | 122.525 | 46.9803 | 75.4532
9146.6406 | 0.076294 | 0.41229 | -0.77545 | -0.24353 | 0.12604 | -0.27557 | -0.19012 | 75.5264 | -45.726 | 0.98419 | -46.8933 | 75.4257 | 46.8475 | 46.8246 | 0.091553 | -0.095062 | 0.065155 | 0.27557 | -0.16022 | -0.18478 | -1.5518 | -1.3596 | -47.1085 | 75.3708 | 75.3342 | 46.8704 | 47.0032 | 122.4792 | 46.907 | 75.5127
9148.4219 | 0.076294 | 0.39627 | -0.77652 | -0.22003 | 0.13886 | -0.23605 | -0.19333 | 80.1086 | -41.304 | 1.6067 | -42.3477 | 80.0766 | 42.2516 | 42.2562 | 0.076294 | -0.069427 | 0.064087 | 0.29266 | -0.13565 | -0.18372 | -1.2863 | -0.99792 | -42.5674 | 80.04 | 79.9713 | 42.2424 | 42.4118 | 122.5845 | 42.2287 | 80.1132
9150.2031 | 0.061035 | 0.40268 | -0.78079 | -0.23819 | 0.11215 | -0.25955 | -0.20187 | 84.2651 | -37.2437 | 2.3163 | -38.1912 | 84.3018 | 38.0447 | 38.0402 | 0.076294 | -0.082245 | 0.082245 | 0.28519 | -0.16235 | -0.16556 | -1.1948 | -1.0345 | -38.4155 | 84.2285 | 84.2148 | 38.0539 | 38.1775 | 122.4335 | 38.1134 | 84.3475
9151.9844 | 0.061035 | 0.41336 | -0.77972 | -0.2243 | 0.13245 | -0.26382 | -0.17303 | 86.6821 | -34.8907 | 2.6321 | -35.8063 | 86.6272 | 35.701 | 35.6918 | 0.045776 | -0.089722 | 0.057678 | 0.27878 | -0.14847 | -0.17517 | -1.0117 | -0.79193 | -35.994 | 86.554 | 86.5356 | 35.701 | 35.82 | 122.5845 | 35.7239 | 86.618
9153.7031 | 0.061035 | 0.40375 | -0.76584 | -0.22324 | 0.1239 | -0.25101 | -0.16663 | 88.2935 | -33.3069 | 2.7832 | -34.1949 | 88.3392 | 34.0256 | 34.0485 | 0.061035 | -0.0737 | 0.067291 | 0.29907 | -0.14313 | -0.17731 | -1.1948 | -0.98419 | -34.4421 | 88.2935 | 88.2797 | 34.0164 | 34.1766 | 122.5067 | 34.0347 | 88.3301
9155.5 | 0.061035 | 0.41657 | -0.78186 | -0.24353 | 0.12924 | -0.29373 | -0.18372 | 88.9801 | -32.4738 | 2.9938 | -33.3984 | 89.0625 | 33.2382 | 33.2382 | 0.091553 | -0.09613 | 0.059814 | 0.28625 | -0.16663 | -0.16983 | -1.0162 | -0.98877 | -33.5861 | 88.9755 | 88.9847 | 33.2794 | 33.3939 | 122.4976 | 33.2703 | 89.1724
9157.2188 | 0.045776 | 0.40375 | -0.77972 | -0.21362 | 0.13138 | -0.24567 | -0.17944 | 89.9048 | -33.0185 | 2.1606 | -33.8058 | 88.8336 | 33.4488 | 33.4442 | 0.030518 | -0.080109 | 0.053406 | 0.28625 | -0.14847 | -0.16876 | -0.32044 | 0.013733 | -32.0984 | 89.6713 | 89.4699 | 32.9407 | 33.1604 | 122.5479 | 33.2703 | 89.0945
9159 | 0.061035 | 0.41657 | -0.77759 | -0.24139 | 0.13779 | -0.28305 | -0.18906 | 76.9638 | -44.1605 | 1.5564 | -45.433 | 76.8631 | 45.3918 | 45.3644 | 0.015259 | -0.10254 | 0.065155 | 0.2681 | -0.16983 | -0.16235 | -2.3071 | -2.6321 | -45.6253 | 76.8173 | 76.7624 | 45.401 | 45.52 | 122.4976 | 45.4102 | 76.9363
9160.7969 | 0.061035 | 0.40802 | -0.77225 | -0.24353 | 0.13992 | -0.26276 | -0.18478 | 48.2437 | -72.1298 | -2.3712 | -74.0479 | 48.1476 | 74.2172 | 74.1211 | 0.061035 | -0.087585 | 0.067291 | 0.29266 | -0.16022 | -0.18051 | -5.8044 | -6.1111 | -74.4186 | 48.1247 | 48.0881 | 74.1531 | 74.3317 | 122.5479 | 75.8743 | 46.2341
9162.5156 | 0.061035 | 0.40909 | -0.77331 | -0.22964 | 0.14206 | -0.26382 | -0.16983 | 15.0833 | -103.5324 | -6.5048 | -105.011 | 15.8798 | 106.4896 | 106.5857 | 0.061035 | -0.084381 | 0.063019 | 0.28091 | -0.15915 | -0.1741 | -11.3617 | -9.0363 | -105.1987 | 15.2847 | 15.0833 | 107.7438 | 108.5724 | 122.5388 | 108.4808 | 14.1357
9164.3281 | 0.076294 | 0.4155 | -0.77652 | -0.23498 | 0.14313 | -0.26916 | -0.18585 | 15.1657 | -103.9124 | -6.9214 | -106.8146 | 15.1428 | 107.1716 | 107.048 | 0.045776 | -0.086517 | 0.063019 | 0.27451 | -0.16235 | -0.16235 | -9.3521 | -11.9476 | -107.2952 | 15.0925 | 15.1199 | 107.0572 | 107.2861 | 122.4518 | 107.0892 | 15.2527
9166.0469 | 0.030518 | 0.40695 | -0.77118 | -0.22217 | 0.1474 | -0.2478 | -0.16983 | 3.3325 | -115.5029 | -8.5693 | -118.6295 | 3.3279 | 119.0369 | 118.9362 | 0.045776 | -0.080109 | 0.064087 | 0.29587 | -0.13779 | -0.17838 | -10.8124 | -13.7924 | -119.0689 | 3.2684 | 3.2593 | 118.9682 | 119.1742 | 122.5937 | 118.9499 | 3.3463
9167.8438 | 0.045776 | 0.39948 | -0.76157 | -0.22217 | 0.14847 | -0.24246 | -0.17517 | 4.5685 | -114.4409 | -8.5373 | -117.5217 | 4.6097 | 117.8925 | 117.7963 | 0.076294 | -0.074768 | 0.066223 | 0.30014 | -0.13992 | -0.17517 | -10.2356 | -13.3255 | -118.0206 | 4.4037 | 4.4083 | 117.8329 | 118.0939 | 122.6852 | 117.6086 | 4.6509
9169.5625 | 0.061035 | 0.41229 | -0.78293 | -0.24139 | 0.13992 | -0.2478 | -0.17944 | 13.3209 | -103.418 | -2.3117 | -108.8287 | 11.3251 | 109.465 | 110.2936 | 0.030518 | -0.1004 | 0.079041 | 0.29266 | -0.14847 | -0.15595 | -7.4844 | -13.9847 | -110.4401 | 7.7591 | 8.67 | 110.0693 | 109.5291 | 122.2641 | 115.8188 | 6.2347
9171.3594 | 0.045776 | 0.40375 | -0.78186 | -0.21362 | 0.14954 | -0.24139 | -0.16449 | 4.6371 | -113.5849 | -9.1736 | -115.329 | 5.1682 | 115.7501 | 115.4938 | 0.045776 | -0.085449 | 0.068359 | 0.28839 | -0.12924 | -0.16876 | -11.8195 | -16.2964 | -108.2382 | 8.3221 | 9.4254 | 113.1226 | 114.9628 | 122.5159 | 116.7023 | 5.777
9173.0781 | 0.076294 | 0.38986 | -0.77118 | -0.23178 | 0.1442 | -0.26382 | -0.16983 | 3.154 | -115.4343 | -8.4412 | -118.7073 | 3.273 | 119.1513 | 119.0186 | 0.030518 | -0.086517 | 0.071564 | 0.28946 | -0.14954 | -0.16983 | -10.73 | -15.2756 | -119.2291 | 3.2135 | 3.2181 | 119.0506 | 119.2474 | 122.5662 | 119.0231 | 3.2547
9174.8594 | 0.061035 | 0.42725 | -0.76263 | -0.2211 | 0.13992 | -0.26382 | -0.16663 | 3.4332 | -115.1138 | -8.3908 | -118.4921 | 3.4332 | 118.8904 | 118.7759 | 0.045776 | -0.087585 | 0.063019 | 0.30228 | -0.15381 | -0.16556 | -11.0825 | -15.9851 | -118.9545 | 3.3737 | 3.392 | 118.7943 | 119.0414 | 122.5616 | 118.8583 | 3.4607
9176.6562 | 0.030518 | 0.40802 | -0.77118 | -0.22858 | 0.13779 | -0.2478 | -0.17838 | 3.4103 | -115.0818 | -8.5144 | -118.4235 | 3.5156 | 118.84 | 118.7622 | 0.091553 | -0.087585 | 0.063019 | 0.28946 | -0.1474 | -0.17303 | -11.2747 | -15.8615 | -118.9499 | 3.4836 | 3.4698 | 118.7668 | 119.0002 | 122.4014 | 118.483 | 3.6896
9178.375 | 0.045776 | 0.40268 | -0.76263 | -0.24139 | 0.13992 | -0.25101 | -0.17517 | 65.1581 | -55.3894 | 0.33875 | -57.0877 | 65.1764 | 56.9778 | 57.0007 | 0.091553 | -0.072632 | 0.075836 | 0.298 | -0.16022 | -0.17197 | -2.5681 | -4.66 | -57.3853 | 65.1352 | 65.1077 | 57.019 | 57.1976 | 122.4426 | 57.1426 | 65.1993
9180.1719 | 0.045776 | 0.39841 | -0.77652 | -0.23926 | 0.13886 | -0.27664 | -0.18478 | 65.3961 | -55.0461 | 0.29297 | -56.8497 | 65.3732 | 56.8222 | 56.7902 | 0.061035 | -0.097198 | 0.066223 | 0.28305 | -0.16556 | -0.16556 | -2.6825 | -5.3925 | -57.1701 | 65.3778 | 65.3412 | 56.8176 | 56.9916 | 122.3694 | 56.955 | 65.4419
9181.9062 | 0.076294 | 0.4187 | -0.77972 | -0.22751 | 0.13458 | -0.28412 | -0.19226 | 65.7166 | -54.744 | 0.44403 | -56.5796 | 65.5975 | 56.5933 | 56.5659 | 0.076294 | -0.099335 | 0.060883 | 0.27878 | -0.16983 | -0.16876 | -2.6779 | -4.4174 | -56.8817 | 65.5884 | 65.5563 | 56.5979 | 56.7581 | 122.3831 | 56.6574 | 65.6982
9183.7031 | 0.045776 | 0.41763 | -0.78079 | -0.23926 | 0.13886 | -0.27771 | -0.18478 | 65.9042 | -54.4693 | 0.49896 | -56.369 | 65.7944 | 56.4102 | 56.3736 | 0.076294 | -0.11963 | 0.049133 | 0.27237 | -0.16449 | -0.17517 | -1.9592 | -5.4337 | -56.6528 | 65.7394 | 65.7257 | 56.4148 | 56.5979 | 122.4243 | 56.4835 | 65.8905
9185.4375 | 0.076294 | 0.39414 | -0.79788 | -0.23178 | 0.1442 | -0.25528 | -0.19333 | 65.95 | -54.4281 | 0.34332 | -56.3461 | 65.9912 | 56.3553 | 56.3141 | 0.076294 | -0.085449 | 0.059814 | 0.29694 | -0.16022 | -0.17838 | -2.1561 | -5.2597 | -56.6574 | 65.918 | 65.8997 | 56.3232 | 56.4789 | 122.4609 | 56.369 | 65.9821
9187.2344 | 0.061035 | 0.41016 | -0.77866 | -0.22537 | 0.11856 | -0.29053 | -0.19333 | 66.1789 | -54.158 | 0.46692 | -56.1218 | 66.124 | 56.1447 | 56.0989 | 0.061035 | -0.098267 | 0.055542 | 0.28946 | -0.16342 | -0.1741 | -2.3438 | -6.0608 | -56.3919 | 66.0599 | 66.0553 | 56.1401 | 56.3049 | 122.4289 | 56.2042 | 66.1926
9189.0312 | 0.045776 | 0.4187 | -0.77866 | -0.24033 | 0.1474 | -0.27557 | -0.19226 | 66.3757 | -53.9062 | 0.70953 | -55.9479 | 66.2109 | 56.0394 | 55.9753 | 0.061035 | -0.10147 | 0.060883 | 0.27451 | -0.16663 | -0.1709 | -3.0121 | -5.0766 | -56.2088 | 66.1789 | 66.1514 | 55.9982 | 56.163 | 122.4838 | 56.0394 | 66.3254
9190.7656 | 0.076294 | 0.41016 | -0.78613 | -0.23178 | 0.12711 | -0.26276 | -0.19333 | 66.5451 | -53.7048 | 0.74616 | -55.7419 | 66.4307 | 55.8334 | 55.8014 | 0.076294 | -0.095062 | 0.054474 | 0.27557 | -0.15167 | -0.18158 | -2.7878 | -5.6671 | -56.0577 | 66.4032 | 66.3574 | 55.8197 | 55.9891 | 122.4197 | 55.8701 | 66.5405
9192.5625 | 0.076294 | 0.41336 | -0.78293 | -0.22537 | 0.13779 | -0.24139 | -0.17944 | 66.5817 | -53.6774 | 0.75989 | -55.7419 | 66.4536 | 55.806 | 55.7785 | 0.061035 | -0.098267 | 0.058746 | 0.28091 | -0.14847 | -0.1741 | -2.417 | -6.5323 | -56.0349 | 66.4078 | 66.3574 | 55.7922 | 55.957 | 122.5388 | 55.8243 | 66.5359
9194.3438 | 0.061035 | 0.38666 | -0.78186 | -0.22751 | 0.13672 | -0.23392 | -0.16983 | 66.6367 | -53.5812 | 0.88348 | -55.7098 | 66.5543 | 55.7739 | 55.7281 | 0.061035 | -0.077972 | 0.066223 | 0.29373 | -0.13672 | -0.18799 | -2.6413 | -6.134 | -56.0394 | 66.4948 | 66.4856 | 55.7465 | 55.9113 | 122.5571 | 55.7373 | 66.5863
9196.1406 | 0.076294 | 0.40268 | -0.78079 | -0.23605 | 0.13992 | -0.25314 | -0.18585 | 66.6138 | -53.5538 | 0.85144 | -55.6641 | 66.6138 | 55.7419 | 55.7007 | 0.030518 | -0.084381 | 0.059814 | 0.298 | -0.14847 | -0.17197 | -2.504 | -6.752 | -56.0303 | 66.5909 | 66.5359 | 55.719 | 55.8701 | 122.5708 | 55.7098 | 66.6092
9197.8594 | 0.045776 | 0.4155 | -0.78079 | -0.23926 | 0.13672 | -0.27985 | -0.18585 | 66.806 | -53.2516 | 1.1353 | -55.4718 | 66.7328 | 55.5313 | 55.513 | 0.061035 | -0.10361 | 0.070496 | 0.28091 | -0.17838 | -0.1709 | -2.2797 | -6.3538 | -55.7419 | 66.6595 | 66.6412 | 55.5176 | 55.6824 | 122.5204 | 55.5817 | 66.7831
9199.6406 | 0.045776 | 0.40161 | -0.77331 | -0.24887 | 0.14633 | -0.25742 | -0.1709 | 66.7831 | -53.2288 | 1.1215 | -55.5084 | 66.7923 | 55.5405 | 55.4993 | 0.061035 | -0.076904 | 0.066223 | 0.28519 | -0.15808 | -0.16769 | -2.8931 | -6.0928 | -55.8151 | 66.7648 | 66.7374 | 55.5267 | 55.6824 | 122.4838 | 55.545 | 66.8472
9201.4219 | 0.045776 | 0.41763 | -0.7872 | -0.23071 | 0.14526 | -0.28091 | -0.18265 | 66.925 | -53.0273 | 1.268 | -55.3574 | 66.8198 | 55.426 | 55.4169 | 0.045776 | -0.10147 | 0.057678 | 0.27557 | -0.15381 | -0.16663 | -3.0808 | -6.102 | -55.632 | 66.774 | 66.7511 | 55.426 | 55.5908 | 122.5296 | 55.4626 | 66.8976
9203.1406 | 0.045776 | 0.42084 | -0.784 | -0.2243 | 0.13351 | -0.27557 | -0.19333 | 66.893 | -53.0319 | 1.1673 | -55.3986 | 66.8198 | 55.4489 | 55.426 | 0.076294 | -0.088654 | 0.058746 | 0.28519 | -0.15808 | -0.18372 | -3.4103 | -6.308 | -55.687 | 66.7969 | 66.7557 | 55.4306 | 55.6 | 122.4655 | 55.4855 | 66.9022
9204.9219 | 0.030518 | 0.39841 | -0.77225 | -0.23498 | 0.13458 | -0.24033 | -0.17517 | 66.6321 | -53.2791 | 1.0391 | -55.6549 | 66.6321 | 55.7419 | 55.7327 | 0.045776 | -0.0737 | 0.052338 | 0.28732 | -0.14633 | -0.1741 | -4.303 | -5.658 | -56.0577 | 66.5085 | 66.4627 | 55.8105 | 55.9708 | 122.6212 | 55.8517 | 66.4856
9206.6562 | 0.061035 | 0.39627 | -0.77438 | -0.23926 | 0.13992 | -0.24246 | -0.17303 | 66.9022 | -52.977 | 1.355 | -55.4031 | 66.8701 | 55.481 | 55.4718 | 0.061035 | -0.077972 | 0.064087 | 0.28412 | -0.13672 | -0.17197 | -4.3808 | -5.2872 | -55.751 | 66.7923 | 66.7557 | 55.4581 | 55.632 | 122.6212 | 55.4535 | 66.9067
9208.4375 | 0.061035 | 0.43045 | -0.78507 | -0.22324 | 0.13565 | -0.27557 | -0.18265 | 67.1036 | -52.6428 | 1.6617 | -55.1422 | 67.0944 | 55.2246 | 55.188 | 0.091553 | -0.11002 | 0.05661 | 0.28091 | -0.16342 | -0.1741 | -3.6758 | -2.829 | -55.4443 | 67.0166 | 66.9846 | 55.2155 | 55.3711 | 122.5433 | 55.22 | 67.1585
9210.1406 | 0.045776 | 0.40375 | -0.784 | -0.24033 | 0.13672 | -0.26382 | -0.17838 | 67.3096 | -52.4506 | 1.6525 | -54.982 | 67.2455 | 55.0735 | 55.0186 | 0.076294 | -0.082245 | 0.054474 | 0.28839 | -0.16129 | -0.1709 | -3.6118 | -2.1927 | -55.3436 | 67.2272 | 67.1997 | 55.101 | 55.2155 | 122.5021 | 55.0964 | 67.3187
9211.9219 | 0.045776 | 0.40588 | -0.77866 | -0.23712 | 0.1442 | -0.27771 | -0.19226 | 67.099 | -52.5925 | 1.8356 | -55.1926 | 67.0029 | 55.3207 | 55.2475 | 0.061035 | -0.099335 | 0.060883 | 0.27557 | -0.15808 | -0.16342 | -3.6072 | -2.6962 | -55.4855 | 66.9067 | 66.9205 | 55.2704 | 55.4352 | 122.5388 | 55.3162 | 67.0395
9213.7031 | 0.061035 | 0.39734 | -0.77331 | -0.21576 | 0.14099 | -0.23285 | -0.16342 | 66.9983 | -52.7115 | 1.7258 | -55.3207 | 66.9891 | 55.3802 | 55.3665 | 0.061035 | -0.065155 | 0.064087 | 0.28946 | -0.13138 | -0.16983 | -3.3188 | -2.3117 | -55.7144 | 66.9067 | 66.8838 | 55.3711 | 55.5496 | 122.5571 | 55.4031 | 66.9342
9215.4062 | 0.061035 | 0.42725 | -0.79575 | -0.22537 | 0.12817 | -0.28519 | -0.18051 | 66.7877 | -52.7893 | 1.8951 | -55.4855 | 66.7236 | 55.5588 | 55.5496 | 0.076294 | -0.11749 | 0.057678 | 0.27237 | -0.16129 | -0.16663 | -3.2593 | -2.7145 | -55.7327 | 66.7328 | 66.6962 | 55.4993 | 55.6366 | 122.5159 | 55.5771 | 66.8106
9217.1875 | 0.061035 | 0.41122 | -0.78507 | -0.22217 | 0.12283 | -0.26062 | -0.17624 | 66.6687 | -52.8717 | 2.0233 | -55.6503 | 66.5085 | 55.7968 | 55.751 | 0.061035 | -0.092926 | 0.054474 | 0.29373 | -0.16235 | -0.16663 | -3.8223 | -2.7237 | -55.9845 | 66.4627 | 66.4444 | 55.7281 | 55.8884 | 122.5021 | 55.7556 | 66.6321
9218.9062 | 0.076294 | 0.42831 | -0.79681 | -0.21896 | 0.14633 | -0.27344 | -0.16769 | 66.3345 | -53.1097 | 2.0554 | -55.9891 | 66.1835 | 56.0761 | 56.0532 | 0.061035 | -0.083313 | 0.063019 | 0.28091 | -0.15381 | -0.17624 | -3.6667 | -2.1698 | -56.2912 | 66.1697 | 66.1377 | 56.0669 | 56.2363 | 122.5159 | 56.1218 | 66.2613
9220.6875 | 0.061035 | 0.4155 | -0.78827 | -0.24567 | 0.13672 | -0.26062 | -0.17624 | 66.4856 | -52.8763 | 2.1286 | -55.8105 | 66.3345 | 55.9433 | 55.9113 | 0.045776 | -0.088654 | 0.058746 | 0.27557 | -0.15274 | -0.1709 | -3.6987 | -3.0899 | -56.1447 | 66.2796 | 66.2704 | 55.9525 | 56.0989 | 122.4884 | 56.0257 | 66.394
9222.4844 | 0.076294 | 0.40161 | -0.77972 | -0.24139 | 0.14313 | -0.24994 | -0.16022 | 66.3803 | -52.9633 | 2.1469 | -55.9067 | 66.2704 | 56.0303 | 55.9891 | 0.045776 | -0.083313 | 0.069427 | 0.29266 | -0.15488 | -0.17731 | -3.8818 | -2.5177 | -56.2546 | 66.2155 | 66.1972 | 56.0394 | 56.1813 | 122.612 | 56.0623 | 66.2521
9224.2656 | 0.045776 | 0.38452 | -0.78293 | -0.24674 | 0.13245 | -0.24567 | -0.17624 | 66.3254 | -53.0228 | 2.2202 | -55.9525 | 66.2933 | 56.0623 | 56.0349 | 0.061035 | -0.082245 | 0.065155 | 0.2948 | -0.15808 | -0.17838 | -3.7262 | -2.5085 | -56.3187 | 66.2338 | 66.2018 | 56.0394 | 56.1722 | 122.6486 | 56.0394 | 66.3345
9226 | 0.061035 | 0.40695 | -0.80215 | -0.24033 | 0.13886 | -0.27451 | -0.18158 | 66.2247 | -52.9724 | 2.3254 | -56.0028 | 66.1743 | 56.1218 | 56.1035 | 0.030518 | -0.095062 | 0.068359 | 0.29266 | -0.1709 | -0.18265 | -3.7491 | -1.973 | -56.3278 | 66.1331 | 66.1194 | 56.0852 | 56.2729 | 122.5204 | 56.1584 | 66.2064
9227.7969 | 0.076294 | 0.40268 | -0.78293 | -0.22537 | 0.13672 | -0.27664 | -0.18265 | 66.0004 | -53.0869 | 2.3117 | -56.2592 | 65.8768 | 56.4194 | 56.3644 | 0.061035 | -0.092926 | 0.061951 | 0.298 | -0.16342 | -0.18799 | -4.2023 | -2.2018 | -56.6025 | 65.7898 | 65.7898 | 56.4056 | 56.575 | 122.5433 | 56.4514 | 65.9637
9229.5781 | 0.076294 | 0.40588 | -0.92178 | -0.21149 | 0.14526 | -0.23178 | -0.16556 | 18.251 | -98.3139 | -7.5485 | -103.7018 | 18.1549 | 104.2969 | 104.1595 | 0.061035 | -0.065155 | 0.061951 | 0.30975 | -0.12711 | -0.18158 | -14.1769 | -14.4791 | -104.3152 | 18.1458 | 18.1183 | 104.2007 | 104.4113 | 122.699 | 104.0817 | 18.1595
9231.3125 | 0.045776 | 0.42831 | -0.93353 | -0.22644 | 0.16129 | -0.27451 | -0.16129 | 16.9418 | -99.3439 | -8.0154 | -104.924 | 16.9006 | 105.5008 | 105.3909 | 0.076294 | -0.10681 | 0.063019 | 0.29587 | -0.15488 | -0.16342 | -15.1016 | -16.1224 | -105.5191 | 16.8777 | 16.8686 | 105.3909 | 105.629 | 122.5937 | 105.4138 | 16.9418
9233.0938 | 0.045776 | 0.40054 | -0.93567 | -0.22858 | 0.16235 | -0.23712 | -0.16342 | 15.9851 | -100.1999 | -8.7524 | -105.9128 | 15.9851 | 106.4713 | 106.3705 | 0.030518 | -0.074768 | 0.067291 | 0.28625 | -0.12817 | -0.16983 | -16.2643 | -16.7633 | -106.5674 | 15.9302 | 15.921 | 106.3934 | 106.5903 | 122.6715 | 106.3568 | 15.9622
9234.8125 | 0.061035 | 0.38238 | -0.94635 | -0.23819 | 0.16129 | -0.22751 | -0.16449 | 15.6555 | -100.2548 | -8.7708 | -106.2103 | 15.6418 | 106.7734 | 106.6956 | 0.076294 | -0.082245 | 0.068359 | 0.29266 | -0.13245 | -0.16342 | -16.2552 | -16.1728 | -106.8695 | 15.5777 | 15.5731 | 106.691 | 106.9519 | 122.6624 | 106.7139 | 15.6052
9236.5938 | 0.061035 | 0.43686 | -0.94955 | -0.24887 | 0.14206 | -0.28412 | -0.16983 | 15.4861 | -100.2548 | -8.7524 | -106.3614 | 15.4449 | 106.9244 | 106.8192 | 0.061035 | -0.087585 | 0.059814 | 0.30441 | -0.15595 | -0.16342 | -15.802 | -18.0588 | -106.9748 | 15.4175 | 15.4221 | 106.8054 | 107.0572 | 122.5433 | 106.9153 | 15.5045
9238.375 | 0.061035 | 0.41977 | -0.9549 | -0.23926 | 0.15488 | -0.2713 | -0.16449 | 14.9918 | -100.5798 | -8.6426 | -106.8604 | 14.9277 | 107.4188 | 107.341 | 0.076294 | -0.097198 | 0.054474 | 0.28839 | -0.14954 | -0.16769 | -16.0858 | -16.2552 | -107.4554 | 14.8865 | 14.8773 | 107.3547 | 107.5607 | 122.5662 | 107.4371 | 14.9826
9240.1562 | 0.030518 | 0.40588 | -0.95169 | -0.22003 | 0.1474 | -0.20935 | -0.16129 | 14.9231 | -100.5203 | -8.725 | -106.9153 | 14.9414 | 107.4738 | 107.3959 | 0.061035 | -0.076904 | 0.064087 | 0.2948 | -0.12817 | -0.16983 | -15.2939 | -19.1803 | -107.6385 | 14.9002 | 14.8911 | 107.4188 | 107.634 | 122.58 | 107.46 | 14.9323
9241.875 | 0.045776 | 0.3952 | -0.95596 | -0.23819 | 0.14954 | -0.2446 | -0.16022 | 14.4196 | -100.7812 | -9.2331 | -107.3776 | 14.4608 | 107.9636 | 107.8903 | 0.045776 | -0.083313 | 0.064087 | 0.30121 | -0.13779 | -0.15808 | -16.3742 | -16.5298 | -108.0734 | 14.415 | 14.4241 | 107.8949 | 108.0917 | 122.6303 | 107.9224 | 14.4516
9243.6562 | 0.030518 | 0.42725 | -0.95383 | -0.2211 | 0.15595 | -0.26276 | -0.16769 | 14.2456 | -100.6897 | -9.2468 | -107.5516 | 14.1815 | 108.1604 | 108.0734 | 0.076294 | -0.091858 | 0.058746 | 0.27771 | -0.15274 | -0.16449 | -16.4429 | -16.5344 | -108.2245 | 14.1174 | 14.1541 | 108.1329 | 108.3435 | 122.5067 | 108.1924 | 14.2548
9245.4375 | 0.061035 | 0.40268 | -0.96664 | -0.2179 | 0.16663 | -0.23178 | -0.15808 | 13.7375 | -101.088 | -9.5352 | -108.0643 | 13.7604 | 108.6639 | 108.5587 | 0.045776 | -0.081177 | 0.058746 | 0.30014 | -0.14633 | -0.16235 | -16.6306 | -16.5756 | -108.7601 | 13.7146 | 13.7054 | 108.5678 | 108.8104 | 122.6486 | 108.5907 | 13.765
9247.1562 | 0.045776 | 0.41122 | -0.94208 | -0.23071 | 0.16556 | -0.24353 | -0.16235 | 13.9023 | -100.6073 | -9.5947 | -107.9086 | 13.8336 | 108.5358 | 108.4396 | 0.061035 | -0.086517 | 0.061951 | 0.29266 | -0.15488 | -0.16663 | -15.8066 | -15.6738 | -108.5587 | 13.765 | 13.7787 | 108.4534 | 108.6411 | 122.644 | 108.5037 | 13.8519
9248.9375 | 0.045776 | 0.39734 | -0.96237 | -0.23285 | 0.15274 | -0.23498 | -0.16876 | 13.385 | -100.8682 | -9.8007 | -108.4122 | 13.3667 | 108.989 | 108.9111 | 0.061035 | -0.089722 | 0.058746 | 0.29159 | -0.14206 | -0.15915 | -15.8981 | -16.507 | -109.0805 | 13.3392 | 13.3255 | 108.9249 | 109.1217 | 122.6715 | 108.9661 | 13.4033
9250.75 | 0.076294 | 0.39627 | -0.96771 | -0.23926 | 0.17197 | -0.25314 | -0.1741 | 13.4445 | -100.4105 | -9.993 | -108.3023 | 13.4903 | 108.9615 | 108.8379 | 0.030518 | -0.09613 | 0.065155 | 0.2948 | -0.16449 | -0.16663 | -15.9714 | -15.8249 | -109.0347 | 13.4491 | 13.4308 | 108.8699 | 109.0805 | 122.5342 | 108.8882 | 13.4949
9252.4688 | 0.076294 | 0.42084 | -0.97626 | -0.24246 | 0.16556 | -0.2681 | -0.16449 | 13.2568 | -100.3143 | -10.199 | -108.4808 | 13.2339 | 109.1125 | 109.0164 | 0.076294 | -0.10574 | 0.066223 | 0.28946 | -0.16022 | -0.16129 | -15.77 | -16.5985 | -109.1858 | 13.179 | 13.1927 | 109.0576 | 109.2865 | 122.5296 | 109.1537 | 13.3026
9254.2969 | 0.076294 | 0.41122 | -0.97092 | -0.24139 | 0.16129 | -0.26062 | -0.17303 | 13.1241 | -100.0763 | -10.3958 | -108.6227 | 13.0463 | 109.3002 | 109.1949 | 0.045776 | -0.1004 | 0.060883 | 0.28946 | -0.15701 | -0.16876 | -15.6052 | -16.6763 | -109.2819 | 12.9959 | 12.9913 | 109.2178 | 109.4559 | 122.5571 | 109.2957 | 13.1149
9256.0625 | 0.061035 | 0.40909 | -0.96878 | -0.22858 | 0.1741 | -0.22644 | -0.16663 | 13.1241 | -99.8383 | -10.6842 | -108.6502 | 13.06 | 109.2911 | 109.1858 | 0.045776 | -0.076904 | 0.059814 | 0.2948 | -0.13031 | -0.16022 | -15.8707 | -16.2369 | -109.3552 | 13.0188 | 12.9959 | 109.2133 | 109.4376 | 122.644 | 109.2682 | 13.0783
9257.7656 | 0.045776 | 0.39307 | -0.9613 | -0.22964 | 0.17517 | -0.2211 | -0.16022 | 13.1332 | -99.5316 | -10.9497 | -108.6365 | 13.0966 | 109.3277 | 109.1858 | 0.061035 | -0.077972 | 0.05661 | 0.31296 | -0.13992 | -0.1709 | -15.7837 | -16.8549 | -109.4055 | 13.028 | 13.0508 | 109.2224 | 109.4696 | 122.5845 | 109.2819 | 13.092
9259.4688 | 0.061035 | 0.40482 | -0.9816 | -0.23926 | 0.15595 | -0.27557 | -0.16449 | 12.8815 | -99.2706 | -11.1191 | -108.8104 | 12.8723 | 109.4604 | 109.3735 | 0.061035 | -0.11108 | 0.066223 | 0.29907 | -0.1709 | -0.16235 | -15.6647 | -17.7933 | -109.5428 | 12.8174 | 12.8128 | 109.4193 | 109.6024 | 122.5021 | 109.4879 | 12.9364
9261.1719 | 0.061035 | 0.41122 | -0.99442 | -0.22217 | 0.16663 | -0.24139 | -0.15274 | 12.8632 | -98.7305 | -11.3571 | -108.8745 | 12.7579 | 109.5795 | 109.465 | 0.045776 | -0.09079 | 0.050201 | 0.28412 | -0.14313 | -0.17197 | -15.77 | -16.7541 | -109.6024 | 12.7029 | 12.7029 | 109.5016 | 109.7031 | 122.58 | 109.5749 | 12.8082
9262.8906 | 0.045776 | 0.40375 | -0.98053 | -0.23178 | 0.18051 | -0.22858 | -0.16022 | 13.1012 | -97.9568 | -11.6089 | -108.5999 | 13.1195 | 109.3231 | 109.1995 | 0.061035 | -0.076904 | 0.061951 | 0.29159 | -0.13458 | -0.17838 | -15.9805 | -17.4774 | -109.4101 | 13.1012 | 13.0875 | 109.2407 | 109.4284 | 122.6212 | 109.227 | 13.1104
9264.6406 | 0.076294 | 0.41336 | -0.98908 | -0.24994 | 0.18585 | -0.26916 | -0.16342 | 12.9318 | -97.5357 | -11.5997 | -108.7509 | 12.8174 | 109.5245 | 109.4055 | 0.061035 | -0.10468 | 0.064087 | 0.29266 | -0.16342 | -0.16342 | -16.4383 | -16.9144 | -109.5016 | 12.7808 | 12.7945 | 109.465 | 109.6481 | 122.5342 | 109.4925 | 12.8998
9266.4062 | 0.061035 | 0.43259 | -0.99121 | -0.2179 | 0.17731 | -0.26489 | -0.16556 | 12.6617 | -97.2702 | -12.1674 | -109.0347 | 12.5702 | 109.7488 | 109.6573 | 0.061035 | -0.10468 | 0.052338 | 0.29907 | -0.13886 | -0.16129 | -16.3651 | -16.8869 | -109.8221 | 12.5153 | 12.5198 | 109.7031 | 109.9182 | 122.5021 | 109.7992 | 12.6389
9268.1562 | 0.061035 | 0.392 | -0.99335 | -0.21362 | 0.1741 | -0.22324 | -0.16556 | 12.6846 | -96.9864 | -12.4741 | -108.989 | 12.6755 | 109.7305 | 109.6161 | 0.061035 | -0.085449 | 0.066223 | 0.30548 | -0.13779 | -0.16876 | -16.832 | -16.6626 | -109.8267 | 12.6389 | 12.6389 | 109.639 | 109.8587 | 122.6486 | 109.6664 | 12.6709
9269.875 | 0.061035 | 0.3952 | -0.99976 | -0.2211 | 0.18372 | -0.22644 | -0.16983 | 12.3917 | -96.9772 | -12.7899 | -109.2453 | 12.41 | 110.0098 | 109.9091 | 0.076294 | -0.082245 | 0.060883 | 0.29694 | -0.13672 | -0.16449 | -16.8091 | -16.7633 | -110.0784 | 12.3596 | 12.3505 | 109.9228 | 110.1196 | 122.6532 | 109.9319 | 12.4237
9271.5938 | 0.061035 | 0.42404 | -1.003 | -0.22751 | 0.16449 | -0.26276 | -0.15595 | 12.204 | -96.3821 | -13.3118 | -109.4101 | 12.117 | 110.2066 | 110.0876 | 0.061035 | -0.10468 | 0.060883 | 0.30014 | -0.14526 | -0.15915 | -17.1112 | -16.9052 | -110.2524 | 12.0941 | 12.1033 | 110.1608 | 110.3806 | 122.5067 | 110.2386 | 12.2086
9273.2969 | 0.061035 | 0.40588 | -0.99442 | -0.2179 | 0.18158 | -0.23071 | -0.15381 | 12.6022 | -95.668 | -13.4903 | -108.989 | 12.6205 | 109.7855 | 109.6664 | 0.061035 | -0.080109 | 0.05661 | 0.30441 | -0.1442 | -0.16129 | -17.3401 | -17.9489 | -109.9091 | 12.5885 | 12.5931 | 109.7397 | 109.9136 | 122.6212 | 109.7351 | 12.6297
9275 | 0.061035 | 0.392 | -0.99548 | -0.2446 | 0.18051 | -0.22644 | -0.16022 | 13.5406 | -94.3817 | -13.2202 | -108.0185 | 13.5452 | 108.8745 | 108.7921 | 0.061035 | -0.087585 | 0.067291 | 0.29907 | -0.14633 | -0.1741 | -17.4454 | -17.9489 | -108.9386 | 13.4995 | 13.504 | 108.783 | 109.0256 | 122.6761 | 108.728 | 13.5086
9276.7188 | 0.061035 | 0.40482 | -1.0062 | -0.2478 | 0.18372 | -0.27344 | -0.15595 | 13.2889 | -93.8644 | -13.7833 | -108.2474 | 13.266 | 109.0805 | 108.9615 | 0.061035 | -0.10254 | 0.070496 | 0.30548 | -0.16663 | -0.16129 | -17.7704 | -18.6035 | -109.108 | 13.2202 | 13.2614 | 109.0073 | 109.2361 | 122.5891 | 109.021 | 13.3255
9278.4375 | 0.061035 | 0.3952 | -1.004 | -0.22858 | 0.18265 | -0.21896 | -0.15595 | 13.1241 | -93.3014 | -14.1403 | -108.403 | 13.1516 | 109.2453 | 109.1537 | 0.061035 | -0.067291 | 0.069427 | 0.30762 | -0.13351 | -0.18051 | -18.4616 | -19.9127 | -109.3781 | 13.1332 | 13.1378 | 109.1812 | 109.3918 | 122.6212 | 109.1812 | 13.1699
9280.1406 | 0.076294 | 0.41336 | -1.02 | -0.23498 | 0.18799 | -0.26703 | -0.1709 | 13.0463 | -92.363 | -14.3326 | -108.4396 | 12.9913 | 109.3552 | 109.259 | 0.045776 | -0.10788 | 0.058746 | 0.29373 | -0.15701 | -0.16342 | -18.7912 | -20.3293 | -109.3369 | 12.941 | 12.9364 | 109.2957 | 109.4971 | 122.58 | 109.3643 | 13.028
9281.8438 | 0.045776 | 0.39948 | -1.0318 | -0.23071 | 0.19546 | -0.2211 | -0.16769 | 13.0051 | -91.7862 | -14.653 | -108.4625 | 13.0188 | 109.3964 | 109.2865 | 0.045776 | -0.082245 | 0.069427 | 0.30655 | -0.14954 | -0.1709 | -19.1025 | -21.0938 | -109.4696 | 12.973 | 13.0005 | 109.3277 | 109.5428 | 122.6624 | 109.2865 | 13.0142
9283.5469 | 0.045776 | 0.40909 | -1.0265 | -0.22217 | 0.21683 | -0.24674 | -0.15488 | 13.3667 | -90.2435 | -14.653 | -108.0414 | 13.2431 | 109.0622 | 108.934 | 0.045776 | -0.11108 | 0.05661 | 0.30548 | -0.14206 | -0.16449 | -18.7592 | -20.9335 | -109.053 | 13.2248 | 13.2339 | 108.9844 | 109.2087 | 122.5891 | 109.053 | 13.3347
9285.2812 | 0.091553 | 0.40375 | -2.1021 | -0.23926 | 0.18265 | 0.90683 | -0.17838 | 43.6066 | -62.1872 | -3.772 | -39.5004 | 43.6203 | 78.5843 | 78.5294 | 0.061035 | -0.11322 | 0.066223 | 0.29373 | -0.16129 | -0.16663 | -10.6384 | -10.5743 | -78.6942 | 43.5699 | 43.5791 | 78.5522 | 78.7445 | 122.2458 | 78.7582 | 43.7302
9287.0312 | 0.045776 | 0.40588 | -3.1178 | -0.23498 | 0.42297 | 1.6908 | -0.16769 | 35.5362 | 16.8549 | -4.2297 | -24.7055 | 35.4492 | 86.7325 | 86.6364 | 0.076294 | -0.097198 | 0.057678 | 0.29907 | -0.15595 | -0.17303 | -12.8723 | -13.3713 | -86.8378 | 35.408 | 35.3851 | 86.7371 | 86.9202 | 122.4335 | 86.8332 | 35.5453
9288.7188 | 0.045776 | 0.40161 | -3.2567 | -0.20828 | 0.43686 | 1.8436 | -0.15488 | 40.8005 | 26.944 | -2.6459 | -13.2843 | 40.9561 | 81.3126 | 81.2347 | 0.076294 | -0.083313 | 0.065155 | 0.30014 | -0.13138 | -0.17303 | -11.4258 | -11.8011 | -81.4407 | 40.979 | 40.9607 | 81.2622 | 81.4774 | 122.5479 | 81.2805 | 40.9927
9290.4219 | 0.061035 | 0.37064 | -3.7448 | -0.23071 | 0.4454 | 2.305 | -0.1506 | 30.3818 | 16.5527 | -6.4362 | -10.9543 | 30.5054 | 91.7221 | 91.658 | 0.061035 | -0.077972 | 0.072632 | 0.29907 | -0.13779 | -0.17944 | -13.9252 | -15.5411 | -91.9556 | 30.4825 | 30.4596 | 91.7267 | 91.9373 | 122.5204 | 91.7221 | 30.5191
9292.1406 | 0.045776 | 0.37918 | -3.8506 | -0.23285 | 0.45395 | 2.4065 | -0.14847 | 28.6789 | 15.239 | -7.3837 | -9.6497 | 28.7659 | 93.457 | 93.3563 | 0.076294 | -0.084381 | 0.079041 | 0.30548 | -0.13245 | -0.1741 | -14.09 | -16.0355 | -93.5532 | 28.7338 | 28.7155 | 93.4296 | 93.6401 | 122.5296 | 93.3884 | 28.775
9293.9688 | 0.076294 | 0.41229 | -3.4895 | -0.2446 | 0.45181 | 2.0187 | -0.16022 | 40.892 | 31.9565 | -3.2364 | -8.2077 | 40.7181 | 81.3263 | 81.2759 | 0.061035 | -0.10681 | 0.070496 | 0.29587 | -0.15808 | -0.16235 | -10.7254 | -12.4146 | -81.6834 | 40.6082 | 40.5991 | 81.5643 | 81.9855 | 122.3877 | 81.4316 | 40.8875
9295.7812 | 0.061035 | 0.38666 | -3.2973 | -0.22003 | 0.45929 | 1.8532 | -0.1474 | 34.3918 | 25.914 | -6.0104 | -20.8054 | 34.433 | 87.767 | 87.6892 | 0.061035 | -0.082245 | 0.055542 | 0.29907 | -0.12924 | -0.17838 | -12.0804 | -14.6393 | -87.9684 | 34.3735 | 34.3735 | 87.7716 | 87.9684 | 122.4564 | 87.7716 | 34.4376
9297.5625 | 0.045776 | 0.41657 | -3.6305 | -0.23605 | 0.45609 | 2.1095 | -0.15808 | 34.0714 | 25.5386 | -6.0287 | -11.9156 | 34.0805 | 88.028 | 87.9181 | 0.061035 | -0.1004 | 0.060883 | 0.2948 | -0.16129 | -0.15915 | -11.9843 | -15.3488 | -88.0966 | 34.0714 | 34.0347 | 88.0692 | 88.2385 | 122.4197 | 88.06 | 34.1949
9299.3594 | 0.045776 | 0.39414 | -3.7779 | -0.22537 | 0.44968 | 2.3018 | -0.15595 | 30.3589 | 21.5057 | -7.695 | -11.1465 | 30.4321 | 91.7816 | 91.6718 | 0.076294 | -0.0737 | 0.063019 | 0.30121 | -0.13992 | -0.17303 | -13.0463 | -17.2989 | -91.9098 | 30.4092 | 30.3497 | 91.7541 | 91.9556 | 122.5067 | 91.7358 | 30.3955
9301.1406 | 0.061035 | 0.40482 | -3.9061 | -0.23071 | 0.4689 | 2.3669 | -0.1709 | 27.4246 | 18.8095 | -8.9172 | -10.5698 | 27.3788 | 94.7021 | 94.606 | 0.076294 | -0.11002 | 0.059814 | 0.29159 | -0.14526 | -0.16235 | -13.829 | -18.6905 | -94.7159 | 27.3788 | 27.3834 | 94.7159 | 94.8853 | 122.4014 | 94.7296 | 27.4979
9302.9375 | 0.076294 | 0.4187 | -4.0994 | -0.2446 | 0.44861 | 2.5464 | -0.15915 | 21.698 | 10.0983 | -11.1694 | -10.6705 | 21.73 | 100.4013 | 100.2823 | 0.045776 | -0.11108 | 0.059814 | 0.30762 | -0.15488 | -0.16663 | -15.2985 | -21.373 | -100.3967 | 21.698 | 21.7072 | 100.3647 | 100.589 | 122.4152 | 100.4105 | 21.7987
9304.7188 | 0.045776 | 0.42511 | -3.3357 | -0.23605 | 0.37384 | 1.9098 | -0.16449 | 40.6631 | 7.5211 | -5.4108 | -8.4778 | 40.6357 | 81.4041 | 81.3675 | 0.061035 | -0.087585 | 0.057678 | 0.29694 | -0.13886 | -0.1741 | -10.2173 | -14.3051 | -81.3126 | 40.7227 | 40.7227 | 81.2851 | 81.5186 | 122.406 | 80.5801 | 41.748
9306.5 | 0.045776 | 0.38238 | -5.4858 | -0.2446 | 2.4866 | 1.7047 | -0.1474 | 30.8487 | 16.9785 | -8.6151 | -26.8387 | 29.2328 | 92.4866 | 91.8274 | 0.045776 | -0.066223 | 0.061951 | 0.30548 | -0.13458 | -0.17303 | -14.2044 | -20.0592 | -92.6743 | 28.3035 | 28.8483 | 92.157 | 92.2348 | 122.3282 | 90.6876 | 31.8878
9308.2188 | 0.045776 | 0.39627 | -3.3432 | -0.22751 | 0.49027 | 1.7325 | -0.15915 | 49.0997 | -0.059509 | -2.0462 | -11.38 | 48.8892 | 73.2422 | 73.1461 | 0.061035 | -0.085449 | 0.059814 | 0.30762 | -0.13138 | -0.17731 | -6.427 | -11.2335 | -72.908 | 49.4659 | 49.4202 | 72.6929 | 72.8943 | 122.4472 | 71.7316 | 50.5875
9310 | 0.045776 | 0.41122 | -3.1264 | -0.21576 | 0.44006 | 1.6695 | -0.15595 | 55.426 | 0.54932 | -4.3488 | -10.73 | 50.592 | 72.6059 | 72.9263 | 0.045776 | -0.11002 | 0.066223 | 0.30762 | -0.15808 | -0.16342 | -8.0109 | -11.8149 | -69.9097 | 49.6857 | 51.1459 | 69.5343 | 68.8431 | 122.3145 | 73.5077 | 48.5504
9311.7812 | 0.061035 | 0.38559 | -6.8808 | -0.22964 | 4.8012 | 1.2721 | -0.16235 | 72.084 | 26.9852 | 6.9077 | -8.7341 | 72.0428 | 49.9054 | 49.9512 | 0.076294 | -0.080109 | 0.075836 | 0.28732 | -0.14526 | -0.18158 | -2.1835 | -2.3941 | -49.9237 | 72.1893 | 72.1985 | 49.8047 | 49.8962 | 122.4106 | 50.4135 | 71.6812
9313.5 | 0.045776 | 0.39734 | -2.5496 | -0.23605 | 0.52338 | 1.0713 | -0.16342 | 72.8165 | -2.1194 | 5.8548 | -7.6813 | 72.7386 | 49.3423 | 49.4156 | 0.076294 | -0.10361 | 0.059814 | 0.29159 | -0.15915 | -0.16342 | -1.68 | -2.536 | -49.8825 | 72.4045 | 73.1644 | 48.5138 | 48.4909 | 122.081 | 51.3428 | 71.9788
9315.2812 | 0.076294 | 0.41763 | -5.2882 | -0.22751 | 3.2321 | 0.99762 | -0.1741 | 73.819 | -2.3712 | 6.308 | -7.8003 | 74.5422 | 47.5479 | 47.525 | 0.061035 | -0.097198 | 0.044861 | 0.28839 | -0.14206 | -0.1741 | -1.0483 | -1.3458 | -47.58 | 74.3454 | 74.4873 | 47.3694 | 47.3328 | 122.3648 | 47.7493 | 74.3408
9317.0625 | 0.061035 | 0.38986 | -24.8155 | -0.2211 | 22.5362 | 1.3843 | -0.16663 | 57.2937 | -3.5934 | 0.15564 | -11.348 | 57.9849 | 63.1485 | 63.1577 | 0.076294 | -0.071564 | 0.071564 | 0.31403 | -0.12176 | -0.17838 | -4.9393 | -9.1736 | -63.8214 | 58.1909 | 58.1772 | 63.6932 | 63.7985 | 122.0856 | 63.9542 | 57.8979
9318.7969 | 0.061035 | 0.39093 | -25.9317 | -0.24567 | 22.4283 | 1.0521 | 1.3309 | 56.6162 | -2.948 | -0.17395 | -10.5286 | 57.2021 | 63.7207 | 63.6658 | 0.045776 | -0.083313 | 0.065155 | 0.31403 | -0.12283 | -0.17517 | -4.8019 | -9.2834 | -63.739 | 57.9712 | 57.9529 | 63.652 | 63.6841 | 121.8246 | 61.4136 | 60.7864
9320.5781 | 0.061035 | 0.38666 | -5.2402 | -0.23071 | 1.1707 | 1.4441 | 1.553 | 60.1868 | 14.6072 | 2.8473 | -7.3837 | 60.1868 | 61.7523 | 61.7523 | 0.061035 | -0.082245 | 0.069427 | 0.31403 | -0.14206 | -0.16983 | -4.2297 | -9.1553 | -62.3474 | 59.7702 | 59.7244 | 62.178 | 62.352 | 122.3511 | 65.0162 | 56.7261
9322.3594 | 0.076294 | -0.064087 | -5.1398 | -0.22858 | 3.4789 | 1.082 | -0.1474 | 56.6025 | 46.2936 | 2.5543 | -5.4794 | 56.5063 | 65.1352 | 64.9338 | 0.045776 | -0.10788 | 0.064087 | 0.3183 | -0.1506 | -0.16342 | -4.6692 | -10.7986 | -64.444 | 57.1793 | 57.1106 | 65.0299 | 65.5014 | 122.2366 | 66.0919 | 55.838
9324.0625 | 0.076294 | 0.35034 | -2.29 | -0.25207 | 0.41229 | 1.0265 | -0.11643 | 83.5785 | -1.2039 | 7.6263 | -4.628 | 83.139 | 38.8412 | 38.8916 | 0.061035 | -0.080109 | 0.071564 | 0.30441 | -0.14526 | -0.17838 | 0.1831 | 0.045776 | -39.006 | 83.4274 | 83.6197 | 38.3926 | 38.5574 | 122.4426 | 38.5941 | 83.2581
9325.8438 | 0.045776 | 0.31509 | -8.7169 | -0.21896 | 0.43366 | 1.7912 | 7.7364 | 80.6076 | 19.5602 | 8.6288 | -7.37 | 81.1935 | 38.4842 | 37.3352 | 0.030518 | -0.083313 | 0.0737 | 0.29159 | -0.13138 | -0.16769 | 3.6209 | 6.3995 | -37.0789 | 87.8128 | 87.1078 | 34.7992 | 35.1562 | 121.8338 | 33.5678 | 87.7762
9327.625 | 0.045776 | 0.38879 | -1.8884 | -0.21576 | 0.37491 | 0.57999 | 0.001068 | 96.6522 | -0.53101 | 11.2701 | -2.8519 | 96.5149 | 25.502 | 25.5524 | 0.045776 | -0.097198 | 0.055542 | 0.30868 | -0.15167 | -0.17303 | -4.5868 | -6.546 | -40.2237 | 82.8873 | 82.489 | 37.9257 | 35.7971 | 122.3969 | 27.182 | 94.4733
9329.4062 | 0.045776 | -1.3234 | -1.5584 | -0.2446 | 0.49133 | 1.7122 | 0.22003 | 42.2379 | -2.6596 | -0.38452 | -6.5094 | 45.1492 | 77.3438 | 75.6088 | 0.076294 | -0.076904 | 0.070496 | 0.32364 | -0.11536 | -0.1741 | -4.6555 | -17.0471 | -73.8922 | 47.9324 | 47.5479 | 75.3708 | 76.0483 | 122.5159 | 77.3804 | 44.8288
9331.1094 | 0.030518 | 0.25421 | -0.60028 | -0.23178 | -0.027771 | -0.29373 | 0.052338 | 0.054932 | 0.032043 | 0.004578 | -0.31128 | 0.086975 | 0.48065 | 0.58136 | 0.061035 | -0.10681 | 0.054474 | 0.28091 | -0.16129 | -0.16235 | 7.9468 | 16.2918 | -0.44403 | 121.4218 | 121.431 | 0.56305 | 0.59509 | 122.2458 | 0.43488 | 99.4263
9332.8906 | 0.061035 | 0.22537 | -0.60242 | -0.21576 | -0.009613 | -0.24246 | 0.060883 | 0.027466 | -0.10071 | -0.16022 | -1.03 | 0.10986 | 1.062 | 1.1765 | 0.091553 | -0.089722 | 0.061951 | 0.2948 | -0.14526 | -0.18372 | 6.9077 | 16.0904 | -1.1398 | 121.0144 | 121.0007 | 1.1444 | 1.181 | 121.9666 | 1.1398 | 120.3003
9334.5938 | 0.045776 | 0.24139 | -0.59601 | -0.23926 | -0.011749 | -0.27344 | 0.048065 | 0.059509 | 0.018311 | -0.16937 | -2.5131 | 0.032043 | 2.6184 | 2.7328 | 0.061035 | -0.098267 | 0.067291 | 0.27985 | -0.16556 | -0.1741 | 6.1295 | 14.9826 | -2.623 | 119.4214 | 119.4489 | 2.7191 | 2.7832 | 106.9336 | 2.504 | 99.1608
9336.375 | 0.045776 | 0.23498 | -0.60349 | -0.23605 | 0.060883 | -0.26382 | -0.044861 | -0.068665 | -0.14648 | -0.38452 | -3.6163 | 0.064087 | 3.6896 | 3.7811 | 0.045776 | -0.098267 | 0.066223 | 0.28305 | -0.15808 | -0.17731 | 5.4016 | 14.5706 | -3.7765 | 118.483 | 118.4647 | 3.7765 | 3.8406 | 121.5866 | 3.6804 | 117.7963
9338.1094 | 0.061035 | 0.23071 | -0.61737 | -0.23712 | 0.001068 | -0.27023 | 0.019226 | 0.004578 | -0.013733 | -0.31128 | -4.4586 | 0.009155 | 4.4312 | 4.5319 | 0.061035 | -0.097198 | 0.084381 | 0.28625 | -0.16129 | -0.1741 | 4.66 | 14.0991 | -4.4815 | 117.691 | 117.6727 | 4.454 | 4.5227 | 104.8004 | 4.3259 | 117.1143
9339.8906 | 0.061035 | 0.23392 | -0.59921 | -0.23071 | 0.02243 | -0.27344 | -0.007477 | -0.086975 | -0.14191 | -0.50354 | -5.9692 | -0.036621 | 6.0516 | 6.134 | 0.061035 | -0.09079 | 0.058746 | 0.28625 | -0.16022 | -0.17197 | 3.891 | 12.9639 | -6.0974 | 116.0751 | 116.0522 | 6.1386 | 6.1752 | 122.4243 | 5.9738 | 107.8766
9341.6562 | 0.045776 | 0.24139 | -0.60135 | -0.21576 | 0.010681 | -0.2446 | 0.019226 | 0.027466 | -0.073242 | -0.25177 | -3.6942 | -0.045776 | 3.7811 | 3.891 | 0.076294 | -0.089722 | 0.049133 | 0.29053 | -0.14847 | -0.18051 | 3.7674 | 14.0808 | -3.7399 | 118.3502 | 118.3502 | 3.8406 | 3.8681 | 122.0535 | 3.8681 | 118.5242
9343.4531 | 0.061035 | 0.21469 | -0.59601 | -0.2179 | 0.027771 | -0.22858 | -0.042725 | -0.23804 | -0.35706 | -0.88348 | -11.3342 | -0.20142 | 11.3846 | 11.499 | 0.030518 | -0.074768 | 0.065155 | 0.31296 | -0.11002 | -0.18265 | 2.7512 | 10.3271 | -11.5585 | 110.7605 | 110.7513 | 11.4716 | 11.5448 | 122.438 | 11.4349 | 110.8383
9345.1719 | 0.061035 | 0.23819 | -0.60028 | -0.23926 | 0.011749 | -0.27344 | -0.040588 | -0.27008 | -0.31128 | -0.78735 | -11.0275 | -0.25635 | 11.0596 | 11.1511 | 0.045776 | -0.098267 | 0.058746 | 0.30014 | -0.14206 | -0.16983 | 2.5589 | 10.6339 | -11.142 | 111.0077 | 111.0168 | 11.1328 | 11.2106 | 122.2046 | 11.1832 | 110.8978
9346.9531 | 0.061035 | 0.23498 | -0.60562 | -0.24139 | 0.020294 | -0.27344 | -0.054474 | -0.21973 | -0.27466 | -0.68207 | -10.6705 | -0.22888 | 10.7254 | 10.817 | 0.061035 | -0.10574 | 0.064087 | 0.30868 | -0.14526 | -0.17303 | 2.4948 | 11.0825 | -10.73 | 111.3602 | 111.351 | 10.8078 | 10.8627 | 121.669 | 10.7986 | 111.5662
9348.7344 | 0.061035 | 0.22324 | -0.59708 | -0.23926 | 0.008545 | -0.24887 | -0.042725 | -0.27008 | -0.35248 | -0.67291 | -10.4782 | -0.24261 | 10.556 | 10.6201 | 0.061035 | -0.082245 | 0.063019 | 0.30334 | -0.13565 | -0.1709 | 2.3621 | 11.5036 | -10.6064 | 111.6531 | 111.5936 | 10.6201 | 10.675 | 121.5317 | 10.6247 | 111.5112
9350.5156 | 0.061035 | 0.21469 | -0.60883 | -0.2243 | 0.012817 | -0.22537 | -0.032043 | -0.17853 | -0.30212 | -0.55389 | -10.4416 | -0.16479 | 10.5057 | 10.5835 | 0.061035 | -0.070496 | 0.074768 | 0.30868 | -0.11429 | -0.17944 | 2.0691 | 11.5723 | -10.5652 | 111.676 | 111.6257 | 10.5743 | 10.643 | 122.3694 | 10.5698 | 111.7401
9352.2969 | 0.061035 | 0.25955 | -0.61096 | -0.22964 | -0.007477 | -0.28305 | -0.040588 | -0.16937 | -0.19684 | -0.32959 | -9.7733 | -0.10071 | 9.8053 | 9.9106 | 0.045776 | -0.10788 | 0.064087 | 0.29587 | -0.13672 | -0.16983 | 1.8356 | 12.1536 | -9.8328 | 112.3215 | 112.2803 | 9.8877 | 9.9564 | 117.1097 | 9.8282 | 112.4359
9354.0781 | 0.045776 | 0.2713 | -0.61844 | -0.23071 | 0.016022 | -0.26596 | -0.045929 | -0.10529 | -0.15106 | -0.25635 | -9.4803 | -0.082397 | 9.5352 | 9.6222 | 0.045776 | -0.091858 | 0.048065 | 0.30121 | -0.12497 | -0.16663 | 1.6708 | 13.2797 | -9.5123 | 112.6236 | 112.6053 | 9.5993 | 9.6542 | 121.8201 | 9.5581 | 112.262
9355.7969 | 0.076294 | 0.2179 | -0.5928 | -0.22644 | 0.05127 | -0.23285 | -0.014954 | -0.34332 | -0.47607 | -0.34332 | -1.4465 | -0.25177 | 1.4374 | 1.593 | 0.061035 | -0.066223 | 0.0737 | 0.28732 | -0.13992 | -0.18478 | 1.5289 | 17.8116 | -1.5472 | 120.8038 | 120.7672 | 1.5289 | 1.5747 | 122.1268 | 1.5152 | 120.7626
9357.5781 | 0.061035 | 0.23498 | -0.60562 | -0.24567 | 0.045929 | -0.27771 | -0.011749 | -0.23804 | -0.24261 | -0.1236 | -1.1993 | -0.27466 | 1.2634 | 1.3916 | 0.076294 | -0.1004 | 0.068359 | 0.27023 | -0.15808 | -0.17624 | 1.5518 | 18.6401 | -1.2268 | 120.8817 | 120.8588 | 1.3641 | 1.4099 | 95.9793 | 1.3367 | 120.3094
9359.2969 | 0.045776 | 0.2681 | -0.60349 | -0.22964 | 0.052338 | -0.27237 | -0.016022 | -0.27466 | -0.31586 | -0.21057 | -1.4191 | -0.2243 | 1.4465 | 1.5701 | 0.061035 | -0.091858 | 0.060883 | 0.28732 | -0.15808 | -0.17303 | 1.3962 | 19.0704 | -1.4511 | 120.7031 | 120.7306 | 1.561 | 1.5976 | 107.0709 | 1.3779 | 120.1355
9361.0781 | 0.030518 | 0.22217 | -0.59815 | -0.23392 | 0.05661 | -0.23712 | 0 | -0.29755 | -0.40283 | -0.33417 | -1.7075 | -0.23346 | 1.7303 | 1.8723 | 0.076294 | -0.075836 | 0.061951 | 0.28198 | -0.13458 | -0.18158 | 1.268 | 19.249 | -1.7853 | 120.4926 | 120.4376 | 1.8402 | 1.886 | 121.8658 | 1.8082 | 120.282
9362.7969 | 0.061035 | 0.19119 | -0.59174 | -0.24994 | 0.043793 | -0.23392 | -0.002136 | -0.43488 | -0.56763 | -0.48981 | -2.6276 | -0.35706 | 2.655 | 2.7969 | 0.045776 | -0.071564 | 0.091858 | 0.30334 | -0.13458 | -0.18585 | 1.1124 | 19.1528 | -2.7466 | 119.5862 | 119.5953 | 2.7649 | 2.8061 | 122.2229 | 2.7603 | 119.22
9364.5938 | 0.045776 | 0.22644 | -0.59921 | -0.23498 | 0.042725 | -0.29266 | -0.018158 | -0.95673 | -0.9613 | -2.7283 | -2.7649 | -0.9613 | 2.8473 | 2.9709 | 0.045776 | -0.10147 | 0.075836 | 0.27664 | -0.16235 | -0.16449 | 1.1719 | 19.2261 | -2.7603 | 119.3298 | 119.2978 | 2.9343 | 2.9892 | 103.9673 | 2.7145 | 118.7164
9366.3125 | 0.076294 | 0.22858 | -0.59708 | -0.21255 | 0.035248 | -0.24567 | -0.008545 | -2.092 | -2.1744 | -3.9276 | -3.891 | -2.0645 | 3.9688 | 4.0878 | 0.061035 | -0.086517 | 0.072632 | 0.29373 | -0.11856 | -0.17517 | 0.96588 | 19.0109 | -3.9047 | 118.2358 | 118.1992 | 4.0283 | 4.0695 | 122.3877 | 4.0421 | 118.3411
9368.0781 | 0.061035 | 0.24674 | -0.60242 | -0.23071 | 0.046997 | -0.2681 | -0.016022 | -2.1652 | -2.1652 | -3.7537 | -4.0512 | -2.1652 | 3.8086 | 3.9413 | 0.045776 | -0.098267 | 0.063019 | 0.27451 | -0.14313 | -0.16983 | 1.3779 | 19.3085 | -3.7491 | 118.3411 | 118.2907 | 3.9276 | 3.9642 | 122.4106 | 3.7949 | 118.2449
9369.875 | 0.061035 | 0.2243 | -0.59921 | -0.24674 | 0.018158 | -0.23498 | -0.027771 | -2.1286 | -2.1835 | -2.9663 | -2.1606 | -2.0874 | 3.0304 | 3.1494 | 0.045776 | -0.084381 | 0.070496 | 0.28625 | -0.1442 | -0.17838 | 0.85602 | 19.5236 | -3.0121 | 119.2062 | 119.1696 | 3.1265 | 3.186 | 122.168 | 3.4378 | 118.396
9371.5938 | 0.061035 | 0.21255 | -0.57465 | -0.23392 | 0.027771 | -0.20508 | -0.023499 | -1.9821 | -2.0782 | -3.0579 | -2.0416 | -1.9363 | 3.1311 | 3.2318 | 0.030518 | -0.068359 | 0.075836 | 0.30121 | -0.13672 | -0.17838 | 1.1673 | 19.455 | -3.1769 | 119.0369 | 118.9957 | 3.3325 | 3.3829 | 122.3007 | 3.3463 | 118.6157
9373.3281 | 0.061035 | 0.25528 | -0.61844 | -0.22324 | -0.003204 | -0.26596 | -0.030975 | -5.1453 | -5.1682 | -5.658 | -5.159 | -5.0446 | 5.6717 | 5.7816 | 0.061035 | -0.089722 | 0.068359 | 0.28091 | -0.12604 | -0.16235 | 0.91095 | 18.0771 | -5.5984 | 116.5009 | 116.4917 | 5.7495 | 5.8182 | 122.0947 | 5.8044 | 116.0934
9375.0938 | 0.045776 | 0.21149 | -0.59494 | -0.23178 | 0.019226 | -0.22324 | -0.021362 | -4.8523 | -4.9759 | -5.4153 | -4.9255 | -4.7516 | 5.4062 | 5.5252 | 0.045776 | -0.064087 | 0.074768 | 0.30655 | -0.12283 | -0.18799 | 0.97504 | 17.7246 | -5.3833 | 116.8625 | 116.835 | 5.5023 | 5.5344 | 122.4792 | 5.484 | 116.478
9376.875 | 0.045776 | 0.23819 | -0.60669 | -0.2211 | 0.018158 | -0.28412 | -0.024567 | -4.8752 | -4.8981 | -5.0262 | -4.8523 | -4.7287 | 5.0446 | 5.1544 | 0.076294 | -0.098267 | 0.057678 | 0.29053 | -0.13992 | -0.16022 | 0.94299 | 17.7246 | -4.9484 | 117.1692 | 117.1555 | 5.1132 | 5.1682 | 121.962 | 5.1132 | 116.89
9378.5938 | 0.045776 | 0.23605 | -0.5896 | -0.22644 | 0.018158 | -0.25955 | -0.024567 | -4.6646 | -4.7104 | -4.6967 | -4.7195 | -4.6051 | 4.7424 | 4.8477 | 0.061035 | -0.092926 | 0.077972 | 0.28305 | -0.13138 | -0.17838 | 1.1078 | 17.3264 | -4.6463 | 117.4301 | 117.3889 | 4.8569 | 4.8889 | 121.9208 | 4.8843 | 117.5537
9380.2969 | 0.045776 | 0.20401 | -0.57999 | -0.22644 | 0.033112 | -0.24033 | -0.003204 | -4.7562 | -4.8889 | -4.8065 | -4.7882 | -4.5639 | 4.7607 | 4.8752 | 0.076294 | -0.065155 | 0.085449 | 0.30121 | -0.10895 | -0.17944 | 0.99792 | 17.0883 | -4.7562 | 117.5079 | 117.4805 | 4.8203 | 4.8981 | 122.4838 | 4.8477 | 117.5766
9382.0781 | 0.045776 | 0.1976 | -0.57892 | -0.23712 | 0.019226 | -0.25528 | -0.009613 | -4.5181 | -4.6234 | -4.5639 | -4.5227 | -4.3259 | 4.509 | 4.6326 | 0.030518 | -0.079041 | 0.09079 | 0.30868 | -0.12817 | -0.16663 | 1.0712 | 17.4591 | -4.4815 | 117.7734 | 117.7277 | 4.5868 | 4.6371 | 122.5021 | 4.5776 | 117.8101
9383.8594 | 0.061035 | 0.22217 | -0.59921 | -0.24674 | 0.02243 | -0.29159 | -0.027771 | -4.7745 | -4.7928 | -4.7424 | -4.7882 | -4.6875 | 4.7882 | 4.8935 | 0.061035 | -0.10147 | 0.063019 | 0.29587 | -0.14526 | -0.16022 | 1.0025 | 17.3492 | -4.6371 | 117.3843 | 117.3706 | 4.8889 | 4.9393 | 122.0032 | 4.7928 | 117.2287
9385.6406 | 0.061035 | 0.21683 | -0.60028 | -0.23178 | 0.019226 | -0.2713 | -0.020294 | -5.5389 | -5.5618 | -5.5023 | -5.5206 | -5.4199 | 5.5618 | 5.6442 | 0.061035 | -0.083313 | 0.069427 | 0.30014 | -0.12711 | -0.17303 | 0.96588 | 17.5095 | -5.4108 | 116.6336 | 116.6336 | 5.6305 | 5.6992 | 121.7926 | 5.6625 | 116.4917
9387.4219 | 0.030518 | 0.22324 | -0.58853 | -0.22644 | 0.018158 | -0.25314 | -0.035248 | -5.4291 | -5.5206 | -5.4565 | -5.4245 | -5.2231 | 5.4153 | 5.5252 | 0.061035 | -0.071564 | 0.0737 | 0.31403 | -0.10788 | -0.16769 | 0.83771 | 17.688 | -5.3284 | 116.89 | 116.8396 | 5.4794 | 5.5481 | 122.3694 | 5.4703 | 116.9449
9389.1406 | 0.061035 | 0.22324 | -0.59067 | -0.23712 | 0.014954 | -0.27664 | -0.016022 | -5.0949 | -5.1132 | -5.0629 | -5.1224 | -5.0308 | 5.1544 | 5.2597 | 0.045776 | -0.10254 | 0.081177 | 0.30121 | -0.12817 | -0.1741 | 0.91553 | 18.4204 | -4.953 | 117.0502 | 117.0227 | 5.2368 | 5.278 | 121.6919 | 5.2368 | 116.5604
9390.9375 | 0.061035 | 0.21576 | -0.58212 | -0.22003 | 0.010681 | -0.25101 | -0.018158 | -4.9072 | -5.0262 | -4.9301 | -4.9393 | -4.7699 | 4.8981 | 5.0079 | 0.061035 | -0.068359 | 0.067291 | 0.30441 | -0.11002 | -0.18158 | 0.83771 | 18.4021 | -4.7607 | 117.3431 | 117.3431 | 4.9805 | 5.04 | 122.5479 | 4.985 | 117.3111
9392.7188 | 0.076294 | 0.22964 | -0.5928 | -0.23926 | 0.007477 | -0.26916 | -0.03418 | -5.0034 | -5.0491 | -4.9713 | -5.0354 | -4.9438 | 5.0262 | 5.1636 | 0.045776 | -0.082245 | 0.077972 | 0.30762 | -0.12604 | -0.1709 | 0.82855 | 18.0862 | -4.8569 | 117.1783 | 117.1738 | 5.1361 | 5.1865 | 121.6507 | 5.1819 | 116.6977
9394.4531 | 0.061035 | 0.21896 | -0.5896 | -0.21683 | 0.010681 | -0.23712 | -0.020294 | -4.9713 | -5.1361 | -5.0262 | -5.0262 | -4.8477 | 4.9988 | 5.0995 | 0.061035 | -0.069427 | 0.0737 | 0.31403 | -0.10254 | -0.18051 | 0.6958 | 18.1824 | -4.9026 | 117.2882 | 117.3111 | 5.072 | 5.127 | 122.4701 | 5.0903 | 117.2333
9396.2344 | 0.076294 | 0.22644 | -0.59921 | -0.2211 | 0.010681 | -0.24674 | -0.012817 | -4.6921 | -4.7974 | -4.7241 | -4.7333 | -4.5456 | 4.6783 | 4.8019 | 0.061035 | -0.066223 | 0.074768 | 0.3183 | -0.093994 | -0.16983 | 0.64087 | 18.3655 | -4.6234 | 117.5949 | 117.5766 | 4.7928 | 4.8386 | 122.4838 | 4.7745 | 117.6224
9398.0312 | 0.045776 | 0.22217 | -0.59067 | -0.22644 | 0.004272 | -0.28412 | -0.016022 | -4.4266 | -4.454 | -4.3945 | -4.4128 | -4.3488 | 4.4403 | 4.5547 | 0.045776 | -0.091858 | 0.076904 | 0.29907 | -0.12711 | -0.17303 | 0.62714 | 18.4525 | -4.2847 | 117.8055 | 117.8238 | 4.5456 | 4.5731 | 121.6919 | 4.5685 | 117.5949
9399.8125 | 0.091553 | 0.23926 | -0.60028 | -0.23498 | 0.002136 | -0.26596 | -0.029907 | -4.0237 | -4.0741 | -4.0192 | -4.0192 | -3.8406 | 4.0009 | 4.1107 | 0.061035 | -0.072632 | 0.071564 | 0.30548 | -0.12283 | -0.1741 | 0.57678 | 19.0704 | -3.8818 | 118.3044 | 118.2678 | 4.0924 | 4.1565 | 121.9666 | 4.1107 | 118.3868
9401.5312 | 0.076294 | 0.23926 | -0.60135 | -0.22964 | 0.014954 | -0.25101 | -0.007477 | -3.8132 | -3.8956 | -3.8315 | -3.8132 | -3.6575 | 3.8086 | 3.9413 | 0.061035 | -0.082245 | 0.084381 | 0.32257 | -0.1207 | -0.16983 | 0.58136 | 19.1574 | -3.6758 | 118.5013 | 118.4463 | 3.8864 | 3.9642 | 122.5479 | 3.8727 | 118.5242
9403.3125 | 0.061035 | 0.25207 | -0.59387 | -0.22537 | 0.008545 | -0.27985 | -0.028839 | -3.7628 | -3.7765 | -3.6987 | -3.7537 | -3.653 | 3.7262 | 3.8498 | 0.061035 | -0.080109 | 0.075836 | 0.31189 | -0.12711 | -0.16876 | 0.60425 | 19.4458 | -3.5614 | 118.483 | 118.4784 | 3.8177 | 3.9139 | 121.9437 | 3.9047 | 118.6295
9405.0312 | 0.076294 | 0.25848 | -0.59708 | -0.22003 | 0.024567 | -0.25955 | -0.01709 | -3.7125 | -3.7491 | -3.6758 | -3.7262 | -3.6942 | 3.7537 | 3.8635 | 0.030518 | -0.060883 | 0.065155 | 0.32684 | -0.11322 | -0.18158 | 0.63629 | 19.4321 | -3.5019 | 118.4738 | 118.4784 | 3.8452 | 3.9093 | 122.4335 | 3.8956 | 118.4372
9406.7969 | 0.061035 | -3.6732 | 3.3795 | -0.21362 | 2.7974 | -0.13886 | 3.8185 | -51.535 | -51.6907 | -51.7227 | -52.272 | -8.9584 | 54.657 | 54.6936 | 0.061035 | 10.6747 | -0.29266 | 0.53833 | 2.5528 | 0.59174 | -0.41657 | -1.6754 | -33.8287 | 65.4236 | 65.3915 | 55.8334 | 56.012 | 121.6965 | 56.3004 | 65.1352
9408.5938 | 0.045776 | 0.23712 | -0.22003 | -0.23712 | -0.085449 | -0.26596 | -0.055542 | 0.11902 | 0.064087 | 0.15564 | 0.07782 | 0.082397 | -0.059509 | 0.073242 | 0.061035 | 18.0341 | -0.28198 | 1.2177 | 8.013 | 8.3815 | 0.20599 | -1.5793 | -6.6513 | 58.9554 | 58.8409 | 62.2192 | 62.439 | 121.7468 | 61.4685 | 60.0998
9410.3281 | 0.061035 | 0.24033 | -0.20721 | -0.25314 | -0.087585 | -0.26916 | -0.048065 | 0.11902 | 0.068665 | 0.1236 | 0.082397 | 0.082397 | -0.054932 | 0.086975 | 0.061035 | 34.9989 | -0.10361 | 1.4879 | 6.6138 | 29.1777 | 0.24261 | -1.8127 | -4.628 | 69.3329 | 69.0079 | 51.21 | 51.5259 | 121.5134 | 53.8513 | 67.1585
9412.1094 | 0.045776 | 0.24246 | -0.2179 | -0.22858 | -0.086517 | -0.26489 | -0.050201 | 0.11902 | 0.032043 | 0.10986 | 0.059509 | 0.09613 | -0.054932 | 0.068665 | 0.045776 | 34.9989 | -0.1207 | 11.4075 | 12.953 | 34.9989 | 2.0279 | -12.9822 | 14.8773 | 34.7809 | 34.8221 | 77.5543 | 76.9684 | 119.4031 | 80.4977 | 38.9145
9413.8281 | 0.030518 | 0.27237 | -0.2179 | -0.2211 | -0.095062 | -0.27344 | -0.054474 | 0.14648 | 0.091553 | 0.14191 | 0.086975 | 0.086975 | -0.041199 | 0.07782 | 0.061035 | 34.9989 | -0.1506 | 15.3307 | 9.848 | 12.9744 | 0.14648 | -3.9185 | -4.3304 | 52.1622 | 52.1805 | 67.4515 | 67.6529 | 121.0281 | 66.7511 | 54.0894
9415.625 | 0.045776 | 0.22751 | -0.22003 | -0.23498 | -0.10574 | -0.2713 | -0.044861 | 0.068665 | 0.013733 | 0.068665 | 0.045776 | 0.09613 | -0.045776 | 0.086975 | 0.045776 | 26.3333 | -0.14099 | 19.0808 | 7.4384 | 0.10254 | 0.11902 | -2.6642 | -5.9601 | 56.4926 | 56.4789 | 63.858 | 64.1876 | 121.3028 | 63.6246 | 57.3578
9417.3594 | 0.076294 | 0.22858 | -0.20615 | -0.22858 | -0.098267 | -0.22964 | -0.044861 | 0.064087 | -0.086975 | -0.009155 | 0.009155 | 0.13275 | -0.018311 | 0.12817 | 0.045776 | 0.16129 | -0.28305 | -0.011749 | -0.092926 | -0.03952 | 0.004578 | -0.29297 | -0.07782 | 0.82398 | 0.82855 | 0.013733 | 0.10071 | 121.312 | 120.0439 | 0.82855
9419.1406 | 0.076294 | 0.2243 | -0.21149 | -0.24567 | -0.088654 | -0.24674 | -0.048065 | 0.054932 | -0.054932 | -0.004578 | 0.004578 | 0.13733 | -0.009155 | 0.14648 | 0.076294 | 0.1474 | -0.29053 | -0.020294 | -0.11643 | -0.036316 | -0.009155 | -0.18768 | -0.068665 | 0.85602 | 0.83313 | 0.045776 | 0.10529 | 121.4539 | 120.3644 | 0.84686
9420.875 | 0.076294 | 0.22324 | -0.20294 | -0.2179 | -0.09079 | -0.24353 | -0.027771 | 0.073242 | -0.068665 | 0.013733 | -0.004578 | 0.13733 | -0.027466 | 0.10986 | 0.030518 | 0.15915 | -0.28625 | -0.019226 | -0.10574 | -0.021362 | 0.050354 | -0.1831 | -0.045776 | 0.91095 | 0.90637 | 0.018311 | 0.11444 | 121.5866 | 120.3598 | 0.92468
9422.6562 | 0.061035 | 0.24246 | -0.20294 | -0.23498 | -0.1004 | -0.2713 | -0.044861 | 0.11444 | 0.045776 | 0.10529 | 0.050354 | 0.091553 | -0.041199 | 0.07782 | 0.061035 | 0.13351 | -0.28946 | -0.030975 | -0.12604 | -0.021362 | 0.086975 | -0.054932 | 0.022888 | 1.2451 | 1.2497 | 0.032043 | 0.068665 | 121.463 | 120.1401 | 1.3275
9424.3906 | 0.061035 | 0.21576 | -0.20401 | -0.25207 | -0.098267 | -0.26062 | -0.045929 | 0.036621 | -0.050354 | 0 | 0.004578 | 0.12817 | -0.004578 | 0.10529 | 0.061035 | 0.16022 | -0.28305 | -0.019226 | -0.11963 | -0.040588 | 0.004578 | -0.086975 | -0.091553 | 1.5015 | 1.4786 | 0.068665 | 0.10986 | 121.5454 | 119.9158 | 1.506
9426.1562 | 0.076294 | 0.20935 | -0.20081 | -0.24246 | -0.085449 | -0.25742 | -0.028839 | 0.050354 | -0.045776 | 0.018311 | 0.032043 | 0.13733 | -0.004578 | 0.12817 | 0.045776 | 0.14954 | -0.29053 | -0.019226 | -0.1004 | -0.027771 | 0.027466 | -0.009155 | -0.045776 | 1.6434 | 1.6342 | 0.050354 | 0.11902 | 121.6415 | 119.7464 | 1.6479
9427.9375 | 0.076294 | 0.21683 | -0.20294 | -0.2179 | -0.091858 | -0.23819 | -0.033112 | 0.013733 | -0.082397 | -0.009155 | 0.004578 | 0.11902 | -0.013733 | 0.1236 | 0.061035 | 0.15381 | -0.28519 | -0.01709 | -0.093994 | -0.023499 | -0.045776 | -0.022888 | -0.10071 | 3.1815 | 3.1815 | 0.045776 | 0.10986 | 121.6187 | 118.2312 | 3.2043
9429.6562 | 0.061035 | 0.2179 | -0.20615 | -0.2211 | -0.082245 | -0.25848 | -0.027771 | 0.10071 | 0.013733 | 0.054932 | 0.050354 | 0.11444 | -0.022888 | 0.11444 | 0.045776 | 0.14526 | -0.29266 | -0.021362 | -0.091858 | -0.026703 | 0.036621 | 0.11444 | -0.018311 | 3.4973 | 3.479 | 0.022888 | 0.09613 | 121.6507 | 117.9565 | 3.5385
9431.4375 | 0.045776 | 0.23605 | -0.2179 | -0.24139 | -0.093994 | -0.29587 | -0.040588 | 0.10529 | 0.10529 | 0.15106 | 0.091553 | 0.091553 | -0.041199 | 0.07782 | 0.045776 | 0.11963 | -0.28519 | -0.033112 | -0.11643 | -0.027771 | 0.10071 | 0.28381 | 0.082397 | 5.8868 | 5.8502 | 0.004578 | 0.091553 | 121.5866 | 115.5991 | 5.9647
9433.1562 | 0.076294 | 0.24033 | -0.20081 | -0.23392 | -0.084381 | -0.27451 | -0.049133 | 0.12817 | 0.068665 | 0.1236 | 0.073242 | 0.068665 | -0.041199 | 0.07782 | 0.061035 | 0.15274 | -0.29587 | -0.024567 | -0.12176 | -0.014954 | 0.09613 | 0.13275 | 0.054932 | 1.1307 | 1.1124 | 0.018311 | 0.10529 | 121.6049 | 120.3552 | 1.2314
9434.9531 | 0.030518 | 0.2478 | -0.22537 | -0.22644 | -0.084381 | -0.28198 | -0.055542 | 0.054932 | 0.018311 | 0.086975 | 0.054932 | 0.10986 | -0.041199 | 0.091553 | 0.076294 | 0.13458 | -0.2948 | -0.028839 | -0.11963 | -0.026703 | 0.059509 | 0.12817 | 0.045776 | 1.1993 | 1.1719 | 0.032043 | 0.086975 | 121.6553 | 120.282 | 1.268
9436.6562 | 0.076294 | 0.22217 | -0.1976 | -0.22644 | -0.085449 | -0.23498 | -0.029907 | 0.082397 | -0.027466 | 0.036621 | 0.041199 | 0.13275 | -0.009155 | 0.1236 | 0.045776 | 0.16449 | -0.28198 | -0.027771 | -0.088654 | -0.029907 | 0 | 0.036621 | -0.050354 | 1.2863 | 1.2497 | 0.027466 | 0.11444 | 121.7194 | 120.2362 | 1.3
9438.4375 | 0.045776 | 0.23178 | -0.1976 | -0.23605 | -0.093994 | -0.2478 | -0.036316 | 0.036621 | -0.068665 | -0.004578 | 0.009155 | 0.13275 | -0.013733 | 0.11444 | 0.061035 | 0.11108 | -0.24246 | -0.019226 | -0.095062 | -0.036316 | 0.018311 | 0.032043 | 0.032043 | 0.72327 | 0.69122 | 0.009155 | 0.073242 | 121.7834 | 120.8176 | 0.73242
9440.1719 | 0.061035 | 0.22644 | -0.20615 | -0.22537 | -0.10361 | -0.24887 | -0.038452 | 0.036621 | -0.032043 | 0.018311 | 0.041199 | 0.1236 | -0.009155 | 0.1236 | 0.045776 | 0.086517 | -0.22324 | -0.028839 | -0.093994 | -0.030975 | 0.027466 | 0.11444 | 0.073242 | 0.62256 | 0.59052 | 0.009155 | 0.068665 | 121.7834 | 120.9412 | 0.61798
9441.9531 | 0.061035 | 0.24994 | -0.20615 | -0.24033 | -0.10361 | -0.27771 | -0.05127 | 0.050354 | 0.036621 | 0.091553 | 0.036621 | 0.086975 | -0.045776 | 0.091553 | 0.061035 | 0.057678 | -0.23285 | -0.036316 | -0.10361 | -0.021362 | 0.068665 | 0.11902 | 0.17853 | 0.50354 | 0.48065 | -0.027466 | 0.050354 | 121.669 | 121.0831 | 0.58594
9443.7188 | 0.061035 | 0.24567 | -0.19867 | -0.21896 | -0.097198 | -0.27344 | -0.042725 | 0.1236 | 0.064087 | 0.14191 | 0.091553 | 0.064087 | -0.050354 | 0.082397 | 0.045776 | 0.053406 | -0.20615 | -0.030975 | -0.095062 | -0.03952 | 0.13275 | 0.17395 | 0.24261 | 0.32959 | 0.31586 | -0.050354 | 0.018311 | 121.7514 | 121.2433 | 0.3891
9445.4375 | 0.061035 | 0.23605 | -0.20508 | -0.2478 | -0.11856 | -0.27557 | -0.055542 | 0.032043 | 0.004578 | 0.064087 | 0.050354 | 0.11444 | -0.036621 | 0.073242 | 0.045776 | 0.040588 | -0.1944 | -0.033112 | -0.10574 | -0.036316 | 0.059509 | 0.12817 | 0.23346 | 0.33875 | 0.31128 | -0.032043 | 0.009155 | 121.7331 | 121.2753 | 0.40283
9447.2031 | 0.045776 | 0.22858 | -0.21149 | -0.23819 | -0.089722 | -0.26489 | -0.041656 | 0.086975 | 0.027466 | 0.082397 | 0.07782 | 0.09613 | -0.018311 | 0.11902 | 0.045776 | 0.054474 | -0.19867 | -0.042725 | -0.087585 | -0.055542 | 0.036621 | 0.086975 | 0.17853 | 0.36163 | 0.33417 | -0.022888 | 0.054932 | 121.701 | 121.2845 | 0.39825
9448.9844 | 0.061035 | 0.24567 | -0.19867 | -0.22751 | -0.093994 | -0.27878 | -0.045929 | 0.064087 | 0.013733 | 0.086975 | 0.045776 | 0.09613 | -0.027466 | 0.091553 | 0.061035 | 0.044861 | -0.21362 | -0.027771 | -0.10147 | -0.054474 | 0.091553 | 0.1236 | 0.28381 | 0.34332 | 0.32501 | -0.050354 | 0.018311 | 121.7697 | 121.2433 | 0.41657
9450.7656 | 0.061035 | 0.23071 | -0.20508 | -0.24246 | -0.077972 | -0.2681 | -0.046997 | 0.036621 | -0.041199 | 0.018311 | 0.004578 | 0.1236 | -0.004578 | 0.10986 | 0.076294 | 0.071564 | -0.21576 | -0.02243 | -0.084381 | -0.069427 | 0.027466 | 0.064087 | 0.19684 | 0.39368 | 0.37537 | -0.018311 | 0.041199 | 121.7377 | 121.2753 | 0.43488
9452.4844 | 0.076294 | 0.2478 | -0.21042 | -0.23392 | -0.079041 | -0.26169 | -0.053406 | 0.091553 | 0.045776 | 0.091553 | 0.059509 | 0.082397 | -0.045776 | 0.07782 | 0.091553 | 0.03952 | -0.21042 | -0.021362 | -0.084381 | -0.045929 | 0.09613 | 0.11444 | 0.29297 | 0.37994 | 0.3479 | -0.064087 | -0.004578 | 121.7239 | 121.2799 | 0.46234
9454.2656 | 0.061035 | 0.19867 | -0.19867 | -0.2243 | -0.097198 | -0.23285 | -0.045929 | 0.068665 | -0.027466 | 0.022888 | 0.045776 | 0.11444 | -0.013733 | 0.10986 | 0.076294 | 0.065155 | -0.20187 | -0.023499 | -0.068359 | -0.05661 | 0.036621 | 0.11902 | 0.21057 | 0.41199 | 0.38452 | -0.054932 | 0.013733 | 121.875 | 121.2387 | 0.42114
9456 | 0.045776 | 0.22003 | -0.20508 | -0.22003 | -0.1004 | -0.24674 | -0.028839 | 0.032043 | -0.086975 | -0.022888 | 0 | 0.11444 | -0.018311 | 0.12817 | 0.045776 | 0.070496 | -0.19119 | -0.028839 | -0.068359 | -0.054474 | 0.013733 | 0.022888 | 0.16022 | 0.40741 | 0.38452 | -0.054932 | 0 | 121.8887 | 121.2799 | 0.40283
9457.7656 | 0.045776 | 0.25742 | -0.21362 | -0.22858 | -0.1004 | -0.27985 | -0.046997 | 0.073242 | 0.041199 | 0.086975 | 0.045776 | 0.07782 | -0.041199 | 0.07782 | 0.061035 | 0.03952 | -0.19974 | -0.035248 | -0.089722 | -0.035248 | 0.073242 | 0.14191 | 0.26093 | 0.35706 | 0.35248 | -0.068665 | 0.004578 | 121.7651 | 121.344 | 0.46234
9459.4844 | 0.061035 | 0.2446 | -0.20935 | -0.23285 | -0.089722 | -0.24567 | -0.042725 | 0.14191 | 0.050354 | 0.1236 | 0.086975 | 0.086975 | -0.054932 | 0.073242 | 0.076294 | 0.052338 | -0.18799 | -0.025635 | -0.082245 | -0.040588 | 0.11902 | 0.18768 | 0.30212 | 0.33875 | 0.33417 | -0.07782 | -0.013733 | 121.907 | 121.2936 | 0.38452
9461.2656 | 0.045776 | 0.22751 | -0.21469 | -0.2446 | -0.095062 | -0.25742 | -0.05661 | 0.032043 | -0.004578 | 0.027466 | 0.018311 | 0.10986 | 0.009155 | 0.10986 | 0.076294 | 0.045929 | -0.1944 | -0.021362 | -0.093994 | -0.03952 | 0.013733 | 0.13733 | 0.19226 | 0.39368 | 0.37079 | -0.050354 | 0.013733 | 121.7834 | 121.3257 | 0.42572
9462.9844 | 0.061035 | 0.24139 | -0.19119 | -0.2243 | -0.088654 | -0.26169 | -0.043793 | 0.11444 | 0 | 0.09613 | 0.091553 | 0.09613 | -0.050354 | 0.07782 | 0.045776 | 0.048065 | -0.19653 | -0.024567 | -0.068359 | -0.043793 | 0.10986 | 0.18768 | 0.29755 | 0.35706 | 0.32501 | -0.10529 | -0.018311 | 121.9208 | 121.3165 | 0.38452
9464.7656 | 0.045776 | 0.22858 | -0.2243 | -0.23285 | -0.09079 | -0.27664 | -0.041656 | 0.064087 | -0.009155 | 0.07782 | 0.050354 | 0.09613 | -0.054932 | 0.082397 | 0.061035 | 0.066223 | -0.22537 | -0.043793 | -0.10895 | -0.03952 | 0.068665 | 0.16937 | 0.20599 | 0.70038 | 0.6958 | -0.054932 | 0.013733 | 121.8521 | 121.0327 | 0.76446
9466.5625 | 0.061035 | 0.23926 | -0.20508 | -0.2243 | -0.099335 | -0.27557 | -0.065155 | 0.07782 | -0.004578 | 0.068665 | 0.041199 | 0.086975 | -0.036621 | 0.082397 | 0.045776 | 0.0737 | -0.23178 | -0.03418 | -0.10147 | -0.042725 | 0.054932 | 0.16937 | 0.16479 | 0.71411 | 0.70496 | -0.068665 | 0.009155 | 121.8246 | 121.0236 | 0.79193
9468.2969 | 0.045776 | 0.23819 | -0.21362 | -0.23498 | -0.097198 | -0.26382 | -0.040588 | 0.036621 | -0.036621 | 0.018311 | 0.004578 | 0.1236 | -0.009155 | 0.12817 | 0.030518 | 0.082245 | -0.2211 | -0.041656 | -0.095062 | -0.033112 | -0.013733 | 0.13275 | 0.082397 | 0.85602 | 0.84686 | -0.013733 | 0.050354 | 121.8292 | 120.9183 | 0.88348
9470.0781 | 0.076294 | 0.23712 | -0.1976 | -0.23498 | -0.088654 | -0.24567 | -0.024567 | 0.10071 | 0.013733 | 0.082397 | 0.059509 | 0.091553 | -0.045776 | 0.091553 | 0.030518 | 0.082245 | -0.24033 | -0.035248 | -0.081177 | -0.037384 | 0.10529 | 0.20142 | 0.17853 | 0.90179 | 0.87891 | -0.068665 | -0.004578 | 121.9666 | 120.7993 | 0.97046
9471.8594 | 0.045776 | 0.23178 | -0.19867 | -0.23605 | -0.091858 | -0.25101 | -0.037384 | 0.054932 | -0.059509 | -0.018311 | 0 | 0.13275 | -0.018311 | 0.10529 | 0.076294 | 0.085449 | -0.21576 | -0.019226 | -0.092926 | -0.03418 | 0.018311 | 0.11444 | 0.09613 | 0.98419 | 0.94299 | -0.045776 | 0.018311 | 121.994 | 120.7535 | 0.99792
9473.6406 | 0.061035 | 0.23605 | -0.21469 | -0.22324 | -0.10361 | -0.29373 | -0.055542 | 0.11902 | 0.10071 | 0.13733 | 0.082397 | 0.086975 | -0.041199 | 0.082397 | 0.045776 | 0.060883 | -0.21149 | -0.038452 | -0.11322 | -0.032043 | 0.13275 | 0.27008 | 0.24719 | 1.0117 | 1.0208 | -0.07782 | -0.018311 | 121.907 | 120.7123 | 1.0941
9475.4219 | 0.045776 | 0.23392 | -0.20721 | -0.22644 | -0.095062 | -0.24887 | -0.043793 | 0.12817 | 0.068665 | 0.11444 | 0.10529 | 0.073242 | -0.045776 | 0.082397 | 0.061035 | 0.061951 | -0.21683 | -0.026703 | -0.081177 | -0.037384 | 0.11444 | 0.20599 | 0.21515 | 1.0117 | 0.98419 | -0.09613 | 0.004578 | 121.9666 | 120.6985 | 1.0574
9477.1875 | 0.076294 | 0.22964 | -0.19119 | -0.23498 | -0.09079 | -0.26169 | -0.03418 | 0.14648 | 0.068665 | 0.12817 | 0.091553 | 0.07782 | -0.045776 | 0.082397 | 0.061035 | 0.072632 | -0.23071 | -0.029907 | -0.099335 | -0.035248 | 0.10986 | 0.23346 | 0.20599 | 1.0574 | 1.0529 | -0.073242 | 0.004578 | 121.9528 | 120.6757 | 1.1169
9478.9688 | 0.061035 | 0.22537 | -0.20935 | -0.24994 | -0.091858 | -0.28091 | -0.046997 | 0.1236 | 0.10529 | 0.15106 | 0.086975 | 0.082397 | -0.036621 | 0.064087 | 0.061035 | 0.049133 | -0.22217 | -0.027771 | -0.11963 | -0.035248 | 0.11444 | 0.27008 | 0.21973 | 1.1719 | 1.1444 | -0.07782 | -0.018311 | 121.8979 | 120.6024 | 1.2543
9480.75 | 0.061035 | 0.20187 | -0.19867 | -0.24353 | -0.10254 | -0.23285 | -0.032043 | 0.10529 | 0.009155 | 0.054932 | 0.045776 | 0.11902 | -0.013733 | 0.091553 | 0.076294 | 0.082245 | -0.22217 | -0.016022 | -0.09079 | -0.053406 | 0.059509 | 0.15564 | 0.10071 | 1.3184 | 1.2955 | -0.050354 | 0.041199 | 121.9894 | 120.4422 | 1.3412
9482.5156 | 0.045776 | 0.21683 | -0.19226 | -0.24033 | -0.086517 | -0.24246 | -0.037384 | 0.064087 | -0.018311 | 0.036621 | 0.054932 | 0.12817 | -0.013733 | 0.1236 | 0.076294 | 0.084381 | -0.21255 | -0.019226 | -0.093994 | -0.032043 | 0.041199 | 0.15564 | 0.068665 | 1.3412 | 1.3092 | -0.018311 | 0.036621 | 122.0352 | 120.4514 | 1.3367
9484.2344 | 0.045776 | 0.22644 | -0.2211 | -0.2478 | -0.093994 | -0.26382 | -0.041656 | 0.013733 | -0.054932 | 0.013733 | -0.013733 | 0.14191 | -0.009155 | 0.11902 | 0.030518 | 0.085449 | -0.23178 | -0.028839 | -0.10468 | -0.03418 | -0.009155 | 0.10986 | 0.059509 | 1.5106 | 1.474 | -0.009155 | 0.050354 | 121.9254 | 120.3369 | 1.5335
9486.0156 | 0.030518 | 0.2446 | -0.21149 | -0.2211 | -0.09079 | -0.2681 | -0.029907 | 0.11444 | 0.064087 | 0.1236 | 0.09613 | 0.086975 | -0.073242 | 0.064087 | 0.061035 | 0.091858 | -0.2446 | -0.029907 | -0.09079 | -0.035248 | 0.11444 | 0.18768 | 0.15106 | 1.5564 | 1.5472 | -0.036621 | 0.027466 | 122.0352 | 120.1996 | 1.6296
9487.7969 | 0.061035 | 0.2478 | -0.21576 | -0.23178 | -0.093994 | -0.29053 | -0.055542 | 0.11444 | 0.082397 | 0.12817 | 0.09613 | 0.09613 | -0.045776 | 0.091553 | 0.076294 | 0.068359 | -0.24567 | -0.036316 | -0.11536 | -0.025635 | 0.10986 | 0.2243 | 0.18768 | 1.8356 | 1.8127 | -0.059509 | 0.027466 | 121.9757 | 119.957 | 1.8951
9489.5156 | 0.030518 | 0.22751 | -0.20935 | -0.25421 | -0.10468 | -0.27771 | -0.044861 | 0.1236 | 0.10071 | 0.15106 | 0.091553 | 0.091553 | -0.054932 | 0.091553 | 0.045776 | 0.10361 | -0.25421 | -0.03418 | -0.11322 | -0.033112 | 0.10529 | 0.22888 | 0.16022 | 1.9684 | 1.918 | -0.009155 | 0.041199 | 121.9437 | 119.8563 | 2.0279
9491.2969 | 0.045776 | 0.23498 | -0.20508 | -0.23071 | -0.09613 | -0.25207 | -0.046997 | 0.091553 | -0.013733 | 0.050354 | 0.041199 | 0.10986 | -0.032043 | 0.10986 | 0.045776 | 0.097198 | -0.25207 | -0.032043 | -0.10147 | -0.038452 | 0.11444 | 0.16022 | 0.086975 | 2.0416 | 2.037 | -0.027466 | 0.045776 | 122.0764 | 119.7556 | 2.1103
9493.0781 | 0.061035 | 0.22217 | -0.21255 | -0.22964 | -0.083313 | -0.25955 | -0.05127 | 0.09613 | 0.07782 | 0.1236 | 0.086975 | 0.09613 | -0.041199 | 0.09613 | 0.061035 | 0.09079 | -0.25955 | -0.033112 | -0.10468 | -0.043793 | 0.059509 | 0.17395 | 0.086975 | 2.0004 | 1.9867 | -0.022888 | 0.054932 | 121.9208 | 119.8563 | 2.0828
9494.8594 | 0.076294 | 0.2211 | -0.20508 | -0.2179 | -0.11322 | -0.25207 | -0.029907 | 0.07782 | 0.009155 | 0.068665 | 0.045776 | 0.09613 | -0.027466 | 0.09613 | 0.061035 | 0.10468 | -0.26596 | -0.035248 | -0.088654 | -0.032043 | 0.091553 | 0.14191 | 0.10529 | 2.0096 | 2.0096 | -0.050354 | 0.050354 | 122.0901 | 119.7601 | 2.0737
9496.5781 | 0.061035 | 0.2478 | -0.21255 | -0.25742 | -0.10254 | -0.27771 | -0.055542 | 0.1236 | 0.11902 | 0.14648 | 0.09613 | 0.082397 | -0.064087 | 0.086975 | 0.045776 | 0.097198 | -0.27557 | -0.040588 | -0.11429 | -0.03418 | 0.13733 | 0.24719 | 0.16937 | 2.1881 | 2.1698 | -0.018311 | 0.054932 | 121.9986 | 119.6503 | 2.2751
9498.375 | 0.045776 | 0.2179 | -0.20721 | -0.24674 | -0.098267 | -0.25955 | -0.049133 | 0.07782 | 0.018311 | 0.07782 | 0.045776 | 0.11444 | -0.027466 | 0.1236 | 0.045776 | 0.11002 | -0.25955 | -0.036316 | -0.10681 | -0.038452 | 0.013733 | 0.10529 | 0.018311 | 2.2751 | 2.243 | 0.013733 | 0.082397 | 121.9574 | 119.6274 | 2.3346
9500.1562 | 0.061035 | 0.22644 | -0.21042 | -0.24887 | -0.082245 | -0.25955 | -0.052338 | 0.059509 | 0.013733 | 0.041199 | 0.022888 | 0.12817 | -0.009155 | 0.12817 | 0.091553 | 0.11536 | -0.26703 | -0.032043 | -0.10147 | -0.03418 | 0 | 0.091553 | -0.004578 | 2.3117 | 2.3026 | 0.036621 | 0.091553 | 121.9803 | 119.577 | 2.3621
9501.875 | 0.061035 | 0.25421 | -0.21362 | -0.2211 | -0.099335 | -0.2681 | -0.041656 | 0.1236 | 0.068665 | 0.13275 | 0.07782 | 0.07782 | -0.054932 | 0.082397 | 0.061035 | 0.10147 | -0.2681 | -0.025635 | -0.099335 | -0.035248 | 0.082397 | 0.14191 | 0.086975 | 2.3666 | 2.3575 | -0.018311 | 0.045776 | 121.9757 | 119.5038 | 2.4857
9503.6562 | 0.061035 | 0.22537 | -0.20721 | -0.23071 | -0.091858 | -0.2478 | -0.037384 | 0.045776 | -0.082397 | -0.027466 | -0.004578 | 0.1236 | -0.009155 | 0.12817 | 0.061035 | 0.098267 | -0.24246 | -0.012817 | -0.097198 | -0.037384 | 0.004578 | 0.045776 | 0 | 2.1606 | 2.1423 | 0.022888 | 0.064087 | 122.1039 | 119.7372 | 2.1835
9505.4531 | 0.045776 | 0.23178 | -0.20828 | -0.22003 | -0.086517 | -0.28198 | -0.052338 | 0.059509 | 0.009155 | 0.082397 | 0.050354 | 0.10529 | -0.004578 | 0.091553 | 0.045776 | 0.085449 | -0.25314 | -0.032043 | -0.11429 | -0.026703 | 0.050354 | 0.13733 | 0.086975 | 1.9089 | 1.8951 | -0.009155 | 0.073242 | 122.0215 | 119.9707 | 2.005
9507.1719 | 0.061035 | 0.2211 | -0.1944 | -0.23498 | -0.080109 | -0.23712 | -0.03418 | 0.11444 | 0.022888 | 0.050354 | 0.050354 | 0.10071 | -0.013733 | 0.10986 | 0.076294 | 0.11856 | -0.23605 | -0.025635 | -0.09079 | -0.045929 | 0.050354 | 0.1236 | 0.018311 | 1.9089 | 1.8677 | -0.004578 | 0.059509 | 122.0856 | 120.0073 | 1.9089
9508.9531 | 0.045776 | 0.22964 | -0.20401 | -0.2211 | -0.088654 | -0.25955 | -0.036316 | 0.064087 | 0.009155 | 0.064087 | 0.050354 | 0.091553 | -0.027466 | 0.086975 | 0.045776 | 0.099335 | -0.26276 | -0.027771 | -0.0737 | -0.029907 | 0.086975 | 0.16937 | 0.082397 | 1.8677 | 1.8448 | -0.036621 | 0.054932 | 122.1313 | 119.9982 | 1.9135
9510.7344 | 0.045776 | 0.23071 | -0.19974 | -0.24139 | -0.10468 | -0.29053 | -0.05127 | 0.064087 | 0.013733 | 0.091553 | 0.041199 | 0.091553 | -0.027466 | 0.10071 | 0.061035 | 0.09079 | -0.25101 | -0.028839 | -0.12924 | -0.03952 | 0.059509 | 0.12817 | 0.07782 | 1.7944 | 1.7899 | -0.013733 | 0.073242 | 122.0123 | 120.0714 | 1.8951
9512.4688 | 0.061035 | 0.23178 | -0.21149 | -0.21896 | -0.10574 | -0.25848 | -0.040588 | 0.068665 | -0.027466 | 0.027466 | 0.027466 | 0.1236 | -0.009155 | 0.12817 | 0.076294 | 0.11108 | -0.26916 | -0.019226 | -0.09079 | -0.037384 | 0.068665 | 0.091553 | 0.059509 | 1.8219 | 1.7944 | -0.041199 | 0.018311 | 122.1634 | 120.0485 | 1.8539
9514.25 | 0.045776 | 0.22537 | -0.20401 | -0.23498 | -0.099335 | -0.2478 | -0.050201 | 0.045776 | -0.059509 | 0.004578 | 0.009155 | 0.12817 | 0 | 0.13733 | 0.061035 | 0.09613 | -0.24139 | -0.016022 | -0.098267 | -0.021362 | 0.018311 | 0.10071 | -0.013733 | 1.7075 | 1.6983 | -0.022888 | 0.054932 | 122.168 | 120.2133 | 1.7441
9516.0469 | 0.061035 | 0.22858 | -0.20508 | -0.23392 | -0.1004 | -0.24887 | -0.032043 | 0.036621 | -0.082397 | -0.018311 | -0.004578 | 0.12817 | 0.009155 | 0.1236 | 0.045776 | 0.10254 | -0.25848 | -0.019226 | -0.10147 | -0.02243 | -0.004578 | 0.036621 | 0.004578 | 1.7899 | 1.7578 | -0.013733 | 0.054932 | 122.1863 | 120.163 | 1.7487
9517.7656 | 0.045776 | 0.24674 | -0.20508 | -0.24033 | -0.083313 | -0.29587 | -0.05127 | 0.054932 | 0.027466 | 0.091553 | 0.054932 | 0.10071 | -0.004578 | 0.1236 | 0.076294 | 0.072632 | -0.23819 | -0.042725 | -0.12817 | -0.020294 | 0.050354 | 0.13733 | 0.10986 | 1.8448 | 1.8127 | -0.064087 | 0.013733 | 122.0581 | 120.0897 | 1.8906
9519.5469 | 0.061035 | 0.22217 | -0.19974 | -0.2211 | -0.095062 | -0.24033 | -0.041656 | 0.027466 | -0.09613 | -0.022888 | 0.004578 | 0.10986 | -0.013733 | 0.1236 | 0.061035 | 0.1004 | -0.23392 | -0.03418 | -0.09079 | -0.032043 | -0.009155 | 0.022888 | -0.018311 | 1.8906 | 1.8539 | 0 | 0.050354 | 122.1451 | 120.076 | 1.8906
9521.2812 | 0.045776 | 0.25101 | -0.20401 | -0.23498 | -0.098267 | -0.28732 | -0.030975 | 0.064087 | 0.032043 | 0.086975 | 0.041199 | 0.082397 | -0.036621 | 0.07782 | 0.045776 | 0.080109 | -0.24139 | -0.025635 | -0.12497 | -0.023499 | 0.045776 | 0.10986 | 0.091553 | 1.7624 | 1.7578 | -0.041199 | 0.032043 | 122.0261 | 120.1859 | 1.8585
9523.0469 | 0.061035 | 0.25421 | -0.21683 | -0.22964 | -0.09613 | -0.27771 | -0.059814 | 0.091553 | 0.032043 | 0.032043 | 0.045776 | 0.07782 | -0.027466 | 0.10529 | 0.061035 | 0.086517 | -0.23605 | -0.023499 | -0.11643 | -0.021362 | 0.041199 | 0.10071 | 0.091553 | 1.7899 | 1.7761 | -0.054932 | 0.032043 | 122.049 | 120.1492 | 1.8677
9524.8125 | 0.061035 | 0.2478 | -0.20935 | -0.23498 | -0.095062 | -0.26382 | -0.045929 | 0.082397 | 0.022888 | 0.068665 | 0.059509 | 0.082397 | -0.027466 | 0.091553 | 0.061035 | 0.086517 | -0.24994 | -0.027771 | -0.11749 | -0.029907 | 0.041199 | 0.10986 | 0.091553 | 1.7578 | 1.7487 | -0.054932 | 0.013733 | 122.0535 | 120.2179 | 1.8585
9526.5938 | 0.091553 | 0.24033 | -0.20294 | -0.22858 | -0.10147 | -0.2478 | -0.050201 | 0.14648 | 0.041199 | 0.059509 | 0.07782 | 0.082397 | -0.041199 | 0.082397 | 0.045776 | 0.095062 | -0.23605 | -0.025635 | -0.095062 | -0.041656 | 0.10529 | 0.15564 | 0.11444 | 1.7487 | 1.7212 | -0.045776 | 0.009155 | 122.1817 | 120.163 | 1.8127
9528.3125 | 0.061035 | 0.24567 | -0.21362 | -0.21576 | -0.092926 | -0.26169 | -0.03952 | 0.15106 | 0.082397 | 0.1236 | 0.082397 | 0.07782 | -0.059509 | 0.082397 | 0.076294 | 0.076904 | -0.25314 | -0.025635 | -0.093994 | -0.033112 | 0.11902 | 0.16479 | 0.15106 | 1.8494 | 1.8127 | -0.068665 | 0.022888 | 122.1451 | 120.108 | 1.918
9530.0781 | 0.045776 | 0.21362 | -0.20294 | -0.24567 | -0.11002 | -0.25421 | -0.043793 | 0.059509 | -0.082397 | -0.009155 | -0.013733 | 0.11444 | 0.004578 | 0.13275 | 0.061035 | 0.085449 | -0.22537 | -0.020294 | -0.099335 | -0.038452 | 0.013733 | 0.022888 | 0.018311 | 1.9775 | 1.9638 | -0.009155 | 0.041199 | 122.2137 | 119.9982 | 1.9775
9531.8438 | 0.061035 | 0.2478 | -0.2211 | -0.23712 | -0.095062 | -0.27985 | -0.03952 | 0.068665 | 0.027466 | -0.004578 | 0.045776 | 0.10071 | -0.036621 | 0.10986 | 0.076294 | 0.061951 | -0.23392 | -0.027771 | -0.11429 | -0.021362 | 0.050354 | 0.091553 | 0.11444 | 1.9913 | 2.0004 | -0.054932 | 0.004578 | 122.1085 | 119.9615 | 2.0691
9533.6406 | 0.061035 | 0.21042 | -0.21042 | -0.24033 | -0.088654 | -0.25955 | -0.048065 | 0.054932 | -0.054932 | -0.068665 | 0 | 0.1236 | 0.018311 | 0.13275 | 0.061035 | 0.091858 | -0.22858 | -0.029907 | -0.10788 | -0.032043 | -0.013733 | 0.045776 | 0.032043 | 1.9638 | 1.9409 | -0.018311 | 0.036621 | 122.1451 | 120.0302 | 1.9775
9535.3594 | 0.045776 | 0.23178 | -0.22003 | -0.23285 | -0.093994 | -0.27664 | -0.048065 | 0.12817 | 0.091553 | 0.073242 | 0.091553 | 0.07782 | -0.022888 | 0.11444 | 0.061035 | 0.071564 | -0.2243 | -0.03418 | -0.11215 | -0.035248 | 0.09613 | 0.20599 | 0.16022 | 1.9135 | 1.8997 | -0.064087 | 0 | 122.0947 | 120.0668 | 1.9821
9537.1562 | 0.076294 | 0.22964 | -0.20615 | -0.23285 | -0.10361 | -0.23605 | -0.043793 | 0.073242 | -0.073242 | -0.073242 | 0 | 0.11902 | -0.013733 | 0.11444 | 0.045776 | 0.088654 | -0.21469 | -0.025635 | -0.10468 | -0.040588 | 0.032043 | 0.027466 | 0.032043 | 1.9958 | 1.9775 | -0.041199 | 0.032043 | 122.2412 | 120.0027 | 2.0004
9538.875 | 0.061035 | 0.21255 | -0.19974 | -0.22751 | -0.093994 | -0.24353 | -0.037384 | 0.091553 | -0.018311 | -0.022888 | 0.045776 | 0.11444 | 0.009155 | 0.12817 | 0.045776 | 0.083313 | -0.22003 | -0.024567 | -0.097198 | -0.040588 | 0.036621 | 0.10071 | 0.064087 | 1.8906 | 1.886 | -0.045776 | 0.018311 | 122.2092 | 120.1035 | 1.8951
9540.6562 | 0.045776 | 0.22003 | -0.21042 | -0.23392 | -0.070496 | -0.25635 | -0.042725 | 0.018311 | -0.068665 | -0.045776 | 0.004578 | 0.11902 | 0.018311 | 0.14648 | 0.061035 | 0.080109 | -0.2179 | -0.014954 | -0.11215 | -0.03418 | -0.022888 | 0.073242 | 0.041199 | 2.0691 | 2.0416 | -0.045776 | 0.022888 | 122.2321 | 119.9341 | 2.0782
9542.4375 | 0.061035 | 0.22217 | -0.21896 | -0.24139 | -0.089722 | -0.27451 | -0.040588 | 0.07782 | 0.009155 | 0.009155 | 0.041199 | 0.10529 | -0.004578 | 0.10071 | 0.045776 | 0.072632 | -0.2179 | -0.02243 | -0.11002 | -0.032043 | -0.009155 | 0.11444 | 0.082397 | 2.0828 | 2.0462 | -0.041199 | 0.022888 | 122.0901 | 119.9661 | 2.1149
9544.1562 | 0.061035 | 0.22644 | -0.19333 | -0.23285 | -0.093994 | -0.27985 | -0.03952 | 0.11902 | 0.050354 | 0.059509 | 0.064087 | 0.086975 | -0.045776 | 0.07782 | 0.076294 | 0.065155 | -0.20721 | -0.020294 | -0.12283 | -0.028839 | 0.086975 | 0.15564 | 0.16937 | 1.9958 | 1.9913 | -0.11902 | -0.036621 | 122.0993 | 120.0211 | 2.0828
9545.9375 | 0.030518 | 0.2211 | -0.20508 | -0.2478 | -0.083313 | -0.25101 | -0.043793 | 0.045776 | -0.068665 | -0.036621 | 0.022888 | 0.10529 | -0.009155 | 0.14191 | 0.030518 | 0.089722 | -0.19974 | -0.019226 | -0.10574 | -0.040588 | 0.018311 | 0.10986 | 0.091553 | 2.0187 | 2.0233 | -0.07782 | -0.022888 | 122.2504 | 119.9661 | 2.0508
9547.6719 | 0.061035 | 0.22964 | -0.21149 | -0.21576 | -0.099335 | -0.2478 | -0.03952 | 0.036621 | -0.10071 | -0.10071 | -0.022888 | 0.10986 | 0 | 0.11444 | 0.076294 | 0.09613 | -0.17624 | -0.011749 | -0.09079 | -0.027771 | -0.009155 | 0.050354 | 0.10529 | 2.417 | 2.3666 | -0.10529 | -0.045776 | 122.2504 | 119.6274 | 2.417
9549.4531 | 0.076294 | 0.22644 | -0.21042 | -0.23392 | -0.09613 | -0.24994 | -0.035248 | 0.082397 | -0.004578 | 0.027466 | 0.045776 | 0.1236 | -0.032043 | 0.10986 | 0.061035 | 0.066223 | -0.2211 | -0.023499 | -0.097198 | -0.035248 | 0.004578 | 0.086975 | 0.041199 | 1.5747 | 1.5747 | -0.054932 | 0.018311 | 122.2275 | 120.4742 | 1.5839
9551.2344 | 0.061035 | 0.25528 | -0.20294 | -0.23712 | -0.097198 | -0.28412 | -0.037384 | 0.09613 | 0.07782 | 0.14648 | 0.064087 | 0.086975 | -0.064087 | 0.082397 | 0.045776 | 0.065155 | -0.25101 | -0.024567 | -0.11215 | -0.027771 | 0.09613 | 0.19684 | 0.13275 | 2.0004 | 1.9958 | -0.082397 | 0 | 122.1634 | 120.0302 | 2.1103
9553.0156 | 0.045776 | 0.24887 | -0.21362 | -0.23285 | -0.099335 | -0.26596 | -0.03952 | 0.11902 | 0.086975 | 0.15106 | 0.082397 | 0.073242 | -0.064087 | 0.050354 | 0.076294 | 0.054474 | -0.24887 | -0.021362 | -0.10147 | -0.033112 | 0.10529 | 0.22888 | 0.16022 | 1.9913 | 1.973 | -0.059509 | -0.032043 | 122.2229 | 120.0302 | 2.0782
9554.7188 | 0.045776 | 0.23605 | -0.22003 | -0.24246 | -0.1004 | -0.28091 | -0.061951 | 0.10986 | 0.10529 | 0.14648 | 0.09613 | 0.082397 | -0.059509 | 0.07782 | 0.076294 | 0.041656 | -0.24674 | -0.036316 | -0.11429 | -0.037384 | 0.1236 | 0.31128 | 0.21057 | 2.0554 | 2.0462 | -0.086975 | -0.018311 | 122.1771 | 119.9524 | 2.1286
9556.5 | 0.045776 | 0.24139 | -0.20615 | -0.21255 | -0.091858 | -0.26916 | -0.040588 | 0.13275 | 0.073242 | 0.14191 | 0.073242 | 0.082397 | -0.050354 | 0.073242 | 0.076294 | 0.052338 | -0.26276 | -0.025635 | -0.11215 | -0.048065 | 0.10071 | 0.23346 | 0.14648 | 2.179 | 2.1606 | -0.091553 | -0.018311 | 122.1725 | 119.8608 | 2.2614
9558.2812 | 0.076294 | 0.20294 | -0.19653 | -0.24994 | -0.09079 | -0.22003 | -0.038452 | 0.082397 | -0.068665 | 0.013733 | 0.009155 | 0.11902 | -0.027466 | 0.10986 | 0.061035 | 0.061951 | -0.22751 | -0.012817 | -0.09079 | -0.049133 | 0 | 0.1236 | 0.027466 | 2.0599 | 2.0462 | -0.068665 | -0.013733 | 122.2366 | 119.9982 | 2.0828
9560.0469 | 0.045776 | 0.25101 | -0.21896 | -0.22217 | -0.10788 | -0.29053 | -0.052338 | 0.073242 | 0.032043 | 0.073242 | 0.059509 | 0.10071 | -0.073242 | 0.09613 | 0.076294 | 0.040588 | -0.23285 | -0.013885 | -0.11749 | -0.025635 | 0.045776 | 0.21057 | 0.1236 | 1.9913 | 2.0004 | -0.10071 | -0.022888 | 122.1497 | 120.0531 | 2.0691
9561.7656 | 0.061035 | 0.21683 | -0.21042 | -0.23392 | -0.1004 | -0.24567 | -0.045929 | 0.064087 | -0.064087 | 0.004578 | 0.018311 | 0.12817 | -0.045776 | 0.11444 | 0.076294 | 0.059814 | -0.23178 | -0.013885 | -0.088654 | -0.043793 | -0.013733 | 0.14191 | 0.027466 | 2.0279 | 2.0279 | -0.073242 | -0.004578 | 122.2458 | 120.0394 | 2.0737
9563.5469 | 0.045776 | 0.24139 | -0.21149 | -0.24674 | -0.10361 | -0.28839 | -0.061951 | 0.045776 | 0 | 0.091553 | 0.050354 | 0.086975 | -0.041199 | 0.09613 | 0.045776 | 0.032043 | -0.22751 | -0.037384 | -0.12924 | -0.026703 | 0.045776 | 0.22888 | 0.17395 | 1.8356 | 1.7944 | -0.091553 | -0.027466 | 122.2137 | 120.2637 | 1.8951
9565.3281 | 0.061035 | 0.21362 | -0.1944 | -0.23605 | -0.10361 | -0.23285 | -0.03418 | 0.11444 | 0.004578 | 0.054932 | 0.041199 | 0.12817 | -0.022888 | 0.09613 | 0.061035 | 0.053406 | -0.2243 | -0.006409 | -0.10468 | -0.040588 | 0.045776 | 0.21515 | 0.07782 | 2.0325 | 2.037 | -0.10529 | -0.022888 | 122.2641 | 120.0394 | 2.0782
9567.0469 | 0.045776 | 0.22324 | -0.20401 | -0.24246 | -0.09613 | -0.26703 | -0.049133 | 0.018311 | -0.036621 | -0.004578 | 0.004578 | 0.1236 | -0.013733 | 0.11902 | 0.061035 | 0.057678 | -0.21896 | -0.026703 | -0.11429 | -0.032043 | -0.018311 | 0.19684 | 0.064087 | 1.9958 | 1.9867 | -0.082397 | -0.027466 | 122.2366 | 120.1126 | 2.005
9568.8125 | 0.061035 | 0.22858 | -0.19653 | -0.23605 | -0.091858 | -0.25207 | -0.03952 | 0.054932 | -0.027466 | 0.018311 | 0.022888 | 0.13733 | -0.032043 | 0.13733 | 0.061035 | 0.09079 | -0.25207 | 0.019226 | -0.13245 | -0.052338 | 0.004578 | 0.38452 | 0.054932 | 1.5335 | 1.5198 | -0.31128 | -0.23346 | 122.2641 | 120.5521 | 1.5472
9570.5312 | 0.061035 | 0.22217 | -0.20721 | -0.23926 | -0.098267 | -0.25635 | -0.037384 | 0.045776 | -0.009155 | 0.032043 | 0.050354 | 0.13275 | -0.013733 | 0.10529 | 0.061035 | 0.11002 | -0.28305 | 0.064087 | -0.17303 | -0.054474 | 0.045776 | 0.65918 | 0.12817 | 0.71411 | 0.6958 | -0.51727 | -0.44403 | 122.3282 | 121.376 | 0.737
9572.25 | 0.076294 | 0.20935 | -0.19546 | -0.22537 | -0.089722 | -0.25421 | -0.035248 | 0.068665 | 0.022888 | 0.059509 | 0.045776 | 0.11902 | -0.027466 | 0.10986 | 0.045776 | 0.11536 | -0.29266 | 0.054474 | -0.16449 | -0.055542 | 0.064087 | 0.6958 | 0.15106 | 0.70038 | 0.69122 | -0.54932 | -0.48065 | 122.3282 | 121.3989 | 0.70496
9574.0156 | 0.061035 | 0.23285 | -0.20294 | -0.23392 | -0.097198 | -0.25101 | -0.040588 | 0.050354 | 0.004578 | 0.050354 | 0.050354 | 0.10071 | -0.009155 | 0.09613 | 0.061035 | 0.11108 | -0.28732 | 0.061951 | -0.17624 | -0.061951 | 0.041199 | 0.69122 | 0.14648 | 0.67291 | 0.67291 | -0.56763 | -0.49439 | 122.3373 | 121.3989 | 0.70496
9575.7812 | 0.076294 | 0.21362 | -0.1976 | -0.23926 | -0.10681 | -0.25314 | -0.038452 | 0.032043 | -0.036621 | 0.032043 | 0.027466 | 0.12817 | -0.032043 | 0.11902 | 0.045776 | 0.1239 | -0.28091 | 0.067291 | -0.16449 | -0.041656 | 0.009155 | 0.61798 | 0.073242 | 0.71411 | 0.69122 | -0.52643 | -0.48065 | 122.2916 | 121.431 | 0.72327
9577.5781 | 0.061035 | 0.22964 | -0.1976 | -0.22644 | -0.09079 | -0.25742 | -0.03952 | 0.07782 | 0.059509 | 0.10529 | 0.073242 | 0.091553 | -0.064087 | 0.091553 | 0.061035 | 0.10361 | -0.29907 | 0.058746 | -0.17838 | -0.046997 | 0.086975 | 0.737 | 0.2243 | 0.67749 | 0.6546 | -0.59052 | -0.53558 | 122.3419 | 121.3943 | 0.71869
9579.2969 | 0.045776 | 0.22003 | -0.20508 | -0.25528 | -0.09613 | -0.24567 | -0.036316 | 0.054932 | 0.013733 | 0.050354 | 0.054932 | 0.1236 | -0.036621 | 0.10986 | 0.076294 | 0.12604 | -0.29587 | 0.057678 | -0.16342 | -0.055542 | 0.027466 | 0.67749 | 0.15564 | 0.68665 | 0.6958 | -0.55847 | -0.49896 | 122.3419 | 121.4127 | 0.70953
9581.0625 | 0.045776 | 0.21042 | -0.19867 | -0.24567 | -0.091858 | -0.25207 | -0.042725 | 0.054932 | -0.004578 | 0.045776 | 0.050354 | 0.12817 | -0.027466 | 0.10986 | 0.061035 | 0.12176 | -0.28839 | 0.069427 | -0.16449 | -0.057678 | 0.050354 | 0.67749 | 0.15564 | 0.70038 | 0.68665 | -0.54932 | -0.48981 | 122.3557 | 121.3943 | 0.73242
9582.8438 | 0.045776 | 0.25528 | -0.20828 | -0.22964 | -0.089722 | -0.30655 | -0.055542 | 0.036621 | 0.036621 | 0.086975 | 0.059509 | 0.086975 | -0.050354 | 0.07782 | 0.045776 | 0.10895 | -0.31509 | 0.054474 | -0.18372 | -0.040588 | 0.064087 | 0.67749 | 0.21515 | 0.72784 | 0.737 | -0.53558 | -0.48523 | 122.2733 | 121.3943 | 0.80109
9584.625 | 0.045776 | 0.2446 | -0.20615 | -0.23178 | -0.10574 | -0.26169 | -0.050201 | 0.10986 | 0.013733 | 0.11444 | 0.09613 | 0.09613 | -0.050354 | 0.07782 | 0.076294 | 0.11002 | -0.30014 | 0.052338 | -0.16663 | -0.049133 | 0.10529 | 0.70496 | 0.22888 | 0.737 | 0.73242 | -0.54932 | -0.49896 | 122.3602 | 121.3623 | 0.80109
9586.4062 | 0.061035 | 0.23605 | -0.21469 | -0.24567 | -0.083313 | -0.2713 | -0.054474 | 0.022888 | -0.041199 | 0.013733 | 0.009155 | 0.13275 | -0.004578 | 0.1236 | 0.030518 | 0.12176 | -0.298 | 0.046997 | -0.17517 | -0.059814 | -0.009155 | 0.6134 | 0.1236 | 0.70953 | 0.69122 | -0.53558 | -0.48523 | 122.2733 | 121.4813 | 0.71869
9588.1875 | 0.076294 | 0.23285 | -0.1976 | -0.2243 | -0.081177 | -0.25955 | -0.044861 | 0.10071 | 0.050354 | 0.091553 | 0.064087 | 0.082397 | -0.054932 | 0.073242 | 0.045776 | 0.11322 | -0.30868 | 0.052338 | -0.15808 | -0.05127 | 0.12817 | 0.70953 | 0.23346 | 0.66834 | 0.6546 | -0.57678 | -0.49896 | 122.3648 | 121.4493 | 0.70496
9589.9062 | 0.045776 | 0.24246 | -0.21576 | -0.23498 | -0.10681 | -0.28839 | -0.048065 | 0.041199 | 0.009155 | 0.082397 | 0.054932 | 0.086975 | -0.064087 | 0.086975 | 0.076294 | 0.11002 | -0.29373 | 0.046997 | -0.1741 | -0.060883 | 0.054932 | 0.65002 | 0.18768 | 0.67291 | 0.64545 | -0.54932 | -0.4715 | 122.2778 | 121.4951 | 0.71869
9591.6875 | 0.061035 | 0.23392 | -0.21469 | -0.24139 | -0.09613 | -0.27557 | -0.054474 | 0.12817 | 0.07782 | 0.13275 | 0.064087 | 0.091553 | -0.050354 | 0.068665 | 0.030518 | 0.10468 | -0.29373 | 0.049133 | -0.16983 | -0.050201 | 0.13275 | 0.66376 | 0.21515 | 0.65002 | 0.62256 | -0.5127 | -0.48065 | 122.2412 | 121.5363 | 0.70953
9593.4688 | 0.061035 | 0.2211 | -0.19012 | -0.25421 | -0.083313 | -0.26489 | -0.049133 | 0.041199 | -0.064087 | -0.004578 | 0.018311 | 0.1236 | -0.009155 | 0.1236 | 0.045776 | 0.11963 | -0.28839 | 0.053406 | -0.15915 | -0.065155 | 0.009155 | 0.59509 | 0.082397 | 0.66834 | 0.6546 | -0.48981 | -0.43488 | 122.3648 | 121.5042 | 0.69122
9595.1875 | 0.061035 | 0.22003 | -0.20294 | -0.23178 | -0.1004 | -0.25314 | -0.042725 | 0.032043 | -0.054932 | -0.013733 | 0.018311 | 0.14191 | -0.009155 | 0.10986 | 0.076294 | 0.1239 | -0.28839 | 0.054474 | -0.15381 | -0.05661 | -0.004578 | 0.58136 | 0.091553 | 0.65002 | 0.63171 | -0.49439 | -0.42114 | 122.3465 | 121.5317 | 0.6546
9596.9531 | 0.061035 | 0.23392 | -0.19653 | -0.22751 | -0.097198 | -0.25742 | -0.043793 | 0.054932 | -0.041199 | 0.009155 | 0.013733 | 0.1236 | -0.032043 | 0.10071 | 0.061035 | 0.099335 | -0.29373 | 0.059814 | -0.15701 | -0.042725 | 0.064087 | 0.59967 | 0.14191 | 0.6546 | 0.63171 | -0.53101 | -0.46692 | 122.406 | 121.5225 | 0.66376
9598.7344 | 0.045776 | 0.21896 | -0.21042 | -0.24674 | -0.086517 | -0.25528 | -0.060883 | 0.013733 | -0.045776 | -0.004578 | 0.018311 | 0.13275 | -0.022888 | 0.11444 | 0.045776 | 0.10788 | -0.28198 | 0.050201 | -0.17731 | -0.040588 | 0 | 0.59052 | 0.07782 | 0.68207 | 0.65918 | -0.49896 | -0.44861 | 122.2961 | 121.5408 | 0.6958
9600.5312 | 0.061035 | 0.23392 | -0.21683 | -0.22003 | -0.083313 | -0.27344 | -0.03418 | 0.1236 | 0.054932 | 0.10986 | 0.09613 | 0.07782 | -0.068665 | 0.082397 | 0.061035 | 0.10574 | -0.30228 | 0.058746 | -0.16663 | -0.05127 | 0.12817 | 0.67749 | 0.19684 | 0.59052 | 0.58594 | -0.54016 | -0.47607 | 122.3923 | 121.5134 | 0.6546
9602.2812 | 0.045776 | 0.21469 | -0.19119 | -0.23498 | -0.092926 | -0.25635 | -0.029907 | 0.050354 | -0.054932 | 0.013733 | 0.018311 | 0.1236 | -0.018311 | 0.10071 | 0.061035 | 0.1239 | -0.28839 | 0.049133 | -0.14526 | -0.046997 | -0.018311 | 0.53558 | 0.054932 | 0.65002 | 0.6134 | -0.48981 | -0.41199 | 122.3557 | 121.5775 | 0.62714
9604.0625 | 0.045776 | 0.25742 | -0.21683 | -0.22003 | -0.098267 | -0.27878 | -0.054474 | 0.10071 | 0.10529 | 0.15106 | 0.10071 | 0.082397 | -0.041199 | 0.068665 | 0.045776 | 0.098267 | -0.30441 | 0.038452 | -0.16663 | -0.041656 | 0.10071 | 0.71869 | 0.2243 | 0.61798 | 0.59509 | -0.53101 | -0.46692 | 122.2961 | 121.5866 | 0.68207
9605.8281 | 0.076294 | 0.24033 | -0.22324 | -0.23285 | -0.1004 | -0.28625 | -0.049133 | 0.07782 | 0.036621 | 0.11444 | 0.068665 | 0.10529 | -0.054932 | 0.064087 | 0.061035 | 0.098267 | -0.30334 | 0.042725 | -0.17944 | -0.048065 | 0.10071 | 0.66376 | 0.21515 | 0.6134 | 0.59967 | -0.52185 | -0.46234 | 122.3373 | 121.6049 | 0.66834
9607.6094 | 0.045776 | 0.2243 | -0.20935 | -0.24246 | -0.093994 | -0.25528 | -0.053406 | 0.054932 | -0.050354 | 0.018311 | 0.009155 | 0.13733 | -0.009155 | 0.1236 | 0.061035 | 0.11749 | -0.28946 | 0.045929 | -0.17517 | -0.036316 | 0.004578 | 0.32501 | 0.09613 | 0.65918 | 0.64087 | -0.48981 | -0.42114 | 122.3053 | 121.5775 | 0.68207
9609.3906 | 0.061035 | 0.23819 | -0.20508 | -0.22217 | -0.097198 | -0.24139 | -0.041656 | 0.050354 | -0.064087 | 0.004578 | 0.022888 | 0.11444 | -0.018311 | 0.10986 | 0.061035 | 0.11536 | -0.28198 | 0.043793 | -0.16449 | -0.042725 | 0.082397 | 0.21057 | 0.1236 | 0.67749 | 0.67749 | -0.54016 | -0.48981 | 122.4472 | 121.5042 | 0.6958
9611.1562 | 0.045776 | 0.23819 | -0.20508 | -0.22537 | -0.099335 | -0.26382 | -0.041656 | 0.15564 | 0.064087 | 0.13275 | 0.086975 | 0.073242 | -0.091553 | 0.059509 | 0.076294 | 0.10254 | -0.29266 | 0.032043 | -0.16556 | -0.029907 | 0.12817 | 0.32044 | 0.21515 | 0.63171 | 0.65002 | -0.57678 | -0.49896 | 122.374 | 121.5225 | 0.71869
9612.9375 | 0.061035 | 0.21469 | -0.20508 | -0.25848 | -0.086517 | -0.25742 | -0.037384 | 0.086975 | -0.027466 | 0.045776 | 0.050354 | 0.12817 | -0.018311 | 0.10529 | 0.045776 | 0.11002 | -0.28091 | 0.036316 | -0.16556 | -0.03418 | 0.041199 | 0.2655 | 0.13733 | 0.68207 | 0.66376 | -0.5127 | -0.45319 | 122.4472 | 121.5042 | 0.70038
9614.7188 | 0.061035 | 0.23605 | -0.21896 | -0.25101 | -0.10147 | -0.29159 | -0.041656 | 0.14191 | 0.10529 | 0.16479 | 0.09613 | 0.073242 | -0.045776 | 0.064087 | 0.061035 | 0.09079 | -0.29159 | 0.033112 | -0.18585 | -0.025635 | 0.12817 | 0.32044 | 0.23804 | 0.63629 | 0.64545 | -0.5722 | -0.50354 | 122.3282 | 121.5454 | 0.71869
9616.5 | 0.045776 | 0.22217 | -0.20187 | -0.22003 | -0.10468 | -0.25848 | -0.045929 | 0.082397 | 0.009155 | 0.064087 | 0.059509 | 0.091553 | -0.059509 | 0.073242 | 0.045776 | 0.099335 | -0.28946 | 0.055542 | -0.16235 | -0.042725 | 0.10986 | 0.19684 | 0.20599 | 0.66834 | 0.65918 | -0.58136 | -0.52643 | 122.4472 | 121.5271 | 0.70953
9618.2188 | 0.061035 | 0.23926 | -0.2179 | -0.23392 | -0.11002 | -0.28946 | -0.057678 | 0.054932 | 0.018311 | 0.086975 | 0.054932 | 0.091553 | -0.041199 | 0.07782 | 0.045776 | 0.084381 | -0.29159 | 0.029907 | -0.16556 | -0.029907 | 0.068665 | 0.58594 | 0.17395 | 0.61798 | 0.58594 | -0.49896 | -0.44861 | 122.3328 | 121.6141 | 0.6958
9620 | 0.076294 | 0.22964 | -0.20294 | -0.2243 | -0.092926 | -0.24674 | -0.03952 | 0.11444 | 0.054932 | 0.10071 | 0.068665 | 0.059509 | -0.050354 | 0.086975 | 0.061035 | 0.10147 | -0.27878 | 0.03418 | -0.14313 | -0.027771 | 0.1236 | 0.65002 | 0.1831 | 0.5722 | 0.56763 | -0.49896 | -0.43488 | 122.4564 | 121.6415 | 0.62714
9621.7344 | 0.045776 | 0.22324 | -0.21255 | -0.23285 | -0.1004 | -0.23178 | -0.03418 | 0.032043 | -0.086975 | -0.013733 | 0.013733 | 0.11902 | -0.027466 | 0.11444 | 0.045776 | 0.10895 | -0.27023 | 0.028839 | -0.1506 | -0.032043 | 0.004578 | 0.5127 | 0.050354 | 0.62714 | 0.6134 | -0.46692 | -0.39825 | 122.4106 | 121.6278 | 0.63629
9623.5312 | 0.045776 | 0.2243 | -0.20401 | -0.26276 | -0.074768 | -0.27344 | -0.044861 | 0.09613 | 0.054932 | 0.10986 | 0.064087 | 0.086975 | -0.032043 | 0.09613 | 0.061035 | 0.088654 | -0.2713 | 0.018158 | -0.16663 | -0.026703 | 0.045776 | 0.62256 | 0.13733 | 0.58594 | 0.59967 | -0.4715 | -0.39368 | 122.3053 | 121.6553 | 0.67291
9625.2656 | 0.076294 | 0.22858 | -0.20401 | -0.22858 | -0.1004 | -0.23819 | -0.048065 | 0.086975 | -0.041199 | 0.013733 | 0.032043 | 0.13733 | -0.018311 | 0.10529 | 0.030518 | 0.11002 | -0.27451 | 0.044861 | -0.13886 | -0.037384 | 0.022888 | 0.54016 | 0.073242 | 0.59509 | 0.59967 | -0.46234 | -0.39368 | 122.406 | 121.6278 | 0.61798
9627.0469 | 0.045776 | 0.26276 | -0.10681 | -0.22217 | -0.097198 | -0.28839 | -0.05661 | 0.064087 | 0.032043 | 0.09613 | 0.073242 | 0.10529 | -0.059509 | 0.07782 | 0.030518 | 0.072632 | -0.29587 | 0.018158 | -0.16983 | -0.029907 | 0.086975 | 0.65918 | 0.19226 | 0.58136 | 0.56763 | -0.48981 | -0.42572 | 122.3831 | 121.6553 | 0.65918
9628.7812 | 0.076294 | 0.21896 | -0.1976 | -0.2446 | -0.092926 | -0.2446 | -0.041656 | 0.068665 | -0.054932 | 0.013733 | 0.036621 | 0.12817 | -0.018311 | 0.10529 | 0.076294 | 0.10468 | -0.27771 | 0.016022 | -0.15595 | -0.048065 | 0.041199 | 0.64087 | 0.10529 | 0.63171 | 0.61798 | -0.49896 | -0.42572 | 122.4701 | 121.5729 | 0.64545
9630.5156 | 0.045776 | 0.2179 | -0.1944 | -0.23498 | -0.089722 | -0.24139 | -0.044861 | 0.09613 | 0.013733 | 0.054932 | 0.045776 | 0.11902 | -0.036621 | 0.11444 | 0.045776 | 0.11215 | -0.27344 | 0.042725 | -0.16022 | -0.043793 | 0.064087 | 0.65918 | 0.13275 | 0.62714 | 0.62714 | -0.49896 | -0.4303 | 122.4564 | 121.5958 | 0.64545
9632.2969 | 0.045776 | 0.22644 | -0.20187 | -0.23071 | -0.091858 | -0.25314 | -0.049133 | 0.091553 | 0.009155 | 0.041199 | 0.036621 | 0.11444 | -0.036621 | 0.11902 | 0.061035 | 0.1004 | -0.27451 | 0.03952 | -0.16769 | -0.030975 | 0.041199 | 0.61798 | 0.10071 | 0.63171 | 0.63171 | -0.48065 | -0.42572 | 122.4289 | 121.6049 | 0.67291
9634.0156 | 0.045776 | 0.25528 | -0.22537 | -0.22537 | -0.095062 | -0.28625 | -0.045929 | 0.091553 | 0.064087 | 0.10986 | 0.073242 | 0.082397 | -0.064087 | 0.091553 | 0.061035 | 0.0737 | -0.28305 | 0.038452 | -0.16876 | -0.020294 | 0.082397 | 0.69122 | 0.17395 | 0.64087 | 0.61798 | -0.50812 | -0.45319 | 122.3511 | 121.6232 | 0.71869
9635.7969 | 0.045776 | 0.23819 | -0.20401 | -0.23285 | -0.10147 | -0.26916 | -0.05127 | 0.027466 | -0.041199 | -0.013733 | 0.004578 | 0.13733 | 0.013733 | 0.13275 | 0.045776 | 0.067291 | -0.24246 | -0.023499 | -0.11963 | -0.019226 | -0.013733 | 1.2863 | 0.032043 | 1.355 | 1.3641 | -0.10529 | -0.064087 | 122.3969 | 120.9183 | 1.4008
9637.5938 | 0.045776 | 0.2179 | -0.20721 | -0.23498 | -0.10254 | -0.25421 | -0.049133 | 0.082397 | -0.027466 | 0.054932 | 0.032043 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | 0.069427 | -0.25742 | -0.005341 | -0.10468 | -0.035248 | -0.009155 | 1.2131 | 0.018311 | 1.3046 | 1.2817 | -0.11444 | -0.054932 | 122.438 | 120.9732 | 1.3138
9639.3125 | 0.061035 | 0.22858 | -0.21255 | -0.24139 | -0.097198 | -0.28198 | -0.046997 | 0.10529 | 0.068665 | 0.14648 | 0.09613 | 0.082397 | -0.054932 | 0.073242 | 0.061035 | 0.067291 | -0.25528 | -0.018158 | -0.12817 | -0.036316 | 0.082397 | 1.3458 | 0.16937 | 1.2222 | 1.2222 | -0.14191 | -0.068665 | 122.3511 | 121.019 | 1.3184
9641.0938 | 0.061035 | 0.23712 | -0.20721 | -0.21896 | -0.091858 | -0.26596 | -0.058746 | 0.14648 | 0.068665 | 0.13733 | 0.10529 | 0.07782 | -0.068665 | 0.082397 | 0.076294 | 0.087585 | -0.28946 | -0.024567 | -0.10895 | -0.025635 | 0.16937 | 1.3321 | 0.15564 | 1.2222 | 1.2268 | -0.15564 | -0.091553 | 122.438 | 120.9869 | 1.3
9642.875 | 0.061035 | 0.22217 | -0.20508 | -0.24353 | -0.095062 | -0.26276 | -0.037384 | 0.045776 | -0.059509 | -0.004578 | 0.013733 | 0.11902 | 0.004578 | 0.11444 | 0.061035 | 0.09079 | -0.27557 | -0.020294 | -0.1207 | -0.025635 | 0.045776 | 1.1719 | 0.036621 | 1.2405 | 1.236 | -0.09613 | -0.022888 | 122.4243 | 121.051 | 1.2726
9644.5938 | 0.030518 | 0.23178 | -0.21362 | -0.24246 | -0.10254 | -0.26596 | -0.041656 | 0.13275 | 0.07782 | 0.13275 | 0.086975 | 0.10529 | -0.054932 | 0.054932 | 0.076294 | 0.021362 | -0.21255 | -0.041656 | -0.11536 | -0.032043 | 0.3067 | 0.36163 | 0.24261 | 0.2655 | 0.25177 | -0.13733 | -0.068665 | 122.3877 | 122.0123 | 0.33875
9646.3125 | 0.091553 | 0.23498 | -0.20935 | -0.23712 | -0.099335 | -0.28519 | -0.05127 | 0.082397 | 0.018311 | 0.10529 | 0.059509 | 0.10071 | -0.059509 | 0.068665 | 0.045776 | 0.006409 | -0.21362 | -0.03418 | -0.11536 | -0.029907 | 0.24261 | 0.31128 | 0.21057 | 0.27008 | 0.24719 | -0.15106 | -0.073242 | 122.3877 | 122.0306 | 0.37537
9648.0938 | 0.061035 | 0.25421 | -0.20721 | -0.23178 | -0.099335 | -0.28198 | -0.058746 | 0.11902 | 0.068665 | 0.1236 | 0.082397 | 0.11444 | -0.054932 | 0.059509 | 0.045776 | 0.038452 | -0.23605 | -0.005341 | -0.13351 | -0.036316 | 0.36163 | 0.45776 | 0.24261 | 0.33417 | 0.32959 | -0.25635 | -0.20142 | 122.4243 | 121.9391 | 0.40283
9649.875 | 0.030518 | 0.24033 | -0.21683 | -0.24033 | -0.087585 | -0.26489 | -0.050201 | 0.10986 | 0.013733 | 0.086975 | 0.068665 | 0.09613 | -0.068665 | 0.073242 | 0.061035 | 0.079041 | -0.25848 | 0.012817 | -0.14633 | -0.041656 | 0.42114 | 0.4715 | 0.14191 | 0.43945 | 0.43488 | -0.33417 | -0.27924 | 122.3648 | 121.8521 | 0.53101
9651.6562 | 0.061035 | 0.20828 | -0.19974 | -0.22644 | -0.089722 | -0.24567 | -0.046997 | 0.091553 | -0.050354 | 0 | 0.013733 | 0.13275 | -0.018311 | 0.12817 | 0.061035 | 0.041656 | -0.22217 | -0.019226 | -0.10574 | -0.040588 | 0.21515 | 0.30212 | 0.13275 | 0.32959 | 0.3067 | -0.15106 | -0.086975 | 122.5067 | 121.9757 | 0.31586
9653.3906 | 0.015259 | 0.22217 | -0.21362 | -0.23285 | -0.087585 | -0.24033 | -0.042725 | 0.064087 | -0.064087 | 0.009155 | 0.018311 | 0.14191 | -0.018311 | 0.10986 | 0.045776 | 0.075836 | -0.24994 | -0.002136 | -0.11856 | -0.044861 | 0.38452 | 0.39368 | 0.07782 | 0.47607 | 0.45319 | -0.31586 | -0.2655 | 122.5204 | 121.8063 | 0.4715
9655.1719 | 0.061035 | 0.22003 | -0.1976 | -0.23712 | -0.093994 | -0.26169 | -0.035248 | 0.050354 | -0.036621 | 0.018311 | 0.036621 | 0.11902 | -0.009155 | 0.10071 | 0.030518 | 0.09079 | -0.24139 | 0.005341 | -0.11963 | -0.041656 | 0.41657 | 0.49896 | 0.073242 | 0.52185 | 0.5127 | -0.2243 | -0.16479 | 122.5113 | 121.7651 | 0.52185
9656.9531 | 0.030518 | 0.23392 | -0.19546 | -0.21362 | -0.10361 | -0.2446 | -0.033112 | 0.11902 | 0.004578 | 0.064087 | 0.050354 | 0.11902 | -0.027466 | 0.10986 | 0.076294 | 0.084381 | -0.24887 | 0.019226 | -0.12817 | -0.040588 | 0.39368 | 0.46234 | 0.073242 | 0.47607 | 0.46234 | -0.28381 | -0.21057 | 122.4701 | 121.8475 | 0.50354
9658.7656 | 0.061035 | 0.22964 | -0.21042 | -0.25101 | -0.093994 | -0.28946 | -0.049133 | 0.10986 | 0.064087 | 0.13733 | 0.073242 | 0.09613 | -0.059509 | 0.064087 | 0.091553 | 0.059814 | -0.25528 | 0.007477 | -0.1474 | -0.027771 | 0.43945 | 0.50354 | 0.16022 | 0.42572 | 0.42572 | -0.32044 | -0.24719 | 122.3969 | 121.8567 | 0.51727
9660.4844 | 0.061035 | 0.22217 | -0.20615 | -0.23071 | -0.098267 | -0.24887 | -0.037384 | 0.036621 | -0.086975 | -0.013733 | 0.013733 | 0.14191 | -0.022888 | 0.09613 | 0.045776 | 0.065155 | -0.23498 | -0.026703 | -0.098267 | -0.026703 | 0.49896 | 0.52643 | 0.004578 | 0.64545 | 0.62714 | -0.059509 | 0 | 122.5067 | 121.6782 | 0.65002
9662.25 | 0.061035 | 0.22964 | -0.20721 | -0.23712 | -0.093994 | -0.25207 | -0.028839 | 0.045776 | -0.050354 | 0.009155 | 0.022888 | 0.13275 | -0.013733 | 0.11444 | 0.061035 | 0.054474 | -0.2243 | -0.02243 | -0.095062 | -0.030975 | 0.5127 | 0.53558 | 0.027466 | 0.6134 | 0.60883 | -0.064087 | 0.004578 | 122.5342 | 121.701 | 0.63171
9663.9688 | 0.045776 | 0.24567 | -0.20935 | -0.24139 | -0.098267 | -0.29373 | -0.057678 | 0.064087 | 0.041199 | 0.10986 | 0.07782 | 0.10986 | -0.041199 | 0.073242 | 0.045776 | 0.036316 | -0.23498 | -0.037384 | -0.13672 | -0.023499 | 0.56763 | 0.67749 | 0.16022 | 0.58594 | 0.58594 | -0.082397 | -0.013733 | 122.438 | 121.7422 | 0.63629
9665.7656 | 0.061035 | 0.23392 | -0.20508 | -0.25207 | -0.099335 | -0.28519 | -0.066223 | 0.10529 | 0.059509 | 0.12817 | 0.091553 | 0.09613 | -0.045776 | 0.082397 | 0.061035 | 0.036316 | -0.2446 | -0.021362 | -0.13458 | -0.036316 | 0.6134 | 0.70496 | 0.16937 | 0.59052 | 0.57678 | -0.10071 | -0.041199 | 122.4472 | 121.7194 | 0.6546
9667.5625 | 0.076294 | 0.2243 | -0.21362 | -0.2478 | -0.091858 | -0.2681 | -0.053406 | 0.13733 | 0.07782 | 0.14191 | 0.10529 | 0.10529 | -0.054932 | 0.082397 | 0.076294 | 0.046997 | -0.22751 | -0.024567 | -0.11963 | -0.037384 | 0.56763 | 0.67291 | 0.15564 | 0.55847 | 0.54932 | -0.091553 | -0.022888 | 122.3923 | 121.7468 | 0.64545
9669.3281 | 0.061035 | 0.22537 | -0.20828 | -0.23712 | -0.088654 | -0.26169 | -0.044861 | 0.10529 | 0.036621 | 0.073242 | 0.059509 | 0.11444 | -0.036621 | 0.091553 | 0.045776 | 0.043793 | -0.22217 | -0.019226 | -0.10681 | -0.043793 | 0.48981 | 0.56763 | 0.082397 | 0.58136 | 0.57678 | -0.07782 | 0 | 122.4106 | 121.7468 | 0.64087
9671.0938 | 0.045776 | 0.20508 | -0.19974 | -0.25207 | -0.091858 | -0.24887 | -0.050201 | 0.050354 | -0.045776 | -0.004578 | 0.027466 | 0.12817 | 0 | 0.10529 | 0.045776 | 0.059814 | -0.21149 | -0.018158 | -0.10468 | -0.042725 | 0.46692 | 0.56305 | 0.032043 | 0.58594 | 0.58594 | -0.073242 | 0 | 122.5204 | 121.6965 | 0.61798
9672.8125 | 0.061035 | 0.19974 | -0.21149 | -0.22537 | -0.084381 | -0.24887 | -0.050201 | 0.073242 | -0.009155 | 0.018311 | 0.041199 | 0.1236 | -0.022888 | 0.09613 | 0.061035 | 0.050201 | -0.22217 | -0.02243 | -0.097198 | -0.035248 | 0.48981 | 0.57678 | 0.073242 | 0.59052 | 0.58136 | -0.054932 | 0 | 122.5525 | 121.7331 | 0.59052
9674.5312 | 0.030518 | 0.21683 | -0.20294 | -0.22964 | -0.092926 | -0.24887 | -0.042725 | 0.082397 | 0.009155 | 0.050354 | 0.050354 | 0.11444 | -0.018311 | 0.10529 | 0.061035 | 0.061951 | -0.22858 | -0.030975 | -0.093994 | -0.029907 | 0.54474 | 0.60883 | 0.073242 | 0.5722 | 0.55847 | -0.082397 | 0 | 122.5296 | 121.7331 | 0.59967
9676.2969 | 0.045776 | 0.21576 | -0.20294 | -0.2243 | -0.086517 | -0.24353 | -0.038452 | 0.059509 | -0.036621 | 0.013733 | 0.013733 | 0.091553 | -0.013733 | 0.1236 | 0.045776 | 0.065155 | -0.22324 | -0.020294 | -0.093994 | -0.029907 | 0.46692 | 0.53558 | 0.022888 | 0.59509 | 0.59052 | -0.068665 | 0.018311 | 122.4884 | 121.7422 | 0.61798
9678.0781 | 0.045776 | 0.2211 | -0.20508 | -0.23498 | -0.097198 | -0.26062 | -0.041656 | 0.032043 | -0.041199 | 0.013733 | 0.050354 | 0.13275 | -0.022888 | 0.10529 | 0.076294 | 0.049133 | -0.23285 | -0.023499 | -0.099335 | -0.028839 | 0.48981 | 0.60883 | 0.068665 | 0.59967 | 0.56763 | -0.073242 | 0.004578 | 122.5525 | 121.7239 | 0.6134
9679.8594 | 0.061035 | 0.24033 | -0.20935 | -0.23819 | -0.097198 | -0.27023 | -0.050201 | 0.013733 | -0.027466 | 0.018311 | 0.009155 | 0.13733 | -0.022888 | 0.10071 | 0.061035 | 0.03952 | -0.2179 | -0.032043 | -0.1207 | -0.016022 | 0.45319 | 0.57678 | 0.045776 | 0.61798 | 0.60883 | -0.091553 | -0.009155 | 122.4335 | 121.7606 | 0.64545
9681.6406 | 0.045776 | 0.22537 | -0.2211 | -0.23712 | -0.10361 | -0.28198 | -0.044861 | 0.14191 | 0.12817 | 0.16479 | 0.10986 | 0.09613 | -0.059509 | 0.07782 | 0.045776 | 0.032043 | -0.23392 | -0.033112 | -0.1239 | -0.03418 | 0.56763 | 0.6958 | 0.19226 | 0.55847 | 0.53558 | -0.10986 | -0.022888 | 122.4655 | 121.7651 | 0.62714
9683.375 | 0.061035 | 0.21896 | -0.20401 | -0.23926 | -0.09613 | -0.25528 | -0.05127 | 0.050354 | -0.054932 | 0 | 0.032043 | 0.12817 | -0.022888 | 0.11444 | 0.045776 | 0.053406 | -0.22003 | -0.027771 | -0.10468 | -0.042725 | 0.44861 | 0.55389 | 0.036621 | 0.59052 | 0.56763 | -0.086975 | -0.013733 | 122.5525 | 121.7285 | 0.59967
9685.1406 | 0.076294 | 0.22644 | -0.20508 | -0.23819 | -0.10254 | -0.25635 | -0.052338 | 0.022888 | -0.054932 | 0.009155 | 0.013733 | 0.14191 | -0.013733 | 0.10986 | 0.061035 | 0.046997 | -0.22003 | -0.023499 | -0.10895 | -0.043793 | 0.4303 | 0.55389 | 0.027466 | 0.59509 | 0.58136 | -0.073242 | 0.018311 | 122.5479 | 121.7422 | 0.59967
9686.8594 | 0.061035 | 0.25314 | -0.23071 | -0.23071 | -0.095062 | -0.29159 | -0.053406 | 0.050354 | 0.027466 | 0.086975 | 0.045776 | 0.10529 | -0.041199 | 0.07782 | 0.061035 | 0.028839 | -0.23178 | -0.025635 | -0.1207 | -0.028839 | 0.50354 | 0.58136 | 0.14191 | 0.54932 | 0.53558 | -0.09613 | -0.036621 | 122.4701 | 121.8109 | 0.62256
9688.6406 | 0.061035 | 0.24139 | -0.2179 | -0.22858 | -0.10574 | -0.28305 | -0.057678 | 0.045776 | 0.013733 | 0.086975 | 0.050354 | 0.082397 | -0.059509 | 0.073242 | 0.045776 | 0.029907 | -0.23285 | -0.03952 | -0.11002 | -0.025635 | 0.50812 | 0.57678 | 0.15564 | 0.56305 | 0.52643 | -0.10529 | -0.041199 | 122.4838 | 121.8018 | 0.62256
9690.3594 | 0.061035 | 0.22537 | -0.21255 | -0.25314 | -0.10147 | -0.26916 | -0.05661 | 0.13275 | 0.10986 | 0.14648 | 0.10529 | 0.091553 | -0.059509 | 0.082397 | 0.061035 | 0.036316 | -0.2243 | -0.023499 | -0.12283 | -0.043793 | 0.53558 | 0.64087 | 0.16479 | 0.54932 | 0.52185 | -0.091553 | -0.045776 | 122.4472 | 121.8292 | 0.61798
9692.125 | 0.061035 | 0.27771 | -0.21896 | -0.21683 | -0.098267 | -0.29373 | -0.061951 | 0.10529 | 0.073242 | 0.10986 | 0.082397 | 0.10529 | -0.045776 | 0.07782 | 0.076294 | 0.029907 | -0.24353 | -0.020294 | -0.11215 | -0.03952 | 0.55389 | 0.65918 | 0.1831 | 0.54474 | 0.53101 | -0.1236 | -0.054932 | 122.4976 | 121.8109 | 0.62256
9693.9062 | 0.076294 | 0.22537 | -0.21362 | -0.24139 | -0.085449 | -0.25635 | -0.064087 | 0.14191 | 0.07782 | 0.13733 | 0.10529 | 0.082397 | -0.050354 | 0.07782 | 0.076294 | 0.043793 | -0.22964 | -0.029907 | -0.11429 | -0.05127 | 0.55389 | 0.64545 | 0.15564 | 0.56305 | 0.53558 | -0.11902 | -0.050354 | 122.4655 | 121.8018 | 0.63171
9695.6406 | 0.061035 | 0.22644 | -0.20294 | -0.24567 | -0.085449 | -0.25955 | -0.058746 | 0.073242 | -0.018311 | 0.041199 | 0.022888 | 0.10986 | -0.013733 | 0.10986 | 0.061035 | 0.044861 | -0.21469 | -0.018158 | -0.11536 | -0.046997 | 0.46692 | 0.53558 | 0.045776 | 0.59967 | 0.59052 | -0.086975 | -0.004578 | 122.4472 | 121.8018 | 0.62714
9697.4375 | 0.061035 | 0.24139 | -0.20294 | -0.22964 | -0.10254 | -0.26276 | -0.053406 | 0.086975 | 0.059509 | 0.07782 | 0.059509 | 0.09613 | -0.059509 | 0.068665 | 0.045776 | 0.037384 | -0.21469 | -0.016022 | -0.11856 | -0.037384 | 0.53558 | 0.57678 | 0.1236 | 0.53101 | 0.53558 | -0.11444 | -0.045776 | 122.4609 | 121.8521 | 0.62256
9699.2188 | 0.061035 | 0.2446 | -0.21042 | -0.23071 | -0.099335 | -0.25101 | -0.046997 | 0.16479 | 0.064087 | 0.1236 | 0.086975 | 0.086975 | -0.059509 | 0.068665 | 0.061035 | 0.042725 | -0.23392 | -0.026703 | -0.088654 | -0.045929 | 0.58136 | 0.60425 | 0.16479 | 0.52185 | 0.50812 | -0.12817 | -0.050354 | 122.5754 | 121.7834 | 0.5722
9701.0156 | 0.061035 | 0.23392 | -0.20401 | -0.23178 | -0.099335 | -0.24567 | -0.035248 | 0.14191 | 0.09613 | 0.14191 | 0.09613 | 0.07782 | -0.054932 | 0.064087 | 0.061035 | 0.037384 | -0.22324 | -0.023499 | -0.09613 | -0.035248 | 0.58594 | 0.62714 | 0.17395 | 0.52643 | 0.50812 | -0.10529 | -0.050354 | 122.5296 | 121.8292 | 0.58136
9702.75 | 0.061035 | 0.23712 | -0.20828 | -0.2211 | -0.093994 | -0.26916 | -0.048065 | 0.14191 | 0.09613 | 0.13733 | 0.086975 | 0.07782 | -0.059509 | 0.059509 | 0.076294 | 0.033112 | -0.23392 | -0.021362 | -0.10147 | -0.041656 | 0.56763 | 0.59967 | 0.17395 | 0.53101 | 0.54932 | -0.10071 | -0.050354 | 122.493 | 121.8613 | 0.59052
9704.5312 | 0.061035 | 0.21683 | -0.20935 | -0.24567 | -0.098267 | -0.25848 | -0.042725 | 0.041199 | -0.032043 | 0.027466 | 0.009155 | 0.13733 | -0.036621 | 0.10529 | 0.061035 | 0.058746 | -0.21683 | -0.019226 | -0.10895 | -0.040588 | 0.4303 | 0.5127 | 0.054932 | 0.55847 | 0.54474 | -0.064087 | -0.013733 | 122.4792 | 121.8384 | 0.58136
9706.2969 | 0.061035 | 0.22324 | -0.21683 | -0.24246 | -0.089722 | -0.26489 | -0.048065 | 0.050354 | -0.036621 | 0 | 0.022888 | 0.11902 | -0.013733 | 0.11444 | 0.045776 | 0.042725 | -0.2243 | -0.006409 | -0.10574 | -0.035248 | 0.43488 | 0.50354 | 0.054932 | 0.56305 | 0.54932 | -0.086975 | -0.013733 | 122.5754 | 121.8109 | 0.55389
9708.0625 | 0.061035 | 0.22858 | -0.20935 | -0.25742 | -0.095062 | -0.26489 | -0.050201 | 0.032043 | -0.027466 | 0.027466 | 0.018311 | 0.14191 | -0.022888 | 0.11444 | 0.030518 | 0.035248 | -0.22217 | -0.012817 | -0.11429 | -0.03952 | 0.41657 | 0.49896 | 0.064087 | 0.57678 | 0.53558 | -0.068665 | -0.018311 | 122.4792 | 121.8567 | 0.58136
9709.7812 | 0.076294 | 0.21576 | -0.19546 | -0.24033 | -0.097198 | -0.24994 | -0.035248 | 0.073242 | -0.027466 | 0.018311 | 0.041199 | 0.13275 | -0.022888 | 0.11902 | 0.061035 | 0.05127 | -0.2179 | -0.02243 | -0.11108 | -0.042725 | 0.4715 | 0.54932 | 0.09613 | 0.54932 | 0.54016 | -0.10529 | -0.032043 | 122.612 | 121.8109 | 0.55847
9711.5625 | 0.076294 | 0.25528 | -0.20401 | -0.22964 | -0.099335 | -0.28732 | -0.049133 | 0.073242 | 0.045776 | 0.091553 | 0.054932 | 0.091553 | -0.054932 | 0.07782 | 0.045776 | 0.028839 | -0.23498 | -0.014954 | -0.11963 | -0.028839 | 0.48981 | 0.55389 | 0.13275 | 0.5127 | 0.5127 | -0.12817 | -0.036621 | 122.493 | 121.8887 | 0.58594
9713.3438 | 0.045776 | 0.22644 | -0.21042 | -0.23392 | -0.085449 | -0.26276 | -0.042725 | 0.082397 | 0.036621 | 0.059509 | 0.050354 | 0.12817 | -0.027466 | 0.10986 | 0.045776 | 0.036316 | -0.23605 | -0.027771 | -0.10468 | -0.030975 | 0.44403 | 0.53101 | 0.064087 | 0.53558 | 0.54016 | -0.086975 | -0.022888 | 122.4792 | 121.8704 | 0.58136
9715.125 | 0.076294 | 0.21576 | -0.1976 | -0.22858 | -0.10468 | -0.24994 | -0.038452 | 0.11902 | 0.013733 | 0.059509 | 0.045776 | 0.11902 | -0.032043 | 0.10071 | 0.061035 | 0.060883 | -0.22217 | -0.02243 | -0.095062 | -0.052338 | 0.4715 | 0.53558 | 0.082397 | 0.55389 | 0.52185 | -0.09613 | -0.013733 | 122.5662 | 121.8246 | 0.56305
9716.8594 | 0.076294 | 0.26062 | -0.20615 | -0.23285 | -0.097198 | -0.298 | -0.050201 | 0.064087 | 0.036621 | 0.09613 | 0.054932 | 0.086975 | -0.036621 | 0.086975 | 0.045776 | 0.030975 | -0.23071 | -0.021362 | -0.11536 | -0.026703 | 0.46234 | 0.56305 | 0.12817 | 0.50812 | 0.50812 | -0.10986 | -0.041199 | 122.5021 | 121.8842 | 0.59509
9718.6406 | 0.030518 | 0.2179 | -0.20721 | -0.23498 | -0.081177 | -0.25314 | -0.054474 | 0.045776 | -0.041199 | 0.004578 | 0.004578 | 0.13733 | -0.018311 | 0.11902 | 0.076294 | 0.045929 | -0.22003 | -0.024567 | -0.10147 | -0.046997 | 0.39368 | 0.49896 | 0.059509 | 0.55389 | 0.54474 | -0.091553 | -0.013733 | 122.5845 | 121.8338 | 0.55847
9720.4375 | 0.076294 | 0.23926 | -0.21576 | -0.24353 | -0.09613 | -0.27664 | -0.053406 | 0.1236 | 0.10071 | 0.15106 | 0.091553 | 0.086975 | -0.045776 | 0.073242 | 0.061035 | 0.035248 | -0.23712 | -0.033112 | -0.1239 | -0.03952 | 0.49896 | 0.63629 | 0.1831 | 0.51727 | 0.50354 | -0.1236 | -0.041199 | 122.4838 | 121.9025 | 0.60883
9722.1562 | 0.061035 | 0.20187 | -0.19974 | -0.25314 | -0.099335 | -0.24994 | -0.048065 | 0.054932 | -0.054932 | 0.013733 | 0.013733 | 0.12817 | -0.027466 | 0.11444 | 0.061035 | 0.053406 | -0.21042 | -0.020294 | -0.11002 | -0.028839 | 0.48523 | 0.5127 | 0.082397 | 0.54474 | 0.53558 | -0.09613 | -0.027466 | 122.644 | 121.843 | 0.56763
9723.9375 | 0.045776 | 0.22003 | -0.20935 | -0.24246 | -0.10468 | -0.24567 | -0.037384 | 0.086975 | 0.027466 | 0.050354 | 0.050354 | 0.11444 | -0.036621 | 0.12817 | 0.045776 | 0.053406 | -0.22537 | -0.018158 | -0.10254 | -0.044861 | 0.47607 | 0.55847 | 0.086975 | 0.55389 | 0.51727 | -0.091553 | -0.027466 | 122.6074 | 121.8567 | 0.5722
9725.7031 | 0.061035 | 0.22537 | -0.21149 | -0.22964 | -0.097198 | -0.26062 | -0.045929 | 0.036621 | -0.013733 | 0.032043 | 0.018311 | 0.1236 | -0.041199 | 0.10986 | 0.061035 | 0.038452 | -0.22537 | -0.024567 | -0.10254 | -0.038452 | 0.47607 | 0.5127 | 0.10529 | 0.51727 | 0.51727 | -0.10071 | -0.018311 | 122.6624 | 121.8613 | 0.54932
9727.4844 | 0.045776 | 0.22003 | -0.21149 | -0.24139 | -0.092926 | -0.27023 | -0.048065 | 0.004578 | -0.022888 | 0.009155 | 0.009155 | 0.13733 | -0.009155 | 0.11902 | 0.045776 | 0.052338 | -0.22324 | -0.025635 | -0.1207 | -0.037384 | 0.39368 | 0.50354 | 0.045776 | 0.54932 | 0.53558 | -0.086975 | -0.004578 | 122.5296 | 121.875 | 0.59052
9729.2031 | 0.045776 | 0.23392 | -0.2243 | -0.23926 | -0.1004 | -0.28198 | -0.050201 | 0.073242 | 0.041199 | 0.086975 | 0.073242 | 0.10071 | -0.045776 | 0.064087 | 0.045776 | 0.033112 | -0.23498 | -0.023499 | -0.12497 | -0.020294 | 0.48065 | 0.55847 | 0.16022 | 0.51727 | 0.49439 | -0.10529 | -0.050354 | 122.5479 | 121.8979 | 0.60425
9730.9844 | 0.045776 | 0.23071 | -0.21362 | -0.24674 | -0.088654 | -0.27771 | -0.046997 | 0.082397 | 0.009155 | 0.086975 | 0.059509 | 0.10529 | -0.045776 | 0.068665 | 0.045776 | 0.042725 | -0.23498 | -0.033112 | -0.12711 | -0.03418 | 0.44861 | 0.53101 | 0.15106 | 0.50354 | 0.49439 | -0.12817 | -0.041199 | 122.5296 | 121.9162 | 0.5722
9732.7812 | 0.061035 | 0.22858 | -0.20615 | -0.23178 | -0.093994 | -0.24033 | -0.045929 | 0.11902 | 0.009155 | 0.041199 | 0.059509 | 0.11444 | -0.032043 | 0.1236 | 0.061035 | 0.061951 | -0.2478 | -0.025635 | -0.093994 | -0.041656 | 0.43945 | 0.52643 | 0.086975 | 0.52643 | 0.49439 | -0.10986 | -0.022888 | 122.6212 | 121.8567 | 0.52643
9734.5781 | 0.061035 | 0.22644 | -0.20401 | -0.22537 | -0.099335 | -0.25314 | -0.03952 | 0.059509 | -0.050354 | -0.004578 | 0.018311 | 0.13733 | -0.027466 | 0.1236 | 0.061035 | 0.05127 | -0.24246 | -0.020294 | -0.089722 | -0.037384 | 0.43945 | 0.44403 | 0.073242 | 0.50812 | 0.49896 | -0.11902 | -0.032043 | 122.6669 | 121.8613 | 0.53101
9736.2812 | 0.061035 | 0.24246 | -0.21255 | -0.23819 | -0.10361 | -0.27557 | -0.057678 | 0.11902 | 0.086975 | 0.1236 | 0.09613 | 0.082397 | -0.045776 | 0.064087 | 0.045776 | 0.044861 | -0.24567 | -0.029907 | -0.11002 | -0.033112 | 0.44403 | 0.56305 | 0.12817 | 0.48523 | 0.49896 | -0.10986 | -0.041199 | 122.4747 | 121.9299 | 0.5722
9738.0469 | 0.030518 | 0.24353 | -0.21362 | -0.23498 | -0.084381 | -0.27023 | -0.055542 | 0.12817 | 0.082397 | 0.13733 | 0.10986 | 0.09613 | -0.059509 | 0.082397 | 0.061035 | 0.043793 | -0.2211 | -0.030975 | -0.11536 | -0.048065 | 0.46692 | 0.5722 | 0.16937 | 0.48523 | 0.46692 | -0.10529 | -0.036621 | 122.493 | 121.9574 | 0.56305
9739.8281 | 0.061035 | 0.24246 | -0.20721 | -0.23071 | -0.091858 | -0.26169 | -0.042725 | 0.14648 | 0.068665 | 0.13733 | 0.09613 | 0.073242 | -0.073242 | 0.050354 | 0.045776 | 0.043793 | -0.24246 | -0.033112 | -0.10147 | -0.046997 | 0.50354 | 0.56763 | 0.18768 | 0.4715 | 0.45776 | -0.1236 | -0.059509 | 122.5525 | 121.962 | 0.53101
9741.6094 | 0.061035 | 0.21576 | -0.20828 | -0.2243 | -0.089722 | -0.23605 | -0.046997 | 0.10529 | -0.009155 | 0.027466 | 0.036621 | 0.1236 | -0.022888 | 0.11444 | 0 | 0.061951 | -0.23819 | -0.016022 | -0.083313 | -0.044861 | 0.37994 | 0.42114 | 0.041199 | 0.48981 | 0.49439 | -0.091553 | -0.027466 | 122.5891 | 121.9391 | 0.52643
9743.3906 | 0.076294 | 0.23605 | -0.20615 | -0.24246 | -0.083313 | -0.26916 | -0.054474 | 0.13733 | 0.07782 | 0.14648 | 0.07782 | 0.10071 | -0.050354 | 0.073242 | 0.061035 | 0.030975 | -0.23071 | -0.019226 | -0.11963 | -0.036316 | 0.48981 | 0.54474 | 0.19226 | 0.45776 | 0.43945 | -0.13275 | -0.068665 | 122.5388 | 121.9711 | 0.52643
9745.1719 | 0.045776 | 0.25742 | -0.20935 | -0.2211 | -0.11322 | -0.26596 | -0.041656 | 0.14191 | 0.091553 | 0.12817 | 0.091553 | 0.086975 | -0.068665 | 0.064087 | 0.061035 | 0.033112 | -0.22003 | -0.026703 | -0.10574 | -0.035248 | 0.5127 | 0.55389 | 0.16022 | 0.46234 | 0.45319 | -0.13733 | -0.064087 | 122.5571 | 121.9574 | 0.56763
9746.8906 | 0.045776 | 0.22644 | -0.20721 | -0.22537 | -0.097198 | -0.26169 | -0.054474 | 0.14191 | 0.082397 | 0.11444 | 0.10986 | 0.091553 | -0.073242 | 0.054932 | 0.076294 | 0.038452 | -0.2211 | -0.020294 | -0.1004 | -0.036316 | 0.54474 | 0.19226 | 0.17853 | 0.49439 | 0.48065 | -0.14648 | -0.064087 | 122.6486 | 121.8796 | 0.58136
9748.6719 | 0.061035 | 0.2211 | -0.20081 | -0.24567 | -0.092926 | -0.25101 | -0.045929 | 0.10986 | 0.009155 | 0.064087 | 0.054932 | 0.10529 | -0.050354 | 0.11444 | 0.061035 | 0.049133 | -0.22858 | -0.023499 | -0.098267 | -0.05127 | 0.47607 | 0.15564 | 0.10071 | 0.56305 | 0.5127 | -0.11902 | -0.036621 | 122.6303 | 121.8933 | 0.54474
9750.3906 | 0.061035 | 0.2179 | -0.20401 | -0.23498 | -0.092926 | -0.2446 | -0.038452 | 0.041199 | -0.068665 | 0.009155 | 0.018311 | 0.10071 | -0.027466 | 0.12817 | 0.045776 | 0.050201 | -0.2179 | -0.026703 | -0.092926 | -0.037384 | 0.39368 | 0.068665 | 0.027466 | 0.56305 | 0.56305 | -0.10529 | -0.032043 | 122.5937 | 121.9116 | 0.57678
9752.1562 | 0.015259 | 0.22324 | -0.21149 | -0.25848 | -0.082245 | -0.27985 | -0.046997 | 0.036621 | -0.004578 | 0.050354 | 0.022888 | 0.13275 | -0.032043 | 0.10986 | 0.076294 | 0.027771 | -0.21042 | -0.019226 | -0.12176 | -0.025635 | 0.41657 | 0.12817 | 0.073242 | 0.54932 | 0.51727 | -0.10071 | -0.018311 | 122.5342 | 121.9345 | 0.59052
9753.875 | 0.061035 | 0.22217 | -0.20187 | -0.2211 | -0.09613 | -0.23819 | -0.044861 | 0.054932 | -0.013733 | 0.027466 | 0.032043 | 0.14191 | -0.027466 | 0.10529 | 0.061035 | 0.049133 | -0.21896 | -0.016022 | -0.091858 | -0.041656 | 0.41657 | 0.10529 | 0.032043 | 0.53101 | 0.53558 | -0.10071 | -0.018311 | 122.6074 | 121.9116 | 0.55389
9755.6719 | 0.045776 | 0.2179 | -0.20935 | -0.23285 | -0.1004 | -0.25848 | -0.042725 | 0.036621 | -0.059509 | 0.018311 | 0.009155 | 0.13275 | -0.018311 | 0.11444 | 0.045776 | 0.049133 | -0.21896 | -0.014954 | -0.1004 | -0.029907 | 0.37537 | 0.068665 | 0.022888 | 0.54016 | 0.52643 | -0.091553 | -0.009155 | 122.6166 | 121.9162 | 0.5722
9757.4531 | 0.045776 | 0.21255 | -0.20935 | -0.25528 | -0.10361 | -0.26276 | -0.040588 | 0.018311 | -0.045776 | 0 | 0.036621 | 0.1236 | -0.004578 | 0.10986 | 0.076294 | 0.040588 | -0.20401 | -0.011749 | -0.12497 | -0.03418 | 0.37994 | 0.10529 | 0.054932 | 0.52185 | 0.51727 | -0.091553 | -0.009155 | 122.6212 | 121.9208 | 0.53558
9759.2188 | 0.061035 | 0.2243 | -0.21683 | -0.24033 | -0.084381 | -0.2681 | -0.045929 | 0.018311 | -0.009155 | 0.032043 | 0.027466 | 0.12817 | -0.022888 | 0.10529 | 0.061035 | 0.029907 | -0.21683 | -0.024567 | -0.1207 | -0.044861 | 0.38452 | 0.11444 | 0.082397 | 0.51727 | 0.50812 | -0.091553 | -0.004578 | 122.5433 | 121.9849 | 0.56305
9760.9531 | 0.076294 | 0.22751 | -0.21042 | -0.23605 | -0.10468 | -0.25955 | -0.045929 | 0.068665 | 0.022888 | 0.050354 | 0.054932 | 0.13275 | -0.036621 | 0.09613 | 0.045776 | 0.055542 | -0.23285 | -0.014954 | -0.10574 | -0.049133 | 0.40741 | 0.45319 | 0.09613 | 0.45776 | 0.46692 | -0.073242 | 0 | 122.6669 | 121.9574 | 0.48523
9762.7344 | 0.045776 | 0.21469 | -0.20721 | -0.2179 | -0.10574 | -0.25635 | -0.044861 | 0.086975 | 0.013733 | 0.045776 | 0.050354 | 0.12817 | -0.032043 | 0.09613 | 0.061035 | 0.054474 | -0.23178 | -0.01709 | -0.093994 | -0.028839 | 0.38452 | 0.31128 | 0.054932 | 0.49439 | 0.48065 | -0.073242 | -0.018311 | 122.6166 | 121.9849 | 0.51727
9764.5156 | 0.030518 | 0.24139 | -0.21683 | -0.23498 | -0.10147 | -0.2948 | -0.053406 | 0.045776 | 0.022888 | 0.073242 | 0.059509 | 0.10071 | -0.050354 | 0.073242 | 0.061035 | 0.019226 | -0.23392 | -0.025635 | -0.12176 | -0.03418 | 0.42114 | 0.16479 | 0.15106 | 0.4715 | 0.4715 | -0.10529 | -0.027466 | 122.5754 | 121.9849 | 0.55389
9766.2344 | 0.045776 | 0.25528 | -0.20721 | -0.23178 | -0.1004 | -0.2713 | -0.053406 | 0.14191 | 0.068665 | 0.13733 | 0.082397 | 0.082397 | -0.068665 | 0.054932 | 0.030518 | 0.052338 | -0.23819 | -0.023499 | -0.11322 | -0.036316 | 0.43945 | 0.47607 | 0.15564 | 0.42572 | 0.40741 | -0.10986 | -0.027466 | 122.5525 | 122.0261 | 0.50812
9768 | 0.045776 | 0.23392 | -0.20828 | -0.24674 | -0.082245 | -0.28305 | -0.05661 | 0.13275 | 0.09613 | 0.14648 | 0.09613 | 0.082397 | -0.054932 | 0.068665 | 0.061035 | 0.049133 | -0.24567 | -0.018158 | -0.12497 | -0.042725 | 0.48523 | 0.54474 | 0.19226 | 0.42572 | 0.40741 | -0.10986 | -0.032043 | 122.5845 | 122.0306 | 0.50354
9769.7812 | 0.091553 | 0.22324 | -0.21149 | -0.22003 | -0.11215 | -0.23819 | -0.044861 | 0.054932 | -0.086975 | -0.009155 | 0.013733 | 0.1236 | -0.027466 | 0.091553 | 0.061035 | 0.071564 | -0.24994 | -0.013885 | -0.09079 | -0.038452 | 0.31586 | 0.34332 | 0.013733 | 0.46234 | 0.44403 | -0.073242 | 0.013733 | 122.6486 | 121.9986 | 0.48065
9771.5625 | 0.061035 | 0.23071 | -0.2179 | -0.25314 | -0.10147 | -0.27344 | -0.058746 | 0.12817 | 0.068665 | 0.1236 | 0.086975 | 0.09613 | -0.054932 | 0.064087 | 0.061035 | 0.046997 | -0.24674 | -0.028839 | -0.1239 | -0.050201 | 0.43488 | 0.53101 | 0.18768 | 0.41657 | 0.41199 | -0.091553 | -0.032043 | 122.5937 | 122.0444 | 0.48065
9773.3438 | 0.045776 | 0.21896 | -0.21576 | -0.23605 | -0.098267 | -0.23605 | -0.045929 | 0.1236 | -0.022888 | 0.064087 | 0.059509 | 0.11902 | -0.009155 | 0.11444 | 0.045776 | 0.068359 | -0.2478 | -0.033112 | -0.097198 | -0.054474 | 0.36163 | 0.44403 | 0.068665 | 0.43945 | 0.42114 | -0.073242 | 0.004578 | 122.6761 | 122.0032 | 0.45776
9775.125 | 0.045776 | 0.24567 | -0.21255 | -0.23071 | -0.09613 | -0.27557 | -0.036316 | 0.13733 | 0.073242 | 0.13275 | 0.10071 | 0.073242 | -0.07782 | 0.068665 | 0.045776 | 0.060883 | -0.25635 | -0.035248 | -0.099335 | -0.036316 | 0.43488 | 0.49896 | 0.15564 | 0.37994 | 0.39368 | -0.091553 | -0.032043 | 122.6303 | 122.0444 | 0.46234
9776.8594 | 0.076294 | 0.2179 | -0.20081 | -0.24033 | -0.11856 | -0.2681 | -0.048065 | 0.041199 | -0.036621 | 0.004578 | 0.032043 | 0.13275 | -0.013733 | 0.11444 | 0.076294 | 0.055542 | -0.22217 | -0.02243 | -0.10895 | -0.038452 | 0.29755 | 0.3891 | 0.027466 | 0.4715 | 0.45776 | -0.050354 | 0.009155 | 122.6074 | 122.0306 | 0.48981
9778.6406 | 0.061035 | 0.22644 | -0.21362 | -0.22537 | -0.089722 | -0.26062 | -0.048065 | 0.14191 | 0.07782 | 0.14648 | 0.09613 | 0.086975 | -0.073242 | 0.059509 | 0.045776 | 0.069427 | -0.26596 | -0.024567 | -0.11108 | -0.033112 | 0.42572 | 0.48523 | 0.15106 | 0.3891 | 0.37994 | -0.082397 | -0.013733 | 122.6395 | 122.0581 | 0.4715
9780.375 | 0.045776 | 0.2179 | -0.20828 | -0.22644 | -0.09079 | -0.24994 | -0.03952 | 0.086975 | -0.022888 | 0.036621 | 0.045776 | 0.11902 | -0.022888 | 0.07782 | 0.061035 | 0.075836 | -0.25742 | -0.018158 | -0.097198 | -0.038452 | 0.38452 | 0.44861 | 0.10071 | 0.43945 | 0.41657 | -0.091553 | -0.022888 | 122.6807 | 122.0078 | 0.45319
9782.1562 | 0.061035 | 0.21683 | -0.21042 | -0.22217 | -0.098267 | -0.24139 | -0.035248 | 0.054932 | -0.054932 | 0 | 0.022888 | 0.13733 | -0.022888 | 0.10986 | 0.045776 | 0.079041 | -0.26062 | -0.013885 | -0.095062 | -0.036316 | 0.27924 | 0.35248 | 0.004578 | 0.4303 | 0.43488 | -0.059509 | 0.009155 | 122.6486 | 122.081 | 0.43945
9783.8906 | 0.061035 | 0.22644 | -0.20081 | -0.23819 | -0.10147 | -0.26489 | -0.048065 | 0.041199 | -0.086975 | -0.004578 | 0.004578 | 0.12817 | -0.009155 | 0.10986 | 0.061035 | 0.10574 | -0.27985 | -0.010681 | -0.10681 | -0.048065 | 0.31128 | 0.35706 | 0.027466 | 0.42572 | 0.40741 | -0.059509 | 0.013733 | 122.7081 | 122.0398 | 0.43488
9785.6875 | 0.061035 | 0.24674 | -0.22751 | -0.23392 | -0.10468 | -0.28305 | -0.042725 | 0.07782 | 0.013733 | 0.10071 | 0.054932 | 0.086975 | -0.059509 | 0.068665 | 0.045776 | 0.084381 | -0.28839 | -0.01709 | -0.12283 | -0.032043 | 0.35706 | 0.44403 | 0.10529 | 0.39368 | 0.40283 | -0.07782 | -0.004578 | 122.5754 | 122.0993 | 0.48523
9787.4688 | 0.030518 | 0.21896 | -0.20828 | -0.23926 | -0.088654 | -0.24246 | -0.036316 | 0.059509 | -0.032043 | -0.004578 | 0.018311 | 0.14648 | -0.027466 | 0.11444 | 0.061035 | 0.11749 | -0.27664 | -0.016022 | -0.097198 | -0.050201 | 0.27008 | 0.35706 | 0.004578 | 0.42114 | 0.4303 | -0.050354 | 0.027466 | 122.6624 | 122.0673 | 0.45776
9789.1875 | 0.061035 | 0.24674 | -0.22217 | -0.22537 | -0.10254 | -0.28412 | -0.044861 | 0.09613 | 0.064087 | 0.10529 | 0.059509 | 0.091553 | -0.054932 | 0.073242 | 0.045776 | 0.085449 | -0.29373 | -0.036316 | -0.11002 | -0.035248 | 0.37537 | 0.45776 | 0.11444 | 0.40741 | 0.38452 | -0.082397 | -0.009155 | 122.5571 | 122.0947 | 0.48981
9790.9844 | 0.061035 | 0.24567 | -0.20828 | -0.22537 | -0.097198 | -0.27557 | -0.052338 | 0.15106 | 0.064087 | 0.14191 | 0.09613 | 0.082397 | -0.059509 | 0.050354 | 0.045776 | 0.083313 | -0.28732 | -0.019226 | -0.11108 | -0.040588 | 0.39825 | 0.48981 | 0.15564 | 0.37994 | 0.37994 | -0.07782 | -0.013733 | 122.6532 | 122.0947 | 0.46692
9792.7656 | 0.045776 | 0.22644 | -0.20508 | -0.24139 | -0.097198 | -0.2446 | -0.029907 | 0.091553 | 0.004578 | 0.045776 | 0.054932 | 0.12817 | -0.036621 | 0.10986 | 0.061035 | 0.11322 | -0.28412 | -0.014954 | -0.11002 | -0.043793 | 0.32501 | 0.43945 | 0.059509 | 0.43945 | 0.40741 | -0.041199 | 0.009155 | 122.7173 | 122.0215 | 0.45776
9794.5 | 0.045776 | 0.22644 | -0.19546 | -0.22644 | -0.099335 | -0.25742 | -0.041656 | 0.045776 | -0.064087 | -0.004578 | 0.013733 | 0.14648 | -0.022888 | 0.10529 | 0.076294 | 0.11322 | -0.28305 | -0.012817 | -0.099335 | -0.032043 | 0.28839 | 0.34332 | 0.036621 | 0.42114 | 0.40283 | -0.041199 | 0.018311 | 122.7127 | 122.0581 | 0.43488
9796.2812 | 0.045776 | 0.25742 | -0.22537 | -0.23926 | -0.095062 | -0.29266 | -0.05661 | 0.068665 | 0.050354 | 0.091553 | 0.054932 | 0.10529 | -0.059509 | 0.064087 | 0.061035 | 0.077972 | -0.28839 | -0.026703 | -0.11108 | -0.037384 | 0.32044 | 0.44403 | 0.10071 | 0.39368 | 0.38452 | -0.073242 | -0.013733 | 122.58 | 122.1405 | 0.46234
9798.0469 | 0.076294 | 0.25421 | -0.23285 | -0.23392 | -0.10361 | -0.29053 | -0.063019 | 0.068665 | 0.018311 | 0.073242 | 0.054932 | 0.10071 | -0.036621 | 0.082397 | 0.061035 | 0.083313 | -0.29159 | -0.036316 | -0.11643 | -0.037384 | 0.32501 | 0.42572 | 0.10529 | 0.36621 | 0.36163 | -0.082397 | -0.009155 | 122.6349 | 122.1268 | 0.46234
9799.7656 | 0.091553 | 0.22858 | -0.20828 | -0.24674 | -0.10681 | -0.2446 | -0.045929 | 0.091553 | -0.032043 | 0.041199 | 0.059509 | 0.1236 | -0.018311 | 0.11444 | 0.045776 | 0.11322 | -0.27557 | -0.01709 | -0.11002 | -0.054474 | 0.29755 | 0.39368 | 0.041199 | 0.3891 | 0.37537 | -0.045776 | 0.045776 | 122.7036 | 122.0764 | 0.42114
9801.5625 | 0.076294 | 0.22751 | -0.20294 | -0.24353 | -0.10574 | -0.25635 | -0.044861 | 0.059509 | -0.032043 | 0.027466 | 0.041199 | 0.13733 | -0.032043 | 0.09613 | 0.030518 | 0.098267 | -0.27237 | -0.005341 | -0.10147 | -0.041656 | 0.3067 | 0.37994 | 0.07782 | 0.40283 | 0.35248 | -0.059509 | -0.004578 | 122.7356 | 122.0947 | 0.42114
9803.2656 | 0.061035 | 0.22644 | -0.21896 | -0.23819 | -0.081177 | -0.24994 | -0.041656 | 0.032043 | -0.045776 | -0.009155 | 0.018311 | 0.13733 | -0.032043 | 0.1236 | 0.061035 | 0.10147 | -0.28305 | -0.02243 | -0.10361 | -0.037384 | 0.25635 | 0.3479 | 0.022888 | 0.41199 | 0.3891 | -0.032043 | 0.032043 | 122.699 | 122.0901 | 0.40283
9805.0469 | 0.061035 | 0.21896 | -0.21469 | -0.22751 | -0.09613 | -0.24567 | -0.041656 | 0.022888 | -0.086975 | -0.009155 | 0.009155 | 0.13275 | -0.013733 | 0.11444 | 0.076294 | 0.11322 | -0.2681 | -0.020294 | -0.10788 | -0.029907 | 0.22888 | 0.27466 | 0 | 0.37537 | 0.36621 | -0.068665 | -0.032043 | 122.699 | 122.1268 | 0.3891
9806.7656 | 0.045776 | 0.22858 | -0.21469 | -0.23178 | -0.092926 | -0.26169 | -0.040588 | 0.068665 | 0.022888 | 0.068665 | 0.050354 | 0.10071 | -0.059509 | 0.068665 | 0.061035 | 0.10147 | -0.28732 | -0.028839 | -0.11536 | -0.007477 | 0.27924 | 0.39825 | 0.11902 | 0.33417 | 0.32501 | -0.17395 | -0.11444 | 122.7173 | 122.1176 | 0.36163
9808.5625 | 0.076294 | 0.24353 | -0.2179 | -0.25528 | -0.10681 | -0.29266 | -0.044861 | 0.041199 | 0.022888 | 0.091553 | 0.054932 | 0.091553 | -0.041199 | 0.09613 | 0.061035 | 0.082245 | -0.28305 | -0.046997 | -0.14526 | -0.002136 | 0.20142 | 0.39825 | 0.13275 | 0.3479 | 0.32501 | -0.23804 | -0.1831 | 122.6395 | 122.1588 | 0.41657
9810.2812 | 0.061035 | 0.21576 | -0.21149 | -0.22644 | -0.099335 | -0.24674 | -0.046997 | 0.041199 | -0.086975 | -0.027466 | 0.018311 | 0.1236 | -0.022888 | 0.09613 | 0.030518 | 0.098267 | -0.26382 | -0.038452 | -0.13458 | -0.003204 | 0.027466 | 0.31586 | 0.009155 | 0.42114 | 0.41199 | -0.26093 | -0.20599 | 122.7081 | 122.0947 | 0.4303
9812.0469 | 0.061035 | 0.25207 | -0.21042 | -0.2211 | -0.093994 | -0.28305 | -0.053406 | 0.1236 | 0.068665 | 0.1236 | 0.059509 | 0.091553 | -0.054932 | 0.064087 | 0.045776 | 0.085449 | -0.28946 | -0.040588 | -0.13886 | 0.01709 | 0.1236 | 0.43945 | 0.14191 | 0.3891 | 0.38452 | -0.29755 | -0.23804 | 122.6028 | 122.1405 | 0.45776
9813.8281 | 0.076294 | 0.22751 | -0.20401 | -0.25742 | -0.09613 | -0.27771 | -0.053406 | 0.12817 | 0.082397 | 0.14648 | 0.09613 | 0.091553 | -0.059509 | 0.091553 | 0.045776 | 0.089722 | -0.27451 | -0.041656 | -0.15701 | 0.001068 | 0.11902 | 0.49896 | 0.16022 | 0.36163 | 0.35706 | -0.29297 | -0.23804 | 122.6028 | 122.1313 | 0.45776
9815.6094 | 0.061035 | 0.20401 | -0.20081 | -0.26276 | -0.095062 | -0.24994 | -0.053406 | 0.045776 | -0.054932 | 0.013733 | 0.022888 | 0.13733 | -0.004578 | 0.11902 | 0.076294 | 0.098267 | -0.2681 | -0.020294 | -0.13672 | -0.005341 | 0.036621 | 0.37079 | 0.027466 | 0.43488 | 0.39368 | -0.27008 | -0.20142 | 122.7264 | 122.0993 | 0.42114
9817.3906 | 0.061035 | 0.24246 | -0.21255 | -0.23392 | -0.09079 | -0.28412 | -0.044861 | 0.091553 | 0.068665 | 0.10986 | 0.050354 | 0.091553 | -0.050354 | 0.068665 | 0.045776 | 0.074768 | -0.27451 | -0.044861 | -0.14847 | 0.013885 | 0.11444 | 0.41657 | 0.11444 | 0.35706 | 0.36621 | -0.27924 | -0.21057 | 122.6074 | 122.1497 | 0.45776
9819.0938 | 0.061035 | 0.21042 | -0.20615 | -0.24994 | -0.098267 | -0.25314 | -0.043793 | 0.041199 | -0.041199 | 0 | 0.036621 | 0.12817 | -0.018311 | 0.11444 | 0.061035 | 0.093994 | -0.27237 | -0.027771 | -0.13351 | -0.018158 | 0.036621 | 0.37537 | 0.045776 | 0.41199 | 0.40283 | -0.24719 | -0.1831 | 122.7219 | 122.0901 | 0.41199
9820.875 | 0.061035 | 0.21255 | -0.20081 | -0.24139 | -0.099335 | -0.24674 | -0.043793 | 0.054932 | -0.013733 | 0.036621 | 0.041199 | 0.11902 | -0.018311 | 0.11444 | 0.045776 | 0.1004 | -0.25848 | -0.026703 | -0.12924 | -0.002136 | 0.050354 | 0.40283 | 0.059509 | 0.40741 | 0.3891 | -0.23346 | -0.1831 | 122.7356 | 122.0947 | 0.44403
9822.6719 | 0.061035 | 0.21683 | -0.1976 | -0.23285 | -0.10147 | -0.26062 | -0.046997 | 0.082397 | 0.022888 | 0.050354 | 0.050354 | 0.13733 | -0.032043 | 0.086975 | 0.061035 | 0.1004 | -0.27664 | -0.033112 | -0.12176 | -0.009613 | 0.073242 | 0.39368 | 0.041199 | 0.3891 | 0.3891 | -0.24261 | -0.19226 | 122.6807 | 122.1176 | 0.42572
9824.3906 | 0.045776 | 0.21683 | -0.21255 | -0.23712 | -0.10468 | -0.26169 | -0.05127 | 0.022888 | -0.022888 | 0.018311 | 0.032043 | 0.13275 | -0.009155 | 0.10986 | 0.045776 | 0.089722 | -0.2713 | -0.035248 | -0.12604 | 0.001068 | 0.041199 | 0.3891 | 0.064087 | 0.42114 | 0.3891 | -0.23346 | -0.17395 | 122.7402 | 122.0947 | 0.40741
9826.1719 | 0.045776 | 0.2179 | -0.20721 | -0.22751 | -0.09613 | -0.24674 | -0.041656 | 0.073242 | 0.027466 | 0.050354 | 0.054932 | 0.12817 | -0.027466 | 0.10529 | 0.061035 | 0.098267 | -0.26596 | -0.026703 | -0.13245 | 0 | 0.082397 | 0.39825 | 0.068665 | 0.37994 | 0.37079 | -0.22888 | -0.1831 | 122.699 | 122.1222 | 0.40283
9827.9688 | 0.061035 | 0.24246 | -0.21255 | -0.22537 | -0.097198 | -0.27023 | -0.041656 | 0.11902 | 0.073242 | 0.11902 | 0.11444 | 0.07782 | -0.068665 | 0.045776 | 0.030518 | 0.088654 | -0.28839 | -0.035248 | -0.13886 | 0.010681 | 0.14191 | 0.46692 | 0.14648 | 0.35706 | 0.33875 | -0.27924 | -0.21057 | 122.7219 | 122.113 | 0.41657
9829.6875 | 0.076294 | 0.2478 | -0.21469 | -0.21896 | -0.083313 | -0.26382 | -0.05661 | 0.050354 | 0 | 0.07782 | 0.050354 | 0.11444 | -0.041199 | 0.091553 | 0.061035 | 0.098267 | -0.27664 | -0.040588 | -0.13031 | 0.003204 | 0.11444 | 0.42114 | 0.10529 | 0.35706 | 0.35248 | -0.25635 | -0.20142 | 122.7402 | 122.113 | 0.41657
9831.4688 | 0.045776 | 0.22644 | -0.2179 | -0.24246 | -0.10468 | -0.26703 | -0.05661 | 0.018311 | -0.045776 | 0.009155 | 0.009155 | 0.12817 | -0.018311 | 0.11902 | 0.061035 | 0.09613 | -0.27557 | -0.036316 | -0.13672 | 0.004272 | 0 | 0.34332 | 0.018311 | 0.40741 | 0.40283 | -0.21515 | -0.15106 | 122.6395 | 122.1588 | 0.4303
9833.25 | 0.061035 | 0.23285 | -0.21149 | -0.26276 | -0.10895 | -0.28091 | -0.057678 | 0.11444 | 0.10529 | 0.16022 | 0.10529 | 0.091553 | -0.041199 | 0.07782 | 0.061035 | 0.083313 | -0.27344 | -0.042725 | -0.16022 | 0.009613 | 0.11902 | 0.48981 | 0.16937 | 0.33875 | 0.32959 | -0.27466 | -0.21973 | 122.6212 | 122.168 | 0.43945
9834.9844 | 0.076294 | 0.22644 | -0.20828 | -0.2478 | -0.095062 | -0.27023 | -0.063019 | 0.086975 | 0.068665 | 0.11444 | 0.086975 | 0.086975 | -0.032043 | 0.073242 | 0.061035 | 0.085449 | -0.27023 | -0.036316 | -0.15167 | -0.001068 | 0.050354 | 0.39825 | 0.07782 | 0.36621 | 0.36621 | -0.22888 | -0.19684 | 122.5891 | 122.1725 | 0.42572
9836.7812 | 0.061035 | 0.2211 | -0.20508 | -0.23178 | -0.099335 | -0.2446 | -0.05127 | 0.09613 | -0.009155 | 0.022888 | 0.054932 | 0.13733 | -0.032043 | 0.12817 | 0.061035 | 0.10254 | -0.28412 | -0.033112 | -0.13138 | -0.01709 | 0.054932 | 0.38452 | 0.059509 | 0.37994 | 0.35706 | -0.24261 | -0.17853 | 122.7448 | 122.1771 | 0.37537
9838.5 | 0.045776 | 0.2179 | -0.20401 | -0.23071 | -0.10147 | -0.25207 | -0.046997 | 0.041199 | -0.07782 | -0.004578 | 0.013733 | 0.12817 | -0.027466 | 0.10986 | 0.061035 | 0.099335 | -0.2681 | -0.048065 | -0.12711 | 0.011749 | -0.027466 | 0.27924 | -0.004578 | 0.37079 | 0.37079 | -0.24261 | -0.16479 | 122.7127 | 122.1588 | 0.37994
9840.2812 | 0.061035 | 0.20401 | -0.20508 | -0.24567 | -0.09079 | -0.24994 | -0.045929 | 0.073242 | 0.004578 | 0.027466 | 0.054932 | 0.14648 | -0.027466 | 0.13275 | 0.061035 | 0.09079 | -0.26276 | -0.032043 | -0.13458 | -0.005341 | 0.054932 | 0.37994 | 0.064087 | 0.38452 | 0.36163 | -0.21973 | -0.17853 | 122.7448 | 122.1497 | 0.38452
9842.0781 | 0.061035 | 0.2446 | -0.22217 | -0.22964 | -0.10468 | -0.28412 | -0.05127 | 0.050354 | 0.041199 | 0.082397 | 0.054932 | 0.09613 | -0.050354 | 0.073242 | 0.045776 | 0.074768 | -0.27985 | -0.040588 | -0.15167 | 0.003204 | 0.059509 | 0.38452 | 0.10529 | 0.35706 | 0.34332 | -0.2655 | -0.1831 | 122.6212 | 122.2046 | 0.43488
9843.875 | 0.061035 | 0.24246 | -0.21576 | -0.25207 | -0.10468 | -0.28839 | -0.060883 | 0.09613 | 0.064087 | 0.1236 | 0.09613 | 0.091553 | -0.059509 | 0.073242 | 0.061035 | 0.0737 | -0.27878 | -0.050201 | -0.14526 | -0.004272 | 0.12817 | 0.46692 | 0.17395 | 0.33875 | 0.33417 | -0.24261 | -0.19684 | 122.6761 | 122.1909 | 0.4303
9845.6562 | 0.076294 | 0.23392 | -0.21683 | -0.23712 | -0.10254 | -0.27237 | -0.057678 | 0.07782 | 0.032043 | 0.082397 | 0.064087 | 0.10986 | -0.050354 | 0.068665 | 0.061035 | 0.075836 | -0.28519 | -0.03952 | -0.13672 | -0.006409 | 0.10529 | 0.4303 | 0.13275 | 0.37079 | 0.36163 | -0.23804 | -0.16937 | 122.6807 | 122.1817 | 0.4303
9847.375 | 0.045776 | 0.2211 | -0.20721 | -0.22644 | -0.085449 | -0.25101 | -0.065155 | 0.054932 | -0.050354 | 0 | 0.013733 | 0.13733 | 0.004578 | 0.13275 | 0.045776 | 0.10361 | -0.27985 | -0.043793 | -0.14099 | -0.011749 | 0.004578 | 0.32959 | 0.018311 | 0.41199 | 0.37537 | -0.19684 | -0.1236 | 122.6898 | 122.168 | 0.41199
9849.1406 | 0.076294 | 0.23926 | -0.21576 | -0.24994 | -0.10147 | -0.27023 | -0.054474 | 0.1236 | 0.086975 | 0.14191 | 0.086975 | 0.086975 | -0.050354 | 0.064087 | 0.076294 | 0.082245 | -0.25955 | -0.03952 | -0.14313 | -0.014954 | 0.10529 | 0.45776 | 0.12817 | 0.33875 | 0.3479 | -0.24719 | -0.16937 | 122.6303 | 122.1634 | 0.45319
9850.875 | 0.030518 | 0.21896 | -0.19867 | -0.22751 | -0.09079 | -0.22324 | -0.040588 | 0.073242 | -0.054932 | 0 | 0.032043 | 0.13275 | -0.032043 | 0.11444 | 0.076294 | 0.10361 | -0.2681 | -0.027771 | -0.11643 | -0.008545 | 0.018311 | 0.3067 | -0.009155 | 0.37994 | 0.37537 | -0.20599 | -0.12817 | 122.7219 | 122.1588 | 0.40283
9852.6719 | 0.076294 | 0.23605 | -0.21255 | -0.22858 | -0.095062 | -0.25955 | -0.036316 | 0.10986 | 0.018311 | 0.086975 | 0.073242 | 0.091553 | -0.041199 | 0.082397 | 0.076294 | 0.071564 | -0.2478 | -0.025635 | -0.09613 | -0.03952 | 0.11902 | 0.61798 | 0.10071 | 0.54932 | 0.54016 | -0.073242 | 0 | 122.7585 | 121.9299 | 0.59052
9854.4375 | 0.045776 | 0.24887 | -0.21576 | -0.23926 | -0.097198 | -0.29053 | -0.060883 | 0.050354 | 0.009155 | 0.086975 | 0.054932 | 0.082397 | -0.041199 | 0.09613 | 0.045776 | 0.048065 | -0.26382 | -0.029907 | -0.11429 | -0.027771 | 0.073242 | 0.56763 | 0.10529 | 0.53558 | 0.53101 | -0.059509 | 0.027466 | 122.6669 | 122.0032 | 0.6134
9856.1406 | 0.045776 | 0.22537 | -0.21896 | -0.24887 | -0.10788 | -0.27557 | -0.05661 | 0.12817 | 0.091553 | 0.13275 | 0.10071 | 0.10529 | -0.064087 | 0.073242 | 0.045776 | 0.060883 | -0.24994 | -0.02243 | -0.11322 | -0.040588 | 0.12817 | 0.65002 | 0.12817 | 0.51727 | 0.52643 | -0.068665 | 0.009155 | 122.6212 | 122.0123 | 0.61798
9857.9375 | 0.045776 | 0.25101 | -0.21362 | -0.21255 | -0.089722 | -0.26489 | -0.052338 | 0.13275 | 0.073242 | 0.13275 | 0.086975 | 0.09613 | -0.059509 | 0.07782 | 0.045776 | 0.058746 | -0.25742 | -0.030975 | -0.10254 | -0.046997 | 0.14191 | 0.6134 | 0.13733 | 0.53101 | 0.5127 | -0.064087 | 0.009155 | 122.6532 | 122.0261 | 0.60425
9859.7188 | 0.061035 | 0.24353 | -0.20721 | -0.22858 | -0.10468 | -0.27985 | -0.049133 | 0.073242 | 0.018311 | 0.07782 | 0.054932 | 0.11902 | -0.050354 | 0.091553 | 0.045776 | 0.058746 | -0.25635 | -0.033112 | -0.11429 | -0.040588 | 0.091553 | 0.56305 | 0.091553 | 0.54016 | 0.51727 | -0.064087 | 0.022888 | 122.6715 | 122.0444 | 0.60425
9861.5156 | 0.061035 | 0.23712 | -0.21042 | -0.25207 | -0.09613 | -0.27344 | -0.055542 | 0.091553 | 0.036621 | 0.091553 | 0.050354 | 0.10071 | -0.059509 | 0.091553 | 0.045776 | 0.053406 | -0.23605 | -0.021362 | -0.11643 | -0.037384 | 0.091553 | 0.57678 | 0.09613 | 0.54474 | 0.51727 | -0.059509 | 0.022888 | 122.6395 | 122.0352 | 0.62256
9863.2344 | 0.061035 | 0.23392 | -0.20828 | -0.25955 | -0.09079 | -0.27664 | -0.052338 | 0.14648 | 0.10529 | 0.15564 | 0.086975 | 0.086975 | -0.050354 | 0.091553 | 0.076294 | 0.054474 | -0.2446 | -0.026703 | -0.11322 | -0.050201 | 0.1236 | 0.65002 | 0.1236 | 0.53558 | 0.54474 | -0.068665 | -0.009155 | 122.6303 | 122.0169 | 0.60883
9865.0156 | 0.076294 | 0.20615 | -0.19653 | -0.22751 | -0.075836 | -0.23392 | -0.040588 | 0.09613 | 0.018311 | 0.050354 | 0.050354 | 0.11444 | -0.022888 | 0.10986 | 0.045776 | 0.070496 | -0.24994 | -0.016022 | -0.092926 | -0.052338 | 0.082397 | 0.56763 | 0.041199 | 0.55389 | 0.54016 | -0.054932 | 0.054932 | 122.7768 | 121.9849 | 0.59052
9866.7969 | 0.061035 | 0.2179 | -0.21255 | -0.25955 | -0.095062 | -0.24033 | -0.052338 | 0.045776 | -0.036621 | 0.004578 | 0.013733 | 0.14648 | 0 | 0.13275 | 0.045776 | 0.079041 | -0.23819 | -0.016022 | -0.10574 | -0.03952 | 0.022888 | 0.50354 | 0 | 0.56305 | 0.53101 | -0.009155 | 0.032043 | 122.7539 | 122.0123 | 0.58594
9868.5156 | 0.045776 | 0.21576 | -0.20508 | -0.24674 | -0.079041 | -0.27344 | -0.046997 | 0.10071 | 0.091553 | 0.13275 | 0.091553 | 0.086975 | -0.041199 | 0.07782 | 0.061035 | 0.065155 | -0.24887 | -0.026703 | -0.11749 | -0.044861 | 0.068665 | 0.60883 | 0.091553 | 0.54474 | 0.53101 | -0.050354 | 0.004578 | 122.6212 | 122.0398 | 0.59509
9870.2812 | 0.061035 | 0.19226 | -0.19333 | -0.23926 | -0.097198 | -0.23071 | -0.037384 | 0.041199 | -0.027466 | 0.004578 | 0.032043 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | 0.0737 | -0.23392 | -0.004272 | -0.089722 | -0.05661 | 0.022888 | 0.48523 | -0.004578 | 0.55389 | 0.52185 | -0.036621 | 0.054932 | 122.7264 | 122.0032 | 0.56305
9872.0781 | 0.076294 | 0.26489 | -0.23178 | -0.2243 | -0.087585 | -0.28198 | -0.05127 | 0.10529 | 0.14191 | 0.15564 | 0.09613 | 0.091553 | -0.050354 | 0.09613 | 0.061035 | 0.052338 | -0.27451 | -0.032043 | -0.11002 | -0.026703 | 0.12817 | 0.64545 | 0.16479 | 0.51727 | 0.49896 | -0.050354 | 0.004578 | 122.6852 | 122.0444 | 0.58594
9873.8594 | 0.061035 | 0.23392 | -0.21896 | -0.25421 | -0.10254 | -0.27237 | -0.049133 | 0.10986 | 0.10529 | 0.13275 | 0.11444 | 0.10529 | -0.054932 | 0.082397 | 0.030518 | 0.058746 | -0.24033 | -0.025635 | -0.11322 | -0.042725 | 0.10071 | 0.64087 | 0.12817 | 0.50812 | 0.50812 | -0.059509 | 0.004578 | 122.6257 | 122.0215 | 0.62256
9875.5938 | 0.061035 | 0.21683 | -0.20187 | -0.24674 | -0.088654 | -0.26703 | -0.050201 | 0.041199 | 0.013733 | 0.045776 | 0.045776 | 0.11902 | -0.013733 | 0.13275 | 0.045776 | 0.074768 | -0.24674 | -0.019226 | -0.11536 | -0.052338 | 0.018311 | 0.52185 | 0.018311 | 0.56305 | 0.55389 | -0.032043 | 0.032043 | 122.6486 | 122.0306 | 0.61798
9877.375 | 0.015259 | 0.25955 | -0.19867 | -0.23071 | -0.097198 | -0.27771 | -0.055542 | 0.086975 | 0.082397 | 0.082397 | 0.054932 | 0.09613 | -0.054932 | 0.07782 | 0.061035 | 0.070496 | -0.26169 | -0.013885 | -0.10681 | -0.043793 | 0.11444 | 0.54474 | 0.10986 | 0.53101 | 0.50812 | -0.064087 | 0.009155 | 122.6532 | 122.0581 | 0.6134
9879.1406 | 0.061035 | 0.24674 | -0.2179 | -0.24353 | -0.10147 | -0.2713 | -0.054474 | 0.068665 | 0.027466 | 0.082397 | 0.064087 | 0.11444 | -0.050354 | 0.068665 | 0.061035 | 0.03952 | -0.23392 | -0.033112 | -0.10895 | -0.044861 | 0.19684 | 0.3479 | 0.10071 | 0.34332 | 0.32044 | -0.045776 | 0.032043 | 122.6578 | 122.2504 | 0.40741
9880.9375 | 0.076294 | 0.21576 | -0.21683 | -0.24353 | -0.10468 | -0.26916 | -0.061951 | 0.091553 | 0.045776 | 0.09613 | 0.059509 | 0.10071 | -0.054932 | 0.082397 | 0.061035 | 0.05127 | -0.2211 | -0.027771 | -0.10468 | -0.046997 | 0.21515 | 0.32959 | 0.09613 | 0.32501 | 0.31586 | -0.027466 | 0.041199 | 122.6578 | 122.2595 | 0.41657
9882.75 | 0.076294 | 0.22217 | -0.20187 | -0.22644 | -0.10147 | -0.25314 | -0.053406 | 0.10071 | -0.027466 | 0.045776 | 0.045776 | 0.13275 | -0.036621 | 0.10071 | 0.076294 | 0.050201 | -0.23926 | -0.019226 | -0.09613 | -0.044861 | 0.2655 | 0.16937 | 0.09613 | 0.33417 | 0.32501 | -0.036621 | 0.022888 | 122.7997 | 122.2 | 0.36621
9884.4688 | 0.061035 | 0.21149 | -0.21896 | -0.24033 | -0.10574 | -0.24887 | -0.046997 | 0.064087 | -0.036621 | -0.004578 | 0.027466 | 0.12817 | 0 | 0.1236 | 0.076294 | 0.063019 | -0.24139 | -0.021362 | -0.10254 | -0.052338 | 0.10071 | 0.32501 | 0.004578 | 0.45319 | 0.44403 | -0.018311 | 0.054932 | 122.7722 | 122.1176 | 0.46692
9886.2344 | 0.045776 | 0.23071 | -0.23071 | -0.2446 | -0.086517 | -0.27237 | -0.044861 | 0.15564 | 0.13733 | 0.14191 | 0.10986 | 0.086975 | -0.068665 | 0.086975 | 0.061035 | 0.024567 | -0.21469 | -0.032043 | -0.10574 | -0.041656 | 0.28381 | 0.24719 | 0.15564 | 0.30212 | 0.27924 | -0.050354 | 0.036621 | 122.6852 | 122.2733 | 0.39825
9888.0469 | 0.045776 | 0.2243 | -0.19974 | -0.22858 | -0.10574 | -0.23819 | -0.046997 | 0.12817 | 0.004578 | 0.041199 | 0.045776 | 0.11444 | -0.013733 | 0.091553 | 0.061035 | 0.075836 | -0.24139 | -0.008545 | -0.10147 | -0.05661 | 0.091553 | 0.19684 | 0.050354 | 0.60425 | 0.58136 | -0.050354 | 0.027466 | 122.7631 | 121.994 | 0.55389
9889.7656 | 0.061035 | 0.25528 | -0.21469 | -0.24139 | -0.10147 | -0.28519 | -0.061951 | 0.091553 | 0.059509 | 0.11444 | 0.082397 | 0.09613 | -0.045776 | 0.082397 | 0.045776 | 0.019226 | -0.2243 | -0.027771 | -0.12176 | -0.03952 | 0.25177 | 0.22888 | 0.14191 | 0.31128 | 0.31128 | -0.054932 | 0.036621 | 122.7219 | 122.2595 | 0.40283
9891.5469 | 0.045776 | 0.22644 | -0.19867 | -0.22644 | -0.095062 | -0.23819 | -0.03418 | 0.041199 | -0.073242 | -0.018311 | 0.018311 | 0.1236 | -0.018311 | 0.11902 | 0.061035 | 0.053406 | -0.21683 | -0.025635 | -0.092926 | -0.050201 | 0.11902 | 0.050354 | -0.036621 | 0.36163 | 0.35248 | -0.022888 | 0.068665 | 122.7448 | 122.2366 | 0.36621
9893.3438 | 0.061035 | 0.25742 | -0.22537 | -0.24353 | -0.11856 | -0.29053 | -0.052338 | 0.10986 | 0.054932 | 0.10071 | 0.054932 | 0.091553 | -0.059509 | 0.07782 | 0.061035 | 0.02243 | -0.22964 | -0.01709 | -0.10895 | -0.026703 | 0.22888 | 0.16022 | 0.091553 | 0.3067 | 0.31128 | -0.036621 | 0.045776 | 122.6578 | 122.2824 | 0.39825
9895.0469 | 0.061035 | 0.24674 | -0.22537 | -0.2446 | -0.10361 | -0.28198 | -0.055542 | 0.091553 | 0.07782 | 0.1236 | 0.07782 | 0.091553 | -0.050354 | 0.09613 | 0.045776 | 0.03952 | -0.24353 | -0.018158 | -0.11963 | -0.050201 | 0.19684 | 0.2655 | 0.13733 | 0.45319 | 0.43945 | -0.059509 | 0.004578 | 122.7127 | 122.1451 | 0.50812
9896.8281 | 0.061035 | 0.22217 | -0.21683 | -0.22644 | -0.088654 | -0.23819 | -0.044861 | 0.10986 | 0.022888 | 0.050354 | 0.054932 | 0.11444 | -0.027466 | 0.11444 | 0.061035 | 0.087585 | -0.24674 | -0.021362 | -0.087585 | -0.05127 | 0.064087 | 0.18768 | 0.013733 | 0.61798 | 0.59509 | -0.050354 | 0.018311 | 122.7676 | 121.9437 | 0.63171
9898.5625 | 0.061035 | 0.23285 | -0.2179 | -0.24994 | -0.10147 | -0.28625 | -0.052338 | 0.12817 | 0.086975 | 0.13733 | 0.10071 | 0.086975 | -0.054932 | 0.086975 | 0.045776 | 0.05127 | -0.25635 | -0.025635 | -0.11108 | -0.048065 | 0.11902 | 0.27924 | 0.11444 | 0.54016 | 0.54016 | -0.041199 | 0.027466 | 122.6761 | 122.0627 | 0.60425
9900.3438 | 0.061035 | 0.27237 | -0.22003 | -0.23498 | -0.10681 | -0.27664 | -0.055542 | 0.1236 | 0.11902 | 0.15106 | 0.10071 | 0.086975 | -0.045776 | 0.086975 | 0.045776 | 0.05127 | -0.25528 | -0.019226 | -0.10895 | -0.044861 | 0.13733 | 0.29297 | 0.13733 | 0.51727 | 0.51727 | -0.064087 | -0.004578 | 122.6807 | 122.0627 | 0.62714
9902.1406 | 0.061035 | 0.20828 | -0.20828 | -0.23819 | -0.085449 | -0.2446 | -0.052338 | 0.054932 | -0.022888 | 0.018311 | 0.045776 | 0.14191 | -0.009155 | 0.10529 | 0.061035 | 0.046997 | -0.22964 | -0.012817 | -0.087585 | -0.061951 | 0.16937 | 0.14191 | 0.036621 | 0.37079 | 0.34332 | -0.009155 | 0.054932 | 122.8134 | 122.2412 | 0.36621
9903.8594 | 0.061035 | 0.24139 | -0.2211 | -0.2446 | -0.095062 | -0.27664 | -0.05127 | 0.13275 | 0.11444 | 0.15564 | 0.10986 | 0.10071 | -0.059509 | 0.086975 | 0.061035 | 0.029907 | -0.21042 | -0.018158 | -0.11322 | -0.045929 | 0.22888 | 0.24719 | 0.1236 | 0.36163 | 0.35248 | -0.054932 | 0.032043 | 122.6715 | 122.2229 | 0.43945
9905.6562 | 0.045776 | 0.2211 | -0.21469 | -0.22537 | -0.10254 | -0.23819 | -0.03952 | 0.10529 | 0.018311 | 0.045776 | 0.054932 | 0.12817 | -0.027466 | 0.10986 | 0.030518 | 0.089722 | -0.25742 | -0.013885 | -0.09079 | -0.052338 | 0.045776 | 0.20142 | 0.009155 | 0.64545 | 0.63629 | -0.036621 | 0.013733 | 122.7493 | 121.9437 | 0.66834
9907.375 | 0.061035 | 0.20294 | -0.20615 | -0.23178 | -0.10361 | -0.2446 | -0.044861 | 0.050354 | -0.091553 | -0.004578 | 0.018311 | 0.12817 | 0 | 0.12817 | 0.045776 | 0.0737 | -0.23926 | -0.023499 | -0.09613 | -0.046997 | 0.07782 | 0.30212 | -0.022888 | 0.40283 | 0.39825 | -0.013733 | 0.045776 | 122.7539 | 122.2 | 0.4303
9909.1406 | 0.061035 | 0.23285 | -0.20828 | -0.23178 | -0.092926 | -0.26596 | -0.040588 | 0.13733 | 0.073242 | 0.1236 | 0.09613 | 0.10529 | -0.064087 | 0.082397 | 0.061035 | 0.077972 | -0.25742 | -0.014954 | -0.10788 | -0.043793 | 0.10986 | 0.56305 | 0.09613 | 0.52185 | 0.53101 | -0.050354 | 0 | 122.7905 | 122.0581 | 0.56763
9910.8594 | 0.061035 | 0.22644 | -0.21896 | -0.22217 | -0.11963 | -0.25635 | -0.036316 | 0.022888 | -0.07782 | -0.013733 | 0.013733 | 0.12817 | -0.032043 | 0.10529 | 0.061035 | 0.054474 | -0.22324 | -0.01709 | -0.097198 | -0.035248 | 0.14191 | 0.18768 | -0.009155 | 0.32044 | 0.31586 | -0.004578 | 0.064087 | 122.7951 | 122.2916 | 0.33875
9912.6562 | 0.061035 | 0.23926 | -0.21362 | -0.24674 | -0.097198 | -0.30014 | -0.059814 | 0.068665 | 0.054932 | 0.11444 | 0.082397 | 0.09613 | -0.059509 | 0.07782 | 0.045776 | 0.058746 | -0.27344 | -0.023499 | -0.12817 | -0.046997 | 0.10986 | 0.44861 | 0.13733 | 0.57678 | 0.54932 | -0.050354 | 0.027466 | 122.7402 | 122.0261 | 0.64087
9914.4531 | 0.045776 | 0.2243 | -0.2211 | -0.23178 | -0.11215 | -0.26276 | -0.05127 | 0.045776 | -0.073242 | -0.013733 | 0.004578 | 0.14648 | -0.032043 | 0.11902 | 0.045776 | 0.057678 | -0.23178 | -0.01709 | -0.091858 | -0.040588 | 0.11444 | 0.25177 | -0.004578 | 0.33875 | 0.32044 | -0.004578 | 0.050354 | 122.8088 | 122.2366 | 0.36621
9916.2344 | 0.030518 | 0.24246 | -0.22537 | -0.23712 | -0.10788 | -0.28198 | -0.053406 | 0.091553 | 0.041199 | 0.10071 | 0.068665 | 0.082397 | -0.059509 | 0.07782 | 0.045776 | 0.05127 | -0.2478 | -0.021362 | -0.11322 | -0.036316 | 0.14648 | 0.39825 | 0.086975 | 0.37994 | 0.35706 | -0.009155 | 0.022888 | 122.6852 | 122.2549 | 0.45319
9918.0312 | 0.045776 | 0.24994 | -0.2211 | -0.2478 | -0.099335 | -0.27451 | -0.043793 | 0.12817 | 0.082397 | 0.13275 | 0.086975 | 0.091553 | -0.045776 | 0.082397 | 0.061035 | 0.069427 | -0.25635 | -0.028839 | -0.1239 | -0.040588 | 0.16479 | 0.53558 | 0.13733 | 0.41657 | 0.40283 | -0.041199 | 0.022888 | 122.7448 | 122.1497 | 0.49439
9919.75 | 0.076294 | 0.25742 | -0.21896 | -0.24353 | -0.091858 | -0.27771 | -0.05661 | 0.091553 | 0.032043 | 0.07782 | 0.054932 | 0.10529 | -0.041199 | 0.082397 | 0.045776 | 0.0737 | -0.27023 | -0.019226 | -0.11536 | -0.048065 | 0.050354 | 0.49439 | 0.059509 | 0.52643 | 0.50812 | -0.045776 | 0.036621 | 122.6944 | 122.0856 | 0.59052
9921.5312 | 0.061035 | 0.23498 | -0.20294 | -0.23178 | -0.095062 | -0.26276 | -0.055542 | 0.14648 | 0.054932 | 0.10529 | 0.068665 | 0.10986 | -0.041199 | 0.086975 | 0.076294 | 0.077972 | -0.26169 | -0.032043 | -0.10147 | -0.044861 | 0.12817 | 0.50354 | 0.086975 | 0.44861 | 0.45776 | -0.041199 | 0.009155 | 122.818 | 122.1313 | 0.50354
9923.3125 | 0.061035 | 0.23926 | -0.21255 | -0.22858 | -0.1004 | -0.24353 | -0.03418 | 0.10071 | -0.013733 | 0.045776 | 0.041199 | 0.11902 | -0.027466 | 0.10529 | 0.076294 | 0.088654 | -0.25848 | -0.010681 | -0.099335 | -0.043793 | 0.12817 | 0.4715 | 0.068665 | 0.4303 | 0.41657 | -0.041199 | 0.036621 | 122.8363 | 122.1222 | 0.47607
9925.0938 | 0.045776 | 0.23926 | -0.22751 | -0.22964 | -0.09613 | -0.25101 | -0.038452 | 0.12817 | 0.064087 | 0.10071 | 0.09613 | 0.09613 | -0.045776 | 0.07782 | 0.061035 | 0.070496 | -0.25742 | -0.019226 | -0.083313 | -0.054474 | 0.16479 | 0.45776 | 0.086975 | 0.37537 | 0.36163 | -0.036621 | 0.027466 | 122.8043 | 122.168 | 0.42572
9926.875 | 0.061035 | 0.21576 | -0.21896 | -0.23605 | -0.091858 | -0.23392 | -0.043793 | 0.059509 | -0.027466 | 0.022888 | 0.013733 | 0.14191 | -0.009155 | 0.11444 | 0.061035 | 0.084381 | -0.24246 | -0.012817 | -0.093994 | -0.044861 | 0.059509 | 0.32501 | -0.032043 | 0.37994 | 0.38452 | 0.004578 | 0.064087 | 122.7585 | 122.2137 | 0.42114
9928.6094 | 0.045776 | 0.24674 | -0.20401 | -0.25207 | -0.11322 | -0.28519 | -0.064087 | 0.068665 | 0.022888 | 0.07782 | 0.045776 | 0.09613 | -0.050354 | 0.073242 | 0.061035 | 0.035248 | -0.22751 | -0.02243 | -0.12497 | -0.038452 | 0.13275 | 0.15564 | 0.091553 | 0.39368 | 0.3891 | -0.050354 | 0.045776 | 122.7036 | 122.2046 | 0.48065
9930.3906 | 0.061035 | 0.23819 | -0.2179 | -0.24994 | -0.10681 | -0.27451 | -0.050201 | 0.11444 | 0.11902 | 0.15106 | 0.10529 | 0.11902 | -0.041199 | 0.082397 | 0.061035 | 0.027771 | -0.23926 | -0.03418 | -0.11215 | -0.044861 | 0.21973 | 0.22888 | 0.12817 | 0.32044 | 0.29297 | -0.045776 | 0.041199 | 122.7127 | 122.287 | 0.40283
9932.1094 | 0.076294 | 0.22324 | -0.20615 | -0.23498 | -0.091858 | -0.2446 | -0.040588 | 0.036621 | -0.07782 | -0.018311 | 0.018311 | 0.1236 | -0.013733 | 0.11444 | 0.045776 | 0.058746 | -0.22644 | -0.014954 | -0.095062 | -0.049133 | 0.086975 | 0.19226 | -0.041199 | 0.3479 | 0.35248 | 0 | 0.068665 | 122.7814 | 122.2778 | 0.36163
9933.9062 | 0.061035 | 0.23926 | -0.21042 | -0.23285 | -0.087585 | -0.26596 | -0.03418 | 0.10986 | 0.004578 | 0.091553 | 0.086975 | 0.10071 | -0.054932 | 0.07782 | 0.061035 | 0.043793 | -0.23285 | -0.023499 | -0.095062 | -0.042725 | 0.21973 | 0.33875 | 0.09613 | 0.28381 | 0.29755 | -0.041199 | 0.032043 | 122.8271 | 122.2641 | 0.34332
9935.7031 | 0.076294 | 0.22964 | -0.20828 | -0.25207 | -0.10254 | -0.28305 | -0.054474 | 0.11444 | 0.13275 | 0.15106 | 0.09613 | 0.086975 | -0.041199 | 0.073242 | 0.061035 | 0.041656 | -0.23178 | -0.019226 | -0.1207 | -0.038452 | 0.18768 | 0.43488 | 0.13733 | 0.31128 | 0.31128 | -0.050354 | 0.027466 | 122.7127 | 122.3007 | 0.42114
9937.4844 | 0.045776 | 0.2243 | -0.21255 | -0.21683 | -0.095062 | -0.2478 | -0.033112 | 0.032043 | -0.068665 | -0.018311 | 0.022888 | 0.13275 | -0.004578 | 0.12817 | 0.061035 | 0.084381 | -0.24567 | -0.014954 | -0.086517 | -0.03952 | 0.059509 | 0.27008 | -0.045776 | 0.45319 | 0.42114 | -0.013733 | 0.054932 | 122.7997 | 122.1817 | 0.44403
9939.2031 | 0.061035 | 0.23178 | -0.20935 | -0.24994 | -0.10254 | -0.28305 | -0.05127 | 0.086975 | 0.09613 | 0.12817 | 0.091553 | 0.10071 | -0.054932 | 0.091553 | 0.030518 | 0.057678 | -0.23178 | -0.028839 | -0.12711 | -0.038452 | 0.13275 | 0.37537 | 0.07782 | 0.3891 | 0.3891 | -0.018311 | 0.045776 | 122.6852 | 122.2183 | 0.46234
9941 | 0.045776 | 0.2211 | -0.20935 | -0.24033 | -0.095062 | -0.25635 | -0.055542 | 0.032043 | -0.036621 | 0.004578 | 0.018311 | 0.13733 | -0.004578 | 0.1236 | 0.061035 | 0.087585 | -0.24033 | -0.020294 | -0.09613 | -0.053406 | 0.022888 | 0.13275 | -0.004578 | 0.53101 | 0.52643 | -0.009155 | 0.054932 | 122.8134 | 122.0581 | 0.54016
9942.7344 | 0.045776 | 0.2243 | -0.19867 | -0.24246 | -0.10895 | -0.25207 | -0.048065 | 0.091553 | 0.009155 | 0.045776 | 0.059509 | 0.14648 | -0.018311 | 0.10986 | 0.045776 | 0.099335 | -0.26169 | -0.012817 | -0.10147 | -0.050201 | 0.064087 | 0.19684 | 0.041199 | 0.60425 | 0.60883 | -0.036621 | 0.050354 | 122.8317 | 121.9986 | 0.60425
9944.5312 | 0.061035 | 0.22217 | -0.20828 | -0.22751 | -0.084381 | -0.2446 | -0.048065 | 0.059509 | -0.009155 | 0.004578 | 0.036621 | 0.1236 | -0.027466 | 0.1236 | 0.076294 | 0.09613 | -0.25421 | -0.010681 | -0.093994 | -0.050201 | 0.022888 | 0.12817 | -0.018311 | 0.54474 | 0.54474 | -0.022888 | 0.045776 | 122.7997 | 122.0718 | 0.56763
9946.25 | 0.045776 | 0.25101 | -0.21362 | -0.24674 | -0.10254 | -0.29907 | -0.053406 | 0.082397 | 0.059509 | 0.11902 | 0.091553 | 0.11444 | -0.050354 | 0.068665 | 0.061035 | 0.061951 | -0.26169 | -0.021362 | -0.12176 | -0.03418 | 0.11902 | 0.27008 | 0.12817 | 0.53558 | 0.5127 | -0.07782 | 0.013733 | 122.7539 | 122.0764 | 0.6134
9948.0469 | 0.045776 | 0.26382 | -0.22858 | -0.24033 | -0.11215 | -0.29587 | -0.063019 | 0.059509 | 0.027466 | 0.07782 | 0.054932 | 0.10986 | -0.050354 | 0.064087 | 0.061035 | 0.05661 | -0.26062 | -0.03418 | -0.10788 | -0.026703 | 0.086975 | 0.17853 | 0.07782 | 0.46692 | 0.46234 | -0.022888 | 0.036621 | 122.7448 | 122.168 | 0.52643
9949.8281 | 0.045776 | 0.21896 | -0.21042 | -0.24994 | -0.11002 | -0.25848 | -0.05127 | 0.041199 | -0.041199 | 0 | 0.018311 | 0.13275 | -0.018311 | 0.12817 | 0.045776 | 0.065155 | -0.24994 | -0.010681 | -0.11108 | -0.045929 | 0.027466 | 0.1236 | 0 | 0.5127 | 0.49896 | 0 | 0.045776 | 122.731 | 122.1497 | 0.53558
9951.5625 | 0.045776 | 0.24994 | -0.21576 | -0.23498 | -0.10468 | -0.27771 | -0.058746 | 0.073242 | 0.027466 | 0.09613 | 0.059509 | 0.10529 | -0.045776 | 0.10071 | 0.045776 | 0.064087 | -0.27237 | -0.018158 | -0.12176 | -0.044861 | 0.073242 | 0.20142 | 0.11444 | 0.58594 | 0.58136 | -0.059509 | 0.018311 | 122.7493 | 122.0581 | 0.66376
9953.3594 | 0.061035 | 0.24674 | -0.21683 | -0.24674 | -0.089722 | -0.27771 | -0.067291 | 0.10529 | 0.045776 | 0.09613 | 0.073242 | 0.10071 | -0.041199 | 0.073242 | 0.045776 | 0.0737 | -0.26382 | -0.016022 | -0.12176 | -0.046997 | 0.10529 | 0.25635 | 0.11444 | 0.56305 | 0.56305 | -0.059509 | 0.004578 | 122.7676 | 122.0581 | 0.65002
9955.1562 | 0.061035 | 0.23392 | -0.21469 | -0.24139 | -0.11322 | -0.26916 | -0.053406 | 0.10986 | 0.018311 | 0.086975 | 0.050354 | 0.091553 | -0.041199 | 0.073242 | 0.061035 | 0.067291 | -0.25314 | -0.02243 | -0.11215 | -0.050201 | 0.059509 | 0.18768 | 0.059509 | 0.57678 | 0.56305 | -0.045776 | 0.032043 | 122.731 | 122.0673 | 0.63171
9956.9531 | 0.061035 | 0.23819 | -0.21683 | -0.2446 | -0.10361 | -0.27664 | -0.064087 | 0.15106 | 0.10529 | 0.13733 | 0.10529 | 0.10529 | -0.041199 | 0.082397 | 0.061035 | 0.074768 | -0.26276 | -0.024567 | -0.1239 | -0.052338 | 0.15106 | 0.2655 | 0.13733 | 0.54474 | 0.52643 | -0.059509 | 0.018311 | 122.7539 | 122.0764 | 0.60883
9958.6875 | 0.045776 | 0.22537 | -0.21149 | -0.21362 | -0.097198 | -0.24674 | -0.048065 | 0.091553 | -0.059509 | 0 | 0.013733 | 0.14648 | -0.009155 | 0.10986 | 0.045776 | 0.088654 | -0.26276 | -0.014954 | -0.10254 | -0.060883 | 0.041199 | 0.11444 | 0.013733 | 0.5722 | 0.55389 | -0.013733 | 0.050354 | 122.8455 | 122.0535 | 0.58594
9960.4844 | 0.045776 | 0.21896 | -0.20081 | -0.22537 | -0.087585 | -0.23712 | -0.043793 | 0.10986 | -0.022888 | 0.022888 | 0.045776 | 0.13275 | -0.022888 | 0.1236 | 0.045776 | 0.10468 | -0.26489 | -0.011749 | -0.081177 | -0.048065 | 0 | 0.1236 | -0.027466 | 0.57678 | 0.56305 | -0.018311 | 0.050354 | 122.8088 | 122.0444 | 0.59967
9962.2031 | 0.061035 | 0.2211 | -0.20615 | -0.2243 | -0.10147 | -0.24994 | -0.048065 | 0.073242 | -0.054932 | 0.013733 | 0.018311 | 0.1236 | -0.018311 | 0.10986 | 0.045776 | 0.09079 | -0.26276 | -0.021362 | -0.10574 | -0.050201 | 0.041199 | 0.13733 | 0.022888 | 0.55847 | 0.54474 | -0.027466 | 0.018311 | 122.8638 | 122.0581 | 0.58136
9964 | 0.045776 | 0.24887 | -0.22324 | -0.23926 | -0.10254 | -0.28839 | -0.052338 | 0.07782 | 0.022888 | 0.082397 | 0.050354 | 0.10071 | -0.036621 | 0.073242 | 0.061035 | 0.05661 | -0.26276 | -0.029907 | -0.1239 | -0.035248 | 0.050354 | 0.18768 | 0.068665 | 0.53101 | 0.51727 | -0.050354 | 0.032043 | 122.7264 | 122.1085 | 0.62256
9965.7812 | 0.045776 | 0.25635 | -0.22964 | -0.24567 | -0.09613 | -0.27557 | -0.05661 | 0.1236 | 0.036621 | 0.10986 | 0.045776 | 0.10071 | -0.050354 | 0.073242 | 0.076294 | 0.083313 | -0.25848 | -0.019226 | -0.12176 | -0.05127 | 0.086975 | 0.20142 | 0.07782 | 0.51727 | 0.5127 | -0.036621 | 0.018311 | 122.7264 | 122.1405 | 0.59052
9967.5625 | 0.045776 | 0.21255 | -0.21362 | -0.2243 | -0.10361 | -0.23605 | -0.052338 | 0.064087 | -0.036621 | -0.009155 | 0.004578 | 0.13733 | -0.013733 | 0.11444 | 0.061035 | 0.087585 | -0.25421 | -0.012817 | -0.10574 | -0.044861 | 0.022888 | 0.10986 | -0.018311 | 0.54016 | 0.53558 | -0.009155 | 0.045776 | 122.8455 | 122.0718 | 0.55389
9969.3438 | 0.045776 | 0.23392 | -0.20508 | -0.24033 | -0.088654 | -0.27985 | -0.061951 | 0.091553 | 0.068665 | 0.09613 | 0.050354 | 0.091553 | -0.054932 | 0.073242 | 0.061035 | 0.065155 | -0.25742 | -0.023499 | -0.10574 | -0.041656 | 0.068665 | 0.20142 | 0.068665 | 0.52185 | 0.49439 | -0.036621 | 0.045776 | 122.7127 | 122.1588 | 0.59509
9971.1406 | 0.061035 | 0.23498 | -0.19333 | -0.22217 | -0.10361 | -0.25101 | -0.045929 | 0.16479 | 0.059509 | 0.10986 | 0.10071 | 0.09613 | -0.082397 | 0.068665 | 0.061035 | 0.076904 | -0.26276 | -0.018158 | -0.10788 | -0.042725 | 0.13733 | 0.21973 | 0.10529 | 0.49439 | 0.46234 | -0.027466 | 0.013733 | 122.8271 | 122.1176 | 0.54932
9972.8906 | 0.061035 | 0.2211 | -0.21149 | -0.23392 | -0.10147 | -0.23926 | -0.03952 | 0.050354 | -0.059509 | -0.009155 | 0.022888 | 0.1236 | -0.022888 | 0.1236 | 0.045776 | 0.088654 | -0.25742 | -0.008545 | -0.10147 | -0.045929 | -0.018311 | 0.091553 | -0.045776 | 0.54474 | 0.49896 | 0.004578 | 0.068665 | 122.7997 | 122.1268 | 0.54932
9974.6875 | 0.061035 | 0.21683 | -0.20187 | -0.23285 | -0.11108 | -0.24887 | -0.03418 | 0.054932 | -0.032043 | 0.009155 | 0.018311 | 0.13733 | -0.022888 | 0.10529 | 0.045776 | 0.093994 | -0.25421 | -0.020294 | -0.089722 | -0.046997 | -0.013733 | 0.11444 | -0.041199 | 0.53558 | 0.53558 | -0.027466 | 0.045776 | 122.7951 | 122.0901 | 0.55389
9976.4688 | 0.061035 | 0.25101 | -0.22003 | -0.23392 | -0.12176 | -0.29266 | -0.046997 | 0.091553 | 0.059509 | 0.11444 | 0.073242 | 0.10529 | -0.054932 | 0.091553 | 0.061035 | 0.05661 | -0.25635 | -0.018158 | -0.12604 | -0.035248 | 0.10986 | 0.2655 | 0.12817 | 0.47607 | 0.48523 | -0.050354 | 0.032043 | 122.7631 | 122.1451 | 0.55389
9978.1875 | 0.061035 | 0.2243 | -0.19867 | -0.23071 | -0.092926 | -0.25207 | -0.05661 | 0.054932 | -0.091553 | -0.004578 | 0.022888 | 0.14191 | -0.013733 | 0.10529 | 0.061035 | 0.10147 | -0.26169 | -0.014954 | -0.1004 | -0.05127 | 0.018311 | 0.10071 | -0.036621 | 0.51727 | 0.50354 | -0.013733 | 0.059509 | 122.8409 | 122.1268 | 0.54016
9979.9844 | 0.061035 | 0.22644 | -0.20615 | -0.24139 | -0.097198 | -0.25955 | -0.046997 | 0.07782 | -0.013733 | 0.027466 | 0.054932 | 0.13275 | -0.022888 | 0.11902 | 0.045776 | 0.083313 | -0.24674 | -0.007477 | -0.10788 | -0.05127 | 0.018311 | 0.16937 | 0.009155 | 0.50354 | 0.48523 | 0 | 0.054932 | 122.8592 | 122.1176 | 0.49896
9981.7188 | 0.061035 | 0.21896 | -0.21042 | -0.23605 | -0.098267 | -0.25207 | -0.049133 | 0.091553 | 0 | 0.036621 | 0.050354 | 0.13733 | -0.004578 | 0.11444 | 0.076294 | 0.081177 | -0.24994 | -0.012817 | -0.11002 | -0.044861 | 0.059509 | 0.18768 | 0.022888 | 0.50812 | 0.50812 | -0.013733 | 0.054932 | 122.8546 | 122.1405 | 0.5127
9983.5156 | 0.045776 | 0.22537 | -0.22644 | -0.24139 | -0.092926 | -0.30441 | -0.050201 | 0.059509 | 0.009155 | 0.082397 | 0.054932 | 0.12817 | -0.036621 | 0.073242 | 0.076294 | 0.064087 | -0.26382 | -0.030975 | -0.1207 | -0.033112 | 0.059509 | 0.20599 | 0.09613 | 0.46234 | 0.48065 | -0.059509 | 0.032043 | 122.7631 | 122.1634 | 0.54932
9985.2344 | 0.045776 | 0.24033 | -0.21255 | -0.25421 | -0.1004 | -0.27664 | -0.063019 | 0.13275 | 0.09613 | 0.14191 | 0.091553 | 0.10071 | -0.027466 | 0.091553 | 0.045776 | 0.064087 | -0.25101 | -0.014954 | -0.12604 | -0.041656 | 0.10529 | 0.29297 | 0.12817 | 0.46234 | 0.45776 | -0.041199 | 0.018311 | 122.731 | 122.1634 | 0.54932
9987.0156 | 0.030518 | 0.24353 | -0.22217 | -0.23178 | -0.087585 | -0.28732 | -0.067291 | 0.054932 | 0.004578 | 0.082397 | 0.054932 | 0.09613 | -0.045776 | 0.10071 | 0.061035 | 0.065155 | -0.26382 | -0.014954 | -0.11322 | -0.040588 | 0.054932 | 0.20142 | 0.07782 | 0.46234 | 0.46234 | -0.036621 | 0.032043 | 122.7631 | 122.1817 | 0.54932
9988.7969 | 0.045776 | 0.22003 | -0.20187 | -0.2179 | -0.093994 | -0.25421 | -0.049133 | 0.073242 | -0.073242 | -0.018311 | 0.013733 | 0.13275 | -0.004578 | 0.1236 | 0.030518 | 0.089722 | -0.2713 | -0.002136 | -0.098267 | -0.055542 | 0.027466 | 0.10529 | -0.004578 | 0.50812 | 0.48065 | 0 | 0.059509 | 122.8729 | 122.1451 | 0.50354
9990.5938 | 0.061035 | 0.23392 | -0.20935 | -0.24139 | -0.09613 | -0.25314 | -0.043793 | 0.14191 | 0.068665 | 0.12817 | 0.10529 | 0.086975 | -0.050354 | 0.086975 | 0.061035 | 0.075836 | -0.25848 | -0.021362 | -0.10147 | -0.045929 | 0.11444 | 0.24261 | 0.10529 | 0.44403 | 0.43488 | -0.027466 | 0.022888 | 122.8317 | 122.1542 | 0.50354
9992.3125 | 0.061035 | 0.22644 | -0.22858 | -0.23819 | -0.099335 | -0.28946 | -0.060883 | 0.14191 | 0.10071 | 0.14191 | 0.091553 | 0.082397 | -0.054932 | 0.068665 | 0.061035 | 0.0737 | -0.27451 | -0.032043 | -0.11643 | -0.040588 | 0.10529 | 0.29755 | 0.1236 | 0.46234 | 0.43945 | -0.045776 | 0.036621 | 122.7585 | 122.1817 | 0.52643
9994.125 | 0.076294 | 0.22217 | -0.19546 | -0.23605 | -0.095062 | -0.2446 | -0.038452 | 0.059509 | -0.059509 | -0.013733 | 0.032043 | 0.13733 | -0.022888 | 0.10071 | 0.045776 | 0.085449 | -0.25421 | -0.020294 | -0.11002 | -0.05661 | 0.022888 | 0.13275 | -0.032043 | 0.49896 | 0.4715 | 0.004578 | 0.073242 | 122.8683 | 122.1725 | 0.5127
9995.8438 | 0.061035 | 0.24033 | -0.21576 | -0.23819 | -0.11749 | -0.27023 | -0.046997 | 0.1236 | 0.064087 | 0.1236 | 0.068665 | 0.07782 | -0.036621 | 0.073242 | 0.045776 | 0.072632 | -0.25955 | -0.024567 | -0.10895 | -0.049133 | 0.082397 | 0.20599 | 0.064087 | 0.45319 | 0.43945 | -0.036621 | 0.022888 | 122.7402 | 122.2137 | 0.53101
9997.6406 | 0.045776 | 0.21362 | -0.1944 | -0.23926 | -0.089722 | -0.26062 | -0.045929 | 0.14648 | 0.059509 | 0.10529 | 0.09613 | 0.10529 | -0.054932 | 0.091553 | 0.061035 | 0.076904 | -0.25421 | -0.018158 | -0.11215 | -0.045929 | 0.12817 | 0.24261 | 0.091553 | 0.45319 | 0.43488 | -0.050354 | 0.032043 | 122.8592 | 122.1542 | 0.5127
9999.4219 | 0.045776 | 0.23392 | -0.20615 | -0.23712 | -0.1004 | -0.24139 | -0.044861 | 0.11444 | 0.022888 | 0.050354 | 0.045776 | 0.11444 | -0.022888 | 0.10529 | 0.045776 | 0.098267 | -0.25101 | -0.014954 | -0.099335 | -0.049133 | 0.050354 | 0.17853 | 0.022888 | 0.48523 | 0.46234 | -0.018311 | 0.059509 | 122.8592 | 122.1497 | 0.5127
10001.1562 | 0.061035 | 0.22751 | -0.20828 | -0.25848 | -0.098267 | -0.27023 | -0.042725 | 0.041199 | -0.041199 | -0.013733 | 0.018311 | 0.1236 | -0.009155 | 0.1236 | 0.030518 | 0.086517 | -0.24887 | -0.013885 | -0.11856 | -0.044861 | 0 | 0.14191 | -0.018311 | 0.49896 | 0.49439 | 0.004578 | 0.073242 | 122.8043 | 122.1771 | 0.5127
10002.9375 | 0.045776 | 0.23605 | -0.20294 | -0.23178 | -0.092926 | -0.26169 | -0.043793 | 0.082397 | -0.027466 | 0.041199 | 0.041199 | 0.11444 | -0.009155 | 0.10529 | 0.045776 | 0.074768 | -0.26169 | -0.008545 | -0.10574 | -0.038452 | 0.082397 | 0.18768 | 0.050354 | 0.46692 | 0.45776 | -0.041199 | 0.027466 | 122.8821 | 122.1588 | 0.50354
10004.7344 | 0.061035 | 0.21683 | -0.21362 | -0.22003 | -0.099335 | -0.24994 | -0.032043 | 0.036621 | -0.09613 | -0.022888 | 0.004578 | 0.14191 | -0.004578 | 0.11444 | 0.061035 | 0.095062 | -0.26169 | -0.021362 | -0.099335 | -0.044861 | -0.036621 | 0.10071 | -0.050354 | 0.48523 | 0.4715 | 0.013733 | 0.082397 | 122.8317 | 122.1954 | 0.49439
10006.5156 | 0.045776 | 0.24033 | -0.21255 | -0.22751 | -0.10254 | -0.28198 | -0.057678 | 0.11444 | 0.091553 | 0.1236 | 0.09613 | 0.082397 | -0.064087 | 0.073242 | 0.045776 | 0.061951 | -0.26062 | -0.029907 | -0.11322 | -0.040588 | 0.10071 | 0.26093 | 0.10986 | 0.44861 | 0.43488 | -0.032043 | 0.032043 | 122.7814 | 122.2092 | 0.53558
10008.2812 | 0.061035 | 0.27023 | -0.22644 | -0.24033 | -0.099335 | -0.27878 | -0.045929 | 0.11902 | 0.1236 | 0.14648 | 0.10071 | 0.10071 | -0.041199 | 0.068665 | 0.076294 | 0.065155 | -0.27237 | -0.027771 | -0.11429 | -0.03952 | 0.12817 | 0.3067 | 0.15564 | 0.45319 | 0.44403 | -0.032043 | 0.050354 | 122.7905 | 122.2046 | 0.50812
10010.0625 | 0.061035 | 0.24674 | -0.2211 | -0.24353 | -0.10468 | -0.28198 | -0.05661 | 0.14648 | 0.11444 | 0.13733 | 0.09613 | 0.082397 | -0.041199 | 0.091553 | 0.045776 | 0.071564 | -0.27771 | -0.029907 | -0.11856 | -0.048065 | 0.10071 | 0.29297 | 0.1236 | 0.43945 | 0.4303 | -0.027466 | 0.054932 | 122.7768 | 122.2046 | 0.5127
10011.8438 | 0.045776 | 0.23285 | -0.20401 | -0.23071 | -0.10468 | -0.25101 | -0.05127 | 0.11444 | 0.018311 | 0.091553 | 0.068665 | 0.09613 | -0.054932 | 0.059509 | 0.061035 | 0.074768 | -0.26382 | -0.01709 | -0.095062 | -0.055542 | 0.10529 | 0.2243 | 0.073242 | 0.45319 | 0.44403 | -0.036621 | 0.041199 | 122.8958 | 122.1771 | 0.47607
10013.5625 | 0.045776 | 0.2478 | -0.22003 | -0.23819 | -0.10788 | -0.27451 | -0.061951 | 0.13275 | 0.068665 | 0.11902 | 0.073242 | 0.091553 | -0.054932 | 0.091553 | 0.076294 | 0.067291 | -0.26596 | -0.018158 | -0.11856 | -0.040588 | 0.086975 | 0.20599 | 0.082397 | 0.43488 | 0.42572 | -0.032043 | 0.041199 | 122.7448 | 122.2504 | 0.53101
10015.3438 | 0.076294 | 0.21469 | -0.20294 | -0.23819 | -0.1004 | -0.23498 | -0.033112 | 0.082397 | -0.004578 | 0.041199 | 0.059509 | 0.14191 | -0.013733 | 0.10986 | 0.076294 | 0.092926 | -0.25848 | -0.010681 | -0.10147 | -0.059814 | 0.032043 | 0.1831 | 0.009155 | 0.45319 | 0.46234 | -0.004578 | 0.068665 | 122.8775 | 122.1725 | 0.48065
10017.125 | 0.061035 | 0.25101 | -0.21255 | -0.23819 | -0.11108 | -0.27451 | -0.044861 | 0.07782 | 0.036621 | 0.086975 | 0.050354 | 0.10529 | -0.054932 | 0.068665 | 0.030518 | 0.072632 | -0.26382 | -0.02243 | -0.11749 | -0.041656 | 0.064087 | 0.20599 | 0.054932 | 0.43488 | 0.41657 | -0.013733 | 0.041199 | 122.7493 | 122.2321 | 0.53101
10018.8438 | 0.045776 | 0.23285 | -0.20508 | -0.2446 | -0.085449 | -0.25528 | -0.054474 | 0.036621 | -0.068665 | -0.013733 | 0.004578 | 0.13275 | -0.032043 | 0.11902 | 0.061035 | 0.085449 | -0.24353 | -0.013885 | -0.091858 | -0.053406 | 0.009155 | 0.091553 | -0.045776 | 0.48523 | 0.44861 | 0.004578 | 0.064087 | 122.8775 | 122.1909 | 0.48065
10020.6406 | 0.061035 | 0.22644 | -0.22751 | -0.24674 | -0.10681 | -0.28198 | -0.069427 | 0.10529 | 0.10986 | 0.15106 | 0.086975 | 0.11902 | -0.036621 | 0.07782 | 0.030518 | 0.058746 | -0.25955 | -0.033112 | -0.11856 | -0.040588 | 0.1236 | 0.27924 | 0.12817 | 0.4303 | 0.41199 | -0.018311 | 0.032043 | 122.818 | 122.2321 | 0.50354
10022.4219 | 0.045776 | 0.22537 | -0.1944 | -0.24353 | -0.11108 | -0.23926 | -0.046997 | 0.045776 | -0.068665 | -0.013733 | 0.027466 | 0.12817 | -0.027466 | 0.10986 | 0.061035 | 0.086517 | -0.24887 | -0.024567 | -0.098267 | -0.052338 | -0.004578 | 0.082397 | -0.059509 | 0.4715 | 0.45319 | 0 | 0.064087 | 122.8592 | 122.2321 | 0.48065
10024.1562 | 0.045776 | 0.23178 | -0.2211 | -0.25207 | -0.1004 | -0.27985 | -0.05127 | 0.11902 | 0.11444 | 0.16479 | 0.086975 | 0.086975 | -0.045776 | 0.091553 | 0.030518 | 0.065155 | -0.25101 | -0.028839 | -0.13138 | -0.048065 | 0.082397 | 0.29297 | 0.11902 | 0.41657 | 0.39825 | -0.036621 | 0.045776 | 122.7676 | 122.2595 | 0.48523
10025.9531 | 0.061035 | 0.23819 | -0.20828 | -0.24674 | -0.10681 | -0.27771 | -0.05661 | 0.068665 | 0.032043 | 0.09613 | 0.050354 | 0.10529 | -0.045776 | 0.10071 | 0.061035 | 0.069427 | -0.25742 | -0.019226 | -0.11322 | -0.03952 | 0.073242 | 0.22888 | 0.082397 | 0.41657 | 0.40741 | -0.032043 | 0.036621 | 122.7951 | 122.2549 | 0.48981
10027.7344 | 0.076294 | 0.21042 | -0.21149 | -0.21896 | -0.088654 | -0.2243 | -0.045929 | 0.11902 | 0.004578 | 0.041199 | 0.045776 | 0.13275 | -0.041199 | 0.10986 | 0.061035 | 0.10788 | -0.26489 | -0.010681 | -0.083313 | -0.059814 | 0.045776 | 0.16937 | -0.009155 | 0.43945 | 0.41199 | 0.004578 | 0.073242 | 122.8363 | 122.2275 | 0.44403
10029.4531 | 0.076294 | 0.19867 | -0.21042 | -0.22644 | -0.091858 | -0.26062 | -0.045929 | 0.07782 | -0.036621 | 0.013733 | 0.045776 | 0.1236 | -0.022888 | 0.12817 | 0.045776 | 0.089722 | -0.26169 | -0.021362 | -0.09613 | -0.048065 | 0.022888 | 0.17853 | -0.004578 | 0.44861 | 0.4303 | -0.009155 | 0.09613 | 122.8912 | 122.2092 | 0.45776
10031.2188 | 0.045776 | 0.20935 | -0.22324 | -0.23178 | -0.099335 | -0.24674 | -0.032043 | 0.041199 | -0.073242 | -0.018311 | 0 | 0.14648 | -0.009155 | 0.13275 | 0.045776 | 0.087585 | -0.25635 | -0.01709 | -0.09613 | -0.037384 | 0 | 0.11902 | -0.022888 | 0.44861 | 0.4303 | 0 | 0.073242 | 122.8775 | 122.2321 | 0.45319
10032.9531 | 0.045776 | 0.2478 | -0.21149 | -0.23819 | -0.092926 | -0.26169 | -0.03952 | 0.10529 | 0.018311 | 0.091553 | 0.068665 | 0.10529 | -0.059509 | 0.068665 | 0.045776 | 0.052338 | -0.25421 | -0.020294 | -0.099335 | -0.032043 | 0.09613 | 0.23346 | 0.086975 | 0.39825 | 0.38452 | -0.032043 | 0.050354 | 122.8775 | 122.2412 | 0.44861
10034.7344 | 0.061035 | 0.22751 | -0.21255 | -0.23071 | -0.11108 | -0.24246 | -0.038452 | 0.1236 | 0.022888 | 0.054932 | 0.050354 | 0.1236 | -0.032043 | 0.1236 | 0.045776 | 0.085449 | -0.25528 | -0.013885 | -0.10361 | -0.041656 | 0.041199 | 0.18768 | 0 | 0.42572 | 0.41657 | 0.004578 | 0.064087 | 122.8455 | 122.2412 | 0.42572
10036.5156 | 0.061035 | 0.22644 | -0.21042 | -0.23498 | -0.10147 | -0.25207 | -0.050201 | 0.018311 | -0.07782 | -0.018311 | 0.009155 | 0.12817 | -0.032043 | 0.11902 | 0.061035 | 0.084381 | -0.25635 | -0.018158 | -0.10254 | -0.041656 | -0.045776 | 0.082397 | -0.054932 | 0.42572 | 0.40741 | 0.009155 | 0.073242 | 122.8546 | 122.2595 | 0.45776
10038.2969 | 0.045776 | 0.2243 | -0.20615 | -0.23926 | -0.11322 | -0.2681 | -0.03418 | 0.041199 | -0.064087 | -0.004578 | 0.018311 | 0.10529 | -0.032043 | 0.10071 | 0.061035 | 0.087585 | -0.25421 | -0.003204 | -0.11002 | -0.041656 | 0.032043 | 0.13733 | 0.004578 | 0.41199 | 0.42572 | -0.004578 | 0.064087 | 122.9004 | 122.2275 | 0.44403
10040.0938 | 0.061035 | 0.22751 | -0.20615 | -0.23605 | -0.10468 | -0.26382 | -0.043793 | 0.045776 | -0.041199 | 0.018311 | 0.041199 | 0.11902 | -0.018311 | 0.11444 | 0.061035 | 0.082245 | -0.25955 | -0.028839 | -0.11108 | -0.054474 | 0.009155 | 0.17853 | 0.004578 | 0.40741 | 0.40741 | 0.018311 | 0.073242 | 122.9004 | 122.2595 | 0.43945
10041.8125 | 0.061035 | 0.22324 | -0.20935 | -0.2478 | -0.099335 | -0.28198 | -0.03952 | 0.027466 | -0.045776 | 0.004578 | 0.004578 | 0.13733 | -0.022888 | 0.11902 | 0.061035 | 0.064087 | -0.25635 | -0.023499 | -0.11856 | -0.040588 | -0.036621 | 0.13733 | -0.027466 | 0.44861 | 0.40283 | 0.027466 | 0.086975 | 122.7722 | 122.287 | 0.46692
10043.5938 | 0.061035 | 0.2179 | -0.21683 | -0.23071 | -0.09613 | -0.25314 | -0.05661 | -0.009155 | -0.091553 | -0.027466 | 0.009155 | 0.14191 | -0.018311 | 0.10986 | 0.045776 | 0.097198 | -0.24674 | -0.020294 | -0.088654 | -0.040588 | -0.018311 | 0.09613 | -0.050354 | 0.42114 | 0.42114 | 0.009155 | 0.082397 | 122.8683 | 122.2504 | 0.45319
10045.3906 | 0.030518 | 0.22217 | -0.20615 | -0.25528 | -0.082245 | -0.28305 | -0.053406 | 0.041199 | 0 | 0.032043 | 0.045776 | 0.11902 | -0.004578 | 0.10529 | 0.061035 | 0.065155 | -0.2478 | -0.029907 | -0.12817 | -0.040588 | -0.022888 | 0.14648 | -0.013733 | 0.40283 | 0.41657 | 0.036621 | 0.09613 | 122.7585 | 122.2824 | 0.47607
10047.1719 | 0.045776 | 0.20721 | -0.20721 | -0.23071 | -0.10147 | -0.24246 | -0.040588 | 0.050354 | -0.036621 | 0.009155 | 0.022888 | 0.14191 | -0.027466 | 0.11444 | 0.061035 | 0.081177 | -0.25635 | -0.014954 | -0.095062 | -0.036316 | -0.032043 | 0.11902 | -0.045776 | 0.4303 | 0.40283 | 0.036621 | 0.082397 | 122.8317 | 122.2733 | 0.45776
10048.8906 | 0.061035 | 0.22003 | -0.1976 | -0.2243 | -0.10254 | -0.26596 | -0.052338 | 0.009155 | -0.082397 | -0.018311 | 0.004578 | 0.14191 | -0.009155 | 0.11902 | 0.030518 | 0.083313 | -0.25314 | -0.013885 | -0.10147 | -0.041656 | -0.027466 | 0.082397 | -0.027466 | 0.43945 | 0.41657 | 0 | 0.07782 | 122.8546 | 122.2595 | 0.45319
10050.6719 | 0.045776 | 0.22751 | -0.21469 | -0.24567 | -0.099335 | -0.26382 | -0.05127 | 0.013733 | -0.054932 | -0.013733 | 0.004578 | 0.15106 | -0.018311 | 0.11444 | 0.076294 | 0.086517 | -0.25742 | -0.013885 | -0.1239 | -0.037384 | -0.050354 | 0.13733 | -0.032043 | 0.42572 | 0.42572 | 0.022888 | 0.09613 | 122.8363 | 122.3007 | 0.4303
10052.4531 | 0.076294 | 0.22324 | -0.20508 | -0.24353 | -0.092926 | -0.27344 | -0.053406 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.13733 | -0.013733 | 0.11902 | 0.061035 | 0.0737 | -0.24246 | -0.016022 | -0.10895 | -0.045929 | 0.018311 | 0.09613 | -0.013733 | 0.37079 | 0.35248 | 0.004578 | 0.073242 | 122.905 | 122.2733 | 0.3891
10054.1719 | 0.061035 | 0.2211 | -0.20187 | -0.24994 | -0.11108 | -0.27664 | -0.044861 | 0.027466 | -0.041199 | 0.009155 | 0.013733 | 0.15106 | -0.013733 | 0.13275 | 0.045776 | 0.067291 | -0.24994 | -0.028839 | -0.1239 | -0.036316 | -0.018311 | 0.1236 | -0.013733 | 0.39825 | 0.38452 | 0.032043 | 0.086975 | 122.7722 | 122.3328 | 0.41199
10055.9688 | 0.061035 | 0.23392 | -0.19653 | -0.23712 | -0.11536 | -0.24887 | -0.054474 | 0.041199 | -0.091553 | -0.022888 | 0.013733 | 0.16022 | -0.027466 | 0.11902 | 0.076294 | 0.075836 | -0.25955 | -0.008545 | -0.11108 | -0.044861 | 0 | 0.10529 | -0.045776 | 0.41199 | 0.42114 | 0.022888 | 0.07782 | 122.905 | 122.2687 | 0.42572
10057.75 | 0.061035 | 0.21469 | -0.19974 | -0.2446 | -0.10895 | -0.25742 | -0.066223 | 0.018311 | -0.045776 | 0.018311 | 0.032043 | 0.11902 | -0.004578 | 0.13275 | 0.061035 | 0.084381 | -0.25207 | -0.013885 | -0.11215 | -0.042725 | -0.013733 | 0.16022 | -0.018311 | 0.40741 | 0.40741 | 0.013733 | 0.07782 | 122.8867 | 122.287 | 0.42114
10059.5156 | 0.030518 | 0.20828 | -0.19867 | -0.25742 | -0.098267 | -0.24674 | -0.046997 | 0.054932 | -0.022888 | 0.036621 | 0.041199 | 0.1236 | -0.022888 | 0.13733 | 0.045776 | 0.089722 | -0.24887 | -0.018158 | -0.10895 | -0.052338 | -0.022888 | 0.1236 | -0.050354 | 0.40741 | 0.38452 | 0.013733 | 0.086975 | 122.8683 | 122.2824 | 0.41657
10061.3125 | 0.045776 | 0.22751 | -0.20294 | -0.24994 | -0.092926 | -0.27557 | -0.048065 | -0.013733 | -0.027466 | 0.022888 | 0.013733 | 0.1236 | -0.032043 | 0.10529 | 0.091553 | 0.080109 | -0.25955 | -0.01709 | -0.11536 | -0.038452 | -0.027466 | 0.14191 | -0.018311 | 0.39825 | 0.3891 | 0.018311 | 0.07782 | 122.7722 | 122.319 | 0.44403
10063.0938 | 0.030518 | 0.25207 | -0.20828 | -0.24246 | -0.10895 | -0.29373 | -0.063019 | 0.059509 | 0.045776 | 0.10529 | 0.073242 | 0.11444 | -0.036621 | 0.07782 | 0.061035 | 0.070496 | -0.26596 | -0.035248 | -0.13031 | -0.036316 | 0.091553 | 0.24261 | 0.10986 | 0.36621 | 0.36163 | -0.045776 | 0.054932 | 122.8226 | 122.3145 | 0.43488
10064.8125 | 0.045776 | 0.22751 | -0.21469 | -0.24887 | -0.11429 | -0.27451 | -0.055542 | 0.1236 | 0.11444 | 0.15564 | 0.09613 | 0.10986 | -0.054932 | 0.082397 | 0.076294 | 0.032043 | -0.21683 | -0.028839 | -0.11749 | -0.052338 | 0.16022 | 0.24261 | 0.1236 | 0.21515 | 0.17395 | -0.018311 | 0.059509 | 122.8363 | 122.4792 | 0.27924
10066.5938 | 0.061035 | 0.23926 | -0.21896 | -0.22324 | -0.10681 | -0.25742 | -0.065155 | 0.059509 | -0.045776 | -0.032043 | 0.022888 | 0.12817 | -0.018311 | 0.13275 | 0.045776 | 0.050201 | -0.22003 | -0.02243 | -0.081177 | -0.05127 | 0.041199 | 0.086975 | -0.004578 | 0.22888 | 0.21057 | 0.041199 | 0.10071 | 122.8958 | 122.4655 | 0.2243
10068.375 | 0.045776 | 0.22964 | -0.21683 | -0.24674 | -0.097198 | -0.26169 | -0.059814 | 0.045776 | -0.054932 | -0.018311 | 0.013733 | 0.15106 | -0.009155 | 0.11902 | 0.045776 | 0.09079 | -0.26062 | -0.03418 | -0.11108 | -0.048065 | -0.032043 | 0.13275 | -0.045776 | 0.38452 | 0.39825 | 0.036621 | 0.091553 | 122.8271 | 122.3145 | 0.41657
10070.1719 | 0.030518 | 0.23392 | -0.23392 | -0.23712 | -0.088654 | -0.27771 | -0.065155 | 0.10529 | 0.09613 | 0.13733 | 0.10529 | 0.10986 | -0.050354 | 0.064087 | 0.061035 | 0.0737 | -0.26062 | -0.035248 | -0.10788 | -0.040588 | 0.064087 | 0.26093 | 0.082397 | 0.3479 | 0.33875 | -0.004578 | 0.041199 | 122.7631 | 122.3419 | 0.4303
10071.9062 | 0.030518 | 0.24353 | -0.23285 | -0.24887 | -0.11322 | -0.27878 | -0.055542 | 0.068665 | 0.045776 | 0.086975 | 0.064087 | 0.10529 | -0.064087 | 0.091553 | 0.061035 | 0.028839 | -0.22964 | -0.037384 | -0.1207 | -0.045929 | 0.11444 | 0.18768 | 0.09613 | 0.25177 | 0.24261 | 0 | 0.064087 | 122.8271 | 122.438 | 0.32959
10073.6875 | 0.061035 | 0.22644 | -0.20828 | -0.24246 | -0.10147 | -0.24139 | -0.05661 | 0.050354 | -0.041199 | 0 | 0.013733 | 0.12817 | -0.013733 | 0.1236 | 0.045776 | 0.085449 | -0.25421 | -0.011749 | -0.10361 | -0.041656 | 0.027466 | 0.10986 | -0.018311 | 0.36163 | 0.36621 | 0.009155 | 0.07782 | 122.9141 | 122.2961 | 0.3891
10075.4688 | 0.076294 | 0.2211 | -0.2211 | -0.2446 | -0.092926 | -0.23926 | -0.048065 | 0.07782 | -0.013733 | 0.032043 | 0.045776 | 0.13275 | -0.013733 | 0.11902 | 0.045776 | 0.093994 | -0.25848 | -0.014954 | -0.10574 | -0.061951 | 0.022888 | 0.16479 | -0.009155 | 0.39368 | 0.37994 | 0.009155 | 0.09613 | 122.9004 | 122.2961 | 0.3891
10077.25 | 0.076294 | 0.20721 | -0.20294 | -0.23178 | -0.091858 | -0.25207 | -0.038452 | 0.050354 | -0.018311 | 0.013733 | 0.018311 | 0.11902 | -0.018311 | 0.11902 | 0.076294 | 0.099335 | -0.26062 | -0.030975 | -0.085449 | -0.033112 | -0.027466 | 0.09613 | -0.041199 | 0.37079 | 0.35248 | 0.018311 | 0.09613 | 122.8638 | 122.3465 | 0.40283
10078.9844 | 0.061035 | 0.23392 | -0.21469 | -0.23285 | -0.097198 | -0.27985 | -0.059814 | 0.09613 | 0.091553 | 0.12817 | 0.091553 | 0.086975 | -0.045776 | 0.082397 | 0.076294 | 0.059814 | -0.26596 | -0.029907 | -0.12176 | -0.036316 | 0.091553 | 0.20599 | 0.068665 | 0.33417 | 0.32044 | -0.004578 | 0.054932 | 122.7814 | 122.3923 | 0.39368
10080.7812 | 0.061035 | 0.22858 | -0.21896 | -0.25955 | -0.1004 | -0.27985 | -0.052338 | 0.13275 | 0.10986 | 0.15564 | 0.10529 | 0.091553 | -0.064087 | 0.091553 | 0.076294 | 0.050201 | -0.23926 | -0.019226 | -0.12283 | -0.046997 | 0.13733 | 0.24719 | 0.11444 | 0.21515 | 0.22888 | -0.013733 | 0.054932 | 122.7951 | 122.4655 | 0.32044
10082.5625 | 0.045776 | 0.2713 | -0.21576 | -0.24033 | -0.1004 | -0.28412 | -0.054474 | 0.064087 | 0.018311 | 0.068665 | 0.050354 | 0.091553 | -0.050354 | 0.09613 | 0.045776 | 0.028839 | -0.23498 | -0.038452 | -0.11536 | -0.046997 | 0.10986 | 0.14648 | 0.064087 | 0.19226 | 0.18768 | 0.009155 | 0.07782 | 122.818 | 122.5113 | 0.27466
10084.2812 | 0.045776 | 0.23819 | -0.20615 | -0.22858 | -0.099335 | -0.25635 | -0.045929 | 0.14648 | 0.050354 | 0.10986 | 0.086975 | 0.09613 | -0.045776 | 0.073242 | 0.045776 | 0.05661 | -0.23926 | -0.03418 | -0.091858 | -0.060883 | 0.13733 | 0.1831 | 0.086975 | 0.21515 | 0.20142 | -0.018311 | 0.054932 | 122.9233 | 122.4289 | 0.27924
10086.0781 | 0.061035 | 0.20828 | -0.19974 | -0.25528 | -0.095062 | -0.23392 | -0.042725 | 0.050354 | -0.07782 | 0.004578 | 0.004578 | 0.13275 | -0.013733 | 0.11444 | 0.045776 | 0.076904 | -0.23926 | -0.020294 | -0.093994 | -0.055542 | -0.013733 | 0.082397 | -0.064087 | 0.32959 | 0.29755 | 0.036621 | 0.10529 | 122.8592 | 122.3969 | 0.32501
10087.8594 | 0.030518 | 0.24887 | -0.22003 | -0.24567 | -0.10361 | -0.27771 | -0.053406 | 0.09613 | 0.086975 | 0.10986 | 0.073242 | 0.091553 | -0.064087 | 0.086975 | 0.045776 | 0.025635 | -0.22964 | -0.027771 | -0.10361 | -0.033112 | 0.15106 | 0.15564 | 0.07782 | 0.19684 | 0.19226 | 0 | 0.059509 | 122.7859 | 122.5571 | 0.25177
10089.6406 | 0.061035 | 0.22644 | -0.20401 | -0.21896 | -0.10788 | -0.24139 | -0.043793 | 0.064087 | -0.036621 | 0.027466 | 0.013733 | 0.12817 | -0.022888 | 0.10986 | 0.030518 | 0.086517 | -0.24994 | -0.020294 | -0.093994 | -0.055542 | 0 | 0.10071 | -0.054932 | 0.32044 | 0.31128 | 0.004578 | 0.091553 | 122.8638 | 122.3969 | 0.3479
10091.4219 | 0.045776 | 0.21683 | -0.20935 | -0.24994 | -0.11002 | -0.26276 | -0.048065 | 0.068665 | -0.009155 | 0.032043 | 0.045776 | 0.13733 | -0.018311 | 0.10071 | 0.061035 | 0.054474 | -0.20828 | -0.023499 | -0.10147 | -0.048065 | 0.10071 | 0.1236 | 0.004578 | 0.20142 | 0.18768 | 0.032043 | 0.09613 | 122.9141 | 122.4792 | 0.21057
10093.2031 | 0.061035 | 0.21255 | -0.20828 | -0.25207 | -0.084381 | -0.25528 | -0.038452 | 0.022888 | -0.036621 | 0.009155 | 0.032043 | 0.13275 | -0.004578 | 0.13275 | 0.061035 | 0.076904 | -0.22644 | -0.009613 | -0.10681 | -0.05127 | 0.018311 | 0.1236 | -0.004578 | 0.28381 | 0.28381 | 0.013733 | 0.09613 | 122.9187 | 122.3923 | 0.28839
10094.9844 | 0.015259 | 0.22217 | -0.21469 | -0.24674 | -0.089722 | -0.28946 | -0.055542 | 0.07782 | 0.054932 | 0.10071 | 0.059509 | 0.10071 | -0.036621 | 0.10071 | 0.076294 | 0.037384 | -0.22003 | -0.030975 | -0.13138 | -0.038452 | 0.068665 | 0.13733 | 0.032043 | 0.16937 | 0.19226 | 0.018311 | 0.09613 | 122.7722 | 122.5204 | 0.25177
10096.7656 | 0.045776 | 0.2446 | -0.21255 | -0.23178 | -0.097198 | -0.25421 | -0.05127 | 0.064087 | -0.004578 | 0.045776 | 0.045776 | 0.1236 | -0.022888 | 0.10529 | 0.045776 | 0.061951 | -0.2211 | -0.02243 | -0.091858 | -0.043793 | 0.13733 | 0.14648 | 0.068665 | 0.19684 | 0.1831 | -0.013733 | 0.068665 | 122.9141 | 122.4884 | 0.23804
10098.5469 | 0.045776 | 0.19867 | -0.18799 | -0.25528 | -0.10361 | -0.2478 | -0.043793 | 0.027466 | -0.068665 | -0.013733 | 0.027466 | 0.13275 | -0.018311 | 0.12817 | 0.076294 | 0.065155 | -0.21255 | -0.02243 | -0.099335 | -0.05127 | 0.013733 | 0.041199 | -0.054932 | 0.21973 | 0.2243 | 0.036621 | 0.10071 | 122.85 | 122.4838 | 0.23346
10100.2656 | 0.045776 | 0.20401 | -0.19333 | -0.24139 | -0.089722 | -0.25314 | -0.036316 | 0.07782 | -0.004578 | 0.032043 | 0.036621 | 0.11902 | -0.022888 | 0.1236 | 0.076294 | 0.059814 | -0.20828 | -0.012817 | -0.098267 | -0.049133 | 0.073242 | 0.086975 | -0.013733 | 0.21057 | 0.1831 | 0.018311 | 0.09613 | 122.8683 | 122.4792 | 0.22888
10102.0469 | 0.030518 | 0.21042 | -0.21362 | -0.23926 | -0.099335 | -0.27023 | -0.057678 | 0.027466 | -0.036621 | -0.004578 | 0.022888 | 0.13733 | -0.027466 | 0.11902 | 0.076294 | 0.060883 | -0.22324 | -0.029907 | -0.10468 | -0.038452 | 0.036621 | 0.13275 | -0.009155 | 0.27008 | 0.27008 | 0.027466 | 0.091553 | 122.9095 | 122.4106 | 0.27008
10103.8281 | 0.061035 | 0.22537 | -0.23498 | -0.23819 | -0.092926 | -0.28305 | -0.044861 | 0.091553 | 0.073242 | 0.091553 | 0.091553 | 0.09613 | -0.036621 | 0.082397 | 0.045776 | 0.064087 | -0.24994 | -0.030975 | -0.1207 | -0.03418 | 0.050354 | 0.20142 | 0.045776 | 0.31128 | 0.3067 | 0.027466 | 0.082397 | 122.7722 | 122.4289 | 0.37079
10105.5625 | 0.045776 | 0.23926 | -0.21896 | -0.23819 | -0.10468 | -0.2948 | -0.058746 | 0.064087 | 0.013733 | 0.073242 | 0.054932 | 0.11902 | -0.045776 | 0.09613 | 0.076294 | 0.069427 | -0.26382 | -0.037384 | -0.1239 | -0.03952 | 0.041199 | 0.19226 | 0.073242 | 0.31586 | 0.31586 | -0.013733 | 0.059509 | 122.8226 | 122.3831 | 0.37994
10107.3281 | 0.061035 | 0.24033 | -0.21469 | -0.23712 | -0.10574 | -0.28091 | -0.060883 | 0.14191 | 0.11902 | 0.14191 | 0.10529 | 0.10529 | -0.050354 | 0.082397 | 0.061035 | 0.072632 | -0.27237 | -0.029907 | -0.11429 | -0.045929 | 0.091553 | 0.27466 | 0.11444 | 0.32959 | 0.29755 | -0.032043 | 0.054932 | 122.8409 | 122.3694 | 0.39368
10109.1094 | 0.076294 | 0.23285 | -0.21576 | -0.23498 | -0.10895 | -0.25101 | -0.048065 | 0.064087 | -0.050354 | 0 | 0.022888 | 0.12817 | -0.032043 | 0.11444 | 0.061035 | 0.088654 | -0.26489 | -0.020294 | -0.10574 | -0.055542 | 0.032043 | 0.11902 | -0.004578 | 0.33875 | 0.31586 | 0.009155 | 0.068665 | 122.9416 | 122.3373 | 0.36163
10110.8906 | 0.061035 | 0.23926 | -0.21576 | -0.23285 | -0.10788 | -0.26703 | -0.048065 | 0.15564 | 0.07782 | 0.12817 | 0.07782 | 0.091553 | -0.064087 | 0.091553 | 0.061035 | 0.058746 | -0.24887 | -0.026703 | -0.10361 | -0.043793 | 0.13275 | 0.20142 | 0.086975 | 0.24719 | 0.24261 | -0.004578 | 0.054932 | 122.8043 | 122.4655 | 0.3067
10112.6094 | 0.045776 | 0.22537 | -0.2179 | -0.22537 | -0.097198 | -0.25955 | -0.048065 | 0.14191 | 0.09613 | 0.13275 | 0.086975 | 0.10071 | -0.064087 | 0.073242 | 0.045776 | 0.075836 | -0.27451 | -0.033112 | -0.095062 | -0.049133 | 0.10529 | 0.22888 | 0.082397 | 0.3067 | 0.28839 | -0.004578 | 0.050354 | 122.8317 | 122.3831 | 0.39368
10114.375 | 0.045776 | 0.2478 | -0.21255 | -0.24033 | -0.10147 | -0.26703 | -0.058746 | 0.1236 | 0.068665 | 0.11902 | 0.07782 | 0.091553 | -0.059509 | 0.041199 | 0.061035 | 0.077972 | -0.26276 | -0.032043 | -0.10895 | -0.03952 | 0.07782 | 0.17853 | 0.059509 | 0.3067 | 0.29755 | -0.018311 | 0.064087 | 122.7997 | 122.4014 | 0.40283
10116.0938 | 0.045776 | 0.22217 | -0.20721 | -0.22964 | -0.097198 | -0.25207 | -0.043793 | 0.054932 | -0.045776 | -0.004578 | 0.022888 | 0.13275 | -0.032043 | 0.10529 | 0.045776 | 0.1004 | -0.26382 | -0.020294 | -0.09613 | -0.059814 | 0.022888 | 0.10529 | -0.013733 | 0.32501 | 0.32501 | 0.004578 | 0.09613 | 122.937 | 122.3465 | 0.3479
10117.875 | 0.076294 | 0.23926 | -0.22003 | -0.25421 | -0.098267 | -0.29373 | -0.050201 | 0.12817 | 0.07782 | 0.13733 | 0.07782 | 0.10529 | -0.036621 | 0.086975 | 0.061035 | 0.059814 | -0.26489 | -0.024567 | -0.12497 | -0.045929 | 0.10986 | 0.26093 | 0.09613 | 0.30212 | 0.29297 | 0.013733 | 0.050354 | 122.85 | 122.406 | 0.37079
10119.5938 | 0.061035 | 0.20935 | -0.20615 | -0.25528 | -0.095062 | -0.2478 | -0.053406 | 0.050354 | -0.059509 | -0.004578 | 0.027466 | 0.15106 | 0 | 0.13733 | 0.061035 | 0.086517 | -0.25101 | -0.016022 | -0.1004 | -0.053406 | -0.009155 | 0.1236 | -0.036621 | 0.3479 | 0.33417 | 0.041199 | 0.082397 | 122.9279 | 122.3511 | 0.35706
10121.375 | 0.061035 | 0.2446 | -0.21149 | -0.2446 | -0.099335 | -0.28519 | -0.049133 | 0.07782 | 0.032043 | 0.07782 | 0.059509 | 0.10071 | -0.045776 | 0.073242 | 0.061035 | 0.072632 | -0.26703 | -0.01709 | -0.1207 | -0.033112 | 0.054932 | 0.1831 | 0.045776 | 0.30212 | 0.31128 | -0.013733 | 0.054932 | 122.8134 | 122.4197 | 0.3891
10123.1562 | 0.045776 | 0.22964 | -0.22537 | -0.24139 | -0.10574 | -0.27985 | -0.054474 | 0.13733 | 0.10529 | 0.15564 | 0.10071 | 0.10071 | -0.050354 | 0.091553 | 0.061035 | 0.085449 | -0.26382 | -0.021362 | -0.11536 | -0.037384 | 0.09613 | 0.2655 | 0.091553 | 0.32044 | 0.28381 | -0.027466 | 0.045776 | 122.7951 | 122.3923 | 0.39825
10124.8906 | 0.045776 | 0.2243 | -0.22537 | -0.24033 | -0.10681 | -0.25742 | -0.052338 | 0.14648 | 0.086975 | 0.1236 | 0.091553 | 0.10071 | -0.036621 | 0.091553 | 0.045776 | 0.072632 | -0.26062 | -0.02243 | -0.11002 | -0.048065 | 0.086975 | 0.25177 | 0.068665 | 0.32044 | 0.32501 | 0.013733 | 0.045776 | 122.8043 | 122.406 | 0.39368
10126.6719 | 0.045776 | 0.22324 | -0.20935 | -0.23071 | -0.1004 | -0.24246 | -0.052338 | 0.064087 | -0.082397 | -0.022888 | 0.032043 | 0.15106 | -0.009155 | 0.10986 | 0.030518 | 0.10361 | -0.25635 | -0.011749 | -0.10574 | -0.059814 | -0.004578 | 0.086975 | -0.059509 | 0.34332 | 0.32501 | 0.027466 | 0.091553 | 122.9416 | 122.3877 | 0.34332
10128.4531 | 0.030518 | 0.24353 | -0.22324 | -0.25314 | -0.11108 | -0.28412 | -0.059814 | 0.10529 | 0.059509 | 0.10986 | 0.082397 | 0.11444 | -0.045776 | 0.10071 | 0.061035 | 0.067291 | -0.26916 | -0.035248 | -0.12283 | -0.043793 | 0.09613 | 0.23346 | 0.10986 | 0.3067 | 0.28839 | -0.013733 | 0.050354 | 122.8455 | 122.4243 | 0.37537
10130.2656 | 0.076294 | 0.24994 | -0.22324 | -0.24246 | -0.10681 | -0.27344 | -0.054474 | 0.16022 | 0.10529 | 0.14191 | 0.10071 | 0.09613 | -0.054932 | 0.082397 | 0.061035 | 0.080109 | -0.26489 | -0.011749 | -0.1207 | -0.040588 | 0.10986 | 0.26093 | 0.10529 | 0.30212 | 0.27466 | 0.004578 | 0.041199 | 122.8409 | 122.4106 | 0.36621
10132.0469 | 0.061035 | 0.2446 | -0.21469 | -0.23819 | -0.10254 | -0.26169 | -0.060883 | 0.13275 | 0.068665 | 0.11444 | 0.086975 | 0.09613 | -0.050354 | 0.086975 | 0.076294 | 0.081177 | -0.2713 | -0.035248 | -0.10681 | -0.049133 | 0.064087 | 0.20142 | 0.032043 | 0.32501 | 0.31586 | 0.004578 | 0.07782 | 122.7859 | 122.4152 | 0.37079
10133.8281 | 0.045776 | 0.25101 | -0.22964 | -0.23071 | -0.093994 | -0.27237 | -0.064087 | 0.10529 | 0.022888 | 0.07782 | 0.045776 | 0.091553 | -0.045776 | 0.07782 | 0.061035 | 0.079041 | -0.27237 | -0.032043 | -0.11002 | -0.040588 | 0.073242 | 0.16022 | 0.036621 | 0.29755 | 0.29297 | -0.013733 | 0.064087 | 122.8134 | 122.4152 | 0.37994
10135.5469 | 0.045776 | 0.25207 | -0.22644 | -0.24033 | -0.11108 | -0.27344 | -0.045929 | 0.11902 | 0.027466 | 0.10986 | 0.082397 | 0.091553 | -0.050354 | 0.082397 | 0.076294 | 0.074768 | -0.26169 | -0.028839 | -0.11215 | -0.054474 | 0.07782 | 0.21515 | 0.073242 | 0.30212 | 0.29297 | -0.009155 | 0.064087 | 122.8363 | 122.4014 | 0.37537
10137.3438 | 0.030518 | 0.18906 | -0.19546 | -0.23819 | -0.095062 | -0.23498 | -0.035248 | 0.073242 | -0.086975 | -0.009155 | 0.013733 | 0.14648 | -0.004578 | 0.1236 | 0.061035 | 0.11002 | -0.25848 | -0.029907 | -0.084381 | -0.050201 | -0.027466 | 0.068665 | -0.091553 | 0.32959 | 0.32959 | 0.032043 | 0.082397 | 122.8912 | 122.406 | 0.37079
10139.125 | 0.045776 | 0.24033 | -0.22644 | -0.2243 | -0.10147 | -0.27771 | -0.049133 | 0.1236 | 0.050354 | 0.10071 | 0.054932 | 0.091553 | -0.041199 | 0.073242 | 0.045776 | 0.076904 | -0.26169 | -0.028839 | -0.11856 | -0.032043 | 0.064087 | 0.17853 | 0.045776 | 0.30212 | 0.28839 | 0.009155 | 0.045776 | 122.7905 | 122.4426 | 0.39368
10140.8438 | 0.061035 | 0.23178 | -0.20615 | -0.23071 | -0.093994 | -0.24567 | -0.040588 | 0.14648 | 0.064087 | 0.09613 | 0.082397 | 0.10986 | -0.036621 | 0.09613 | 0.061035 | 0.084381 | -0.27023 | -0.030975 | -0.10254 | -0.050201 | 0.10529 | 0.21057 | 0.064087 | 0.29755 | 0.27466 | -0.018311 | 0.041199 | 122.9233 | 122.3923 | 0.36621
10142.625 | 0.091553 | 0.25742 | -0.21896 | -0.24353 | -0.099335 | -0.28412 | -0.05661 | 0.09613 | 0.068665 | 0.11444 | 0.07782 | 0.09613 | -0.050354 | 0.082397 | 0.061035 | 0.063019 | -0.26489 | -0.030975 | -0.11322 | -0.038452 | 0.091553 | 0.24261 | 0.091553 | 0.30212 | 0.29297 | 0 | 0.059509 | 122.8592 | 122.3969 | 0.37079
10144.3438 | 0.061035 | 0.24994 | -0.20294 | -0.23605 | -0.10361 | -0.25635 | -0.045929 | 0.15564 | 0.082397 | 0.15564 | 0.082397 | 0.09613 | -0.064087 | 0.050354 | 0.030518 | 0.081177 | -0.25101 | -0.019226 | -0.10681 | -0.05127 | 0.11902 | 0.20599 | 0.086975 | 0.29297 | 0.28839 | -0.013733 | 0.059509 | 122.85 | 122.4197 | 0.35706
10146.125 | 0.045776 | 0.23071 | -0.21896 | -0.24033 | -0.10681 | -0.26703 | -0.044861 | 0.13275 | 0.10529 | 0.14191 | 0.10529 | 0.086975 | -0.050354 | 0.09613 | 0.061035 | 0.0737 | -0.24887 | -0.020294 | -0.10574 | -0.040588 | 0.09613 | 0.24261 | 0.082397 | 0.28381 | 0.27466 | 0 | 0.050354 | 122.818 | 122.406 | 0.37079
10147.8438 | 0.061035 | 0.21362 | -0.22003 | -0.25421 | -0.089722 | -0.25635 | -0.044861 | 0.054932 | -0.041199 | 0.013733 | 0.009155 | 0.1236 | -0.018311 | 0.13275 | 0.061035 | 0.098267 | -0.24994 | -0.02243 | -0.10468 | -0.05661 | -0.009155 | 0.11444 | -0.032043 | 0.35248 | 0.33875 | 0.036621 | 0.10529 | 122.8409 | 122.4335 | 0.37079
10149.625 | 0.045776 | 0.2179 | -0.19226 | -0.2478 | -0.088654 | -0.2446 | -0.05127 | 0.082397 | 0 | 0.027466 | 0.050354 | 0.14648 | -0.022888 | 0.13275 | 0.061035 | 0.098267 | -0.25101 | -0.021362 | -0.10147 | -0.053406 | 0.032043 | 0.16022 | 0 | 0.33417 | 0.31128 | 0.027466 | 0.068665 | 122.9462 | 122.4152 | 0.3479
10151.4062 | 0.061035 | 0.24994 | -0.20721 | -0.23712 | -0.09079 | -0.28839 | -0.05127 | 0.045776 | 0.027466 | 0.07782 | 0.064087 | 0.10986 | -0.041199 | 0.10071 | 0.061035 | 0.0737 | -0.26062 | -0.033112 | -0.12497 | -0.035248 | 0.036621 | 0.1831 | 0.032043 | 0.30212 | 0.28381 | 0 | 0.054932 | 122.8271 | 122.4243 | 0.41199
10153.1719 | 0.061035 | 0.2446 | -0.22003 | -0.24033 | -0.1004 | -0.28519 | -0.053406 | 0.07782 | 0.045776 | 0.086975 | 0.07782 | 0.11444 | -0.032043 | 0.082397 | 0.061035 | 0.0737 | -0.25635 | -0.029907 | -0.11215 | -0.038452 | 0.091553 | 0.2243 | 0.091553 | 0.29297 | 0.29755 | -0.018311 | 0.054932 | 122.8592 | 122.4197 | 0.37537
10154.9688 | 0.076294 | 0.21576 | -0.19546 | -0.23926 | -0.09079 | -0.25421 | -0.049133 | 0.073242 | -0.041199 | 0 | 0.041199 | 0.13733 | -0.018311 | 0.11444 | 0.076294 | 0.095062 | -0.24994 | -0.011749 | -0.097198 | -0.042725 | 0 | 0.12817 | -0.045776 | 0.32959 | 0.32044 | 0.009155 | 0.10529 | 122.937 | 122.3694 | 0.34332
10156.75 | 0.045776 | 0.20828 | -0.20615 | -0.22858 | -0.098267 | -0.24674 | -0.03952 | 0.073242 | -0.018311 | 0.013733 | 0.050354 | 0.13733 | -0.013733 | 0.11444 | 0.045776 | 0.095062 | -0.26382 | -0.028839 | -0.087585 | -0.059814 | 0.018311 | 0.15564 | -0.022888 | 0.33417 | 0.32959 | 0.018311 | 0.082397 | 122.9507 | 122.3923 | 0.32959
10158.4688 | 0.061035 | 0.23819 | -0.22858 | -0.24246 | -0.10361 | -0.28839 | -0.05661 | 0.054932 | 0.018311 | 0.082397 | 0.064087 | 0.10986 | -0.036621 | 0.091553 | 0.061035 | 0.070496 | -0.25207 | -0.037384 | -0.11215 | -0.032043 | 0.054932 | 0.19684 | 0.082397 | 0.30212 | 0.29297 | -0.009155 | 0.07782 | 122.8683 | 122.438 | 0.37079
10160.2656 | 0.030518 | 0.25848 | -0.21683 | -0.23071 | -0.11215 | -0.28519 | -0.057678 | 0.073242 | 0.022888 | 0.07782 | 0.045776 | 0.10071 | -0.032043 | 0.10986 | 0.045776 | 0.079041 | -0.26489 | -0.029907 | -0.12176 | -0.046997 | 0.064087 | 0.18768 | 0.050354 | 0.29297 | 0.29297 | -0.004578 | 0.050354 | 122.85 | 122.4289 | 0.36163
10162.0625 | 0.061035 | 0.24353 | -0.21362 | -0.23285 | -0.10468 | -0.2713 | -0.050201 | 0.13733 | 0.13275 | 0.13733 | 0.10071 | 0.10071 | -0.036621 | 0.07782 | 0.045776 | 0.077972 | -0.26169 | -0.018158 | -0.11429 | -0.045929 | 0.09613 | 0.25635 | 0.082397 | 0.29755 | 0.27008 | 0.004578 | 0.054932 | 122.8363 | 122.4426 | 0.37537
10163.8438 | 0.045776 | 0.21896 | -0.21149 | -0.24033 | -0.10681 | -0.22964 | -0.054474 | 0.07782 | -0.036621 | 0.009155 | 0.022888 | 0.12817 | -0.022888 | 0.11444 | 0.061035 | 0.09079 | -0.24674 | -0.021362 | -0.10361 | -0.049133 | 0.050354 | 0.13275 | -0.004578 | 0.3067 | 0.27924 | 0.004578 | 0.073242 | 122.9782 | 122.4106 | 0.32959
10165.625 | 0.061035 | 0.23285 | -0.21576 | -0.24887 | -0.092926 | -0.26703 | -0.052338 | 0.12817 | 0.10071 | 0.13733 | 0.086975 | 0.09613 | -0.041199 | 0.086975 | 0.076294 | 0.072632 | -0.25848 | -0.02243 | -0.1207 | -0.048065 | 0.054932 | 0.21973 | 0.045776 | 0.30212 | 0.28381 | 0.009155 | 0.073242 | 122.8043 | 122.4564 | 0.36163
10167.4219 | 0.061035 | 0.20828 | -0.21255 | -0.24353 | -0.083313 | -0.24674 | -0.048065 | 0.059509 | -0.045776 | 0.013733 | 0.022888 | 0.14191 | -0.013733 | 0.1236 | 0.045776 | 0.10254 | -0.24887 | -0.013885 | -0.10254 | -0.053406 | 0.041199 | 0.10986 | -0.027466 | 0.30212 | 0.30212 | 0.022888 | 0.068665 | 122.9645 | 122.3923 | 0.31128
10169.125 | 0.045776 | 0.22537 | -0.22858 | -0.24353 | -0.092926 | -0.26916 | -0.045929 | 0.09613 | 0.082397 | 0.10986 | 0.073242 | 0.11444 | -0.032043 | 0.10071 | 0.061035 | 0.079041 | -0.27023 | -0.020294 | -0.11215 | -0.046997 | 0.036621 | 0.20599 | 0.022888 | 0.31128 | 0.3067 | 0 | 0.07782 | 122.8043 | 122.4335 | 0.37537
10170.9062 | 0.061035 | 0.23605 | -0.21896 | -0.24033 | -0.087585 | -0.28198 | -0.060883 | 0.13275 | 0.12817 | 0.15564 | 0.10986 | 0.09613 | -0.045776 | 0.086975 | 0.045776 | 0.076904 | -0.25314 | -0.035248 | -0.10681 | -0.042725 | 0.11444 | 0.27008 | 0.10986 | 0.29297 | 0.2655 | 0.009155 | 0.050354 | 122.8592 | 122.4289 | 0.36163
10172.6406 | 0.045776 | 0.20081 | -0.21362 | -0.24139 | -0.091858 | -0.25101 | -0.043793 | 0.068665 | -0.054932 | -0.009155 | 0.032043 | 0.12817 | 0 | 0.12817 | 0.061035 | 0.10361 | -0.25101 | -0.02243 | -0.11215 | -0.048065 | -0.022888 | 0.13275 | -0.041199 | 0.32044 | 0.31128 | 0.032043 | 0.10071 | 122.9141 | 122.406 | 0.32044
10174.4219 | 0.076294 | 0.24033 | -0.21042 | -0.24033 | -0.095062 | -0.28412 | -0.066223 | 0.050354 | 0.041199 | 0.086975 | 0.068665 | 0.10529 | -0.050354 | 0.07782 | 0.045776 | 0.071564 | -0.24994 | -0.029907 | -0.11749 | -0.037384 | 0.059509 | 0.19684 | 0.073242 | 0.28381 | 0.25635 | -0.009155 | 0.064087 | 122.8455 | 122.4243 | 0.36163
10176.2031 | 0.045776 | 0.23071 | -0.2211 | -0.24033 | -0.10147 | -0.27344 | -0.055542 | 0.14191 | 0.11902 | 0.14648 | 0.09613 | 0.09613 | -0.027466 | 0.073242 | 0.061035 | 0.068359 | -0.25955 | -0.027771 | -0.11429 | -0.045929 | 0.10071 | 0.27466 | 0.10529 | 0.28381 | 0.28839 | -0.022888 | 0.059509 | 122.8409 | 122.4518 | 0.35248
10178.0156 | 0.030518 | 0.22003 | -0.1976 | -0.22644 | -0.10254 | -0.23178 | -0.036316 | 0.13733 | 0.009155 | 0.045776 | 0.050354 | 0.1236 | -0.022888 | 0.091553 | 0.045776 | 0.10147 | -0.26382 | -0.007477 | -0.092926 | -0.055542 | 0.018311 | 0.12817 | -0.050354 | 0.31128 | 0.30212 | 0.032043 | 0.091553 | 122.9095 | 122.406 | 0.32501
10179.7344 | 0.045776 | 0.21896 | -0.19974 | -0.23605 | -0.09079 | -0.23498 | -0.05127 | 0.068665 | -0.036621 | 0.013733 | 0.018311 | 0.13275 | -0.009155 | 0.12817 | 0.045776 | 0.097198 | -0.26703 | -0.019226 | -0.088654 | -0.038452 | -0.022888 | 0.086975 | -0.07782 | 0.31586 | 0.29755 | 0.018311 | 0.091553 | 122.8912 | 122.4335 | 0.32501
10181.4531 | 0.076294 | 0.23498 | -0.21362 | -0.2446 | -0.10468 | -0.28625 | -0.049133 | 0.082397 | 0.054932 | 0.09613 | 0.041199 | 0.082397 | -0.036621 | 0.086975 | 0.061035 | 0.077972 | -0.25101 | -0.029907 | -0.1239 | -0.042725 | 0.073242 | 0.17395 | 0.045776 | 0.27466 | 0.25635 | -0.004578 | 0.045776 | 122.8134 | 122.4701 | 0.37994
10183.2344 | 0.076294 | 0.2211 | -0.20721 | -0.24139 | -0.093994 | -0.24674 | -0.040588 | 0.1236 | 0.004578 | 0.036621 | 0.050354 | 0.11444 | -0.036621 | 0.10986 | 0.045776 | 0.092926 | -0.24353 | -0.014954 | -0.09613 | -0.058746 | 0.013733 | 0.15564 | -0.022888 | 0.32044 | 0.28839 | 0.022888 | 0.09613 | 122.8958 | 122.4472 | 0.31128
10185.0312 | 0.061035 | 0.21576 | -0.20081 | -0.24246 | -0.1004 | -0.24246 | -0.036316 | 0.11444 | 0.004578 | 0.041199 | 0.050354 | 0.11444 | -0.027466 | 0.10986 | 0.030518 | 0.1004 | -0.24353 | -0.014954 | -0.099335 | -0.046997 | 0.022888 | 0.16479 | 0 | 0.28381 | 0.29755 | 0.013733 | 0.082397 | 122.905 | 122.4289 | 0.31586
10186.8125 | 0.061035 | 0.26062 | -0.20828 | -0.24139 | -0.098267 | -0.29694 | -0.057678 | 0.10071 | 0.059509 | 0.10986 | 0.059509 | 0.07782 | -0.036621 | 0.082397 | 0.045776 | 0.081177 | -0.26703 | -0.020294 | -0.12711 | -0.041656 | 0.059509 | 0.17853 | 0.064087 | 0.28381 | 0.2655 | 0.004578 | 0.068665 | 122.8226 | 122.4701 | 0.33875
10188.5938 | 0.061035 | 0.21683 | -0.21469 | -0.23819 | -0.09613 | -0.24994 | -0.03952 | 0.10986 | 0 | 0.027466 | 0.041199 | 0.11444 | -0.013733 | 0.11444 | 0.076294 | 0.092926 | -0.25314 | -0.018158 | -0.10254 | -0.05127 | 0.009155 | 0.10986 | -0.027466 | 0.30212 | 0.28839 | 0.027466 | 0.082397 | 122.9095 | 122.4197 | 0.32044
10190.3438 | 0.061035 | 0.22964 | -0.21469 | -0.22751 | -0.09613 | -0.27344 | -0.044861 | 0.12817 | 0.082397 | 0.1236 | 0.09613 | 0.082397 | -0.050354 | 0.086975 | 0.061035 | 0.077972 | -0.2681 | -0.023499 | -0.093994 | -0.032043 | 0.10529 | 0.21057 | 0.07782 | 0.25635 | 0.23804 | -0.009155 | 0.064087 | 122.9233 | 122.438 | 0.31128
10192.125 | 0.045776 | 0.20721 | -0.21255 | -0.22964 | -0.10254 | -0.25955 | -0.05661 | 0.054932 | -0.050354 | -0.004578 | 0.027466 | 0.1236 | -0.027466 | 0.11902 | 0.076294 | 0.091858 | -0.26382 | -0.004272 | -0.095062 | -0.035248 | 0.004578 | 0.082397 | -0.009155 | 0.3067 | 0.29297 | 0.032043 | 0.091553 | 122.9645 | 122.4106 | 0.29755
10193.8906 | 0.076294 | 0.23819 | -0.2179 | -0.23071 | -0.10681 | -0.28198 | -0.05661 | 0.12817 | 0.054932 | 0.11444 | 0.07782 | 0.086975 | -0.036621 | 0.086975 | 0.061035 | 0.069427 | -0.2713 | -0.021362 | -0.11429 | -0.035248 | 0.073242 | 0.18768 | 0.054932 | 0.28381 | 0.2655 | -0.004578 | 0.064087 | 122.8226 | 122.4701 | 0.36163
10195.6719 | 0.045776 | 0.22964 | -0.20935 | -0.24887 | -0.098267 | -0.25742 | -0.043793 | 0.14191 | 0.050354 | 0.13733 | 0.10529 | 0.10071 | -0.068665 | 0.073242 | 0.045776 | 0.082245 | -0.2446 | -0.023499 | -0.11749 | -0.048065 | 0.10529 | 0.20599 | 0.091553 | 0.26093 | 0.26093 | -0.027466 | 0.068665 | 122.9187 | 122.4655 | 0.3067
10197.3906 | 0.076294 | 0.24353 | -0.20935 | -0.24674 | -0.11215 | -0.27878 | -0.061951 | 0.07782 | 0.013733 | 0.091553 | 0.064087 | 0.086975 | -0.027466 | 0.09613 | 0.061035 | 0.067291 | -0.25421 | -0.029907 | -0.12176 | -0.040588 | 0.045776 | 0.16022 | 0.041199 | 0.27466 | 0.26093 | 0.009155 | 0.064087 | 122.8317 | 122.4792 | 0.3479
10199.1562 | 0.045776 | 0.24353 | -0.2179 | -0.24887 | -0.11643 | -0.27771 | -0.068359 | 0.086975 | 0.027466 | 0.10071 | 0.054932 | 0.10986 | -0.045776 | 0.068665 | 0.045776 | 0.081177 | -0.25955 | -0.02243 | -0.11429 | -0.03952 | 0.068665 | 0.19226 | 0.07782 | 0.25177 | 0.26093 | 0 | 0.064087 | 122.8638 | 122.4701 | 0.35706
10200.9375 | 0.061035 | 0.22751 | -0.22217 | -0.22324 | -0.095062 | -0.25742 | -0.044861 | 0.16022 | 0.036621 | 0.09613 | 0.07782 | 0.09613 | -0.07782 | 0.068665 | 0.030518 | 0.097198 | -0.26382 | -0.026703 | -0.083313 | -0.05127 | 0.091553 | 0.18768 | 0.059509 | 0.26093 | 0.23804 | 0.004578 | 0.045776 | 122.9416 | 122.4609 | 0.31586
10202.7344 | 0.061035 | 0.21896 | -0.21469 | -0.2446 | -0.098267 | -0.25635 | -0.043793 | 0.054932 | -0.064087 | -0.013733 | 0.018311 | 0.15106 | -0.004578 | 0.11902 | 0.076294 | 0.087585 | -0.24674 | -0.029907 | -0.10468 | -0.046997 | -0.018311 | 0.11902 | -0.050354 | 0.31586 | 0.28381 | 0.041199 | 0.10986 | 122.9233 | 122.438 | 0.30212
10204.4531 | 0.045776 | 0.20828 | -0.20294 | -0.25101 | -0.083313 | -0.23498 | -0.044861 | 0.12817 | 0.018311 | 0.045776 | 0.050354 | 0.12817 | -0.018311 | 0.10529 | 0.061035 | 0.10361 | -0.23605 | -0.013885 | -0.098267 | -0.048065 | 0.050354 | 0.14648 | -0.018311 | 0.30212 | 0.27466 | 0.018311 | 0.10529 | 122.9187 | 122.4564 | 0.29755
10206.2344 | 0.045776 | 0.24353 | -0.22537 | -0.24353 | -0.10574 | -0.28305 | -0.060883 | 0.082397 | 0.022888 | 0.091553 | 0.041199 | 0.09613 | -0.050354 | 0.086975 | 0.061035 | 0.063019 | -0.25742 | -0.026703 | -0.11856 | -0.038452 | 0.032043 | 0.14191 | 0.045776 | 0.26093 | 0.2655 | -0.009155 | 0.059509 | 122.8134 | 122.5021 | 0.34332
10207.9688 | 0.061035 | 0.22858 | -0.21576 | -0.22537 | -0.091858 | -0.25528 | -0.05127 | 0.10986 | -0.004578 | 0.059509 | 0.041199 | 0.11444 | -0.050354 | 0.09613 | 0.045776 | 0.091858 | -0.25635 | -0.019226 | -0.098267 | -0.046997 | 0.068665 | 0.19226 | 0.036621 | 0.2655 | 0.24719 | 0.004578 | 0.073242 | 122.9416 | 122.4289 | 0.3067
10209.75 | 0.045776 | 0.21469 | -0.20508 | -0.25955 | -0.098267 | -0.25421 | -0.044861 | 0.045776 | -0.041199 | 0.009155 | 0.018311 | 0.14648 | -0.009155 | 0.11902 | 0.045776 | 0.09613 | -0.2478 | -0.028839 | -0.11322 | -0.046997 | -0.036621 | 0.11444 | -0.045776 | 0.30212 | 0.28839 | 0.018311 | 0.10071 | 122.9279 | 122.4426 | 0.31128
10211.4688 | 0.061035 | 0.22644 | -0.21576 | -0.2446 | -0.10681 | -0.29907 | -0.050201 | 0.12817 | 0.091553 | 0.13275 | 0.09613 | 0.091553 | -0.032043 | 0.091553 | 0.045776 | 0.072632 | -0.25101 | -0.024567 | -0.11963 | -0.035248 | 0.11444 | 0.25177 | 0.11444 | 0.24719 | 0.24261 | 0 | 0.064087 | 122.8821 | 122.4701 | 0.32501
10213.2656 | 0.030518 | 0.23178 | -0.20721 | -0.24674 | -0.10147 | -0.2713 | -0.038452 | 0.13275 | 0.064087 | 0.11444 | 0.07782 | 0.086975 | -0.064087 | 0.064087 | 0.045776 | 0.088654 | -0.24674 | -0.027771 | -0.11322 | -0.03952 | 0.091553 | 0.17853 | 0.059509 | 0.26093 | 0.26093 | -0.018311 | 0.082397 | 122.8226 | 122.5159 | 0.33875
10215.0625 | 0.045776 | 0.21362 | -0.20721 | -0.2243 | -0.085449 | -0.24353 | -0.046997 | 0.12817 | 0.009155 | 0.036621 | 0.054932 | 0.1236 | -0.022888 | 0.10529 | 0.061035 | 0.10361 | -0.24674 | -0.02243 | -0.099335 | -0.060883 | 0.022888 | 0.12817 | -0.027466 | 0.27924 | 0.25177 | 0.022888 | 0.09613 | 122.9187 | 122.4976 | 0.3067
10216.7812 | 0.045776 | 0.22751 | -0.22003 | -0.2446 | -0.10254 | -0.28091 | -0.054474 | 0.12817 | 0.11902 | 0.15106 | 0.09613 | 0.09613 | -0.041199 | 0.073242 | 0.045776 | 0.071564 | -0.25635 | -0.026703 | -0.11002 | -0.048065 | 0.082397 | 0.26093 | 0.10529 | 0.25177 | 0.24261 | -0.013733 | 0.059509 | 122.85 | 122.4747 | 0.33417
10218.5625 | 0.076294 | 0.23071 | -0.2179 | -0.23712 | -0.1004 | -0.29053 | -0.049133 | 0.14191 | 0.13275 | 0.16022 | 0.11902 | 0.09613 | -0.050354 | 0.082397 | 0.061035 | 0.080109 | -0.25955 | -0.032043 | -0.12176 | -0.048065 | 0.10071 | 0.25635 | 0.09613 | 0.24261 | 0.24719 | -0.004578 | 0.064087 | 122.8683 | 122.4976 | 0.32044
10220.3594 | 0.076294 | 0.21469 | -0.21042 | -0.22644 | -0.098267 | -0.23285 | -0.041656 | 0.11902 | 0.013733 | 0.041199 | 0.045776 | 0.1236 | -0.009155 | 0.12817 | 0.061035 | 0.097198 | -0.26596 | -0.02243 | -0.093994 | -0.054474 | 0.036621 | 0.16022 | -0.009155 | 0.28381 | 0.27008 | 0.027466 | 0.086975 | 122.9553 | 122.4518 | 0.27924
10222.1406 | 0.061035 | 0.25421 | -0.21042 | -0.23285 | -0.093994 | -0.28732 | -0.052338 | 0.059509 | 0.013733 | 0.082397 | 0.068665 | 0.086975 | -0.032043 | 0.09613 | 0.045776 | 0.074768 | -0.26276 | -0.033112 | -0.11856 | -0.029907 | 0.050354 | 0.19226 | 0.050354 | 0.25635 | 0.25635 | 0.009155 | 0.068665 | 122.8683 | 122.493 | 0.32959
10223.9375 | 0.061035 | 0.23071 | -0.2243 | -0.26169 | -0.098267 | -0.28198 | -0.053406 | 0.10986 | 0.059509 | 0.11444 | 0.082397 | 0.10071 | -0.045776 | 0.086975 | 0.045776 | 0.070496 | -0.24994 | -0.023499 | -0.12711 | -0.043793 | 0.086975 | 0.23804 | 0.11444 | 0.25177 | 0.23804 | 0 | 0.073242 | 122.8775 | 122.4884 | 0.32959
10225.6562 | 0.061035 | 0.23178 | -0.20935 | -0.22217 | -0.095062 | -0.25207 | -0.044861 | 0.14648 | 0.045776 | 0.10071 | 0.059509 | 0.082397 | -0.041199 | 0.064087 | 0.045776 | 0.09079 | -0.24887 | -0.018158 | -0.1004 | -0.05127 | 0.10529 | 0.19684 | 0.068665 | 0.25177 | 0.2243 | -0.004578 | 0.059509 | 122.9691 | 122.4655 | 0.32044
10227.4375 | 0.061035 | 0.21362 | -0.21255 | -0.24246 | -0.09613 | -0.23392 | -0.043793 | 0.054932 | -0.082397 | -0.022888 | 0.022888 | 0.13275 | -0.032043 | 0.12817 | 0.061035 | 0.088654 | -0.2446 | -0.021362 | -0.088654 | -0.050201 | -0.022888 | 0.073242 | -0.068665 | 0.29297 | 0.28839 | 0.036621 | 0.10529 | 122.9233 | 122.4701 | 0.31128
10229.2188 | 0.061035 | 0.20828 | -0.20187 | -0.24674 | -0.097198 | -0.24353 | -0.041656 | 0.086975 | 0.022888 | 0.054932 | 0.054932 | 0.1236 | -0.013733 | 0.13733 | 0.061035 | 0.10254 | -0.24567 | -0.013885 | -0.098267 | -0.042725 | 0.045776 | 0.16937 | -0.018311 | 0.27924 | 0.27008 | 0.032043 | 0.09613 | 122.9553 | 122.4655 | 0.29297
10230.9375 | 0.076294 | 0.22324 | -0.20508 | -0.22537 | -0.099335 | -0.24139 | -0.046997 | 0.027466 | -0.041199 | 0 | 0 | 0.14191 | -0.004578 | 0.10986 | 0.045776 | 0.09079 | -0.25314 | -0.013885 | -0.1004 | -0.038452 | -0.045776 | 0.07782 | -0.082397 | 0.27466 | 0.28381 | 0.032043 | 0.10529 | 122.9187 | 122.4747 | 0.29297
10232.7188 | 0.045776 | 0.23819 | -0.20615 | -0.25101 | -0.10147 | -0.28519 | -0.042725 | 0.09613 | 0.10071 | 0.1236 | 0.068665 | 0.086975 | -0.050354 | 0.064087 | 0.061035 | 0.077972 | -0.25421 | -0.019226 | -0.1239 | -0.038452 | 0.10071 | 0.21057 | 0.07782 | 0.23346 | 0.21973 | -0.013733 | 0.059509 | 122.85 | 122.4884 | 0.31128
10234.5 | 0.061035 | 0.23285 | -0.22217 | -0.2446 | -0.10254 | -0.28625 | -0.049133 | 0.11444 | 0.1236 | 0.13733 | 0.10986 | 0.086975 | -0.027466 | 0.073242 | 0.045776 | 0.070496 | -0.25528 | -0.036316 | -0.12283 | -0.046997 | 0.086975 | 0.2655 | 0.10529 | 0.24261 | 0.25635 | -0.018311 | 0.068665 | 122.8775 | 122.4747 | 0.32501
10236.2812 | 0.061035 | 0.2211 | -0.21042 | -0.22751 | -0.10895 | -0.23498 | -0.055542 | 0.064087 | -0.064087 | -0.009155 | 0.018311 | 0.13733 | -0.018311 | 0.11902 | 0.061035 | 0.099335 | -0.25635 | -0.012817 | -0.088654 | -0.041656 | -0.027466 | 0.059509 | -0.082397 | 0.29755 | 0.28839 | 0.027466 | 0.10986 | 122.9187 | 122.4838 | 0.31128
10238.0156 | 0.045776 | 0.22964 | -0.22003 | -0.25421 | -0.11002 | -0.30334 | -0.064087 | 0.10071 | 0.045776 | 0.10986 | 0.082397 | 0.10529 | -0.054932 | 0.064087 | 0.076294 | 0.076904 | -0.24567 | -0.030975 | -0.1239 | -0.038452 | 0.086975 | 0.21515 | 0.10071 | 0.25635 | 0.2655 | 0.013733 | 0.059509 | 122.8546 | 122.4701 | 0.31128
10239.7969 | 0.061035 | 0.20935 | -0.21362 | -0.22858 | -0.098267 | -0.24674 | -0.061951 | 0.09613 | 0.009155 | 0.041199 | 0.050354 | 0.13275 | -0.022888 | 0.13733 | 0.061035 | 0.1004 | -0.24994 | -0.018158 | -0.098267 | -0.041656 | 0.032043 | 0.16479 | -0.009155 | 0.28381 | 0.26093 | 0.041199 | 0.082397 | 122.9507 | 122.4289 | 0.29755
10241.5 | 0.061035 | 0.23498 | -0.21683 | -0.22858 | -0.093994 | -0.26596 | -0.044861 | 0.1236 | 0.073242 | 0.13275 | 0.091553 | 0.082397 | -0.041199 | 0.082397 | 0.030518 | 0.085449 | -0.25742 | -0.025635 | -0.11322 | -0.044861 | 0.10071 | 0.21973 | 0.091553 | 0.25635 | 0.24719 | -0.004578 | 0.064087 | 122.937 | 122.4838 | 0.30212
10243.2812 | 0.045776 | 0.21149 | -0.21042 | -0.23605 | -0.1004 | -0.24674 | -0.052338 | 0.027466 | -0.11902 | -0.027466 | -0.009155 | 0.14191 | -0.004578 | 0.12817 | 0.061035 | 0.10147 | -0.23712 | -0.02243 | -0.099335 | -0.036316 | -0.018311 | 0.054932 | -0.064087 | 0.28839 | 0.28839 | 0.032043 | 0.091553 | 122.9462 | 122.4655 | 0.31128
10245.0625 | 0.045776 | 0.2179 | -0.21255 | -0.22537 | -0.095062 | -0.25742 | -0.045929 | 0.073242 | -0.027466 | 0.027466 | 0.022888 | 0.14648 | -0.027466 | 0.11444 | 0.061035 | 0.09079 | -0.24033 | -0.009613 | -0.091858 | -0.042725 | -0.022888 | 0.09613 | -0.068665 | 0.29755 | 0.25635 | 0.036621 | 0.10071 | 122.9095 | 122.5113 | 0.30212
10246.7812 | 0.061035 | 0.20401 | -0.20401 | -0.25848 | -0.10147 | -0.26489 | -0.046997 | 0.041199 | -0.041199 | 0.004578 | 0.032043 | 0.13733 | -0.018311 | 0.1236 | 0.030518 | 0.09613 | -0.24246 | -0.018158 | -0.10788 | -0.048065 | 0.009155 | 0.13733 | -0.022888 | 0.27466 | 0.27924 | 0.032043 | 0.09613 | 122.9645 | 122.4564 | 0.2655
10248.5469 | 0.030518 | 0.22858 | -0.21469 | -0.23819 | -0.10361 | -0.2478 | -0.048065 | 0.059509 | -0.032043 | 0.036621 | 0.018311 | 0.14191 | -0.018311 | 0.11444 | 0.030518 | 0.070496 | -0.24674 | -0.018158 | -0.1004 | -0.038452 | 0.022888 | 0.13733 | 0.009155 | 0.27008 | 0.24719 | 0.013733 | 0.07782 | 123.0011 | 122.4884 | 0.28839
10250.3281 | 0.061035 | 0.23498 | -0.22324 | -0.23285 | -0.09613 | -0.298 | -0.061951 | 0.050354 | 0.018311 | 0.082397 | 0.054932 | 0.09613 | -0.041199 | 0.091553 | 0.076294 | 0.068359 | -0.24994 | -0.036316 | -0.12817 | -0.037384 | 0.022888 | 0.17395 | 0.059509 | 0.25177 | 0.24719 | 0.009155 | 0.086975 | 122.8867 | 122.525 | 0.33417
10252.0469 | 0.076294 | 0.23285 | -0.20828 | -0.23178 | -0.095062 | -0.25848 | -0.05127 | 0.1236 | 0.059509 | 0.10071 | 0.07782 | 0.10986 | -0.073242 | 0.073242 | 0.045776 | 0.083313 | -0.24246 | -0.027771 | -0.1004 | -0.05127 | 0.082397 | 0.1831 | 0.068665 | 0.24261 | 0.2243 | -0.032043 | 0.064087 | 122.9462 | 122.4792 | 0.29755
10253.8438 | 0.076294 | 0.20721 | -0.20187 | -0.23392 | -0.085449 | -0.24994 | -0.042725 | 0.009155 | -0.091553 | -0.018311 | 0 | 0.12817 | -0.027466 | 0.11444 | 0.091553 | 0.10254 | -0.24674 | -0.025635 | -0.09079 | -0.048065 | -0.022888 | 0.059509 | -0.064087 | 0.27466 | 0.27466 | 0.027466 | 0.086975 | 122.9416 | 122.4701 | 0.28381
10255.625 | 0.061035 | 0.23392 | -0.20828 | -0.22537 | -0.10468 | -0.26703 | -0.044861 | 0.09613 | 0.054932 | 0.10986 | 0.09613 | 0.09613 | -0.054932 | 0.091553 | 0.061035 | 0.075836 | -0.25314 | -0.023499 | -0.10361 | -0.038452 | 0.10071 | 0.17853 | 0.073242 | 0.21973 | 0.21515 | -0.004578 | 0.050354 | 122.9553 | 122.493 | 0.27924
10257.3594 | 0.061035 | 0.22537 | -0.20935 | -0.24353 | -0.10468 | -0.27237 | -0.045929 | 0.11444 | 0.07782 | 0.13733 | 0.09613 | 0.086975 | -0.059509 | 0.082397 | 0.030518 | 0.076904 | -0.24246 | -0.013885 | -0.11108 | -0.050201 | 0.086975 | 0.21057 | 0.082397 | 0.22888 | 0.2243 | -0.004578 | 0.059509 | 122.85 | 122.5159 | 0.32501
10259.1406 | 0.045776 | 0.21576 | -0.21149 | -0.26169 | -0.088654 | -0.27557 | -0.05661 | 0.022888 | 0 | 0.032043 | 0.013733 | 0.14191 | -0.009155 | 0.11902 | 0.045776 | 0.076904 | -0.24033 | -0.028839 | -0.11429 | -0.046997 | -0.022888 | 0.11444 | -0.027466 | 0.28381 | 0.27924 | 0.032043 | 0.13733 | 122.8592 | 122.5113 | 0.3067
10260.9219 | 0.061035 | 0.25207 | -0.21149 | -0.23926 | -0.095062 | -0.29053 | -0.058746 | 0.073242 | 0.045776 | 0.068665 | 0.059509 | 0.086975 | -0.041199 | 0.068665 | 0.061035 | 0.083313 | -0.25955 | -0.032043 | -0.12283 | -0.044861 | 0.054932 | 0.16022 | 0.045776 | 0.22888 | 0.23346 | 0.018311 | 0.07782 | 122.8363 | 122.5296 | 0.32501
10262.6406 | 0.061035 | 0.21042 | -0.20187 | -0.23285 | -0.099335 | -0.23498 | -0.045929 | 0.10071 | 0.013733 | 0.036621 | 0.036621 | 0.13275 | -0.018311 | 0.12817 | 0.061035 | 0.099335 | -0.26062 | -0.019226 | -0.09613 | -0.055542 | 0.013733 | 0.10529 | -0.036621 | 0.25177 | 0.25635 | 0.032043 | 0.10071 | 122.9141 | 122.5113 | 0.28381
10264.4375 | 0.045776 | 0.23605 | -0.21469 | -0.22858 | -0.099335 | -0.27664 | -0.045929 | 0.12817 | 0.082397 | 0.13733 | 0.091553 | 0.082397 | -0.054932 | 0.073242 | 0.061035 | 0.074768 | -0.25955 | -0.030975 | -0.11002 | -0.03952 | 0.09613 | 0.2243 | 0.064087 | 0.23346 | 0.21973 | -0.018311 | 0.050354 | 122.8912 | 122.4976 | 0.29297
10266.1562 | 0.061035 | 0.21896 | -0.20935 | -0.22751 | -0.10788 | -0.25207 | -0.050201 | 0.11444 | 0.027466 | 0.050354 | 0.050354 | 0.12817 | -0.027466 | 0.11444 | 0.061035 | 0.093994 | -0.25101 | -0.029907 | -0.09613 | -0.052338 | 0.045776 | 0.15564 | -0.009155 | 0.25177 | 0.24261 | 0.013733 | 0.086975 | 122.9279 | 122.4747 | 0.27008
10267.9531 | 0.076294 | 0.20721 | -0.21042 | -0.22751 | -0.10574 | -0.25635 | -0.036316 | 0.036621 | -0.07782 | -0.004578 | 0.009155 | 0.11902 | -0.013733 | 0.13275 | 0.045776 | 0.084381 | -0.25528 | -0.016022 | -0.089722 | -0.040588 | -0.050354 | 0.045776 | -0.07782 | 0.28381 | 0.24719 | 0.018311 | 0.10071 | 122.9233 | 122.493 | 0.28381
10269.7344 | 0.061035 | 0.20935 | -0.20081 | -0.24033 | -0.097198 | -0.26489 | -0.041656 | 0.045776 | -0.032043 | -0.004578 | 0.018311 | 0.12817 | -0.009155 | 0.09613 | 0.076294 | 0.093994 | -0.2478 | -0.027771 | -0.097198 | -0.03418 | 0.045776 | 0.10986 | -0.004578 | 0.25635 | 0.23346 | 0.022888 | 0.073242 | 122.9874 | 122.4747 | 0.27924
10271.4688 | 0.076294 | 0.22858 | -0.20721 | -0.24674 | -0.10895 | -0.27023 | -0.044861 | 0.027466 | -0.036621 | 0.009155 | 0.013733 | 0.13733 | -0.018311 | 0.13733 | 0.045776 | 0.084381 | -0.23712 | -0.027771 | -0.11749 | -0.044861 | -0.045776 | 0.10071 | -0.036621 | 0.27466 | 0.24719 | 0.032043 | 0.09613 | 122.8867 | 122.5204 | 0.31128
10273.25 | 0.076294 | 0.22858 | -0.20615 | -0.23926 | -0.093994 | -0.27344 | -0.038452 | 0.11444 | 0.045776 | 0.10986 | 0.068665 | 0.09613 | -0.041199 | 0.10071 | 0.045776 | 0.077972 | -0.24246 | -0.030975 | -0.11215 | -0.046997 | 0.07782 | 0.19684 | 0.068665 | 0.21973 | 0.19684 | -0.013733 | 0.073242 | 122.9691 | 122.5021 | 0.26093
10275.0312 | 0.045776 | 0.21683 | -0.20508 | -0.24246 | -0.09613 | -0.24567 | -0.049133 | 0.082397 | 0.004578 | 0.032043 | 0.064087 | 0.13275 | -0.022888 | 0.11902 | 0.061035 | 0.084381 | -0.24567 | -0.014954 | -0.098267 | -0.046997 | 0.009155 | 0.1236 | -0.036621 | 0.26093 | 0.23346 | 0.032043 | 0.091553 | 122.9279 | 122.525 | 0.2655
10276.7344 | 0.061035 | 0.22964 | -0.2179 | -0.23498 | -0.097198 | -0.26596 | -0.042725 | 0.068665 | -0.018311 | 0.036621 | 0.027466 | 0.1236 | -0.041199 | 0.11444 | 0.061035 | 0.092926 | -0.25955 | -0.011749 | -0.09613 | -0.042725 | 0.050354 | 0.14648 | 0.032043 | 0.23804 | 0.23804 | -0.009155 | 0.07782 | 122.9828 | 122.4884 | 0.29297
10278.5312 | 0.030518 | 0.23605 | -0.19867 | -0.25421 | -0.098267 | -0.28091 | -0.045929 | 0.10071 | 0.07782 | 0.13275 | 0.073242 | 0.086975 | -0.050354 | 0.073242 | 0.061035 | 0.072632 | -0.2446 | -0.021362 | -0.1207 | -0.042725 | 0.07782 | 0.17853 | 0.064087 | 0.2243 | 0.21515 | 0.009155 | 0.073242 | 122.8455 | 122.5296 | 0.32044
10280.2656 | 0.061035 | 0.2243 | -0.21362 | -0.22537 | -0.10468 | -0.25955 | -0.055542 | 0.036621 | -0.082397 | -0.027466 | 0.009155 | 0.1236 | -0.013733 | 0.11902 | 0.061035 | 0.10147 | -0.25635 | -0.013885 | -0.092926 | -0.043793 | -0.022888 | 0.050354 | -0.064087 | 0.2655 | 0.25635 | 0.036621 | 0.07782 | 122.9599 | 122.5159 | 0.27466
10282.0312 | 0.076294 | 0.20828 | -0.19974 | -0.25314 | -0.10681 | -0.25101 | -0.050201 | 0.045776 | -0.027466 | 0.022888 | 0.045776 | 0.12817 | -0.018311 | 0.10986 | 0.061035 | 0.10147 | -0.23392 | -0.025635 | -0.10895 | -0.050201 | 0.013733 | 0.14191 | -0.013733 | 0.25177 | 0.24719 | 0.032043 | 0.09613 | 122.9645 | 122.493 | 0.26093
10283.8125 | 0.045776 | 0.24994 | -0.2243 | -0.23926 | -0.10681 | -0.29907 | -0.061951 | 0.091553 | 0.073242 | 0.12817 | 0.082397 | 0.11444 | -0.036621 | 0.09613 | 0.061035 | 0.074768 | -0.24994 | -0.025635 | -0.11322 | -0.028839 | 0.082397 | 0.22888 | 0.10071 | 0.2243 | 0.22888 | -0.013733 | 0.064087 | 122.8912 | 122.525 | 0.3067
10285.5312 | 0.045776 | 0.22858 | -0.20828 | -0.22324 | -0.098267 | -0.25101 | -0.054474 | 0.059509 | -0.041199 | 0.009155 | 0.013733 | 0.12817 | -0.036621 | 0.12817 | 0.076294 | 0.093994 | -0.24353 | -0.02243 | -0.10468 | -0.05661 | 0.027466 | 0.10986 | -0.013733 | 0.24719 | 0.22888 | 0.013733 | 0.082397 | 123.0148 | 122.4655 | 0.25177
10287.3125 | 0.030518 | 0.22964 | -0.22324 | -0.23285 | -0.093994 | -0.27557 | -0.055542 | 0.1236 | 0.086975 | 0.13275 | 0.086975 | 0.10071 | -0.036621 | 0.091553 | 0.045776 | 0.083313 | -0.26169 | -0.028839 | -0.11002 | -0.038452 | 0.050354 | 0.22888 | 0.059509 | 0.21973 | 0.21057 | -0.009155 | 0.068665 | 122.8409 | 122.5204 | 0.3067
10289.0938 | 0.076294 | 0.23178 | -0.21576 | -0.23605 | -0.1004 | -0.27664 | -0.054474 | 0.14191 | 0.09613 | 0.13275 | 0.091553 | 0.10986 | -0.041199 | 0.082397 | 0.045776 | 0.071564 | -0.25207 | -0.018158 | -0.12283 | -0.050201 | 0.07782 | 0.24719 | 0.10071 | 0.22888 | 0.21973 | -0.009155 | 0.073242 | 122.8729 | 122.525 | 0.29755
10290.875 | 0.045776 | 0.21576 | -0.20935 | -0.23819 | -0.097198 | -0.23392 | -0.046997 | 0.11444 | 0.018311 | 0.059509 | 0.059509 | 0.14191 | -0.013733 | 0.12817 | 0.061035 | 0.099335 | -0.24674 | -0.010681 | -0.093994 | -0.054474 | 0.045776 | 0.13275 | -0.022888 | 0.25177 | 0.2243 | 0.036621 | 0.091553 | 122.9553 | 122.4838 | 0.26093
10292.6719 | 0.045776 | 0.23285 | -0.2211 | -0.25314 | -0.10361 | -0.28946 | -0.053406 | 0.07782 | 0.018311 | 0.07782 | 0.059509 | 0.086975 | -0.054932 | 0.091553 | 0.061035 | 0.074768 | -0.24887 | -0.03418 | -0.11963 | -0.042725 | 0.045776 | 0.15106 | 0.032043 | 0.22888 | 0.21057 | -0.009155 | 0.091553 | 122.8638 | 122.5525 | 0.29755
10294.4062 | 0.061035 | 0.22003 | -0.20508 | -0.21683 | -0.097198 | -0.24246 | -0.057678 | 0.045776 | -0.09613 | -0.018311 | 0.004578 | 0.14191 | -0.032043 | 0.11902 | 0.045776 | 0.1004 | -0.25207 | -0.021362 | -0.098267 | -0.049133 | -0.032043 | 0.036621 | -0.086975 | 0.24261 | 0.24261 | 0.022888 | 0.10529 | 122.9416 | 122.5342 | 0.27008
10296.1719 | 0.045776 | 0.25314 | -0.21469 | -0.23498 | -0.10468 | -0.26703 | -0.038452 | 0.13733 | 0.086975 | 0.13275 | 0.07782 | 0.091553 | -0.045776 | 0.07782 | 0.030518 | 0.0737 | -0.2446 | -0.032043 | -0.10788 | -0.03952 | 0.086975 | 0.20599 | 0.068665 | 0.19226 | 0.20142 | -0.004578 | 0.064087 | 122.8729 | 122.5525 | 0.28839
10297.9688 | 0.061035 | 0.21255 | -0.20294 | -0.25421 | -0.099335 | -0.2446 | -0.043793 | 0.10071 | 0 | 0.041199 | 0.041199 | 0.13733 | -0.018311 | 0.11444 | 0.045776 | 0.10147 | -0.23712 | -0.016022 | -0.093994 | -0.048065 | 0.041199 | 0.15564 | -0.022888 | 0.25177 | 0.21973 | 0.018311 | 0.10529 | 122.9553 | 122.5021 | 0.26093
10299.6875 | 0.076294 | 0.2243 | -0.19226 | -0.23285 | -0.1004 | -0.24353 | -0.037384 | 0.027466 | -0.054932 | 0.009155 | 0.004578 | 0.13275 | -0.022888 | 0.12817 | 0.045776 | 0.093994 | -0.2446 | -0.018158 | -0.10361 | -0.050201 | -0.041199 | 0.059509 | -0.07782 | 0.2655 | 0.23346 | 0.036621 | 0.10986 | 122.9279 | 122.5296 | 0.2655
10301.4688 | 0.061035 | 0.22324 | -0.21469 | -0.23605 | -0.09079 | -0.25742 | -0.041656 | 0.045776 | -0.032043 | 0.022888 | 0.027466 | 0.13733 | -0.009155 | 0.11902 | 0.045776 | 0.079041 | -0.24994 | -0.013885 | -0.09079 | -0.033112 | 0.032043 | 0.13275 | 0.004578 | 0.23804 | 0.23346 | 0.013733 | 0.091553 | 123.0148 | 122.5159 | 0.24261
10303.25 | 0.061035 | 0.23178 | -0.20508 | -0.22858 | -0.099335 | -0.28412 | -0.048065 | 0.091553 | 0.050354 | 0.10071 | 0.059509 | 0.09613 | -0.036621 | 0.082397 | 0.061035 | 0.0737 | -0.24887 | -0.030975 | -0.11856 | -0.032043 | 0.054932 | 0.16937 | 0.027466 | 0.21515 | 0.21515 | 0.009155 | 0.07782 | 122.8409 | 122.5616 | 0.29297
10304.9844 | 0.076294 | 0.23285 | -0.19333 | -0.23498 | -0.10361 | -0.24353 | -0.03952 | 0.064087 | -0.059509 | 0.013733 | 0.032043 | 0.1236 | -0.013733 | 0.10529 | 0.076294 | 0.10361 | -0.23926 | -0.013885 | -0.10147 | -0.049133 | -0.018311 | 0.082397 | -0.07782 | 0.25177 | 0.22888 | 0.027466 | 0.11444 | 122.9279 | 122.5571 | 0.26093
10306.75 | 0.045776 | 0.21255 | -0.20187 | -0.25421 | -0.10147 | -0.25314 | -0.049133 | 0.09613 | 0.013733 | 0.045776 | 0.050354 | 0.1236 | -0.022888 | 0.13275 | 0.045776 | 0.10147 | -0.23605 | -0.016022 | -0.092926 | -0.038452 | 0.041199 | 0.16022 | -0.032043 | 0.22888 | 0.23346 | 0.027466 | 0.086975 | 122.9416 | 122.525 | 0.24261
10308.5469 | 0.030518 | 0.26062 | -0.20615 | -0.24246 | -0.10895 | -0.2948 | -0.055542 | 0.073242 | 0.022888 | 0.086975 | 0.054932 | 0.09613 | -0.045776 | 0.082397 | 0.045776 | 0.060883 | -0.24674 | -0.027771 | -0.1207 | -0.03418 | 0.027466 | 0.15564 | 0.050354 | 0.21973 | 0.20142 | -0.013733 | 0.059509 | 122.8683 | 122.5571 | 0.28839
10310.2656 | 0.045776 | 0.1944 | -0.19226 | -0.24887 | -0.10361 | -0.23926 | -0.054474 | 0.086975 | -0.022888 | 0.027466 | 0.041199 | 0.13733 | -0.013733 | 0.10529 | 0.045776 | 0.10147 | -0.23712 | -0.007477 | -0.10574 | -0.064087 | 0 | 0.091553 | -0.050354 | 0.23346 | 0.22888 | 0.036621 | 0.10071 | 122.9279 | 122.525 | 0.27008
10312.0469 | 0.076294 | 0.26062 | -0.21896 | -0.23071 | -0.099335 | -0.29053 | -0.061951 | 0.11444 | 0.12817 | 0.14191 | 0.10529 | 0.10071 | -0.045776 | 0.09613 | 0.045776 | 0.072632 | -0.25314 | -0.016022 | -0.12711 | -0.040588 | 0.086975 | 0.24261 | 0.10986 | 0.19684 | 0.20599 | -0.004578 | 0.064087 | 122.8729 | 122.5433 | 0.29297
10313.8281 | 0.061035 | 0.2211 | -0.21042 | -0.24887 | -0.10361 | -0.27878 | -0.036316 | 0.11444 | 0.07782 | 0.1236 | 0.091553 | 0.07782 | -0.064087 | 0.09613 | 0.061035 | 0.074768 | -0.25207 | -0.02243 | -0.093994 | -0.036316 | 0.091553 | 0.20142 | 0.082397 | 0.20599 | 0.19684 | 0.004578 | 0.073242 | 122.8638 | 122.5479 | 0.31128
10315.6094 | 0.061035 | 0.22644 | -0.22751 | -0.24674 | -0.091858 | -0.28091 | -0.064087 | 0.10529 | 0.10529 | 0.15564 | 0.082397 | 0.091553 | -0.036621 | 0.091553 | 0.015259 | 0.074768 | -0.2446 | -0.019226 | -0.1207 | -0.041656 | 0.073242 | 0.25635 | 0.086975 | 0.21057 | 0.19226 | 0.004578 | 0.068665 | 122.8638 | 122.5388 | 0.29297
10317.3906 | 0.061035 | 0.20294 | -0.20294 | -0.24246 | -0.10468 | -0.24246 | -0.05127 | 0.041199 | -0.082397 | -0.013733 | 0 | 0.15564 | -0.013733 | 0.12817 | 0.061035 | 0.10254 | -0.24246 | -0.018158 | -0.10574 | -0.046997 | 0 | 0.050354 | -0.054932 | 0.24719 | 0.22888 | 0.027466 | 0.09613 | 122.9782 | 122.5342 | 0.27466
10319.1094 | 0.076294 | 0.25742 | -0.21255 | -0.22644 | -0.10895 | -0.26596 | -0.052338 | 0.11902 | 0.091553 | 0.14191 | 0.086975 | 0.086975 | -0.050354 | 0.064087 | 0.045776 | 0.077972 | -0.25528 | -0.013885 | -0.10361 | -0.03952 | 0.10986 | 0.19226 | 0.064087 | 0.21057 | 0.20142 | 0 | 0.064087 | 122.8546 | 122.5479 | 0.27924
10320.8906 | 0.061035 | 0.21576 | -0.1976 | -0.24994 | -0.091858 | -0.2446 | -0.03952 | 0.082397 | -0.027466 | 0.009155 | 0.022888 | 0.12817 | -0.009155 | 0.11444 | 0.045776 | 0.1004 | -0.24353 | -0.01709 | -0.10147 | -0.052338 | -0.022888 | 0.086975 | -0.086975 | 0.23804 | 0.23804 | 0.022888 | 0.10986 | 122.9233 | 122.5479 | 0.24719
10322.6719 | 0.045776 | 0.23178 | -0.20187 | -0.22324 | -0.09079 | -0.26596 | -0.045929 | 0.064087 | 0 | 0.059509 | 0.032043 | 0.10986 | -0.036621 | 0.091553 | 0.045776 | 0.099335 | -0.24994 | -0.029907 | -0.10147 | -0.042725 | 0.068665 | 0.16937 | 0.041199 | 0.21973 | 0.19684 | -0.009155 | 0.068665 | 122.9965 | 122.5113 | 0.24261
10324.4844 | 0.045776 | 0.23498 | -0.21469 | -0.23392 | -0.10681 | -0.27451 | -0.065155 | 0.027466 | -0.027466 | 0.004578 | 0.009155 | 0.13733 | 0.013733 | 0.1236 | 0.061035 | 0.080109 | -0.25955 | -0.027771 | -0.10681 | -0.03418 | -0.054932 | 0.09613 | -0.050354 | 0.24719 | 0.23804 | 0.050354 | 0.1236 | 122.8638 | 122.5479 | 0.27924
10326.2031 | 0.076294 | 0.23392 | -0.21576 | -0.25955 | -0.10361 | -0.28091 | -0.055542 | 0.064087 | 0.041199 | 0.09613 | 0.068665 | 0.091553 | -0.050354 | 0.086975 | 0.061035 | 0.070496 | -0.25101 | -0.02243 | -0.1207 | -0.042725 | 0.054932 | 0.19226 | 0.073242 | 0.21057 | 0.20142 | -0.004578 | 0.059509 | 122.8958 | 122.5662 | 0.30212
10328 | 0.076294 | 0.2179 | -0.20828 | -0.24994 | -0.088654 | -0.2681 | -0.044861 | 0.086975 | 0.059509 | 0.091553 | 0.07782 | 0.11902 | -0.036621 | 0.10529 | 0.091553 | 0.098267 | -0.24994 | -0.024567 | -0.11749 | -0.03418 | 0.013733 | 0.14648 | 0 | 0.2243 | 0.20142 | 0.022888 | 0.09613 | 122.8363 | 122.5662 | 0.27924
10329.7812 | 0.061035 | 0.21255 | -0.21576 | -0.23285 | -0.095062 | -0.24246 | -0.060883 | 0.09613 | 0.009155 | 0.045776 | 0.045776 | 0.11902 | -0.018311 | 0.11902 | 0.061035 | 0.10361 | -0.25421 | -0.019226 | -0.10361 | -0.057678 | 0.045776 | 0.15564 | -0.018311 | 0.24261 | 0.21973 | 0.022888 | 0.10529 | 122.9507 | 122.5159 | 0.24719
10331.5781 | 0.045776 | 0.24674 | -0.21149 | -0.22644 | -0.099335 | -0.26276 | -0.052338 | 0.14191 | 0.082397 | 0.1236 | 0.091553 | 0.086975 | -0.054932 | 0.064087 | 0.045776 | 0.079041 | -0.25742 | -0.026703 | -0.10574 | -0.03952 | 0.09613 | 0.21057 | 0.082397 | 0.20599 | 0.16937 | -0.009155 | 0.073242 | 122.9095 | 122.5388 | 0.27466
10333.3594 | 0.030518 | 0.22217 | -0.21042 | -0.23285 | -0.10361 | -0.25848 | -0.046997 | 0.032043 | -0.073242 | -0.022888 | 0.004578 | 0.16479 | -0.032043 | 0.11902 | 0.045776 | 0.09079 | -0.24033 | -0.019226 | -0.10254 | -0.05127 | -0.027466 | 0.054932 | -0.059509 | 0.25635 | 0.23346 | 0.022888 | 0.09613 | 122.9782 | 122.5296 | 0.24719
10335.1562 | 0.061035 | 0.21576 | -0.20401 | -0.22217 | -0.11856 | -0.2446 | -0.040588 | 0.018311 | -0.086975 | -0.041199 | -0.013733 | 0.13275 | -0.018311 | 0.11902 | 0.076294 | 0.080109 | -0.24353 | -0.020294 | -0.095062 | -0.042725 | -0.027466 | 0.050354 | -0.073242 | 0.25177 | 0.23346 | 0.041199 | 0.09613 | 122.9599 | 122.5342 | 0.25177
10336.9531 | 0.076294 | 0.22644 | -0.22858 | -0.25528 | -0.10574 | -0.27985 | -0.049133 | 0.027466 | -0.036621 | 0 | 0.013733 | 0.13733 | -0.013733 | 0.12817 | 0.030518 | 0.086517 | -0.25101 | -0.021362 | -0.11536 | -0.038452 | -0.032043 | 0.10071 | -0.041199 | 0.25177 | 0.23346 | 0.054932 | 0.10986 | 122.8821 | 122.5754 | 0.27924
10338.7344 | 0.076294 | 0.22324 | -0.20508 | -0.23605 | -0.10254 | -0.26489 | -0.042725 | 0.11902 | 0.041199 | 0.10529 | 0.09613 | 0.10529 | -0.045776 | 0.086975 | 0.061035 | 0.080109 | -0.24033 | -0.018158 | -0.11002 | -0.046997 | 0.082397 | 0.19226 | 0.068665 | 0.19684 | 0.19684 | 0.018311 | 0.064087 | 122.9828 | 122.5204 | 0.25177
10340.4688 | 0.076294 | 0.21255 | -0.20935 | -0.24139 | -0.095062 | -0.23819 | -0.037384 | 0.045776 | -0.032043 | 0.004578 | 0.004578 | 0.1236 | -0.032043 | 0.10986 | 0.076294 | 0.087585 | -0.24674 | -0.011749 | -0.091858 | -0.043793 | -0.045776 | 0.073242 | -0.07782 | 0.23346 | 0.2243 | 0.036621 | 0.10071 | 122.9187 | 122.5433 | 0.25635
10342.25 | 0.061035 | 0.23819 | -0.2179 | -0.24567 | -0.10361 | -0.29159 | -0.054474 | 0.11444 | 0.1236 | 0.15564 | 0.10071 | 0.09613 | -0.045776 | 0.09613 | 0.061035 | 0.065155 | -0.24994 | -0.025635 | -0.12283 | -0.044861 | 0.091553 | 0.25177 | 0.10071 | 0.20599 | 0.1831 | 0 | 0.082397 | 122.8867 | 122.5571 | 0.27924
10343.9844 | 0.076294 | 0.2179 | -0.22003 | -0.24994 | -0.098267 | -0.27451 | -0.055542 | 0.10986 | 0.10529 | 0.14648 | 0.10986 | 0.09613 | -0.045776 | 0.068665 | 0.045776 | 0.065155 | -0.25528 | -0.030975 | -0.1207 | -0.045929 | 0.073242 | 0.24719 | 0.10529 | 0.20142 | 0.20599 | -0.009155 | 0.073242 | 122.8638 | 122.5342 | 0.27466
10345.7656 | 0.030518 | 0.22644 | -0.19867 | -0.22644 | -0.10895 | -0.2478 | -0.063019 | 0.032043 | -0.07782 | -0.036621 | 0.013733 | 0.15106 | -0.027466 | 0.11902 | 0.045776 | 0.091858 | -0.24994 | -0.013885 | -0.10361 | -0.058746 | -0.041199 | 0.050354 | -0.07782 | 0.23346 | 0.24261 | 0.050354 | 0.09613 | 122.9507 | 122.58 | 0.25177
10347.5625 | 0.091553 | 0.22537 | -0.20615 | -0.22003 | -0.10254 | -0.2478 | -0.038452 | 0.027466 | -0.073242 | -0.027466 | 0.022888 | 0.13733 | -0.009155 | 0.11444 | 0.030518 | 0.099335 | -0.24246 | -0.02243 | -0.1004 | -0.041656 | -0.064087 | 0.041199 | -0.082397 | 0.24719 | 0.23346 | 0.050354 | 0.10986 | 122.9233 | 122.5388 | 0.25177
10349.3438 | 0.045776 | 0.22324 | -0.21896 | -0.24353 | -0.093994 | -0.27557 | -0.059814 | 0.032043 | -0.004578 | 0.018311 | 0.036621 | 0.12817 | -0.018311 | 0.1236 | 0.061035 | 0.087585 | -0.24033 | -0.035248 | -0.12604 | -0.033112 | -0.032043 | 0.11902 | -0.022888 | 0.25177 | 0.23804 | 0.027466 | 0.11902 | 122.8546 | 122.5708 | 0.27466
10351.0625 | 0.061035 | 0.21683 | -0.21469 | -0.24353 | -0.09079 | -0.2478 | -0.049133 | 0.054932 | -0.041199 | 0 | 0.018311 | 0.12817 | -0.013733 | 0.13275 | 0.061035 | 0.099335 | -0.24246 | -0.009613 | -0.11429 | -0.060883 | -0.045776 | 0.064087 | -0.082397 | 0.24261 | 0.21057 | 0.050354 | 0.10986 | 122.9416 | 122.5479 | 0.25177
10352.8281 | 0.045776 | 0.24887 | -0.22964 | -0.23498 | -0.10895 | -0.29373 | -0.060883 | 0.11444 | 0.11902 | 0.13733 | 0.10529 | 0.10986 | -0.045776 | 0.086975 | 0.076294 | 0.070496 | -0.24994 | -0.023499 | -0.11322 | -0.038452 | 0.09613 | 0.24719 | 0.10529 | 0.21057 | 0.20142 | 0.004578 | 0.059509 | 122.905 | 122.5433 | 0.25635
10354.625 | 0.045776 | 0.2478 | -0.19653 | -0.24033 | -0.087585 | -0.25207 | -0.05127 | 0.032043 | -0.045776 | 0 | 0.027466 | 0.1236 | -0.018311 | 0.12817 | 0.045776 | 0.088654 | -0.24353 | -0.021362 | -0.10361 | -0.048065 | -0.032043 | 0.11444 | -0.045776 | 0.22888 | 0.22888 | 0.022888 | 0.10529 | 122.9782 | 122.5433 | 0.24261
10356.4062 | 0.061035 | 0.25528 | -0.20721 | -0.23178 | -0.10574 | -0.27664 | -0.05661 | 0.022888 | -0.009155 | 0.022888 | 0.027466 | 0.12817 | -0.018311 | 0.11444 | 0.061035 | 0.076904 | -0.2478 | -0.021362 | -0.11429 | -0.043793 | -0.027466 | 0.11444 | -0.041199 | 0.23346 | 0.23804 | 0.050354 | 0.10529 | 122.8409 | 122.5754 | 0.29297
10358.125 | 0.045776 | 0.24139 | -0.20401 | -0.2446 | -0.10147 | -0.27023 | -0.054474 | 0.027466 | -0.059509 | -0.004578 | 0 | 0.14191 | 0 | 0.11902 | 0.061035 | 0.088654 | -0.24033 | -0.027771 | -0.11963 | -0.05127 | -0.041199 | 0.091553 | -0.059509 | 0.24261 | 0.23804 | 0.045776 | 0.10529 | 122.9187 | 122.5525 | 0.26093
10359.9062 | 0.061035 | 0.19653 | -0.21042 | -0.22644 | -0.11215 | -0.25101 | -0.042725 | 0.054932 | -0.07782 | -0.027466 | 0.013733 | 0.14191 | -0.009155 | 0.13733 | 0.045776 | 0.097198 | -0.24139 | -0.023499 | -0.1004 | -0.050201 | -0.018311 | 0.041199 | -0.073242 | 0.24261 | 0.23804 | 0.041199 | 0.11444 | 122.9691 | 122.5479 | 0.23346
10361.6875 | 0.091553 | 0.23498 | -0.21362 | -0.24567 | -0.10254 | -0.28625 | -0.048065 | 0.10986 | 0.091553 | 0.13275 | 0.082397 | 0.10071 | -0.041199 | 0.086975 | 0.061035 | 0.068359 | -0.24887 | -0.033112 | -0.11002 | -0.046997 | 0.064087 | 0.23804 | 0.07782 | 0.21515 | 0.20599 | 0.004578 | 0.07782 | 122.8409 | 122.5708 | 0.29755
10363.4688 | 0.045776 | 0.21683 | -0.23498 | -0.21469 | -0.10147 | -0.25848 | -0.046997 | 0.13733 | 0.064087 | 0.10986 | 0.09613 | 0.10529 | -0.07782 | 0.09613 | 0.045776 | 0.087585 | -0.25207 | -0.021362 | -0.10574 | -0.054474 | 0.086975 | 0.19684 | 0.068665 | 0.20142 | 0.21057 | -0.004578 | 0.041199 | 122.9782 | 122.525 | 0.25635
10365.1875 | 0.061035 | 0.22217 | -0.22324 | -0.23926 | -0.095062 | -0.29266 | -0.058746 | 0.082397 | 0.018311 | 0.091553 | 0.064087 | 0.11444 | -0.032043 | 0.09613 | 0.015259 | 0.061951 | -0.24246 | -0.026703 | -0.12497 | -0.043793 | 0.041199 | 0.17395 | 0.054932 | 0.21057 | 0.20599 | 0.004578 | 0.086975 | 122.9004 | 122.5616 | 0.2655
10366.9688 | 0.045776 | 0.23819 | -0.20721 | -0.24994 | -0.1004 | -0.24674 | -0.052338 | 0.059509 | -0.036621 | 0.013733 | 0.032043 | 0.11902 | -0.027466 | 0.12817 | 0.030518 | 0.09613 | -0.23498 | -0.024567 | -0.10574 | -0.055542 | 0.004578 | 0.13733 | -0.027466 | 0.24261 | 0.21973 | 0.027466 | 0.10986 | 122.9965 | 122.5479 | 0.24719
10368.75 | 0.045776 | 0.22217 | -0.20615 | -0.2211 | -0.10361 | -0.24567 | -0.046997 | 0.041199 | -0.059509 | -0.013733 | 0.022888 | 0.14648 | 0 | 0.11902 | 0.045776 | 0.095062 | -0.24139 | -0.036316 | -0.087585 | -0.050201 | -0.050354 | 0.050354 | -0.09613 | 0.25177 | 0.25177 | 0.050354 | 0.11444 | 122.9324 | 122.5388 | 0.24261
10370.5625 | 0.061035 | 0.2243 | -0.21896 | -0.22858 | -0.10254 | -0.28091 | -0.038452 | 0.15106 | 0.068665 | 0.13275 | 0.086975 | 0.086975 | -0.064087 | 0.07782 | 0.045776 | 0.071564 | -0.2478 | -0.030975 | -0.11002 | -0.044861 | 0.082397 | 0.19684 | 0.068665 | 0.19684 | 0.18768 | 0.004578 | 0.050354 | 122.9095 | 122.5616 | 0.27924
10372.2812 | 0.061035 | 0.24033 | -0.21042 | -0.22751 | -0.12283 | -0.26489 | -0.048065 | 0.12817 | 0.086975 | 0.13733 | 0.07782 | 0.091553 | -0.059509 | 0.086975 | 0.045776 | 0.076904 | -0.25955 | -0.024567 | -0.11215 | -0.044861 | 0.10071 | 0.19226 | 0.059509 | 0.20599 | 0.18768 | -0.004578 | 0.059509 | 122.8729 | 122.58 | 0.27466
10374.0625 | 0.045776 | 0.1976 | -0.21683 | -0.24139 | -0.10361 | -0.23819 | -0.049133 | 0.1236 | 0 | 0.050354 | 0.045776 | 0.12817 | -0.032043 | 0.1236 | 0.045776 | 0.085449 | -0.23392 | -0.010681 | -0.095062 | -0.057678 | 0.009155 | 0.11902 | -0.050354 | 0.2243 | 0.21515 | 0.013733 | 0.086975 | 122.9324 | 122.5296 | 0.24719
10375.8438 | 0.045776 | 0.22324 | -0.21149 | -0.24567 | -0.09613 | -0.26703 | -0.042725 | 0.12817 | 0.073242 | 0.1236 | 0.10071 | 0.07782 | -0.054932 | 0.086975 | 0.061035 | 0.068359 | -0.22964 | -0.028839 | -0.10468 | -0.041656 | 0.10529 | 0.18768 | 0.082397 | 0.20599 | 0.17853 | -0.004578 | 0.059509 | 122.9507 | 122.5342 | 0.25635
10377.6406 | 0.045776 | 0.21362 | -0.21042 | -0.22858 | -0.087585 | -0.23819 | -0.03952 | 0.068665 | 0.009155 | 0.018311 | 0.041199 | 0.13275 | -0.022888 | 0.1236 | 0.045776 | 0.1004 | -0.25742 | -0.01709 | -0.095062 | -0.044861 | -0.018311 | 0.086975 | -0.073242 | 0.25177 | 0.2243 | 0.050354 | 0.091553 | 122.937 | 122.5433 | 0.2655
10379.375 | 0.045776 | 0.21042 | -0.20294 | -0.2179 | -0.093994 | -0.25528 | -0.05127 | 0.036621 | -0.082397 | -0.018311 | 0.013733 | 0.12817 | -0.009155 | 0.10071 | 0.061035 | 0.091858 | -0.23712 | -0.025635 | -0.09613 | -0.044861 | -0.050354 | 0.050354 | -0.091553 | 0.24261 | 0.2243 | 0.032043 | 0.10071 | 122.9324 | 122.5388 | 0.23804
10381.1719 | 0.061035 | 0.21362 | -0.21469 | -0.23712 | -0.099335 | -0.25528 | -0.043793 | 0.027466 | -0.07782 | -0.013733 | 0.004578 | 0.15106 | -0.009155 | 0.12817 | 0.061035 | 0.10254 | -0.23498 | -0.009613 | -0.11429 | -0.037384 | -0.022888 | 0.036621 | -0.068665 | 0.23346 | 0.22888 | 0.041199 | 0.10529 | 122.9691 | 122.5616 | 0.26093
10382.9062 | 0.076294 | 0.21683 | -0.20828 | -0.25421 | -0.09079 | -0.2681 | -0.053406 | 0.018311 | -0.050354 | -0.004578 | 0.018311 | 0.15106 | -0.004578 | 0.1236 | 0.045776 | 0.082245 | -0.23285 | -0.01709 | -0.12817 | -0.040588 | -0.041199 | 0.086975 | -0.064087 | 0.25177 | 0.2243 | 0.050354 | 0.10071 | 122.9141 | 122.5296 | 0.2655
10384.6875 | 0.061035 | 0.24139 | -0.21576 | -0.23605 | -0.097198 | -0.29587 | -0.059814 | 0.041199 | 0.022888 | 0.07782 | 0.045776 | 0.12817 | -0.041199 | 0.091553 | 0.045776 | 0.072632 | -0.25207 | -0.024567 | -0.1239 | -0.043793 | 0.004578 | 0.16022 | 0.050354 | 0.20142 | 0.21057 | 0.013733 | 0.086975 | 122.8958 | 122.5983 | 0.28839
10386.4688 | 0.045776 | 0.23498 | -0.22324 | -0.24353 | -0.10681 | -0.27985 | -0.050201 | 0.12817 | 0.07782 | 0.11444 | 0.091553 | 0.10071 | -0.050354 | 0.082397 | 0.061035 | 0.075836 | -0.24567 | -0.036316 | -0.11429 | -0.041656 | 0.041199 | 0.21973 | 0.041199 | 0.21057 | 0.21515 | -0.004578 | 0.091553 | 122.8546 | 122.5754 | 0.27466
10388.1875 | 0.061035 | 0.2179 | -0.21896 | -0.24139 | -0.092926 | -0.28198 | -0.057678 | 0.11902 | 0.059509 | 0.10986 | 0.091553 | 0.10071 | -0.027466 | 0.09613 | 0.061035 | 0.082245 | -0.23712 | -0.027771 | -0.11108 | -0.045929 | 0.018311 | 0.1831 | 0.027466 | 0.2243 | 0.21973 | 0.009155 | 0.086975 | 122.8363 | 122.58 | 0.28381
10389.9688 | 0.061035 | 0.23605 | -0.21042 | -0.23712 | -0.10254 | -0.27878 | -0.066223 | 0.13733 | 0.091553 | 0.13275 | 0.086975 | 0.10071 | -0.059509 | 0.086975 | 0.030518 | 0.077972 | -0.24139 | -0.035248 | -0.11643 | -0.049133 | 0.068665 | 0.22888 | 0.064087 | 0.21515 | 0.1831 | 0.013733 | 0.073242 | 122.8409 | 122.58 | 0.27008
10391.7656 | 0.061035 | 0.2211 | -0.21255 | -0.25528 | -0.10361 | -0.27451 | -0.057678 | 0.13733 | 0.091553 | 0.14648 | 0.091553 | 0.07782 | -0.036621 | 0.10529 | 0.061035 | 0.075836 | -0.24246 | -0.026703 | -0.1239 | -0.053406 | 0.086975 | 0.22888 | 0.091553 | 0.21515 | 0.19684 | 0 | 0.068665 | 122.8317 | 122.58 | 0.27924
10393.4844 | 0.091553 | 0.24353 | -0.22003 | -0.23071 | -0.10574 | -0.2681 | -0.050201 | 0.13275 | 0.07782 | 0.10529 | 0.082397 | 0.086975 | -0.059509 | 0.068665 | 0.076294 | 0.074768 | -0.24567 | -0.021362 | -0.11322 | -0.055542 | 0.10071 | 0.17853 | 0.050354 | 0.21057 | 0.20599 | 0.032043 | 0.073242 | 122.8592 | 122.5937 | 0.27008
10395.2812 | 0.061035 | 0.22003 | -0.20935 | -0.23712 | -0.11856 | -0.25848 | -0.059814 | 0.045776 | -0.045776 | -0.013733 | -0.004578 | 0.14648 | 0 | 0.14191 | 0.030518 | 0.095062 | -0.23712 | -0.014954 | -0.10788 | -0.041656 | -0.027466 | 0.091553 | -0.059509 | 0.24261 | 0.23804 | 0.050354 | 0.11902 | 122.937 | 122.5388 | 0.2655
10397.0156 | 0.045776 | 0.22858 | -0.21255 | -0.22644 | -0.1004 | -0.25101 | -0.049133 | 0.050354 | -0.050354 | 0 | 0.013733 | 0.15564 | -0.018311 | 0.13275 | 0.045776 | 0.091858 | -0.23926 | -0.009613 | -0.098267 | -0.038452 | 0.004578 | 0.064087 | -0.050354 | 0.21973 | 0.21515 | 0.036621 | 0.10529 | 122.9874 | 122.5479 | 0.24261
10398.7969 | 0.045776 | 0.23285 | -0.20615 | -0.24246 | -0.1004 | -0.27344 | -0.049133 | 0.045776 | 0.022888 | 0.059509 | 0.022888 | 0.10529 | -0.027466 | 0.10529 | 0.030518 | 0.083313 | -0.23605 | -0.026703 | -0.11322 | -0.041656 | -0.027466 | 0.11444 | -0.032043 | 0.23804 | 0.22888 | 0.045776 | 0.091553 | 122.8409 | 122.5891 | 0.28381
10400.6094 | 0.030518 | 0.2211 | -0.20615 | -0.25421 | -0.095062 | -0.2681 | -0.060883 | 0.018311 | -0.013733 | 0.009155 | 0.013733 | 0.13275 | 0.009155 | 0.12817 | 0.061035 | 0.083313 | -0.23819 | -0.024567 | -0.10361 | -0.041656 | -0.022888 | 0.091553 | -0.045776 | 0.21515 | 0.2243 | 0.032043 | 0.11444 | 122.8821 | 122.5937 | 0.28381
10402.3281 | 0.045776 | 0.23926 | -0.22003 | -0.24887 | -0.09079 | -0.28732 | -0.058746 | 0.12817 | 0.15106 | 0.16022 | 0.09613 | 0.086975 | -0.022888 | 0.10529 | 0.030518 | 0.064087 | -0.23392 | -0.024567 | -0.11749 | -0.044861 | 0.086975 | 0.26093 | 0.09613 | 0.19226 | 0.18768 | 0 | 0.068665 | 122.8912 | 122.58 | 0.27008
10404.125 | 0.045776 | 0.22964 | -0.22217 | -0.2446 | -0.10254 | -0.27878 | -0.053406 | 0.091553 | 0.064087 | 0.10071 | 0.041199 | 0.091553 | -0.045776 | 0.082397 | 0.045776 | 0.075836 | -0.24139 | -0.032043 | -0.11002 | -0.038452 | 0.050354 | 0.16022 | 0.036621 | 0.18768 | 0.17853 | 0.009155 | 0.07782 | 122.8455 | 122.5937 | 0.27924
10405.9219 | 0.061035 | 0.25955 | -0.22324 | -0.23285 | -0.093994 | -0.27451 | -0.05661 | 0.07782 | 0.054932 | 0.082397 | 0.050354 | 0.10529 | -0.032043 | 0.082397 | 0.030518 | 0.068359 | -0.24674 | -0.044861 | -0.11002 | -0.041656 | 0.050354 | 0.15564 | 0.036621 | 0.20599 | 0.20599 | 0 | 0.10071 | 122.8592 | 122.5983 | 0.27466
10407.7031 | 0.030518 | 0.22644 | -0.2179 | -0.24674 | -0.09613 | -0.26489 | -0.057678 | 0.064087 | 0 | 0.045776 | 0.041199 | 0.1236 | -0.004578 | 0.1236 | 0.061035 | 0.081177 | -0.23819 | -0.028839 | -0.11002 | -0.046997 | -0.013733 | 0.09613 | -0.041199 | 0.22888 | 0.2243 | 0.027466 | 0.10071 | 122.8546 | 122.5845 | 0.27924
10409.4219 | 0.045776 | 0.22324 | -0.22003 | -0.24246 | -0.10361 | -0.27237 | -0.050201 | 0.13275 | 0.09613 | 0.1236 | 0.10986 | 0.09613 | -0.032043 | 0.10529 | 0.045776 | 0.067291 | -0.23712 | -0.026703 | -0.11429 | -0.057678 | 0.068665 | 0.21057 | 0.050354 | 0.21057 | 0.19226 | -0.004578 | 0.086975 | 122.8363 | 122.5891 | 0.29297
10411.2188 | 0.061035 | 0.23712 | -0.2179 | -0.23392 | -0.10788 | -0.28091 | -0.05127 | 0.16022 | 0.12817 | 0.13733 | 0.10529 | 0.086975 | -0.036621 | 0.082397 | 0.045776 | 0.071564 | -0.25955 | -0.021362 | -0.12283 | -0.05127 | 0.10071 | 0.23804 | 0.086975 | 0.1831 | 0.16937 | 0 | 0.073242 | 122.9095 | 122.5754 | 0.27466
10413.0156 | 0.061035 | 0.23926 | -0.20721 | -0.21683 | -0.10788 | -0.2478 | -0.046997 | 0.16937 | 0.073242 | 0.11902 | 0.091553 | 0.10071 | -0.059509 | 0.091553 | 0.045776 | 0.080109 | -0.25314 | -0.021362 | -0.1004 | -0.050201 | 0.10986 | 0.19226 | 0.059509 | 0.20142 | 0.17853 | 0.013733 | 0.068665 | 122.905 | 122.58 | 0.25177
10414.7344 | 0.061035 | 0.23926 | -0.2179 | -0.24246 | -0.088654 | -0.27237 | -0.065155 | 0.14648 | 0.11444 | 0.15564 | 0.09613 | 0.086975 | -0.027466 | 0.091553 | 0.061035 | 0.064087 | -0.23392 | -0.035248 | -0.11429 | -0.049133 | 0.082397 | 0.27008 | 0.082397 | 0.19684 | 0.16022 | 0.013733 | 0.073242 | 122.8683 | 122.5662 | 0.27466
10416.5469 | 0.076294 | 0.23712 | -0.2179 | -0.23712 | -0.10895 | -0.27237 | -0.053406 | 0.17395 | 0.10986 | 0.14648 | 0.09613 | 0.09613 | -0.054932 | 0.082397 | 0.061035 | 0.081177 | -0.24567 | -0.03418 | -0.10574 | -0.050201 | 0.086975 | 0.24719 | 0.082397 | 0.19684 | 0.1831 | 0.013733 | 0.073242 | 122.8729 | 122.58 | 0.2655
10418.3281 | 0.061035 | 0.22003 | -0.20401 | -0.22003 | -0.092926 | -0.23819 | -0.05127 | 0.073242 | -0.059509 | 0 | 0.013733 | 0.15106 | -0.004578 | 0.11444 | 0.061035 | 0.09613 | -0.24139 | -0.02243 | -0.09079 | -0.044861 | 0.018311 | 0.07782 | -0.032043 | 0.25177 | 0.20599 | 0.054932 | 0.09613 | 122.9919 | 122.5479 | 0.2243
10420.1094 | 0.061035 | 0.21362 | -0.20828 | -0.23392 | -0.093994 | -0.23605 | -0.040588 | 0.10071 | -0.022888 | 0.027466 | 0.036621 | 0.10986 | -0.013733 | 0.11902 | 0.045776 | 0.10361 | -0.23285 | -0.025635 | -0.086517 | -0.042725 | -0.013733 | 0.082397 | -0.054932 | 0.21515 | 0.21515 | 0.036621 | 0.11444 | 122.9416 | 122.5662 | 0.23804
10421.8906 | 0.045776 | 0.22751 | -0.22751 | -0.25101 | -0.10468 | -0.28305 | -0.05127 | 0.07782 | 0.050354 | 0.091553 | 0.073242 | 0.11902 | -0.032043 | 0.091553 | 0.061035 | 0.067291 | -0.24139 | -0.026703 | -0.12604 | -0.048065 | 0.082397 | 0.20599 | 0.082397 | 0.20599 | 0.18768 | 0.022888 | 0.086975 | 122.9233 | 122.6028 | 0.28381
10423.6719 | 0.030518 | 0.23498 | -0.21469 | -0.24246 | -0.097198 | -0.25101 | -0.048065 | 0.10071 | -0.009155 | 0.027466 | 0.041199 | 0.13275 | -0.041199 | 0.10071 | 0.045776 | 0.09079 | -0.23605 | -0.021362 | -0.085449 | -0.05127 | 0.082397 | 0.16022 | 0.022888 | 0.19684 | 0.19684 | 0.022888 | 0.073242 | 123.0057 | 122.5388 | 0.24261
10425.4062 | 0.045776 | 0.22537 | -0.20508 | -0.23819 | -0.11536 | -0.27344 | -0.041656 | 0.13733 | 0.091553 | 0.14191 | 0.09613 | 0.07782 | -0.064087 | 0.073242 | 0.030518 | 0.072632 | -0.23819 | -0.027771 | -0.11215 | -0.037384 | 0.10071 | 0.19226 | 0.064087 | 0.19684 | 0.17853 | 0.018311 | 0.064087 | 122.9095 | 122.58 | 0.27008
10427.2031 | 0.045776 | 0.2446 | -0.23605 | -0.24353 | -0.093994 | -0.29266 | -0.054474 | 0.11444 | 0.068665 | 0.11444 | 0.073242 | 0.09613 | -0.032043 | 0.07782 | 0.045776 | 0.068359 | -0.25101 | -0.02243 | -0.1239 | -0.043793 | 0.086975 | 0.21515 | 0.091553 | 0.19684 | 0.16479 | 0.018311 | 0.07782 | 122.9187 | 122.5662 | 0.27008
10428.9844 | 0.061035 | 0.2446 | -0.21896 | -0.23712 | -0.10681 | -0.27878 | -0.069427 | 0.091553 | 0.013733 | 0.082397 | 0.054932 | 0.1236 | -0.045776 | 0.091553 | 0.045776 | 0.076904 | -0.2478 | -0.026703 | -0.11856 | -0.044861 | 0.027466 | 0.13733 | 0.036621 | 0.20142 | 0.19226 | 0.004578 | 0.073242 | 122.8912 | 122.5983 | 0.27466
10430.6875 | 0.045776 | 0.21362 | -0.21469 | -0.24994 | -0.092926 | -0.24353 | -0.052338 | 0.059509 | -0.041199 | -0.009155 | 0.022888 | 0.14648 | 0.009155 | 0.12817 | 0.061035 | 0.1004 | -0.22537 | -0.016022 | -0.10361 | -0.059814 | -0.022888 | 0.086975 | -0.050354 | 0.23346 | 0.20599 | 0.041199 | 0.10986 | 122.9187 | 122.5479 | 0.25635
10432.6875 | 0.030518 | 0.20401 | -0.21896 | -0.23071 | -0.097198 | -0.24674 | -0.053406 | 0.15564 | 0.068665 | 0.1236 | 0.10529 | 0.10071 | -0.073242 | 0.082397 | 0.061035 | 0.082245 | -0.23605 | -0.023499 | -0.1004 | -0.042725 | 0.10071 | 0.19684 | 0.054932 | 0.17853 | 0.16022 | -0.004578 | 0.068665 | 122.9828 | 122.5571 | 0.24261
10436.5938 | 0.061035 | 0.22964 | -0.21469 | -0.2243 | -0.084381 | -0.2478 | -0.043793 | 0.054932 | -0.054932 | -0.027466 | 0.004578 | 0.13733 | -0.018311 | 0.1236 | 0.045776 | 0.09079 | -0.24033 | -0.012817 | -0.1004 | -0.045929 | 0 | 0.045776 | -0.07782 | 0.2243 | 0.21515 | 0.041199 | 0.09613 | 122.9691 | 122.5845 | 0.24261
10440.1719 | 0.045776 | 0.21149 | -0.21042 | -0.25635 | -0.10361 | -0.27023 | -0.043793 | 0.10071 | 0.041199 | 0.07782 | 0.064087 | 0.10986 | -0.027466 | 0.11902 | 0.045776 | 0.082245 | -0.22644 | -0.01709 | -0.11643 | -0.049133 | 0 | 0.12817 | -0.018311 | 0.2243 | 0.20599 | 0.032043 | 0.10986 | 122.8683 | 122.5845 | 0.27466
10445.9375 | 0.061035 | 0.26916 | -0.21683 | -0.23498 | -0.10895 | -0.28198 | -0.053406 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.10529 | -0.045776 | 0.082397 | 0.045776 | 0.081177 | -0.23926 | -0.023499 | -0.11643 | -0.045929 | 0.07782 | 0.23804 | 0.082397 | 0.18768 | 0.16937 | 0.018311 | 0.082397 | 122.8683 | 122.5891 | 0.27008
10447.7344 | 0.061035 | 0.25207 | -0.22751 | -0.23178 | -0.1004 | -0.28946 | -0.042725 | 0.064087 | 0.032043 | 0.07782 | 0.054932 | 0.10529 | -0.032043 | 0.091553 | 0.045776 | 0.068359 | -0.24139 | -0.027771 | -0.10361 | -0.042725 | 0.032043 | 0.14648 | 0.036621 | 0.19226 | 0.18768 | 0 | 0.082397 | 122.8729 | 122.6257 | 0.26093
10449.5156 | 0.061035 | 0.25101 | -0.21255 | -0.22858 | -0.11322 | -0.26596 | -0.067291 | 0.12817 | 0.073242 | 0.12817 | 0.064087 | 0.09613 | -0.054932 | 0.082397 | 0.030518 | 0.070496 | -0.23712 | -0.025635 | -0.10681 | -0.033112 | 0.073242 | 0.16022 | 0.036621 | 0.16022 | 0.1831 | 0 | 0.073242 | 122.8638 | 122.612 | 0.25177
10451.2344 | 0.076294 | 0.22644 | -0.21149 | -0.22858 | -0.10254 | -0.23819 | -0.050201 | 0.064087 | -0.073242 | -0.013733 | 0.022888 | 0.12817 | -0.022888 | 0.13275 | 0.061035 | 0.09613 | -0.24139 | -0.020294 | -0.093994 | -0.041656 | -0.009155 | 0.036621 | -0.068665 | 0.21515 | 0.2243 | 0.032043 | 0.10529 | 122.9736 | 122.5937 | 0.21973
10453.0469 | 0.061035 | 0.23605 | -0.22003 | -0.23178 | -0.095062 | -0.26382 | -0.053406 | 0.12817 | 0.082397 | 0.1236 | 0.073242 | 0.10529 | -0.059509 | 0.07782 | 0.061035 | 0.083313 | -0.23285 | -0.027771 | -0.11536 | -0.043793 | 0.09613 | 0.18768 | 0.054932 | 0.18768 | 0.16479 | 0.022888 | 0.07782 | 122.8683 | 122.6349 | 0.26093
10454.8281 | 0.045776 | 0.2211 | -0.19226 | -0.21576 | -0.11108 | -0.24567 | -0.040588 | 0.050354 | -0.059509 | -0.013733 | 0.018311 | 0.14191 | -0.013733 | 0.11444 | 0.061035 | 0.091858 | -0.22858 | -0.018158 | -0.087585 | -0.053406 | -0.036621 | 0.050354 | -0.09613 | 0.2243 | 0.21057 | 0.032043 | 0.11444 | 122.9462 | 122.58 | 0.23346
10456.6094 | 0.061035 | 0.23498 | -0.21469 | -0.23498 | -0.10147 | -0.28625 | -0.05661 | 0.12817 | 0.091553 | 0.11902 | 0.07782 | 0.086975 | -0.050354 | 0.091553 | 0.030518 | 0.071564 | -0.23819 | -0.030975 | -0.11536 | -0.042725 | 0.059509 | 0.17395 | 0.041199 | 0.16937 | 0.17853 | 0 | 0.086975 | 122.8638 | 122.6074 | 0.2655
10458.3438 | 0.045776 | 0.22003 | -0.21469 | -0.25207 | -0.089722 | -0.26062 | -0.057678 | 0.054932 | -0.045776 | 0 | 0.013733 | 0.14648 | 0 | 0.12817 | 0.045776 | 0.085449 | -0.22644 | -0.027771 | -0.11215 | -0.040588 | -0.022888 | 0.11902 | -0.050354 | 0.22888 | 0.19684 | 0.045776 | 0.11444 | 122.9874 | 122.5662 | 0.2243
10460.0625 | 0.061035 | 0.25742 | -0.2179 | -0.23071 | -0.091858 | -0.29266 | -0.050201 | 0.07782 | 0.045776 | 0.07782 | 0.059509 | 0.10071 | -0.041199 | 0.086975 | 0.061035 | 0.064087 | -0.24353 | -0.02243 | -0.10681 | -0.040588 | 0.045776 | 0.18768 | 0.064087 | 0.1831 | 0.17853 | 0.009155 | 0.091553 | 122.9233 | 122.5845 | 0.24261
10461.7812 | 0.045776 | 0.20615 | -0.21576 | -0.24567 | -0.086517 | -0.25421 | -0.03952 | 0.041199 | -0.054932 | -0.013733 | 0.032043 | 0.16022 | -0.009155 | 0.1236 | 0.061035 | 0.081177 | -0.2243 | -0.019226 | -0.10788 | -0.063019 | -0.022888 | 0.10071 | -0.059509 | 0.23346 | 0.19226 | 0.050354 | 0.10071 | 122.9828 | 122.5525 | 0.21515
10463.5 | 0.045776 | 0.22003 | -0.21149 | -0.22644 | -0.10361 | -0.24674 | -0.049133 | 0.036621 | -0.073242 | -0.022888 | 0.004578 | 0.14191 | -0.018311 | 0.11444 | 0.045776 | 0.086517 | -0.21683 | -0.013885 | -0.10468 | -0.045929 | -0.022888 | 0.054932 | -0.068665 | 0.21515 | 0.19684 | 0.027466 | 0.10986 | 122.9965 | 122.5983 | 0.21973
10465.2188 | 0.061035 | 0.24033 | -0.21896 | -0.24674 | -0.092926 | -0.28412 | -0.05661 | 0.050354 | 0.036621 | 0.082397 | 0.059509 | 0.10986 | -0.032043 | 0.07782 | 0.061035 | 0.057678 | -0.23819 | -0.026703 | -0.12283 | -0.042725 | 0.050354 | 0.16022 | 0.036621 | 0.20142 | 0.1831 | 0.018311 | 0.07782 | 122.8821 | 122.612 | 0.25635
10467 | 0.045776 | 0.2211 | -0.20721 | -0.24567 | -0.098267 | -0.26489 | -0.049133 | 0.032043 | -0.022888 | 0.004578 | 0.009155 | 0.12817 | -0.009155 | 0.15106 | 0.061035 | 0.074768 | -0.21683 | -0.023499 | -0.10895 | -0.054474 | -0.032043 | 0.091553 | -0.054932 | 0.21973 | 0.21973 | 0.054932 | 0.10986 | 122.8821 | 122.6212 | 0.26093
10468.7188 | 0.045776 | 0.23392 | -0.21576 | -0.22644 | -0.10574 | -0.26382 | -0.043793 | 0.1236 | 0.086975 | 0.1236 | 0.10986 | 0.082397 | -0.045776 | 0.073242 | 0.061035 | 0.080109 | -0.24033 | -0.027771 | -0.093994 | -0.046997 | 0.11902 | 0.21515 | 0.073242 | 0.16937 | 0.14648 | 0.013733 | 0.068665 | 122.937 | 122.58 | 0.2243
10470.5156 | 0.061035 | 0.23605 | -0.22003 | -0.24887 | -0.10468 | -0.28732 | -0.064087 | 0.064087 | 0.009155 | 0.07782 | 0.054932 | 0.086975 | -0.050354 | 0.091553 | 0.061035 | 0.071564 | -0.23392 | -0.033112 | -0.12176 | -0.041656 | 0.036621 | 0.14191 | 0.036621 | 0.19684 | 0.19226 | 0.022888 | 0.09613 | 122.8867 | 122.6028 | 0.26093
10472.2969 | 0.061035 | 0.18478 | -0.20935 | -0.23819 | -0.098267 | -0.23712 | -0.052338 | 0.054932 | -0.091553 | -0.013733 | 0.018311 | 0.13733 | -0.009155 | 0.13733 | 0.061035 | 0.098267 | -0.21362 | -0.01709 | -0.093994 | -0.054474 | -0.045776 | 0.036621 | -0.09613 | 0.21515 | 0.19226 | 0.036621 | 0.11444 | 122.9599 | 122.58 | 0.24261
10474.0781 | 0.061035 | 0.19226 | -0.19867 | -0.24139 | -0.091858 | -0.24674 | -0.049133 | 0.059509 | -0.018311 | 0.013733 | 0.032043 | 0.14191 | -0.009155 | 0.12817 | 0.061035 | 0.088654 | -0.22217 | -0.011749 | -0.10895 | -0.053406 | 0.009155 | 0.12817 | -0.018311 | 0.20599 | 0.19684 | 0.041199 | 0.11902 | 122.9874 | 122.5616 | 0.21515
10475.8438 | 0.045776 | 0.21149 | -0.20508 | -0.2243 | -0.099335 | -0.24994 | -0.043793 | 0.027466 | -0.068665 | -0.022888 | 0.004578 | 0.14191 | -0.018311 | 0.12817 | 0.045776 | 0.086517 | -0.23285 | -0.005341 | -0.099335 | -0.03418 | -0.054932 | 0.050354 | -0.086975 | 0.21057 | 0.21057 | 0.041199 | 0.10529 | 122.9645 | 122.6028 | 0.22888
10477.6562 | 0.045776 | 0.21576 | -0.20508 | -0.25207 | -0.11108 | -0.24567 | -0.038452 | 0.018311 | -0.054932 | 0 | 0.013733 | 0.13733 | -0.004578 | 0.1236 | 0.045776 | 0.081177 | -0.22751 | -0.026703 | -0.10361 | -0.041656 | -0.013733 | 0.07782 | -0.045776 | 0.21515 | 0.20142 | 0.041199 | 0.10529 | 123.0148 | 122.5891 | 0.21973
10479.3906 | 0.045776 | 0.23926 | -0.2179 | -0.24246 | -0.11963 | -0.29694 | -0.055542 | 0.027466 | 0.036621 | 0.091553 | 0.054932 | 0.09613 | -0.022888 | 0.091553 | 0.045776 | 0.061951 | -0.23498 | -0.026703 | -0.12497 | -0.042725 | 0.032043 | 0.16937 | 0.064087 | 0.17395 | 0.16022 | 0.018311 | 0.07782 | 122.9095 | 122.5937 | 0.25177
10481.1562 | 0.061035 | 0.20828 | -0.22324 | -0.25207 | -0.11002 | -0.28519 | -0.054474 | 0.11902 | 0.064087 | 0.10071 | 0.091553 | 0.10529 | -0.027466 | 0.09613 | 0.030518 | 0.083313 | -0.22858 | -0.020294 | -0.11429 | -0.041656 | 0.009155 | 0.17395 | 0.013733 | 0.19226 | 0.18768 | 0.027466 | 0.11444 | 122.85 | 122.612 | 0.25635
10482.9531 | 0.045776 | 0.20935 | -0.20615 | -0.22751 | -0.095062 | -0.24567 | -0.046997 | 0.073242 | -0.027466 | 0.022888 | 0.059509 | 0.1236 | -0.004578 | 0.1236 | 0.061035 | 0.097198 | -0.23285 | -0.027771 | -0.098267 | -0.059814 | 0.009155 | 0.13733 | -0.022888 | 0.20142 | 0.19226 | 0.032043 | 0.10986 | 122.9874 | 122.58 | 0.21515
10484.7344 | 0.061035 | 0.2478 | -0.21683 | -0.24567 | -0.10361 | -0.30868 | -0.052338 | 0.064087 | 0.050354 | 0.10986 | 0.073242 | 0.10529 | -0.050354 | 0.10529 | 0.076294 | 0.066223 | -0.23178 | -0.036316 | -0.1239 | -0.044861 | 0.064087 | 0.19684 | 0.082397 | 0.18768 | 0.16479 | 0 | 0.054932 | 122.9233 | 122.6074 | 0.27008
10486.4531 | 0.076294 | 0.22751 | -0.20935 | -0.24567 | -0.10681 | -0.28625 | -0.058746 | 0.10986 | 0.068665 | 0.13275 | 0.10071 | 0.10986 | -0.032043 | 0.09613 | 0.045776 | 0.076904 | -0.23178 | -0.03418 | -0.13138 | -0.050201 | 0.091553 | 0.2243 | 0.09613 | 0.16479 | 0.15564 | 0.009155 | 0.07782 | 122.9187 | 122.5891 | 0.24261
10488.1719 | 0.030518 | 0.2211 | -0.21362 | -0.25101 | -0.088654 | -0.26062 | -0.066223 | 0.13275 | 0.10986 | 0.13733 | 0.09613 | 0.10071 | -0.045776 | 0.082397 | 0.076294 | 0.0737 | -0.22964 | -0.018158 | -0.11429 | -0.041656 | 0.082397 | 0.23346 | 0.07782 | 0.18768 | 0.16022 | 0.004578 | 0.068665 | 122.8683 | 122.6028 | 0.24719
10489.8906 | 0.061035 | 0.22537 | -0.20401 | -0.2179 | -0.098267 | -0.2446 | -0.035248 | 0.059509 | -0.032043 | 0.009155 | 0.022888 | 0.14191 | 0 | 0.10529 | 0.045776 | 0.084381 | -0.24033 | -0.024567 | -0.092926 | -0.054474 | 0.036621 | 0.10529 | -0.009155 | 0.18768 | 0.16937 | 0.009155 | 0.086975 | 123.0331 | 122.5708 | 0.23346
10491.6875 | 0.045776 | 0.22644 | -0.19867 | -0.22537 | -0.10574 | -0.2446 | -0.046997 | 0.041199 | -0.068665 | -0.027466 | 0 | 0.15106 | 0.004578 | 0.12817 | 0.045776 | 0.088654 | -0.23819 | -0.020294 | -0.098267 | -0.041656 | -0.009155 | 0.054932 | -0.050354 | 0.21515 | 0.21057 | 0.036621 | 0.10986 | 122.9874 | 122.5937 | 0.2243
10493.4844 | 0.061035 | 0.22324 | -0.21469 | -0.23819 | -0.10147 | -0.2446 | -0.046997 | 0.09613 | 0.009155 | 0.041199 | 0.050354 | 0.13733 | -0.018311 | 0.11902 | 0.076294 | 0.099335 | -0.23712 | -0.021362 | -0.093994 | -0.050201 | 0.013733 | 0.14191 | -0.013733 | 0.20599 | 0.18768 | 0.027466 | 0.10071 | 122.9782 | 122.5708 | 0.19684
10495.2656 | 0.045776 | 0.26169 | -0.22003 | -0.23605 | -0.10361 | -0.298 | -0.053406 | 0.1236 | 0.13733 | 0.14191 | 0.10986 | 0.10071 | -0.041199 | 0.10071 | 0.045776 | 0.061951 | -0.22644 | -0.028839 | -0.12497 | -0.040588 | 0.082397 | 0.24719 | 0.091553 | 0.14191 | 0.15564 | 0.018311 | 0.07782 | 122.9141 | 122.6257 | 0.23346
10496.9844 | 0.045776 | 0.24567 | -0.10895 | -0.23605 | -0.10681 | -0.29159 | -0.060883 | 0.050354 | 0.050354 | 0.082397 | 0.064087 | 0.10071 | -0.036621 | 0.10071 | 0.076294 | 0.05127 | -0.2446 | -0.03418 | -0.10788 | -0.036316 | 0.073242 | 0.18768 | 0.064087 | 0.17853 | 0.16479 | 0.036621 | 0.073242 | 122.9141 | 122.6303 | 0.2655
10498.7656 | 0.061035 | 0.21683 | -0.21042 | -0.23392 | -0.098267 | -0.24139 | -0.053406 | 0.10986 | 0.041199 | 0.045776 | 0.059509 | 0.14191 | -0.013733 | 0.11902 | 0.061035 | 0.091858 | -0.22964 | -0.023499 | -0.098267 | -0.053406 | 0.036621 | 0.1236 | -0.027466 | 0.19684 | 0.17395 | 0.032043 | 0.10529 | 122.9599 | 122.5616 | 0.21515
10500.5625 | 0.061035 | 0.22537 | -0.21469 | -0.23071 | -0.10895 | -0.25314 | -0.043793 | 0.041199 | -0.082397 | -0.018311 | 0.004578 | 0.15106 | 0.004578 | 0.10986 | 0.045776 | 0.099335 | -0.23498 | -0.02243 | -0.10574 | -0.042725 | -0.032043 | 0.036621 | -0.068665 | 0.21057 | 0.19684 | 0.045776 | 0.10529 | 122.9919 | 122.612 | 0.21057
10502.2812 | 0.076294 | 0.21255 | -0.21469 | -0.24246 | -0.11108 | -0.26382 | -0.042725 | 0.027466 | -0.082397 | -0.022888 | 0.004578 | 0.14191 | 0 | 0.11902 | 0.061035 | 0.098267 | -0.21576 | -0.020294 | -0.09613 | -0.03952 | -0.041199 | 0.045776 | -0.07782 | 0.19684 | 0.19684 | 0.041199 | 0.10071 | 122.9782 | 122.6166 | 0.2243
10504.0625 | 0.076294 | 0.22858 | -0.20935 | -0.2478 | -0.10254 | -0.27664 | -0.05661 | 0.068665 | 0.013733 | 0.059509 | 0.068665 | 0.10986 | -0.013733 | 0.10529 | 0.061035 | 0.076904 | -0.22964 | -0.013885 | -0.11963 | -0.037384 | -0.027466 | 0.11444 | -0.041199 | 0.19684 | 0.20142 | 0.018311 | 0.11444 | 122.8638 | 122.6212 | 0.24719
10505.8438 | 0.061035 | 0.24674 | -0.22644 | -0.24994 | -0.10681 | -0.298 | -0.061951 | 0.082397 | 0.045776 | 0.091553 | 0.07782 | 0.10986 | -0.032043 | 0.086975 | 0.076294 | 0.067291 | -0.23285 | -0.035248 | -0.12283 | -0.040588 | 0.054932 | 0.20599 | 0.059509 | 0.16937 | 0.16937 | 0.022888 | 0.086975 | 122.9141 | 122.6303 | 0.22888
10507.6406 | 0.061035 | 0.21362 | -0.22217 | -0.23926 | -0.098267 | -0.26169 | -0.065155 | 0.054932 | -0.064087 | 0.013733 | 0.032043 | 0.13275 | -0.009155 | 0.11902 | 0.076294 | 0.083313 | -0.21683 | -0.019226 | -0.11002 | -0.057678 | -0.027466 | 0.091553 | -0.050354 | 0.19226 | 0.19226 | 0.041199 | 0.09613 | 122.9874 | 122.5754 | 0.21057
10509.4219 | 0.061035 | 0.20935 | -0.20828 | -0.22751 | -0.10361 | -0.25848 | -0.050201 | 0.13275 | 0.004578 | 0.041199 | 0.054932 | 0.1236 | -0.009155 | 0.1236 | 0.061035 | 0.098267 | -0.22217 | -0.019226 | -0.09079 | -0.055542 | 0.004578 | 0.1236 | -0.032043 | 0.20142 | 0.1831 | 0.045776 | 0.10071 | 122.9599 | 122.5937 | 0.19684
10511.2031 | 0.045776 | 0.21362 | -0.21683 | -0.22644 | -0.10681 | -0.25421 | -0.053406 | 0.027466 | -0.082397 | -0.032043 | 0.018311 | 0.12817 | -0.004578 | 0.11444 | 0.045776 | 0.086517 | -0.23712 | -0.021362 | -0.10254 | -0.040588 | -0.036621 | 0.050354 | -0.068665 | 0.19226 | 0.19226 | 0.032043 | 0.086975 | 123.0011 | 122.6212 | 0.20599
10513 | 0.061035 | 0.21576 | -0.2211 | -0.23285 | -0.09079 | -0.25207 | -0.05661 | 0.054932 | -0.045776 | 0.004578 | 0.032043 | 0.16022 | -0.018311 | 0.14648 | 0.045776 | 0.089722 | -0.22217 | -0.02243 | -0.11856 | -0.049133 | -0.018311 | 0.13275 | -0.018311 | 0.18768 | 0.19684 | 0.032043 | 0.1236 | 123.0103 | 122.5937 | 0.20599
10514.7812 | 0.061035 | 0.23819 | -0.21042 | -0.25314 | -0.10788 | -0.29373 | -0.060883 | 0.12817 | 0.10071 | 0.13275 | 0.09613 | 0.09613 | -0.045776 | 0.09613 | 0.061035 | 0.055542 | -0.22964 | -0.025635 | -0.13992 | -0.03418 | 0.10071 | 0.26093 | 0.10529 | 0.16479 | 0.17395 | 0 | 0.073242 | 122.9279 | 122.6074 | 0.23804
10516.5 | 0.061035 | 0.24246 | -0.21149 | -0.24994 | -0.1004 | -0.29159 | -0.068359 | 0.050354 | 0.013733 | 0.07782 | 0.059509 | 0.10986 | -0.059509 | 0.10071 | 0.045776 | 0.059814 | -0.23285 | -0.032043 | -0.12176 | -0.040588 | 0.009155 | 0.15564 | 0.032043 | 0.1831 | 0.16022 | 0.013733 | 0.09613 | 122.8958 | 122.6395 | 0.23346
10518.2656 | 0.045776 | 0.18692 | -0.20401 | -0.23285 | -0.11002 | -0.23605 | -0.05127 | 0.07782 | -0.045776 | 0.009155 | 0.013733 | 0.13733 | -0.009155 | 0.12817 | 0.061035 | 0.089722 | -0.2243 | -0.014954 | -0.093994 | -0.052338 | -0.036621 | 0.054932 | -0.09613 | 0.20599 | 0.1831 | 0.050354 | 0.11902 | 122.9507 | 122.6257 | 0.21973
10519.9844 | 0.045776 | 0.25528 | -0.21576 | -0.25101 | -0.10788 | -0.28625 | -0.057678 | 0.050354 | 0.013733 | 0.082397 | 0.064087 | 0.10071 | -0.036621 | 0.09613 | 0.061035 | 0.058746 | -0.22751 | -0.023499 | -0.12283 | -0.03952 | 0.036621 | 0.16937 | 0.054932 | 0.1831 | 0.16022 | 0.013733 | 0.07782 | 122.9004 | 122.6166 | 0.22888
10521.7656 | 0.045776 | 0.24567 | -0.1976 | -0.22964 | -0.1004 | -0.25101 | -0.059814 | 0.13733 | 0.059509 | 0.11902 | 0.091553 | 0.091553 | -0.041199 | 0.086975 | 0.030518 | 0.081177 | -0.22964 | -0.01709 | -0.099335 | -0.044861 | 0.086975 | 0.17395 | 0.054932 | 0.14191 | 0.15106 | 0 | 0.059509 | 122.9919 | 122.5891 | 0.21515
10523.4844 | 0.061035 | 0.22324 | -0.21362 | -0.23392 | -0.093994 | -0.25955 | -0.058746 | 0.045776 | -0.045776 | -0.009155 | 0.036621 | 0.14191 | 0.009155 | 0.13275 | 0.061035 | 0.09613 | -0.22964 | -0.026703 | -0.099335 | -0.05127 | -0.032043 | 0.10529 | -0.059509 | 0.19226 | 0.19226 | 0.050354 | 0.10986 | 122.9874 | 122.5891 | 0.21057
10525.2812 | 0.045776 | 0.20508 | -0.21042 | -0.24674 | -0.09613 | -0.25421 | -0.055542 | 0.041199 | -0.086975 | -0.022888 | 0.013733 | 0.14648 | -0.009155 | 0.12817 | 0.076294 | 0.11215 | -0.23178 | -0.02243 | -0.091858 | -0.053406 | -0.041199 | 0.022888 | -0.082397 | 0.1831 | 0.19226 | 0.054932 | 0.10071 | 122.9599 | 122.6166 | 0.21515
10527.0625 | 0.030518 | 0.23178 | -0.22217 | -0.25314 | -0.09079 | -0.29373 | -0.061951 | 0.10986 | 0.10529 | 0.13733 | 0.09613 | 0.10986 | -0.041199 | 0.082397 | 0.045776 | 0.068359 | -0.2446 | -0.033112 | -0.12711 | -0.037384 | 0.10071 | 0.21973 | 0.09613 | 0.14191 | 0.13733 | 0.009155 | 0.068665 | 122.9324 | 122.6349 | 0.21515
10528.8594 | 0.045776 | 0.23712 | -0.21042 | -0.23712 | -0.09613 | -0.27985 | -0.075836 | 0.086975 | 0.050354 | 0.10986 | 0.073242 | 0.091553 | -0.045776 | 0.10071 | 0.045776 | 0.070496 | -0.23392 | -0.040588 | -0.1207 | -0.045929 | 0.073242 | 0.19684 | 0.07782 | 0.15564 | 0.16937 | -0.004578 | 0.073242 | 122.9095 | 122.6303 | 0.22888
10530.6562 | 0.091553 | 0.20828 | -0.21149 | -0.24246 | -0.095062 | -0.24887 | -0.046997 | 0.082397 | -0.022888 | 0.022888 | 0.054932 | 0.13733 | -0.009155 | 0.10529 | 0.045776 | 0.10361 | -0.2211 | -0.023499 | -0.10895 | -0.057678 | 0.004578 | 0.12817 | -0.027466 | 0.18768 | 0.1831 | 0.045776 | 0.091553 | 122.9919 | 122.5983 | 0.1831
10532.4375 | 0.061035 | 0.25848 | -0.25207 | -0.2243 | -0.095062 | -0.29587 | -0.054474 | 0.09613 | 0.082397 | 0.10071 | 0.07782 | 0.11444 | -0.032043 | 0.09613 | 0.030518 | 0.079041 | -0.24567 | -0.025635 | -0.11643 | -0.032043 | 0.07782 | 0.20599 | 0.07782 | 0.15106 | 0.14648 | -0.018311 | 0.07782 | 122.9004 | 122.6395 | 0.21973
10534.1562 | 0.061035 | 0.2179 | -0.20828 | -0.25635 | -0.098267 | -0.27237 | -0.060883 | 0.10529 | 0.082397 | 0.11902 | 0.091553 | 0.11902 | -0.041199 | 0.082397 | 0.061035 | 0.061951 | -0.22003 | -0.032043 | -0.10895 | -0.063019 | 0.041199 | 0.16022 | 0.022888 | 0.14191 | 0.15564 | 0.032043 | 0.10986 | 122.8409 | 122.6715 | 0.23346
10535.9375 | 0.061035 | 0.2211 | -0.19974 | -0.22003 | -0.098267 | -0.24567 | -0.055542 | 0.09613 | 0.018311 | 0.036621 | 0.054932 | 0.13733 | -0.013733 | 0.11444 | 0.061035 | 0.075836 | -0.20721 | -0.020294 | -0.098267 | -0.046997 | 0.027466 | 0.082397 | -0.059509 | 0.15564 | 0.15106 | 0.036621 | 0.12817 | 122.9553 | 122.6166 | 0.16022
10537.7188 | 0.061035 | 0.21576 | -0.22644 | -0.2478 | -0.10361 | -0.28946 | -0.043793 | 0.10986 | 0.12817 | 0.15106 | 0.10986 | 0.091553 | -0.036621 | 0.10071 | 0.045776 | 0.058746 | -0.22217 | -0.032043 | -0.11856 | -0.048065 | 0.068665 | 0.2243 | 0.082397 | 0.11902 | 0.11902 | 0 | 0.07782 | 122.8775 | 122.6257 | 0.21057
10539.5156 | 0.045776 | 0.23819 | -0.22858 | -0.22964 | -0.097198 | -0.26596 | -0.050201 | 0.11444 | 0.082397 | 0.12817 | 0.073242 | 0.091553 | -0.054932 | 0.073242 | 0.061035 | 0.053406 | -0.20721 | -0.026703 | -0.11215 | -0.045929 | 0.07782 | 0.13275 | 0.036621 | 0.12817 | 0.10529 | 0.022888 | 0.07782 | 122.8821 | 122.6944 | 0.20142
10541.2344 | 0.045776 | 0.22858 | -0.21469 | -0.23712 | -0.10361 | -0.24887 | -0.045929 | 0.045776 | -0.041199 | -0.004578 | 0.013733 | 0.15106 | -0.009155 | 0.13733 | 0.015259 | 0.068359 | -0.19974 | -0.024567 | -0.10254 | -0.05661 | -0.022888 | 0.064087 | -0.054932 | 0.16022 | 0.15106 | 0.054932 | 0.1236 | 122.9782 | 122.6761 | 0.14648
10543.0156 | 0.061035 | 0.22537 | -0.2211 | -0.2243 | -0.11002 | -0.25528 | -0.053406 | 0.045776 | -0.054932 | -0.018311 | 0 | 0.13733 | -0.013733 | 0.13275 | 0.045776 | 0.069427 | -0.1976 | -0.024567 | -0.097198 | -0.045929 | -0.004578 | 0.050354 | -0.036621 | 0.15106 | 0.13733 | 0.045776 | 0.091553 | 123.0103 | 122.6395 | 0.15106
10544.7969 | 0.045776 | 0.21149 | -0.21576 | -0.23712 | -0.097198 | -0.24994 | -0.045929 | 0.032043 | -0.041199 | -0.009155 | 0 | 0.13733 | -0.018311 | 0.10986 | 0.030518 | 0.064087 | -0.18799 | -0.011749 | -0.09613 | -0.029907 | 0.004578 | 0.059509 | -0.045776 | 0.14648 | 0.1236 | 0.050354 | 0.086975 | 123.0194 | 122.6578 | 0.12817
10546.5781 | 0.030518 | 0.22324 | -0.19226 | -0.24353 | -0.1004 | -0.25421 | -0.038452 | 0.050354 | -0.045776 | 0.009155 | 0.027466 | 0.1236 | -0.013733 | 0.12817 | 0.061035 | 0.064087 | -0.18585 | -0.025635 | -0.099335 | -0.043793 | -0.032043 | 0.054932 | -0.07782 | 0.12817 | 0.13733 | 0.045776 | 0.1236 | 122.9507 | 122.6578 | 0.14191
10548.2969 | 0.045776 | 0.1976 | -0.1976 | -0.24353 | -0.10788 | -0.24994 | -0.042725 | 0.018311 | -0.07782 | -0.009155 | 0 | 0.13275 | -0.013733 | 0.13275 | 0.061035 | 0.046997 | -0.19012 | -0.007477 | -0.11108 | -0.052338 | -0.022888 | 0.022888 | -0.073242 | 0.15106 | 0.1236 | 0.045776 | 0.11902 | 122.9782 | 122.6624 | 0.16022
10550.0938 | 0.076294 | 0.22537 | -0.21149 | -0.24033 | -0.098267 | -0.25742 | -0.038452 | 0.032043 | -0.07782 | -0.018311 | 0 | 0.15106 | -0.004578 | 0.11444 | 0.076294 | 0.057678 | -0.18478 | -0.020294 | -0.098267 | -0.046997 | -0.018311 | 0.004578 | -0.07782 | 0.13733 | 0.11902 | 0.041199 | 0.10529 | 122.9874 | 122.6761 | 0.14191
10551.875 | 0.045776 | 0.2446 | -0.23926 | -0.24246 | -0.10147 | -0.29907 | -0.05661 | 0.045776 | 0.013733 | 0.07782 | 0.064087 | 0.086975 | -0.036621 | 0.09613 | 0.061035 | 0.033112 | -0.19546 | -0.025635 | -0.12924 | -0.038452 | 0.032043 | 0.11444 | 0.050354 | 0.11444 | 0.091553 | 0.013733 | 0.086975 | 122.9279 | 122.7264 | 0.18768
10553.6562 | 0.076294 | 0.21683 | -0.20401 | -0.23498 | -0.097198 | -0.24567 | -0.050201 | 0.09613 | 0.022888 | 0.045776 | 0.050354 | 0.14191 | -0.013733 | 0.12817 | 0.061035 | 0.05127 | -0.18692 | -0.01709 | -0.10254 | -0.060883 | 0.059509 | 0.10986 | -0.009155 | 0.11902 | 0.11444 | 0.036621 | 0.10529 | 122.9553 | 122.644 | 0.13733
10555.3906 | 0.045776 | 0.25314 | -0.21149 | -0.2478 | -0.10254 | -0.30121 | -0.071564 | 0.054932 | 0.036621 | 0.082397 | 0.050354 | 0.10986 | -0.054932 | 0.082397 | 0.061035 | 0.02243 | -0.1944 | -0.028839 | -0.12711 | -0.036316 | 0.045776 | 0.10986 | 0.050354 | 0.091553 | 0.10071 | 0.009155 | 0.082397 | 122.8867 | 122.7219 | 0.17395
10557.1562 | 0.045776 | 0.22324 | -0.20721 | -0.24887 | -0.089722 | -0.2713 | -0.058746 | 0.10071 | 0.086975 | 0.13275 | 0.09613 | 0.11444 | -0.022888 | 0.09613 | 0.061035 | 0.028839 | -0.18585 | -0.028839 | -0.1207 | -0.050201 | 0.068665 | 0.19226 | 0.054932 | 0.10529 | 0.086975 | 0.036621 | 0.086975 | 122.8867 | 122.699 | 0.1831
10558.9375 | 0.045776 | 0.22964 | -0.22217 | -0.24674 | -0.099335 | -0.25635 | -0.054474 | 0.050354 | -0.045776 | -0.013733 | 0.018311 | 0.14191 | 0.013733 | 0.13275 | 0.061035 | 0.053406 | -0.19653 | -0.027771 | -0.11108 | -0.060883 | -0.032043 | 0.059509 | -0.041199 | 0.14191 | 0.13275 | 0.041199 | 0.11444 | 122.9462 | 122.6669 | 0.16937
10560.75 | 0.076294 | 0.20615 | -0.20935 | -0.23712 | -0.09079 | -0.24246 | -0.049133 | 0.091553 | 0.018311 | 0.050354 | 0.068665 | 0.14191 | 0 | 0.11444 | 0.045776 | 0.05661 | -0.19974 | -0.030975 | -0.098267 | -0.05127 | 0.022888 | 0.12817 | -0.013733 | 0.13275 | 0.1236 | 0.036621 | 0.10529 | 123.0011 | 122.6349 | 0.14191
10562.4688 | 0.061035 | 0.22537 | -0.20187 | -0.23712 | -0.10895 | -0.2478 | -0.048065 | 0.11444 | 0.004578 | 0.036621 | 0.054932 | 0.11444 | -0.009155 | 0.10986 | 0.045776 | 0.0737 | -0.20187 | -0.027771 | -0.1004 | -0.05127 | 0.013733 | 0.10071 | -0.032043 | 0.12817 | 0.11902 | 0.041199 | 0.10071 | 122.9462 | 122.6578 | 0.15564
10564.2344 | 0.061035 | 0.22858 | -0.22324 | -0.2478 | -0.091858 | -0.26703 | -0.052338 | 0.009155 | -0.041199 | 0.009155 | 0.004578 | 0.12817 | 0.004578 | 0.14648 | 0.045776 | 0.054474 | -0.19012 | -0.009613 | -0.12283 | -0.044861 | -0.027466 | 0.07782 | -0.045776 | 0.14191 | 0.11902 | 0.045776 | 0.11444 | 122.8867 | 122.6852 | 0.1831
10566.0312 | 0.045776 | 0.22217 | -0.20935 | -0.26062 | -0.10895 | -0.27451 | -0.050201 | 0.041199 | -0.032043 | 0.041199 | 0.027466 | 0.12817 | -0.004578 | 0.11444 | 0.030518 | 0.055542 | -0.19546 | -0.023499 | -0.12924 | -0.040588 | -0.022888 | 0.09613 | -0.032043 | 0.15106 | 0.1236 | 0.064087 | 0.11444 | 122.8729 | 122.6761 | 0.19226
10567.75 | 0.061035 | 0.21576 | -0.1976 | -0.23712 | -0.11856 | -0.24353 | -0.041656 | 0.050354 | -0.054932 | -0.013733 | 0.027466 | 0.15564 | -0.004578 | 0.1236 | 0.045776 | 0.089722 | -0.21255 | -0.011749 | -0.10681 | -0.05127 | -0.041199 | 0.050354 | -0.073242 | 0.17853 | 0.14191 | 0.054932 | 0.11444 | 122.9462 | 122.6395 | 0.1831
10569.4688 | 0.076294 | 0.25528 | -0.22324 | -0.23392 | -0.10361 | -0.29587 | -0.053406 | 0.059509 | 0.027466 | 0.07782 | 0.045776 | 0.10986 | -0.022888 | 0.086975 | 0.045776 | 0.063019 | -0.23285 | -0.025635 | -0.12283 | -0.041656 | 0.036621 | 0.13275 | 0.036621 | 0.15106 | 0.13275 | 0.036621 | 0.07782 | 122.8821 | 122.6624 | 0.21973
10571.25 | 0.076294 | 0.22858 | -0.23285 | -0.23392 | -0.10788 | -0.27771 | -0.066223 | 0.064087 | 0.018311 | 0.07782 | 0.050354 | 0.11444 | -0.032043 | 0.086975 | 0.076294 | 0.064087 | -0.2243 | -0.027771 | -0.1239 | -0.046997 | 0.027466 | 0.14648 | 0.045776 | 0.13275 | 0.14191 | 0.013733 | 0.086975 | 122.905 | 122.6578 | 0.21515
10572.9844 | 0.076294 | 0.23712 | -0.2179 | -0.25635 | -0.092926 | -0.28305 | -0.0737 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.11444 | -0.041199 | 0.086975 | 0.061035 | 0.083313 | -0.23819 | -0.020294 | -0.12497 | -0.050201 | 0.11444 | 0.23346 | 0.11444 | 0.13733 | 0.12817 | 0.004578 | 0.068665 | 122.9279 | 122.6257 | 0.21057
10574.7812 | 0.045776 | 0.21683 | -0.19653 | -0.23819 | -0.099335 | -0.26062 | -0.054474 | 0.15564 | 0.059509 | 0.11444 | 0.11902 | 0.091553 | -0.050354 | 0.086975 | 0.045776 | 0.084381 | -0.2179 | -0.021362 | -0.11536 | -0.060883 | 0.10529 | 0.1831 | 0.073242 | 0.11902 | 0.10071 | -0.004578 | 0.064087 | 122.9874 | 122.6303 | 0.1831
10576.5625 | 0.061035 | 0.23285 | -0.22858 | -0.24353 | -0.093994 | -0.28305 | -0.059814 | 0.11444 | 0.073242 | 0.13275 | 0.091553 | 0.11444 | -0.036621 | 0.091553 | 0.061035 | 0.060883 | -0.21149 | -0.028839 | -0.12176 | -0.050201 | 0.11902 | 0.20599 | 0.091553 | 0.1236 | 0.10986 | 0.004578 | 0.064087 | 122.9279 | 122.6578 | 0.20142
10578.3594 | 0.045776 | 0.20828 | -0.20828 | -0.22644 | -0.1004 | -0.23712 | -0.049133 | 0.041199 | -0.073242 | -0.022888 | 0.009155 | 0.16022 | -0.009155 | 0.11902 | 0.045776 | 0.095062 | -0.24246 | -0.005341 | -0.092926 | -0.050201 | -0.013733 | 0.022888 | -0.07782 | 0.18768 | 0.15564 | 0.045776 | 0.10986 | 122.9782 | 122.6166 | 0.16937
10580.0781 | 0.045776 | 0.18906 | -0.21042 | -0.23285 | -0.10254 | -0.24246 | -0.046997 | 0.045776 | -0.082397 | -0.009155 | -0.004578 | 0.15106 | 0 | 0.11444 | 0.076294 | 0.09079 | -0.20935 | -0.009613 | -0.09613 | -0.048065 | -0.013733 | 0.027466 | -0.082397 | 0.17395 | 0.14648 | 0.054932 | 0.11444 | 122.9919 | 122.6303 | 0.16022
10581.8594 | 0.061035 | 0.22751 | -0.20721 | -0.23392 | -0.092926 | -0.24567 | -0.044861 | 0.050354 | -0.064087 | -0.013733 | 0.013733 | 0.14191 | 0.004578 | 0.1236 | 0.045776 | 0.1004 | -0.21255 | -0.014954 | -0.09613 | -0.049133 | -0.027466 | 0.036621 | -0.073242 | 0.17395 | 0.16022 | 0.050354 | 0.11444 | 122.9965 | 122.6532 | 0.15564
10583.6406 | 0.061035 | 0.22217 | -0.22003 | -0.23605 | -0.10361 | -0.26062 | -0.041656 | 0.068665 | -0.004578 | 0.050354 | 0.045776 | 0.10529 | -0.041199 | 0.10529 | 0.061035 | 0.09079 | -0.21469 | -0.019226 | -0.10574 | -0.038452 | 0.073242 | 0.14648 | 0.036621 | 0.15106 | 0.10986 | 0.009155 | 0.073242 | 123.024 | 122.6212 | 0.1831
10585.4375 | 0.076294 | 0.23392 | -0.22217 | -0.25742 | -0.10254 | -0.28839 | -0.044861 | 0.10529 | 0.1236 | 0.16022 | 0.10071 | 0.09613 | -0.050354 | 0.10071 | 0.045776 | 0.071564 | -0.22858 | -0.026703 | -0.11643 | -0.040588 | 0.086975 | 0.23346 | 0.086975 | 0.11902 | 0.11444 | 0.013733 | 0.07782 | 122.9279 | 122.6624 | 0.19684
10587.1562 | 0.045776 | 0.21683 | -0.22324 | -0.23392 | -0.10468 | -0.25101 | -0.050201 | 0.027466 | -0.07782 | -0.041199 | 0.009155 | 0.14191 | -0.004578 | 0.13275 | 0.061035 | 0.09079 | -0.2211 | -0.024567 | -0.099335 | -0.048065 | -0.018311 | 0.032043 | -0.082397 | 0.17853 | 0.15106 | 0.032043 | 0.10986 | 122.9965 | 122.644 | 0.1831
10588.9375 | 0.061035 | 0.23926 | -0.22217 | -0.25421 | -0.10788 | -0.28305 | -0.059814 | 0.12817 | 0.12817 | 0.15106 | 0.10071 | 0.10529 | -0.054932 | 0.09613 | 0.076294 | 0.070496 | -0.21362 | -0.020294 | -0.13031 | -0.050201 | 0.07782 | 0.23346 | 0.086975 | 0.13275 | 0.12817 | -0.004578 | 0.091553 | 122.9187 | 122.6578 | 0.19226
10590.7344 | 0.030518 | 0.23498 | -0.2179 | -0.25101 | -0.10147 | -0.26703 | -0.061951 | 0.050354 | 0 | 0.027466 | 0.036621 | 0.13733 | -0.004578 | 0.13733 | 0.045776 | 0.092926 | -0.23605 | -0.023499 | -0.10468 | -0.053406 | -0.032043 | 0.10986 | -0.045776 | 0.17395 | 0.15106 | 0.041199 | 0.09613 | 122.8867 | 122.6624 | 0.21057
10592.5312 | 0.061035 | 0.21576 | -0.21255 | -0.23178 | -0.10681 | -0.25207 | -0.055542 | 0.050354 | -0.082397 | -0.041199 | 0 | 0.13733 | -0.018311 | 0.11902 | 0.061035 | 0.10147 | -0.23392 | -0.026703 | -0.098267 | -0.043793 | -0.022888 | 0.022888 | -0.073242 | 0.16022 | 0.16937 | 0.032043 | 0.10986 | 122.9874 | 122.6303 | 0.1831
10594.2656 | 0.045776 | 0.20828 | -0.21576 | -0.23392 | -0.10254 | -0.26062 | -0.05127 | 0.050354 | -0.064087 | -0.009155 | 0.013733 | 0.13733 | 0 | 0.14648 | 0.061035 | 0.10361 | -0.22751 | -0.01709 | -0.10895 | -0.036316 | -0.036621 | 0.082397 | -0.059509 | 0.17853 | 0.15106 | 0.036621 | 0.09613 | 122.9874 | 122.6349 | 0.18768
10596.0312 | 0.061035 | 0.2179 | -0.21576 | -0.2478 | -0.10147 | -0.26382 | -0.059814 | 0.027466 | -0.045776 | -0.013733 | 0.013733 | 0.15564 | -0.004578 | 0.14648 | 0.061035 | 0.10574 | -0.22537 | -0.025635 | -0.11536 | -0.046997 | -0.022888 | 0.082397 | -0.045776 | 0.16022 | 0.16479 | 0.059509 | 0.10071 | 122.9874 | 122.6624 | 0.16937
10597.8125 | 0.076294 | 0.23285 | -0.20721 | -0.23392 | -0.10361 | -0.26596 | -0.05127 | 0.1236 | 0.059509 | 0.10071 | 0.091553 | 0.10529 | -0.054932 | 0.07782 | 0.045776 | 0.10574 | -0.2446 | -0.019226 | -0.10468 | -0.049133 | 0.09613 | 0.16479 | 0.064087 | 0.09613 | 0.10071 | -0.013733 | 0.068665 | 123.0011 | 122.6578 | 0.15106
10599.6094 | 0.061035 | 0.2243 | -0.20615 | -0.23712 | -0.089722 | -0.25528 | -0.050201 | 0.091553 | 0.027466 | 0.036621 | 0.059509 | 0.13733 | -0.004578 | 0.12817 | 0.061035 | 0.12176 | -0.24353 | -0.014954 | -0.11002 | -0.05127 | 0.036621 | 0.11902 | -0.027466 | 0.13733 | 0.11444 | 0.045776 | 0.10529 | 123.0148 | 122.6532 | 0.14648
10601.3438 | 0.061035 | 0.24246 | -0.21255 | -0.24994 | -0.09079 | -0.29587 | -0.058746 | 0.073242 | 0.059509 | 0.11444 | 0.073242 | 0.10986 | -0.032043 | 0.10529 | 0.045776 | 0.11002 | -0.26169 | -0.025635 | -0.11536 | -0.03952 | 0.068665 | 0.1831 | 0.091553 | 0.1236 | 0.091553 | 0.022888 | 0.086975 | 122.9279 | 122.6715 | 0.17395
10603.125 | 0.076294 | 0.24887 | -0.2243 | -0.23392 | -0.10895 | -0.29053 | -0.053406 | 0.064087 | 0.022888 | 0.082397 | 0.068665 | 0.11444 | -0.045776 | 0.10071 | 0.061035 | 0.11002 | -0.26596 | -0.023499 | -0.11536 | -0.044861 | 0.050354 | 0.13275 | 0.059509 | 0.10986 | 0.10986 | 0 | 0.091553 | 122.9141 | 122.6761 | 0.1831
10604.8438 | 0.061035 | 0.22217 | -0.20187 | -0.23071 | -0.095062 | -0.24139 | -0.053406 | 0.091553 | 0 | 0.022888 | 0.054932 | 0.14191 | -0.013733 | 0.11902 | 0.061035 | 0.14313 | -0.25742 | -0.013885 | -0.09613 | -0.053406 | 0.027466 | 0.11444 | -0.018311 | 0.13275 | 0.1236 | 0.050354 | 0.1236 | 123.0057 | 122.6257 | 0.15106
10606.6406 | 0.076294 | 0.21255 | -0.21255 | -0.23178 | -0.086517 | -0.24994 | -0.066223 | 0.059509 | -0.004578 | 0.013733 | 0.041199 | 0.1236 | -0.032043 | 0.11444 | 0.061035 | 0.12283 | -0.26703 | -0.019226 | -0.084381 | -0.055542 | -0.004578 | 0.041199 | -0.064087 | 0.14648 | 0.11902 | 0.050354 | 0.12817 | 122.9645 | 122.6532 | 0.16022
10608.4219 | 0.076294 | 0.22217 | -0.21896 | -0.24567 | -0.10361 | -0.28839 | -0.05661 | 0.10071 | 0.073242 | 0.10529 | 0.086975 | 0.091553 | -0.032043 | 0.091553 | 0.030518 | 0.10681 | -0.25207 | -0.033112 | -0.11002 | -0.038452 | 0.018311 | 0.15106 | 0.032043 | 0.10986 | 0.11444 | 0.022888 | 0.10071 | 122.85 | 122.7081 | 0.19226
10610.1562 | 0.045776 | 0.21896 | -0.20294 | -0.23926 | -0.099335 | -0.24353 | -0.05127 | 0.10529 | 0.018311 | 0.054932 | 0.054932 | 0.12817 | -0.013733 | 0.1236 | 0.076294 | 0.12924 | -0.24246 | -0.026703 | -0.099335 | -0.044861 | 0.036621 | 0.11444 | -0.013733 | 0.1236 | 0.12817 | 0.027466 | 0.10986 | 122.9599 | 122.6486 | 0.13275
10611.9375 | 0.061035 | 0.22537 | -0.21042 | -0.22858 | -0.10254 | -0.24887 | -0.046997 | 0.082397 | 0.018311 | 0.050354 | 0.054932 | 0.14191 | -0.018311 | 0.11902 | 0.061035 | 0.13031 | -0.25742 | -0.007477 | -0.095062 | -0.048065 | 0.032043 | 0.12817 | -0.009155 | 0.13275 | 0.10529 | 0.050354 | 0.086975 | 122.9828 | 122.6852 | 0.16022
10613.7344 | 0.061035 | 0.20615 | -0.20294 | -0.2478 | -0.098267 | -0.25207 | -0.048065 | 0.07782 | 0.013733 | 0.045776 | 0.041199 | 0.13733 | -0.013733 | 0.13275 | 0.015259 | 0.12283 | -0.24994 | -0.018158 | -0.10254 | -0.05127 | 0.022888 | 0.12817 | -0.009155 | 0.1236 | 0.10986 | 0.041199 | 0.1236 | 123.0011 | 122.6578 | 0.12817
10615.5312 | 0.061035 | 0.23071 | -0.21576 | -0.24567 | -0.093994 | -0.27237 | -0.041656 | 0.10529 | 0.07782 | 0.12817 | 0.10071 | 0.09613 | -0.068665 | 0.091553 | 0.076294 | 0.11643 | -0.24887 | -0.019226 | -0.10788 | -0.045929 | 0.09613 | 0.16479 | 0.086975 | 0.09613 | 0.082397 | 0.009155 | 0.082397 | 122.9965 | 122.6807 | 0.14648
10617.25 | 0.061035 | 0.20828 | -0.21042 | -0.23392 | -0.095062 | -0.25742 | -0.040588 | 0.10071 | 0.013733 | 0.041199 | 0.054932 | 0.14191 | -0.004578 | 0.1236 | 0.061035 | 0.13245 | -0.25635 | -0.019226 | -0.1004 | -0.054474 | 0.018311 | 0.07782 | -0.032043 | 0.1236 | 0.11902 | 0.027466 | 0.10529 | 122.9507 | 122.6486 | 0.13733
10619.0156 | 0.076294 | 0.23178 | -0.21896 | -0.23392 | -0.10254 | -0.27344 | -0.05127 | 0.082397 | 0.032043 | 0.07782 | 0.068665 | 0.12817 | -0.041199 | 0.10071 | 0.045776 | 0.11856 | -0.25955 | -0.018158 | -0.10468 | -0.048065 | 0.082397 | 0.14191 | 0.054932 | 0.10529 | 0.10071 | 0.018311 | 0.073242 | 123.024 | 122.6624 | 0.14648
10620.7656 | 0.076294 | 0.22217 | -0.20187 | -0.23071 | -0.10254 | -0.26916 | -0.061951 | 0.082397 | -0.013733 | 0.064087 | 0.045776 | 0.12817 | -0.027466 | 0.11444 | 0.061035 | 0.13458 | -0.25742 | -0.018158 | -0.10468 | -0.045929 | 0.059509 | 0.12817 | 0.050354 | 0.09613 | 0.09613 | 0.022888 | 0.073242 | 123.0194 | 122.6669 | 0.12817
10622.5625 | 0.061035 | 0.23712 | -0.21576 | -0.22537 | -0.10681 | -0.2713 | -0.053406 | 0.13733 | 0.059509 | 0.10071 | 0.09613 | 0.091553 | -0.045776 | 0.086975 | 0.030518 | 0.1239 | -0.26703 | -0.027771 | -0.10254 | -0.053406 | 0.09613 | 0.16022 | 0.082397 | 0.082397 | 0.073242 | 0.013733 | 0.073242 | 123.0103 | 122.6761 | 0.13733
10624.3438 | 0.061035 | 0.22858 | -0.21576 | -0.23178 | -0.10361 | -0.27878 | -0.054474 | 0.10986 | 0.082397 | 0.13275 | 0.086975 | 0.086975 | -0.041199 | 0.091553 | 0.061035 | 0.11963 | -0.26703 | -0.030975 | -0.10788 | -0.043793 | 0.091553 | 0.15564 | 0.082397 | 0.091553 | 0.07782 | 0.004578 | 0.073242 | 122.8867 | 122.7127 | 0.16022
10626.1406 | 0.061035 | 0.23178 | -0.21362 | -0.24994 | -0.099335 | -0.28412 | -0.061951 | 0.11444 | 0.091553 | 0.14191 | 0.09613 | 0.091553 | -0.041199 | 0.10529 | 0.030518 | 0.11215 | -0.26382 | -0.040588 | -0.12176 | -0.057678 | 0.068665 | 0.19226 | 0.086975 | 0.10071 | 0.091553 | 0.027466 | 0.091553 | 122.8775 | 122.6944 | 0.1831
10627.9219 | 0.061035 | 0.24887 | -0.20721 | -0.24353 | -0.10254 | -0.29159 | -0.063019 | 0.064087 | 0.009155 | 0.07782 | 0.064087 | 0.11444 | -0.032043 | 0.10529 | 0.061035 | 0.11429 | -0.26169 | -0.030975 | -0.11749 | -0.046997 | 0.054932 | 0.13733 | 0.073242 | 0.091553 | 0.10071 | 0.018311 | 0.086975 | 122.937 | 122.6761 | 0.16937
10629.7031 | 0.045776 | 0.21362 | -0.20935 | -0.24139 | -0.10147 | -0.24887 | -0.052338 | 0.059509 | -0.041199 | -0.013733 | 0.032043 | 0.13275 | 0.004578 | 0.15106 | 0.061035 | 0.14847 | -0.26916 | -0.01709 | -0.10147 | -0.077972 | -0.009155 | 0.086975 | -0.036621 | 0.12817 | 0.10986 | 0.045776 | 0.10986 | 123.0011 | 122.6669 | 0.11444
10631.4375 | 0.076294 | 0.21042 | -0.20721 | -0.2446 | -0.11643 | -0.25528 | -0.052338 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.1236 | -0.027466 | 0.13275 | 0.045776 | 0.14206 | -0.26276 | -0.007477 | -0.10361 | -0.070496 | 0 | 0.013733 | -0.054932 | 0.13275 | 0.11902 | 0.045776 | 0.11444 | 123.0148 | 122.6807 | 0.1236
10633.2031 | 0.030518 | 0.24674 | -0.21362 | -0.22644 | -0.095062 | -0.28305 | -0.063019 | 0.082397 | 0.045776 | 0.07782 | 0.050354 | 0.10529 | -0.041199 | 0.091553 | 0.015259 | 0.12176 | -0.27023 | -0.025635 | -0.11322 | -0.043793 | 0.050354 | 0.12817 | 0.045776 | 0.07782 | 0.091553 | -0.009155 | 0.068665 | 122.8821 | 122.731 | 0.16937
10634.9375 | 0.061035 | 0.22537 | -0.21576 | -0.25848 | -0.10254 | -0.28839 | -0.05661 | 0.068665 | 0.018311 | 0.068665 | 0.068665 | 0.11902 | -0.054932 | 0.09613 | 0.061035 | 0.12604 | -0.25101 | -0.008545 | -0.12497 | -0.057678 | 0.032043 | 0.10986 | 0.050354 | 0.091553 | 0.10071 | 0.013733 | 0.086975 | 122.8043 | 122.7127 | 0.17853
10636.7188 | 0.061035 | 0.22003 | -0.20935 | -0.23178 | -0.10468 | -0.25314 | -0.05127 | 0.073242 | -0.054932 | -0.009155 | 0.018311 | 0.13275 | -0.022888 | 0.13733 | 0.061035 | 0.15488 | -0.2713 | -0.009613 | -0.09613 | -0.059814 | 0.009155 | 0.036621 | -0.041199 | 0.11444 | 0.091553 | 0.036621 | 0.09613 | 123.0194 | 122.6761 | 0.13275
10638.4375 | 0.045776 | 0.23819 | -0.21149 | -0.22751 | -0.11963 | -0.28625 | -0.063019 | 0.068665 | 0.018311 | 0.068665 | 0.054932 | 0.10986 | -0.032043 | 0.082397 | 0.045776 | 0.13031 | -0.27344 | -0.011749 | -0.11643 | -0.046997 | 0.036621 | 0.11902 | 0.050354 | 0.10986 | 0.073242 | 0.018311 | 0.09613 | 122.9141 | 122.7402 | 0.1831
10640.2188 | 0.061035 | 0.1944 | -0.21683 | -0.23178 | -0.093994 | -0.23605 | -0.05127 | 0.1236 | 0 | 0.045776 | 0.059509 | 0.14648 | -0.027466 | 0.12817 | 0.045776 | 0.1442 | -0.25848 | -0.019226 | -0.091858 | -0.063019 | 0.032043 | 0.11444 | -0.022888 | 0.14191 | 0.13733 | 0.045776 | 0.11444 | 123.0011 | 122.6669 | 0.13275
10642.0156 | 0.076294 | 0.2243 | -0.20935 | -0.23285 | -0.10468 | -0.25421 | -0.045929 | 0.073242 | -0.041199 | 0.018311 | 0.027466 | 0.14191 | -0.027466 | 0.10986 | 0.076294 | 0.1442 | -0.2681 | -0.008545 | -0.095062 | -0.055542 | 0.045776 | 0.09613 | 0.009155 | 0.10071 | 0.086975 | 0.013733 | 0.091553 | 123.0331 | 122.6852 | 0.13733
10643.75 | 0.045776 | 0.23178 | -0.21149 | -0.23605 | -0.092926 | -0.27237 | -0.053406 | 0.13733 | 0.068665 | 0.11902 | 0.10071 | 0.10529 | -0.041199 | 0.091553 | 0.061035 | 0.14313 | -0.25421 | -0.018158 | -0.099335 | -0.046997 | 0.09613 | 0.15106 | 0.064087 | 0.086975 | 0.07782 | 0.018311 | 0.064087 | 123.0011 | 122.6669 | 0.13275
10645.5469 | 0.045776 | 0.25528 | -0.10681 | -0.23178 | -0.091858 | -0.29053 | -0.057678 | 0.082397 | 0.045776 | 0.09613 | 0.068665 | 0.10529 | -0.041199 | 0.10071 | 0.076294 | 0.11536 | -0.28305 | -0.024567 | -0.12176 | -0.03952 | 0.073242 | 0.17853 | 0.082397 | 0.09613 | 0.082397 | 0.018311 | 0.073242 | 122.9233 | 122.6898 | 0.16479
10647.3281 | 0.045776 | 0.23498 | -0.21896 | -0.24994 | -0.10895 | -0.28412 | -0.059814 | 0.14191 | 0.1236 | 0.14191 | 0.091553 | 0.10986 | -0.050354 | 0.10071 | 0.045776 | 0.11963 | -0.25101 | -0.024567 | -0.12497 | -0.059814 | 0.086975 | 0.21973 | 0.086975 | 0.091553 | 0.073242 | -0.013733 | 0.082397 | 122.9095 | 122.6852 | 0.17395
10649.0938 | 0.076294 | 0.22964 | -0.20401 | -0.25635 | -0.095062 | -0.28091 | -0.0737 | 0.10986 | 0.045776 | 0.086975 | 0.073242 | 0.11444 | -0.018311 | 0.10529 | 0.061035 | 0.12924 | -0.24887 | -0.01709 | -0.11963 | -0.053406 | 0 | 0.12817 | -0.009155 | 0.12817 | 0.11902 | 0.036621 | 0.11444 | 122.8729 | 122.731 | 0.16937
10650.9219 | 0.076294 | 0.22537 | -0.20935 | -0.25101 | -0.097198 | -0.24994 | -0.052338 | 0.045776 | -0.041199 | -0.009155 | 0.004578 | 0.13733 | -0.004578 | 0.13733 | 0.061035 | 0.13565 | -0.25101 | -0.014954 | -0.10895 | -0.058746 | -0.041199 | 0.068665 | -0.068665 | 0.14648 | 0.1236 | 0.050354 | 0.12817 | 122.9233 | 122.6898 | 0.16022
10652.7188 | 0.061035 | 0.22964 | -0.21255 | -0.2179 | -0.1004 | -0.25314 | -0.046997 | 0.064087 | -0.036621 | -0.004578 | 0.018311 | 0.15106 | -0.027466 | 0.11902 | 0.061035 | 0.13992 | -0.26489 | -0.01709 | -0.1004 | -0.059814 | 0.022888 | 0.059509 | -0.027466 | 0.11902 | 0.10986 | 0.032043 | 0.10071 | 123.0148 | 122.644 | 0.1236
10654.5 | 0.045776 | 0.22964 | -0.21683 | -0.25101 | -0.11108 | -0.26169 | -0.05661 | 0.041199 | -0.045776 | 0.004578 | 0.013733 | 0.13733 | -0.004578 | 0.13275 | 0.030518 | 0.13672 | -0.24139 | -0.013885 | -0.10895 | -0.055542 | -0.032043 | 0.07782 | -0.068665 | 0.13733 | 0.11902 | 0.045776 | 0.10986 | 122.9187 | 122.7173 | 0.16022
10656.2188 | 0.061035 | 0.20828 | -0.21362 | -0.24353 | -0.087585 | -0.2713 | -0.054474 | 0.045776 | -0.041199 | 0.004578 | 0.036621 | 0.13733 | -0.004578 | 0.13733 | 0.076294 | 0.13458 | -0.25101 | -0.019226 | -0.11429 | -0.061951 | -0.009155 | 0.07782 | -0.032043 | 0.13275 | 0.11902 | 0.022888 | 0.10071 | 123.0011 | 122.6715 | 0.12817
10658 | 0.045776 | 0.2243 | -0.21896 | -0.22324 | -0.10147 | -0.27344 | -0.043793 | 0.11444 | 0.054932 | 0.10986 | 0.073242 | 0.09613 | -0.045776 | 0.082397 | 0.045776 | 0.13138 | -0.25421 | -0.009613 | -0.09613 | -0.049133 | 0.091553 | 0.16022 | 0.045776 | 0.07782 | 0.07782 | 0.004578 | 0.054932 | 122.9965 | 122.6761 | 0.13275
10659.7812 | 0.061035 | 0.22324 | -0.20294 | -0.23392 | -0.097198 | -0.24674 | -0.040588 | 0.073242 | -0.018311 | 0.009155 | 0.032043 | 0.12817 | -0.013733 | 0.11902 | 0.030518 | 0.15701 | -0.24994 | -0.014954 | -0.092926 | -0.05661 | -0.018311 | 0.064087 | -0.059509 | 0.13275 | 0.10986 | 0.013733 | 0.091553 | 122.9645 | 122.6898 | 0.14191
10661.5781 | 0.061035 | 0.25101 | -0.21896 | -0.22217 | -0.11856 | -0.29694 | -0.054474 | 0.059509 | 0.054932 | 0.086975 | 0.054932 | 0.091553 | -0.036621 | 0.091553 | 0.061035 | 0.1239 | -0.25955 | -0.020294 | -0.12283 | -0.053406 | 0.022888 | 0.12817 | 0.027466 | 0.086975 | 0.10529 | 0 | 0.082397 | 122.8912 | 122.699 | 0.17853
10663.2969 | 0.061035 | 0.26382 | -0.22324 | -0.22537 | -0.11322 | -0.27771 | -0.063019 | 0.09613 | 0.086975 | 0.12817 | 0.086975 | 0.10529 | -0.050354 | 0.082397 | 0.076294 | 0.12817 | -0.28091 | -0.012817 | -0.11643 | -0.054474 | 0.09613 | 0.19226 | 0.09613 | 0.10529 | 0.073242 | 0.018311 | 0.059509 | 122.9416 | 122.6944 | 0.15106
10665.0625 | 0.045776 | 0.22324 | -0.2211 | -0.25742 | -0.11215 | -0.27451 | -0.055542 | 0.11444 | 0.086975 | 0.11902 | 0.10071 | 0.11444 | -0.054932 | 0.09613 | 0.030518 | 0.13565 | -0.25848 | -0.01709 | -0.11643 | -0.070496 | 0.050354 | 0.17853 | 0.068665 | 0.091553 | 0.073242 | 0.013733 | 0.068665 | 122.8638 | 122.699 | 0.16937
10666.8594 | 0.030518 | 0.21042 | -0.20401 | -0.24887 | -0.10254 | -0.24139 | -0.054474 | 0.09613 | -0.018311 | 0.036621 | 0.045776 | 0.15106 | -0.013733 | 0.11444 | 0.061035 | 0.16342 | -0.25421 | 0.004272 | -0.095062 | -0.072632 | -0.004578 | 0.10529 | -0.027466 | 0.10986 | 0.11444 | 0.036621 | 0.091553 | 123.0057 | 122.644 | 0.13275
10668.5938 | 0.030518 | 0.24567 | -0.22003 | -0.23605 | -0.09079 | -0.28625 | -0.048065 | 0.07782 | 0.018311 | 0.082397 | 0.073242 | 0.10986 | -0.045776 | 0.09613 | 0.045776 | 0.13138 | -0.26916 | -0.011749 | -0.12176 | -0.050201 | 0.032043 | 0.10529 | 0.036621 | 0.082397 | 0.09613 | -0.009155 | 0.09613 | 122.8867 | 122.7219 | 0.18768
10670.375 | 0.030518 | 0.21576 | -0.20187 | -0.24353 | -0.098267 | -0.23819 | -0.052338 | 0.10529 | 0.022888 | 0.022888 | 0.059509 | 0.14191 | -0.022888 | 0.13275 | 0.030518 | 0.15915 | -0.25314 | -0.005341 | -0.093994 | -0.086517 | 0.032043 | 0.11444 | -0.018311 | 0.11444 | 0.09613 | 0.041199 | 0.091553 | 122.9919 | 122.6715 | 0.13733
10672.1562 | 0.076294 | 0.24674 | -0.23285 | -0.23926 | -0.092926 | -0.26916 | -0.060883 | 0.068665 | 0.045776 | 0.059509 | 0.054932 | 0.091553 | -0.022888 | 0.11902 | 0.061035 | 0.13779 | -0.26703 | -0.002136 | -0.10574 | -0.060883 | -0.018311 | 0.10986 | -0.022888 | 0.1236 | 0.10986 | 0.045776 | 0.1236 | 122.8867 | 122.7081 | 0.16479
10673.9531 | 0.030518 | 0.2446 | -0.2243 | -0.23498 | -0.10681 | -0.28519 | -0.053406 | 0.082397 | 0.059509 | 0.09613 | 0.064087 | 0.10986 | -0.041199 | 0.09613 | 0.030518 | 0.13031 | -0.25848 | -0.016022 | -0.11002 | -0.05661 | 0.054932 | 0.1236 | 0.054932 | 0.09613 | 0.091553 | 0.004578 | 0.091553 | 122.8775 | 122.7081 | 0.16937
10675.75 | 0.045776 | 0.23712 | -0.21149 | -0.25528 | -0.10147 | -0.28625 | -0.05661 | 0.11444 | 0.07782 | 0.13733 | 0.073242 | 0.10986 | -0.022888 | 0.086975 | 0.076294 | 0.13138 | -0.26169 | -0.018158 | -0.1239 | -0.055542 | 0.091553 | 0.18768 | 0.09613 | 0.09613 | 0.09613 | 0.018311 | 0.064087 | 122.9279 | 122.699 | 0.17395
10677.4844 | 0.076294 | 0.20935 | -0.21469 | -0.23498 | -0.093994 | -0.24139 | -0.05661 | 0.073242 | -0.009155 | 0.018311 | 0.050354 | 0.13275 | -0.004578 | 0.11902 | 0.076294 | 0.14847 | -0.25101 | -0.018158 | -0.095062 | -0.074768 | 0.004578 | 0.091553 | -0.013733 | 0.13275 | 0.10529 | 0.054932 | 0.10071 | 122.9965 | 122.6578 | 0.11902
10679.25 | 0.061035 | 0.21362 | -0.20828 | -0.2243 | -0.10254 | -0.24994 | -0.055542 | 0.045776 | -0.059509 | -0.022888 | 0.018311 | 0.12817 | 0.004578 | 0.14191 | 0.030518 | 0.1442 | -0.2446 | -0.036316 | -0.099335 | -0.042725 | 0.004578 | 0.032043 | -0.027466 | 0.13275 | 0.1236 | 0.050354 | 0.10071 | 123.0194 | 122.6715 | 0.12817
10681.0469 | 0.045776 | 0.22324 | -0.21042 | -0.23926 | -0.11429 | -0.25314 | -0.046997 | 0.032043 | -0.054932 | -0.009155 | 0.004578 | 0.13275 | -0.004578 | 0.12817 | 0.061035 | 0.15274 | -0.26062 | -0.035248 | -0.098267 | -0.029907 | -0.018311 | 0.013733 | -0.068665 | 0.13275 | 0.10071 | 0.045776 | 0.11444 | 122.9782 | 122.6486 | 0.14191
10682.7812 | 0.061035 | 0.23498 | -0.21683 | -0.25101 | -0.087585 | -0.2948 | -0.065155 | 0.11902 | 0.11444 | 0.14191 | 0.09613 | 0.10529 | -0.050354 | 0.07782 | 0.061035 | 0.12711 | -0.24887 | -0.040588 | -0.11429 | -0.026703 | 0.054932 | 0.20142 | 0.091553 | 0.091553 | 0.09613 | 0 | 0.086975 | 122.8867 | 122.6578 | 0.16022
10684.5 | 0.061035 | 0.22858 | -0.22217 | -0.24994 | -0.11002 | -0.28625 | -0.063019 | 0.082397 | 0.054932 | 0.09613 | 0.050354 | 0.09613 | -0.022888 | 0.091553 | 0.061035 | 0.12924 | -0.24674 | -0.026703 | -0.13138 | -0.040588 | 0.036621 | 0.13275 | 0.050354 | 0.10529 | 0.086975 | 0.018311 | 0.082397 | 122.8729 | 122.7081 | 0.20142
10686.2969 | 0.045776 | 0.25955 | -0.23285 | -0.23498 | -0.11322 | -0.28198 | -0.058746 | 0.073242 | 0.036621 | 0.07782 | 0.064087 | 0.10529 | -0.027466 | 0.10071 | 0.030518 | 0.13672 | -0.25742 | -0.049133 | -0.1004 | -0.037384 | 0.022888 | 0.11902 | 0.045776 | 0.10529 | 0.091553 | 0.009155 | 0.073242 | 122.9004 | 122.6944 | 0.19684
10688.0156 | 0.030518 | 0.2179 | -0.21362 | -0.23178 | -0.10574 | -0.23926 | -0.049133 | 0.1236 | 0.022888 | 0.032043 | 0.050354 | 0.12817 | -0.018311 | 0.10986 | 0.061035 | 0.15701 | -0.25207 | -0.036316 | -0.086517 | -0.052338 | 0.022888 | 0.10071 | -0.041199 | 0.11902 | 0.11444 | 0.036621 | 0.10986 | 122.9736 | 122.6852 | 0.15564
10689.7969 | 0.061035 | 0.23819 | -0.21896 | -0.24567 | -0.11215 | -0.27985 | -0.043793 | 0.064087 | 0.041199 | 0.082397 | 0.054932 | 0.10071 | -0.032043 | 0.09613 | 0.061035 | 0.11002 | -0.23071 | -0.054474 | -0.1239 | -0.021362 | 0.004578 | 0.11444 | 0.022888 | 0.13275 | 0.09613 | 0.022888 | 0.073242 | 122.8958 | 122.7081 | 0.19684
10691.5781 | 0.061035 | 0.24674 | -0.22217 | -0.23605 | -0.10574 | -0.2713 | -0.057678 | 0.10071 | 0.041199 | 0.09613 | 0.059509 | 0.09613 | -0.045776 | 0.086975 | 0.061035 | 0.10788 | -0.22858 | -0.036316 | -0.11322 | -0.028839 | 0.045776 | 0.13733 | 0.022888 | 0.1236 | 0.10071 | 0.027466 | 0.07782 | 122.8821 | 122.6898 | 0.18768
10693.3594 | 0.045776 | 0.23071 | -0.21469 | -0.23498 | -0.10468 | -0.26596 | -0.055542 | 0.13733 | 0.07782 | 0.13275 | 0.086975 | 0.09613 | -0.036621 | 0.09613 | 0.061035 | 0.11002 | -0.23285 | -0.035248 | -0.11643 | -0.027771 | 0.086975 | 0.14648 | 0.050354 | 0.10529 | 0.09613 | 0 | 0.073242 | 122.8821 | 122.699 | 0.17395
10695.125 | 0.045776 | 0.21683 | -0.22537 | -0.22537 | -0.097198 | -0.25528 | -0.053406 | 0.10071 | -0.027466 | 0.032043 | 0.032043 | 0.12817 | -0.018311 | 0.10529 | 0.061035 | 0.13351 | -0.23712 | -0.033112 | -0.089722 | -0.026703 | 0.068665 | 0.1236 | 0.013733 | 0.11444 | 0.11444 | 0.004578 | 0.07782 | 123.0286 | 122.6349 | 0.16937
10696.8594 | 0.061035 | 0.21576 | -0.21255 | -0.23285 | -0.095062 | -0.24674 | -0.045929 | 0.045776 | -0.059509 | -0.013733 | 0.004578 | 0.15106 | -0.018311 | 0.13275 | 0.061035 | 0.1239 | -0.23178 | -0.038452 | -0.09079 | -0.033112 | -0.009155 | 0.045776 | -0.068665 | 0.14191 | 0.11902 | 0.027466 | 0.10529 | 123.0103 | 122.6212 | 0.13733
10698.6406 | 0.061035 | 0.20508 | -0.21042 | -0.25101 | -0.1004 | -0.2446 | -0.052338 | 0.10529 | 0 | 0.036621 | 0.059509 | 0.13733 | 0 | 0.10986 | 0.076294 | 0.13565 | -0.22644 | -0.042725 | -0.10895 | -0.023499 | 0.009155 | 0.1236 | -0.018311 | 0.13733 | 0.11902 | 0.027466 | 0.091553 | 123.0011 | 122.6486 | 0.16479
10700.3594 | 0.045776 | 0.25207 | -0.22324 | -0.22751 | -0.086517 | -0.28946 | -0.054474 | 0.10529 | 0.073242 | 0.11444 | 0.07782 | 0.091553 | -0.041199 | 0.10529 | 0.076294 | 0.11108 | -0.23712 | -0.044861 | -0.11749 | -0.023499 | 0.036621 | 0.14191 | 0.041199 | 0.10071 | 0.09613 | 0 | 0.091553 | 122.8775 | 122.7081 | 0.17853
10702.1562 | 0.030518 | 0.21896 | -0.20935 | -0.24567 | -0.10468 | -0.25101 | -0.05127 | 0.068665 | -0.009155 | 0.032043 | 0.041199 | 0.11902 | -0.022888 | 0.086975 | 0.076294 | 0.13138 | -0.23498 | -0.038452 | -0.1004 | -0.043793 | 0.041199 | 0.13275 | 0.022888 | 0.1236 | 0.10529 | -0.004578 | 0.073242 | 122.9965 | 122.6395 | 0.16479
10703.8906 | 0.076294 | 0.22644 | -0.20721 | -0.25742 | -0.093994 | -0.27237 | -0.050201 | 0.041199 | -0.036621 | 0.018311 | 0.004578 | 0.14648 | 0.004578 | 0.14648 | 0.061035 | 0.13779 | -0.21576 | -0.021362 | -0.1207 | -0.043793 | -0.050354 | 0.064087 | -0.054932 | 0.15106 | 0.14191 | 0.050354 | 0.10986 | 122.9141 | 122.6944 | 0.16479
10705.6719 | 0.045776 | 0.20401 | -0.2179 | -0.26062 | -0.1207 | -0.25314 | -0.052338 | 0.091553 | 0.022888 | 0.041199 | 0.054932 | 0.14191 | -0.009155 | 0.12817 | 0.091553 | 0.1474 | -0.21896 | -0.024567 | -0.11002 | -0.05661 | 0 | 0.1236 | -0.027466 | 0.14191 | 0.12817 | 0.022888 | 0.09613 | 123.0011 | 122.6486 | 0.14191
10707.4688 | 0.061035 | 0.2179 | -0.20615 | -0.22217 | -0.099335 | -0.24353 | -0.049133 | 0.036621 | -0.064087 | -0.009155 | 0.018311 | 0.13733 | 0.004578 | 0.13733 | 0.061035 | 0.13886 | -0.23285 | -0.014954 | -0.10254 | -0.043793 | -0.054932 | 0.045776 | -0.091553 | 0.12817 | 0.14648 | 0.022888 | 0.10071 | 122.9507 | 122.6486 | 0.16479
10709.25 | 0.061035 | 0.23071 | -0.21683 | -0.24887 | -0.1004 | -0.298 | -0.057678 | 0.13275 | 0.11902 | 0.13733 | 0.10986 | 0.11444 | -0.032043 | 0.10529 | 0.061035 | 0.13031 | -0.24246 | -0.038452 | -0.12711 | -0.029907 | 0.068665 | 0.21973 | 0.09613 | 0.091553 | 0.091553 | 0.009155 | 0.064087 | 122.905 | 122.6715 | 0.1831
10710.9688 | 0.045776 | 0.22537 | -0.21576 | -0.24246 | -0.10254 | -0.26382 | -0.060883 | 0.054932 | -0.041199 | 0.013733 | 0.022888 | 0.12817 | 0 | 0.12817 | 0.030518 | 0.13886 | -0.24033 | -0.025635 | -0.10681 | -0.037384 | 0.009155 | 0.059509 | -0.027466 | 0.14648 | 0.12817 | 0.018311 | 0.07782 | 123.0057 | 122.6257 | 0.15106
10712.7656 | 0.045776 | 0.24033 | -0.21896 | -0.2243 | -0.10147 | -0.28198 | -0.058746 | 0.14191 | 0.073242 | 0.11902 | 0.09613 | 0.10071 | -0.036621 | 0.086975 | 0.076294 | 0.12711 | -0.23712 | -0.037384 | -0.11429 | -0.033112 | 0.07782 | 0.1831 | 0.073242 | 0.10529 | 0.09613 | -0.009155 | 0.059509 | 122.9004 | 122.6807 | 0.16479
10714.5469 | 0.091553 | 0.23819 | -0.2243 | -0.24887 | -0.088654 | -0.25421 | -0.071564 | 0.045776 | -0.054932 | 0 | 0.027466 | 0.16479 | -0.009155 | 0.13275 | 0.045776 | 0.14633 | -0.21469 | -0.043793 | -0.11429 | -0.028839 | -0.050354 | 0.073242 | -0.064087 | 0.14191 | 0.14191 | 0.036621 | 0.10986 | 122.9691 | 122.6532 | 0.17395
10716.2656 | 0.061035 | 0.20187 | -0.21683 | -0.25848 | -0.098267 | -0.26489 | -0.059814 | 0.068665 | -0.041199 | 0.004578 | 0.036621 | 0.11902 | 0.009155 | 0.1236 | 0.061035 | 0.12817 | -0.22217 | -0.054474 | -0.10361 | -0.027771 | -0.009155 | 0.09613 | -0.036621 | 0.14648 | 0.13275 | 0.013733 | 0.1236 | 123.0057 | 122.6349 | 0.13733
10718.0625 | 0.10681 | 0.24139 | -0.22217 | -0.21683 | -0.10788 | -0.27344 | -0.040588 | 0.14648 | 0.07782 | 0.13275 | 0.10071 | 0.09613 | -0.054932 | 0.082397 | 0.030518 | 0.13031 | -0.22751 | -0.03952 | -0.11002 | -0.025635 | 0.09613 | 0.18768 | 0.068665 | 0.09613 | 0.091553 | 0.004578 | 0.073242 | 122.9416 | 122.6532 | 0.17853
10719.8438 | 0.061035 | 0.22858 | -0.21896 | -0.25528 | -0.098267 | -0.29159 | -0.064087 | 0.086975 | 0.009155 | 0.09613 | 0.059509 | 0.10529 | -0.045776 | 0.086975 | 0.061035 | 0.12283 | -0.21362 | -0.045929 | -0.13031 | -0.019226 | 0.009155 | 0.14191 | 0.032043 | 0.12817 | 0.10986 | 0 | 0.082397 | 122.8867 | 122.6944 | 0.19226
10721.5781 | 0.045776 | 0.24139 | -0.20294 | -0.22964 | -0.10468 | -0.27878 | -0.052338 | 0.15106 | 0.073242 | 0.13275 | 0.07782 | 0.10071 | -0.032043 | 0.082397 | 0.045776 | 0.1239 | -0.2179 | -0.041656 | -0.11749 | -0.026703 | 0.086975 | 0.16937 | 0.064087 | 0.10986 | 0.10071 | 0 | 0.064087 | 122.8683 | 122.6898 | 0.1831
10723.375 | 0.061035 | 0.21469 | -0.20615 | -0.23498 | -0.097198 | -0.24139 | -0.046997 | 0.086975 | -0.036621 | 0 | 0.022888 | 0.13275 | 0 | 0.13733 | 0.045776 | 0.14847 | -0.21576 | -0.035248 | -0.093994 | -0.03952 | -0.036621 | 0.054932 | -0.07782 | 0.13275 | 0.13275 | 0.059509 | 0.10986 | 122.9416 | 122.6303 | 0.16022
10725.0938 | 0.030518 | 0.23071 | -0.21362 | -0.23819 | -0.10788 | -0.28946 | -0.065155 | 0.059509 | 0.018311 | 0.086975 | 0.064087 | 0.11444 | -0.032043 | 0.10529 | 0.076294 | 0.11536 | -0.2211 | -0.042725 | -0.12176 | -0.02243 | 0.018311 | 0.13275 | 0.054932 | 0.13733 | 0.10986 | 0.013733 | 0.07782 | 122.905 | 122.6807 | 0.21515
10726.8906 | 0.030518 | 0.22003 | -0.21042 | -0.25207 | -0.099335 | -0.26382 | -0.05661 | 0.036621 | 0 | 0.032043 | 0.018311 | 0.13275 | -0.013733 | 0.13733 | 0.061035 | 0.12497 | -0.20615 | -0.03418 | -0.11856 | -0.030975 | -0.013733 | 0.086975 | -0.045776 | 0.16937 | 0.14648 | 0.045776 | 0.10986 | 122.8867 | 122.6669 | 0.19226
10728.6719 | 0.061035 | 0.21149 | -0.20294 | -0.24674 | -0.09613 | -0.24139 | -0.081177 | 0.1236 | 0.018311 | 0.050354 | 0.054932 | 0.14191 | -0.032043 | 0.13275 | 0.061035 | 0.12497 | -0.16129 | -0.45395 | -0.093994 | -0.023499 | 0.022888 | 0.11444 | -0.041199 | 0.10986 | 0.09613 | 0.032043 | 0.10071 | 122.9233 | 122.6028 | 0.11902
10730.4688 | 0.061035 | 0.25635 | -0.22537 | -0.24033 | -0.10254 | -0.28519 | -0.077972 | 0.082397 | 0.036621 | 0.09613 | 0.050354 | 0.086975 | -0.054932 | 0.09613 | 0.045776 | 0.097198 | -0.17624 | -0.45822 | -0.11643 | -0.020294 | 0.013733 | 0.11444 | 0.036621 | 0.07782 | 0.07782 | 0.013733 | 0.086975 | 122.8546 | 122.7036 | 0.15564
10732.1875 | 0.045776 | 0.23285 | -0.19974 | -0.24139 | -0.085449 | -0.25528 | -0.080109 | 0.082397 | 0.004578 | 0.050354 | 0.045776 | 0.10529 | -0.032043 | 0.09613 | 0.030518 | 0.10468 | -0.17303 | -0.45929 | -0.11749 | -0.020294 | 0.054932 | 0.10986 | 0.032043 | 0.073242 | 0.068665 | 0.018311 | 0.068665 | 123.0103 | 122.6486 | 0.10529
10733.9844 | 0.061035 | 0.22964 | -0.22644 | -0.24033 | -0.091858 | -0.24887 | -0.058746 | 0.10529 | 0.013733 | 0.041199 | 0.045776 | 0.1236 | -0.018311 | 0.12817 | 0.030518 | 0.1207 | -0.1741 | -0.45288 | -0.10895 | -0.019226 | 0.013733 | 0.091553 | -0.041199 | 0.086975 | 0.091553 | 0.036621 | 0.10529 | 122.9553 | 122.6669 | 0.11902
10735.7656 | 0.045776 | 0.24994 | -0.2211 | -0.24887 | -0.1004 | -0.29053 | -0.081177 | 0.032043 | 0.027466 | 0.082397 | 0.045776 | 0.11902 | -0.022888 | 0.086975 | 0.061035 | 0.087585 | -0.16129 | -0.45609 | -0.13138 | -0.008545 | 0.009155 | 0.10071 | 0.032043 | 0.073242 | 0.059509 | 0.027466 | 0.07782 | 122.8775 | 122.7036 | 0.14191
10737.5 | 0.061035 | 0.22217 | -0.21469 | -0.2478 | -0.097198 | -0.2478 | -0.070496 | 0.032043 | -0.059509 | -0.018311 | 0.009155 | 0.13275 | 0 | 0.11902 | 0.030518 | 0.11536 | -0.17624 | -0.45929 | -0.10147 | -0.02243 | -0.068665 | -0.009155 | -0.11444 | 0.10071 | 0.09613 | 0.054932 | 0.11444 | 122.9599 | 122.6944 | 0.13733
10739.2812 | 0.061035 | 0.2478 | -0.2243 | -0.22858 | -0.10147 | -0.28412 | -0.074768 | 0.091553 | 0.073242 | 0.10529 | 0.050354 | 0.10071 | -0.054932 | 0.07782 | 0.061035 | 0.088654 | -0.17838 | -0.47318 | -0.11322 | -0.006409 | 0.054932 | 0.10986 | 0.027466 | 0.064087 | 0.064087 | 0.013733 | 0.073242 | 122.8821 | 122.7402 | 0.13275
10741 | 0.045776 | 0.20935 | -0.20935 | -0.23712 | -0.10361 | -0.25207 | -0.076904 | 0.018311 | -0.07782 | -0.045776 | -0.004578 | 0.15564 | -0.013733 | 0.10986 | 0.076294 | 0.12176 | -0.16876 | -0.45181 | -0.10468 | -0.012817 | -0.045776 | 0.004578 | -0.073242 | 0.11902 | 0.086975 | 0.054932 | 0.1236 | 122.9782 | 122.6807 | 0.10986
10742.7969 | 0.061035 | 0.25101 | -0.22537 | -0.23392 | -0.10574 | -0.28946 | -0.074768 | 0.054932 | 0.045776 | 0.091553 | 0.045776 | 0.09613 | -0.045776 | 0.086975 | 0.061035 | 0.093994 | -0.17197 | -0.45929 | -0.11963 | -0.010681 | 0.009155 | 0.10529 | 0.027466 | 0.064087 | 0.068665 | 0.004578 | 0.10071 | 122.8867 | 122.7356 | 0.15564
10744.5156 | 0.045776 | 0.24246 | -0.22003 | -0.23819 | -0.10468 | -0.27557 | -0.080109 | 0.13733 | 0.07782 | 0.12817 | 0.082397 | 0.09613 | -0.059509 | 0.09613 | 0.061035 | 0.089722 | -0.18265 | -0.46783 | -0.12283 | -0.020294 | 0.054932 | 0.11444 | 0.041199 | 0.082397 | 0.036621 | 0.009155 | 0.09613 | 122.8775 | 122.7631 | 0.15564
10746.3125 | 0.030518 | 0.25955 | -0.23071 | -0.25207 | -0.09079 | -0.27771 | -0.085449 | 0.07782 | 0.032043 | 0.07782 | 0.045776 | 0.11444 | -0.041199 | 0.10071 | 0.045776 | 0.083313 | -0.18265 | -0.46143 | -0.12711 | -0.021362 | 0.022888 | 0.091553 | 0.018311 | 0.073242 | 0.064087 | 0.022888 | 0.10071 | 122.9279 | 122.7493 | 0.13733
10748.1094 | 0.045776 | 0.23498 | -0.22644 | -0.26169 | -0.089722 | -0.27557 | -0.091858 | 0.064087 | 0.027466 | 0.07782 | 0.050354 | 0.10529 | -0.032043 | 0.10071 | 0.045776 | 0.092926 | -0.1709 | -0.46463 | -0.13245 | -0.026703 | 0.036621 | 0.11444 | 0.050354 | 0.073242 | 0.073242 | 0.018311 | 0.091553 | 122.9462 | 122.7539 | 0.14191
10749.8281 | 0.091553 | 0.24139 | -0.20935 | -0.23819 | -0.091858 | -0.2478 | -0.077972 | 0.15106 | 0.10071 | 0.13733 | 0.09613 | 0.10071 | -0.036621 | 0.068665 | 0.061035 | 0.10574 | -0.16983 | -0.46249 | -0.11536 | -0.020294 | 0.09613 | 0.16022 | 0.059509 | 0.059509 | 0.041199 | 0.013733 | 0.073242 | 122.9736 | 122.7219 | 0.15106
10751.625 | 0.045776 | 0.2446 | -0.23071 | -0.25207 | -0.097198 | -0.26596 | -0.081177 | 0.091553 | 0.064087 | 0.091553 | 0.064087 | 0.091553 | -0.050354 | 0.07782 | 0.030518 | 0.10468 | -0.16769 | -0.4689 | -0.1207 | -0.010681 | 0.045776 | 0.10986 | 0.009155 | 0.07782 | 0.050354 | -0.004578 | 0.073242 | 122.8867 | 122.7448 | 0.14648
10753.4219 | 0.061035 | 0.24674 | -0.23712 | -0.23178 | -0.083313 | -0.26489 | -0.083313 | 0.13275 | 0.1236 | 0.12817 | 0.10529 | 0.086975 | -0.041199 | 0.09613 | 0.045776 | 0.092926 | -0.18906 | -0.46249 | -0.11429 | -0.02243 | 0.068665 | 0.16937 | 0.054932 | 0.064087 | 0.07782 | 0.032043 | 0.07782 | 122.8958 | 122.7493 | 0.13275
10755.125 | 0.045776 | 0.2211 | -0.2211 | -0.23498 | -0.091858 | -0.23071 | -0.082245 | 0.073242 | -0.068665 | -0.018311 | 0.009155 | 0.14191 | -0.009155 | 0.13275 | 0.045776 | 0.12497 | -0.17303 | -0.45502 | -0.095062 | -0.036316 | -0.022888 | 0 | -0.07782 | 0.09613 | 0.086975 | 0.045776 | 0.11902 | 123.0103 | 122.731 | 0.11444
10756.9219 | 0.030518 | 0.21469 | -0.21362 | -0.24033 | -0.088654 | -0.24246 | -0.076904 | 0.10529 | 0.013733 | 0.032043 | 0.068665 | 0.15106 | 0 | 0.12817 | 0.061035 | 0.12711 | -0.17731 | -0.45929 | -0.10468 | -0.021362 | 0.004578 | 0.10986 | -0.041199 | 0.091553 | 0.07782 | 0.050354 | 0.10986 | 123.0194 | 122.699 | 0.10529
10758.7031 | 0.045776 | 0.21362 | -0.21042 | -0.25421 | -0.09613 | -0.25955 | -0.080109 | 0.027466 | -0.041199 | -0.004578 | 0.018311 | 0.13733 | -0.009155 | 0.13275 | 0.045776 | 0.10254 | -0.16663 | -0.46143 | -0.12176 | -0.019226 | -0.041199 | 0.050354 | -0.068665 | 0.11444 | 0.09613 | 0.064087 | 0.11444 | 122.9416 | 122.7173 | 0.12817
10760.4844 | 0.030518 | 0.23392 | -0.23498 | -0.25848 | -0.10147 | -0.29266 | -0.080109 | 0.1236 | 0.1236 | 0.14648 | 0.09613 | 0.10986 | -0.027466 | 0.09613 | 0.076294 | 0.080109 | -0.16876 | -0.45715 | -0.13992 | -0.014954 | 0.091553 | 0.21057 | 0.10986 | 0.054932 | 0.059509 | 0.022888 | 0.086975 | 122.612 | 122.3831 | 0.1236
10762.25 | 0.030518 | 0.21255 | -0.22537 | -0.24567 | -0.1004 | -0.24674 | -0.085449 | 0.059509 | -0.036621 | -0.013733 | 0.032043 | 0.14191 | 0.009155 | 0.12817 | 0.045776 | 0.11856 | -0.16769 | -0.44968 | -0.10895 | -0.023499 | -0.036621 | 0.073242 | -0.036621 | 0.10986 | 0.09613 | 0.068665 | 0.10986 | 122.8134 | 122.4655 | 0.10071
10764.0469 | 0.076294 | 0.22964 | -0.21469 | -0.22537 | -0.089722 | -0.27023 | -0.066223 | 0.15564 | 0.073242 | 0.1236 | 0.09613 | 0.09613 | -0.032043 | 0.082397 | 0.045776 | 0.10574 | -0.18692 | -0.46143 | -0.10895 | -0.023499 | 0.09613 | 0.16479 | 0.064087 | 0.054932 | 0.054932 | 0.022888 | 0.073242 | 122.7951 | 122.5204 | 0.11444
10765.8281 | 0.061035 | 0.21149 | -0.21042 | -0.24246 | -0.099335 | -0.24139 | -0.0737 | 0.10529 | 0.027466 | 0.045776 | 0.045776 | 0.13275 | -0.004578 | 0.12817 | 0.061035 | 0.12283 | -0.15595 | -0.45395 | -0.10574 | -0.02243 | 0.022888 | 0.10071 | -0.032043 | 0.082397 | 0.082397 | 0.032043 | 0.1236 | 122.8134 | 122.5342 | 0.09613
10767.5469 | 0.045776 | 0.23178 | -0.22217 | -0.23819 | -0.10574 | -0.25742 | -0.076904 | 0.050354 | -0.036621 | -0.013733 | -0.004578 | 0.13275 | -0.004578 | 0.12817 | 0.061035 | 0.11749 | -0.1709 | -0.45502 | -0.11002 | -0.011749 | 0.009155 | 0.054932 | -0.022888 | 0.09613 | 0.073242 | 0.018311 | 0.11444 | 122.8912 | 122.5525 | 0.086975
10769.3438 | 0.045776 | 0.22217 | -0.21362 | -0.23392 | -0.095062 | -0.2478 | -0.075836 | 0.032043 | -0.073242 | -0.018311 | 0 | 0.13733 | -0.009155 | 0.13275 | 0.076294 | 0.11749 | -0.16129 | -0.44647 | -0.10788 | -0.008545 | -0.041199 | 0.018311 | -0.059509 | 0.082397 | 0.091553 | 0.054932 | 0.11444 | 122.8638 | 122.5662 | 0.1236
10771.125 | 0.061035 | 0.21362 | -0.21255 | -0.24246 | -0.097198 | -0.25314 | -0.076904 | 0.036621 | -0.073242 | -0.027466 | 0.009155 | 0.12817 | 0.004578 | 0.13275 | 0.045776 | 0.11215 | -0.16449 | -0.45715 | -0.11322 | -0.009613 | -0.041199 | 0.013733 | -0.073242 | 0.091553 | 0.10071 | 0.064087 | 0.11444 | 122.8729 | 122.58 | 0.10529
10772.8594 | 0.030518 | 0.22003 | -0.20294 | -0.24887 | -0.093994 | -0.25528 | -0.069427 | 0.09613 | 0.022888 | 0.045776 | 0.045776 | 0.1236 | -0.004578 | 0.13733 | 0.061035 | 0.11002 | -0.15381 | -0.45715 | -0.11963 | -0.014954 | 0.027466 | 0.10986 | -0.022888 | 0.09613 | 0.091553 | 0.041199 | 0.10986 | 122.8867 | 122.58 | 0.11444
10774.6406 | 0.076294 | 0.21469 | -0.2179 | -0.26489 | -0.10147 | -0.28946 | -0.087585 | 0.086975 | 0.064087 | 0.10986 | 0.086975 | 0.10071 | -0.018311 | 0.10986 | 0.045776 | 0.1004 | -0.16022 | -0.46677 | -0.13245 | -0.020294 | -0.004578 | 0.12817 | 0.018311 | 0.07782 | 0.086975 | 0.036621 | 0.10986 | 122.7402 | 122.6212 | 0.14191
10776.3594 | 0.045776 | 0.22217 | -0.2243 | -0.24353 | -0.09079 | -0.27557 | -0.077972 | 0.036621 | 0 | 0.032043 | 0.027466 | 0.11902 | -0.009155 | 0.13733 | 0.045776 | 0.095062 | -0.18692 | -0.46036 | -0.12604 | -0.02243 | -0.036621 | 0.064087 | -0.059509 | 0.10986 | 0.086975 | 0.064087 | 0.11902 | 122.0627 | 121.9254 | 0.14191
10778.1406 | 0.061035 | 0.21255 | -0.22537 | -0.22003 | -0.10468 | -0.2478 | -0.070496 | 0.082397 | -0.022888 | 0.004578 | 0.036621 | 0.12817 | -0.013733 | 0.1236 | 0.061035 | 0.11002 | -0.18051 | -0.46249 | -0.10147 | -0.024567 | -0.032043 | 0.022888 | -0.086975 | 0.082397 | 0.10529 | 0.045776 | 0.12817 | 122.3419 | 122.0764 | 0.11902
10779.9219 | 0.045776 | 0.25101 | -0.22537 | -0.24353 | -0.099335 | -0.30548 | -0.089722 | 0.050354 | 0.022888 | 0.073242 | 0.050354 | 0.11902 | -0.027466 | 0.11444 | 0.030518 | 0.092926 | -0.1741 | -0.45715 | -0.13565 | -0.014954 | 0.027466 | 0.1236 | 0.045776 | 0.064087 | 0.059509 | 0.027466 | 0.10529 | 121.8933 | 121.6324 | 0.14191
10781.7188 | 0.061035 | 0.22644 | -0.22644 | -0.2446 | -0.093994 | -0.27237 | -0.09079 | 0.11444 | 0.09613 | 0.13275 | 0.086975 | 0.10071 | -0.022888 | 0.09613 | 0.061035 | 0.087585 | -0.17731 | -0.46677 | -0.12817 | -0.023499 | 0.036621 | 0.17395 | 0.041199 | 0.068665 | 0.059509 | 0.018311 | 0.09613 | 122.1909 | 122.0215 | 0.15106
10783.4531 | 0.061035 | 0.25955 | -0.22217 | -0.22751 | -0.10468 | -0.27451 | -0.084381 | 0.14191 | 0.054932 | 0.10986 | 0.054932 | 0.09613 | -0.050354 | 0.086975 | 0.045776 | 0.12283 | -0.14633 | -0.46463 | -0.11856 | -0.01709 | 0.045776 | 0.13733 | 0.036621 | 0.086975 | 0.064087 | 0.022888 | 0.091553 | 121.8475 | 121.6049 | 0.16022
10785.2344 | 0.076294 | 0.23926 | -0.21683 | -0.24994 | -0.085449 | -0.28946 | -0.084381 | 0.073242 | 0.018311 | 0.086975 | 0.059509 | 0.11902 | -0.027466 | 0.10986 | 0.076294 | 0.12497 | -0.1239 | -0.47104 | -0.12604 | -0.009613 | 0.045776 | 0.13275 | 0.059509 | 0.07782 | 0.07782 | 0.022888 | 0.082397 | 122.0261 | 121.7697 | 0.15106
10786.9688 | 0.061035 | 0.23071 | -0.2211 | -0.23285 | -0.098267 | -0.25742 | -0.081177 | 0.073242 | -0.050354 | 0.009155 | 0.009155 | 0.14191 | -0.018311 | 0.11444 | 0.061035 | 0.13779 | -0.16022 | -0.46249 | -0.10147 | -0.016022 | 0.032043 | 0.041199 | -0.032043 | 0.086975 | 0.086975 | 0.022888 | 0.073242 | 117.366 | 117.0273 | 0.086975
10788.75 | 0.061035 | 0.21362 | -0.22858 | -0.22537 | -0.082245 | -0.25421 | -0.083313 | 0.064087 | -0.045776 | 0.013733 | 0.018311 | 0.14648 | -0.013733 | 0.13275 | 0.076294 | 0.14847 | -0.12497 | -0.46677 | -0.11108 | -0.009613 | 0.013733 | 0.054932 | -0.013733 | 0.091553 | 0.091553 | 0.027466 | 0.10071 | 121.8933 | 121.5088 | 0.13733
10790.5469 | 0.061035 | 0.22003 | -0.21576 | -0.26062 | -0.082245 | -0.27878 | -0.082245 | 0.082397 | 0.027466 | 0.059509 | 0.045776 | 0.13275 | -0.004578 | 0.13275 | 0.061035 | 0.16235 | -0.10788 | -0.46997 | -0.12283 | -0.010681 | -0.018311 | 0.082397 | -0.036621 | 0.11902 | 0.11444 | 0.045776 | 0.10529 | 121.8567 | 121.6873 | 0.14191
10792.2656 | 0.045776 | 0.2681 | -0.22751 | -0.22324 | -0.093994 | -0.29159 | -0.086517 | 0.14191 | 0.11444 | 0.14191 | 0.09613 | 0.10529 | -0.054932 | 0.10529 | 0.045776 | 0.1474 | -0.12817 | -0.47958 | -0.1239 | -0.005341 | 0.082397 | 0.19684 | 0.10529 | 0.073242 | 0.082397 | 0.009155 | 0.068665 | 121.9437 | 121.7148 | 0.15106
10794.0312 | 0.061035 | 0.21576 | -0.21362 | -0.23605 | -0.082245 | -0.24033 | -0.080109 | 0.10529 | 0.013733 | 0.054932 | 0.054932 | 0.14648 | -0.013733 | 0.11902 | 0.045776 | 0.17838 | -0.1004 | -0.4657 | -0.10468 | -0.007477 | 0.013733 | 0.10529 | -0.009155 | 0.1236 | 0.09613 | 0.022888 | 0.09613 | 122.049 | 121.7285 | 0.12817
10795.8281 | 0.045776 | 0.24353 | -0.23605 | -0.23392 | -0.082245 | -0.26169 | -0.088654 | 0.068665 | 0.013733 | 0.032043 | 0.059509 | 0.18768 | -0.036621 | 0.10529 | 0.045776 | 1.2625 | 1.3223 | -0.74554 | -0.11536 | 0.25742 | 0.13275 | 0.2243 | 0.16022 | 0.37994 | 0.36621 | -0.14648 | -0.091553 | 121.994 | 121.2753 | 0.41199
10797.5625 | 0.061035 | 0.24353 | -0.22858 | -0.22537 | -0.089722 | -0.25314 | -0.14206 | 0.054932 | -0.045776 | -0.004578 | 0.009155 | 0.14191 | -0.032043 | 0.1236 | 0.061035 | 0.053406 | -0.03952 | -0.52338 | 0.021362 | -0.13672 | 0.018311 | 0.050354 | -0.050354 | 0.09613 | 0.10071 | 0.032043 | 0.10529 | 120.7718 | 120.4605 | 0.10529
10799.3594 | 0.061035 | 0.23498 | -0.22217 | -0.2446 | -0.091858 | -0.24674 | -0.14526 | 0.086975 | -0.022888 | 0.036621 | 0.064087 | 0.13733 | -0.022888 | 0.1236 | 0.061035 | 0.12283 | -0.10788 | -0.49774 | -0.11749 | -0.030975 | -0.018311 | 0.086975 | -0.027466 | 0.091553 | 0.10986 | 0.050354 | 0.10529 | 121.3852 | 121.0464 | 0.11444
10801.1406 | 0.061035 | 0.24033 | -0.23712 | -0.23819 | -0.075836 | -0.25421 | -0.14099 | 0.027466 | -0.10071 | -0.004578 | 0.004578 | 0.16022 | -0.004578 | 0.11902 | 0.061035 | 0.11963 | -0.10895 | -0.51376 | -0.10361 | -0.023499 | -0.041199 | -0.013733 | -0.091553 | 0.10071 | 0.10071 | 0.041199 | 0.11902 | 121.4447 | 121.1746 | 0.11902
10802.875 | 0.061035 | 0.25635 | -0.24033 | -0.24567 | -0.093994 | -0.29587 | -0.14954 | 0.068665 | 0.036621 | 0.10071 | 0.082397 | 0.12817 | -0.022888 | 0.10529 | 0.061035 | 0.092926 | -0.10574 | -0.52765 | -0.1442 | -0.016022 | 0.032043 | 0.15564 | 0.073242 | 0.073242 | 0.059509 | 0.032043 | 0.082397 | 121.4676 | 121.2616 | 0.13733
10804.6719 | 0.045776 | 0.23712 | -0.2211 | -0.24246 | -0.09079 | -0.23605 | -0.14847 | 0.10071 | 0.004578 | 0.041199 | 0.064087 | 0.14648 | -0.009155 | 0.11444 | 0.061035 | 0.12711 | -0.093994 | -0.51056 | -0.11643 | -0.035248 | 0.004578 | 0.09613 | -0.018311 | 0.091553 | 0.073242 | 0.054932 | 0.11444 | 121.5912 | 121.2845 | 0.10529
10806.3906 | 0.076294 | 0.2243 | -0.22537 | -0.23285 | -0.067291 | -0.2478 | -0.1442 | 0.11444 | 0.027466 | 0.041199 | 0.050354 | 0.16022 | 0.004578 | 0.11444 | 0.045776 | 0.1207 | -0.099335 | -0.50095 | -0.11322 | -0.033112 | 0.018311 | 0.09613 | -0.027466 | 0.086975 | 0.073242 | 0.050354 | 0.10071 | 121.5958 | 121.344 | 0.12817
10808.1719 | 0.030518 | 0.2478 | -0.22537 | -0.23819 | -0.084381 | -0.27237 | -0.14526 | 0.13733 | 0.082397 | 0.12817 | 0.086975 | 0.10071 | -0.036621 | 0.064087 | 0.045776 | 0.10574 | -0.1004 | -0.52231 | -0.11536 | -0.021362 | 0.068665 | 0.14648 | 0.068665 | 0.050354 | 0.041199 | 0.027466 | 0.07782 | 121.6599 | 121.3577 | 0.11444
10809.9062 | 0.061035 | 0.23285 | -0.23071 | -0.23605 | -0.083313 | -0.2446 | -0.13886 | 0.059509 | -0.027466 | -0.004578 | 0.022888 | 0.1236 | -0.004578 | 0.12817 | 0.061035 | 0.11963 | -0.10254 | -0.5159 | -0.10361 | -0.027771 | -0.045776 | 0.027466 | -0.086975 | 0.10529 | 0.09613 | 0.045776 | 0.11902 | 121.6507 | 121.3669 | 0.12817
10811.6875 | 0.045776 | 0.24567 | -0.22964 | -0.23498 | -0.081177 | -0.27451 | -0.16235 | 0.022888 | -0.022888 | 0.013733 | 0.009155 | 0.11902 | -0.013733 | 0.13733 | 0.061035 | 0.10788 | -0.10361 | -0.5127 | -0.12497 | -0.024567 | -0.041199 | 0.054932 | -0.045776 | 0.11902 | 0.10986 | 0.059509 | 0.1236 | 121.6049 | 121.4401 | 0.12817
10813.4844 | 0.061035 | 0.2713 | -0.25101 | -0.23392 | -0.093994 | -0.29159 | -0.15701 | 0.10986 | 0.073242 | 0.11902 | 0.091553 | 0.11902 | -0.045776 | 0.07782 | 0.030518 | 0.09613 | -0.10681 | -0.51804 | -0.13565 | -0.01709 | 0.064087 | 0.18768 | 0.086975 | 0.068665 | 0.054932 | 0.004578 | 0.082397 | 121.6553 | 121.463 | 0.13275
10815.1875 | 0.061035 | 0.23071 | -0.22964 | -0.21469 | -0.091858 | -0.24353 | -0.1506 | 0.064087 | -0.068665 | -0.013733 | 0.018311 | 0.13275 | 0 | 0.14191 | 0.061035 | 0.1239 | -0.082245 | -0.51697 | -0.11002 | -0.025635 | -0.073242 | 0.009155 | -0.091553 | 0.10529 | 0.091553 | 0.059509 | 0.11444 | 121.7194 | 121.463 | 0.1236
10816.9844 | 0.061035 | 0.22644 | -0.22751 | -0.23498 | -0.09079 | -0.25101 | -0.14847 | 0.027466 | -0.10529 | -0.036621 | -0.013733 | 0.15106 | -0.018311 | 0.1236 | 0.045776 | 0.1207 | -0.09079 | -0.51483 | -0.11002 | -0.019226 | -0.054932 | -0.013733 | -0.082397 | 0.10986 | 0.10986 | 0.050354 | 0.11444 | 121.7606 | 121.4584 | 0.13275
10818.7812 | 0.061035 | 0.23071 | -0.21896 | -0.22751 | -0.081177 | -0.25314 | -0.14206 | 0.07782 | -0.004578 | 0.013733 | 0.027466 | 0.13733 | 0 | 0.11902 | 0.061035 | 0.12924 | -0.081177 | -0.50736 | -0.10254 | -0.021362 | -0.032043 | 0.045776 | -0.07782 | 0.10071 | 0.086975 | 0.050354 | 0.1236 | 121.7422 | 121.4905 | 0.11902
10820.5781 | 0.061035 | 0.23712 | -0.24139 | -0.22751 | -0.085449 | -0.27771 | -0.13992 | 0.12817 | 0.073242 | 0.11444 | 0.10071 | 0.10071 | -0.050354 | 0.068665 | 0.045776 | 0.10468 | -0.091858 | -0.52872 | -0.11643 | -0.010681 | 0.086975 | 0.14648 | 0.059509 | 0.059509 | 0.064087 | 0.004578 | 0.082397 | 121.7926 | 121.5088 | 0.11902
10822.3125 | 0.061035 | 0.2179 | -0.23392 | -0.25848 | -0.082245 | -0.24887 | -0.14099 | 0.045776 | -0.054932 | 0 | 0.018311 | 0.14648 | -0.022888 | 0.11902 | 0.061035 | 0.12497 | -0.070496 | -0.51697 | -0.11002 | -0.021362 | -0.054932 | 0.013733 | -0.09613 | 0.10529 | 0.10071 | 0.064087 | 0.10986 | 121.8018 | 121.5363 | 0.11444
10824.0938 | 0.061035 | 0.22751 | -0.22217 | -0.23819 | -0.087585 | -0.25314 | -0.1442 | 0.018311 | -0.082397 | -0.036621 | 0.004578 | 0.1236 | -0.009155 | 0.12817 | 0.076294 | 0.12497 | -0.081177 | -0.51483 | -0.11429 | -0.01709 | -0.073242 | -0.009155 | -0.10071 | 0.10071 | 0.10986 | 0.041199 | 0.11444 | 121.8155 | 121.5546 | 0.11444
10825.875 | 0.061035 | 0.25528 | -0.23712 | -0.25421 | -0.082245 | -0.28625 | -0.14954 | 0.082397 | 0.018311 | 0.10071 | 0.064087 | 0.09613 | -0.050354 | 0.091553 | 0.076294 | 0.10147 | -0.068359 | -0.52338 | -0.13565 | -0.010681 | 0.036621 | 0.10529 | 0.041199 | 0.073242 | 0.064087 | 0.018311 | 0.091553 | 121.7285 | 121.6049 | 0.16022
10827.6719 | 0.061035 | 0.25635 | -0.22003 | -0.23178 | -0.088654 | -0.26382 | -0.14954 | 0.11902 | 0.050354 | 0.11444 | 0.09613 | 0.10529 | -0.041199 | 0.09613 | 0.061035 | 0.11215 | -0.068359 | -0.5191 | -0.1239 | -0.013885 | 0.064087 | 0.13733 | 0.054932 | 0.068665 | 0.059509 | 0.004578 | 0.07782 | 121.8842 | 121.5637 | 0.11902
10829.4062 | 0.061035 | 0.23926 | -0.22964 | -0.26169 | -0.09613 | -0.28305 | -0.15701 | 0.050354 | 0.032043 | 0.064087 | 0.054932 | 0.13275 | 0 | 0.12817 | 0.030518 | 0.10468 | -0.066223 | -0.52551 | -0.1239 | -0.012817 | -0.022888 | 0.059509 | -0.032043 | 0.10986 | 0.09613 | 0.054932 | 0.11444 | 121.7743 | 121.6187 | 0.16479
10831.1719 | 0.061035 | 0.23605 | -0.23285 | -0.23071 | -0.085449 | -0.25742 | -0.1506 | 0.036621 | -0.07782 | -0.032043 | 0 | 0.15106 | 0 | 0.14648 | 0.030518 | 0.13458 | -0.069427 | -0.52338 | -0.11002 | -0.024567 | -0.064087 | -0.018311 | -0.086975 | 0.10986 | 0.10529 | 0.041199 | 0.10529 | 121.8613 | 121.6003 | 0.1236
10832.9062 | 0.061035 | 0.24246 | -0.23392 | -0.22537 | -0.083313 | -0.26916 | -0.15167 | 0.10986 | 0.068665 | 0.1236 | 0.09613 | 0.10071 | -0.054932 | 0.09613 | 0.061035 | 0.11856 | -0.072632 | -0.5159 | -0.11963 | -0.013885 | 0.07782 | 0.15106 | 0.068665 | 0.064087 | 0.054932 | 0.013733 | 0.068665 | 121.9208 | 121.5866 | 0.12817
10834.7031 | 0.076294 | 0.22217 | -0.22217 | -0.2179 | -0.088654 | -0.24353 | -0.13992 | 0.054932 | -0.064087 | -0.018311 | 0.009155 | 0.14648 | -0.009155 | 0.14191 | 0.061035 | 0.13779 | -0.057678 | -0.52658 | -0.099335 | -0.023499 | -0.045776 | 0.018311 | -0.091553 | 0.1236 | 0.10529 | 0.045776 | 0.10529 | 121.8796 | 121.6232 | 0.11902
10836.5 | 0.045776 | 0.24994 | -0.23819 | -0.2446 | -0.074768 | -0.27451 | -0.15701 | 0.032043 | -0.054932 | -0.004578 | 0.009155 | 0.14191 | 0 | 0.13733 | 0.061035 | 0.14206 | -0.05661 | -0.53085 | -0.12924 | -0.001068 | -0.045776 | 0.045776 | -0.064087 | 0.11902 | 0.10071 | 0.045776 | 0.11444 | 121.8658 | 121.6553 | 0.13733
10838.2188 | 0.061035 | 0.2446 | -0.22537 | -0.22003 | -0.080109 | -0.25528 | -0.15381 | 0.073242 | -0.018311 | 0.022888 | 0.027466 | 0.14648 | -0.032043 | 0.082397 | 0.045776 | 0.31403 | 0.16022 | -0.58426 | -0.11429 | 0.044861 | 0.041199 | 0.10071 | 0.036621 | 0.13275 | 0.12817 | -0.018311 | 0.041199 | 121.9849 | 121.5912 | 0.16937
10840.0156 | 0.061035 | 0.23498 | -0.23178 | -0.22644 | -0.074768 | -0.26703 | -0.15701 | 0.13275 | 0.064087 | 0.13275 | 0.10071 | 0.10071 | -0.054932 | 0.073242 | 0.045776 | 0.31296 | 0.17944 | -0.57999 | -0.11215 | 0.053406 | 0.10529 | 0.1831 | 0.10986 | 0.10529 | 0.10529 | -0.027466 | 0.050354 | 121.9574 | 121.6003 | 0.1831
10841.7969 | 0.045776 | 0.2478 | -0.23605 | -0.23712 | -0.081177 | -0.27878 | -0.16129 | 0.09613 | 0.045776 | 0.086975 | 0.064087 | 0.11902 | -0.032043 | 0.11444 | 0.045776 | 0.31723 | 0.18585 | -0.59387 | -0.12924 | 0.044861 | 0.004578 | 0.11444 | 0.018311 | 0.13733 | 0.13733 | 0.018311 | 0.07782 | 121.8475 | 121.6507 | 0.20599
10843.5938 | 0.076294 | 0.22217 | -0.22964 | -0.24567 | -0.086517 | -0.26276 | -0.15808 | 0.064087 | -0.041199 | 0.022888 | 0.050354 | 0.16022 | -0.013733 | 0.1236 | 0.061035 | 0.33325 | 0.19653 | -0.59815 | -0.11856 | 0.049133 | 0 | 0.091553 | 0.004578 | 0.17853 | 0.15106 | -0.004578 | 0.07782 | 121.9711 | 121.6049 | 0.17853
10845.3125 | 0.030518 | 0.24353 | -0.22751 | -0.24353 | -0.089722 | -0.23819 | -0.14633 | 0.032043 | -0.07782 | -0.022888 | 0.022888 | 0.16479 | -0.022888 | 0.12817 | 0.061035 | 0.33646 | 0.19226 | -0.58853 | -0.11429 | 0.049133 | -0.009155 | 0.036621 | -0.050354 | 0.15564 | 0.13733 | 0.013733 | 0.082397 | 121.9711 | 121.6324 | 0.19684
10847.0938 | 0.061035 | 0.22324 | -0.22644 | -0.25848 | -0.072632 | -0.26382 | -0.15808 | 0.022888 | -0.032043 | -0.004578 | 0.022888 | 0.17395 | -0.004578 | 0.10986 | 0.045776 | 0.33539 | 0.20721 | -0.58105 | -0.12924 | 0.059814 | -0.018311 | 0.086975 | -0.018311 | 0.17853 | 0.14191 | 0.009155 | 0.073242 | 121.9757 | 121.6324 | 0.1831
10848.8906 | 0.045776 | 0.23605 | -0.21896 | -0.23178 | -0.083313 | -0.25742 | -0.15274 | 0.036621 | -0.032043 | 0.004578 | 0.022888 | 0.14648 | -0.013733 | 0.12817 | 0.045776 | 0.33539 | 0.1944 | -0.58853 | -0.10681 | 0.044861 | 0.013733 | 0.068665 | -0.013733 | 0.16479 | 0.13733 | 0.009155 | 0.073242 | 122.0398 | 121.6553 | 0.1831
10850.7031 | 0.076294 | 0.24139 | -0.22751 | -0.22324 | -0.082245 | -0.25848 | -0.14954 | 0.068665 | 0.009155 | 0.009155 | 0.041199 | 0.16022 | -0.027466 | 0.10529 | 0.061035 | 0.3418 | 0.22003 | -0.5896 | -0.10574 | 0.057678 | -0.004578 | 0.073242 | -0.032043 | 0.15564 | 0.17853 | -0.004578 | 0.059509 | 121.994 | 121.6736 | 0.17853
10852.5 | 0.030518 | 0.25314 | -0.24887 | -0.24567 | -0.09079 | -0.27771 | -0.16663 | 0.022888 | -0.027466 | 0.032043 | 0.027466 | 0.14648 | -0.022888 | 0.13275 | 0.061035 | 0.33005 | 0.21042 | -0.60883 | -0.13886 | 0.057678 | -0.018311 | 0.10986 | -0.004578 | 0.17853 | 0.17395 | 0.022888 | 0.07782 | 121.9208 | 121.6644 | 0.21057
10854.2188 | 0.061035 | 0.2713 | -0.23819 | -0.22644 | -0.081177 | -0.30014 | -0.16342 | 0.07782 | 0.022888 | 0.086975 | 0.068665 | 0.11902 | -0.032043 | 0.091553 | 0.061035 | 0.31937 | 0.19867 | -0.60455 | -0.12924 | 0.057678 | 0.041199 | 0.15106 | 0.068665 | 0.13275 | 0.12817 | -0.027466 | 0.045776 | 121.9482 | 121.7331 | 0.20599
10856.0312 | 0.061035 | 0.25101 | -0.23819 | -0.2478 | -0.083313 | -0.28625 | -0.14847 | 0.15564 | 0.10986 | 0.15106 | 0.10529 | 0.11902 | -0.054932 | 0.091553 | 0.076294 | 0.32364 | 0.20828 | -0.60883 | -0.12924 | 0.053406 | 0.09613 | 0.23346 | 0.14191 | 0.12817 | 0.11902 | -0.032043 | 0.032043 | 121.962 | 121.6965 | 0.20599
10857.8281 | 0.030518 | 0.24567 | -0.24246 | -0.25101 | -0.09613 | -0.28412 | -0.15488 | 0.10071 | 0.050354 | 0.11902 | 0.082397 | 0.14191 | -0.041199 | 0.091553 | 0.045776 | 0.32471 | 0.21255 | -0.60028 | -0.13992 | 0.059814 | 0.09613 | 0.17395 | 0.10986 | 0.13275 | 0.12817 | -0.032043 | 0.054932 | 121.9849 | 121.7331 | 0.19684
10859.6406 | 0.045776 | 0.24353 | -0.23178 | -0.22858 | -0.086517 | -0.25207 | -0.15595 | 0.082397 | -0.041199 | 0.027466 | 0.036621 | 0.15564 | -0.032043 | 0.12817 | 0.045776 | 0.34073 | 0.20828 | -0.60242 | -0.11002 | 0.05127 | 0.064087 | 0.086975 | 0.027466 | 0.14191 | 0.15106 | -0.004578 | 0.059509 | 122.1085 | 121.6873 | 0.17395
10861.3594 | 0.061035 | 0.21042 | -0.2179 | -0.25207 | -0.076904 | -0.23392 | -0.13458 | 0.082397 | -0.045776 | 0.004578 | 0.027466 | 0.14191 | -0.032043 | 0.11902 | 0.061035 | 0.35568 | 0.22324 | -0.59067 | -0.11643 | 0.045929 | -0.013733 | 0.050354 | -0.036621 | 0.16479 | 0.14191 | 0.009155 | 0.07782 | 122.0352 | 121.7056 | 0.20599
10863.1406 | 0.030518 | 0.23071 | -0.23178 | -0.25955 | -0.086517 | -0.26596 | -0.14954 | 0.041199 | -0.027466 | -0.004578 | 0.022888 | 0.16937 | 0 | 0.11444 | 0.045776 | 0.34607 | 0.23498 | -0.59067 | -0.13031 | 0.042725 | 0 | 0.073242 | -0.027466 | 0.16937 | 0.15564 | 0.027466 | 0.064087 | 122.0306 | 121.7285 | 0.17853
10864.875 | 0.045776 | 0.26276 | -0.23071 | -0.22751 | -0.091858 | -0.29159 | -0.15381 | 0.07782 | 0.050354 | 0.09613 | 0.068665 | 0.10529 | -0.064087 | 0.086975 | 0.076294 | 0.32577 | 0.21042 | -0.59921 | -0.13992 | 0.068359 | 0.082397 | 0.16937 | 0.10986 | 0.15106 | 0.14191 | -0.036621 | 0.041199 | 122.0306 | 121.7331 | 0.20142
10866.6719 | 0.061035 | 0.26703 | -0.22003 | -0.23926 | -0.079041 | -0.27985 | -0.16556 | 0.10529 | 0.054932 | 0.09613 | 0.073242 | 0.1236 | -0.045776 | 0.064087 | 0.045776 | 0.33646 | 0.21042 | -0.59174 | -0.12817 | 0.061951 | 0.07782 | 0.15106 | 0.068665 | 0.1236 | 0.11902 | -0.036621 | 0.032043 | 121.9711 | 121.7789 | 0.21057
10868.4688 | 0.061035 | 0.25528 | -0.22644 | -0.25101 | -0.074768 | -0.27237 | -0.15808 | 0.082397 | 0.018311 | 0.10071 | 0.064087 | 0.12817 | -0.022888 | 0.086975 | 0.045776 | 0.33646 | 0.23285 | -0.59921 | -0.13245 | 0.057678 | 0.068665 | 0.13275 | 0.068665 | 0.12817 | 0.11444 | -0.022888 | 0.041199 | 121.994 | 121.7468 | 0.20599
10870.2656 | 0.061035 | 0.25848 | -0.23178 | -0.22003 | -0.088654 | -0.24994 | -0.15488 | 0.15106 | 0.10071 | 0.1236 | 0.091553 | 0.11444 | -0.059509 | 0.073242 | 0.061035 | 0.34821 | 0.21149 | -0.60242 | -0.10895 | 0.058746 | 0.12817 | 0.17853 | 0.10071 | 0.1236 | 0.11902 | -0.018311 | 0.018311 | 122.0032 | 121.7834 | 0.21515
10871.9844 | 0.076294 | 0.24887 | -0.22644 | -0.22644 | -0.064087 | -0.24994 | -0.14526 | 0.14648 | 0.059509 | 0.091553 | 0.073242 | 0.11902 | -0.050354 | 0.09613 | 0.091553 | 0.35996 | 0.22751 | -0.59815 | -0.10681 | 0.05661 | 0.11902 | 0.17853 | 0.10529 | 0.13275 | 0.1236 | -0.041199 | 0.032043 | 122.1268 | 121.7285 | 0.19226
10873.7812 | 0.045776 | 0.24353 | -0.23178 | -0.22964 | -0.079041 | -0.26276 | -0.15274 | 0.16479 | 0.082397 | 0.14191 | 0.11444 | 0.10071 | -0.064087 | 0.086975 | 0.045776 | 0.36743 | 0.2211 | -0.60135 | -0.11643 | 0.05661 | 0.13275 | 0.21057 | 0.10529 | 0.1236 | 0.11902 | -0.045776 | 0.036621 | 122.0947 | 121.7606 | 0.19226
10875.5781 | 0.045776 | 0.24246 | -0.23926 | -0.25955 | -0.084381 | -0.25635 | -0.15595 | 0.059509 | -0.032043 | 0.009155 | 0.032043 | 0.17395 | 0 | 0.13275 | 0.061035 | 0.35782 | 0.2446 | -0.60028 | -0.12604 | 0.065155 | -0.004578 | 0.07782 | -0.027466 | 0.1831 | 0.15564 | -0.004578 | 0.064087 | 122.0718 | 121.7514 | 0.19226
10877.3594 | 0.061035 | 0.26169 | -0.24246 | -0.23712 | -0.088654 | -0.28305 | -0.15167 | 0.14191 | 0.10071 | 0.14191 | 0.10071 | 0.11444 | -0.064087 | 0.07782 | 0.061035 | 0.35248 | 0.23819 | -0.60562 | -0.12176 | 0.064087 | 0.10529 | 0.21973 | 0.11444 | 0.12817 | 0.11444 | -0.041199 | 0.054932 | 122.0215 | 121.8018 | 0.21515
10879.0781 | 0.061035 | 0.24567 | -0.24139 | -0.26489 | -0.081177 | -0.26382 | -0.1474 | 0.15106 | 0.10529 | 0.13733 | 0.09613 | 0.09613 | -0.041199 | 0.082397 | 0.030518 | 0.36636 | 0.24994 | -0.60455 | -0.13351 | 0.058746 | 0.09613 | 0.21057 | 0.10071 | 0.13733 | 0.13275 | -0.009155 | 0.022888 | 122.0169 | 121.8063 | 0.2243
10880.8906 | 0.076294 | 0.24246 | -0.22324 | -0.25101 | -0.066223 | -0.25955 | -0.16022 | 0.036621 | -0.027466 | 0.009155 | 0.022888 | 0.16022 | -0.018311 | 0.13733 | 0.045776 | 0.27023 | 0.1239 | -0.56717 | -0.11536 | 0.025635 | -0.009155 | 0.073242 | -0.045776 | 0.15564 | 0.15564 | 0.022888 | 0.10529 | 122.0993 | 121.8246 | 0.17853
10882.6875 | 0.061035 | 0.24567 | -0.24674 | -0.24887 | -0.084381 | -0.27451 | -0.15488 | 0.12817 | 0.13733 | 0.13733 | 0.10071 | 0.10529 | -0.036621 | 0.086975 | 0.061035 | 0.18692 | 0.043793 | -0.56183 | -0.12924 | 0.003204 | 0.09613 | 0.2243 | 0.10529 | 0.086975 | 0.068665 | -0.027466 | 0.064087 | 122.0673 | 121.8521 | 0.17395
10884.4844 | 0.091553 | 0.24994 | -0.2211 | -0.24353 | -0.083313 | -0.25955 | -0.15167 | 0.11902 | 0.091553 | 0.11444 | 0.07782 | 0.10529 | -0.059509 | 0.091553 | 0.076294 | 0.19546 | 0.053406 | -0.55328 | -0.11322 | 0.023499 | 0.09613 | 0.15564 | 0.068665 | 0.091553 | 0.07782 | -0.013733 | 0.054932 | 122.0627 | 121.8842 | 0.16479
10886.2188 | 0.045776 | 0.24674 | -0.2243 | -0.22324 | -0.097198 | -0.23605 | -0.14206 | 0.050354 | -0.036621 | 0 | 0.013733 | 0.13733 | -0.032043 | 0.12817 | 0.061035 | 0.20721 | 0.027771 | -0.5426 | -0.10681 | -0.004272 | -0.009155 | 0.032043 | -0.050354 | 0.11902 | 0.11444 | 0.036621 | 0.11444 | 122.1863 | 121.8567 | 0.14191
10888.0156 | 0.045776 | 0.23819 | -0.23178 | -0.2478 | -0.086517 | -0.26596 | -0.1506 | 0.041199 | -0.018311 | 0.004578 | 0.009155 | 0.13733 | -0.018311 | 0.12817 | 0.030518 | 0.18692 | 0.036316 | -0.54153 | -0.13886 | 0.002136 | -0.018311 | 0.07782 | -0.027466 | 0.14191 | 0.11444 | 0.050354 | 0.10986 | 122.0856 | 121.8887 | 0.15564
10889.8125 | 0.045776 | 0.23926 | -0.22003 | -0.23071 | -0.091858 | -0.26596 | -0.13565 | 0.09613 | 0.022888 | 0.064087 | 0.064087 | 0.10529 | -0.045776 | 0.091553 | 0.045776 | 0.1976 | 0.020294 | -0.54688 | -0.11322 | -0.002136 | 0.091553 | 0.11902 | 0.054932 | 0.091553 | 0.09613 | -0.018311 | 0.073242 | 122.2 | 121.8887 | 0.14191
10891.5312 | 0.076294 | 0.25955 | -0.22644 | -0.23392 | -0.091858 | -0.27557 | -0.15808 | 0.10529 | 0.082397 | 0.11444 | 0.068665 | 0.10529 | -0.054932 | 0.082397 | 0.076294 | 0.19226 | 0.020294 | -0.54367 | -0.12497 | 0.013885 | 0.068665 | 0.13275 | 0.059509 | 0.10071 | 0.07782 | -0.004578 | 0.059509 | 122.081 | 121.8979 | 0.17853
10893.3281 | 0.061035 | 0.25207 | -0.22324 | -0.2243 | -0.074768 | -0.25101 | -0.15167 | 0.1236 | 0.054932 | 0.10986 | 0.082397 | 0.12817 | -0.045776 | 0.086975 | 0.061035 | 0.20615 | 0.026703 | -0.55115 | -0.10895 | 0.008545 | 0.086975 | 0.16022 | 0.059509 | 0.091553 | 0.091553 | -0.009155 | 0.054932 | 122.1954 | 121.8567 | 0.13733
10895.125 | 0.061035 | 0.25635 | -0.22644 | -0.23498 | -0.080109 | -0.28305 | -0.14206 | 0.10529 | 0.086975 | 0.13733 | 0.082397 | 0.10986 | -0.07782 | 0.091553 | 0.061035 | 0.19333 | 0.03418 | -0.55328 | -0.12497 | 0.016022 | 0.07782 | 0.13275 | 0.059509 | 0.086975 | 0.09613 | -0.009155 | 0.054932 | 122.0718 | 121.9025 | 0.18768
10896.9219 | 0.061035 | 0.23285 | -0.24353 | -0.25207 | -0.086517 | -0.27023 | -0.15274 | 0.027466 | -0.032043 | -0.004578 | 0.004578 | 0.15106 | -0.004578 | 0.15106 | 0.061035 | 0.075836 | -0.076904 | -0.50629 | -0.13458 | -0.029907 | -0.050354 | 0.036621 | -0.068665 | 0.10986 | 0.091553 | 0.054932 | 0.12817 | 122.1313 | 121.9299 | 0.13733
10898.7188 | 0.061035 | 0.23178 | -0.22217 | -0.23819 | -0.097198 | -0.23712 | -0.13351 | 0.11444 | 0.032043 | 0.050354 | 0.064087 | 0.11902 | -0.022888 | 0.12817 | 0.045776 | 0.095062 | -0.074768 | -0.5159 | -0.10468 | -0.03418 | 0.013733 | 0.091553 | -0.054932 | 0.091553 | 0.068665 | 0.041199 | 0.11902 | 122.1909 | 121.9482 | 0.10071
10900.4531 | 0.061035 | 0.25742 | -0.24567 | -0.24567 | -0.081177 | -0.28412 | -0.15488 | 0.09613 | 0.050354 | 0.10071 | 0.073242 | 0.10986 | -0.018311 | 0.11444 | 0.045776 | 0.061951 | -0.075836 | -0.5191 | -0.13565 | -0.027771 | 0.054932 | 0.15106 | 0.073242 | 0.068665 | 0.054932 | 0.027466 | 0.086975 | 122.168 | 121.9528 | 0.13275
10902.2344 | 0.061035 | 0.2446 | -0.22751 | -0.26062 | -0.087585 | -0.2446 | -0.15488 | 0.036621 | -0.054932 | 0.004578 | 0.032043 | 0.15564 | 0 | 0.12817 | 0.045776 | 0.086517 | -0.071564 | -0.51056 | -0.11322 | -0.029907 | -0.041199 | 0.064087 | -0.07782 | 0.10986 | 0.082397 | 0.064087 | 0.1236 | 122.2366 | 121.962 | 0.09613
10904.0469 | 0.045776 | 0.25955 | -0.23285 | -0.22217 | -0.086517 | -0.27344 | -0.13351 | 0.14648 | 0.07782 | 0.11902 | 0.082397 | 0.10071 | -0.045776 | 0.086975 | 0.045776 | 0.070496 | -0.081177 | -0.50842 | -0.10254 | -0.019226 | 0.086975 | 0.14648 | 0.059509 | 0.054932 | 0.041199 | 0.032043 | 0.086975 | 122.2 | 121.9803 | 0.14191
10905.8438 | 0.045776 | 0.24139 | -0.24887 | -0.25101 | -0.085449 | -0.27771 | -0.14099 | 0.050354 | -0.013733 | 0.022888 | 0.013733 | 0.13733 | -0.009155 | 0.13733 | 0.045776 | 0.086517 | -0.059814 | -0.50629 | -0.12176 | -0.012817 | -0.036621 | 0.064087 | -0.050354 | 0.1236 | 0.10071 | 0.045776 | 0.11444 | 122.1451 | 122.0078 | 0.12817
10907.6406 | 0.045776 | 0.25848 | -0.24139 | -0.25742 | -0.081177 | -0.27557 | -0.1474 | 0.11444 | 0.091553 | 0.1236 | 0.086975 | 0.10986 | -0.022888 | 0.091553 | 0.076294 | 0.072632 | -0.05127 | -0.52231 | -0.12604 | -0.028839 | 0.082397 | 0.17853 | 0.10986 | 0.064087 | 0.059509 | 0.022888 | 0.064087 | 122.2183 | 122.0078 | 0.12817
10909.3594 | 0.061035 | 0.2478 | -0.22751 | -0.22217 | -0.089722 | -0.24994 | -0.14099 | 0.086975 | -0.004578 | 0.027466 | 0.032043 | 0.12817 | -0.022888 | 0.10071 | 0.061035 | 0.10254 | -0.064087 | -0.52231 | -0.10468 | -0.027771 | 0.045776 | 0.11444 | 0.018311 | 0.068665 | 0.064087 | 0.018311 | 0.086975 | 122.3007 | 121.9757 | 0.091553
10911.1562 | 0.061035 | 0.23498 | -0.22751 | -0.22644 | -0.092926 | -0.24567 | -0.13992 | 0.068665 | -0.045776 | 0.004578 | 0.022888 | 0.15106 | -0.022888 | 0.12817 | 0.076294 | 0.11749 | -0.05127 | -0.50736 | -0.097198 | -0.02243 | 0.009155 | 0.059509 | -0.032043 | 0.091553 | 0.073242 | 0.045776 | 0.09613 | 122.3145 | 121.9803 | 0.10986
10912.9531 | 0.061035 | 0.26703 | -0.24567 | -0.23285 | -0.09613 | -0.28091 | -0.15701 | 0.10071 | 0.064087 | 0.10986 | 0.050354 | 0.10986 | -0.041199 | 0.09613 | 0.061035 | 0.10574 | -0.045929 | -0.51804 | -0.12711 | -0.016022 | 0.054932 | 0.11444 | 0.036621 | 0.068665 | 0.050354 | 0.032043 | 0.091553 | 122.1725 | 122.0306 | 0.15106
10914.7344 | 0.076294 | 0.26169 | -0.22964 | -0.24139 | -0.092926 | -0.26062 | -0.1474 | 0.13275 | 0.086975 | 0.12817 | 0.10986 | 0.10071 | -0.059509 | 0.091553 | 0.061035 | 0.11108 | -0.02243 | -0.52978 | -0.10788 | -0.019226 | 0.086975 | 0.15106 | 0.054932 | 0.082397 | 0.068665 | 0.018311 | 0.054932 | 122.2733 | 122.0032 | 0.13733
10916.4688 | 0.061035 | 0.24674 | -0.24033 | -0.24567 | -0.079041 | -0.24887 | -0.1474 | 0.045776 | -0.022888 | -0.004578 | 0.022888 | 0.14648 | -0.004578 | 0.13275 | 0.030518 | 0.1506 | 0 | -0.52872 | -0.10788 | -0.014954 | -0.041199 | 0.073242 | -0.050354 | 0.11902 | 0.086975 | 0.054932 | 0.10071 | 122.2916 | 121.962 | 0.12817
10918.25 | 0.045776 | 0.23819 | -0.23498 | -0.25314 | -0.077972 | -0.26916 | -0.15381 | 0.036621 | -0.036621 | -0.004578 | 0.013733 | 0.14191 | 0.004578 | 0.14191 | 0.076294 | 0.21042 | 0.093994 | -0.55008 | -0.1207 | 0.010681 | -0.032043 | 0.054932 | -0.045776 | 0.12817 | 0.1236 | 0.032043 | 0.11444 | 122.2504 | 121.9711 | 0.16022
10920.0469 | 0.061035 | 0.27023 | -0.2446 | -0.23285 | -0.035248 | -0.29266 | -0.20401 | 0.20599 | 0.19684 | 0.2243 | 0.22888 | 0.26093 | -0.19684 | -0.045776 | 0.015259 | 4.2458 | 5.4324 | -1.8863 | -0.12604 | 1.3341 | 0.66376 | 0.78735 | 0.85602 | 1.1581 | 1.1444 | -0.81482 | -0.75989 | 121.8887 | 120.5383 | 1.3229
10921.8438 | 0.045776 | 0.2211 | -0.23178 | -0.23712 | -0.088654 | -0.24674 | -0.15274 | 0.10529 | 0.018311 | 0.022888 | 0.054932 | 0.13275 | -0.004578 | 0.13275 | 0.061035 | 0.050201 | -0.12283 | -0.49347 | -0.10574 | -0.049133 | 0.018311 | 0.09613 | -0.045776 | 0.09613 | 0.073242 | 0.059509 | 0.1236 | 122.0901 | 121.7834 | 0.09613
10923.6406 | 0.045776 | 0.23285 | -0.22858 | -0.23178 | -0.093994 | -0.2446 | -0.14954 | 0.041199 | -0.050354 | -0.022888 | 0.009155 | 0.14648 | -0.004578 | 0.13733 | 0.061035 | 0.053406 | -0.13138 | -0.48172 | -0.11963 | -0.035248 | -0.032043 | 0.009155 | -0.059509 | 0.073242 | 0.073242 | 0.064087 | 0.13275 | 122.1954 | 121.8979 | 0.086975
10925.375 | 0.061035 | 0.27878 | -0.22964 | -0.25742 | -0.077972 | -0.29266 | -0.15488 | 0.054932 | 0.036621 | 0.082397 | 0.036621 | 0.1236 | -0.032043 | 0.10986 | 0.061035 | 0.020294 | -0.13351 | -0.49454 | -0.13458 | -0.030975 | 0.009155 | 0.10529 | 0.022888 | 0.050354 | 0.036621 | 0.041199 | 0.10986 | 122.0993 | 121.9894 | 0.15106
10927.1719 | 0.061035 | 0.23285 | -0.22324 | -0.23926 | -0.080109 | -0.24887 | -0.1474 | 0.086975 | 0.004578 | 0.041199 | 0.045776 | 0.13733 | -0.022888 | 0.13733 | 0.030518 | 0.046997 | -0.1239 | -0.50308 | -0.10468 | -0.041656 | -0.004578 | 0.086975 | -0.041199 | 0.082397 | 0.07782 | 0.050354 | 0.11444 | 122.2366 | 121.9528 | 0.091553
10928.9688 | 0.061035 | 0.24353 | -0.24139 | -0.23392 | -0.098267 | -0.25528 | -0.14206 | 0.054932 | -0.027466 | 0.009155 | 0.013733 | 0.13275 | 0.004578 | 0.11902 | 0.045776 | 0.044861 | -0.12283 | -0.4892 | -0.10681 | -0.027771 | 0 | 0.036621 | -0.032043 | 0.073242 | 0.059509 | 0.036621 | 0.10529 | 122.2824 | 121.9711 | 0.10529
10930.6875 | 0.061035 | 0.23498 | -0.22964 | -0.25314 | -0.083313 | -0.28732 | -0.14954 | 0.10071 | 0.082397 | 0.13275 | 0.091553 | 0.10529 | -0.036621 | 0.10529 | 0.030518 | 0.037384 | -0.12176 | -0.49561 | -0.13458 | -0.033112 | 0.018311 | 0.16937 | 0.027466 | 0.073242 | 0.032043 | 0.045776 | 0.09613 | 122.1542 | 122.0215 | 0.13733
10932.4688 | 0.061035 | 0.25314 | -0.24674 | -0.25955 | -0.09613 | -0.29373 | -0.15274 | 0.11902 | 0.11902 | 0.14648 | 0.10529 | 0.10071 | -0.041199 | 0.09613 | 0.045776 | 0.025635 | -0.11643 | -0.50629 | -0.13565 | -0.036316 | 0.086975 | 0.19684 | 0.091553 | 0.050354 | 0.032043 | 0.036621 | 0.091553 | 122.2 | 122.0169 | 0.11444
10934.2344 | 0.061035 | 0.24887 | -0.24994 | -0.23712 | -0.085449 | -0.28091 | -0.16129 | 0.13733 | 0.1236 | 0.14648 | 0.10986 | 0.10986 | -0.041199 | 0.091553 | 0.061035 | 0.03418 | -0.13565 | -0.50842 | -0.13138 | -0.041656 | 0.082397 | 0.19684 | 0.07782 | 0.041199 | 0.036621 | 0.018311 | 0.10071 | 122.2321 | 122.049 | 0.1236
10936.0312 | 0.061035 | 0.24353 | -0.22751 | -0.24033 | -0.088654 | -0.27237 | -0.15595 | 0.14191 | 0.10986 | 0.13733 | 0.091553 | 0.10986 | -0.032043 | 0.10071 | 0.045776 | 0.025635 | -0.11429 | -0.51056 | -0.12283 | -0.048065 | 0.054932 | 0.19226 | 0.059509 | 0.045776 | 0.041199 | 0.022888 | 0.086975 | 122.1954 | 122.0352 | 0.11902
10937.8281 | 0.061035 | 0.25528 | -0.23178 | -0.25528 | -0.1004 | -0.26596 | -0.15488 | 0.082397 | 0.045776 | 0.07782 | 0.041199 | 0.11444 | -0.032043 | 0.10529 | 0.045776 | 0.024567 | -0.11749 | -0.50415 | -0.1239 | -0.046997 | 0.032043 | 0.091553 | 0.004578 | 0.07782 | 0.032043 | 0.032043 | 0.086975 | 122.2 | 122.0627 | 0.13733
10939.625 | 0.061035 | 0.24887 | -0.22644 | -0.23285 | -0.09079 | -0.25314 | -0.14633 | 0.16022 | 0.091553 | 0.10986 | 0.10071 | 0.086975 | -0.041199 | 0.09613 | 0.061035 | 0.042725 | -0.1239 | -0.50522 | -0.10361 | -0.036316 | 0.10071 | 0.13733 | 0.041199 | 0.041199 | 0.013733 | 0.032043 | 0.091553 | 122.3145 | 122.0169 | 0.10529
10941.3594 | 0.061035 | 0.24674 | -0.23605 | -0.23498 | -0.089722 | -0.28091 | -0.15488 | 0.09613 | 0.036621 | 0.082397 | 0.050354 | 0.11902 | -0.041199 | 0.09613 | 0.061035 | 0.032043 | -0.11215 | -0.51163 | -0.11749 | -0.042725 | 0.018311 | 0.091553 | 0.018311 | 0.059509 | 0.054932 | 0.036621 | 0.091553 | 122.2092 | 122.0901 | 0.12817
10943.1406 | 0.045776 | 0.2243 | -0.22644 | -0.25314 | -0.083313 | -0.23071 | -0.14633 | 0.10986 | -0.009155 | 0.036621 | 0.059509 | 0.15564 | -0.009155 | 0.12817 | 0.061035 | 0.058746 | -0.11002 | -0.50201 | -0.11536 | -0.045929 | -0.004578 | 0.068665 | -0.050354 | 0.07782 | 0.059509 | 0.041199 | 0.1236 | 122.3557 | 122.0261 | 0.082397
10944.8594 | 0.030518 | 0.23285 | -0.22644 | -0.22003 | -0.092926 | -0.24033 | -0.1442 | 0.054932 | -0.073242 | -0.027466 | 0.013733 | 0.12817 | -0.018311 | 0.13275 | 0.045776 | 0.069427 | -0.10361 | -0.4892 | -0.099335 | -0.03952 | -0.064087 | 0.004578 | -0.1236 | 0.09613 | 0.09613 | 0.054932 | 0.1236 | 122.2916 | 122.0627 | 0.10529
10946.5938 | 0.061035 | 0.22644 | -0.22537 | -0.25635 | -0.088654 | -0.26276 | -0.14633 | 0.036621 | -0.036621 | -0.009155 | 0.022888 | 0.14191 | 0 | 0.14191 | 0.061035 | 0.05127 | -0.10468 | -0.50201 | -0.11856 | -0.030975 | -0.036621 | 0.068665 | -0.059509 | 0.091553 | 0.082397 | 0.068665 | 0.13733 | 122.3373 | 122.0627 | 0.091553
10948.375 | 0.061035 | 0.23712 | -0.2243 | -0.24246 | -0.085449 | -0.25635 | -0.13886 | 0.10071 | 0.027466 | 0.054932 | 0.041199 | 0.13275 | -0.022888 | 0.11444 | 0.061035 | 0.071564 | -0.099335 | -0.48813 | -0.11429 | -0.046997 | 0.018311 | 0.082397 | -0.036621 | 0.082397 | 0.068665 | 0.068665 | 0.11902 | 122.3328 | 122.0581 | 0.11902
10950.1562 | 0.061035 | 0.26169 | -0.24033 | -0.22537 | -0.089722 | -0.28839 | -0.14206 | 0.036621 | 0.036621 | 0.082397 | 0.064087 | 0.10529 | -0.018311 | 0.09613 | 0.045776 | 0.033112 | -0.1207 | -0.50949 | -0.12924 | -0.014954 | -0.004578 | 0.086975 | 0.013733 | 0.059509 | 0.059509 | 0.032043 | 0.09613 | 122.2412 | 122.1313 | 0.12817
10951.9531 | 0.061035 | 0.24033 | -0.22644 | -0.23071 | -0.093994 | -0.24994 | -0.14526 | 0.082397 | 0.009155 | 0.054932 | 0.045776 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | 0.061951 | -0.11215 | -0.50095 | -0.10254 | -0.036316 | 0.045776 | 0.10071 | 0.027466 | 0.068665 | 0.041199 | 0.027466 | 0.082397 | 122.3877 | 122.0627 | 0.091553
10953.6719 | 0.045776 | 0.25207 | -0.22644 | -0.23712 | -0.098267 | -0.26596 | -0.14206 | 0.1236 | 0.064087 | 0.11902 | 0.091553 | 0.082397 | -0.054932 | 0.07782 | 0.061035 | 0.050201 | -0.10254 | -0.50095 | -0.11856 | -0.027771 | 0.064087 | 0.15106 | 0.050354 | 0.054932 | 0.045776 | 0.027466 | 0.09613 | 122.3648 | 122.0718 | 0.1236
10955.4531 | 0.045776 | 0.22644 | -0.22003 | -0.25421 | -0.084381 | -0.26276 | -0.13886 | 0.1236 | 0.073242 | 0.1236 | 0.10986 | 0.091553 | -0.054932 | 0.10071 | 0.076294 | 0.053406 | -0.092926 | -0.5191 | -0.12283 | -0.041656 | 0.086975 | 0.13275 | 0.054932 | 0.054932 | 0.032043 | 0.018311 | 0.09613 | 122.3465 | 122.0993 | 0.091553
10957.1719 | 0.045776 | 0.23071 | -0.22324 | -0.24139 | -0.084381 | -0.25101 | -0.1506 | 0.10071 | 0.022888 | 0.032043 | 0.045776 | 0.15564 | -0.004578 | 0.15106 | 0.076294 | 0.072632 | -0.092926 | -0.51056 | -0.10361 | -0.035248 | 0.004578 | 0.10071 | -0.032043 | 0.082397 | 0.068665 | 0.064087 | 0.09613 | 122.3648 | 122.0535 | 0.10071
10958.9688 | 0.091553 | 0.23178 | -0.22644 | -0.23392 | -0.083313 | -0.26276 | -0.15167 | 0.018311 | -0.013733 | 0.004578 | 0.032043 | 0.13733 | -0.013733 | 0.15106 | 0.045776 | 0.068359 | -0.09079 | -0.51056 | -0.11749 | -0.032043 | -0.050354 | 0.059509 | -0.041199 | 0.09613 | 0.091553 | 0.059509 | 0.12817 | 122.3969 | 122.0901 | 0.10986
10960.7656 | 0.045776 | 0.2446 | -0.2478 | -0.2446 | -0.099335 | -0.28946 | -0.1474 | 0.11444 | 0.13275 | 0.14648 | 0.09613 | 0.10529 | -0.036621 | 0.10071 | 0.076294 | 0.036316 | -0.087585 | -0.51697 | -0.13031 | -0.028839 | 0.064087 | 0.18768 | 0.073242 | 0.054932 | 0.059509 | 0.022888 | 0.082397 | 122.3145 | 122.1039 | 0.1236
10962.5 | 0.061035 | 0.2446 | -0.2211 | -0.22858 | -0.077972 | -0.2478 | -0.14099 | 0.032043 | -0.041199 | -0.004578 | -0.004578 | 0.13733 | -0.009155 | 0.15106 | 0.045776 | 0.081177 | -0.084381 | -0.5159 | -0.11322 | -0.03952 | -0.018311 | 0.009155 | -0.059509 | 0.07782 | 0.073242 | 0.041199 | 0.11444 | 122.4106 | 122.1085 | 0.10529
10964.2812 | 0.045776 | 0.2478 | -0.24033 | -0.24887 | -0.092926 | -0.28412 | -0.1442 | 0.036621 | -0.032043 | 0.022888 | 0.009155 | 0.1236 | -0.009155 | 0.13733 | 0.10681 | 0.068359 | -0.092926 | -0.51483 | -0.12497 | -0.027771 | -0.045776 | 0.054932 | -0.059509 | 0.09613 | 0.086975 | 0.073242 | 0.12817 | 122.2824 | 122.1451 | 0.13733
10966.0625 | 0.045776 | 0.23819 | -0.22324 | -0.23926 | -0.080109 | -0.2681 | -0.14847 | 0.10986 | 0.041199 | 0.09613 | 0.082397 | 0.09613 | -0.036621 | 0.10071 | 0.061035 | 0.072632 | -0.0737 | -0.50308 | -0.11963 | -0.033112 | 0.064087 | 0.11444 | 0.032043 | 0.054932 | 0.032043 | 0.009155 | 0.082397 | 122.4289 | 122.0947 | 0.11444
10967.8438 | 0.045776 | 0.23178 | -0.22217 | -0.24353 | -0.081177 | -0.26169 | -0.1474 | 0.032043 | -0.054932 | -0.004578 | 0.018311 | 0.14648 | 0 | 0.14191 | 0.045776 | 0.072632 | -0.070496 | -0.50629 | -0.13351 | -0.048065 | -0.036621 | 0.041199 | -0.064087 | 0.10529 | 0.091553 | 0.073242 | 0.14191 | 122.3877 | 122.1085 | 0.10986
10969.5625 | 0.045776 | 0.23819 | -0.22858 | -0.24246 | -0.077972 | -0.25848 | -0.14954 | 0.064087 | -0.027466 | 0.009155 | 0.045776 | 0.13733 | -0.013733 | 0.14191 | 0.061035 | 0.079041 | -0.077972 | -0.50201 | -0.11856 | -0.03418 | -0.004578 | 0.082397 | -0.032043 | 0.09613 | 0.073242 | 0.050354 | 0.1236 | 122.4289 | 122.1176 | 0.11444
10971.3438 | 0.030518 | 0.22217 | -0.21576 | -0.23819 | -0.088654 | -0.25635 | -0.13992 | 0.073242 | -0.018311 | 0.036621 | 0.036621 | 0.13733 | -0.013733 | 0.13275 | 0.030518 | 0.080109 | -0.065155 | -0.50415 | -0.11429 | -0.029907 | -0.022888 | 0.086975 | -0.041199 | 0.086975 | 0.07782 | 0.064087 | 0.1236 | 122.4243 | 122.0947 | 0.10529
10973.0625 | 0.076294 | 0.22751 | -0.22324 | -0.23498 | -0.084381 | -0.24887 | -0.14206 | 0.086975 | 0.013733 | 0.027466 | 0.050354 | 0.12817 | 0 | 0.11444 | 0.045776 | 0.087585 | -0.061951 | -0.49881 | -0.10147 | -0.037384 | -0.013733 | 0.059509 | -0.059509 | 0.091553 | 0.07782 | 0.050354 | 0.11444 | 122.3831 | 122.1451 | 0.10071
10974.8438 | 0.061035 | 0.26489 | -0.23605 | -0.22003 | -0.091858 | -0.30014 | -0.14847 | 0.032043 | 0.009155 | 0.073242 | 0.050354 | 0.13275 | -0.022888 | 0.09613 | 0.030518 | 0.067291 | -0.064087 | -0.5159 | -0.12817 | -0.010681 | 0.013733 | 0.11444 | 0.036621 | 0.064087 | 0.073242 | 0.041199 | 0.086975 | 122.3465 | 122.1588 | 0.15106
10976.6406 | 0.061035 | 0.24246 | -0.2478 | -0.24994 | -0.079041 | -0.26703 | -0.15381 | 0.059509 | 0.013733 | 0.064087 | 0.050354 | 0.13275 | -0.018311 | 0.11902 | 0.045776 | 0.097198 | -0.035248 | -0.52124 | -0.12711 | -0.020294 | -0.041199 | 0.082397 | -0.036621 | 0.10071 | 0.091553 | 0.054932 | 0.11444 | 122.3145 | 122.1588 | 0.14191
10978.3594 | 0.061035 | 0.26703 | -0.23819 | -0.23605 | -0.082245 | -0.28625 | -0.14847 | 0.068665 | 0.041199 | 0.091553 | 0.059509 | 0.10529 | -0.041199 | 0.10071 | 0.061035 | 0.070496 | -0.043793 | -0.52551 | -0.13672 | -0.006409 | 0.022888 | 0.10529 | 0.013733 | 0.086975 | 0.045776 | 0.045776 | 0.10071 | 122.319 | 122.1771 | 0.16022
10980.1406 | 0.045776 | 0.25101 | -0.22324 | -0.23498 | -0.084381 | -0.26382 | -0.1474 | 0.12817 | 0.073242 | 0.11902 | 0.09613 | 0.10986 | -0.036621 | 0.082397 | 0.045776 | 0.11856 | -0.038452 | -0.52765 | -0.099335 | -0.025635 | 0.07782 | 0.14191 | 0.073242 | 0.073242 | 0.064087 | 0.022888 | 0.054932 | 122.4152 | 122.168 | 0.10529
10981.875 | 0.061035 | 0.23712 | -0.24033 | -0.25955 | -0.086517 | -0.26489 | -0.15808 | 0.041199 | -0.041199 | 0.018311 | 0.009155 | 0.14191 | 0.004578 | 0.13275 | 0.045776 | 0.1506 | 0.029907 | -0.53833 | -0.12817 | -0.010681 | -0.036621 | 0.064087 | -0.059509 | 0.1236 | 0.1236 | 0.054932 | 0.10529 | 122.3465 | 122.1771 | 0.14648
10983.6719 | 0.076294 | 0.23178 | -0.23178 | -0.25314 | -0.074768 | -0.2713 | -0.14954 | 0.07782 | 0.027466 | 0.064087 | 0.064087 | 0.1236 | -0.018311 | 0.11902 | 0.061035 | 0.16983 | 0.063019 | -0.55222 | -0.1239 | 0 | -0.018311 | 0.10071 | -0.018311 | 0.11902 | 0.10529 | 0.045776 | 0.11444 | 122.3236 | 122.1863 | 0.17395
10985.4688 | 0.061035 | 0.22751 | -0.2243 | -0.23819 | -0.082245 | -0.25955 | -0.14847 | 0.09613 | -0.009155 | 0.036621 | 0.064087 | 0.15106 | 0.009155 | 0.13275 | 0.030518 | 0.21255 | 0.11108 | -0.53513 | -0.10895 | 0.006409 | 0.032043 | 0.11444 | -0.013733 | 0.13275 | 0.10529 | 0.013733 | 0.10071 | 122.4792 | 122.0947 | 0.15564
10987.2656 | 0.061035 | 0.27771 | -0.24994 | -0.22858 | -0.087585 | -0.28732 | -0.15701 | 0.082397 | 0.032043 | 0.086975 | 0.068665 | 0.11902 | -0.045776 | 0.091553 | 0.015259 | 0.20935 | 0.12604 | -0.55435 | -0.1239 | 0.02243 | 0.045776 | 0.14191 | 0.07782 | 0.10529 | 0.10529 | -0.013733 | 0.068665 | 122.374 | 122.1405 | 0.17853
10988.9844 | 0.076294 | 0.23605 | -0.22964 | -0.23285 | -0.072632 | -0.24674 | -0.15167 | 0.1236 | 0.022888 | 0.050354 | 0.054932 | 0.14191 | -0.018311 | 0.11902 | 0.045776 | 0.30121 | 0.22003 | -0.58746 | -0.098267 | 0.023499 | 0.032043 | 0.11444 | 0 | 0.15106 | 0.13733 | 0.018311 | 0.073242 | 122.4472 | 122.0947 | 0.17853
10990.7656 | 0.061035 | 0.26703 | -0.23071 | -0.23926 | -0.074768 | -0.2948 | -0.16663 | 0.09613 | 0.07782 | 0.13275 | 0.10986 | 0.14648 | -0.068665 | 0.054932 | 0.076294 | 1.3351 | 1.6449 | -0.93246 | -0.13565 | 0.38025 | 0.21057 | 0.32501 | 0.28839 | 0.38452 | 0.3891 | -0.2243 | -0.16022 | 122.3602 | 121.7789 | 0.51727
10992.4844 | 0.045776 | 0.21896 | -0.22537 | -0.24246 | -0.059814 | -0.25421 | -0.15167 | 0.09613 | -0.018311 | 0.045776 | 0.054932 | 0.17853 | -0.045776 | 0.10071 | 0.076294 | 0.99655 | 1.1557 | -0.78507 | -0.099335 | 0.37705 | 0.27008 | 0.29755 | 0.28381 | 0.41657 | 0.39368 | -0.24261 | -0.18768 | 122.4426 | 121.6507 | 0.58136
10994.2656 | 0.045776 | 0.23819 | -0.22858 | -0.23926 | -0.023499 | -0.25742 | -0.19867 | 0.21515 | 0.11902 | 0.15106 | 0.19226 | 0.32044 | -0.17853 | -0.032043 | 0.061035 | 5.2402 | 6.8199 | -2.1384 | -0.10895 | 1.6011 | 0.72327 | 0.78735 | 0.92468 | 1.3916 | 1.3824 | -0.95215 | -0.89264 | 122.2595 | 120.5246 | 1.5793
10995.9844 | 0.030518 | 0.23498 | -0.22751 | -0.24994 | -0.070496 | -0.26276 | -0.16556 | 0.086975 | 0.027466 | 0.054932 | 0.091553 | 0.18768 | -0.050354 | 0.09613 | 0.076294 | 1.5135 | 1.8147 | -0.93246 | -0.10895 | 0.3952 | 0.16022 | 0.28381 | 0.21057 | 0.46234 | 0.4303 | -0.21973 | -0.15106 | 122.2549 | 121.4859 | 0.54474
10997.7812 | 0.061035 | 0.25742 | -0.22964 | -0.23605 | -0.052338 | -0.28732 | -0.18478 | 0.24261 | 0.20599 | 0.24261 | 0.22888 | 0.24261 | -0.17853 | -0.054932 | 0.076294 | 4.0193 | 5.2391 | -1.7496 | -0.13138 | 1.2251 | 0.61798 | 0.71869 | 0.80109 | 1.0574 | 1.0437 | -0.75989 | -0.68665 | 121.9528 | 120.6665 | 1.2909
10999.5625 | 0.045776 | 0.25528 | -0.22324 | -0.22644 | -0.076904 | -0.2713 | -0.14526 | 0.11902 | 0.091553 | 0.12817 | 0.082397 | 0.091553 | -0.045776 | 0.09613 | 0.045776 | 0.048065 | -0.092926 | -0.49667 | -0.1239 | -0.038452 | 0.054932 | 0.14648 | 0.045776 | 0.032043 | 0.036621 | 0.018311 | 0.09613 | 122.3099 | 122.0764 | 0.11902
11001.2656 | 0.061035 | 0.20935 | -0.22858 | -0.25421 | -0.09079 | -0.25101 | -0.1506 | 0.10071 | 0 | 0.041199 | 0.045776 | 0.14191 | -0.004578 | 0.1236 | 0.061035 | 0.19012 | 0.074768 | -0.52551 | -0.12283 | -0.01709 | 0.018311 | 0.11444 | -0.022888 | 0.11902 | 0.09613 | 0.041199 | 0.086975 | 122.3831 | 122.049 | 0.13733
11003.0625 | 0.061035 | 0.24139 | -0.2243 | -0.24567 | -0.085449 | -0.25528 | -0.1474 | 0.054932 | -0.004578 | 0.027466 | 0.054932 | 0.14191 | 0.004578 | 0.1236 | 0.045776 | 0.13565 | 0.009613 | -0.52338 | -0.12497 | -0.007477 | -0.004578 | 0.091553 | -0.009155 | 0.11444 | 0.07782 | 0.041199 | 0.10529 | 122.4152 | 122.0901 | 0.1236
11004.8594 | 0.061035 | 0.24887 | -0.24246 | -0.25742 | -0.09079 | -0.29159 | -0.15595 | 0.032043 | 0.050354 | 0.086975 | 0.059509 | 0.10529 | -0.041199 | 0.11902 | 0.030518 | 0.19012 | 0.11002 | -0.55756 | -0.13565 | 0.014954 | 0.045776 | 0.15106 | 0.091553 | 0.09613 | 0.086975 | 0.009155 | 0.073242 | 122.3465 | 122.0947 | 0.18768
11006.6406 | 0.061035 | 0.23605 | -0.23392 | -0.2211 | -0.082245 | -0.25635 | -0.15381 | 0.13275 | 0.054932 | 0.10071 | 0.10071 | 0.10986 | -0.050354 | 0.11902 | 0.045776 | 0.064087 | -0.097198 | -0.50522 | -0.10254 | -0.038452 | 0.068665 | 0.14191 | 0.041199 | 0.050354 | 0.041199 | 0.013733 | 0.073242 | 122.438 | 122.1451 | 0.09613
11008.3594 | 0.061035 | 0.23926 | -0.23605 | -0.23071 | -0.088654 | -0.25955 | -0.14099 | 0.12817 | 0.050354 | 0.10071 | 0.091553 | 0.10071 | -0.054932 | 0.09613 | 0.061035 | 0.065155 | -0.087585 | -0.51163 | -0.11215 | -0.028839 | 0.073242 | 0.13275 | 0.032043 | 0.054932 | 0.041199 | 0.027466 | 0.091553 | 122.4518 | 122.1451 | 0.10986
11010.1406 | 0.030518 | 0.22751 | -0.23178 | -0.25421 | -0.072632 | -0.2713 | -0.15167 | 0.041199 | -0.036621 | 0 | 0.032043 | 0.14191 | -0.013733 | 0.13733 | 0.045776 | 0.33112 | 0.27451 | -0.58105 | -0.1207 | 0.044861 | -0.004578 | 0.073242 | -0.022888 | 0.18768 | 0.12817 | 0.018311 | 0.068665 | 122.4609 | 122.0718 | 0.16479
11011.875 | 0.061035 | 0.25528 | -0.23285 | -0.24246 | -0.069427 | -0.28625 | -0.15381 | 0.12817 | 0.10071 | 0.13733 | 0.09613 | 0.13275 | -0.073242 | 0.07782 | 0.061035 | 0.81177 | 0.95383 | -0.74448 | -0.13245 | 0.21683 | 0.13733 | 0.2243 | 0.17395 | 0.23804 | 0.23346 | -0.10071 | -0.059509 | 122.2549 | 121.9299 | 0.37079
11013.6719 | 0.045776 | 0.23285 | -0.21469 | -0.2478 | -0.083313 | -0.25421 | -0.15488 | 0.082397 | 0.004578 | 0.054932 | 0.050354 | 0.11902 | -0.050354 | 0.11444 | 0.061035 | 0.20721 | 0.11536 | -0.54581 | -0.11429 | 0.007477 | 0.073242 | 0.11902 | 0.054932 | 0.09613 | 0.086975 | -0.004578 | 0.073242 | 122.4564 | 122.1542 | 0.09613
11015.3906 | 0.030518 | 0.21576 | -0.22217 | -0.25207 | -0.091858 | -0.26062 | -0.13565 | 0.073242 | 0.013733 | 0.032043 | 0.045776 | 0.13733 | -0.004578 | 0.13733 | 0.045776 | 0.069427 | -0.084381 | -0.49774 | -0.11108 | -0.043793 | -0.013733 | 0.086975 | -0.032043 | 0.073242 | 0.064087 | 0.059509 | 0.13733 | 122.4655 | 122.1359 | 0.086975
11017.1875 | 0.076294 | 0.25207 | -0.22324 | -0.23392 | -0.084381 | -0.27557 | -0.15701 | 0.10071 | 0.086975 | 0.1236 | 0.07782 | 0.10529 | -0.045776 | 0.09613 | 0.045776 | 0.044861 | -0.09613 | -0.49881 | -0.12604 | -0.026703 | 0.054932 | 0.10986 | 0.032043 | 0.050354 | 0.059509 | 0.022888 | 0.10986 | 122.3557 | 122.2366 | 0.14191
11018.9219 | 0.091553 | 0.22644 | -0.22644 | -0.23498 | -0.088654 | -0.25635 | -0.15167 | 0.054932 | 0.009155 | 0.018311 | 0.036621 | 0.13275 | -0.018311 | 0.14191 | 0.076294 | 0.061951 | -0.097198 | -0.49988 | -0.10468 | -0.055542 | 0 | 0.073242 | -0.032043 | 0.10071 | 0.073242 | 0.041199 | 0.12817 | 122.4747 | 122.1817 | 0.07782
11020.7031 | 0.045776 | 0.24567 | -0.23605 | -0.26382 | -0.079041 | -0.28305 | -0.15488 | 0.10071 | 0.091553 | 0.13275 | 0.10071 | 0.10529 | -0.032043 | 0.086975 | 0.076294 | 0.11322 | 0.029907 | -0.51376 | -0.13458 | -0.005341 | 0.059509 | 0.1831 | 0.054932 | 0.064087 | 0.07782 | 0.018311 | 0.073242 | 122.406 | 122.2183 | 0.16937
11022.5 | 0.061035 | 0.24246 | -0.23712 | -0.25528 | -0.077972 | -0.25742 | -0.15274 | 0.022888 | -0.045776 | -0.013733 | 0.009155 | 0.14648 | 0.018311 | 0.14648 | 0.061035 | 0.065155 | -0.09613 | -0.50415 | -0.11856 | -0.036316 | -0.064087 | 0.045776 | -0.073242 | 0.10071 | 0.073242 | 0.07782 | 0.12817 | 122.4426 | 122.2046 | 0.11444
11024.2344 | 0.015259 | 0.25955 | -0.24246 | -0.22324 | -0.09079 | -0.28198 | -0.14847 | 0.10071 | 0.091553 | 0.1236 | 0.082397 | 0.09613 | -0.045776 | 0.091553 | 0.030518 | 0.050201 | -0.10361 | -0.50949 | -0.10895 | -0.029907 | 0.07782 | 0.14191 | 0.050354 | 0.041199 | 0.032043 | 0.022888 | 0.091553 | 122.3877 | 122.2458 | 0.13733
11026.0156 | 0.076294 | 0.24033 | -0.23498 | -0.25101 | -0.081177 | -0.25207 | -0.16663 | 0.068665 | -0.004578 | 0.027466 | 0.050354 | 0.16479 | -0.032043 | 0.10986 | 0.061035 | 0.88119 | 0.99335 | -0.76263 | -0.11643 | 0.21469 | 0.064087 | 0.17395 | 0.082397 | 0.3067 | 0.29297 | -0.10071 | -0.036621 | 122.4976 | 121.9299 | 0.32501
11027.8125 | 0.061035 | 0.22537 | -0.2243 | -0.24139 | -0.084381 | -0.23926 | -0.15808 | 0.073242 | 0 | 0.045776 | 0.054932 | 0.15564 | -0.036621 | 0.091553 | 0.061035 | 1.1813 | 1.3811 | -0.84701 | -0.10574 | 0.31937 | 0.1236 | 0.16937 | 0.12817 | 0.37994 | 0.35706 | -0.17395 | -0.10071 | 122.3923 | 121.7743 | 0.43488
11029.5938 | 0.061035 | 0.23605 | -0.22964 | -0.25207 | -0.064087 | -0.26703 | -0.16342 | 0.10529 | 0.027466 | 0.068665 | 0.10986 | 0.17853 | -0.054932 | 0.082397 | 0.061035 | 1.3725 | 1.6727 | -0.90683 | -0.11429 | 0.36636 | 0.16937 | 0.27924 | 0.21973 | 0.41657 | 0.41657 | -0.20599 | -0.15106 | 122.3099 | 121.669 | 0.45776
11031.375 | 0.045776 | 0.23712 | -0.23819 | -0.22964 | -0.060883 | -0.27237 | -0.17517 | 0.11902 | 0.059509 | 0.10986 | 0.10529 | 0.20142 | -0.082397 | 0.064087 | 0.045776 | 1.9557 | 2.4802 | -1.0905 | -0.10574 | 0.56397 | 0.28381 | 0.37079 | 0.37537 | 0.56305 | 0.55389 | -0.34332 | -0.28839 | 122.3145 | 121.4493 | 0.6546
11033.1719 | 0.061035 | 0.22751 | -0.22217 | -0.23819 | -0.072632 | -0.23926 | -0.17624 | 0.14648 | 0.07782 | 0.091553 | 0.11902 | 0.21057 | -0.10071 | 0.064087 | 0.045776 | 2.2409 | 2.8358 | -1.1856 | -0.10468 | 0.65155 | 0.27924 | 0.38452 | 0.34332 | 0.62256 | 0.61798 | -0.36621 | -0.32044 | 122.2 | 121.3531 | 0.71411
11034.9688 | 0.045776 | 0.23712 | -0.2243 | -0.23819 | -0.055542 | -0.27878 | -0.18799 | 0.086975 | 0.050354 | 0.091553 | 0.09613 | 0.20142 | -0.091553 | 0.068665 | 0.030518 | 2.3274 | 2.9886 | -1.2166 | -0.13138 | 0.69 | 0.2655 | 0.39825 | 0.3891 | 0.67291 | 0.6546 | -0.39368 | -0.31586 | 122.0764 | 121.2524 | 0.76446
11036.7656 | 0.030518 | 0.2446 | -0.23392 | -0.25421 | -0.03418 | -0.29587 | -0.1976 | 0.21515 | 0.19226 | 0.23346 | 0.20599 | 0.20599 | -0.13275 | -0.009155 | 0.045776 | 2.7258 | 3.5312 | -1.3416 | -0.14313 | 0.81711 | 0.42572 | 0.59967 | 0.57678 | 0.737 | 0.72327 | -0.50812 | -0.42572 | 122.0123 | 121.0602 | 0.90179
11038.5625 | 0.061035 | 0.23392 | -0.22003 | -0.25101 | -0.040588 | -0.2478 | -0.18906 | 0.15564 | 0.032043 | 0.09613 | 0.10529 | 0.22888 | -0.086975 | 0.032043 | 0.045776 | 2.8625 | 3.6818 | -1.3693 | -0.11536 | 0.83313 | 0.37994 | 0.46234 | 0.5127 | 0.80566 | 0.76904 | -0.5127 | -0.43488 | 122.0856 | 120.9412 | 0.89264
11040.2812 | 0.045776 | 0.21896 | -0.21469 | -0.24567 | -0.057678 | -0.25101 | -0.16342 | 0.086975 | -0.022888 | 0.050354 | 0.073242 | 0.20142 | -0.059509 | 0.068665 | 0.045776 | 1.7902 | 2.1843 | -1.0126 | -0.11002 | 0.49347 | 0.18768 | 0.24261 | 0.21973 | 0.53101 | 0.5127 | -0.27466 | -0.21057 | 122.0306 | 121.17 | 0.60425
11042.0625 | 0.076294 | 0.2243 | -0.22003 | -0.2478 | -0.042725 | -0.25314 | -0.18906 | 0.18768 | 0.09613 | 0.12817 | 0.16022 | 0.25177 | -0.10071 | 0.050354 | 0.061035 | 3.027 | 3.8794 | -1.4185 | -0.11749 | 0.87906 | 0.39825 | 0.53101 | 0.53101 | 0.82398 | 0.82398 | -0.53101 | -0.45776 | 122.0078 | 120.8176 | 0.94299
11043.8594 | 0.061035 | 0.23712 | -0.22644 | -0.23819 | -0.012817 | -0.26916 | -0.21149 | 0.24261 | 0.19684 | 0.23804 | 0.22888 | 0.26093 | -0.17395 | -0.045776 | 0.030518 | 4.3622 | 5.7518 | -1.8468 | -0.12711 | 1.3063 | 0.64087 | 0.79651 | 0.86517 | 1.1307 | 1.1261 | -0.82398 | -0.74616 | 121.843 | 120.3186 | 1.3184
11045.6562 | 0.061035 | 0.2211 | -0.2179 | -0.23498 | -0.048065 | -0.25207 | -0.18051 | 0.11444 | 0.018311 | 0.064087 | 0.10986 | 0.23804 | -0.10986 | 0.022888 | 0.045776 | 2.9469 | 3.7726 | -1.3768 | -0.11215 | 0.84274 | 0.34332 | 0.43945 | 0.44861 | 0.79651 | 0.80109 | -0.48981 | -0.4303 | 121.756 | 120.7764 | 0.86517
11047.375 | 0.076294 | 0.24033 | -0.23819 | -0.24887 | -0.050201 | -0.29159 | -0.18799 | 0.16937 | 0.14191 | 0.17395 | 0.1831 | 0.20599 | -0.1236 | 0.022888 | 0.061035 | 2.9427 | 3.8313 | -1.4131 | -0.12283 | 0.86517 | 0.3891 | 0.50354 | 0.49439 | 0.81482 | 0.79193 | -0.51727 | -0.43945 | 121.7285 | 120.7672 | 0.93384
11049.1719 | 0.030518 | 0.25101 | -0.22858 | -0.24033 | 0.03952 | -0.28946 | -0.27985 | 0.37079 | 0.36163 | 0.40741 | 0.40283 | 0.4303 | -0.35248 | -0.19684 | 0.061035 | 9.5233 | 12.6262 | -3.4062 | -0.13886 | 2.869 | 1.3229 | 1.5656 | 1.8585 | 2.3987 | 2.3987 | -1.7853 | -1.7258 | 121.5134 | 118.602 | 2.7878
11050.9531 | 0.061035 | 0.24139 | -0.23071 | -0.24567 | -0.054474 | -0.28732 | -0.20401 | 0.1831 | 0.16022 | 0.20599 | 0.18768 | 0.21057 | -0.14191 | -0.004578 | 0.061035 | 3.1627 | 4.1368 | -1.4644 | -0.13351 | 0.92819 | 0.48981 | 0.62714 | 0.64545 | 0.85144 | 0.82855 | -0.54932 | -0.50812 | 121.3898 | 120.3232 | 0.99335
11052.75 | 0.045776 | 0.23178 | -0.23285 | -0.22751 | -0.052338 | -0.24353 | -0.18799 | 0.12817 | 0.041199 | 0.086975 | 0.11444 | 0.21515 | -0.07782 | 0.064087 | 0.045776 | 2.2772 | 2.8561 | -1.1739 | -0.10468 | 0.63232 | 0.28839 | 0.42114 | 0.36621 | 0.63629 | 0.60883 | -0.36621 | -0.29297 | 121.6507 | 120.6665 | 0.70953
11054.4844 | 0.045776 | 0.24033 | -0.22858 | -0.23071 | -0.077972 | -0.25742 | -0.1474 | 0.032043 | -0.041199 | -0.009155 | 0.027466 | 0.15564 | 0.022888 | 0.16937 | 0.045776 | 0.061951 | -0.092926 | -0.49454 | -0.10681 | -0.033112 | -0.050354 | 0.054932 | -0.073242 | 0.07782 | 0.082397 | 0.045776 | 0.11444 | 121.5866 | 121.5408 | 0.10529
11056.2656 | 0.045776 | 0.23178 | -0.21896 | -0.23498 | -0.082245 | -0.24994 | -0.13031 | 0.09613 | 0.013733 | 0.050354 | 0.050354 | 0.14648 | -0.027466 | 0.13275 | 0.045776 | 0.19546 | 0.063019 | -0.53513 | -0.11429 | -0.009613 | 0.036621 | 0.09613 | -0.009155 | 0.1236 | 0.10529 | 0.045776 | 0.10071 | 121.8109 | 121.5317 | 0.091553
11058 | 0.045776 | 0.23605 | -0.22324 | -0.22858 | -0.077972 | -0.26382 | -0.1474 | 0.10529 | 0.027466 | 0.059509 | 0.059509 | 0.15564 | -0.027466 | 0.11444 | 0.076294 | 0.52124 | 0.53299 | -0.63019 | -0.11108 | 0.098267 | 0.068665 | 0.14648 | 0.045776 | 0.1831 | 0.17853 | -0.027466 | 0.009155 | 121.7651 | 121.4218 | 0.2243
11059.7969 | 0.030518 | 0.24353 | -0.24139 | -0.24033 | -0.09079 | -0.28946 | -0.1506 | 0.09613 | 0.10529 | 0.13733 | 0.082397 | 0.091553 | -0.027466 | 0.09613 | 0.076294 | 0.023499 | -0.10895 | -0.51163 | -0.12817 | -0.029907 | 0.027466 | 0.17853 | 0.059509 | 0.050354 | 0.068665 | 0.032043 | 0.10986 | 121.7285 | 121.6232 | 0.14191
11061.5938 | 0.076294 | 0.23712 | -0.24033 | -0.24567 | -0.089722 | -0.29159 | -0.14954 | 0.036621 | 0.027466 | 0.068665 | 0.054932 | 0.086975 | -0.032043 | 0.086975 | 0.061035 | 0.025635 | -0.11536 | -0.50308 | -0.12924 | -0.027771 | -0.013733 | 0.10071 | 0.009155 | 0.059509 | 0.054932 | 0.036621 | 0.10529 | 121.907 | 121.756 | 0.13733
11063.375 | 0.045776 | 0.2243 | -0.22217 | -0.24139 | -0.092926 | -0.24567 | -0.14633 | 0.11444 | 0.009155 | 0.036621 | 0.059509 | 0.11444 | -0.013733 | 0.12817 | 0.045776 | 0.11643 | -0.026703 | -0.51804 | -0.10681 | -0.030975 | -0.004578 | 0.09613 | -0.013733 | 0.091553 | 0.09613 | 0.036621 | 0.10071 | 121.907 | 121.5637 | 0.1236
11065.1562 | 0.045776 | 0.2211 | -0.23285 | -0.23926 | -0.081177 | -0.26703 | -0.15915 | 0.045776 | -0.036621 | -0.004578 | 0.027466 | 0.15106 | -0.004578 | 0.12817 | 0.061035 | 0.23926 | 0.13458 | -0.55969 | -0.12283 | 0.010681 | -0.022888 | 0.082397 | -0.013733 | 0.13733 | 0.13275 | 0.032043 | 0.091553 | 121.6003 | 121.3028 | 0.13275
11066.8906 | 0.030518 | 0.23498 | -0.24353 | -0.2478 | -0.085449 | -0.28625 | -0.15488 | 0.10071 | 0.091553 | 0.10071 | 0.10986 | 0.11902 | -0.054932 | 0.09613 | 0.061035 | 0.42618 | 0.37811 | -0.63019 | -0.12176 | 0.079041 | 0.022888 | 0.17853 | 0.091553 | 0.15564 | 0.15564 | -0.027466 | 0.041199 | 118.3273 | 118.2953 | 0.21057
11068.6875 | 0.061035 | 0.23926 | -0.23071 | -0.21896 | -0.057678 | -0.25955 | -0.17197 | 0.11902 | 0.045776 | 0.091553 | 0.10986 | 0.17853 | -0.073242 | 0.054932 | 0.061035 | 1.7218 | 2.1437 | -0.99869 | -0.11429 | 0.46249 | 0.27008 | 0.36163 | 0.33875 | 0.47607 | 0.45776 | -0.29297 | -0.2243 | 121.5134 | 120.726 | 0.55847
11070.4062 | 0.076294 | 0.23071 | -0.21683 | -0.24246 | -0.071564 | -0.25101 | -0.15808 | 0.15564 | 0.054932 | 0.086975 | 0.082397 | 0.15564 | -0.054932 | 0.091553 | 0.030518 | 1.1279 | 1.3618 | -0.82031 | -0.10895 | 0.28305 | 0.14648 | 0.23346 | 0.14191 | 0.36163 | 0.34332 | -0.13275 | -0.091553 | 121.3257 | 120.7031 | 0.39825
11072.1875 | 0.045776 | 0.26276 | -0.23926 | -0.22964 | -0.0737 | -0.29266 | -0.15381 | 0.10986 | 0.11444 | 0.15564 | 0.11444 | 0.11902 | -0.050354 | 0.091553 | 0.061035 | 0.3717 | 0.37918 | -0.63446 | -0.13565 | 0.083313 | 0.11902 | 0.24719 | 0.14648 | 0.12817 | 0.14191 | -0.041199 | 0.022888 | 121.138 | 120.8679 | 0.2243
11073.9844 | 0.045776 | 0.23819 | -0.23071 | -0.25101 | -0.10254 | -0.26489 | -0.1474 | 0.027466 | -0.041199 | -0.009155 | 0.018311 | 0.15564 | -0.013733 | 0.15564 | 0.076294 | 0.072632 | -0.079041 | -0.49988 | -0.12604 | -0.042725 | -0.064087 | 0.018311 | -0.07782 | 0.10071 | 0.10529 | 0.059509 | 0.13275 | 121.4447 | 121.2799 | 0.11444
11075.7188 | 0.045776 | 0.23178 | -0.2211 | -0.23498 | -0.075836 | -0.24887 | -0.14313 | 0.13275 | 0.013733 | 0.027466 | 0.054932 | 0.14191 | -0.022888 | 0.1236 | 0.030518 | 0.10681 | -0.048065 | -0.50308 | -0.11002 | -0.019226 | 0.009155 | 0.082397 | -0.041199 | 0.086975 | 0.091553 | 0.059509 | 0.10986 | 121.2524 | 120.9641 | 0.09613
11077.5156 | 0.061035 | 0.25742 | -0.22537 | -0.25101 | -0.088654 | -0.29694 | -0.14633 | 0.050354 | 0.013733 | 0.07782 | 0.059509 | 0.10986 | -0.045776 | 0.11444 | 0.030518 | 0.037384 | -0.10788 | -0.50842 | -0.14099 | -0.024567 | 0.009155 | 0.086975 | 0.018311 | 0.073242 | 0.054932 | 0.027466 | 0.086975 | 121.0007 | 120.845 | 0.14191
11079.25 | 0.045776 | 0.27985 | -0.23498 | -0.23819 | -0.089722 | -0.27664 | -0.14847 | 0.086975 | 0.032043 | 0.082397 | 0.050354 | 0.09613 | -0.045776 | 0.091553 | 0.061035 | 0.030975 | -0.13031 | -0.49667 | -0.13458 | -0.041656 | 0.027466 | 0.10529 | 0.018311 | 0.064087 | 0.050354 | 0.036621 | 0.10071 | 121.2708 | 121.0968 | 0.12817
11081.0312 | 0.061035 | 0.23498 | -0.22964 | -0.25742 | -0.091858 | -0.26489 | -0.15381 | 0.036621 | -0.036621 | 0.013733 | 0.004578 | 0.15106 | 0.004578 | 0.15564 | 0.061035 | 0.038452 | -0.11536 | -0.49881 | -0.11963 | -0.045929 | -0.064087 | 0.032043 | -0.068665 | 0.091553 | 0.082397 | 0.073242 | 0.13275 | 121.4905 | 121.3303 | 0.09613
11082.8281 | 0.061035 | 0.23178 | -0.22751 | -0.23712 | -0.084381 | -0.27878 | -0.16769 | 0.091553 | 0.059509 | 0.07782 | 0.064087 | 0.11444 | -0.022888 | 0.10529 | 0.061035 | 0.035248 | -0.11002 | -0.50842 | -0.1239 | -0.041656 | -0.013733 | 0.086975 | -0.013733 | 0.059509 | 0.068665 | 0.064087 | 0.1236 | 121.5134 | 121.3898 | 0.11902
11084.5469 | 0.045776 | 0.24246 | -0.22003 | -0.23071 | -0.10254 | -0.24994 | -0.13779 | 0.059509 | -0.050354 | -0.013733 | 0.013733 | 0.16479 | -0.009155 | 0.1236 | 0.076294 | 0.040588 | -0.11643 | -0.49133 | -0.10147 | -0.048065 | -0.022888 | 0.009155 | -0.054932 | 0.073242 | 0.068665 | 0.059509 | 0.13733 | 121.7285 | 121.3852 | 0.091553
11086.3281 | 0.045776 | 0.22644 | -0.22324 | -0.2446 | -0.079041 | -0.25742 | -0.14526 | 0.045776 | -0.041199 | 0.004578 | 0.032043 | 0.14191 | 0.004578 | 0.14191 | 0.061035 | 0.050201 | -0.12176 | -0.49561 | -0.11002 | -0.05127 | -0.032043 | 0.064087 | -0.041199 | 0.086975 | 0.073242 | 0.068665 | 0.1236 | 121.7514 | 121.4172 | 0.086975
11088.1094 | 0.091553 | 0.22751 | -0.22217 | -0.23498 | -0.072632 | -0.25421 | -0.13672 | 0.09613 | 0.013733 | 0.050354 | 0.032043 | 0.1236 | -0.009155 | 0.13733 | 0.045776 | 0.052338 | -0.11749 | -0.48172 | -0.10468 | -0.053406 | 0 | 0.086975 | -0.045776 | 0.086975 | 0.082397 | 0.059509 | 0.12817 | 121.7514 | 121.4447 | 0.07782
11089.9062 | 0.061035 | 0.26169 | -0.24139 | -0.24246 | -0.09079 | -0.28839 | -0.15274 | 0.022888 | 0.022888 | 0.07782 | 0.045776 | 0.1236 | -0.032043 | 0.10529 | 0.061035 | 0.018158 | -0.12924 | -0.49027 | -0.13886 | -0.028839 | 0.013733 | 0.10986 | 0.018311 | 0.064087 | 0.064087 | 0.041199 | 0.11444 | 121.7194 | 121.5271 | 0.1236
11091.6875 | 0.061035 | 0.2681 | -0.24994 | -0.23285 | -0.084381 | -0.29266 | -0.15381 | 0.054932 | 0.027466 | 0.086975 | 0.041199 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | 0.024567 | -0.13458 | -0.48599 | -0.13245 | -0.032043 | -0.009155 | 0.082397 | 0.022888 | 0.041199 | 0.050354 | 0.032043 | 0.091553 | 121.6965 | 121.5546 | 0.12817
11093.4062 | 0.045776 | 0.26489 | -0.23178 | -0.23498 | -0.09079 | -0.28412 | -0.15701 | 0.10529 | 0.059509 | 0.11444 | 0.050354 | 0.10986 | -0.027466 | 0.10071 | 0.045776 | 0.027771 | -0.12711 | -0.50522 | -0.12283 | -0.046997 | 0.064087 | 0.14191 | 0.064087 | 0.050354 | 0.045776 | 0.022888 | 0.10071 | 121.7606 | 121.5546 | 0.13275
11095.1875 | 0.030518 | 0.26169 | -0.23071 | -0.24567 | -0.084381 | -0.28198 | -0.15274 | 0.073242 | 0.032043 | 0.091553 | 0.064087 | 0.11902 | -0.036621 | 0.10986 | 0.061035 | 0.02243 | -0.13138 | -0.50949 | -0.13351 | -0.037384 | 0.032043 | 0.11444 | 0.036621 | 0.054932 | 0.045776 | 0.041199 | 0.11902 | 121.7789 | 121.582 | 0.09613
11096.9531 | 0.045776 | 0.27451 | -0.24139 | -0.22858 | -0.10788 | -0.27771 | -0.15595 | 0.07782 | 0.036621 | 0.086975 | 0.050354 | 0.12817 | -0.022888 | 0.10071 | 0.076294 | 0.025635 | -0.13351 | -0.49347 | -0.13031 | -0.049133 | 0.032043 | 0.10986 | 0.027466 | 0.073242 | 0.050354 | 0.041199 | 0.10986 | 121.7972 | 121.6187 | 0.12817
11098.7344 | 0.061035 | 0.25101 | -0.24246 | -0.21469 | -0.088654 | -0.26062 | -0.15595 | 0.15106 | 0.073242 | 0.11902 | 0.07782 | 0.09613 | -0.032043 | 0.07782 | 0.091553 | 0.032043 | -0.13992 | -0.50201 | -0.10468 | -0.052338 | 0.073242 | 0.13275 | 0.027466 | 0.045776 | 0.045776 | 0.022888 | 0.086975 | 121.7834 | 121.6278 | 0.11902
11100.5312 | 0.061035 | 0.2478 | -0.23178 | -0.2446 | -0.0737 | -0.27878 | -0.15488 | 0.12817 | 0.059509 | 0.10529 | 0.068665 | 0.091553 | -0.027466 | 0.10529 | 0.061035 | 0.026703 | -0.12924 | -0.50201 | -0.11963 | -0.043793 | 0.050354 | 0.086975 | -0.009155 | 0.059509 | 0.036621 | 0.027466 | 0.10986 | 121.788 | 121.6599 | 0.14648
11102.2656 | 0.061035 | 0.2243 | -0.22537 | -0.25314 | -0.082245 | -0.25101 | -0.15381 | 0.059509 | -0.036621 | 0.004578 | 0.036621 | 0.14648 | 0 | 0.11902 | 0.030518 | 0.058746 | -0.11749 | -0.49988 | -0.10681 | -0.059814 | -0.018311 | 0.082397 | -0.068665 | 0.07782 | 0.064087 | 0.082397 | 0.13275 | 121.9299 | 121.6049 | 0.086975
11104.0469 | 0.061035 | 0.20721 | -0.2211 | -0.24246 | -0.086517 | -0.22858 | -0.14206 | 0.032043 | -0.054932 | -0.022888 | 0.018311 | 0.15106 | 0.009155 | 0.14191 | 0.030518 | 0.054474 | -0.11215 | -0.4924 | -0.099335 | -0.044861 | -0.068665 | 0 | -0.11444 | 0.082397 | 0.064087 | 0.07782 | 0.13275 | 121.8842 | 121.6507 | 0.10986
11105.8281 | 0.045776 | 0.25742 | -0.23285 | -0.24994 | -0.085449 | -0.28625 | -0.14206 | 0.073242 | 0.086975 | 0.10071 | 0.054932 | 0.11444 | -0.050354 | 0.091553 | 0.061035 | 0.025635 | -0.10681 | -0.49774 | -0.13138 | -0.029907 | 0.045776 | 0.1236 | 0.013733 | 0.050354 | 0.041199 | 0.032043 | 0.082397 | 121.8246 | 121.7102 | 0.1236
11107.6094 | 0.076294 | 0.21042 | -0.21683 | -0.22858 | -0.087585 | -0.24674 | -0.14099 | 0.041199 | -0.041199 | -0.018311 | 0.018311 | 0.12817 | -0.004578 | 0.12817 | 0.061035 | 0.052338 | -0.11215 | -0.49561 | -0.11536 | -0.050201 | -0.027466 | 0.018311 | -0.11444 | 0.07782 | 0.068665 | 0.068665 | 0.12817 | 121.9299 | 121.6736 | 0.10986
11109.4062 | 0.045776 | 0.23712 | -0.21896 | -0.23926 | -0.071564 | -0.26596 | -0.13565 | 0.1236 | 0.064087 | 0.10071 | 0.091553 | 0.10986 | -0.041199 | 0.091553 | 0.076294 | 0.03952 | -0.13031 | -0.48706 | -0.10895 | -0.041656 | 0.068665 | 0.14191 | 0.036621 | 0.041199 | 0.036621 | 0.032043 | 0.09613 | 121.9849 | 121.6782 | 0.09613
11111.1875 | 0.030518 | 0.23392 | -0.23392 | -0.25314 | -0.089722 | -0.28732 | -0.13992 | 0.11444 | 0.11444 | 0.14191 | 0.10986 | 0.10529 | -0.036621 | 0.10986 | 0.061035 | 0.009613 | -0.13886 | -0.5127 | -0.1239 | -0.043793 | 0.045776 | 0.19226 | 0.064087 | 0.050354 | 0.045776 | 0.032043 | 0.10986 | 121.8567 | 121.7148 | 0.11902
11112.9844 | 0.045776 | 0.2446 | -0.21683 | -0.23819 | -0.091858 | -0.23819 | -0.13672 | 0.09613 | -0.009155 | 0.009155 | 0.041199 | 0.12817 | -0.027466 | 0.11444 | 0.061035 | 0.05661 | -0.11643 | -0.49454 | -0.095062 | -0.048065 | -0.018311 | 0.041199 | -0.07782 | 0.07782 | 0.064087 | 0.073242 | 0.1236 | 121.9711 | 121.7285 | 0.10071
11114.7656 | 0.061035 | 0.23819 | -0.22217 | -0.22964 | -0.081177 | -0.2478 | -0.15381 | 0.064087 | -0.032043 | 0.013733 | 0.022888 | 0.12817 | -0.018311 | 0.12817 | 0.045776 | 0.040588 | -0.12604 | -0.48599 | -0.11322 | -0.041656 | 0.018311 | 0.073242 | -0.018311 | 0.07782 | 0.054932 | 0.054932 | 0.11444 | 122.0444 | 121.7056 | 0.10529
11116.4844 | 0.076294 | 0.25848 | -0.22751 | -0.22751 | -0.082245 | -0.27557 | -0.14099 | 0.1236 | 0.064087 | 0.1236 | 0.091553 | 0.082397 | -0.032043 | 0.09613 | 0.045776 | 0.036316 | -0.12497 | -0.49667 | -0.1207 | -0.037384 | 0.073242 | 0.14648 | 0.054932 | 0.032043 | 0.041199 | 0.018311 | 0.09613 | 121.9345 | 121.7606 | 0.12817
11118.2656 | 0.076294 | 0.24887 | -0.2211 | -0.23605 | -0.092926 | -0.27451 | -0.14526 | 0.1236 | 0.082397 | 0.13275 | 0.07782 | 0.091553 | -0.036621 | 0.09613 | 0.061035 | 0.037384 | -0.11429 | -0.49347 | -0.1207 | -0.03418 | 0.07782 | 0.13733 | 0.050354 | 0.036621 | 0.036621 | 0.050354 | 0.10529 | 121.9299 | 121.7743 | 0.1236
11120 | 0.061035 | 0.24139 | -0.22964 | -0.24246 | -0.088654 | -0.28091 | -0.15381 | 0.12817 | 0.10071 | 0.11902 | 0.082397 | 0.086975 | -0.041199 | 0.10071 | 0.061035 | 0.027771 | -0.12924 | -0.50415 | -0.10681 | -0.043793 | 0.064087 | 0.12817 | 0.022888 | 0.041199 | 0.041199 | 0.022888 | 0.09613 | 121.9391 | 121.8018 | 0.11444
11121.7812 | 0.045776 | 0.22751 | -0.23605 | -0.22858 | -0.087585 | -0.25101 | -0.13992 | 0.054932 | -0.068665 | -0.022888 | 0.009155 | 0.14648 | -0.004578 | 0.13275 | 0.045776 | 0.053406 | -0.12497 | -0.50629 | -0.10147 | -0.043793 | -0.036621 | -0.013733 | -0.10529 | 0.07782 | 0.073242 | 0.064087 | 0.13733 | 122.0398 | 121.7697 | 0.082397
11123.5625 | 0.030518 | 0.24353 | -0.21469 | -0.23926 | -0.088654 | -0.25101 | -0.13779 | 0.086975 | 0.018311 | 0.054932 | 0.054932 | 0.13275 | -0.013733 | 0.12817 | 0.045776 | 0.046997 | -0.11215 | -0.49988 | -0.11536 | -0.048065 | 0 | 0.086975 | -0.036621 | 0.091553 | 0.082397 | 0.073242 | 0.11444 | 122.0627 | 121.7606 | 0.09613
11125.2969 | 0.045776 | 0.22644 | -0.21896 | -0.25101 | -0.083313 | -0.25101 | -0.13565 | 0.07782 | 0.009155 | 0.027466 | 0.032043 | 0.10529 | -0.018311 | 0.12817 | 0.045776 | 0.045929 | -0.10468 | -0.49667 | -0.11215 | -0.046997 | -0.013733 | 0.059509 | -0.068665 | 0.082397 | 0.068665 | 0.059509 | 0.10986 | 122.0306 | 121.7834 | 0.10529
11127.0938 | 0.045776 | 0.24139 | -0.22003 | -0.23926 | -0.092926 | -0.27023 | -0.13351 | 0 | -0.054932 | -0.027466 | 0.013733 | 0.14648 | -0.004578 | 0.13275 | 0.061035 | 0.05661 | -0.11108 | -0.49988 | -0.11108 | -0.03418 | -0.050354 | 0 | -0.068665 | 0.07782 | 0.082397 | 0.064087 | 0.11902 | 122.081 | 121.7789 | 0.086975
11128.9062 | 0.061035 | 0.21576 | -0.22964 | -0.2681 | -0.076904 | -0.25848 | -0.14954 | 0.045776 | -0.004578 | 0.041199 | 0.054932 | 0.14648 | 0.004578 | 0.12817 | 0.045776 | 0.048065 | -0.09613 | -0.50201 | -0.12924 | -0.040588 | -0.027466 | 0.07782 | -0.036621 | 0.10986 | 0.082397 | 0.050354 | 0.13275 | 122.0993 | 121.8063 | 0.10071
11130.6406 | 0.045776 | 0.24674 | -0.22858 | -0.24353 | -0.077972 | -0.28519 | -0.15488 | 0.091553 | 0.10529 | 0.14648 | 0.10071 | 0.091553 | -0.027466 | 0.10071 | 0.045776 | 0.02243 | -0.11108 | -0.50201 | -0.12817 | -0.038452 | 0.032043 | 0.17853 | 0.064087 | 0.064087 | 0.041199 | 0.041199 | 0.11444 | 121.9803 | 121.843 | 0.10529
11132.4219 | 0.045776 | 0.25848 | -0.24353 | -0.22751 | -0.079041 | -0.28091 | -0.16022 | 0.09613 | 0.09613 | 0.11902 | 0.082397 | 0.09613 | -0.032043 | 0.11902 | 0.061035 | 0.028839 | -0.11963 | -0.50522 | -0.1207 | -0.043793 | 0.045776 | 0.11902 | 0.045776 | 0.059509 | 0.059509 | 0.036621 | 0.091553 | 122.0078 | 121.8796 | 0.14191
11134.2031 | 0.045776 | 0.24567 | -0.23178 | -0.22644 | -0.076904 | -0.26703 | -0.15167 | 0.1236 | 0.086975 | 0.1236 | 0.10071 | 0.10071 | -0.045776 | 0.086975 | 0.045776 | 0.037384 | -0.13458 | -0.50201 | -0.10574 | -0.048065 | 0.068665 | 0.13733 | 0.064087 | 0.041199 | 0.027466 | 0.027466 | 0.091553 | 122.0856 | 121.8475 | 0.10529
11135.9219 | 0.061035 | 0.23819 | -0.21683 | -0.22751 | -0.099335 | -0.26382 | -0.13672 | 0.07782 | -0.018311 | 0.027466 | 0.036621 | 0.13733 | -0.032043 | 0.10986 | 0.061035 | 0.05661 | -0.12283 | -0.49774 | -0.095062 | -0.040588 | 0.045776 | 0.09613 | 0.004578 | 0.054932 | 0.032043 | 0.018311 | 0.091553 | 122.1588 | 121.843 | 0.09613
11137.7031 | 0.076294 | 0.22751 | -0.23285 | -0.25421 | -0.092926 | -0.25101 | -0.15381 | 0.054932 | -0.054932 | 0.004578 | 0.022888 | 0.13275 | -0.009155 | 0.12817 | 0.045776 | 0.050201 | -0.11322 | -0.4924 | -0.1207 | -0.046997 | -0.064087 | 0.054932 | -0.068665 | 0.091553 | 0.07782 | 0.064087 | 0.14191 | 122.1405 | 121.8521 | 0.091553
11139.4844 | 0.045776 | 0.22324 | -0.22964 | -0.25207 | -0.084381 | -0.26062 | -0.15167 | 0.082397 | -0.004578 | 0.022888 | 0.045776 | 0.15106 | -0.018311 | 0.12817 | 0.076294 | 0.059814 | -0.095062 | -0.4892 | -0.11536 | -0.03952 | -0.009155 | 0.07782 | -0.059509 | 0.068665 | 0.086975 | 0.041199 | 0.14191 | 122.1542 | 121.8521 | 0.07782
11141.2031 | 0.045776 | 0.22964 | -0.21896 | -0.2446 | -0.085449 | -0.24887 | -0.1474 | 0.10986 | 0.018311 | 0.041199 | 0.050354 | 0.14191 | 0 | 0.11902 | 0.076294 | 0.045929 | -0.10681 | -0.49667 | -0.12176 | -0.045929 | 0.013733 | 0.073242 | -0.045776 | 0.068665 | 0.086975 | 0.059509 | 0.11444 | 122.1268 | 121.8613 | 0.09613
11142.9844 | 0.045776 | 0.22537 | -0.23285 | -0.2446 | -0.099335 | -0.25207 | -0.14099 | 0.10529 | 0.004578 | 0.045776 | 0.050354 | 0.13275 | -0.036621 | 0.12817 | 0.045776 | 0.044861 | -0.11108 | -0.48065 | -0.11215 | -0.048065 | 0 | 0.082397 | -0.054932 | 0.073242 | 0.073242 | 0.054932 | 0.11902 | 122.1222 | 121.8933 | 0.068665
11144.7812 | 0.030518 | 0.24246 | -0.22537 | -0.23178 | -0.083313 | -0.27451 | -0.13886 | 0.086975 | 0.064087 | 0.091553 | 0.082397 | 0.12817 | -0.022888 | 0.10986 | 0.061035 | 0.037384 | -0.11749 | -0.48813 | -0.11536 | -0.032043 | 0.059509 | 0.1236 | 0.036621 | 0.045776 | 0.045776 | 0.022888 | 0.073242 | 122.1725 | 121.8704 | 0.091553
11146.5156 | 0.061035 | 0.23819 | -0.22964 | -0.23819 | -0.091858 | -0.27451 | -0.15488 | 0.11444 | 0.041199 | 0.10986 | 0.086975 | 0.086975 | -0.050354 | 0.10529 | 0.061035 | 0.036316 | -0.10788 | -0.49561 | -0.13031 | -0.037384 | 0.059509 | 0.13275 | 0.041199 | 0.050354 | 0.036621 | 0.022888 | 0.091553 | 122.2 | 121.8979 | 0.10071
11148.3125 | 0.076294 | 0.23819 | -0.23819 | -0.25207 | -0.076904 | -0.29053 | -0.15915 | 0.10071 | 0.082397 | 0.10986 | 0.086975 | 0.10071 | -0.027466 | 0.091553 | 0.045776 | 0.020294 | -0.10788 | -0.49774 | -0.13672 | -0.038452 | 0.07782 | 0.1831 | 0.082397 | 0.054932 | 0.045776 | 0.041199 | 0.091553 | 122.1222 | 121.9254 | 0.11444
11150.0312 | 0.045776 | 0.25314 | -0.2446 | -0.23819 | -0.088654 | -0.29587 | -0.15701 | 0.10986 | 0.068665 | 0.1236 | 0.082397 | 0.10071 | -0.027466 | 0.10529 | 0.061035 | 0.028839 | -0.12283 | -0.50308 | -0.13138 | -0.042725 | 0.068665 | 0.16479 | 0.082397 | 0.059509 | 0.050354 | 0.022888 | 0.10071 | 122.1268 | 121.9345 | 0.10071
11151.8281 | 0.045776 | 0.24353 | -0.22537 | -0.24674 | -0.086517 | -0.25955 | -0.15274 | 0.032043 | -0.045776 | -0.018311 | 0.004578 | 0.16022 | 0 | 0.13733 | 0.045776 | 0.053406 | -0.11429 | -0.50629 | -0.11536 | -0.048065 | -0.064087 | 0.022888 | -0.091553 | 0.09613 | 0.07782 | 0.068665 | 0.13733 | 122.1359 | 121.9116 | 0.1236
11153.5625 | 0.045776 | 0.25101 | -0.22751 | -0.23498 | -0.09079 | -0.29373 | -0.15915 | 0.13275 | 0.09613 | 0.13733 | 0.091553 | 0.11902 | -0.050354 | 0.09613 | 0.061035 | 0.026703 | -0.12604 | -0.49881 | -0.13031 | -0.045929 | 0.086975 | 0.16937 | 0.082397 | 0.050354 | 0.064087 | 0.027466 | 0.091553 | 122.1497 | 121.9528 | 0.10986
11155.3594 | 0.061035 | 0.25207 | -0.24139 | -0.21896 | -0.09079 | -0.26169 | -0.15595 | 0.15106 | 0.07782 | 0.12817 | 0.073242 | 0.10071 | -0.041199 | 0.086975 | 0.076294 | 0.044861 | -0.12497 | -0.49988 | -0.10147 | -0.043793 | 0.068665 | 0.11902 | 0.041199 | 0.050354 | 0.045776 | 0.045776 | 0.10986 | 122.1359 | 121.9849 | 0.13275
11157.1406 | 0.061035 | 0.23285 | -0.23178 | -0.22217 | -0.079041 | -0.25421 | -0.14847 | 0.07782 | -0.032043 | 0.013733 | 0.018311 | 0.12817 | -0.022888 | 0.11444 | 0.061035 | 0.046997 | -0.11002 | -0.49667 | -0.10895 | -0.050201 | 0.018311 | 0.054932 | -0.018311 | 0.068665 | 0.036621 | 0.041199 | 0.10529 | 122.2458 | 121.9666 | 0.086975
11158.9375 | 0.061035 | 0.23285 | -0.21149 | -0.23498 | -0.084381 | -0.24353 | -0.13886 | 0.045776 | -0.086975 | -0.032043 | 0.004578 | 0.12817 | -0.013733 | 0.14648 | 0.076294 | 0.048065 | -0.11108 | -0.47958 | -0.10361 | -0.038452 | -0.054932 | -0.022888 | -0.10529 | 0.09613 | 0.082397 | 0.054932 | 0.12817 | 122.2137 | 121.9666 | 0.09613
11160.6719 | 0.061035 | 0.25528 | -0.21896 | -0.25421 | -0.09079 | -0.28412 | -0.15488 | 0.091553 | 0.068665 | 0.091553 | 0.07782 | 0.11444 | -0.013733 | 0.11902 | 0.061035 | 0.020294 | -0.11215 | -0.50949 | -0.11963 | -0.044861 | -0.009155 | 0.11444 | -0.027466 | 0.050354 | 0.064087 | 0.073242 | 0.11444 | 122.0993 | 121.9986 | 0.12817
11162.4531 | 0.061035 | 0.2243 | -0.22003 | -0.23498 | -0.089722 | -0.24139 | -0.13245 | 0.041199 | -0.041199 | 0 | 0.009155 | 0.14191 | -0.009155 | 0.10529 | 0.045776 | 0.05127 | -0.10147 | -0.49454 | -0.10147 | -0.041656 | -0.064087 | 0.009155 | -0.10529 | 0.073242 | 0.07782 | 0.045776 | 0.14191 | 122.2183 | 121.9894 | 0.11444
11164.25 | 0.015259 | 0.22644 | -0.21896 | -0.22644 | -0.087585 | -0.25207 | -0.13672 | 0.036621 | -0.045776 | -0.013733 | 0.004578 | 0.13733 | 0.004578 | 0.13275 | 0.045776 | 0.046997 | -0.11749 | -0.48813 | -0.10254 | -0.043793 | -0.064087 | 0.018311 | -0.11444 | 0.09613 | 0.082397 | 0.050354 | 0.15564 | 122.2183 | 121.9894 | 0.09613
11166 | 0.045776 | 0.23819 | -0.23605 | -0.23071 | -0.087585 | -0.26382 | -0.1442 | 0.059509 | -0.013733 | 0.013733 | 0.045776 | 0.12817 | -0.004578 | 0.14191 | 0.045776 | 0.052338 | -0.12497 | -0.50201 | -0.11643 | -0.037384 | -0.032043 | 0.091553 | -0.036621 | 0.068665 | 0.086975 | 0.054932 | 0.12817 | 122.2641 | 121.9849 | 0.082397
11167.7812 | 0.045776 | 0.2681 | -0.23392 | -0.24887 | -0.092926 | -0.30121 | -0.15274 | 0.032043 | 0.027466 | 0.086975 | 0.050354 | 0.10986 | -0.022888 | 0.11902 | 0.045776 | 0.019226 | -0.12283 | -0.50201 | -0.12817 | -0.026703 | -0.009155 | 0.10071 | 0.022888 | 0.068665 | 0.041199 | 0.036621 | 0.10986 | 122.1954 | 122.0215 | 0.11902
11169.5781 | 0.061035 | 0.22003 | -0.22324 | -0.25635 | -0.076904 | -0.26169 | -0.15381 | 0.041199 | -0.059509 | 0 | 0.022888 | 0.14191 | -0.004578 | 0.14648 | 0.030518 | 0.053406 | -0.11215 | -0.49454 | -0.13458 | -0.045929 | -0.059509 | 0.027466 | -0.073242 | 0.082397 | 0.10529 | 0.064087 | 0.1236 | 122.2824 | 121.9849 | 0.10529
11171.2969 | 0.045776 | 0.20401 | -0.2179 | -0.24353 | -0.10254 | -0.25207 | -0.15167 | 0.036621 | -0.068665 | -0.013733 | 0.009155 | 0.13733 | -0.022888 | 0.13275 | 0.045776 | 0.058746 | -0.10254 | -0.49133 | -0.10895 | -0.044861 | -0.073242 | 0.004578 | -0.11444 | 0.091553 | 0.091553 | 0.068665 | 0.12817 | 122.2321 | 122.0078 | 0.10986
11173.0625 | 0.061035 | 0.25207 | -0.22751 | -0.22858 | -0.085449 | -0.27451 | -0.13779 | 0.11902 | 0.086975 | 0.12817 | 0.09613 | 0.09613 | -0.041199 | 0.082397 | 0.076294 | 0.036316 | -0.12176 | -0.49667 | -0.11215 | -0.049133 | 0.068665 | 0.14191 | 0.059509 | 0.036621 | 0.027466 | 0.022888 | 0.086975 | 122.2733 | 122.0261 | 0.091553
11174.8594 | 0.061035 | 0.24674 | -0.23819 | -0.25101 | -0.088654 | -0.28091 | -0.15701 | 0.10529 | 0.10071 | 0.14191 | 0.086975 | 0.09613 | -0.050354 | 0.10071 | 0.045776 | 0.028839 | -0.11536 | -0.50736 | -0.13458 | -0.046997 | 0.027466 | 0.16937 | 0.050354 | 0.045776 | 0.045776 | 0.032043 | 0.09613 | 122.1863 | 122.0398 | 0.14648
11176.5781 | 0.045776 | 0.23926 | -0.22858 | -0.25955 | -0.088654 | -0.27771 | -0.15167 | 0.086975 | 0.07782 | 0.10529 | 0.086975 | 0.11444 | -0.027466 | 0.10986 | 0.045776 | 0.032043 | -0.11002 | -0.49881 | -0.12176 | -0.049133 | -0.013733 | 0.11902 | -0.004578 | 0.073242 | 0.073242 | 0.054932 | 0.12817 | 122.1725 | 122.0673 | 0.12817
11178.3594 | 0.061035 | 0.24139 | -0.24353 | -0.24567 | -0.089722 | -0.26062 | -0.15701 | 0.013733 | -0.018311 | 0 | 0.009155 | 0.14648 | 0.009155 | 0.15564 | 0.030518 | 0.040588 | -0.12283 | -0.50629 | -0.12604 | -0.042725 | -0.059509 | 0.041199 | -0.064087 | 0.091553 | 0.09613 | 0.09613 | 0.14191 | 122.2183 | 122.0444 | 0.11444
11180.1406 | 0.076294 | 0.23926 | -0.2243 | -0.22644 | -0.10361 | -0.24994 | -0.14633 | 0.036621 | -0.07782 | -0.032043 | 0.009155 | 0.14191 | 0.004578 | 0.14191 | 0.061035 | 0.049133 | -0.11108 | -0.50842 | -0.10574 | -0.030975 | -0.036621 | 0 | -0.091553 | 0.10071 | 0.082397 | 0.086975 | 0.14191 | 122.3099 | 122.0169 | 0.10071
11181.8906 | 0.061035 | 0.23392 | -0.22644 | -0.24246 | -0.082245 | -0.25742 | -0.15488 | 0.032043 | -0.027466 | 0 | 0.032043 | 0.14191 | 0.009155 | 0.16479 | 0.030518 | 0.05127 | -0.12176 | -0.48279 | -0.12283 | -0.054474 | -0.036621 | 0.07782 | -0.045776 | 0.09613 | 0.07782 | 0.054932 | 0.11444 | 122.3328 | 122.0398 | 0.086975
11183.6719 | 0.076294 | 0.26703 | -0.22964 | -0.23498 | -0.082245 | -0.28412 | -0.14633 | 0.10529 | 0.091553 | 0.1236 | 0.07782 | 0.091553 | -0.041199 | 0.086975 | 0.061035 | 0.040588 | -0.11429 | -0.49667 | -0.12497 | -0.028839 | 0.068665 | 0.13275 | 0.045776 | 0.050354 | 0.045776 | 0.032043 | 0.10071 | 122.2275 | 122.1085 | 0.13275
11185.4062 | 0.045776 | 0.22537 | -0.22003 | -0.22858 | -0.085449 | -0.2478 | -0.1474 | 0.022888 | -0.068665 | -0.009155 | 0.009155 | 0.16479 | -0.009155 | 0.15106 | 0.076294 | 0.061951 | -0.11108 | -0.49667 | -0.10254 | -0.037384 | -0.068665 | -0.009155 | -0.10529 | 0.10071 | 0.073242 | 0.068665 | 0.13275 | 122.2961 | 122.0718 | 0.10529
11187.1875 | 0.061035 | 0.24567 | -0.23926 | -0.25421 | -0.091858 | -0.28412 | -0.15488 | 0.11902 | 0.11444 | 0.13275 | 0.091553 | 0.10071 | -0.032043 | 0.10529 | 0.061035 | 0.027771 | -0.11536 | -0.49774 | -0.13458 | -0.037384 | 0.059509 | 0.20142 | 0.068665 | 0.050354 | 0.027466 | 0.032043 | 0.091553 | 122.2549 | 122.0856 | 0.14191
11188.9844 | 0.061035 | 0.25742 | -0.22964 | -0.23498 | -0.084381 | -0.27771 | -0.14633 | 0.13275 | 0.091553 | 0.11902 | 0.082397 | 0.086975 | -0.059509 | 0.09613 | 0.061035 | 0.044861 | -0.12176 | -0.50095 | -0.12283 | -0.043793 | 0.064087 | 0.13275 | 0.032043 | 0.032043 | 0.036621 | 0.022888 | 0.091553 | 122.2366 | 122.0993 | 0.11902
11190.7656 | 0.076294 | 0.23498 | -0.22751 | -0.22964 | -0.09079 | -0.25635 | -0.13672 | 0.10071 | 0.036621 | 0.082397 | 0.064087 | 0.11902 | -0.027466 | 0.10986 | 0.061035 | 0.050201 | -0.12283 | -0.50736 | -0.10681 | -0.052338 | 0.045776 | 0.10529 | 0.022888 | 0.059509 | 0.036621 | 0.018311 | 0.09613 | 122.374 | 122.0856 | 0.10071
11192.5469 | 0.030518 | 0.22003 | -0.2211 | -0.24887 | -0.09613 | -0.24246 | -0.1442 | 0.10986 | 0.013733 | 0.027466 | 0.054932 | 0.14191 | -0.009155 | 0.1236 | 0.045776 | 0.05661 | -0.10788 | -0.48813 | -0.1207 | -0.046997 | 0.018311 | 0.10071 | -0.036621 | 0.07782 | 0.050354 | 0.059509 | 0.12817 | 122.3557 | 122.081 | 0.086975
11194.2656 | 0.076294 | 0.28091 | -0.25742 | -0.23605 | -0.085449 | -0.2948 | -0.15488 | 0.10529 | 0.068665 | 0.10529 | 0.073242 | 0.11444 | -0.032043 | 0.11444 | 0.061035 | 0.03418 | -0.12924 | -0.50201 | -0.13672 | -0.028839 | 0.050354 | 0.17395 | 0.068665 | 0.050354 | 0.050354 | 0.027466 | 0.10071 | 122.2916 | 122.1039 | 0.10986
11196.0469 | 0.045776 | 0.24674 | -0.22751 | -0.23071 | -0.09079 | -0.26596 | -0.15701 | 0.14191 | 0.064087 | 0.10986 | 0.10071 | 0.10529 | -0.045776 | 0.10071 | 0.045776 | 0.044861 | -0.11322 | -0.49667 | -0.11215 | -0.048065 | 0.064087 | 0.13733 | 0.036621 | 0.032043 | 0.022888 | 0.018311 | 0.091553 | 122.3877 | 122.0993 | 0.091553
11197.8281 | 0.061035 | 0.23071 | -0.22644 | -0.24139 | -0.086517 | -0.24246 | -0.14847 | 0.10986 | 0.013733 | 0.041199 | 0.054932 | 0.13733 | 0 | 0.12817 | 0.030518 | 0.052338 | -0.10681 | -0.49561 | -0.10681 | -0.042725 | 0.022888 | 0.073242 | -0.054932 | 0.082397 | 0.073242 | 0.054932 | 0.1236 | 122.3557 | 122.0856 | 0.082397
11199.5469 | 0.045776 | 0.24353 | -0.22751 | -0.25848 | -0.091858 | -0.26916 | -0.15808 | 0.041199 | -0.054932 | 0 | -0.009155 | 0.1236 | -0.004578 | 0.15106 | 0.045776 | 0.045929 | -0.11429 | -0.4892 | -0.13031 | -0.042725 | -0.068665 | 0.041199 | -0.07782 | 0.09613 | 0.086975 | 0.082397 | 0.14648 | 122.2961 | 122.1085 | 0.11902
11201.3281 | 0.045776 | 0.24033 | -0.23712 | -0.24994 | -0.084381 | -0.28412 | -0.13886 | 0.11444 | 0.09613 | 0.11902 | 0.091553 | 0.10529 | -0.045776 | 0.10986 | 0.076294 | 0.038452 | -0.11002 | -0.51376 | -0.12711 | -0.032043 | 0.027466 | 0.17853 | 0.036621 | 0.054932 | 0.045776 | 0.059509 | 0.10986 | 122.2504 | 122.1268 | 0.12817
11203.1094 | 0.076294 | 0.25955 | -0.23071 | -0.23712 | -0.080109 | -0.28625 | -0.15808 | 0.07782 | 0.018311 | 0.068665 | 0.064087 | 0.10986 | -0.036621 | 0.10986 | 0.091553 | 0.035248 | -0.1207 | -0.50522 | -0.13672 | -0.03418 | 0.013733 | 0.086975 | 0.004578 | 0.064087 | 0.059509 | 0.041199 | 0.10071 | 122.2916 | 122.1359 | 0.13733
11204.8281 | 0.061035 | 0.25742 | -0.23285 | -0.24353 | -0.097198 | -0.27771 | -0.16876 | 0.13275 | 0.09613 | 0.11902 | 0.082397 | 0.11902 | -0.036621 | 0.10071 | 0.061035 | 0.036316 | -0.12497 | -0.50415 | -0.13138 | -0.035248 | 0.064087 | 0.16937 | 0.07782 | 0.045776 | 0.036621 | 0.032043 | 0.10071 | 122.3328 | 122.1405 | 0.12817
11206.6094 | 0.061035 | 0.24994 | -0.23498 | -0.23285 | -0.082245 | -0.24567 | -0.14633 | 0.050354 | -0.068665 | -0.013733 | -0.004578 | 0.15106 | -0.013733 | 0.12817 | 0.045776 | 0.054474 | -0.10788 | -0.4892 | -0.10681 | -0.049133 | -0.009155 | 0.022888 | -0.068665 | 0.091553 | 0.068665 | 0.068665 | 0.13733 | 122.4243 | 122.0947 | 0.082397
11208.4062 | 0.015259 | 0.23819 | -0.2211 | -0.23819 | -0.071564 | -0.25207 | -0.14633 | 0.10071 | 0.032043 | 0.041199 | 0.064087 | 0.13733 | -0.013733 | 0.13733 | 0.076294 | 0.049133 | -0.11429 | -0.49774 | -0.10574 | -0.054474 | 0.013733 | 0.09613 | -0.036621 | 0.086975 | 0.068665 | 0.068665 | 0.12817 | 122.3969 | 122.0947 | 0.068665
11210.1875 | 0.076294 | 0.26276 | -0.23285 | -0.23605 | -0.09613 | -0.29373 | -0.16449 | 0.059509 | 0.050354 | 0.082397 | 0.054932 | 0.10986 | -0.036621 | 0.10986 | 0.061035 | 0.025635 | -0.11322 | -0.51697 | -0.13031 | -0.038452 | 0.022888 | 0.10071 | 0.009155 | 0.054932 | 0.054932 | 0.013733 | 0.10071 | 122.2916 | 122.1954 | 0.14191
11211.9219 | 0.061035 | 0.27023 | -0.23071 | -0.2446 | -0.085449 | -0.28412 | -0.1506 | 0.073242 | 0.041199 | 0.086975 | 0.041199 | 0.10071 | -0.036621 | 0.082397 | 0.061035 | 0.032043 | -0.12604 | -0.50308 | -0.11856 | -0.045929 | 0.022888 | 0.09613 | 0.013733 | 0.086975 | 0.050354 | 0.036621 | 0.10071 | 122.3145 | 122.1863 | 0.12817
11213.7031 | 0.061035 | 0.23819 | -0.2243 | -0.23285 | -0.089722 | -0.23819 | -0.14526 | 0.032043 | -0.073242 | -0.009155 | 0.013733 | 0.14191 | 0 | 0.14648 | 0.030518 | 0.069427 | -0.11215 | -0.48492 | -0.10468 | -0.05127 | -0.036621 | -0.009155 | -0.10529 | 0.10071 | 0.068665 | 0.068665 | 0.14191 | 122.4243 | 122.1588 | 0.10071
11215.5 | 0.061035 | 0.24246 | -0.23178 | -0.22003 | -0.1004 | -0.25848 | -0.13886 | 0.12817 | 0.082397 | 0.10529 | 0.082397 | 0.1236 | -0.036621 | 0.10529 | 0.045776 | 0.046997 | -0.11429 | -0.50415 | -0.10361 | -0.041656 | 0.086975 | 0.12817 | 0.022888 | 0.041199 | 0.018311 | 0.045776 | 0.10071 | 122.4472 | 122.1268 | 0.10529
11217.2969 | 0.076294 | 0.23819 | -0.2243 | -0.24353 | -0.10361 | -0.25314 | -0.13672 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.17395 | 0.004578 | 0.13275 | 0.061035 | 0.058746 | -0.10361 | -0.50308 | -0.11429 | -0.036316 | -0.036621 | 0.018311 | -0.068665 | 0.09613 | 0.073242 | 0.064087 | 0.12817 | 122.4701 | 122.1451 | 0.086975
11219.0938 | 0.030518 | 0.23071 | -0.2243 | -0.24139 | -0.076904 | -0.25421 | -0.14313 | 0.018311 | -0.07782 | -0.018311 | 0.009155 | 0.14648 | -0.009155 | 0.1236 | 0.076294 | 0.059814 | -0.11856 | -0.48492 | -0.097198 | -0.042725 | -0.064087 | -0.009155 | -0.086975 | 0.082397 | 0.086975 | 0.073242 | 0.13275 | 122.4472 | 122.1359 | 0.091553
11220.8906 | 0.045776 | 0.25742 | -0.23819 | -0.25955 | -0.097198 | -0.29159 | -0.1506 | 0.036621 | 0.032043 | 0.086975 | 0.054932 | 0.11902 | -0.036621 | 0.10071 | 0.045776 | 0.028839 | -0.11322 | -0.50308 | -0.14313 | -0.040588 | 0.018311 | 0.1236 | 0.032043 | 0.064087 | 0.054932 | 0.041199 | 0.11444 | 122.3557 | 122.1725 | 0.12817
11222.6719 | 0.076294 | 0.22964 | -0.21469 | -0.24567 | -0.093994 | -0.23712 | -0.14099 | 0.09613 | -0.013733 | 0.022888 | 0.022888 | 0.1236 | -0.013733 | 0.13733 | 0.061035 | 0.057678 | -0.10895 | -0.47638 | -0.11215 | -0.060883 | -0.032043 | 0.045776 | -0.082397 | 0.068665 | 0.073242 | 0.054932 | 0.11902 | 122.406 | 122.1588 | 0.091553
11224.4062 | 0.061035 | 0.24353 | -0.24674 | -0.24887 | -0.074768 | -0.26382 | -0.15167 | 0.022888 | -0.054932 | 0 | 0.009155 | 0.14648 | 0 | 0.11902 | 0.061035 | 0.043793 | -0.11108 | -0.50522 | -0.12176 | -0.026703 | -0.064087 | 0.032043 | -0.07782 | 0.09613 | 0.091553 | 0.073242 | 0.13275 | 122.406 | 122.1725 | 0.11444
11226.2031 | 0.061035 | 0.22324 | -0.23819 | -0.25635 | -0.086517 | -0.26382 | -0.1474 | 0.027466 | -0.050354 | -0.009155 | 0.009155 | 0.14648 | -0.004578 | 0.14648 | 0.076294 | 0.046997 | -0.10361 | -0.48492 | -0.12604 | -0.042725 | -0.059509 | 0.032043 | -0.073242 | 0.09613 | 0.091553 | 0.059509 | 0.14191 | 122.4564 | 122.1771 | 0.10071
11227.9219 | 0.045776 | 0.23712 | -0.23392 | -0.23285 | -0.079041 | -0.26062 | -0.14313 | 0.11902 | 0.045776 | 0.10071 | 0.09613 | 0.11444 | -0.050354 | 0.091553 | 0.076294 | 0.049133 | -0.11643 | -0.48492 | -0.1239 | -0.037384 | 0.045776 | 0.13733 | 0.022888 | 0.041199 | 0.032043 | 0.022888 | 0.07782 | 122.4838 | 122.1954 | 0.09613
11229.7031 | 0.045776 | 0.23392 | -0.22003 | -0.24353 | -0.087585 | -0.24994 | -0.14847 | 0.022888 | -0.07782 | -0.027466 | 0 | 0.13733 | -0.009155 | 0.13275 | 0.061035 | 0.066223 | -0.10468 | -0.49347 | -0.10574 | -0.052338 | -0.091553 | -0.009155 | -0.12817 | 0.073242 | 0.07782 | 0.054932 | 0.13275 | 122.4335 | 122.1817 | 0.10529
11231.5156 | 0.061035 | 0.22537 | -0.22644 | -0.24353 | -0.09613 | -0.26169 | -0.15381 | 0.059509 | -0.004578 | 0.032043 | 0.064087 | 0.14648 | -0.013733 | 0.1236 | 0.061035 | 0.061951 | -0.1004 | -0.48813 | -0.11215 | -0.038452 | -0.018311 | 0.086975 | -0.041199 | 0.091553 | 0.068665 | 0.059509 | 0.13275 | 122.4792 | 122.1588 | 0.07782
11233.2344 | 0.045776 | 0.22324 | -0.2243 | -0.24033 | -0.077972 | -0.25635 | -0.13992 | 0.050354 | -0.013733 | 0.027466 | 0.050354 | 0.12817 | 0.004578 | 0.15106 | 0.061035 | 0.059814 | -0.095062 | -0.48813 | -0.11215 | -0.03418 | -0.027466 | 0.07782 | -0.032043 | 0.082397 | 0.064087 | 0.054932 | 0.12817 | 122.493 | 122.1634 | 0.082397
11235.0156 | 0.061035 | 0.23712 | -0.23285 | -0.25635 | -0.081177 | -0.28198 | -0.15274 | 0.050354 | 0.018311 | 0.045776 | 0.045776 | 0.11902 | 0 | 0.13275 | 0.045776 | 0.05661 | -0.10574 | -0.50095 | -0.13245 | -0.032043 | -0.050354 | 0.054932 | -0.059509 | 0.091553 | 0.07782 | 0.064087 | 0.13733 | 122.3648 | 122.2137 | 0.11444
11236.8125 | 0.061035 | 0.24994 | -0.23712 | -0.24674 | -0.093994 | -0.29159 | -0.16235 | 0.11444 | 0.10529 | 0.14648 | 0.10071 | 0.11444 | -0.041199 | 0.091553 | 0.045776 | 0.049133 | -0.084381 | -0.50629 | -0.13458 | -0.038452 | 0.068665 | 0.20599 | 0.091553 | 0.050354 | 0.068665 | 0.013733 | 0.10986 | 122.406 | 122.2275 | 0.13733
11238.5312 | 0.061035 | 0.24353 | -0.22217 | -0.24139 | -0.093994 | -0.25207 | -0.14954 | 0.045776 | -0.050354 | 0.004578 | 0 | 0.15564 | -0.009155 | 0.11902 | 0.030518 | 0.064087 | -0.089722 | -0.50736 | -0.10681 | -0.038452 | -0.022888 | 0.018311 | -0.068665 | 0.086975 | 0.064087 | 0.068665 | 0.11902 | 122.493 | 122.1817 | 0.10071
11240.3281 | 0.061035 | 0.24567 | -0.23605 | -0.24994 | -0.086517 | -0.28839 | -0.14954 | 0.10071 | 0.10529 | 0.13733 | 0.091553 | 0.09613 | -0.045776 | 0.10986 | 0.076294 | 0.050201 | -0.09079 | -0.51376 | -0.12711 | -0.035248 | 0.027466 | 0.16479 | 0.041199 | 0.068665 | 0.036621 | 0.041199 | 0.10071 | 122.374 | 122.2275 | 0.12817
11242.125 | 0.061035 | 0.24994 | -0.23392 | -0.23926 | -0.086517 | -0.2713 | -0.14954 | 0.13275 | 0.082397 | 0.11902 | 0.086975 | 0.091553 | -0.050354 | 0.086975 | 0.045776 | 0.035248 | -0.12711 | -0.49774 | -0.12497 | -0.035248 | 0.073242 | 0.13275 | 0.036621 | 0.073242 | 0.054932 | 0.009155 | 0.07782 | 122.3969 | 122.2549 | 0.13275
11243.8438 | 0.030518 | 0.23178 | -0.23498 | -0.24033 | -0.086517 | -0.25101 | -0.1442 | 0.054932 | -0.032043 | -0.004578 | 0.027466 | 0.16479 | -0.004578 | 0.14648 | 0.061035 | 0.05661 | -0.1239 | -0.4924 | -0.11749 | -0.046997 | -0.050354 | 0.064087 | -0.064087 | 0.09613 | 0.073242 | 0.064087 | 0.11444 | 122.493 | 122.1909 | 0.086975
11245.625 | 0.030518 | 0.26703 | -0.24567 | -0.23498 | -0.093994 | -0.27771 | -0.14313 | 0.091553 | 0.064087 | 0.09613 | 0.059509 | 0.10529 | -0.036621 | 0.10529 | 0.076294 | 0.038452 | -0.12497 | -0.49881 | -0.12283 | -0.032043 | 0.036621 | 0.09613 | 0.013733 | 0.041199 | 0.050354 | 0.050354 | 0.10071 | 122.3831 | 122.2366 | 0.14648
11247.4219 | 0.045776 | 0.22537 | -0.23712 | -0.2446 | -0.080109 | -0.25742 | -0.14633 | 0.036621 | -0.045776 | -0.013733 | 0.009155 | 0.15564 | 0.013733 | 0.14191 | 0.061035 | 0.044861 | -0.11215 | -0.49667 | -0.12711 | -0.046997 | -0.054932 | 0.036621 | -0.086975 | 0.10071 | 0.082397 | 0.091553 | 0.14191 | 122.4564 | 122.2 | 0.091553
11249.2031 | 0.045776 | 0.24674 | -0.21683 | -0.22964 | -0.077972 | -0.25848 | -0.13992 | 0.09613 | 0.018311 | 0.082397 | 0.073242 | 0.12817 | -0.054932 | 0.10071 | 0.045776 | 0.050201 | -0.11002 | -0.49133 | -0.11643 | -0.040588 | 0.064087 | 0.11902 | 0.022888 | 0.050354 | 0.045776 | 0.041199 | 0.07782 | 122.525 | 122.2229 | 0.091553
11251 | 0.061035 | 0.22751 | -0.2243 | -0.22644 | -0.077972 | -0.25207 | -0.13779 | 0.009155 | -0.068665 | -0.022888 | 0 | 0.14648 | 0 | 0.13733 | 0.061035 | 0.052338 | -0.10788 | -0.49881 | -0.10468 | -0.035248 | -0.064087 | -0.036621 | -0.1236 | 0.082397 | 0.086975 | 0.054932 | 0.13733 | 122.4838 | 122.2229 | 0.086975
11252.7344 | 0.076294 | 0.22644 | -0.22858 | -0.22644 | -0.092926 | -0.25742 | -0.13992 | 0.022888 | -0.059509 | -0.013733 | 0 | 0.14191 | 0 | 0.1236 | 0.076294 | 0.052338 | -0.10361 | -0.49027 | -0.11108 | -0.040588 | -0.036621 | -0.009155 | -0.082397 | 0.09613 | 0.059509 | 0.050354 | 0.1236 | 122.525 | 122.2183 | 0.091553
11254.4844 | 0.076294 | 0.2446 | -0.23926 | -0.22537 | -0.083313 | -0.28091 | -0.13779 | 0.12817 | 0.07782 | 0.11902 | 0.09613 | 0.091553 | -0.059509 | 0.09613 | 0.061035 | 0.042725 | -0.11536 | -0.51056 | -0.11643 | -0.035248 | 0.073242 | 0.14648 | 0.054932 | 0.036621 | 0.050354 | 0.022888 | 0.082397 | 122.5113 | 122.2641 | 0.10071
11256.2812 | 0.045776 | 0.22537 | -0.22003 | -0.24139 | -0.082245 | -0.25635 | -0.14954 | 0.032043 | -0.068665 | -0.004578 | 0.004578 | 0.13733 | 0 | 0.13733 | 0.076294 | 0.058746 | -0.10788 | -0.49027 | -0.11108 | -0.044861 | -0.091553 | -0.013733 | -0.10071 | 0.082397 | 0.086975 | 0.050354 | 0.13733 | 122.4838 | 122.2595 | 0.09613
11258.0156 | 0.061035 | 0.24246 | -0.23285 | -0.24567 | -0.070496 | -0.26169 | -0.14847 | 0.027466 | -0.045776 | -0.022888 | 0.022888 | 0.15106 | 0.009155 | 0.15106 | 0.076294 | 0.042725 | -0.10895 | -0.48813 | -0.12176 | -0.040588 | -0.073242 | 0.054932 | -0.068665 | 0.10986 | 0.09613 | 0.091553 | 0.13275 | 122.525 | 122.2275 | 0.091553
11259.75 | 0.030518 | 0.23712 | -0.22751 | -0.25314 | -0.081177 | -0.27771 | -0.1442 | 0.027466 | -0.054932 | -0.009155 | -0.009155 | 0.14191 | -0.004578 | 0.14191 | 0.045776 | 0.045929 | -0.10681 | -0.49988 | -0.13031 | -0.036316 | -0.068665 | 0.054932 | -0.091553 | 0.10529 | 0.10529 | 0.073242 | 0.12817 | 122.438 | 122.287 | 0.11444
11261.5469 | 0.030518 | 0.24033 | -0.23071 | -0.21896 | -0.092926 | -0.26382 | -0.13458 | 0.059509 | -0.036621 | 0.018311 | 0.009155 | 0.14648 | -0.027466 | 0.11444 | 0.030518 | 0.044861 | -0.10895 | -0.50949 | -0.11215 | -0.044861 | 0.004578 | 0.050354 | -0.009155 | 0.073242 | 0.059509 | 0.018311 | 0.1236 | 122.5937 | 122.2595 | 0.091553
11263.3281 | 0.061035 | 0.24246 | -0.22858 | -0.25421 | -0.099335 | -0.28091 | -0.15595 | 0.10529 | 0.07782 | 0.11902 | 0.10071 | 0.10071 | -0.041199 | 0.10071 | 0.061035 | 0.032043 | -0.11749 | -0.49454 | -0.13351 | -0.035248 | 0 | 0.15106 | 0.013733 | 0.050354 | 0.059509 | 0.036621 | 0.12817 | 122.4152 | 122.2504 | 0.11902
11265.0625 | 0.045776 | 0.24567 | -0.24033 | -0.24674 | -0.087585 | -0.29053 | -0.1506 | 0.12817 | 0.10071 | 0.12817 | 0.086975 | 0.10071 | -0.045776 | 0.082397 | 0.061035 | 0.025635 | -0.11002 | -0.50201 | -0.12924 | -0.03952 | 0.082397 | 0.1831 | 0.09613 | 0.054932 | 0.054932 | 0.036621 | 0.10529 | 122.4976 | 122.2961 | 0.10986
11266.8594 | 0.076294 | 0.23392 | -0.22751 | -0.22537 | -0.088654 | -0.24887 | -0.15167 | 0.054932 | -0.054932 | -0.018311 | 0.009155 | 0.14648 | -0.013733 | 0.13733 | 0.076294 | 0.05661 | -0.11108 | -0.50201 | -0.11002 | -0.049133 | -0.032043 | 0.009155 | -0.07782 | 0.091553 | 0.082397 | 0.050354 | 0.12817 | 122.5662 | 122.2687 | 0.082397
11268.6406 | 0.061035 | 0.22324 | -0.23819 | -0.23712 | -0.095062 | -0.26276 | -0.14847 | 0.022888 | -0.036621 | -0.009155 | 0.009155 | 0.12817 | 0.018311 | 0.14648 | 0.061035 | 0.048065 | -0.10574 | -0.4892 | -0.11643 | -0.046997 | -0.073242 | 0.032043 | -0.091553 | 0.09613 | 0.09613 | 0.07782 | 0.14648 | 122.4884 | 122.2733 | 0.11902
11270.4219 | 0.061035 | 0.24887 | -0.23285 | -0.22644 | -0.095062 | -0.27237 | -0.15488 | 0.032043 | -0.041199 | -0.009155 | 0.009155 | 0.15564 | 0.013733 | 0.16022 | 0.030518 | 0.041656 | -0.12497 | -0.50415 | -0.11749 | -0.037384 | -0.059509 | 0.036621 | -0.07782 | 0.086975 | 0.082397 | 0.073242 | 0.14191 | 122.4792 | 122.3099 | 0.11444
11272.1562 | 0.061035 | 0.24033 | -0.2179 | -0.23926 | -0.095062 | -0.25207 | -0.1506 | 0.045776 | -0.082397 | -0.041199 | 0.013733 | 0.14648 | -0.009155 | 0.14648 | 0.045776 | 0.057678 | -0.10895 | -0.48386 | -0.1207 | -0.043793 | -0.045776 | 0.009155 | -0.073242 | 0.082397 | 0.086975 | 0.059509 | 0.12817 | 122.58 | 122.2778 | 0.07782
11273.9531 | 0.061035 | 0.25101 | -0.22858 | -0.24353 | -0.087585 | -0.28412 | -0.13458 | 0.10529 | 0.09613 | 0.1236 | 0.082397 | 0.10529 | -0.022888 | 0.11902 | 0.061035 | 0.043793 | -0.10574 | -0.50201 | -0.13245 | -0.036316 | 0.009155 | 0.13733 | 0.022888 | 0.050354 | 0.050354 | 0.041199 | 0.10529 | 122.4289 | 122.3236 | 0.1236
11275.6719 | 0.061035 | 0.25848 | -0.23498 | -0.22964 | -0.10574 | -0.27771 | -0.15701 | 0.059509 | 0.041199 | 0.082397 | 0.059509 | 0.10986 | -0.036621 | 0.10071 | 0.045776 | 0.027771 | -0.11215 | -0.50842 | -0.12924 | -0.036316 | -0.004578 | 0.091553 | 0.009155 | 0.050354 | 0.050354 | 0.054932 | 0.1236 | 122.4564 | 122.3282 | 0.10986
11277.4531 | 0.061035 | 0.24994 | -0.23926 | -0.22644 | -0.077972 | -0.26276 | -0.15167 | 0.15106 | 0.059509 | 0.13275 | 0.086975 | 0.10529 | -0.041199 | 0.10986 | 0.061035 | 0.037384 | -0.11749 | -0.50095 | -0.11749 | -0.045929 | 0.068665 | 0.16022 | 0.045776 | 0.045776 | 0.045776 | 0.022888 | 0.07782 | 122.5342 | 122.2961 | 0.10986
11279.1719 | 0.061035 | 0.24994 | -0.24139 | -0.2478 | -0.084381 | -0.29053 | -0.15381 | 0.14191 | 0.10529 | 0.15564 | 0.10529 | 0.086975 | -0.027466 | 0.09613 | 0.076294 | 0.028839 | -0.10895 | -0.49133 | -0.13565 | -0.045929 | 0.054932 | 0.17853 | 0.064087 | 0.041199 | 0.054932 | 0.041199 | 0.09613 | 122.5021 | 122.3053 | 0.13275
11280.9688 | 0.030518 | 0.24567 | -0.24033 | -0.25955 | -0.1004 | -0.27985 | -0.16342 | 0.14648 | 0.11902 | 0.14191 | 0.10986 | 0.082397 | -0.032043 | 0.10529 | 0.061035 | 0.030975 | -0.11429 | -0.50522 | -0.12924 | -0.048065 | 0.068665 | 0.19684 | 0.064087 | 0.064087 | 0.032043 | 0.036621 | 0.10529 | 122.4747 | 122.3419 | 0.11902
11282.7656 | 0.045776 | 0.25314 | -0.24139 | -0.24033 | -0.088654 | -0.26916 | -0.16235 | 0.068665 | 0.022888 | 0.082397 | 0.073242 | 0.11444 | -0.041199 | 0.10529 | 0.061035 | 0.044861 | -0.099335 | -0.50949 | -0.11429 | -0.03952 | 0.004578 | 0.07782 | 0.022888 | 0.059509 | 0.045776 | 0.032043 | 0.10529 | 122.4884 | 122.3373 | 0.13733
11284.5781 | 0.045776 | 0.22217 | -0.22964 | -0.23285 | -0.082245 | -0.23605 | -0.13992 | 0.045776 | -0.064087 | -0.013733 | 0.009155 | 0.15564 | 0.009155 | 0.14648 | 0.076294 | 0.074768 | -0.089722 | -0.49988 | -0.1004 | -0.05661 | -0.059509 | -0.013733 | -0.11902 | 0.086975 | 0.068665 | 0.054932 | 0.12817 | 122.5525 | 122.287 | 0.10529
11286.2969 | 0.045776 | 0.26703 | -0.26062 | -0.23819 | -0.085449 | -0.28946 | -0.15167 | 0.059509 | 0.045776 | 0.07782 | 0.064087 | 0.12817 | -0.013733 | 0.11444 | 0.045776 | 0.030975 | -0.12497 | -0.51163 | -0.11322 | -0.033112 | 0.022888 | 0.1236 | 0.032043 | 0.054932 | 0.059509 | 0.027466 | 0.10986 | 122.5479 | 122.3145 | 0.12817
11288.0938 | 0.045776 | 0.23605 | -0.22751 | -0.24139 | -0.088654 | -0.25101 | -0.14313 | 0.09613 | 0.004578 | 0.045776 | 0.041199 | 0.10986 | -0.022888 | 0.11902 | 0.045776 | 0.046997 | -0.092926 | -0.50095 | -0.11322 | -0.045929 | 0.050354 | 0.11444 | -0.004578 | 0.045776 | 0.054932 | 0.022888 | 0.10986 | 122.6074 | 122.3145 | 0.086975
11289.8906 | 0.076294 | 0.26169 | -0.24887 | -0.24353 | -0.099335 | -0.28519 | -0.15808 | 0.13275 | 0.13733 | 0.14648 | 0.086975 | 0.10071 | -0.032043 | 0.082397 | 0.061035 | 0.025635 | -0.10468 | -0.50736 | -0.12283 | -0.036316 | 0.059509 | 0.19684 | 0.050354 | 0.045776 | 0.032043 | 0.036621 | 0.091553 | 122.5067 | 122.3282 | 0.1236
11291.6094 | 0.045776 | 0.21255 | -0.21683 | -0.25314 | -0.086517 | -0.25635 | -0.15167 | 0.059509 | -0.059509 | -0.013733 | 0.018311 | 0.13733 | -0.009155 | 0.13733 | 0.061035 | 0.068359 | -0.10254 | -0.49027 | -0.11963 | -0.046997 | -0.032043 | 0.050354 | -0.064087 | 0.09613 | 0.10071 | 0.064087 | 0.1236 | 122.5891 | 122.3053 | 0.10071
11293.4062 | 0.030518 | 0.24567 | -0.22751 | -0.23712 | -0.09079 | -0.26703 | -0.14954 | 0.041199 | -0.009155 | 0.022888 | 0.004578 | 0.13275 | -0.013733 | 0.13733 | 0.076294 | 0.052338 | -0.11856 | -0.49454 | -0.13672 | -0.030975 | -0.045776 | 0.041199 | -0.068665 | 0.10529 | 0.082397 | 0.064087 | 0.13733 | 122.5021 | 122.3877 | 0.11902
11295.1875 | 0.076294 | 0.23712 | -0.23178 | -0.2478 | -0.084381 | -0.26276 | -0.1474 | 0.059509 | -0.050354 | -0.009155 | 0.004578 | 0.15564 | 0.013733 | 0.13275 | 0.045776 | 0.052338 | -0.10681 | -0.49027 | -0.11856 | -0.044861 | -0.054932 | 0.045776 | -0.086975 | 0.10986 | 0.086975 | 0.059509 | 0.15106 | 122.5845 | 122.3373 | 0.09613
11296.9375 | 0.061035 | 0.24567 | -0.22644 | -0.22858 | -0.081177 | -0.25101 | -0.13779 | 0.064087 | -0.07782 | -0.036621 | 0.018311 | 0.15106 | -0.013733 | 0.13733 | 0.061035 | 0.054474 | -0.10254 | -0.48279 | -0.11643 | -0.037384 | -0.041199 | 0.013733 | -0.091553 | 0.086975 | 0.073242 | 0.050354 | 0.12817 | 122.6166 | 122.3282 | 0.10071
11298.7188 | 0.061035 | 0.23605 | -0.24139 | -0.25101 | -0.09613 | -0.27664 | -0.14847 | 0.032043 | -0.009155 | 0.018311 | 0.013733 | 0.13733 | 0.009155 | 0.15106 | 0.030518 | 0.05127 | -0.11963 | -0.50095 | -0.12817 | -0.045929 | -0.045776 | 0.050354 | -0.07782 | 0.091553 | 0.10071 | 0.091553 | 0.15106 | 122.493 | 122.3877 | 0.10986
11300.4531 | 0.061035 | 0.23498 | -0.23819 | -0.23392 | -0.086517 | -0.24994 | -0.14526 | 0.054932 | -0.059509 | -0.018311 | 0.004578 | 0.13275 | 0 | 0.13275 | 0.091553 | 0.066223 | -0.10895 | -0.48386 | -0.10788 | -0.036316 | -0.013733 | 0.013733 | -0.059509 | 0.07782 | 0.068665 | 0.073242 | 0.1236 | 122.644 | 122.3145 | 0.091553
11302.2344 | 0.061035 | 0.22537 | -0.21896 | -0.23285 | -0.088654 | -0.24033 | -0.13992 | 0.054932 | -0.086975 | -0.022888 | 0.022888 | 0.15106 | -0.013733 | 0.13733 | 0.045776 | 0.053406 | -0.11643 | -0.49347 | -0.10468 | -0.030975 | -0.059509 | 0 | -0.10071 | 0.086975 | 0.07782 | 0.07782 | 0.14648 | 122.6166 | 122.3511 | 0.091553
11303.9531 | 0.076294 | 0.23819 | -0.23392 | -0.22537 | -0.087585 | -0.27023 | -0.13351 | 0.13275 | 0.059509 | 0.12817 | 0.10986 | 0.07782 | -0.036621 | 0.11444 | 0.061035 | 0.046997 | -0.11108 | -0.49774 | -0.11643 | -0.03952 | 0.068665 | 0.15564 | 0.054932 | 0.036621 | 0.041199 | 0.027466 | 0.086975 | 122.612 | 122.3328 | 0.09613
11305.7344 | 0.076294 | 0.22537 | -0.22003 | -0.24353 | -0.082245 | -0.25528 | -0.1442 | 0.059509 | -0.068665 | -0.004578 | 0.018311 | 0.14648 | -0.009155 | 0.13733 | 0.030518 | 0.059814 | -0.10895 | -0.4892 | -0.11215 | -0.03952 | -0.068665 | -0.004578 | -0.09613 | 0.091553 | 0.082397 | 0.068665 | 0.14191 | 122.6074 | 122.3373 | 0.10071
11307.5469 | 0.045776 | 0.25314 | -0.23605 | -0.26276 | -0.092926 | -0.29373 | -0.13565 | 0.12817 | 0.10986 | 0.12817 | 0.10529 | 0.10529 | -0.027466 | 0.11444 | 0.061035 | 0.03418 | -0.10574 | -0.50949 | -0.14099 | -0.045929 | 0.054932 | 0.20142 | 0.064087 | 0.054932 | 0.045776 | 0.032043 | 0.10529 | 122.5388 | 122.3557 | 0.10986
11309.2656 | 0.030518 | 0.22751 | -0.21576 | -0.24246 | -0.082245 | -0.25635 | -0.14099 | 0.036621 | -0.054932 | -0.009155 | 0.032043 | 0.15106 | 0 | 0.13275 | 0.045776 | 0.064087 | -0.11856 | -0.50095 | -0.11856 | -0.052338 | -0.054932 | 0.059509 | -0.059509 | 0.086975 | 0.091553 | 0.064087 | 0.13275 | 122.6303 | 122.3465 | 0.091553
11311.0469 | 0.061035 | 0.22964 | -0.23712 | -0.2478 | -0.10254 | -0.2681 | -0.14633 | 0.036621 | -0.041199 | 0.009155 | 0.041199 | 0.14191 | 0 | 0.12817 | 0.030518 | 0.055542 | -0.11002 | -0.50522 | -0.11963 | -0.055542 | -0.050354 | 0.059509 | -0.054932 | 0.064087 | 0.082397 | 0.059509 | 0.11902 | 122.644 | 122.3373 | 0.091553
11312.7812 | 0.030518 | 0.25207 | -0.22324 | -0.23498 | -0.088654 | -0.25635 | -0.14099 | 0.054932 | -0.059509 | -0.013733 | 0.009155 | 0.15106 | -0.009155 | 0.13733 | 0.061035 | 0.059814 | -0.11536 | -0.49667 | -0.11536 | -0.042725 | -0.022888 | 0.027466 | -0.050354 | 0.068665 | 0.07782 | 0.027466 | 0.11902 | 122.6669 | 122.3465 | 0.073242
11314.5938 | 0.076294 | 0.23071 | -0.22964 | -0.25955 | -0.081177 | -0.28412 | -0.1506 | 0.041199 | -0.004578 | 0.027466 | 0.027466 | 0.14191 | 0 | 0.16479 | 0.061035 | 0.05127 | -0.10681 | -0.49988 | -0.13779 | -0.043793 | -0.059509 | 0.054932 | -0.059509 | 0.091553 | 0.091553 | 0.073242 | 0.14191 | 122.5204 | 122.4014 | 0.13275
11316.3906 | 0.076294 | 0.21042 | -0.22751 | -0.22858 | -0.092926 | -0.24033 | -0.15167 | 0.032043 | -0.09613 | -0.022888 | 0.018311 | 0.14648 | -0.004578 | 0.11444 | 0.061035 | 0.05661 | -0.10361 | -0.50201 | -0.11429 | -0.045929 | -0.050354 | -0.004578 | -0.091553 | 0.091553 | 0.073242 | 0.059509 | 0.13733 | 122.644 | 122.3877 | 0.082397
11318.125 | 0.061035 | 0.21896 | -0.22537 | -0.22644 | -0.093994 | -0.25848 | -0.14206 | 0.10071 | 0.018311 | 0.050354 | 0.032043 | 0.14191 | -0.027466 | 0.1236 | 0.061035 | 0.066223 | -0.092926 | -0.49133 | -0.1004 | -0.045929 | -0.009155 | 0.086975 | -0.041199 | 0.073242 | 0.086975 | 0.064087 | 0.11444 | 122.6257 | 122.3648 | 0.07782
11319.9219 | 0.030518 | 0.2243 | -0.2211 | -0.25421 | -0.098267 | -0.26596 | -0.15167 | 0.027466 | -0.054932 | -0.013733 | 0.036621 | 0.16022 | 0 | 0.14191 | 0.061035 | 0.05127 | -0.095062 | -0.49027 | -0.12924 | -0.035248 | -0.073242 | 0.050354 | -0.064087 | 0.091553 | 0.07782 | 0.07782 | 0.12817 | 122.6349 | 122.3373 | 0.11444
11321.6562 | 0.061035 | 0.22644 | -0.22964 | -0.23392 | -0.092926 | -0.25528 | -0.13565 | 0.027466 | -0.09613 | -0.027466 | -0.004578 | 0.14191 | -0.004578 | 0.12817 | 0.091553 | 0.05127 | -0.10895 | -0.47852 | -0.10681 | -0.040588 | -0.050354 | 0 | -0.09613 | 0.073242 | 0.07782 | 0.054932 | 0.15106 | 122.6578 | 122.3969 | 0.086975
11323.4531 | 0.076294 | 0.22964 | -0.22858 | -0.2243 | -0.088654 | -0.25742 | -0.14313 | 0.041199 | -0.082397 | -0.027466 | 0.009155 | 0.15564 | -0.009155 | 0.12817 | 0.061035 | 0.049133 | -0.10574 | -0.49133 | -0.11108 | -0.043793 | -0.041199 | 0.009155 | -0.064087 | 0.073242 | 0.073242 | 0.068665 | 0.13733 | 122.6578 | 122.3969 | 0.086975
11325.1719 | 0.045776 | 0.22537 | -0.23178 | -0.24139 | -0.082245 | -0.26062 | -0.14847 | 0.004578 | -0.10071 | -0.027466 | 0.013733 | 0.13733 | 0 | 0.13275 | 0.061035 | 0.05661 | -0.10681 | -0.4924 | -0.11108 | -0.033112 | -0.07782 | -0.004578 | -0.10071 | 0.09613 | 0.073242 | 0.059509 | 0.13275 | 122.6486 | 122.3923 | 0.082397
11326.9688 | 0.061035 | 0.25742 | -0.22964 | -0.24887 | -0.095062 | -0.28732 | -0.15167 | 0.10071 | 0.068665 | 0.10986 | 0.082397 | 0.091553 | -0.036621 | 0.09613 | 0.045776 | 0.036316 | -0.10788 | -0.49774 | -0.13672 | -0.028839 | 0.022888 | 0.10071 | 0.036621 | 0.059509 | 0.041199 | 0.041199 | 0.11444 | 122.5296 | 122.4289 | 0.12817
11328.7656 | 0.061035 | 0.23498 | -0.23498 | -0.23178 | -0.093994 | -0.25635 | -0.14633 | 0.032043 | -0.050354 | -0.022888 | 0.018311 | 0.15564 | -0.009155 | 0.12817 | 0.045776 | 0.048065 | -0.098267 | -0.48706 | -0.11429 | -0.036316 | -0.045776 | 0.004578 | -0.086975 | 0.09613 | 0.073242 | 0.054932 | 0.1236 | 122.6852 | 122.4014 | 0.082397
11330.5 | 0.045776 | 0.23392 | -0.2211 | -0.23498 | -0.067291 | -0.26382 | -0.16663 | 0.068665 | -0.045776 | 0 | 0.036621 | 0.18768 | -0.022888 | 0.11902 | 0.076294 | 1.1354 | 1.1247 | -0.74127 | -0.10681 | 0.19226 | 0.10071 | 0.20599 | 0.10986 | 0.35706 | 0.32959 | -0.11444 | -0.054932 | 122.5204 | 121.9482 | 0.36163
11332.2812 | 0.061035 | -0.028839 | 0.02243 | -0.24567 | -0.91644 | -0.26703 | 0.62378 | 0.28381 | 0.25177 | 0.32959 | 0.24261 | 0.27008 | -0.16022 | -0.018311 | 0.045776 | 34.9989 | 34.9989 | -5.41 | -0.86838 | 5.5692 | 0.20599 | 18.1503 | 14.5477 | 23.0804 | 22.9156 | -8.963 | -8.8486 | 119.7144 | 91.1819 | 28.3218
11334.0781 | 0.076294 | 0.20721 | -0.21149 | -0.23819 | -0.20935 | -0.25421 | -0.10468 | 0.086975 | 0.004578 | 0.045776 | 0.054932 | 0.14648 | -0.009155 | 0.13733 | 0.061035 | 0.84167 | 1.3127 | -0.56717 | -0.11429 | 0.027771 | -0.009155 | 0.16937 | 0.027466 | 0.21973 | 0.21057 | -0.045776 | 0.027466 | 122.1451 | 121.6003 | 0.24261
11335.7969 | 0.045776 | 0.2478 | -0.22751 | -0.2446 | -0.22324 | -0.30228 | -0.086517 | 0.09613 | 0.073242 | 0.10986 | 0.073242 | 0.11902 | -0.032043 | 0.10986 | 0.076294 | 1.772 | 3.0099 | -0.65475 | -0.13138 | 0.12497 | 0.059509 | 0.35706 | 0.25177 | 0.35706 | 0.36163 | -0.21515 | -0.12817 | 122.0673 | 121.3898 | 0.50354
11337.5938 | 0.045776 | 0.23285 | -0.22324 | -0.24567 | -0.18051 | -0.27344 | -0.11749 | 0.027466 | -0.054932 | -0.018311 | 0 | 0.16022 | 0.013733 | 0.15106 | 0.076294 | 0.084381 | -0.027771 | -0.50736 | -0.12497 | -0.03418 | -0.082397 | 0.027466 | -0.082397 | 0.091553 | 0.082397 | 0.073242 | 0.13275 | 122.2137 | 122.0123 | 0.1236
11339.3906 | 0.045776 | 0.24246 | -0.23071 | -0.26169 | -0.1944 | -0.28946 | -0.10361 | 0.050354 | 0.018311 | 0.082397 | 0.050354 | 0.11444 | -0.032043 | 0.10529 | 0.091553 | 0.3418 | 0.46036 | -0.54367 | -0.13351 | -0.007477 | -0.009155 | 0.1236 | 0.041199 | 0.11902 | 0.10529 | 0 | 0.068665 | 122.1176 | 121.8933 | 0.21057
11341.1719 | 0.061035 | 0.22003 | -0.21896 | -0.24353 | -0.20081 | -0.25314 | -0.11856 | 0.045776 | -0.059509 | -0.009155 | 0.027466 | 0.15106 | 0.013733 | 0.13733 | 0.061035 | 0.11215 | -0.006409 | -0.50842 | -0.10895 | -0.043793 | -0.068665 | 0.041199 | -0.059509 | 0.10529 | 0.09613 | 0.073242 | 0.12817 | 122.3145 | 121.9803 | 0.09613
11342.9062 | 0.045776 | 0.26382 | -0.22858 | -0.24353 | -0.19012 | -0.30334 | -0.12176 | 0.064087 | 0.013733 | 0.073242 | 0.073242 | 0.11902 | -0.018311 | 0.10529 | 0.045776 | 0.074768 | -0.03418 | -0.51483 | -0.13245 | -0.02243 | 0.018311 | 0.12817 | 0.041199 | 0.054932 | 0.050354 | 0.041199 | 0.09613 | 122.2595 | 122.049 | 0.10986
11344.6875 | 0.061035 | 0.22644 | -0.21896 | -0.2446 | -0.19546 | -0.24674 | -0.11536 | 0.086975 | -0.027466 | 0.013733 | 0.041199 | 0.16022 | 0.009155 | 0.12817 | 0.061035 | 0.11002 | -0.028839 | -0.50736 | -0.11536 | -0.036316 | -0.004578 | 0.068665 | -0.045776 | 0.07782 | 0.086975 | 0.068665 | 0.11902 | 122.3419 | 122.0261 | 0.07782
11346.4688 | 0.030518 | 0.23605 | -0.22964 | -0.25314 | -0.19546 | -0.27664 | -0.11963 | 0.045776 | -0.045776 | 0.013733 | 0.009155 | 0.13275 | 0.013733 | 0.12817 | 0.061035 | 0.29373 | 0.32791 | -0.51483 | -0.13138 | -0.004272 | -0.059509 | 0.073242 | -0.036621 | 0.14191 | 0.15564 | 0.045776 | 0.10071 | 122.2183 | 122.0444 | 0.15564
11348.25 | 0.045776 | 0.25742 | -0.22964 | -0.23392 | -0.20401 | -0.28946 | -0.10788 | 0.073242 | 0.009155 | 0.068665 | 0.050354 | 0.11444 | -0.022888 | 0.10071 | 0.061035 | 0.074768 | -0.035248 | -0.50415 | -0.13138 | -0.016022 | -0.004578 | 0.091553 | 0.009155 | 0.059509 | 0.050354 | 0.045776 | 0.09613 | 122.2549 | 122.1176 | 0.13733
11350.0469 | 0.045776 | 0.23605 | -0.22537 | -0.25101 | -0.1944 | -0.27237 | -0.11536 | 0.045776 | -0.045776 | 0.018311 | 0.004578 | 0.16022 | 0.004578 | 0.13733 | 0.076294 | 0.086517 | -0.01709 | -0.52978 | -0.11963 | -0.024567 | -0.059509 | 0.036621 | -0.07782 | 0.10529 | 0.086975 | 0.082397 | 0.13733 | 122.1817 | 122.0901 | 0.10071
11351.7812 | 0.076294 | 0.24033 | -0.23071 | -0.25635 | -0.18585 | -0.28091 | -0.13138 | 0.11902 | 0.10986 | 0.13275 | 0.073242 | 0.086975 | -0.027466 | 0.09613 | 0.061035 | 0.076904 | -0.029907 | -0.53406 | -0.12283 | -0.026703 | 0.059509 | 0.18768 | 0.064087 | 0.036621 | 0.041199 | 0.045776 | 0.10071 | 122.2687 | 122.1268 | 0.13733
11353.5781 | 0.045776 | 0.23819 | -0.20935 | -0.23498 | -0.18265 | -0.25742 | -0.10361 | 0.16022 | 0.059509 | 0.11444 | 0.10071 | 0.09613 | -0.045776 | 0.082397 | 0.061035 | 0.087585 | -0.037384 | -0.5127 | -0.10147 | -0.036316 | 0.07782 | 0.12817 | 0.064087 | 0.050354 | 0.045776 | 0.022888 | 0.10071 | 122.3602 | 122.1222 | 0.12817
11355.3594 | 0.061035 | 0.24033 | -0.21896 | -0.22217 | -0.19974 | -0.24994 | -0.1004 | 0.10986 | 0.032043 | 0.07782 | 0.064087 | 0.11444 | -0.036621 | 0.09613 | 0.045776 | 0.092926 | -0.036316 | -0.51163 | -0.10574 | -0.033112 | 0.050354 | 0.12817 | 0.036621 | 0.073242 | 0.036621 | 0.032043 | 0.086975 | 122.4152 | 122.1039 | 0.10986
11357.0781 | 0.091553 | 0.23819 | -0.2211 | -0.22964 | -0.20721 | -0.25848 | -0.11108 | 0.068665 | -0.013733 | 0.018311 | 0.027466 | 0.13275 | -0.018311 | 0.11902 | 0.030518 | 0.10147 | -0.01709 | -0.52017 | -0.09613 | -0.026703 | 0.041199 | 0.082397 | 0.004578 | 0.054932 | 0.050354 | 0.027466 | 0.10986 | 122.438 | 122.1313 | 0.09613
11358.875 | 0.045776 | 0.2243 | -0.23498 | -0.26062 | -0.20401 | -0.27344 | -0.11963 | 0.10071 | 0.086975 | 0.11444 | 0.10071 | 0.10529 | -0.022888 | 0.1236 | 0.061035 | 0.088654 | -0.019226 | -0.51376 | -0.13031 | -0.023499 | 0.018311 | 0.14648 | 0.013733 | 0.073242 | 0.059509 | 0.032043 | 0.11444 | 122.2778 | 122.1588 | 0.14191
11360.6562 | 0.045776 | 0.2179 | -0.22217 | -0.24033 | -0.1944 | -0.24246 | -0.1004 | 0.11444 | 0.027466 | 0.059509 | 0.050354 | 0.13275 | -0.004578 | 0.13275 | 0.061035 | 0.098267 | -0.011749 | -0.49667 | -0.10681 | -0.042725 | -0.018311 | 0.064087 | -0.054932 | 0.07782 | 0.059509 | 0.064087 | 0.13733 | 122.4106 | 122.1268 | 0.086975
11362.4531 | 0.045776 | 0.23712 | -0.2179 | -0.23498 | -0.21042 | -0.24674 | -0.10361 | 0.09613 | 0.022888 | 0.036621 | 0.054932 | 0.15564 | 0.009155 | 0.10986 | 0.045776 | 1.9632 | 3.4564 | -0.71671 | -0.12283 | 0.19974 | -0.022888 | 0.27466 | 0.16479 | 0.46234 | 0.44403 | -0.21973 | -0.15106 | 122.3785 | 121.6187 | 0.54016
11364.1875 | 0.061035 | 0.22751 | -0.22217 | -0.23178 | -0.1944 | -0.25635 | -0.10574 | 0.036621 | -0.091553 | -0.036621 | 0.004578 | 0.15106 | 0 | 0.14648 | 0.061035 | 0.11322 | -0.02243 | -0.5127 | -0.10574 | -0.014954 | -0.054932 | 0 | -0.091553 | 0.082397 | 0.086975 | 0.059509 | 0.14191 | 122.4335 | 122.1497 | 0.09613
11365.9688 | 0.061035 | 0.2478 | -0.23392 | -0.23178 | -0.18906 | -0.29373 | -0.12817 | 0.086975 | 0.064087 | 0.09613 | 0.073242 | 0.09613 | -0.032043 | 0.10071 | 0.045776 | 0.081177 | -0.03418 | -0.52551 | -0.12604 | -0.013885 | 0.018311 | 0.10986 | 0.018311 | 0.041199 | 0.054932 | 0.041199 | 0.10071 | 122.3419 | 122.2321 | 0.13733
11367.75 | 0.030518 | 0.23071 | -0.22003 | -0.23819 | -0.18692 | -0.26382 | -0.10895 | 0.032043 | -0.022888 | 0 | 0.027466 | 0.15106 | 0 | 0.14648 | 0.061035 | 0.097198 | -0.025635 | -0.51483 | -0.1207 | -0.030975 | -0.050354 | 0.064087 | -0.054932 | 0.10986 | 0.068665 | 0.073242 | 0.11902 | 122.4747 | 122.1588 | 0.10529
11369.4844 | 0.045776 | 0.25101 | -0.22858 | -0.23285 | -0.18265 | -0.27237 | -0.11963 | 0.11444 | 0.09613 | 0.14191 | 0.10071 | 0.09613 | -0.045776 | 0.09613 | 0.061035 | 0.43686 | 0.66971 | -0.55969 | -0.12283 | 0.028839 | 0.050354 | 0.15564 | 0.091553 | 0.12817 | 0.10986 | -0.032043 | 0.041199 | 122.4197 | 122.1313 | 0.16937
11371.2656 | 0.045776 | 0.23712 | -0.23178 | -0.25742 | -0.17517 | -0.26489 | -0.12711 | 0.027466 | -0.059509 | -0.004578 | 0 | 0.13733 | -0.004578 | 0.14648 | 0.076294 | 0.10254 | -0.013885 | -0.51697 | -0.12283 | -0.030975 | -0.082397 | 0.022888 | -0.091553 | 0.11444 | 0.091553 | 0.09613 | 0.11902 | 122.3785 | 122.2046 | 0.12817
11373 | 0.061035 | 0.24246 | -0.21896 | -0.24994 | -0.19012 | -0.27344 | -0.11963 | 0.07782 | 0 | 0.041199 | 0.073242 | 0.13275 | -0.018311 | 0.1236 | 0.061035 | 0.09079 | -0.021362 | -0.49881 | -0.12924 | -0.037384 | -0.050354 | 0.064087 | -0.054932 | 0.068665 | 0.086975 | 0.054932 | 0.11444 | 122.374 | 122.2229 | 0.14191
11374.7969 | 0.061035 | 0.21576 | -0.21896 | -0.25101 | -0.17624 | -0.26169 | -0.12176 | 0.054932 | -0.059509 | -0.013733 | 0.004578 | 0.15564 | 0.004578 | 0.13275 | 0.045776 | 0.092926 | -0.004272 | -0.50095 | -0.11856 | -0.037384 | -0.054932 | 0.054932 | -0.082397 | 0.10529 | 0.082397 | 0.073242 | 0.13275 | 122.4884 | 122.1909 | 0.09613
11376.5938 | 0.076294 | 0.23392 | -0.21683 | -0.2243 | -0.18478 | -0.24994 | -0.11322 | 0.032043 | -0.054932 | -0.013733 | 0.013733 | 0.15106 | -0.004578 | 0.12817 | 0.061035 | 0.088654 | -0.004272 | -0.50629 | -0.10361 | -0.033112 | -0.032043 | 0.004578 | -0.07782 | 0.091553 | 0.064087 | 0.054932 | 0.1236 | 122.5159 | 122.2183 | 0.07782
11378.3906 | 0.045776 | 0.22217 | -0.22964 | -0.25314 | -0.19867 | -0.28732 | -0.11215 | 0.1236 | 0.064087 | 0.11444 | 0.091553 | 0.082397 | -0.041199 | 0.086975 | 0.030518 | 0.084381 | 0.086517 | -0.49988 | -0.12711 | -0.020294 | 0.068665 | 0.13733 | 0.027466 | 0.054932 | 0.054932 | 0.027466 | 0.09613 | 122.3465 | 122.2229 | 0.17395
11380.1094 | 0.045776 | 0.24246 | -0.22537 | -0.2243 | -0.17838 | -0.25955 | -0.11643 | 0.10071 | 0.032043 | 0.073242 | 0.073242 | 0.11444 | -0.022888 | 0.09613 | 0.076294 | 1.6791 | 3.654 | -0.59601 | -0.12604 | 0.065155 | 0.054932 | 0.16022 | 0.036621 | 0.22888 | 0.20599 | -0.064087 | 0.004578 | 122.4243 | 121.8887 | 0.32501
11381.9062 | 0.030518 | 0.22644 | -0.22537 | -0.23285 | -0.19226 | -0.24139 | -0.11429 | 0.09613 | 0.013733 | 0.018311 | 0.045776 | 0.12817 | -0.004578 | 0.1236 | 0.061035 | 1.6086 | 5.7838 | -0.68893 | -0.11643 | 0.1741 | -0.018311 | 0.07782 | -0.068665 | 0.3479 | 0.32959 | -0.11444 | -0.045776 | 122.2641 | 121.6736 | 0.47607
11383.6562 | 0.061035 | 0.22644 | -0.21576 | -0.23178 | -0.17517 | -0.26489 | -0.11108 | 0.10986 | 0.045776 | 0.041199 | 0.054932 | 0.15106 | -0.013733 | 0.11902 | 0.030518 | 2.729 | 10.2507 | -0.82565 | -0.14206 | 0.31082 | 0.004578 | 0.16937 | -0.032043 | 0.51727 | 0.5127 | -0.27008 | -0.20599 | 122.2229 | 121.2936 | 0.72784
11385.4531 | 0.061035 | 0.23712 | -0.22217 | -0.2681 | -0.17944 | -0.27771 | -0.12924 | 0.027466 | -0.022888 | 0.036621 | 0.018311 | 0.15106 | 0.004578 | 0.13275 | 0.045776 | 4.156 | 14.2006 | -0.90576 | -0.19119 | 0.47211 | -0.073242 | 0.14191 | -0.032043 | 0.737 | 0.69122 | -0.3479 | -0.30212 | 121.8842 | 120.9137 | 1.0437
11387.2344 | 0.045776 | 0.23712 | -0.21896 | -0.24994 | -0.19226 | -0.25207 | -0.11856 | 0.009155 | -0.091553 | -0.045776 | -0.013733 | 0.14191 | -0.009155 | 0.14191 | 0.045776 | 0.22324 | 0.54047 | -0.52017 | -0.11963 | 0.013885 | -0.013733 | 0.004578 | -0.12817 | 0.11444 | 0.1236 | 0.036621 | 0.11444 | 121.788 | 121.3348 | 0.15564
11389.0469 | 0.030518 | 0.25742 | -0.23819 | -0.23392 | -0.19653 | -0.30228 | -0.11749 | 0.10071 | 0.11444 | 0.13733 | 0.10071 | 0.09613 | -0.022888 | 0.10986 | 0.061035 | 0.055542 | -0.018158 | -0.52231 | -0.11963 | -0.024567 | 0.036621 | 0.19226 | 0.073242 | 0.050354 | 0.045776 | 0.032043 | 0.086975 | 121.8796 | 121.7148 | 0.11902
11390.8281 | 0.045776 | 0.23071 | -0.2243 | -0.24887 | -0.1944 | -0.2478 | -0.1239 | 0.036621 | -0.064087 | -0.022888 | 0.018311 | 0.15106 | -0.009155 | 0.14648 | 0.061035 | 0.084381 | -0.004272 | -0.50522 | -0.10574 | -0.024567 | -0.041199 | 0 | -0.086975 | 0.10071 | 0.064087 | 0.064087 | 0.12817 | 122.1222 | 121.8155 | 0.091553
11392.5625 | 0.061035 | 0.23392 | -0.22217 | -0.24674 | -0.18265 | -0.26382 | -0.10895 | 0.091553 | 0.009155 | 0.073242 | 0.059509 | 0.13733 | -0.032043 | 0.11902 | 0.061035 | 0.076904 | -0.012817 | -0.50949 | -0.12283 | -0.026703 | 0.041199 | 0.1236 | 0.027466 | 0.054932 | 0.050354 | 0.036621 | 0.10529 | 122.1634 | 121.8567 | 0.086975
11394.3594 | 0.061035 | 0.24674 | -0.23071 | -0.23926 | -0.18051 | -0.26596 | -0.11002 | 0.11444 | 0.054932 | 0.086975 | 0.073242 | 0.10986 | -0.045776 | 0.086975 | 0.045776 | 0.072632 | -0.011749 | -0.5191 | -0.11963 | -0.032043 | 0.064087 | 0.11902 | 0.032043 | 0.036621 | 0.050354 | 0.027466 | 0.091553 | 122.1909 | 121.9162 | 0.10071
11396.0781 | 0.076294 | 0.28305 | -0.23819 | -0.25101 | -0.18799 | -0.29694 | -0.12176 | 0.027466 | 0.027466 | 0.073242 | 0.064087 | 0.1236 | -0.018311 | 0.11444 | 0.076294 | 0.060883 | -0.009613 | -0.51163 | -0.13138 | -0.014954 | 0.004578 | 0.10071 | 0.018311 | 0.054932 | 0.059509 | 0.032043 | 0.10071 | 122.1313 | 121.9345 | 0.1236
11397.8438 | 0.015259 | 0.24246 | -0.23819 | -0.24887 | -0.18799 | -0.27985 | -0.12924 | 0.15106 | 0.11444 | 0.15106 | 0.10071 | 0.09613 | -0.036621 | 0.091553 | 0.076294 | 0.064087 | 0.003204 | -0.52658 | -0.13565 | -0.019226 | 0.059509 | 0.17395 | 0.068665 | 0.036621 | 0.032043 | 0.027466 | 0.091553 | 122.1542 | 121.962 | 0.13275
11399.6562 | 0.061035 | 0.24353 | -0.23819 | -0.25742 | -0.18692 | -0.28091 | -0.12711 | 0.10529 | 0.054932 | 0.10529 | 0.09613 | 0.10071 | -0.027466 | 0.11902 | 0.045776 | 0.065155 | 0.011749 | -0.51163 | -0.1239 | -0.035248 | 0.064087 | 0.15106 | 0.054932 | 0.068665 | 0.045776 | 0.027466 | 0.10529 | 122.1909 | 121.994 | 0.11902
11401.3906 | 0.061035 | 0.23819 | -0.2243 | -0.24033 | -0.1741 | -0.26916 | -0.12711 | 0.11902 | 0.09613 | 0.12817 | 0.10986 | 0.10986 | -0.050354 | 0.10986 | 0.061035 | 0.060883 | 0.010681 | -0.51483 | -0.11536 | -0.032043 | 0.022888 | 0.14648 | 0.004578 | 0.059509 | 0.045776 | 0.036621 | 0.10529 | 122.1313 | 121.994 | 0.13275
11403.1875 | 0.030518 | 0.24139 | -0.22644 | -0.24674 | -0.19012 | -0.27878 | -0.12604 | 0.10529 | 0.064087 | 0.10986 | 0.10071 | 0.10529 | -0.036621 | 0.10529 | 0.076294 | 0.076904 | -0.001068 | -0.52872 | -0.11963 | -0.036316 | 0.064087 | 0.15564 | 0.064087 | 0.059509 | 0.045776 | 0.032043 | 0.082397 | 122.2137 | 122.0032 | 0.10071
11404.9219 | 0.061035 | 0.22537 | -0.22964 | -0.21683 | -0.19119 | -0.25421 | -0.12924 | 0.14648 | 0.07782 | 0.091553 | 0.082397 | 0.10071 | -0.045776 | 0.11902 | 0.061035 | 0.092926 | 0.009613 | -0.50522 | -0.10147 | -0.037384 | 0.082397 | 0.1236 | 0.018311 | 0.064087 | 0.027466 | 0.032043 | 0.10529 | 122.2961 | 122.0169 | 0.091553
11406.7188 | 0.045776 | 0.24994 | -0.23498 | -0.26062 | -0.18692 | -0.27771 | -0.1207 | 0.10986 | 0.091553 | 0.10986 | 0.082397 | 0.10529 | -0.027466 | 0.10071 | 0.045776 | 0.063019 | 0.012817 | -0.52124 | -0.1442 | -0.037384 | 0.073242 | 0.15106 | 0.050354 | 0.059509 | 0.041199 | 0.027466 | 0.10529 | 122.2321 | 122.0169 | 0.11444
11408.5156 | 0.076294 | 0.24033 | -0.21255 | -0.23605 | -0.18585 | -0.24994 | -0.10788 | 0.10071 | -0.013733 | 0.032043 | 0.032043 | 0.11902 | -0.032043 | 0.11902 | 0.045776 | 0.083313 | 0 | -0.50522 | -0.10147 | -0.041656 | 0.064087 | 0.10986 | -0.009155 | 0.054932 | 0.045776 | 0.022888 | 0.09613 | 122.3419 | 122.0352 | 0.091553
11410.3125 | 0.076294 | 0.26169 | -0.22324 | -0.24033 | -0.17731 | -0.27557 | -0.11643 | 0.091553 | 0.027466 | 0.068665 | 0.054932 | 0.11902 | -0.022888 | 0.09613 | 0.061035 | 0.0737 | 0.008545 | -0.50522 | -0.13672 | -0.03418 | 0.022888 | 0.10071 | 0 | 0.059509 | 0.050354 | 0.036621 | 0.10071 | 122.2137 | 122.081 | 0.11902
11412.0938 | 0.076294 | 0.24567 | -0.22003 | -0.22324 | -0.18585 | -0.25742 | -0.11322 | 0.15106 | 0.07782 | 0.10529 | 0.091553 | 0.09613 | -0.050354 | 0.10071 | 0.076294 | 0.084381 | 0.014954 | -0.50522 | -0.10361 | -0.036316 | 0.082397 | 0.14191 | 0.036621 | 0.041199 | 0.036621 | 0.018311 | 0.09613 | 122.3648 | 122.049 | 0.09613
11413.8125 | 0.030518 | 0.22858 | -0.2211 | -0.24887 | -0.19119 | -0.23926 | -0.11215 | 0.059509 | -0.054932 | 0.013733 | 0.041199 | 0.14648 | 0.018311 | 0.14648 | 0.061035 | 0.43259 | 1.1771 | -0.53406 | -0.11856 | 0.003204 | -0.027466 | 0.086975 | -0.059509 | 0.14191 | 0.10529 | 0.032043 | 0.091553 | 122.2824 | 121.9666 | 0.14648
11415.6094 | 0.045776 | 0.23178 | -0.2211 | -0.24674 | -0.18906 | -0.25635 | -0.11215 | 0.10071 | 0.013733 | 0.036621 | 0.054932 | 0.14191 | -0.004578 | 0.13733 | 0.061035 | 0.095062 | 0.002136 | -0.50629 | -0.11429 | -0.032043 | 0.018311 | 0.07782 | -0.050354 | 0.068665 | 0.068665 | 0.07782 | 0.1236 | 122.3877 | 122.0627 | 0.07782
11417.4062 | 0.061035 | 0.21896 | -0.22324 | -0.24246 | -0.19119 | -0.25955 | -0.10895 | 0.10071 | -0.009155 | 0.032043 | 0.027466 | 0.13275 | -0.013733 | 0.13733 | 0.030518 | 0.089722 | 0.003204 | -0.50201 | -0.11215 | -0.028839 | -0.018311 | 0.050354 | -0.10071 | 0.082397 | 0.050354 | 0.068665 | 0.11902 | 122.3465 | 122.0856 | 0.091553
11419.2031 | 0.061035 | 0.21576 | -0.21149 | -0.24033 | -0.18265 | -0.26596 | -0.1207 | 0.059509 | -0.027466 | 0.009155 | 0.041199 | 0.13733 | 0.013733 | 0.14648 | 0.045776 | 0.086517 | 0.002136 | -0.51056 | -0.12817 | -0.032043 | -0.032043 | 0.091553 | -0.041199 | 0.09613 | 0.07782 | 0.059509 | 0.14648 | 122.406 | 122.081 | 0.11444
11420.9219 | 0.076294 | 0.22858 | -0.21896 | -0.24033 | -0.18906 | -0.24994 | -0.11215 | 0.10071 | -0.013733 | 0.018311 | 0.045776 | 0.11444 | -0.013733 | 0.14648 | 0.076294 | 0.084381 | 0.008545 | -0.50201 | -0.12176 | -0.026703 | -0.022888 | 0.059509 | -0.068665 | 0.07782 | 0.07782 | 0.068665 | 0.12817 | 122.374 | 122.0993 | 0.082397
11422.7031 | 0.045776 | 0.23819 | -0.23712 | -0.2478 | -0.18799 | -0.28305 | -0.12924 | 0.082397 | 0.086975 | 0.11444 | 0.09613 | 0.10071 | -0.036621 | 0.10071 | 0.061035 | 0.069427 | 0.004272 | -0.50629 | -0.13992 | -0.027771 | -0.009155 | 0.13733 | 0.013733 | 0.059509 | 0.050354 | 0.050354 | 0.11902 | 122.2824 | 122.1451 | 0.13733
11424.5156 | 0.045776 | 0.23819 | -0.22003 | -0.22858 | -0.18265 | -0.25421 | -0.10788 | 0.022888 | -0.036621 | -0.013733 | 0 | 0.14648 | -0.013733 | 0.12817 | 0.076294 | 0.082245 | 0.018158 | -0.50415 | -0.10895 | -0.026703 | -0.036621 | 0.027466 | -0.064087 | 0.09613 | 0.073242 | 0.082397 | 0.13275 | 122.4197 | 122.113 | 0.11444
11426.2969 | 0.061035 | 0.20721 | -0.22217 | -0.25101 | -0.18799 | -0.25101 | -0.11643 | 0.064087 | 0.032043 | 0.036621 | 0.050354 | 0.13733 | -0.004578 | 0.11902 | 0.076294 | 0.088654 | 0.026703 | -0.50736 | -0.11429 | -0.038452 | 0.013733 | 0.09613 | -0.036621 | 0.091553 | 0.064087 | 0.059509 | 0.11902 | 122.4106 | 122.1313 | 0.09613
11428.0781 | 0.091553 | 0.2478 | -0.23071 | -0.23926 | -0.19546 | -0.27237 | -0.11856 | 0.009155 | -0.036621 | -0.018311 | 0.013733 | 0.14648 | 0.009155 | 0.15106 | 0.045776 | 0.075836 | 0.001068 | -0.5159 | -0.12497 | -0.027771 | -0.091553 | 0.036621 | -0.068665 | 0.10529 | 0.10071 | 0.07782 | 0.13733 | 122.3465 | 122.1588 | 0.10071
11429.875 | 0.076294 | 0.24246 | -0.22751 | -0.25955 | -0.18692 | -0.29266 | -0.12817 | 0.10986 | 0.11902 | 0.13733 | 0.10986 | 0.086975 | -0.032043 | 0.10071 | 0.061035 | 0.053406 | 0.014954 | -0.5191 | -0.13138 | -0.024567 | 0.050354 | 0.19226 | 0.054932 | 0.050354 | 0.054932 | 0.032043 | 0.082397 | 122.3419 | 122.1817 | 0.11902
11431.6719 | 0.045776 | 0.22858 | -0.21683 | -0.23926 | -0.18585 | -0.24139 | -0.11215 | 0.091553 | -0.022888 | 0.018311 | 0.041199 | 0.12817 | -0.018311 | 0.12817 | 0.061035 | 0.09613 | 0.011749 | -0.50415 | -0.10147 | -0.029907 | -0.032043 | 0.050354 | -0.082397 | 0.091553 | 0.082397 | 0.073242 | 0.13275 | 122.4106 | 122.1771 | 0.086975
11433.3906 | 0.061035 | 0.25207 | -0.23178 | -0.23926 | -0.19546 | -0.28625 | -0.11856 | 0.11902 | 0.054932 | 0.10529 | 0.07782 | 0.086975 | -0.045776 | 0.091553 | 0.045776 | 0.059814 | 0.003204 | -0.51056 | -0.12497 | -0.025635 | 0.018311 | 0.11902 | 0.027466 | 0.050354 | 0.050354 | 0.032043 | 0.073242 | 122.3282 | 122.2229 | 0.14648
11435.1719 | 0.076294 | 0.24246 | -0.21896 | -0.23178 | -0.19974 | -0.26916 | -0.11536 | 0.091553 | -0.022888 | 0.032043 | 0.032043 | 0.1236 | -0.018311 | 0.1236 | 0.045776 | 0.083313 | -0.002136 | -0.49881 | -0.11643 | -0.027771 | 0.027466 | 0.10071 | 0.009155 | 0.082397 | 0.045776 | 0.036621 | 0.10071 | 122.4747 | 122.1542 | 0.086975
11436.9688 | 0.045776 | 0.24246 | -0.24674 | -0.25528 | -0.18585 | -0.28305 | -0.13031 | 0.045776 | 0.027466 | 0.091553 | 0.054932 | 0.11444 | -0.036621 | 0.091553 | 0.045776 | 0.058746 | 0.004272 | -0.52551 | -0.12711 | -0.019226 | 0.022888 | 0.12817 | 0.050354 | 0.073242 | 0.045776 | 0.064087 | 0.10529 | 122.4014 | 122.1909 | 0.11902
11438.7031 | 0.030518 | 0.23926 | -0.23071 | -0.23819 | -0.19226 | -0.27451 | -0.12176 | 0.1236 | 0.082397 | 0.11902 | 0.07782 | 0.07782 | -0.050354 | 0.09613 | 0.061035 | 0.068359 | -0.005341 | -0.51697 | -0.11215 | -0.033112 | 0.059509 | 0.12817 | 0.027466 | 0.041199 | 0.045776 | 0.027466 | 0.10529 | 122.3648 | 122.2275 | 0.13275
11440.5 | 0.045776 | 0.22537 | -0.2211 | -0.23178 | -0.1709 | -0.23712 | -0.11322 | 0.11902 | 0.018311 | 0.050354 | 0.059509 | 0.13275 | 0.004578 | 0.13275 | 0.076294 | 0.092926 | 0.014954 | -0.50842 | -0.11215 | -0.03952 | 0.004578 | 0.07782 | -0.054932 | 0.07782 | 0.073242 | 0.054932 | 0.12817 | 122.4609 | 122.1909 | 0.082397
11442.2969 | 0.091553 | 0.22003 | -0.21255 | -0.24887 | -0.19226 | -0.2478 | -0.11002 | 0.11444 | 0.013733 | 0.036621 | 0.059509 | 0.12817 | 0.009155 | 0.13275 | 0.076294 | 0.083313 | 0.019226 | -0.50736 | -0.1207 | -0.041656 | -0.004578 | 0.09613 | -0.045776 | 0.073242 | 0.073242 | 0.068665 | 0.1236 | 122.4701 | 122.1954 | 0.068665
11444.0781 | 0.061035 | 0.25955 | -0.23285 | -0.23498 | -0.20081 | -0.29694 | -0.12924 | 0.068665 | 0.027466 | 0.064087 | 0.059509 | 0.10529 | -0.036621 | 0.09613 | 0.076294 | 0.055542 | -0.006409 | -0.5127 | -0.12497 | -0.013885 | -0.009155 | 0.086975 | 0.022888 | 0.068665 | 0.050354 | 0.045776 | 0.086975 | 122.3785 | 122.2458 | 0.13275
11445.8125 | 0.045776 | 0.22858 | -0.2243 | -0.23178 | -0.18478 | -0.24887 | -0.11643 | 0.11902 | 0.018311 | 0.036621 | 0.041199 | 0.13733 | -0.022888 | 0.1236 | 0.045776 | 0.09079 | 0.008545 | -0.49988 | -0.10468 | -0.032043 | 0 | 0.068665 | -0.059509 | 0.082397 | 0.064087 | 0.045776 | 0.11444 | 122.4426 | 122.2092 | 0.091553
11447.6094 | 0.061035 | 0.2446 | -0.22751 | -0.25955 | -0.19119 | -0.28946 | -0.12176 | 0.091553 | 0.07782 | 0.1236 | 0.082397 | 0.12817 | -0.045776 | 0.11444 | 0.061035 | 0.058746 | 0.004272 | -0.51483 | -0.15274 | -0.035248 | 0.059509 | 0.15106 | 0.059509 | 0.041199 | 0.045776 | 0.036621 | 0.09613 | 122.4243 | 122.2412 | 0.09613
11449.3438 | 0.076294 | 0.24033 | -0.23819 | -0.24033 | -0.18372 | -0.27237 | -0.13031 | 0.036621 | -0.045776 | -0.018311 | 0.004578 | 0.14191 | 0.022888 | 0.14648 | 0.061035 | 0.072632 | 0.010681 | -0.50415 | -0.11963 | -0.033112 | -0.068665 | 0.032043 | -0.086975 | 0.09613 | 0.082397 | 0.073242 | 0.14191 | 122.4426 | 122.2275 | 0.086975
11451.125 | 0.061035 | 0.25101 | -0.24674 | -0.24246 | -0.20401 | -0.29266 | -0.11429 | 0.064087 | 0.045776 | 0.10071 | 0.064087 | 0.1236 | -0.032043 | 0.1236 | 0.076294 | 0.055542 | 0 | -0.52231 | -0.13458 | -0.02243 | 0.022888 | 0.13733 | 0.054932 | 0.07782 | 0.036621 | 0.045776 | 0.10529 | 122.4335 | 122.2549 | 0.12817
11452.9062 | 0.045776 | 0.23285 | -0.21469 | -0.24887 | -0.18585 | -0.25207 | -0.10895 | 0.041199 | -0.045776 | -0.022888 | 0.009155 | 0.14191 | 0.009155 | 0.14648 | 0.045776 | 0.088654 | 0.005341 | -0.50842 | -0.10788 | -0.03952 | -0.036621 | 0.009155 | -0.068665 | 0.073242 | 0.064087 | 0.059509 | 0.12817 | 122.525 | 122.2092 | 0.086975
11454.7031 | 0.045776 | 0.21896 | -0.20615 | -0.26276 | -0.19226 | -0.24567 | -0.11429 | 0.073242 | -0.018311 | 0.022888 | 0.050354 | 0.13733 | 0 | 0.14648 | 0.045776 | 0.080109 | 0.032043 | -0.49561 | -0.12604 | -0.041656 | -0.018311 | 0.073242 | -0.041199 | 0.07782 | 0.073242 | 0.068665 | 0.11902 | 122.5296 | 122.2092 | 0.086975
11456.4375 | 0.045776 | 0.23392 | -0.22751 | -0.23819 | -0.18158 | -0.2713 | -0.11108 | 0.1236 | 0.041199 | 0.10529 | 0.082397 | 0.11902 | -0.027466 | 0.10071 | 0.061035 | 0.081177 | 0.020294 | -0.51804 | -0.10361 | -0.018158 | 0.050354 | 0.12817 | 0.018311 | 0.064087 | 0.027466 | 0.018311 | 0.091553 | 122.5296 | 122.2275 | 0.10529
11458.2188 | 0.030518 | 0.24246 | -0.2243 | -0.24674 | -0.19226 | -0.27023 | -0.11749 | 0.1236 | 0.07782 | 0.13733 | 0.091553 | 0.10071 | -0.032043 | 0.091553 | 0.061035 | 0.74127 | 2.9555 | -0.60883 | -0.13458 | 0.050201 | 0.10986 | 0.24719 | 0.091553 | 0.17853 | 0.16479 | -0.073242 | -0.022888 | 122.3648 | 122.0718 | 0.22888
11460.0156 | 0.045776 | 0.23178 | -0.22003 | -0.25848 | -0.18906 | -0.28839 | -0.11643 | 0.10071 | 0.086975 | 0.12817 | 0.09613 | 0.10529 | -0.032043 | 0.10986 | 0.015259 | 0.42191 | 1.506 | -0.5629 | -0.13992 | 0.023499 | 0.018311 | 0.15106 | 0.009155 | 0.13275 | 0.1236 | 0.004578 | 0.073242 | 122.3099 | 122.1313 | 0.20599
11461.8125 | 0.076294 | 0.2243 | -0.21683 | -0.24567 | -0.18265 | -0.25314 | -0.11963 | 0.07782 | -0.013733 | 0.022888 | 0.050354 | 0.15106 | -0.004578 | 0.13275 | 0.061035 | 0.15488 | 0.28839 | -0.51697 | -0.11536 | -0.028839 | -0.027466 | 0.091553 | -0.050354 | 0.091553 | 0.09613 | 0.045776 | 0.11444 | 122.4792 | 122.1313 | 0.10529
11463.6094 | 0.061035 | 0.22537 | -0.23498 | -0.24887 | -0.1741 | -0.2713 | -0.11429 | 0.032043 | -0.045776 | -0.013733 | 0.009155 | 0.14191 | 0 | 0.15564 | 0.061035 | 0.31509 | 0.64621 | -0.51056 | -0.14099 | -0.032043 | -0.036621 | 0.032043 | -0.086975 | 0.11902 | 0.10986 | 0.050354 | 0.1236 | 121.8201 | 121.5683 | 0.15564
11465.4062 | 0.076294 | 0.23392 | -0.22644 | -0.23285 | -0.18158 | -0.25314 | -0.13031 | 0.054932 | -0.036621 | 0 | 0.032043 | 0.14191 | 0.004578 | 0.13275 | 0.030518 | 0.080109 | -0.003204 | -0.50949 | -0.12283 | -0.040588 | -0.032043 | 0.073242 | -0.050354 | 0.086975 | 0.082397 | 0.054932 | 0.11902 | 122.1863 | 121.8796 | 0.073242
11467.125 | 0.076294 | 0.21576 | -0.21255 | -0.25742 | -0.18906 | -0.23926 | -0.10468 | 0.018311 | -0.11444 | -0.027466 | 0.009155 | 0.14648 | 0 | 0.13275 | 0.045776 | 0.075836 | 0.007477 | -0.50415 | -0.11749 | -0.036316 | -0.050354 | -0.004578 | -0.10529 | 0.07782 | 0.068665 | 0.064087 | 0.13733 | 122.2321 | 121.9482 | 0.091553
11468.9062 | 0.076294 | 0.23926 | -0.23285 | -0.2478 | -0.18906 | -0.29053 | -0.11536 | 0.045776 | 0.036621 | 0.07782 | 0.050354 | 0.10986 | -0.032043 | 0.10529 | 0.061035 | 0.033112 | -0.005341 | -0.51483 | -0.1506 | -0.016022 | 0.013733 | 0.10071 | 0 | 0.045776 | 0.059509 | 0.054932 | 0.12817 | 122.1634 | 122.0261 | 0.13733
11470.6406 | 0.045776 | 0.22217 | -0.22324 | -0.23392 | -0.19653 | -0.24139 | -0.11215 | 0.027466 | -0.064087 | -0.009155 | 0.004578 | 0.15106 | 0.004578 | 0.13733 | 0.045776 | 0.075836 | -0.003204 | -0.50629 | -0.10895 | -0.032043 | -0.086975 | -0.018311 | -0.12817 | 0.082397 | 0.07782 | 0.068665 | 0.15106 | 122.2824 | 122.0261 | 0.082397
11472.3594 | 0.045776 | 0.2713 | -0.22858 | -0.23498 | -0.17838 | -0.28839 | -0.1207 | 0.050354 | 0.036621 | 0.091553 | 0.041199 | 0.10071 | -0.041199 | 0.086975 | 0.045776 | 0.053406 | -0.006409 | -0.51056 | -0.12497 | -0.02243 | 0.018311 | 0.09613 | 0.009155 | 0.054932 | 0.050354 | 0.036621 | 0.09613 | 122.2275 | 122.081 | 0.12817
11474.1406 | 0.030518 | 0.21683 | -0.2211 | -0.24353 | -0.18906 | -0.23498 | -0.1004 | 0.09613 | -0.013733 | 0.018311 | 0.045776 | 0.13275 | -0.018311 | 0.13733 | 0.076294 | 0.081177 | 0.005341 | -0.50949 | -0.10681 | -0.044861 | -0.018311 | 0.054932 | -0.07782 | 0.07782 | 0.068665 | 0.082397 | 0.11902 | 122.3282 | 122.0581 | 0.09613
11475.8594 | 0.061035 | 0.23178 | -0.23071 | -0.2478 | -0.18372 | -0.29159 | -0.13031 | 0.09613 | 0.054932 | 0.082397 | 0.082397 | 0.10986 | -0.009155 | 0.11444 | 0.061035 | 0.075836 | 0.39093 | -0.51376 | -0.14633 | 0.016022 | 0.082397 | -0.064087 | -0.086975 | 0.10071 | 0.091553 | 0.050354 | 0.10529 | 122.2366 | 122.0535 | 0.15106
11477.6562 | 0.061035 | 0.2478 | -0.2211 | -0.23071 | -0.18799 | -0.24994 | -0.10788 | 0.11902 | 0.050354 | 0.091553 | 0.086975 | 0.091553 | -0.032043 | 0.082397 | 0.045776 | 0.7135 | 2.8241 | -0.5928 | -0.12817 | 0.057678 | 0.059509 | 0.25177 | 0.07782 | 0.18768 | 0.18768 | -0.07782 | -0.013733 | 122.3145 | 121.8109 | 0.28839
11479.4531 | 0.030518 | 0.24139 | -0.22964 | -0.24139 | -0.19653 | -0.29373 | -0.13138 | 0.086975 | 0.07782 | 0.1236 | 0.082397 | 0.10529 | -0.036621 | 0.10529 | 0.061035 | 0.071564 | 0.089722 | -0.51056 | -0.13458 | -0.024567 | 0.050354 | 0.17395 | 0.073242 | 0.054932 | 0.032043 | 0.013733 | 0.082397 | 122.2046 | 122.0718 | 0.11444
11481.1719 | 0.045776 | 0.22217 | -0.2179 | -0.24353 | -0.18692 | -0.23926 | -0.11322 | 0.041199 | -0.086975 | -0.027466 | 0.013733 | 0.13733 | -0.004578 | 0.14191 | 0.061035 | 0.13992 | 0.11856 | -0.4892 | -0.11002 | -0.03952 | 0.013733 | 0.082397 | -0.036621 | 0.11444 | 0.11444 | 0.054932 | 0.10529 | 122.3785 | 122.2137 | 0.086975
11482.9531 | 0.061035 | 0.23498 | -0.22324 | -0.26062 | -0.19333 | -0.26916 | -0.11536 | 0.018311 | -0.041199 | -0.004578 | -0.004578 | 0.15564 | 0.013733 | 0.14191 | 0.045776 | 0.41657 | 1.3779 | -0.52978 | -0.14313 | 0.002136 | -0.054932 | 0.054932 | -0.050354 | 0.15106 | 0.15106 | 0.018311 | 0.041199 | 122.2916 | 122.0261 | 0.18768
11484.6875 | 0.045776 | 0.23605 | -0.22537 | -0.22858 | -0.19012 | -0.25207 | -0.11215 | 0.045776 | -0.059509 | 0.032043 | 0.018311 | 0.13733 | -0.018311 | 0.12817 | 0.061035 | 0.43259 | 1.1675 | -0.54047 | -0.10147 | -0.001068 | -0.018311 | 0.064087 | -0.018311 | 0.12817 | 0.10529 | 0 | 0.082397 | 122.3511 | 122.0169 | 0.16479
11486.4844 | 0.045776 | 0.23392 | -0.22537 | -0.2478 | -0.19119 | -0.28198 | -0.12711 | 0.09613 | 0.11444 | 0.13275 | 0.09613 | 0.086975 | -0.018311 | 0.1236 | 0.061035 | 0.63232 | 2.1768 | -0.56503 | -0.13886 | 0.023499 | 0.004578 | 0.14191 | 0.10529 | 0.16022 | 0.11902 | -0.018311 | 0.041199 | 122.1542 | 121.9482 | 0.21973
11488.2656 | 0.076294 | 0.22858 | -0.21683 | -0.23712 | -0.19119 | -0.24994 | -0.11108 | 0.059509 | -0.045776 | -0.013733 | 0.013733 | 0.14648 | -0.013733 | 0.12817 | 0.061035 | 0.82031 | 0.77225 | -0.33646 | -0.9346 | 0.62912 | 0.013733 | 0.11444 | -0.041199 | 0.09613 | 0.086975 | 0.068665 | 0.15106 | 121.0236 | 120.5887 | 0.16022
11490.0469 | 0.061035 | 0.25421 | -0.23605 | -0.22217 | -0.1944 | -0.27985 | -0.099335 | 0.1831 | 0.13275 | 0.16479 | 0.12817 | 0.13733 | -0.064087 | 0.064087 | 0.045776 | 10.5647 | 34.9989 | -1.5936 | -0.4689 | 1.4334 | 0.34332 | 0.69122 | 0.10529 | 2.8336 | 2.7328 | -2.2476 | -2.2018 | 121.2158 | 116.8213 | 4.6097
11491.8438 | 0.061035 | 0.24674 | -0.23392 | -0.24246 | -0.18799 | -0.27771 | -0.12283 | 0.082397 | 0.032043 | 0.073242 | 0.041199 | 0.10529 | -0.041199 | 0.10986 | 0.045776 | 0.012817 | 0.068359 | -0.50201 | -0.13458 | -0.025635 | 0.009155 | 0.09613 | 0.009155 | 0.064087 | 0.050354 | 0.050354 | 0.10529 | 121.756 | 121.6599 | 0.12817
11493.5781 | 0.045776 | 0.2243 | -0.2179 | -0.23819 | -0.17944 | -0.2478 | -0.12497 | 0.10986 | -0.009155 | 0.045776 | 0.059509 | 0.13275 | 0.009155 | 0.13733 | 0.045776 | 0.16556 | 0.8374 | -0.5191 | -0.10788 | -0.026703 | 0 | 0.059509 | -0.041199 | 0.10529 | 0.11902 | 0.036621 | 0.10529 | 122.0535 | 121.6415 | 0.13275
11495.375 | 0.045776 | 0.22217 | -0.22644 | -0.22644 | -0.19119 | -0.25635 | -0.11429 | 0.022888 | -0.086975 | -0.036621 | -0.004578 | 0.14648 | -0.018311 | 0.14191 | 0.030518 | 0.024567 | 0.021362 | -0.49347 | -0.11215 | -0.042725 | -0.050354 | 0 | -0.10071 | 0.09613 | 0.073242 | 0.068665 | 0.13733 | 122.0123 | 121.7926 | 0.086975
11497.1562 | 0.061035 | 0.26489 | -0.23605 | -0.22537 | -0.19119 | -0.29373 | -0.12924 | 0.1236 | 0.10986 | 0.11902 | 0.086975 | 0.11444 | -0.022888 | 0.11444 | 0.091553 | 0.002136 | -0.002136 | -0.5127 | -0.12817 | -0.026703 | 0.068665 | 0.18768 | 0.073242 | 0.064087 | 0.045776 | 0.032043 | 0.10071 | 121.9894 | 121.8018 | 0.12817
11498.9375 | 0.061035 | 0.26062 | -0.23605 | -0.24567 | -0.20081 | -0.30334 | -0.13031 | 0.10071 | 0.07782 | 0.11444 | 0.15564 | 0.16937 | -0.07782 | 0.059509 | 0.045776 | 12.7373 | 34.9989 | -1.9643 | -0.33539 | 1.5028 | 0.58136 | 0.93384 | -0.036621 | 2.774 | 2.6733 | -2.124 | -2.0737 | 121.2296 | 118.0618 | 3.2501
11500.6719 | 0.045776 | 0.26703 | -0.22537 | -0.23498 | -0.18265 | -0.27344 | -0.13779 | 0.11444 | 0.068665 | 0.11444 | 0.073242 | 0.091553 | -0.050354 | 0.10529 | 0.061035 | 0.027771 | -0.018158 | -0.50415 | -0.13031 | -0.032043 | 0.045776 | 0.10986 | 0.022888 | 0.054932 | 0.041199 | 0.036621 | 0.09613 | 121.6141 | 121.4355 | 0.11902
11502.4531 | 0.045776 | 0.22537 | -0.22324 | -0.24567 | -0.18478 | -0.22858 | -0.11429 | 0.1236 | 0.013733 | 0.041199 | 0.045776 | 0.11444 | 0 | 0.15564 | 0.045776 | 0.053406 | 0.008545 | -0.49561 | -0.10681 | -0.043793 | 0 | 0.064087 | -0.054932 | 0.073242 | 0.073242 | 0.050354 | 0.10986 | 121.8887 | 121.6049 | 0.086975
11504.25 | 0.045776 | 0.2179 | -0.23071 | -0.23285 | -0.1944 | -0.25528 | -0.09613 | 0.022888 | -0.082397 | -0.032043 | 0 | 0.14191 | 0.018311 | 0.14191 | 0.076294 | 0.040588 | 0.008545 | -0.49347 | -0.11322 | -0.030975 | -0.064087 | 0.009155 | -0.11444 | 0.091553 | 0.07782 | 0.064087 | 0.14191 | 121.8933 | 121.637 | 0.09613
11505.9688 | 0.045776 | 0.26169 | -0.22964 | -0.23605 | -0.20401 | -0.29053 | -0.11856 | 0.09613 | 0.059509 | 0.11444 | 0.054932 | 0.10986 | -0.027466 | 0.11902 | 0.076294 | 0.035248 | 0.002136 | -0.49667 | -0.11963 | -0.032043 | 0.041199 | 0.09613 | 0.009155 | 0.054932 | 0.050354 | 0.041199 | 0.091553 | 121.8704 | 121.7377 | 0.12817
11507.75 | 0.061035 | 0.25848 | -0.22964 | -0.24033 | -0.18265 | -0.26916 | -0.10895 | 0.14191 | 0.073242 | 0.12817 | 0.086975 | 0.10529 | -0.041199 | 0.09613 | 0.061035 | 0.054474 | -0.008545 | -0.49561 | -0.13351 | -0.024567 | 0.068665 | 0.12817 | 0.032043 | 0.032043 | 0.054932 | 0.041199 | 0.086975 | 121.5317 | 121.3486 | 0.11902
11509.5469 | 0.045776 | 0.23498 | -0.21576 | -0.2446 | -0.18906 | -0.25955 | -0.11749 | 0.15564 | 0.068665 | 0.1236 | 0.091553 | 0.07782 | -0.054932 | 0.086975 | 0.076294 | 0.088654 | 0.088654 | -0.48599 | -0.15915 | -0.006409 | 0.073242 | 0.12817 | 0.032043 | 0.027466 | 0.022888 | 0.041199 | 0.091553 | 121.7743 | 121.5775 | 0.10529
11511.3438 | 0.061035 | 0.22537 | -0.22644 | -0.2446 | -0.1976 | -0.26916 | -0.11322 | 0.13733 | 0.082397 | 0.11902 | 0.086975 | 0.10529 | -0.050354 | 0.09613 | 0.061035 | -0.038452 | -0.05661 | -0.47745 | -0.1239 | -0.044861 | 0.073242 | 0.1236 | 0.032043 | 0.073242 | 0.045776 | 0.036621 | 0.068665 | 121.5042 | 121.4767 | 0.12817
11513.125 | 0.061035 | 0.23819 | -0.22003 | -0.23605 | -0.18692 | -0.28198 | -0.12176 | 0.15106 | 0.09613 | 0.13733 | 0.09613 | 0.1236 | -0.027466 | 0.10529 | 0.045776 | -0.041656 | -0.055542 | -0.47424 | -0.13138 | -0.044861 | 0.045776 | 0.17853 | 0.045776 | 0.036621 | 0.041199 | 0.041199 | 0.11444 | 121.6553 | 121.5546 | 0.12817
11514.8594 | 0.061035 | 0.23712 | -0.23392 | -0.24994 | -0.18372 | -0.27451 | -0.1207 | 0.13733 | 0.086975 | 0.13275 | 0.10071 | 0.10986 | -0.027466 | 0.10071 | 0.061035 | -0.046997 | -0.052338 | -0.46783 | -0.1239 | -0.050201 | 0.050354 | 0.16022 | 0.050354 | 0.059509 | 0.054932 | 0.059509 | 0.09613 | 121.6827 | 121.6232 | 0.12817
11516.6562 | 0.030518 | 0.22751 | -0.21683 | -0.23392 | -0.19119 | -0.23605 | -0.11108 | 0.13275 | 0.018311 | 0.041199 | 0.041199 | 0.13733 | -0.013733 | 0.11444 | 0.061035 | -0.019226 | -0.046997 | -0.46463 | -0.10254 | -0.052338 | 0.009155 | 0.050354 | -0.059509 | 0.07782 | 0.073242 | 0.086975 | 0.13733 | 121.8384 | 121.6095 | 0.11444
11518.4531 | 0.061035 | 0.24674 | -0.2446 | -0.24139 | -0.19012 | -0.29694 | -0.11643 | 0.10529 | 0.09613 | 0.11902 | 0.082397 | 0.11444 | -0.027466 | 0.11444 | 0.061035 | -0.046997 | -0.053406 | -0.49027 | -0.12924 | -0.03418 | 0.064087 | 0.17853 | 0.082397 | 0.050354 | 0.045776 | 0.013733 | 0.10986 | 121.843 | 121.6599 | 0.1236
11520.2344 | 0.045776 | 0.23071 | -0.22324 | -0.23712 | -0.19226 | -0.24033 | -0.11749 | 0.050354 | -0.068665 | -0.018311 | 0.004578 | 0.14648 | 0 | 0.12817 | 0.076294 | -0.01709 | -0.05127 | -0.47211 | -0.10895 | -0.05127 | -0.036621 | 0.004578 | -0.073242 | 0.10071 | 0.07782 | 0.059509 | 0.14191 | 121.9345 | 121.6415 | 0.09613
11522.0469 | 0.015259 | 0.24887 | -0.22858 | -0.21896 | -0.1976 | -0.27878 | -0.10895 | 0.09613 | 0.073242 | 0.10071 | 0.064087 | 0.10529 | -0.045776 | 0.10529 | 0.045776 | -0.040588 | -0.055542 | -0.48599 | -0.12711 | -0.040588 | 0.032043 | 0.11444 | 0.013733 | 0.059509 | 0.041199 | 0.022888 | 0.10986 | 121.8384 | 121.7056 | 0.14191
11523.8438 | 0.061035 | 0.23178 | -0.2179 | -0.2446 | -0.18158 | -0.24567 | -0.10895 | 0.10071 | 0.009155 | 0.041199 | 0.059509 | 0.12817 | -0.013733 | 0.15106 | 0.045776 | -0.014954 | -0.05127 | -0.4657 | -0.11536 | -0.043793 | 0.013733 | 0.086975 | -0.050354 | 0.09613 | 0.064087 | 0.064087 | 0.13275 | 121.9803 | 121.669 | 0.07782
11525.5781 | 0.076294 | 0.21683 | -0.20828 | -0.23712 | -0.18265 | -0.24674 | -0.11108 | 0.09613 | 0.004578 | 0.032043 | 0.054932 | 0.12817 | -0.004578 | 0.14191 | 0.061035 | -0.024567 | -0.057678 | -0.45502 | -0.10681 | -0.053406 | -0.022888 | 0.050354 | -0.082397 | 0.082397 | 0.073242 | 0.059509 | 0.12817 | 121.9711 | 121.7285 | 0.09613
11527.375 | 0.045776 | 0.23926 | -0.22537 | -0.23285 | -0.18478 | -0.24887 | -0.11322 | 0.09613 | 0.036621 | 0.045776 | 0.054932 | 0.1236 | -0.009155 | 0.12817 | 0.076294 | -0.024567 | -0.037384 | -0.47638 | -0.11429 | -0.037384 | 0 | 0.082397 | -0.064087 | 0.073242 | 0.073242 | 0.059509 | 0.13733 | 121.9757 | 121.7422 | 0.10529
11529.0938 | 0.045776 | 0.23178 | -0.22217 | -0.26916 | -0.1709 | -0.27664 | -0.1207 | 0.041199 | 0.022888 | 0.050354 | 0.054932 | 0.14191 | -0.009155 | 0.1236 | 0.045776 | -0.028839 | -0.041656 | -0.48492 | -0.1442 | -0.032043 | -0.064087 | 0.082397 | -0.059509 | 0.091553 | 0.073242 | 0.064087 | 0.14191 | 121.9208 | 121.7834 | 0.11902
11530.8906 | 0.061035 | 0.23712 | -0.22644 | -0.24353 | -0.18799 | -0.24887 | -0.11002 | 0.09613 | 0.018311 | 0.027466 | 0.041199 | 0.15106 | -0.018311 | 0.14191 | 0.061035 | -0.016022 | -0.043793 | -0.47318 | -0.11215 | -0.040588 | -0.018311 | 0.068665 | -0.059509 | 0.10986 | 0.059509 | 0.041199 | 0.13733 | 122.0123 | 121.7514 | 0.086975
11532.6406 | 0.061035 | 0.24674 | -0.23712 | -0.24246 | -0.19333 | -0.28305 | -0.12817 | 0.054932 | 0.054932 | 0.082397 | 0.050354 | 0.11902 | -0.022888 | 0.13733 | 0.030518 | -0.044861 | -0.048065 | -0.48172 | -0.13565 | -0.046997 | -0.032043 | 0.086975 | -0.036621 | 0.07782 | 0.082397 | 0.059509 | 0.13733 | 121.9437 | 121.8018 | 0.11444
11534.4375 | 0.045776 | 0.23819 | -0.24567 | -0.24887 | -0.18478 | -0.28625 | -0.13886 | 0.09613 | 0.11902 | 0.14648 | 0.09613 | 0.091553 | -0.032043 | 0.10986 | 0.076294 | -0.035248 | -0.050201 | -0.48599 | -0.13245 | -0.040588 | 0.041199 | 0.18768 | 0.073242 | 0.045776 | 0.041199 | 0.027466 | 0.10529 | 121.9849 | 121.7926 | 0.1236
11536.1719 | 0.076294 | 0.22858 | -0.22858 | -0.23071 | -0.17838 | -0.24567 | -0.11963 | 0.07782 | -0.018311 | 0.018311 | 0.036621 | 0.13275 | 0.004578 | 0.13275 | 0.045776 | -0.020294 | -0.059814 | -0.48172 | -0.10574 | -0.03952 | -0.050354 | 0.022888 | -0.10071 | 0.082397 | 0.064087 | 0.068665 | 0.15106 | 122.0306 | 121.8201 | 0.10071
11537.9531 | 0.061035 | 0.2446 | -0.21362 | -0.25955 | -0.1709 | -0.2713 | -0.11536 | 0.013733 | -0.013733 | 0.009155 | 0.009155 | 0.1236 | 0.009155 | 0.15564 | 0.030518 | -0.026703 | -0.057678 | -0.48172 | -0.13565 | -0.046997 | -0.059509 | 0.054932 | -0.064087 | 0.09613 | 0.073242 | 0.07782 | 0.14191 | 121.9849 | 121.8475 | 0.10986
11539.75 | 0.045776 | 0.2179 | -0.22644 | -0.23926 | -0.1944 | -0.24674 | -0.1239 | 0.09613 | 0.018311 | 0.036621 | 0.050354 | 0.13733 | -0.009155 | 0.13733 | 0.076294 | -0.023499 | -0.048065 | -0.48813 | -0.11215 | -0.046997 | -0.009155 | 0.082397 | -0.036621 | 0.07782 | 0.064087 | 0.073242 | 0.1236 | 122.1085 | 121.8292 | 0.091553
11541.4844 | 0.091553 | 0.21896 | -0.2179 | -0.24994 | -0.19226 | -0.26596 | -0.11749 | 0.036621 | -0.050354 | -0.013733 | 0.027466 | 0.15106 | 0 | 0.16022 | 0.030518 | -0.020294 | -0.050201 | -0.48172 | -0.12817 | -0.041656 | -0.064087 | 0.032043 | -0.068665 | 0.10071 | 0.091553 | 0.082397 | 0.13733 | 122.1039 | 121.8338 | 0.091553
11543.2656 | 0.061035 | 0.25528 | -0.22324 | -0.23178 | -0.19546 | -0.29694 | -0.12817 | 0.059509 | 0.036621 | 0.073242 | 0.064087 | 0.11444 | -0.036621 | 0.10071 | 0.061035 | -0.053406 | -0.05661 | -0.48386 | -0.13245 | -0.025635 | 0.013733 | 0.10529 | 0.004578 | 0.054932 | 0.064087 | 0.059509 | 0.11444 | 122.0169 | 121.8796 | 0.14191
11545.0625 | 0.061035 | 0.2179 | -0.21362 | -0.23498 | -0.19119 | -0.24033 | -0.10574 | 0.10071 | 0 | 0.022888 | 0.022888 | 0.13733 | -0.004578 | 0.10986 | 0.045776 | -0.01709 | -0.065155 | -0.47852 | -0.11429 | -0.038452 | -0.050354 | 0.036621 | -0.086975 | 0.082397 | 0.073242 | 0.059509 | 0.12817 | 122.1085 | 121.875 | 0.086975
11546.875 | 0.045776 | 0.22858 | -0.2243 | -0.23605 | -0.18692 | -0.25207 | -0.11963 | 0.082397 | 0 | 0.036621 | 0.045776 | 0.12817 | 0 | 0.13275 | 0.030518 | -0.03418 | -0.054474 | -0.47531 | -0.11536 | -0.044861 | -0.013733 | 0.09613 | -0.050354 | 0.068665 | 0.082397 | 0.059509 | 0.13733 | 122.168 | 121.843 | 0.07782
11548.6094 | 0.076294 | 0.25635 | -0.22964 | -0.24353 | -0.18265 | -0.28732 | -0.12711 | 0.09613 | 0.050354 | 0.10071 | 0.073242 | 0.10986 | -0.041199 | 0.10529 | 0.045776 | -0.042725 | -0.057678 | -0.47638 | -0.13458 | -0.027771 | 0.036621 | 0.10071 | 0.004578 | 0.064087 | 0.041199 | 0.054932 | 0.10986 | 122.0398 | 121.9299 | 0.11902
11550.3906 | 0.076294 | 0.23926 | -0.22324 | -0.23285 | -0.18692 | -0.24887 | -0.11749 | 0.059509 | -0.041199 | 0.004578 | 0.009155 | 0.15106 | -0.027466 | 0.13733 | 0.061035 | -0.02243 | -0.059814 | -0.47318 | -0.11643 | -0.029907 | -0.009155 | 0.036621 | -0.041199 | 0.068665 | 0.073242 | 0.054932 | 0.10986 | 122.2046 | 121.8887 | 0.091553
11552.1719 | 0.045776 | 0.2179 | -0.21896 | -0.24994 | -0.18372 | -0.25421 | -0.12176 | 0.064087 | -0.032043 | 0.009155 | 0.036621 | 0.13733 | 0 | 0.13275 | 0.061035 | -0.01709 | -0.05127 | -0.46783 | -0.12497 | -0.041656 | -0.032043 | 0.073242 | -0.032043 | 0.086975 | 0.073242 | 0.059509 | 0.12817 | 122.1909 | 121.8933 | 0.07782
11553.8906 | 0.061035 | 0.23605 | -0.22324 | -0.24139 | -0.1944 | -0.25101 | -0.11429 | 0.064087 | -0.041199 | 0.018311 | 0.027466 | 0.13733 | -0.004578 | 0.1236 | 0.045776 | -0.040588 | -0.05127 | -0.48065 | -0.11429 | -0.037384 | -0.004578 | 0.054932 | -0.022888 | 0.07782 | 0.064087 | 0.045776 | 0.10529 | 122.2275 | 121.8933 | 0.11444
11555.6875 | 0.091553 | 0.24033 | -0.22324 | -0.23071 | -0.18799 | -0.27344 | -0.1207 | 0.13275 | 0.059509 | 0.11902 | 0.086975 | 0.082397 | -0.045776 | 0.09613 | 0.061035 | -0.03418 | -0.065155 | -0.47211 | -0.13351 | -0.03418 | 0.059509 | 0.1236 | 0.032043 | 0.041199 | 0.041199 | 0.050354 | 0.086975 | 122.2046 | 121.9391 | 0.10071
11557.4844 | 0.061035 | 0.24139 | -0.2211 | -0.26276 | -0.19119 | -0.28839 | -0.13138 | 0.12817 | 0.11444 | 0.15106 | 0.09613 | 0.10071 | -0.045776 | 0.091553 | 0.076294 | -0.057678 | -0.054474 | -0.48492 | -0.14313 | -0.038452 | 0.050354 | 0.18768 | 0.064087 | 0.041199 | 0.041199 | 0.036621 | 0.086975 | 122.1451 | 121.9299 | 0.10986
11559.2656 | 0.061035 | 0.27023 | -0.24246 | -0.24674 | -0.20294 | -0.28305 | -0.11856 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.10986 | -0.036621 | 0.10071 | 0.076294 | -0.043793 | -0.059814 | -0.48065 | -0.13565 | -0.035248 | 0.073242 | 0.19226 | 0.068665 | 0.045776 | 0.032043 | 0.050354 | 0.10529 | 122.1542 | 121.9528 | 0.12817
11560.9844 | 0.045776 | 0.26489 | -0.24139 | -0.22644 | -0.19546 | -0.28198 | -0.12817 | 0.07782 | 0.027466 | 0.068665 | 0.054932 | 0.10986 | -0.036621 | 0.086975 | 0.061035 | -0.043793 | -0.070496 | -0.48279 | -0.13031 | -0.032043 | 0.004578 | 0.082397 | 0.004578 | 0.050354 | 0.050354 | 0.032043 | 0.10986 | 122.1222 | 121.994 | 0.10529
11562.7812 | 0.076294 | 0.24567 | -0.22858 | -0.2243 | -0.19546 | -0.25207 | -0.12924 | 0.041199 | -0.045776 | -0.013733 | 0.018311 | 0.14191 | 0.004578 | 0.13733 | 0.045776 | -0.018158 | -0.067291 | -0.48065 | -0.11002 | -0.046997 | -0.064087 | 0.036621 | -0.073242 | 0.091553 | 0.086975 | 0.059509 | 0.13733 | 122.2366 | 121.9528 | 0.09613
11564.5781 | 0.045776 | 0.22003 | -0.20935 | -0.23498 | -0.19226 | -0.24887 | -0.10361 | 0.10071 | 0.036621 | 0.027466 | 0.041199 | 0.14648 | 0.009155 | 0.13733 | 0.045776 | -0.033112 | -0.060883 | -0.47531 | -0.10681 | -0.040588 | 0.013733 | 0.07782 | -0.050354 | 0.073242 | 0.064087 | 0.064087 | 0.12817 | 122.2366 | 121.9757 | 0.091553
11566.2969 | 0.061035 | 0.2179 | -0.23285 | -0.24887 | -0.18478 | -0.25848 | -0.11215 | 0.036621 | -0.059509 | -0.013733 | -0.009155 | 0.13733 | -0.018311 | 0.12817 | 0.045776 | -0.029907 | -0.05127 | -0.47424 | -0.12283 | -0.036316 | -0.041199 | 0.009155 | -0.091553 | 0.09613 | 0.091553 | 0.082397 | 0.1236 | 122.2687 | 121.9574 | 0.086975
11568.0781 | 0.061035 | 0.1976 | -0.21576 | -0.26062 | -0.1944 | -0.23712 | -0.10681 | 0.073242 | 0 | 0.036621 | 0.041199 | 0.13733 | 0.018311 | 0.13275 | 0.045776 | -0.021362 | -0.040588 | -0.46997 | -0.11536 | -0.05127 | -0.036621 | 0.032043 | -0.086975 | 0.086975 | 0.07782 | 0.068665 | 0.1236 | 122.2275 | 121.9666 | 0.082397
11569.875 | 0.061035 | 0.24353 | -0.22751 | -0.23178 | -0.18692 | -0.27451 | -0.11536 | 0.13733 | 0.07782 | 0.10529 | 0.082397 | 0.10529 | -0.041199 | 0.091553 | 0.061035 | -0.032043 | -0.063019 | -0.46677 | -0.12711 | -0.033112 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.054932 | 0.022888 | 0.091553 | 122.2549 | 121.9894 | 0.09613
11571.625 | 0.045776 | 0.2179 | -0.22324 | -0.22858 | -0.18265 | -0.25635 | -0.12283 | 0.032043 | -0.036621 | -0.013733 | 0.018311 | 0.13733 | 0.004578 | 0.12817 | 0.061035 | -0.021362 | -0.05661 | -0.46783 | -0.11002 | -0.046997 | -0.068665 | 0.004578 | -0.11444 | 0.086975 | 0.07782 | 0.086975 | 0.14191 | 122.2229 | 121.994 | 0.091553
11573.4219 | 0.045776 | 0.2211 | -0.23071 | -0.22537 | -0.18158 | -0.25955 | -0.11643 | 0.050354 | -0.004578 | 0.013733 | 0.041199 | 0.13733 | -0.004578 | 0.14191 | 0.045776 | -0.020294 | -0.068359 | -0.48172 | -0.11749 | -0.041656 | -0.027466 | 0.082397 | -0.036621 | 0.07782 | 0.073242 | 0.059509 | 0.1236 | 122.3007 | 121.9803 | 0.091553
11575.2031 | 0.061035 | 0.22644 | -0.23071 | -0.23285 | -0.18585 | -0.26062 | -0.12176 | 0.027466 | -0.059509 | -0.013733 | 0.009155 | 0.13733 | 0.004578 | 0.1236 | 0.045776 | -0.026703 | -0.061951 | -0.47211 | -0.11856 | -0.03418 | -0.045776 | 0 | -0.068665 | 0.091553 | 0.07782 | 0.073242 | 0.11902 | 122.3099 | 121.9986 | 0.086975
11577.0156 | 0.061035 | 0.25207 | -0.24033 | -0.24353 | -0.1976 | -0.30121 | -0.12283 | 0.041199 | 0.027466 | 0.07782 | 0.059509 | 0.10071 | -0.045776 | 0.091553 | 0.030518 | -0.044861 | -0.054474 | -0.4892 | -0.12817 | -0.028839 | -0.013733 | 0.086975 | 0.027466 | 0.068665 | 0.054932 | 0.032043 | 0.10529 | 122.2 | 122.0398 | 0.10529
11578.75 | 0.045776 | 0.2478 | -0.22644 | -0.25848 | -0.19546 | -0.28839 | -0.12604 | 0.045776 | 0.041199 | 0.11444 | 0.073242 | 0.11444 | -0.036621 | 0.09613 | 0.061035 | -0.045929 | -0.054474 | -0.48492 | -0.13886 | -0.044861 | 0.036621 | 0.12817 | 0.050354 | 0.054932 | 0.041199 | 0.045776 | 0.10071 | 122.2275 | 122.0398 | 0.11902
11580.5469 | 0.061035 | 0.24567 | -0.22964 | -0.24994 | -0.18692 | -0.27985 | -0.1239 | 0.11902 | 0.068665 | 0.1236 | 0.07782 | 0.10071 | -0.036621 | 0.09613 | 0.061035 | -0.048065 | -0.065155 | -0.48279 | -0.12924 | -0.043793 | 0.064087 | 0.10529 | 0.013733 | 0.045776 | 0.045776 | 0.036621 | 0.10986 | 122.1909 | 122.0581 | 0.1236
11582.3438 | 0.045776 | 0.22751 | -0.22003 | -0.25848 | -0.18372 | -0.26062 | -0.11856 | 0.041199 | -0.054932 | -0.013733 | 0.018311 | 0.13733 | -0.004578 | 0.14191 | 0.030518 | -0.021362 | -0.050201 | -0.47318 | -0.13992 | -0.045929 | -0.054932 | 0.041199 | -0.086975 | 0.11444 | 0.082397 | 0.082397 | 0.13275 | 122.2458 | 122.0535 | 0.11902
11584.0625 | 0.030518 | 0.26276 | -0.22324 | -0.23178 | -0.18585 | -0.28519 | -0.12711 | 0.086975 | 0.036621 | 0.086975 | 0.068665 | 0.11902 | -0.032043 | 0.10986 | 0.061035 | -0.042725 | -0.060883 | -0.48599 | -0.12176 | -0.033112 | 0.027466 | 0.12817 | 0.050354 | 0.059509 | 0.041199 | 0.050354 | 0.082397 | 122.2504 | 122.0627 | 0.11444
11585.8594 | 0.061035 | 0.23926 | -0.23285 | -0.24567 | -0.20508 | -0.28412 | -0.13138 | 0.073242 | 0.009155 | 0.082397 | 0.059509 | 0.11444 | -0.036621 | 0.11902 | 0.030518 | -0.040588 | -0.05127 | -0.48492 | -0.14206 | -0.050201 | 0.013733 | 0.086975 | 0.004578 | 0.059509 | 0.059509 | 0.018311 | 0.11444 | 122.2595 | 122.0627 | 0.12817
11587.5938 | 0.061035 | 0.24353 | -0.22537 | -0.23392 | -0.18158 | -0.26062 | -0.11643 | 0.16022 | 0.064087 | 0.1236 | 0.091553 | 0.10071 | -0.050354 | 0.091553 | 0.045776 | -0.030975 | -0.066223 | -0.47638 | -0.1239 | -0.045929 | 0.07782 | 0.11902 | 0.041199 | 0.045776 | 0.041199 | 0.027466 | 0.09613 | 122.2366 | 122.0856 | 0.13733
11589.3906 | 0.045776 | 0.23605 | -0.22751 | -0.24353 | -0.1976 | -0.24246 | -0.1207 | 0.068665 | -0.068665 | -0.009155 | 0.013733 | 0.15106 | -0.004578 | 0.15106 | 0.045776 | -0.009613 | -0.061951 | -0.47745 | -0.12283 | -0.049133 | -0.036621 | 0.032043 | -0.086975 | 0.10529 | 0.07782 | 0.073242 | 0.1236 | 122.3236 | 122.0398 | 0.091553
11591.1719 | 0.045776 | 0.22003 | -0.22324 | -0.24567 | -0.18158 | -0.24674 | -0.12604 | 0.045776 | -0.036621 | -0.009155 | 0.027466 | 0.14648 | 0.022888 | 0.13733 | 0.061035 | -0.021362 | -0.045929 | -0.47638 | -0.11215 | -0.055542 | -0.050354 | 0.059509 | -0.07782 | 0.09613 | 0.073242 | 0.091553 | 0.11902 | 122.3557 | 122.049 | 0.068665
11592.9688 | 0.061035 | 0.22858 | -0.22858 | -0.25101 | -0.18051 | -0.27237 | -0.11856 | 0.036621 | -0.018311 | 0 | 0.004578 | 0.14191 | 0.013733 | 0.15106 | 0.045776 | -0.030975 | -0.061951 | -0.47958 | -0.11536 | -0.037384 | -0.068665 | 0.050354 | -0.07782 | 0.10529 | 0.082397 | 0.091553 | 0.13733 | 122.2778 | 122.113 | 0.1236
11594.7031 | 0.061035 | 0.23605 | -0.23071 | -0.22644 | -0.19119 | -0.2713 | -0.11643 | 0.1236 | 0.091553 | 0.13275 | 0.086975 | 0.082397 | -0.050354 | 0.07782 | 0.076294 | -0.024567 | -0.064087 | -0.47958 | -0.12711 | -0.035248 | 0.07782 | 0.14648 | 0.050354 | 0.032043 | 0.027466 | 0.022888 | 0.082397 | 122.287 | 122.0947 | 0.10071
11596.5 | 0.030518 | 0.24567 | -0.23285 | -0.23926 | -0.17944 | -0.28946 | -0.11215 | 0.064087 | 0.022888 | 0.082397 | 0.059509 | 0.10071 | -0.045776 | 0.10986 | 0.061035 | -0.035248 | -0.064087 | -0.48492 | -0.13138 | -0.03418 | 0.027466 | 0.091553 | 0.018311 | 0.059509 | 0.059509 | 0.018311 | 0.10529 | 122.2458 | 122.1222 | 0.1236
11598.2344 | 0.030518 | 0.24139 | -0.24139 | -0.24033 | -0.18265 | -0.27557 | -0.12817 | 0.073242 | 0.036621 | 0.082397 | 0.068665 | 0.11902 | -0.036621 | 0.11444 | 0.061035 | -0.042725 | -0.066223 | -0.48172 | -0.13245 | -0.037384 | 0.036621 | 0.13275 | 0.041199 | 0.068665 | 0.045776 | 0.041199 | 0.086975 | 122.287 | 122.1176 | 0.1236
11600.0156 | 0.045776 | 0.22217 | -0.22003 | -0.2478 | -0.19226 | -0.24033 | -0.11536 | 0.11902 | 0 | 0.036621 | 0.050354 | 0.13733 | -0.009155 | 0.13733 | 0.061035 | -0.024567 | -0.057678 | -0.46997 | -0.11215 | -0.059814 | 0.009155 | 0.091553 | -0.064087 | 0.082397 | 0.073242 | 0.073242 | 0.14191 | 122.3923 | 122.0764 | 0.091553
11601.8125 | 0.061035 | 0.21683 | -0.22751 | -0.2446 | -0.18158 | -0.24353 | -0.10361 | 0.054932 | -0.059509 | -0.027466 | 0 | 0.14191 | -0.004578 | 0.12817 | 0.045776 | -0.016022 | -0.060883 | -0.46783 | -0.10361 | -0.029907 | -0.041199 | -0.004578 | -0.086975 | 0.086975 | 0.059509 | 0.064087 | 0.13275 | 122.4014 | 122.0856 | 0.07782
11603.5469 | 0.061035 | 0.23605 | -0.22537 | -0.23071 | -0.17517 | -0.2681 | -0.12711 | 0.022888 | -0.013733 | -0.004578 | 0.013733 | 0.16937 | 0.004578 | 0.15106 | 0.061035 | -0.03952 | -0.053406 | -0.48492 | -0.11215 | -0.03418 | -0.068665 | 0.041199 | -0.091553 | 0.10529 | 0.068665 | 0.07782 | 0.12817 | 122.3328 | 122.168 | 0.11444
11605.3281 | 0.061035 | 0.25314 | -0.22964 | -0.23498 | -0.17517 | -0.28519 | -0.11536 | 0.10071 | 0.091553 | 0.10529 | 0.091553 | 0.091553 | -0.036621 | 0.10986 | 0.076294 | -0.036316 | -0.071564 | -0.4924 | -0.11963 | -0.035248 | -0.004578 | 0.13733 | 0.013733 | 0.064087 | 0.054932 | 0.054932 | 0.11902 | 122.2687 | 122.1588 | 0.12817
11607.1094 | 0.061035 | 0.22964 | -0.22964 | -0.23498 | -0.19653 | -0.25314 | -0.11536 | 0.054932 | -0.054932 | -0.009155 | 0.009155 | 0.15564 | -0.022888 | 0.11902 | 0.061035 | -0.021362 | -0.054474 | -0.47424 | -0.11002 | -0.046997 | -0.009155 | 0.027466 | -0.045776 | 0.082397 | 0.059509 | 0.045776 | 0.11902 | 122.4243 | 122.1039 | 0.091553
11608.8594 | 0.061035 | 0.24139 | -0.23926 | -0.24033 | -0.18158 | -0.27344 | -0.11749 | 0.041199 | -0.036621 | -0.018311 | 0.004578 | 0.14191 | -0.004578 | 0.14648 | 0.030518 | -0.028839 | -0.064087 | -0.49027 | -0.12924 | -0.029907 | -0.068665 | 0.036621 | -0.068665 | 0.091553 | 0.091553 | 0.068665 | 0.13733 | 122.319 | 122.1725 | 0.10071
11610.6562 | 0.061035 | 0.24887 | -0.22324 | -0.2243 | -0.17944 | -0.24674 | -0.10681 | 0.032043 | -0.068665 | -0.013733 | 0.004578 | 0.14648 | 0 | 0.14191 | 0.045776 | -0.014954 | -0.052338 | -0.47852 | -0.11429 | -0.040588 | -0.050354 | -0.004578 | -0.082397 | 0.091553 | 0.068665 | 0.059509 | 0.11902 | 122.4106 | 122.168 | 0.082397
11612.4375 | 0.061035 | 0.26916 | -0.2713 | -0.22964 | -0.18478 | -0.30548 | -0.1207 | 0.050354 | 0.036621 | 0.091553 | 0.086975 | 0.10986 | -0.036621 | 0.1236 | 0.045776 | -0.041656 | -0.069427 | -0.47852 | -0.14206 | -0.035248 | 0.013733 | 0.11902 | 0.032043 | 0.054932 | 0.050354 | 0.032043 | 0.10986 | 122.3465 | 122.1588 | 0.11902
11614.2188 | 0.061035 | 0.24246 | -0.22858 | -0.25742 | -0.18478 | -0.27557 | -0.12497 | 0.14191 | 0.10986 | 0.12817 | 0.09613 | 0.10529 | -0.027466 | 0.10071 | 0.045776 | -0.041656 | -0.064087 | -0.48492 | -0.14633 | -0.03418 | 0.064087 | 0.20142 | 0.068665 | 0.050354 | 0.045776 | 0.027466 | 0.10071 | 122.3145 | 122.1909 | 0.10529
11615.9688 | 0.030518 | 0.22751 | -0.21469 | -0.25421 | -0.19333 | -0.24353 | -0.11643 | 0.10071 | -0.018311 | 0.027466 | 0.054932 | 0.13275 | 0 | 0.14191 | 0.061035 | -0.009613 | -0.045929 | -0.4657 | -0.11856 | -0.052338 | 0 | 0.086975 | -0.045776 | 0.09613 | 0.07782 | 0.059509 | 0.12817 | 122.4518 | 122.1497 | 0.082397
11617.75 | 0.061035 | 0.21896 | -0.21576 | -0.24033 | -0.18372 | -0.24139 | -0.10788 | 0.07782 | -0.022888 | 0.009155 | 0.036621 | 0.14191 | -0.013733 | 0.14191 | 0.061035 | -0.024567 | -0.048065 | -0.46783 | -0.11429 | -0.05127 | -0.036621 | 0.027466 | -0.091553 | 0.07782 | 0.059509 | 0.050354 | 0.12817 | 122.4106 | 122.1359 | 0.091553
11619.5469 | 0.045776 | 0.22858 | -0.2211 | -0.2446 | -0.19226 | -0.27985 | -0.11643 | 0.027466 | -0.004578 | 0.022888 | 0.032043 | 0.12817 | -0.009155 | 0.14191 | 0.061035 | -0.037384 | -0.060883 | -0.47531 | -0.13351 | -0.038452 | -0.045776 | 0.045776 | -0.054932 | 0.082397 | 0.073242 | 0.068665 | 0.14191 | 122.3328 | 122.1863 | 0.13275
11621.2656 | 0.061035 | 0.23498 | -0.22858 | -0.24246 | -0.19226 | -0.27664 | -0.11536 | 0.022888 | -0.032043 | -0.009155 | 0.009155 | 0.14191 | -0.004578 | 0.15106 | 0.045776 | -0.020294 | -0.057678 | -0.47318 | -0.12924 | -0.048065 | -0.068665 | 0.054932 | -0.064087 | 0.10529 | 0.10986 | 0.09613 | 0.13733 | 122.3557 | 122.1542 | 0.10529
11623.0625 | 0.045776 | 0.2478 | -0.23498 | -0.24994 | -0.18158 | -0.2681 | -0.12283 | 0.050354 | -0.004578 | 0.027466 | 0.022888 | 0.13733 | -0.009155 | 0.13733 | 0.045776 | -0.029907 | -0.068359 | -0.47424 | -0.1239 | -0.038452 | -0.064087 | 0.068665 | -0.059509 | 0.09613 | 0.091553 | 0.064087 | 0.13733 | 122.3511 | 122.2 | 0.1236
11624.8438 | 0.061035 | 0.26916 | -0.23605 | -0.24353 | -0.20294 | -0.28946 | -0.12176 | 0.091553 | 0.10529 | 0.11902 | 0.086975 | 0.10529 | -0.036621 | 0.09613 | 0.045776 | -0.05127 | -0.067291 | -0.47852 | -0.13886 | -0.044861 | 0.07782 | 0.17853 | 0.091553 | 0.050354 | 0.036621 | 0.032043 | 0.10986 | 122.4014 | 122.2046 | 0.11444
11626.6406 | 0.061035 | 0.23926 | -0.21896 | -0.24887 | -0.19012 | -0.2713 | -0.1207 | 0.086975 | 0.064087 | 0.10071 | 0.064087 | 0.11444 | -0.009155 | 0.10986 | 0.076294 | -0.03418 | -0.052338 | -0.48492 | -0.12817 | -0.05127 | 0.004578 | 0.10529 | -0.022888 | 0.064087 | 0.059509 | 0.059509 | 0.12817 | 122.3236 | 122.2 | 0.12817
11628.4531 | 0.015259 | 0.26062 | -0.23392 | -0.23605 | -0.18158 | -0.27557 | -0.1207 | 0.082397 | 0.050354 | 0.091553 | 0.050354 | 0.10986 | -0.041199 | 0.10529 | 0.045776 | -0.030975 | -0.055542 | -0.48279 | -0.12283 | -0.03952 | 0.036621 | 0.10071 | 0.004578 | 0.036621 | 0.036621 | 0.036621 | 0.09613 | 122.3648 | 122.2366 | 0.12817
11630.2344 | 0.061035 | 0.22751 | -0.21896 | -0.25101 | -0.18372 | -0.26276 | -0.12817 | 0.11902 | 0.07782 | 0.10529 | 0.091553 | 0.10071 | -0.036621 | 0.11444 | 0.061035 | -0.032043 | -0.064087 | -0.46783 | -0.13031 | -0.050201 | 0.013733 | 0.15564 | 0.027466 | 0.054932 | 0.054932 | 0.041199 | 0.11902 | 122.3602 | 122.2137 | 0.11902
11631.9844 | 0.061035 | 0.22324 | -0.2179 | -0.22858 | -0.18692 | -0.24674 | -0.1207 | 0.059509 | -0.050354 | -0.027466 | 0.009155 | 0.13733 | 0.004578 | 0.13275 | 0.061035 | -0.020294 | -0.061951 | -0.48706 | -0.10468 | -0.048065 | -0.068665 | -0.013733 | -0.1236 | 0.09613 | 0.07782 | 0.082397 | 0.11902 | 122.4472 | 122.2092 | 0.10986
11633.7812 | 0.076294 | 0.25528 | -0.23498 | -0.23819 | -0.18692 | -0.28839 | -0.11429 | 0.068665 | 0.032043 | 0.073242 | 0.059509 | 0.11444 | -0.032043 | 0.10071 | 0.091553 | -0.030975 | -0.069427 | -0.47424 | -0.13031 | -0.041656 | 0.009155 | 0.09613 | 0.004578 | 0.045776 | 0.045776 | 0.027466 | 0.09613 | 122.374 | 122.2412 | 0.11444
11635.5781 | 0.061035 | 0.23926 | -0.22644 | -0.25528 | -0.19226 | -0.27344 | -0.11963 | 0.09613 | 0.091553 | 0.10529 | 0.091553 | 0.10986 | -0.036621 | 0.10986 | 0.061035 | -0.038452 | -0.066223 | -0.47958 | -0.13031 | -0.045929 | 0.013733 | 0.13733 | -0.009155 | 0.068665 | 0.059509 | 0.050354 | 0.11444 | 122.3557 | 122.2458 | 0.14648
11637.3281 | 0.045776 | 0.22858 | -0.20721 | -0.23819 | -0.1741 | -0.25207 | -0.1207 | 0.07782 | -0.041199 | -0.009155 | 0.022888 | 0.15106 | 0 | 0.1236 | 0.061035 | -0.019226 | -0.055542 | -0.4689 | -0.10788 | -0.048065 | -0.013733 | 0.022888 | -0.064087 | 0.086975 | 0.068665 | 0.064087 | 0.11444 | 122.5204 | 122.2092 | 0.091553
11639.1094 | 0.061035 | 0.23071 | -0.22537 | -0.26276 | -0.1741 | -0.27237 | -0.11322 | 0.09613 | 0.041199 | 0.07782 | 0.059509 | 0.11902 | -0.027466 | 0.13275 | 0.061035 | -0.033112 | -0.054474 | -0.47318 | -0.11963 | -0.044861 | -0.036621 | 0.068665 | -0.036621 | 0.07782 | 0.068665 | 0.059509 | 0.1236 | 122.3831 | 122.2687 | 0.10071
11640.8594 | 0.045776 | 0.25421 | -0.22858 | -0.23926 | -0.19012 | -0.28198 | -0.12817 | 0.09613 | 0.027466 | 0.082397 | 0.059509 | 0.11444 | -0.027466 | 0.11444 | 0.030518 | -0.03952 | -0.060883 | -0.46783 | -0.12817 | -0.041656 | 0.013733 | 0.09613 | 0.009155 | 0.054932 | 0.054932 | 0.054932 | 0.086975 | 122.4014 | 122.2687 | 0.12817
11642.6562 | 0.030518 | 0.2179 | -0.21469 | -0.24887 | -0.18585 | -0.26276 | -0.1207 | 0.054932 | -0.054932 | 0.009155 | -0.009155 | 0.12817 | 0.009155 | 0.12817 | 0.045776 | -0.020294 | -0.052338 | -0.47211 | -0.12924 | -0.049133 | -0.059509 | 0.036621 | -0.082397 | 0.09613 | 0.073242 | 0.054932 | 0.13733 | 122.4197 | 122.2321 | 0.11444
11644.4531 | 0.061035 | 0.25528 | -0.22964 | -0.24994 | -0.17838 | -0.28839 | -0.1207 | 0.082397 | 0.045776 | 0.07782 | 0.054932 | 0.11902 | 0.009155 | 0.10529 | 0.061035 | -0.040588 | -0.053406 | -0.48492 | -0.13138 | -0.03418 | 0.036621 | 0.12817 | 0.054932 | 0.059509 | 0.068665 | 0.032043 | 0.11444 | 122.4518 | 122.2412 | 0.10071
11646.2344 | 0.045776 | 0.25742 | -0.23498 | -0.23926 | -0.18158 | -0.26703 | -0.12283 | 0.082397 | 0.022888 | 0.07782 | 0.059509 | 0.11902 | -0.032043 | 0.09613 | 0.061035 | -0.026703 | -0.070496 | -0.48706 | -0.1207 | -0.043793 | 0.004578 | 0.10071 | 0.013733 | 0.068665 | 0.050354 | 0.027466 | 0.086975 | 122.4152 | 122.2504 | 0.1236
11647.9688 | 0.076294 | 0.25635 | -0.22751 | -0.20615 | -0.18158 | -0.25955 | -0.12176 | 0.13733 | 0.082397 | 0.10986 | 0.064087 | 0.10529 | -0.018311 | 0.09613 | 0.061035 | -0.041656 | -0.074768 | -0.48813 | -0.12604 | -0.036316 | 0.050354 | 0.10529 | 0.013733 | 0.050354 | 0.027466 | 0.045776 | 0.10529 | 122.3923 | 122.2733 | 0.12817
11649.75 | 0.045776 | 0.24674 | -0.23285 | -0.23819 | -0.19333 | -0.24887 | -0.10788 | 0.14191 | 0.027466 | 0.086975 | 0.082397 | 0.11444 | -0.041199 | 0.09613 | 0.061035 | -0.014954 | -0.064087 | -0.47745 | -0.11429 | -0.045929 | 0.07782 | 0.12817 | 0.032043 | 0.032043 | 0.022888 | 0.027466 | 0.09613 | 122.5342 | 122.2275 | 0.07782
11651.5469 | 0.045776 | 0.23712 | -0.23178 | -0.24139 | -0.18478 | -0.27344 | -0.11322 | 0.11444 | 0.086975 | 0.12817 | 0.09613 | 0.10071 | -0.032043 | 0.11902 | 0.045776 | -0.032043 | -0.066223 | -0.48599 | -0.12924 | -0.045929 | 0.036621 | 0.16479 | 0.022888 | 0.068665 | 0.041199 | 0.027466 | 0.10529 | 122.4106 | 122.3007 | 0.12817
11653.3438 | 0.076294 | 0.27344 | -0.2243 | -0.22858 | -0.1976 | -0.27985 | -0.12817 | 0.064087 | 0.045776 | 0.073242 | 0.059509 | 0.10529 | -0.032043 | 0.10986 | 0.076294 | -0.032043 | -0.079041 | -0.49027 | -0.13351 | -0.032043 | 0.009155 | 0.09613 | 0.004578 | 0.050354 | 0.045776 | 0.032043 | 0.09613 | 122.438 | 122.3053 | 0.12817
11655.1406 | 0.061035 | 0.24139 | -0.23071 | -0.25421 | -0.18051 | -0.27878 | -0.12176 | 0.10986 | 0.091553 | 0.11902 | 0.086975 | 0.10071 | -0.027466 | 0.10529 | 0.045776 | -0.020294 | -0.05661 | -0.47638 | -0.12176 | -0.043793 | 0.018311 | 0.14191 | 0.018311 | 0.045776 | 0.045776 | 0.059509 | 0.11902 | 122.4197 | 122.3053 | 0.1236
11656.9375 | 0.061035 | 0.25207 | -0.23392 | -0.22858 | -0.17303 | -0.28412 | -0.1207 | 0.07782 | 0.050354 | 0.09613 | 0.068665 | 0.11902 | -0.036621 | 0.09613 | 0.045776 | -0.033112 | -0.059814 | -0.48386 | -0.11429 | -0.03952 | 0.050354 | 0.13275 | 0.036621 | 0.054932 | 0.054932 | 0.036621 | 0.10529 | 122.4747 | 122.3007 | 0.11902
11658.6719 | 0.045776 | 0.22324 | -0.23285 | -0.23819 | -0.20081 | -0.24994 | -0.12176 | 0.041199 | -0.022888 | -0.013733 | 0.009155 | 0.14191 | 0.004578 | 0.16479 | 0.061035 | -0.013885 | -0.050201 | -0.48813 | -0.1239 | -0.052338 | -0.036621 | 0.036621 | -0.091553 | 0.07782 | 0.091553 | 0.064087 | 0.14648 | 122.4747 | 122.287 | 0.09613
11660.4688 | 0.045776 | 0.23819 | -0.23605 | -0.23392 | -0.17197 | -0.24994 | -0.11963 | 0.050354 | -0.013733 | 0.004578 | 0.036621 | 0.12817 | -0.013733 | 0.13733 | 0.061035 | -0.01709 | -0.060883 | -0.48172 | -0.10361 | -0.042725 | -0.041199 | 0.068665 | -0.050354 | 0.09613 | 0.073242 | 0.054932 | 0.12817 | 122.5616 | 122.2412 | 0.07782
11662.2031 | 0.045776 | 0.23392 | -0.22217 | -0.2478 | -0.18372 | -0.25635 | -0.11643 | 0.050354 | -0.013733 | -0.013733 | 0.022888 | 0.15106 | 0.009155 | 0.15106 | 0.045776 | -0.016022 | -0.052338 | -0.46143 | -0.11429 | -0.054474 | -0.041199 | 0.059509 | -0.07782 | 0.073242 | 0.073242 | 0.054932 | 0.13733 | 122.5571 | 122.2778 | 0.07782
11664.0156 | 0.061035 | 0.2446 | -0.24353 | -0.25955 | -0.1976 | -0.28625 | -0.12711 | 0.11902 | 0.12817 | 0.14191 | 0.09613 | 0.10529 | -0.032043 | 0.11444 | 0.045776 | -0.044861 | -0.045929 | -0.48386 | -0.13672 | -0.026703 | 0.091553 | 0.18768 | 0.091553 | 0.041199 | 0.041199 | 0.022888 | 0.086975 | 122.4792 | 122.2687 | 0.11444
11665.75 | 0.061035 | 0.26489 | -0.22751 | -0.22217 | -0.19653 | -0.28198 | -0.10574 | 0.10071 | 0.082397 | 0.10529 | 0.064087 | 0.10986 | -0.036621 | 0.091553 | 0.061035 | -0.03952 | -0.060883 | -0.48813 | -0.12817 | -0.033112 | 0.027466 | 0.10529 | 0.022888 | 0.050354 | 0.022888 | 0.041199 | 0.10071 | 122.4426 | 122.3099 | 0.12817
11667.5469 | 0.045776 | 0.23605 | -0.24139 | -0.2446 | -0.19119 | -0.26703 | -0.11429 | 0.11902 | 0.10529 | 0.1236 | 0.09613 | 0.10986 | -0.041199 | 0.10071 | 0.045776 | -0.040588 | -0.065155 | -0.48813 | -0.11856 | -0.049133 | 0.032043 | 0.16937 | 0.036621 | 0.045776 | 0.032043 | 0.045776 | 0.091553 | 122.4426 | 122.3145 | 0.12817
11669.2656 | 0.061035 | 0.23071 | -0.22217 | -0.23392 | -0.18799 | -0.25848 | -0.11215 | 0.091553 | 0.018311 | 0.059509 | 0.045776 | 0.10529 | -0.027466 | 0.10986 | 0.030518 | -0.011749 | -0.05661 | -0.47211 | -0.11643 | -0.05661 | 0.054932 | 0.11444 | 0.013733 | 0.050354 | 0.041199 | 0.036621 | 0.10071 | 122.6028 | 122.2778 | 0.091553
11671.0781 | 0.045776 | 0.23605 | -0.22537 | -0.23712 | -0.19012 | -0.2478 | -0.11963 | 0.045776 | -0.027466 | 0.009155 | 0.022888 | 0.16022 | -0.004578 | 0.13275 | 0.061035 | -0.020294 | -0.052338 | -0.47531 | -0.10574 | -0.042725 | 0 | 0.022888 | -0.054932 | 0.086975 | 0.045776 | 0.050354 | 0.11902 | 122.5983 | 122.2916 | 0.091553
11672.875 | 0.076294 | 0.23392 | -0.21683 | -0.23926 | -0.17731 | -0.27451 | -0.12497 | 0.11444 | 0.1236 | 0.14648 | 0.09613 | 0.10071 | -0.045776 | 0.11444 | 0.045776 | -0.041656 | -0.065155 | -0.4924 | -0.12924 | -0.041656 | 0.050354 | 0.18768 | 0.054932 | 0.050354 | 0.022888 | 0.041199 | 0.10529 | 122.4747 | 122.3236 | 0.1236
11674.6719 | 0.045776 | 0.26062 | -0.23605 | -0.22537 | -0.1741 | -0.27985 | -0.11963 | 0.086975 | 0.045776 | 0.086975 | 0.050354 | 0.09613 | -0.018311 | 0.1236 | 0.076294 | -0.037384 | -0.068359 | -0.48279 | -0.13458 | -0.042725 | 0.027466 | 0.10986 | 0.013733 | 0.054932 | 0.041199 | 0.027466 | 0.10529 | 122.4747 | 122.3282 | 0.12817
11676.4688 | 0.045776 | 0.23712 | -0.21469 | -0.23392 | -0.17517 | -0.22964 | -0.11643 | 0.050354 | -0.082397 | -0.036621 | 0.022888 | 0.13275 | -0.004578 | 0.11902 | 0.061035 | -0.003204 | -0.069427 | -0.46997 | -0.11108 | -0.043793 | -0.045776 | 0.013733 | -0.086975 | 0.091553 | 0.091553 | 0.07782 | 0.14191 | 122.5708 | 122.3145 | 0.07782
11678.1875 | 0.061035 | 0.23819 | -0.23178 | -0.24887 | -0.17838 | -0.28839 | -0.11536 | 0.14648 | 0.13275 | 0.15564 | 0.10071 | 0.10071 | -0.027466 | 0.10529 | 0.061035 | -0.040588 | -0.067291 | -0.4892 | -0.13565 | -0.037384 | 0.068665 | 0.1831 | 0.073242 | 0.064087 | 0.036621 | 0.027466 | 0.10071 | 122.5159 | 122.3282 | 0.11902
11680 | 0.045776 | 0.23178 | -0.22858 | -0.23178 | -0.18906 | -0.27451 | -0.1207 | 0.1236 | 0.059509 | 0.10071 | 0.064087 | 0.10071 | -0.041199 | 0.091553 | 0.030518 | -0.032043 | -0.063019 | -0.48706 | -0.11749 | -0.041656 | 0.050354 | 0.10071 | 0.013733 | 0.050354 | 0.022888 | 0.036621 | 0.091553 | 122.4747 | 122.3419 | 0.11902
11681.7969 | 0.045776 | 0.23926 | -0.22858 | -0.24994 | -0.18051 | -0.26382 | -0.12176 | 0.086975 | 0.041199 | 0.064087 | 0.059509 | 0.11902 | -0.009155 | 0.12817 | 0.045776 | -0.029907 | -0.052338 | -0.48492 | -0.11963 | -0.041656 | -0.036621 | 0.09613 | -0.050354 | 0.09613 | 0.068665 | 0.054932 | 0.13733 | 122.4701 | 122.3328 | 0.1236
11683.6094 | 0.045776 | 0.23178 | -0.2243 | -0.25421 | -0.18265 | -0.27985 | -0.12711 | 0.13733 | 0.1236 | 0.13275 | 0.091553 | 0.10071 | -0.027466 | 0.11444 | 0.030518 | -0.029907 | -0.057678 | -0.47638 | -0.13458 | -0.052338 | 0.054932 | 0.20142 | 0.050354 | 0.036621 | 0.045776 | 0.009155 | 0.091553 | 122.493 | 122.3328 | 0.12817
11685.3906 | 0.045776 | 0.22751 | -0.2211 | -0.23071 | -0.1709 | -0.26596 | -0.10147 | 0.15106 | 0.091553 | 0.11902 | 0.086975 | 0.091553 | -0.059509 | 0.07782 | 0.061035 | -0.028839 | -0.064087 | -0.48279 | -0.11002 | -0.042725 | 0.082397 | 0.14648 | 0.041199 | 0.041199 | 0.018311 | 0.032043 | 0.086975 | 122.5571 | 122.3694 | 0.10529
11687.125 | 0.061035 | 0.24353 | -0.22217 | -0.2478 | -0.19226 | -0.27878 | -0.12497 | 0.11444 | 0.054932 | 0.10529 | 0.07782 | 0.10986 | -0.045776 | 0.10986 | 0.061035 | -0.030975 | -0.05661 | -0.48599 | -0.13992 | -0.049133 | 0.054932 | 0.14191 | 0.064087 | 0.059509 | 0.050354 | 0.032043 | 0.091553 | 122.5342 | 122.3602 | 0.10986
11688.9375 | 0.061035 | 0.22964 | -0.22964 | -0.22003 | -0.18692 | -0.23498 | -0.11108 | 0.064087 | -0.064087 | -0.036621 | -0.009155 | 0.13733 | -0.018311 | 0.1236 | 0.061035 | -0.012817 | -0.065155 | -0.47958 | -0.10788 | -0.044861 | -0.032043 | -0.004578 | -0.091553 | 0.091553 | 0.07782 | 0.068665 | 0.1236 | 122.6074 | 122.3236 | 0.091553
11690.6719 | 0.061035 | 0.23605 | -0.22003 | -0.25207 | -0.19226 | -0.25528 | -0.11856 | 0.054932 | -0.022888 | 0.032043 | 0.018311 | 0.14191 | -0.013733 | 0.13275 | 0.061035 | -0.02243 | -0.05661 | -0.47531 | -0.13351 | -0.041656 | -0.045776 | 0.054932 | -0.068665 | 0.082397 | 0.086975 | 0.082397 | 0.12817 | 122.5021 | 122.374 | 0.1236
11692.4531 | 0.061035 | 0.2243 | -0.22964 | -0.25101 | -0.19012 | -0.24674 | -0.11322 | 0.073242 | -0.027466 | 0 | 0.027466 | 0.13733 | 0.009155 | 0.14191 | 0.061035 | -0.020294 | -0.05127 | -0.48492 | -0.12604 | -0.048065 | -0.032043 | 0.07782 | -0.064087 | 0.086975 | 0.054932 | 0.07782 | 0.13275 | 122.6303 | 122.3145 | 0.086975
11694.1719 | 0.091553 | 0.23926 | -0.23819 | -0.24674 | -0.18799 | -0.26382 | -0.11749 | 0.022888 | -0.027466 | -0.004578 | 0.009155 | 0.16022 | 0.018311 | 0.14191 | 0.045776 | -0.018158 | -0.057678 | -0.47638 | -0.12817 | -0.043793 | -0.045776 | 0.045776 | -0.07782 | 0.10071 | 0.086975 | 0.07782 | 0.12817 | 122.5204 | 122.3557 | 0.11902
11695.9688 | 0.061035 | 0.2211 | -0.21469 | -0.23498 | -0.16769 | -0.24674 | -0.11322 | 0.086975 | 0.018311 | 0.022888 | 0.054932 | 0.15106 | 0.004578 | 0.12817 | 0.061035 | -0.023499 | -0.050201 | -0.47531 | -0.10788 | -0.044861 | 0 | 0.086975 | -0.041199 | 0.073242 | 0.073242 | 0.050354 | 0.12817 | 122.6395 | 122.3053 | 0.086975
11697.7656 | 0.045776 | 0.24994 | -0.2179 | -0.23392 | -0.17624 | -0.28946 | -0.12604 | 0.082397 | 0.086975 | 0.10529 | 0.091553 | 0.10986 | -0.041199 | 0.10529 | 0.076294 | -0.032043 | -0.059814 | -0.4924 | -0.12817 | -0.029907 | 0.013733 | 0.14648 | 0.009155 | 0.054932 | 0.059509 | 0.036621 | 0.10986 | 122.4747 | 122.3831 | 0.13733
11699.5 | 0.076294 | 0.25314 | -0.22644 | -0.22751 | -0.19546 | -0.26382 | -0.12283 | 0.11902 | 0.10071 | 0.13275 | 0.091553 | 0.091553 | -0.032043 | 0.091553 | 0.061035 | -0.027771 | -0.058746 | -0.49027 | -0.1207 | -0.037384 | 0.068665 | 0.13733 | 0.054932 | 0.059509 | 0.022888 | 0.045776 | 0.073242 | 122.5525 | 122.3785 | 0.11444
11701.2969 | 0.061035 | 0.26489 | -0.23285 | -0.23285 | -0.19867 | -0.28412 | -0.11856 | 0.054932 | 0.036621 | 0.07782 | 0.045776 | 0.11902 | -0.022888 | 0.10071 | 0.061035 | -0.023499 | -0.077972 | -0.4892 | -0.1239 | -0.030975 | -0.022888 | 0.082397 | 0.018311 | 0.059509 | 0.041199 | 0.036621 | 0.10529 | 122.5571 | 122.3831 | 0.13275
11703.1094 | 0.045776 | 0.24887 | -0.22964 | -0.24887 | -0.19974 | -0.27664 | -0.12817 | 0.059509 | 0.027466 | 0.068665 | 0.050354 | 0.11444 | -0.032043 | 0.10071 | 0.030518 | -0.035248 | -0.064087 | -0.47958 | -0.14954 | -0.03952 | 0.013733 | 0.10986 | 0.032043 | 0.064087 | 0.054932 | 0.054932 | 0.10529 | 122.5754 | 122.3694 | 0.11902
11707.5781 | 0.061035 | 0.2179 | -0.21683 | -0.25742 | -0.18051 | -0.24353 | -0.11322 | 0.068665 | -0.07782 | -0.018311 | 0.013733 | 0.14191 | 0.004578 | 0.13275 | 0.061035 | -0.012817 | -0.045929 | -0.46143 | -0.11536 | -0.045929 | -0.009155 | 0.009155 | -0.082397 | 0.091553 | 0.073242 | 0.054932 | 0.11902 | 122.6624 | 122.3602 | 0.064087
11709.625 | 0.061035 | 0.2243 | -0.2243 | -0.25528 | -0.17731 | -0.26062 | -0.11856 | 0.050354 | -0.068665 | -0.009155 | 0.009155 | 0.13733 | 0.009155 | 0.15564 | 0.061035 | -0.019226 | -0.042725 | -0.47424 | -0.11856 | -0.041656 | -0.059509 | 0.036621 | -0.068665 | 0.10071 | 0.082397 | 0.068665 | 0.11444 | 122.612 | 122.3694 | 0.11902
11712.25 | 0.045776 | 0.23712 | -0.22644 | -0.22537 | -0.18265 | -0.24567 | -0.11322 | 0.050354 | -0.073242 | -0.032043 | 0.009155 | 0.15564 | -0.009155 | 0.15564 | 0.045776 | -0.005341 | -0.054474 | -0.46036 | -0.11215 | -0.040588 | -0.027466 | 0.009155 | -0.07782 | 0.07782 | 0.064087 | 0.054932 | 0.1236 | 122.6761 | 122.3877 | 0.09613
11714.1406 | 0.030518 | 0.23071 | -0.22751 | -0.23819 | -0.18265 | -0.28198 | -0.11215 | 0.10986 | 0.073242 | 0.10986 | 0.09613 | 0.10529 | -0.027466 | 0.10529 | 0.045776 | -0.024567 | -0.059814 | -0.48492 | -0.12497 | -0.045929 | 0.018311 | 0.12817 | 0 | 0.059509 | 0.073242 | 0.050354 | 0.11902 | 122.5113 | 122.4197 | 0.1236
11715.9375 | 0.045776 | 0.24567 | -0.24246 | -0.21896 | -0.18799 | -0.27557 | -0.12711 | 0.12817 | 0.073242 | 0.11902 | 0.068665 | 0.10071 | -0.036621 | 0.086975 | 0.045776 | -0.029907 | -0.068359 | -0.48279 | -0.11643 | -0.029907 | 0.050354 | 0.1236 | 0.027466 | 0.050354 | 0.050354 | 0.041199 | 0.09613 | 122.5433 | 122.4289 | 0.1236
11717.7656 | 0.045776 | 0.22751 | -0.21362 | -0.22751 | -0.16983 | -0.24033 | -0.11322 | 0.045776 | -0.064087 | -0.022888 | 0.013733 | 0.15106 | -0.004578 | 0.1236 | 0.045776 | -0.001068 | -0.057678 | -0.47745 | -0.099335 | -0.041656 | -0.07782 | 0 | -0.10986 | 0.082397 | 0.073242 | 0.068665 | 0.13733 | 122.6257 | 122.3923 | 0.10071
11719.6094 | 0.045776 | 0.23071 | -0.23285 | -0.2446 | -0.17838 | -0.27237 | -0.1239 | 0.082397 | 0.036621 | 0.068665 | 0.059509 | 0.11902 | -0.009155 | 0.12817 | 0.045776 | -0.024567 | -0.054474 | -0.47318 | -0.1239 | -0.03418 | -0.050354 | 0.09613 | -0.050354 | 0.082397 | 0.07782 | 0.068665 | 0.12817 | 122.5479 | 122.4243 | 0.11902
11721.4062 | 0.061035 | 0.21469 | -0.22003 | -0.24353 | -0.17944 | -0.23926 | -0.093994 | 0.064087 | -0.045776 | -0.004578 | 0.018311 | 0.14648 | -0.018311 | 0.12817 | 0.045776 | -0.007477 | -0.048065 | -0.47318 | -0.1207 | -0.048065 | -0.059509 | 0.009155 | -0.10986 | 0.091553 | 0.082397 | 0.054932 | 0.14648 | 122.6303 | 122.3877 | 0.091553
11723.2812 | 0.015259 | 0.23605 | -0.21576 | -0.24994 | -0.18585 | -0.26169 | -0.11749 | 0.022888 | -0.045776 | 0.004578 | 0.027466 | 0.15564 | 0 | 0.15106 | 0.045776 | -0.023499 | -0.052338 | -0.47211 | -0.12817 | -0.040588 | -0.054932 | 0.054932 | -0.07782 | 0.091553 | 0.068665 | 0.068665 | 0.12817 | 122.6761 | 122.3648 | 0.10986
11725.0625 | 0.045776 | 0.22858 | -0.21896 | -0.25421 | -0.1976 | -0.27451 | -0.11108 | 0.018311 | -0.041199 | 0 | 0.032043 | 0.15106 | 0.013733 | 0.15564 | 0.030518 | -0.01709 | -0.049133 | -0.47638 | -0.1239 | -0.032043 | -0.068665 | 0.050354 | -0.073242 | 0.091553 | 0.073242 | 0.082397 | 0.1236 | 122.6807 | 122.3831 | 0.064087
11726.8438 | 0.091553 | 0.26169 | -0.22324 | -0.24353 | -0.18585 | -0.28839 | -0.11536 | 0.032043 | 0.013733 | 0.073242 | 0.054932 | 0.10986 | -0.018311 | 0.11444 | 0.030518 | -0.048065 | -0.057678 | -0.48706 | -0.12497 | -0.025635 | -0.004578 | 0.10986 | 0.032043 | 0.059509 | 0.036621 | 0.045776 | 0.09613 | 122.6028 | 122.4197 | 0.13275
11728.7188 | 0.045776 | 0.22324 | -0.22537 | -0.22217 | -0.17517 | -0.25207 | -0.11643 | 0.013733 | -0.068665 | -0.022888 | 0.004578 | 0.16022 | -0.004578 | 0.13275 | 0.076294 | -0.011749 | -0.057678 | -0.47211 | -0.10574 | -0.030975 | -0.054932 | -0.013733 | -0.10529 | 0.086975 | 0.068665 | 0.064087 | 0.14648 | 122.6624 | 122.4197 | 0.073242
11730.5469 | 0.076294 | 0.23605 | -0.21576 | -0.23498 | -0.1741 | -0.26169 | -0.11215 | 0.082397 | -0.004578 | 0.050354 | 0.036621 | 0.11902 | -0.027466 | 0.10986 | 0.045776 | -0.016022 | -0.054474 | -0.47531 | -0.11856 | -0.041656 | 0.050354 | 0.082397 | 0.022888 | 0.027466 | 0.050354 | 0.009155 | 0.09613 | 122.7036 | 122.3969 | 0.064087
11732.2969 | 0.061035 | 0.20187 | -0.22644 | -0.24994 | -0.18158 | -0.24887 | -0.11322 | 0.086975 | 0.022888 | 0.050354 | 0.050354 | 0.13275 | -0.009155 | 0.13733 | 0.076294 | -0.020294 | -0.054474 | -0.47211 | -0.11643 | -0.043793 | 0 | 0.09613 | -0.050354 | 0.068665 | 0.064087 | 0.054932 | 0.1236 | 122.6852 | 122.4014 | 0.082397
11734.0938 | 0.030518 | 0.22217 | -0.23926 | -0.24033 | -0.17303 | -0.28091 | -0.11429 | 0.064087 | 0.036621 | 0.082397 | 0.073242 | 0.14191 | -0.013733 | 0.1236 | 0.061035 | -0.018158 | -0.055542 | -0.48065 | -0.14099 | -0.043793 | -0.045776 | 0.07782 | -0.041199 | 0.082397 | 0.073242 | 0.059509 | 0.13733 | 122.5708 | 122.4564 | 0.11902
11735.9219 | 0.061035 | 0.22003 | -0.22537 | -0.2446 | -0.18372 | -0.25848 | -0.11856 | 0.082397 | 0.022888 | 0.032043 | 0.050354 | 0.1236 | -0.009155 | 0.12817 | 0.061035 | -0.020294 | -0.057678 | -0.47852 | -0.11002 | -0.033112 | -0.022888 | 0.064087 | -0.068665 | 0.07782 | 0.068665 | 0.064087 | 0.1236 | 122.6624 | 122.4197 | 0.091553
11738.6094 | 0.061035 | 0.23498 | -0.23071 | -0.24033 | -0.1944 | -0.25421 | -0.10895 | 0.041199 | -0.013733 | 0 | 0.013733 | 0.13275 | -0.013733 | 0.12817 | 0.045776 | -0.01709 | -0.042725 | -0.47638 | -0.12604 | -0.030975 | -0.004578 | 0.073242 | -0.009155 | 0.068665 | 0.032043 | 0.041199 | 0.10071 | 122.7402 | 122.406 | 0.091553
11741 | 0.076294 | 0.23178 | -0.22751 | -0.24139 | -0.19119 | -0.25101 | -0.11429 | 0.086975 | 0.027466 | 0.032043 | 0.041199 | 0.1236 | -0.013733 | 0.1236 | 0.061035 | -0.013885 | -0.059814 | -0.47424 | -0.11002 | -0.032043 | 0 | 0.09613 | -0.050354 | 0.086975 | 0.059509 | 0.059509 | 0.12817 | 122.6898 | 122.406 | 0.086975
11742.8125 | 0.045776 | 0.23285 | -0.22644 | -0.26382 | -0.18799 | -0.29587 | -0.1442 | 0.10529 | 0.11444 | 0.14191 | 0.10529 | 0.10986 | -0.036621 | 0.10071 | 0.045776 | -0.03952 | -0.060883 | -0.48065 | -0.14313 | -0.042725 | 0.050354 | 0.18768 | 0.07782 | 0.041199 | 0.036621 | 0.009155 | 0.09613 | 122.612 | 122.4472 | 0.12817
11744.75 | 0.061035 | 0.22858 | -0.21255 | -0.22644 | -0.18906 | -0.25955 | -0.12176 | 0.10071 | -0.009155 | 0.022888 | 0.050354 | 0.12817 | -0.018311 | 0.13733 | 0.045776 | -0.010681 | -0.05661 | -0.46463 | -0.10574 | -0.043793 | -0.036621 | 0.036621 | -0.082397 | 0.073242 | 0.073242 | 0.054932 | 0.1236 | 122.6761 | 122.4335 | 0.09613
11746.5469 | 0.030518 | 0.2478 | -0.21896 | -0.24994 | -0.18906 | -0.28839 | -0.12283 | 0.11902 | 0.10529 | 0.13733 | 0.10986 | 0.10071 | -0.036621 | 0.10529 | 0.061035 | -0.036316 | -0.068359 | -0.49347 | -0.13458 | -0.042725 | 0.050354 | 0.17853 | 0.07782 | 0.059509 | 0.050354 | 0.027466 | 0.11444 | 122.6395 | 122.4335 | 0.10071
11748.5 | 0.045776 | 0.26382 | -0.24674 | -0.23819 | -0.19226 | -0.2948 | -0.12497 | 0.13275 | 0.11902 | 0.13275 | 0.10986 | 0.11902 | -0.036621 | 0.11902 | 0.045776 | -0.030975 | -0.063019 | -0.4924 | -0.13031 | -0.038452 | 0.073242 | 0.16937 | 0.086975 | 0.045776 | 0.027466 | 0.022888 | 0.09613 | 122.6486 | 122.4426 | 0.10986
11751.0312 | 0.045776 | 0.24033 | -0.23285 | -0.22217 | -0.18158 | -0.24674 | -0.1207 | 0.045776 | -0.059509 | -0.018311 | 0.009155 | 0.14648 | -0.004578 | 0.13275 | 0.061035 | -0.011749 | -0.065155 | -0.47745 | -0.11002 | -0.050201 | -0.032043 | 0 | -0.07782 | 0.082397 | 0.07782 | 0.059509 | 0.14191 | 122.7356 | 122.4518 | 0.09613
11753.7031 | 0.061035 | 0.2446 | -0.24139 | -0.23071 | -0.18265 | -0.29053 | -0.11963 | 0.045776 | 0.022888 | 0.064087 | 0.064087 | 0.11444 | -0.041199 | 0.10529 | 0.045776 | -0.032043 | -0.059814 | -0.49133 | -0.12711 | -0.027771 | -0.013733 | 0.082397 | 0.004578 | 0.045776 | 0.041199 | 0.036621 | 0.10986 | 122.6349 | 122.4701 | 0.11444
11756.3281 | 0.045776 | 0.23819 | -0.23392 | -0.23178 | -0.18478 | -0.25528 | -0.11108 | 0.091553 | 0.009155 | 0.036621 | 0.041199 | 0.12817 | -0.022888 | 0.11902 | 0.045776 | -0.024567 | -0.063019 | -0.48065 | -0.11215 | -0.040588 | 0.054932 | 0.086975 | 0.022888 | 0.050354 | 0.041199 | 0.027466 | 0.091553 | 122.7493 | 122.4426 | 0.086975
11758.7656 | 0.061035 | 0.1944 | -0.22964 | -0.26382 | -0.18265 | -0.25207 | -0.11643 | 0.032043 | -0.07782 | -0.027466 | 0.018311 | 0.14191 | -0.004578 | 0.12817 | 0.076294 | -0.009613 | -0.03952 | -0.47745 | -0.11215 | -0.050201 | -0.082397 | -0.004578 | -0.11902 | 0.09613 | 0.068665 | 0.082397 | 0.14648 | 122.7036 | 122.4564 | 0.10071
11761.2188 | 0.045776 | 0.24033 | -0.23178 | -0.22964 | -0.17517 | -0.25635 | -0.11429 | 0.086975 | 0.027466 | 0.064087 | 0.054932 | 0.1236 | -0.045776 | 0.10529 | 0.045776 | -0.026703 | -0.055542 | -0.47958 | -0.12924 | -0.036316 | 0.032043 | 0.1236 | 0.022888 | 0.045776 | 0.041199 | 0.022888 | 0.09613 | 122.7585 | 122.4518 | 0.073242
11763.125 | 0.045776 | 0.24994 | -0.23712 | -0.23819 | -0.19653 | -0.29694 | -0.12176 | 0.059509 | 0.013733 | 0.07782 | 0.064087 | 0.1236 | -0.036621 | 0.10529 | 0.045776 | -0.030975 | -0.064087 | -0.49454 | -0.13138 | -0.028839 | -0.004578 | 0.091553 | 0.013733 | 0.050354 | 0.054932 | 0.022888 | 0.10071 | 122.644 | 122.4838 | 0.1236
11764.9062 | 0.061035 | 0.23285 | -0.22964 | -0.23392 | -0.19867 | -0.24994 | -0.11429 | 0.054932 | -0.10071 | -0.004578 | 0.004578 | 0.13733 | 0.009155 | 0.14191 | 0.045776 | -0.01709 | -0.05127 | -0.47104 | -0.10468 | -0.041656 | -0.050354 | -0.013733 | -0.11902 | 0.09613 | 0.086975 | 0.068665 | 0.13733 | 122.7356 | 122.4655 | 0.10071
11767 | 0.045776 | 0.25635 | -0.23605 | -0.22537 | -0.16449 | -0.28198 | -0.11429 | 0.073242 | 0.045776 | 0.09613 | 0.054932 | 0.10529 | -0.045776 | 0.09613 | 0.030518 | -0.043793 | -0.063019 | -0.49133 | -0.12924 | -0.032043 | 0.027466 | 0.091553 | 0.009155 | 0.041199 | 0.050354 | 0.027466 | 0.09613 | 122.6349 | 122.493 | 0.1236
11768.8594 | 0.045776 | 0.2446 | -0.24139 | -0.25314 | -0.20721 | -0.28625 | -0.12176 | 0.082397 | 0.032043 | 0.086975 | 0.064087 | 0.10071 | -0.032043 | 0.10986 | 0.030518 | -0.048065 | -0.05661 | -0.48599 | -0.13351 | -0.040588 | 0.022888 | 0.1236 | 0.045776 | 0.059509 | 0.041199 | 0.032043 | 0.11902 | 122.6807 | 122.4747 | 0.13275
11770.6406 | 0.045776 | 0.25421 | -0.22537 | -0.24567 | -0.19653 | -0.26596 | -0.13458 | 0.13275 | 0.07782 | 0.11902 | 0.09613 | 0.11902 | -0.041199 | 0.10986 | 0.030518 | -0.036316 | -0.058746 | -0.49133 | -0.13351 | -0.045929 | 0.07782 | 0.17395 | 0.07782 | 0.050354 | 0.045776 | 0.022888 | 0.086975 | 122.6852 | 122.4838 | 0.09613
11772.5469 | 0.061035 | 0.23178 | -0.2211 | -0.25635 | -0.18692 | -0.24674 | -0.12283 | 0.068665 | -0.050354 | 0 | 0.036621 | 0.14191 | 0 | 0.13733 | 0.076294 | -0.018158 | -0.055542 | -0.47958 | -0.12604 | -0.057678 | -0.041199 | 0.036621 | -0.082397 | 0.10071 | 0.068665 | 0.082397 | 0.1236 | 122.7585 | 122.4655 | 0.07782
11774.2656 | 0.076294 | 0.23392 | -0.22964 | -0.24674 | -0.17624 | -0.26596 | -0.11215 | 0.1236 | 0.068665 | 0.10529 | 0.082397 | 0.10986 | -0.022888 | 0.11902 | 0.045776 | -0.025635 | -0.054474 | -0.48386 | -0.13245 | -0.043793 | 0 | 0.12817 | -0.013733 | 0.073242 | 0.064087 | 0.041199 | 0.11444 | 122.6257 | 122.5159 | 0.11902
11776.0469 | 0.061035 | 0.22537 | -0.23071 | -0.21469 | -0.18692 | -0.24033 | -0.11108 | 0.045776 | -0.059509 | -0.022888 | 0.027466 | 0.13733 | -0.004578 | 0.1236 | 0.061035 | -0.016022 | -0.061951 | -0.47531 | -0.093994 | -0.036316 | -0.050354 | -0.004578 | -0.10071 | 0.082397 | 0.07782 | 0.07782 | 0.1236 | 122.7493 | 122.4655 | 0.10071
11777.7656 | 0.061035 | 0.22644 | -0.21042 | -0.23498 | -0.18906 | -0.24994 | -0.10788 | 0.10986 | 0.032043 | 0.032043 | 0.054932 | 0.12817 | 0.009155 | 0.11902 | 0.061035 | -0.025635 | -0.048065 | -0.48065 | -0.11002 | -0.045929 | 0.018311 | 0.086975 | -0.068665 | 0.073242 | 0.068665 | 0.059509 | 0.11902 | 122.7448 | 122.4609 | 0.091553
11779.4844 | 0.076294 | 0.22217 | -0.23178 | -0.23498 | -0.19653 | -0.26382 | -0.11002 | 0.036621 | -0.027466 | -0.013733 | 0.013733 | 0.13733 | -0.004578 | 0.14191 | 0.030518 | -0.009613 | -0.05127 | -0.47852 | -0.11002 | -0.027771 | -0.013733 | 0.022888 | -0.050354 | 0.073242 | 0.054932 | 0.068665 | 0.1236 | 122.7859 | 122.493 | 0.07782
11781.2344 | 0.045776 | 0.24674 | -0.23712 | -0.25848 | -0.18799 | -0.298 | -0.11856 | 0.11444 | 0.10529 | 0.13733 | 0.11902 | 0.11444 | -0.036621 | 0.10986 | 0.061035 | -0.030975 | -0.05661 | -0.49561 | -0.14313 | -0.036316 | 0.036621 | 0.17853 | 0.045776 | 0.036621 | 0.041199 | 0.022888 | 0.09613 | 122.6395 | 122.5067 | 0.12817
11782.9375 | 0.061035 | 0.22858 | -0.23712 | -0.23498 | -0.18692 | -0.25635 | -0.11215 | 0.041199 | -0.059509 | -0.004578 | 0.013733 | 0.13733 | -0.004578 | 0.14648 | 0.045776 | -0.019226 | -0.059814 | -0.47531 | -0.1207 | -0.043793 | -0.041199 | 0.013733 | -0.086975 | 0.086975 | 0.064087 | 0.059509 | 0.12817 | 122.7951 | 122.4792 | 0.10529
11784.7031 | 0.061035 | 0.22324 | -0.22324 | -0.25528 | -0.18158 | -0.2713 | -0.12924 | 0.018311 | -0.032043 | 0 | 0.013733 | 0.15564 | -0.004578 | 0.15106 | 0.030518 | -0.018158 | -0.036316 | -0.47745 | -0.13351 | -0.03418 | -0.064087 | 0.032043 | -0.07782 | 0.086975 | 0.068665 | 0.07782 | 0.14648 | 122.6807 | 122.5296 | 0.12817
11786.4062 | 0.076294 | 0.22751 | -0.2243 | -0.22537 | -0.18799 | -0.25314 | -0.12176 | 0.032043 | -0.032043 | -0.027466 | 0.013733 | 0.15106 | 0 | 0.15106 | 0.045776 | -0.020294 | -0.053406 | -0.46143 | -0.12283 | -0.037384 | -0.045776 | 0.013733 | -0.091553 | 0.09613 | 0.07782 | 0.064087 | 0.13733 | 122.8043 | 122.4976 | 0.07782
11788.2031 | 0.061035 | 0.22537 | -0.21896 | -0.24139 | -0.17624 | -0.26916 | -0.11002 | 0.027466 | -0.027466 | -0.004578 | 0.018311 | 0.12817 | 0.004578 | 0.14191 | 0.061035 | -0.014954 | -0.046997 | -0.47318 | -0.11856 | -0.042725 | -0.018311 | 0.036621 | -0.050354 | 0.07782 | 0.064087 | 0.059509 | 0.13733 | 122.7997 | 122.4564 | 0.082397
11790 | 0.061035 | 0.2243 | -0.21896 | -0.25207 | -0.18585 | -0.26062 | -0.11002 | 0.059509 | -0.009155 | 0.018311 | 0.054932 | 0.13733 | -0.013733 | 0.13733 | 0.030518 | -0.012817 | -0.044861 | -0.48813 | -0.11429 | -0.033112 | -0.018311 | 0.086975 | -0.032043 | 0.073242 | 0.064087 | 0.068665 | 0.11902 | 122.7997 | 122.4564 | 0.073242
11791.9531 | 0.061035 | 0.24353 | -0.22858 | -0.24139 | -0.18799 | -0.29694 | -0.11536 | 0.054932 | 0.054932 | 0.086975 | 0.050354 | 0.09613 | -0.036621 | 0.09613 | 0.061035 | -0.048065 | -0.053406 | -0.4924 | -0.12924 | -0.038452 | 0 | 0.09613 | 0.013733 | 0.054932 | 0.054932 | 0.009155 | 0.09613 | 122.6578 | 122.525 | 0.1236
11793.8594 | 0.061035 | 0.25101 | -0.22537 | -0.23605 | -0.19119 | -0.29373 | -0.1239 | 0.07782 | 0.041199 | 0.07782 | 0.054932 | 0.11444 | -0.041199 | 0.10986 | 0.061035 | -0.027771 | -0.065155 | -0.48386 | -0.12817 | -0.041656 | 0.018311 | 0.10071 | 0.022888 | 0.054932 | 0.032043 | 0.013733 | 0.09613 | 122.6761 | 122.5571 | 0.12817
11795.7188 | 0.045776 | 0.25742 | -0.23071 | -0.23285 | -0.17517 | -0.26703 | -0.12817 | 0.07782 | 0.018311 | 0.022888 | 0.027466 | 0.1236 | -0.009155 | 0.13733 | 0.061035 | -0.01709 | -0.05127 | -0.48172 | -0.11963 | -0.042725 | -0.036621 | 0.054932 | -0.054932 | 0.07782 | 0.054932 | 0.059509 | 0.1236 | 122.6715 | 122.5525 | 0.13275
11797.5469 | 0.030518 | 0.25742 | -0.23712 | -0.21896 | -0.18799 | -0.27878 | -0.12283 | 0.1236 | 0.068665 | 0.10529 | 0.073242 | 0.10986 | -0.022888 | 0.091553 | 0.061035 | -0.037384 | -0.064087 | -0.48386 | -0.12711 | -0.041656 | 0.041199 | 0.10071 | 0.004578 | 0.045776 | 0.032043 | 0.054932 | 0.10529 | 122.6669 | 122.58 | 0.11902
11799.5156 | 0.076294 | 0.23071 | -0.22751 | -0.25848 | -0.17731 | -0.27023 | -0.1239 | 0.11444 | 0.045776 | 0.086975 | 0.082397 | 0.11444 | -0.018311 | 0.1236 | 0.061035 | -0.029907 | -0.050201 | -0.48172 | -0.14099 | -0.037384 | -0.009155 | 0.10071 | -0.009155 | 0.086975 | 0.059509 | 0.032043 | 0.1236 | 122.6486 | 122.5479 | 0.13733
11801.7812 | 0.061035 | 0.24353 | -0.22217 | -0.23926 | -0.18051 | -0.25421 | -0.11536 | 0.14648 | 0.064087 | 0.09613 | 0.091553 | 0.11444 | -0.032043 | 0.09613 | 0.061035 | -0.030975 | -0.061951 | -0.48172 | -0.11322 | -0.041656 | 0.068665 | 0.11902 | 0.018311 | 0.041199 | 0.032043 | 0.041199 | 0.09613 | 122.7905 | 122.5067 | 0.086975
11803.5625 | 0.061035 | 0.24033 | -0.23498 | -0.23926 | -0.18372 | -0.25742 | -0.11856 | 0.082397 | -0.050354 | 0 | 0.013733 | 0.14648 | 0.022888 | 0.12817 | 0.061035 | -0.007477 | -0.054474 | -0.47531 | -0.1207 | -0.032043 | 0 | 0.027466 | -0.059509 | 0.073242 | 0.068665 | 0.032043 | 0.11444 | 122.8317 | 122.493 | 0.073242
11805.5 | 0.045776 | 0.23071 | -0.22751 | -0.24033 | -0.18906 | -0.24567 | -0.11856 | 0.09613 | 0.009155 | 0.027466 | 0.045776 | 0.13733 | -0.004578 | 0.1236 | 0.045776 | -0.011749 | -0.045929 | -0.48706 | -0.1004 | -0.040588 | -0.009155 | 0.041199 | -0.091553 | 0.064087 | 0.064087 | 0.059509 | 0.12817 | 122.7631 | 122.525 | 0.07782
11807.2969 | 0.030518 | 0.23498 | -0.23178 | -0.23498 | -0.18478 | -0.27557 | -0.11429 | 0.11902 | 0.091553 | 0.13275 | 0.10071 | 0.10071 | -0.045776 | 0.091553 | 0.061035 | -0.03418 | -0.059814 | -0.48386 | -0.12176 | -0.030975 | 0.059509 | 0.15106 | 0.041199 | 0.032043 | 0.018311 | 0.027466 | 0.10071 | 122.7676 | 122.5433 | 0.11902
11809.1094 | 0.030518 | 0.24246 | -0.22003 | -0.25314 | -0.19012 | -0.2681 | -0.10895 | 0.068665 | 0.004578 | 0.045776 | 0.045776 | 0.11902 | -0.022888 | 0.10071 | 0.061035 | -0.018158 | -0.055542 | -0.48279 | -0.12283 | -0.040588 | 0.041199 | 0.10529 | -0.004578 | 0.050354 | 0.041199 | 0.027466 | 0.09613 | 122.8363 | 122.4884 | 0.082397
11810.9062 | 0.076294 | 0.2243 | -0.22964 | -0.24246 | -0.16769 | -0.26916 | -0.11749 | 0.045776 | -0.013733 | 0.018311 | 0.032043 | 0.13275 | -0.004578 | 0.13275 | 0.045776 | -0.021362 | -0.058746 | -0.47318 | -0.13245 | -0.044861 | -0.054932 | 0.064087 | -0.068665 | 0.091553 | 0.07782 | 0.054932 | 0.14191 | 122.6852 | 122.525 | 0.11902
11812.8438 | 0.045776 | 0.20615 | -0.22644 | -0.25528 | -0.19226 | -0.24246 | -0.11643 | 0.10529 | 0.027466 | 0.054932 | 0.059509 | 0.14191 | -0.022888 | 0.13275 | 0.061035 | 0.003204 | -0.03952 | -0.47745 | -0.11429 | -0.045929 | 0.004578 | 0.07782 | -0.050354 | 0.07782 | 0.073242 | 0.054932 | 0.12817 | 122.7722 | 122.5204 | 0.082397
11814.5938 | 0.061035 | 0.22537 | -0.2211 | -0.23712 | -0.18158 | -0.26169 | -0.11002 | 0.09613 | 0.022888 | 0.086975 | 0.064087 | 0.11902 | -0.032043 | 0.11902 | 0.061035 | -0.014954 | -0.057678 | -0.47745 | -0.12497 | -0.038452 | 0.045776 | 0.1236 | 0.032043 | 0.059509 | 0.054932 | 0.013733 | 0.10071 | 122.8363 | 122.5113 | 0.10071
11816.4688 | 0.061035 | 0.24994 | -0.23712 | -0.23285 | -0.18265 | -0.298 | -0.13886 | 0.10986 | 0.09613 | 0.12817 | 0.10071 | 0.10529 | -0.045776 | 0.09613 | 0.030518 | -0.027771 | -0.065155 | -0.48065 | -0.13779 | -0.027771 | 0.073242 | 0.1831 | 0.091553 | 0.036621 | 0.032043 | 0.022888 | 0.10529 | 122.7676 | 122.5433 | 0.10529
11818.3125 | 0.045776 | 0.20081 | -0.20935 | -0.25101 | -0.19653 | -0.24887 | -0.10895 | 0.12817 | 0.013733 | 0.032043 | 0.045776 | 0.13733 | -0.009155 | 0.13275 | 0.045776 | -0.006409 | -0.03952 | -0.47531 | -0.11963 | -0.048065 | -0.004578 | 0.068665 | -0.073242 | 0.09613 | 0.073242 | 0.054932 | 0.13275 | 122.7859 | 122.5159 | 0.09613
11820.0781 | 0.045776 | 0.20935 | -0.20828 | -0.23712 | -0.17624 | -0.24139 | -0.11215 | 0.09613 | 0.027466 | 0.036621 | 0.054932 | 0.13275 | -0.018311 | 0.12817 | 0.045776 | 0.004272 | -0.041656 | -0.47318 | -0.11643 | -0.044861 | 0.009155 | 0.082397 | -0.054932 | 0.064087 | 0.059509 | 0.054932 | 0.12817 | 122.8043 | 122.5479 | 0.09613
11821.9219 | 0.030518 | 0.2243 | -0.20935 | -0.23605 | -0.19333 | -0.25207 | -0.095062 | 0.054932 | -0.045776 | -0.004578 | 0.018311 | 0.1236 | -0.004578 | 0.13275 | 0.076294 | -0.007477 | -0.05661 | -0.46783 | -0.10574 | -0.036316 | -0.082397 | 0.013733 | -0.10529 | 0.082397 | 0.086975 | 0.054932 | 0.13275 | 122.7859 | 122.5159 | 0.10071
11823.875 | 0.076294 | 0.23498 | -0.22324 | -0.23712 | -0.18265 | -0.26703 | -0.11002 | 0.027466 | -0.041199 | 0.009155 | 0.013733 | 0.14648 | 0 | 0.14648 | 0.061035 | -0.005341 | -0.052338 | -0.47531 | -0.11322 | -0.027771 | -0.013733 | 0.045776 | -0.041199 | 0.073242 | 0.091553 | 0.041199 | 0.12817 | 122.8638 | 122.525 | 0.091553
11826 | 0.045776 | 0.24567 | -0.23392 | -0.24139 | -0.18158 | -0.298 | -0.11643 | 0.045776 | 0.064087 | 0.09613 | 0.073242 | 0.13275 | -0.022888 | 0.09613 | 0.076294 | -0.040588 | -0.054474 | -0.48599 | -0.13779 | -0.041656 | 0.027466 | 0.16022 | 0.050354 | 0.045776 | 0.032043 | 0.018311 | 0.09613 | 122.7585 | 122.5525 | 0.11444
11828.0781 | 0.076294 | 0.26489 | -0.23285 | -0.23285 | -0.19226 | -0.28625 | -0.13031 | 0.086975 | 0.059509 | 0.091553 | 0.059509 | 0.10071 | -0.068665 | 0.10529 | 0.076294 | -0.03418 | -0.061951 | -0.4924 | -0.11963 | -0.03418 | 0.022888 | 0.07782 | 0.018311 | 0.036621 | 0.045776 | 0.041199 | 0.09613 | 122.7036 | 122.5891 | 0.11902
11829.875 | 0.061035 | 0.2243 | -0.22644 | -0.22324 | -0.19119 | -0.27023 | -0.11643 | 0.032043 | -0.064087 | -0.018311 | 0.009155 | 0.13733 | -0.009155 | 0.13733 | 0.076294 | -0.007477 | -0.069427 | -0.47638 | -0.10468 | -0.040588 | -0.036621 | 0.013733 | -0.064087 | 0.09613 | 0.064087 | 0.059509 | 0.11444 | 122.8409 | 122.5433 | 0.086975
11831.6875 | 0.061035 | 0.25528 | -0.22537 | -0.23498 | -0.18051 | -0.27771 | -0.12924 | 0.10986 | 0.082397 | 0.1236 | 0.07782 | 0.10071 | -0.050354 | 0.086975 | 0.061035 | -0.028839 | -0.057678 | -0.48279 | -0.13138 | -0.02243 | 0.059509 | 0.11444 | 0.027466 | 0.054932 | 0.036621 | 0.045776 | 0.082397 | 122.7219 | 122.58 | 0.13733
11833.5469 | 0.091553 | 0.23178 | -0.22217 | -0.25635 | -0.17731 | -0.27344 | -0.13138 | 0.059509 | 0 | 0.045776 | 0.041199 | 0.13275 | -0.013733 | 0.14648 | 0.045776 | -0.014954 | -0.045929 | -0.48599 | -0.14954 | -0.049133 | -0.054932 | 0.059509 | -0.059509 | 0.10986 | 0.068665 | 0.059509 | 0.15564 | 122.731 | 122.5708 | 0.13733
11835.2656 | 0.076294 | 0.22858 | -0.20828 | -0.23392 | -0.18478 | -0.23392 | -0.11002 | 0.041199 | -0.073242 | -0.022888 | -0.004578 | 0.14648 | 0 | 0.12817 | 0.076294 | -0.005341 | -0.054474 | -0.47745 | -0.11002 | -0.05127 | -0.082397 | -0.027466 | -0.13733 | 0.09613 | 0.073242 | 0.073242 | 0.13275 | 122.8134 | 122.5708 | 0.10986
11836.9844 | 0.076294 | 0.23605 | -0.21896 | -0.24353 | -0.18478 | -0.27557 | -0.12817 | 0.10529 | 0.068665 | 0.11902 | 0.082397 | 0.11444 | -0.041199 | 0.073242 | 0.045776 | -0.025635 | -0.05661 | -0.48065 | -0.13245 | -0.035248 | 0.050354 | 0.1236 | 0.018311 | 0.050354 | 0.041199 | 0.022888 | 0.07782 | 122.7356 | 122.5754 | 0.12817
11838.7188 | 0.045776 | 0.24994 | -0.23071 | -0.23926 | -0.18906 | -0.29159 | -0.11322 | 0.068665 | 0.032043 | 0.073242 | 0.059509 | 0.10529 | -0.036621 | 0.10071 | 0.061035 | -0.025635 | -0.064087 | -0.49133 | -0.12604 | -0.035248 | 0.004578 | 0.09613 | 0.022888 | 0.059509 | 0.036621 | 0.041199 | 0.091553 | 122.7402 | 122.5983 | 0.11902
11840.4688 | 0.045776 | 0.2211 | -0.22964 | -0.24353 | -0.18478 | -0.25528 | -0.11749 | 0.059509 | -0.027466 | 0.004578 | 0.041199 | 0.13275 | 0.009155 | 0.12817 | 0.061035 | -0.014954 | -0.05661 | -0.49774 | -0.12176 | -0.041656 | -0.036621 | 0.059509 | -0.068665 | 0.082397 | 0.07782 | 0.054932 | 0.13275 | 122.8455 | 122.5342 | 0.073242
11842.1719 | 0.045776 | 0.23605 | -0.21576 | -0.23392 | -0.19226 | -0.2478 | -0.11643 | 0.036621 | -0.059509 | -0.032043 | 0.004578 | 0.14191 | 0.009155 | 0.13275 | 0.030518 | -0.006409 | -0.052338 | -0.46783 | -0.11643 | -0.036316 | -0.050354 | -0.036621 | -0.10986 | 0.09613 | 0.059509 | 0.082397 | 0.13275 | 122.85 | 122.5662 | 0.086975
11843.8906 | 0.045776 | 0.23819 | -0.21362 | -0.22003 | -0.18372 | -0.25314 | -0.10147 | 0.027466 | -0.036621 | -0.013733 | 0.018311 | 0.15564 | -0.018311 | 0.13733 | 0.045776 | -0.007477 | -0.055542 | -0.48065 | -0.10681 | -0.029907 | -0.022888 | 0.022888 | -0.059509 | 0.086975 | 0.068665 | 0.064087 | 0.10071 | 122.8592 | 122.5754 | 0.09613
11845.6562 | 0.061035 | 0.2179 | -0.22217 | -0.23392 | -0.1709 | -0.26916 | -0.10681 | 0.059509 | -0.018311 | 0.018311 | 0.054932 | 0.13275 | -0.009155 | 0.12817 | 0.045776 | -0.007477 | -0.050201 | -0.47852 | -0.12176 | -0.044861 | -0.027466 | 0.091553 | -0.041199 | 0.054932 | 0.086975 | 0.068665 | 0.14648 | 122.8729 | 122.5616 | 0.082397
11847.4219 | 0.061035 | 0.25207 | -0.22751 | -0.24567 | -0.18265 | -0.29587 | -0.11002 | 0.036621 | 0.027466 | 0.086975 | 0.045776 | 0.11902 | -0.032043 | 0.11444 | 0.061035 | -0.040588 | -0.059814 | -0.48706 | -0.13031 | -0.023499 | -0.004578 | 0.09613 | 0.013733 | 0.059509 | 0.041199 | 0.032043 | 0.086975 | 122.7631 | 122.5937 | 0.12817
11849.1406 | 0.076294 | 0.25421 | -0.22964 | -0.22751 | -0.18692 | -0.27023 | -0.11536 | 0.13733 | 0.091553 | 0.11902 | 0.091553 | 0.082397 | -0.050354 | 0.091553 | 0.061035 | -0.023499 | -0.072632 | -0.48813 | -0.11429 | -0.036316 | 0.054932 | 0.12817 | 0.054932 | 0.036621 | 0.032043 | 0.009155 | 0.086975 | 122.7905 | 122.5662 | 0.10529
11850.8438 | 0.076294 | 0.26169 | -0.22324 | -0.25528 | -0.19546 | -0.298 | -0.13031 | 0.12817 | 0.10986 | 0.14648 | 0.09613 | 0.10986 | -0.045776 | 0.09613 | 0.061035 | -0.03952 | -0.061951 | -0.48279 | -0.13992 | -0.032043 | 0.07782 | 0.19684 | 0.073242 | 0.041199 | 0.041199 | 0.041199 | 0.10986 | 122.7768 | 122.58 | 0.1236
11852.5625 | 0.076294 | 0.22644 | -0.22217 | -0.23926 | -0.1741 | -0.23178 | -0.11002 | 0.041199 | -0.09613 | -0.036621 | -0.004578 | 0.13733 | -0.004578 | 0.13275 | 0.045776 | 0.002136 | -0.059814 | -0.47852 | -0.11215 | -0.041656 | -0.054932 | -0.013733 | -0.11444 | 0.086975 | 0.07782 | 0.064087 | 0.13733 | 122.8363 | 122.5754 | 0.091553
11854.2812 | 0.045776 | 0.22644 | -0.22324 | -0.25421 | -0.19119 | -0.26703 | -0.12497 | 0.022888 | -0.036621 | 0 | 0.004578 | 0.14191 | 0.009155 | 0.13275 | 0.045776 | -0.014954 | -0.058746 | -0.47958 | -0.13779 | -0.040588 | -0.059509 | 0.045776 | -0.07782 | 0.091553 | 0.091553 | 0.068665 | 0.13275 | 122.7676 | 122.5891 | 0.10529
11856.0312 | 0.045776 | 0.25101 | -0.23071 | -0.24353 | -0.18372 | -0.28625 | -0.11536 | 0.10986 | 0.11444 | 0.13733 | 0.10071 | 0.10986 | -0.032043 | 0.09613 | 0.061035 | -0.027771 | -0.05127 | -0.4892 | -0.14099 | -0.024567 | 0.082397 | 0.18768 | 0.091553 | 0.045776 | 0.036621 | 0.032043 | 0.086975 | 122.7905 | 122.5708 | 0.11902
11857.75 | 0.045776 | 0.24567 | -0.21255 | -0.22644 | -0.1709 | -0.27344 | -0.11963 | 0.13275 | 0.091553 | 0.13275 | 0.091553 | 0.10071 | -0.050354 | 0.086975 | 0.061035 | -0.018158 | -0.068359 | -0.49027 | -0.11856 | -0.037384 | 0.068665 | 0.1236 | 0.027466 | 0.045776 | 0.027466 | 0.022888 | 0.091553 | 122.7676 | 122.6028 | 0.1236
11859.4844 | 0.045776 | 0.22751 | -0.22217 | -0.2478 | -0.17197 | -0.24887 | -0.11215 | 0.11902 | 0.022888 | 0.045776 | 0.050354 | 0.14648 | -0.022888 | 0.10529 | 0.061035 | 0.008545 | -0.052338 | -0.48065 | -0.11749 | -0.049133 | 0.004578 | 0.073242 | -0.054932 | 0.073242 | 0.073242 | 0.050354 | 0.11902 | 122.8409 | 122.5708 | 0.10986
11861.2031 | 0.045776 | 0.25528 | -0.22324 | -0.23819 | -0.19119 | -0.28091 | -0.11215 | 0.11902 | 0.064087 | 0.10529 | 0.064087 | 0.10529 | -0.036621 | 0.082397 | 0.061035 | -0.02243 | -0.060883 | -0.48386 | -0.13779 | -0.045929 | 0.045776 | 0.10986 | 0.018311 | 0.050354 | 0.041199 | 0.022888 | 0.086975 | 122.7493 | 122.6257 | 0.13275
11862.9688 | 0.061035 | 0.24033 | -0.2243 | -0.23926 | -0.17197 | -0.26596 | -0.11856 | 0.14648 | 0.07782 | 0.1236 | 0.10986 | 0.09613 | -0.045776 | 0.09613 | 0.091553 | -0.028839 | -0.054474 | -0.47958 | -0.11322 | -0.042725 | 0.064087 | 0.15106 | 0.045776 | 0.050354 | 0.050354 | 0.032043 | 0.082397 | 122.8363 | 122.6028 | 0.10071
11864.7344 | 0.061035 | 0.2179 | -0.22217 | -0.23071 | -0.18585 | -0.23819 | -0.11215 | 0.12817 | 0.018311 | 0.041199 | 0.050354 | 0.13275 | -0.013733 | 0.12817 | 0.030518 | -0.001068 | -0.05127 | -0.48492 | -0.10574 | -0.03952 | 0.004578 | 0.068665 | -0.073242 | 0.073242 | 0.064087 | 0.054932 | 0.11902 | 122.8592 | 122.5937 | 0.091553
11866.4531 | 0.076294 | 0.24139 | -0.21683 | -0.22003 | -0.18372 | -0.25742 | -0.10361 | 0.036621 | -0.064087 | -0.022888 | 0.004578 | 0.13733 | -0.004578 | 0.14191 | 0.061035 | -0.012817 | -0.055542 | -0.46783 | -0.11002 | -0.035248 | -0.041199 | -0.004578 | -0.07782 | 0.091553 | 0.073242 | 0.07782 | 0.13275 | 122.8867 | 122.58 | 0.082397
11868.2188 | 0.076294 | 0.23605 | -0.23605 | -0.25742 | -0.17731 | -0.27878 | -0.11749 | 0.073242 | 0.082397 | 0.10529 | 0.082397 | 0.10986 | -0.041199 | 0.10986 | 0.061035 | -0.025635 | -0.052338 | -0.48813 | -0.12711 | -0.033112 | 0 | 0.13733 | 0 | 0.054932 | 0.036621 | 0.045776 | 0.11444 | 122.7448 | 122.612 | 0.13733
11869.9219 | 0.061035 | 0.22324 | -0.22324 | -0.22858 | -0.19333 | -0.24887 | -0.12283 | 0.027466 | -0.07782 | -0.032043 | 0 | 0.16022 | -0.004578 | 0.15106 | 0.061035 | 0.001068 | -0.063019 | -0.46677 | -0.10468 | -0.033112 | -0.059509 | -0.009155 | -0.086975 | 0.09613 | 0.068665 | 0.054932 | 0.12817 | 122.85 | 122.5845 | 0.091553
11871.6406 | 0.061035 | 0.25101 | -0.23819 | -0.25421 | -0.18906 | -0.29053 | -0.11749 | 0.10071 | 0.086975 | 0.13275 | 0.10071 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | -0.038452 | -0.072632 | -0.48813 | -0.14099 | -0.028839 | 0.068665 | 0.19684 | 0.09613 | 0.036621 | 0.032043 | 0.018311 | 0.09613 | 122.8226 | 122.612 | 0.10071
11873.375 | 0.030518 | 0.22644 | -0.22858 | -0.25314 | -0.18906 | -0.28091 | -0.12604 | 0.082397 | 0.041199 | 0.10529 | 0.054932 | 0.10071 | -0.036621 | 0.091553 | 0.061035 | -0.027771 | -0.066223 | -0.47531 | -0.13031 | -0.035248 | 0.036621 | 0.10529 | 0.009155 | 0.059509 | 0.041199 | 0.022888 | 0.09613 | 122.7814 | 122.6257 | 0.13275
11875.125 | 0.061035 | 0.24246 | -0.23392 | -0.24674 | -0.17944 | -0.27557 | -0.11963 | 0.1236 | 0.082397 | 0.10986 | 0.082397 | 0.11444 | -0.045776 | 0.091553 | 0.076294 | -0.020294 | -0.072632 | -0.49027 | -0.1239 | -0.035248 | 0.045776 | 0.1236 | 0.018311 | 0.073242 | 0.018311 | 0.027466 | 0.10071 | 122.7676 | 122.6395 | 0.12817
11876.8438 | 0.061035 | 0.23071 | -0.22858 | -0.22644 | -0.18478 | -0.24567 | -0.11963 | 0.054932 | -0.045776 | -0.009155 | 0.004578 | 0.15564 | -0.004578 | 0.14648 | 0.061035 | -0.005341 | -0.071564 | -0.48706 | -0.093994 | -0.045929 | -0.009155 | 0.013733 | -0.073242 | 0.07782 | 0.059509 | 0.036621 | 0.11902 | 122.9141 | 122.5754 | 0.091553
11878.6094 | 0.076294 | 0.23926 | -0.2243 | -0.24994 | -0.17944 | -0.28412 | -0.1207 | 0.12817 | 0.11444 | 0.13275 | 0.10529 | 0.10071 | -0.045776 | 0.10529 | 0.061035 | -0.023499 | -0.070496 | -0.50201 | -0.13565 | -0.03952 | 0.059509 | 0.1831 | 0.045776 | 0.041199 | 0.041199 | 0.022888 | 0.091553 | 122.7722 | 122.6074 | 0.12817
11880.5 | 0.076294 | 0.22964 | -0.23285 | -0.24994 | -0.19867 | -0.27557 | -0.1239 | 0.11902 | 0.10529 | 0.13275 | 0.09613 | 0.10071 | -0.027466 | 0.09613 | 0.076294 | -0.021362 | -0.058746 | -0.48065 | -0.11963 | -0.043793 | 0.045776 | 0.16937 | 0.059509 | 0.050354 | 0.032043 | 0.022888 | 0.10529 | 122.7768 | 122.6349 | 0.11444
11882.3125 | 0.061035 | 0.26169 | -0.24353 | -0.22644 | -0.18799 | -0.27451 | -0.12176 | 0.059509 | 0.032043 | 0.073242 | 0.050354 | 0.11902 | -0.022888 | 0.082397 | 0.045776 | -0.020294 | -0.069427 | -0.48813 | -0.11856 | -0.027771 | 0.018311 | 0.10071 | 0.013733 | 0.054932 | 0.064087 | 0.032043 | 0.10529 | 122.8088 | 122.6578 | 0.13733
11884.0469 | 0.061035 | 0.23712 | -0.22217 | -0.24033 | -0.19226 | -0.23926 | -0.10895 | 0.11902 | 0.022888 | 0.032043 | 0.050354 | 0.13275 | -0.009155 | 0.11902 | 0.030518 | 0.004272 | -0.065155 | -0.47531 | -0.10574 | -0.046997 | 0.018311 | 0.091553 | -0.064087 | 0.07782 | 0.068665 | 0.036621 | 0.11444 | 122.8867 | 122.5891 | 0.07782
11885.8438 | 0.045776 | 0.24674 | -0.2446 | -0.24567 | -0.19226 | -0.2948 | -0.11963 | 0.045776 | 0.036621 | 0.10071 | 0.068665 | 0.11902 | -0.009155 | 0.11902 | 0.030518 | -0.046997 | -0.061951 | -0.49027 | -0.12817 | -0.024567 | 0.018311 | 0.11444 | 0.050354 | 0.059509 | 0.036621 | 0.032043 | 0.10071 | 122.8317 | 122.644 | 0.11902
11887.6562 | 0.045776 | 0.22858 | -0.21683 | -0.22217 | -0.18158 | -0.24567 | -0.11002 | 0.059509 | -0.027466 | -0.009155 | 0 | 0.14191 | 0 | 0.12817 | 0.061035 | -0.006409 | -0.070496 | -0.47638 | -0.10681 | -0.043793 | -0.018311 | 0.027466 | -0.045776 | 0.073242 | 0.054932 | 0.032043 | 0.11444 | 122.9279 | 122.5937 | 0.091553
11889.3906 | 0.045776 | 0.23178 | -0.23498 | -0.2446 | -0.19119 | -0.27451 | -0.11536 | 0.10071 | 0.059509 | 0.086975 | 0.068665 | 0.11444 | -0.018311 | 0.11444 | 0.030518 | -0.014954 | -0.058746 | -0.48706 | -0.13458 | -0.037384 | -0.018311 | 0.10071 | -0.032043 | 0.068665 | 0.091553 | 0.059509 | 0.1236 | 122.7722 | 122.6166 | 0.13733
11891.1875 | 0.030518 | 0.23819 | -0.21042 | -0.23819 | -0.18906 | -0.2446 | -0.11108 | 0.10071 | 0.009155 | 0.022888 | 0.054932 | 0.14191 | 0 | 0.13275 | 0.061035 | 0.001068 | -0.05661 | -0.47531 | -0.11215 | -0.054474 | 0.013733 | 0.086975 | -0.054932 | 0.07782 | 0.064087 | 0.059509 | 0.11444 | 122.9141 | 122.6212 | 0.07782
11892.9219 | 0.061035 | 0.23605 | -0.22217 | -0.23712 | -0.18051 | -0.2478 | -0.11643 | 0.10071 | -0.004578 | 0.018311 | 0.050354 | 0.14191 | 0.004578 | 0.16479 | 0.076294 | 0.001068 | -0.061951 | -0.47104 | -0.11215 | -0.03952 | 0.009155 | 0.10071 | -0.050354 | 0.068665 | 0.064087 | 0.041199 | 0.11902 | 122.9187 | 122.58 | 0.073242
11894.7188 | 0.061035 | 0.2478 | -0.21362 | -0.22964 | -0.18478 | -0.27451 | -0.11963 | 0.11902 | 0.10071 | 0.13275 | 0.10071 | 0.091553 | -0.036621 | 0.11444 | 0.061035 | -0.028839 | -0.063019 | -0.48492 | -0.12497 | -0.029907 | 0.073242 | 0.15106 | 0.050354 | 0.041199 | 0.032043 | 0.036621 | 0.10071 | 122.8363 | 122.6395 | 0.12817
11896.5156 | 0.045776 | 0.23712 | -0.22964 | -0.23392 | -0.18799 | -0.25848 | -0.10788 | 0.041199 | -0.068665 | -0.045776 | 0.009155 | 0.15106 | -0.004578 | 0.15106 | 0.061035 | -0.01709 | -0.054474 | -0.47638 | -0.11002 | -0.029907 | -0.032043 | 0.013733 | -0.07782 | 0.073242 | 0.073242 | 0.064087 | 0.12817 | 122.9187 | 122.6303 | 0.09613
11898.2344 | 0.061035 | 0.26276 | -0.23178 | -0.22324 | -0.19653 | -0.28946 | -0.11536 | 0.086975 | 0.041199 | 0.086975 | 0.050354 | 0.082397 | -0.022888 | 0.091553 | 0.045776 | -0.023499 | -0.064087 | -0.49454 | -0.13351 | -0.023499 | 0.018311 | 0.10529 | 0.009155 | 0.041199 | 0.045776 | 0.032043 | 0.09613 | 122.7859 | 122.6486 | 0.13733
11900.0156 | 0.045776 | 0.25101 | -0.23392 | -0.24033 | -0.19012 | -0.27451 | -0.1207 | 0.13275 | 0.07782 | 0.1236 | 0.09613 | 0.11444 | -0.036621 | 0.10529 | 0.045776 | -0.011749 | -0.066223 | -0.48172 | -0.11108 | -0.029907 | 0.059509 | 0.12817 | 0.041199 | 0.045776 | 0.036621 | 0.032043 | 0.10071 | 122.8088 | 122.6486 | 0.12817
11901.7969 | 0.061035 | 0.23605 | -0.21469 | -0.2478 | -0.19333 | -0.24567 | -0.11429 | 0.054932 | -0.082397 | -0.027466 | 0.004578 | 0.13275 | -0.013733 | 0.13275 | 0.061035 | 0.009613 | -0.050201 | -0.47211 | -0.11749 | -0.045929 | -0.045776 | -0.013733 | -0.091553 | 0.091553 | 0.082397 | 0.059509 | 0.13275 | 122.9187 | 122.6257 | 0.086975
11903.5781 | 0.061035 | 0.23605 | -0.21896 | -0.23285 | -0.18158 | -0.24353 | -0.1207 | 0.086975 | -0.018311 | 0.009155 | 0.032043 | 0.10986 | 0.013733 | 0.14648 | 0.061035 | -0.007477 | -0.049133 | -0.47745 | -0.10788 | -0.03418 | -0.041199 | 0.013733 | -0.086975 | 0.073242 | 0.068665 | 0.064087 | 0.12817 | 122.8775 | 122.6349 | 0.091553
11905.3125 | 0.061035 | 0.23285 | -0.21149 | -0.23926 | -0.18692 | -0.25421 | -0.11856 | 0.032043 | -0.050354 | -0.013733 | 0.009155 | 0.15564 | -0.009155 | 0.14648 | 0.076294 | -0.009613 | -0.058746 | -0.48492 | -0.11643 | -0.035248 | -0.022888 | 0.022888 | -0.050354 | 0.09613 | 0.054932 | 0.054932 | 0.11902 | 122.937 | 122.6212 | 0.086975
11907.1094 | 0.076294 | 0.24674 | -0.22858 | -0.23498 | -0.1741 | -0.28305 | -0.11215 | 0.11902 | 0.086975 | 0.1236 | 0.091553 | 0.082397 | -0.027466 | 0.086975 | 0.030518 | -0.032043 | -0.065155 | -0.48386 | -0.13245 | -0.026703 | 0.050354 | 0.1236 | 0.032043 | 0.064087 | 0.027466 | 0.022888 | 0.10071 | 122.818 | 122.6532 | 0.11902
11908.9062 | 0.061035 | 0.22324 | -0.21896 | -0.23605 | -0.17197 | -0.25848 | -0.10574 | 0.036621 | -0.082397 | -0.022888 | 0.018311 | 0.12817 | -0.004578 | 0.13275 | 0.045776 | 0.001068 | -0.053406 | -0.47958 | -0.11322 | -0.041656 | -0.082397 | -0.018311 | -0.13275 | 0.086975 | 0.073242 | 0.059509 | 0.13733 | 122.8912 | 122.6578 | 0.10529
11910.7031 | 0.061035 | 0.26062 | -0.22964 | -0.22644 | -0.18051 | -0.29159 | -0.11963 | 0.10986 | 0.10071 | 0.11902 | 0.07782 | 0.082397 | -0.050354 | 0.10071 | 0.030518 | -0.025635 | -0.058746 | -0.48492 | -0.12924 | -0.035248 | 0.050354 | 0.14648 | 0.041199 | 0.032043 | 0.027466 | 0.027466 | 0.082397 | 122.8271 | 122.6944 | 0.10986
11912.5 | 0.076294 | 0.22537 | -0.22217 | -0.23285 | -0.18692 | -0.26596 | -0.11536 | 0.032043 | -0.045776 | 0.009155 | 0.009155 | 0.13733 | -0.022888 | 0.13275 | 0.061035 | -0.003204 | -0.059814 | -0.48065 | -0.11749 | -0.040588 | -0.027466 | 0.022888 | -0.054932 | 0.07782 | 0.059509 | 0.050354 | 0.1236 | 122.937 | 122.6074 | 0.068665
11914.2812 | 0.061035 | 0.23178 | -0.21576 | -0.2446 | -0.1976 | -0.25848 | -0.11643 | 0.050354 | -0.036621 | 0 | 0.013733 | 0.15564 | -0.009155 | 0.12817 | 0.061035 | -0.008545 | -0.05127 | -0.46997 | -0.12283 | -0.042725 | 0 | 0.045776 | -0.041199 | 0.068665 | 0.064087 | 0.050354 | 0.10529 | 122.9507 | 122.6395 | 0.086975
11916.0156 | 0.061035 | 0.24353 | -0.21683 | -0.23392 | -0.19012 | -0.26169 | -0.11429 | 0.050354 | -0.041199 | 0.013733 | 0.018311 | 0.13733 | -0.013733 | 0.10529 | 0.045776 | -0.014954 | -0.058746 | -0.47318 | -0.12283 | -0.038452 | 0.018311 | 0.07782 | -0.022888 | 0.054932 | 0.054932 | 0.036621 | 0.10529 | 122.9553 | 122.6028 | 0.10071
11917.7969 | 0.061035 | 0.22964 | -0.2243 | -0.23926 | -0.17838 | -0.25848 | -0.11002 | 0.032043 | -0.064087 | -0.022888 | 0.013733 | 0.14191 | -0.004578 | 0.13275 | 0.076294 | -0.002136 | -0.042725 | -0.48065 | -0.11108 | -0.042725 | -0.036621 | 0.004578 | -0.07782 | 0.073242 | 0.064087 | 0.059509 | 0.13733 | 122.9553 | 122.6166 | 0.091553
11919.5938 | 0.045776 | 0.23392 | -0.2211 | -0.23071 | -0.18585 | -0.26703 | -0.11749 | 0.036621 | -0.022888 | 0.027466 | 0.027466 | 0.14191 | -0.009155 | 0.11902 | 0.091553 | -0.006409 | -0.058746 | -0.47852 | -0.11749 | -0.03952 | -0.004578 | 0.064087 | -0.027466 | 0.054932 | 0.045776 | 0.036621 | 0.10071 | 122.9553 | 122.6578 | 0.082397
11921.4062 | 0.045776 | 0.23285 | -0.23178 | -0.25742 | -0.17944 | -0.28412 | -0.12817 | 0.11444 | 0.086975 | 0.13733 | 0.091553 | 0.086975 | -0.050354 | 0.10986 | 0.076294 | -0.018158 | -0.054474 | -0.48279 | -0.13351 | -0.036316 | 0.027466 | 0.17395 | 0.050354 | 0.059509 | 0.041199 | 0.032043 | 0.086975 | 122.7951 | 122.6944 | 0.10986
11923.125 | 0.076294 | 0.22537 | -0.22003 | -0.23392 | -0.17517 | -0.2478 | -0.10574 | 0.073242 | -0.036621 | 0.009155 | 0.032043 | 0.11902 | -0.009155 | 0.13275 | 0.030518 | 0.001068 | -0.057678 | -0.47211 | -0.1239 | -0.038452 | -0.041199 | 0.004578 | -0.09613 | 0.082397 | 0.091553 | 0.068665 | 0.13275 | 122.8958 | 122.6578 | 0.086975
11924.9375 | 0.045776 | 0.23178 | -0.2243 | -0.23605 | -0.17944 | -0.26062 | -0.10788 | 0.032043 | -0.036621 | 0 | 0.022888 | 0.13733 | -0.004578 | 0.13733 | 0.061035 | -0.003204 | -0.052338 | -0.48492 | -0.12283 | -0.041656 | -0.041199 | 0.07782 | -0.059509 | 0.07782 | 0.064087 | 0.059509 | 0.12817 | 122.9507 | 122.644 | 0.086975
11926.7344 | 0.045776 | 0.24353 | -0.22964 | -0.25207 | -0.17624 | -0.27344 | -0.13031 | 0.054932 | 0 | 0.022888 | 0.036621 | 0.11902 | -0.009155 | 0.13275 | 0.061035 | -0.010681 | -0.05127 | -0.47958 | -0.14633 | -0.028839 | -0.059509 | 0.050354 | -0.059509 | 0.073242 | 0.086975 | 0.07782 | 0.11444 | 122.818 | 122.6898 | 0.1236
11928.5312 | 0.045776 | 0.24887 | -0.22003 | -0.24994 | -0.18478 | -0.26916 | -0.12283 | 0.018311 | -0.054932 | -0.004578 | 0.004578 | 0.15106 | 0.009155 | 0.15106 | 0.076294 | -0.005341 | -0.055542 | -0.47745 | -0.13458 | -0.03952 | -0.068665 | 0.032043 | -0.082397 | 0.09613 | 0.073242 | 0.068665 | 0.1236 | 122.8455 | 122.6898 | 0.10986
11930.2656 | 0.061035 | 0.25421 | -0.23071 | -0.23498 | -0.19119 | -0.28625 | -0.1239 | 0.036621 | 0.018311 | 0.073242 | 0.054932 | 0.11444 | -0.045776 | 0.11902 | 0.061035 | -0.026703 | -0.066223 | -0.48279 | -0.13245 | -0.030975 | -0.009155 | 0.10071 | 0.032043 | 0.054932 | 0.054932 | 0.041199 | 0.10071 | 122.8592 | 122.6852 | 0.10071
11932.0625 | 0.076294 | 0.20721 | -0.21149 | -0.24994 | -0.17517 | -0.23498 | -0.11215 | 0.027466 | -0.082397 | -0.032043 | 0 | 0.15106 | 0.004578 | 0.14191 | 0.076294 | 0 | -0.045929 | -0.46997 | -0.11856 | -0.046997 | -0.059509 | -0.022888 | -0.11444 | 0.07782 | 0.068665 | 0.064087 | 0.13733 | 122.9187 | 122.6624 | 0.07782
11933.7969 | 0.045776 | 0.22217 | -0.22964 | -0.23392 | -0.18478 | -0.25207 | -0.11429 | 0.086975 | 0.004578 | 0.036621 | 0.045776 | 0.13733 | -0.009155 | 0.13275 | 0.061035 | -0.002136 | -0.063019 | -0.48279 | -0.10681 | -0.049133 | 0.018311 | 0.09613 | -0.036621 | 0.068665 | 0.064087 | 0.054932 | 0.13275 | 122.9187 | 122.6486 | 0.10071
11935.5781 | 0.076294 | 0.2211 | -0.21469 | -0.24567 | -0.17838 | -0.2446 | -0.099335 | 0.10529 | -0.004578 | 0.036621 | 0.054932 | 0.13733 | -0.013733 | 0.14191 | 0.030518 | -0.005341 | -0.05661 | -0.47318 | -0.10895 | -0.040588 | -0.004578 | 0.068665 | -0.059509 | 0.073242 | 0.07782 | 0.036621 | 0.11902 | 122.9233 | 122.6532 | 0.07782
11937.375 | 0.076294 | 0.23819 | -0.21469 | -0.24033 | -0.18372 | -0.26382 | -0.11536 | 0.018311 | -0.09613 | -0.032043 | -0.009155 | 0.12817 | 0 | 0.13275 | 0.045776 | 0.001068 | -0.058746 | -0.47318 | -0.11215 | -0.032043 | -0.054932 | -0.013733 | -0.091553 | 0.091553 | 0.068665 | 0.064087 | 0.12817 | 122.9187 | 122.6532 | 0.10986
11939.1094 | 0.030518 | 0.23285 | -0.22324 | -0.22751 | -0.17731 | -0.25848 | -0.10788 | 0.009155 | -0.086975 | -0.022888 | 0.009155 | 0.16022 | 0.004578 | 0.13275 | 0.061035 | 0 | -0.059814 | -0.47424 | -0.11429 | -0.03952 | -0.064087 | -0.018311 | -0.086975 | 0.09613 | 0.068665 | 0.059509 | 0.1236 | 122.9553 | 122.6532 | 0.10071
11940.9062 | 0.045776 | 0.23498 | -0.24139 | -0.25314 | -0.1741 | -0.29159 | -0.11536 | 0.10071 | 0.10071 | 0.12817 | 0.10529 | 0.10529 | -0.036621 | 0.10529 | 0.045776 | -0.023499 | -0.059814 | -0.49988 | -0.13779 | -0.032043 | 0.022888 | 0.1831 | 0.054932 | 0.036621 | 0.036621 | 0.013733 | 0.10071 | 122.8271 | 122.6852 | 0.13275
11942.7031 | 0.061035 | 0.24567 | -0.21683 | -0.23605 | -0.18478 | -0.25528 | -0.11856 | 0.050354 | -0.022888 | 0.013733 | 0.041199 | 0.14191 | -0.022888 | 0.14191 | 0.030518 | 0.002136 | -0.060883 | -0.48279 | -0.12497 | -0.027771 | -0.036621 | 0.073242 | -0.041199 | 0.086975 | 0.073242 | 0.059509 | 0.12817 | 122.9782 | 122.6486 | 0.073242
11944.5 | 0.045776 | 0.23071 | -0.2243 | -0.22644 | -0.18158 | -0.25848 | -0.11108 | 0.086975 | 0.009155 | 0.027466 | 0.068665 | 0.1236 | -0.013733 | 0.11902 | 0.061035 | 0 | -0.058746 | -0.47958 | -0.1239 | -0.043793 | -0.013733 | 0.082397 | -0.041199 | 0.068665 | 0.07782 | 0.045776 | 0.1236 | 122.937 | 122.6761 | 0.09613
11946.3125 | 0.030518 | 0.24887 | -0.24033 | -0.24033 | -0.18906 | -0.29266 | -0.11749 | 0.091553 | 0.09613 | 0.10529 | 0.064087 | 0.10071 | -0.027466 | 0.10529 | 0.045776 | -0.025635 | -0.075836 | -0.50201 | -0.12283 | -0.025635 | 0.018311 | 0.10986 | 0.027466 | 0.059509 | 0.054932 | 0.032043 | 0.10071 | 122.8409 | 122.6944 | 0.11444
11948.0469 | 0.061035 | 0.26596 | -0.2478 | -0.24567 | -0.19546 | -0.28198 | -0.11643 | 0.073242 | 0.036621 | 0.073242 | 0.045776 | 0.086975 | -0.041199 | 0.091553 | 0.076294 | -0.030975 | -0.069427 | -0.48599 | -0.1239 | -0.026703 | 0.004578 | 0.07782 | 0.013733 | 0.054932 | 0.059509 | 0.022888 | 0.09613 | 122.8409 | 122.7127 | 0.14191
11949.8438 | 0.061035 | 0.25848 | -0.23926 | -0.23712 | -0.19974 | -0.28198 | -0.1207 | 0.13275 | 0.064087 | 0.12817 | 0.068665 | 0.091553 | -0.027466 | 0.10986 | 0.061035 | -0.01709 | -0.070496 | -0.48813 | -0.12283 | -0.027771 | 0.032043 | 0.10529 | 0.018311 | 0.050354 | 0.050354 | 0.027466 | 0.09613 | 122.8592 | 122.7264 | 0.13733
11951.6406 | 0.061035 | 0.21149 | -0.2179 | -0.23392 | -0.19119 | -0.24994 | -0.11429 | 0.1236 | -0.004578 | 0.027466 | 0.059509 | 0.12817 | -0.013733 | 0.14648 | 0.045776 | 0.007477 | -0.053406 | -0.48599 | -0.11322 | -0.044861 | 0 | 0.082397 | -0.045776 | 0.064087 | 0.073242 | 0.054932 | 0.12817 | 122.9691 | 122.6669 | 0.082397
11953.4375 | 0.076294 | 0.23712 | -0.23285 | -0.23712 | -0.18585 | -0.27451 | -0.10147 | 0.14191 | 0.07782 | 0.13275 | 0.10986 | 0.10529 | -0.041199 | 0.082397 | 0.061035 | -0.029907 | -0.069427 | -0.48065 | -0.12283 | -0.033112 | 0.068665 | 0.13733 | 0.036621 | 0.041199 | 0.036621 | 0.027466 | 0.086975 | 122.9553 | 122.6944 | 0.09613
11955.2344 | 0.061035 | 0.23392 | -0.23605 | -0.24139 | -0.18051 | -0.27985 | -0.1239 | 0.13733 | 0.11444 | 0.14191 | 0.10071 | 0.10071 | -0.032043 | 0.10986 | 0.045776 | -0.023499 | -0.058746 | -0.49454 | -0.13031 | -0.03952 | 0.054932 | 0.18768 | 0.064087 | 0.050354 | 0.041199 | 0.018311 | 0.09613 | 122.8592 | 122.699 | 0.10529
11956.9688 | 0.045776 | 0.25635 | -0.23071 | -0.24353 | -0.19546 | -0.29053 | -0.12604 | 0.11444 | 0.073242 | 0.10529 | 0.082397 | 0.10529 | -0.022888 | 0.11902 | 0.076294 | 0.059814 | 0.14313 | -0.50201 | -0.13779 | -0.023499 | 0.064087 | 0.15564 | 0.07782 | 0.07782 | 0.059509 | 0.009155 | 0.09613 | 122.8958 | 122.6669 | 0.1236
11958.75 | 0.061035 | 0.22644 | -0.2243 | -0.24994 | -0.18585 | -0.26382 | -0.11749 | 0.054932 | -0.018311 | 0 | 0.027466 | 0.15106 | 0 | 0.14191 | 0.045776 | -0.007477 | -0.049133 | -0.47745 | -0.13138 | -0.042725 | -0.064087 | 0.032043 | -0.073242 | 0.10071 | 0.07782 | 0.064087 | 0.12817 | 122.8592 | 122.7081 | 0.11444
11960.5625 | 0.061035 | 0.23285 | -0.21896 | -0.2211 | -0.19546 | -0.24674 | -0.11108 | 0.073242 | -0.050354 | -0.018311 | 0 | 0.13275 | 0 | 0.12817 | 0.061035 | 0.003204 | -0.05127 | -0.48065 | -0.11108 | -0.045929 | -0.013733 | 0.027466 | -0.068665 | 0.09613 | 0.064087 | 0.041199 | 0.10986 | 122.9965 | 122.6715 | 0.07782
11962.2812 | 0.045776 | 0.26596 | -0.22964 | -0.23178 | -0.18906 | -0.27878 | -0.11963 | 0.073242 | 0.018311 | 0.07782 | 0.064087 | 0.10986 | -0.018311 | 0.10986 | 0.076294 | -0.018158 | -0.068359 | -0.48492 | -0.14206 | -0.021362 | 0.041199 | 0.13275 | 0.032043 | 0.073242 | 0.050354 | 0.027466 | 0.091553 | 122.8912 | 122.7127 | 0.10986
11964.0781 | 0.045776 | 0.22217 | -0.2179 | -0.25421 | -0.18372 | -0.24567 | -0.1207 | 0.059509 | -0.041199 | 0 | 0.036621 | 0.15564 | 0.018311 | 0.13733 | 0.061035 | 0.070496 | 0.16235 | -0.48172 | -0.11536 | -0.044861 | -0.027466 | 0.059509 | -0.064087 | 0.10986 | 0.09613 | 0.064087 | 0.1236 | 122.9782 | 122.6349 | 0.086975
11965.875 | 0.061035 | 0.21362 | -0.22644 | -0.2243 | -0.19226 | -0.25101 | -0.10788 | 0.032043 | -0.054932 | -0.022888 | 0.022888 | 0.12817 | 0 | 0.13733 | 0.061035 | 0.002136 | -0.070496 | -0.48065 | -0.10468 | -0.032043 | -0.041199 | -0.013733 | -0.09613 | 0.09613 | 0.064087 | 0.059509 | 0.13733 | 122.9874 | 122.6669 | 0.086975
11967.6719 | 0.045776 | 0.23819 | -0.21576 | -0.22858 | -0.18799 | -0.26703 | -0.11643 | 0.10986 | 0.054932 | 0.09613 | 0.10071 | 0.10986 | -0.041199 | 0.10071 | 0.045776 | -0.010681 | -0.05661 | -0.48172 | -0.11108 | -0.042725 | 0.073242 | 0.1236 | 0.027466 | 0.045776 | 0.032043 | 0.013733 | 0.082397 | 122.9782 | 122.6807 | 0.091553
11969.4688 | 0.045776 | 0.23285 | -0.23178 | -0.25101 | -0.17838 | -0.27557 | -0.12283 | 0.009155 | -0.027466 | 0.018311 | 0.004578 | 0.13733 | 0 | 0.14191 | 0.030518 | -0.014954 | -0.05661 | -0.48492 | -0.12283 | -0.021362 | -0.045776 | 0.045776 | -0.082397 | 0.10071 | 0.068665 | 0.059509 | 0.15106 | 122.8638 | 122.7219 | 0.10529
11971.2656 | 0.061035 | 0.21149 | -0.21042 | -0.2446 | -0.18265 | -0.24887 | -0.10895 | 0.013733 | -0.07782 | -0.032043 | 0.009155 | 0.14191 | -0.009155 | 0.1236 | 0.061035 | 0.003204 | -0.059814 | -0.47531 | -0.11856 | -0.028839 | -0.050354 | -0.004578 | -0.10071 | 0.073242 | 0.068665 | 0.054932 | 0.14648 | 122.9645 | 122.6852 | 0.091553
11973.0156 | 0.061035 | 0.22751 | -0.21469 | -0.22644 | -0.19119 | -0.25528 | -0.11108 | 0.022888 | -0.068665 | -0.009155 | 0.004578 | 0.14191 | -0.013733 | 0.14648 | 0.061035 | -0.002136 | -0.055542 | -0.47745 | -0.11108 | -0.040588 | -0.091553 | 0.004578 | -0.12817 | 0.091553 | 0.082397 | 0.054932 | 0.11902 | 122.9507 | 122.7173 | 0.10071
11974.8125 | 0.076294 | 0.22964 | -0.23178 | -0.24246 | -0.17944 | -0.29587 | -0.1207 | 0.11444 | 0.11902 | 0.14191 | 0.10529 | 0.10986 | -0.041199 | 0.10529 | 0.061035 | -0.029907 | -0.069427 | -0.48599 | -0.14206 | -0.042725 | 0.064087 | 0.19684 | 0.054932 | 0.036621 | 0.032043 | 0.013733 | 0.082397 | 122.8821 | 122.7127 | 0.11444
11976.5625 | 0.045776 | 0.22964 | -0.23178 | -0.23178 | -0.1976 | -0.28198 | -0.11643 | 0.10529 | 0.07782 | 0.09613 | 0.09613 | 0.11902 | -0.027466 | 0.1236 | 0.076294 | -0.016022 | -0.061951 | -0.49561 | -0.12497 | -0.041656 | -0.013733 | 0.11902 | 0 | 0.064087 | 0.073242 | 0.041199 | 0.1236 | 122.8455 | 122.7493 | 0.10986
11978.3438 | 0.076294 | 0.24674 | -0.22537 | -0.2243 | -0.18692 | -0.28091 | -0.1239 | 0.13275 | 0.068665 | 0.1236 | 0.07782 | 0.086975 | -0.036621 | 0.091553 | 0.061035 | -0.023499 | -0.070496 | -0.47424 | -0.12924 | -0.029907 | 0.054932 | 0.1236 | 0.036621 | 0.045776 | 0.032043 | 0.022888 | 0.082397 | 122.8821 | 122.7448 | 0.11902
11980.125 | 0.030518 | 0.23712 | -0.21362 | -0.23178 | -0.18906 | -0.25635 | -0.11215 | 0.041199 | -0.10071 | -0.022888 | -0.009155 | 0.14648 | -0.004578 | 0.14648 | 0.045776 | 0.002136 | -0.050201 | -0.47745 | -0.12176 | -0.043793 | -0.050354 | -0.009155 | -0.10986 | 0.091553 | 0.073242 | 0.041199 | 0.12817 | 122.9691 | 122.7036 | 0.09613
11981.8594 | 0.076294 | 0.27664 | -0.23712 | -0.23178 | -0.19546 | -0.29266 | -0.11536 | 0.050354 | 0.018311 | 0.068665 | 0.045776 | 0.11902 | -0.022888 | 0.10986 | 0.045776 | -0.024567 | -0.072632 | -0.49454 | -0.12711 | -0.019226 | 0.009155 | 0.10986 | 0.022888 | 0.050354 | 0.032043 | 0.050354 | 0.11444 | 122.905 | 122.7173 | 0.13275
11983.6406 | 0.045776 | 0.2179 | -0.2179 | -0.24674 | -0.17624 | -0.24353 | -0.11215 | 0.11902 | 0 | 0.036621 | 0.054932 | 0.14648 | 0 | 0.13275 | 0.030518 | 0.22858 | 0.026703 | -0.43152 | -0.11749 | 0.20294 | 0.009155 | 0.07782 | -0.045776 | 0.073242 | 0.09613 | 0.082397 | 0.1236 | 122.9874 | 122.6852 | 0.086975
11985.4375 | 0.045776 | 0.22751 | -0.21896 | -0.23605 | -0.19226 | -0.24887 | -0.10361 | 0.036621 | -0.086975 | -0.032043 | 0.009155 | 0.14191 | 0.009155 | 0.15106 | 0.045776 | 0.004272 | -0.057678 | -0.48172 | -0.11536 | -0.03952 | -0.07782 | -0.013733 | -0.1236 | 0.07782 | 0.068665 | 0.059509 | 0.1236 | 122.9462 | 122.7127 | 0.11444
11987.2344 | 0.061035 | 0.25955 | -0.23285 | -0.25207 | -0.18051 | -0.29587 | -0.12283 | 0.050354 | 0.022888 | 0.086975 | 0.054932 | 0.11444 | -0.045776 | 0.10529 | 0.045776 | -0.019226 | -0.060883 | -0.49667 | -0.13031 | -0.033112 | 0.018311 | 0.13733 | 0.036621 | 0.064087 | 0.054932 | 0.036621 | 0.086975 | 122.9141 | 122.7219 | 0.13275
11988.9688 | 0.061035 | 0.24994 | -0.22751 | -0.2243 | -0.18372 | -0.26062 | -0.12497 | 0.15106 | 0.064087 | 0.1236 | 0.07782 | 0.09613 | -0.054932 | 0.091553 | 0.076294 | -0.012817 | -0.071564 | -0.47745 | -0.11215 | -0.037384 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.041199 | 0.013733 | 0.10529 | 122.9416 | 122.7081 | 0.11902
11990.7656 | 0.076294 | 0.22003 | -0.23712 | -0.24674 | -0.1976 | -0.28732 | -0.11322 | 0.12817 | 0.10071 | 0.13733 | 0.086975 | 0.082397 | -0.041199 | 0.09613 | 0.061035 | -0.008545 | -0.058746 | -0.49133 | -0.12604 | -0.03418 | 0.054932 | 0.18768 | 0.064087 | 0.041199 | 0.032043 | 0.004578 | 0.091553 | 122.8912 | 122.7219 | 0.11902
11992.5781 | 0.076294 | 0.19974 | -0.21576 | -0.2243 | -0.18906 | -0.25207 | -0.11643 | 0.045776 | -0.09613 | -0.041199 | 0.009155 | 0.15106 | 0 | 0.12817 | 0.076294 | 0.001068 | -0.069427 | -0.47745 | -0.10147 | -0.041656 | -0.050354 | -0.013733 | -0.10986 | 0.09613 | 0.082397 | 0.064087 | 0.11902 | 122.9782 | 122.7402 | 0.10529
11994.3125 | 0.045776 | 0.27557 | -0.22858 | -0.23926 | -0.18372 | -0.28839 | -0.12176 | 0.091553 | 0.013733 | 0.082397 | 0.054932 | 0.10529 | -0.032043 | 0.10529 | 0.045776 | -0.011749 | -0.075836 | -0.48813 | -0.13458 | -0.020294 | -0.009155 | 0.09613 | 0.013733 | 0.054932 | 0.041199 | 0.022888 | 0.11902 | 122.8867 | 122.7539 | 0.13275
11996.1094 | 0.045776 | 0.24246 | -0.22751 | -0.25314 | -0.18799 | -0.27878 | -0.12283 | 0.16022 | 0.11444 | 0.15106 | 0.10986 | 0.11444 | -0.032043 | 0.10529 | 0.030518 | -0.014954 | -0.065155 | -0.48386 | -0.13779 | -0.041656 | 0.054932 | 0.19226 | 0.064087 | 0.064087 | 0.045776 | 0.013733 | 0.082397 | 122.9233 | 122.7402 | 0.11444
11997.9062 | 0.045776 | 0.26276 | -0.22003 | -0.23071 | -0.19974 | -0.27771 | -0.12497 | 0.13733 | 0.064087 | 0.11444 | 0.064087 | 0.10071 | -0.050354 | 0.10071 | 0.076294 | -0.007477 | -0.054474 | -0.48386 | -0.11749 | -0.03952 | 0.045776 | 0.10529 | 0.013733 | 0.050354 | 0.041199 | 0.018311 | 0.09613 | 122.8775 | 122.7493 | 0.12817
11999.6875 | 0.045776 | 0.24674 | -0.24033 | -0.24033 | -0.17944 | -0.2713 | -0.12817 | 0.14191 | 0.10071 | 0.11902 | 0.073242 | 0.10529 | -0.036621 | 0.11444 | 0.045776 | -0.003204 | -0.067291 | -0.48386 | -0.11108 | -0.03418 | 0.073242 | 0.10529 | 0.022888 | 0.050354 | 0.045776 | 0.045776 | 0.091553 | 122.905 | 122.7539 | 0.13275
12001.4219 | 0.030518 | 0.22644 | -0.22751 | -0.2243 | -0.20401 | -0.24246 | -0.11536 | 0.045776 | -0.064087 | -0.027466 | 0.009155 | 0.14648 | 0 | 0.14191 | 0.061035 | 0.021362 | -0.063019 | -0.47424 | -0.088654 | -0.037384 | -0.068665 | -0.013733 | -0.13275 | 0.086975 | 0.082397 | 0.054932 | 0.10986 | 122.9828 | 122.7081 | 0.10986
12003.2344 | 0.061035 | 0.22964 | -0.2243 | -0.24353 | -0.19012 | -0.25314 | -0.11429 | 0.073242 | -0.009155 | 0.036621 | 0.041199 | 0.11902 | -0.009155 | 0.11902 | 0.076294 | -0.001068 | -0.066223 | -0.48279 | -0.11536 | -0.030975 | 0.054932 | 0.10071 | 0.022888 | 0.064087 | 0.041199 | 0.036621 | 0.082397 | 123.0331 | 122.7036 | 0.091553
12005.0156 | 0.061035 | 0.22537 | -0.20935 | -0.23498 | -0.19546 | -0.27344 | -0.10468 | 0.13275 | 0.086975 | 0.11902 | 0.09613 | 0.086975 | -0.022888 | 0.09613 | 0.061035 | -0.007477 | -0.060883 | -0.4892 | -0.12497 | -0.030975 | 0.086975 | 0.15106 | 0.041199 | 0.036621 | 0.045776 | 0.022888 | 0.091553 | 123.0011 | 122.731 | 0.09613
12006.75 | 0.045776 | 0.21576 | -0.2179 | -0.23392 | -0.18906 | -0.24246 | -0.11536 | 0.10071 | 0.027466 | 0.027466 | 0.050354 | 0.12817 | 0 | 0.12817 | 0.045776 | 0.009613 | -0.052338 | -0.48706 | -0.11215 | -0.041656 | 0.004578 | 0.073242 | -0.059509 | 0.091553 | 0.054932 | 0.041199 | 0.11902 | 122.9828 | 122.7036 | 0.07782
12008.5469 | 0.061035 | 0.2211 | -0.23712 | -0.25101 | -0.17944 | -0.25848 | -0.11856 | 0.022888 | -0.036621 | -0.004578 | 0.013733 | 0.16022 | 0 | 0.15106 | 0.061035 | 0.002136 | -0.050201 | -0.48813 | -0.1239 | -0.03418 | -0.059509 | 0.054932 | -0.086975 | 0.10529 | 0.082397 | 0.064087 | 0.13275 | 122.9965 | 122.7127 | 0.091553
12010.3438 | 0.045776 | 0.2446 | -0.22217 | -0.22858 | -0.18692 | -0.25314 | -0.11429 | 0.064087 | 0.027466 | 0.032043 | 0.045776 | 0.1236 | 0.013733 | 0.13733 | 0.045776 | 0.11215 | 0.12176 | -0.49774 | -0.11643 | -0.021362 | 0.004578 | 0.09613 | -0.036621 | 0.09613 | 0.086975 | 0.054932 | 0.11902 | 123.0194 | 122.6715 | 0.086975
12012.1406 | 0.061035 | 0.23285 | -0.23392 | -0.2478 | -0.20081 | -0.2948 | -0.1207 | 0.091553 | 0.10529 | 0.15106 | 0.10071 | 0.086975 | -0.027466 | 0.09613 | 0.076294 | -0.005341 | -0.075836 | -0.49347 | -0.14526 | -0.023499 | 0.041199 | 0.18768 | 0.036621 | 0.050354 | 0.045776 | 0.027466 | 0.09613 | 122.8958 | 122.7448 | 0.10986
12013.8594 | 0.061035 | 0.21255 | -0.2243 | -0.24139 | -0.17624 | -0.24887 | -0.10468 | 0.073242 | 0 | 0.022888 | 0.032043 | 0.13275 | -0.018311 | 0.12817 | 0.061035 | 0.019226 | -0.059814 | -0.48065 | -0.10468 | -0.036316 | -0.032043 | 0.045776 | -0.07782 | 0.059509 | 0.064087 | 0.059509 | 0.11902 | 122.9691 | 122.7264 | 0.07782
12015.6562 | 0.045776 | 0.23926 | -0.23285 | -0.25207 | -0.18478 | -0.30548 | -0.11429 | 0.086975 | 0.10986 | 0.13733 | 0.10071 | 0.10986 | -0.050354 | 0.11444 | 0.045776 | 0.10468 | 0.10788 | -0.50736 | -0.13672 | -0.018158 | 0.068665 | 0.19226 | 0.09613 | 0.091553 | 0.059509 | -0.004578 | 0.073242 | 122.9416 | 122.7402 | 0.13733
12017.4531 | 0.061035 | 0.23605 | -0.23071 | -0.22858 | -0.18051 | -0.27451 | -0.1207 | 0.11902 | 0.091553 | 0.10529 | 0.09613 | 0.10071 | -0.045776 | 0.10071 | 0.061035 | 0.004272 | -0.085449 | -0.49667 | -0.10681 | -0.029907 | 0.073242 | 0.14191 | 0.054932 | 0.041199 | 0.018311 | 0.036621 | 0.07782 | 122.9919 | 122.7081 | 0.091553
12019.25 | 0.061035 | 0.23926 | -0.2243 | -0.22858 | -0.17517 | -0.26169 | -0.10895 | 0.12817 | 0.091553 | 0.1236 | 0.10529 | 0.10986 | -0.059509 | 0.091553 | 0.061035 | 0.004272 | -0.067291 | -0.4924 | -0.10681 | -0.029907 | 0.054932 | 0.13275 | 0.041199 | 0.036621 | 0.013733 | 0.009155 | 0.086975 | 123.0194 | 122.7173 | 0.09613
12021.0312 | 0.045776 | 0.23498 | -0.22537 | -0.23285 | -0.18906 | -0.28946 | -0.11322 | 0.068665 | 0.032043 | 0.09613 | 0.068665 | 0.09613 | -0.041199 | 0.11902 | 0.030518 | -0.004272 | -0.060883 | -0.49561 | -0.12283 | -0.030975 | 0 | 0.086975 | 0.009155 | 0.059509 | 0.041199 | 0.032043 | 0.10529 | 122.9095 | 122.7402 | 0.14191
12022.7656 | 0.061035 | 0.23178 | -0.20294 | -0.22858 | -0.18478 | -0.23712 | -0.10468 | 0.09613 | -0.004578 | 0.018311 | 0.036621 | 0.13275 | -0.004578 | 0.14191 | 0.061035 | 0.013885 | -0.069427 | -0.47531 | -0.1207 | -0.05127 | -0.018311 | 0.036621 | -0.09613 | 0.086975 | 0.068665 | 0.059509 | 0.10529 | 122.9919 | 122.7356 | 0.082397
12024.5625 | 0.076294 | 0.23498 | -0.22003 | -0.25101 | -0.17731 | -0.26276 | -0.10254 | 0.027466 | -0.036621 | -0.009155 | 0.013733 | 0.12817 | 0.004578 | 0.13275 | 0.061035 | 0.019226 | -0.064087 | -0.47424 | -0.11536 | -0.029907 | -0.013733 | 0.027466 | -0.064087 | 0.082397 | 0.054932 | 0.054932 | 0.11902 | 123.0469 | 122.7173 | 0.068665
12026.2969 | 0.045776 | 0.26062 | -0.21149 | -0.23926 | -0.18265 | -0.28732 | -0.12283 | 0.10071 | 0.086975 | 0.11444 | 0.073242 | 0.10071 | -0.032043 | 0.11444 | 0.045776 | 0.003204 | -0.085449 | -0.48065 | -0.13245 | -0.018158 | 0.032043 | 0.11902 | 0.018311 | 0.064087 | 0.041199 | 0.036621 | 0.10529 | 122.9095 | 122.7905 | 0.13275
12028.1094 | 0.091553 | 0.25635 | -0.2243 | -0.25101 | -0.19012 | -0.27878 | -0.1239 | 0.11444 | 0.07782 | 0.10071 | 0.082397 | 0.091553 | -0.050354 | 0.10529 | 0.061035 | 0.011749 | -0.082245 | -0.47424 | -0.12924 | -0.037384 | 0.050354 | 0.10986 | 0.027466 | 0.054932 | 0.041199 | 0.036621 | 0.091553 | 122.905 | 122.7676 | 0.10986
12029.8906 | 0.061035 | 0.27878 | -0.2179 | -0.23392 | -0.21255 | -0.28732 | -0.12497 | 0.068665 | 0.036621 | 0.073242 | 0.068665 | 0.12817 | -0.022888 | 0.10071 | 0.061035 | -0.003204 | -0.088654 | -0.49454 | -0.13031 | -0.038452 | 0.032043 | 0.11902 | 0.041199 | 0.054932 | 0.041199 | 0.018311 | 0.09613 | 122.9507 | 122.7539 | 0.11902
12031.6875 | 0.061035 | 0.24246 | -0.22644 | -0.23819 | -0.18906 | -0.29266 | -0.11322 | 0.13275 | 0.11902 | 0.12817 | 0.10071 | 0.11444 | -0.032043 | 0.10986 | 0.061035 | 0.002136 | -0.0737 | -0.48706 | -0.1239 | -0.041656 | 0.064087 | 0.19684 | 0.054932 | 0.041199 | 0.032043 | 0.018311 | 0.10071 | 122.9462 | 122.7356 | 0.10986
12033.4219 | 0.061035 | 0.23392 | -0.22537 | -0.23926 | -0.18051 | -0.2446 | -0.11536 | 0.068665 | -0.022888 | -0.004578 | 0.041199 | 0.12817 | 0 | 0.11444 | 0.076294 | 0.014954 | -0.070496 | -0.4892 | -0.10254 | -0.046997 | -0.022888 | 0.068665 | -0.054932 | 0.091553 | 0.054932 | 0.050354 | 0.10986 | 123.0331 | 122.731 | 0.086975
12035.2188 | 0.061035 | 0.24887 | -0.23178 | -0.23392 | -0.18585 | -0.25635 | -0.10147 | 0.14191 | 0.059509 | 0.10986 | 0.07782 | 0.10529 | -0.059509 | 0.10071 | 0.061035 | 0 | -0.076904 | -0.47958 | -0.11536 | -0.042725 | 0.068665 | 0.14191 | 0.036621 | 0.032043 | 0.050354 | 0.009155 | 0.10529 | 123.0377 | 122.7631 | 0.09613
12036.9531 | 0.061035 | 0.2179 | -0.22537 | -0.22751 | -0.18158 | -0.24674 | -0.11002 | 0.041199 | -0.07782 | -0.045776 | 0.009155 | 0.14648 | -0.018311 | 0.14648 | 0.045776 | 0.014954 | -0.050201 | -0.47531 | -0.11643 | -0.03952 | -0.050354 | 0.004578 | -0.09613 | 0.091553 | 0.064087 | 0.059509 | 0.1236 | 122.9965 | 122.7402 | 0.10071
12038.7344 | 0.061035 | 0.25742 | -0.22751 | -0.23392 | -0.19012 | -0.28412 | -0.10468 | 0.10529 | 0.091553 | 0.1236 | 0.073242 | 0.10529 | -0.050354 | 0.10986 | 0.076294 | -0.007477 | -0.075836 | -0.49881 | -0.12176 | -0.037384 | 0.064087 | 0.11444 | 0.032043 | 0.041199 | 0.022888 | 0.032043 | 0.11444 | 122.9324 | 122.7859 | 0.13275
12040.4688 | 0.045776 | 0.21683 | -0.20828 | -0.23392 | -0.18265 | -0.24139 | -0.099335 | 0.054932 | -0.068665 | -0.013733 | 0.022888 | 0.14191 | 0.004578 | 0.14191 | 0.061035 | 0.016022 | -0.060883 | -0.47638 | -0.10788 | -0.033112 | -0.068665 | -0.004578 | -0.11444 | 0.091553 | 0.07782 | 0.068665 | 0.13733 | 123.0057 | 122.7585 | 0.10071
12042.2656 | 0.061035 | 0.22003 | -0.22858 | -0.25314 | -0.18478 | -0.26596 | -0.10147 | 0.054932 | -0.041199 | -0.004578 | 0.022888 | 0.1236 | 0 | 0.13275 | 0.045776 | 0.010681 | -0.046997 | -0.48599 | -0.12176 | -0.033112 | -0.054932 | 0.045776 | -0.064087 | 0.073242 | 0.07782 | 0.073242 | 0.13733 | 123.0377 | 122.7356 | 0.082397
12044.0469 | 0.045776 | 0.22751 | -0.2211 | -0.24139 | -0.17944 | -0.26276 | -0.11215 | 0.027466 | -0.073242 | -0.022888 | 0.013733 | 0.13275 | -0.004578 | 0.13733 | 0.076294 | 0.016022 | -0.070496 | -0.47531 | -0.11108 | -0.036316 | -0.041199 | 0.013733 | -0.07782 | 0.10071 | 0.086975 | 0.045776 | 0.1236 | 123.0515 | 122.7539 | 0.10071
12045.7812 | 0.030518 | 0.23498 | -0.21255 | -0.23285 | -0.17944 | -0.25207 | -0.10361 | 0.11444 | 0.013733 | 0.032043 | 0.045776 | 0.12817 | -0.022888 | 0.13733 | 0.061035 | 0.02243 | -0.057678 | -0.48706 | -0.11643 | -0.033112 | -0.004578 | 0.07782 | -0.059509 | 0.073242 | 0.07782 | 0.054932 | 0.10529 | 123.0057 | 122.7448 | 0.068665
12047.5938 | 0.061035 | 0.24139 | -0.2211 | -0.23178 | -0.19012 | -0.27557 | -0.11963 | 0.027466 | -0.045776 | -0.027466 | 0.009155 | 0.12817 | 0.009155 | 0.14648 | 0.045776 | 0.008545 | -0.071564 | -0.48172 | -0.13138 | -0.028839 | -0.064087 | 0.050354 | -0.07782 | 0.09613 | 0.086975 | 0.064087 | 0.11902 | 123.0011 | 122.7631 | 0.082397
12049.3906 | 0.045776 | 0.2446 | -0.22217 | -0.25207 | -0.18158 | -0.28625 | -0.11643 | 0.091553 | 0.045776 | 0.073242 | 0.068665 | 0.12817 | -0.013733 | 0.11902 | 0.045776 | 0.002136 | -0.065155 | -0.49133 | -0.13672 | -0.033112 | -0.027466 | 0.10071 | -0.027466 | 0.082397 | 0.064087 | 0.054932 | 0.1236 | 122.9004 | 122.7951 | 0.13733
12051.125 | 0.030518 | 0.24567 | -0.23712 | -0.24994 | -0.19974 | -0.28839 | -0.12711 | 0.10986 | 0.09613 | 0.14191 | 0.091553 | 0.09613 | -0.027466 | 0.11902 | 0.061035 | -0.008545 | -0.066223 | -0.48492 | -0.13992 | -0.041656 | 0.036621 | 0.19226 | 0.045776 | 0.045776 | 0.036621 | 0.022888 | 0.091553 | 122.9233 | 122.7585 | 0.11444
12052.9375 | 0.030518 | 0.22751 | -0.22858 | -0.23819 | -0.18051 | -0.2713 | -0.1207 | 0.027466 | -0.041199 | -0.013733 | 0 | 0.15106 | -0.004578 | 0.12817 | 0.030518 | 0.010681 | -0.076904 | -0.48386 | -0.12176 | -0.045929 | -0.086975 | 0.045776 | -0.07782 | 0.10071 | 0.082397 | 0.064087 | 0.13275 | 122.937 | 122.7905 | 0.1236
12054.7188 | 0.045776 | 0.23819 | -0.22644 | -0.22644 | -0.18906 | -0.26489 | -0.12604 | 0.032043 | -0.036621 | 0.009155 | 0.013733 | 0.14191 | 0.018311 | 0.14648 | 0.061035 | 0.006409 | -0.061951 | -0.47531 | -0.1239 | -0.028839 | -0.054932 | 0.036621 | -0.07782 | 0.10986 | 0.086975 | 0.068665 | 0.14191 | 122.937 | 122.7722 | 0.13275
12056.4531 | 0.076294 | 0.25314 | -0.22003 | -0.22324 | -0.18265 | -0.25528 | -0.12283 | 0.13275 | 0.041199 | 0.091553 | 0.09613 | 0.10071 | -0.045776 | 0.091553 | 0.045776 | 0.001068 | -0.068359 | -0.48492 | -0.11002 | -0.037384 | 0.068665 | 0.13733 | 0.032043 | 0.041199 | 0.027466 | 0.027466 | 0.10986 | 123.056 | 122.7539 | 0.091553
12058.25 | 0.045776 | 0.23605 | -0.22751 | -0.24139 | -0.17944 | -0.28839 | -0.11108 | 0.11902 | 0.086975 | 0.11444 | 0.10071 | 0.10986 | -0.022888 | 0.10071 | 0.076294 | -0.010681 | -0.069427 | -0.49454 | -0.12176 | -0.036316 | 0.027466 | 0.16022 | 0.050354 | 0.050354 | 0.054932 | 0.009155 | 0.10529 | 122.9233 | 122.7997 | 0.1236
12060.0312 | 0.061035 | 0.26489 | -0.23498 | -0.23819 | -0.17303 | -0.27023 | -0.11429 | 0.1236 | 0.068665 | 0.10529 | 0.091553 | 0.09613 | -0.050354 | 0.082397 | 0.061035 | -0.008545 | -0.067291 | -0.48813 | -0.1207 | -0.03418 | 0.054932 | 0.10529 | 0.036621 | 0.073242 | 0.036621 | 0.036621 | 0.10529 | 122.9324 | 122.8134 | 0.13275
12061.8125 | 0.045776 | 0.22964 | -0.22858 | -0.25314 | -0.17838 | -0.25421 | -0.11215 | 0.041199 | -0.050354 | -0.018311 | 0.018311 | 0.15106 | -0.004578 | 0.14648 | 0.045776 | 0.003204 | -0.058746 | -0.48172 | -0.12283 | -0.040588 | -0.041199 | 0.059509 | -0.086975 | 0.086975 | 0.082397 | 0.059509 | 0.13733 | 123.0469 | 122.7402 | 0.082397
12063.6094 | 0.045776 | 0.25421 | -0.22217 | -0.23071 | -0.18265 | -0.26703 | -0.11643 | 0.13275 | 0.07782 | 0.13275 | 0.086975 | 0.082397 | -0.041199 | 0.091553 | 0.045776 | -0.008545 | -0.067291 | -0.48813 | -0.1239 | -0.03418 | 0.073242 | 0.14648 | 0.041199 | 0.059509 | 0.036621 | 0.027466 | 0.07782 | 122.9782 | 122.7814 | 0.13733
12065.3438 | 0.076294 | 0.2243 | -0.22858 | -0.23926 | -0.19333 | -0.25207 | -0.11429 | 0.041199 | -0.07782 | -0.027466 | 0 | 0.13733 | 0.004578 | 0.14191 | 0.061035 | 0.008545 | -0.065155 | -0.48172 | -0.11429 | -0.03418 | -0.050354 | -0.018311 | -0.10071 | 0.086975 | 0.068665 | 0.054932 | 0.1236 | 123.0515 | 122.7631 | 0.09613
12067.125 | 0.045776 | 0.22858 | -0.21683 | -0.23926 | -0.18478 | -0.26596 | -0.11002 | 0.045776 | -0.022888 | 0.009155 | 0.013733 | 0.13275 | 0 | 0.13733 | 0.045776 | 0.008545 | -0.059814 | -0.47745 | -0.10895 | -0.030975 | 0.004578 | 0.032043 | -0.050354 | 0.064087 | 0.059509 | 0.050354 | 0.1236 | 123.0743 | 122.7448 | 0.091553
12068.875 | 0.030518 | 0.23178 | -0.22537 | -0.24033 | -0.19653 | -0.2681 | -0.11002 | 0.1236 | 0.082397 | 0.10986 | 0.09613 | 0.10986 | -0.041199 | 0.10071 | 0.076294 | 0.003204 | -0.067291 | -0.48065 | -0.12176 | -0.030975 | 0.064087 | 0.12817 | 0.041199 | 0.027466 | 0.027466 | 0.027466 | 0.10071 | 123.0606 | 122.7585 | 0.10529
12070.6875 | 0.030518 | 0.23605 | -0.21896 | -0.2478 | -0.19012 | -0.24353 | -0.10788 | 0.10071 | 0.009155 | 0.032043 | 0.045776 | 0.10986 | -0.013733 | 0.13733 | 0.045776 | 0.004272 | -0.067291 | -0.47852 | -0.11536 | -0.044861 | 0.004578 | 0.091553 | -0.050354 | 0.059509 | 0.07782 | 0.050354 | 0.11902 | 123.0606 | 122.7493 | 0.086975
12072.5 | 0.061035 | 0.23285 | -0.2478 | -0.25848 | -0.20081 | -0.28732 | -0.11749 | 0.10529 | 0.10986 | 0.14191 | 0.09613 | 0.09613 | -0.032043 | 0.082397 | 0.061035 | -0.018158 | -0.075836 | -0.49774 | -0.1442 | -0.037384 | 0.054932 | 0.19226 | 0.064087 | 0.054932 | 0.036621 | 0.013733 | 0.10071 | 122.9599 | 122.7997 | 0.11902
12074.2812 | 0.061035 | 0.24139 | -0.21576 | -0.25207 | -0.18051 | -0.2681 | -0.11215 | 0.036621 | -0.054932 | -0.009155 | 0 | 0.13733 | 0.004578 | 0.14648 | 0.061035 | 0.005341 | -0.067291 | -0.48386 | -0.12283 | -0.033112 | -0.064087 | 0.032043 | -0.073242 | 0.091553 | 0.086975 | 0.064087 | 0.13275 | 122.9691 | 122.7951 | 0.11902
12076.0625 | 0.045776 | 0.26276 | -0.2179 | -0.23071 | -0.19226 | -0.27985 | -0.11002 | 0.10986 | 0.082397 | 0.11444 | 0.07782 | 0.10986 | -0.054932 | 0.091553 | 0.061035 | -0.007477 | -0.084381 | -0.48065 | -0.12497 | -0.025635 | 0.041199 | 0.10986 | 0.022888 | 0.050354 | 0.036621 | 0.032043 | 0.091553 | 122.937 | 122.8226 | 0.13733
12077.8594 | 0.045776 | 0.23071 | -0.22324 | -0.23178 | -0.19333 | -0.26276 | -0.11536 | 0.13733 | 0.059509 | 0.1236 | 0.091553 | 0.10529 | -0.059509 | 0.09613 | 0.061035 | 0.016022 | -0.067291 | -0.47958 | -0.12283 | -0.036316 | 0.064087 | 0.13733 | 0.041199 | 0.041199 | 0.013733 | 0.027466 | 0.091553 | 123.056 | 122.7585 | 0.086975
12079.5938 | 0.061035 | 0.23819 | -0.23819 | -0.2446 | -0.17624 | -0.298 | -0.12283 | 0.14648 | 0.11444 | 0.13275 | 0.11444 | 0.10529 | -0.027466 | 0.091553 | 0.061035 | -0.016022 | -0.074768 | -0.49454 | -0.13886 | -0.033112 | 0.091553 | 0.19684 | 0.086975 | 0.050354 | 0.050354 | 0.018311 | 0.086975 | 122.9874 | 122.7997 | 0.11444
12081.4062 | 0.045776 | 0.23392 | -0.22751 | -0.23605 | -0.18158 | -0.24246 | -0.09079 | 0.086975 | 0.009155 | 0.018311 | 0.045776 | 0.13275 | 0.004578 | 0.13275 | 0.061035 | 0.020294 | -0.069427 | -0.48386 | -0.10574 | -0.038452 | -0.036621 | 0.022888 | -0.10071 | 0.086975 | 0.059509 | 0.050354 | 0.13275 | 123.024 | 122.7951 | 0.091553
12083.2031 | 0.045776 | 0.27237 | -0.22964 | -0.24139 | -0.18906 | -0.28732 | -0.11002 | 0.054932 | 0.041199 | 0.082397 | 0.073242 | 0.11902 | -0.013733 | 0.10986 | 0.061035 | -0.016022 | -0.065155 | -0.49347 | -0.14099 | -0.028839 | 0.022888 | 0.10986 | 0.027466 | 0.073242 | 0.018311 | 0.036621 | 0.086975 | 122.9965 | 122.7859 | 0.11444
12084.9219 | 0.061035 | 0.23071 | -0.21683 | -0.25742 | -0.18585 | -0.25101 | -0.11429 | 0.032043 | -0.045776 | -0.009155 | 0.022888 | 0.13733 | 0.004578 | 0.13733 | 0.061035 | 0.013885 | -0.048065 | -0.47852 | -0.12283 | -0.032043 | -0.054932 | 0.041199 | -0.082397 | 0.086975 | 0.073242 | 0.073242 | 0.13275 | 123.0606 | 122.7768 | 0.086975
12086.7188 | 0.061035 | 0.24246 | -0.23392 | -0.24887 | -0.19226 | -0.29266 | -0.1239 | 0.10986 | 0.13275 | 0.11902 | 0.09613 | 0.10071 | -0.041199 | 0.11444 | 0.045776 | -0.007477 | -0.061951 | -0.48065 | -0.13458 | -0.035248 | 0.054932 | 0.19226 | 0.059509 | 0.050354 | 0.050354 | 0.027466 | 0.09613 | 122.9874 | 122.7768 | 0.10986
12088.5156 | 0.045776 | 0.23712 | -0.20721 | -0.24246 | -0.18265 | -0.26489 | -0.1207 | 0.086975 | 0 | 0.022888 | 0.041199 | 0.13733 | -0.018311 | 0.1236 | 0.045776 | 0.001068 | -0.069427 | -0.48492 | -0.11215 | -0.03952 | 0.045776 | 0.07782 | -0.009155 | 0.059509 | 0.059509 | 0.013733 | 0.09613 | 123.0881 | 122.7676 | 0.086975
12090.2344 | 0.076294 | 0.25635 | -0.22324 | -0.23926 | -0.1944 | -0.28198 | -0.11963 | 0.059509 | 0.018311 | 0.082397 | 0.050354 | 0.11444 | -0.022888 | 0.10986 | 0.076294 | -0.008545 | -0.054474 | -0.49133 | -0.12817 | -0.029907 | 0.027466 | 0.11902 | 0.027466 | 0.050354 | 0.050354 | 0.027466 | 0.10986 | 123.0057 | 122.8226 | 0.14191
12092.0312 | 0.061035 | 0.23926 | -0.21149 | -0.22324 | -0.1741 | -0.24887 | -0.11215 | 0.07782 | -0.009155 | 0.018311 | 0.032043 | 0.1236 | -0.013733 | 0.1236 | 0.061035 | 0.001068 | -0.068359 | -0.49133 | -0.10681 | -0.040588 | 0.050354 | 0.086975 | -0.027466 | 0.059509 | 0.045776 | 0.004578 | 0.086975 | 123.0972 | 122.7859 | 0.086975
12093.8281 | 0.061035 | 0.22537 | -0.22537 | -0.23285 | -0.1944 | -0.2446 | -0.11322 | 0.073242 | -0.013733 | 0.009155 | 0.032043 | 0.13275 | 0.018311 | 0.12817 | 0.045776 | 0.010681 | -0.061951 | -0.48706 | -0.10574 | -0.048065 | -0.050354 | 0.027466 | -0.10071 | 0.082397 | 0.064087 | 0.054932 | 0.14191 | 123.0331 | 122.7905 | 0.10529
12095.5781 | 0.045776 | 0.23498 | -0.21896 | -0.22858 | -0.17838 | -0.25742 | -0.10468 | 0.10986 | 0.036621 | 0.073242 | 0.064087 | 0.11444 | -0.027466 | 0.10071 | 0.076294 | 0.016022 | -0.072632 | -0.4892 | -0.11856 | -0.032043 | 0.059509 | 0.11902 | 0.022888 | 0.036621 | 0.041199 | 0.027466 | 0.082397 | 123.0835 | 122.7951 | 0.082397
12097.375 | 0.030518 | 0.22964 | -0.22003 | -0.24033 | -0.19974 | -0.2478 | -0.10468 | 0.10071 | 0.018311 | 0.036621 | 0.045776 | 0.13275 | -0.004578 | 0.15106 | 0.045776 | 0.016022 | -0.065155 | -0.48386 | -0.11002 | -0.032043 | -0.004578 | 0.09613 | -0.050354 | 0.082397 | 0.07782 | 0.059509 | 0.12817 | 123.0835 | 122.7585 | 0.082397
12099.1719 | 0.076294 | 0.23285 | -0.23392 | -0.26062 | -0.17944 | -0.27985 | -0.11215 | 0.07782 | 0.068665 | 0.07782 | 0.059509 | 0.10071 | -0.032043 | 0.1236 | 0.045776 | 0 | -0.072632 | -0.48065 | -0.13138 | -0.037384 | -0.018311 | 0.10529 | -0.032043 | 0.059509 | 0.041199 | 0.041199 | 0.1236 | 122.9553 | 122.7951 | 0.1236
12100.9844 | 0.045776 | 0.24674 | -0.21683 | -0.23178 | -0.19119 | -0.26489 | -0.11108 | 0.13733 | 0.082397 | 0.11444 | 0.086975 | 0.10071 | -0.032043 | 0.09613 | 0.061035 | 0 | -0.080109 | -0.48065 | -0.11643 | -0.041656 | 0.068665 | 0.1236 | 0.045776 | 0.064087 | 0.022888 | 0.027466 | 0.086975 | 123.0835 | 122.7997 | 0.07782
12102.7188 | 0.045776 | 0.26703 | -0.22644 | -0.24033 | -0.1741 | -0.28625 | -0.12817 | 0.13275 | 0.1236 | 0.12817 | 0.086975 | 0.10071 | -0.041199 | 0.10071 | 0.030518 | -0.002136 | -0.080109 | -0.49667 | -0.13351 | -0.035248 | 0.064087 | 0.18768 | 0.082397 | 0.054932 | 0.036621 | 0.022888 | 0.086975 | 122.9828 | 122.8088 | 0.11444
12104.5156 | 0.061035 | 0.22003 | -0.22537 | -0.25848 | -0.18478 | -0.25955 | -0.11963 | 0.036621 | -0.050354 | -0.009155 | 0.009155 | 0.14648 | 0.009155 | 0.16022 | 0.061035 | 0.011749 | -0.060883 | -0.47958 | -0.13565 | -0.041656 | -0.059509 | 0.027466 | -0.068665 | 0.082397 | 0.07782 | 0.073242 | 0.14648 | 122.9874 | 122.8088 | 0.09613
12106.2344 | 0.061035 | 0.23392 | -0.22751 | -0.22003 | -0.18799 | -0.25848 | -0.10681 | 0.068665 | -0.041199 | 0.004578 | 0.022888 | 0.12817 | -0.027466 | 0.13733 | 0.045776 | 0.012817 | -0.070496 | -0.47638 | -0.12176 | -0.041656 | 0.009155 | 0.054932 | -0.032043 | 0.082397 | 0.064087 | 0.059509 | 0.10529 | 123.1155 | 122.7631 | 0.10071
12108.0469 | 0.045776 | 0.23392 | -0.22324 | -0.22537 | -0.18692 | -0.24674 | -0.11002 | 0.10071 | 0.009155 | 0.018311 | 0.054932 | 0.12817 | 0 | 0.1236 | 0.061035 | 0.02243 | -0.069427 | -0.47424 | -0.10147 | -0.038452 | -0.018311 | 0.059509 | -0.064087 | 0.082397 | 0.068665 | 0.059509 | 0.1236 | 123.056 | 122.7951 | 0.09613
12109.8281 | 0.061035 | 0.23712 | -0.23712 | -0.24246 | -0.18478 | -0.2948 | -0.11536 | 0.11902 | 0.09613 | 0.12817 | 0.10529 | 0.10986 | -0.050354 | 0.10071 | 0.076294 | -0.012817 | -0.075836 | -0.48279 | -0.14206 | -0.030975 | 0.073242 | 0.20142 | 0.09613 | 0.050354 | 0.027466 | 0.004578 | 0.091553 | 123.0057 | 122.8363 | 0.10986
12111.5625 | 0.061035 | 0.23605 | -0.23285 | -0.23071 | -0.17838 | -0.24353 | -0.11002 | 0.11444 | 0.009155 | 0.036621 | 0.059509 | 0.13275 | 0.004578 | 0.1236 | 0.045776 | 0.02243 | -0.085449 | -0.47638 | -0.11002 | -0.040588 | 0.009155 | 0.10071 | -0.045776 | 0.082397 | 0.068665 | 0.050354 | 0.1236 | 123.0927 | 122.7768 | 0.086975
12113.3594 | 0.030518 | 0.23178 | -0.22644 | -0.2478 | -0.18372 | -0.26489 | -0.11749 | 0.013733 | -0.027466 | -0.018311 | 0.013733 | 0.15106 | 0.004578 | 0.14648 | 0.045776 | 0.004272 | -0.058746 | -0.49027 | -0.12711 | -0.028839 | -0.068665 | 0.045776 | -0.073242 | 0.082397 | 0.07782 | 0.073242 | 0.12817 | 122.9828 | 122.8271 | 0.10986
12115.1562 | 0.061035 | 0.23392 | -0.21896 | -0.24994 | -0.17838 | -0.27344 | -0.12497 | 0.032043 | 0.004578 | 0.018311 | 0.018311 | 0.13275 | -0.004578 | 0.13733 | 0.076294 | 0.003204 | -0.0737 | -0.49027 | -0.12817 | -0.029907 | -0.068665 | 0.059509 | -0.054932 | 0.091553 | 0.082397 | 0.068665 | 0.13275 | 122.9828 | 122.8271 | 0.11902
12116.9688 | 0.061035 | 0.21683 | -0.21362 | -0.25101 | -0.17517 | -0.25421 | -0.11108 | 0.068665 | -0.032043 | 0.004578 | 0.036621 | 0.14191 | -0.004578 | 0.13275 | 0.045776 | 0.010681 | -0.064087 | -0.48599 | -0.13565 | -0.036316 | -0.018311 | 0.086975 | -0.045776 | 0.082397 | 0.07782 | 0.059509 | 0.11902 | 123.1018 | 122.7722 | 0.10529
12118.7031 | 0.045776 | 0.24674 | -0.21896 | -0.23819 | -0.18158 | -0.26916 | -0.11215 | 0.09613 | 0.073242 | 0.091553 | 0.086975 | 0.07782 | -0.041199 | 0.10071 | 0.076294 | 0.005341 | -0.076904 | -0.48279 | -0.12817 | -0.030975 | 0.050354 | 0.13275 | 0.036621 | 0.050354 | 0.022888 | 0.013733 | 0.09613 | 123.0927 | 122.7859 | 0.10529
12120.5 | 0.061035 | 0.21896 | -0.21683 | -0.22964 | -0.18478 | -0.25207 | -0.11215 | 0.091553 | 0.004578 | 0.041199 | 0.068665 | 0.12817 | -0.013733 | 0.15106 | 0.076294 | 0.02243 | -0.0737 | -0.4892 | -0.10574 | -0.046997 | 0 | 0.10071 | -0.041199 | 0.086975 | 0.064087 | 0.054932 | 0.1236 | 123.0927 | 122.7676 | 0.086975
12122.2969 | 0.061035 | 0.27237 | -0.22324 | -0.24033 | -0.17838 | -0.29373 | -0.11856 | 0.068665 | 0.036621 | 0.086975 | 0.050354 | 0.09613 | -0.018311 | 0.10529 | 0.061035 | -0.005341 | -0.083313 | -0.47958 | -0.13886 | -0.027771 | -0.004578 | 0.09613 | 0.027466 | 0.059509 | 0.041199 | 0.032043 | 0.091553 | 122.9736 | 122.8455 | 0.12817
12124.0938 | 0.076294 | 0.26169 | -0.22644 | -0.22964 | -0.18372 | -0.29266 | -0.11643 | 0.091553 | 0.054932 | 0.082397 | 0.041199 | 0.10071 | -0.032043 | 0.10071 | 0.045776 | -0.005341 | -0.092926 | -0.4892 | -0.12817 | -0.030975 | 0.009155 | 0.10986 | 0.013733 | 0.045776 | 0.054932 | 0.036621 | 0.10986 | 122.9736 | 122.8455 | 0.14191
12125.8906 | 0.076294 | 0.22858 | -0.22644 | -0.22858 | -0.18906 | -0.26382 | -0.12604 | 0.045776 | -0.018311 | 0 | 0.009155 | 0.14191 | -0.009155 | 0.14648 | 0.045776 | 0.007477 | -0.067291 | -0.48813 | -0.12283 | -0.025635 | -0.064087 | 0.036621 | -0.068665 | 0.10071 | 0.086975 | 0.07782 | 0.12817 | 123.0057 | 122.818 | 0.10986
12127.7031 | 0.076294 | 0.2179 | -0.21362 | -0.22644 | -0.17624 | -0.24994 | -0.1004 | 0.09613 | 0.004578 | 0.036621 | 0.045776 | 0.14191 | 0.004578 | 0.12817 | 0.061035 | 0.02243 | -0.065155 | -0.48599 | -0.10468 | -0.043793 | 0.009155 | 0.086975 | -0.032043 | 0.082397 | 0.068665 | 0.050354 | 0.10529 | 123.0881 | 122.7768 | 0.086975
12129.4531 | 0.061035 | 0.24139 | -0.23285 | -0.26276 | -0.18799 | -0.29373 | -0.11749 | 0.086975 | 0.045776 | 0.10529 | 0.073242 | 0.10986 | -0.032043 | 0.10529 | 0.045776 | -0.011749 | -0.066223 | -0.4924 | -0.1474 | -0.032043 | 0.050354 | 0.15106 | 0.073242 | 0.054932 | 0.036621 | 0.013733 | 0.10529 | 123.024 | 122.8317 | 0.11902
12131.25 | 0.045776 | 0.22537 | -0.21896 | -0.24994 | -0.18906 | -0.25101 | -0.10788 | 0.09613 | 0.004578 | 0.022888 | 0.032043 | 0.14191 | 0 | 0.14191 | 0.045776 | 0.029907 | -0.054474 | -0.48279 | -0.11643 | -0.042725 | -0.004578 | 0.086975 | -0.050354 | 0.086975 | 0.064087 | 0.059509 | 0.11902 | 123.1018 | 122.7905 | 0.082397
12132.9844 | 0.015259 | 0.22858 | -0.2243 | -0.24246 | -0.16876 | -0.2713 | -0.1004 | 0.041199 | -0.036621 | 0 | 0.009155 | 0.12817 | 0.004578 | 0.14648 | 0.061035 | 0.016022 | -0.063019 | -0.48172 | -0.13245 | -0.035248 | -0.054932 | 0.050354 | -0.073242 | 0.09613 | 0.091553 | 0.068665 | 0.14648 | 122.9919 | 122.8363 | 0.10529
12134.7656 | 0.076294 | 0.22644 | -0.21683 | -0.25528 | -0.18372 | -0.26276 | -0.11322 | 0.027466 | -0.064087 | 0 | 0.036621 | 0.14191 | -0.004578 | 0.12817 | 0.061035 | 0.020294 | -0.052338 | -0.47958 | -0.12711 | -0.029907 | -0.054932 | 0.054932 | -0.073242 | 0.086975 | 0.07782 | 0.068665 | 0.11444 | 123.0881 | 122.7905 | 0.086975
12136.5 | 0.045776 | 0.2243 | -0.21042 | -0.22751 | -0.17517 | -0.24994 | -0.11429 | 0.10986 | 0.018311 | 0.027466 | 0.054932 | 0.1236 | -0.013733 | 0.11902 | 0.061035 | 0.019226 | -0.069427 | -0.46783 | -0.099335 | -0.040588 | -0.013733 | 0.064087 | -0.068665 | 0.07782 | 0.059509 | 0.064087 | 0.11444 | 123.0606 | 122.818 | 0.10529
12138.3125 | 0.061035 | 0.23605 | -0.2211 | -0.25314 | -0.17517 | -0.26916 | -0.11963 | 0.013733 | -0.036621 | -0.013733 | 0.013733 | 0.14648 | 0.004578 | 0.15106 | 0.045776 | 0.004272 | -0.052338 | -0.47958 | -0.11856 | -0.023499 | -0.059509 | 0.059509 | -0.082397 | 0.086975 | 0.073242 | 0.07782 | 0.13733 | 123.0652 | 122.8088 | 0.09613
12140.1094 | 0.076294 | 0.2446 | -0.21683 | -0.22537 | -0.1976 | -0.26916 | -0.11749 | 0.10986 | 0.064087 | 0.10071 | 0.09613 | 0.10071 | -0.041199 | 0.10986 | 0.10681 | 0.003204 | -0.069427 | -0.48706 | -0.10468 | -0.026703 | 0.064087 | 0.13275 | 0.059509 | 0.027466 | 0.032043 | 0.013733 | 0.07782 | 123.1064 | 122.8043 | 0.09613
12141.8281 | 0.061035 | 0.22217 | -0.22644 | -0.23712 | -0.19012 | -0.25421 | -0.10361 | 0.10071 | 0.022888 | 0.032043 | 0.054932 | 0.11902 | -0.018311 | 0.13275 | 0.061035 | 0.016022 | -0.080109 | -0.47424 | -0.11536 | -0.033112 | -0.004578 | 0.073242 | -0.064087 | 0.064087 | 0.082397 | 0.041199 | 0.12817 | 123.0743 | 122.8226 | 0.086975
12143.6406 | 0.045776 | 0.23498 | -0.23392 | -0.24246 | -0.19333 | -0.29907 | -0.11643 | 0.086975 | 0.068665 | 0.10071 | 0.082397 | 0.091553 | -0.022888 | 0.11444 | 0.061035 | 0.001068 | -0.074768 | -0.49881 | -0.13458 | -0.032043 | -0.004578 | 0.12817 | 0 | 0.068665 | 0.064087 | 0.036621 | 0.10986 | 122.9782 | 122.8683 | 0.11444
12145.3906 | 0.045776 | 0.22858 | -0.21683 | -0.25314 | -0.18372 | -0.27771 | -0.11643 | 0.13275 | 0.082397 | 0.13275 | 0.086975 | 0.086975 | -0.036621 | 0.086975 | 0.061035 | 0 | -0.069427 | -0.47958 | -0.13245 | -0.03418 | 0.059509 | 0.14648 | 0.045776 | 0.041199 | 0.036621 | 0.036621 | 0.068665 | 123.024 | 122.8226 | 0.09613
12147.1875 | 0.061035 | 0.24246 | -0.22003 | -0.22644 | -0.18158 | -0.25101 | -0.11643 | 0.12817 | 0.041199 | 0.10071 | 0.086975 | 0.09613 | -0.045776 | 0.11902 | 0.076294 | 0.011749 | -0.066223 | -0.48492 | -0.11643 | -0.03418 | 0.050354 | 0.13733 | 0.032043 | 0.050354 | 0.027466 | 0.004578 | 0.086975 | 123.1018 | 122.8088 | 0.086975
12148.9844 | 0.061035 | 0.21042 | -0.2243 | -0.25421 | -0.18372 | -0.25528 | -0.11643 | 0.045776 | -0.045776 | -0.009155 | 0.013733 | 0.15106 | -0.004578 | 0.13275 | 0.061035 | 0.002136 | -0.063019 | -0.48279 | -0.12817 | -0.046997 | -0.045776 | 0.054932 | -0.059509 | 0.091553 | 0.064087 | 0.064087 | 0.1236 | 123.111 | 122.7997 | 0.09613
12150.7188 | 0.061035 | 0.22751 | -0.21255 | -0.22964 | -0.17731 | -0.2446 | -0.11322 | 0.082397 | 0.004578 | 0.013733 | 0.041199 | 0.13733 | -0.022888 | 0.13733 | 0.045776 | 0.02243 | -0.059814 | -0.47211 | -0.10895 | -0.042725 | -0.018311 | 0.054932 | -0.064087 | 0.082397 | 0.073242 | 0.050354 | 0.1236 | 123.056 | 122.8134 | 0.086975
12152.5156 | 0.045776 | 0.23178 | -0.23392 | -0.23712 | -0.19333 | -0.27557 | -0.10681 | 0.009155 | -0.059509 | -0.013733 | 0.009155 | 0.14191 | -0.004578 | 0.13275 | 0.045776 | 0.010681 | -0.070496 | -0.48386 | -0.11322 | -0.029907 | -0.032043 | 0.013733 | -0.068665 | 0.091553 | 0.082397 | 0.054932 | 0.11902 | 123.1247 | 122.7997 | 0.091553
12154.25 | 0.030518 | 0.24246 | -0.22217 | -0.25742 | -0.19012 | -0.29053 | -0.11002 | 0.082397 | 0.091553 | 0.10986 | 0.091553 | 0.10529 | -0.027466 | 0.10986 | 0.061035 | -0.006409 | -0.055542 | -0.48706 | -0.13245 | -0.030975 | 0.004578 | 0.14648 | 0.018311 | 0.073242 | 0.073242 | 0.041199 | 0.10071 | 122.9782 | 122.8592 | 0.13275
12156.0469 | 0.045776 | 0.20721 | -0.20294 | -0.26276 | -0.18478 | -0.25528 | -0.11429 | 0.086975 | -0.018311 | 0.022888 | 0.050354 | 0.12817 | -0.009155 | 0.14191 | 0.061035 | 0.013885 | -0.041656 | -0.47958 | -0.12283 | -0.05127 | -0.013733 | 0.07782 | -0.050354 | 0.064087 | 0.086975 | 0.050354 | 0.14191 | 123.1201 | 122.7859 | 0.082397
12157.8438 | 0.030518 | 0.2478 | -0.22964 | -0.24033 | -0.18158 | -0.28412 | -0.1239 | 0.07782 | 0.10071 | 0.11902 | 0.10529 | 0.091553 | -0.032043 | 0.10071 | 0.061035 | -0.006409 | -0.066223 | -0.49667 | -0.12604 | -0.036316 | 0.013733 | 0.15106 | 0.032043 | 0.054932 | 0.054932 | 0.041199 | 0.10071 | 122.9965 | 122.8729 | 0.1236
12159.5938 | 0.076294 | 0.23178 | -0.23392 | -0.2446 | -0.18372 | -0.27344 | -0.1207 | 0.022888 | -0.036621 | 0.022888 | 0.018311 | 0.13275 | -0.004578 | 0.13733 | 0.045776 | -0.004272 | -0.05661 | -0.49027 | -0.14099 | -0.036316 | -0.054932 | 0.036621 | -0.068665 | 0.10071 | 0.086975 | 0.064087 | 0.13275 | 123.0103 | 122.8683 | 0.11902
12161.4062 | 0.061035 | 0.2478 | -0.22324 | -0.24674 | -0.18585 | -0.28839 | -0.13031 | 0.054932 | 0.022888 | 0.073242 | 0.054932 | 0.11444 | -0.027466 | 0.11444 | 0.076294 | 0 | -0.058746 | -0.48599 | -0.14954 | -0.033112 | 0.032043 | 0.11444 | 0.045776 | 0.059509 | 0.059509 | 0.036621 | 0.09613 | 123.0469 | 122.85 | 0.12817
12163.2031 | 0.015259 | 0.23285 | -0.2179 | -0.2211 | -0.17517 | -0.26169 | -0.11002 | 0.13733 | 0.068665 | 0.11444 | 0.091553 | 0.091553 | -0.041199 | 0.09613 | 0.045776 | 0.008545 | -0.05661 | -0.48599 | -0.10788 | -0.03418 | 0.050354 | 0.13733 | 0.036621 | 0.032043 | 0.027466 | 0.041199 | 0.082397 | 123.1018 | 122.8271 | 0.09613
12165.0156 | 0.076294 | 0.23178 | -0.23071 | -0.24139 | -0.17944 | -0.27344 | -0.11322 | 0.091553 | 0.050354 | 0.073242 | 0.068665 | 0.1236 | -0.018311 | 0.11444 | 0.076294 | 0.008545 | -0.0737 | -0.48813 | -0.11856 | -0.043793 | -0.013733 | 0.091553 | -0.041199 | 0.086975 | 0.068665 | 0.045776 | 0.10529 | 122.9828 | 122.8775 | 0.12817
12166.7656 | 0.061035 | 0.23712 | -0.23178 | -0.23926 | -0.19226 | -0.2681 | -0.12817 | 0.11902 | 0.086975 | 0.12817 | 0.09613 | 0.09613 | -0.027466 | 0.11902 | 0.045776 | -0.004272 | -0.0737 | -0.48813 | -0.12711 | -0.03952 | 0.041199 | 0.15564 | 0.041199 | 0.064087 | 0.036621 | 0.036621 | 0.09613 | 123.0011 | 122.8546 | 0.13733
12168.5625 | 0.061035 | 0.24567 | -0.23071 | -0.25207 | -0.18692 | -0.27664 | -0.12283 | 0.13275 | 0.11444 | 0.13733 | 0.091553 | 0.091553 | -0.050354 | 0.09613 | 0.076294 | -0.001068 | -0.070496 | -0.48386 | -0.12817 | -0.037384 | 0.073242 | 0.19226 | 0.059509 | 0.027466 | 0.050354 | 0.022888 | 0.091553 | 123.0148 | 122.8409 | 0.11902
12170.3125 | 0.061035 | 0.26703 | -0.23819 | -0.23178 | -0.18158 | -0.27664 | -0.12497 | 0.07782 | 0.013733 | 0.07782 | 0.064087 | 0.09613 | -0.036621 | 0.091553 | 0.045776 | -0.012817 | -0.079041 | -0.47531 | -0.13138 | -0.033112 | 0.004578 | 0.086975 | 0.022888 | 0.050354 | 0.064087 | 0.004578 | 0.09613 | 123.0423 | 122.85 | 0.1236
12172.1094 | 0.076294 | 0.24353 | -0.21576 | -0.22964 | -0.19226 | -0.23285 | -0.11322 | 0.11444 | -0.004578 | 0.041199 | 0.036621 | 0.14191 | -0.027466 | 0.10529 | 0.061035 | 0.021362 | -0.066223 | -0.46249 | -0.1207 | -0.048065 | 0.054932 | 0.11902 | 0 | 0.041199 | 0.059509 | 0.013733 | 0.10071 | 123.1293 | 122.8546 | 0.086975
12173.9062 | 0.061035 | 0.21576 | -0.2179 | -0.23926 | -0.1709 | -0.23178 | -0.11856 | 0.11444 | 0.013733 | 0.050354 | 0.068665 | 0.14191 | -0.009155 | 0.15106 | 0.061035 | 0.032043 | -0.053406 | -0.48386 | -0.12176 | -0.054474 | 0.013733 | 0.091553 | -0.050354 | 0.073242 | 0.054932 | 0.050354 | 0.10986 | 123.1338 | 122.8088 | 0.086975
12175.6562 | 0.045776 | 0.23498 | -0.23178 | -0.24887 | -0.16983 | -0.27985 | -0.10788 | 0.10071 | 0.086975 | 0.11444 | 0.086975 | 0.09613 | -0.022888 | 0.11902 | 0.045776 | -0.011749 | -0.063019 | -0.48599 | -0.12176 | -0.02243 | 0.022888 | 0.14191 | 0.009155 | 0.064087 | 0.045776 | 0.036621 | 0.10071 | 122.9965 | 122.8592 | 0.13275
12177.4375 | 0.061035 | 0.24033 | -0.23071 | -0.24674 | -0.19226 | -0.27985 | -0.12497 | 0.11902 | 0.10529 | 0.12817 | 0.091553 | 0.10071 | -0.027466 | 0.11902 | 0.045776 | -0.005341 | -0.058746 | -0.50415 | -0.13992 | -0.029907 | 0.068665 | 0.20142 | 0.064087 | 0.036621 | 0.022888 | 0.032043 | 0.086975 | 123.0331 | 122.8134 | 0.11902
12179.1719 | 0.076294 | 0.2243 | -0.22217 | -0.23071 | -0.19119 | -0.24033 | -0.10574 | 0.082397 | -0.013733 | 0.004578 | 0.045776 | 0.11444 | -0.018311 | 0.13733 | 0.061035 | 0.029907 | -0.057678 | -0.49027 | -0.099335 | -0.042725 | -0.032043 | 0.032043 | -0.09613 | 0.064087 | 0.082397 | 0.045776 | 0.11902 | 123.0927 | 122.8317 | 0.10986
12180.9062 | 0.076294 | 0.25848 | -0.22751 | -0.23712 | -0.19867 | -0.2948 | -0.11749 | 0.09613 | 0.073242 | 0.10529 | 0.068665 | 0.10986 | -0.027466 | 0.11444 | 0.061035 | -0.003204 | -0.071564 | -0.48599 | -0.13672 | -0.024567 | 0.064087 | 0.16479 | 0.059509 | 0.064087 | 0.045776 | 0.045776 | 0.091553 | 123.0515 | 122.8592 | 0.10529
12182.7031 | 0.061035 | 0.26276 | -0.23498 | -0.23071 | -0.16983 | -0.26169 | -0.11963 | 0.10529 | 0.073242 | 0.10529 | 0.091553 | 0.082397 | -0.032043 | 0.1236 | 0.045776 | 0.005341 | -0.072632 | -0.48279 | -0.12283 | -0.03418 | 0.059509 | 0.1236 | 0.018311 | 0.054932 | 0.032043 | 0.018311 | 0.10529 | 123.0286 | 122.8775 | 0.10529
12184.5 | 0.061035 | 0.22858 | -0.21362 | -0.22964 | -0.18799 | -0.23819 | -0.11429 | 0.050354 | -0.059509 | -0.018311 | 0.018311 | 0.15106 | -0.004578 | 0.12817 | 0.030518 | 0.036316 | -0.058746 | -0.48706 | -0.10361 | -0.03952 | -0.073242 | 0 | -0.11444 | 0.082397 | 0.054932 | 0.054932 | 0.12817 | 123.0927 | 122.8638 | 0.10529
12186.2344 | 0.061035 | 0.24674 | -0.22324 | -0.23712 | -0.19546 | -0.27451 | -0.1207 | 0.064087 | 0.027466 | 0.07782 | 0.050354 | 0.1236 | -0.032043 | 0.10529 | 0.076294 | -0.007477 | -0.069427 | -0.48706 | -0.12924 | -0.021362 | 0.009155 | 0.09613 | 0.022888 | 0.054932 | 0.064087 | 0.032043 | 0.09613 | 123.024 | 122.8867 | 0.1236
12188.0312 | 0.061035 | 0.2478 | -0.23392 | -0.2446 | -0.18906 | -0.27344 | -0.11322 | 0.082397 | 0.022888 | 0.073242 | 0.054932 | 0.082397 | -0.018311 | 0.10986 | 0.045776 | 0.004272 | -0.072632 | -0.49347 | -0.13351 | -0.029907 | 0.013733 | 0.091553 | 0.018311 | 0.054932 | 0.045776 | 0.027466 | 0.09613 | 123.0286 | 122.8683 | 0.14191
12189.8438 | 0.061035 | 0.20508 | -0.23285 | -0.25207 | -0.18478 | -0.25742 | -0.12283 | 0.036621 | -0.045776 | -0.018311 | 0.009155 | 0.1236 | 0.018311 | 0.15106 | 0.030518 | 0.021362 | -0.052338 | -0.49027 | -0.11322 | -0.042725 | -0.059509 | 0.045776 | -0.09613 | 0.10529 | 0.059509 | 0.07782 | 0.14191 | 123.056 | 122.8683 | 0.10529
12191.5781 | 0.061035 | 0.2478 | -0.23071 | -0.23498 | -0.17944 | -0.27985 | -0.12497 | 0.050354 | 0.027466 | 0.082397 | 0.054932 | 0.11444 | -0.050354 | 0.10529 | 0.061035 | -0.004272 | -0.070496 | -0.4924 | -0.13992 | -0.032043 | 0.022888 | 0.10529 | 0.032043 | 0.064087 | 0.045776 | 0.032043 | 0.10071 | 123.0698 | 122.8592 | 0.12817
12193.3594 | 0.061035 | 0.25207 | -0.21362 | -0.24567 | -0.18906 | -0.27237 | -0.11963 | 0.064087 | 0.032043 | 0.082397 | 0.054932 | 0.10071 | -0.032043 | 0.10986 | 0.061035 | 0.006409 | -0.082245 | -0.49133 | -0.12497 | -0.029907 | 0.009155 | 0.10986 | 0.013733 | 0.045776 | 0.059509 | 0.036621 | 0.10529 | 123.0469 | 122.8683 | 0.13733
12195.1562 | 0.030518 | 0.24887 | -0.23819 | -0.23819 | -0.17517 | -0.27664 | -0.11749 | 0.054932 | 0.018311 | 0.068665 | 0.045776 | 0.11902 | -0.036621 | 0.10071 | 0.045776 | 0.008545 | -0.066223 | -0.49561 | -0.12283 | -0.026703 | 0.022888 | 0.10071 | 0.032043 | 0.050354 | 0.036621 | 0.041199 | 0.10986 | 123.0469 | 122.8958 | 0.11444
12196.9531 | 0.030518 | 0.23392 | -0.22217 | -0.23071 | -0.18799 | -0.26596 | -0.11536 | 0.12817 | 0.10071 | 0.11444 | 0.07782 | 0.091553 | -0.050354 | 0.10071 | 0.076294 | 0.019226 | -0.067291 | -0.49347 | -0.12497 | -0.040588 | 0.073242 | 0.11902 | 0.027466 | 0.059509 | 0.032043 | 0.022888 | 0.09613 | 123.024 | 122.8912 | 0.13275
12198.75 | 0.045776 | 0.22537 | -0.21896 | -0.2446 | -0.18692 | -0.23819 | -0.11108 | 0.11444 | 0.032043 | 0.032043 | 0.054932 | 0.14648 | -0.013733 | 0.13275 | 0.061035 | 0.036316 | -0.05661 | -0.47211 | -0.10788 | -0.041656 | 0.022888 | 0.082397 | -0.050354 | 0.086975 | 0.054932 | 0.045776 | 0.10529 | 123.1338 | 122.8317 | 0.082397
12200.5625 | 0.045776 | 0.22858 | -0.23392 | -0.2179 | -0.18906 | -0.25742 | -0.1004 | 0.07782 | 0.022888 | 0.036621 | 0.059509 | 0.13733 | -0.013733 | 0.12817 | 0.045776 | 0.013885 | -0.058746 | -0.48813 | -0.10788 | -0.038452 | 0.009155 | 0.086975 | -0.054932 | 0.091553 | 0.054932 | 0.07782 | 0.1236 | 123.143 | 122.8363 | 0.068665
12202.2969 | 0.076294 | 0.25848 | -0.22324 | -0.23819 | -0.18585 | -0.28519 | -0.10895 | 0.10071 | 0.086975 | 0.11444 | 0.068665 | 0.086975 | -0.045776 | 0.073242 | 0.076294 | 0.003204 | -0.072632 | -0.48172 | -0.12283 | -0.02243 | 0.059509 | 0.12817 | 0.027466 | 0.045776 | 0.050354 | 0.027466 | 0.086975 | 123.0286 | 122.8912 | 0.1236
12204.0625 | 0.061035 | 0.20081 | -0.21576 | -0.24139 | -0.19012 | -0.2478 | -0.1004 | 0.022888 | -0.068665 | -0.027466 | 0.009155 | 0.16022 | -0.018311 | 0.12817 | 0.076294 | 0.023499 | -0.059814 | -0.49133 | -0.11322 | -0.03952 | -0.041199 | -0.009155 | -0.10529 | 0.10986 | 0.068665 | 0.064087 | 0.13733 | 123.1155 | 122.8546 | 0.10529
12205.8125 | 0.045776 | 0.27023 | -0.22537 | -0.23178 | -0.18906 | -0.28412 | -0.11322 | 0.082397 | 0.054932 | 0.07782 | 0.064087 | 0.10986 | -0.045776 | 0.11444 | 0.061035 | 0.005341 | -0.075836 | -0.48813 | -0.12817 | -0.024567 | 0.018311 | 0.10529 | 0.027466 | 0.045776 | 0.045776 | 0.018311 | 0.086975 | 123.024 | 122.8821 | 0.11902
12207.6094 | 0.061035 | 0.23819 | -0.22324 | -0.24994 | -0.18372 | -0.2713 | -0.11322 | 0.09613 | 0.07782 | 0.10529 | 0.091553 | 0.10529 | -0.018311 | 0.09613 | 0.061035 | 0.011749 | -0.069427 | -0.48599 | -0.13565 | -0.038452 | -0.004578 | 0.10986 | 0.004578 | 0.054932 | 0.068665 | 0.045776 | 0.11444 | 123.0057 | 122.9095 | 0.11444
12209.3438 | 0.030518 | 0.24994 | -0.2243 | -0.23071 | -0.18158 | -0.28412 | -0.11429 | 0.10529 | 0.036621 | 0.091553 | 0.059509 | 0.10529 | -0.050354 | 0.10071 | 0.061035 | 0.014954 | -0.063019 | -0.47852 | -0.13031 | -0.03418 | 0.032043 | 0.10071 | 0.022888 | 0.059509 | 0.045776 | 0.036621 | 0.09613 | 123.0148 | 122.8912 | 0.12817
12211.125 | 0.061035 | 0.24887 | -0.2179 | -0.2211 | -0.1741 | -0.26276 | -0.11963 | 0.16022 | 0.059509 | 0.10071 | 0.10986 | 0.10529 | -0.050354 | 0.082397 | 0.030518 | 0.024567 | -0.067291 | -0.47958 | -0.10681 | -0.044861 | 0.073242 | 0.13733 | 0.041199 | 0.045776 | 0.022888 | 0.013733 | 0.064087 | 123.1476 | 122.8455 | 0.11444
12212.9219 | 0.076294 | 0.22537 | -0.21042 | -0.2478 | -0.18906 | -0.24887 | -0.11002 | 0.07782 | -0.045776 | -0.004578 | 0.036621 | 0.13733 | -0.022888 | 0.13733 | 0.061035 | 0.027771 | -0.072632 | -0.4892 | -0.11749 | -0.045929 | -0.027466 | 0.073242 | -0.054932 | 0.091553 | 0.082397 | 0.050354 | 0.13275 | 123.143 | 122.8363 | 0.082397
12214.7031 | 0.076294 | 0.23178 | -0.22324 | -0.2211 | -0.17944 | -0.25101 | -0.10468 | 0.12817 | 0.013733 | 0.018311 | 0.032043 | 0.14191 | 0 | 0.14648 | 0.076294 | 0.037384 | -0.059814 | -0.47424 | -0.099335 | -0.042725 | -0.009155 | 0.07782 | -0.068665 | 0.068665 | 0.07782 | 0.050354 | 0.10986 | 123.0972 | 122.8455 | 0.09613
12216.5 | 0.061035 | 0.26169 | -0.21896 | -0.22964 | -0.19226 | -0.28946 | -0.11963 | 0.09613 | 0.064087 | 0.09613 | 0.050354 | 0.10071 | -0.022888 | 0.11444 | 0.076294 | -0.004272 | -0.063019 | -0.4892 | -0.13138 | -0.026703 | 0.018311 | 0.10986 | 0.018311 | 0.050354 | 0.050354 | 0.036621 | 0.091553 | 123.0286 | 122.8958 | 0.13275
12218.2969 | 0.061035 | 0.23712 | -0.22644 | -0.25314 | -0.18906 | -0.27344 | -0.10574 | 0.036621 | -0.032043 | 0.013733 | 0.009155 | 0.15564 | 0.009155 | 0.12817 | 0.061035 | 0.013885 | -0.053406 | -0.48492 | -0.12283 | -0.036316 | -0.059509 | 0.050354 | -0.059509 | 0.086975 | 0.068665 | 0.07782 | 0.12817 | 123.0377 | 122.8729 | 0.10986
12220.0312 | 0.045776 | 0.23071 | -0.24033 | -0.24674 | -0.18265 | -0.26382 | -0.12604 | 0.045776 | -0.022888 | 0.004578 | 0.004578 | 0.13733 | 0 | 0.14191 | 0.061035 | 0.01709 | -0.057678 | -0.4892 | -0.12924 | -0.03952 | -0.068665 | 0.045776 | -0.073242 | 0.09613 | 0.086975 | 0.07782 | 0.12817 | 123.0423 | 122.8775 | 0.12817
12221.8281 | 0.030518 | 0.25848 | -0.22537 | -0.24674 | -0.18478 | -0.28625 | -0.11643 | 0.036621 | 0.032043 | 0.082397 | 0.054932 | 0.11902 | -0.032043 | 0.10986 | 0.045776 | -0.001068 | -0.066223 | -0.50201 | -0.13138 | -0.03418 | 0.018311 | 0.11444 | 0.032043 | 0.050354 | 0.045776 | 0.018311 | 0.11444 | 123.0835 | 122.8958 | 0.1236
12223.625 | 0.076294 | 0.22858 | -0.21255 | -0.2446 | -0.19012 | -0.24033 | -0.11643 | 0.12817 | 0.018311 | 0.041199 | 0.050354 | 0.13275 | 0.009155 | 0.11444 | 0.076294 | 0.023499 | -0.059814 | -0.48279 | -0.11108 | -0.043793 | 0.018311 | 0.086975 | -0.054932 | 0.09613 | 0.054932 | 0.050354 | 0.12817 | 123.1201 | 122.85 | 0.09613
12225.4375 | 0.061035 | 0.22964 | -0.22003 | -0.24139 | -0.19867 | -0.24674 | -0.11215 | 0.11444 | 0 | 0.022888 | 0.045776 | 0.1236 | -0.027466 | 0.11444 | 0.076294 | 0.021362 | -0.066223 | -0.4657 | -0.1207 | -0.030975 | -0.004578 | 0.068665 | -0.082397 | 0.073242 | 0.064087 | 0.050354 | 0.13275 | 123.1064 | 122.8271 | 0.091553
12227.2344 | 0.045776 | 0.22751 | -0.21683 | -0.23285 | -0.18906 | -0.25207 | -0.10574 | 0.073242 | 0.004578 | 0.032043 | 0.064087 | 0.13733 | 0 | 0.14191 | 0.076294 | 0.013885 | -0.068359 | -0.48706 | -0.11215 | -0.044861 | -0.022888 | 0.086975 | -0.036621 | 0.086975 | 0.082397 | 0.045776 | 0.13733 | 123.1567 | 122.8271 | 0.091553
12228.9688 | 0.076294 | 0.24887 | -0.2243 | -0.2243 | -0.18478 | -0.27557 | -0.10895 | 0.13275 | 0.082397 | 0.12817 | 0.09613 | 0.091553 | -0.059509 | 0.086975 | 0.045776 | -0.007477 | -0.074768 | -0.48599 | -0.11749 | -0.029907 | 0.068665 | 0.15106 | 0.054932 | 0.032043 | 0.032043 | 0.022888 | 0.082397 | 123.0972 | 122.8683 | 0.10986
12230.7656 | 0.076294 | 0.25848 | -0.22217 | -0.24246 | -0.18051 | -0.29373 | -0.10895 | 0.086975 | 0.036621 | 0.086975 | 0.045776 | 0.09613 | -0.032043 | 0.10529 | 0.061035 | -0.003204 | -0.054474 | -0.49561 | -0.12924 | -0.033112 | 0.018311 | 0.10071 | 0.022888 | 0.050354 | 0.036621 | 0.036621 | 0.091553 | 123.0423 | 122.905 | 0.12817
12232.5 | 0.061035 | 0.2243 | -0.2179 | -0.23498 | -0.1944 | -0.24887 | -0.12176 | 0.045776 | -0.045776 | -0.013733 | 0.013733 | 0.14191 | 0 | 0.12817 | 0.061035 | 0.018158 | -0.067291 | -0.48599 | -0.10895 | -0.033112 | -0.018311 | 0.022888 | -0.064087 | 0.082397 | 0.068665 | 0.036621 | 0.12817 | 123.1705 | 122.8546 | 0.07782
12234.2812 | 0.045776 | 0.2681 | -0.22964 | -0.22751 | -0.19546 | -0.29266 | -0.13245 | 0.10071 | 0.082397 | 0.11902 | 0.082397 | 0.10986 | -0.036621 | 0.10529 | 0.045776 | 0.002136 | -0.072632 | -0.49027 | -0.13245 | -0.028839 | 0.050354 | 0.17853 | 0.073242 | 0.050354 | 0.036621 | 0.027466 | 0.091553 | 123.0972 | 122.8683 | 0.10071
12236.0156 | 0.076294 | 0.24887 | -0.23605 | -0.24994 | -0.18158 | -0.29159 | -0.1239 | 0.12817 | 0.091553 | 0.12817 | 0.073242 | 0.10986 | -0.036621 | 0.10071 | 0.045776 | -0.006409 | -0.063019 | -0.48492 | -0.13992 | -0.036316 | 0.091553 | 0.19226 | 0.07782 | 0.059509 | 0.032043 | 0.022888 | 0.086975 | 123.0972 | 122.8775 | 0.11902
12237.8281 | 0.030518 | 0.23712 | -0.2179 | -0.23498 | -0.17624 | -0.25528 | -0.10681 | 0.14648 | 0.086975 | 0.13275 | 0.073242 | 0.091553 | -0.050354 | 0.082397 | 0.030518 | 0.006409 | -0.068359 | -0.49133 | -0.11856 | -0.048065 | 0.07782 | 0.1236 | 0.059509 | 0.045776 | 0.036621 | 0.022888 | 0.091553 | 123.0789 | 122.905 | 0.10071
12239.5625 | 0.030518 | 0.2243 | -0.21362 | -0.22537 | -0.19119 | -0.23178 | -0.10361 | 0.068665 | -0.018311 | 0 | 0.027466 | 0.13733 | -0.013733 | 0.12817 | 0.030518 | 0.018158 | -0.045929 | -0.48279 | -0.095062 | -0.038452 | -0.041199 | 0.022888 | -0.086975 | 0.086975 | 0.07782 | 0.054932 | 0.10986 | 123.1155 | 122.8683 | 0.10071
12241.3438 | 0.030518 | 0.23285 | -0.21576 | -0.22964 | -0.1944 | -0.24887 | -0.099335 | 0.027466 | -0.086975 | -0.041199 | 0.009155 | 0.14648 | -0.018311 | 0.12817 | 0.061035 | 0.01709 | -0.049133 | -0.46677 | -0.1207 | -0.052338 | -0.045776 | -0.004578 | -0.11444 | 0.064087 | 0.07782 | 0.050354 | 0.1236 | 123.1293 | 122.8683 | 0.091553
12243.125 | 0.061035 | 0.2179 | -0.22003 | -0.24567 | -0.19012 | -0.25314 | -0.10895 | 0.022888 | -0.082397 | -0.009155 | 0.013733 | 0.13275 | -0.004578 | 0.14648 | 0.076294 | 0.020294 | -0.05661 | -0.47531 | -0.10147 | -0.037384 | -0.050354 | -0.027466 | -0.086975 | 0.086975 | 0.082397 | 0.068665 | 0.13275 | 123.1476 | 122.8546 | 0.086975
12244.8594 | 0.061035 | 0.23392 | -0.2243 | -0.23712 | -0.18051 | -0.25848 | -0.10788 | 0.041199 | -0.041199 | 0.004578 | 0.018311 | 0.14191 | -0.009155 | 0.13733 | 0.061035 | 0.016022 | -0.067291 | -0.47745 | -0.11749 | -0.033112 | -0.004578 | 0.027466 | -0.041199 | 0.082397 | 0.073242 | 0.054932 | 0.09613 | 123.1888 | 122.8729 | 0.082397
12246.6562 | 0.061035 | 0.25848 | -0.22324 | -0.26382 | -0.19333 | -0.2948 | -0.1207 | 0.10986 | 0.073242 | 0.1236 | 0.073242 | 0.10071 | -0.036621 | 0.10529 | 0.076294 | -0.003204 | -0.059814 | -0.48279 | -0.13886 | -0.032043 | 0.073242 | 0.16937 | 0.082397 | 0.036621 | 0.059509 | -0.004578 | 0.086975 | 123.0881 | 122.8592 | 0.10529
12248.4531 | 0.045776 | 0.25635 | -0.22537 | -0.21042 | -0.17838 | -0.27237 | -0.10788 | 0.10529 | 0.10071 | 0.12817 | 0.064087 | 0.082397 | -0.032043 | 0.086975 | 0.076294 | 0.003204 | -0.071564 | -0.49774 | -0.11108 | -0.03418 | 0.064087 | 0.14191 | 0.054932 | 0.054932 | 0.027466 | 0.022888 | 0.082397 | 123.0698 | 122.9004 | 0.1236
12250.1719 | 0.061035 | 0.26596 | -0.24033 | -0.22537 | -0.18158 | -0.29053 | -0.11429 | 0.14648 | 0.11902 | 0.1236 | 0.10529 | 0.09613 | -0.041199 | 0.091553 | 0.061035 | 0.001068 | -0.0737 | -0.49774 | -0.12176 | -0.036316 | 0.059509 | 0.17853 | 0.082397 | 0.045776 | 0.036621 | 0.032043 | 0.07782 | 123.0743 | 122.8958 | 0.11444
12251.9688 | 0.030518 | 0.23285 | -0.23926 | -0.24246 | -0.18585 | -0.25528 | -0.12176 | 0.045776 | -0.045776 | -0.022888 | 0.013733 | 0.16022 | -0.004578 | 0.16022 | 0.045776 | 0.013885 | -0.057678 | -0.49667 | -0.12604 | -0.050201 | -0.054932 | 0.045776 | -0.082397 | 0.10071 | 0.091553 | 0.068665 | 0.13275 | 123.0927 | 122.8775 | 0.10529
12253.7031 | 0.045776 | 0.26916 | -0.22751 | -0.23712 | -0.20294 | -0.26382 | -0.11429 | 0.11902 | 0.045776 | 0.091553 | 0.059509 | 0.082397 | -0.032043 | 0.086975 | 0.061035 | 0.005341 | -0.069427 | -0.48279 | -0.13886 | -0.03952 | 0.036621 | 0.10986 | 0.013733 | 0.054932 | 0.050354 | 0.027466 | 0.091553 | 123.0423 | 122.905 | 0.11902
12255.4844 | 0.061035 | 0.24887 | -0.22324 | -0.23712 | -0.17838 | -0.26062 | -0.11429 | 0.15564 | 0.054932 | 0.10529 | 0.09613 | 0.1236 | -0.036621 | 0.10529 | 0.030518 | 0.013885 | -0.066223 | -0.48279 | -0.1207 | -0.038452 | 0.068665 | 0.13733 | 0.045776 | 0.045776 | 0.045776 | 0.032043 | 0.07782 | 123.1476 | 122.8821 | 0.082397
12257.2031 | 0.045776 | 0.23071 | -0.2243 | -0.21683 | -0.19867 | -0.25635 | -0.10574 | 0.13733 | 0.086975 | 0.13275 | 0.09613 | 0.086975 | -0.054932 | 0.09613 | 0.045776 | 0.002136 | -0.075836 | -0.48279 | -0.10895 | -0.02243 | 0.082397 | 0.15106 | 0.041199 | 0.027466 | 0.045776 | 0.027466 | 0.082397 | 123.1293 | 122.8912 | 0.091553
12259 | 0.061035 | 0.24139 | -0.22217 | -0.25742 | -0.17303 | -0.27451 | -0.11215 | 0.068665 | 0.027466 | 0.086975 | 0.054932 | 0.10986 | -0.041199 | 0.10071 | 0.045776 | -0.003204 | -0.05127 | -0.49347 | -0.12817 | -0.035248 | 0.009155 | 0.082397 | -0.004578 | 0.068665 | 0.041199 | 0.022888 | 0.10986 | 123.0423 | 122.9095 | 0.1236
12260.75 | 0.076294 | 0.24994 | -0.23926 | -0.22751 | -0.18799 | -0.27451 | -0.11002 | 0.14191 | 0.086975 | 0.12817 | 0.09613 | 0.10071 | -0.045776 | 0.091553 | 0.061035 | 0.001068 | -0.05661 | -0.4924 | -0.10895 | -0.033112 | 0.082397 | 0.14648 | 0.041199 | 0.059509 | 0.032043 | 0.009155 | 0.082397 | 123.0789 | 122.905 | 0.13275
12262.5469 | 0.061035 | 0.25101 | -0.23605 | -0.23926 | -0.19012 | -0.27771 | -0.1207 | 0.11444 | 0.073242 | 0.10986 | 0.045776 | 0.09613 | -0.041199 | 0.10529 | 0.061035 | -0.005341 | -0.049133 | -0.4892 | -0.12604 | -0.03418 | 0.041199 | 0.10071 | 0.004578 | 0.054932 | 0.041199 | 0.032043 | 0.082397 | 123.0469 | 122.905 | 0.12817
12264.3594 | 0.076294 | 0.23605 | -0.21896 | -0.2211 | -0.18372 | -0.26276 | -0.11963 | 0.059509 | -0.009155 | 0.018311 | 0.013733 | 0.13733 | 0.004578 | 0.14191 | 0.045776 | 0.008545 | -0.054474 | -0.48706 | -0.11749 | -0.042725 | -0.041199 | 0.050354 | -0.059509 | 0.086975 | 0.07782 | 0.068665 | 0.14648 | 123.0469 | 122.905 | 0.10529
12266.0938 | 0.045776 | 0.24567 | -0.2243 | -0.23605 | -0.19333 | -0.25635 | -0.11749 | 0.14191 | 0.068665 | 0.10986 | 0.09613 | 0.09613 | -0.041199 | 0.10529 | 0.076294 | 0.011749 | -0.052338 | -0.46997 | -0.1207 | -0.045929 | 0.082397 | 0.12817 | 0.027466 | 0.050354 | 0.022888 | -0.004578 | 0.068665 | 123.1659 | 122.8775 | 0.09613
12267.875 | 0.076294 | 0.23071 | -0.22751 | -0.25528 | -0.18158 | -0.27451 | -0.11749 | 0.11902 | 0.07782 | 0.13733 | 0.10529 | 0.09613 | -0.041199 | 0.11902 | 0.045776 | -0.006409 | -0.063019 | -0.48599 | -0.12711 | -0.035248 | 0.027466 | 0.16022 | 0.027466 | 0.050354 | 0.032043 | 0.032043 | 0.11444 | 123.0606 | 122.9187 | 0.12817
12269.6719 | 0.076294 | 0.24887 | -0.20935 | -0.21255 | -0.17517 | -0.25207 | -0.11002 | 0.14648 | 0.082397 | 0.11444 | 0.09613 | 0.091553 | -0.036621 | 0.09613 | 0.045776 | 0.007477 | -0.059814 | -0.49347 | -0.12817 | -0.03952 | 0.064087 | 0.14648 | 0.045776 | 0.027466 | 0.027466 | 0.032043 | 0.10071 | 123.0789 | 122.9095 | 0.10986
12271.4062 | 0.091553 | 0.23926 | -0.21469 | -0.23071 | -0.17731 | -0.24887 | -0.11215 | 0.054932 | -0.050354 | -0.018311 | 0.009155 | 0.14191 | -0.009155 | 0.15106 | 0.061035 | 0.020294 | -0.044861 | -0.48813 | -0.11002 | -0.042725 | -0.027466 | 0.004578 | -0.086975 | 0.091553 | 0.054932 | 0.054932 | 0.11902 | 123.1705 | 122.8912 | 0.082397
12273.2031 | 0.061035 | 0.22217 | -0.2211 | -0.22644 | -0.18158 | -0.25528 | -0.10788 | 0.045776 | -0.036621 | -0.004578 | 0.013733 | 0.12817 | -0.004578 | 0.1236 | 0.030518 | 0.021362 | -0.059814 | -0.47958 | -0.11749 | -0.032043 | -0.018311 | 0.027466 | -0.059509 | 0.068665 | 0.045776 | 0.050354 | 0.11902 | 123.1888 | 122.8867 | 0.07782
12274.9375 | 0.076294 | 0.24674 | -0.22858 | -0.24033 | -0.19119 | -0.27985 | -0.11856 | 0.036621 | 0.027466 | 0.091553 | 0.064087 | 0.1236 | -0.041199 | 0.10071 | 0.061035 | 0 | -0.057678 | -0.48599 | -0.13031 | -0.033112 | 0.018311 | 0.10529 | 0.027466 | 0.050354 | 0.036621 | 0.041199 | 0.10071 | 123.111 | 122.9324 | 0.12817
12276.7344 | 0.091553 | 0.21896 | -0.21576 | -0.23819 | -0.18585 | -0.24246 | -0.10361 | 0.1236 | 0.032043 | 0.045776 | 0.054932 | 0.11902 | -0.018311 | 0.12817 | 0.045776 | 0.02243 | -0.058746 | -0.48172 | -0.10147 | -0.044861 | 0 | 0.07782 | -0.059509 | 0.059509 | 0.059509 | 0.036621 | 0.11444 | 123.143 | 122.8775 | 0.07782
12278.5312 | 0.045776 | 0.25314 | -0.23498 | -0.23178 | -0.18051 | -0.29694 | -0.11429 | 0.041199 | 0.022888 | 0.082397 | 0.064087 | 0.09613 | -0.036621 | 0.10986 | 0.076294 | 0.002136 | -0.070496 | -0.4924 | -0.13031 | -0.027771 | 0.013733 | 0.11902 | 0.027466 | 0.050354 | 0.059509 | 0.041199 | 0.086975 | 123.0972 | 122.9279 | 0.11444
12280.25 | 0.045776 | 0.22751 | -0.2243 | -0.24246 | -0.18372 | -0.27344 | -0.12176 | 0.032043 | -0.036621 | 0 | 0.004578 | 0.14191 | 0.013733 | 0.14648 | 0.061035 | 0.019226 | -0.049133 | -0.48599 | -0.12711 | -0.033112 | -0.050354 | 0.045776 | -0.068665 | 0.09613 | 0.082397 | 0.054932 | 0.13733 | 123.0789 | 122.9004 | 0.10986
12282.0312 | 0.061035 | 0.23712 | -0.22537 | -0.25421 | -0.17838 | -0.27771 | -0.12283 | 0.11902 | 0.082397 | 0.10986 | 0.091553 | 0.11444 | -0.032043 | 0.09613 | 0.061035 | -0.002136 | -0.058746 | -0.4892 | -0.13672 | -0.043793 | 0.032043 | 0.15106 | 0.013733 | 0.054932 | 0.032043 | 0.050354 | 0.082397 | 123.0423 | 122.8958 | 0.1236
12283.8281 | 0.061035 | 0.24033 | -0.21042 | -0.22644 | -0.18478 | -0.24033 | -0.12176 | 0.082397 | -0.018311 | 0.013733 | 0.027466 | 0.13275 | -0.009155 | 0.14191 | 0.061035 | 0.025635 | -0.041656 | -0.47211 | -0.11002 | -0.042725 | -0.036621 | 0.022888 | -0.091553 | 0.07782 | 0.064087 | 0.073242 | 0.1236 | 123.1522 | 122.8912 | 0.09613
12285.5781 | 0.045776 | 0.24353 | -0.22003 | -0.24353 | -0.18692 | -0.28732 | -0.13351 | 0.12817 | 0.10071 | 0.12817 | 0.10071 | 0.10071 | -0.054932 | 0.091553 | 0.045776 | -0.002136 | -0.063019 | -0.48492 | -0.13565 | -0.038452 | 0.041199 | 0.1831 | 0.059509 | 0.064087 | 0.041199 | 0.032043 | 0.086975 | 123.0606 | 122.8958 | 0.10986
12287.375 | 0.045776 | 0.24033 | -0.2211 | -0.24033 | -0.18692 | -0.27237 | -0.12283 | 0.091553 | 0.068665 | 0.086975 | 0.082397 | 0.10529 | -0.013733 | 0.1236 | 0.030518 | 0.006409 | -0.055542 | -0.49454 | -0.13031 | -0.037384 | 0 | 0.1236 | -0.009155 | 0.068665 | 0.050354 | 0.041199 | 0.11444 | 123.0377 | 122.9416 | 0.10071
12289.1562 | 0.076294 | 0.24033 | -0.21896 | -0.2243 | -0.18692 | -0.25955 | -0.11963 | 0.13733 | 0.054932 | 0.082397 | 0.09613 | 0.09613 | -0.045776 | 0.10071 | 0.030518 | 0.006409 | -0.055542 | -0.47638 | -0.11002 | -0.037384 | 0.064087 | 0.14648 | 0.036621 | 0.059509 | 0.041199 | 0.032043 | 0.091553 | 123.1842 | 122.9004 | 0.07782
12290.9062 | 0.045776 | 0.23498 | -0.21683 | -0.22003 | -0.17838 | -0.26169 | -0.10361 | 0.12817 | 0.082397 | 0.11902 | 0.091553 | 0.09613 | -0.045776 | 0.091553 | 0.045776 | 0.005341 | -0.066223 | -0.4924 | -0.10468 | -0.029907 | 0.086975 | 0.14191 | 0.050354 | 0.045776 | 0.018311 | 0.013733 | 0.07782 | 123.1613 | 122.9095 | 0.10986
12292.7031 | 0.061035 | 0.23178 | -0.23712 | -0.25742 | -0.19653 | -0.28946 | -0.12497 | 0.059509 | 0.036621 | 0.07782 | 0.045776 | 0.09613 | -0.036621 | 0.09613 | 0.045776 | 0.005341 | -0.054474 | -0.49133 | -0.13565 | -0.040588 | 0 | 0.10071 | 0.018311 | 0.064087 | 0.045776 | 0.013733 | 0.086975 | 123.0789 | 122.9279 | 0.11444
12294.5 | 0.061035 | 0.23392 | -0.23498 | -0.24994 | -0.18585 | -0.2446 | -0.11749 | 0.045776 | -0.036621 | -0.018311 | 0.022888 | 0.16479 | 0.013733 | 0.15106 | 0.061035 | 0.026703 | -0.041656 | -0.47638 | -0.11215 | -0.038452 | -0.059509 | 0.059509 | -0.073242 | 0.09613 | 0.073242 | 0.064087 | 0.11444 | 123.1567 | 122.8683 | 0.09613
12296.2344 | 0.061035 | 0.22751 | -0.21683 | -0.23819 | -0.18906 | -0.23498 | -0.10147 | 0.091553 | -0.009155 | 0.009155 | 0.041199 | 0.1236 | -0.013733 | 0.14191 | 0.061035 | 0.029907 | -0.043793 | -0.47638 | -0.11322 | -0.03418 | -0.032043 | 0.022888 | -0.086975 | 0.07782 | 0.064087 | 0.064087 | 0.13275 | 123.1613 | 122.8958 | 0.09613
12298.0312 | 0.030518 | 0.24139 | -0.23926 | -0.23819 | -0.18265 | -0.26596 | -0.11002 | 0.013733 | -0.027466 | -0.013733 | 0.027466 | 0.14648 | 0.009155 | 0.14191 | 0.030518 | 0.008545 | -0.057678 | -0.47852 | -0.12176 | -0.028839 | -0.068665 | 0.059509 | -0.073242 | 0.09613 | 0.059509 | 0.050354 | 0.12817 | 123.1842 | 122.8867 | 0.073242
12299.8281 | 0.061035 | 0.23926 | -0.2179 | -0.24139 | -0.17731 | -0.25421 | -0.11322 | 0.068665 | 0.018311 | 0.027466 | 0.050354 | 0.1236 | -0.013733 | 0.14191 | 0.045776 | 0.014954 | -0.045929 | -0.46997 | -0.11429 | -0.03952 | 0 | 0.10529 | -0.041199 | 0.068665 | 0.054932 | 0.036621 | 0.12817 | 123.1888 | 122.8683 | 0.07782
12301.5781 | 0.061035 | 0.24033 | -0.22751 | -0.22964 | -0.1944 | -0.26703 | -0.11536 | 0.036621 | -0.009155 | 0.009155 | 0.032043 | 0.13275 | -0.013733 | 0.11902 | 0.076294 | 0.012817 | -0.048065 | -0.48065 | -0.11322 | -0.023499 | -0.004578 | 0.07782 | -0.018311 | 0.059509 | 0.041199 | 0.032043 | 0.10071 | 123.2208 | 122.9004 | 0.07782
12303.3594 | 0.045776 | 0.25421 | -0.2243 | -0.23498 | -0.1944 | -0.29266 | -0.11749 | 0.059509 | 0.036621 | 0.086975 | 0.054932 | 0.10529 | -0.036621 | 0.091553 | 0.076294 | -0.004272 | -0.048065 | -0.48172 | -0.13992 | -0.019226 | 0.004578 | 0.09613 | 0.018311 | 0.045776 | 0.045776 | 0.027466 | 0.11444 | 123.0652 | 122.9141 | 0.12817
12305.1406 | 0.076294 | 0.23178 | -0.22324 | -0.25314 | -0.18478 | -0.28091 | -0.11963 | 0.064087 | 0.013733 | 0.050354 | 0.050354 | 0.1236 | -0.009155 | 0.12817 | 0.076294 | 0.018158 | -0.053406 | -0.47745 | -0.13672 | -0.049133 | -0.045776 | 0.068665 | -0.050354 | 0.07782 | 0.068665 | 0.054932 | 0.1236 | 123.0881 | 122.9233 | 0.10529
12306.9531 | 0.061035 | 0.24246 | -0.2243 | -0.22858 | -0.19226 | -0.26489 | -0.10574 | 0.15106 | 0.036621 | 0.09613 | 0.086975 | 0.10529 | -0.050354 | 0.10529 | 0.045776 | 0.006409 | -0.054474 | -0.48386 | -0.11963 | -0.035248 | 0.059509 | 0.12817 | 0.050354 | 0.041199 | 0.022888 | 0.018311 | 0.086975 | 123.1705 | 122.8958 | 0.09613
12308.7656 | 0.061035 | 0.24353 | -0.2243 | -0.23498 | -0.18372 | -0.25314 | -0.11536 | 0.064087 | -0.013733 | 0.009155 | 0.041199 | 0.14648 | -0.009155 | 0.14648 | 0.061035 | 0.016022 | -0.044861 | -0.47852 | -0.11536 | -0.046997 | -0.036621 | 0.082397 | -0.041199 | 0.091553 | 0.064087 | 0.064087 | 0.11902 | 123.2025 | 122.8775 | 0.07782
12310.5625 | 0.061035 | 0.26276 | -0.22964 | -0.23926 | -0.18372 | -0.29587 | -0.11749 | 0.054932 | 0.018311 | 0.07782 | 0.059509 | 0.11444 | -0.032043 | 0.11444 | 0.061035 | -0.003204 | -0.053406 | -0.4924 | -0.13672 | -0.020294 | 0 | 0.10071 | 0.004578 | 0.045776 | 0.036621 | 0.036621 | 0.09613 | 123.0881 | 122.9233 | 0.13733
12312.3594 | 0.045776 | 0.22858 | -0.2179 | -0.22751 | -0.18478 | -0.2478 | -0.10361 | 0.050354 | -0.07782 | -0.009155 | 0.013733 | 0.15564 | 0.004578 | 0.14191 | 0.045776 | 0.025635 | -0.043793 | -0.48599 | -0.10574 | -0.05661 | -0.073242 | 0 | -0.11902 | 0.10071 | 0.082397 | 0.082397 | 0.14191 | 123.1476 | 122.9141 | 0.07782
12314.0625 | 0.045776 | 0.21896 | -0.20721 | -0.25314 | -0.17944 | -0.25421 | -0.11536 | 0.073242 | -0.036621 | 0.004578 | 0.045776 | 0.1236 | -0.018311 | 0.15106 | 0.061035 | 0.018158 | -0.036316 | -0.48065 | -0.11963 | -0.046997 | -0.027466 | 0.073242 | -0.050354 | 0.068665 | 0.068665 | 0.054932 | 0.11902 | 123.2071 | 122.8775 | 0.068665
12315.8594 | 0.076294 | 0.23605 | -0.23071 | -0.2211 | -0.18478 | -0.27557 | -0.11108 | 0.1236 | 0.054932 | 0.10071 | 0.091553 | 0.10071 | -0.045776 | 0.086975 | 0.045776 | 0.011749 | -0.060883 | -0.47852 | -0.11749 | -0.029907 | 0.064087 | 0.13275 | 0.045776 | 0.036621 | 0.041199 | 0.027466 | 0.082397 | 123.1934 | 122.9095 | 0.082397
12317.6719 | 0.030518 | 0.23285 | -0.20615 | -0.2446 | -0.18478 | -0.25207 | -0.11429 | 0.09613 | -0.013733 | 0.027466 | 0.050354 | 0.10986 | 0.013733 | 0.12817 | 0.061035 | 0.03952 | -0.042725 | -0.47531 | -0.12924 | -0.037384 | -0.018311 | 0.086975 | -0.050354 | 0.07782 | 0.07782 | 0.045776 | 0.10986 | 123.1934 | 122.8912 | 0.091553
12319.4688 | 0.045776 | 0.23285 | -0.22217 | -0.23392 | -0.19012 | -0.25955 | -0.11429 | 0.036621 | -0.07782 | -0.018311 | 0.022888 | 0.12817 | -0.004578 | 0.13733 | 0.061035 | 0.011749 | -0.045929 | -0.48172 | -0.11002 | -0.032043 | -0.054932 | 0 | -0.09613 | 0.068665 | 0.068665 | 0.064087 | 0.11444 | 123.175 | 122.905 | 0.064087
12321.1875 | 0.030518 | 0.2243 | -0.22003 | -0.25421 | -0.17731 | -0.27878 | -0.11002 | 0.013733 | -0.073242 | -0.009155 | 0.018311 | 0.15106 | 0.018311 | 0.14648 | 0.030518 | 0.013885 | -0.046997 | -0.47852 | -0.13565 | -0.032043 | -0.059509 | 0.036621 | -0.091553 | 0.10071 | 0.091553 | 0.068665 | 0.13275 | 123.1384 | 122.905 | 0.09613
12323 | 0.045776 | 0.23712 | -0.23392 | -0.24994 | -0.18265 | -0.28625 | -0.11322 | 0.10986 | 0.11444 | 0.14648 | 0.10986 | 0.10529 | -0.045776 | 0.10529 | 0.061035 | -0.006409 | -0.046997 | -0.48706 | -0.14206 | -0.033112 | 0.054932 | 0.19684 | 0.068665 | 0.050354 | 0.032043 | 0.018311 | 0.09613 | 123.1064 | 122.9324 | 0.10071
12324.7969 | 0.045776 | 0.24246 | -0.22537 | -0.23392 | -0.18585 | -0.27771 | -0.12924 | 0.082397 | 0.050354 | 0.07782 | 0.068665 | 0.10071 | -0.018311 | 0.13275 | 0.076294 | 0.005341 | -0.049133 | -0.48065 | -0.12604 | -0.03952 | -0.032043 | 0.091553 | -0.032043 | 0.050354 | 0.068665 | 0.045776 | 0.11902 | 123.0652 | 122.9279 | 0.11444
12326.5312 | 0.061035 | 0.23071 | -0.21576 | -0.22644 | -0.19226 | -0.2446 | -0.10468 | 0.013733 | -0.068665 | -0.045776 | 0.009155 | 0.15106 | 0 | 0.13275 | 0.061035 | 0.025635 | -0.044861 | -0.48599 | -0.10681 | -0.03952 | -0.059509 | -0.009155 | -0.091553 | 0.086975 | 0.068665 | 0.045776 | 0.11902 | 123.1567 | 122.9141 | 0.10529
12328.3281 | 0.061035 | 0.23392 | -0.21576 | -0.2211 | -0.17731 | -0.26062 | -0.11215 | 0.11444 | 0.073242 | 0.11902 | 0.10071 | 0.09613 | -0.050354 | 0.09613 | 0.061035 | 0.003204 | -0.053406 | -0.4924 | -0.10788 | -0.032043 | 0.064087 | 0.13275 | 0.041199 | 0.041199 | 0.018311 | 0.009155 | 0.073242 | 123.1934 | 122.9004 | 0.10529
12330.1094 | 0.061035 | 0.23285 | -0.23605 | -0.24567 | -0.18372 | -0.27557 | -0.11322 | 0.009155 | -0.018311 | 0.013733 | 0.009155 | 0.13275 | -0.013733 | 0.13733 | 0.076294 | 0.008545 | -0.059814 | -0.49347 | -0.12604 | -0.026703 | -0.068665 | 0.054932 | -0.068665 | 0.091553 | 0.082397 | 0.064087 | 0.1236 | 123.0789 | 122.9416 | 0.10986
12331.8438 | 0.061035 | 0.22324 | -0.2243 | -0.25101 | -0.19012 | -0.25207 | -0.11536 | 0.10529 | 0.018311 | 0.045776 | 0.064087 | 0.13275 | -0.022888 | 0.13275 | 0.030518 | 0.033112 | -0.045929 | -0.47638 | -0.11429 | -0.038452 | 0.009155 | 0.068665 | -0.054932 | 0.07782 | 0.054932 | 0.050354 | 0.1236 | 123.1796 | 122.9141 | 0.07782
12333.6406 | 0.061035 | 0.22644 | -0.23071 | -0.25528 | -0.18585 | -0.28305 | -0.11749 | 0.027466 | -0.022888 | 0.013733 | 0.013733 | 0.13733 | -0.009155 | 0.14648 | 0.076294 | 0.008545 | -0.05127 | -0.48172 | -0.14633 | -0.02243 | -0.064087 | 0.054932 | -0.064087 | 0.09613 | 0.073242 | 0.064087 | 0.12817 | 123.0927 | 122.9324 | 0.09613
12335.4219 | 0.045776 | 0.2243 | -0.2211 | -0.25421 | -0.19012 | -0.27557 | -0.11856 | 0.022888 | -0.064087 | -0.018311 | 0.004578 | 0.16022 | 0.013733 | 0.14648 | 0.076294 | 0.016022 | -0.045929 | -0.47104 | -0.12924 | -0.03952 | -0.073242 | 0.032043 | -0.07782 | 0.086975 | 0.091553 | 0.054932 | 0.11902 | 123.1522 | 122.905 | 0.091553
12337.1562 | 0.045776 | 0.24246 | -0.21896 | -0.22324 | -0.19012 | -0.25314 | -0.11429 | 0.064087 | -0.059509 | 0.004578 | 0.009155 | 0.14191 | 0 | 0.1236 | 0.061035 | 0.02243 | -0.042725 | -0.4689 | -0.11643 | -0.042725 | -0.032043 | 0.018311 | -0.073242 | 0.082397 | 0.064087 | 0.050354 | 0.11902 | 123.2162 | 122.9004 | 0.091553
12338.9531 | 0.045776 | 0.26596 | -0.23926 | -0.23285 | -0.18372 | -0.30228 | -0.12283 | 0.041199 | 0.022888 | 0.086975 | 0.050354 | 0.091553 | -0.036621 | 0.10529 | 0.076294 | -0.008545 | -0.041656 | -0.48492 | -0.14206 | -0.028839 | 0.009155 | 0.10071 | 0.022888 | 0.059509 | 0.068665 | 0.045776 | 0.10071 | 123.1247 | 122.9645 | 0.09613
12340.6875 | 0.061035 | 0.24033 | -0.21362 | -0.22644 | -0.18051 | -0.24246 | -0.11536 | 0.022888 | -0.07782 | -0.032043 | 0.009155 | 0.13733 | 0 | 0.14191 | 0.061035 | 0.021362 | -0.043793 | -0.48386 | -0.11002 | -0.030975 | -0.073242 | -0.013733 | -0.1236 | 0.091553 | 0.07782 | 0.073242 | 0.13733 | 123.1613 | 122.9233 | 0.082397
12342.4844 | 0.061035 | 0.24994 | -0.2243 | -0.24246 | -0.1944 | -0.28946 | -0.11963 | 0.10529 | 0.10986 | 0.12817 | 0.10071 | 0.10986 | -0.027466 | 0.091553 | 0.091553 | -0.008545 | -0.03952 | -0.48599 | -0.13672 | -0.026703 | 0.059509 | 0.20142 | 0.068665 | 0.054932 | 0.027466 | 0.032043 | 0.082397 | 123.1201 | 122.9141 | 0.10529
12344.2812 | 0.045776 | 0.2446 | -0.23392 | -0.23498 | -0.19333 | -0.28305 | -0.13565 | 0.07782 | 0.032043 | 0.10529 | 0.073242 | 0.10071 | -0.041199 | 0.11902 | 0.076294 | -0.002136 | -0.045929 | -0.4924 | -0.12711 | -0.044861 | 0.036621 | 0.12817 | 0.050354 | 0.054932 | 0.036621 | 0.022888 | 0.09613 | 123.1384 | 122.9462 | 0.11444
12346.0156 | 0.076294 | 0.24246 | -0.21576 | -0.25955 | -0.18265 | -0.28091 | -0.13458 | 0.1236 | 0.073242 | 0.10529 | 0.082397 | 0.10529 | -0.022888 | 0.10529 | 0.061035 | 0.003204 | -0.035248 | -0.48599 | -0.12497 | -0.038452 | 0.013733 | 0.12817 | -0.004578 | 0.059509 | 0.050354 | 0.064087 | 0.11902 | 123.0469 | 122.9507 | 0.1236
12347.8281 | 0.045776 | 0.25101 | -0.23071 | -0.24139 | -0.18906 | -0.27985 | -0.12176 | 0.068665 | 0.022888 | 0.068665 | 0.064087 | 0.09613 | -0.027466 | 0.09613 | 0.045776 | -0.003204 | -0.042725 | -0.49027 | -0.12817 | -0.040588 | 0 | 0.09613 | 0.004578 | 0.068665 | 0.041199 | 0.045776 | 0.10986 | 123.0927 | 122.9279 | 0.1236
12349.5781 | 0.061035 | 0.23926 | -0.22964 | -0.2478 | -0.18265 | -0.27237 | -0.12497 | 0.10071 | 0.073242 | 0.086975 | 0.059509 | 0.11902 | -0.036621 | 0.10071 | 0.045776 | 0.006409 | -0.05127 | -0.49027 | -0.13031 | -0.040588 | 0.027466 | 0.082397 | 0.009155 | 0.045776 | 0.041199 | 0.027466 | 0.10986 | 123.1064 | 122.9462 | 0.1236
12351.3594 | 0.045776 | 0.22003 | -0.22217 | -0.22324 | -0.18478 | -0.24246 | -0.10788 | 0.045776 | -0.082397 | -0.041199 | 0 | 0.13275 | -0.009155 | 0.15106 | 0.045776 | 0.028839 | -0.035248 | -0.47211 | -0.11108 | -0.059814 | -0.032043 | -0.013733 | -0.11444 | 0.086975 | 0.073242 | 0.041199 | 0.1236 | 123.1934 | 122.9233 | 0.1236
12353.1562 | 0.061035 | 0.22644 | -0.22217 | -0.22537 | -0.17197 | -0.24567 | -0.10895 | 0.068665 | 0.009155 | 0.013733 | 0.045776 | 0.13275 | -0.004578 | 0.13733 | 0.045776 | 0.013885 | -0.03418 | -0.47745 | -0.10468 | -0.044861 | 0 | 0.068665 | -0.054932 | 0.07782 | 0.064087 | 0.068665 | 0.13275 | 123.23 | 122.8958 | 0.086975
12354.9531 | 0.076294 | 0.22644 | -0.23285 | -0.25421 | -0.18265 | -0.28305 | -0.11002 | 0.10071 | 0.086975 | 0.12817 | 0.10071 | 0.10529 | -0.045776 | 0.10529 | 0.045776 | 0.003204 | -0.03418 | -0.48706 | -0.14099 | -0.038452 | 0.022888 | 0.14648 | 0.018311 | 0.041199 | 0.054932 | 0.032043 | 0.10529 | 123.0743 | 122.9691 | 0.12817
12356.75 | 0.061035 | 0.23819 | -0.23178 | -0.23712 | -0.18158 | -0.27237 | -0.11215 | 0.082397 | 0.073242 | 0.082397 | 0.073242 | 0.10986 | -0.018311 | 0.13275 | 0.045776 | 0 | -0.044861 | -0.48706 | -0.11856 | -0.025635 | -0.018311 | 0.10529 | -0.050354 | 0.082397 | 0.054932 | 0.050354 | 0.11444 | 123.0881 | 122.9462 | 0.12817
12358.5 | 0.030518 | 0.2243 | -0.2179 | -0.24887 | -0.17731 | -0.27664 | -0.11963 | 0.09613 | 0.091553 | 0.09613 | 0.10071 | 0.11444 | -0.032043 | 0.10986 | 0.061035 | 0.009613 | -0.03952 | -0.48813 | -0.13886 | -0.043793 | 0.018311 | 0.14191 | 0.013733 | 0.059509 | 0.064087 | 0.027466 | 0.10986 | 123.0698 | 122.9782 | 0.11444
12360.2969 | 0.045776 | 0.2681 | -0.22644 | -0.23392 | -0.18478 | -0.27237 | -0.12176 | 0.16022 | 0.16479 | 0.11902 | 0.10071 | 0.10529 | -0.027466 | 0.10071 | 0.061035 | -0.002136 | -0.040588 | -0.48172 | -0.12924 | -0.028839 | 0.059509 | 0.19684 | 0.059509 | 0.050354 | 0.050354 | 0.022888 | 0.11902 | 123.1338 | 122.9599 | 0.11444
12362.0156 | 0.030518 | 0.24139 | -0.22751 | -0.21469 | -0.18799 | -0.25848 | -0.11002 | 0.13275 | 0.086975 | 0.12817 | 0.091553 | 0.10529 | -0.036621 | 0.091553 | 0.045776 | 0.006409 | -0.045929 | -0.49027 | -0.11429 | -0.041656 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.018311 | 0.041199 | 0.082397 | 123.1705 | 122.9462 | 0.10071
12363.8125 | 0.061035 | 0.22537 | -0.21896 | -0.2243 | -0.18906 | -0.23605 | -0.10681 | 0.082397 | -0.018311 | 0 | 0.027466 | 0.13733 | -0.013733 | 0.14191 | 0.061035 | 0.028839 | -0.040588 | -0.48172 | -0.10895 | -0.045929 | -0.045776 | 0.009155 | -0.10529 | 0.086975 | 0.059509 | 0.064087 | 0.13733 | 123.175 | 122.937 | 0.10529
12365.5469 | 0.061035 | 0.22537 | -0.23605 | -0.24139 | -0.18051 | -0.28091 | -0.11322 | 0.10529 | 0.11444 | 0.13733 | 0.10071 | 0.10529 | -0.059509 | 0.09613 | 0.045776 | -0.004272 | -0.03418 | -0.48813 | -0.13245 | -0.033112 | 0.054932 | 0.19226 | 0.050354 | 0.050354 | 0.041199 | 0.022888 | 0.09613 | 123.0972 | 122.9507 | 0.13275
12367.3438 | 0.061035 | 0.23498 | -0.2243 | -0.23926 | -0.18585 | -0.25955 | -0.11643 | 0.027466 | -0.041199 | -0.004578 | 0.027466 | 0.14648 | -0.004578 | 0.15106 | 0.045776 | 0.014954 | -0.02243 | -0.47958 | -0.1239 | -0.038452 | -0.059509 | 0.054932 | -0.073242 | 0.086975 | 0.091553 | 0.064087 | 0.11444 | 123.23 | 122.9279 | 0.086975
12369.0781 | 0.076294 | 0.23926 | -0.23605 | -0.24033 | -0.18585 | -0.26382 | -0.10468 | 0.13275 | 0.09613 | 0.11444 | 0.09613 | 0.10071 | -0.045776 | 0.091553 | 0.076294 | 0.003204 | -0.03952 | -0.4892 | -0.11215 | -0.030975 | 0.068665 | 0.14648 | 0.041199 | 0.022888 | 0.027466 | 0.027466 | 0.09613 | 123.2071 | 122.9141 | 0.10071
12370.875 | 0.045776 | 0.23178 | -0.22644 | -0.26169 | -0.17944 | -0.2713 | -0.11429 | 0.11444 | 0.07782 | 0.10071 | 0.09613 | 0.10529 | -0.027466 | 0.09613 | 0.061035 | 0.011749 | -0.037384 | -0.48706 | -0.13672 | -0.044861 | 0.009155 | 0.1236 | -0.009155 | 0.041199 | 0.054932 | 0.041199 | 0.10071 | 123.0789 | 122.9233 | 0.12817
12372.6094 | 0.061035 | 0.24567 | -0.22217 | -0.23178 | -0.18051 | -0.2681 | -0.10788 | 0.14191 | 0.086975 | 0.1236 | 0.10071 | 0.086975 | -0.045776 | 0.091553 | 0.076294 | -0.002136 | -0.042725 | -0.48706 | -0.11963 | -0.049133 | 0.064087 | 0.14191 | 0.041199 | 0.045776 | 0.027466 | 0.041199 | 0.082397 | 123.1842 | 122.9416 | 0.11444
12374.4219 | 0.076294 | 0.23498 | -0.2211 | -0.22751 | -0.18799 | -0.25635 | -0.11749 | 0.036621 | -0.027466 | 0 | 0.027466 | 0.1236 | 0 | 0.13733 | 0.061035 | 0.019226 | -0.041656 | -0.47318 | -0.11002 | -0.042725 | -0.045776 | 0.07782 | -0.064087 | 0.091553 | 0.054932 | 0.064087 | 0.11444 | 123.2391 | 122.9187 | 0.091553
12376.2031 | 0.061035 | 0.27023 | -0.23392 | -0.22858 | -0.19653 | -0.28412 | -0.12711 | 0.041199 | 0.032043 | 0.07782 | 0.050354 | 0.11444 | -0.059509 | 0.10071 | 0.061035 | 0 | -0.057678 | -0.49774 | -0.12924 | -0.033112 | 0.004578 | 0.082397 | 0.013733 | 0.068665 | 0.050354 | 0.036621 | 0.11902 | 123.111 | 122.9553 | 0.1236
12378 | 0.076294 | 0.24994 | -0.22751 | -0.23605 | -0.18051 | -0.25742 | -0.11322 | 0.10986 | 0.004578 | 0.041199 | 0.041199 | 0.11902 | -0.036621 | 0.13275 | 0.061035 | 0.008545 | -0.048065 | -0.48706 | -0.11536 | -0.038452 | 0.050354 | 0.11902 | 0.013733 | 0.036621 | 0.036621 | 0.036621 | 0.09613 | 123.2346 | 122.9187 | 0.086975
12379.7969 | 0.045776 | 0.22217 | -0.22217 | -0.25314 | -0.1741 | -0.25314 | -0.11215 | 0.041199 | -0.059509 | 0.004578 | 0.027466 | 0.12817 | -0.009155 | 0.12817 | 0.061035 | 0.011749 | -0.029907 | -0.48279 | -0.13138 | -0.041656 | -0.054932 | 0.045776 | -0.082397 | 0.068665 | 0.10529 | 0.068665 | 0.13275 | 123.2025 | 122.9324 | 0.07782
12381.5938 | 0.061035 | 0.23605 | -0.22324 | -0.23071 | -0.16983 | -0.25955 | -0.10574 | 0.14648 | 0.064087 | 0.10529 | 0.091553 | 0.09613 | -0.041199 | 0.10071 | 0.045776 | 0.009613 | -0.035248 | -0.47745 | -0.11963 | -0.036316 | 0.068665 | 0.14191 | 0.032043 | 0.045776 | 0.045776 | 0.018311 | 0.068665 | 123.2208 | 122.9233 | 0.07782
12383.3438 | 0.061035 | 0.22003 | -0.21255 | -0.23285 | -0.17838 | -0.2478 | -0.10361 | 0.054932 | -0.032043 | -0.009155 | 0.027466 | 0.12817 | -0.013733 | 0.14191 | 0.061035 | 0.02243 | -0.030975 | -0.48279 | -0.10147 | -0.035248 | -0.059509 | 0.009155 | -0.11444 | 0.086975 | 0.082397 | 0.068665 | 0.11444 | 123.1888 | 122.9279 | 0.09613
12385.1406 | 0.045776 | 0.25314 | -0.24033 | -0.22858 | -0.18906 | -0.28946 | -0.11215 | 0.10529 | 0.082397 | 0.1236 | 0.082397 | 0.082397 | -0.032043 | 0.09613 | 0.076294 | -0.002136 | -0.043793 | -0.49774 | -0.11429 | -0.027771 | 0.041199 | 0.1236 | 0.027466 | 0.054932 | 0.009155 | 0.036621 | 0.10529 | 123.1155 | 122.9691 | 0.1236
12386.875 | 0.061035 | 0.22217 | -0.2243 | -0.24139 | -0.18799 | -0.25528 | -0.10468 | 0.068665 | 0.009155 | 0.041199 | 0.050354 | 0.12817 | 0.013733 | 0.15106 | 0.045776 | 0.006409 | -0.037384 | -0.48706 | -0.1207 | -0.036316 | -0.027466 | 0.086975 | -0.045776 | 0.07782 | 0.045776 | 0.050354 | 0.11902 | 123.2346 | 122.937 | 0.086975
12388.6719 | 0.061035 | 0.25848 | -0.22217 | -0.24674 | -0.18158 | -0.29587 | -0.12711 | 0.045776 | 0.036621 | 0.07782 | 0.050354 | 0.10529 | -0.027466 | 0.10986 | 0.045776 | -0.012817 | -0.043793 | -0.48172 | -0.12604 | -0.026703 | -0.013733 | 0.091553 | 0.018311 | 0.059509 | 0.036621 | 0.027466 | 0.10071 | 123.1384 | 122.9736 | 0.11444
12390.4688 | 0.061035 | 0.21469 | -0.23071 | -0.23392 | -0.18799 | -0.25101 | -0.11215 | 0.09613 | 0.018311 | 0.032043 | 0.059509 | 0.1236 | -0.022888 | 0.12817 | 0.045776 | 0.010681 | -0.035248 | -0.48492 | -0.1004 | -0.038452 | 0.009155 | 0.091553 | -0.050354 | 0.068665 | 0.054932 | 0.059509 | 0.11902 | 123.2346 | 122.9233 | 0.082397
12392.25 | 0.045776 | 0.2446 | -0.22644 | -0.25848 | -0.17517 | -0.28946 | -0.12497 | 0.045776 | 0.032043 | 0.086975 | 0.059509 | 0.11444 | -0.022888 | 0.09613 | 0.045776 | -0.011749 | -0.036316 | -0.48492 | -0.15915 | -0.024567 | 0.032043 | 0.1236 | 0.041199 | 0.050354 | 0.041199 | 0.036621 | 0.091553 | 123.1338 | 122.9645 | 0.11902
12394 | 0.076294 | 0.24567 | -0.23285 | -0.23712 | -0.17517 | -0.27985 | -0.11536 | 0.12817 | 0.073242 | 0.11444 | 0.064087 | 0.091553 | -0.050354 | 0.07782 | 0.045776 | 0.008545 | -0.048065 | -0.48706 | -0.13458 | -0.037384 | 0.054932 | 0.10071 | 0.013733 | 0.054932 | 0.027466 | 0.027466 | 0.091553 | 123.111 | 122.9874 | 0.13275
12395.7969 | 0.061035 | 0.23926 | -0.2211 | -0.23071 | -0.17303 | -0.2681 | -0.12283 | 0.13275 | 0.073242 | 0.11444 | 0.07782 | 0.10071 | -0.050354 | 0.10986 | 0.061035 | 0.002136 | -0.052338 | -0.48279 | -0.12176 | -0.028839 | 0.068665 | 0.12817 | 0.041199 | 0.032043 | 0.045776 | 0.022888 | 0.086975 | 123.1064 | 122.9553 | 0.11444
12397.6094 | 0.061035 | 0.24139 | -0.2211 | -0.23819 | -0.17303 | -0.25635 | -0.11322 | 0.059509 | -0.036621 | -0.009155 | 0.022888 | 0.14191 | 0 | 0.13275 | 0.061035 | 0.026703 | -0.036316 | -0.48706 | -0.10895 | -0.046997 | -0.027466 | 0.064087 | -0.059509 | 0.10071 | 0.068665 | 0.050354 | 0.10529 | 123.2346 | 122.9279 | 0.091553
12399.3438 | 0.045776 | 0.24674 | -0.22644 | -0.23712 | -0.17197 | -0.26276 | -0.11856 | 0.013733 | -0.018311 | 0.013733 | 0.009155 | 0.13275 | -0.009155 | 0.14191 | 0.061035 | 0.006409 | -0.037384 | -0.49133 | -0.11749 | -0.035248 | -0.045776 | 0.036621 | -0.082397 | 0.10071 | 0.064087 | 0.082397 | 0.1236 | 123.1155 | 122.9599 | 0.10071
12401.125 | 0.076294 | 0.25421 | -0.23071 | -0.24033 | -0.18799 | -0.29373 | -0.11322 | 0.045776 | 0.018311 | 0.059509 | 0.054932 | 0.10986 | -0.022888 | 0.09613 | 0.030518 | -0.012817 | -0.038452 | -0.48492 | -0.13245 | -0.042725 | 0.004578 | 0.10986 | 0.004578 | 0.059509 | 0.050354 | 0.027466 | 0.10071 | 123.1522 | 122.9691 | 0.11902
12402.9219 | 0.061035 | 0.25848 | -0.22537 | -0.23071 | -0.18051 | -0.25421 | -0.11429 | 0.14191 | 0.068665 | 0.10071 | 0.091553 | 0.10071 | -0.050354 | 0.10071 | 0.061035 | 0.01709 | -0.043793 | -0.48386 | -0.11749 | -0.041656 | 0.073242 | 0.12817 | 0.027466 | 0.036621 | 0.027466 | 0.036621 | 0.07782 | 123.23 | 122.9141 | 0.086975
12404.6562 | 0.045776 | 0.23926 | -0.21896 | -0.22324 | -0.18051 | -0.25742 | -0.11749 | 0.13275 | 0.082397 | 0.091553 | 0.09613 | 0.091553 | -0.045776 | 0.086975 | 0.061035 | 0.012817 | -0.05127 | -0.48386 | -0.10788 | -0.042725 | 0.073242 | 0.12817 | 0.041199 | 0.050354 | 0.013733 | 0.013733 | 0.082397 | 123.2254 | 122.937 | 0.091553
12406.4531 | 0.061035 | 0.25207 | -0.22751 | -0.25101 | -0.19226 | -0.27664 | -0.12604 | 0.091553 | 0.054932 | 0.09613 | 0.045776 | 0.10071 | -0.050354 | 0.10529 | 0.076294 | 0.005341 | -0.025635 | -0.47852 | -0.13138 | -0.035248 | 0.027466 | 0.091553 | 0.009155 | 0.036621 | 0.045776 | 0.032043 | 0.091553 | 123.1155 | 122.9691 | 0.1236
12408.25 | 0.045776 | 0.25528 | -0.23605 | -0.22964 | -0.19546 | -0.27344 | -0.11536 | 0.12817 | 0.091553 | 0.10986 | 0.068665 | 0.09613 | -0.050354 | 0.10986 | 0.061035 | 0.009613 | -0.033112 | -0.49133 | -0.11108 | -0.036316 | 0.068665 | 0.11444 | 0.004578 | 0.041199 | 0.027466 | 0.032043 | 0.086975 | 123.111 | 123.0011 | 0.13733
12410.0625 | 0.030518 | 0.2681 | -0.23605 | -0.23071 | -0.1944 | -0.26169 | -0.1207 | 0.12817 | 0.068665 | 0.091553 | 0.054932 | 0.09613 | -0.041199 | 0.11444 | 0.061035 | 0.003204 | -0.043793 | -0.48813 | -0.12924 | -0.042725 | 0.041199 | 0.086975 | -0.004578 | 0.045776 | 0.032043 | 0.027466 | 0.082397 | 123.1064 | 122.9874 | 0.11902
12411.7969 | 0.076294 | 0.24887 | -0.22537 | -0.23178 | -0.18158 | -0.24674 | -0.11963 | 0.054932 | -0.032043 | -0.022888 | 0.018311 | 0.13733 | -0.013733 | 0.15106 | 0.061035 | 0.025635 | -0.03952 | -0.48492 | -0.11429 | -0.03952 | -0.064087 | 0.018311 | -0.09613 | 0.086975 | 0.07782 | 0.068665 | 0.1236 | 123.1659 | 122.937 | 0.10071
12413.5938 | 0.061035 | 0.23819 | -0.23712 | -0.24246 | -0.18692 | -0.27664 | -0.12497 | 0.13733 | 0.14191 | 0.14648 | 0.10529 | 0.10529 | -0.036621 | 0.10986 | 0.045776 | -0.003204 | -0.03418 | -0.49561 | -0.13992 | -0.038452 | 0.068665 | 0.19226 | 0.064087 | 0.054932 | 0.032043 | 0.032043 | 0.091553 | 123.1613 | 122.9462 | 0.10986
12415.3906 | 0.045776 | 0.25421 | -0.22964 | -0.24567 | -0.18372 | -0.28091 | -0.11963 | 0.086975 | 0.032043 | 0.091553 | 0.036621 | 0.10986 | -0.032043 | 0.10529 | 0.076294 | 0.006409 | -0.032043 | -0.4892 | -0.13565 | -0.040588 | 0.027466 | 0.086975 | 0 | 0.059509 | 0.045776 | 0.041199 | 0.10986 | 123.1247 | 122.9828 | 0.11902
12417.1094 | 0.030518 | 0.26276 | -0.23498 | -0.23285 | -0.18906 | -0.27557 | -0.12497 | 0.050354 | 0.032043 | 0.07782 | 0.059509 | 0.11902 | -0.027466 | 0.10529 | 0.076294 | -0.010681 | -0.025635 | -0.4924 | -0.13351 | -0.042725 | 0.022888 | 0.11444 | 0.022888 | 0.045776 | 0.036621 | 0.022888 | 0.09613 | 123.1659 | 122.9599 | 0.12817
12418.9062 | 0.045776 | 0.21362 | -0.21149 | -0.25101 | -0.17731 | -0.23178 | -0.10254 | 0.14191 | 0.018311 | 0.036621 | 0.064087 | 0.1236 | -0.004578 | 0.14648 | 0.076294 | 0.027771 | -0.036316 | -0.47318 | -0.10468 | -0.05661 | 0.022888 | 0.07782 | -0.07782 | 0.073242 | 0.050354 | 0.045776 | 0.13275 | 123.1888 | 122.9507 | 0.073242
12420.6406 | 0.045776 | 0.23605 | -0.21255 | -0.23712 | -0.19333 | -0.24353 | -0.10574 | 0.11444 | 0.013733 | 0.036621 | 0.059509 | 0.13733 | -0.004578 | 0.13275 | 0.061035 | 0.032043 | -0.026703 | -0.47211 | -0.11536 | -0.044861 | 0.013733 | 0.082397 | -0.050354 | 0.073242 | 0.082397 | 0.041199 | 0.10529 | 123.2208 | 122.9416 | 0.07782
12422.4219 | 0.045776 | 0.23285 | -0.21896 | -0.23819 | -0.19546 | -0.25101 | -0.10681 | 0.068665 | -0.009155 | 0 | 0.009155 | 0.11444 | -0.013733 | 0.12817 | 0.061035 | 0.029907 | -0.029907 | -0.48065 | -0.10574 | -0.029907 | -0.045776 | 0.032043 | -0.10986 | 0.068665 | 0.07782 | 0.064087 | 0.11444 | 123.1842 | 122.9645 | 0.091553
12424.2188 | 0.061035 | 0.24887 | -0.22217 | -0.24139 | -0.19333 | -0.29694 | -0.11429 | 0.059509 | 0.032043 | 0.082397 | 0.059509 | 0.086975 | -0.036621 | 0.082397 | 0.061035 | 0.002136 | -0.032043 | -0.4892 | -0.13031 | -0.026703 | 0 | 0.10529 | 0.013733 | 0.059509 | 0.041199 | 0.036621 | 0.082397 | 123.1247 | 122.9874 | 0.12817
12425.9531 | 0.030518 | 0.23178 | -0.20721 | -0.23498 | -0.19333 | -0.24139 | -0.10254 | 0.10986 | 0.009155 | 0.022888 | 0.054932 | 0.12817 | -0.018311 | 0.11902 | 0.030518 | 0.027771 | -0.037384 | -0.47852 | -0.10895 | -0.035248 | -0.004578 | 0.086975 | -0.073242 | 0.073242 | 0.068665 | 0.059509 | 0.11902 | 123.1842 | 122.9645 | 0.082397
12427.75 | 0.061035 | 0.26169 | -0.23285 | -0.23819 | -0.18906 | -0.29373 | -0.11536 | 0.10071 | 0.10986 | 0.14191 | 0.091553 | 0.10071 | -0.041199 | 0.10529 | 0.091553 | -0.010681 | -0.030975 | -0.49133 | -0.13672 | -0.030975 | 0.073242 | 0.17853 | 0.082397 | 0.041199 | 0.027466 | 0.027466 | 0.07782 | 123.1659 | 122.9691 | 0.1236
12429.4844 | 0.045776 | 0.21255 | -0.22537 | -0.25848 | -0.1709 | -0.25742 | -0.11429 | 0.050354 | -0.050354 | -0.027466 | 0.013733 | 0.14648 | 0 | 0.1236 | 0.061035 | 0.019226 | -0.02243 | -0.47638 | -0.13245 | -0.042725 | -0.064087 | 0.054932 | -0.068665 | 0.073242 | 0.064087 | 0.064087 | 0.13275 | 123.2117 | 122.9324 | 0.10071
12431.2656 | 0.045776 | 0.23498 | -0.21469 | -0.23605 | -0.18799 | -0.2478 | -0.10147 | 0.068665 | -0.009155 | -0.004578 | 0.027466 | 0.15106 | 0 | 0.1236 | 0.061035 | 0.026703 | -0.036316 | -0.48065 | -0.10574 | -0.041656 | -0.032043 | 0.027466 | -0.10529 | 0.091553 | 0.068665 | 0.054932 | 0.11902 | 123.1979 | 122.9645 | 0.082397
12433.0625 | 0.045776 | 0.23392 | -0.22324 | -0.24033 | -0.17838 | -0.28946 | -0.12176 | 0.10986 | 0.11444 | 0.13275 | 0.091553 | 0.09613 | -0.036621 | 0.10071 | 0.061035 | -0.002136 | -0.03952 | -0.50095 | -0.1239 | -0.033112 | 0.041199 | 0.16479 | 0.045776 | 0.045776 | 0.027466 | 0.027466 | 0.10529 | 123.111 | 122.9828 | 0.10986
12434.8125 | 0.045776 | 0.24033 | -0.2243 | -0.24246 | -0.18051 | -0.28519 | -0.11643 | 0.10071 | 0.07782 | 0.091553 | 0.082397 | 0.11444 | -0.022888 | 0.11444 | 0.045776 | 0.002136 | -0.030975 | -0.49027 | -0.12817 | -0.030975 | 0.004578 | 0.11444 | -0.022888 | 0.068665 | 0.050354 | 0.054932 | 0.1236 | 123.1018 | 122.9919 | 0.10986
12436.6094 | 0.061035 | 0.23819 | -0.22537 | -0.22537 | -0.17838 | -0.26703 | -0.11856 | 0.12817 | 0.086975 | 0.10529 | 0.09613 | 0.082397 | -0.050354 | 0.10071 | 0.061035 | 0.002136 | -0.024567 | -0.47852 | -0.11536 | -0.037384 | 0.059509 | 0.15106 | 0.036621 | 0.032043 | 0.027466 | 0.022888 | 0.09613 | 123.23 | 122.9553 | 0.09613
12438.3906 | 0.061035 | 0.23178 | -0.21683 | -0.23605 | -0.17731 | -0.25207 | -0.11856 | 0.050354 | -0.041199 | 0.004578 | 0.018311 | 0.14191 | -0.004578 | 0.13275 | 0.045776 | 0.020294 | -0.027771 | -0.48599 | -0.11429 | -0.040588 | -0.018311 | 0.027466 | -0.054932 | 0.059509 | 0.050354 | 0.050354 | 0.11902 | 123.262 | 122.9462 | 0.086975
12440.1875 | 0.061035 | 0.25101 | -0.23178 | -0.2446 | -0.17838 | -0.29053 | -0.1207 | 0.036621 | 0.032043 | 0.082397 | 0.059509 | 0.10986 | -0.022888 | 0.1236 | 0.045776 | -0.012817 | -0.025635 | -0.49027 | -0.14099 | -0.018158 | -0.004578 | 0.09613 | 0.027466 | 0.050354 | 0.050354 | 0.032043 | 0.1236 | 123.1522 | 122.9507 | 0.11902
12441.9375 | 0.076294 | 0.23712 | -0.22751 | -0.24567 | -0.17303 | -0.26703 | -0.11856 | 0.14191 | 0.082397 | 0.11902 | 0.09613 | 0.073242 | -0.050354 | 0.082397 | 0.061035 | -0.002136 | -0.02243 | -0.48706 | -0.12604 | -0.045929 | 0.059509 | 0.14648 | 0.027466 | 0.032043 | 0.022888 | 0.022888 | 0.07782 | 123.1567 | 122.9782 | 0.10986
12443.7344 | 0.061035 | 0.23178 | -0.22644 | -0.25101 | -0.18158 | -0.28412 | -0.12924 | 0.13733 | 0.10071 | 0.11902 | 0.09613 | 0.10529 | -0.041199 | 0.10529 | 0.076294 | 0.011749 | -0.035248 | -0.49027 | -0.13031 | -0.032043 | 0.041199 | 0.16022 | 0.032043 | 0.032043 | 0.027466 | 0.018311 | 0.10071 | 123.1247 | 123.0011 | 0.11902
12445.5312 | 0.045776 | 0.23819 | -0.22644 | -0.23498 | -0.17517 | -0.24246 | -0.11963 | 0.068665 | -0.027466 | -0.004578 | 0.009155 | 0.14648 | -0.009155 | 0.11902 | 0.045776 | 0.014954 | -0.018158 | -0.48065 | -0.11322 | -0.045929 | 0.009155 | 0.041199 | -0.036621 | 0.059509 | 0.045776 | 0.036621 | 0.11902 | 123.2758 | 122.9507 | 0.082397
12447.2656 | 0.045776 | 0.22964 | -0.20828 | -0.25314 | -0.17838 | -0.24033 | -0.099335 | 0.10986 | 0.009155 | 0.032043 | 0.045776 | 0.13733 | -0.009155 | 0.11902 | 0.045776 | 0.038452 | -0.029907 | -0.47424 | -0.12176 | -0.05127 | 0.009155 | 0.082397 | -0.059509 | 0.050354 | 0.041199 | 0.041199 | 0.11444 | 123.2529 | 122.9324 | 0.091553
12449.0781 | 0.061035 | 0.21469 | -0.21469 | -0.2446 | -0.18906 | -0.25742 | -0.10895 | 0.068665 | -0.013733 | 0.036621 | 0.045776 | 0.10529 | -0.027466 | 0.11444 | 0.061035 | 0.011749 | -0.016022 | -0.47958 | -0.12817 | -0.035248 | 0.045776 | 0.10529 | 0 | 0.050354 | 0.022888 | 0.027466 | 0.09613 | 123.2666 | 122.9691 | 0.082397
12450.8125 | 0.030518 | 0.2179 | -0.21896 | -0.2243 | -0.18265 | -0.25742 | -0.10147 | 0.004578 | -0.064087 | -0.036621 | 0.004578 | 0.14648 | 0.009155 | 0.14191 | 0.045776 | 0.02243 | -0.027771 | -0.4924 | -0.10788 | -0.042725 | -0.045776 | 0.013733 | -0.09613 | 0.10071 | 0.064087 | 0.045776 | 0.10529 | 123.2208 | 122.9553 | 0.10529
12452.6094 | 0.045776 | 0.23819 | -0.23178 | -0.23285 | -0.18906 | -0.2713 | -0.11215 | 0.11902 | 0.10529 | 0.12817 | 0.10071 | 0.11444 | -0.036621 | 0.10071 | 0.061035 | 0.013885 | -0.029907 | -0.47745 | -0.11643 | -0.023499 | 0.064087 | 0.15564 | 0.050354 | 0.041199 | 0.036621 | 0.022888 | 0.09613 | 123.1979 | 122.9691 | 0.082397
12454.4062 | 0.061035 | 0.22324 | -0.23498 | -0.23392 | -0.18158 | -0.25528 | -0.1004 | 0.091553 | 0.018311 | 0.032043 | 0.050354 | 0.12817 | 0 | 0.12817 | 0.045776 | 0.024567 | -0.013885 | -0.48813 | -0.11429 | -0.044861 | 0 | 0.086975 | -0.054932 | 0.068665 | 0.050354 | 0.050354 | 0.09613 | 123.2483 | 122.937 | 0.091553
12456.125 | 0.030518 | 0.23178 | -0.21683 | -0.23712 | -0.17944 | -0.24567 | -0.1004 | 0.041199 | -0.054932 | -0.013733 | 0.018311 | 0.1236 | -0.009155 | 0.1236 | 0.061035 | 0.020294 | -0.020294 | -0.47958 | -0.11749 | -0.029907 | -0.054932 | 0.004578 | -0.10986 | 0.091553 | 0.068665 | 0.068665 | 0.12817 | 123.1979 | 122.9691 | 0.086975
12457.9219 | 0.045776 | 0.2446 | -0.23178 | -0.24353 | -0.17838 | -0.2948 | -0.11215 | 0.054932 | 0.041199 | 0.086975 | 0.054932 | 0.10529 | -0.050354 | 0.10529 | 0.061035 | -0.008545 | -0.020294 | -0.49881 | -0.13779 | -0.02243 | 0.013733 | 0.10529 | 0.013733 | 0.045776 | 0.059509 | 0.009155 | 0.09613 | 123.111 | 123.0148 | 0.10529
12459.7344 | 0.061035 | 0.23071 | -0.22858 | -0.23285 | -0.17517 | -0.25635 | -0.1239 | 0.036621 | -0.059509 | -0.027466 | 0.036621 | 0.13275 | -0.022888 | 0.12817 | 0.045776 | 0.01709 | -0.032043 | -0.48279 | -0.10254 | -0.035248 | -0.054932 | -0.004578 | -0.091553 | 0.086975 | 0.073242 | 0.054932 | 0.13275 | 123.2391 | 122.9645 | 0.082397
12461.4688 | 0.061035 | 0.21683 | -0.21255 | -0.23926 | -0.17731 | -0.24567 | -0.10574 | 0.045776 | -0.036621 | -0.009155 | 0.018311 | 0.14191 | -0.004578 | 0.14191 | 0.045776 | 0.013885 | -0.032043 | -0.49027 | -0.11002 | -0.043793 | -0.050354 | 0.004578 | -0.09613 | 0.068665 | 0.064087 | 0.059509 | 0.1236 | 123.2071 | 122.9645 | 0.07782
12463.25 | 0.076294 | 0.22003 | -0.2243 | -0.23819 | -0.17624 | -0.24887 | -0.11215 | 0.068665 | 0 | 0.009155 | 0.036621 | 0.1236 | -0.009155 | 0.13275 | 0.061035 | 0.032043 | -0.03418 | -0.47424 | -0.11643 | -0.03952 | -0.036621 | 0.045776 | -0.082397 | 0.07782 | 0.059509 | 0.073242 | 0.1236 | 123.1888 | 122.9553 | 0.082397
12465.0469 | 0.076294 | 0.22217 | -0.21896 | -0.2478 | -0.17731 | -0.27878 | -0.1207 | 0 | -0.045776 | -0.022888 | 0.032043 | 0.14191 | 0 | 0.14648 | 0.045776 | 0.016022 | -0.018158 | -0.48386 | -0.11536 | -0.035248 | -0.064087 | 0.054932 | -0.068665 | 0.10071 | 0.068665 | 0.07782 | 0.15106 | 123.23 | 122.9279 | 0.091553
12466.7812 | 0.061035 | 0.22537 | -0.21255 | -0.25101 | -0.18692 | -0.25635 | -0.11749 | 0.073242 | 0.013733 | 0.036621 | 0.054932 | 0.1236 | -0.013733 | 0.15564 | 0.076294 | 0.026703 | -0.010681 | -0.48279 | -0.12283 | -0.033112 | -0.013733 | 0.086975 | -0.036621 | 0.073242 | 0.064087 | 0.054932 | 0.11444 | 123.2483 | 122.9553 | 0.082397
12468.5781 | 0.061035 | 0.25421 | -0.23178 | -0.23712 | -0.18478 | -0.29694 | -0.11749 | 0.027466 | 0.032043 | 0.064087 | 0.045776 | 0.11444 | -0.032043 | 0.10986 | 0.061035 | -0.008545 | -0.016022 | -0.49133 | -0.12924 | -0.018158 | -0.022888 | 0.086975 | 0.022888 | 0.059509 | 0.054932 | 0.022888 | 0.091553 | 123.175 | 123.0011 | 0.10986
12470.3594 | 0.061035 | 0.23498 | -0.2211 | -0.24246 | -0.19226 | -0.25848 | -0.1239 | 0.036621 | -0.059509 | 0 | 0.027466 | 0.13275 | -0.009155 | 0.12817 | 0.076294 | 0.014954 | -0.008545 | -0.49027 | -0.12604 | -0.046997 | -0.054932 | 0.050354 | -0.073242 | 0.082397 | 0.07782 | 0.068665 | 0.10071 | 123.2529 | 122.9279 | 0.064087
12472.1562 | 0.061035 | 0.24353 | -0.22964 | -0.23819 | -0.18585 | -0.27344 | -0.1239 | 0.032043 | -0.050354 | -0.004578 | 0.032043 | 0.14191 | 0 | 0.14191 | 0.076294 | 0.009613 | -0.021362 | -0.48386 | -0.11002 | -0.036316 | -0.07782 | 0.045776 | -0.07782 | 0.082397 | 0.086975 | 0.064087 | 0.13275 | 123.2391 | 122.9507 | 0.091553
12473.8906 | 0.061035 | 0.24567 | -0.23178 | -0.25742 | -0.17731 | -0.29159 | -0.11856 | 0.086975 | 0.09613 | 0.14648 | 0.086975 | 0.10986 | -0.032043 | 0.10071 | 0.076294 | -0.013885 | -0.018158 | -0.4892 | -0.14633 | -0.029907 | 0.064087 | 0.19226 | 0.07782 | 0.041199 | 0.032043 | 0.018311 | 0.082397 | 123.1796 | 122.9919 | 0.10986
12475.6875 | 0.045776 | 0.22751 | -0.23819 | -0.22751 | -0.17838 | -0.24567 | -0.11108 | 0.036621 | -0.045776 | -0.027466 | 0.009155 | 0.13733 | -0.009155 | 0.12817 | 0.045776 | 0.026703 | -0.02243 | -0.48172 | -0.10681 | -0.048065 | -0.086975 | -0.004578 | -0.1236 | 0.086975 | 0.054932 | 0.068665 | 0.1236 | 123.2071 | 122.9645 | 0.10986
12477.4844 | 0.061035 | 0.23498 | -0.2211 | -0.23498 | -0.19333 | -0.26062 | -0.11002 | 0.041199 | -0.045776 | -0.018311 | 0.004578 | 0.15106 | 0 | 0.13733 | 0.045776 | 0.018158 | -0.021362 | -0.47638 | -0.11536 | -0.03418 | -0.027466 | 0.009155 | -0.082397 | 0.073242 | 0.073242 | 0.036621 | 0.13275 | 123.2712 | 122.9507 | 0.064087
12479.2656 | 0.061035 | 0.23178 | -0.23498 | -0.25207 | -0.18051 | -0.28305 | -0.11536 | 0.091553 | 0.041199 | 0.064087 | 0.068665 | 0.10529 | -0.036621 | 0.1236 | 0.061035 | 0.006409 | -0.012817 | -0.48706 | -0.12711 | -0.027771 | -0.050354 | 0.073242 | -0.045776 | 0.068665 | 0.07782 | 0.054932 | 0.12817 | 123.1338 | 122.9874 | 0.11902
12481 | 0.061035 | 0.22537 | -0.2179 | -0.24246 | -0.16769 | -0.28091 | -0.13351 | 0.036621 | -0.018311 | 0.036621 | 0.027466 | 0.13275 | 0.018311 | 0.13275 | 0.030518 | 0.011749 | -0.020294 | -0.48813 | -0.13886 | -0.038452 | -0.064087 | 0.050354 | -0.050354 | 0.086975 | 0.082397 | 0.050354 | 0.14191 | 123.143 | 123.0148 | 0.1236
12482.7812 | 0.045776 | 0.22751 | -0.22537 | -0.23819 | -0.17944 | -0.26916 | -0.1207 | 0.032043 | -0.032043 | -0.013733 | 0.013733 | 0.13275 | 0.013733 | 0.13275 | 0.076294 | 0.016022 | -0.011749 | -0.4892 | -0.12711 | -0.029907 | -0.064087 | 0.045776 | -0.091553 | 0.073242 | 0.082397 | 0.064087 | 0.13275 | 123.1567 | 122.9645 | 0.10986
12484.5781 | 0.061035 | 0.25421 | -0.21469 | -0.23712 | -0.18158 | -0.26382 | -0.11643 | 0.041199 | -0.050354 | -0.018311 | 0.009155 | 0.14648 | 0.004578 | 0.13733 | 0.076294 | 0.014954 | -0.021362 | -0.47424 | -0.13351 | -0.03952 | -0.064087 | 0.032043 | -0.082397 | 0.07782 | 0.082397 | 0.068665 | 0.10529 | 123.2162 | 122.9507 | 0.091553
12486.375 | 0.061035 | 0.26276 | -0.23071 | -0.2211 | -0.19974 | -0.26596 | -0.11856 | 0.14648 | 0.086975 | 0.1236 | 0.09613 | 0.086975 | -0.054932 | 0.10071 | 0.061035 | -0.001068 | -0.029907 | -0.48492 | -0.11536 | -0.023499 | 0.068665 | 0.13275 | 0.059509 | 0.050354 | 0.036621 | 0.018311 | 0.09613 | 123.1659 | 122.9965 | 0.1236
12488.1094 | 0.076294 | 0.2243 | -0.22003 | -0.23498 | -0.18799 | -0.2446 | -0.11429 | 0.10986 | 0.004578 | 0.032043 | 0.045776 | 0.1236 | -0.013733 | 0.12817 | 0.076294 | 0.018158 | -0.016022 | -0.48279 | -0.11002 | -0.043793 | 0.022888 | 0.086975 | -0.050354 | 0.064087 | 0.07782 | 0.054932 | 0.10071 | 123.2346 | 122.9507 | 0.086975
12489.9219 | 0.030518 | 0.24139 | -0.22003 | -0.25207 | -0.1741 | -0.30441 | -0.12711 | 0.12817 | 0.13275 | 0.16022 | 0.09613 | 0.10071 | -0.027466 | 0.10071 | 0.061035 | -0.004272 | -0.019226 | -0.49027 | -0.1442 | -0.023499 | 0.059509 | 0.17853 | 0.064087 | 0.045776 | 0.045776 | 0.032043 | 0.09613 | 123.1613 | 123.0011 | 0.11444
12491.6562 | 0.076294 | 0.2681 | -0.22858 | -0.24246 | -0.18585 | -0.28198 | -0.13351 | 0.068665 | 0.009155 | 0.082397 | 0.054932 | 0.11444 | -0.027466 | 0.10071 | 0.045776 | 0.006409 | -0.024567 | -0.48706 | -0.13672 | -0.02243 | -0.009155 | 0.09613 | 0.004578 | 0.050354 | 0.050354 | 0.032043 | 0.11444 | 123.1522 | 123.024 | 0.13275
12493.4531 | 0.045776 | 0.24567 | -0.2179 | -0.24353 | -0.18372 | -0.27985 | -0.13031 | 0.073242 | 0.013733 | 0.068665 | 0.054932 | 0.10986 | -0.036621 | 0.11444 | 0.076294 | 0.009613 | -0.025635 | -0.48813 | -0.13886 | -0.03418 | 0.022888 | 0.11902 | 0.013733 | 0.045776 | 0.032043 | 0.041199 | 0.10529 | 123.1888 | 122.9874 | 0.11444
12495.25 | 0.061035 | 0.24674 | -0.2243 | -0.21469 | -0.17624 | -0.25848 | -0.11215 | 0.14191 | 0.091553 | 0.11902 | 0.086975 | 0.09613 | -0.041199 | 0.082397 | 0.061035 | 0.014954 | -0.023499 | -0.48065 | -0.12817 | -0.045929 | 0.059509 | 0.1236 | 0.027466 | 0.036621 | 0.032043 | 0.013733 | 0.10529 | 123.1338 | 123.0286 | 0.11902
12497 | 0.061035 | 0.23712 | -0.2179 | -0.24567 | -0.18265 | -0.23605 | -0.11963 | 0.068665 | -0.09613 | -0.041199 | -0.004578 | 0.11902 | -0.013733 | 0.14648 | 0.045776 | 0.025635 | -0.007477 | -0.47958 | -0.10788 | -0.040588 | -0.032043 | -0.018311 | -0.09613 | 0.091553 | 0.07782 | 0.064087 | 0.11444 | 123.2346 | 122.9828 | 0.091553
12498.7969 | 0.030518 | 0.25635 | -0.24139 | -0.24033 | -0.18692 | -0.29266 | -0.11856 | 0.11444 | 0.086975 | 0.11902 | 0.09613 | 0.11902 | -0.036621 | 0.10529 | 0.045776 | 0.004272 | -0.024567 | -0.48386 | -0.13992 | -0.025635 | 0.091553 | 0.17853 | 0.068665 | 0.041199 | 0.027466 | 0.009155 | 0.09613 | 123.2071 | 122.9874 | 0.10529
12500.5312 | 0.061035 | 0.22751 | -0.2179 | -0.23178 | -0.17517 | -0.2446 | -0.11963 | 0.11444 | 0.036621 | 0.027466 | 0.050354 | 0.12817 | -0.009155 | 0.13275 | 0.045776 | 0.037384 | -0.013885 | -0.48279 | -0.11429 | -0.050201 | 0.018311 | 0.09613 | -0.050354 | 0.059509 | 0.059509 | 0.054932 | 0.11902 | 123.2437 | 122.9416 | 0.07782
12502.3125 | 0.061035 | 0.24887 | -0.23498 | -0.23605 | -0.19226 | -0.28519 | -0.12283 | 0.10986 | 0.13275 | 0.14191 | 0.11444 | 0.091553 | -0.036621 | 0.086975 | 0.045776 | 0.009613 | -0.012817 | -0.49881 | -0.12497 | -0.033112 | 0.054932 | 0.19226 | 0.059509 | 0.050354 | 0.045776 | 0.018311 | 0.082397 | 123.1522 | 122.9965 | 0.09613
12504.1094 | 0.076294 | 0.2713 | -0.22537 | -0.23071 | -0.19012 | -0.26382 | -0.12176 | 0.12817 | 0.086975 | 0.10071 | 0.07782 | 0.091553 | -0.045776 | 0.10529 | 0.061035 | 0.003204 | -0.008545 | -0.47958 | -0.11643 | -0.038452 | 0.068665 | 0.1236 | 0.041199 | 0.045776 | 0.018311 | 0.036621 | 0.091553 | 123.1522 | 123.0011 | 0.11444
12505.8438 | 0.061035 | 0.22644 | -0.21469 | -0.24246 | -0.18265 | -0.25421 | -0.11749 | 0.041199 | -0.009155 | 0 | 0.036621 | 0.13733 | -0.013733 | 0.15106 | 0.076294 | 0.025635 | -0.006409 | -0.48813 | -0.1207 | -0.048065 | -0.027466 | 0.064087 | -0.064087 | 0.086975 | 0.073242 | 0.059509 | 0.11902 | 123.2666 | 122.9599 | 0.086975
12507.6406 | 0.061035 | 0.22003 | -0.23605 | -0.25955 | -0.17944 | -0.26489 | -0.12924 | 0.036621 | -0.027466 | -0.013733 | 0.013733 | 0.15564 | -0.004578 | 0.14648 | 0.061035 | 0.011749 | -0.001068 | -0.48599 | -0.12711 | -0.036316 | -0.068665 | 0.041199 | -0.07782 | 0.082397 | 0.073242 | 0.064087 | 0.14191 | 123.23 | 122.9919 | 0.07782
12509.4375 | 0.061035 | 0.2243 | -0.21683 | -0.23819 | -0.17838 | -0.2446 | -0.10895 | 0.054932 | 0 | 0.022888 | 0.041199 | 0.13733 | -0.022888 | 0.1236 | 0.076294 | 0.021362 | -0.008545 | -0.48492 | -0.11749 | -0.035248 | -0.018311 | 0.082397 | -0.045776 | 0.086975 | 0.059509 | 0.059509 | 0.1236 | 123.2758 | 122.9462 | 0.068665
12511.2344 | 0.061035 | 0.22858 | -0.23285 | -0.23071 | -0.18372 | -0.24994 | -0.10681 | 0.004578 | -0.045776 | -0.018311 | 0.004578 | 0.11902 | -0.004578 | 0.12817 | 0.061035 | 0.016022 | -0.007477 | -0.48492 | -0.1207 | -0.030975 | -0.050354 | -0.013733 | -0.091553 | 0.073242 | 0.064087 | 0.045776 | 0.11902 | 123.2437 | 122.9919 | 0.086975
12512.9688 | 0.076294 | 0.23712 | -0.22964 | -0.24567 | -0.17838 | -0.28519 | -0.12604 | 0.013733 | -0.013733 | 0 | 0.004578 | 0.11444 | -0.013733 | 0.11902 | 0.061035 | 0.03418 | -0.003204 | -0.48386 | -0.13458 | -0.020294 | -0.064087 | 0.050354 | -0.082397 | 0.086975 | 0.091553 | 0.064087 | 0.14648 | 123.175 | 122.9919 | 0.1236
12514.7188 | 0.061035 | 0.24887 | -0.22217 | -0.26382 | -0.18158 | -0.30014 | -0.1239 | 0.041199 | 0.022888 | 0.073242 | 0.041199 | 0.11444 | -0.027466 | 0.1236 | 0.045776 | -0.006409 | -0.002136 | -0.48492 | -0.15167 | -0.029907 | 0 | 0.10986 | 0.013733 | 0.045776 | 0.036621 | 0.004578 | 0.10986 | 123.1934 | 122.9782 | 0.11444
12516.5156 | 0.061035 | 0.24246 | -0.21576 | -0.23071 | -0.18158 | -0.26489 | -0.12497 | 0.12817 | 0.082397 | 0.11444 | 0.09613 | 0.086975 | -0.045776 | 0.09613 | 0.061035 | 0.009613 | -0.016022 | -0.49027 | -0.12176 | -0.032043 | 0.064087 | 0.14648 | 0.050354 | 0.027466 | 0.036621 | 0.022888 | 0.091553 | 123.2346 | 122.9828 | 0.10529
12518.2344 | 0.061035 | 0.24994 | -0.22324 | -0.21149 | -0.17303 | -0.25955 | -0.11963 | 0.054932 | -0.036621 | 0.004578 | 0.009155 | 0.1236 | -0.004578 | 0.1236 | 0.061035 | 0.030975 | -0.019226 | -0.48172 | -0.10895 | -0.042725 | 0.009155 | 0.054932 | -0.027466 | 0.073242 | 0.064087 | 0.045776 | 0.10071 | 123.3032 | 122.9599 | 0.086975
12520.0156 | 0.061035 | 0.22644 | -0.23285 | -0.22644 | -0.19119 | -0.25207 | -0.11536 | 0.054932 | -0.054932 | -0.009155 | 0.022888 | 0.15106 | -0.018311 | 0.12817 | 0.061035 | 0.028839 | -0.01709 | -0.47211 | -0.11429 | -0.03952 | -0.027466 | 0.018311 | -0.054932 | 0.073242 | 0.059509 | 0.054932 | 0.11902 | 123.2895 | 122.9645 | 0.082397
12521.7969 | 0.045776 | 0.22964 | -0.2243 | -0.23178 | -0.17197 | -0.25635 | -0.11108 | 0.054932 | -0.07782 | -0.009155 | 0.013733 | 0.14191 | 0 | 0.13275 | 0.076294 | 0.033112 | 0.001068 | -0.48065 | -0.11322 | -0.043793 | -0.027466 | 0.013733 | -0.07782 | 0.091553 | 0.073242 | 0.064087 | 0.1236 | 123.2758 | 122.9919 | 0.073242
12523.5312 | 0.061035 | 0.2211 | -0.22537 | -0.23285 | -0.19012 | -0.25101 | -0.11536 | 0.082397 | -0.004578 | 0.032043 | 0.050354 | 0.12817 | -0.032043 | 0.14648 | 0.045776 | 0.027771 | -0.003204 | -0.49027 | -0.10574 | -0.042725 | 0 | 0.086975 | -0.036621 | 0.07782 | 0.050354 | 0.050354 | 0.10529 | 123.2803 | 122.9599 | 0.082397
12525.3125 | 0.030518 | 0.24246 | -0.21469 | -0.22003 | -0.17944 | -0.2681 | -0.11536 | 0.036621 | -0.054932 | 0.013733 | 0.036621 | 0.15106 | -0.009155 | 0.11444 | 0.061035 | 0.019226 | -0.001068 | -0.47424 | -0.10361 | -0.025635 | 0.004578 | 0.064087 | -0.032043 | 0.041199 | 0.050354 | 0.027466 | 0.10071 | 123.317 | 122.9599 | 0.07782
12527.1094 | 0.061035 | 0.25955 | -0.22858 | -0.25207 | -0.18372 | -0.29907 | -0.1207 | 0.045776 | 0.022888 | 0.07782 | 0.064087 | 0.10071 | -0.036621 | 0.11902 | 0.061035 | -0.005341 | -0.007477 | -0.49133 | -0.14099 | -0.023499 | -0.004578 | 0.10071 | 0.004578 | 0.045776 | 0.036621 | 0.045776 | 0.09613 | 123.1842 | 123.0011 | 0.12817
12528.9219 | 0.061035 | 0.24567 | -0.2211 | -0.24353 | -0.1709 | -0.29373 | -0.12283 | 0.086975 | 0.050354 | 0.11444 | 0.086975 | 0.09613 | -0.027466 | 0.091553 | 0.061035 | -0.003204 | -0.012817 | -0.48706 | -0.13886 | -0.029907 | 0.059509 | 0.15106 | 0.082397 | 0.050354 | 0.013733 | 0.032043 | 0.082397 | 123.2025 | 122.9782 | 0.11444
12530.6562 | 0.061035 | 0.25314 | -0.23712 | -0.23071 | -0.17303 | -0.27664 | -0.1207 | 0.12817 | 0.091553 | 0.12817 | 0.09613 | 0.082397 | -0.036621 | 0.07782 | 0.045776 | 0.012817 | -0.011749 | -0.4924 | -0.1207 | -0.036316 | 0.073242 | 0.13275 | 0.036621 | 0.050354 | 0.018311 | 0.036621 | 0.09613 | 123.1796 | 122.9919 | 0.10071
12532.4531 | 0.045776 | 0.22217 | -0.23605 | -0.25207 | -0.18158 | -0.26489 | -0.12283 | 0.045776 | -0.045776 | -0.013733 | 0.009155 | 0.15106 | 0.013733 | 0.13733 | 0.045776 | 0.037384 | 0.009613 | -0.47638 | -0.12604 | -0.044861 | -0.059509 | 0.032043 | -0.07782 | 0.086975 | 0.07782 | 0.064087 | 0.12817 | 123.1979 | 122.9736 | 0.11444
12534.2344 | 0.076294 | 0.24994 | -0.2211 | -0.23071 | -0.18478 | -0.27237 | -0.11749 | 0.11902 | 0.07782 | 0.10986 | 0.10071 | 0.09613 | -0.045776 | 0.09613 | 0.030518 | 0.018158 | -0.011749 | -0.4892 | -0.1239 | -0.040588 | 0.068665 | 0.13275 | 0.041199 | 0.036621 | 0.036621 | 0.027466 | 0.082397 | 123.175 | 122.9736 | 0.10986
12536.0312 | 0.076294 | 0.23605 | -0.2243 | -0.24139 | -0.18692 | -0.24353 | -0.10895 | 0.032043 | -0.09613 | -0.041199 | 0.009155 | 0.15564 | 0 | 0.12817 | 0.061035 | 0.028839 | -0.004272 | -0.47852 | -0.11002 | -0.035248 | -0.045776 | 0 | -0.10529 | 0.082397 | 0.082397 | 0.07782 | 0.14191 | 123.2391 | 122.9828 | 0.082397
12537.7656 | 0.061035 | 0.24994 | -0.22964 | -0.22644 | -0.18585 | -0.26703 | -0.11749 | 0.018311 | -0.013733 | -0.004578 | 0.009155 | 0.14648 | 0.013733 | 0.14191 | 0.030518 | 0.021362 | 0.004272 | -0.49774 | -0.12711 | -0.027771 | -0.050354 | 0.036621 | -0.07782 | 0.082397 | 0.073242 | 0.036621 | 0.12817 | 123.23 | 122.9828 | 0.09613
12539.5625 | 0.061035 | 0.23819 | -0.22537 | -0.25848 | -0.17197 | -0.27557 | -0.11749 | 0.032043 | -0.036621 | -0.004578 | 0.022888 | 0.14648 | 0.009155 | 0.14191 | 0.061035 | 0.010681 | 0.005341 | -0.49774 | -0.13351 | -0.035248 | -0.045776 | 0.036621 | -0.082397 | 0.082397 | 0.07782 | 0.068665 | 0.11902 | 123.2483 | 122.9691 | 0.086975
12541.375 | 0.045776 | 0.22964 | -0.21683 | -0.23819 | -0.18051 | -0.25101 | -0.11429 | 0.045776 | -0.027466 | 0 | 0.009155 | 0.12817 | 0.004578 | 0.1236 | 0.076294 | 0.023499 | 0.007477 | -0.47745 | -0.11963 | -0.036316 | 0 | 0.032043 | -0.041199 | 0.073242 | 0.054932 | 0.036621 | 0.11902 | 123.2895 | 122.9828 | 0.082397
12543.1719 | 0.061035 | 0.23178 | -0.23498 | -0.24246 | -0.17197 | -0.28839 | -0.11963 | 0.073242 | 0.07782 | 0.086975 | 0.073242 | 0.11444 | -0.041199 | 0.10529 | 0.061035 | 0.013885 | 0.012817 | -0.49347 | -0.13138 | -0.030975 | -0.022888 | 0.07782 | -0.018311 | 0.07782 | 0.045776 | 0.054932 | 0.10529 | 123.1384 | 123.0011 | 0.1236
12544.9062 | 0.061035 | 0.22324 | -0.2211 | -0.24033 | -0.18372 | -0.25528 | -0.11322 | 0.09613 | 0.018311 | 0.045776 | 0.059509 | 0.14191 | -0.013733 | 0.13733 | 0.091553 | 0.035248 | -0.001068 | -0.4892 | -0.11108 | -0.032043 | 0.004578 | 0.10071 | -0.036621 | 0.073242 | 0.054932 | 0.041199 | 0.11444 | 123.2803 | 123.0011 | 0.091553
12546.7031 | 0.061035 | 0.25207 | -0.22964 | -0.25528 | -0.17303 | -0.28625 | -0.12711 | 0.11444 | 0.10071 | 0.14191 | 0.10529 | 0.07782 | -0.036621 | 0.10071 | 0.061035 | 0.007477 | 0.005341 | -0.49347 | -0.13245 | -0.03418 | 0.045776 | 0.17853 | 0.045776 | 0.041199 | 0.041199 | 0.027466 | 0.091553 | 123.1705 | 122.9919 | 0.11902
12548.4844 | 0.045776 | 0.1976 | -0.21362 | -0.24246 | -0.18372 | -0.25101 | -0.1207 | 0.086975 | 0.013733 | 0.022888 | 0.059509 | 0.11902 | -0.018311 | 0.13275 | 0.061035 | 0.033112 | 0.009613 | -0.48386 | -0.11536 | -0.03952 | 0.004578 | 0.082397 | -0.054932 | 0.07782 | 0.068665 | 0.054932 | 0.11444 | 123.2758 | 122.9736 | 0.064087
12550.2812 | 0.061035 | 0.2446 | -0.22537 | -0.2243 | -0.17303 | -0.26703 | -0.11322 | 0.09613 | 0.050354 | 0.082397 | 0.073242 | 0.10986 | -0.036621 | 0.086975 | 0.030518 | 0.006409 | 0.012817 | -0.48172 | -0.10681 | -0.038452 | 0.045776 | 0.13733 | 0.022888 | 0.045776 | 0.009155 | 0.022888 | 0.10071 | 123.2803 | 122.9462 | 0.07782
12552.0156 | 0.061035 | 0.23071 | -0.22003 | -0.24674 | -0.17303 | -0.27878 | -0.12497 | 0.013733 | -0.027466 | 0.013733 | 0.022888 | 0.14191 | 0 | 0.12817 | 0.061035 | 0 | 0.010681 | -0.4892 | -0.13138 | -0.03418 | -0.068665 | 0.050354 | -0.064087 | 0.082397 | 0.073242 | 0.059509 | 0.1236 | 123.1522 | 123.0057 | 0.12817
12553.8125 | 0.061035 | 0.26703 | -0.23498 | -0.2478 | -0.18158 | -0.2948 | -0.11856 | 0.045776 | 0.045776 | 0.086975 | 0.073242 | 0.11902 | -0.036621 | 0.09613 | 0.076294 | -0.004272 | 0.012817 | -0.49881 | -0.13351 | -0.03418 | 0.013733 | 0.13275 | 0.050354 | 0.059509 | 0.041199 | 0.018311 | 0.086975 | 123.1979 | 122.9919 | 0.1236
12555.6094 | 0.030518 | 0.22217 | -0.21255 | -0.2446 | -0.18158 | -0.24033 | -0.12176 | 0.10986 | 0.009155 | 0.041199 | 0.059509 | 0.13275 | -0.013733 | 0.14191 | 0.061035 | 0.048065 | 0.011749 | -0.47211 | -0.11108 | -0.03952 | 0.018311 | 0.086975 | -0.050354 | 0.059509 | 0.054932 | 0.027466 | 0.11902 | 123.262 | 122.9691 | 0.086975
12557.3438 | 0.061035 | 0.25101 | -0.23071 | -0.2478 | -0.18372 | -0.30334 | -0.11963 | 0.064087 | 0.054932 | 0.10529 | 0.068665 | 0.10986 | -0.032043 | 0.09613 | 0.061035 | 0 | 0.009613 | -0.4892 | -0.14206 | -0.020294 | 0.045776 | 0.15106 | 0.041199 | 0.041199 | 0.041199 | 0.018311 | 0.082397 | 123.1888 | 123.0011 | 0.10529
12559.1562 | 0.030518 | 0.23605 | -0.22964 | -0.23498 | -0.17624 | -0.25207 | -0.11215 | 0.07782 | 0.013733 | 0.045776 | 0.054932 | 0.10986 | -0.013733 | 0.11444 | 0.061035 | 0.027771 | 0.008545 | -0.47958 | -0.10574 | -0.037384 | 0.07782 | 0.086975 | 0.018311 | 0.045776 | 0.036621 | 0.022888 | 0.091553 | 123.3078 | 122.9782 | 0.091553
12560.9688 | 0.061035 | 0.25528 | -0.23392 | -0.23926 | -0.18478 | -0.2948 | -0.12924 | 0.10529 | 0.11444 | 0.13733 | 0.10071 | 0.10986 | -0.050354 | 0.09613 | 0.061035 | 0.011749 | 0.011749 | -0.49133 | -0.13351 | -0.024567 | 0.082397 | 0.17853 | 0.091553 | 0.041199 | 0.032043 | 0.032043 | 0.086975 | 123.1979 | 122.9919 | 0.1236
12562.7656 | 0.076294 | 0.2243 | -0.22537 | -0.24033 | -0.17517 | -0.27237 | -0.13779 | 0.10071 | 0.10529 | 0.11902 | 0.10071 | 0.091553 | -0.041199 | 0.1236 | 0.061035 | 0.018158 | 0.024567 | -0.49133 | -0.12924 | -0.040588 | 0.032043 | 0.16479 | 0.036621 | 0.045776 | 0.036621 | 0.027466 | 0.10529 | 123.143 | 123.0103 | 0.1236
12564.5625 | 0.076294 | 0.25955 | -0.2211 | -0.23605 | -0.17944 | -0.26062 | -0.11429 | 0.13733 | 0.082397 | 0.11444 | 0.086975 | 0.10986 | -0.050354 | 0.086975 | 0.045776 | 0.026703 | 0.016022 | -0.48386 | -0.11856 | -0.036316 | 0.082397 | 0.13275 | 0.036621 | 0.059509 | 0.022888 | 0.013733 | 0.086975 | 123.2529 | 123.0011 | 0.086975
12566.3594 | 0.061035 | 0.24353 | -0.23285 | -0.24353 | -0.1741 | -0.27771 | -0.12711 | 0.11902 | 0.1236 | 0.13733 | 0.086975 | 0.09613 | -0.041199 | 0.10529 | 0.061035 | 0.016022 | 0.008545 | -0.4924 | -0.12817 | -0.037384 | 0.068665 | 0.18768 | 0.059509 | 0.050354 | 0.027466 | 0.018311 | 0.068665 | 123.1705 | 123.0057 | 0.11444
12568.0938 | 0.061035 | 0.23392 | -0.22537 | -0.23178 | -0.18158 | -0.2446 | -0.10361 | 0.054932 | -0.036621 | -0.018311 | 0.022888 | 0.14648 | 0 | 0.12817 | 0.076294 | 0.030975 | 0.01709 | -0.48386 | -0.11643 | -0.036316 | -0.018311 | 0.009155 | -0.082397 | 0.059509 | 0.059509 | 0.059509 | 0.11902 | 123.3032 | 122.9782 | 0.082397
12569.875 | 0.061035 | 0.23392 | -0.23285 | -0.24246 | -0.17731 | -0.2478 | -0.11108 | 0.022888 | -0.059509 | -0.013733 | 0.013733 | 0.14191 | 0 | 0.14191 | 0.045776 | 0.041656 | 0.016022 | -0.48386 | -0.11108 | -0.030975 | -0.027466 | -0.009155 | -0.09613 | 0.082397 | 0.07782 | 0.041199 | 0.11902 | 123.2803 | 122.9919 | 0.059509
12571.6875 | 0.076294 | 0.22537 | -0.21683 | -0.23605 | -0.17944 | -0.24353 | -0.1239 | 0.027466 | -0.032043 | -0.009155 | 0.013733 | 0.13733 | -0.004578 | 0.13733 | 0.061035 | 0.03418 | 0.013885 | -0.48706 | -0.11963 | -0.028839 | -0.068665 | 0.013733 | -0.10986 | 0.082397 | 0.07782 | 0.045776 | 0.12817 | 123.2391 | 122.9691 | 0.073242
12573.4844 | 0.061035 | 0.23178 | -0.23498 | -0.22751 | -0.18478 | -0.27664 | -0.10574 | 0.050354 | -0.004578 | 0.036621 | 0.036621 | 0.11902 | -0.027466 | 0.10529 | 0.061035 | 0.03952 | 0.016022 | -0.48386 | -0.11749 | -0.027771 | 0.022888 | 0.086975 | -0.013733 | 0.054932 | 0.050354 | 0.018311 | 0.082397 | 123.2941 | 122.9553 | 0.082397
12575.2812 | 0.045776 | 0.2681 | -0.23285 | -0.24353 | -0.17944 | -0.28305 | -0.099335 | 0.10071 | 0.10071 | 0.12817 | 0.091553 | 0.086975 | -0.045776 | 0.10071 | 0.030518 | 0.011749 | 0.014954 | -0.49988 | -0.13886 | -0.027771 | 0.036621 | 0.20142 | 0.054932 | 0.050354 | 0.041199 | 0.022888 | 0.09613 | 123.1567 | 123.0148 | 0.12817
12577.0312 | 0.061035 | 0.23071 | -0.21469 | -0.23712 | -0.18265 | -0.24994 | -0.11643 | 0.068665 | -0.027466 | 0.004578 | 0.018311 | 0.13733 | -0.022888 | 0.1236 | 0.061035 | 0.035248 | 0.014954 | -0.47531 | -0.1207 | -0.035248 | 0.018311 | 0.050354 | -0.036621 | 0.07782 | 0.054932 | 0.036621 | 0.091553 | 123.3261 | 122.9645 | 0.07782
12578.8281 | 0.061035 | 0.24139 | -0.23392 | -0.25848 | -0.19226 | -0.30121 | -0.12817 | 0.11902 | 0.11444 | 0.14648 | 0.10529 | 0.10071 | -0.041199 | 0.082397 | 0.076294 | 0.011749 | 0.01709 | -0.49454 | -0.14633 | -0.036316 | 0.073242 | 0.19226 | 0.082397 | 0.041199 | 0.022888 | 0.036621 | 0.082397 | 123.2025 | 123.0103 | 0.10529
12580.625 | 0.076294 | 0.22964 | -0.22858 | -0.24887 | -0.17517 | -0.26596 | -0.12176 | 0.027466 | -0.022888 | -0.009155 | 0.013733 | 0.14191 | 0 | 0.14191 | 0.061035 | 0.02243 | 0.029907 | -0.48492 | -0.12604 | -0.044861 | -0.059509 | 0.032043 | -0.07782 | 0.082397 | 0.082397 | 0.073242 | 0.12817 | 123.1842 | 123.0057 | 0.11902
12582.4062 | 0.061035 | 0.21255 | -0.21683 | -0.24887 | -0.18906 | -0.24994 | -0.11536 | 0.07782 | 0 | 0.027466 | 0.050354 | 0.14191 | -0.013733 | 0.14191 | 0.030518 | 0.029907 | 0.040588 | -0.48065 | -0.1207 | -0.036316 | -0.018311 | 0.091553 | -0.059509 | 0.068665 | 0.059509 | 0.059509 | 0.10529 | 123.2849 | 122.9965 | 0.082397
12584.1719 | 0.061035 | 0.22964 | -0.22537 | -0.23178 | -0.17197 | -0.24246 | -0.11215 | 0.10071 | 0.027466 | 0.018311 | 0.045776 | 0.13275 | -0.022888 | 0.13275 | 0.045776 | 0.03952 | 0.024567 | -0.48386 | -0.10574 | -0.03952 | -0.022888 | 0.054932 | -0.082397 | 0.07782 | 0.064087 | 0.041199 | 0.11902 | 123.2437 | 122.9828 | 0.064087
12585.9844 | 0.076294 | 0.22644 | -0.2211 | -0.23071 | -0.18158 | -0.26062 | -0.11215 | 0.045776 | -0.018311 | -0.009155 | 0.036621 | 0.12817 | 0 | 0.13733 | 0.076294 | 0.029907 | 0.021362 | -0.48386 | -0.11856 | -0.028839 | -0.032043 | 0.064087 | -0.068665 | 0.07782 | 0.082397 | 0.054932 | 0.10529 | 123.2712 | 122.9599 | 0.082397
12587.7344 | 0.076294 | 0.23712 | -0.23071 | -0.23926 | -0.18692 | -0.28198 | -0.13138 | 0.050354 | 0.027466 | 0.054932 | 0.045776 | 0.1236 | -0.018311 | 0.13733 | 0.076294 | 0.023499 | 0.050201 | -0.48172 | -0.12604 | -0.026703 | -0.059509 | 0.068665 | -0.054932 | 0.07782 | 0.064087 | 0.059509 | 0.14648 | 123.1613 | 123.0194 | 0.13733
12589.5312 | 0.045776 | 0.23926 | -0.23285 | -0.25528 | -0.18372 | -0.29159 | -0.12497 | 0.10529 | 0.10071 | 0.13275 | 0.10071 | 0.086975 | -0.032043 | 0.082397 | 0.061035 | 0.009613 | 0.02243 | -0.48706 | -0.13138 | -0.02243 | 0.027466 | 0.17395 | 0.045776 | 0.050354 | 0.041199 | 0.041199 | 0.10071 | 123.1613 | 123.0103 | 0.11902
12591.3281 | 0.045776 | 0.21149 | -0.20615 | -0.25528 | -0.17944 | -0.24139 | -0.11002 | 0.11444 | 0.009155 | 0.045776 | 0.045776 | 0.1236 | -0.018311 | 0.1236 | 0.076294 | 0.040588 | 0.046997 | -0.47958 | -0.1239 | -0.049133 | -0.013733 | 0.054932 | -0.059509 | 0.07782 | 0.054932 | 0.059509 | 0.13275 | 123.2483 | 123.0103 | 0.091553
12593.0625 | 0.061035 | 0.25101 | -0.23285 | -0.23498 | -0.18372 | -0.29266 | -0.12497 | 0.10986 | 0.11902 | 0.13275 | 0.11444 | 0.10986 | -0.036621 | 0.10529 | 0.061035 | 0.009613 | 0.033112 | -0.4892 | -0.13245 | -0.029907 | 0.045776 | 0.19226 | 0.064087 | 0.027466 | 0.036621 | 0.018311 | 0.07782 | 123.1796 | 123.0331 | 0.10986
12594.8594 | 0.076294 | 0.22644 | -0.2179 | -0.22537 | -0.18372 | -0.24246 | -0.11108 | 0.068665 | -0.004578 | 0.013733 | 0.045776 | 0.11902 | -0.027466 | 0.13275 | 0.061035 | 0.043793 | 0.033112 | -0.47745 | -0.10895 | -0.040588 | -0.027466 | 0.036621 | -0.091553 | 0.086975 | 0.054932 | 0.059509 | 0.11444 | 123.2391 | 123.0148 | 0.09613
12596.6562 | 0.061035 | 0.22537 | -0.22217 | -0.24674 | -0.16983 | -0.25207 | -0.098267 | 0.082397 | 0.009155 | 0.036621 | 0.059509 | 0.1236 | -0.022888 | 0.13733 | 0.045776 | 0.028839 | 0.033112 | -0.47958 | -0.10468 | -0.023499 | 0.004578 | 0.10986 | -0.045776 | 0.073242 | 0.064087 | 0.054932 | 0.11444 | 123.2574 | 122.9828 | 0.07782
12598.4531 | 0.045776 | 0.2211 | -0.21896 | -0.23605 | -0.18372 | -0.25314 | -0.11002 | 0.082397 | 0.013733 | 0.045776 | 0.054932 | 0.12817 | -0.009155 | 0.11902 | 0.061035 | 0.053406 | 0.042725 | -0.47958 | -0.10895 | -0.026703 | -0.004578 | 0.082397 | -0.050354 | 0.086975 | 0.068665 | 0.050354 | 0.13733 | 123.2803 | 122.9691 | 0.082397
12600.25 | 0.076294 | 0.23178 | -0.22324 | -0.22217 | -0.17624 | -0.26169 | -0.11963 | 0.032043 | -0.064087 | -0.018311 | 0.018311 | 0.14648 | -0.018311 | 0.13733 | 0.076294 | 0.046997 | 0.03418 | -0.48065 | -0.11322 | -0.020294 | -0.059509 | -0.004578 | -0.086975 | 0.082397 | 0.07782 | 0.041199 | 0.10986 | 123.2849 | 123.0057 | 0.07782
12602 | 0.061035 | 0.24139 | -0.23926 | -0.25528 | -0.18692 | -0.28732 | -0.12497 | 0.064087 | 0.036621 | 0.07782 | 0.059509 | 0.10986 | -0.018311 | 0.10986 | 0.076294 | 0.030975 | 0.045929 | -0.48706 | -0.13886 | -0.025635 | -0.054932 | 0.091553 | -0.050354 | 0.086975 | 0.073242 | 0.050354 | 0.10986 | 123.1567 | 123.0103 | 0.10529
12603.7969 | 0.076294 | 0.22644 | -0.23605 | -0.22964 | -0.17624 | -0.25955 | -0.11536 | 0.073242 | 0 | 0.022888 | 0.050354 | 0.14191 | 0 | 0.15106 | 0.030518 | 0.048065 | 0.036316 | -0.49454 | -0.11856 | -0.035248 | -0.022888 | 0.073242 | -0.050354 | 0.091553 | 0.082397 | 0.054932 | 0.12817 | 123.2849 | 122.9828 | 0.082397
12605.5938 | 0.076294 | 0.23498 | -0.22324 | -0.22858 | -0.18478 | -0.26169 | -0.1239 | 0.041199 | -0.050354 | -0.004578 | 0.009155 | 0.12817 | -0.009155 | 0.13733 | 0.045776 | 0.036316 | 0.043793 | -0.48492 | -0.12604 | -0.029907 | -0.018311 | 0.036621 | -0.050354 | 0.082397 | 0.064087 | 0.041199 | 0.10986 | 123.3078 | 122.9645 | 0.091553
12607.3281 | 0.061035 | 0.22751 | -0.23285 | -0.23498 | -0.16876 | -0.26169 | -0.12711 | 0.050354 | -0.022888 | 0.004578 | 0.045776 | 0.10986 | -0.013733 | 0.13275 | 0.045776 | 0.036316 | 0.052338 | -0.48706 | -0.11749 | -0.033112 | -0.036621 | 0.073242 | -0.050354 | 0.082397 | 0.068665 | 0.045776 | 0.12817 | 123.2986 | 122.9553 | 0.07782
12609.1406 | 0.061035 | 0.23071 | -0.22324 | -0.22537 | -0.18585 | -0.25742 | -0.1004 | 0.07782 | 0 | 0.032043 | 0.045776 | 0.12817 | -0.009155 | 0.11902 | 0.061035 | 0.040588 | 0.050201 | -0.48706 | -0.11002 | -0.042725 | -0.036621 | 0.054932 | -0.07782 | 0.064087 | 0.068665 | 0.041199 | 0.11444 | 123.2666 | 122.9965 | 0.091553
12610.875 | 0.076294 | 0.23071 | -0.23071 | -0.23178 | -0.17624 | -0.25421 | -0.10361 | 0.045776 | -0.032043 | 0 | 0.022888 | 0.1236 | -0.013733 | 0.13275 | 0.045776 | 0.050201 | 0.053406 | -0.47852 | -0.11322 | -0.030975 | -0.064087 | 0.022888 | -0.10071 | 0.082397 | 0.068665 | 0.054932 | 0.13275 | 123.2437 | 123.0011 | 0.09613
12612.6719 | 0.061035 | 0.22858 | -0.22217 | -0.23819 | -0.17838 | -0.25101 | -0.11856 | 0.07782 | 0.032043 | 0.027466 | 0.041199 | 0.1236 | -0.018311 | 0.13275 | 0.045776 | 0.049133 | 0.060883 | -0.49454 | -0.11963 | -0.025635 | -0.018311 | 0.064087 | -0.068665 | 0.068665 | 0.073242 | 0.050354 | 0.10529 | 123.2529 | 122.9828 | 0.091553
12614.4531 | 0.061035 | 0.22537 | -0.22751 | -0.26703 | -0.16983 | -0.28412 | -0.12176 | 0.004578 | -0.054932 | 0 | 0 | 0.13275 | 0.009155 | 0.16022 | 0.061035 | 0.03418 | 0.066223 | -0.48279 | -0.13992 | -0.035248 | -0.086975 | 0.036621 | -0.082397 | 0.09613 | 0.07782 | 0.059509 | 0.12817 | 123.1934 | 123.0103 | 0.10071
12616.1875 | 0.076294 | 0.24246 | -0.21255 | -0.23071 | -0.18051 | -0.25955 | -0.11643 | 0.10071 | 0.041199 | 0.091553 | 0.086975 | 0.091553 | -0.041199 | 0.091553 | 0.076294 | 0.03952 | 0.050201 | -0.47958 | -0.11536 | -0.028839 | 0.041199 | 0.1236 | 0.022888 | 0.045776 | 0.027466 | 0.018311 | 0.082397 | 123.2895 | 123.0103 | 0.082397
12618 | 0.061035 | 0.23712 | -0.21896 | -0.23392 | -0.18372 | -0.2446 | -0.11856 | 0.07782 | -0.004578 | 0.027466 | 0.064087 | 0.1236 | -0.018311 | 0.13733 | 0.061035 | 0.048065 | 0.060883 | -0.4892 | -0.12176 | -0.042725 | -0.022888 | 0.086975 | -0.050354 | 0.082397 | 0.073242 | 0.045776 | 0.10071 | 123.2849 | 122.9782 | 0.091553
12619.7969 | 0.061035 | 0.25314 | -0.23071 | -0.23498 | -0.18585 | -0.30975 | -0.14313 | 0.050354 | 0.013733 | 0.086975 | 0.054932 | 0.10986 | -0.050354 | 0.10071 | 0.061035 | 0.020294 | 0.057678 | -0.49347 | -0.14526 | -0.021362 | 0 | 0.10986 | 0.032043 | 0.068665 | 0.045776 | 0.032043 | 0.082397 | 123.2025 | 123.0331 | 0.13275
12621.5312 | 0.091553 | 0.27878 | -0.22858 | -0.23605 | -0.17731 | -0.30014 | -0.13672 | 0.07782 | 0.054932 | 0.10071 | 0.073242 | 0.10071 | -0.054932 | 0.10986 | 0.061035 | 0.033112 | 0.055542 | -0.49133 | -0.14526 | -0.03418 | 0.045776 | 0.15106 | 0.068665 | 0.050354 | 0.036621 | 0.036621 | 0.086975 | 123.2025 | 123.0057 | 0.10986
12623.3125 | 0.061035 | 0.2446 | -0.22964 | -0.24567 | -0.17731 | -0.27878 | -0.12817 | 0.10071 | 0.064087 | 0.10071 | 0.082397 | 0.10529 | -0.045776 | 0.10071 | 0.076294 | 0.030975 | 0.058746 | -0.49454 | -0.13565 | -0.035248 | 0.013733 | 0.11444 | 0.004578 | 0.045776 | 0.041199 | 0.041199 | 0.10986 | 123.1522 | 123.0103 | 0.11444
12625.1094 | 0.030518 | 0.25848 | -0.2243 | -0.2243 | -0.18585 | -0.27451 | -0.12176 | 0.11444 | 0.045776 | 0.10071 | 0.064087 | 0.10071 | -0.036621 | 0.10071 | 0.045776 | 0.030975 | 0.059814 | -0.48279 | -0.13245 | -0.019226 | 0.027466 | 0.091553 | 0.009155 | 0.050354 | 0.041199 | 0.013733 | 0.09613 | 123.1476 | 123.0469 | 0.11902
12626.9062 | 0.045776 | 0.26489 | -0.23605 | -0.23605 | -0.16449 | -0.28198 | -0.12283 | 0.1236 | 0.050354 | 0.10071 | 0.054932 | 0.10986 | -0.036621 | 0.10071 | 0.076294 | 0.037384 | 0.063019 | -0.48813 | -0.12283 | -0.032043 | 0.045776 | 0.091553 | 0 | 0.050354 | 0.041199 | 0.013733 | 0.07782 | 123.1613 | 123.0286 | 0.12817
12628.7188 | 0.030518 | 0.2478 | -0.23819 | -0.24246 | -0.19012 | -0.27664 | -0.12497 | 0.082397 | 0.018311 | 0.073242 | 0.054932 | 0.10529 | -0.041199 | 0.10529 | 0.061035 | 0.043793 | 0.082245 | -0.49667 | -0.13565 | -0.030975 | 0.004578 | 0.086975 | 0.013733 | 0.064087 | 0.054932 | 0.041199 | 0.091553 | 123.1842 | 123.0377 | 0.11902
12630.5156 | 0.076294 | 0.2243 | -0.23712 | -0.24033 | -0.18692 | -0.23605 | -0.11749 | 0.059509 | -0.036621 | 0.004578 | 0.022888 | 0.1236 | 0.009155 | 0.15106 | 0.045776 | 0.067291 | 0.074768 | -0.4892 | -0.11749 | -0.036316 | -0.018311 | 0.059509 | -0.07782 | 0.086975 | 0.073242 | 0.041199 | 0.13733 | 123.2941 | 122.9599 | 0.086975
12632.3125 | 0.061035 | 0.23178 | -0.23926 | -0.24139 | -0.17731 | -0.26169 | -0.12176 | 0.059509 | 0 | 0.032043 | 0.032043 | 0.1236 | -0.022888 | 0.14648 | 0.061035 | 0.05127 | 0.088654 | -0.49133 | -0.12817 | -0.026703 | -0.036621 | 0.050354 | -0.086975 | 0.09613 | 0.07782 | 0.050354 | 0.11902 | 123.1659 | 123.0423 | 0.12817
12634.0312 | 0.061035 | 0.22003 | -0.23178 | -0.23498 | -0.18372 | -0.2446 | -0.11856 | 0.054932 | -0.013733 | 0.009155 | 0.041199 | 0.13275 | -0.009155 | 0.13275 | 0.061035 | 0.054474 | 0.085449 | -0.48279 | -0.11215 | -0.044861 | -0.004578 | 0.07782 | -0.041199 | 0.07782 | 0.068665 | 0.045776 | 0.11444 | 123.2803 | 122.9736 | 0.068665
12635.8125 | 0.045776 | 0.24033 | -0.2243 | -0.25207 | -0.1709 | -0.27451 | -0.11429 | 0.059509 | 0.018311 | 0.059509 | 0.050354 | 0.1236 | -0.018311 | 0.11444 | 0.061035 | 0.043793 | 0.082245 | -0.48706 | -0.12604 | -0.024567 | -0.045776 | 0.068665 | -0.059509 | 0.073242 | 0.082397 | 0.054932 | 0.12817 | 123.1613 | 123.024 | 0.11902
12637.5469 | 0.045776 | 0.20187 | -0.21683 | -0.25421 | -0.17838 | -0.24246 | -0.10254 | 0.054932 | -0.059509 | -0.009155 | 0.022888 | 0.12817 | -0.004578 | 0.11902 | 0.030518 | 0.060883 | 0.097198 | -0.47531 | -0.11749 | -0.030975 | -0.064087 | -0.004578 | -0.10986 | 0.09613 | 0.054932 | 0.045776 | 0.12817 | 123.2437 | 123.024 | 0.09613
12639.3438 | 0.076294 | 0.23498 | -0.20187 | -0.23285 | -0.16876 | -0.25635 | -0.10254 | 0.11444 | 0.032043 | 0.045776 | 0.045776 | 0.11444 | -0.013733 | 0.14648 | 0.061035 | 0.068359 | 0.089722 | -0.48279 | -0.10574 | -0.026703 | 0 | 0.09613 | -0.064087 | 0.073242 | 0.059509 | 0.032043 | 0.10986 | 123.2574 | 122.9828 | 0.086975
12641.0781 | 0.045776 | 0.24674 | -0.22324 | -0.22751 | -0.18478 | -0.27878 | -0.10574 | 0.12817 | 0.082397 | 0.11902 | 0.086975 | 0.082397 | -0.045776 | 0.086975 | 0.076294 | 0.048065 | 0.087585 | -0.48492 | -0.11215 | -0.028839 | 0.073242 | 0.14191 | 0.045776 | 0.022888 | 0.027466 | 0.004578 | 0.086975 | 123.2666 | 123.0103 | 0.091553
12642.8594 | 0.045776 | 0.24246 | -0.22537 | -0.24139 | -0.18478 | -0.29694 | -0.10895 | 0.13275 | 0.1236 | 0.15564 | 0.11444 | 0.082397 | -0.027466 | 0.10529 | 0.045776 | -0.03952 | -0.14313 | -0.47745 | -0.14099 | -0.025635 | 0.045776 | 0.18768 | 0.082397 | 0.018311 | 0.022888 | 0.041199 | 0.09613 | 0.2243 | 0.13275 | 0.073242
12644.6562 | 0.061035 | 0.24567 | -0.23178 | -0.23392 | -0.18372 | -0.26596 | -0.11963 | 0.082397 | -0.018311 | 0.045776 | 0.041199 | 0.13733 | -0.032043 | 0.13275 | 0.061035 | -0.020294 | -0.14954 | -0.48706 | -0.11215 | -0.03952 | 0.036621 | 0.10986 | -0.004578 | 0.041199 | 0.045776 | 0.032043 | 0.091553 | 0.3479 | 0.28839 | 0.050354
12646.4531 | 0.030518 | 0.25101 | -0.23498 | -0.24139 | -0.18478 | -0.30121 | -0.12176 | 0.1236 | 0.10529 | 0.12817 | 0.091553 | 0.082397 | -0.050354 | 0.11444 | 0.061035 | -0.042725 | -0.1442 | -0.49561 | -0.12497 | -0.03952 | 0.050354 | 0.18768 | 0.059509 | 0.036621 | 0.041199 | 0.036621 | 0.10071 | 0.2243 | 0.20142 | 0.10071
12648.2031 | 0.061035 | 0.2446 | -0.23712 | -0.24994 | -0.17624 | -0.28412 | -0.12497 | 0.13275 | 0.11444 | 0.16022 | 0.10529 | 0.10071 | -0.032043 | 0.10529 | 0.061035 | -0.053406 | -0.14206 | -0.47104 | -0.13458 | -0.03952 | 0.064087 | 0.19226 | 0.07782 | 0.022888 | 0.022888 | 0.036621 | 0.082397 | 0.21973 | 0.27008 | 0.073242
12649.9531 | 0.061035 | 0.23926 | -0.22537 | -0.22644 | -0.18158 | -0.24994 | -0.10788 | 0.10071 | -0.013733 | 0.041199 | 0.041199 | 0.11902 | -0.032043 | 0.11444 | 0.030518 | -0.021362 | -0.13351 | -0.47958 | -0.11108 | -0.041656 | 0.045776 | 0.10071 | 0.004578 | 0.041199 | 0.032043 | 0.027466 | 0.09613 | 0.30212 | 0.22888 | 0.041199
12651.75 | 0.061035 | 0.23819 | -0.22858 | -0.23498 | -0.18051 | -0.25742 | -0.11215 | 0.11444 | 0.050354 | 0.086975 | 0.07782 | 0.09613 | -0.050354 | 0.10071 | 0.061035 | -0.025635 | -0.13672 | -0.47318 | -0.12283 | -0.045929 | 0.073242 | 0.11902 | 0.009155 | 0.041199 | 0.022888 | 0.013733 | 0.086975 | 0.30212 | 0.21973 | 0.054932
12653.4844 | 0.061035 | 0.22324 | -0.21683 | -0.24353 | -0.17731 | -0.24033 | -0.11322 | 0.10071 | 0.022888 | 0.045776 | 0.045776 | 0.11902 | -0.022888 | 0.1236 | 0.076294 | -0.016022 | -0.13031 | -0.47424 | -0.11856 | -0.05127 | 0.009155 | 0.091553 | -0.050354 | 0.068665 | 0.041199 | 0.036621 | 0.1236 | 0.28839 | 0.21515 | 0.054932
12655.2656 | 0.076294 | 0.21149 | -0.2179 | -0.25528 | -0.18158 | -0.25314 | -0.10361 | 0.054932 | -0.009155 | 0.022888 | 0.054932 | 0.11902 | -0.013733 | 0.1236 | 0.061035 | -0.030975 | -0.12176 | -0.47852 | -0.11749 | -0.050201 | -0.022888 | 0.07782 | -0.054932 | 0.064087 | 0.054932 | 0.059509 | 0.13733 | 0.29755 | 0.20142 | 0.050354
12657.0156 | 0.076294 | 0.22324 | -0.22964 | -0.23285 | -0.18158 | -0.26169 | -0.098267 | 0.036621 | -0.059509 | -0.022888 | 0.013733 | 0.13275 | 0 | 0.12817 | 0.061035 | -0.026703 | -0.12924 | -0.47318 | -0.11215 | -0.036316 | -0.032043 | 0.004578 | -0.073242 | 0.068665 | 0.054932 | 0.064087 | 0.13275 | 0.27924 | 0.20142 | 0.050354
12658.8281 | 0.045776 | 0.24567 | -0.23285 | -0.24567 | -0.16342 | -0.28091 | -0.11108 | 0.013733 | -0.027466 | 0.018311 | 0.013733 | 0.11444 | 0 | 0.13733 | 0.045776 | -0.030975 | -0.14954 | -0.46783 | -0.13565 | -0.03418 | -0.054932 | 0.064087 | -0.068665 | 0.07782 | 0.07782 | 0.068665 | 0.12817 | 0.17395 | 0.22888 | 0.064087
12660.5625 | 0.061035 | 0.23498 | -0.22964 | -0.23712 | -0.17944 | -0.26382 | -0.10361 | 0.10529 | 0.027466 | 0.036621 | 0.032043 | 0.12817 | 0 | 0.1236 | 0.030518 | -0.018158 | -0.14206 | -0.48706 | -0.11322 | -0.033112 | -0.013733 | 0.091553 | -0.050354 | 0.045776 | 0.054932 | 0.045776 | 0.10986 | 0.2655 | 0.20599 | 0.032043
12662.3594 | 0.045776 | 0.2446 | -0.23071 | -0.24567 | -0.18158 | -0.2948 | -0.11108 | 0.082397 | 0.09613 | 0.11444 | 0.10071 | 0.091553 | -0.045776 | 0.09613 | 0.045776 | -0.043793 | -0.13031 | -0.49027 | -0.13245 | -0.032043 | 0.009155 | 0.16479 | 0.036621 | 0.050354 | 0.022888 | 0.041199 | 0.10986 | 0.13733 | 0.23804 | 0.07782
12664.1094 | 0.061035 | 0.25742 | -0.22858 | -0.22537 | -0.17838 | -0.28519 | -0.12176 | 0.064087 | 0.027466 | 0.07782 | 0.050354 | 0.10529 | -0.036621 | 0.10071 | 0.061035 | -0.048065 | -0.1442 | -0.48172 | -0.12924 | -0.032043 | 0.009155 | 0.09613 | 0.018311 | 0.050354 | 0.045776 | 0.045776 | 0.10986 | 0.14648 | 0.21973 | 0.068665
12665.9062 | 0.061035 | 0.25207 | -0.24033 | -0.22751 | -0.18585 | -0.27771 | -0.11643 | 0.086975 | 0.018311 | 0.07782 | 0.050354 | 0.091553 | -0.022888 | 0.10529 | 0.076294 | -0.036316 | -0.14633 | -0.49561 | -0.12924 | -0.042725 | 0.018311 | 0.11444 | 0.027466 | 0.045776 | 0.045776 | 0.036621 | 0.10071 | 0.19684 | 0.20599 | 0.054932
12667.7188 | 0.061035 | 0.22858 | -0.21896 | -0.22964 | -0.16663 | -0.24887 | -0.11963 | 0.054932 | -0.068665 | -0.022888 | 0.018311 | 0.11902 | -0.004578 | 0.13733 | 0.091553 | -0.018158 | -0.12283 | -0.47745 | -0.10788 | -0.03952 | -0.036621 | 0.009155 | -0.09613 | 0.091553 | 0.050354 | 0.059509 | 0.10986 | 0.2655 | 0.18768 | 0.045776
12669.5156 | 0.091553 | 0.26382 | -0.2478 | -0.23285 | -0.1709 | -0.28519 | -0.11215 | 0.054932 | 0.027466 | 0.082397 | 0.050354 | 0.091553 | -0.013733 | 0.10529 | 0.076294 | -0.050201 | -0.13992 | -0.4892 | -0.13138 | -0.03418 | -0.013733 | 0.082397 | 0.013733 | 0.059509 | 0.027466 | 0.032043 | 0.10071 | 0.16022 | 0.20142 | 0.07782
12671.3125 | 0.061035 | 0.23712 | -0.21255 | -0.22217 | -0.18799 | -0.25421 | -0.11856 | 0.10071 | 0.036621 | 0.064087 | 0.041199 | 0.086975 | -0.041199 | 0.10071 | 0.045776 | -0.019226 | -0.14847 | -0.49561 | -0.10681 | -0.046997 | 0.068665 | 0.10529 | 0.004578 | 0.041199 | 0.013733 | 0.018311 | 0.09613 | 0.28381 | 0.18768 | 0.050354
12673.1094 | 0.061035 | 0.24887 | -0.23819 | -0.25742 | -0.18478 | -0.29053 | -0.12176 | 0.11444 | 0.09613 | 0.1236 | 0.07782 | 0.09613 | -0.045776 | 0.09613 | 0.061035 | -0.046997 | -0.13886 | -0.49881 | -0.14313 | -0.040588 | 0.073242 | 0.17395 | 0.064087 | 0.027466 | 0.013733 | 0.036621 | 0.07782 | 0.19684 | 0.19684 | 0.059509
12674.8594 | 0.061035 | 0.24033 | -0.22751 | -0.23285 | -0.18906 | -0.2478 | -0.11322 | 0.054932 | -0.045776 | -0.009155 | 0.009155 | 0.12817 | -0.013733 | 0.12817 | 0.061035 | -0.018158 | -0.14206 | -0.47852 | -0.11108 | -0.042725 | -0.036621 | 0.013733 | -0.09613 | 0.082397 | 0.045776 | 0.045776 | 0.1236 | 0.29297 | 0.1831 | 0.032043
12676.6562 | 0.061035 | 0.24567 | -0.22751 | -0.23178 | -0.18265 | -0.24139 | -0.10361 | 0.050354 | -0.022888 | 0.018311 | 0.004578 | 0.12817 | -0.018311 | 0.12817 | 0.045776 | -0.027771 | -0.13138 | -0.47852 | -0.11856 | -0.041656 | 0.004578 | 0.050354 | -0.027466 | 0.064087 | 0.041199 | 0.027466 | 0.09613 | 0.27924 | 0.17395 | 0.045776
12678.4531 | 0.076294 | 0.26276 | -0.23392 | -0.24033 | -0.1976 | -0.30548 | -0.11002 | 0.07782 | 0.045776 | 0.09613 | 0.064087 | 0.10071 | -0.045776 | 0.11444 | 0.061035 | -0.042725 | -0.1474 | -0.48492 | -0.13992 | -0.044861 | 0.041199 | 0.14648 | 0.073242 | 0.032043 | 0.004578 | 0.013733 | 0.09613 | 0.19226 | 0.20142 | 0.059509
12680.1875 | 0.091553 | 0.23392 | -0.22537 | -0.23819 | -0.17624 | -0.25314 | -0.1207 | 0.036621 | -0.027466 | -0.004578 | 0.018311 | 0.1236 | 0.004578 | 0.13733 | 0.061035 | -0.025635 | -0.1442 | -0.47852 | -0.11749 | -0.03952 | -0.059509 | 0.059509 | -0.082397 | 0.073242 | 0.045776 | 0.064087 | 0.12817 | 0.27924 | 0.17395 | 0.036621
12682 | 0.030518 | 0.22324 | -0.22324 | -0.22858 | -0.17197 | -0.23926 | -0.11643 | 0.086975 | 0 | 0.018311 | 0.050354 | 0.13275 | -0.004578 | 0.15106 | 0.045776 | -0.018158 | -0.14099 | -0.47531 | -0.10788 | -0.046997 | -0.009155 | 0.082397 | -0.064087 | 0.054932 | 0.059509 | 0.050354 | 0.13275 | 0.28381 | 0.16937 | 0.022888
12683.8125 | 0.061035 | 0.2211 | -0.22537 | -0.23712 | -0.16342 | -0.25207 | -0.11643 | 0.07782 | -0.013733 | 0.022888 | 0.045776 | 0.13275 | -0.004578 | 0.12817 | 0.061035 | -0.004272 | -0.13779 | -0.47958 | -0.11856 | -0.041656 | -0.013733 | 0.073242 | -0.050354 | 0.064087 | 0.050354 | 0.041199 | 0.11902 | 0.28381 | 0.19226 | 0.036621
12685.5938 | 0.015259 | 0.2713 | -0.10895 | -0.2243 | -0.1709 | -0.31403 | -0.12176 | 0.059509 | 0.068665 | 0.09613 | 0.073242 | 0.10986 | -0.027466 | 0.10529 | 0.076294 | -0.048065 | -0.14526 | -0.49027 | -0.13138 | -0.03418 | 0.050354 | 0.15106 | 0.059509 | 0.041199 | 0.027466 | 0.018311 | 0.082397 | 0.17853 | 0.20599 | 0.064087
12687.4062 | 0.045776 | 0.23392 | -0.2211 | -0.24033 | -0.18372 | -0.24674 | -0.11322 | 0.054932 | -0.045776 | -0.009155 | 0.009155 | 0.14191 | -0.004578 | 0.13275 | 0.045776 | -0.032043 | -0.1442 | -0.47424 | -0.10788 | -0.033112 | -0.018311 | 0.022888 | -0.068665 | 0.073242 | 0.036621 | 0.054932 | 0.11444 | 0.27008 | 0.17853 | 0.032043
12689.2188 | 0.045776 | 0.23498 | -0.22217 | -0.24246 | -0.18158 | -0.26596 | -0.11536 | 0.022888 | -0.050354 | -0.004578 | 0.009155 | 0.13275 | -0.009155 | 0.15106 | 0.045776 | -0.023499 | -0.13779 | -0.48065 | -0.13351 | -0.03952 | -0.068665 | 0.050354 | -0.086975 | 0.059509 | 0.073242 | 0.054932 | 0.13733 | 0.25177 | 0.18768 | 0.045776
12690.9531 | 0.061035 | 0.25955 | -0.22964 | -0.23712 | -0.18265 | -0.29373 | -0.11429 | 0.10529 | 0.10071 | 0.1236 | 0.082397 | 0.073242 | -0.045776 | 0.091553 | 0.030518 | -0.042725 | -0.1442 | -0.4892 | -0.1442 | -0.036316 | 0.073242 | 0.1831 | 0.073242 | 0.041199 | 0.054932 | 0.013733 | 0.09613 | 0.19226 | 0.18768 | 0.045776
12692.75 | 0.045776 | 0.2211 | -0.23071 | -0.24033 | -0.17731 | -0.25101 | -0.11643 | 0.11902 | 0.018311 | 0.027466 | 0.045776 | 0.13733 | 0 | 0.11444 | 0.061035 | -0.019226 | -0.13245 | -0.47958 | -0.11002 | -0.049133 | -0.018311 | 0.054932 | -0.068665 | 0.068665 | 0.036621 | 0.050354 | 0.10529 | 0.24719 | 0.19684 | 0.027466
12694.5625 | 0.045776 | 0.24139 | -0.22644 | -0.24353 | -0.17838 | -0.28305 | -0.1207 | 0.07782 | 0.041199 | 0.09613 | 0.064087 | 0.10071 | -0.045776 | 0.11444 | 0.061035 | -0.042725 | -0.14954 | -0.49027 | -0.13245 | -0.032043 | 0.032043 | 0.09613 | 0 | 0.027466 | 0.032043 | 0.032043 | 0.091553 | 0.13275 | 0.21057 | 0.07782
12696.375 | 0.045776 | 0.24994 | -0.22537 | -0.23498 | -0.17197 | -0.26382 | -0.11749 | 0.1236 | 0.091553 | 0.13275 | 0.09613 | 0.091553 | -0.045776 | 0.082397 | 0.061035 | -0.030975 | -0.1442 | -0.48172 | -0.11536 | -0.032043 | 0.068665 | 0.14191 | 0.036621 | 0.027466 | 0.027466 | 0.027466 | 0.091553 | 0.21057 | 0.1831 | 0.045776
12698.1094 | 0.061035 | 0.24139 | -0.24139 | -0.24139 | -0.17517 | -0.28412 | -0.11963 | 0.11444 | 0.10986 | 0.13275 | 0.091553 | 0.10071 | -0.036621 | 0.10529 | 0.061035 | -0.045929 | -0.15167 | -0.48813 | -0.13031 | -0.033112 | 0.050354 | 0.1831 | 0.059509 | 0.022888 | 0.013733 | 0.013733 | 0.11444 | 0.15106 | 0.19684 | 0.050354
12699.9219 | 0.030518 | 0.23392 | -0.2179 | -0.23605 | -0.16769 | -0.23712 | -0.10468 | 0.064087 | -0.022888 | 0 | 0.009155 | 0.11902 | 0.009155 | 0.14191 | 0.061035 | -0.005341 | -0.1474 | -0.46783 | -0.10895 | -0.040588 | -0.050354 | 0 | -0.11902 | 0.068665 | 0.045776 | 0.064087 | 0.14191 | 0.21973 | 0.18768 | 0.041199
12701.7188 | 0.061035 | 0.26169 | -0.23178 | -0.24139 | -0.18585 | -0.28412 | -0.11856 | 0.059509 | 0.018311 | 0.086975 | 0.041199 | 0.10529 | -0.041199 | 0.10986 | 0.045776 | -0.050201 | -0.14633 | -0.48065 | -0.14099 | -0.035248 | 0.013733 | 0.082397 | 0.009155 | 0.041199 | 0.041199 | 0.013733 | 0.086975 | 0.14648 | 0.19226 | 0.082397
12703.5156 | 0.061035 | 0.24994 | -0.2446 | -0.24887 | -0.17303 | -0.27771 | -0.12817 | 0.12817 | 0.091553 | 0.11902 | 0.091553 | 0.10529 | -0.036621 | 0.10986 | 0.045776 | -0.036316 | -0.14847 | -0.49027 | -0.13351 | -0.033112 | 0.068665 | 0.17853 | 0.07782 | 0.032043 | 0.018311 | 0.032043 | 0.10071 | 0.17853 | 0.19226 | 0.054932
12705.25 | 0.061035 | 0.23819 | -0.2211 | -0.2243 | -0.18692 | -0.23819 | -0.11215 | 0.12817 | 0.018311 | 0.045776 | 0.050354 | 0.1236 | -0.009155 | 0.1236 | 0.076294 | -0.003204 | -0.13992 | -0.46997 | -0.10681 | -0.046997 | 0.027466 | 0.07782 | -0.059509 | 0.059509 | 0.054932 | 0.045776 | 0.10986 | 0.26093 | 0.17853 | 0.027466
12707.0625 | 0.061035 | 0.23071 | -0.22964 | -0.2446 | -0.17624 | -0.28519 | -0.11749 | 0.07782 | 0.013733 | 0.036621 | 0.041199 | 0.13275 | -0.009155 | 0.1236 | 0.045776 | -0.035248 | -0.13886 | -0.47638 | -0.13565 | -0.037384 | -0.045776 | 0.068665 | -0.059509 | 0.064087 | 0.050354 | 0.054932 | 0.12817 | 0.13275 | 0.20142 | 0.073242
12708.8125 | 0.061035 | 0.26489 | -0.22751 | -0.25635 | -0.17303 | -0.28412 | -0.12924 | 0.10529 | 0.10071 | 0.13733 | 0.10071 | 0.073242 | -0.032043 | 0.10529 | 0.061035 | -0.042725 | -0.13672 | -0.48172 | -0.12711 | -0.03418 | 0.064087 | 0.17853 | 0.059509 | 0.032043 | 0.032043 | 0.032043 | 0.091553 | 0.16479 | 0.20142 | 0.050354
12710.6094 | 0.061035 | 0.24674 | -0.22751 | -0.2243 | -0.18692 | -0.28839 | -0.12176 | 0.10529 | 0.082397 | 0.11902 | 0.082397 | 0.091553 | -0.050354 | 0.073242 | 0.045776 | -0.036316 | -0.14847 | -0.48386 | -0.13458 | -0.032043 | 0.082397 | 0.17853 | 0.082397 | 0.009155 | 0.022888 | 0.036621 | 0.082397 | 0.16937 | 0.19226 | 0.068665
12712.4219 | 0.061035 | 0.24139 | -0.23498 | -0.23926 | -0.16129 | -0.27985 | -0.1239 | 0.054932 | 0.022888 | 0.073242 | 0.059509 | 0.10529 | -0.050354 | 0.10071 | 0.061035 | -0.040588 | -0.14633 | -0.49347 | -0.12604 | -0.033112 | -0.004578 | 0.091553 | 0.004578 | 0.032043 | 0.009155 | 0.032043 | 0.086975 | 0.13275 | 0.19684 | 0.073242
12714.25 | 0.045776 | 0.25207 | -0.23285 | -0.24994 | -0.18585 | -0.27557 | -0.12924 | 0.14191 | 0.12817 | 0.14191 | 0.10986 | 0.091553 | -0.022888 | 0.082397 | 0.045776 | -0.038452 | -0.14847 | -0.48172 | -0.13245 | -0.048065 | 0.073242 | 0.19226 | 0.059509 | 0.036621 | 0.004578 | 0.009155 | 0.086975 | 0.16479 | 0.16479 | 0.054932
12715.9844 | 0.076294 | 0.23926 | -0.21255 | -0.23071 | -0.1741 | -0.23285 | -0.10681 | 0.1236 | 0.032043 | 0.032043 | 0.045776 | 0.11444 | -0.013733 | 0.13275 | 0.045776 | -0.004272 | -0.14526 | -0.47531 | -0.11108 | -0.052338 | -0.004578 | 0.041199 | -0.068665 | 0.054932 | 0.032043 | 0.054932 | 0.12817 | 0.2243 | 0.17395 | 0.036621
12717.7812 | 0.076294 | 0.22537 | -0.2179 | -0.22964 | -0.17303 | -0.24994 | -0.1004 | 0.027466 | -0.036621 | -0.018311 | 0.027466 | 0.1236 | -0.009155 | 0.13275 | 0.030518 | -0.01709 | -0.13886 | -0.46783 | -0.10361 | -0.037384 | -0.050354 | 0.013733 | -0.11444 | 0.059509 | 0.041199 | 0.064087 | 0.13275 | 0.21057 | 0.1831 | 0.041199
12719.5938 | 0.076294 | 0.23712 | -0.22858 | -0.23498 | -0.16235 | -0.27771 | -0.11215 | 0.054932 | 0.068665 | 0.059509 | 0.054932 | 0.11444 | -0.013733 | 0.1236 | 0.061035 | -0.020294 | -0.13458 | -0.48279 | -0.1239 | -0.040588 | -0.036621 | 0.09613 | -0.054932 | 0.059509 | 0.041199 | 0.045776 | 0.11444 | 0.10986 | 0.19684 | 0.045776
12721.3906 | 0.045776 | 0.2446 | -0.2211 | -0.2179 | -0.18265 | -0.2681 | -0.10788 | 0.13275 | 0.10529 | 0.1236 | 0.10071 | 0.082397 | -0.050354 | 0.091553 | 0.030518 | -0.021362 | -0.15381 | -0.49454 | -0.11749 | -0.030975 | 0.082397 | 0.14648 | 0.036621 | 0.018311 | 0.022888 | 0.022888 | 0.09613 | 0.21515 | 0.17395 | 0.045776
12723.125 | 0.061035 | 0.24674 | -0.24246 | -0.24674 | -0.16983 | -0.2948 | -0.11536 | 0.11902 | 0.11444 | 0.13733 | 0.091553 | 0.086975 | -0.041199 | 0.09613 | 0.045776 | -0.030975 | -0.13886 | -0.4892 | -0.13245 | -0.040588 | 0.082397 | 0.19684 | 0.073242 | 0.022888 | 0.013733 | 0.022888 | 0.091553 | 0.16937 | 0.17853 | 0.045776
12724.9375 | 0.045776 | 0.23819 | -0.22644 | -0.23285 | -0.18372 | -0.24887 | -0.10254 | 0.064087 | -0.041199 | -0.004578 | 0 | 0.12817 | -0.004578 | 0.1236 | 0.061035 | -0.016022 | -0.14526 | -0.48706 | -0.10788 | -0.036316 | 0 | 0.013733 | -0.050354 | 0.068665 | 0.050354 | 0.064087 | 0.11444 | 0.27008 | 0.15106 | 0.027466
12726.6719 | 0.045776 | 0.24139 | -0.2243 | -0.25314 | -0.18692 | -0.26703 | -0.11429 | 0.027466 | -0.027466 | -0.004578 | 0.009155 | 0.13275 | 0.004578 | 0.14648 | 0.045776 | -0.011749 | -0.12711 | -0.47638 | -0.11856 | -0.024567 | -0.068665 | 0.054932 | -0.091553 | 0.091553 | 0.068665 | 0.054932 | 0.1236 | 0.16937 | 0.18768 | 0.054932
12728.4531 | 0.076294 | 0.23285 | -0.21149 | -0.22644 | -0.17731 | -0.24139 | -0.10788 | 0.032043 | -0.068665 | -0.018311 | 0.013733 | 0.12817 | 0 | 0.13733 | 0.061035 | -0.014954 | -0.14526 | -0.47104 | -0.10681 | -0.049133 | -0.054932 | 0.009155 | -0.1236 | 0.073242 | 0.059509 | 0.059509 | 0.12817 | 0.20599 | 0.1831 | 0.050354
12730.25 | 0.061035 | 0.22217 | -0.2179 | -0.24139 | -0.17197 | -0.24353 | -0.11322 | 0.091553 | 0.018311 | 0.027466 | 0.054932 | 0.11444 | -0.018311 | 0.13733 | 0.061035 | -0.014954 | -0.14206 | -0.48813 | -0.11749 | -0.052338 | 0.004578 | 0.10071 | -0.050354 | 0.059509 | 0.045776 | 0.064087 | 0.11902 | 0.23804 | 0.15106 | 0.018311
12732.0469 | 0.061035 | 0.22964 | -0.21469 | -0.22537 | -0.16663 | -0.25742 | -0.10788 | 0.013733 | -0.064087 | -0.032043 | -0.009155 | 0.13275 | -0.018311 | 0.13733 | 0.076294 | -0.02243 | -0.14526 | -0.4689 | -0.11322 | -0.036316 | -0.050354 | -0.018311 | -0.086975 | 0.068665 | 0.045776 | 0.054932 | 0.12817 | 0.23804 | 0.15564 | 0.054932
12733.8594 | 0.045776 | 0.24887 | -0.23071 | -0.25101 | -0.17197 | -0.28198 | -0.11429 | 0.018311 | -0.036621 | -0.009155 | 0.013733 | 0.13275 | 0.004578 | 0.13733 | 0.076294 | -0.025635 | -0.13886 | -0.48065 | -0.12711 | -0.038452 | -0.054932 | 0.054932 | -0.064087 | 0.068665 | 0.045776 | 0.073242 | 0.13733 | 0.22888 | 0.15106 | 0.036621
12735.5938 | 0.076294 | 0.046997 | -0.03418 | -0.040588 | -0.014954 | -0.037384 | -0.040588 | 0.3891 | -0.29297 | 0.62256 | -0.21973 | -0.07782 | -0.21973 | -0.31128 | 0.061035 | -0.03418 | -0.028839 | -0.036316 | -0.040588 | -0.038452 | -0.17395 | 0.09613 | 0.46692 | -0.14191 | -0.10986 | -0.082397 | -0.737 | 0.25177 | 0.14648 | 0.018311
12737.3906 | 0.045776 | 0.008545 | 0.002136 | -0.007477 | 0.025635 | -0.005341 | -0.005341 | 22.7646 | 27.626 | 20.5353 | 16.3605 | 0.027466 | 0.018311 | 0.022888 | 0.061035 | -0.002136 | 0.007477 | 0.002136 | -0.007477 | -0.006409 | 27.7039 | 28.8025 | 27.8549 | 0.027466 | 0.022888 | 0.018311 | 0.022888 | 0.40741 | -9.0591 | -8.7891
12739.1875 | 0.061035 | 0.007477 | 0.003204 | -0.002136 | 0.018158 | -0.001068 | -0.003204 | 7.5897 | 19.313 | 16.8503 | 13.7878 | 0.027466 | 0.013733 | 0.018311 | 0.091553 | 0 | 0.006409 | 0.002136 | -0.006409 | -0.005341 | 19.4046 | 19.9631 | 19.5465 | 0.027466 | 0.018311 | 0.009155 | 0.022888 | 6.3171 | 0.022888 | 0.022888
12740.9844 | 0.061035 | 0.005341 | 0.002136 | 0 | 0.010681 | 0.001068 | -0.002136 | -3.6209 | 16.777 | 13.884 | 11.2701 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0 | 0.006409 | 0.004272 | -0.002136 | -0.005341 | 13.3392 | 17.276 | 17.0288 | 0.022888 | 0.022888 | 0.013733 | 0.018311 | 4.4449 | 0.022888 | 0.027466
12742.7812 | 0.061035 | 0.006409 | 0.004272 | 0.001068 | 0.005341 | 0.001068 | 0.001068 | -7.6584 | 14.7858 | 11.6547 | 9.819 | 0.027466 | 0.027466 | 0.018311 | 0.076294 | 0.001068 | 0.005341 | 0.002136 | -0.003204 | -0.004272 | 3.653 | 16.2003 | 16.0355 | 0.027466 | 0.022888 | 0.018311 | 0.022888 | 1.181 | 0.018311 | 0.032043
12744.5938 | 0.045776 | 0.006409 | 0.002136 | 0.002136 | 0.001068 | 0.002136 | -0.002136 | -8.4 | 11.3297 | 9.137 | 8.4595 | 0.022888 | 0.018311 | 0.018311 | 0.045776 | 0.001068 | 0.003204 | 0.002136 | -0.002136 | -0.004272 | -3.5065 | 15.5914 | 15.509 | 0.022888 | 0.013733 | 0.018311 | 0.022888 | -1.2085 | 0.018311 | 0.027466
12746.4062 | 0.061035 | 0.006409 | 0.001068 | 0.003204 | 0.002136 | 0.002136 | 0.001068 | -8.9584 | 7.8598 | 6.9672 | 7.4066 | 0.022888 | 0.018311 | 0.013733 | 0.091553 | 0.003204 | 0.002136 | 0.003204 | 0.001068 | -0.003204 | -10.7162 | 11.7966 | 15.184 | 0.022888 | 0.018311 | 0.013733 | 0.013733 | -2.9663 | 0.018311 | 0.022888
12748.1875 | 0.061035 | 0.006409 | 0.001068 | 0.002136 | 0 | 0.001068 | 0 | -8.5419 | 5.5984 | 5.3513 | 6.4728 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.002136 | 0.003204 | 0.004272 | 0.001068 | -0.001068 | -12.4146 | 7.5302 | 14.9368 | 0.022888 | 0.009155 | 0.018311 | 0.027466 | -3.2501 | 0.018311 | 0.027466
12749.9219 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0 | 0.004272 | -0.001068 | -8.075 | 3.8315 | 4.1245 | 5.7678 | 0.022888 | 0.013733 | 0.018311 | 0.045776 | 0.004272 | 0.003204 | 0.002136 | 0.003204 | 0 | -12.291 | 4.248 | 14.6255 | 0.018311 | 0.022888 | 0.018311 | 0.022888 | -3.0075 | 0.022888 | 0.018311
12751.7188 | 0.045776 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.001068 | -7.4661 | 2.4994 | 3.0945 | 5.072 | 0.013733 | 0.013733 | 0.013733 | 0.076294 | 0.004272 | 0.003204 | 0.004272 | 0.002136 | 0.002136 | -12.1811 | 1.3138 | 13.06 | 0.022888 | 0.013733 | 0.022888 | 0.022888 | -2.5543 | 0.013733 | 0.022888
12753.5156 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.002136 | -6.9901 | 1.3412 | 2.3117 | 4.5731 | 0.018311 | 0.022888 | 0.018311 | 0.030518 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | 0 | -12.085 | -1.7944 | 10.2448 | 0.022888 | 0.018311 | 0.022888 | 0.013733 | -2.0599 | 0.032043 | 0.027466
12755.25 | 0.061035 | 0.005341 | 0.004272 | 0.004272 | 0.001068 | 0.002136 | 0.002136 | -6.4499 | 0.40741 | 1.4099 | 3.9459 | 0.009155 | 0.018311 | 0.022888 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.001068 | -12.0117 | -5.6351 | 7.0175 | 0.018311 | 0.013733 | 0.022888 | 0.018311 | -1.4557 | 0.018311 | 0.022888
12757.0469 | 0.045776 | 0.006409 | 0.002136 | 0.004272 | 0.002136 | 0.002136 | 0.004272 | -5.864 | -0.20142 | 0.69122 | 3.4103 | 0.022888 | 0.018311 | 0.022888 | 0.045776 | 0.002136 | 0.004272 | 0.004272 | 0.002136 | 0.001068 | -11.9385 | -9.1415 | 4.0649 | 0.022888 | 0.018311 | 0.018311 | 0.009155 | -0.86975 | 0.018311 | 0.032043
12758.8438 | 0.045776 | 0.005341 | 0.002136 | 0.005341 | 0.001068 | 0.003204 | 0.002136 | -5.2826 | -0.69122 | 0.091553 | 2.948 | 0.027466 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.003204 | 0 | 0.001068 | -11.8652 | -10.5011 | 2.0279 | 0.022888 | 0.013733 | 0.018311 | 0.018311 | -0.53558 | 0.027466 | 0.018311
12760.5781 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.002136 | 0.004272 | -4.7104 | -1.03 | -0.42572 | 2.4811 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.004272 | 0.005341 | 0.003204 | 0.002136 | -11.7966 | -11.142 | 0.041199 | 0.022888 | 0.013733 | 0.018311 | 0.022888 | -0.07782 | 0.022888 | 0.018311
12762.375 | 0.061035 | 0.005341 | 0.003204 | 0.004272 | 0 | 0.002136 | 0.003204 | -4.1061 | -1.236 | -0.81024 | 2.0645 | 0.018311 | 0.022888 | 0.018311 | 0.076294 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | 0.002136 | -11.7233 | -11.38 | -2.1423 | 0.013733 | 0.022888 | 0.027466 | 0.022888 | 0.086975 | 0.022888 | 0.018311
12764.1719 | 0.091553 | 0.006409 | 0.003204 | 0.002136 | 0 | 0.002136 | 0.002136 | -3.5431 | -1.3641 | -1.1032 | 1.6754 | 0.018311 | 0.013733 | 0.018311 | 0.061035 | 0.004272 | 0 | 0.001068 | 0.003204 | 0.001068 | -11.6135 | -11.4624 | -4.5364 | 0.022888 | 0.022888 | 0.018311 | 0.018311 | 0.21057 | 0.027466 | 0.022888
12765.9844 | 0.061035 | 0.006409 | 0.003204 | 0.004272 | 0.001068 | 0.004272 | 0.003204 | -3.0075 | -1.4374 | -1.3 | 1.3504 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.004272 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | -11.412 | -11.4761 | -6.7978 | 0.013733 | 0.009155 | 0.018311 | 0.018311 | 0.36621 | 0.027466 | 0.022888
12767.7812 | 0.061035 | 0.005341 | 0.002136 | 0.001068 | 0 | 0.001068 | 0.001068 | -2.5314 | -1.4877 | -1.4603 | 1.0849 | 0.018311 | 0.022888 | 0.018311 | 0.045776 | 0.004272 | 0.004272 | 0.001068 | 0.004272 | 0.002136 | -11.0596 | -11.4349 | -8.1985 | 0.013733 | 0.013733 | 0.013733 | 0.018311 | 0.44403 | 0.022888 | 0.027466
12769.5156 | 0.045776 | 0.006409 | 0.001068 | 0.003204 | 0 | 0.004272 | 0.005341 | -2.1011 | -1.5152 | -1.5198 | 0.84686 | 0.013733 | 0.018311 | 0.013733 | 0.061035 | 0.003204 | 0.003204 | 0.002136 | 0.002136 | 0.003204 | -10.5515 | -11.3663 | -8.9493 | 0.018311 | 0.013733 | 0.018311 | 0.018311 | 0.50812 | 0.022888 | 0.027466
12771.3125 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0 | 0.003204 | 0.002136 | -1.7212 | -1.506 | -1.5793 | 0.64545 | 0.013733 | 0.022888 | 0.013733 | 0.061035 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | 0.003204 | -9.8923 | -11.2335 | -9.4254 | 0.018311 | 0.022888 | 0.013733 | 0.018311 | 0.53101 | 0.022888 | 0.022888
12773.1094 | 0.061035 | 0.005341 | 0.001068 | 0.002136 | 0.002136 | 0.003204 | 0 | -1.3824 | -1.4786 | -1.5884 | 0.48065 | 0.018311 | 0.018311 | 0.022888 | 0.045776 | 0.001068 | 0.003204 | 0.004272 | 0.002136 | 0.004272 | -9.2056 | -11.0413 | -9.7458 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | 0.39368 | 0.022888 | 0.022888
12774.8594 | 0.076294 | 0.005341 | 0.002136 | 0.003204 | -0.001068 | 0.003204 | 0.002136 | -1.0849 | -1.4557 | -1.593 | 0.34332 | 0.027466 | 0.018311 | 0.009155 | 0.076294 | 0.003204 | 0.002136 | 0.003204 | 0.004272 | 0.003204 | -8.5236 | -10.7895 | -9.9747 | 0.013733 | 0.013733 | 0.022888 | 0.013733 | 0.30212 | 0.022888 | 0.018311
12776.6562 | 0.061035 | 0.005341 | 0.002136 | 0.002136 | 0 | 0.002136 | 0.003204 | -0.89722 | -1.4786 | -1.6296 | 0.21515 | 0.018311 | 0.022888 | 0.022888 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.002136 | 0.003204 | -7.9376 | -10.4553 | -10.0388 | 0 | 0.018311 | 0.009155 | 0.018311 | 0.07782 | 0.018311 | 0.022888
12778.4531 | 0.076294 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.003204 | 0.002136 | -0.76904 | -1.4969 | -1.6434 | 0.10071 | 0.018311 | 0.013733 | 0.022888 | 0.030518 | 0.003204 | 0.002136 | 0.003204 | 0.003204 | 0.002136 | -7.3654 | -10.0937 | -10.0479 | 0.013733 | 0.018311 | 0.013733 | 0.018311 | 0.032043 | 0.018311 | 0.018311
12780.1875 | 0.061035 | 0.006409 | 0.003204 | 0.003204 | 0.001068 | 0.004272 | 0.003204 | -0.62714 | -1.4832 | -1.6434 | -0.013733 | 0.018311 | 0.018311 | 0.013733 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.003204 | 0.002136 | -6.8436 | -9.6954 | -10.0113 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | -0.1831 | 0.027466 | 0.018311
12781.9844 | 0.076294 | 0.006409 | 0.002136 | 0.003204 | -0.001068 | 0.004272 | 0.003204 | -0.51727 | -1.4557 | -1.6571 | -0.12817 | 0.018311 | 0.018311 | 0.018311 | 0.030518 | 0.002136 | 0.001068 | 0.002136 | 0.004272 | 0.002136 | -6.3309 | -9.2285 | -9.8694 | 0.022888 | 0.018311 | 0.022888 | 0.022888 | -0.29755 | 0.022888 | 0.022888
12783.7188 | 0.045776 | 0.007477 | 0.003204 | 0.002136 | 0.001068 | 0.003204 | 0 | -0.43945 | -1.4603 | -1.6708 | -0.21973 | 0.018311 | 0.018311 | 0.032043 | 0.076294 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.003204 | -5.9143 | -8.8303 | -9.7275 | 0.013733 | 0.022888 | 0.018311 | 0.018311 | -0.33875 | 0.018311 | 0.027466
12785.5156 | 0.061035 | 0.006409 | 0.001068 | 0.004272 | 0.001068 | 0.003204 | 0.002136 | -0.37994 | -1.4603 | -1.6891 | -0.32044 | 0.022888 | 0.013733 | 0.013733 | 0.076294 | 0.002136 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | -5.484 | -8.3771 | -9.5078 | 0.013733 | 0.018311 | 0.018311 | 0.027466 | -0.6546 | 0.022888 | 0.018311
12787.3125 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | -0.001068 | 0.003204 | 0.002136 | -0.33875 | -1.4694 | -1.7212 | -0.42114 | 0.022888 | 0.022888 | 0.018311 | 0.045776 | 0.003204 | 0.002136 | 0.004272 | 0.003204 | 0.004272 | -5.1086 | -7.9697 | -9.2972 | 0.018311 | 0.018311 | 0.022888 | 0.027466 | -0.67291 | 0.018311 | 0.022888
12789.0938 | 0.076294 | 0.005341 | 0.002136 | 0.004272 | 0 | 0.003204 | 0.003204 | -0.32044 | -1.4557 | -1.7487 | -0.52185 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.004272 | 0.003204 | 0.003204 | -4.7791 | -7.5897 | -9.0546 | 0.022888 | 0.022888 | 0.018311 | 0.022888 | -0.82398 | 0.022888 | 0.018311
12790.8281 | 0.061035 | 0.004272 | 0.003204 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.29755 | -1.4648 | -1.7715 | -0.6134 | 0.018311 | 0.022888 | 0.018311 | 0.091553 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | 0.004272 | -4.4769 | -7.2098 | -8.8211 | 0.013733 | 0.018311 | 0.022888 | 0.018311 | -0.9613 | 0.022888 | 0.022888
12792.6094 | 0.061035 | 0.006409 | 0.002136 | 0.002136 | -0.001068 | 0.003204 | 0.002136 | -0.29755 | -1.4603 | -1.8082 | -0.72784 | 0.018311 | 0.018311 | 0.018311 | 0.061035 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0.004272 | -4.184 | -6.8481 | -8.5373 | 0.022888 | 0.018311 | 0.022888 | 0.022888 | -1.1032 | 0.018311 | 0.018311
12794.3438 | 0.076294 | 0.005341 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -0.29297 | -1.4511 | -1.8356 | -0.8194 | 0.022888 | 0.022888 | 0.009155 | 0.045776 | 0.005341 | 0.002136 | 0.004272 | 0.004272 | 0.003204 | -3.923 | -6.5231 | -8.2764 | 0.009155 | 0.013733 | 0.013733 | 0.022888 | -1.2772 | 0.022888 | 0.027466
12796.1406 | 0.061035 | 0.005341 | 0.003204 | 0.003204 | -0.002136 | 0.004272 | 0.001068 | -0.3067 | -1.4557 | -1.8768 | -0.9201 | 0.013733 | 0.027466 | 0.018311 | 0.076294 | 0.003204 | 0.002136 | 0.002136 | 0.002136 | 0.002136 | -3.6804 | -6.1935 | -7.9926 | 0.018311 | 0.013733 | 0.013733 | 0.013733 | -1.3275 | 0.018311 | 0.027466
12797.9375 | 0.076294 | 0.004272 | 0.005341 | 0.003204 | 0.001068 | 0.002136 | 0.002136 | -0.32501 | -1.4511 | -1.9089 | -1.0254 | 0.022888 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.003204 | 0.002136 | 0.005341 | 0.004272 | -3.4561 | -5.9006 | -7.7042 | 0.022888 | 0.018311 | 0.009155 | 0.018311 | -1.506 | 0.022888 | 0.013733
12799.6719 | 0.061035 | 0.006409 | 0.002136 | 0.004272 | 0.001068 | 0.003204 | 0.003204 | -0.32501 | -1.4465 | -1.9547 | -1.1215 | 0.027466 | 0.013733 | 0.022888 | 0.061035 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | 0.003204 | -3.2593 | -5.6305 | -7.4615 | 0.013733 | 0.018311 | 0.018311 | 0.022888 | -1.5839 | 0.027466 | 0.027466
12801.4844 | 0.045776 | 0.005341 | 0.003204 | 0.003204 | 0.001068 | 0.003204 | 0 | -0.37079 | -1.4511 | -1.9913 | -1.2268 | 0.018311 | 0.018311 | 0.018311 | 0.045776 | 0.004272 | 0.002136 | 0.001068 | 0.003204 | 0.003204 | -3.0808 | -5.365 | -7.1823 | 0.013733 | 0.018311 | 0.018311 | 0.018311 | -1.7212 | 0.022888 | 0.018311
12803.2812 | 0.076294 | 0.007477 | 0.002136 | 0.002136 | 0 | 0.003204 | 0.002136 | -0.37079 | -1.4603 | -2.037 | -1.3458 | 0.013733 | 0.018311 | 0.022888 | 0.045776 | 0.003204 | 0.005341 | 0.002136 | 0.002136 | 0.004272 | -2.8976 | -5.127 | -6.9305 | 0.018311 | 0.022888 | 0.018311 | 0.022888 | -1.6296 | 0.022888 | 0.018311
12805.0781 | 0.076294 | 0.006409 | 0.003204 | 0.003204 | 0.002136 | 0.003204 | 0.002136 | -0.3891 | -1.4374 | -2.0554 | -1.4374 | 0.013733 | 0.018311 | 0.018311 | 0.061035 | 0.004272 | 0.004272 | 0.002136 | 0.004272 | 0.003204 | -2.7603 | -4.8935 | -6.6696 | 0.009155 | 0.013733 | 0.022888 | 0.022888 | -1.7487 | 0.022888 | 0.032043
12806.8594 | 0.061035 | 0.005341 | 0.001068 | 0.003204 | 0.001068 | 0.002136 | 0.001068 | -0.42114 | -1.4511 | -2.1057 | -1.5472 | 0.018311 | 0.018311 | 0.022888 | 0.061035 | 0.003204 | 0.003204 | 0.004272 | 0.003204 | 0.002136 | -2.6321 | -4.6921 | -6.4453 | 0.018311 | 0.022888 | 0.013733 | 0.022888 | -1.9318 | 0.027466 | 0.022888

## Final Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.42188 | 122.9324 | -62.3428 | 60.2417 | 0.0074006 | -0.058108 | 0.12893 | 0.030255 | 0.038418 | -0.035519 | -0.025669 | 7.627e-05 | -0.0095638 | 0.029081 | 0.061543 | -0.019833 | -0.020679 | 60.3745 | -62.2467 | 0.064087 | -62.471 | 60.1913 | -62.3566 | -62.2742 | 0.027466 | 0.10071 | -62.6404 | 60.1593 | 60.1593 | -62.265 | -62.4664 | -0.013733 | 0.068664 | -0.050354 | 0.09613 | -0.12817 | -0.19684 | 0.13275 | 0.077819 | -0.1236 | -0.082397 | 62.3703 | -0.29755 | -0.17395 | -0.082397 | 122.5342 | 122.7173 | 62.4069 | -122.5159 | 122.5021 | 122.5021 | 62.4435 | -122.7081
1.3125 | 122.8409 | -62.3932 | 60.2921 | -0.0078584 | -0.058748 | 0.12679 | 0.034314 | 0.039273 | -0.042569 | -0.026523 | 7.627e-05 | -0.011486 | 0.031858 | 0.058766 | -0.023678 | -0.022815 | 60.3287 | -62.2971 | 0.041199 | -62.4939 | 60.2051 | -62.3383 | -62.2696 | -0.022888 | 0 | -62.6633 | 60.1959 | 60.1913 | -62.2421 | -62.4481 | 0.054931 | 0.1236 | -0.086975 | 0.09613 | -0.10071 | -0.2243 | 0.036621 | 0.15106 | -0.054932 | -0.09613 | 62.3703 | -0.27008 | -0.21515 | -0.10071 | 122.5983 | 122.7219 | 62.4344 | -122.5616 | 122.5891 | 122.5845 | 62.3932 | -122.7402
3.0781 | 122.8317 | -62.3611 | 60.3195 | -0.00022891 | -0.062166 | 0.12935 | 0.025983 | 0.039913 | -0.041073 | -0.025242 | 7.627e-05 | -0.010632 | 0.027799 | 0.059406 | -0.022823 | -0.020892 | 60.4568 | -62.1414 | 0.10529 | -62.3932 | 60.1913 | -62.2787 | -62.2009 | 0.11444 | 0.14648 | -62.5351 | 60.1868 | 60.1913 | -62.178 | -62.384 | 0.082397 | 0.16022 | -0.12817 | 0.21973 | -0.032043 | -0.19226 | 0.13733 | 0.1831 | -0.022888 | -0.13275 | 62.4756 | -0.17395 | -0.15106 | -0.12817 | 122.5525 | 122.818 | 62.4664 | -122.5204 | 122.5479 | 122.5525 | 62.5076 | -122.7036
4.7969 | 122.8363 | -62.3657 | 60.3699 | -0.0078584 | -0.06003 | 0.12914 | 0.031751 | 0.038418 | -0.041928 | -0.027164 | 0.0077058 | -0.013836 | 0.027158 | 0.058338 | -0.02496 | -0.02132 | 60.434 | -62.2055 | 0.064087 | -62.4115 | 60.2417 | -62.265 | -62.2192 | 0.032043 | 0.073242 | -62.5397 | 60.2051 | 60.2188 | -62.1872 | -62.3886 | 0.10071 | 0.14649 | -0.12817 | 0.16022 | -0.045776 | -0.19226 | 0.064087 | 0.17853 | -0.022888 | -0.16479 | 62.3978 | -0.17395 | -0.15106 | -0.15106 | 122.6074 | 122.7997 | 62.4298 | -122.5891 | 122.5708 | 122.5845 | 62.439 | -122.7585
6.5625 | 122.8546 | -62.3566 | 60.3149 | -0.00022891 | -0.060457 | 0.1285 | 0.031537 | 0.041622 | -0.04086 | -0.0293 | 7.627e-05 | -0.010418 | 0.02844 | 0.061115 | -0.02731 | -0.021533 | 60.5026 | -62.1368 | 0.14191 | -62.3749 | 60.2097 | -62.2833 | -62.2192 | 0.1236 | 0.14648 | -62.4756 | 60.2005 | 60.1639 | -62.1826 | -62.3932 | 0.073242 | 0.13733 | -0.10528 | 0.21973 | -0.018311 | -0.15564 | 0.18768 | 0.17395 | -0.036621 | -0.11444 | 62.4802 | -0.11902 | -0.082398 | -0.15106 | 122.5662 | 122.8592 | 62.4985 | -122.5342 | 122.5571 | 122.5204 | 62.5031 | -122.7081
8.2812 | 122.9416 | -62.3474 | 60.2463 | -0.00022891 | -0.051485 | 0.12743 | 0.028333 | 0.040982 | -0.032315 | -0.026737 | 0.015335 | -0.0095638 | 0.03143 | 0.060688 | -0.018765 | -0.023456 | 60.3836 | -62.2879 | 0.054932 | -62.4664 | 60.2234 | -62.3566 | -62.265 | 0.013733 | 0.054932 | -62.6541 | 60.2051 | 60.1547 | -62.2604 | -62.4664 | -0.009155 | 0.082397 | -0.022888 | 0.059509 | -0.11902 | -0.20142 | 0.13733 | 0.086975 | -0.11902 | -0.041199 | 62.3611 | -0.3067 | -0.18768 | -0.091553 | 122.5708 | 122.731 | 62.4023 | -122.5113 | 122.5525 | 122.5021 | 62.4023 | -122.7127
10.0469 | 122.9004 | -62.3657 | 60.2737 | -0.00022891 | -0.05768 | 0.12658 | 0.027478 | 0.040341 | -0.032956 | -0.02396 | 0.0077058 | -0.0082822 | 0.030362 | 0.062183 | -0.019619 | -0.024097 | 60.3424 | -62.3428 | -0.018311 | -62.5214 | 60.2234 | -62.3474 | -62.2787 | 0.013733 | 0.036621 | -62.7045 | 60.2188 | 60.1776 | -62.2604 | -62.4344 | 0.018311 | 0.086975 | -0.050354 | 0.022889 | -0.15564 | -0.24261 | 0.068664 | 0.10529 | -0.068664 | -0.054932 | 62.3795 | -0.33874 | -0.27008 | -0.096131 | 122.5891 | 122.7081 | 62.3474 | -122.5525 | 122.5845 | 122.5433 | 62.4023 | -122.7081
11.8281 | 122.7997 | -62.3474 | 60.2875 | -0.00022891 | -0.058321 | 0.12957 | 0.031537 | 0.037564 | -0.041073 | -0.023533 | 7.627e-05 | -0.013195 | 0.028867 | 0.057911 | -0.021969 | -0.02196 | 60.4797 | -62.1231 | 0.15106 | -62.384 | 60.1822 | -62.2742 | -62.2101 | 0.07782 | 0.12817 | -62.5214 | 60.1685 | 60.1913 | -62.2101 | -62.4023 | 0.073242 | 0.13733 | -0.10529 | 0.2243 | -0.036621 | -0.17395 | 0.19226 | 0.13733 | -0.054932 | -0.11902 | 62.4252 | -0.17395 | -0.11902 | -0.096131 | 122.5296 | 122.8271 | 62.4985 | -122.4976 | 122.5159 | 122.5388 | 62.4756 | -122.6898
13.6094 | 122.8271 | -62.3703 | 60.2692 | 0.0074006 | -0.057467 | 0.12914 | 0.029828 | 0.03735 | -0.037228 | -0.02396 | 7.627e-05 | -0.0080686 | 0.029508 | 0.059193 | -0.022396 | -0.023883 | 60.3699 | -62.2879 | 0.032043 | -62.471 | 60.2417 | -62.3428 | -62.2513 | -0.022888 | 0.009155 | -62.6678 | 60.2142 | 60.2234 | -62.2467 | -62.4344 | 0.027466 | 0.11902 | -0.027466 | 0.082397 | -0.10071 | -0.21973 | 0.10071 | 0.1236 | -0.064087 | -0.054932 | 62.3474 | -0.29755 | -0.23346 | -0.045776 | 122.612 | 122.7402 | 62.4023 | -122.5204 | 122.5845 | 122.5937 | 62.3795 | -122.7036
15.3281 | 122.9599 | -62.3291 | 60.2737 | 0.0074006 | -0.057467 | 0.12978 | 0.028974 | 0.040127 | -0.034665 | -0.025028 | -0.0075532 | -0.0087094 | 0.029722 | 0.06197 | -0.021542 | -0.020679 | 60.3928 | -62.2879 | 0 | -62.471 | 60.2188 | -62.3245 | -62.2559 | 0.073242 | 0.09613 | -62.6312 | 60.1822 | 60.2005 | -62.2421 | -62.4252 | 0.004578 | 0.073243 | -0.054932 | 0.041199 | -0.14191 | -0.21515 | 0.11902 | 0.086976 | -0.09613 | -0.091553 | 62.4023 | -0.30212 | -0.20599 | -0.073243 | 122.5479 | 122.7219 | 62.3291 | -122.5296 | 122.5113 | 122.5296 | 62.4252 | -122.699
17.0312 | 122.7997 | -62.3245 | 60.3424 | -0.0078584 | -0.059817 | 0.13106 | 0.030255 | 0.038845 | -0.038937 | -0.025028 | 7.627e-05 | -0.012555 | 0.029294 | 0.060474 | -0.025173 | -0.022174 | 60.4385 | -62.1643 | 0.07782 | -62.4069 | 60.2005 | -62.2925 | -62.1918 | 0.064087 | 0.10071 | -62.5442 | 60.1959 | 60.2051 | -62.1689 | -62.3795 | 0.032044 | 0.13275 | -0.14191 | 0.16022 | -0.082397 | -0.21515 | 0.096131 | 0.15564 | -0.054932 | -0.14648 | 62.3886 | -0.21973 | -0.16479 | -0.13733 | 122.525 | 122.7631 | 62.4023 | -122.5342 | 122.5204 | 122.5296 | 62.4252 | -122.7219
18.8125 | 122.8043 | -62.3337 | 60.3378 | -0.00022891 | -0.061739 | 0.12978 | 0.029828 | 0.039913 | -0.039792 | -0.025242 | 7.627e-05 | -0.012555 | 0.027799 | 0.059834 | -0.023037 | -0.022174 | 60.4385 | -62.1826 | 0.068665 | -62.4161 | 60.2188 | -62.2925 | -62.2055 | 0.054932 | 0.09613 | -62.558 | 60.2051 | 60.1822 | -62.178 | -62.3749 | 0.041199 | 0.12817 | -0.11902 | 0.15106 | -0.082398 | -0.21057 | 0.10071 | 0.15564 | -0.041199 | -0.13275 | 62.3886 | -0.2243 | -0.1831 | -0.15564 | 122.5525 | 122.7722 | 62.4023 | -122.5433 | 122.5388 | 122.5159 | 62.4298 | -122.7127
20.5938 | 122.9004 | -62.3245 | 60.2829 | -0.0078584 | -0.055117 | 0.12337 | 0.031964 | 0.038632 | -0.033383 | -0.02396 | -0.0075532 | -0.0087094 | 0.031003 | 0.060474 | -0.020046 | -0.025378 | 60.3561 | -62.3199 | -0.009155 | -62.5031 | 60.2371 | -62.352 | -62.2971 | 0.041199 | 0.022888 | -62.7136 | 60.2051 | 60.2051 | -62.2375 | -62.4619 | -0.027466 | 0.027466 | -0.045776 | 0.004578 | -0.17853 | -0.20599 | 0.073242 | 0.086975 | -0.13733 | -0.07782 | 62.3657 | -0.3891 | -0.25177 | -0.07782 | 122.5616 | 122.6807 | 62.3154 | -122.58 | 122.5296 | 122.5296 | 62.3474 | -122.7448
22.3594 | 122.9599 | -62.3108 | 60.2692 | 0.0074006 | -0.059389 | 0.12871 | 0.027478 | 0.037564 | -0.036587 | -0.025455 | 7.627e-05 | -0.011273 | 0.029508 | 0.061115 | -0.020687 | -0.022388 | 60.3653 | -62.2604 | 0.018311 | -62.4573 | 60.1913 | -62.3291 | -62.2559 | 0.091553 | 0.10986 | -62.6038 | 60.1868 | 60.1501 | -62.2192 | -62.4298 | -0.018311 | 0.054932 | -0.07782 | 0.050354 | -0.14648 | -0.20142 | 0.09613 | 0.091553 | -0.11902 | -0.082397 | 62.4023 | -0.29297 | -0.17395 | -0.11902 | 122.5021 | 122.6761 | 62.3291 | -122.525 | 122.4976 | 122.4609 | 62.4207 | -122.699
24.125 | 122.8683 | -62.3337 | 60.2646 | -0.00022891 | -0.055971 | 0.12935 | 0.030042 | 0.036923 | -0.033596 | -0.021824 | 0.0077058 | -0.007855 | 0.030362 | 0.061115 | -0.019406 | -0.023669 | 60.3745 | -62.2467 | 0.054932 | -62.4619 | 60.1913 | -62.3383 | -62.2833 | 0.041199 | 0.068665 | -62.6907 | 60.1501 | 60.1456 | -62.2421 | -62.4573 | -0.004578 | 0.050354 | -0.073242 | 0.086975 | -0.12817 | -0.17853 | 0.10986 | 0.091553 | -0.1236 | -0.11444 | 62.3749 | -0.35706 | -0.23346 | -0.11902 | 122.525 | 122.7081 | 62.3886 | -122.5479 | 122.4838 | 122.4792 | 62.4023 | -122.7219
25.8438 | 122.7722 | -62.3611 | 60.3058 | 0.0074006 | -0.057894 | 0.12871 | 0.033673 | 0.041622 | -0.038296 | -0.025882 | 0.0077058 | -0.014477 | 0.028226 | 0.061115 | -0.024319 | -0.023456 | 60.4477 | -62.1277 | 0.16022 | -62.3978 | 60.1822 | -62.2879 | -62.1964 | 0.050354 | 0.11902 | -62.5442 | 60.1593 | 60.1822 | -62.2055 | -62.3978 | 0.073242 | 0.16479 | -0.1236 | 0.23346 | -0.036621 | -0.20142 | 0.14191 | 0.15564 | -0.036621 | -0.14648 | 62.4115 | -0.1831 | -0.14648 | -0.1236 | 122.5433 | 122.8088 | 62.5214 | -122.5021 | 122.5204 | 122.5433 | 62.4802 | -122.7036
27.6406 | 122.7905 | -62.3566 | 60.3378 | -0.00022891 | -0.061312 | 0.12764 | 0.030255 | 0.039273 | -0.040219 | -0.025455 | 0.0077058 | -0.011486 | 0.028867 | 0.05962 | -0.024105 | -0.021747 | 60.4385 | -62.1552 | 0.073242 | -62.4069 | 60.2234 | -62.2879 | -62.1735 | 0.073242 | 0.11902 | -62.5397 | 60.1959 | 60.1868 | -62.1735 | -62.3932 | 0.068664 | 0.1831 | -0.11444 | 0.20142 | -0.050354 | -0.23346 | 0.10071 | 0.1831 | -0.036621 | -0.14191 | 62.4298 | -0.18311 | -0.14648 | -0.15106 | 122.58 | 122.7951 | 62.4298 | -122.5113 | 122.5525 | 122.5433 | 62.4756 | -122.731
29.3594 | 122.9141 | -62.3291 | 60.2829 | -0.00022891 | -0.058108 | 0.12593 | 0.02876 | 0.037991 | -0.03381 | -0.024814 | -0.0075532 | -0.0087094 | 0.029508 | 0.06197 | -0.021114 | -0.023242 | 60.3882 | -62.3108 | -0.022888 | -62.4802 | 60.2371 | -62.3383 | -62.2696 | 0.036621 | 0.041199 | -62.677 | 60.1959 | 60.2005 | -62.2513 | -62.4573 | -0.009155 | 0.05951 | -0.045776 | 0.018311 | -0.15106 | -0.21057 | 0.10529 | 0.07782 | -0.12817 | -0.086975 | 62.3657 | -0.3479 | -0.21973 | -0.082398 | 122.5662 | 122.7173 | 62.3062 | -122.5525 | 122.525 | 122.5296 | 62.3703 | -122.7402
31.1094 | 122.7997 | -62.3566 | 60.3241 | -0.0078584 | -0.061739 | 0.12871 | 0.030042 | 0.039059 | -0.042141 | -0.024173 | 7.627e-05 | -0.013409 | 0.026517 | 0.057484 | -0.024532 | -0.02196 | 60.4431 | -62.1552 | 0.091553 | -62.3932 | 60.2051 | -62.2696 | -62.2101 | 0.050354 | 0.09613 | -62.5442 | 60.1959 | 60.1822 | -62.1689 | -62.3978 | 0.086975 | 0.14648 | -0.11902 | 0.20142 | -0.036621 | -0.18311 | 0.11902 | 0.18768 | -0.041199 | -0.12817 | 62.4069 | -0.18768 | -0.14648 | -0.14191 | 122.5616 | 122.7997 | 62.4481 | -122.5342 | 122.5525 | 122.5388 | 62.4527 | -122.7219
32.8906 | 122.8226 | -62.3291 | 60.3241 | 0.0074006 | -0.060457 | 0.12893 | 0.032605 | 0.039273 | -0.039578 | -0.025455 | 7.627e-05 | -0.013409 | 0.030362 | 0.056843 | -0.024746 | -0.024738 | 60.4935 | -62.1002 | 0.15564 | -62.3611 | 60.1822 | -62.2742 | -62.1918 | 0.11444 | 0.15564 | -62.4985 | 60.1822 | 60.1639 | -62.2147 | -62.3886 | 0.054932 | 0.13733 | -0.14191 | 0.22888 | -0.032043 | -0.16937 | 0.16937 | 0.11444 | -0.059509 | -0.14191 | 62.4435 | -0.16937 | -0.10986 | -0.16022 | 122.5113 | 122.8226 | 62.4847 | -122.5159 | 122.5113 | 122.493 | 62.4847 | -122.7127
34.6719 | 122.7859 | -62.3428 | 60.3378 | -0.00022891 | -0.058108 | 0.12679 | 0.030683 | 0.036282 | -0.036587 | -0.02631 | 7.627e-05 | -0.012768 | 0.029722 | 0.058979 | -0.022396 | -0.022815 | 60.466 | -62.146 | 0.09613 | -62.384 | 60.1868 | -62.3016 | -62.1964 | 0.1236 | 0.15106 | -62.5259 | 60.173 | 60.1501 | -62.1735 | -62.3932 | 0.041198 | 0.14648 | -0.15106 | 0.19684 | -0.041199 | -0.18768 | 0.12817 | 0.16937 | -0.050354 | -0.16479 | 62.4664 | -0.18311 | -0.13275 | -0.18768 | 122.5296 | 122.8088 | 62.439 | -122.5342 | 122.5159 | 122.493 | 62.4939 | -122.731
36.4531 | 122.7722 | -62.3611 | 60.3149 | -0.00022891 | -0.058962 | 0.12807 | 0.028974 | 0.038204 | -0.037869 | -0.026951 | 0.0077058 | -0.012341 | 0.031217 | 0.059193 | -0.021755 | -0.024097 | 60.4614 | -62.1368 | 0.14648 | -62.3703 | 60.1913 | -62.2925 | -62.2375 | 0.059509 | 0.11444 | -62.5442 | 60.1685 | 60.173 | -62.2238 | -62.3978 | 0.068665 | 0.1236 | -0.1236 | 0.2243 | -0.009155 | -0.13275 | 0.14649 | 0.13733 | -0.036621 | -0.14648 | 62.4207 | -0.1831 | -0.14648 | -0.14191 | 122.5525 | 122.8226 | 62.5076 | -122.5525 | 122.5296 | 122.5342 | 62.4756 | -122.7127
38.2344 | 122.8683 | -62.3291 | 60.2966 | 0.0074006 | -0.054476 | 0.12679 | 0.027265 | 0.040554 | -0.034451 | -0.02396 | 0.0077058 | -0.010418 | 0.031003 | 0.060902 | -0.019192 | -0.023669 | 60.3241 | -62.3291 | -0.013733 | -62.4893 | 60.228 | -62.352 | -62.265 | 0.027466 | 0.032043 | -62.6907 | 60.2051 | 60.1639 | -62.2559 | -62.4664 | -0.022888 | 0.064087 | -0.068665 | 0 | -0.16022 | -0.2243 | 0.027466 | 0.073243 | -0.13733 | -0.091553 | 62.3566 | -0.36163 | -0.2243 | -0.13275 | 122.5571 | 122.6532 | 62.3154 | -122.5616 | 122.5342 | 122.493 | 62.3611 | -122.7631
40 | 122.7768 | -62.3474 | 60.3149 | -0.00022891 | -0.060671 | 0.12764 | 0.030255 | 0.040554 | -0.038723 | -0.023533 | 0.0077058 | -0.012555 | 0.029294 | 0.058338 | -0.021755 | -0.021533 | 60.4614 | -62.1185 | 0.10071 | -62.3932 | 60.173 | -62.2925 | -62.1964 | 0.12817 | 0.14191 | -62.5168 | 60.173 | 60.1593 | -62.1414 | -62.3749 | 0.054932 | 0.15106 | -0.14191 | 0.22888 | -0.045776 | -0.19684 | 0.14649 | 0.20599 | -0.027466 | -0.14191 | 62.4756 | -0.16937 | -0.14191 | -0.15564 | 122.5204 | 122.8088 | 62.4481 | -122.5113 | 122.5204 | 122.5067 | 62.4893 | -122.6898
41.7188 | 122.7997 | -62.3199 | 60.3333 | 0.0074006 | -0.062594 | 0.12893 | 0.032178 | 0.038204 | -0.03851 | -0.02631 | -0.015182 | -0.012127 | 0.028226 | 0.058552 | -0.023678 | -0.022815 | 60.4248 | -62.1506 | 0.068665 | -62.384 | 60.2234 | -62.2742 | -62.1964 | 0.050354 | 0.082397 | -62.5442 | 60.1913 | 60.2142 | -62.1597 | -62.3978 | 0.045776 | 0.1236 | -0.10986 | 0.16937 | -0.064087 | -0.18768 | 0.091553 | 0.16022 | -0.07782 | -0.14191 | 62.3703 | -0.2243 | -0.14648 | -0.11902 | 122.5433 | 122.7448 | 62.3886 | -122.5296 | 122.5113 | 122.5342 | 62.4023 | -122.731
43.4844 | 122.7631 | -62.352 | 60.3378 | 0.0074006 | -0.06003 | 0.12786 | 0.029614 | 0.0397 | -0.036587 | -0.026096 | 7.627e-05 | -0.010632 | 0.026304 | 0.05962 | -0.021328 | -0.024524 | 60.466 | -62.1368 | 0.10529 | -62.3886 | 60.2005 | -62.2787 | -62.1918 | 0.10071 | 0.13275 | -62.5442 | 60.1639 | 60.1593 | -62.1689 | -62.3978 | 0.073242 | 0.16022 | -0.13733 | 0.21515 | -0.036621 | -0.19684 | 0.12817 | 0.18311 | -0.045776 | -0.17395 | 62.4527 | -0.19226 | -0.14648 | -0.17853 | 122.5525 | 122.818 | 62.4573 | -122.5296 | 122.5159 | 122.5113 | 62.4847 | -122.7356
45.1875 | 122.8867 | -62.2925 | 60.2783 | -0.00022891 | -0.058962 | 0.12807 | 0.029614 | 0.038632 | -0.033596 | -0.02396 | 7.627e-05 | -0.0082822 | 0.030362 | 0.060047 | -0.018337 | -0.023456 | 60.347 | -62.3062 | 0.004578 | -62.4756 | 60.2325 | -62.3245 | -62.2559 | 0.027466 | 0.036621 | -62.6907 | 60.2051 | 60.1593 | -62.233 | -62.4664 | -0.032044 | 0.036621 | -0.045776 | -0.013733 | -0.18311 | -0.21973 | 0.068665 | 0.059509 | -0.17395 | -0.073242 | 62.3199 | -0.39825 | -0.2243 | -0.11902 | 122.525 | 122.6395 | 62.2971 | -122.5342 | 122.4976 | 122.4518 | 62.3291 | -122.7448
46.9688 | 122.8363 | -62.3383 | 60.3149 | -0.00022891 | -0.058535 | 0.12807 | 0.031964 | 0.039913 | -0.040219 | -0.024173 | 0.015335 | -0.012982 | 0.031217 | 0.057697 | -0.025814 | -0.023456 | 60.4752 | -62.0728 | 0.13275 | -62.3611 | 60.1868 | -62.2559 | -62.1964 | 0.11444 | 0.15564 | -62.4527 | 60.1776 | 60.1501 | -62.1872 | -62.3886 | 0.082398 | 0.14191 | -0.12817 | 0.2655 | -0.022888 | -0.16479 | 0.16022 | 0.15106 | -0.050354 | -0.13733 | 62.4527 | -0.11444 | -0.064087 | -0.16479 | 122.525 | 122.8134 | 62.471 | -122.5113 | 122.5159 | 122.4884 | 62.4939 | -122.7036
48.7344 | 122.8088 | -62.3245 | 60.3195 | 0.01503 | -0.061312 | 0.12743 | 0.029401 | 0.039486 | -0.04086 | -0.026523 | 7.627e-05 | -0.01405 | 0.028653 | 0.061115 | -0.023251 | -0.025592 | 60.4294 | -62.1414 | 0.086975 | -62.3749 | 60.1868 | -62.2742 | -62.2009 | 0.09613 | 0.11902 | -62.4939 | 60.1959 | 60.1776 | -62.1368 | -62.3657 | 0.050354 | 0.1236 | -0.13275 | 0.18311 | -0.050354 | -0.17395 | 0.10986 | 0.18768 | -0.041199 | -0.1236 | 62.4207 | -0.16937 | -0.12817 | -0.14191 | 122.5113 | 122.7539 | 62.4115 | -122.5204 | 122.5204 | 122.5021 | 62.4435 | -122.6852
50.4531 | 122.8134 | -62.3245 | 60.3241 | -0.00022891 | -0.060671 | 0.12893 | 0.026196 | 0.037564 | -0.035519 | -0.024387 | 7.627e-05 | -0.011914 | 0.026731 | 0.060047 | -0.019192 | -0.023883 | 60.4706 | -62.1231 | 0.11444 | -62.3749 | 60.1868 | -62.265 | -62.2192 | 0.1236 | 0.16479 | -62.5122 | 60.1501 | 60.1227 | -62.1872 | -62.3795 | 0.059509 | 0.10529 | -0.13733 | 0.20142 | -0.050354 | -0.15564 | 0.14648 | 0.13733 | -0.054932 | -0.17395 | 62.4481 | -0.18768 | -0.13275 | -0.20142 | 122.5113 | 122.7951 | 62.439 | -122.5433 | 122.4747 | 122.4472 | 62.4893 | -122.7036
52.2188 | 122.8592 | -62.3199 | 60.26 | -0.00022891 | -0.058321 | 0.127 | 0.030042 | 0.037991 | -0.030392 | -0.023533 | 0.0077058 | -0.0080686 | 0.028867 | 0.061756 | -0.020687 | -0.025165 | 60.3287 | -62.3016 | -0.013733 | -62.4802 | 60.2142 | -62.3474 | -62.265 | 0.032043 | 0.027466 | -62.6816 | 60.1959 | 60.1318 | -62.2375 | -62.4252 | -0.027466 | 0.054931 | -0.045777 | 0.01831 | -0.16022 | -0.21515 | 0.068664 | 0.082397 | -0.10529 | -0.064087 | 62.352 | -0.36163 | -0.25635 | -0.12817 | 122.5342 | 122.6486 | 62.3062 | -122.525 | 122.5159 | 122.4518 | 62.3474 | -122.6852
53.9844 | 122.9004 | -62.2925 | 60.2783 | 0.0074006 | -0.058108 | 0.12828 | 0.028974 | 0.038845 | -0.03381 | -0.024173 | 7.627e-05 | -0.010632 | 0.027585 | 0.059406 | -0.021114 | -0.023242 | 60.4294 | -62.1414 | 0.07782 | -62.384 | 60.2005 | -62.3199 | -62.2101 | 0.13275 | 0.17853 | -62.5259 | 60.1639 | 60.1135 | -62.1872 | -62.3932 | -0.027466 | 0.082397 | -0.07782 | 0.15106 | -0.091553 | -0.17395 | 0.15106 | 0.10528 | -0.10071 | -0.11444 | 62.4252 | -0.23346 | -0.13275 | -0.16479 | 122.493 | 122.7219 | 62.3703 | -122.4884 | 122.4564 | 122.406 | 62.471 | -122.6715
55.75 | 122.8134 | -62.3108 | 60.3149 | -0.00022891 | -0.060244 | 0.13213 | 0.034528 | 0.039486 | -0.041073 | -0.025882 | 7.627e-05 | -0.011273 | 0.028867 | 0.059193 | -0.022823 | -0.02132 | 60.4523 | -62.1231 | 0.10071 | -62.3657 | 60.2234 | -62.2787 | -62.1689 | 0.10071 | 0.12817 | -62.4802 | 60.173 | 60.1868 | -62.1506 | -62.352 | 0.032043 | 0.14191 | -0.091552 | 0.18768 | -0.054932 | -0.19684 | 0.13733 | 0.16022 | -0.041199 | -0.14191 | 62.4115 | -0.16937 | -0.12817 | -0.12817 | 122.5342 | 122.7631 | 62.4115 | -122.4838 | 122.4838 | 122.4976 | 62.439 | -122.6669
57.5312 | 122.8043 | -62.3062 | 60.2692 | -0.00022891 | -0.056826 | 0.12914 | 0.032605 | 0.040341 | -0.040005 | -0.024173 | 0.015335 | -0.011486 | 0.032071 | 0.062397 | -0.024105 | -0.023669 | 60.4889 | -62.0956 | 0.16479 | -62.352 | 60.2097 | -62.2787 | -62.1918 | 0.10529 | 0.13733 | -62.4664 | 60.141 | 60.1456 | -62.1689 | -62.3657 | 0.027465 | 0.11444 | -0.059509 | 0.21057 | -0.045777 | -0.16022 | 0.21973 | 0.13733 | -0.05951 | -0.12817 | 62.4115 | -0.16022 | -0.10071 | -0.1236 | 122.5159 | 122.7951 | 62.471 | -122.4609 | 122.4472 | 122.4518 | 62.4435 | -122.6349
59.2344 | 122.818 | -62.3199 | 60.2509 | -0.00022891 | -0.058748 | 0.12957 | 0.031964 | 0.0397 | -0.036587 | -0.026951 | 7.627e-05 | -0.0093502 | 0.029935 | 0.060047 | -0.019833 | -0.022601 | 60.3653 | -62.2375 | 0.036621 | -62.4527 | 60.2234 | -62.3245 | -62.2604 | 0 | 0.022888 | -62.645 | 60.1868 | 60.1501 | -62.2238 | -62.4252 | -0.004578 | 0.059509 | -0.027465 | 0.082397 | -0.13275 | -0.19226 | 0.11444 | 0.09613 | -0.10529 | -0.064086 | 62.3199 | -0.32501 | -0.21973 | -0.10071 | 122.5433 | 122.6852 | 62.3566 | -122.5113 | 122.5067 | 122.4701 | 62.3428 | -122.6761
61.0312 | 122.7585 | -62.3611 | 60.3149 | -0.00022891 | -0.058962 | 0.13021 | 0.030255 | 0.037136 | -0.037228 | -0.023746 | 7.627e-05 | -0.013623 | 0.027799 | 0.059193 | -0.020687 | -0.023242 | 60.4431 | -62.1323 | 0.12817 | -62.3795 | 60.1776 | -62.2879 | -62.2101 | 0.041199 | 0.082397 | -62.5717 | 60.1593 | 60.1501 | -62.2192 | -62.4207 | 0.073242 | 0.15106 | -0.13733 | 0.22888 | -0.018311 | -0.16937 | 0.12817 | 0.14191 | -0.059509 | -0.15564 | 62.4023 | -0.21057 | -0.15106 | -0.16479 | 122.5388 | 122.8043 | 62.4893 | -122.525 | 122.5204 | 122.5113 | 62.4435 | -122.7356
62.8281 | 122.8226 | -62.3154 | 60.3058 | 0.0074006 | -0.057253 | 0.12914 | 0.03111 | 0.040341 | -0.039364 | -0.025455 | 0.0077058 | -0.010632 | 0.02844 | 0.059193 | -0.024319 | -0.023456 | 60.466 | -62.1002 | 0.12817 | -62.3611 | 60.228 | -62.2559 | -62.2055 | 0.09613 | 0.12817 | -62.4847 | 60.1913 | 60.1593 | -62.1552 | -62.3703 | 0.05951 | 0.10986 | -0.07782 | 0.21515 | -0.045776 | -0.15564 | 0.16022 | 0.16022 | -0.054931 | -0.11444 | 62.4115 | -0.16937 | -0.11444 | -0.14648 | 122.5433 | 122.7814 | 62.4435 | -122.5113 | 122.5067 | 122.4747 | 62.4435 | -122.6761
64.5469 | 122.7631 | -62.3291 | 60.3058 | -0.00022891 | -0.058108 | 0.12871 | 0.030255 | 0.040341 | -0.035946 | -0.025882 | 0.0077058 | -0.0117 | 0.028867 | 0.059834 | -0.022396 | -0.023456 | 60.466 | -62.1002 | 0.16479 | -62.352 | 60.1685 | -62.2787 | -62.2009 | 0.086975 | 0.12817 | -62.5076 | 60.1822 | 60.1273 | -62.1872 | -62.4069 | 0.050354 | 0.12817 | -0.13733 | 0.22888 | -0.022888 | -0.15106 | 0.16022 | 0.14191 | -0.077819 | -0.1236 | 62.4161 | -0.17853 | -0.10071 | -0.17853 | 122.4976 | 122.7951 | 62.4939 | -122.5067 | 122.5113 | 122.4564 | 62.4573 | -122.7127
66.3281 | 122.8363 | -62.3016 | 60.3012 | -0.00022891 | -0.060885 | 0.12893 | 0.032178 | 0.038204 | -0.035305 | -0.02396 | 7.627e-05 | -0.013195 | 0.028013 | 0.061115 | -0.022183 | -0.025378 | 60.4706 | -62.1185 | 0.1236 | -62.3703 | 60.1868 | -62.2879 | -62.2101 | 0.1236 | 0.17395 | -62.5076 | 60.1547 | 60.1273 | -62.1964 | -62.3932 | 0.013733 | 0.091553 | -0.11444 | 0.18311 | -0.068664 | -0.16022 | 0.16937 | 0.10529 | -0.091552 | -0.14648 | 62.4252 | -0.20599 | -0.11444 | -0.17395 | 122.4884 | 122.7722 | 62.4252 | -122.5113 | 122.4564 | 122.4289 | 62.4756 | -122.6944
68.1094 | 122.8226 | -62.3108 | 60.2966 | -0.00022891 | -0.060671 | 0.12764 | 0.030896 | 0.035641 | -0.039151 | -0.024601 | -0.0075532 | -0.013409 | 0.027372 | 0.058979 | -0.023678 | -0.022388 | 60.4614 | -62.0956 | 0.1236 | -62.3474 | 60.2142 | -62.2513 | -62.1872 | 0.11444 | 0.13275 | -62.4619 | 60.1593 | 60.1501 | -62.1689 | -62.3566 | 0.059509 | 0.1236 | -0.082398 | 0.21515 | -0.036621 | -0.16022 | 0.1648 | 0.14191 | -0.045776 | -0.13733 | 62.4252 | -0.15106 | -0.10529 | -0.14648 | 122.525 | 122.7722 | 62.4344 | -122.4838 | 122.4701 | 122.4609 | 62.4435 | -122.6532
69.8125 | 122.85 | -62.3199 | 60.2325 | -0.015487 | -0.053622 | 0.12423 | 0.031751 | 0.039486 | -0.031247 | -0.022892 | -0.015182 | -0.0067868 | 0.029294 | 0.062611 | -0.02026 | -0.024097 | 60.4065 | -62.2147 | 0.09613 | -62.4344 | 60.1776 | -62.352 | -62.2696 | 0.07782 | 0.086975 | -62.6175 | 60.141 | 60.0723 | -62.2421 | -62.4527 | -0.032044 | 0.050354 | -0.054932 | 0.10529 | -0.11444 | -0.16479 | 0.17395 | 0.07782 | -0.13275 | -0.091553 | 62.3978 | -0.29755 | -0.1648 | -0.16022 | 122.4976 | 122.7264 | 62.4161 | -122.5021 | 122.4609 | 122.3923 | 62.4069 | -122.6852
71.5938 | 122.8409 | -62.3428 | 60.2646 | -0.00022891 | -0.052981 | 0.12764 | 0.029401 | 0.037564 | -0.031887 | -0.021824 | 7.627e-05 | -0.010418 | 0.029508 | 0.061756 | -0.018978 | -0.023669 | 60.3287 | -62.2604 | 0.036621 | -62.4756 | 60.2005 | -62.3611 | -62.265 | 0.018311 | 0.059509 | -62.6587 | 60.1685 | 60.1364 | -62.2604 | -62.4481 | -0.018311 | 0.077819 | -0.064087 | 0.082397 | -0.13275 | -0.21057 | 0.064087 | 0.082397 | -0.10529 | -0.09613 | 62.3611 | -0.31586 | -0.21057 | -0.12817 | 122.5433 | 122.6715 | 62.3795 | -122.5296 | 122.5113 | 122.4792 | 62.4023 | -122.7127
73.375 | 122.8912 | -62.2833 | 60.2737 | -0.0078584 | -0.058108 | 0.12978 | 0.029828 | 0.039059 | -0.036587 | -0.021824 | 7.627e-05 | -0.010418 | 0.027158 | 0.060688 | -0.021114 | -0.02132 | 60.4065 | -62.1597 | 0.082397 | -62.384 | 60.2005 | -62.3154 | -62.2009 | 0.12817 | 0.16022 | -62.5122 | 60.1685 | 60.1364 | -62.1872 | -62.384 | -0.032044 | 0.082397 | -0.073243 | 0.1236 | -0.10071 | -0.18311 | 0.13275 | 0.09613 | -0.10071 | -0.10529 | 62.4115 | -0.22888 | -0.12817 | -0.13733 | 122.4838 | 122.6898 | 62.3657 | -122.4747 | 122.4518 | 122.4197 | 62.4435 | -122.6578
75.1562 | 122.8638 | -62.3108 | 60.2463 | -0.00022891 | -0.057467 | 0.12807 | 0.032819 | 0.036923 | -0.035092 | -0.022464 | 7.627e-05 | -0.011914 | 0.029935 | 0.058766 | -0.022823 | -0.021533 | 60.3195 | -62.2421 | 0.059509 | -62.4619 | 60.2234 | -62.3154 | -62.2513 | -0.004578 | 0.041199 | -62.6358 | 60.1868 | 60.1639 | -62.2375 | -62.439 | -0.004578 | 0.059509 | -0.022888 | 0.068665 | -0.15106 | -0.21057 | 0.073242 | 0.073242 | -0.12817 | -0.059509 | 62.3062 | -0.32501 | -0.19684 | -0.082398 | 122.5342 | 122.6303 | 62.3703 | -122.4976 | 122.4976 | 122.4747 | 62.352 | -122.6852
76.875 | 122.7997 | -62.3154 | 60.3149 | -0.00022891 | -0.061953 | 0.12999 | 0.033887 | 0.037564 | -0.042782 | -0.024387 | 7.627e-05 | -0.012341 | 0.029935 | 0.060047 | -0.024105 | -0.020892 | 60.3882 | -62.146 | 0.059509 | -62.384 | 60.2142 | -62.2604 | -62.1918 | 0.045776 | 0.091553 | -62.5305 | 60.173 | 60.1639 | -62.1368 | -62.3932 | 0.054932 | 0.1236 | -0.10071 | 0.16937 | -0.068664 | -0.19226 | 0.073243 | 0.17853 | -0.077819 | -0.14191 | 62.3611 | -0.21515 | -0.13733 | -0.15106 | 122.5296 | 122.7036 | 62.3749 | -122.5067 | 122.4884 | 122.4792 | 62.4069 | -122.7081
78.6562 | 122.8546 | -62.3016 | 60.2875 | 0.01503 | -0.05704 | 0.12722 | 0.02876 | 0.038418 | -0.034237 | -0.022464 | 7.627e-05 | -0.005505 | 0.026944 | 0.062611 | -0.018337 | -0.023669 | 60.3333 | -62.2513 | 0.022888 | -62.4664 | 60.1776 | -62.3154 | -62.2833 | 0.022888 | 0.054932 | -62.6678 | 60.1868 | 60.1593 | -62.2421 | -62.4527 | -0.013733 | 0.018311 | -0.10986 | 0.050354 | -0.16479 | -0.18311 | 0.045776 | 0.05951 | -0.15106 | -0.10071 | 62.3245 | -0.36621 | -0.21515 | -0.12817 | 122.4792 | 122.6349 | 62.3245 | -122.5708 | 122.4884 | 122.4609 | 62.3566 | -122.7402
80.4375 | 122.8958 | -62.2787 | 60.2463 | 0.0074006 | -0.059176 | 0.12658 | 0.031751 | 0.0397 | -0.03616 | -0.024173 | -0.0075532 | -0.011059 | 0.027158 | 0.058338 | -0.022183 | -0.023242 | 60.3699 | -62.2284 | 0.032043 | -62.4252 | 60.2188 | -62.3154 | -62.2192 | 0.091553 | 0.11902 | -62.5534 | 60.1501 | 60.1685 | -62.1826 | -62.3795 | -0.036621 | 0.05951 | -0.027466 | 0.050354 | -0.14648 | -0.20599 | 0.1236 | 0.096131 | -0.10071 | -0.096131 | 62.3703 | -0.27466 | -0.17395 | -0.07782 | 122.4976 | 122.6486 | 62.3108 | -122.4655 | 122.4289 | 122.4472 | 62.3978 | -122.6257
82.1875 | 122.7905 | -62.3245 | 60.2783 | -0.00022891 | -0.058321 | 0.12893 | 0.034528 | 0.039059 | -0.041501 | -0.027164 | 0.015335 | -0.015332 | 0.029508 | 0.060688 | -0.024746 | -0.023456 | 60.4477 | -62.1048 | 0.1236 | -62.3428 | 60.2051 | -62.2513 | -62.178 | 0.086975 | 0.13275 | -62.4619 | 60.1639 | 60.1593 | -62.1414 | -62.3749 | 0.073242 | 0.14648 | -0.073242 | 0.21973 | -0.01831 | -0.16479 | 0.16937 | 0.18311 | -0.050354 | -0.11444 | 62.4115 | -0.13733 | -0.086975 | -0.11902 | 122.5296 | 122.7722 | 62.4481 | -122.4564 | 122.4884 | 122.4838 | 62.4573 | -122.6532
83.9219 | 122.7448 | -62.352 | 60.2829 | -0.00022891 | -0.05704 | 0.12871 | 0.031751 | 0.038845 | -0.038723 | -0.02631 | -0.0075532 | -0.012127 | 0.031858 | 0.060688 | -0.022396 | -0.022174 | 60.379 | -62.2101 | 0.07782 | -62.4252 | 60.1868 | -62.3016 | -62.2421 | 0.004578 | 0.022888 | -62.6083 | 60.2005 | 60.1593 | -62.2101 | -62.4527 | 0.050354 | 0.10986 | -0.09613 | 0.14191 | -0.073242 | -0.18311 | 0.09613 | 0.14191 | -0.10071 | -0.082398 | 62.3566 | -0.25635 | -0.15564 | -0.1236 | 122.5388 | 122.731 | 62.4298 | -122.525 | 122.5525 | 122.5113 | 62.3749 | -122.7356
85.7031 | 122.7997 | -62.3062 | 60.2966 | 0.0074006 | -0.058962 | 0.13363 | 0.03346 | 0.036709 | -0.040432 | -0.027164 | 7.627e-05 | -0.014477 | 0.028226 | 0.057911 | -0.025601 | -0.022601 | 60.4568 | -62.0636 | 0.14191 | -62.3428 | 60.1639 | -62.2513 | -62.178 | 0.10071 | 0.15106 | -62.4481 | 60.1639 | 60.1135 | -62.1826 | -62.3566 | 0.054931 | 0.12817 | -0.13275 | 0.24261 | -0.036621 | -0.16479 | 0.16022 | 0.1236 | -0.050354 | -0.13275 | 62.4069 | -0.14191 | -0.091553 | -0.18311 | 122.4701 | 122.7631 | 62.4481 | -122.4747 | 122.4701 | 122.4197 | 62.4573 | -122.6532
87.4844 | 122.8317 | -62.2787 | 60.2966 | 0.0074006 | -0.059389 | 0.12636 | 0.030042 | 0.039486 | -0.036587 | -0.024173 | 7.627e-05 | -0.0099912 | 0.027158 | 0.060261 | -0.021328 | -0.024097 | 60.466 | -62.1185 | 0.11444 | -62.3657 | 60.1593 | -62.2467 | -62.1735 | 0.12817 | 0.16479 | -62.4847 | 60.1501 | 60.1227 | -62.1597 | -62.3795 | 0.032044 | 0.10529 | -0.13733 | 0.16022 | -0.086975 | -0.19226 | 0.16937 | 0.11902 | -0.10071 | -0.14648 | 62.4069 | -0.20599 | -0.10529 | -0.17395 | 122.4381 | 122.7448 | 62.3932 | -122.4701 | 122.4289 | 122.4014 | 62.4435 | -122.6761
89.25 | 122.8775 | -62.2879 | 60.2783 | -0.00022891 | -0.054262 | 0.12636 | 0.033032 | 0.038632 | -0.036587 | -0.024173 | 0.0077058 | -0.012768 | 0.030149 | 0.060902 | -0.018978 | -0.023883 | 60.4385 | -62.1735 | 0.086975 | -62.3749 | 60.1776 | -62.2742 | -62.2009 | 0.13733 | 0.15564 | -62.5351 | 60.1593 | 60.1227 | -62.1826 | -62.3611 | 0.013733 | 0.086975 | -0.10071 | 0.11444 | -0.086975 | -0.17395 | 0.16022 | 0.10529 | -0.073242 | -0.11902 | 62.4252 | -0.24719 | -0.17395 | -0.15564 | 122.4655 | 122.7264 | 62.3749 | -122.4792 | 122.4472 | 122.4106 | 62.4435 | -122.6395
90.9531 | 122.8043 | -62.2925 | 60.3058 | 0.01503 | -0.057253 | 0.1285 | 0.03111 | 0.037991 | -0.039792 | -0.026096 | 0.0077058 | -0.013623 | 0.028867 | 0.060474 | -0.023464 | -0.023029 | 60.4385 | -62.0911 | 0.11444 | -62.3474 | 60.2234 | -62.2559 | -62.1964 | 0.086975 | 0.11902 | -62.471 | 60.173 | 60.1501 | -62.1414 | -62.3566 | 0.036621 | 0.09613 | -0.082397 | 0.20142 | -0.054932 | -0.15106 | 0.13275 | 0.15106 | -0.064087 | -0.13275 | 62.3795 | -0.17853 | -0.11444 | -0.15564 | 122.5159 | 122.731 | 62.4069 | -122.5021 | 122.4655 | 122.4426 | 62.4115 | -122.6624
92.7188 | 122.7493 | -62.3108 | 60.3149 | 0.0074006 | -0.060457 | 0.12722 | 0.032178 | 0.038204 | -0.039578 | -0.027805 | 0.0077058 | -0.010846 | 0.02844 | 0.060688 | -0.024105 | -0.022601 | 60.4065 | -62.1552 | 0.082397 | -62.3795 | 60.2234 | -62.2375 | -62.1826 | 0.059509 | 0.10529 | -62.5397 | 60.1913 | 60.1776 | -62.178 | -62.3611 | 0.073242 | 0.12817 | -0.091552 | 0.15564 | -0.068665 | -0.19684 | 0.091553 | 0.13275 | -0.050354 | -0.1236 | 62.3703 | -0.22888 | -0.17853 | -0.13733 | 122.5342 | 122.7173 | 62.3932 | -122.4976 | 122.5021 | 122.4884 | 62.4161 | -122.6761
94.5 | 122.7448 | -62.3383 | 60.2646 | -0.00022891 | -0.055971 | 0.12893 | 0.032178 | 0.038418 | -0.035092 | -0.024173 | -0.0075532 | -0.0080686 | 0.027585 | 0.059834 | -0.021969 | -0.025378 | 60.3745 | -62.233 | 0.068665 | -62.4619 | 60.2097 | -62.3016 | -62.2421 | 0 | 0.022888 | -62.6129 | 60.1913 | 60.1685 | -62.2284 | -62.439 | 0.036621 | 0.096131 | -0.054931 | 0.10529 | -0.1236 | -0.21973 | 0.10986 | 0.10986 | -0.10071 | -0.073242 | 62.3383 | -0.27466 | -0.17395 | -0.09613 | 122.5479 | 122.7127 | 62.4069 | -122.5067 | 122.5296 | 122.5067 | 62.3611 | -122.7036
96.2188 | 122.7356 | -62.3062 | 60.2966 | -0.00022891 | -0.059603 | 0.12935 | 0.032819 | 0.039913 | -0.037655 | -0.026737 | 0.0077058 | -0.012768 | 0.028867 | 0.058125 | -0.022396 | -0.024738 | 60.4568 | -62.0819 | 0.16022 | -62.3474 | 60.1685 | -62.2467 | -62.1826 | 0.073242 | 0.14648 | -62.4847 | 60.1501 | 60.0998 | -62.1735 | -62.3795 | 0.059509 | 0.1236 | -0.12817 | 0.2243 | -0.041199 | -0.16479 | 0.16022 | 0.13275 | -0.073243 | -0.14648 | 62.3795 | -0.17853 | -0.10529 | -0.19684 | 122.4747 | 122.7631 | 62.4664 | -122.4792 | 122.4564 | 122.406 | 62.4527 | -122.6761
98.0156 | 122.7676 | -62.2879 | 60.3149 | -0.00022891 | -0.057894 | 0.12722 | 0.029401 | 0.038204 | -0.036801 | -0.024387 | 7.627e-05 | -0.013409 | 0.025235 | 0.058338 | -0.02261 | -0.02196 | 60.4523 | -62.0911 | 0.10529 | -62.352 | 60.173 | -62.2787 | -62.2009 | 0.11902 | 0.15564 | -62.4939 | 60.1501 | 60.1135 | -62.1643 | -62.3474 | 0.009155 | 0.086975 | -0.14191 | 0.19684 | -0.064087 | -0.15106 | 0.13733 | 0.1236 | -0.059509 | -0.16479 | 62.4069 | -0.20599 | -0.14648 | -0.20142 | 122.4609 | 122.7402 | 62.3932 | -122.5159 | 122.438 | 122.4014 | 62.4435 | -122.6624
99.7344 | 122.7493 | -62.3245 | 60.2829 | -0.00022891 | -0.060457 | 0.12999 | 0.030469 | 0.038204 | -0.037228 | -0.025028 | -0.0075532 | -0.012982 | 0.028653 | 0.05727 | -0.02261 | -0.022174 | 60.4431 | -62.0636 | 0.16479 | -62.3657 | 60.1822 | -62.2604 | -62.1872 | 0.07782 | 0.13733 | -62.4985 | 60.141 | 60.1227 | -62.1643 | -62.3657 | 0.064087 | 0.13733 | -0.10071 | 0.26092 | -0.041199 | -0.17853 | 0.16022 | 0.16022 | -0.041199 | -0.14191 | 62.4023 | -0.17395 | -0.13275 | -0.16022 | 122.5067 | 122.7676 | 62.4893 | -122.4701 | 122.4655 | 122.4472 | 62.4619 | -122.6486
101.5156 | 122.8271 | -62.3062 | 60.2554 | 0.0074006 | -0.058321 | 0.12551 | 0.02876 | 0.036923 | -0.032101 | -0.025455 | 7.627e-05 | -0.0095638 | 0.030149 | 0.061329 | -0.01791 | -0.024951 | 60.3378 | -62.265 | 0 | -62.4664 | 60.2142 | -62.3291 | -62.233 | 0.004578 | 0.032043 | -62.677 | 60.1822 | 60.1501 | -62.2284 | -62.4527 | -0.022889 | 0.073242 | -0.041199 | 0.041198 | -0.16022 | -0.23346 | 0.082398 | 0.077819 | -0.14648 | -0.073242 | 62.3108 | -0.37079 | -0.2243 | -0.10529 | 122.5204 | 122.644 | 62.3062 | -122.4884 | 122.4884 | 122.4564 | 62.3383 | -122.7081
103.2812 | 122.7539 | -62.2925 | 60.3287 | 0.0074006 | -0.063021 | 0.12978 | 0.030896 | 0.037564 | -0.041714 | -0.025242 | -0.015182 | -0.013409 | 0.027158 | 0.058552 | -0.02261 | -0.02196 | 60.3973 | -62.1231 | 0.073242 | -62.3703 | 60.2097 | -62.2513 | -62.178 | 0.054932 | 0.09613 | -62.4939 | 60.1593 | 60.1685 | -62.1414 | -62.352 | 0.041198 | 0.11444 | -0.11902 | 0.16937 | -0.07782 | -0.19226 | 0.068665 | 0.15106 | -0.05951 | -0.16937 | 62.3474 | -0.20142 | -0.14191 | -0.16022 | 122.5021 | 122.6898 | 62.3657 | -122.5067 | 122.4518 | 122.4609 | 62.3886 | -122.6807
104.9844 | 122.7676 | -62.3062 | 60.2921 | -0.00022891 | -0.060457 | 0.13063 | 0.032392 | 0.040127 | -0.040432 | -0.025669 | 0.0077058 | -0.012127 | 0.027799 | 0.060047 | -0.025387 | -0.020679 | 60.3973 | -62.1323 | 0.082397 | -62.3749 | 60.2097 | -62.2559 | -62.178 | 0.059509 | 0.10071 | -62.5031 | 60.1822 | 60.1501 | -62.1368 | -62.3566 | 0.050354 | 0.12817 | -0.082397 | 0.17395 | -0.068665 | -0.19684 | 0.10529 | 0.16937 | -0.050354 | -0.10986 | 62.3657 | -0.19684 | -0.14648 | -0.14191 | 122.5159 | 122.7036 | 62.3886 | -122.4701 | 122.4884 | 122.4564 | 62.4069 | -122.6486
106.7812 | 122.7859 | -62.2971 | 60.3012 | 0.0074006 | -0.059389 | 0.12914 | 0.032178 | 0.038632 | -0.038937 | -0.025028 | -0.0075532 | -0.012555 | 0.028013 | 0.060261 | -0.022823 | -0.022601 | 60.4752 | -62.0911 | 0.12817 | -62.3383 | 60.1913 | -62.2238 | -62.1506 | 0.10529 | 0.13275 | -62.4756 | 60.1685 | 60.173 | -62.1597 | -62.3611 | 0.073242 | 0.14648 | -0.10986 | 0.20599 | -0.041199 | -0.18768 | 0.17395 | 0.13733 | -0.064087 | -0.13275 | 62.4023 | -0.17853 | -0.11444 | -0.12817 | 122.4884 | 122.7722 | 62.4252 | -122.4518 | 122.4655 | 122.4701 | 62.4298 | -122.6624
108.5781 | 122.8729 | -62.2879 | 60.2509 | 0.0074006 | -0.057253 | 0.12487 | 0.029401 | 0.039273 | -0.034665 | -0.025242 | 0.0077058 | -0.0091366 | 0.027372 | 0.061543 | -0.021114 | -0.027087 | 60.4385 | -62.1735 | 0.073242 | -62.3795 | 60.1639 | -62.2787 | -62.2009 | 0.13275 | 0.15564 | -62.5031 | 60.1593 | 60.141 | -62.178 | -62.3566 | 0.009155 | 0.086975 | -0.086975 | 0.11444 | -0.091553 | -0.17853 | 0.18768 | 0.10986 | -0.068664 | -0.091552 | 62.4207 | -0.21515 | -0.14648 | -0.10986 | 122.4518 | 122.7264 | 62.3611 | -122.4518 | 122.4472 | 122.4289 | 62.4435 | -122.6074
110.2969 | 122.8363 | -62.3154 | 60.2371 | 0.0074006 | -0.058108 | 0.12828 | 0.031323 | 0.038204 | -0.03381 | -0.023319 | -0.0075532 | -0.007855 | 0.030149 | 0.060047 | -0.021542 | -0.025378 | 60.3378 | -62.2467 | 0.045776 | -62.4298 | 60.2097 | -62.3199 | -62.2467 | 0.013733 | 0.022888 | -62.6266 | 60.1959 | 60.1364 | -62.2559 | -62.4298 | -0.004577 | 0.068665 | -0.027466 | 0.068665 | -0.11444 | -0.18311 | 0.10071 | 0.05951 | -0.11444 | -0.041199 | 62.3291 | -0.31128 | -0.19684 | -0.10071 | 122.525 | 122.6532 | 62.3611 | -122.4838 | 122.5113 | 122.4518 | 62.3383 | -122.6669
112.0469 | 122.85 | -62.3199 | 60.2371 | 0.0074006 | -0.051272 | 0.12935 | 0.029614 | 0.039486 | -0.033596 | -0.024173 | 0.0077058 | -0.0093502 | 0.032071 | 0.060902 | -0.019192 | -0.023242 | 60.3287 | -62.2696 | -0.013733 | -62.4481 | 60.1868 | -62.3291 | -62.2375 | 0.022888 | 0.050354 | -62.6633 | 60.173 | 60.141 | -62.2192 | -62.4252 | -0.009156 | 0.082397 | -0.050354 | 0.050354 | -0.12817 | -0.21057 | 0.091552 | 0.10071 | -0.10529 | -0.064087 | 62.3428 | -0.34332 | -0.23804 | -0.096131 | 122.5067 | 122.6486 | 62.3062 | -122.4747 | 122.493 | 122.4609 | 62.3703 | -122.6624
113.7656 | 122.7585 | -62.3108 | 60.2829 | -0.0078584 | -0.060885 | 0.12786 | 0.03111 | 0.039059 | -0.041714 | -0.025028 | 7.627e-05 | -0.015118 | 0.02844 | 0.058125 | -0.025601 | -0.023456 | 60.466 | -62.0407 | 0.14648 | -62.3245 | 60.1776 | -62.2192 | -62.1689 | 0.086975 | 0.16022 | -62.4619 | 60.1456 | 60.1181 | -62.1552 | -62.3749 | 0.091553 | 0.14191 | -0.10529 | 0.27008 | -0.013733 | -0.15564 | 0.1831 | 0.15564 | -0.064087 | -0.13733 | 62.3978 | -0.15106 | -0.086975 | -0.1648 | 122.4884 | 122.7768 | 62.4573 | -122.4518 | 122.4564 | 122.4289 | 62.471 | -122.6578
115.5469 | 122.7859 | -62.2925 | 60.2737 | -0.00022891 | -0.058748 | 0.13042 | 0.031751 | 0.040341 | -0.040005 | -0.025669 | 7.627e-05 | -0.015118 | 0.029722 | 0.059193 | -0.025173 | -0.022174 | 60.4523 | -62.0544 | 0.15106 | -62.3337 | 60.173 | -62.2375 | -62.1689 | 0.10986 | 0.16479 | -62.439 | 60.1181 | 60.1364 | -62.1506 | -62.3657 | 0.054931 | 0.1236 | -0.10071 | 0.23804 | -0.041199 | -0.16479 | 0.17853 | 0.14191 | -0.073243 | -0.15564 | 62.4023 | -0.14649 | -0.073242 | -0.13733 | 122.4655 | 122.7448 | 62.4435 | -122.4426 | 122.4106 | 122.4289 | 62.4573 | -122.6395
117.3281 | 122.7448 | -62.3199 | 60.3149 | -0.00022891 | -0.054476 | 0.12999 | 0.032819 | 0.0397 | -0.037869 | -0.024601 | -0.015182 | -0.012127 | 0.028653 | 0.057057 | -0.020901 | -0.023883 | 60.3241 | -62.2147 | 0.045776 | -62.4344 | 60.2005 | -62.3199 | -62.2284 | -0.009155 | 0.009155 | -62.5992 | 60.1913 | 60.1318 | -62.233 | -62.4023 | 0 | 0.091552 | -0.11444 | 0.10529 | -0.11444 | -0.20599 | 0.009156 | 0.086975 | -0.082398 | -0.1236 | 62.3108 | -0.27924 | -0.19684 | -0.1831 | 122.5204 | 122.644 | 62.3657 | -122.5433 | 122.5113 | 122.4518 | 62.3291 | -122.7173
119.0312 | 122.8638 | -62.265 | 60.2463 | 0.0074006 | -0.059389 | 0.12999 | 0.027905 | 0.038418 | -0.031033 | -0.023746 | -0.0075532 | -0.008923 | 0.026517 | 0.059193 | -0.018551 | -0.022174 | 60.3195 | -62.2513 | -0.022888 | -62.4481 | 60.2417 | -62.3016 | -62.2467 | 0.050354 | 0.064087 | -62.6266 | 60.1685 | 60.1135 | -62.2055 | -62.4069 | -0.036621 | 0.018311 | -0.004578 | 0.013733 | -0.18311 | -0.20142 | 0.073242 | 0.05951 | -0.14191 | -0.07782 | 62.3154 | -0.36163 | -0.21973 | -0.13275 | 122.5067 | 122.5845 | 62.2421 | -122.493 | 122.4335 | 122.3785 | 62.3291 | -122.6532
120.8125 | 122.7951 | -62.3062 | 60.228 | -0.00022891 | -0.05469 | 0.12957 | 0.031751 | 0.037564 | -0.035305 | -0.02396 | -0.0075532 | -0.0095638 | 0.028013 | 0.061115 | -0.023037 | -0.022174 | 60.3104 | -62.2421 | 0.045776 | -62.4344 | 60.1959 | -62.3062 | -62.233 | 0 | 0.004578 | -62.6175 | 60.1776 | 60.1501 | -62.2055 | -62.4115 | 0 | 0.073242 | -0.032043 | 0.064087 | -0.12817 | -0.20142 | 0.082398 | 0.10071 | -0.10529 | -0.050354 | 62.3062 | -0.31128 | -0.20599 | -0.07782 | 122.5021 | 122.6166 | 62.352 | -122.4609 | 122.4838 | 122.4564 | 62.3108 | -122.6395
122.5781 | 122.8317 | -62.2971 | 60.2142 | 0.01503 | -0.057253 | 0.12658 | 0.029828 | 0.038632 | -0.03616 | -0.023105 | 0.015335 | -0.0091366 | 0.027799 | 0.060261 | -0.018765 | -0.023029 | 60.2966 | -62.2559 | -0.009155 | -62.4573 | 60.1959 | -62.3199 | -62.233 | 0.027466 | 0.041199 | -62.645 | 60.1593 | 60.1318 | -62.2192 | -62.4435 | -0.022888 | 0.064087 | -0.01831 | 0.041199 | -0.16022 | -0.2243 | 0.082398 | 0.07782 | -0.14648 | -0.054931 | 62.3245 | -0.3479 | -0.20142 | -0.082397 | 122.493 | 122.5937 | 62.2879 | -122.4472 | 122.4564 | 122.4289 | 62.3383 | -122.6578
124.3594 | 122.8363 | -62.3291 | 60.2051 | 0.0074006 | -0.05234 | 0.12572 | 0.029828 | 0.039486 | -0.033169 | -0.023746 | 0.0077058 | -0.0093502 | 0.029508 | 0.061756 | -0.021114 | -0.023456 | 60.347 | -62.1964 | 0.091553 | -62.4435 | 60.1593 | -62.3245 | -62.2604 | 0.073242 | 0.09613 | -62.59 | 60.1227 | 60.1318 | -62.2284 | -62.4207 | 0.004578 | 0.068665 | -0.045776 | 0.13275 | -0.11444 | -0.1831 | 0.14191 | 0.10071 | -0.091552 | -0.082397 | 62.4023 | -0.26093 | -0.16937 | -0.073242 | 122.4884 | 122.6761 | 62.4207 | -122.4655 | 122.4518 | 122.4609 | 62.4252 | -122.6257
126.125 | 122.7264 | -62.3108 | 60.2737 | -0.00022891 | -0.055331 | 0.12871 | 0.033887 | 0.038204 | -0.041928 | -0.024173 | 7.627e-05 | -0.011914 | 0.029722 | 0.059834 | -0.025173 | -0.022174 | 60.4202 | -62.0819 | 0.15564 | -62.3428 | 60.1547 | -62.2559 | -62.1735 | 0.07782 | 0.13275 | -62.4893 | 60.1273 | 60.141 | -62.1643 | -62.3611 | 0.054932 | 0.13733 | -0.11902 | 0.22888 | -0.032043 | -0.16937 | 0.14648 | 0.14648 | -0.050354 | -0.14649 | 62.3886 | -0.17853 | -0.12817 | -0.13275 | 122.4655 | 122.731 | 62.4664 | -122.4472 | 122.438 | 122.4518 | 62.4435 | -122.6349
127.8281 | 122.8455 | -62.3016 | 60.2188 | -0.00022891 | -0.055117 | 0.12828 | 0.030896 | 0.039913 | -0.035946 | -0.023319 | 0.015335 | -0.0093502 | 0.029081 | 0.05962 | -0.020046 | -0.023669 | 60.347 | -62.1964 | 0.086975 | -62.4115 | 60.1913 | -62.3291 | -62.2147 | 0.041199 | 0.091553 | -62.5854 | 60.1318 | 60.1089 | -62.233 | -62.4252 | -0.027466 | 0.086975 | -0.027466 | 0.10529 | -0.10986 | -0.19684 | 0.12817 | 0.068665 | -0.1236 | -0.086975 | 62.3428 | -0.28381 | -0.16022 | -0.10986 | 122.493 | 122.6486 | 62.3886 | -122.4335 | 122.4335 | 122.4106 | 62.3932 | -122.644
129.6094 | 122.8409 | -62.2833 | 60.2005 | -0.00022891 | -0.053835 | 0.12722 | 0.030255 | 0.041622 | -0.034878 | -0.023746 | 7.627e-05 | -0.010418 | 0.029081 | 0.063679 | -0.020474 | -0.023883 | 60.347 | -62.2055 | 0.068665 | -62.4207 | 60.1776 | -62.3108 | -62.265 | 0.050354 | 0.07782 | -62.59 | 60.1593 | 60.1181 | -62.2375 | -62.4252 | -0.027466 | 0.01831 | -0.022888 | 0.07782 | -0.13733 | -0.15564 | 0.14648 | 0.045776 | -0.14191 | -0.041198 | 62.3337 | -0.3067 | -0.16479 | -0.082397 | 122.4609 | 122.6303 | 62.352 | -122.4655 | 122.4426 | 122.4014 | 62.3611 | -122.6257
131.3906 | 122.7997 | -62.3154 | 60.228 | -0.00022891 | -0.056826 | 0.12722 | 0.029614 | 0.039273 | -0.035519 | -0.022892 | -0.0075532 | -0.0093502 | 0.029722 | 0.06197 | -0.02026 | -0.021747 | 60.2966 | -62.2513 | 0 | -62.4481 | 60.1913 | -62.3245 | -62.233 | -0.009155 | 0.041199 | -62.6404 | 60.1547 | 60.1913 | -62.233 | -62.3978 | -0.009155 | 0.082398 | -0.036621 | 0.064087 | -0.13275 | -0.21515 | 0.068665 | 0.082398 | -0.082397 | -0.073242 | 62.3062 | -0.32501 | -0.24262 | -0.036621 | 122.5067 | 122.612 | 62.3154 | -122.4609 | 122.4701 | 122.5067 | 62.3566 | -122.6257
133.1562 | 122.7127 | -62.3245 | 60.2783 | -0.00022891 | -0.058962 | 0.12828 | 0.02876 | 0.039486 | -0.040432 | -0.025242 | 0.0077058 | -0.012982 | 0.028867 | 0.059193 | -0.021542 | -0.023883 | 60.3195 | -62.1735 | 0.068665 | -62.4207 | 60.1639 | -62.2925 | -62.2101 | -0.013733 | 0.022888 | -62.5854 | 60.1685 | 60.1685 | -62.2238 | -62.3886 | 0.032044 | 0.11444 | -0.11444 | 0.15106 | -0.09613 | -0.21057 | 0.041199 | 0.10071 | -0.064087 | -0.10986 | 62.3108 | -0.26093 | -0.19684 | -0.10986 | 122.4884 | 122.644 | 62.3932 | -122.4884 | 122.493 | 122.493 | 62.3474 | -122.6669
134.8906 | 122.7173 | -62.3383 | 60.26 | -0.00022891 | -0.05768 | 0.12679 | 0.032392 | 0.039059 | -0.039578 | -0.025669 | 0.015335 | -0.0084958 | 0.028867 | 0.059834 | -0.025601 | -0.02132 | 60.3287 | -62.1964 | 0.059509 | -62.4115 | 60.2051 | -62.2742 | -62.2147 | -0.018311 | 0.009155 | -62.6038 | 60.1685 | 60.1685 | -62.2147 | -62.4023 | 0.064087 | 0.1236 | -0.054932 | 0.14191 | -0.073242 | -0.19684 | 0.068664 | 0.1236 | -0.064087 | -0.091553 | 62.3199 | -0.2655 | -0.20142 | -0.091553 | 122.5433 | 122.6669 | 62.3978 | -122.4747 | 122.5067 | 122.5067 | 62.3474 | -122.6624
136.6875 | 122.7585 | -62.3062 | 60.2554 | -0.00022891 | -0.05704 | 0.12978 | 0.032605 | 0.040341 | -0.040005 | -0.026096 | -0.0075532 | -0.014477 | 0.027372 | 0.059406 | -0.026241 | -0.022601 | 60.4431 | -62.059 | 0.14648 | -62.3337 | 60.1822 | -62.2284 | -62.1368 | 0.10986 | 0.16479 | -62.4207 | 60.1547 | 60.1501 | -62.1597 | -62.3291 | 0.077819 | 0.16937 | -0.073242 | 0.24719 | -0.027466 | -0.19684 | 0.18768 | 0.14648 | -0.022889 | -0.10071 | 62.4161 | -0.11444 | -0.091552 | -0.10529 | 122.4884 | 122.7493 | 62.4527 | -122.3923 | 122.4609 | 122.4564 | 62.471 | -122.5845
138.4062 | 122.7173 | -62.2833 | 60.3104 | -0.0078584 | -0.059176 | 0.12893 | 0.029187 | 0.040768 | -0.039578 | -0.026951 | -0.0075532 | -0.013623 | 0.025022 | 0.05962 | -0.022183 | -0.024097 | 60.4111 | -62.1185 | 0.086975 | -62.3703 | 60.173 | -62.2101 | -62.1597 | 0.07782 | 0.13275 | -62.5076 | 60.1547 | 60.1547 | -62.1506 | -62.3428 | 0.073242 | 0.1236 | -0.13733 | 0.16479 | -0.086975 | -0.21057 | 0.10071 | 0.13275 | -0.059509 | -0.15564 | 62.3611 | -0.2243 | -0.16479 | -0.15564 | 122.4564 | 122.6944 | 62.3703 | -122.4701 | 122.438 | 122.438 | 62.4161 | -122.6532
140.1719 | 122.7127 | -62.3016 | 60.2554 | -0.00022891 | -0.058108 | 0.12807 | 0.031537 | 0.039273 | -0.039151 | -0.025882 | 0.0077058 | -0.010418 | 0.028653 | 0.05962 | -0.025601 | -0.025165 | 60.4431 | -62.0911 | 0.16937 | -62.3337 | 60.1822 | -62.2375 | -62.1826 | 0.073242 | 0.1236 | -62.4756 | 60.1639 | 60.1273 | -62.1689 | -62.352 | 0.064087 | 0.11902 | -0.073242 | 0.21057 | -0.032043 | -0.15106 | 0.18768 | 0.13275 | -0.050354 | -0.091553 | 62.3749 | -0.17395 | -0.1236 | -0.12817 | 122.4838 | 122.7448 | 62.471 | -122.438 | 122.4655 | 122.4289 | 62.4252 | -122.6074
141.9531 | 122.8226 | -62.3016 | 60.2051 | -0.015487 | -0.053408 | 0.12743 | 0.030469 | 0.036068 | -0.032742 | -0.02396 | 7.627e-05 | -0.0093502 | 0.03079 | 0.060474 | -0.020046 | -0.024524 | 60.3561 | -62.1964 | 0.086975 | -62.4161 | 60.1868 | -62.3199 | -62.2375 | 0.068665 | 0.086975 | -62.5946 | 60.141 | 60.1181 | -62.2284 | -62.4298 | -0.01831 | 0.064087 | -0.01831 | 0.10529 | -0.11444 | -0.17853 | 0.15106 | 0.073242 | -0.12817 | -0.064087 | 62.3703 | -0.29297 | -0.16479 | -0.086975 | 122.4884 | 122.6578 | 62.3886 | -122.4426 | 122.4426 | 122.4197 | 62.3886 | -122.6349
143.7188 | 122.8363 | -62.2787 | 60.2371 | -0.00022891 | -0.055331 | 0.12807 | 0.02876 | 0.038632 | -0.034451 | -0.022464 | 7.627e-05 | -0.011914 | 0.029294 | 0.060047 | -0.020474 | -0.023456 | 60.347 | -62.1826 | 0.027466 | -62.3978 | 60.1822 | -62.2925 | -62.1964 | 0.09613 | 0.12817 | -62.5351 | 60.1501 | 60.1044 | -62.1918 | -62.3566 | -0.013732 | 0.082398 | -0.054932 | 0.096131 | -0.11902 | -0.20142 | 0.10986 | 0.086976 | -0.077819 | -0.086976 | 62.3749 | -0.25635 | -0.17853 | -0.13275 | 122.4609 | 122.6257 | 62.3062 | -122.4335 | 122.4289 | 122.3831 | 62.4069 | -122.5937
145.4375 | 122.7905 | -62.2971 | 60.2554 | -0.00022891 | -0.054903 | 0.12572 | 0.030683 | 0.037777 | -0.034024 | -0.022251 | 7.627e-05 | -0.0091366 | 0.028867 | 0.061543 | -0.022183 | -0.022174 | 60.347 | -62.1918 | 0.068665 | -62.4252 | 60.1547 | -62.3291 | -62.2238 | 0.050354 | 0.073242 | -62.6266 | 60.1273 | 60.1501 | -62.1964 | -62.4252 | -0.032044 | 0.073242 | -0.10071 | 0.10529 | -0.12817 | -0.20142 | 0.091553 | 0.10071 | -0.12817 | -0.12817 | 62.3474 | -0.32959 | -0.20142 | -0.10529 | 122.4518 | 122.644 | 62.3657 | -122.4792 | 122.4243 | 122.4472 | 62.3703 | -122.6807
147.1875 | 122.7127 | -62.2971 | 60.2966 | -0.00022891 | -0.06238 | 0.12978 | 0.030896 | 0.037564 | -0.041928 | -0.024387 | 7.627e-05 | -0.015973 | 0.028867 | 0.060688 | -0.024319 | -0.024097 | 60.3928 | -62.1048 | 0.091553 | -62.3566 | 60.1776 | -62.2513 | -62.146 | 0.07782 | 0.11902 | -62.4939 | 60.1501 | 60.1547 | -62.1414 | -62.3474 | 0.045776 | 0.15106 | -0.11902 | 0.19226 | -0.059509 | -0.21057 | 0.09613 | 0.15564 | -0.050354 | -0.14648 | 62.3749 | -0.19684 | -0.14648 | -0.14191 | 122.4747 | 122.6898 | 62.3886 | -122.4426 | 122.4472 | 122.4518 | 62.4161 | -122.644
148.9844 | 122.7219 | -62.3016 | 60.3287 | -0.00022891 | -0.060885 | 0.1285 | 0.031537 | 0.037564 | -0.042141 | -0.025455 | 0.0077058 | -0.013623 | 0.030362 | 0.057911 | -0.023464 | -0.023242 | 60.3973 | -62.114 | 0.082397 | -62.352 | 60.1456 | -62.2009 | -62.1689 | 0.082397 | 0.10529 | -62.5122 | 60.1501 | 60.141 | -62.146 | -62.3611 | 0.10071 | 0.13275 | -0.1831 | 0.18768 | -0.050354 | -0.18311 | 0.068665 | 0.15564 | -0.059509 | -0.17853 | 62.384 | -0.21057 | -0.15106 | -0.18768 | 122.4472 | 122.699 | 62.384 | -122.4976 | 122.4518 | 122.4426 | 62.4069 | -122.6898
150.7031 | 122.7402 | -62.2833 | 60.3058 | -0.00022891 | -0.054049 | 0.12871 | 0.034741 | 0.037991 | -0.037442 | -0.02396 | 0.0077058 | -0.0117 | 0.030149 | 0.060474 | -0.02261 | -0.024951 | 60.4202 | -62.0911 | 0.10071 | -62.3383 | 60.173 | -62.2513 | -62.1597 | 0.1236 | 0.16479 | -62.4619 | 60.0998 | 60.0998 | -62.1506 | -62.3703 | 0.032043 | 0.1236 | -0.13275 | 0.19226 | -0.054932 | -0.17853 | 0.11444 | 0.13275 | -0.086975 | -0.20599 | 62.4069 | -0.17853 | -0.091553 | -0.20599 | 122.4564 | 122.7036 | 62.384 | -122.4655 | 122.3831 | 122.3831 | 62.4481 | -122.6761
152.4844 | 122.8409 | -62.2742 | 60.2646 | -0.015487 | -0.057467 | 0.12658 | 0.029614 | 0.036282 | -0.034237 | -0.025882 | 7.627e-05 | -0.011486 | 0.029081 | 0.059193 | -0.019406 | -0.025806 | 60.4156 | -62.1048 | 0.091553 | -62.3383 | 60.1456 | -62.2696 | -62.1689 | 0.14191 | 0.16937 | -62.4847 | 60.141 | 60.0906 | -62.1735 | -62.3428 | 0.004578 | 0.10529 | -0.11902 | 0.16937 | -0.064087 | -0.16937 | 0.15106 | 0.10071 | -0.068664 | -0.1236 | 62.4161 | -0.21057 | -0.14191 | -0.17395 | 122.4197 | 122.6898 | 62.3657 | -122.4335 | 122.4152 | 122.3648 | 62.4435 | -122.6074
154.2656 | 122.7493 | -62.2833 | 60.2783 | 0.0074006 | -0.064944 | 0.12764 | 0.028119 | 0.038418 | -0.04086 | -0.026096 | 7.627e-05 | -0.013623 | 0.026731 | 0.060474 | -0.022823 | -0.022174 | 60.4202 | -62.0682 | 0.11902 | -62.3291 | 60.1776 | -62.2238 | -62.1506 | 0.10071 | 0.11902 | -62.4435 | 60.1501 | 60.1456 | -62.146 | -62.3291 | 0.059509 | 0.13275 | -0.10071 | 0.21515 | -0.045777 | -0.17853 | 0.14191 | 0.13733 | -0.045777 | -0.12817 | 62.384 | -0.16022 | -0.11444 | -0.13275 | 122.4609 | 122.7036 | 62.4023 | -122.4289 | 122.4335 | 122.4289 | 62.4023 | -122.6074
155.9688 | 122.7173 | -62.3062 | 60.2921 | -0.00022891 | -0.052767 | 0.1285 | 0.034955 | 0.038418 | -0.035946 | -0.025669 | 7.627e-05 | -0.011059 | 0.029935 | 0.060688 | -0.024532 | -0.026019 | 60.3378 | -62.1689 | 0.068665 | -62.3978 | 60.2005 | -62.2879 | -62.2192 | -0.013733 | 0 | -62.5992 | 60.1868 | 60.1364 | -62.2192 | -62.3749 | 0.01831 | 0.086975 | -0.091553 | 0.13733 | -0.091553 | -0.17853 | 0.045777 | 0.086975 | -0.068665 | -0.10529 | 62.2925 | -0.29297 | -0.2243 | -0.15564 | 122.5067 | 122.644 | 62.3749 | -122.5113 | 122.493 | 122.4426 | 62.3062 | -122.6669
157.7344 | 122.8088 | -62.3154 | 60.1822 | 0.0074006 | -0.05469 | 0.127 | 0.026196 | 0.038418 | -0.032528 | -0.023319 | -0.0075532 | -0.0080686 | 0.028867 | 0.060261 | -0.019619 | -0.022388 | 60.3561 | -62.178 | 0.07782 | -62.4115 | 60.1501 | -62.3016 | -62.2604 | 0.073242 | 0.086975 | -62.5946 | 60.1364 | 60.0998 | -62.2009 | -62.4161 | 0.013733 | 0.054932 | -0.032044 | 0.13733 | -0.09613 | -0.15106 | 0.17395 | 0.11444 | -0.10071 | -0.045776 | 62.3886 | -0.27923 | -0.17853 | -0.082398 | 122.4655 | 122.6715 | 62.3932 | -122.4426 | 122.4518 | 122.4152 | 62.4023 | -122.5983
159.5156 | 122.7539 | -62.2559 | 60.2646 | 0.0074006 | -0.060885 | 0.12957 | 0.032605 | 0.036923 | -0.043637 | -0.025242 | 0.0077058 | -0.012768 | 0.028653 | 0.059193 | -0.023464 | -0.023456 | 60.4111 | -62.0499 | 0.1236 | -62.3199 | 60.1868 | -62.2375 | -62.146 | 0.09613 | 0.13733 | -62.4435 | 60.1181 | 60.1318 | -62.1414 | -62.3474 | 0.01831 | 0.10986 | -0.077819 | 0.20599 | -0.064087 | -0.17395 | 0.14648 | 0.11444 | -0.091553 | -0.14648 | 62.352 | -0.18768 | -0.09613 | -0.13275 | 122.4426 | 122.6669 | 62.3795 | -122.4106 | 122.374 | 122.3877 | 62.3932 | -122.612
161.2344 | 122.8226 | -62.2787 | 60.2325 | -0.00022891 | -0.056185 | 0.12807 | 0.028333 | 0.039273 | -0.032742 | -0.025882 | 7.627e-05 | -0.0084958 | 0.027585 | 0.059193 | -0.021969 | -0.021106 | 60.3058 | -62.2467 | -0.027466 | -62.4435 | 60.2005 | -62.2925 | -62.2375 | 0.045776 | 0.036621 | -62.6129 | 60.1456 | 60.141 | -62.1964 | -62.4023 | -0.013732 | 0.041199 | -0.032044 | 0.032044 | -0.16479 | -0.20599 | 0.073242 | 0.082398 | -0.1236 | -0.086975 | 62.3245 | -0.33417 | -0.21057 | -0.091553 | 122.4792 | 122.5845 | 62.2513 | -122.4701 | 122.4243 | 122.4197 | 62.3154 | -122.6349
163.0156 | 122.6898 | -62.3199 | 60.2783 | -0.0078584 | -0.055758 | 0.13149 | 0.03346 | 0.037777 | -0.039364 | -0.026737 | 0.015335 | -0.012982 | 0.029081 | 0.057911 | -0.024746 | -0.021747 | 60.3699 | -62.1094 | 0.1236 | -62.352 | 60.1639 | -62.2467 | -62.1735 | 0.018311 | 0.07782 | -62.5488 | 60.1501 | 60.1364 | -62.178 | -62.3932 | 0.073242 | 0.14648 | -0.11444 | 0.21057 | -0.032044 | -0.17853 | 0.091553 | 0.14191 | -0.073242 | -0.12817 | 62.3383 | -0.22888 | -0.15564 | -0.14191 | 122.4838 | 122.6898 | 62.4435 | -122.4518 | 122.4701 | 122.4564 | 62.3978 | -122.6715
164.7969 | 122.7631 | -62.2925 | 60.228 | -0.00022891 | -0.056399 | 0.12572 | 0.031323 | 0.03735 | -0.034024 | -0.023533 | 7.627e-05 | -0.010846 | 0.029294 | 0.061756 | -0.020687 | -0.022601 | 60.3149 | -62.2559 | 0.004578 | -62.4435 | 60.173 | -62.3062 | -62.233 | 0.013733 | 0.032043 | -62.6633 | 60.141 | 60.1364 | -62.2009 | -62.4115 | -0.013733 | 0.059509 | -0.054931 | 0.036621 | -0.15106 | -0.21057 | 0.086975 | 0.091552 | -0.11902 | -0.086975 | 62.3062 | -0.37079 | -0.25177 | -0.091552 | 122.4655 | 122.6074 | 62.2971 | -122.4609 | 122.4335 | 122.4289 | 62.3245 | -122.6395
166.5938 | 122.7631 | -62.2879 | 60.2783 | 0.0074006 | -0.058748 | 0.13063 | 0.032178 | 0.036282 | -0.04086 | -0.027378 | 7.627e-05 | -0.013836 | 0.027585 | 0.060474 | -0.023678 | -0.02431 | 60.3928 | -62.0911 | 0.10529 | -62.3337 | 60.1822 | -62.233 | -62.1506 | 0.082397 | 0.13733 | -62.4481 | 60.1547 | 60.1456 | -62.1277 | -62.3383 | 0.054932 | 0.13733 | -0.09613 | 0.19684 | -0.045776 | -0.1831 | 0.11444 | 0.16022 | -0.050354 | -0.1236 | 62.3703 | -0.16022 | -0.10986 | -0.13275 | 122.4701 | 122.6807 | 62.3932 | -122.4289 | 122.4426 | 122.4335 | 62.4252 | -122.6166
168.375 | 122.7631 | -62.2833 | 60.2692 | 0.0074006 | -0.058321 | 0.12807 | 0.034101 | 0.038418 | -0.041501 | -0.023746 | -0.0075532 | -0.013409 | 0.028013 | 0.057697 | -0.024746 | -0.022815 | 60.3745 | -62.1094 | 0.086975 | -62.3245 | 60.1959 | -62.2192 | -62.1597 | 0.082397 | 0.1236 | -62.439 | 60.1456 | 60.141 | -62.1368 | -62.3474 | 0.064087 | 0.1236 | -0.073242 | 0.17395 | -0.041199 | -0.16479 | 0.10529 | 0.14648 | -0.064087 | -0.1236 | 62.3657 | -0.15564 | -0.091553 | -0.12817 | 122.4792 | 122.6578 | 62.3703 | -122.4289 | 122.4289 | 122.4243 | 62.4069 | -122.6166
170.0781 | 122.7356 | -62.2971 | 60.2692 | -0.0078584 | -0.061526 | 0.12893 | 0.031323 | 0.039059 | -0.040432 | -0.024601 | 7.627e-05 | -0.014904 | 0.027158 | 0.058125 | -0.021114 | -0.023029 | 60.379 | -62.1277 | 0.064087 | -62.3566 | 60.2005 | -62.2055 | -62.1552 | 0.068665 | 0.086975 | -62.4893 | 60.1639 | 60.141 | -62.1414 | -62.3566 | 0.091553 | 0.14191 | -0.068665 | 0.16937 | -0.059509 | -0.20142 | 0.10986 | 0.15564 | -0.059509 | -0.10529 | 62.3657 | -0.19226 | -0.13275 | -0.12817 | 122.4976 | 122.6761 | 62.3611 | -122.4243 | 122.4609 | 122.438 | 62.384 | -122.6257
171.8438 | 122.7264 | -62.2879 | 60.2875 | 0.0074006 | -0.060457 | 0.12871 | 0.031323 | 0.039273 | -0.037228 | -0.024387 | 7.627e-05 | -0.012555 | 0.028226 | 0.059834 | -0.019192 | -0.02431 | 60.4294 | -62.0544 | 0.11444 | -62.3474 | 60.1547 | -62.2238 | -62.1323 | 0.12817 | 0.16937 | -62.4619 | 60.1273 | 60.1044 | -62.1552 | -62.3611 | 0.064087 | 0.15564 | -0.13275 | 0.23346 | -0.059509 | -0.21515 | 0.14191 | 0.13275 | -0.073242 | -0.16022 | 62.4161 | -0.17395 | -0.10071 | -0.18311 | 122.4426 | 122.7173 | 62.4023 | -122.4197 | 122.4152 | 122.3923 | 62.4573 | -122.6486
173.625 | 122.8134 | -62.265 | 60.2234 | -0.00022891 | -0.054903 | 0.12593 | 0.034528 | 0.036495 | -0.034878 | -0.025455 | -0.0075532 | -0.0082822 | 0.028013 | 0.058766 | -0.019619 | -0.026447 | 60.3287 | -62.2192 | 0.045776 | -62.4252 | 60.2005 | -62.2833 | -62.233 | 0.004578 | 0.036621 | -62.6083 | 60.1868 | 60.1135 | -62.2192 | -62.4069 | -0.01831 | 0.032044 | -0.022889 | 0.045777 | -0.16022 | -0.19226 | 0.10529 | 0.045777 | -0.14191 | -0.036621 | 62.2696 | -0.34332 | -0.20142 | -0.10986 | 122.4655 | 122.5937 | 62.3108 | -122.4564 | 122.4518 | 122.3785 | 62.3016 | -122.6303
175.3281 | 122.7859 | -62.2833 | 60.2692 | 0.0074006 | -0.06003 | 0.12807 | 0.029187 | 0.038632 | -0.037228 | -0.023533 | 7.627e-05 | -0.011273 | 0.026304 | 0.061543 | -0.021328 | -0.024738 | 60.4248 | -62.0728 | 0.10986 | -62.3199 | 60.1456 | -62.2284 | -62.1643 | 0.13733 | 0.1831 | -62.4847 | 60.1364 | 60.0998 | -62.146 | -62.3474 | 0.054931 | 0.11902 | -0.1236 | 0.21057 | -0.036621 | -0.15564 | 0.15564 | 0.13733 | -0.064087 | -0.13275 | 62.4207 | -0.20142 | -0.13733 | -0.16937 | 122.4289 | 122.7081 | 62.3932 | -122.4335 | 122.4197 | 122.3831 | 62.4664 | -122.6166
177.0938 | 122.7219 | -62.2925 | 60.2783 | -0.0078584 | -0.056612 | 0.12722 | 0.035809 | 0.038632 | -0.039364 | -0.026523 | -0.0075532 | -0.0117 | 0.026731 | 0.059834 | -0.026028 | -0.023883 | 60.4477 | -62.0544 | 0.16022 | -62.3108 | 60.1639 | -62.2147 | -62.1506 | 0.12817 | 0.16479 | -62.4298 | 60.1273 | 60.141 | -62.146 | -62.3566 | 0.077819 | 0.14191 | -0.11444 | 0.23804 | -0.018311 | -0.16022 | 0.16937 | 0.14648 | -0.064087 | -0.15106 | 62.4207 | -0.13733 | -0.073243 | -0.13733 | 122.4564 | 122.7402 | 62.4527 | -122.4289 | 122.4197 | 122.4335 | 62.4573 | -122.6349
178.8906 | 122.6807 | -62.3245 | 60.2692 | 0.0074006 | -0.060671 | 0.127 | 0.02876 | 0.037991 | -0.03851 | -0.026523 | 0.0077058 | -0.0091366 | 0.028013 | 0.059406 | -0.02261 | -0.024097 | 60.3928 | -62.1002 | 0.11902 | -62.3611 | 60.1547 | -62.2604 | -62.1918 | 0.022888 | 0.059509 | -62.5488 | 60.1501 | 60.141 | -62.1826 | -62.3886 | 0.064087 | 0.13275 | -0.11444 | 0.2243 | -0.036621 | -0.16937 | 0.1236 | 0.14191 | -0.064087 | -0.11902 | 62.3474 | -0.2243 | -0.16022 | -0.12817 | 122.4792 | 122.7173 | 62.4435 | -122.4609 | 122.4747 | 122.4655 | 62.384 | -122.6578
180.5938 | 122.818 | -62.2559 | 60.2051 | -0.0078584 | -0.057467 | 0.12871 | 0.027265 | 0.038632 | -0.033169 | -0.022892 | 0.0077058 | -0.0091366 | 0.026944 | 0.060688 | -0.019192 | -0.024097 | 60.3149 | -62.2284 | -0.013733 | -62.4207 | 60.1959 | -62.2971 | -62.2101 | 0.054932 | 0.054932 | -62.6083 | 60.173 | 60.1181 | -62.1964 | -62.4069 | -0.041199 | 0.045776 | -0.009155 | 0.027465 | -0.16479 | -0.21057 | 0.10986 | 0.059509 | -0.15106 | -0.032043 | 62.3108 | -0.35248 | -0.20142 | -0.086975 | 122.4518 | 122.5708 | 62.2421 | -122.4152 | 122.4289 | 122.374 | 62.3108 | -122.612
182.3594 | 122.7814 | -62.2879 | 60.2097 | 0.0074006 | -0.057467 | 0.12658 | 0.030469 | 0.038418 | -0.034237 | -0.025028 | 7.627e-05 | -0.010205 | 0.030576 | 0.059834 | -0.020901 | -0.02132 | 60.2966 | -62.265 | -0.013733 | -62.4435 | 60.1913 | -62.2879 | -62.2238 | 0.013733 | 0.041199 | -62.6404 | 60.1501 | 60.1318 | -62.2055 | -62.4298 | 0 | 0.064087 | -0.018311 | 0.022888 | -0.15564 | -0.21973 | 0.086975 | 0.082398 | -0.14191 | -0.05951 | 62.3016 | -0.35248 | -0.21057 | -0.07782 | 122.4792 | 122.5845 | 62.2742 | -122.4335 | 122.438 | 122.4197 | 62.3291 | -122.6395
184.1562 | 122.8134 | -62.2742 | 60.2005 | 0.0074006 | -0.053622 | 0.12871 | 0.030255 | 0.038418 | -0.035733 | -0.024601 | 7.627e-05 | -0.010205 | 0.030362 | 0.060902 | -0.021969 | -0.02431 | 60.3287 | -62.1597 | 0.082397 | -62.4115 | 60.1593 | -62.3016 | -62.2421 | 0.068665 | 0.091553 | -62.5763 | 60.1135 | 60.1227 | -62.2192 | -62.3932 | -0.027466 | 0.032044 | -0.041198 | 0.11444 | -0.13733 | -0.16937 | 0.12817 | 0.054932 | -0.11902 | -0.086975 | 62.3428 | -0.30212 | -0.18311 | -0.077819 | 122.4335 | 122.6028 | 62.3566 | -122.4426 | 122.3877 | 122.3969 | 62.3657 | -122.5937
185.875 | 122.7676 | -62.2513 | 60.2737 | -0.00022891 | -0.053835 | 0.12679 | 0.034741 | 0.035214 | -0.039578 | -0.023105 | 0.015335 | -0.013195 | 0.029935 | 0.057911 | -0.021114 | -0.022388 | 60.4111 | -62.0865 | 0.10529 | -62.3291 | 60.1456 | -62.2467 | -62.1643 | 0.1236 | 0.17395 | -62.4619 | 60.1181 | 60.1089 | -62.1414 | -62.3428 | 0.004578 | 0.086975 | -0.12817 | 0.1648 | -0.07782 | -0.16479 | 0.13733 | 0.10986 | -0.091552 | -0.15564 | 62.3749 | -0.21057 | -0.11902 | -0.1648 | 122.3969 | 122.6624 | 62.3566 | -122.4381 | 122.3694 | 122.3602 | 62.4252 | -122.6166
187.6562 | 122.7631 | -62.2971 | 60.2051 | 0.0074006 | -0.056826 | 0.12593 | 0.028119 | 0.038418 | -0.033596 | -0.022678 | 0.0077058 | -0.008923 | 0.02844 | 0.062611 | -0.019619 | -0.02196 | 60.2921 | -62.2467 | 0.013733 | -62.4252 | 60.1776 | -62.3016 | -62.2238 | 0.004578 | 0.032043 | -62.6358 | 60.1639 | 60.1501 | -62.2147 | -62.3932 | -0.004578 | 0.073242 | -0.027466 | 0.050354 | -0.12817 | -0.20142 | 0.086975 | 0.082397 | -0.09613 | -0.041199 | 62.3016 | -0.33875 | -0.24262 | -0.054932 | 122.4747 | 122.5891 | 62.3108 | -122.4289 | 122.4609 | 122.4472 | 62.3291 | -122.5983
189.375 | 122.6898 | -62.2787 | 60.2829 | -0.00022891 | -0.056826 | 0.12978 | 0.033887 | 0.037777 | -0.041287 | -0.023746 | 7.627e-05 | -0.01405 | 0.027799 | 0.059193 | -0.025387 | -0.023669 | 60.4019 | -62.0819 | 0.10986 | -62.3383 | 60.141 | -62.2192 | -62.146 | 0.11902 | 0.15106 | -62.4573 | 60.1227 | 60.1456 | -62.1277 | -62.3245 | 0.05951 | 0.13275 | -0.14191 | 0.19684 | -0.059509 | -0.19226 | 0.11902 | 0.15106 | -0.045776 | -0.16022 | 62.3978 | -0.17853 | -0.13275 | -0.13733 | 122.4197 | 122.6807 | 62.3886 | -122.4289 | 122.4014 | 122.4243 | 62.4298 | -122.6074
191.1406 | 122.7493 | -62.3108 | 60.2097 | -0.0078584 | -0.053408 | 0.12828 | 0.032819 | 0.036068 | -0.034451 | -0.026523 | 0.0077058 | -0.010632 | 0.029722 | 0.063038 | -0.021969 | -0.024524 | 60.2966 | -62.2284 | 0.036621 | -62.4207 | 60.1913 | -62.2833 | -62.2055 | -0.004578 | 0 | -62.5992 | 60.1639 | 60.1593 | -62.2101 | -62.3932 | 0.027466 | 0.10529 | -0.018311 | 0.082397 | -0.10986 | -0.21515 | 0.086975 | 0.10071 | -0.082397 | -0.045777 | 62.3062 | -0.28839 | -0.20599 | -0.050354 | 122.5021 | 122.6074 | 62.3474 | -122.4152 | 122.4747 | 122.4701 | 62.3108 | -122.6028
192.9219 | 122.7905 | -62.2833 | 60.2097 | -0.00022891 | -0.05768 | 0.12658 | 0.029187 | 0.036068 | -0.034665 | -0.025669 | 0.0077058 | -0.008923 | 0.030362 | 0.06197 | -0.021114 | -0.024951 | 60.2921 | -62.2604 | -0.022888 | -62.4344 | 60.2051 | -62.2787 | -62.2055 | 0.027466 | 0.045776 | -62.6221 | 60.1547 | 60.1547 | -62.2238 | -62.4161 | 0.004577 | 0.07782 | -0.004578 | 0.022888 | -0.15106 | -0.22888 | 0.082397 | 0.059509 | -0.13275 | -0.054932 | 62.3108 | -0.33875 | -0.20599 | -0.054932 | 122.4884 | 122.5754 | 62.2604 | -122.4152 | 122.438 | 122.438 | 62.3291 | -122.6257
194.7031 | 122.6807 | -62.2925 | 60.2692 | -0.00022891 | -0.055758 | 0.12935 | 0.031537 | 0.038418 | -0.041501 | -0.026951 | 7.627e-05 | -0.012768 | 0.028867 | 0.061115 | -0.023678 | -0.023456 | 60.4111 | -62.0682 | 0.16479 | -62.3154 | 60.173 | -62.2375 | -62.1414 | 0.073242 | 0.1236 | -62.4619 | 60.1364 | 60.1364 | -62.1277 | -62.3566 | 0.054931 | 0.15106 | -0.09613 | 0.2243 | -0.022889 | -0.17395 | 0.14191 | 0.16479 | -0.064087 | -0.13275 | 62.3657 | -0.16937 | -0.10529 | -0.13275 | 122.4655 | 122.7036 | 62.4573 | -122.4106 | 122.4289 | 122.4289 | 62.4161 | -122.6257
196.4219 | 122.7997 | -62.265 | 60.2188 | 0.0074006 | -0.05704 | 0.12957 | 0.02876 | 0.038418 | -0.035946 | -0.025028 | 7.627e-05 | -0.0093502 | 0.028867 | 0.060261 | -0.019619 | -0.023242 | 60.3012 | -62.2421 | -0.027466 | -62.4298 | 60.1685 | -62.3016 | -62.2284 | 0.027466 | 0.054932 | -62.6221 | 60.1639 | 60.1318 | -62.2009 | -62.4115 | -0.036621 | 0.036621 | -0.050354 | 0.022889 | -0.1648 | -0.20142 | 0.082397 | 0.064087 | -0.14648 | -0.054932 | 62.2925 | -0.35706 | -0.21057 | -0.086975 | 122.4335 | 122.5662 | 62.2375 | -122.4472 | 122.4289 | 122.3969 | 62.3199 | -122.6303
198.1875 | 122.7081 | -62.2696 | 60.2875 | -0.015487 | -0.06238 | 0.12807 | 0.033032 | 0.040768 | -0.042569 | -0.026096 | 0.0077058 | -0.014264 | 0.027372 | 0.05962 | -0.026028 | -0.023242 | 60.3607 | -62.1231 | 0.064087 | -62.3337 | 60.1776 | -62.2192 | -62.146 | 0.045776 | 0.10071 | -62.4756 | 60.1547 | 60.1501 | -62.1277 | -62.352 | 0.050354 | 0.1236 | -0.10986 | 0.14648 | -0.064087 | -0.18768 | 0.073242 | 0.14191 | -0.082398 | -0.13275 | 62.3154 | -0.20599 | -0.1236 | -0.13733 | 122.4472 | 122.6303 | 62.3337 | -122.4335 | 122.4243 | 122.4197 | 62.3703 | -122.6395
199.9688 | 122.7814 | -62.2925 | 60.1959 | 0.01503 | -0.055544 | 0.12658 | 0.030683 | 0.038418 | -0.034665 | -0.026523 | 7.627e-05 | -0.008923 | 0.029508 | 0.05962 | -0.020901 | -0.024524 | 60.3058 | -62.2055 | 0.045776 | -62.4252 | 60.1685 | -62.2971 | -62.2375 | 0.004578 | 0.036621 | -62.59 | 60.1639 | 60.1273 | -62.2055 | -62.3886 | -0.004578 | 0.054931 | -0.027466 | 0.086975 | -0.13275 | -0.18768 | 0.10986 | 0.086975 | -0.096131 | -0.032044 | 62.2971 | -0.29755 | -0.20142 | -0.068665 | 122.4609 | 122.5983 | 62.3383 | -122.4335 | 122.4564 | 122.4197 | 62.3291 | -122.5845
201.6875 | 122.7264 | -62.265 | 60.2692 | -0.00022891 | -0.058962 | 0.12893 | 0.033032 | 0.035214 | -0.041287 | -0.02631 | 0.0077058 | -0.015118 | 0.02844 | 0.060688 | -0.026882 | -0.023669 | 60.3973 | -62.0865 | 0.10986 | -62.3199 | 60.1593 | -62.2238 | -62.1368 | 0.073242 | 0.12817 | -62.4298 | 60.1181 | 60.1547 | -62.146 | -62.352 | 0.041199 | 0.12817 | -0.10986 | 0.17853 | -0.054931 | -0.18311 | 0.12817 | 0.11902 | -0.086975 | -0.15106 | 62.3383 | -0.1648 | -0.07782 | -0.11444 | 122.4243 | 122.6624 | 62.3749 | -122.406 | 122.3831 | 122.4197 | 62.3932 | -122.6212
203.4531 | 122.6761 | -62.2833 | 60.2829 | -0.0078584 | -0.060457 | 0.12914 | 0.029828 | 0.034573 | -0.039151 | -0.027805 | -0.0075532 | -0.012341 | 0.027158 | 0.060261 | -0.021969 | -0.024738 | 60.3745 | -62.0911 | 0.091553 | -62.3383 | 60.173 | -62.2147 | -62.1414 | 0.07782 | 0.09613 | -62.4893 | 60.1547 | 60.1456 | -62.1506 | -62.3474 | 0.068664 | 0.14191 | -0.10986 | 0.19226 | -0.054932 | -0.19684 | 0.091553 | 0.13275 | -0.064087 | -0.12817 | 62.3611 | -0.20599 | -0.14191 | -0.13733 | 122.4564 | 122.6578 | 62.3749 | -122.4243 | 122.438 | 122.4289 | 62.3795 | -122.6303
205.2188 | 122.7951 | -62.2559 | 60.2325 | -0.00022891 | -0.057894 | 0.12786 | 0.027692 | 0.037991 | -0.034237 | -0.026951 | 0.0077058 | -0.0117 | 0.026517 | 0.060261 | -0.019406 | -0.022815 | 60.4111 | -62.0865 | 0.091553 | -62.3154 | 60.1318 | -62.2559 | -62.1689 | 0.13275 | 0.17395 | -62.4802 | 60.1227 | 60.0952 | -62.1826 | -62.3566 | 0 | 0.086975 | -0.10071 | 0.16937 | -0.05951 | -0.14648 | 0.17853 | 0.073242 | -0.10071 | -0.10986 | 62.3886 | -0.22431 | -0.1236 | -0.13733 | 122.3877 | 122.6669 | 62.3474 | -122.4014 | 122.3785 | 122.3511 | 62.4298 | -122.5891
207 | 122.6715 | -62.2879 | 60.2692 | -0.00022891 | -0.056826 | 0.12807 | 0.034101 | 0.036495 | -0.037228 | -0.02631 | 7.627e-05 | -0.012341 | 0.030576 | 0.058338 | -0.023037 | -0.023456 | 60.4065 | -62.1002 | 0.082397 | -62.3337 | 60.1822 | -62.2101 | -62.1323 | 0.091553 | 0.12817 | -62.4802 | 60.1456 | 60.1273 | -62.1277 | -62.3383 | 0.07782 | 0.15564 | -0.086975 | 0.18768 | -0.045776 | -0.20142 | 0.13733 | 0.16022 | -0.050354 | -0.1236 | 62.3795 | -0.19226 | -0.14191 | -0.14191 | 122.4701 | 122.6944 | 62.3703 | -122.4014 | 122.4335 | 122.4152 | 62.4161 | -122.6074
208.7812 | 122.7676 | -62.2833 | 60.1959 | -0.0078584 | -0.05469 | 0.12871 | 0.030469 | 0.037991 | -0.031033 | -0.026096 | -0.0075532 | -0.0063596 | 0.030362 | 0.05962 | -0.018765 | -0.026019 | 60.3561 | -62.1918 | 0.059509 | -62.4023 | 60.1501 | -62.2925 | -62.2284 | 0.07782 | 0.10986 | -62.5809 | 60.1227 | 60.1044 | -62.2055 | -62.3932 | -0.009155 | 0.054931 | -0.045777 | 0.091553 | -0.11902 | -0.17395 | 0.16022 | 0.07782 | -0.10986 | -0.073242 | 62.3611 | -0.29755 | -0.18768 | -0.091553 | 122.4335 | 122.6395 | 62.3428 | -122.4243 | 122.406 | 122.3877 | 62.3932 | -122.5891
210.5625 | 122.818 | -62.2559 | 60.2234 | -0.00022891 | -0.057467 | 0.12636 | 0.03111 | 0.038418 | -0.035305 | -0.024814 | 7.627e-05 | -0.010632 | 0.028867 | 0.062183 | -0.02261 | -0.024097 | 60.3378 | -62.178 | 0.041199 | -62.3886 | 60.1685 | -62.2421 | -62.2238 | 0.10986 | 0.13733 | -62.5168 | 60.1501 | 60.141 | -62.1597 | -62.3474 | 0.013733 | 0.032043 | -0.054932 | 0.077819 | -0.13275 | -0.16479 | 0.11444 | 0.09613 | -0.091553 | -0.073243 | 62.3657 | -0.26093 | -0.16937 | -0.082398 | 122.4243 | 122.5937 | 62.2971 | -122.4472 | 122.406 | 122.3969 | 62.3932 | -122.5708
212.2812 | 122.8363 | -62.2559 | 60.2371 | 0.0074006 | -0.057894 | 0.12764 | 0.031323 | 0.040341 | -0.035305 | -0.026096 | 7.627e-05 | -0.0080686 | 0.027799 | 0.061115 | -0.021755 | -0.02196 | 60.3333 | -62.2055 | 0.027466 | -62.3978 | 60.1547 | -62.2513 | -62.1918 | 0.07782 | 0.10986 | -62.5305 | 60.1318 | 60.1227 | -62.1597 | -62.3566 | 0.004577 | 0.064087 | -0.082398 | 0.050354 | -0.14191 | -0.20599 | 0.09613 | 0.09613 | -0.10071 | -0.10529 | 62.3337 | -0.27466 | -0.17395 | -0.11444 | 122.4106 | 122.5891 | 62.2833 | -122.4289 | 122.3877 | 122.3785 | 62.3657 | -122.5937
214.0781 | 122.7951 | -62.2696 | 60.1822 | -0.00022891 | -0.054262 | 0.12508 | 0.035809 | 0.037777 | -0.037655 | -0.024601 | 0.0077058 | -0.007214 | 0.03079 | 0.060047 | -0.023892 | -0.023456 | 60.2966 | -62.1872 | 0.045776 | -62.3978 | 60.1639 | -62.2925 | -62.2192 | 0.022888 | 0.064087 | -62.5854 | 60.1227 | 60.1456 | -62.1918 | -62.4069 | -0.022888 | 0.050354 | -0.018311 | 0.082397 | -0.12817 | -0.17853 | 0.11444 | 0.07782 | -0.13733 | -0.059509 | 62.2925 | -0.31586 | -0.17853 | -0.036621 | 122.4335 | 122.5662 | 62.3154 | -122.4014 | 122.3923 | 122.4152 | 62.3337 | -122.5891
215.7969 | 122.7219 | -62.2696 | 60.2554 | -0.0078584 | -0.056399 | 0.127 | 0.03346 | 0.038418 | -0.043637 | -0.025455 | -0.015182 | -0.014477 | 0.028226 | 0.057484 | -0.025601 | -0.021747 | 60.379 | -62.1048 | 0.10529 | -62.3245 | 60.173 | -62.2101 | -62.146 | 0.091553 | 0.13733 | -62.4344 | 60.141 | 60.1639 | -62.146 | -62.3199 | 0.059509 | 0.1236 | -0.082397 | 0.1648 | -0.054932 | -0.17853 | 0.1236 | 0.1236 | -0.050354 | -0.11444 | 62.3611 | -0.16479 | -0.11444 | -0.091553 | 122.4426 | 122.6486 | 62.3749 | -122.4014 | 122.4106 | 122.4335 | 62.4069 | -122.5754
217.5781 | 122.6578 | -62.2971 | 60.2783 | -0.00022891 | -0.054903 | 0.13106 | 0.033032 | 0.038845 | -0.036374 | -0.025882 | -0.0075532 | -0.014904 | 0.029081 | 0.059406 | -0.023464 | -0.023242 | 60.379 | -62.0911 | 0.13733 | -62.3383 | 60.1318 | -62.2375 | -62.1872 | 0.041199 | 0.086975 | -62.4893 | 60.1135 | 60.1364 | -62.1964 | -62.3566 | 0.059509 | 0.10986 | -0.14648 | 0.20599 | -0.041199 | -0.15106 | 0.10071 | 0.10071 | -0.059509 | -0.16479 | 62.3383 | -0.19226 | -0.13275 | -0.14191 | 122.4289 | 122.6761 | 62.4344 | -122.4655 | 122.4106 | 122.4335 | 62.384 | -122.6349
219.2812 | 122.731 | -62.265 | 60.2417 | -0.00022891 | -0.059389 | 0.12957 | 0.031751 | 0.039059 | -0.041073 | -0.026523 | -0.0075532 | -0.012127 | 0.026944 | 0.05962 | -0.024746 | -0.023883 | 60.4111 | -62.0407 | 0.14191 | -62.3062 | 60.1776 | -62.1964 | -62.1597 | 0.11444 | 0.14648 | -62.4161 | 60.1044 | 60.1364 | -62.1231 | -62.3154 | 0.068665 | 0.10529 | -0.064087 | 0.22431 | -0.041198 | -0.14648 | 0.16937 | 0.14191 | -0.050354 | -0.13733 | 62.3795 | -0.15106 | -0.10071 | -0.10528 | 122.4426 | 122.6761 | 62.4069 | -122.4014 | 122.3694 | 122.4014 | 62.4115 | -122.5571
221.0625 | 122.8088 | -62.2787 | 60.1959 | -0.00022891 | -0.053835 | 0.12508 | 0.031537 | 0.038418 | -0.032956 | -0.024814 | 7.627e-05 | -0.008923 | 0.030149 | 0.059834 | -0.02026 | -0.022174 | 60.3241 | -62.1689 | 0.073242 | -62.3795 | 60.1501 | -62.2879 | -62.233 | 0.068665 | 0.068665 | -62.5626 | 60.1318 | 60.0952 | -62.1964 | -62.4207 | -0.009155 | 0.045777 | -0.045777 | 0.10986 | -0.10071 | -0.14648 | 0.12817 | 0.082398 | -0.14191 | -0.064087 | 62.3474 | -0.28381 | -0.14191 | -0.10071 | 122.4289 | 122.6028 | 62.352 | -122.4289 | 122.4106 | 122.374 | 62.3474 | -122.6166
222.8281 | 122.6669 | -62.2879 | 60.2646 | -0.00022891 | -0.054476 | 0.1285 | 0.032392 | 0.037991 | -0.039151 | -0.025669 | 7.627e-05 | -0.011059 | 0.026304 | 0.060474 | -0.020901 | -0.024097 | 60.3378 | -62.1368 | 0.082397 | -62.3703 | 60.1685 | -62.2742 | -62.1918 | 0.009155 | 0.022888 | -62.5626 | 60.1593 | 60.141 | -62.1826 | -62.3703 | 0.013733 | 0.096131 | -0.09613 | 0.15106 | -0.082397 | -0.17853 | 0.073243 | 0.10529 | -0.082397 | -0.10529 | 62.2971 | -0.27466 | -0.19226 | -0.1236 | 122.4564 | 122.6257 | 62.3703 | -122.4564 | 122.4472 | 122.4289 | 62.3108 | -122.6349
224.6094 | 122.8043 | -62.265 | 60.1913 | 0.0074006 | -0.056826 | 0.12764 | 0.029401 | 0.039273 | -0.03381 | -0.023533 | 0.0077058 | -0.0070004 | 0.027585 | 0.061329 | -0.017483 | -0.022388 | 60.3333 | -62.178 | 0.064087 | -62.3749 | 60.1501 | -62.2971 | -62.2284 | 0.073242 | 0.082397 | -62.5717 | 60.1318 | 60.1181 | -62.2101 | -62.4207 | -0.032043 | 0.036621 | -0.041199 | 0.086975 | -0.10986 | -0.14648 | 0.14191 | 0.054932 | -0.15564 | -0.059509 | 62.3383 | -0.3067 | -0.15106 | -0.073242 | 122.4152 | 122.5983 | 62.3291 | -122.4197 | 122.3969 | 122.3831 | 62.3474 | -122.612
226.3125 | 122.7951 | -62.2604 | 60.1776 | 0.0074006 | -0.053835 | 0.12807 | 0.032392 | 0.037564 | -0.03616 | -0.025028 | 7.627e-05 | -0.010846 | 0.029935 | 0.060474 | -0.020687 | -0.022601 | 60.3058 | -62.1689 | 0.07782 | -62.3749 | 60.1547 | -62.2696 | -62.2421 | 0.036621 | 0.07782 | -62.5626 | 60.1227 | 60.1044 | -62.1918 | -62.3795 | -0.009155 | 0.018311 | -0.022888 | 0.091553 | -0.11444 | -0.13275 | 0.12817 | 0.068665 | -0.11902 | -0.054931 | 62.2971 | -0.30212 | -0.18311 | -0.073242 | 122.4152 | 122.5662 | 62.3383 | -122.4197 | 122.3831 | 122.3648 | 62.3383 | -122.5571
228.0781 | 122.7859 | -62.2879 | 60.2005 | -0.0078584 | -0.05234 | 0.12679 | 0.037091 | 0.037991 | -0.034665 | -0.025242 | -0.0075532 | -0.011059 | 0.032926 | 0.061756 | -0.023251 | -0.02431 | 60.3012 | -62.1689 | 0.091553 | -62.3886 | 60.1593 | -62.3016 | -62.2284 | 0.059509 | 0.091553 | -62.5488 | 60.0998 | 60.1044 | -62.1872 | -62.3932 | -0.013733 | 0.059509 | -0.041198 | 0.11902 | -0.10071 | -0.16022 | 0.10071 | 0.10071 | -0.10529 | -0.10071 | 62.3474 | -0.26093 | -0.15564 | -0.09613 | 122.4472 | 122.5891 | 62.3795 | -122.4289 | 122.3877 | 122.3923 | 62.3795 | -122.5937
229.8594 | 122.7127 | -62.2742 | 60.2509 | 0.0074006 | -0.058321 | 0.12978 | 0.033673 | 0.037991 | -0.04385 | -0.026096 | 7.627e-05 | -0.015759 | 0.02844 | 0.058338 | -0.025173 | -0.022601 | 60.3882 | -62.0132 | 0.15106 | -62.3016 | 60.1501 | -62.2009 | -62.1277 | 0.09613 | 0.16022 | -62.3932 | 60.1318 | 60.1181 | -62.1414 | -62.3428 | 0.073242 | 0.14648 | -0.10071 | 0.26093 | -0.027466 | -0.17395 | 0.13733 | 0.13275 | -0.068664 | -0.11902 | 62.3703 | -0.11902 | -0.050354 | -0.13275 | 122.4243 | 122.6624 | 62.4252 | -122.3785 | 122.406 | 122.3923 | 62.4344 | -122.5937
231.625 | 122.6715 | -62.3016 | 60.2554 | -0.00022891 | -0.054262 | 0.12722 | 0.033032 | 0.035855 | -0.037869 | -0.025882 | 7.627e-05 | -0.011273 | 0.029722 | 0.059406 | -0.021969 | -0.023029 | 60.2783 | -62.1689 | 0.050354 | -62.3932 | 60.1639 | -62.2833 | -62.178 | -0.013733 | 0.013733 | -62.5671 | 60.1501 | 60.1547 | -62.2055 | -62.3703 | 0.018311 | 0.1236 | -0.091553 | 0.13275 | -0.091552 | -0.21515 | 0.022888 | 0.096131 | -0.068664 | -0.10529 | 62.2879 | -0.2655 | -0.19684 | -0.10071 | 122.4655 | 122.58 | 62.352 | -122.4335 | 122.4518 | 122.4564 | 62.3154 | -122.6257
233.3281 | 122.7905 | -62.2696 | 60.1639 | -0.0078584 | -0.054262 | 0.12893 | 0.03346 | 0.038418 | -0.034878 | -0.025028 | 0.0077058 | -0.0093502 | 0.02844 | 0.060474 | -0.022396 | -0.024097 | 60.3058 | -62.178 | 0.064087 | -62.3932 | 60.1501 | -62.3108 | -62.2101 | 0.036621 | 0.082397 | -62.5534 | 60.1181 | 60.1318 | -62.2192 | -62.3795 | -0.041199 | 0.059509 | -0.013733 | 0.091552 | -0.1236 | -0.18311 | 0.14191 | 0.050354 | -0.10986 | -0.045776 | 62.3062 | -0.28381 | -0.17395 | -0.032043 | 122.4197 | 122.5754 | 62.3337 | -122.374 | 122.3877 | 122.4014 | 62.352 | -122.5433
235.1094 | 122.7127 | -62.2787 | 60.2188 | -0.00022891 | -0.055758 | 0.12786 | 0.033246 | 0.038418 | -0.038083 | -0.026523 | -0.0075532 | -0.0095638 | 0.027799 | 0.059834 | -0.021969 | -0.023029 | 60.2921 | -62.2009 | 0.022888 | -62.4115 | 60.1822 | -62.2742 | -62.2192 | 0 | 0.018311 | -62.5809 | 60.1639 | 60.1639 | -62.2009 | -62.384 | 0.004578 | 0.05951 | -0.036621 | 0.07782 | -0.13275 | -0.19226 | 0.073242 | 0.07782 | -0.10529 | -0.054932 | 62.2787 | -0.30212 | -0.19684 | -0.054932 | 122.4609 | 122.5708 | 62.3016 | -122.438 | 122.4426 | 122.4426 | 62.2971 | -122.6028
236.9062 | 122.6532 | -62.2833 | 60.2692 | 0.0074006 | -0.057467 | 0.12572 | 0.034955 | 0.038632 | -0.041714 | -0.025455 | 7.627e-05 | -0.015118 | 0.032285 | 0.059834 | -0.024532 | -0.020679 | 60.379 | -62.0636 | 0.15564 | -62.3154 | 60.1593 | -62.2192 | -62.1506 | 0.073242 | 0.13733 | -62.4481 | 60.0998 | 60.1044 | -62.1552 | -62.3611 | 0.064087 | 0.13275 | -0.10986 | 0.21973 | -0.032044 | -0.16479 | 0.10986 | 0.12817 | -0.07782 | -0.16937 | 62.3566 | -0.1648 | -0.086975 | -0.16479 | 122.4426 | 122.6624 | 62.439 | -122.4197 | 122.3831 | 122.3877 | 62.4207 | -122.6303
238.6875 | 122.7905 | -62.2513 | 60.2325 | -0.00022891 | -0.060457 | 0.12935 | 0.029614 | 0.036709 | -0.037228 | -0.024173 | 0.015335 | -0.012341 | 0.027585 | 0.060261 | -0.020046 | -0.024097 | 60.3516 | -62.1002 | 0.086975 | -62.3154 | 60.1456 | -62.2284 | -62.1643 | 0.1236 | 0.16937 | -62.4527 | 60.0952 | 60.0952 | -62.1506 | -62.3337 | 0.022888 | 0.086975 | -0.086975 | 0.15106 | -0.064087 | -0.15106 | 0.11902 | 0.10071 | -0.082397 | -0.13733 | 62.3749 | -0.20142 | -0.11902 | -0.13733 | 122.3969 | 122.6028 | 62.3383 | -122.3969 | 122.3465 | 122.3465 | 62.4207 | -122.5662
240.4688 | 122.7905 | -62.2559 | 60.2188 | -0.0078584 | -0.057894 | 0.12551 | 0.027265 | 0.036709 | -0.036801 | -0.025882 | 7.627e-05 | -0.0093502 | 0.030576 | 0.05962 | -0.020046 | -0.02196 | 60.2692 | -62.2284 | -0.018311 | -62.4207 | 60.1776 | -62.265 | -62.2238 | 0.045776 | 0.050354 | -62.59 | 60.141 | 60.1273 | -62.1643 | -62.4069 | -0.009156 | 0.032043 | -0.041199 | 0.027465 | -0.16479 | -0.19684 | 0.050354 | 0.091552 | -0.15106 | -0.07782 | 62.3016 | -0.33417 | -0.18311 | -0.091553 | 122.4335 | 122.525 | 62.2375 | -122.4426 | 122.3969 | 122.3831 | 62.3062 | -122.6257
242.25 | 122.7814 | -62.2284 | 60.228 | -0.0078584 | -0.058321 | 0.12786 | 0.028333 | 0.033932 | -0.03851 | -0.024387 | 7.627e-05 | -0.013836 | 0.027372 | 0.058125 | -0.02026 | -0.021533 | 60.379 | -62.0682 | 0.091553 | -62.3245 | 60.1501 | -62.233 | -62.1506 | 0.11902 | 0.16937 | -62.4527 | 60.1089 | 60.0723 | -62.1506 | -62.3383 | -0.004577 | 0.07782 | -0.07782 | 0.16022 | -0.09613 | -0.17395 | 0.15106 | 0.07782 | -0.10986 | -0.11902 | 62.3474 | -0.2243 | -0.11444 | -0.15564 | 122.3785 | 122.6074 | 62.3199 | -122.3785 | 122.3373 | 122.3007 | 62.3978 | -122.5662
243.9688 | 122.7173 | -62.265 | 60.2554 | -0.0078584 | -0.05704 | 0.12914 | 0.034101 | 0.037777 | -0.04385 | -0.026951 | 7.627e-05 | -0.014264 | 0.029935 | 0.05727 | -0.026028 | -0.022601 | 60.347 | -62.1002 | 0.091553 | -62.3245 | 60.1776 | -62.2284 | -62.146 | 0.073242 | 0.10986 | -62.439 | 60.1318 | 60.1501 | -62.1277 | -62.3337 | 0.036621 | 0.11902 | -0.07782 | 0.16479 | -0.059509 | -0.17853 | 0.091553 | 0.13733 | -0.068664 | -0.1236 | 62.3383 | -0.17395 | -0.10529 | -0.10529 | 122.4426 | 122.612 | 62.3566 | -122.4014 | 122.3969 | 122.4152 | 62.3749 | -122.5891
245.75 | 122.7814 | -62.2513 | 60.228 | 0.0074006 | -0.05768 | 0.12786 | 0.02876 | 0.038845 | -0.034878 | -0.024601 | 7.627e-05 | -0.0095638 | 0.030149 | 0.059193 | -0.021114 | -0.023029 | 60.2966 | -62.2009 | -0.009155 | -62.3932 | 60.1868 | -62.2787 | -62.2147 | 0.045776 | 0.064087 | -62.5717 | 60.1456 | 60.1135 | -62.1964 | -62.3795 | -0.027466 | 0.036621 | -0.041198 | 0.050354 | -0.14191 | -0.17853 | 0.068665 | 0.054932 | -0.12817 | -0.082397 | 62.2971 | -0.32043 | -0.19226 | -0.11444 | 122.4381 | 122.5479 | 62.2421 | -122.4426 | 122.3969 | 122.3648 | 62.3154 | -122.6074
247.5312 | 122.6532 | -62.2604 | 60.26 | 0.0074006 | -0.056399 | 0.12871 | 0.035169 | 0.035641 | -0.040005 | -0.024387 | 0.0077058 | -0.013623 | 0.027799 | 0.057697 | -0.023251 | -0.023029 | 60.3973 | -62.027 | 0.17853 | -62.3016 | 60.1318 | -62.2009 | -62.1689 | 0.07782 | 0.14648 | -62.4527 | 60.0952 | 60.1044 | -62.146 | -62.3474 | 0.059509 | 0.091553 | -0.12817 | 0.23346 | -0.041199 | -0.13275 | 0.13733 | 0.11444 | -0.086975 | -0.16479 | 62.3383 | -0.19226 | -0.10529 | -0.15564 | 122.3923 | 122.6578 | 62.439 | -122.4289 | 122.3557 | 122.3648 | 62.4069 | -122.6074
249.2344 | 122.7585 | -62.233 | 60.228 | -0.00022891 | -0.056612 | 0.13128 | 0.031751 | 0.036495 | -0.038083 | -0.024173 | 0.0077058 | -0.013195 | 0.027799 | 0.059834 | -0.020474 | -0.025165 | 60.4019 | -62.059 | 0.10071 | -62.3016 | 60.1501 | -62.2467 | -62.1597 | 0.12817 | 0.17395 | -62.4619 | 60.0952 | 60.1044 | -62.1277 | -62.352 | -0.013733 | 0.073242 | -0.07782 | 0.17395 | -0.068665 | -0.14191 | 0.17395 | 0.10529 | -0.11902 | -0.13275 | 62.3611 | -0.22888 | -0.10986 | -0.1236 | 122.3831 | 122.6349 | 62.3337 | -122.3877 | 122.3282 | 122.3373 | 62.4069 | -122.58
251.0156 | 122.7676 | -62.2513 | 60.1822 | -0.00022891 | -0.052981 | 0.12615 | 0.031537 | 0.036282 | -0.032742 | -0.02396 | 0.015335 | -0.010418 | 0.030149 | 0.060047 | -0.020046 | -0.026233 | 60.3195 | -62.1414 | 0.082397 | -62.3795 | 60.1639 | -62.2787 | -62.2192 | 0.054932 | 0.073242 | -62.558 | 60.1135 | 60.1089 | -62.1918 | -62.3978 | -0.027466 | 0.032044 | -0.018311 | 0.10986 | -0.12817 | -0.16022 | 0.13733 | 0.05951 | -0.14648 | -0.068665 | 62.3062 | -0.3067 | -0.16022 | -0.073242 | 122.4152 | 122.5708 | 62.3337 | -122.4014 | 122.3648 | 122.3602 | 62.3245 | -122.58
252.7969 | 122.7356 | -62.2742 | 60.1913 | -0.00022891 | -0.055971 | 0.12658 | 0.030469 | 0.038632 | -0.034451 | -0.02396 | 7.627e-05 | -0.0099912 | 0.028653 | 0.060047 | -0.020687 | -0.024951 | 60.3287 | -62.1552 | 0.073242 | -62.3886 | 60.1273 | -62.2833 | -62.2055 | 0.050354 | 0.082397 | -62.5854 | 60.1227 | 60.1181 | -62.2101 | -62.3886 | -0.009155 | 0.068665 | -0.064087 | 0.11902 | -0.11444 | -0.18311 | 0.13733 | 0.064087 | -0.11444 | -0.068664 | 62.3245 | -0.31128 | -0.19684 | -0.073242 | 122.4014 | 122.6028 | 62.3474 | -122.3969 | 122.3969 | 122.3923 | 62.3566 | -122.58
254.5781 | 122.6395 | -62.2787 | 60.26 | -0.00022891 | -0.060885 | 0.12679 | 0.035169 | 0.038204 | -0.041501 | -0.028446 | -0.0075532 | -0.014691 | 0.027372 | 0.059834 | -0.023037 | -0.02196 | 60.3424 | -62.0819 | 0.07782 | -62.3291 | 60.1776 | -62.233 | -62.1231 | 0.054932 | 0.10071 | -62.4802 | 60.1044 | 60.1456 | -62.1231 | -62.3199 | 0.045777 | 0.15564 | -0.082398 | 0.19684 | -0.050354 | -0.20599 | 0.082397 | 0.15564 | -0.041198 | -0.15564 | 62.3337 | -0.20142 | -0.16022 | -0.11444 | 122.4564 | 122.6212 | 62.3566 | -122.3831 | 122.3831 | 122.4243 | 62.3795 | -122.58
256.3594 | 122.644 | -62.2696 | 60.2325 | -0.0078584 | -0.05704 | 0.12978 | 0.034101 | 0.037564 | -0.039364 | -0.024601 | 7.627e-05 | -0.011914 | 0.026731 | 0.059406 | -0.022183 | -0.025165 | 60.3745 | -62.0453 | 0.16479 | -62.3108 | 60.1181 | -62.2238 | -62.1414 | 0.059509 | 0.11902 | -62.4527 | 60.1089 | 60.1044 | -62.1506 | -62.3245 | 0.045776 | 0.12817 | -0.11444 | 0.2243 | -0.041199 | -0.16937 | 0.14191 | 0.11902 | -0.054932 | -0.1236 | 62.3291 | -0.18311 | -0.12817 | -0.12817 | 122.3877 | 122.644 | 62.4344 | -122.374 | 122.3785 | 122.374 | 62.3886 | -122.5571
258.0625 | 122.7402 | -62.2742 | 60.228 | -0.00022891 | -0.051272 | 0.12658 | 0.033673 | 0.037136 | -0.032315 | -0.02396 | 7.627e-05 | -0.0097776 | 0.03079 | 0.061543 | -0.019833 | -0.023456 | 60.2692 | -62.233 | 0.018311 | -62.4115 | 60.1593 | -62.2925 | -62.1918 | 0.009155 | 0.032043 | -62.6266 | 60.1501 | 60.0998 | -62.2101 | -62.3932 | -0.01831 | 0.082398 | -0.068664 | 0.041199 | -0.13733 | -0.21973 | 0.041199 | 0.064087 | -0.11902 | -0.07782 | 62.2833 | -0.35248 | -0.23346 | -0.12817 | 122.4335 | 122.5433 | 62.2925 | -122.4197 | 122.4243 | 122.374 | 62.3062 | -122.6212
259.8438 | 122.7631 | -62.2742 | 60.1639 | -0.00022891 | -0.056399 | 0.12764 | 0.029614 | 0.039273 | -0.035519 | -0.023533 | -0.0075532 | -0.0093502 | 0.029294 | 0.061756 | -0.018124 | -0.02431 | 60.3104 | -62.1323 | 0.091553 | -62.3749 | 60.141 | -62.2879 | -62.2192 | 0.07782 | 0.10071 | -62.5626 | 60.0998 | 60.0815 | -62.1964 | -62.4069 | -0.013733 | 0.054932 | -0.022888 | 0.14191 | -0.10071 | -0.15564 | 0.14648 | 0.07782 | -0.13275 | -0.064087 | 62.352 | -0.28839 | -0.15564 | -0.082397 | 122.4152 | 122.5845 | 62.3657 | -122.3831 | 122.374 | 122.3557 | 62.3749 | -122.5708
261.6406 | 122.7036 | -62.2421 | 60.2646 | -0.00022891 | -0.056826 | 0.12999 | 0.033673 | 0.036709 | -0.043423 | -0.026523 | 0.0077058 | -0.012982 | 0.028653 | 0.058338 | -0.024746 | -0.022815 | 60.347 | -62.0773 | 0.11444 | -62.3062 | 60.1364 | -62.2055 | -62.1368 | 0.068665 | 0.1236 | -62.4161 | 60.1227 | 60.1318 | -62.0956 | -62.3154 | 0.036621 | 0.10529 | -0.12817 | 0.16479 | -0.064087 | -0.16937 | 0.082398 | 0.14648 | -0.073243 | -0.14191 | 62.3108 | -0.17395 | -0.10071 | -0.13275 | 122.3785 | 122.5891 | 62.3566 | -122.4014 | 122.3648 | 122.374 | 62.3657 | -122.58
263.3438 | 122.7081 | -62.2375 | 60.26 | 0.0074006 | -0.061526 | 0.12679 | 0.028333 | 0.036068 | -0.039364 | -0.024387 | 7.627e-05 | -0.011273 | 0.02609 | 0.058766 | -0.021114 | -0.024951 | 60.3836 | -62.0453 | 0.10529 | -62.3108 | 60.1318 | -62.2101 | -62.1414 | 0.12817 | 0.16479 | -62.4527 | 60.0815 | 60.0952 | -62.1414 | -62.3337 | 0.027466 | 0.096131 | -0.12817 | 0.19226 | -0.073242 | -0.16937 | 0.1236 | 0.096131 | -0.09613 | -0.17853 | 62.3657 | -0.21515 | -0.11902 | -0.16479 | 122.3694 | 122.6212 | 62.3428 | -122.4014 | 122.319 | 122.3328 | 62.4023 | -122.5937
265.1094 | 122.6852 | -62.2421 | 60.2509 | -0.00022891 | -0.059603 | 0.13063 | 0.029828 | 0.036923 | -0.038083 | -0.026096 | 0.0077058 | -0.011059 | 0.026944 | 0.060261 | -0.019406 | -0.02431 | 60.3745 | -62.0544 | 0.10986 | -62.3108 | 60.1181 | -62.2101 | -62.1414 | 0.11444 | 0.16479 | -62.4435 | 60.1044 | 60.1089 | -62.146 | -62.3199 | 0.032043 | 0.10071 | -0.13275 | 0.18768 | -0.068665 | -0.16937 | 0.1236 | 0.09613 | -0.07782 | -0.14648 | 62.3566 | -0.20142 | -0.1236 | -0.14191 | 122.3602 | 122.6166 | 62.352 | -122.3923 | 122.3465 | 122.3511 | 62.4069 | -122.5708
266.8906 | 122.7585 | -62.2467 | 60.2234 | 0.0074006 | -0.056399 | 0.12978 | 0.030683 | 0.036709 | -0.034024 | -0.024173 | 7.627e-05 | -0.010418 | 0.027799 | 0.060261 | -0.019833 | -0.020892 | 60.2966 | -62.2284 | -0.022888 | -62.4069 | 60.1822 | -62.265 | -62.2238 | 0.032043 | 0.054932 | -62.5946 | 60.1547 | 60.1227 | -62.1964 | -62.3932 | -0.018311 | 0.022888 | -0.041199 | 0.01831 | -0.16022 | -0.1831 | 0.073242 | 0.050354 | -0.14648 | -0.068665 | 62.2787 | -0.3479 | -0.20142 | -0.10071 | 122.4289 | 122.5433 | 62.2238 | -122.4472 | 122.4014 | 122.3694 | 62.3016 | -122.6166
268.6719 | 122.6212 | -62.2604 | 60.2692 | -0.015487 | -0.055117 | 0.12722 | 0.036023 | 0.040341 | -0.038083 | -0.025455 | 7.627e-05 | -0.012555 | 0.030149 | 0.058766 | -0.024746 | -0.023669 | 60.3653 | -62.0819 | 0.12817 | -62.3108 | 60.1456 | -62.2375 | -62.1735 | 0.018311 | 0.068665 | -62.4939 | 60.1456 | 60.141 | -62.1552 | -62.3657 | 0.022888 | 0.086975 | -0.1236 | 0.17853 | -0.050354 | -0.13733 | 0.09613 | 0.10529 | -0.10529 | -0.1236 | 62.2787 | -0.23346 | -0.12817 | -0.12817 | 122.406 | 122.6257 | 62.3886 | -122.4426 | 122.406 | 122.4014 | 62.3291 | -122.6349
270.4531 | 122.7905 | -62.2467 | 60.1959 | 0.0074006 | -0.057894 | 0.12764 | 0.029614 | 0.035641 | -0.033383 | -0.025669 | 7.627e-05 | -0.011273 | 0.029935 | 0.058979 | -0.019619 | -0.021533 | 60.2921 | -62.1964 | 0.004578 | -62.3886 | 60.1776 | -62.2604 | -62.2009 | 0.068665 | 0.073242 | -62.558 | 60.141 | 60.1135 | -62.1735 | -62.3566 | -0.013733 | 0.045776 | -0.018311 | 0.050354 | -0.14191 | -0.18768 | 0.09613 | 0.073242 | -0.10986 | -0.054932 | 62.3154 | -0.31128 | -0.20142 | -0.082398 | 122.4243 | 122.5388 | 62.2513 | -122.3969 | 122.3877 | 122.3602 | 62.3199 | -122.5525
272.1562 | 122.7722 | -62.2559 | 60.2097 | 0.01503 | -0.057894 | 0.12636 | 0.031537 | 0.037991 | -0.034665 | -0.025455 | 7.627e-05 | -0.0091366 | 0.029722 | 0.060688 | -0.021114 | -0.024738 | 60.2829 | -62.2192 | -0.013733 | -62.4115 | 60.1822 | -62.2742 | -62.2192 | 0.041199 | 0.059509 | -62.5763 | 60.1364 | 60.1318 | -62.1643 | -62.4023 | -0.018311 | 0.036621 | -0.027466 | 0.036621 | -0.15564 | -0.19226 | 0.073242 | 0.091552 | -0.14648 | -0.073242 | 62.2971 | -0.32043 | -0.17395 | -0.07782 | 122.438 | 122.5388 | 62.2421 | -122.4289 | 122.3923 | 122.3877 | 62.3154 | -122.612
273.9219 | 122.7722 | -62.2421 | 60.2325 | -0.00022891 | -0.059389 | 0.12786 | 0.031537 | 0.036495 | -0.037655 | -0.02396 | 0.0077058 | -0.012768 | 0.027799 | 0.060474 | -0.022823 | -0.024524 | 60.3561 | -62.0682 | 0.086975 | -62.3199 | 60.1501 | -62.2147 | -62.146 | 0.13733 | 0.16937 | -62.4481 | 60.1089 | 60.0769 | -62.1277 | -62.3108 | 0.027465 | 0.09613 | -0.082398 | 0.17395 | -0.07782 | -0.17395 | 0.1236 | 0.11444 | -0.068665 | -0.1236 | 62.3795 | -0.20599 | -0.13733 | -0.15564 | 122.3923 | 122.5983 | 62.3291 | -122.3785 | 122.3511 | 122.319 | 62.4115 | -122.5433
275.7031 | 122.6669 | -62.2467 | 60.2737 | -0.0078584 | -0.056185 | 0.12893 | 0.034101 | 0.037136 | -0.041287 | -0.025669 | 7.627e-05 | -0.013836 | 0.029294 | 0.060261 | -0.023464 | -0.024738 | 60.3561 | -62.1002 | 0.064087 | -62.3199 | 60.1547 | -62.1826 | -62.1231 | 0.041199 | 0.091553 | -62.4756 | 60.1547 | 60.1501 | -62.114 | -62.2925 | 0.064087 | 0.1236 | -0.11902 | 0.14648 | -0.073242 | -0.19684 | 0.082397 | 0.13275 | -0.045776 | -0.11902 | 62.2879 | -0.22888 | -0.18311 | -0.1236 | 122.4014 | 122.6028 | 62.3108 | -122.3969 | 122.4014 | 122.3969 | 62.3383 | -122.5662
277.4219 | 122.6166 | -62.2833 | 60.2509 | -0.0078584 | -0.058748 | 0.1285 | 0.032819 | 0.039913 | -0.03851 | -0.027378 | 7.627e-05 | -0.014264 | 0.028867 | 0.058766 | -0.021114 | -0.023456 | 60.3699 | -62.0407 | 0.14648 | -62.3016 | 60.1501 | -62.2192 | -62.1506 | 0.064087 | 0.10529 | -62.4573 | 60.1273 | 60.0906 | -62.1552 | -62.3383 | 0.064087 | 0.13275 | -0.10071 | 0.24262 | -0.018311 | -0.15106 | 0.11902 | 0.12817 | -0.054932 | -0.1236 | 62.3474 | -0.17395 | -0.11902 | -0.16022 | 122.4335 | 122.6532 | 62.4298 | -122.4014 | 122.4106 | 122.374 | 62.3886 | -122.5891
279.2031 | 122.7814 | -62.2513 | 60.2005 | -0.00022891 | -0.056185 | 0.12764 | 0.030896 | 0.037564 | -0.034237 | -0.023746 | 0.0077058 | -0.0117 | 0.025663 | 0.057911 | -0.018765 | -0.02431 | 60.3012 | -62.1735 | 0.004578 | -62.3657 | 60.1639 | -62.2604 | -62.1552 | 0.086975 | 0.11902 | -62.5076 | 60.1227 | 60.0952 | -62.1597 | -62.3474 | -0.009155 | 0.096131 | -0.036621 | 0.07782 | -0.11444 | -0.21057 | 0.10071 | 0.091553 | -0.09613 | -0.077819 | 62.3383 | -0.25635 | -0.16022 | -0.10528 | 122.4152 | 122.5525 | 62.2559 | -122.3557 | 122.374 | 122.3465 | 62.3703 | -122.5479
280.9844 | 122.7585 | -62.2513 | 60.1959 | 0.0074006 | -0.052981 | 0.12722 | 0.03111 | 0.0397 | -0.035092 | -0.025028 | 7.627e-05 | -0.0097776 | 0.030362 | 0.061543 | -0.022823 | -0.02196 | 60.26 | -62.1735 | 0.045776 | -62.3795 | 60.1822 | -62.2604 | -62.2055 | -0.004578 | 0.027466 | -62.5763 | 60.1273 | 60.0815 | -62.2192 | -62.3886 | -0.009155 | 0.045777 | -0.013733 | 0.07782 | -0.12817 | -0.17395 | 0.064087 | 0.032044 | -0.13733 | -0.068665 | 62.2467 | -0.32501 | -0.18768 | -0.11444 | 122.4335 | 122.5113 | 62.2971 | -122.4014 | 122.3785 | 122.3328 | 62.2787 | -122.5845
282.7031 | 122.7493 | -62.2467 | 60.1959 | 0.0074006 | -0.05469 | 0.12786 | 0.032178 | 0.037136 | -0.035092 | -0.024173 | 7.627e-05 | -0.012127 | 0.029294 | 0.062397 | -0.020687 | -0.023456 | 60.2646 | -62.2284 | -0.018311 | -62.4069 | 60.1593 | -62.2467 | -62.1918 | 0.041199 | 0.054932 | -62.5992 | 60.1181 | 60.1227 | -62.2192 | -62.3886 | 0 | 0.054932 | -0.036621 | 0.01831 | -0.16022 | -0.21515 | 0.068664 | 0.027466 | -0.14191 | -0.07782 | 62.2879 | -0.35248 | -0.21057 | -0.073242 | 122.406 | 122.5113 | 62.2284 | -122.3877 | 122.3648 | 122.3694 | 62.3016 | -122.5845
284.5 | 122.7493 | -62.2513 | 60.1868 | -0.0078584 | -0.054049 | 0.12658 | 0.030683 | 0.036709 | -0.035092 | -0.024387 | 0.0077058 | -0.008923 | 0.028013 | 0.060902 | -0.019406 | -0.02431 | 60.3058 | -62.1368 | 0.064087 | -62.3657 | 60.1364 | -62.2833 | -62.2238 | 0.059509 | 0.09613 | -62.5626 | 60.0815 | 60.0815 | -62.2101 | -62.4115 | -0.032043 | 0.027466 | -0.050354 | 0.11444 | -0.11444 | -0.14191 | 0.11902 | 0.041199 | -0.16022 | -0.10529 | 62.3108 | -0.31128 | -0.15106 | -0.10529 | 122.3877 | 122.5571 | 62.3154 | -122.4106 | 122.3328 | 122.3328 | 62.3474 | -122.5983
286.2812 | 122.6486 | -62.2742 | 60.2692 | -0.0078584 | -0.057894 | 0.12764 | 0.031751 | 0.036923 | -0.040432 | -0.021824 | -0.0075532 | -0.012341 | 0.029294 | 0.058979 | -0.025173 | -0.021533 | 60.347 | -62.0407 | 0.09613 | -62.3154 | 60.1273 | -62.1964 | -62.1323 | 0.12817 | 0.15106 | -62.439 | 60.1089 | 60.0952 | -62.1094 | -62.3199 | 0.07782 | 0.14191 | -0.14191 | 0.23346 | -0.041199 | -0.18311 | 0.07782 | 0.16479 | -0.045776 | -0.16022 | 62.4023 | -0.1648 | -0.11902 | -0.17395 | 122.4014 | 122.6212 | 62.3703 | -122.4014 | 122.3831 | 122.3694 | 62.4252 | -122.5891
288.0469 | 122.7173 | -62.265 | 60.2188 | -0.00022891 | -0.056612 | 0.12593 | 0.031964 | 0.039486 | -0.031674 | -0.025669 | 0.022965 | -0.0099912 | 0.028013 | 0.061329 | -0.022183 | -0.022601 | 60.2646 | -62.2238 | 0.004578 | -62.4023 | 60.1593 | -62.2879 | -62.2238 | 0 | 0.036621 | -62.6312 | 60.1364 | 60.1364 | -62.2055 | -62.3886 | -0.022888 | 0.041199 | -0.059509 | 0.041199 | -0.13733 | -0.17853 | 0.045776 | 0.05951 | -0.1236 | -0.082397 | 62.265 | -0.36621 | -0.24262 | -0.082397 | 122.4243 | 122.5296 | 62.2696 | -122.4426 | 122.4014 | 122.4014 | 62.3016 | -122.6074
289.8281 | 122.7722 | -62.2238 | 60.1959 | -0.00022891 | -0.057467 | 0.12807 | 0.030469 | 0.036495 | -0.037869 | -0.024814 | 7.627e-05 | -0.012982 | 0.029722 | 0.059834 | -0.018765 | -0.023883 | 60.3561 | -62.0819 | 0.064087 | -62.3154 | 60.1364 | -62.2101 | -62.1597 | 0.11902 | 0.17395 | -62.4527 | 60.1135 | 60.1044 | -62.1414 | -62.3062 | 0.013733 | 0.064087 | -0.059509 | 0.14191 | -0.091553 | -0.15564 | 0.16022 | 0.082398 | -0.082397 | -0.082398 | 62.3428 | -0.22888 | -0.14648 | -0.091553 | 122.3602 | 122.58 | 62.2879 | -122.3557 | 122.3373 | 122.3282 | 62.3978 | -122.5021
291.5469 | 122.6349 | -62.2559 | 60.2463 | -0.00022891 | -0.060671 | 0.12999 | 0.031964 | 0.03735 | -0.042569 | -0.028873 | 0.0077058 | -0.014264 | 0.029294 | 0.059193 | -0.023464 | -0.023883 | 60.3241 | -62.1002 | 0.050354 | -62.3245 | 60.1685 | -62.2101 | -62.1414 | 0.050354 | 0.10071 | -62.4619 | 60.1227 | 60.1227 | -62.114 | -62.3199 | 0.045776 | 0.11444 | -0.07782 | 0.15564 | -0.068665 | -0.18311 | 0.07782 | 0.14191 | -0.064087 | -0.1236 | 62.3062 | -0.20599 | -0.14191 | -0.1236 | 122.4243 | 122.58 | 62.3062 | -122.3877 | 122.3785 | 122.3785 | 62.3566 | -122.5662
293.3125 | 122.7905 | -62.2421 | 60.1959 | 0.0074006 | -0.058535 | 0.12957 | 0.028333 | 0.037136 | -0.035305 | -0.025028 | 7.627e-05 | -0.0117 | 0.026731 | 0.05962 | -0.02026 | -0.02431 | 60.2829 | -62.1735 | -0.004578 | -62.3795 | 60.1868 | -62.2559 | -62.1826 | 0.073242 | 0.091553 | -62.5259 | 60.1227 | 60.0906 | -62.1506 | -62.3337 | -0.013733 | 0.059509 | -0.009155 | 0.068664 | -0.13733 | -0.19684 | 0.086975 | 0.091552 | -0.091553 | -0.073242 | 62.3154 | -0.28381 | -0.19226 | -0.10529 | 122.4289 | 122.525 | 62.2375 | -122.3785 | 122.3648 | 122.3328 | 62.3337 | -122.5296
295.0156 | 122.6669 | -62.2559 | 60.26 | -0.0078584 | -0.058535 | 0.12914 | 0.032819 | 0.036068 | -0.041714 | -0.02631 | 7.627e-05 | -0.012768 | 0.026304 | 0.054493 | -0.022823 | -0.025806 | 60.4019 | -61.9995 | 0.17853 | -62.2787 | 60.1318 | -62.2101 | -62.146 | 0.09613 | 0.15106 | -62.4115 | 60.0952 | 60.0998 | -62.1094 | -62.3291 | 0.045776 | 0.10986 | -0.12817 | 0.25635 | -0.022889 | -0.13275 | 0.14191 | 0.14648 | -0.073243 | -0.16479 | 62.352 | -0.15564 | -0.082397 | -0.16022 | 122.3877 | 122.6578 | 62.4344 | -122.406 | 122.3511 | 122.3557 | 62.4069 | -122.5891
296.8125 | 122.6212 | -62.2787 | 60.2463 | -0.00022891 | -0.056612 | 0.12764 | 0.034955 | 0.036923 | -0.041287 | -0.029514 | 0.0077058 | -0.013409 | 0.029081 | 0.059834 | -0.025601 | -0.024524 | 60.3928 | -62.0178 | 0.16022 | -62.2925 | 60.1456 | -62.2101 | -62.1506 | 0.082397 | 0.12817 | -62.4252 | 60.0906 | 60.1089 | -62.1368 | -62.3199 | 0.068665 | 0.12817 | -0.10071 | 0.26093 | -0.013732 | -0.14191 | 0.14648 | 0.14191 | -0.041198 | -0.15564 | 62.3611 | -0.14648 | -0.10529 | -0.13733 | 122.4243 | 122.6715 | 62.439 | -122.3969 | 122.3694 | 122.3877 | 62.4069 | -122.5662
298.5938 | 122.6852 | -62.2787 | 60.2051 | -0.00022891 | -0.058535 | 0.13063 | 0.030255 | 0.037991 | -0.038296 | -0.025669 | 0.0077058 | -0.011273 | 0.029935 | 0.060688 | -0.021328 | -0.024951 | 60.2692 | -62.1964 | 0.032043 | -62.3886 | 60.173 | -62.2696 | -62.1918 | 0 | -0.004578 | -62.5809 | 60.1501 | 60.1181 | -62.1872 | -62.3886 | 0.009156 | 0.086976 | -0.032043 | 0.082398 | -0.10986 | -0.19684 | 0.064087 | 0.091553 | -0.10986 | -0.054932 | 62.2787 | -0.30212 | -0.19226 | -0.086975 | 122.4518 | 122.5479 | 62.3108 | -122.3969 | 122.4289 | 122.3969 | 62.2742 | -122.5937
300.375 | 122.7585 | -62.233 | 60.1685 | -0.00022891 | -0.05469 | 0.12658 | 0.032819 | 0.038632 | -0.034665 | -0.023746 | 7.627e-05 | -0.007855 | 0.029722 | 0.063038 | -0.021969 | -0.025378 | 60.3241 | -62.1414 | 0.086975 | -62.352 | 60.1593 | -62.2879 | -62.1918 | 0.054932 | 0.091553 | -62.558 | 60.0998 | 60.1044 | -62.1872 | -62.3932 | -0.054932 | 0.041199 | -0.009155 | 0.091553 | -0.11902 | -0.16022 | 0.15564 | 0.045776 | -0.16022 | -0.068665 | 62.2879 | -0.32501 | -0.16479 | -0.064087 | 122.3923 | 122.5571 | 62.3199 | -122.3602 | 122.3328 | 122.3373 | 62.3245 | -122.5616
302.0938 | 122.6486 | -62.2696 | 60.2692 | -0.00022891 | -0.056399 | 0.12957 | 0.03346 | 0.036068 | -0.041073 | -0.025028 | 7.627e-05 | -0.014264 | 0.027585 | 0.059834 | -0.024532 | -0.02196 | 60.3928 | -61.9766 | 0.16937 | -62.2787 | 60.1547 | -62.2055 | -62.1277 | 0.091553 | 0.16022 | -62.4069 | 60.0861 | 60.1044 | -62.1414 | -62.3199 | 0.064087 | 0.14191 | -0.11444 | 0.29297 | -0.009156 | -0.15106 | 0.1236 | 0.12817 | -0.050354 | -0.1831 | 62.3611 | -0.13733 | -0.086975 | -0.16479 | 122.4243 | 122.6624 | 62.439 | -122.3969 | 122.3557 | 122.374 | 62.4298 | -122.5891
303.875 | 122.7493 | -62.2192 | 60.2142 | -0.0078584 | -0.055544 | 0.1285 | 0.030042 | 0.03735 | -0.037655 | -0.024814 | 7.627e-05 | -0.013195 | 0.026304 | 0.058766 | -0.019619 | -0.025592 | 60.3699 | -62.0682 | 0.09613 | -62.2925 | 60.1089 | -62.1964 | -62.1552 | 0.1236 | 0.16479 | -62.4481 | 60.0906 | 60.0677 | -62.1231 | -62.3383 | 0.022888 | 0.064087 | -0.10529 | 0.15106 | -0.073242 | -0.13733 | 0.15564 | 0.09613 | -0.11902 | -0.1236 | 62.3428 | -0.22888 | -0.10986 | -0.14648 | 122.3282 | 122.5891 | 62.3154 | -122.3694 | 122.3099 | 122.287 | 62.384 | -122.5525
305.5938 | 122.6532 | -62.2375 | 60.2509 | -0.00022891 | -0.055331 | 0.12957 | 0.034955 | 0.036709 | -0.040646 | -0.025455 | 7.627e-05 | -0.013623 | 0.026944 | 0.057484 | -0.023464 | -0.023456 | 60.3836 | -61.9904 | 0.16479 | -62.2879 | 60.1501 | -62.1964 | -62.1414 | 0.086975 | 0.16022 | -62.4069 | 60.1181 | 60.0632 | -62.146 | -62.3291 | 0.041199 | 0.096131 | -0.10071 | 0.24719 | -0.050354 | -0.14648 | 0.13275 | 0.091553 | -0.091553 | -0.13275 | 62.3245 | -0.16937 | -0.077819 | -0.18768 | 122.3877 | 122.6212 | 62.4023 | -122.3923 | 122.3557 | 122.3007 | 62.3978 | -122.58
307.375 | 122.6395 | -62.2467 | 60.2371 | -0.00022891 | -0.055971 | 0.12722 | 0.035169 | 0.039913 | -0.038296 | -0.026523 | 7.627e-05 | -0.013195 | 0.027799 | 0.056629 | -0.022183 | -0.025378 | 60.3928 | -61.9904 | 0.16937 | -62.2833 | 60.1501 | -62.2009 | -62.1323 | 0.09613 | 0.15106 | -62.4115 | 60.0998 | 60.0952 | -62.1231 | -62.3474 | 0.045776 | 0.11444 | -0.086976 | 0.25635 | -0.036621 | -0.15106 | 0.15564 | 0.1236 | -0.10071 | -0.13733 | 62.3428 | -0.16479 | -0.064087 | -0.14191 | 122.3969 | 122.6395 | 62.4161 | -122.3694 | 122.3465 | 122.3419 | 62.3978 | -122.5845
309.1719 | 122.731 | -62.2467 | 60.1868 | 0.0074006 | -0.053622 | 0.12679 | 0.034101 | 0.036282 | -0.034451 | -0.027591 | 0.015335 | -0.007855 | 0.028867 | 0.062611 | -0.02026 | -0.025592 | 60.2875 | -62.1872 | 0.032043 | -62.3749 | 60.1776 | -62.265 | -62.1826 | 0 | 0.004578 | -62.5809 | 60.141 | 60.141 | -62.178 | -62.3703 | -0.018311 | 0.064087 | -0.009156 | 0.059509 | -0.12817 | -0.19226 | 0.10071 | 0.068664 | -0.1236 | -0.045777 | 62.2467 | -0.33417 | -0.21057 | -0.045777 | 122.4243 | 122.5342 | 62.2787 | -122.3694 | 122.3877 | 122.3877 | 62.2513 | -122.5571
310.8906 | 122.6578 | -62.2604 | 60.2509 | -0.0078584 | -0.056185 | 0.1285 | 0.031964 | 0.039913 | -0.04086 | -0.024814 | 7.627e-05 | -0.014477 | 0.028013 | 0.05962 | -0.023037 | -0.026233 | 60.3973 | -61.9995 | 0.15564 | -62.2742 | 60.1364 | -62.2009 | -62.1231 | 0.086975 | 0.16022 | -62.3886 | 60.1181 | 60.0998 | -62.114 | -62.2971 | 0.059509 | 0.13733 | -0.11444 | 0.26093 | -0.013733 | -0.15106 | 0.14649 | 0.14648 | -0.036621 | -0.13275 | 62.3474 | -0.12817 | -0.091553 | -0.15106 | 122.3969 | 122.6578 | 62.4161 | -122.374 | 122.3785 | 122.3602 | 62.4207 | -122.5479
312.6875 | 122.7631 | -62.2467 | 60.2005 | -0.00022891 | -0.055971 | 0.12893 | 0.028119 | 0.037564 | -0.032528 | -0.024173 | 7.627e-05 | -0.0095638 | 0.028013 | 0.062611 | -0.019406 | -0.024524 | 60.2737 | -62.2147 | -0.018311 | -62.4023 | 60.1776 | -62.265 | -62.1918 | 0.050354 | 0.045776 | -62.5854 | 60.1273 | 60.1089 | -62.1872 | -62.3749 | -0.018311 | 0.054932 | -0.022888 | 0.032043 | -0.15564 | -0.21057 | 0.073243 | 0.059509 | -0.12817 | -0.073242 | 62.2971 | -0.33874 | -0.21057 | -0.091552 | 122.4243 | 122.5204 | 62.2284 | -122.3923 | 122.374 | 122.3557 | 62.2925 | -122.5754
314.4062 | 122.6715 | -62.2375 | 60.26 | 0.0074006 | -0.058108 | 0.13085 | 0.034955 | 0.036709 | -0.040646 | -0.024601 | 7.627e-05 | -0.014477 | 0.030149 | 0.058979 | -0.02496 | -0.02431 | 60.3287 | -62.0682 | 0.07782 | -62.3062 | 60.1639 | -62.2147 | -62.1552 | 0.068665 | 0.11902 | -62.4435 | 60.1227 | 60.1135 | -62.1002 | -62.3199 | 0.022888 | 0.082398 | -0.096131 | 0.16937 | -0.068664 | -0.15106 | 0.068664 | 0.13733 | -0.082397 | -0.13733 | 62.3062 | -0.20599 | -0.1236 | -0.14648 | 122.4014 | 122.5662 | 62.3154 | -122.4152 | 122.3602 | 122.3511 | 62.3566 | -122.58
316.1875 | 122.6486 | -62.2421 | 60.2188 | -0.0078584 | -0.057467 | 0.12764 | 0.031751 | 0.036282 | -0.038723 | -0.026737 | 7.627e-05 | -0.010632 | 0.027372 | 0.060261 | -0.023892 | -0.024738 | 60.4111 | -61.9766 | 0.16022 | -62.265 | 60.1364 | -62.2192 | -62.1414 | 0.073242 | 0.15106 | -62.4161 | 60.1181 | 60.1089 | -62.1185 | -62.3199 | 0.022888 | 0.10071 | -0.082397 | 0.2655 | -0.022889 | -0.1236 | 0.19226 | 0.1236 | -0.07782 | -0.10071 | 62.3154 | -0.17395 | -0.096131 | -0.10986 | 122.3785 | 122.6532 | 62.4023 | -122.3602 | 122.3602 | 122.3511 | 62.3932 | -122.5388
317.9531 | 122.7768 | -62.233 | 60.1593 | 0.0074006 | -0.053835 | 0.12807 | 0.034741 | 0.039059 | -0.032956 | -0.02631 | 7.627e-05 | -0.0091366 | 0.028867 | 0.060474 | -0.023464 | -0.025165 | 60.2783 | -62.1826 | 0.041199 | -62.3749 | 60.1685 | -62.2833 | -62.1964 | 0.009155 | 0.054932 | -62.5671 | 60.1318 | 60.1044 | -62.2101 | -62.3978 | -0.050354 | 0.036621 | 0.009155 | 0.050354 | -0.14191 | -0.17853 | 0.11902 | 0.022888 | -0.16479 | -0.027466 | 62.2421 | -0.33417 | -0.16937 | -0.054932 | 122.4014 | 122.5113 | 62.2742 | -122.3557 | 122.3648 | 122.3373 | 62.2879 | -122.5571
319.6719 | 122.6257 | -62.2284 | 60.2554 | 0.0074006 | -0.058748 | 0.12743 | 0.033032 | 0.039059 | -0.039151 | -0.025028 | 7.627e-05 | -0.013409 | 0.028867 | 0.061329 | -0.023892 | -0.023669 | 60.3333 | -62.059 | 0.064087 | -62.3108 | 60.1639 | -62.2055 | -62.1048 | 0.068665 | 0.091553 | -62.4573 | 60.1273 | 60.1044 | -62.1094 | -62.3291 | 0.022889 | 0.1236 | -0.091553 | 0.16937 | -0.082397 | -0.20599 | 0.07782 | 0.11902 | -0.10071 | -0.12817 | 62.2971 | -0.22888 | -0.12817 | -0.15106 | 122.3923 | 122.5616 | 62.2925 | -122.3602 | 122.3557 | 122.3328 | 62.3199 | -122.5845
321.4531 | 122.6532 | -62.2513 | 60.2646 | -0.015487 | -0.057894 | 0.12636 | 0.02876 | 0.039273 | -0.036801 | -0.026737 | -0.0075532 | -0.012341 | 0.027585 | 0.061329 | -0.020901 | -0.025165 | 60.3973 | -62.027 | 0.10986 | -62.3062 | 60.1318 | -62.2055 | -62.1277 | 0.12817 | 0.16022 | -62.4252 | 60.1089 | 60.0952 | -62.1231 | -62.3428 | 0.045777 | 0.1236 | -0.13275 | 0.2243 | -0.054931 | -0.17853 | 0.13275 | 0.12817 | -0.091552 | -0.15564 | 62.3795 | -0.17395 | -0.082398 | -0.16937 | 122.3831 | 122.6486 | 62.3611 | -122.3923 | 122.3602 | 122.3465 | 62.4115 | -122.6074
323.2344 | 122.7631 | -62.233 | 60.2234 | -0.0078584 | -0.056826 | 0.12978 | 0.027905 | 0.037136 | -0.034237 | -0.024387 | 0.0077058 | -0.011486 | 0.026304 | 0.060261 | -0.016201 | -0.023029 | 60.3378 | -62.1185 | 0.041199 | -62.3474 | 60.1547 | -62.2192 | -62.178 | 0.12817 | 0.16022 | -62.4664 | 60.1227 | 60.0632 | -62.1597 | -62.3199 | 0.013733 | 0.054931 | -0.068665 | 0.11444 | -0.11444 | -0.16937 | 0.11444 | 0.073242 | -0.086975 | -0.10071 | 62.3611 | -0.23346 | -0.14648 | -0.16022 | 122.3877 | 122.5708 | 62.2742 | -122.4014 | 122.3557 | 122.2961 | 62.3932 | -122.5433
325.0156 | 122.7493 | -62.2421 | 60.1685 | -0.00022891 | -0.056185 | 0.12722 | 0.031323 | 0.033932 | -0.032956 | -0.026523 | 0.0077058 | -0.0084958 | 0.028013 | 0.061756 | -0.020046 | -0.026019 | 60.3104 | -62.1552 | 0.068665 | -62.3566 | 60.1181 | -62.2787 | -62.2192 | 0.073242 | 0.10071 | -62.5534 | 60.0952 | 60.0632 | -62.1872 | -62.4298 | -0.036622 | 0.022888 | -0.050354 | 0.086975 | -0.11444 | -0.13733 | 0.14191 | 0.054931 | -0.18768 | -0.073242 | 62.3154 | -0.31128 | -0.1236 | -0.10529 | 122.3602 | 122.5525 | 62.3108 | -122.3877 | 122.3373 | 122.3053 | 62.3428 | -122.5983
326.7969 | 122.6578 | -62.2421 | 60.2966 | -0.015487 | -0.060457 | 0.12957 | 0.031751 | 0.036068 | -0.042782 | -0.025242 | 0.0077058 | -0.015545 | 0.026944 | 0.057057 | -0.023464 | -0.020465 | 60.3195 | -62.0773 | 0.059509 | -62.3154 | 60.1776 | -62.2009 | -62.1323 | 0.041199 | 0.10071 | -62.4435 | 60.141 | 60.1318 | -62.1185 | -62.2879 | 0.041198 | 0.10986 | -0.11902 | 0.16479 | -0.073243 | -0.18311 | 0.022888 | 0.1236 | -0.045777 | -0.15564 | 62.2833 | -0.20142 | -0.15564 | -0.16479 | 122.4197 | 122.5616 | 62.3016 | -122.4289 | 122.3831 | 122.374 | 62.3428 | -122.5845
328.5 | 122.7448 | -62.2467 | 60.1868 | -0.0078584 | -0.049349 | 0.12679 | 0.032819 | 0.036709 | -0.032315 | -0.023533 | 0.015335 | -0.0099912 | 0.03143 | 0.061329 | -0.019833 | -0.02666 | 60.2371 | -62.2192 | 0 | -62.4115 | 60.1639 | -62.2696 | -62.2284 | 0.032043 | 0.041199 | -62.6038 | 60.1501 | 60.0998 | -62.2055 | -62.3749 | -0.022888 | 0.01831 | -0.022889 | 0.027466 | -0.16479 | -0.1831 | 0.050354 | 0.041199 | -0.12817 | -0.036622 | 62.2787 | -0.35706 | -0.22888 | -0.086976 | 122.4106 | 122.4838 | 62.2467 | -122.4152 | 122.3969 | 122.3465 | 62.2879 | -122.5616
330.2812 | 122.6212 | -62.2696 | 60.2371 | -0.0078584 | -0.056826 | 0.12807 | 0.034955 | 0.037777 | -0.040432 | -0.02396 | 0.0077058 | -0.013623 | 0.030576 | 0.060474 | -0.02261 | -0.023029 | 60.3195 | -62.0728 | 0.10071 | -62.3291 | 60.1501 | -62.2421 | -62.178 | 0.018311 | 0.050354 | -62.5214 | 60.1181 | 60.1044 | -62.1552 | -62.3566 | 0.027466 | 0.091552 | -0.086976 | 0.19684 | -0.05951 | -0.15106 | 0.082397 | 0.11444 | -0.086975 | -0.11902 | 62.2879 | -0.25177 | -0.1648 | -0.13275 | 122.4197 | 122.5891 | 62.3703 | -122.4152 | 122.3877 | 122.374 | 62.3199 | -122.5937
332.0625 | 122.7493 | -62.2559 | 60.1822 | -0.00022891 | -0.05234 | 0.12593 | 0.034101 | 0.037136 | -0.033383 | -0.024387 | 0.0077058 | -0.0097776 | 0.03079 | 0.05962 | -0.020901 | -0.025165 | 60.26 | -62.1735 | 0.059509 | -62.3611 | 60.1501 | -62.2742 | -62.1826 | 0.009155 | 0.050354 | -62.558 | 60.1227 | 60.0906 | -62.1826 | -62.3886 | -0.018311 | 0.073242 | -0.032044 | 0.082397 | -0.10529 | -0.17853 | 0.07782 | 0.073242 | -0.13275 | -0.059509 | 62.265 | -0.30212 | -0.16937 | -0.091553 | 122.406 | 122.5159 | 62.3154 | -122.3648 | 122.3785 | 122.3465 | 62.3062 | -122.5708
333.8438 | 122.7173 | -62.2284 | 60.1959 | 0.01503 | -0.055544 | 0.12786 | 0.029828 | 0.035214 | -0.034665 | -0.023319 | 0.0077058 | -0.010846 | 0.027158 | 0.060261 | -0.018765 | -0.021533 | 60.2097 | -62.2101 | -0.013733 | -62.4069 | 60.1593 | -62.265 | -62.2009 | 0 | 0.041199 | -62.59 | 60.1089 | 60.0952 | -62.178 | -62.3611 | -0.036621 | 0.027466 | -0.036621 | 0.018311 | -0.17853 | -0.20599 | 0.013733 | 0.050354 | -0.13275 | -0.086975 | 62.2284 | -0.36163 | -0.22888 | -0.10071 | 122.3877 | 122.4381 | 62.2147 | -122.3969 | 122.3373 | 122.3236 | 62.2696 | -122.5571
335.6094 | 122.7127 | -62.233 | 60.2371 | 0.0074006 | -0.057467 | 0.1285 | 0.032178 | 0.038418 | -0.039792 | -0.023746 | 7.627e-05 | -0.014691 | 0.027585 | 0.060047 | -0.019192 | -0.023669 | 60.3424 | -62.0316 | 0.10529 | -62.2925 | 60.1273 | -62.2147 | -62.1414 | 0.11902 | 0.17395 | -62.4344 | 60.0632 | 60.054 | -62.1368 | -62.3337 | 0.01831 | 0.091553 | -0.10986 | 0.20142 | -0.059509 | -0.15106 | 0.10529 | 0.09613 | -0.10071 | -0.17395 | 62.352 | -0.20142 | -0.10071 | -0.18311 | 122.3602 | 122.5754 | 62.3383 | -122.3785 | 122.2961 | 122.287 | 62.4069 | -122.5708
337.3281 | 122.7036 | -62.265 | 60.1868 | -0.00022891 | -0.052553 | 0.12636 | 0.03346 | 0.039059 | -0.032742 | -0.023319 | -0.0075532 | -0.010205 | 0.028226 | 0.06197 | -0.022396 | -0.024524 | 60.2966 | -62.1414 | 0.07782 | -62.3795 | 60.1456 | -62.2833 | -62.1872 | 0.059509 | 0.082397 | -62.5488 | 60.1089 | 60.0769 | -62.1918 | -62.3703 | -0.01831 | 0.07782 | -0.041199 | 0.1236 | -0.11444 | -0.19226 | 0.10986 | 0.073243 | -0.10529 | -0.07782 | 62.3245 | -0.28381 | -0.17853 | -0.10986 | 122.4106 | 122.5616 | 62.3428 | -122.374 | 122.374 | 122.3419 | 62.3474 | -122.5571
339.1094 | 122.644 | -62.2559 | 60.2371 | -0.015487 | -0.056826 | 0.12935 | 0.034955 | 0.038204 | -0.04086 | -0.026096 | 7.627e-05 | -0.014264 | 0.029508 | 0.059834 | -0.024319 | -0.023242 | 60.3607 | -61.9904 | 0.15106 | -62.2833 | 60.1364 | -62.2009 | -62.1277 | 0.091553 | 0.15106 | -62.384 | 60.0906 | 60.1181 | -62.1277 | -62.2833 | 0.054931 | 0.12817 | -0.10071 | 0.2655 | -0.027466 | -0.15564 | 0.1236 | 0.12817 | -0.027466 | -0.14648 | 62.3474 | -0.12817 | -0.10071 | -0.11902 | 122.3923 | 122.6166 | 62.4069 | -122.3648 | 122.3465 | 122.374 | 62.4069 | -122.5204
340.8281 | 122.612 | -62.233 | 60.26 | -0.00022891 | -0.05704 | 0.12636 | 0.032605 | 0.035641 | -0.041501 | -0.026096 | 7.627e-05 | -0.01405 | 0.027585 | 0.059834 | -0.021969 | -0.024951 | 60.3561 | -62.0544 | 0.086975 | -62.3108 | 60.1456 | -62.178 | -62.1323 | 0.09613 | 0.13733 | -62.4298 | 60.1227 | 60.1181 | -62.1094 | -62.3016 | 0.054931 | 0.10071 | -0.11444 | 0.17853 | -0.07782 | -0.17853 | 0.09613 | 0.1236 | -0.068665 | -0.13733 | 62.3291 | -0.19684 | -0.12817 | -0.14191 | 122.3785 | 122.5891 | 62.3199 | -122.3923 | 122.3557 | 122.3511 | 62.3703 | -122.5616
342.6094 | 122.7493 | -62.2421 | 60.173 | -0.00022891 | -0.052981 | 0.12658 | 0.030469 | 0.036923 | -0.033169 | -0.023746 | 0.0077058 | -0.010205 | 0.029508 | 0.05962 | -0.018337 | -0.024738 | 60.3104 | -62.1368 | 0.086975 | -62.3566 | 60.1364 | -62.2787 | -62.178 | 0.054932 | 0.086975 | -62.5397 | 60.1089 | 60.0677 | -62.1735 | -62.3886 | -0.036622 | 0.064086 | -0.036621 | 0.10529 | -0.11444 | -0.17853 | 0.13733 | 0.068664 | -0.14648 | -0.064087 | 62.2971 | -0.29755 | -0.15106 | -0.10529 | 122.3785 | 122.5525 | 62.3291 | -122.3511 | 122.3511 | 122.3099 | 62.3291 | -122.5616
344.375 | 122.644 | -62.2375 | 60.26 | 0.0074006 | -0.056826 | 0.1317 | 0.031964 | 0.038845 | -0.041501 | -0.02631 | -0.015182 | -0.012555 | 0.030362 | 0.057057 | -0.024746 | -0.023669 | 60.3058 | -62.0728 | 0.059509 | -62.3154 | 60.1593 | -62.1918 | -62.1185 | 0.050354 | 0.091553 | -62.4481 | 60.1364 | 60.1181 | -62.1231 | -62.3016 | 0.045777 | 0.11902 | -0.10071 | 0.16479 | -0.07782 | -0.19684 | 0.045776 | 0.11444 | -0.064087 | -0.1236 | 62.2879 | -0.21057 | -0.14648 | -0.14191 | 122.3969 | 122.5433 | 62.2971 | -122.3785 | 122.374 | 122.3557 | 62.3291 | -122.5616
346.0938 | 122.7081 | -62.2238 | 60.1959 | -0.00022891 | -0.056185 | 0.12615 | 0.030469 | 0.037991 | -0.035519 | -0.025882 | 7.627e-05 | -0.013836 | 0.027158 | 0.05962 | -0.020687 | -0.02431 | 60.3745 | -62.0453 | 0.10071 | -62.2879 | 60.1273 | -62.2147 | -62.1323 | 0.12817 | 0.18768 | -62.4344 | 60.0861 | 60.054 | -62.1368 | -62.3199 | 0.009155 | 0.091553 | -0.068665 | 0.17853 | -0.064087 | -0.15564 | 0.17853 | 0.086975 | -0.09613 | -0.10986 | 62.352 | -0.21057 | -0.11444 | -0.14191 | 122.3511 | 122.5983 | 62.3245 | -122.3282 | 122.3099 | 122.2778 | 62.4115 | -122.5159
347.875 | 122.6761 | -62.2238 | 60.2325 | -0.00022891 | -0.05768 | 0.13042 | 0.029401 | 0.036709 | -0.038296 | -0.024173 | -0.0075532 | -0.013195 | 0.026304 | 0.057484 | -0.019833 | -0.024951 | 60.3699 | -62.0453 | 0.10986 | -62.2833 | 60.1273 | -62.1964 | -62.1231 | 0.12817 | 0.16937 | -62.4252 | 60.0998 | 60.0723 | -62.1231 | -62.3245 | 0.027466 | 0.10071 | -0.10529 | 0.17853 | -0.059509 | -0.16022 | 0.13733 | 0.10071 | -0.10071 | -0.13275 | 62.352 | -0.20142 | -0.10071 | -0.16022 | 122.3511 | 122.5937 | 62.3337 | -122.3557 | 122.3236 | 122.2961 | 62.3932 | -122.5571
349.6719 | 122.6852 | -62.2284 | 60.2005 | -0.00022891 | -0.054903 | 0.12572 | 0.030042 | 0.036282 | -0.032956 | -0.023105 | -0.0075532 | -0.0099912 | 0.02844 | 0.060688 | -0.01791 | -0.024524 | 60.2554 | -62.1643 | 0.050354 | -62.384 | 60.1364 | -62.2742 | -62.2101 | 0.032043 | 0.054932 | -62.5671 | 60.1273 | 60.0815 | -62.1918 | -62.3978 | -0.045776 | 0.018311 | -0.064086 | 0.064087 | -0.15564 | -0.17395 | 0.054932 | 0.036622 | -0.16937 | -0.073242 | 62.2604 | -0.33874 | -0.16937 | -0.11902 | 122.3648 | 122.4838 | 62.2787 | -122.4106 | 122.3557 | 122.3099 | 62.2833 | -122.5983
351.4531 | 122.6944 | -62.2604 | 60.1822 | 0.0074006 | -0.053835 | 0.12807 | 0.032392 | 0.0397 | -0.034024 | -0.024601 | 7.627e-05 | -0.013409 | 0.02844 | 0.060047 | -0.019406 | -0.020465 | 60.2509 | -62.178 | 0.041199 | -62.4023 | 60.1181 | -62.2787 | -62.1918 | 0.032043 | 0.064087 | -62.59 | 60.1318 | 60.0998 | -62.2101 | -62.3886 | -0.018311 | 0.068665 | -0.064087 | 0.082397 | -0.14191 | -0.21057 | 0.068664 | 0.050354 | -0.12817 | -0.050354 | 62.2925 | -0.32959 | -0.20142 | -0.082398 | 122.3785 | 122.5113 | 62.3016 | -122.374 | 122.3923 | 122.3602 | 62.3245 | -122.5708
353.1719 | 122.7539 | -62.2147 | 60.173 | -0.0078584 | -0.055971 | 0.12572 | 0.034314 | 0.035855 | -0.03616 | -0.025242 | 7.627e-05 | -0.010418 | 0.030362 | 0.059834 | -0.023464 | -0.023669 | 60.2463 | -62.1597 | 0.036621 | -62.3749 | 60.1685 | -62.2513 | -62.1918 | -0.009155 | 0.032043 | -62.5534 | 60.1364 | 60.0998 | -62.1918 | -62.3566 | -0.036621 | 0.022889 | -0.004578 | 0.054932 | -0.16022 | -0.18311 | 0.073242 | 0.022889 | -0.14191 | -0.036621 | 62.2055 | -0.33875 | -0.19684 | -0.073243 | 122.3831 | 122.4609 | 62.2513 | -122.3648 | 122.3511 | 122.3145 | 62.2467 | -122.5296
354.9531 | 122.6669 | -62.2375 | 60.2188 | -0.00022891 | -0.057894 | 0.13021 | 0.033673 | 0.035427 | -0.042569 | -0.028019 | 0.0077058 | -0.014264 | 0.026731 | 0.058338 | -0.026455 | -0.023456 | 60.3516 | -62.0041 | 0.13275 | -62.2696 | 60.1456 | -62.178 | -62.1094 | 0.091553 | 0.14191 | -62.3886 | 60.0952 | 60.0952 | -62.1185 | -62.3016 | 0.059509 | 0.12817 | -0.073242 | 0.23346 | -0.032043 | -0.16022 | 0.13275 | 0.11902 | -0.064087 | -0.1236 | 62.3291 | -0.15106 | -0.086975 | -0.1236 | 122.3831 | 122.5891 | 62.3703 | -122.3282 | 122.3328 | 122.3328 | 62.3795 | -122.5204
356.6719 | 122.6349 | -62.2513 | 60.2417 | -0.0078584 | -0.060671 | 0.1285 | 0.032819 | 0.036282 | -0.040005 | -0.029728 | 7.627e-05 | -0.0164 | 0.025663 | 0.056416 | -0.022183 | -0.022174 | 60.3104 | -62.0636 | 0.064087 | -62.2925 | 60.1547 | -62.1918 | -62.1231 | 0.050354 | 0.086975 | -62.4481 | 60.1227 | 60.1044 | -62.1414 | -62.3383 | 0.05951 | 0.12817 | -0.086975 | 0.18768 | -0.041198 | -0.16937 | 0.068665 | 0.10986 | -0.086975 | -0.11902 | 62.3016 | -0.19684 | -0.10986 | -0.13733 | 122.406 | 122.5616 | 62.3154 | -122.3648 | 122.374 | 122.3557 | 62.3383 | -122.58
358.4375 | 122.7493 | -62.2101 | 60.1868 | 0.0074006 | -0.055971 | 0.12359 | 0.031964 | 0.038418 | -0.034878 | -0.024814 | -0.0075532 | -0.0099912 | 0.028013 | 0.061329 | -0.019833 | -0.023883 | 60.2829 | -62.178 | 0.009155 | -62.3795 | 60.1822 | -62.2513 | -62.2147 | 0.07782 | 0.082397 | -62.5397 | 60.1547 | 60.0952 | -62.1506 | -62.3795 | -0.041199 | -0.004578 | -0.004578 | 0.032043 | -0.16937 | -0.16479 | 0.09613 | 0.059509 | -0.16937 | -0.032044 | 62.2879 | -0.32959 | -0.16022 | -0.091553 | 122.3923 | 122.493 | 62.2192 | -122.4014 | 122.3648 | 122.3053 | 62.2925 | -122.5662
360.2188 | 122.699 | -62.2147 | 60.1959 | 0.0074006 | -0.054262 | 0.12743 | 0.029828 | 0.036923 | -0.032528 | -0.023319 | -0.0075532 | -0.010632 | 0.027799 | 0.061115 | -0.019192 | -0.02431 | 60.2463 | -62.2101 | 0 | -62.3795 | 60.1685 | -62.2421 | -62.2101 | 0 | 0.032043 | -62.6038 | 60.1318 | 60.0952 | -62.178 | -62.3703 | -0.027465 | 0.004578 | -0.027466 | 0.004578 | -0.16479 | -0.16937 | 0.050354 | 0.036621 | -0.15564 | -0.064087 | 62.2147 | -0.3891 | -0.23346 | -0.10071 | 122.3831 | 122.4609 | 62.2147 | -122.406 | 122.3465 | 122.3099 | 62.2467 | -122.5662
362.0156 | 122.6715 | -62.2513 | 60.173 | -0.015487 | -0.055544 | 0.12828 | 0.033887 | 0.037564 | -0.038296 | -0.024814 | 7.627e-05 | -0.011486 | 0.027372 | 0.060902 | -0.023251 | -0.021533 | 60.2417 | -62.1506 | 0.045776 | -62.3886 | 60.1501 | -62.2513 | -62.2009 | -0.004578 | 0.004578 | -62.558 | 60.1547 | 60.1227 | -62.178 | -62.3703 | 0 | 0.050354 | -0.022889 | 0.10071 | -0.13733 | -0.18768 | 0.068664 | 0.073242 | -0.11902 | -0.018311 | 62.2467 | -0.3067 | -0.18768 | -0.050354 | 122.4014 | 122.493 | 62.2971 | -122.374 | 122.406 | 122.374 | 62.2559 | -122.5433
363.75 | 122.7356 | -62.2147 | 60.2051 | 0.0074006 | -0.058321 | 0.12658 | 0.03111 | 0.037777 | -0.037014 | -0.02396 | 0.0077058 | -0.011914 | 0.030149 | 0.061756 | -0.019192 | -0.023029 | 60.2554 | -62.1689 | -0.009155 | -62.3749 | 60.1776 | -62.2375 | -62.2101 | 0.036621 | 0.059509 | -62.5442 | 60.1181 | 60.0998 | -62.1735 | -62.3611 | -0.022888 | 0.004578 | -0.027466 | 0.045777 | -0.16022 | -0.1648 | 0.050354 | 0.041199 | -0.14648 | -0.086975 | 62.2513 | -0.32959 | -0.1831 | -0.10529 | 122.3923 | 122.4701 | 62.2055 | -122.4152 | 122.3328 | 122.3145 | 62.2742 | -122.5662
365.5156 | 122.6715 | -62.2559 | 60.1868 | -0.00022891 | -0.055117 | 0.12572 | 0.032819 | 0.035855 | -0.033383 | -0.022251 | 0.015335 | -0.011486 | 0.030149 | 0.059834 | -0.02261 | -0.023029 | 60.2554 | -62.1964 | 0.009155 | -62.3978 | 60.1273 | -62.2742 | -62.2055 | 0.004578 | 0.064087 | -62.59 | 60.1364 | 60.1044 | -62.1872 | -62.3886 | -0.018311 | 0.050354 | -0.05951 | 0.059509 | -0.14191 | -0.19226 | 0.068664 | 0.068664 | -0.13275 | -0.050354 | 62.2604 | -0.33417 | -0.20142 | -0.082398 | 122.3831 | 122.5113 | 62.265 | -122.3923 | 122.3923 | 122.3602 | 62.3199 | -122.5754
367.2969 | 122.6028 | -62.2375 | 60.2646 | 0.0074006 | -0.056612 | 0.12978 | 0.031751 | 0.03735 | -0.04086 | -0.025882 | 0.015335 | -0.015759 | 0.025663 | 0.058979 | -0.023678 | -0.022601 | 60.3424 | -62.0407 | 0.082397 | -62.3016 | 60.1227 | -62.1597 | -62.1185 | 0.07782 | 0.12817 | -62.439 | 60.1044 | 60.1089 | -62.1185 | -62.3016 | 0.07782 | 0.11902 | -0.14191 | 0.19684 | -0.064087 | -0.18311 | 0.07782 | 0.11902 | -0.064087 | -0.16022 | 62.3154 | -0.20142 | -0.13733 | -0.15564 | 122.3602 | 122.58 | 62.3199 | -122.3831 | 122.3419 | 122.3465 | 62.3657 | -122.5662
369.0781 | 122.5937 | -62.2513 | 60.2646 | 0.0074006 | -0.05768 | 0.12764 | 0.034528 | 0.037564 | -0.041714 | -0.024814 | 7.627e-05 | -0.011273 | 0.02609 | 0.058125 | -0.024532 | -0.023669 | 60.3195 | -62.0544 | 0.064087 | -62.2971 | 60.1639 | -62.1826 | -62.1048 | 0.068665 | 0.10071 | -62.4527 | 60.1135 | 60.1135 | -62.1231 | -62.2971 | 0.068665 | 0.14649 | -0.10071 | 0.19684 | -0.045776 | -0.19226 | 0.054932 | 0.12817 | -0.045776 | -0.15106 | 62.3199 | -0.20142 | -0.15564 | -0.15106 | 122.4152 | 122.5708 | 62.3154 | -122.3694 | 122.3648 | 122.3648 | 62.352 | -122.5616
370.7969 | 122.7173 | -62.2238 | 60.1639 | 0.01503 | -0.056826 | 0.12722 | 0.030255 | 0.036495 | -0.034878 | -0.026096 | -0.015182 | -0.010632 | 0.026517 | 0.058125 | -0.018337 | -0.026019 | 60.2142 | -62.2284 | -0.004578 | -62.4023 | 60.1685 | -62.2467 | -62.1735 | 0.036621 | 0.027466 | -62.5763 | 60.0998 | 60.1089 | -62.1735 | -62.3795 | -0.022888 | 0.050354 | 0.004578 | -0.004578 | -0.17853 | -0.22888 | 0.050354 | 0.050354 | -0.15564 | -0.064087 | 62.2604 | -0.35248 | -0.19684 | -0.054931 | 122.3923 | 122.438 | 62.2192 | -122.3373 | 122.3236 | 122.3328 | 62.2513 | -122.5433
372.5781 | 122.6028 | -62.233 | 60.26 | 0.0074006 | -0.05704 | 0.13042 | 0.033032 | 0.037991 | -0.040005 | -0.028232 | 0.0077058 | -0.016613 | 0.029081 | 0.056202 | -0.026028 | -0.023883 | 60.3195 | -62.0682 | 0.059509 | -62.3154 | 60.1318 | -62.1735 | -62.1323 | 0.064087 | 0.086975 | -62.4344 | 60.1227 | 60.1044 | -62.1231 | -62.3199 | 0.059509 | 0.10071 | -0.12817 | 0.16479 | -0.082398 | -0.18311 | 0.059509 | 0.10986 | -0.086975 | -0.13733 | 62.2971 | -0.20142 | -0.11444 | -0.15564 | 122.3648 | 122.5525 | 62.2925 | -122.3923 | 122.3557 | 122.3373 | 62.3199 | -122.58
374.3594 | 122.7448 | -62.2147 | 60.2142 | 0.01503 | -0.055971 | 0.1285 | 0.031537 | 0.036709 | -0.034451 | -0.024387 | 0.0077058 | -0.011914 | 0.02844 | 0.061329 | -0.021542 | -0.024951 | 60.3058 | -62.114 | 0.032043 | -62.3291 | 60.1685 | -62.2238 | -62.146 | 0.10529 | 0.14191 | -62.4527 | 60.1089 | 60.0861 | -62.1414 | -62.3245 | -0.009155 | 0.068665 | -0.045776 | 0.10071 | -0.11444 | -0.18311 | 0.091553 | 0.073243 | -0.10986 | -0.10529 | 62.3199 | -0.23804 | -0.12817 | -0.12817 | 122.3831 | 122.5204 | 62.2467 | -122.3602 | 122.3236 | 122.3007 | 62.3566 | -122.5388
376.0625 | 122.6715 | -62.2284 | 60.2554 | -0.00022891 | -0.06003 | 0.13106 | 0.031537 | 0.035641 | -0.04086 | -0.027378 | 0.0077058 | -0.015973 | 0.024381 | 0.059406 | -0.023037 | -0.024738 | 60.3653 | -61.9858 | 0.13275 | -62.265 | 60.141 | -62.178 | -62.1185 | 0.11444 | 0.14648 | -62.3795 | 60.1089 | 60.0998 | -62.1368 | -62.3291 | 0.050354 | 0.10986 | -0.11444 | 0.24262 | -0.036621 | -0.14648 | 0.10986 | 0.091553 | -0.10071 | -0.14648 | 62.3428 | -0.15106 | -0.050354 | -0.15564 | 122.3694 | 122.5937 | 62.3611 | -122.374 | 122.3373 | 122.3282 | 62.3749 | -122.5845
377.8438 | 122.6578 | -62.2559 | 60.2005 | -0.0078584 | -0.053835 | 0.12807 | 0.034314 | 0.036068 | -0.033169 | -0.026737 | 7.627e-05 | -0.0117 | 0.029508 | 0.061115 | -0.02261 | -0.02431 | 60.2509 | -62.1552 | 0.027466 | -62.3795 | 60.1776 | -62.2375 | -62.1964 | -0.004578 | 0.004578 | -62.5626 | 60.1547 | 60.0861 | -62.1826 | -62.3703 | 0.01831 | 0.059509 | -0.022888 | 0.10071 | -0.1236 | -0.18311 | 0.050354 | 0.073242 | -0.11444 | -0.045776 | 62.2513 | -0.3067 | -0.19226 | -0.11444 | 122.4335 | 122.5067 | 62.2833 | -122.3969 | 122.4106 | 122.3419 | 62.2604 | -122.5708
379.5469 | 122.6257 | -62.2284 | 60.2554 | -0.00022891 | -0.06238 | 0.12978 | 0.032392 | 0.034359 | -0.040432 | -0.026951 | 7.627e-05 | -0.012341 | 0.026731 | 0.058552 | -0.022823 | -0.025165 | 60.3287 | -62.0636 | 0.07782 | -62.2971 | 60.2005 | -62.1826 | -62.1231 | 0.059509 | 0.086975 | -62.4527 | 60.1135 | 60.1227 | -62.0865 | -62.2925 | 0.045777 | 0.10529 | -0.054932 | 0.16479 | -0.068664 | -0.17395 | 0.073242 | 0.14191 | -0.064086 | -0.14191 | 62.2879 | -0.2243 | -0.16022 | -0.13275 | 122.4289 | 122.5571 | 62.3062 | -122.3785 | 122.3419 | 122.3511 | 62.3154 | -122.5479
381.3125 | 122.7448 | -62.2375 | 60.1913 | -0.00022891 | -0.056185 | 0.127 | 0.029614 | 0.035427 | -0.037228 | -0.024173 | 7.627e-05 | -0.010205 | 0.02374 | 0.059406 | -0.019619 | -0.025165 | 60.3058 | -62.1506 | 0.022888 | -62.3657 | 60.1593 | -62.2513 | -62.1552 | 0.10529 | 0.1236 | -62.4756 | 60.1227 | 60.0861 | -62.146 | -62.3337 | -0.013733 | 0.082398 | -0.032043 | 0.086975 | -0.12817 | -0.21057 | 0.11444 | 0.091553 | -0.09613 | -0.068664 | 62.3428 | -0.23804 | -0.14191 | -0.10528 | 122.3969 | 122.5433 | 62.2604 | -122.3465 | 122.3602 | 122.3236 | 62.3611 | -122.525
383.0312 | 122.7356 | -62.2238 | 60.1776 | -0.00022891 | -0.055544 | 0.12743 | 0.032605 | 0.036282 | -0.033596 | -0.025242 | 7.627e-05 | -0.010632 | 0.029081 | 0.060261 | -0.021969 | -0.024951 | 60.2737 | -62.2055 | -0.018311 | -62.3886 | 60.1593 | -62.2513 | -62.1964 | 0.050354 | 0.041199 | -62.5626 | 60.1318 | 60.1364 | -62.1735 | -62.3611 | -0.027466 | 0.027466 | -0.01831 | 0.018311 | -0.16479 | -0.19226 | 0.096131 | 0.050354 | -0.13733 | -0.045776 | 62.2742 | -0.33875 | -0.20142 | -0.041198 | 122.3831 | 122.4976 | 62.2055 | -122.374 | 122.3557 | 122.3602 | 62.265 | -122.5388
384.8125 | 122.6074 | -62.2238 | 60.2234 | -0.0078584 | -0.058748 | 0.12722 | 0.033246 | 0.039273 | -0.040219 | -0.027591 | -0.015182 | -0.012555 | 0.026944 | 0.060902 | -0.024746 | -0.023669 | 60.347 | -62.0316 | 0.10986 | -62.2879 | 60.1181 | -62.1918 | -62.1277 | 0.1236 | 0.16022 | -62.4115 | 60.0861 | 60.0998 | -62.0911 | -62.2833 | 0.032044 | 0.09613 | -0.10529 | 0.19226 | -0.064087 | -0.16022 | 0.1236 | 0.13275 | -0.059509 | -0.13733 | 62.3474 | -0.18768 | -0.12817 | -0.1236 | 122.3419 | 122.5708 | 62.3337 | -122.3511 | 122.3099 | 122.3236 | 62.384 | -122.5067
386.5156 | 122.6532 | -62.2421 | 60.2371 | -0.0078584 | -0.059817 | 0.13063 | 0.031537 | 0.036495 | -0.042355 | -0.026523 | 7.627e-05 | -0.016613 | 0.026731 | 0.059406 | -0.022183 | -0.023669 | 60.3149 | -62.0636 | 0.082397 | -62.2925 | 60.1501 | -62.178 | -62.1002 | 0.07782 | 0.11902 | -62.4161 | 60.1089 | 60.0952 | -62.1094 | -62.2787 | 0.064086 | 0.14191 | -0.086976 | 0.17853 | -0.050354 | -0.19226 | 0.077819 | 0.13275 | -0.036622 | -0.12817 | 62.3199 | -0.17395 | -0.13733 | -0.14191 | 122.3923 | 122.5571 | 62.3245 | -122.3373 | 122.3511 | 122.3373 | 62.3611 | -122.5159
388.2969 | 122.5754 | -62.2604 | 60.2417 | -0.00022891 | -0.057253 | 0.12957 | 0.031964 | 0.035855 | -0.037655 | -0.027164 | 7.627e-05 | -0.013623 | 0.028653 | 0.061329 | -0.021542 | -0.026019 | 60.3287 | -62.0499 | 0.12817 | -62.2879 | 60.1318 | -62.2147 | -62.1597 | 0.027466 | 0.059509 | -62.5031 | 60.1135 | 60.0815 | -62.1735 | -62.3291 | 0.045776 | 0.10071 | -0.10986 | 0.21057 | -0.027466 | -0.12817 | 0.086975 | 0.086975 | -0.068665 | -0.12817 | 62.2879 | -0.24261 | -0.17395 | -0.16022 | 122.3923 | 122.5891 | 62.3886 | -122.4014 | 122.374 | 122.3419 | 62.3199 | -122.5708
390.0625 | 122.5983 | -62.2513 | 60.2463 | -0.00022891 | -0.061312 | 0.12893 | 0.029828 | 0.034573 | -0.03851 | -0.026096 | 0.0077058 | -0.0117 | 0.024808 | 0.060474 | -0.021114 | -0.02431 | 60.3287 | -62.0316 | 0.073242 | -62.2971 | 60.1501 | -62.1552 | -62.1094 | 0.082397 | 0.10071 | -62.439 | 60.1227 | 60.1089 | -62.1002 | -62.3062 | 0.096131 | 0.14191 | -0.096131 | 0.21973 | -0.045776 | -0.18768 | 0.082397 | 0.15106 | -0.054931 | -0.1236 | 62.3337 | -0.18768 | -0.13275 | -0.13733 | 122.4014 | 122.58 | 62.3245 | -122.3557 | 122.374 | 122.3602 | 62.352 | -122.5525
391.8438 | 122.6486 | -62.2238 | 60.2371 | -0.00022891 | -0.056826 | 0.1285 | 0.03346 | 0.036923 | -0.038083 | -0.025455 | 0.0077058 | -0.012127 | 0.027158 | 0.057484 | -0.024105 | -0.026874 | 60.3287 | -62.059 | 0.050354 | -62.3108 | 60.1685 | -62.1826 | -62.1231 | 0.068665 | 0.07782 | -62.4481 | 60.1273 | 60.1227 | -62.1002 | -62.2971 | 0.041199 | 0.10071 | -0.068665 | 0.16479 | -0.086975 | -0.18768 | 0.091552 | 0.1236 | -0.073242 | -0.10986 | 62.2925 | -0.2243 | -0.15106 | -0.11444 | 122.3923 | 122.5525 | 62.2742 | -122.3602 | 122.3511 | 122.3465 | 62.3016 | -122.5342
393.6406 | 122.7219 | -62.2101 | 60.1547 | -0.00022891 | -0.054262 | 0.12529 | 0.030255 | 0.037991 | -0.031033 | -0.025455 | 0.0077058 | -0.0093502 | 0.028013 | 0.061329 | -0.019406 | -0.025806 | 60.2646 | -62.1872 | -0.032043 | -62.3657 | 60.1685 | -62.2513 | -62.1735 | 0.064087 | 0.064087 | -62.558 | 60.1318 | 60.1044 | -62.1414 | -62.3428 | -0.041199 | 0.036621 | 0.013733 | 0.022888 | -0.15564 | -0.19226 | 0.10986 | 0.068665 | -0.13275 | -0.022888 | 62.2742 | -0.3479 | -0.21515 | -0.050354 | 122.3785 | 122.4747 | 62.178 | -122.3282 | 122.3419 | 122.3145 | 62.2742 | -122.4976
395.3594 | 122.7127 | -62.233 | 60.2097 | -0.00022891 | -0.055971 | 0.12743 | 0.029614 | 0.038204 | -0.035946 | -0.02396 | 7.627e-05 | -0.010846 | 0.028013 | 0.059193 | -0.018124 | -0.025806 | 60.3607 | -62.0224 | 0.09613 | -62.2742 | 60.141 | -62.2009 | -62.1506 | 0.14191 | 0.16937 | -62.4161 | 60.0723 | 60.0494 | -62.1277 | -62.3199 | 0.032043 | 0.082397 | -0.068665 | 0.21057 | -0.041199 | -0.1236 | 0.15106 | 0.10529 | -0.086975 | -0.13733 | 62.3749 | -0.18311 | -0.096131 | -0.16022 | 122.374 | 122.5937 | 62.3291 | -122.3602 | 122.3053 | 122.2824 | 62.4023 | -122.5296
397.1406 | 122.7539 | -62.2192 | 60.173 | -0.0078584 | -0.054476 | 0.12786 | 0.031323 | 0.036282 | -0.035519 | -0.023746 | 7.627e-05 | -0.010205 | 0.027585 | 0.060261 | -0.021328 | -0.02431 | 60.2692 | -62.1552 | -0.009155 | -62.3795 | 60.1593 | -62.233 | -62.1735 | 0.073242 | 0.086975 | -62.5305 | 60.0998 | 60.0723 | -62.1597 | -62.3611 | -0.013733 | 0.045776 | -0.013733 | 0.064087 | -0.16022 | -0.20599 | 0.09613 | 0.059509 | -0.14191 | -0.073243 | 62.2925 | -0.31128 | -0.16937 | -0.10071 | 122.3785 | 122.4884 | 62.2101 | -122.3465 | 122.319 | 122.2916 | 62.3062 | -122.5342
398.875 | 122.6349 | -62.2055 | 60.228 | -0.0078584 | -0.057253 | 0.13063 | 0.035169 | 0.035641 | -0.040219 | -0.026523 | 7.627e-05 | -0.013409 | 0.027158 | 0.059406 | -0.023464 | -0.023242 | 60.3607 | -62.0178 | 0.11444 | -62.2513 | 60.173 | -62.1826 | -62.1185 | 0.086975 | 0.13275 | -62.3886 | 60.1044 | 60.0906 | -62.1048 | -62.3016 | 0.022888 | 0.086975 | -0.054931 | 0.18768 | -0.045777 | -0.13275 | 0.13275 | 0.10071 | -0.096131 | -0.1236 | 62.2925 | -0.18311 | -0.086975 | -0.13733 | 122.3785 | 122.5662 | 62.3199 | -122.3465 | 122.3099 | 122.2961 | 62.3383 | -122.5296
400.6406 | 122.6532 | -62.2467 | 60.2234 | -0.00022891 | -0.058535 | 0.12786 | 0.033032 | 0.036282 | -0.040005 | -0.028019 | 7.627e-05 | -0.013409 | 0.026304 | 0.060474 | -0.023037 | -0.025165 | 60.3653 | -62.0041 | 0.10986 | -62.265 | 60.1501 | -62.1735 | -62.1277 | 0.10071 | 0.13733 | -62.3886 | 60.1227 | 60.1044 | -62.1094 | -62.2787 | 0.073242 | 0.11902 | -0.073243 | 0.24262 | -0.018311 | -0.13733 | 0.14191 | 0.13733 | -0.032044 | -0.10071 | 62.3474 | -0.14191 | -0.10986 | -0.11902 | 122.3969 | 122.612 | 62.3566 | -122.3511 | 122.3694 | 122.3511 | 62.384 | -122.5021
402.4219 | 122.6303 | -62.2742 | 60.173 | 0.0074006 | -0.054262 | 0.12615 | 0.03346 | 0.039059 | -0.037014 | -0.025242 | 0.0077058 | -0.010418 | 0.029294 | 0.060902 | -0.021114 | -0.024524 | 60.2692 | -62.1597 | 0.045776 | -62.3795 | 60.1685 | -62.2513 | -62.178 | -0.009155 | 0.004578 | -62.5534 | 60.141 | 60.1089 | -62.2009 | -62.3657 | 0.022888 | 0.09613 | -0.004578 | 0.11444 | -0.10529 | -0.20142 | 0.09613 | 0.073242 | -0.091553 | -0.032044 | 62.265 | -0.27924 | -0.18768 | -0.064087 | 122.4426 | 122.5433 | 62.3199 | -122.3511 | 122.4152 | 122.3831 | 62.2787 | -122.5388
404.2031 | 122.6303 | -62.2421 | 60.2188 | 0.0074006 | -0.05704 | 0.12828 | 0.032605 | 0.034573 | -0.039151 | -0.025028 | 7.627e-05 | -0.013409 | 0.027158 | 0.058552 | -0.023464 | -0.025806 | 60.3928 | -61.972 | 0.15106 | -62.2696 | 60.1364 | -62.1872 | -62.1277 | 0.13275 | 0.16937 | -62.3657 | 60.1089 | 60.0632 | -62.1002 | -62.3016 | 0.054931 | 0.11444 | -0.082397 | 0.27008 | -0.027466 | -0.14191 | 0.17395 | 0.14191 | -0.05951 | -0.10986 | 62.3749 | -0.1236 | -0.064087 | -0.15564 | 122.3785 | 122.6349 | 62.3932 | -122.3465 | 122.3511 | 122.3053 | 62.4115 | -122.5204
405.9688 | 122.6257 | -62.2421 | 60.2463 | -0.00022891 | -0.058748 | 0.12786 | 0.031751 | 0.034146 | -0.037869 | -0.027378 | 7.627e-05 | -0.015545 | 0.026304 | 0.058125 | -0.024319 | -0.023669 | 60.3836 | -61.972 | 0.14648 | -62.2513 | 60.1318 | -62.1826 | -62.1231 | 0.11902 | 0.16022 | -62.3703 | 60.0815 | 60.0769 | -62.1323 | -62.2879 | 0.059509 | 0.11902 | -0.11444 | 0.27008 | -0.009156 | -0.12817 | 0.13733 | 0.10986 | -0.045777 | -0.16479 | 62.3611 | -0.12817 | -0.082397 | -0.16937 | 122.374 | 122.6257 | 62.3886 | -122.3694 | 122.3236 | 122.319 | 62.4023 | -122.5342
407.7031 | 122.5983 | -62.2421 | 60.2417 | 0.01503 | -0.058108 | 0.12999 | 0.030896 | 0.037991 | -0.038723 | -0.02631 | 7.627e-05 | -0.012341 | 0.025449 | 0.057911 | -0.02026 | -0.024524 | 60.3653 | -62.0224 | 0.10071 | -62.2971 | 60.1456 | -62.1597 | -62.0956 | 0.09613 | 0.14191 | -62.439 | 60.1181 | 60.0998 | -62.0773 | -62.3154 | 0.082397 | 0.14648 | -0.09613 | 0.21973 | -0.054932 | -0.20142 | 0.1236 | 0.16479 | -0.073243 | -0.1236 | 62.3383 | -0.19684 | -0.1236 | -0.14191 | 122.3877 | 122.6074 | 62.3428 | -122.3373 | 122.3602 | 122.3419 | 62.384 | -122.5571
409.4688 | 122.6395 | -62.2238 | 60.2463 | -0.00022891 | -0.060244 | 0.12935 | 0.033032 | 0.035 | -0.039578 | -0.025882 | 7.627e-05 | -0.013623 | 0.026731 | 0.057484 | -0.021114 | -0.023669 | 60.3836 | -61.9858 | 0.13733 | -62.2467 | 60.1273 | -62.178 | -62.1368 | 0.12817 | 0.16937 | -62.384 | 60.1089 | 60.0677 | -62.1368 | -62.2879 | 0.045776 | 0.086975 | -0.11902 | 0.23804 | -0.022888 | -0.10986 | 0.13733 | 0.086975 | -0.064087 | -0.13733 | 62.352 | -0.16022 | -0.09613 | -0.17853 | 122.3511 | 122.6074 | 62.3611 | -122.3831 | 122.3328 | 122.2916 | 62.3932 | -122.5342
411.2344 | 122.6578 | -62.2101 | 60.2325 | -0.0078584 | -0.058748 | 0.12999 | 0.032178 | 0.038204 | -0.039364 | -0.026737 | -0.0075532 | -0.014691 | 0.029294 | 0.056843 | -0.023892 | -0.025165 | 60.347 | -62.027 | 0.09613 | -62.2787 | 60.1501 | -62.2009 | -62.1368 | 0.091553 | 0.13733 | -62.3978 | 60.0998 | 60.0861 | -62.0956 | -62.3016 | 0.009155 | 0.073242 | -0.082398 | 0.1831 | -0.068665 | -0.14191 | 0.11444 | 0.11444 | -0.091553 | -0.13275 | 62.3016 | -0.18768 | -0.09613 | -0.14648 | 122.3602 | 122.5571 | 62.3062 | -122.3694 | 122.3099 | 122.2961 | 62.3474 | -122.5342
413.0312 | 122.5754 | -62.2696 | 60.228 | -0.00022891 | -0.054262 | 0.12743 | 0.031537 | 0.036495 | -0.035733 | -0.024173 | -0.0075532 | -0.011486 | 0.027585 | 0.059406 | -0.02261 | -0.028155 | 60.3516 | -62.027 | 0.11902 | -62.2925 | 60.141 | -62.2284 | -62.1506 | 0.045776 | 0.073242 | -62.4802 | 60.1089 | 60.0906 | -62.1414 | -62.3245 | 0.041198 | 0.11902 | -0.086975 | 0.24261 | -0.022888 | -0.14191 | 0.1236 | 0.12817 | -0.054932 | -0.11902 | 62.3154 | -0.21057 | -0.15564 | -0.13733 | 122.4106 | 122.6212 | 62.3886 | -122.3785 | 122.3785 | 122.3602 | 62.3428 | -122.5525
414.75 | 122.6669 | -62.2375 | 60.228 | 0.0074006 | -0.057894 | 0.12679 | 0.030683 | 0.037564 | -0.038083 | -0.024814 | 0.0077058 | -0.012982 | 0.026731 | 0.05962 | -0.020687 | -0.025165 | 60.3653 | -62.0178 | 0.11902 | -62.2604 | 60.1227 | -62.1872 | -62.1277 | 0.15564 | 0.17853 | -62.4207 | 60.0998 | 60.0449 | -62.1277 | -62.3199 | 0.050354 | 0.10986 | -0.10529 | 0.21973 | -0.022888 | -0.13275 | 0.13733 | 0.10986 | -0.082397 | -0.12817 | 62.3932 | -0.1831 | -0.10071 | -0.18311 | 122.3602 | 122.6028 | 62.3566 | -122.3557 | 122.3373 | 122.2824 | 62.4161 | -122.5479
416.5156 | 122.7081 | -62.2009 | 60.2097 | 0.0074006 | -0.057253 | 0.12743 | 0.031751 | 0.035214 | -0.035733 | -0.025455 | 0.0077058 | -0.010418 | 0.028867 | 0.060902 | -0.018978 | -0.024097 | 60.347 | -62.0453 | 0.064087 | -62.2833 | 60.1593 | -62.2009 | -62.1414 | 0.13733 | 0.16937 | -62.4252 | 60.0861 | 60.0769 | -62.1368 | -62.3154 | 0 | 0.05951 | -0.050354 | 0.15564 | -0.082397 | -0.14191 | 0.13733 | 0.064087 | -0.11444 | -0.1236 | 62.3383 | -0.2243 | -0.10986 | -0.13275 | 122.3602 | 122.5479 | 62.265 | -122.3511 | 122.287 | 122.2778 | 62.3703 | -122.525
418.3125 | 122.5891 | -62.2238 | 60.2737 | -0.00022891 | -0.056399 | 0.12935 | 0.032392 | 0.035855 | -0.036374 | -0.025455 | -0.0075532 | -0.014904 | 0.025663 | 0.058979 | -0.02261 | -0.023669 | 60.3561 | -62.0132 | 0.10529 | -62.2833 | 60.1227 | -62.1689 | -62.1094 | 0.13275 | 0.14191 | -62.4298 | 60.0952 | 60.0677 | -62.0956 | -62.3245 | 0.054932 | 0.11444 | -0.15106 | 0.21057 | -0.059509 | -0.17395 | 0.082397 | 0.12817 | -0.10071 | -0.17853 | 62.3566 | -0.20599 | -0.10529 | -0.20599 | 122.3465 | 122.58 | 62.3291 | -122.3831 | 122.319 | 122.2916 | 62.3657 | -122.5983
420.0312 | 122.6074 | -62.2192 | 60.26 | -0.00022891 | -0.05704 | 0.12786 | 0.030683 | 0.033505 | -0.03851 | -0.026951 | 0.0077058 | -0.013623 | 0.028013 | 0.058338 | -0.021542 | -0.025165 | 60.3149 | -62.0453 | 0.07782 | -62.2971 | 60.1501 | -62.178 | -62.114 | 0.068665 | 0.091553 | -62.4344 | 60.1044 | 60.0906 | -62.1277 | -62.2971 | 0.041198 | 0.10528 | -0.10986 | 0.17395 | -0.07782 | -0.1831 | 0.054931 | 0.091552 | -0.07782 | -0.15564 | 62.2879 | -0.21515 | -0.13733 | -0.16937 | 122.3694 | 122.5342 | 62.2971 | -122.374 | 122.3236 | 122.3099 | 62.3108 | -122.5571
421.8281 | 122.7036 | -62.2238 | 60.1456 | -0.00022891 | -0.053194 | 0.12615 | 0.03346 | 0.038418 | -0.031887 | -0.024173 | -0.0075532 | -0.0097776 | 0.029722 | 0.063465 | -0.021755 | -0.02666 | 60.2783 | -62.1231 | 0.032043 | -62.3383 | 60.1593 | -62.2604 | -62.1872 | 0.041199 | 0.064087 | -62.5305 | 60.0906 | 60.0632 | -62.1643 | -62.3657 | -0.036621 | 0.036621 | 0.013733 | 0.10071 | -0.11444 | -0.15106 | 0.13275 | 0.059509 | -0.14191 | -0.054932 | 62.265 | -0.3067 | -0.16479 | -0.082398 | 122.3831 | 122.5021 | 62.2559 | -122.3328 | 122.3145 | 122.287 | 62.2879 | -122.5113
423.5938 | 122.6669 | -62.233 | 60.2325 | 0.0074006 | -0.058962 | 0.12807 | 0.030255 | 0.037777 | -0.037442 | -0.023319 | -0.0075532 | -0.01405 | 0.028013 | 0.05962 | -0.021542 | -0.024524 | 60.3333 | -61.9995 | 0.09613 | -62.265 | 60.1181 | -62.178 | -62.114 | 0.12817 | 0.1831 | -62.4023 | 60.0815 | 60.0311 | -62.1506 | -62.3199 | 0.054931 | 0.11902 | -0.11444 | 0.23346 | -0.032044 | -0.15106 | 0.10071 | 0.082397 | -0.086975 | -0.15106 | 62.3611 | -0.16937 | -0.082398 | -0.20142 | 122.3511 | 122.5662 | 62.3291 | -122.3465 | 122.3145 | 122.2641 | 62.4161 | -122.5525
425.375 | 122.612 | -62.2284 | 60.2509 | -0.00022891 | -0.056185 | 0.12572 | 0.031537 | 0.038204 | -0.036801 | -0.026951 | 7.627e-05 | -0.013195 | 0.027799 | 0.059834 | -0.021755 | -0.024524 | 60.3561 | -62.0087 | 0.10986 | -62.2742 | 60.1135 | -62.178 | -62.1094 | 0.13275 | 0.16022 | -62.4115 | 60.0861 | 60.0632 | -62.0956 | -62.3291 | 0.050354 | 0.11902 | -0.13733 | 0.21973 | -0.045776 | -0.16479 | 0.10529 | 0.13275 | -0.10071 | -0.16479 | 62.3611 | -0.1831 | -0.082397 | -0.18768 | 122.3419 | 122.5845 | 62.3383 | -122.3602 | 122.3145 | 122.2916 | 62.3886 | -122.58
427.0938 | 122.7264 | -62.2101 | 60.1822 | -0.00022891 | -0.056826 | 0.12743 | 0.028974 | 0.038204 | -0.035519 | -0.024814 | 7.627e-05 | -0.011914 | 0.02609 | 0.059834 | -0.01791 | -0.02431 | 60.3058 | -62.1048 | 0.041199 | -62.3337 | 60.1364 | -62.2192 | -62.1597 | 0.10986 | 0.15564 | -62.4573 | 60.0998 | 60.054 | -62.1506 | -62.3291 | -0.009155 | 0.050354 | -0.045776 | 0.10529 | -0.1236 | -0.17395 | 0.1236 | 0.059509 | -0.11902 | -0.082398 | 62.3199 | -0.24719 | -0.12817 | -0.12817 | 122.3465 | 122.5159 | 62.2513 | -122.3419 | 122.3099 | 122.2641 | 62.3657 | -122.5113
428.875 | 122.5845 | -62.2513 | 60.2417 | -0.00022891 | -0.053408 | 0.12807 | 0.035382 | 0.036068 | -0.036587 | -0.024601 | 0.0077058 | -0.011486 | 0.029081 | 0.058552 | -0.022823 | -0.026019 | 60.3058 | -62.0407 | 0.10529 | -62.2971 | 60.1318 | -62.2101 | -62.1323 | 0.032043 | 0.064087 | -62.4847 | 60.1181 | 60.0861 | -62.1552 | -62.3383 | 0.041199 | 0.11902 | -0.10986 | 0.21057 | -0.045776 | -0.16479 | 0.064087 | 0.096131 | -0.086975 | -0.1236 | 62.2833 | -0.23346 | -0.14648 | -0.15564 | 122.3831 | 122.5571 | 62.3566 | -122.374 | 122.3694 | 122.3373 | 62.3154 | -122.58
430.6406 | 122.731 | -62.233 | 60.1593 | -0.015487 | -0.052981 | 0.12487 | 0.034101 | 0.03735 | -0.033383 | -0.023746 | 0.015335 | -0.010205 | 0.031217 | 0.060474 | -0.018551 | -0.025165 | 60.2692 | -62.0956 | 0.068665 | -62.3383 | 60.1456 | -62.2604 | -62.2009 | 0.054932 | 0.073242 | -62.5259 | 60.1135 | 60.0632 | -62.1735 | -62.3795 | -0.027466 | 0.032043 | -0.013733 | 0.13733 | -0.10529 | -0.13733 | 0.10986 | 0.059509 | -0.14648 | -0.045777 | 62.2879 | -0.29297 | -0.14648 | -0.096131 | 122.3785 | 122.5021 | 62.3016 | -122.3602 | 122.3465 | 122.2961 | 62.3062 | -122.5388
432.3438 | 122.731 | -62.1964 | 60.1776 | 0.0074006 | -0.057467 | 0.12615 | 0.031751 | 0.036709 | -0.03616 | -0.026096 | 0.0077058 | -0.010632 | 0.027799 | 0.060261 | -0.02261 | -0.022174 | 60.2646 | -62.1368 | 0.009155 | -62.3566 | 60.1456 | -62.2375 | -62.1735 | 0.073242 | 0.10071 | -62.4802 | 60.1135 | 60.1044 | -62.1277 | -62.3291 | -0.041199 | 0.022888 | -0.032043 | 0.059509 | -0.16022 | -0.1831 | 0.086975 | 0.068664 | -0.13275 | -0.064087 | 62.2696 | -0.28381 | -0.15106 | -0.073242 | 122.3419 | 122.4609 | 62.2055 | -122.3511 | 122.3099 | 122.3007 | 62.2971 | -122.5067
434.1406 | 122.644 | -62.2101 | 60.2234 | -0.00022891 | -0.057467 | 0.12658 | 0.030896 | 0.037564 | -0.039792 | -0.025242 | 7.627e-05 | -0.014264 | 0.02609 | 0.059406 | -0.020687 | -0.024524 | 60.3333 | -62.0178 | 0.10986 | -62.2879 | 60.0952 | -62.1918 | -62.1094 | 0.1236 | 0.17853 | -62.4069 | 60.0677 | 60.0494 | -62.114 | -62.3108 | 0.018311 | 0.10071 | -0.12817 | 0.19226 | -0.07782 | -0.17853 | 0.10986 | 0.09613 | -0.10071 | -0.15564 | 62.3337 | -0.19684 | -0.09613 | -0.17395 | 122.3053 | 122.5433 | 62.3199 | -122.3328 | 122.2778 | 122.2595 | 62.3886 | -122.5342
435.8594 | 122.58 | -62.2559 | 60.26 | -0.00022891 | -0.058321 | 0.12935 | 0.033032 | 0.035641 | -0.041714 | -0.026523 | 7.627e-05 | -0.013623 | 0.028653 | 0.060047 | -0.023251 | -0.024738 | 60.3333 | -62.0178 | 0.09613 | -62.2833 | 60.1273 | -62.1552 | -62.1094 | 0.091553 | 0.13733 | -62.4161 | 60.0906 | 60.0677 | -62.0819 | -62.2971 | 0.10071 | 0.14648 | -0.13275 | 0.23804 | -0.027466 | -0.17395 | 0.073242 | 0.17395 | -0.041199 | -0.16937 | 62.3474 | -0.16022 | -0.11902 | -0.19226 | 122.3831 | 122.5891 | 62.352 | -122.3694 | 122.3465 | 122.3236 | 62.3932 | -122.5571
437.6406 | 122.7081 | -62.2055 | 60.1547 | 0.0074006 | -0.052553 | 0.12914 | 0.034101 | 0.035855 | -0.032315 | -0.025242 | 7.627e-05 | -0.0099912 | 0.028653 | 0.059193 | -0.020046 | -0.026447 | 60.2325 | -62.146 | 0.045776 | -62.3474 | 60.1364 | -62.2604 | -62.2009 | 0.013733 | 0.041199 | -62.5397 | 60.1227 | 60.0815 | -62.178 | -62.3749 | -0.054932 | 0.004577 | -0.01831 | 0.059509 | -0.14191 | -0.14648 | 0.07782 | 0.027465 | -0.16937 | -0.032043 | 62.2192 | -0.33417 | -0.16479 | -0.073242 | 122.3419 | 122.438 | 62.2513 | -122.3557 | 122.3282 | 122.287 | 62.2467 | -122.5296
439.3594 | 122.6395 | -62.2192 | 60.2371 | -0.0078584 | -0.054903 | 0.12871 | 0.034955 | 0.036068 | -0.041287 | -0.028446 | 7.627e-05 | -0.013836 | 0.028867 | 0.058552 | -0.024319 | -0.024097 | 60.2966 | -62.0224 | 0.082397 | -62.2879 | 60.1364 | -62.1826 | -62.1185 | 0.086975 | 0.11444 | -62.3886 | 60.1089 | 60.0906 | -62.0956 | -62.3199 | 0.036621 | 0.10071 | -0.10071 | 0.19684 | -0.068665 | -0.16937 | 0.059509 | 0.1236 | -0.10071 | -0.12817 | 62.3062 | -0.16937 | -0.068665 | -0.14648 | 122.3557 | 122.5159 | 62.3016 | -122.3557 | 122.3282 | 122.3099 | 62.3337 | -122.5571
441.1406 | 122.6852 | -62.2192 | 60.173 | 0.0074006 | -0.054903 | 0.12636 | 0.029401 | 0.034573 | -0.03616 | -0.024814 | -0.0075532 | -0.007214 | 0.028653 | 0.063038 | -0.021755 | -0.02431 | 60.2188 | -62.2055 | -0.041199 | -62.3932 | 60.1501 | -62.2559 | -62.1826 | 0.032043 | 0.032043 | -62.5717 | 60.1135 | 60.0815 | -62.1597 | -62.3611 | -0.036621 | 0.036621 | -0.022889 | 0.013733 | -0.17395 | -0.21057 | 0.045776 | 0.059509 | -0.14191 | -0.05951 | 62.2513 | -0.35248 | -0.21057 | -0.091553 | 122.3694 | 122.438 | 62.178 | -122.3557 | 122.3328 | 122.3007 | 62.2513 | -122.5342
442.9219 | 122.5754 | -62.2696 | 60.2188 | -0.0078584 | -0.053835 | 0.13021 | 0.033673 | 0.035855 | -0.039151 | -0.02631 | -0.0075532 | -0.013623 | 0.026517 | 0.058766 | -0.023251 | -0.02431 | 60.3241 | -62.0132 | 0.14648 | -62.2787 | 60.1181 | -62.2101 | -62.1231 | 0.036621 | 0.10071 | -62.4573 | 60.0952 | 60.0861 | -62.1277 | -62.352 | 0.059509 | 0.14648 | -0.10071 | 0.25635 | -0.009156 | -0.15564 | 0.10529 | 0.14191 | -0.082398 | -0.1236 | 62.3062 | -0.18768 | -0.10529 | -0.13275 | 122.3877 | 122.5937 | 62.4161 | -122.3419 | 122.3648 | 122.3557 | 62.3703 | -122.5708
444.7031 | 122.5983 | -62.2467 | 60.2097 | -0.015487 | -0.05768 | 0.12764 | 0.031964 | 0.035641 | -0.037869 | -0.027378 | 0.0077058 | -0.014264 | 0.025876 | 0.06197 | -0.023251 | -0.025378 | 60.3378 | -62.0132 | 0.091553 | -62.2833 | 60.1089 | -62.2055 | -62.114 | 0.12817 | 0.16022 | -62.4115 | 60.0677 | 60.0952 | -62.1231 | -62.3154 | 0.041199 | 0.13275 | -0.10071 | 0.23346 | -0.036621 | -0.16937 | 0.12817 | 0.1236 | -0.068665 | -0.14191 | 62.3749 | -0.16479 | -0.09613 | -0.11444 | 122.3557 | 122.5845 | 62.3383 | -122.3236 | 122.3145 | 122.3419 | 62.4069 | -122.525
446.4062 | 122.6303 | -62.2009 | 60.2234 | 0.0074006 | -0.058748 | 0.12658 | 0.034101 | 0.036495 | -0.040432 | -0.024173 | -0.0075532 | -0.015118 | 0.028013 | 0.05962 | -0.026455 | -0.023029 | 60.3561 | -62.0041 | 0.11902 | -62.2375 | 60.1547 | -62.1918 | -62.1048 | 0.10071 | 0.13733 | -62.3703 | 60.1227 | 60.0815 | -62.0956 | -62.2971 | 0.009156 | 0.096131 | -0.068665 | 0.19684 | -0.036621 | -0.13275 | 0.13275 | 0.10529 | -0.09613 | -0.10071 | 62.3016 | -0.16937 | -0.073242 | -0.14191 | 122.3557 | 122.5571 | 62.3199 | -122.3282 | 122.3236 | 122.2824 | 62.3383 | -122.5204
448.1719 | 122.5983 | -62.2375 | 60.1959 | -0.0078584 | -0.053835 | 0.12893 | 0.033246 | 0.036068 | -0.037014 | -0.028232 | 7.627e-05 | -0.012127 | 0.028653 | 0.060688 | -0.022183 | -0.024951 | 60.2463 | -62.1185 | 0.045776 | -62.3566 | 60.173 | -62.2375 | -62.1735 | 0.009155 | 0 | -62.5305 | 60.1318 | 60.0861 | -62.1826 | -62.384 | 0 | 0.064087 | -0.022888 | 0.11902 | -0.11902 | -0.1831 | 0.050354 | 0.054932 | -0.14648 | -0.064087 | 62.2467 | -0.29297 | -0.14648 | -0.10986 | 122.4106 | 122.4838 | 62.2833 | -122.3694 | 122.3694 | 122.3236 | 62.2375 | -122.58
449.9375 | 122.6303 | -62.2101 | 60.2188 | -0.00022891 | -0.062594 | 0.12786 | 0.030896 | 0.03735 | -0.040005 | -0.027591 | 7.627e-05 | -0.015332 | 0.026944 | 0.058338 | -0.023251 | -0.02196 | 60.3607 | -61.9675 | 0.14191 | -62.2604 | 60.1318 | -62.1689 | -62.1048 | 0.13275 | 0.16479 | -62.352 | 60.0998 | 60.0769 | -62.1185 | -62.3062 | 0.041199 | 0.10529 | -0.086975 | 0.24262 | -0.050354 | -0.15564 | 0.14191 | 0.091553 | -0.09613 | -0.11902 | 62.3428 | -0.14191 | -0.045777 | -0.14191 | 122.3419 | 122.5708 | 62.352 | -122.3236 | 122.3099 | 122.287 | 62.3749 | -122.525
451.6562 | 122.6257 | -62.2147 | 60.228 | 0.0074006 | -0.056826 | 0.12828 | 0.034101 | 0.036495 | -0.041073 | -0.027164 | 7.627e-05 | -0.014264 | 0.026304 | 0.058125 | -0.023678 | -0.024524 | 60.3653 | -61.9766 | 0.14191 | -62.265 | 60.1456 | -62.1872 | -62.1414 | 0.13275 | 0.15106 | -62.3749 | 60.1089 | 60.0815 | -62.0956 | -62.2925 | 0.027466 | 0.073243 | -0.082397 | 0.23804 | -0.050354 | -0.1236 | 0.13733 | 0.11902 | -0.077819 | -0.11902 | 62.3474 | -0.16022 | -0.082398 | -0.14648 | 122.3602 | 122.58 | 62.3566 | -122.3694 | 122.3236 | 122.2961 | 62.3657 | -122.5204
453.4219 | 122.5708 | -62.2604 | 60.2142 | -0.00022891 | -0.056399 | 0.12935 | 0.035809 | 0.037991 | -0.038937 | -0.027805 | 7.627e-05 | -0.012341 | 0.028226 | 0.057911 | -0.021755 | -0.025165 | 60.3104 | -62.0499 | 0.10071 | -62.3245 | 60.1227 | -62.2284 | -62.1506 | 0.032043 | 0.041199 | -62.4893 | 60.1227 | 60.0723 | -62.1643 | -62.3428 | 0.032043 | 0.10986 | -0.091552 | 0.21057 | -0.064087 | -0.17395 | 0.096131 | 0.09613 | -0.082397 | -0.091552 | 62.2925 | -0.22888 | -0.14648 | -0.14191 | 122.3831 | 122.5708 | 62.3611 | -122.3648 | 122.3831 | 122.3328 | 62.3016 | -122.5571
455.1406 | 122.699 | -62.2192 | 60.1639 | -0.00022891 | -0.052981 | 0.12444 | 0.030469 | 0.033932 | -0.032101 | -0.023746 | 7.627e-05 | -0.0095638 | 0.02609 | 0.062397 | -0.018978 | -0.025806 | 60.2875 | -62.1094 | 0.07782 | -62.3428 | 60.1593 | -62.2375 | -62.178 | 0.068665 | 0.091553 | -62.5076 | 60.0815 | 60.0677 | -62.1735 | -62.3657 | -0.018311 | 0.041198 | -0.004577 | 0.10986 | -0.1236 | -0.16479 | 0.1236 | 0.045776 | -0.14649 | -0.082397 | 62.2879 | -0.28839 | -0.14191 | -0.09613 | 122.3785 | 122.5067 | 62.2971 | -122.3419 | 122.3007 | 122.287 | 62.3108 | -122.5296
456.9219 | 122.5891 | -62.233 | 60.2554 | -0.00022891 | -0.059603 | 0.12658 | 0.033673 | 0.03735 | -0.039151 | -0.023105 | 7.627e-05 | -0.016827 | 0.027585 | 0.06197 | -0.021755 | -0.023029 | 60.3333 | -62.0087 | 0.091553 | -62.2787 | 60.1364 | -62.1689 | -62.1048 | 0.10071 | 0.13733 | -62.4252 | 60.1044 | 60.0906 | -62.114 | -62.2925 | 0.064087 | 0.12817 | -0.11902 | 0.2243 | -0.045777 | -0.17395 | 0.07782 | 0.11902 | -0.059509 | -0.15106 | 62.3337 | -0.19226 | -0.13275 | -0.16479 | 122.3694 | 122.5662 | 62.3245 | -122.3602 | 122.3373 | 122.3236 | 62.3703 | -122.5479
458.7031 | 122.5662 | -62.2513 | 60.2234 | -0.00022891 | -0.056612 | 0.12615 | 0.033673 | 0.038845 | -0.041287 | -0.024387 | 0.0077058 | -0.013195 | 0.029722 | 0.060688 | -0.023037 | -0.025592 | 60.3333 | -61.9949 | 0.14648 | -62.2559 | 60.1135 | -62.1918 | -62.114 | 0.068665 | 0.1236 | -62.4023 | 60.0906 | 60.0403 | -62.1277 | -62.3108 | 0.05951 | 0.13733 | -0.10986 | 0.25635 | -0.004577 | -0.14191 | 0.10986 | 0.1236 | -0.059509 | -0.13275 | 62.3199 | -0.15106 | -0.091553 | -0.18311 | 122.3648 | 122.5845 | 62.3978 | -122.3373 | 122.3419 | 122.2916 | 62.3749 | -122.5342
460.4219 | 122.6578 | -62.2101 | 60.173 | -0.00022891 | -0.053622 | 0.12423 | 0.028546 | 0.035214 | -0.032101 | -0.022678 | -0.0075532 | -0.010846 | 0.029081 | 0.061329 | -0.018337 | -0.026019 | 60.2921 | -62.1002 | 0.082397 | -62.3474 | 60.1273 | -62.2559 | -62.1597 | 0.068665 | 0.09613 | -62.5397 | 60.0998 | 60.0403 | -62.1597 | -62.3703 | -0.045776 | 0.050354 | -0.045777 | 0.10986 | -0.13733 | -0.18768 | 0.11902 | 0.050354 | -0.16022 | -0.073243 | 62.2787 | -0.32959 | -0.16937 | -0.13275 | 122.3373 | 122.5021 | 62.2925 | -122.3328 | 122.3099 | 122.2504 | 62.3062 | -122.5433
462.2031 | 122.5845 | -62.2009 | 60.2509 | -0.00022891 | -0.056399 | 0.12764 | 0.032605 | 0.035214 | -0.041287 | -0.027164 | 7.627e-05 | -0.015332 | 0.02844 | 0.059406 | -0.023678 | -0.023883 | 60.2783 | -62.0178 | 0.054932 | -62.2925 | 60.1501 | -62.178 | -62.1231 | 0.054932 | 0.09613 | -62.4161 | 60.1135 | 60.0861 | -62.0911 | -62.3108 | 0.022888 | 0.07782 | -0.10071 | 0.18311 | -0.091552 | -0.16937 | 0.027466 | 0.10986 | -0.10986 | -0.13733 | 62.2559 | -0.21515 | -0.10529 | -0.16479 | 122.3511 | 122.4792 | 62.2559 | -122.374 | 122.3145 | 122.287 | 62.2971 | -122.5616
463.9844 | 122.5937 | -62.2284 | 60.2646 | -0.00022891 | -0.057253 | 0.12957 | 0.030042 | 0.03735 | -0.037869 | -0.024173 | 0.0077058 | -0.013195 | 0.026304 | 0.060047 | -0.020474 | -0.02431 | 60.3378 | -61.9995 | 0.10071 | -62.2787 | 60.1318 | -62.1689 | -62.114 | 0.12817 | 0.13733 | -62.4069 | 60.0998 | 60.0769 | -62.0911 | -62.2879 | 0.05951 | 0.11444 | -0.13275 | 0.22888 | -0.050354 | -0.16479 | 0.073243 | 0.13733 | -0.059509 | -0.16479 | 62.3566 | -0.17853 | -0.11902 | -0.18768 | 122.3602 | 122.5662 | 62.3291 | -122.3785 | 122.3282 | 122.3053 | 62.3657 | -122.5525
465.7656 | 122.7264 | -62.2147 | 60.1959 | -0.015487 | -0.055331 | 0.12636 | 0.03346 | 0.035641 | -0.034024 | -0.02396 | 0.0077058 | -0.010632 | 0.027585 | 0.059406 | -0.021969 | -0.027301 | 60.2509 | -62.1643 | 0 | -62.3657 | 60.141 | -62.233 | -62.1643 | 0.059509 | 0.054932 | -62.5214 | 60.1181 | 60.1044 | -62.1414 | -62.3383 | -0.01831 | 0.050354 | -0.054932 | 0.050354 | -0.15106 | -0.20142 | 0.054931 | 0.073243 | -0.1236 | -0.07782 | 62.2742 | -0.3067 | -0.18311 | -0.091553 | 122.3557 | 122.4655 | 62.2147 | -122.3602 | 122.3328 | 122.319 | 62.2696 | -122.5342
467.5312 | 122.6807 | -62.2421 | 60.1593 | -0.00022891 | -0.052767 | 0.12572 | 0.031537 | 0.039273 | -0.032956 | -0.024173 | 0.0077058 | -0.010418 | 0.029935 | 0.05962 | -0.020474 | -0.024738 | 60.2554 | -62.1094 | 0.07782 | -62.3474 | 60.1135 | -62.2375 | -62.1872 | 0.082397 | 0.11902 | -62.5214 | 60.0723 | 60.0769 | -62.1689 | -62.384 | 0.004577 | 0.054931 | -0.045777 | 0.13275 | -0.10529 | -0.16022 | 0.09613 | 0.073242 | -0.14191 | -0.086975 | 62.3245 | -0.27924 | -0.13733 | -0.082398 | 122.3557 | 122.4976 | 62.3199 | -122.3465 | 122.3145 | 122.319 | 62.3611 | -122.5433
469.3438 | 122.5525 | -62.2467 | 60.2142 | -0.0078584 | -0.055544 | 0.127 | 0.037732 | 0.035427 | -0.039364 | -0.026523 | 7.627e-05 | -0.014904 | 0.030362 | 0.058552 | -0.023678 | -0.022174 | 60.2554 | -62.0819 | 0.086975 | -62.3337 | 60.1501 | -62.2238 | -62.1368 | 0.009155 | 0.022888 | -62.5122 | 60.1273 | 60.0998 | -62.1597 | -62.3428 | 0.022888 | 0.10986 | -0.064087 | 0.16479 | -0.086975 | -0.19684 | 0.041199 | 0.086975 | -0.09613 | -0.086975 | 62.2559 | -0.2655 | -0.16937 | -0.11444 | 122.3969 | 122.5021 | 62.3337 | -122.3511 | 122.374 | 122.3465 | 62.2696 | -122.5571
471.0469 | 122.6166 | -62.233 | 60.1868 | -0.0078584 | -0.054262 | 0.12871 | 0.033887 | 0.034573 | -0.036801 | -0.02631 | 7.627e-05 | -0.010846 | 0.029722 | 0.060688 | -0.022183 | -0.025378 | 60.2234 | -62.146 | 0.022888 | -62.3611 | 60.1501 | -62.2513 | -62.1872 | -0.013733 | 0.009155 | -62.5397 | 60.1273 | 60.1044 | -62.1643 | -62.3474 | -0.018311 | 0.045776 | -0.036622 | 0.086975 | -0.12817 | -0.17395 | 0.036621 | 0.068664 | -0.11444 | -0.05951 | 62.2192 | -0.3067 | -0.19226 | -0.082398 | 122.3831 | 122.4564 | 62.2559 | -122.374 | 122.3602 | 122.3373 | 62.2421 | -122.5342
472.8281 | 122.5754 | -62.2192 | 60.2371 | -0.00022891 | -0.060457 | 0.12807 | 0.03346 | 0.033718 | -0.041287 | -0.026951 | -0.0075532 | -0.014691 | 0.026731 | 0.059834 | -0.024746 | -0.024097 | 60.2966 | -62.0453 | 0.054932 | -62.2833 | 60.1273 | -62.1506 | -62.0956 | 0.059509 | 0.10071 | -62.4344 | 60.1181 | 60.1135 | -62.1002 | -62.2971 | 0.068664 | 0.1236 | -0.10986 | 0.17395 | -0.064087 | -0.18768 | 0.059509 | 0.11902 | -0.07782 | -0.11902 | 62.2787 | -0.21515 | -0.13733 | -0.1236 | 122.3465 | 122.5159 | 62.2742 | -122.3328 | 122.3373 | 122.3328 | 62.3199 | -122.5342
474.5312 | 122.5525 | -62.2192 | 60.2371 | -0.00022891 | -0.052553 | 0.12807 | 0.034101 | 0.036282 | -0.038083 | -0.025882 | 7.627e-05 | -0.015759 | 0.026731 | 0.059193 | -0.023892 | -0.026233 | 60.3287 | -61.9904 | 0.13733 | -62.2559 | 60.1227 | -62.178 | -62.1048 | 0.059509 | 0.12817 | -62.4069 | 60.0861 | 60.0677 | -62.1506 | -62.352 | 0.041198 | 0.11444 | -0.11444 | 0.22888 | -0.036621 | -0.15106 | 0.091552 | 0.068664 | -0.13275 | -0.15106 | 62.2787 | -0.18768 | -0.054931 | -0.16937 | 122.3419 | 122.5479 | 62.3566 | -122.3419 | 122.3053 | 122.287 | 62.3474 | -122.5891
476.2969 | 122.6395 | -62.2421 | 60.1685 | 0.0074006 | -0.054049 | 0.1285 | 0.032392 | 0.034359 | -0.035733 | -0.027378 | 7.627e-05 | -0.0117 | 0.027799 | 0.060688 | -0.021755 | -0.025378 | 60.2371 | -62.146 | 0.036621 | -62.3611 | 60.173 | -62.2147 | -62.1964 | -0.004578 | 0.027466 | -62.5397 | 60.1273 | 60.1273 | -62.1506 | -62.3703 | 0.027465 | 0.045776 | 0.004578 | 0.09613 | -0.11902 | -0.16479 | 0.068665 | 0.091552 | -0.12817 | -0.041199 | 62.2375 | -0.29755 | -0.16937 | -0.041199 | 122.4152 | 122.4792 | 62.2787 | -122.3648 | 122.3694 | 122.3694 | 62.2696 | -122.5388
478.0625 | 122.6303 | -62.2192 | 60.228 | -0.0078584 | -0.061526 | 0.12999 | 0.02876 | 0.032009 | -0.040219 | -0.026523 | -0.0075532 | -0.016827 | 0.025449 | 0.057697 | -0.020901 | -0.022601 | 60.3333 | -62.0087 | 0.091553 | -62.265 | 60.1456 | -62.1597 | -62.114 | 0.09613 | 0.13275 | -62.3795 | 60.1135 | 60.0723 | -62.0865 | -62.2879 | 0.059509 | 0.10528 | -0.082397 | 0.21057 | -0.045777 | -0.15106 | 0.10529 | 0.13275 | -0.068665 | -0.11444 | 62.3154 | -0.16022 | -0.091553 | -0.15564 | 122.3648 | 122.5525 | 62.3108 | -122.3419 | 122.3328 | 122.2916 | 62.352 | -122.5159
479.8438 | 122.6166 | -62.233 | 60.2188 | -0.00022891 | -0.056399 | 0.13021 | 0.035382 | 0.034146 | -0.040005 | -0.026951 | 7.627e-05 | -0.01405 | 0.02609 | 0.058552 | -0.022183 | -0.02431 | 60.347 | -61.9812 | 0.1236 | -62.2696 | 60.141 | -62.1643 | -62.114 | 0.1236 | 0.13275 | -62.3657 | 60.0769 | 60.0815 | -62.0865 | -62.2742 | 0.068664 | 0.11902 | -0.07782 | 0.25177 | -0.036621 | -0.15564 | 0.12817 | 0.14648 | -0.041199 | -0.14191 | 62.3566 | -0.13275 | -0.091553 | -0.13733 | 122.374 | 122.58 | 62.3566 | -122.3328 | 122.3099 | 122.3145 | 62.3657 | -122.493
481.625 | 122.58 | -62.2238 | 60.2371 | -0.00022891 | -0.060457 | 0.12935 | 0.032178 | 0.035641 | -0.036801 | -0.02396 | 0.015335 | -0.015759 | 0.026944 | 0.058552 | -0.021542 | -0.025165 | 60.3561 | -61.9904 | 0.09613 | -62.2787 | 60.1044 | -62.1918 | -62.1185 | 0.12817 | 0.15564 | -62.3978 | 60.0906 | 60.0632 | -62.1185 | -62.3199 | 0.032044 | 0.10529 | -0.13275 | 0.23346 | -0.054932 | -0.16022 | 0.11902 | 0.10529 | -0.09613 | -0.14648 | 62.352 | -0.17395 | -0.07782 | -0.17395 | 122.3282 | 122.58 | 62.3199 | -122.3557 | 122.3145 | 122.287 | 62.3795 | -122.5571
483.4062 | 122.58 | -62.2559 | 60.2371 | 0.0074006 | -0.055544 | 0.13021 | 0.035596 | 0.037136 | -0.037442 | -0.028019 | 0.0077058 | -0.014691 | 0.031003 | 0.060261 | -0.022823 | -0.024524 | 60.3561 | -61.9858 | 0.16479 | -62.2513 | 60.1273 | -62.2009 | -62.1231 | 0.086975 | 0.14191 | -62.3978 | 60.0906 | 60.054 | -62.114 | -62.3154 | 0.054931 | 0.13275 | -0.10986 | 0.27008 | 0.004577 | -0.12817 | 0.11902 | 0.14191 | -0.05951 | -0.14648 | 62.3428 | -0.14191 | -0.082397 | -0.18311 | 122.3831 | 122.612 | 62.4207 | -122.3602 | 122.3465 | 122.3099 | 62.3978 | -122.5525
485.125 | 122.6578 | -62.2192 | 60.1776 | -0.0078584 | -0.05234 | 0.12593 | 0.033887 | 0.03735 | -0.031247 | -0.024814 | 7.627e-05 | -0.0091366 | 0.028013 | 0.062183 | -0.017056 | -0.028583 | 60.2829 | -62.1277 | 0.068665 | -62.3474 | 60.141 | -62.2559 | -62.1872 | 0.054932 | 0.059509 | -62.5534 | 60.1227 | 60.0586 | -62.1826 | -62.3795 | -0.036621 | 0.032043 | -0.036621 | 0.091552 | -0.12817 | -0.16022 | 0.10529 | 0.036621 | -0.16022 | -0.054931 | 62.2742 | -0.33417 | -0.17395 | -0.11902 | 122.3602 | 122.5021 | 62.2879 | -122.3648 | 122.3419 | 122.2778 | 62.2787 | -122.5571
486.9062 | 122.5616 | -62.2467 | 60.2417 | 0.0074006 | -0.055117 | 0.12658 | 0.034955 | 0.036282 | -0.039364 | -0.026737 | -0.0075532 | -0.013836 | 0.029935 | 0.05962 | -0.024319 | -0.024738 | 60.3241 | -61.9904 | 0.15106 | -62.2604 | 60.1227 | -62.1826 | -62.1277 | 0.07782 | 0.12817 | -62.4161 | 60.0769 | 60.0815 | -62.1094 | -62.3199 | 0.064087 | 0.11902 | -0.11902 | 0.25635 | -0.013733 | -0.13275 | 0.082398 | 0.13733 | -0.073242 | -0.16479 | 62.3245 | -0.16937 | -0.096131 | -0.16022 | 122.3694 | 122.5708 | 62.3978 | -122.3694 | 122.3236 | 122.3282 | 62.3749 | -122.5616
488.6719 | 122.5845 | -62.2467 | 60.1868 | -0.00022891 | -0.05704 | 0.127 | 0.033246 | 0.036709 | -0.036374 | -0.025669 | 0.0077058 | -0.0097776 | 0.028226 | 0.061543 | -0.019406 | -0.024097 | 60.2371 | -62.1277 | 0.032043 | -62.352 | 60.1685 | -62.2513 | -62.1689 | 0.004578 | 0.004578 | -62.5534 | 60.1318 | 60.1089 | -62.1643 | -62.3428 | -0.004578 | 0.07782 | -0.018311 | 0.11902 | -0.10529 | -0.18311 | 0.050354 | 0.082397 | -0.09613 | -0.054932 | 62.2513 | -0.3067 | -0.21057 | -0.07782 | 122.4152 | 122.4838 | 62.2787 | -122.3557 | 122.3785 | 122.3557 | 62.2513 | -122.5296
490.3906 | 122.6257 | -62.1872 | 60.2234 | -0.00022891 | -0.055117 | 0.1285 | 0.031751 | 0.035855 | -0.039578 | -0.02631 | 7.627e-05 | -0.015759 | 0.027585 | 0.058125 | -0.02261 | -0.023456 | 60.3287 | -61.9263 | 0.12817 | -62.2467 | 60.1318 | -62.178 | -62.0911 | 0.1236 | 0.15106 | -62.3611 | 60.0906 | 60.0632 | -62.0865 | -62.3108 | 0.009155 | 0.096131 | -0.091553 | 0.26093 | -0.059509 | -0.15564 | 0.10529 | 0.10071 | -0.1236 | -0.13275 | 62.3108 | -0.17395 | -0.050354 | -0.16022 | 122.319 | 122.5159 | 62.3154 | -122.3145 | 122.2778 | 122.2504 | 62.3383 | -122.5342
492.1719 | 122.5891 | -62.2284 | 60.228 | 0.0074006 | -0.055758 | 0.12786 | 0.033673 | 0.036068 | -0.035946 | -0.026096 | 7.627e-05 | -0.012555 | 0.02844 | 0.057697 | -0.021755 | -0.024951 | 60.228 | -62.114 | 0.041199 | -62.3566 | 60.1593 | -62.2238 | -62.1643 | -0.013733 | 0.018311 | -62.5168 | 60.0998 | 60.0906 | -62.178 | -62.3611 | 0.004578 | 0.064087 | -0.068664 | 0.11444 | -0.12817 | -0.19226 | 0 | 0.050354 | -0.13275 | -0.12817 | 62.2147 | -0.28839 | -0.15564 | -0.13733 | 122.3877 | 122.4564 | 62.2696 | -122.3923 | 122.3282 | 122.319 | 62.2467 | -122.5891
493.9531 | 122.5708 | -62.233 | 60.2463 | -0.00022891 | -0.05704 | 0.12636 | 0.034528 | 0.037564 | -0.03851 | -0.026096 | 7.627e-05 | -0.014477 | 0.028013 | 0.060474 | -0.024105 | -0.024951 | 60.3149 | -62.0132 | 0.09613 | -62.2879 | 60.141 | -62.1689 | -62.1048 | 0.086975 | 0.1236 | -62.3978 | 60.1044 | 60.0815 | -62.1048 | -62.3199 | 0.064087 | 0.12817 | -0.10529 | 0.21973 | -0.054932 | -0.18311 | 0.068664 | 0.12817 | -0.086975 | -0.14191 | 62.3199 | -0.16479 | -0.07782 | -0.16479 | 122.374 | 122.5479 | 62.3291 | -122.3511 | 122.3373 | 122.3145 | 62.3566 | -122.5662
495.6562 | 122.6257 | -62.2375 | 60.1776 | -0.00022891 | -0.053194 | 0.13128 | 0.032819 | 0.036495 | -0.034451 | -0.025882 | 0.015335 | -0.011486 | 0.027372 | 0.058125 | -0.022823 | -0.024524 | 60.228 | -62.114 | 0.036621 | -62.352 | 60.1776 | -62.233 | -62.1735 | -0.004578 | 0.009155 | -62.5397 | 60.1273 | 60.0861 | -62.1643 | -62.3566 | 0.004578 | 0.064087 | 0 | 0.1236 | -0.11444 | -0.17853 | 0.050354 | 0.073242 | -0.11902 | -0.050354 | 62.233 | -0.30212 | -0.18311 | -0.091552 | 122.4152 | 122.4655 | 62.2742 | -122.3511 | 122.3648 | 122.3236 | 62.2467 | -122.5342
497.4375 | 122.6212 | -62.2009 | 60.2325 | -0.0078584 | -0.057894 | 0.12978 | 0.034955 | 0.036923 | -0.042141 | -0.026523 | 0.0077058 | -0.015545 | 0.027372 | 0.058338 | -0.024105 | -0.025806 | 60.3149 | -61.972 | 0.11902 | -62.2559 | 60.1547 | -62.178 | -62.1048 | 0.10071 | 0.13275 | -62.3566 | 60.0861 | 60.0723 | -62.1002 | -62.3062 | 0.022888 | 0.096131 | -0.07782 | 0.22888 | -0.054931 | -0.15106 | 0.082397 | 0.10071 | -0.10529 | -0.14648 | 62.3016 | -0.15564 | -0.050354 | -0.16022 | 122.3557 | 122.5159 | 62.3199 | -122.3373 | 122.287 | 122.2733 | 62.3337 | -122.5388
499.1562 | 122.7219 | -62.1826 | 60.1822 | -0.015487 | -0.054262 | 0.127 | 0.031964 | 0.035427 | -0.03381 | -0.025242 | 7.627e-05 | -0.012555 | 0.027585 | 0.055988 | -0.017483 | -0.024097 | 60.2554 | -62.1094 | 0 | -62.3474 | 60.1547 | -62.2284 | -62.146 | 0.10071 | 0.10529 | -62.4893 | 60.1318 | 60.054 | -62.146 | -62.3199 | -0.045777 | 0.036621 | -0.027466 | 0.073242 | -0.16479 | -0.20142 | 0.073242 | 0.036621 | -0.13733 | -0.050354 | 62.2833 | -0.3067 | -0.16937 | -0.12817 | 122.3373 | 122.438 | 62.1826 | -122.3282 | 122.3145 | 122.2366 | 62.2879 | -122.5021
500.9219 | 122.5891 | -62.1918 | 60.2234 | 0.0074006 | -0.059817 | 0.12957 | 0.031537 | 0.03735 | -0.038296 | -0.026523 | 7.627e-05 | -0.010632 | 0.024381 | 0.058338 | -0.020687 | -0.023029 | 60.3195 | -61.972 | 0.10986 | -62.2742 | 60.0906 | -62.1964 | -62.1002 | 0.11444 | 0.16022 | -62.3886 | 60.0815 | 60.0632 | -62.0956 | -62.2879 | -0.004578 | 0.091552 | -0.13275 | 0.21973 | -0.082398 | -0.17395 | 0.09613 | 0.09613 | -0.096131 | -0.14191 | 62.3062 | -0.19684 | -0.10071 | -0.16022 | 122.2824 | 122.5113 | 62.3016 | -122.3236 | 122.2733 | 122.2549 | 62.352 | -122.5113
502.7031 | 122.6028 | -62.1964 | 60.228 | -0.00022891 | -0.055971 | 0.12786 | 0.02876 | 0.036068 | -0.037014 | -0.02631 | 7.627e-05 | -0.01405 | 0.024381 | 0.058979 | -0.023251 | -0.026019 | 60.3333 | -61.9995 | 0.10071 | -62.2604 | 60.1227 | -62.1597 | -62.0819 | 0.11902 | 0.1831 | -62.3886 | 60.0861 | 60.0357 | -62.1002 | -62.2925 | 0.036621 | 0.11444 | -0.10529 | 0.19684 | -0.064087 | -0.17853 | 0.10529 | 0.09613 | -0.09613 | -0.14191 | 62.3154 | -0.19226 | -0.096131 | -0.19226 | 122.319 | 122.5296 | 62.2971 | -122.3099 | 122.2824 | 122.2321 | 62.3795 | -122.5204
504.4844 | 122.6761 | -62.2192 | 60.1501 | -0.00022891 | -0.052126 | 0.12743 | 0.035809 | 0.037564 | -0.037014 | -0.024173 | 0.015335 | -0.010418 | 0.028653 | 0.058552 | -0.020901 | -0.025165 | 60.2417 | -62.1414 | 0.045776 | -62.352 | 60.1639 | -62.2192 | -62.2009 | 0.004578 | 0.027466 | -62.5351 | 60.1318 | 60.0769 | -62.1597 | -62.3566 | 0 | 0.01831 | 0.013733 | 0.07782 | -0.13275 | -0.15106 | 0.091553 | 0.059509 | -0.13733 | -0.01831 | 62.2238 | -0.31586 | -0.17853 | -0.073242 | 122.3831 | 122.4609 | 62.265 | -122.3511 | 122.3511 | 122.2961 | 62.2467 | -122.5067
506.25 | 122.612 | -62.2055 | 60.1776 | -0.00022891 | -0.052553 | 0.12893 | 0.037946 | 0.036923 | -0.038083 | -0.025455 | 7.627e-05 | -0.011273 | 0.027585 | 0.061756 | -0.022183 | -0.024951 | 60.2234 | -62.1414 | 0.041199 | -62.352 | 60.1593 | -62.2009 | -62.1826 | -0.009155 | 0.004578 | -62.5351 | 60.1089 | 60.1089 | -62.1689 | -62.3657 | 0.004577 | 0.022888 | -0.01831 | 0.064087 | -0.14648 | -0.16937 | 0.045777 | 0.036621 | -0.16022 | -0.068664 | 62.1964 | -0.32959 | -0.16937 | -0.068664 | 122.3648 | 122.4289 | 62.2467 | -122.3602 | 122.3145 | 122.3145 | 62.2101 | -122.5433
508.0156 | 122.5754 | -62.2467 | 60.1822 | -0.0078584 | -0.054476 | 0.12999 | 0.03111 | 0.035214 | -0.037655 | -0.025455 | 7.627e-05 | -0.012768 | 0.027799 | 0.05962 | -0.022823 | -0.023242 | 60.228 | -62.114 | 0.050354 | -62.352 | 60.1593 | -62.2467 | -62.1689 | 0 | 0 | -62.5259 | 60.1135 | 60.0952 | -62.1552 | -62.3611 | 0 | 0.07782 | -0.022888 | 0.13275 | -0.10529 | -0.18311 | 0.045776 | 0.091553 | -0.11444 | -0.068665 | 62.2467 | -0.27924 | -0.16479 | -0.086975 | 122.406 | 122.4747 | 62.2971 | -122.3511 | 122.3602 | 122.3419 | 62.2467 | -122.5433
509.7656 | 122.5616 | -62.2467 | 60.1959 | -0.0078584 | -0.05469 | 0.12764 | 0.032819 | 0.036709 | -0.040646 | -0.025669 | -0.0075532 | -0.011059 | 0.025663 | 0.059834 | -0.023251 | -0.025592 | 60.26 | -62.0728 | 0.07782 | -62.3108 | 60.141 | -62.2192 | -62.1414 | 0 | 0.018311 | -62.4985 | 60.0998 | 60.0815 | -62.1689 | -62.3337 | 0.027466 | 0.10529 | -0.054932 | 0.17395 | -0.064087 | -0.16937 | 0.064087 | 0.07782 | -0.086975 | -0.096131 | 62.2467 | -0.25177 | -0.1648 | -0.11444 | 122.3877 | 122.5067 | 62.3245 | -122.3373 | 122.3465 | 122.3282 | 62.265 | -122.5296
511.5469 | 122.612 | -62.2055 | 60.2097 | -0.00022891 | -0.061098 | 0.13128 | 0.033246 | 0.035427 | -0.042782 | -0.02631 | 0.0077058 | -0.015332 | 0.025449 | 0.059406 | -0.023037 | -0.023029 | 60.2921 | -62.0316 | 0.068665 | -62.2696 | 60.1501 | -62.1552 | -62.0911 | 0.059509 | 0.12817 | -62.4023 | 60.0906 | 60.0906 | -62.0682 | -62.2925 | 0.050354 | 0.11444 | -0.05951 | 0.17395 | -0.064087 | -0.17853 | 0.082397 | 0.13733 | -0.086975 | -0.11902 | 62.265 | -0.19684 | -0.10986 | -0.11902 | 122.3557 | 122.4976 | 62.2742 | -122.3007 | 122.2961 | 122.2961 | 62.3337 | -122.5021
513.3125 | 122.6028 | -62.2055 | 60.2234 | -0.0078584 | -0.056399 | 0.13042 | 0.033032 | 0.034146 | -0.04086 | -0.025669 | 7.627e-05 | -0.015332 | 0.025022 | 0.058125 | -0.022396 | -0.026447 | 60.3836 | -61.9354 | 0.16479 | -62.2421 | 60.1318 | -62.1597 | -62.1094 | 0.11444 | 0.15106 | -62.3749 | 60.0906 | 60.0769 | -62.0956 | -62.2925 | 0.045776 | 0.09613 | -0.091553 | 0.27008 | -0.036621 | -0.13275 | 0.16022 | 0.10986 | -0.086975 | -0.13275 | 62.3199 | -0.16937 | -0.082398 | -0.14648 | 122.3373 | 122.5891 | 62.3703 | -122.3328 | 122.2961 | 122.2824 | 62.3566 | -122.5159
515.0156 | 122.6807 | -62.2101 | 60.1593 | -0.00022891 | -0.053622 | 0.12636 | 0.029187 | 0.037991 | -0.032315 | -0.025242 | -0.0075532 | -0.0117 | 0.028226 | 0.062824 | -0.018124 | -0.024951 | 60.2829 | -62.0956 | 0.073242 | -62.3383 | 60.1273 | -62.2467 | -62.1918 | 0.082397 | 0.082397 | -62.5122 | 60.0861 | 60.0494 | -62.1826 | -62.3611 | -0.036621 | 0.018311 | -0.032044 | 0.11444 | -0.12817 | -0.14648 | 0.1236 | 0.027466 | -0.15106 | -0.073242 | 62.2925 | -0.30212 | -0.15106 | -0.10986 | 122.3373 | 122.493 | 62.2833 | -122.3511 | 122.2961 | 122.2595 | 62.2925 | -122.5204
516.8281 | 122.7036 | -62.2147 | 60.1959 | -0.00022891 | -0.057253 | 0.12999 | 0.030896 | 0.036709 | -0.034878 | -0.024814 | 7.627e-05 | -0.014691 | 0.027372 | 0.059406 | -0.020687 | -0.027087 | 60.2554 | -62.1277 | 0.018311 | -62.3291 | 60.1318 | -62.2101 | -62.1552 | 0.091553 | 0.10071 | -62.4847 | 60.0769 | 60.0494 | -62.1597 | -62.3337 | 0.004578 | 0.05951 | -0.064087 | 0.086975 | -0.11444 | -0.17395 | 0.059509 | 0.054932 | -0.11902 | -0.11902 | 62.3062 | -0.27008 | -0.15106 | -0.14648 | 122.3465 | 122.4701 | 62.233 | -122.3511 | 122.2916 | 122.2641 | 62.3154 | -122.5296
518.625 | 122.5662 | -62.2147 | 60.2417 | -0.0078584 | -0.058748 | 0.127 | 0.031964 | 0.037136 | -0.042355 | -0.022678 | 7.627e-05 | -0.014691 | 0.02609 | 0.059406 | -0.022183 | -0.022815 | 60.3287 | -61.9995 | 0.10071 | -62.2833 | 60.0906 | -62.2009 | -62.1277 | 0.1236 | 0.16022 | -62.3932 | 60.1044 | 60.0815 | -62.1048 | -62.3154 | 0.013733 | 0.086975 | -0.15106 | 0.21515 | -0.068664 | -0.15564 | 0.086975 | 0.10986 | -0.10071 | -0.13733 | 62.3383 | -0.17853 | -0.077819 | -0.16022 | 122.3053 | 122.5433 | 62.3154 | -122.3694 | 122.319 | 122.2961 | 62.3749 | -122.5571
520.75 | 122.5708 | -62.2467 | 60.2142 | -0.00022891 | -0.053835 | 0.12978 | 0.034741 | 0.035214 | -0.039151 | -0.025028 | 7.627e-05 | -0.012768 | 0.028867 | 0.05727 | -0.024105 | -0.024951 | 60.2463 | -62.1048 | 0.054932 | -62.3199 | 60.141 | -62.2101 | -62.1506 | -0.004578 | 0.022888 | -62.5168 | 60.1227 | 60.0906 | -62.1735 | -62.3428 | 0.036621 | 0.09613 | -0.073242 | 0.14191 | -0.073242 | -0.16937 | 0.032044 | 0.073242 | -0.09613 | -0.091552 | 62.2421 | -0.27008 | -0.17395 | -0.1236 | 122.3877 | 122.493 | 62.3016 | -122.3648 | 122.3694 | 122.3373 | 62.2696 | -122.5571
522.5469 | 122.699 | -62.1689 | 60.141 | -0.0078584 | -0.05469 | 0.12572 | 0.033887 | 0.036709 | -0.034237 | -0.025669 | -0.0075532 | -0.0093502 | 0.027799 | 0.059193 | -0.021542 | -0.025378 | 60.2371 | -62.1231 | 0.054932 | -62.3245 | 60.141 | -62.2421 | -62.1826 | 0.050354 | 0.07782 | -62.5168 | 60.0998 | 60.0815 | -62.1506 | -62.3703 | -0.073242 | -0.013733 | 0 | 0.045776 | -0.15564 | -0.14191 | 0.096131 | 0.01831 | -0.20142 | -0.041199 | 62.2192 | -0.3479 | -0.14648 | -0.059509 | 122.3099 | 122.406 | 62.2238 | -122.3236 | 122.2687 | 122.2504 | 62.2467 | -122.5113
524.4688 | 122.5571 | -62.2559 | 60.1913 | -0.00022891 | -0.05234 | 0.12593 | 0.034528 | 0.036282 | -0.039792 | -0.024173 | 0.0077058 | -0.013409 | 0.028226 | 0.059406 | -0.022396 | -0.022388 | 60.228 | -62.1185 | 0.064087 | -62.3428 | 60.1501 | -62.2192 | -62.1552 | 0.009155 | 0.022888 | -62.5076 | 60.1135 | 60.0906 | -62.1643 | -62.3611 | 0.036621 | 0.10071 | -0.041199 | 0.13733 | -0.086975 | -0.18768 | 0.036621 | 0.091552 | -0.10529 | -0.07782 | 62.265 | -0.25177 | -0.14648 | -0.10071 | 122.406 | 122.4838 | 62.3199 | -122.3465 | 122.3694 | 122.3465 | 62.2787 | -122.5525
528.8594 | 122.5708 | -62.2009 | 60.1913 | -0.00022891 | -0.05704 | 0.12828 | 0.034955 | 0.036068 | -0.039364 | -0.026523 | 7.627e-05 | -0.015973 | 0.026517 | 0.059406 | -0.02496 | -0.024738 | 60.3378 | -61.9629 | 0.16479 | -62.2513 | 60.1181 | -62.178 | -62.1231 | 0.086975 | 0.15564 | -62.3657 | 60.0677 | 60.0769 | -62.1094 | -62.3016 | 0.022888 | 0.07782 | -0.073242 | 0.23804 | -0.050354 | -0.12817 | 0.14648 | 0.091553 | -0.10071 | -0.1236 | 62.2879 | -0.1648 | -0.064087 | -0.11444 | 122.319 | 122.5388 | 62.3657 | -122.3145 | 122.2687 | 122.2778 | 62.3566 | -122.493
530.9062 | 122.5983 | -62.1964 | 60.2188 | 0.0074006 | -0.053408 | 0.12807 | 0.033887 | 0.036923 | -0.041073 | -0.026737 | -0.0075532 | -0.014477 | 0.028013 | 0.056843 | -0.024532 | -0.025806 | 60.2875 | -62.0499 | 0.07782 | -62.2833 | 60.1456 | -62.1643 | -62.1048 | 0.054932 | 0.09613 | -62.3978 | 60.1181 | 60.1135 | -62.0956 | -62.3062 | 0.032043 | 0.091553 | -0.073242 | 0.14648 | -0.086975 | -0.17853 | 0.068665 | 0.10071 | -0.10986 | -0.10071 | 62.2513 | -0.20142 | -0.091553 | -0.10529 | 122.3419 | 122.4838 | 62.2742 | -122.3236 | 122.3145 | 122.3099 | 62.2925 | -122.525
532.6875 | 122.7081 | -62.1826 | 60.173 | -0.00022891 | -0.054903 | 0.12551 | 0.030683 | 0.036068 | -0.031247 | -0.025028 | 0.0077058 | -0.0095638 | 0.028013 | 0.062824 | -0.021969 | -0.02666 | 60.2417 | -62.1414 | 0 | -62.3474 | 60.1364 | -62.233 | -62.1689 | 0.073242 | 0.059509 | -62.4985 | 60.0952 | 60.0861 | -62.146 | -62.352 | -0.050354 | 0.013733 | -0.036621 | 0.041199 | -0.16479 | -0.17853 | 0.068664 | 0.036621 | -0.16937 | -0.07782 | 62.2559 | -0.31586 | -0.14648 | -0.086975 | 122.319 | 122.4243 | 62.1826 | -122.3419 | 122.2778 | 122.2687 | 62.2421 | -122.525
534.4375 | 122.58 | -62.2238 | 60.2097 | -0.00022891 | -0.056399 | 0.12914 | 0.034314 | 0.035855 | -0.040219 | -0.025669 | 0.0077058 | -0.012982 | 0.027158 | 0.055988 | -0.022396 | -0.020892 | 60.3745 | -61.9446 | 0.14648 | -62.2467 | 60.1181 | -62.1689 | -62.1002 | 0.10071 | 0.16479 | -62.352 | 60.0815 | 60.0769 | -62.1231 | -62.2879 | 0.054932 | 0.1236 | -0.091553 | 0.27924 | -0.022888 | -0.14648 | 0.16479 | 0.10071 | -0.064087 | -0.12817 | 62.3245 | -0.12817 | -0.064087 | -0.13275 | 122.3419 | 122.5983 | 62.3703 | -122.3099 | 122.3053 | 122.3007 | 62.3886 | -122.4976
536.375 | 122.644 | -62.2192 | 60.1868 | 0.0074006 | -0.054903 | 0.12828 | 0.029614 | 0.035427 | -0.034451 | -0.024601 | -0.015182 | -0.010418 | 0.029081 | 0.05962 | -0.01791 | -0.025592 | 60.2097 | -62.1735 | -0.018311 | -62.3749 | 60.1456 | -62.2192 | -62.1643 | 0.041199 | 0.036621 | -62.558 | 60.1181 | 60.0586 | -62.178 | -62.3657 | 0 | 0.054931 | -0.041199 | 0.045776 | -0.15564 | -0.21057 | 0.022888 | 0.041198 | -0.14649 | -0.068665 | 62.2604 | -0.33875 | -0.19226 | -0.12817 | 122.3648 | 122.4289 | 62.2009 | -122.3511 | 122.3373 | 122.2778 | 62.2559 | -122.5525
538.875 | 122.6669 | -62.2238 | 60.1685 | -0.00022891 | -0.05469 | 0.12593 | 0.032178 | 0.035855 | -0.033596 | -0.025242 | -0.0075532 | -0.0117 | 0.028867 | 0.05962 | -0.01791 | -0.024097 | 60.1913 | -62.178 | -0.018311 | -62.3703 | 60.1685 | -62.2421 | -62.1918 | 0.041199 | 0.045776 | -62.5671 | 60.1135 | 60.0769 | -62.178 | -62.384 | -0.01831 | 0.032044 | 0 | 0.045776 | -0.14648 | -0.17853 | 0.022888 | 0.045776 | -0.16022 | -0.054932 | 62.265 | -0.34332 | -0.18311 | -0.091553 | 122.3923 | 122.4152 | 62.2055 | -122.3602 | 122.3373 | 122.3007 | 62.2696 | -122.5525
540.6562 | 122.5525 | -62.2192 | 60.228 | -0.0078584 | -0.06238 | 0.12978 | 0.031964 | 0.03735 | -0.044064 | -0.025882 | 7.627e-05 | -0.013836 | 0.02844 | 0.058125 | -0.023251 | -0.022388 | 60.2829 | -62.0178 | 0.073242 | -62.2787 | 60.1273 | -62.146 | -62.0956 | 0.054932 | 0.10529 | -62.4115 | 60.0906 | 60.0861 | -62.0911 | -62.2787 | 0.073242 | 0.1236 | -0.10071 | 0.20142 | -0.05951 | -0.18311 | 0.054932 | 0.12817 | -0.05951 | -0.13733 | 62.2742 | -0.19226 | -0.13275 | -0.14191 | 122.3465 | 122.5021 | 62.2925 | -122.3236 | 122.3099 | 122.3053 | 62.3245 | -122.5067
542.5781 | 122.644 | -62.2101 | 60.1776 | -0.00022891 | -0.055117 | 0.12807 | 0.032819 | 0.03735 | -0.032956 | -0.025882 | 0.0077058 | -0.0095638 | 0.029081 | 0.061115 | -0.018337 | -0.023669 | 60.2005 | -62.2009 | -0.004578 | -62.3703 | 60.1318 | -62.2375 | -62.178 | 0.041199 | 0.050354 | -62.5626 | 60.1044 | 60.0815 | -62.1597 | -62.3657 | -0.027466 | 0.032043 | -0.045776 | 0.009155 | -0.16022 | -0.19226 | 0.022888 | 0.050354 | -0.15564 | -0.073242 | 62.2513 | -0.35248 | -0.19684 | -0.09613 | 122.3419 | 122.4106 | 62.2055 | -122.3557 | 122.3145 | 122.2916 | 62.2604 | -122.5433
544.4062 | 122.6624 | -62.2009 | 60.1685 | -0.0078584 | -0.050631 | 0.12636 | 0.035169 | 0.035 | -0.034024 | -0.023533 | 0.0077058 | -0.011273 | 0.027372 | 0.061115 | -0.020687 | -0.025378 | 60.2325 | -62.0865 | 0.073242 | -62.3245 | 60.1181 | -62.2238 | -62.178 | 0.064087 | 0.09613 | -62.5031 | 60.0906 | 60.0632 | -62.1735 | -62.3749 | -0.022888 | 0.022888 | -0.050354 | 0.11444 | -0.1236 | -0.14648 | 0.064087 | 0.027466 | -0.17395 | -0.07782 | 62.265 | -0.30212 | -0.12817 | -0.10529 | 122.319 | 122.4335 | 62.2742 | -122.3465 | 122.2916 | 122.2641 | 62.2971 | -122.5433
546.2812 | 122.525 | -62.2238 | 60.2005 | -0.00022891 | -0.052981 | 0.12615 | 0.035596 | 0.035641 | -0.04086 | -0.025669 | 0.0077058 | -0.012341 | 0.028653 | 0.059193 | -0.026455 | -0.022388 | 60.2966 | -61.9904 | 0.14191 | -62.2696 | 60.1089 | -62.1735 | -62.1185 | 0.036621 | 0.10071 | -62.4435 | 60.0906 | 60.0815 | -62.1323 | -62.3337 | 0.050354 | 0.10529 | -0.091552 | 0.23346 | -0.045776 | -0.15106 | 0.096131 | 0.091553 | -0.10986 | -0.10986 | 62.2604 | -0.21973 | -0.10986 | -0.11902 | 122.3328 | 122.5204 | 62.3657 | -122.319 | 122.3145 | 122.3053 | 62.3245 | -122.5342
548.0938 | 122.6257 | -62.2238 | 60.1547 | 0.0074006 | -0.055758 | 0.12722 | 0.030896 | 0.03735 | -0.034024 | -0.024814 | 7.627e-05 | -0.012127 | 0.027799 | 0.058125 | -0.019619 | -0.026874 | 60.1913 | -62.1735 | 0.004578 | -62.352 | 60.1593 | -62.2238 | -62.1964 | 0.004578 | 0.041199 | -62.5717 | 60.1135 | 60.1135 | -62.1735 | -62.3611 | 0 | 0.027466 | 0.004578 | 0.050354 | -0.12817 | -0.15564 | 0.036621 | 0.050354 | -0.13733 | -0.041199 | 62.2284 | -0.3479 | -0.21057 | -0.041199 | 122.3831 | 122.4152 | 62.2284 | -122.3511 | 122.3373 | 122.3373 | 62.265 | -122.5159
549.9062 | 122.5342 | -62.2101 | 60.2234 | -0.00022891 | -0.056399 | 0.12807 | 0.033673 | 0.037136 | -0.040646 | -0.027378 | 7.627e-05 | -0.015118 | 0.027585 | 0.057911 | -0.025173 | -0.023029 | 60.2966 | -61.9904 | 0.16937 | -62.2604 | 60.1181 | -62.1872 | -62.1277 | 0.050354 | 0.11444 | -62.439 | 60.0906 | 60.0815 | -62.1048 | -62.3108 | 0.022888 | 0.082397 | -0.10529 | 0.21973 | -0.050354 | -0.13275 | 0.073242 | 0.10529 | -0.10071 | -0.13275 | 62.2604 | -0.22888 | -0.12817 | -0.14191 | 122.3282 | 122.5067 | 62.3795 | -122.3511 | 122.3007 | 122.2916 | 62.3245 | -122.5342
551.625 | 122.5433 | -62.2375 | 60.2005 | -0.00022891 | -0.054903 | 0.12679 | 0.033673 | 0.036495 | -0.041073 | -0.028019 | 7.627e-05 | -0.014477 | 0.02844 | 0.060902 | -0.025814 | -0.024524 | 60.3149 | -61.9904 | 0.14648 | -62.2513 | 60.1135 | -62.1826 | -62.1094 | 0.050354 | 0.12817 | -62.3932 | 60.0769 | 60.0998 | -62.1094 | -62.3245 | 0.054932 | 0.12817 | -0.086975 | 0.24719 | -0.013733 | -0.14191 | 0.11444 | 0.12817 | -0.086975 | -0.1236 | 62.2879 | -0.15564 | -0.068664 | -0.10071 | 122.3511 | 122.5525 | 62.384 | -122.3099 | 122.3145 | 122.3373 | 62.3657 | -122.525
553.3438 | 122.5845 | -62.2147 | 60.2005 | -0.00022891 | -0.055544 | 0.12828 | 0.033246 | 0.037991 | -0.042996 | -0.027378 | -0.015182 | -0.015759 | 0.025449 | 0.058766 | -0.02496 | -0.024738 | 60.2875 | -62.0407 | 0.073242 | -62.265 | 60.1593 | -62.146 | -62.0773 | 0.064087 | 0.10071 | -62.3978 | 60.0769 | 60.1181 | -62.0956 | -62.3016 | 0.068665 | 0.13733 | -0.041198 | 0.17395 | -0.050354 | -0.18768 | 0.086976 | 0.11902 | -0.086975 | -0.1236 | 62.2787 | -0.1831 | -0.09613 | -0.082397 | 122.374 | 122.5021 | 62.2879 | -122.2778 | 122.2916 | 122.3328 | 62.3154 | -122.5021
555.0625 | 122.6852 | -62.2147 | 60.141 | 0.0074006 | -0.051272 | 0.12615 | 0.033887 | 0.035 | -0.034451 | -0.027164 | 7.627e-05 | -0.0087094 | 0.02844 | 0.061543 | -0.020046 | -0.027515 | 60.2509 | -62.1414 | 0.054932 | -62.3245 | 60.1639 | -62.265 | -62.1872 | 0.041199 | 0.068665 | -62.5168 | 60.1044 | 60.0769 | -62.1735 | -62.352 | -0.050354 | 0.027466 | 0.022888 | 0.073243 | -0.10986 | -0.13733 | 0.10986 | 0.041199 | -0.13733 | -0.036621 | 62.2559 | -0.30212 | -0.16479 | -0.064087 | 122.3785 | 122.4655 | 62.2696 | -122.3282 | 122.319 | 122.2916 | 62.2833 | -122.493
556.8906 | 122.5845 | -62.2101 | 60.1776 | -0.0078584 | -0.06003 | 0.12935 | 0.030255 | 0.035855 | -0.04086 | -0.02631 | 0.0077058 | -0.014904 | 0.02374 | 0.060688 | -0.021114 | -0.023669 | 60.347 | -61.9492 | 0.14191 | -62.2375 | 60.1089 | -62.1597 | -62.1002 | 0.10071 | 0.14191 | -62.3566 | 60.0723 | 60.1227 | -62.0728 | -62.3154 | 0.050354 | 0.10986 | -0.068664 | 0.26093 | -0.027466 | -0.13733 | 0.16937 | 0.13733 | -0.10529 | -0.10529 | 62.3108 | -0.14648 | -0.041198 | -0.054931 | 122.319 | 122.5571 | 62.352 | -122.2778 | 122.2824 | 122.3328 | 62.352 | -122.493
558.6562 | 122.612 | -62.178 | 60.2051 | 0.0074006 | -0.058535 | 0.1285 | 0.032605 | 0.036709 | -0.041714 | -0.027805 | 7.627e-05 | -0.014264 | 0.026517 | 0.060474 | -0.025387 | -0.024951 | 60.3287 | -62.0224 | 0.10071 | -62.2604 | 60.1364 | -62.1735 | -62.1231 | 0.091553 | 0.13733 | -62.352 | 60.1089 | 60.1135 | -62.1094 | -62.2696 | 0.004578 | 0.054932 | -0.068664 | 0.15564 | -0.082397 | -0.13733 | 0.1236 | 0.068665 | -0.091552 | -0.09613 | 62.2696 | -0.17395 | -0.082398 | -0.091553 | 122.3145 | 122.5067 | 62.2787 | -122.3282 | 122.287 | 122.2916 | 62.3154 | -122.4747
560.375 | 122.6349 | -62.1964 | 60.2005 | -0.00022891 | -0.053835 | 0.12658 | 0.030255 | 0.036068 | -0.037442 | -0.026951 | 7.627e-05 | -0.011914 | 0.027372 | 0.058552 | -0.020046 | -0.025165 | 60.3516 | -61.9949 | 0.10529 | -62.2559 | 60.1135 | -62.1826 | -62.1231 | 0.15564 | 0.16022 | -62.3932 | 60.0815 | 60.0632 | -62.1048 | -62.3154 | 0.013733 | 0.073242 | -0.086975 | 0.20142 | -0.059509 | -0.13275 | 0.15106 | 0.091553 | -0.11902 | -0.11902 | 62.352 | -0.19684 | -0.077819 | -0.13733 | 122.3099 | 122.5479 | 62.3016 | -122.3236 | 122.2778 | 122.2595 | 62.3566 | -122.5159
562.1562 | 122.7036 | -62.2009 | 60.1868 | -0.00022891 | -0.053835 | 0.12764 | 0.03111 | 0.036709 | -0.035305 | -0.025455 | 7.627e-05 | -0.011273 | 0.026517 | 0.061543 | -0.018337 | -0.024951 | 60.2509 | -62.1231 | -0.004578 | -62.3383 | 60.1593 | -62.1964 | -62.1826 | 0.082397 | 0.091553 | -62.4664 | 60.0998 | 60.0815 | -62.1323 | -62.3383 | 0.004578 | 0.018311 | -0.027466 | 0.07782 | -0.13733 | -0.15564 | 0.064086 | 0.068665 | -0.13733 | -0.086976 | 62.2833 | -0.2655 | -0.12817 | -0.10529 | 122.3602 | 122.4518 | 62.1963 | -122.3694 | 122.3007 | 122.2824 | 62.2925 | -122.525
563.875 | 122.7036 | -62.178 | 60.1639 | 0.0074006 | -0.055758 | 0.12508 | 0.030469 | 0.036068 | -0.035305 | -0.024814 | 0.0077058 | -0.011486 | 0.026944 | 0.062397 | -0.021542 | -0.023029 | 60.2325 | -62.1277 | 0.004578 | -62.3337 | 60.141 | -62.2055 | -62.1506 | 0.082397 | 0.082397 | -62.4893 | 60.1044 | 60.0906 | -62.1323 | -62.3291 | -0.027465 | 0.027466 | -0.022888 | 0.050354 | -0.15564 | -0.1831 | 0.068665 | 0.045777 | -0.15106 | -0.059509 | 62.2604 | -0.31128 | -0.16022 | -0.073242 | 122.319 | 122.4106 | 62.1826 | -122.3145 | 122.2824 | 122.2687 | 62.2604 | -122.493
565.6562 | 122.6944 | -62.1918 | 60.1639 | 0.0074006 | -0.054476 | 0.12935 | 0.030683 | 0.035214 | -0.037442 | -0.025242 | 0.0077058 | -0.011486 | 0.027158 | 0.059193 | -0.019833 | -0.023883 | 60.26 | -62.1185 | 0.004578 | -62.3474 | 60.1456 | -62.2238 | -62.146 | 0.091553 | 0.10529 | -62.471 | 60.1044 | 60.0906 | -62.1094 | -62.3337 | -0.032044 | 0.045776 | -0.01831 | 0.073242 | -0.15564 | -0.20142 | 0.096131 | 0.082397 | -0.14191 | -0.059509 | 62.2833 | -0.27924 | -0.13733 | -0.073242 | 122.3373 | 122.4518 | 62.1964 | -122.3099 | 122.2961 | 122.2824 | 62.2971 | -122.4976
567.3906 | 122.5571 | -62.2009 | 60.2188 | -0.00022891 | -0.058108 | 0.12807 | 0.031751 | 0.032437 | -0.041714 | -0.026951 | 0.0077058 | -0.015545 | 0.024808 | 0.056843 | -0.021114 | -0.022815 | 60.2783 | -62.027 | 0.054932 | -62.265 | 60.1227 | -62.1414 | -62.1002 | 0.068665 | 0.10071 | -62.4115 | 60.0815 | 60.1044 | -62.0956 | -62.2971 | 0.05951 | 0.10071 | -0.09613 | 0.17395 | -0.064087 | -0.16479 | 0.059509 | 0.10529 | -0.09613 | -0.13733 | 62.2696 | -0.21057 | -0.11444 | -0.11444 | 122.3236 | 122.4792 | 62.2559 | -122.319 | 122.2824 | 122.3053 | 62.3016 | -122.5159
569.1562 | 122.5433 | -62.1918 | 60.2325 | -0.00022891 | -0.058962 | 0.12764 | 0.031964 | 0.035427 | -0.041287 | -0.028446 | -0.0075532 | -0.014477 | 0.025449 | 0.060474 | -0.023464 | -0.024524 | 60.2921 | -62.027 | 0.068665 | -62.2787 | 60.141 | -62.1323 | -62.0911 | 0.054932 | 0.10071 | -62.3978 | 60.1135 | 60.0998 | -62.0956 | -62.3062 | 0.059509 | 0.10071 | -0.091553 | 0.16479 | -0.086976 | -0.18768 | 0.059509 | 0.09613 | -0.11444 | -0.11902 | 62.2467 | -0.20599 | -0.091553 | -0.13275 | 122.3328 | 122.4838 | 62.2604 | -122.3236 | 122.3053 | 122.2916 | 62.2925 | -122.5388
570.9375 | 122.5342 | -62.2147 | 60.2325 | -0.00022891 | -0.056399 | 0.12636 | 0.031323 | 0.035427 | -0.035946 | -0.028019 | 7.627e-05 | -0.012341 | 0.029294 | 0.059193 | -0.022183 | -0.024097 | 60.2463 | -62.0728 | 0.073242 | -62.3108 | 60.1593 | -62.2101 | -62.146 | -0.009155 | 0.013733 | -62.5031 | 60.1227 | 60.0677 | -62.1689 | -62.3291 | 0.004578 | 0.068665 | -0.073242 | 0.14191 | -0.09613 | -0.1648 | 0.013733 | 0.045777 | -0.11444 | -0.10986 | 62.2055 | -0.28839 | -0.17395 | -0.16479 | 122.374 | 122.4609 | 62.2879 | -122.3785 | 122.3373 | 122.2824 | 62.2284 | -122.5616
572.6562 | 122.6807 | -62.1735 | 60.1501 | -0.0078584 | -0.054476 | 0.12679 | 0.034314 | 0.034786 | -0.034451 | -0.025882 | 7.627e-05 | -0.011059 | 0.025876 | 0.061543 | -0.018978 | -0.024738 | 60.2509 | -62.146 | -0.004578 | -62.3474 | 60.1593 | -62.2238 | -62.1735 | 0.050354 | 0.068665 | -62.5168 | 60.0906 | 60.0952 | -62.1735 | -62.352 | -0.050354 | 0 | 0.009156 | 0.027466 | -0.17395 | -0.17395 | 0.10071 | 0 | -0.17853 | -0.059509 | 62.2238 | -0.34332 | -0.16479 | -0.054931 | 122.3328 | 122.4243 | 62.1689 | -122.3236 | 122.2641 | 122.2687 | 62.2421 | -122.5021
574.3906 | 122.5067 | -62.2284 | 60.228 | -0.00022891 | -0.052981 | 0.12786 | 0.036237 | 0.035855 | -0.040005 | -0.026096 | -0.0075532 | -0.013836 | 0.028013 | 0.059834 | -0.020687 | -0.023242 | 60.3012 | -62.0087 | 0.12817 | -62.2604 | 60.1135 | -62.178 | -62.1368 | 0.050354 | 0.086975 | -62.4481 | 60.0998 | 60.0861 | -62.1323 | -62.3108 | 0.050354 | 0.091553 | -0.11444 | 0.21973 | -0.032043 | -0.1236 | 0.073242 | 0.096131 | -0.082397 | -0.12817 | 62.2787 | -0.21973 | -0.13733 | -0.14191 | 122.3419 | 122.5296 | 62.3566 | -122.3648 | 122.3282 | 122.3145 | 62.3154 | -122.5388
576.1562 | 122.5616 | -62.1964 | 60.2371 | -0.015487 | -0.059603 | 0.12828 | 0.034741 | 0.036709 | -0.041928 | -0.027805 | 7.627e-05 | -0.016186 | 0.02609 | 0.060047 | -0.024105 | -0.025378 | 60.2875 | -62.0407 | 0.07782 | -62.2833 | 60.1456 | -62.146 | -62.0773 | 0.059509 | 0.086975 | -62.4069 | 60.1044 | 60.0906 | -62.0819 | -62.2833 | 0.050354 | 0.11902 | -0.091553 | 0.15564 | -0.086975 | -0.20599 | 0.050354 | 0.11444 | -0.086975 | -0.13275 | 62.2559 | -0.21057 | -0.1236 | -0.14648 | 122.3419 | 122.4838 | 62.2742 | -122.3145 | 122.3007 | 122.287 | 62.2833 | -122.5204
577.8594 | 122.6669 | -62.1872 | 60.1547 | 0.0074006 | -0.05234 | 0.12658 | 0.03645 | 0.034359 | -0.033169 | -0.025669 | 0.0077058 | -0.0097776 | 0.028013 | 0.060047 | -0.020687 | -0.024097 | 60.2371 | -62.1368 | 0.041199 | -62.3245 | 60.1501 | -62.2192 | -62.1689 | 0.009155 | 0.032043 | -62.5259 | 60.1089 | 60.054 | -62.1643 | -62.3611 | -0.032043 | 0.018311 | -0.004578 | 0.050354 | -0.13733 | -0.15564 | 0.082398 | 0.022888 | -0.17395 | -0.045776 | 62.1964 | -0.33874 | -0.16479 | -0.10071 | 122.3373 | 122.4243 | 62.2284 | -122.3236 | 122.2961 | 122.2412 | 62.2192 | -122.5159
579.625 | 122.6669 | -62.2147 | 60.2005 | -0.0078584 | -0.053835 | 0.12658 | 0.032605 | 0.036923 | -0.034878 | -0.022678 | 7.627e-05 | -0.0117 | 0.028226 | 0.060688 | -0.019192 | -0.024097 | 60.2234 | -62.1735 | -0.022888 | -62.3474 | 60.1501 | -62.2238 | -62.1735 | 0.045776 | 0.036621 | -62.5351 | 60.0952 | 60.0906 | -62.1597 | -62.3474 | -0.009155 | 0.041199 | -0.050354 | 0.041199 | -0.13275 | -0.17395 | 0.022889 | 0.054932 | -0.13275 | -0.10528 | 62.2604 | -0.32043 | -0.18768 | -0.10986 | 122.3648 | 122.4381 | 62.1918 | -122.374 | 122.3099 | 122.3053 | 62.2513 | -122.5479
581.4219 | 122.525 | -62.2284 | 60.2097 | -0.0078584 | -0.055971 | 0.12764 | 0.032392 | 0.034146 | -0.041287 | -0.026523 | -0.0075532 | -0.014904 | 0.029294 | 0.060047 | -0.023892 | -0.024951 | 60.26 | -62.0636 | 0.07782 | -62.3062 | 60.1135 | -62.2147 | -62.1414 | -0.013733 | 0.013733 | -62.4985 | 60.1089 | 60.1089 | -62.1368 | -62.3383 | 0.013733 | 0.086976 | -0.096131 | 0.16479 | -0.077819 | -0.16479 | 0.050354 | 0.091553 | -0.10986 | -0.10071 | 62.2147 | -0.27008 | -0.16022 | -0.10071 | 122.3419 | 122.4884 | 62.3062 | -122.3511 | 122.3373 | 122.3373 | 62.2421 | -122.5479
583.2031 | 122.6669 | -62.1964 | 60.1318 | 0.0074006 | -0.054049 | 0.12551 | 0.032819 | 0.038204 | -0.033383 | -0.023105 | 7.627e-05 | -0.010632 | 0.02844 | 0.061543 | -0.021328 | -0.023883 | 60.2692 | -62.0911 | 0.073242 | -62.3291 | 60.1501 | -62.2238 | -62.1689 | 0.073242 | 0.091553 | -62.4939 | 60.0723 | 60.0677 | -62.146 | -62.384 | -0.027466 | 0.027466 | 0.01831 | 0.10529 | -0.13275 | -0.16022 | 0.13733 | 0.050354 | -0.18768 | -0.059509 | 62.2696 | -0.29755 | -0.10986 | -0.064087 | 122.3465 | 122.4655 | 62.2696 | -122.3007 | 122.2687 | 122.2641 | 62.2879 | -122.5159
584.9844 | 122.6624 | -62.1826 | 60.1639 | -0.0078584 | -0.056185 | 0.12636 | 0.029614 | 0.036495 | -0.039151 | -0.023746 | 7.627e-05 | -0.014264 | 0.025876 | 0.059834 | -0.020687 | -0.025378 | 60.3058 | -62.0178 | 0.10071 | -62.2559 | 60.1044 | -62.1643 | -62.1231 | 0.13275 | 0.16479 | -62.3978 | 60.0449 | 60.0861 | -62.0956 | -62.2925 | 0.01831 | 0.059509 | -0.059509 | 0.16479 | -0.073242 | -0.13275 | 0.14191 | 0.086975 | -0.10986 | -0.11902 | 62.3154 | -0.21515 | -0.10529 | -0.077819 | 122.287 | 122.4884 | 62.2833 | -122.287 | 122.2275 | 122.2687 | 62.3474 | -122.4564
586.7031 | 122.5296 | -62.2101 | 60.2234 | 0.0074006 | -0.055971 | 0.12935 | 0.032819 | 0.034146 | -0.039578 | -0.027164 | -0.0075532 | -0.017041 | 0.02844 | 0.058766 | -0.021755 | -0.023883 | 60.3058 | -61.9949 | 0.16479 | -62.2467 | 60.0952 | -62.1826 | -62.1094 | 0.068665 | 0.1236 | -62.4023 | 60.0677 | 60.0586 | -62.114 | -62.3016 | 0.027466 | 0.10071 | -0.12817 | 0.21515 | -0.036621 | -0.13733 | 0.082397 | 0.09613 | -0.091553 | -0.15564 | 62.2787 | -0.19226 | -0.10071 | -0.16479 | 122.3053 | 122.5159 | 62.3749 | -122.3328 | 122.2778 | 122.2687 | 62.3337 | -122.525
588.4375 | 122.5983 | -62.2238 | 60.2188 | 0.0074006 | -0.055971 | 0.12978 | 0.035382 | 0.036068 | -0.040219 | -0.027591 | 7.627e-05 | -0.015973 | 0.027799 | 0.057911 | -0.025601 | -0.023669 | 60.3149 | -61.9858 | 0.1236 | -62.2375 | 60.1364 | -62.1552 | -62.0956 | 0.11902 | 0.14648 | -62.352 | 60.0723 | 60.0677 | -62.114 | -62.2879 | 0.068665 | 0.12817 | -0.082397 | 0.23804 | -0.013733 | -0.14191 | 0.09613 | 0.10986 | -0.064087 | -0.14648 | 62.3428 | -0.12817 | -0.064087 | -0.15106 | 122.3602 | 122.5388 | 62.3474 | -122.3145 | 122.2961 | 122.2916 | 62.3703 | -122.5067
590.2031 | 122.5479 | -62.1964 | 60.2463 | -0.00022891 | -0.059603 | 0.12935 | 0.034101 | 0.034786 | -0.038723 | -0.02866 | 0.0077058 | -0.014904 | 0.026304 | 0.058125 | -0.021755 | -0.025378 | 60.2966 | -62.027 | 0.07782 | -62.2742 | 60.1456 | -62.1323 | -62.0819 | 0.064087 | 0.09613 | -62.3978 | 60.1044 | 60.0861 | -62.0819 | -62.2833 | 0.064087 | 0.11444 | -0.10071 | 0.16937 | -0.07782 | -0.19226 | 0.050354 | 0.11444 | -0.086975 | -0.14191 | 62.2604 | -0.20142 | -0.11444 | -0.16022 | 122.3419 | 122.493 | 62.2742 | -122.3282 | 122.3007 | 122.2824 | 62.2925 | -122.5296
592 | 122.644 | -62.2055 | 60.1685 | 0.0074006 | -0.054903 | 0.12593 | 0.033673 | 0.034786 | -0.032742 | -0.024173 | 7.627e-05 | -0.010846 | 0.027372 | 0.058766 | -0.019619 | -0.026019 | 60.2417 | -62.1185 | 0.032043 | -62.3474 | 60.1181 | -62.2284 | -62.1826 | 0.045776 | 0.064087 | -62.5534 | 60.0815 | 60.0494 | -62.1918 | -62.3795 | -0.022889 | 0.022888 | -0.050354 | 0.086975 | -0.14191 | -0.16479 | 0.073242 | 0.013733 | -0.17395 | -0.086975 | 62.2513 | -0.3479 | -0.17395 | -0.11902 | 122.3236 | 122.4472 | 62.2375 | -122.3511 | 122.287 | 122.2549 | 62.2696 | -122.5479
593.7031 | 122.644 | -62.2055 | 60.1456 | -0.0078584 | -0.056612 | 0.12529 | 0.031751 | 0.035 | -0.034237 | -0.023105 | -0.0075532 | -0.0099912 | 0.029081 | 0.060474 | -0.020046 | -0.024097 | 60.1913 | -62.1597 | -0.013733 | -62.3566 | 60.1456 | -62.2375 | -62.1872 | 0.032043 | 0.036621 | -62.5397 | 60.1135 | 60.0815 | -62.178 | -62.3383 | -0.032044 | 0.01831 | 0 | 0.045776 | -0.15106 | -0.16937 | 0.045776 | 0.027465 | -0.13275 | -0.032044 | 62.2375 | -0.33417 | -0.20142 | -0.064087 | 122.3511 | 122.3969 | 62.1918 | -122.3328 | 122.319 | 122.287 | 62.2421 | -122.4838
595.4844 | 122.6349 | -62.178 | 60.1547 | -0.00022891 | -0.054262 | 0.12786 | 0.034955 | 0.036282 | -0.034237 | -0.025455 | -0.0075532 | -0.011486 | 0.027158 | 0.061756 | -0.021114 | -0.025165 | 60.26 | -62.0819 | 0.07782 | -62.3291 | 60.1089 | -62.2284 | -62.1689 | 0.054932 | 0.09613 | -62.5076 | 60.0677 | 60.0769 | -62.1689 | -62.352 | -0.050354 | 0.009156 | -0.045776 | 0.096131 | -0.15106 | -0.16022 | 0.10529 | 0.009156 | -0.17395 | -0.086975 | 62.233 | -0.32959 | -0.15564 | -0.07782 | 122.287 | 122.4381 | 62.2559 | -122.3236 | 122.2458 | 122.2549 | 62.2742 | -122.5067
597.25 | 122.5204 | -62.2009 | 60.2325 | -0.00022891 | -0.060885 | 0.12871 | 0.032605 | 0.035 | -0.04086 | -0.02631 | -0.0075532 | -0.0164 | 0.025449 | 0.057911 | -0.022183 | -0.022388 | 60.2966 | -61.9949 | 0.073242 | -62.2787 | 60.1273 | -62.1323 | -62.1002 | 0.086975 | 0.11902 | -62.3932 | 60.0952 | 60.0815 | -62.114 | -62.2925 | 0.068665 | 0.10071 | -0.10529 | 0.20599 | -0.07782 | -0.17853 | 0.064087 | 0.086975 | -0.091552 | -0.13733 | 62.2879 | -0.19226 | -0.10071 | -0.15106 | 122.3282 | 122.4976 | 62.2742 | -122.3328 | 122.2961 | 122.2824 | 62.3199 | -122.525
599.8906 | 122.5342 | -62.178 | 60.2188 | -0.00022891 | -0.058748 | 0.12978 | 0.031964 | 0.038204 | -0.040432 | -0.026737 | -0.0075532 | -0.015332 | 0.02609 | 0.058552 | -0.021542 | -0.024951 | 60.3104 | -61.9766 | 0.10071 | -62.2604 | 60.1135 | -62.1552 | -62.0956 | 0.11902 | 0.13733 | -62.4023 | 60.0906 | 60.1135 | -62.0956 | -62.2787 | 0.022889 | 0.082398 | -0.10529 | 0.20142 | -0.082397 | -0.1648 | 0.091553 | 0.082398 | -0.10071 | -0.12817 | 62.2971 | -0.2243 | -0.1236 | -0.10529 | 122.2916 | 122.4884 | 62.2787 | -122.3145 | 122.2687 | 122.2916 | 62.3154 | -122.4976
602.0938 | 122.5296 | -62.2101 | 60.2051 | -0.0078584 | -0.058321 | 0.12957 | 0.032605 | 0.035641 | -0.039364 | -0.028232 | 7.627e-05 | -0.014264 | 0.027372 | 0.058979 | -0.022823 | -0.023669 | 60.2692 | -62.0316 | 0.091553 | -62.2833 | 60.1273 | -62.1689 | -62.146 | 0.027466 | 0.027466 | -62.4573 | 60.141 | 60.0952 | -62.1735 | -62.3291 | 0.041199 | 0.064087 | -0.07782 | 0.17853 | -0.073242 | -0.13733 | 0.064087 | 0.036621 | -0.11902 | -0.064087 | 62.2375 | -0.24719 | -0.12817 | -0.10986 | 122.3373 | 122.4792 | 62.3016 | -122.3511 | 122.3511 | 122.3053 | 62.2375 | -122.5342
604.4688 | 122.6624 | -62.1872 | 60.1364 | -0.0078584 | -0.052767 | 0.12786 | 0.032819 | 0.035427 | -0.034665 | -0.026523 | 7.627e-05 | -0.012982 | 0.02844 | 0.060474 | -0.021969 | -0.024738 | 60.2142 | -62.1231 | 0.041199 | -62.3199 | 60.1364 | -62.233 | -62.1643 | 0.032043 | 0.059509 | -62.4985 | 60.1044 | 60.0906 | -62.1735 | -62.352 | -0.045776 | 0.022888 | 0 | 0.064087 | -0.13275 | -0.15564 | 0.077819 | 0.013733 | -0.16479 | -0.032044 | 62.2192 | -0.31128 | -0.14648 | -0.045777 | 122.3236 | 122.4014 | 62.2284 | -122.3007 | 122.2916 | 122.2778 | 62.2467 | -122.4884
606.7656 | 122.612 | -62.1872 | 60.2097 | -0.0078584 | -0.055971 | 0.12828 | 0.032819 | 0.035214 | -0.038723 | -0.024173 | 7.627e-05 | -0.015332 | 0.028013 | 0.060902 | -0.023892 | -0.024738 | 60.3241 | -61.9949 | 0.10529 | -62.2513 | 60.1181 | -62.1872 | -62.1094 | 0.1236 | 0.16937 | -62.3795 | 60.1135 | 60.0861 | -62.1094 | -62.2833 | 0 | 0.07782 | -0.091553 | 0.19226 | -0.064087 | -0.14191 | 0.11444 | 0.07782 | -0.09613 | -0.096131 | 62.3108 | -0.19226 | -0.096131 | -0.1236 | 122.3053 | 122.5113 | 62.2925 | -122.319 | 122.3007 | 122.2733 | 62.3566 | -122.493
608.8281 | 122.525 | -62.2055 | 60.2097 | -0.015487 | -0.054049 | 0.12636 | 0.035169 | 0.035855 | -0.039578 | -0.025242 | 7.627e-05 | -0.012127 | 0.027158 | 0.061756 | -0.025814 | -0.022815 | 60.3058 | -61.9858 | 0.14648 | -62.2513 | 60.1181 | -62.1689 | -62.114 | 0.059509 | 0.11444 | -62.3978 | 60.0998 | 60.0586 | -62.1323 | -62.3154 | 0.036621 | 0.091552 | -0.091553 | 0.21973 | -0.045777 | -0.13733 | 0.09613 | 0.073242 | -0.10986 | -0.10986 | 62.265 | -0.19226 | -0.082397 | -0.15106 | 122.3236 | 122.5113 | 62.352 | -122.3236 | 122.3053 | 122.2641 | 62.3199 | -122.525
611.1406 | 122.6257 | -62.2101 | 60.1501 | -0.0078584 | -0.053622 | 0.12487 | 0.03346 | 0.035641 | -0.033169 | -0.024601 | 7.627e-05 | -0.0099912 | 0.028013 | 0.061115 | -0.019406 | -0.025592 | 60.2646 | -62.0911 | 0.068665 | -62.3291 | 60.1273 | -62.233 | -62.1964 | 0.068665 | 0.082397 | -62.5305 | 60.0861 | 60.0815 | -62.1735 | -62.3749 | -0.022888 | 0.013733 | -0.022888 | 0.11902 | -0.11902 | -0.13275 | 0.11444 | 0.036621 | -0.1648 | -0.064086 | 62.2787 | -0.32044 | -0.15564 | -0.068664 | 122.3373 | 122.4747 | 62.2787 | -122.3465 | 122.2961 | 122.2916 | 62.2925 | -122.525
612.9375 | 122.6761 | -62.1643 | 60.1776 | -0.0078584 | -0.053622 | 0.12615 | 0.033246 | 0.036923 | -0.035092 | -0.025882 | 0.015335 | -0.013409 | 0.028013 | 0.062397 | -0.018551 | -0.02431 | 60.2142 | -62.1414 | -0.018311 | -62.3428 | 60.1685 | -62.2147 | -62.1414 | 0.045776 | 0.064087 | -62.5122 | 60.1089 | 60.0906 | -62.1735 | -62.3474 | -0.050354 | 0.022889 | -0.009155 | 0.022889 | -0.17853 | -0.20142 | 0.036621 | -0.009155 | -0.1831 | -0.068664 | 62.2101 | -0.3479 | -0.16479 | -0.086975 | 122.3328 | 122.3785 | 62.146 | -122.319 | 122.2733 | 122.2549 | 62.2284 | -122.525
615.0625 | 122.5525 | -62.1826 | 60.2509 | -0.00022891 | -0.058962 | 0.12871 | 0.034101 | 0.035427 | -0.043637 | -0.028232 | 0.0077058 | -0.016827 | 0.025876 | 0.057911 | -0.023251 | -0.024738 | 60.2692 | -62.0087 | 0.064087 | -62.2604 | 60.1135 | -62.1689 | -62.1094 | 0.073242 | 0.091553 | -62.4023 | 60.1227 | 60.0998 | -62.0956 | -62.2833 | 0.013733 | 0.073242 | -0.13733 | 0.17395 | -0.07782 | -0.15106 | 0.018311 | 0.086975 | -0.10071 | -0.12817 | 62.2559 | -0.21973 | -0.11902 | -0.15106 | 122.2961 | 122.4518 | 62.2467 | -122.3602 | 122.3053 | 122.2824 | 62.2742 | -122.5342
618.0625 | 122.5754 | -62.1964 | 60.2234 | 0.0074006 | -0.061953 | 0.12957 | 0.033673 | 0.034359 | -0.042355 | -0.027591 | -0.0075532 | -0.0164 | 0.025449 | 0.059834 | -0.022396 | -0.024951 | 60.2829 | -62.027 | 0.068665 | -62.2559 | 60.1547 | -62.1506 | -62.0773 | 0.045776 | 0.10071 | -62.3978 | 60.1227 | 60.1135 | -62.0956 | -62.2833 | 0.045776 | 0.11902 | -0.068665 | 0.16937 | -0.059509 | -0.17853 | 0.059509 | 0.10071 | -0.086975 | -0.10071 | 62.2421 | -0.20142 | -0.11444 | -0.10986 | 122.3511 | 122.4792 | 62.265 | -122.3007 | 122.319 | 122.3099 | 62.2971 | -122.5067
620.125 | 122.5021 | -62.2147 | 60.1868 | -0.015487 | -0.053622 | 0.1285 | 0.035809 | 0.034146 | -0.037228 | -0.028446 | -0.0075532 | -0.012127 | 0.027585 | 0.057484 | -0.021114 | -0.025592 | 60.3104 | -61.9949 | 0.11902 | -62.2604 | 60.1181 | -62.2147 | -62.1277 | 0.032043 | 0.068665 | -62.4527 | 60.1181 | 60.0815 | -62.1414 | -62.3428 | 0 | 0.086975 | -0.068665 | 0.21973 | -0.045776 | -0.13275 | 0.1236 | 0.073243 | -0.12817 | -0.068665 | 62.2467 | -0.23804 | -0.10986 | -0.10529 | 122.3328 | 122.525 | 62.3337 | -122.3145 | 122.3328 | 122.2961 | 62.2833 | -122.5296
622.1094 | 122.6028 | -62.1964 | 60.1913 | -0.00022891 | -0.056399 | 0.12529 | 0.031964 | 0.035641 | -0.035305 | -0.026523 | 0.0077058 | -0.012982 | 0.026517 | 0.05962 | -0.021114 | -0.025165 | 60.347 | -62.0041 | 0.11444 | -62.2467 | 60.1044 | -62.1597 | -62.1048 | 0.14191 | 0.18768 | -62.384 | 60.0677 | 60.054 | -62.0956 | -62.2742 | 0.036621 | 0.091553 | -0.086975 | 0.19226 | -0.050354 | -0.14191 | 0.15564 | 0.10071 | -0.07782 | -0.1236 | 62.3383 | -0.18768 | -0.10986 | -0.13733 | 122.3007 | 122.5433 | 62.3108 | -122.2961 | 122.2641 | 122.2504 | 62.384 | -122.4655
624.1406 | 122.6028 | -62.2147 | 60.1547 | -0.0078584 | -0.053622 | 0.12615 | 0.028974 | 0.035641 | -0.033169 | -0.025882 | -0.0075532 | -0.010846 | 0.02844 | 0.062183 | -0.018124 | -0.028155 | 60.2554 | -62.1094 | 0.050354 | -62.3474 | 60.1181 | -62.2375 | -62.1643 | 0.041199 | 0.064087 | -62.5214 | 60.0906 | 60.0632 | -62.178 | -62.3749 | -0.022888 | 0.050354 | -0.036621 | 0.10529 | -0.13275 | -0.1831 | 0.10071 | 0.036621 | -0.16022 | -0.064087 | 62.2559 | -0.3067 | -0.14648 | -0.091553 | 122.3328 | 122.4701 | 62.265 | -122.319 | 122.3053 | 122.2778 | 62.2787 | -122.5296
626.3594 | 122.5342 | -62.2055 | 60.2325 | -0.00022891 | -0.057253 | 0.127 | 0.035169 | 0.036495 | -0.039578 | -0.026951 | 0.0077058 | -0.015973 | 0.026304 | 0.05727 | -0.023251 | -0.024097 | 60.3195 | -61.972 | 0.15564 | -62.2467 | 60.1135 | -62.1597 | -62.1048 | 0.064087 | 0.1236 | -62.4023 | 60.0998 | 60.0952 | -62.146 | -62.3154 | 0.045776 | 0.10071 | -0.11902 | 0.23346 | -0.041199 | -0.14191 | 0.086975 | 0.059509 | -0.10986 | -0.13275 | 62.2696 | -0.19684 | -0.086975 | -0.13733 | 122.319 | 122.525 | 62.3611 | -122.3373 | 122.3053 | 122.3007 | 62.3291 | -122.5479
628.2812 | 122.644 | -62.2009 | 60.1547 | -0.0078584 | -0.053408 | 0.12658 | 0.033887 | 0.037564 | -0.036587 | -0.02631 | -0.0075532 | -0.0117 | 0.025876 | 0.058766 | -0.021755 | -0.024951 | 60.2234 | -62.1277 | 0.041199 | -62.3199 | 60.141 | -62.2009 | -62.178 | 0.018311 | 0.045776 | -62.4985 | 60.1044 | 60.0815 | -62.1689 | -62.3611 | 0 | 0.022888 | -0.013733 | 0.073242 | -0.11902 | -0.14191 | 0.068665 | 0.032044 | -0.16022 | -0.050354 | 62.2192 | -0.29755 | -0.13733 | -0.073242 | 122.3419 | 122.4243 | 62.2421 | -122.3328 | 122.3053 | 122.2824 | 62.2467 | -122.5159
630 | 122.644 | -62.1872 | 60.1273 | -0.0078584 | -0.051699 | 0.12572 | 0.031537 | 0.037777 | -0.034665 | -0.024387 | 0.0077058 | -0.011914 | 0.029081 | 0.060688 | -0.019833 | -0.025165 | 60.2646 | -62.0865 | 0.07782 | -62.3154 | 60.1227 | -62.2192 | -62.1414 | 0.059509 | 0.086975 | -62.4847 | 60.0815 | 60.0586 | -62.1735 | -62.3474 | -0.032043 | 0.045777 | -0.004577 | 0.10071 | -0.12817 | -0.17395 | 0.13733 | 0.013733 | -0.16022 | -0.045776 | 62.2467 | -0.29755 | -0.13733 | -0.068664 | 122.3099 | 122.4518 | 62.265 | -122.2687 | 122.2687 | 122.2458 | 62.2742 | -122.4747
631.7812 | 122.6395 | -62.178 | 60.1822 | 0.0074006 | -0.053408 | 0.12828 | 0.033032 | 0.035855 | -0.035519 | -0.02631 | 0.0077058 | -0.011273 | 0.026731 | 0.061329 | -0.020046 | -0.023883 | 60.2051 | -62.1643 | -0.013733 | -62.352 | 60.1501 | -62.2147 | -62.1826 | 0.036621 | 0.045776 | -62.5351 | 60.0952 | 60.0998 | -62.1689 | -62.3566 | -0.036621 | -0.004577 | -0.032044 | 0.013733 | -0.17395 | -0.16937 | 0.022888 | 0.009156 | -0.17853 | -0.086975 | 62.2147 | -0.35705 | -0.17853 | -0.082398 | 122.3282 | 122.3831 | 62.1643 | -122.3648 | 122.2733 | 122.2778 | 62.2238 | -122.5388
633.5156 | 122.5891 | -62.1918 | 60.2097 | -0.00022891 | -0.05704 | 0.12999 | 0.035382 | 0.033718 | -0.041714 | -0.027378 | 7.627e-05 | -0.016827 | 0.026731 | 0.058766 | -0.023678 | -0.02132 | 60.3149 | -61.9766 | 0.1236 | -62.2375 | 60.1456 | -62.1368 | -62.0865 | 0.10986 | 0.12817 | -62.3291 | 60.0952 | 60.0815 | -62.0956 | -62.3016 | 0.054931 | 0.10529 | -0.064087 | 0.21515 | -0.045777 | -0.15106 | 0.10528 | 0.09613 | -0.10986 | -0.11444 | 62.3016 | -0.13733 | -0.027466 | -0.12817 | 122.3373 | 122.5067 | 62.3154 | -122.2961 | 122.287 | 122.2733 | 62.3199 | -122.5113
635.2812 | 122.5342 | -62.2101 | 60.2371 | -0.00022891 | -0.059176 | 0.13021 | 0.029828 | 0.035855 | -0.042569 | -0.028446 | 7.627e-05 | -0.018109 | 0.026731 | 0.060688 | -0.023251 | -0.024738 | 60.2783 | -62.0178 | 0.050354 | -62.2696 | 60.1318 | -62.1414 | -62.0773 | 0.068665 | 0.10071 | -62.3886 | 60.0769 | 60.0861 | -62.0956 | -62.2742 | 0.068665 | 0.13275 | -0.10529 | 0.19226 | -0.059509 | -0.19226 | 0.041198 | 0.11444 | -0.064087 | -0.16022 | 62.2787 | -0.17853 | -0.11444 | -0.15106 | 122.3419 | 122.4884 | 62.2604 | -122.3145 | 122.287 | 122.2961 | 62.3108 | -122.5113
637.0469 | 122.5891 | -62.2009 | 60.2051 | -0.0078584 | -0.056185 | 0.12764 | 0.032819 | 0.035427 | -0.041073 | -0.028873 | 0.0077058 | -0.014904 | 0.027372 | 0.056843 | -0.024319 | -0.024951 | 60.3149 | -61.9537 | 0.11444 | -62.233 | 60.1456 | -62.146 | -62.0956 | 0.10071 | 0.13275 | -62.3428 | 60.1044 | 60.0494 | -62.1002 | -62.2879 | 0.054932 | 0.10529 | -0.059509 | 0.24719 | -0.032043 | -0.13733 | 0.10986 | 0.10071 | -0.086975 | -0.10071 | 62.3016 | -0.14191 | -0.054931 | -0.15564 | 122.3465 | 122.5159 | 62.3154 | -122.3007 | 122.3053 | 122.2504 | 62.3337 | -122.493
638.7656 | 122.6761 | -62.2055 | 60.1547 | 0.0074006 | -0.054903 | 0.12764 | 0.031964 | 0.034146 | -0.032956 | -0.026951 | 7.627e-05 | -0.011273 | 0.027372 | 0.057911 | -0.02026 | -0.027942 | 60.2371 | -62.0819 | 0.054932 | -62.3016 | 60.1318 | -62.2284 | -62.1689 | 0.064087 | 0.07782 | -62.4756 | 60.0998 | 60.0586 | -62.1689 | -62.3474 | -0.022889 | 0.036621 | -0.022888 | 0.1236 | -0.096131 | -0.13275 | 0.082398 | 0.036621 | -0.14191 | -0.054932 | 62.2696 | -0.27008 | -0.12817 | -0.09613 | 122.3373 | 122.4426 | 62.2604 | -122.3236 | 122.3053 | 122.2641 | 62.2833 | -122.5021
640.5625 | 122.5342 | -62.1964 | 60.2051 | 0.0074006 | -0.056185 | 0.12957 | 0.034314 | 0.036068 | -0.039578 | -0.027378 | 7.627e-05 | -0.014264 | 0.026731 | 0.059406 | -0.024532 | -0.025378 | 60.3195 | -61.9629 | 0.16479 | -62.2375 | 60.0998 | -62.1552 | -62.0865 | 0.082397 | 0.15106 | -62.3886 | 60.054 | 60.0815 | -62.1002 | -62.2742 | 0.041199 | 0.10986 | -0.10529 | 0.23346 | -0.041199 | -0.15106 | 0.11444 | 0.09613 | -0.07782 | -0.15106 | 62.2787 | -0.19226 | -0.11444 | -0.1236 | 122.2961 | 122.5159 | 62.3611 | -122.2916 | 122.2504 | 122.2778 | 62.3474 | -122.4792
642.2812 | 122.612 | -62.2055 | 60.1593 | -0.00022891 | -0.051272 | 0.12722 | 0.030896 | 0.034146 | -0.032956 | -0.022892 | 7.627e-05 | -0.010846 | 0.026731 | 0.060261 | -0.019406 | -0.024524 | 60.2097 | -62.1552 | 0.004578 | -62.3657 | 60.1318 | -62.2238 | -62.1597 | 0.013733 | 0.041199 | -62.5671 | 60.1364 | 60.1044 | -62.1643 | -62.3566 | -0.018311 | 0.045776 | -0.027466 | 0.050354 | -0.16022 | -0.20599 | 0.050354 | 0.041198 | -0.15106 | -0.022888 | 62.2192 | -0.36163 | -0.21057 | -0.054932 | 122.3373 | 122.4152 | 62.2101 | -122.319 | 122.3419 | 122.3099 | 62.2467 | -122.5159
644.2812 | 122.5662 | -62.178 | 60.2142 | -0.0078584 | -0.055758 | 0.127 | 0.032178 | 0.035855 | -0.042141 | -0.02631 | -0.0075532 | -0.018322 | 0.026944 | 0.05962 | -0.024532 | -0.02431 | 60.3287 | -61.9354 | 0.14648 | -62.2238 | 60.1089 | -62.1231 | -62.1185 | 0.12817 | 0.16937 | -62.3199 | 60.0815 | 60.0815 | -62.0911 | -62.2787 | 0.054932 | 0.05951 | -0.10529 | 0.24262 | -0.045776 | -0.10529 | 0.11444 | 0.086976 | -0.10071 | -0.13275 | 62.3062 | -0.14191 | -0.041198 | -0.13275 | 122.287 | 122.5067 | 62.3245 | -122.3328 | 122.2595 | 122.2595 | 62.3474 | -122.493
646.25 | 122.6212 | -62.1826 | 60.1318 | -0.00022891 | -0.04764 | 0.13021 | 0.035596 | 0.037777 | -0.031674 | -0.023746 | 0.0077058 | -0.011059 | 0.027799 | 0.05727 | -0.02026 | -0.027087 | 60.26 | -62.0819 | 0.073242 | -62.3154 | 60.1273 | -62.2192 | -62.1735 | 0.091553 | 0.091553 | -62.4756 | 60.0723 | 60.0494 | -62.1597 | -62.3749 | -0.036621 | 0.009155 | -0.004578 | 0.10071 | -0.13275 | -0.14191 | 0.12817 | 0.022888 | -0.19226 | -0.059509 | 62.2742 | -0.29297 | -0.10071 | -0.082398 | 122.3099 | 122.4426 | 62.2559 | -122.3053 | 122.2549 | 122.2321 | 62.2742 | -122.5067
648.4844 | 122.6257 | -62.2055 | 60.1273 | -0.00022891 | -0.048067 | 0.12679 | 0.035382 | 0.038204 | -0.035519 | -0.026096 | 7.627e-05 | -0.010632 | 0.028226 | 0.062611 | -0.020474 | -0.026874 | 60.26 | -62.0728 | 0.086975 | -62.3154 | 60.1318 | -62.2101 | -62.1735 | 0.07782 | 0.086975 | -62.5031 | 60.0861 | 60.0677 | -62.178 | -62.352 | -0.004578 | 0.032043 | 0.004578 | 0.13275 | -0.10986 | -0.14191 | 0.13275 | 0.027465 | -0.14648 | -0.041198 | 62.2833 | -0.29755 | -0.15106 | -0.059509 | 122.3373 | 122.4655 | 62.2925 | -122.3007 | 122.2916 | 122.2733 | 62.2925 | -122.4792
650.6875 | 122.5891 | -62.2101 | 60.1639 | 0.0074006 | -0.052553 | 0.12828 | 0.036023 | 0.033718 | -0.039151 | -0.026737 | -0.0075532 | -0.012982 | 0.028867 | 0.059193 | -0.022823 | -0.025592 | 60.2097 | -62.114 | 0.041199 | -62.3383 | 60.141 | -62.2238 | -62.1552 | 0 | 0.022888 | -62.5168 | 60.0998 | 60.0952 | -62.1597 | -62.352 | -0.013733 | 0.054932 | -0.022888 | 0.09613 | -0.12817 | -0.18311 | 0.045777 | 0.050354 | -0.14191 | -0.064087 | 62.2101 | -0.3067 | -0.16479 | -0.068664 | 122.3511 | 122.4197 | 62.2513 | -122.319 | 122.3099 | 122.3053 | 62.233 | -122.5159
652.9531 | 122.6532 | -62.146 | 60.173 | -0.00022891 | -0.053194 | 0.12572 | 0.030896 | 0.034786 | -0.035092 | -0.026096 | -0.0075532 | -0.012341 | 0.028013 | 0.061115 | -0.02261 | -0.023242 | 60.1959 | -62.1643 | -0.018311 | -62.352 | 60.1318 | -62.2147 | -62.1506 | 0.036621 | 0.054932 | -62.5259 | 60.0998 | 60.0952 | -62.1506 | -62.3474 | -0.068665 | -0.004578 | -0.041199 | -0.018311 | -0.20599 | -0.20142 | 0.022888 | -0.004578 | -0.20142 | -0.073243 | 62.1826 | -0.37994 | -0.17853 | -0.07782 | 122.2778 | 122.3419 | 62.1277 | -122.3236 | 122.2458 | 122.2412 | 62.2009 | -122.5204
655.4688 | 122.5388 | -62.2055 | 60.2371 | -0.0078584 | -0.055117 | 0.12679 | 0.032605 | 0.035427 | -0.041501 | -0.027378 | 0.0077058 | -0.016827 | 0.027372 | 0.059834 | -0.023251 | -0.02431 | 60.2921 | -61.9812 | 0.10071 | -62.265 | 60.1273 | -62.1414 | -62.1002 | 0.10071 | 0.12817 | -62.3978 | 60.1089 | 60.0952 | -62.0956 | -62.2833 | 0.064087 | 0.10529 | -0.10986 | 0.2243 | -0.05951 | -0.16479 | 0.054931 | 0.10986 | -0.07782 | -0.12817 | 62.3062 | -0.19226 | -0.11444 | -0.14191 | 122.3328 | 122.4976 | 62.3062 | -122.3373 | 122.3145 | 122.3007 | 62.3337 | -122.5204
657.3906 | 122.5525 | -62.2055 | 60.2554 | -0.00022891 | -0.055117 | 0.127 | 0.032178 | 0.041195 | -0.041501 | -0.026096 | 7.627e-05 | -0.016186 | 0.027585 | 0.056843 | -0.024319 | -0.025165 | 60.2554 | -62.0041 | 0.073242 | -62.265 | 60.1501 | -62.1323 | -62.0728 | 0.068665 | 0.09613 | -62.3932 | 60.0906 | 60.0861 | -62.1002 | -62.2925 | 0.073242 | 0.13275 | -0.10529 | 0.20142 | -0.05951 | -0.19226 | 0 | 0.10529 | -0.086975 | -0.16479 | 62.2742 | -0.18768 | -0.10071 | -0.16937 | 122.3557 | 122.4609 | 62.2787 | -122.3282 | 122.2961 | 122.2916 | 62.3016 | -122.5479
659.4062 | 122.5525 | -62.2101 | 60.2142 | -0.00022891 | -0.058962 | 0.12593 | 0.032392 | 0.037136 | -0.038937 | -0.028446 | -0.0075532 | -0.01405 | 0.024808 | 0.061115 | -0.022183 | -0.025592 | 60.3241 | -61.9812 | 0.10529 | -62.2696 | 60.1181 | -62.1735 | -62.1414 | 0.13733 | 0.15106 | -62.3749 | 60.0906 | 60.0357 | -62.0819 | -62.3154 | 0.036621 | 0.068665 | -0.09613 | 0.22888 | -0.059509 | -0.12817 | 0.10986 | 0.12817 | -0.10529 | -0.1236 | 62.3474 | -0.1648 | -0.059509 | -0.17853 | 122.3282 | 122.5342 | 62.3154 | -122.3557 | 122.3007 | 122.2458 | 62.3611 | -122.5296
661.3438 | 122.6624 | -62.1918 | 60.1456 | -0.00022891 | -0.051913 | 0.12551 | 0.032819 | 0.032223 | -0.034024 | -0.027164 | 7.627e-05 | -0.011486 | 0.026731 | 0.060261 | -0.020687 | -0.026447 | 60.2234 | -62.1231 | 0.027466 | -62.3291 | 60.1501 | -62.2147 | -62.1597 | 0.018311 | 0.032043 | -62.5168 | 60.1044 | 60.0952 | -62.1735 | -62.3474 | -0.022889 | 0.032043 | 0.004577 | 0.068664 | -0.13733 | -0.16937 | 0.07782 | 0.01831 | -0.15564 | -0.041199 | 62.2101 | -0.32501 | -0.16937 | -0.050354 | 122.3419 | 122.4152 | 62.2192 | -122.3053 | 122.2961 | 122.287 | 62.2238 | -122.493
663.2188 | 122.6807 | -62.1872 | 60.1593 | -0.00022891 | -0.056185 | 0.12551 | 0.034101 | 0.035214 | -0.036374 | -0.024814 | -0.0075532 | -0.0117 | 0.028653 | 0.06197 | -0.019833 | -0.025165 | 60.2188 | -62.1323 | -0.022888 | -62.3291 | 60.1593 | -62.1918 | -62.146 | 0.059509 | 0.064087 | -62.5076 | 60.1227 | 60.0677 | -62.1414 | -62.3337 | -0.004577 | 0.041199 | 0 | 0.054932 | -0.14191 | -0.18311 | 0.059509 | 0.045777 | -0.14648 | -0.036621 | 62.2467 | -0.32043 | -0.17395 | -0.091553 | 122.3465 | 122.406 | 62.1643 | -122.3053 | 122.3099 | 122.2549 | 62.2513 | -122.493
664.9375 | 122.612 | -62.1689 | 60.1959 | 0.0074006 | -0.051699 | 0.12636 | 0.033887 | 0.035641 | -0.03851 | -0.024387 | 7.627e-05 | -0.013195 | 0.026517 | 0.05962 | -0.021969 | -0.024951 | 60.3149 | -61.9812 | 0.10529 | -62.2421 | 60.0815 | -62.1597 | -62.114 | 0.12817 | 0.18768 | -62.3611 | 60.0677 | 60.054 | -62.114 | -62.2971 | 0.009155 | 0.054931 | -0.11444 | 0.18768 | -0.073242 | -0.12817 | 0.11902 | 0.054931 | -0.12817 | -0.12817 | 62.2971 | -0.19226 | -0.064087 | -0.14191 | 122.2504 | 122.4838 | 62.2742 | -122.3099 | 122.2366 | 122.2229 | 62.3566 | -122.493
666.7188 | 122.58 | -62.1689 | 60.2325 | -0.00022891 | -0.053408 | 0.12764 | 0.031751 | 0.034573 | -0.039578 | -0.025882 | 0.0077058 | -0.01405 | 0.026731 | 0.059193 | -0.02026 | -0.022174 | 60.3104 | -61.9629 | 0.10071 | -62.2513 | 60.0906 | -62.1414 | -62.1094 | 0.12817 | 0.15564 | -62.3749 | 60.0815 | 60.0769 | -62.1048 | -62.2742 | 0.027466 | 0.059509 | -0.14191 | 0.20599 | -0.082398 | -0.14191 | 0.07782 | 0.064087 | -0.10529 | -0.15106 | 62.2971 | -0.20599 | -0.10071 | -0.15564 | 122.2595 | 122.4792 | 62.2696 | -122.3419 | 122.2504 | 122.2458 | 62.3245 | -122.5067
668.5625 | 122.5342 | -62.1918 | 60.2463 | -0.00022891 | -0.05768 | 0.12893 | 0.031751 | 0.035855 | -0.040646 | -0.02631 | -0.0075532 | -0.016186 | 0.025449 | 0.060688 | -0.022183 | -0.023242 | 60.3058 | -61.972 | 0.09613 | -62.2604 | 60.1181 | -62.1506 | -62.0956 | 0.11902 | 0.15564 | -62.3703 | 60.0815 | 60.0815 | -62.1048 | -62.2696 | 0.041198 | 0.09613 | -0.12817 | 0.21973 | -0.068665 | -0.1648 | 0.059509 | 0.086975 | -0.07782 | -0.16479 | 62.3108 | -0.17853 | -0.10071 | -0.16479 | 122.3099 | 122.4976 | 62.2879 | -122.3419 | 122.2733 | 122.2733 | 62.3474 | -122.5159
671.3906 | 122.5204 | -62.178 | 60.228 | -0.00022891 | -0.058535 | 0.12999 | 0.028974 | 0.036495 | -0.03851 | -0.026737 | 0.0077058 | -0.013195 | 0.025876 | 0.058125 | -0.020046 | -0.023669 | 60.3333 | -61.9675 | 0.10529 | -62.2467 | 60.1318 | -62.1552 | -62.114 | 0.13275 | 0.14648 | -62.3795 | 60.0769 | 60.0586 | -62.1002 | -62.2925 | 0.022889 | 0.064087 | -0.09613 | 0.21057 | -0.068664 | -0.13275 | 0.10529 | 0.07782 | -0.11444 | -0.15106 | 62.3108 | -0.20142 | -0.086976 | -0.16937 | 122.3099 | 122.5113 | 62.2833 | -122.3419 | 122.2549 | 122.2366 | 62.3245 | -122.5204
673.75 | 122.6578 | -62.1552 | 60.1776 | -0.0078584 | -0.05469 | 0.12679 | 0.032605 | 0.035641 | -0.036374 | -0.026523 | -0.0075532 | -0.012341 | 0.027799 | 0.058552 | -0.020474 | -0.023669 | 60.2829 | -62.059 | 0.041199 | -62.2833 | 60.1501 | -62.1643 | -62.146 | 0.11902 | 0.16937 | -62.4161 | 60.0723 | 60.054 | -62.1048 | -62.3062 | -0.009156 | 0.009155 | -0.027466 | 0.09613 | -0.12817 | -0.13733 | 0.10529 | 0.050354 | -0.15106 | -0.10529 | 62.2742 | -0.26093 | -0.10986 | -0.1236 | 122.3053 | 122.438 | 62.1963 | -122.3236 | 122.2275 | 122.2092 | 62.3245 | -122.4838
675.6719 | 122.6669 | -62.1735 | 60.173 | -0.00022891 | -0.052981 | 0.12572 | 0.031964 | 0.033505 | -0.034878 | -0.024601 | 7.627e-05 | -0.01405 | 0.026517 | 0.059406 | -0.021114 | -0.024097 | 60.2554 | -62.0865 | 0.032043 | -62.2971 | 60.1227 | -62.1872 | -62.1277 | 0.12817 | 0.13733 | -62.4298 | 60.0998 | 60.0632 | -62.1231 | -62.3108 | -0.013733 | 0.045776 | -0.050354 | 0.086975 | -0.1236 | -0.16937 | 0.082397 | 0.050354 | -0.13733 | -0.073243 | 62.3016 | -0.25635 | -0.11902 | -0.10986 | 122.2961 | 122.4289 | 62.2055 | -122.3007 | 122.2733 | 122.2366 | 62.3108 | -122.4838
677.3906 | 122.5708 | -62.2147 | 60.1959 | 0.0074006 | -0.055544 | 0.12743 | 0.036878 | 0.033718 | -0.041073 | -0.027591 | 0.015335 | -0.016827 | 0.02844 | 0.057697 | -0.02261 | -0.022601 | 60.3195 | -61.9537 | 0.14191 | -62.2375 | 60.1273 | -62.146 | -62.0773 | 0.10071 | 0.14648 | -62.3337 | 60.0677 | 60.0677 | -62.0911 | -62.2604 | 0.068665 | 0.13733 | -0.068665 | 0.26093 | -0.022888 | -0.16022 | 0.1236 | 0.1236 | -0.045776 | -0.12817 | 62.3154 | -0.11902 | -0.073242 | -0.12817 | 122.3419 | 122.5342 | 62.3566 | -122.2733 | 122.2824 | 122.2824 | 62.3611 | -122.4564
679.2812 | 122.5433 | -62.1964 | 60.2417 | 0.0074006 | -0.058962 | 0.12636 | 0.032819 | 0.035 | -0.039151 | -0.02631 | -0.0075532 | -0.016613 | 0.025663 | 0.057057 | -0.023892 | -0.023883 | 60.2875 | -62.0132 | 0.068665 | -62.2513 | 60.1456 | -62.1552 | -62.0911 | 0.054932 | 0.082397 | -62.3978 | 60.0998 | 60.0769 | -62.0911 | -62.2833 | 0.041199 | 0.10529 | -0.09613 | 0.18311 | -0.054932 | -0.16022 | 0.045777 | 0.10529 | -0.086975 | -0.14191 | 62.2513 | -0.20142 | -0.11444 | -0.16479 | 122.3419 | 122.4838 | 62.265 | -122.3328 | 122.2961 | 122.2733 | 62.2787 | -122.525
681.0469 | 122.5479 | -62.2055 | 60.1868 | -0.00022891 | -0.054903 | 0.12893 | 0.034955 | 0.035855 | -0.037442 | -0.027591 | -0.0075532 | -0.015118 | 0.027158 | 0.059193 | -0.023251 | -0.026019 | 60.3653 | -61.9217 | 0.14191 | -62.2238 | 60.1135 | -62.1368 | -62.1048 | 0.10986 | 0.15106 | -62.352 | 60.0952 | 60.054 | -62.0911 | -62.2879 | 0.068664 | 0.10071 | -0.073243 | 0.28381 | -0.018311 | -0.11902 | 0.17853 | 0.11444 | -0.082398 | -0.091553 | 62.3154 | -0.14648 | -0.064087 | -0.13275 | 122.319 | 122.5708 | 62.3474 | -122.2916 | 122.3007 | 122.2595 | 62.3566 | -122.4747
682.8438 | 122.644 | -62.1918 | 60.1273 | 0.0074006 | -0.054476 | 0.12828 | 0.032605 | 0.033718 | -0.033169 | -0.025455 | 7.627e-05 | -0.0097776 | 0.027585 | 0.060902 | -0.019833 | -0.02666 | 60.2371 | -62.1414 | -0.013733 | -62.3291 | 60.1639 | -62.1826 | -62.1689 | 0.059509 | 0.041199 | -62.5214 | 60.1089 | 60.0861 | -62.1597 | -62.3566 | 0.009155 | 0.022888 | 0.036621 | 0.050354 | -0.13733 | -0.16022 | 0.10986 | 0.032043 | -0.16479 | -0.01831 | 62.2513 | -0.32959 | -0.1648 | -0.041198 | 122.3557 | 122.4289 | 62.178 | -122.2961 | 122.3007 | 122.2778 | 62.233 | -122.4838
684.7188 | 122.5113 | -62.2284 | 60.2142 | -0.0078584 | -0.054476 | 0.12636 | 0.035382 | 0.033932 | -0.04086 | -0.026096 | 0.0077058 | -0.014477 | 0.029081 | 0.056843 | -0.023892 | -0.023456 | 60.2646 | -62.0087 | 0.10529 | -62.2742 | 60.141 | -62.1964 | -62.1323 | 0.032043 | 0.027466 | -62.4619 | 60.1273 | 60.0632 | -62.1643 | -62.3337 | 0.032044 | 0.096131 | -0.073242 | 0.21973 | -0.045776 | -0.14191 | 0.050354 | 0.064087 | -0.10528 | -0.086975 | 62.2604 | -0.23346 | -0.12817 | -0.15106 | 122.3694 | 122.493 | 62.3337 | -122.3465 | 122.3557 | 122.2916 | 62.2559 | -122.5479
687.2969 | 122.5754 | -62.1872 | 60.2097 | 0.0074006 | -0.05704 | 0.12914 | 0.035809 | 0.037136 | -0.040646 | -0.027378 | 7.627e-05 | -0.012982 | 0.02609 | 0.060261 | -0.026455 | -0.027728 | 60.3516 | -61.9171 | 0.13275 | -62.2284 | 60.1273 | -62.1414 | -62.0956 | 0.14648 | 0.17395 | -62.3199 | 60.0723 | 60.0769 | -62.0956 | -62.2879 | 0.045777 | 0.091553 | -0.082398 | 0.27008 | -0.041199 | -0.13275 | 0.14191 | 0.091553 | -0.10071 | -0.13733 | 62.3337 | -0.13275 | -0.032043 | -0.13275 | 122.3145 | 122.5388 | 62.3199 | -122.3053 | 122.2595 | 122.2641 | 62.3611 | -122.4976
689.0781 | 122.525 | -62.1918 | 60.2371 | -0.00022891 | -0.057467 | 0.13063 | 0.030896 | 0.033505 | -0.03851 | -0.028446 | 7.627e-05 | -0.013195 | 0.026304 | 0.058979 | -0.021328 | -0.025592 | 60.3012 | -61.9904 | 0.073242 | -62.265 | 60.1456 | -62.1552 | -62.0773 | 0.10071 | 0.10986 | -62.3978 | 60.0906 | 60.0998 | -62.0773 | -62.2833 | 0.036621 | 0.11444 | -0.091553 | 0.20142 | -0.073243 | -0.18768 | 0.064086 | 0.11444 | -0.091553 | -0.14648 | 62.2925 | -0.20599 | -0.11444 | -0.13733 | 122.3373 | 122.493 | 62.265 | -122.3145 | 122.2824 | 122.2916 | 62.3016 | -122.5204
690.9688 | 122.5525 | -62.178 | 60.2371 | -0.00022891 | -0.057253 | 0.12978 | 0.032392 | 0.036923 | -0.038937 | -0.026737 | 0.0077058 | -0.01405 | 0.024167 | 0.058552 | -0.020474 | -0.023883 | 60.3012 | -62.0178 | 0.073242 | -62.2513 | 60.1364 | -62.1735 | -62.0728 | 0.073242 | 0.07782 | -62.3795 | 60.1044 | 60.0906 | -62.1048 | -62.2696 | 0.004578 | 0.10529 | -0.10071 | 0.16022 | -0.073242 | -0.17853 | 0.064086 | 0.073243 | -0.091552 | -0.13275 | 62.2513 | -0.20142 | -0.10986 | -0.14648 | 122.3145 | 122.4792 | 62.2513 | -122.3099 | 122.2824 | 122.2687 | 62.2559 | -122.5067
692.8125 | 122.5525 | -62.2055 | 60.1959 | -0.0078584 | -0.05234 | 0.12893 | 0.034741 | 0.033932 | -0.037655 | -0.024814 | -0.0075532 | -0.011486 | 0.02844 | 0.059406 | -0.021114 | -0.027301 | 60.2234 | -62.0682 | 0.045776 | -62.3154 | 60.1639 | -62.2147 | -62.1735 | 0 | 0.018311 | -62.5076 | 60.1318 | 60.0769 | -62.1826 | -62.3291 | -0.009156 | 0.032043 | -0.032044 | 0.13733 | -0.10986 | -0.14191 | 0.027466 | 0.022888 | -0.1236 | -0.064087 | 62.2055 | -0.30212 | -0.17853 | -0.11902 | 122.3694 | 122.4289 | 62.2513 | -122.3694 | 122.3373 | 122.2824 | 62.2238 | -122.525
694.5312 | 122.5388 | -62.2192 | 60.2005 | -0.00022891 | -0.051913 | 0.12722 | 0.035169 | 0.035855 | -0.038296 | -0.025882 | 7.627e-05 | -0.012768 | 0.026731 | 0.060261 | -0.024532 | -0.027301 | 60.2234 | -62.0773 | 0.032043 | -62.3245 | 60.1501 | -62.2147 | -62.1643 | -0.004578 | 0.009155 | -62.4802 | 60.1273 | 60.1044 | -62.1506 | -62.3154 | 0.004577 | 0.054931 | -0.050354 | 0.14191 | -0.10529 | -0.16022 | 0.022889 | 0.068664 | -0.096131 | -0.073242 | 62.2147 | -0.26093 | -0.1648 | -0.09613 | 122.3694 | 122.4426 | 62.2513 | -122.3648 | 122.3465 | 122.3236 | 62.2284 | -122.5159
696.25 | 122.5433 | -62.2009 | 60.1822 | 0.0074006 | -0.053194 | 0.12679 | 0.034955 | 0.032223 | -0.036374 | -0.02631 | 7.627e-05 | -0.013409 | 0.030576 | 0.060474 | -0.02261 | -0.026019 | 60.2097 | -62.0773 | 0.050354 | -62.3245 | 60.1685 | -62.1964 | -62.146 | 0.013733 | 0.022888 | -62.4939 | 60.1364 | 60.0861 | -62.146 | -62.3383 | 0.004578 | 0.054932 | -0.013733 | 0.1236 | -0.1236 | -0.17853 | 0.027466 | 0.054932 | -0.13733 | -0.045776 | 62.2147 | -0.29297 | -0.15564 | -0.09613 | 122.3694 | 122.4106 | 62.2513 | -122.3282 | 122.3373 | 122.287 | 62.2238 | -122.5204
697.9844 | 122.6532 | -62.1918 | 60.1273 | -0.015487 | -0.053622 | 0.12508 | 0.030469 | 0.035214 | -0.034237 | -0.025028 | 0.0077058 | -0.011273 | 0.026944 | 0.061115 | -0.019406 | -0.027515 | 60.2325 | -62.0773 | 0.064087 | -62.2971 | 60.1364 | -62.2284 | -62.1689 | 0.054932 | 0.09613 | -62.4893 | 60.0632 | 60.054 | -62.1643 | -62.352 | -0.036622 | 0.022888 | 0.009156 | 0.11444 | -0.10529 | -0.12817 | 0.10529 | 0.027465 | -0.16022 | -0.064087 | 62.2467 | -0.29755 | -0.13733 | -0.073242 | 122.3282 | 122.4243 | 62.2559 | -122.2961 | 122.2549 | 122.2458 | 62.2879 | -122.4792
699.8438 | 122.6166 | -62.1918 | 60.173 | 0.0074006 | -0.053408 | 0.12593 | 0.030469 | 0.035214 | -0.034665 | -0.023105 | 0.0077058 | -0.012555 | 0.027158 | 0.060902 | -0.019406 | -0.023883 | 60.173 | -62.1552 | -0.018311 | -62.3566 | 60.1273 | -62.233 | -62.1506 | 0.032043 | 0.054932 | -62.5397 | 60.0952 | 60.0906 | -62.178 | -62.3657 | -0.041199 | 0.041198 | -0.045777 | 0.036621 | -0.16479 | -0.20599 | 0 | 0.013732 | -0.17395 | -0.07782 | 62.2238 | -0.3479 | -0.17395 | -0.082398 | 122.319 | 122.3648 | 62.1735 | -122.3236 | 122.287 | 122.2824 | 62.2467 | -122.5388
701.6406 | 122.6349 | -62.1643 | 60.1501 | 0.0074006 | -0.051699 | 0.12529 | 0.031964 | 0.035214 | -0.035519 | -0.025028 | -0.0075532 | -0.013409 | 0.027372 | 0.05727 | -0.017483 | -0.024097 | 60.2234 | -62.0544 | 0.073242 | -62.3016 | 60.1456 | -62.2147 | -62.1643 | 0.091553 | 0.11902 | -62.471 | 60.0952 | 60.0449 | -62.1643 | -62.3657 | -0.050354 | 0 | -0.004577 | 0.10986 | -0.13733 | -0.13733 | 0.073243 | 0 | -0.20142 | -0.054931 | 62.2559 | -0.3067 | -0.10528 | -0.10529 | 122.3099 | 122.3877 | 62.2375 | -122.3145 | 122.2595 | 122.2092 | 62.2833 | -122.5159
703.375 | 122.5891 | -62.1735 | 60.2051 | -0.00022891 | -0.05768 | 0.12935 | 0.035169 | 0.032864 | -0.043423 | -0.025242 | 0.0077058 | -0.015332 | 0.02844 | 0.058766 | -0.025601 | -0.023242 | 60.3012 | -61.9308 | 0.12817 | -62.2147 | 60.1318 | -62.1414 | -62.1048 | 0.1236 | 0.16479 | -62.3154 | 60.0632 | 60.0677 | -62.1002 | -62.2833 | 0.032044 | 0.068665 | -0.073242 | 0.24262 | -0.041199 | -0.10986 | 0.09613 | 0.073242 | -0.10986 | -0.14191 | 62.2971 | -0.14191 | -0.032044 | -0.13733 | 122.3053 | 122.4747 | 62.3016 | -122.3099 | 122.2366 | 122.2412 | 62.3383 | -122.4884
705.1562 | 122.5159 | -62.1826 | 60.2188 | -0.00022891 | -0.053622 | 0.12722 | 0.036023 | 0.034359 | -0.040219 | -0.026737 | 7.627e-05 | -0.012982 | 0.028867 | 0.058766 | -0.025173 | -0.025165 | 60.2829 | -61.9583 | 0.15106 | -62.2284 | 60.1135 | -62.146 | -62.0911 | 0.059509 | 0.11902 | -62.3886 | 60.0906 | 60.0494 | -62.114 | -62.2925 | 0.036621 | 0.091553 | -0.10529 | 0.2243 | -0.045777 | -0.13733 | 0.064087 | 0.068664 | -0.10986 | -0.12817 | 62.2421 | -0.20599 | -0.096131 | -0.16937 | 122.2961 | 122.4655 | 62.3337 | -122.3099 | 122.2733 | 122.2321 | 62.3016 | -122.5113
706.9375 | 122.5342 | -62.2192 | 60.1868 | -0.00022891 | -0.051272 | 0.12764 | 0.035169 | 0.034786 | -0.038723 | -0.028873 | 7.627e-05 | -0.012982 | 0.027799 | 0.06197 | -0.023037 | -0.026019 | 60.2097 | -62.0682 | 0.054932 | -62.3337 | 60.1593 | -62.2055 | -62.1506 | -0.004578 | 0.004578 | -62.471 | 60.0952 | 60.0998 | -62.1597 | -62.3566 | 0.013733 | 0.068664 | -0.027466 | 0.15106 | -0.11444 | -0.1831 | 0.022888 | 0.059509 | -0.13733 | -0.091553 | 62.2147 | -0.25177 | -0.11444 | -0.086976 | 122.3785 | 122.4289 | 62.2742 | -122.3373 | 122.3145 | 122.319 | 62.2238 | -122.5433
708.6562 | 122.525 | -62.1689 | 60.2463 | -0.00022891 | -0.053622 | 0.12871 | 0.032178 | 0.033932 | -0.039792 | -0.025882 | 0.0077058 | -0.014904 | 0.025876 | 0.057911 | -0.021542 | -0.024951 | 60.3012 | -61.9583 | 0.07782 | -62.2559 | 60.0998 | -62.1323 | -62.0911 | 0.10986 | 0.13733 | -62.3703 | 60.0998 | 60.0357 | -62.1002 | -62.2696 | 0.036621 | 0.07782 | -0.14648 | 0.21057 | -0.086975 | -0.16479 | 0.054931 | 0.068664 | -0.10071 | -0.14648 | 62.2787 | -0.20142 | -0.10071 | -0.21057 | 122.2687 | 122.4701 | 62.2467 | -122.3373 | 122.2687 | 122.2046 | 62.3062 | -122.5159
710.4531 | 122.5342 | -62.178 | 60.2142 | -0.00022891 | -0.054903 | 0.12935 | 0.034741 | 0.035855 | -0.040646 | -0.027378 | -0.0075532 | -0.016186 | 0.02609 | 0.058979 | -0.020474 | -0.024951 | 60.3149 | -61.908 | 0.14648 | -62.2147 | 60.141 | -62.1506 | -62.0911 | 0.086975 | 0.15564 | -62.3245 | 60.0769 | 60.0449 | -62.0956 | -62.2742 | 0.027466 | 0.086976 | -0.073242 | 0.27008 | -0.036621 | -0.1236 | 0.10071 | 0.082398 | -0.09613 | -0.13733 | 62.265 | -0.14648 | -0.050354 | -0.16937 | 122.319 | 122.493 | 62.3245 | -122.3053 | 122.2549 | 122.2229 | 62.3337 | -122.4884
712.2188 | 122.5983 | -62.2009 | 60.1776 | -0.00022891 | -0.05234 | 0.127 | 0.033032 | 0.03265 | -0.035733 | -0.026951 | 7.627e-05 | -0.012555 | 0.027799 | 0.058979 | -0.021755 | -0.025592 | 60.2005 | -62.1002 | 0.027466 | -62.3108 | 60.1593 | -62.2055 | -62.1643 | 0.004578 | 0.027466 | -62.4939 | 60.1227 | 60.0815 | -62.1689 | -62.3428 | -0.004577 | 0.036621 | -0.01831 | 0.10071 | -0.10986 | -0.14648 | 0.022888 | 0.032044 | -0.14191 | -0.054931 | 62.2055 | -0.29297 | -0.15106 | -0.09613 | 122.3602 | 122.4014 | 62.2284 | -122.3419 | 122.3236 | 122.2824 | 62.2284 | -122.5204
714 | 122.6074 | -62.1918 | 60.1776 | 0.0074006 | -0.054903 | 0.12615 | 0.031751 | 0.036068 | -0.033596 | -0.023533 | 7.627e-05 | -0.010205 | 0.026304 | 0.061756 | -0.018124 | -0.025378 | 60.2371 | -62.114 | 0.009155 | -62.3383 | 60.1364 | -62.2101 | -62.178 | 0.041199 | 0.059509 | -62.5076 | 60.1181 | 60.0586 | -62.146 | -62.3657 | -0.018311 | 0.013732 | -0.041198 | 0.077819 | -0.14648 | -0.16022 | 0.05951 | 0.045776 | -0.17395 | -0.059509 | 62.233 | -0.31586 | -0.14191 | -0.11902 | 122.3282 | 122.4289 | 62.2009 | -122.3557 | 122.3099 | 122.2504 | 62.2513 | -122.5433
715.7969 | 122.5937 | -62.1597 | 60.2142 | -0.0078584 | -0.056826 | 0.12978 | 0.029401 | 0.035427 | -0.037869 | -0.02396 | 0.0077058 | -0.014477 | 0.025022 | 0.060688 | -0.020687 | -0.023669 | 60.3058 | -61.9629 | 0.10529 | -62.233 | 60.1044 | -62.1414 | -62.0773 | 0.13733 | 0.1831 | -62.3611 | 60.0677 | 60.054 | -62.0819 | -62.2925 | 0.018311 | 0.082397 | -0.10986 | 0.19684 | -0.073242 | -0.15564 | 0.091553 | 0.07782 | -0.13275 | -0.14648 | 62.2971 | -0.20142 | -0.068665 | -0.16022 | 122.2641 | 122.4655 | 62.265 | -122.2916 | 122.2275 | 122.2137 | 62.3428 | -122.5067
717.5781 | 122.6349 | -62.1689 | 60.1776 | -0.00022891 | -0.052126 | 0.12658 | 0.036023 | 0.037777 | -0.035305 | -0.025242 | 7.627e-05 | -0.011273 | 0.029294 | 0.060474 | -0.021542 | -0.024524 | 60.1685 | -62.1506 | -0.032043 | -62.3428 | 60.1501 | -62.2101 | -62.1735 | 0.041199 | 0.041199 | -62.5259 | 60.1044 | 60.0998 | -62.1597 | -62.3566 | -0.041199 | -0.004578 | -0.027466 | 0.01831 | -0.17395 | -0.16937 | -0.009155 | 0.009155 | -0.18768 | -0.073242 | 62.2101 | -0.35706 | -0.16937 | -0.07782 | 122.319 | 122.3373 | 62.1368 | -122.3511 | 122.2733 | 122.2687 | 62.2101 | -122.5342
719.2812 | 122.5571 | -62.178 | 60.2097 | 0.0074006 | -0.056826 | 0.127 | 0.037091 | 0.034146 | -0.041073 | -0.026523 | 7.627e-05 | -0.017254 | 0.027799 | 0.058979 | -0.026241 | -0.022174 | 60.2737 | -61.972 | 0.086975 | -62.2284 | 60.1685 | -62.1277 | -62.0728 | 0.09613 | 0.1236 | -62.3291 | 60.0952 | 60.0815 | -62.0865 | -62.265 | 0.050354 | 0.10529 | -0.041199 | 0.20599 | -0.050354 | -0.15564 | 0.064087 | 0.091553 | -0.086975 | -0.11444 | 62.2742 | -0.15106 | -0.064087 | -0.12817 | 122.3465 | 122.4518 | 62.265 | -122.2824 | 122.2733 | 122.2595 | 62.3016 | -122.4747
721.0781 | 122.612 | -62.1735 | 60.141 | -0.00022891 | -0.049349 | 0.12786 | 0.032392 | 0.035214 | -0.032101 | -0.025242 | -0.0075532 | -0.0097776 | 0.027372 | 0.060902 | -0.021114 | -0.026874 | 60.2097 | -62.114 | 0.009155 | -62.3245 | 60.1364 | -62.2238 | -62.1689 | 0.036621 | 0.041199 | -62.5259 | 60.0952 | 60.054 | -62.1414 | -62.3337 | -0.050354 | 0.004578 | -0.004577 | 0.059509 | -0.15106 | -0.15564 | 0.068665 | 0.032044 | -0.16022 | -0.045776 | 62.2101 | -0.35248 | -0.19226 | -0.086975 | 122.3099 | 122.3831 | 62.1826 | -122.3099 | 122.2687 | 122.2275 | 62.2147 | -122.4747
722.875 | 122.5388 | -62.1826 | 60.228 | 0.0074006 | -0.055117 | 0.12935 | 0.033887 | 0.034359 | -0.041501 | -0.027805 | 7.627e-05 | -0.017468 | 0.026304 | 0.059193 | -0.023678 | -0.023242 | 60.2554 | -61.9904 | 0.068665 | -62.2375 | 60.1685 | -62.1185 | -62.0865 | 0.050354 | 0.091553 | -62.3566 | 60.1044 | 60.0906 | -62.0773 | -62.2559 | 0.064087 | 0.09613 | -0.059509 | 0.19226 | -0.054932 | -0.15106 | 0.027466 | 0.10529 | -0.073242 | -0.1236 | 62.233 | -0.17395 | -0.10071 | -0.13733 | 122.3511 | 122.438 | 62.2513 | -122.3145 | 122.287 | 122.2733 | 62.2742 | -122.4838
724.5938 | 122.6486 | -62.1643 | 60.1959 | -0.00022891 | -0.05704 | 0.12615 | 0.028974 | 0.034146 | -0.037869 | -0.026951 | 7.627e-05 | -0.015973 | 0.026304 | 0.05962 | -0.018337 | -0.027087 | 60.2829 | -61.9949 | 0.059509 | -62.2375 | 60.1364 | -62.1643 | -62.1048 | 0.13275 | 0.16479 | -62.3703 | 60.0815 | 60.0403 | -62.0819 | -62.2742 | 0 | 0.05951 | -0.059509 | 0.16937 | -0.073242 | -0.13275 | 0.086975 | 0.082398 | -0.10986 | -0.11444 | 62.2971 | -0.20599 | -0.09613 | -0.15564 | 122.3007 | 122.4472 | 62.2238 | -122.3007 | 122.2458 | 122.2046 | 62.3291 | -122.4701
726.3125 | 122.5388 | -62.1872 | 60.2417 | 0.0074006 | -0.056826 | 0.127 | 0.035809 | 0.036495 | -0.038937 | -0.029087 | 7.627e-05 | -0.015118 | 0.027372 | 0.060474 | -0.023678 | -0.025378 | 60.2737 | -62.0087 | 0.064087 | -62.2559 | 60.1501 | -62.1277 | -62.0682 | 0.068665 | 0.10529 | -62.3749 | 60.1181 | 60.0998 | -62.0911 | -62.2742 | 0.059509 | 0.11902 | -0.091553 | 0.17853 | -0.068664 | -0.18768 | 0.032044 | 0.096131 | -0.086975 | -0.1236 | 62.2559 | -0.18768 | -0.10071 | -0.14191 | 122.3373 | 122.4609 | 62.2513 | -122.3099 | 122.3053 | 122.287 | 62.2925 | -122.5159
728.0156 | 122.6532 | -62.1643 | 60.1501 | -0.00022891 | -0.051272 | 0.127 | 0.031964 | 0.032437 | -0.033596 | -0.02631 | 7.627e-05 | -0.0099912 | 0.026944 | 0.061115 | -0.018124 | -0.02666 | 60.26 | -62.0544 | 0.07782 | -62.3016 | 60.1273 | -62.2055 | -62.146 | 0.073242 | 0.07782 | -62.4802 | 60.1044 | 60.0403 | -62.1597 | -62.352 | -0.041198 | 0.018311 | -0.022888 | 0.10986 | -0.13733 | -0.15564 | 0.10986 | 0.004578 | -0.18768 | -0.045776 | 62.2375 | -0.31586 | -0.12817 | -0.10986 | 122.2916 | 122.4243 | 62.2421 | -122.2961 | 122.2687 | 122.2046 | 62.2421 | -122.5021
729.8125 | 122.6532 | -62.1506 | 60.1639 | -0.00022891 | -0.053194 | 0.12679 | 0.034101 | 0.036068 | -0.036374 | -0.024814 | 0.0077058 | -0.0117 | 0.02844 | 0.061756 | -0.021542 | -0.025592 | 60.2417 | -62.0819 | 0.045776 | -62.3108 | 60.1501 | -62.2101 | -62.1597 | 0.045776 | 0.086975 | -62.4527 | 60.1273 | 60.0998 | -62.1552 | -62.352 | -0.059509 | -0.009155 | -0.013733 | 0.068665 | -0.16022 | -0.15106 | 0.07782 | -0.004577 | -0.20142 | -0.036621 | 62.1963 | -0.30212 | -0.10071 | -0.064087 | 122.3007 | 122.3923 | 62.1963 | -122.3236 | 122.2778 | 122.2504 | 62.2375 | -122.5159
731.6094 | 122.6166 | -62.1643 | 60.1685 | -0.00022891 | -0.05469 | 0.127 | 0.034528 | 0.033932 | -0.038937 | -0.026096 | 7.627e-05 | -0.014691 | 0.028867 | 0.05962 | -0.022183 | -0.025592 | 60.2097 | -62.0865 | 0.032043 | -62.3108 | 60.1364 | -62.2192 | -62.1277 | 0 | 0.027466 | -62.4985 | 60.1273 | 60.0952 | -62.1552 | -62.3062 | -0.054931 | 0.036621 | -0.032043 | 0.07782 | -0.14648 | -0.18311 | 0.041199 | 0.009156 | -0.14191 | -0.041199 | 62.1643 | -0.33417 | -0.19226 | -0.073242 | 122.3007 | 122.374 | 62.1964 | -122.2961 | 122.2916 | 122.2595 | 62.1918 | -122.4747
733.4062 | 122.5159 | -62.146 | 60.2371 | -0.00022891 | -0.056185 | 0.12893 | 0.036237 | 0.037136 | -0.041501 | -0.025028 | 7.627e-05 | -0.0164 | 0.02844 | 0.060902 | -0.026028 | -0.02431 | 60.2875 | -61.9995 | 0.064087 | -62.2513 | 60.1685 | -62.1414 | -62.0728 | 0.07782 | 0.10986 | -62.3703 | 60.1044 | 60.0906 | -62.0728 | -62.2375 | 0.004578 | 0.073242 | -0.068665 | 0.14648 | -0.10529 | -0.17853 | 0.050354 | 0.073242 | -0.091553 | -0.13275 | 62.2238 | -0.2243 | -0.13275 | -0.14648 | 122.3145 | 122.4335 | 62.2101 | -122.3099 | 122.2504 | 122.2366 | 62.2559 | -122.4747
735.1875 | 122.5021 | -62.1918 | 60.2234 | -0.00022891 | -0.053835 | 0.12871 | 0.035382 | 0.035641 | -0.040219 | -0.026951 | 0.0077058 | -0.015118 | 0.028013 | 0.05727 | -0.022823 | -0.026447 | 60.3195 | -61.9446 | 0.13733 | -62.2147 | 60.1364 | -62.146 | -62.0819 | 0.054932 | 0.10071 | -62.384 | 60.1181 | 60.0861 | -62.1414 | -62.265 | 0.045776 | 0.10986 | -0.086975 | 0.24719 | -0.022889 | -0.13275 | 0.09613 | 0.050354 | -0.073243 | -0.10529 | 62.2467 | -0.19226 | -0.11902 | -0.13733 | 122.3282 | 122.5113 | 62.3291 | -122.3053 | 122.3099 | 122.2778 | 62.2925 | -122.4884
736.9688 | 122.5479 | -62.1597 | 60.2554 | 0.0074006 | -0.055331 | 0.12658 | 0.033032 | 0.036923 | -0.03851 | -0.027378 | 0.015335 | -0.0164 | 0.027158 | 0.060474 | -0.021328 | -0.02666 | 60.3333 | -61.94 | 0.10529 | -62.233 | 60.1135 | -62.1231 | -62.059 | 0.13275 | 0.16937 | -62.352 | 60.1044 | 60.0861 | -62.0911 | -62.2513 | 0.036621 | 0.10071 | -0.14191 | 0.21973 | -0.073242 | -0.17395 | 0.07782 | 0.068665 | -0.091553 | -0.15106 | 62.2925 | -0.19226 | -0.10071 | -0.16937 | 122.2733 | 122.493 | 62.265 | -122.3145 | 122.2641 | 122.2458 | 62.3291 | -122.5067
738.7031 | 122.6532 | -62.1277 | 60.1776 | -0.00022891 | -0.054049 | 0.12572 | 0.032178 | 0.032437 | -0.035733 | -0.023746 | -0.0075532 | -0.013623 | 0.027158 | 0.060261 | -0.020901 | -0.026019 | 60.3012 | -62.0087 | 0.073242 | -62.233 | 60.1501 | -62.1597 | -62.1094 | 0.14191 | 0.17395 | -62.3657 | 60.1135 | 60.0632 | -62.0956 | -62.265 | -0.032043 | 0.018311 | -0.027466 | 0.11902 | -0.10529 | -0.1236 | 0.1236 | 0.032044 | -0.13733 | -0.064087 | 62.2696 | -0.23804 | -0.10071 | -0.11444 | 122.2778 | 122.4289 | 62.2009 | -122.287 | 122.2412 | 122.1909 | 62.3016 | -122.4426
740.5 | 122.644 | -62.178 | 60.1501 | 0.0074006 | -0.05234 | 0.12722 | 0.034741 | 0.035855 | -0.035733 | -0.025028 | -0.0075532 | -0.010846 | 0.025663 | 0.062611 | -0.021755 | -0.02666 | 60.2737 | -62.0453 | 0.068665 | -62.2787 | 60.1593 | -62.2009 | -62.1277 | 0.059509 | 0.086975 | -62.4664 | 60.0952 | 60.0723 | -62.1368 | -62.352 | -0.022888 | 0.050354 | 0.009156 | 0.13275 | -0.10071 | -0.15106 | 0.1236 | 0.041199 | -0.17395 | -0.054931 | 62.2375 | -0.28839 | -0.11444 | -0.077819 | 122.3373 | 122.4518 | 62.2467 | -122.2778 | 122.2733 | 122.2504 | 62.265 | -122.5021
742.2969 | 122.6532 | -62.1552 | 60.1685 | -0.00022891 | -0.052767 | 0.12786 | 0.033246 | 0.033718 | -0.038296 | -0.026523 | 7.627e-05 | -0.012341 | 0.02609 | 0.059406 | -0.020046 | -0.024524 | 60.2188 | -62.0819 | 0.036621 | -62.2971 | 60.1547 | -62.2009 | -62.1552 | 0.004578 | 0.041199 | -62.471 | 60.1089 | 60.0952 | -62.1277 | -62.352 | -0.045777 | 0 | -0.013733 | 0.073242 | -0.14191 | -0.14191 | 0.050354 | 0.027465 | -0.19684 | -0.059509 | 62.1597 | -0.31586 | -0.11902 | -0.073242 | 122.3099 | 122.374 | 62.1918 | -122.3236 | 122.2641 | 122.2504 | 62.1963 | -122.5204
744.0781 | 122.5204 | -62.1414 | 60.2554 | -0.00022891 | -0.058748 | 0.12935 | 0.031751 | 0.034786 | -0.041501 | -0.024814 | 0.0077058 | -0.016186 | 0.024808 | 0.057697 | -0.020474 | -0.023669 | 60.2921 | -61.972 | 0.068665 | -62.2284 | 60.1501 | -62.1185 | -62.0499 | 0.10071 | 0.11444 | -62.3428 | 60.1135 | 60.1227 | -62.0544 | -62.233 | 0.022888 | 0.091552 | -0.10529 | 0.16937 | -0.086976 | -0.17853 | 0.036621 | 0.086975 | -0.091553 | -0.14191 | 62.2421 | -0.20142 | -0.10986 | -0.13275 | 122.2916 | 122.4335 | 62.2101 | -122.3053 | 122.2549 | 122.2641 | 62.2559 | -122.4884
745.875 | 122.5204 | -62.146 | 60.2417 | -0.00022891 | -0.055331 | 0.12786 | 0.037518 | 0.035 | -0.040219 | -0.027164 | 7.627e-05 | -0.014904 | 0.027799 | 0.058979 | -0.02496 | -0.026019 | 60.2875 | -61.9812 | 0.059509 | -62.2375 | 60.1776 | -62.1094 | -62.0682 | 0.073242 | 0.10529 | -62.3657 | 60.141 | 60.1089 | -62.0728 | -62.2467 | 0.036621 | 0.07782 | -0.064087 | 0.16479 | -0.091553 | -0.16937 | 0.045777 | 0.073242 | -0.10071 | -0.10071 | 62.2192 | -0.21973 | -0.11902 | -0.13275 | 122.3236 | 122.4335 | 62.2055 | -122.3099 | 122.287 | 122.2549 | 62.2513 | -122.4884
747.6094 | 122.5388 | -62.178 | 60.2417 | 0.0074006 | -0.055117 | 0.12893 | 0.036878 | 0.035214 | -0.039364 | -0.028019 | 7.627e-05 | -0.016613 | 0.027799 | 0.058979 | -0.025173 | -0.026447 | 60.3516 | -61.9034 | 0.15564 | -62.1872 | 60.1593 | -62.1094 | -62.0819 | 0.11444 | 0.15106 | -62.3108 | 60.1089 | 60.0952 | -62.0728 | -62.233 | 0.068665 | 0.096131 | -0.082397 | 0.27466 | -0.009155 | -0.10529 | 0.10986 | 0.10529 | -0.054931 | -0.13275 | 62.2925 | -0.13275 | -0.07782 | -0.14648 | 122.3373 | 122.5296 | 62.3337 | -122.3236 | 122.287 | 122.2733 | 62.3291 | -122.4747
749.3906 | 122.5479 | -62.1597 | 60.2371 | -0.00022891 | -0.057467 | 0.12807 | 0.027905 | 0.033932 | -0.035305 | -0.027805 | 0.0077058 | -0.015545 | 0.025663 | 0.060261 | -0.022396 | -0.025378 | 60.3516 | -61.94 | 0.10986 | -62.2284 | 60.1273 | -62.114 | -62.0544 | 0.14191 | 0.15106 | -62.3383 | 60.1181 | 60.0952 | -62.0773 | -62.265 | 0.045776 | 0.10529 | -0.10986 | 0.21973 | -0.068665 | -0.17395 | 0.11444 | 0.082397 | -0.10529 | -0.11902 | 62.3016 | -0.17853 | -0.073242 | -0.14191 | 122.287 | 122.5113 | 62.2696 | -122.2916 | 122.2778 | 122.2549 | 62.3108 | -122.5021
751.0938 | 122.6624 | -62.1231 | 60.1776 | -0.00022891 | -0.055117 | 0.12914 | 0.030469 | 0.035641 | -0.034237 | -0.024387 | 7.627e-05 | -0.012555 | 0.027585 | 0.06197 | -0.018124 | -0.025806 | 60.2554 | -62.0682 | -0.004578 | -62.2971 | 60.1913 | -62.1552 | -62.1414 | 0.086975 | 0.073242 | -62.4435 | 60.1547 | 60.1044 | -62.1002 | -62.2696 | -0.032043 | -0.01831 | 0.013733 | 0.054932 | -0.17395 | -0.15564 | 0.07782 | 0.022888 | -0.14648 | -0.022888 | 62.2101 | -0.32043 | -0.17395 | -0.073242 | 122.3145 | 122.3785 | 62.1185 | -122.319 | 122.2778 | 122.2275 | 62.1964 | -122.4472
752.8906 | 122.644 | -62.1368 | 60.1593 | 0.0074006 | -0.049563 | 0.12593 | 0.033032 | 0.036068 | -0.034024 | -0.023319 | 7.627e-05 | -0.011914 | 0.026517 | 0.060902 | -0.020687 | -0.025592 | 60.2692 | -62.0499 | 0.082397 | -62.2604 | 60.141 | -62.1643 | -62.146 | 0.068665 | 0.10071 | -62.4481 | 60.1181 | 60.1044 | -62.146 | -62.3016 | -0.027466 | -0.009155 | -0.018311 | 0.086975 | -0.1236 | -0.11444 | 0.10986 | -0.009155 | -0.1648 | -0.041199 | 62.2055 | -0.31128 | -0.14648 | -0.054932 | 122.2778 | 122.406 | 62.2192 | -122.3053 | 122.2549 | 122.2412 | 62.2375 | -122.4609
754.5938 | 122.5113 | -62.146 | 60.2554 | -0.00022891 | -0.058748 | 0.12764 | 0.035596 | 0.03735 | -0.044064 | -0.027164 | 0.015335 | -0.015118 | 0.02609 | 0.058766 | -0.024319 | -0.022815 | 60.3195 | -61.9629 | 0.073242 | -62.2238 | 60.1639 | -62.1002 | -62.0453 | 0.10529 | 0.11444 | -62.352 | 60.1089 | 60.1456 | -62.0728 | -62.2238 | 0.045776 | 0.10071 | -0.091553 | 0.1831 | -0.07782 | -0.17853 | 0.064087 | 0.073242 | -0.07782 | -0.14648 | 62.2513 | -0.20599 | -0.12817 | -0.10986 | 122.3099 | 122.4655 | 62.2192 | -122.3007 | 122.2549 | 122.2916 | 62.2604 | -122.4792
756.375 | 122.6624 | -62.114 | 60.2005 | 0.0074006 | -0.053408 | 0.12935 | 0.03111 | 0.03735 | -0.03616 | -0.027378 | 7.627e-05 | -0.012768 | 0.025876 | 0.062183 | -0.019619 | -0.025806 | 60.2463 | -62.0544 | -0.004578 | -62.2787 | 60.1913 | -62.1277 | -62.1231 | 0.068665 | 0.091553 | -62.439 | 60.1181 | 60.1044 | -62.0911 | -62.2833 | -0.013733 | -0.009155 | -0.009155 | 0.05951 | -0.16479 | -0.15564 | 0.045777 | 0.022889 | -0.16937 | -0.082397 | 62.1826 | -0.32501 | -0.15564 | -0.09613 | 122.3053 | 122.3602 | 62.1094 | -122.3236 | 122.2321 | 122.2183 | 62.2055 | -122.4838
758.1406 | 122.5662 | -62.1323 | 60.2417 | 0.0074006 | -0.059603 | 0.12999 | 0.030896 | 0.036282 | -0.042355 | -0.025242 | 0.0077058 | -0.0164 | 0.025022 | 0.057697 | -0.024746 | -0.024097 | 60.3012 | -61.9308 | 0.091553 | -62.1918 | 60.1868 | -62.1002 | -62.0361 | 0.10071 | 0.12817 | -62.3062 | 60.1181 | 60.1318 | -62.0407 | -62.2513 | 0.032043 | 0.09613 | -0.054931 | 0.20142 | -0.059509 | -0.15564 | 0.059509 | 0.091553 | -0.11902 | -0.1236 | 62.233 | -0.17395 | -0.054931 | -0.10986 | 122.319 | 122.4335 | 62.2238 | -122.2778 | 122.2504 | 122.2641 | 62.2604 | -122.493
759.9219 | 122.6349 | -62.1368 | 60.2097 | -0.00022891 | -0.051485 | 0.12465 | 0.035169 | 0.036495 | -0.032956 | -0.024601 | 0.0077058 | -0.010846 | 0.029081 | 0.05962 | -0.021969 | -0.026874 | 60.3058 | -62.0316 | 0.082397 | -62.2604 | 60.1593 | -62.1643 | -62.1277 | 0.054932 | 0.07782 | -62.4344 | 60.1273 | 60.0906 | -62.1323 | -62.3291 | -0.027466 | 0.009155 | -0.050354 | 0.10529 | -0.1236 | -0.13275 | 0.09613 | 0.004578 | -0.19226 | -0.082398 | 62.1918 | -0.29755 | -0.10529 | -0.11902 | 122.2961 | 122.4426 | 62.2192 | -122.3373 | 122.2641 | 122.2275 | 62.2147 | -122.5388
761.6406 | 122.6532 | -62.1231 | 60.1593 | -0.0078584 | -0.051485 | 0.12444 | 0.034314 | 0.036495 | -0.034665 | -0.025882 | 7.627e-05 | -0.012982 | 0.029935 | 0.061115 | -0.021755 | -0.025165 | 60.2783 | -62.0361 | 0.064087 | -62.265 | 60.173 | -62.1964 | -62.1323 | 0.045776 | 0.091553 | -62.4344 | 60.1273 | 60.1273 | -62.1323 | -62.3062 | -0.073242 | -0.009155 | 0.013733 | 0.086975 | -0.14191 | -0.13275 | 0.11902 | -0.009155 | -0.1831 | -0.032044 | 62.1689 | -0.31128 | -0.12817 | -0.032044 | 122.2961 | 122.4014 | 62.1872 | -122.2916 | 122.2504 | 122.2504 | 62.2147 | -122.4655
763.4219 | 122.644 | -62.1231 | 60.2097 | -0.015487 | -0.052981 | 0.12487 | 0.029401 | 0.036709 | -0.036374 | -0.025882 | 0.0077058 | -0.011273 | 0.02609 | 0.060047 | -0.023251 | -0.023883 | 60.2417 | -62.0865 | -0.009155 | -62.2833 | 60.1913 | -62.1506 | -62.1368 | 0.059509 | 0.073242 | -62.4481 | 60.1364 | 60.1456 | -62.1185 | -62.2971 | -0.027466 | -0.013733 | -0.018311 | 0.036621 | -0.16022 | -0.14648 | 0.032043 | 0.004578 | -0.17395 | -0.073242 | 62.1826 | -0.32501 | -0.15106 | -0.064087 | 122.3145 | 122.3648 | 62.114 | -122.3465 | 122.2595 | 122.2687 | 62.1964 | -122.5067
765.125 | 122.6349 | -62.1185 | 60.2325 | 0.0074006 | -0.053622 | 0.12871 | 0.032178 | 0.035855 | -0.035305 | -0.024387 | 0.0077058 | -0.011273 | 0.026944 | 0.060688 | -0.020046 | -0.021533 | 60.2188 | -62.0911 | -0.022888 | -62.2971 | 60.1685 | -62.1597 | -62.146 | 0.041199 | 0.064087 | -62.471 | 60.1456 | 60.1181 | -62.1094 | -62.3062 | -0.041199 | -0.027466 | -0.064087 | 0.027466 | -0.17853 | -0.15106 | -0.013733 | 0.009155 | -0.18768 | -0.086975 | 62.1597 | -0.35248 | -0.16479 | -0.11444 | 122.287 | 122.3373 | 62.0956 | -122.3785 | 122.2641 | 122.2366 | 62.1826 | -122.5388
766.9219 | 122.6303 | -62.1368 | 60.2097 | 0.0074006 | -0.052553 | 0.12807 | 0.033673 | 0.030514 | -0.037228 | -0.022892 | 0.0077058 | -0.013623 | 0.029508 | 0.060474 | -0.020046 | -0.025165 | 60.2142 | -62.1002 | -0.013733 | -62.3016 | 60.1822 | -62.1552 | -62.1414 | 0.027466 | 0.041199 | -62.471 | 60.1364 | 60.1364 | -62.1231 | -62.2879 | -0.01831 | -0.004577 | -0.027466 | 0.036621 | -0.1648 | -0.16022 | 0.004577 | 0.013733 | -0.15106 | -0.073242 | 62.1643 | -0.33417 | -0.1831 | -0.073242 | 122.319 | 122.3511 | 62.1231 | -122.3511 | 122.2733 | 122.2733 | 62.178 | -122.4976
768.7031 | 122.5662 | -62.1368 | 60.2646 | -0.00022891 | -0.057467 | 0.12658 | 0.033887 | 0.035 | -0.043423 | -0.027591 | -0.015182 | -0.018536 | 0.025663 | 0.060688 | -0.026028 | -0.021747 | 60.2783 | -61.9492 | 0.068665 | -62.2147 | 60.2051 | -62.1094 | -62.0316 | 0.054932 | 0.10986 | -62.3154 | 60.1227 | 60.1501 | -62.0865 | -62.2421 | 0.027466 | 0.10529 | -0.059509 | 0.18768 | -0.07782 | -0.18311 | 0.013733 | 0.050354 | -0.10529 | -0.14191 | 62.1918 | -0.17853 | -0.073243 | -0.11444 | 122.3419 | 122.4152 | 62.2055 | -122.2961 | 122.2595 | 122.287 | 62.2467 | -122.5067
770.4844 | 122.4884 | -62.1689 | 60.2646 | -0.0078584 | -0.051699 | 0.12679 | 0.037305 | 0.036923 | -0.038083 | -0.027591 | -0.0075532 | -0.014904 | 0.029508 | 0.059193 | -0.023464 | -0.026233 | 60.2966 | -61.9217 | 0.12817 | -62.1872 | 60.1639 | -62.1231 | -62.059 | 0.050354 | 0.091553 | -62.3703 | 60.1273 | 60.1227 | -62.0956 | -62.2879 | 0.045776 | 0.10986 | -0.10071 | 0.24719 | -0.018311 | -0.12817 | 0.032044 | 0.073242 | -0.11902 | -0.13733 | 62.2192 | -0.20142 | -0.082397 | -0.14191 | 122.3328 | 122.4655 | 62.2971 | -122.3236 | 122.2961 | 122.2916 | 62.2604 | -122.5525
772.2656 | 122.5113 | -62.1506 | 60.2966 | 0.0074006 | -0.059603 | 0.12957 | 0.030683 | 0.036923 | -0.040646 | -0.027591 | -0.0075532 | -0.015759 | 0.025449 | 0.060902 | -0.021542 | -0.023029 | 60.3287 | -61.908 | 0.086975 | -62.1918 | 60.1547 | -62.0636 | -62.0361 | 0.10529 | 0.13275 | -62.3245 | 60.1593 | 60.1364 | -62.0728 | -62.2467 | 0.086975 | 0.11444 | -0.14191 | 0.24262 | -0.041198 | -0.15564 | 0.032043 | 0.07782 | -0.09613 | -0.13733 | 62.2559 | -0.17395 | -0.07782 | -0.16022 | 122.3053 | 122.4792 | 62.2375 | -122.3328 | 122.3099 | 122.287 | 62.2833 | -122.5433
773.9688 | 122.6669 | -62.1094 | 60.2188 | -0.0078584 | -0.054262 | 0.1285 | 0.031537 | 0.032864 | -0.034451 | -0.027164 | 7.627e-05 | -0.012555 | 0.026304 | 0.059834 | -0.018765 | -0.026019 | 60.26 | -62.0224 | 0.022888 | -62.2467 | 60.1913 | -62.1552 | -62.0728 | 0.10529 | 0.11444 | -62.3611 | 60.1547 | 60.0906 | -62.0636 | -62.233 | -0.045776 | 0.036621 | -0.027466 | 0.086975 | -0.13733 | -0.17395 | 0.041199 | 0.045776 | -0.1236 | -0.064087 | 62.2147 | -0.25177 | -0.12817 | -0.12817 | 122.3007 | 122.3694 | 62.1323 | -122.2916 | 122.2641 | 122.2 | 62.2238 | -122.4518
775.7656 | 122.6303 | -62.1231 | 60.1959 | -0.0078584 | -0.053622 | 0.12828 | 0.033887 | 0.036923 | -0.03616 | -0.023105 | -0.0075532 | -0.013195 | 0.026304 | 0.060474 | -0.018765 | -0.02666 | 60.2737 | -62.0178 | 0.073242 | -62.2375 | 60.1913 | -62.1552 | -62.1094 | 0.059509 | 0.082397 | -62.4115 | 60.1547 | 60.1227 | -62.0956 | -62.3199 | -0.032043 | 0.013733 | -0.004578 | 0.10529 | -0.11444 | -0.12817 | 0.07782 | 0.027466 | -0.19684 | -0.041199 | 62.1826 | -0.28839 | -0.091553 | -0.073242 | 122.3145 | 122.3969 | 62.1964 | -122.3053 | 122.2778 | 122.2458 | 62.2055 | -122.5159
777.5781 | 122.5342 | -62.1277 | 60.2646 | 0.0074006 | -0.055544 | 0.12871 | 0.03645 | 0.034786 | -0.041073 | -0.025882 | 7.627e-05 | -0.015545 | 0.028867 | 0.059406 | -0.024746 | -0.026447 | 60.3516 | -61.8668 | 0.16937 | -62.1597 | 60.2005 | -62.0865 | -62.0316 | 0.10071 | 0.16022 | -62.2833 | 60.1273 | 60.1089 | -62.0316 | -62.2238 | 0.041199 | 0.096131 | -0.064087 | 0.26093 | -0.032043 | -0.12817 | 0.086975 | 0.096131 | -0.09613 | -0.13733 | 62.2284 | -0.15564 | -0.059509 | -0.15564 | 122.3282 | 122.4792 | 62.2971 | -122.2961 | 122.2549 | 122.2366 | 62.2879 | -122.4884
779.2969 | 122.6532 | -62.0911 | 60.2234 | -0.00022891 | -0.056185 | 0.12722 | 0.032178 | 0.03735 | -0.03616 | -0.023746 | 0.015335 | -0.013623 | 0.027585 | 0.057697 | -0.019192 | -0.026874 | 60.3149 | -61.9766 | 0.050354 | -62.2284 | 60.1959 | -62.1048 | -62.059 | 0.13275 | 0.15106 | -62.3428 | 60.1501 | 60.1227 | -62.0499 | -62.2375 | -0.013733 | 0.032043 | -0.027466 | 0.11444 | -0.13733 | -0.16937 | 0.091552 | 0.041198 | -0.14648 | -0.073243 | 62.2238 | -0.25177 | -0.10529 | -0.10071 | 122.287 | 122.406 | 62.1414 | -122.2824 | 122.2412 | 122.2137 | 62.2421 | -122.4609
781.0625 | 122.5021 | -62.114 | 60.3149 | -0.0078584 | -0.057253 | 0.127 | 0.03111 | 0.035427 | -0.041073 | -0.028019 | 7.627e-05 | -0.017041 | 0.027158 | 0.058125 | -0.022396 | -0.02196 | 60.3561 | -61.8896 | 0.10529 | -62.178 | 60.2005 | -62.0819 | -62.0178 | 0.10986 | 0.13275 | -62.3154 | 60.1547 | 60.1501 | -62.0316 | -62.2284 | 0.032044 | 0.096131 | -0.11444 | 0.22431 | -0.064087 | -0.16022 | 0.041199 | 0.082398 | -0.11444 | -0.16022 | 62.2238 | -0.20142 | -0.086975 | -0.16479 | 122.3145 | 122.4701 | 62.2192 | -122.3328 | 122.2687 | 122.2641 | 62.2467 | -122.5433
782.875 | 122.5525 | -62.0911 | 60.2417 | -0.015487 | -0.053408 | 0.13106 | 0.034955 | 0.036282 | -0.040432 | -0.026096 | -0.015182 | -0.016613 | 0.029081 | 0.059406 | -0.027096 | -0.025592 | 60.379 | -61.8668 | 0.13733 | -62.1368 | 60.2097 | -62.0865 | -62.0224 | 0.13733 | 0.15564 | -62.2421 | 60.1547 | 60.1135 | -62.0132 | -62.1918 | 0.004577 | 0.068664 | -0.032043 | 0.2243 | -0.045777 | -0.11444 | 0.13733 | 0.077819 | -0.10071 | -0.086975 | 62.2284 | -0.15106 | -0.050354 | -0.12817 | 122.3007 | 122.4701 | 62.2284 | -122.2641 | 122.2458 | 122.2046 | 62.2467 | -122.4335
784.5938 | 122.6303 | -62.1185 | 60.2005 | -0.00022891 | -0.052126 | 0.12658 | 0.030683 | 0.033932 | -0.034024 | -0.026523 | -0.0075532 | -0.012127 | 0.024595 | 0.05962 | -0.01791 | -0.02901 | 60.2966 | -62.0087 | 0.073242 | -62.233 | 60.2234 | -62.1368 | -62.0865 | 0.054932 | 0.064087 | -62.4069 | 60.1501 | 60.1135 | -62.0865 | -62.2604 | -0.018311 | 0.032043 | 0.022889 | 0.10986 | -0.11444 | -0.14648 | 0.096131 | 0.032043 | -0.14191 | -0.050354 | 62.1735 | -0.28839 | -0.14648 | -0.086975 | 122.3419 | 122.4152 | 62.1918 | -122.287 | 122.2687 | 122.2321 | 62.1826 | -122.4609
786.375 | 122.6578 | -62.0911 | 60.2417 | 0.01503 | -0.051913 | 0.12679 | 0.031751 | 0.036495 | -0.035519 | -0.024601 | 0.0077058 | -0.013623 | 0.02609 | 0.058125 | -0.020046 | -0.023242 | 60.2554 | -62.0316 | -0.013733 | -62.2467 | 60.2234 | -62.146 | -62.0682 | 0.064087 | 0.050354 | -62.4298 | 60.173 | 60.141 | -62.0728 | -62.2421 | -0.054932 | 0.022888 | -0.01831 | 0.059509 | -0.15564 | -0.17853 | 0.013733 | 0.01831 | -0.15106 | -0.068664 | 62.1552 | -0.33875 | -0.18768 | -0.10071 | 122.3145 | 122.3465 | 62.0773 | -122.3099 | 122.2641 | 122.2321 | 62.1414 | -122.4838
788.1562 | 122.5433 | -62.1048 | 60.2829 | -0.00022891 | -0.055544 | 0.12871 | 0.033246 | 0.033505 | -0.04086 | -0.025455 | 7.627e-05 | -0.016613 | 0.025876 | 0.059193 | -0.024105 | -0.023456 | 60.3882 | -61.7981 | 0.16479 | -62.1185 | 60.1913 | -62.0636 | -62.0132 | 0.09613 | 0.16479 | -62.2559 | 60.1501 | 60.141 | -62.0224 | -62.2101 | 0.041198 | 0.091552 | -0.091553 | 0.3067 | -0.013733 | -0.10529 | 0.10529 | 0.082397 | -0.10529 | -0.13275 | 62.2009 | -0.15106 | -0.045776 | -0.14191 | 122.2961 | 122.493 | 62.2696 | -122.2961 | 122.2549 | 122.2458 | 62.2696 | -122.493
789.875 | 122.6532 | -62.0636 | 60.2371 | -0.00022891 | -0.054049 | 0.127 | 0.033673 | 0.033077 | -0.035519 | -0.025882 | -0.0075532 | -0.013409 | 0.026517 | 0.058552 | -0.019192 | -0.025165 | 60.26 | -62.0407 | -0.009155 | -62.2604 | 60.2325 | -62.1231 | -62.0636 | 0.036621 | 0.059509 | -62.4161 | 60.1913 | 60.1593 | -62.0682 | -62.2421 | -0.059509 | 0 | -0.004578 | 0.022889 | -0.19684 | -0.19684 | 0.022888 | -0.004577 | -0.17853 | -0.045777 | 62.1002 | -0.35248 | -0.17395 | -0.07782 | 122.2961 | 122.3236 | 62.0544 | -122.3007 | 122.2549 | 122.2229 | 62.1231 | -122.4792
791.6562 | 122.6028 | -62.0773 | 60.2554 | -0.00022891 | -0.049349 | 0.12679 | 0.031751 | 0.036923 | -0.034878 | -0.02396 | 7.627e-05 | -0.011059 | 0.025876 | 0.057697 | -0.018551 | -0.025806 | 60.2692 | -62.0132 | 0.018311 | -62.2421 | 60.2234 | -62.1231 | -62.0773 | 0.027466 | 0.050354 | -62.4435 | 60.2005 | 60.1456 | -62.0636 | -62.2742 | -0.045776 | 0 | -0.032043 | 0.064087 | -0.16479 | -0.16479 | 0.013733 | 0.013733 | -0.19684 | -0.054932 | 62.1048 | -0.36621 | -0.16937 | -0.10986 | 122.3007 | 122.3465 | 62.0956 | -122.3328 | 122.2778 | 122.2229 | 62.1277 | -122.5296
793.4375 | 122.6486 | -62.0865 | 60.2142 | -0.023117 | -0.051699 | 0.12764 | 0.033887 | 0.036709 | -0.035946 | -0.024814 | 7.627e-05 | -0.012982 | 0.028013 | 0.058979 | -0.02026 | -0.024951 | 60.2966 | -61.9629 | 0.07782 | -62.2009 | 60.228 | -62.1323 | -62.0682 | 0.036621 | 0.09613 | -62.3703 | 60.2051 | 60.1501 | -62.0728 | -62.2742 | -0.045776 | 0.018311 | 0.013733 | 0.1236 | -0.11444 | -0.13275 | 0.082398 | 0.013733 | -0.18768 | -0.009155 | 62.1231 | -0.28381 | -0.09613 | -0.064087 | 122.3145 | 122.3831 | 62.1643 | -122.2824 | 122.2916 | 122.2366 | 62.1826 | -122.4884
795.1562 | 122.6349 | -62.0728 | 60.228 | 0.0074006 | -0.052767 | 0.12807 | 0.0388 | 0.034786 | -0.03851 | -0.027591 | 7.627e-05 | -0.011486 | 0.028653 | 0.060474 | -0.022183 | -0.023456 | 60.2692 | -61.9995 | 0.054932 | -62.2055 | 60.2371 | -62.1094 | -62.0682 | 0.004578 | 0.036621 | -62.4069 | 60.1639 | 60.1822 | -62.0682 | -62.233 | -0.036621 | 0.004578 | 0.009156 | 0.073242 | -0.13275 | -0.13733 | 0.041199 | 0.004578 | -0.16022 | -0.064087 | 62.0773 | -0.33417 | -0.17395 | -0.045776 | 122.3099 | 122.3419 | 62.1277 | -122.2961 | 122.2366 | 122.2549 | 62.1094 | -122.4609
796.9375 | 122.5616 | -62.0453 | 60.3241 | -0.0078584 | -0.052767 | 0.12487 | 0.037946 | 0.034786 | -0.04385 | -0.029087 | -0.0075532 | -0.018536 | 0.026731 | 0.061756 | -0.025601 | -0.024524 | 60.3561 | -61.8759 | 0.10529 | -62.1231 | 60.2554 | -62.0178 | -61.9949 | 0.086975 | 0.13733 | -62.2467 | 60.1822 | 60.1868 | -61.9583 | -62.1643 | 0.027466 | 0.050354 | -0.068665 | 0.16937 | -0.07782 | -0.12817 | 0.032043 | 0.086975 | -0.11902 | -0.14191 | 62.1323 | -0.20142 | -0.082397 | -0.13733 | 122.3007 | 122.4014 | 62.1506 | -122.319 | 122.2275 | 122.2321 | 62.1826 | -122.4884
798.6719 | 122.5525 | -62.0911 | 60.2829 | -0.00022891 | -0.05234 | 0.1285 | 0.036664 | 0.033932 | -0.039792 | -0.027164 | 7.627e-05 | -0.015545 | 0.027372 | 0.058766 | -0.025601 | -0.02901 | 60.4111 | -61.7889 | 0.16479 | -62.0956 | 60.2371 | -62.0544 | -61.9812 | 0.10529 | 0.16937 | -62.2284 | 60.1913 | 60.173 | -61.9858 | -62.1689 | 0.036621 | 0.10986 | -0.045776 | 0.30212 | -0.004578 | -0.11444 | 0.12817 | 0.10529 | -0.07782 | -0.091553 | 62.1964 | -0.13733 | -0.05951 | -0.10986 | 122.3282 | 122.5021 | 62.2559 | -122.2641 | 122.2824 | 122.2641 | 62.2604 | -122.4518
800.4688 | 122.6074 | -62.1002 | 60.2875 | -0.00022891 | -0.05469 | 0.12572 | 0.030896 | 0.034146 | -0.037655 | -0.026096 | -0.0075532 | -0.012341 | 0.025449 | 0.059406 | -0.020901 | -0.028155 | 60.4294 | -61.8622 | 0.11444 | -62.1323 | 60.2234 | -62.0178 | -61.9904 | 0.16022 | 0.18768 | -62.2559 | 60.1913 | 60.1639 | -62.0224 | -62.178 | 0.082398 | 0.10986 | -0.064087 | 0.23804 | -0.032043 | -0.14191 | 0.14191 | 0.07782 | -0.07782 | -0.096131 | 62.2604 | -0.15564 | -0.077819 | -0.1236 | 122.3236 | 122.5296 | 62.2147 | -122.2778 | 122.2916 | 122.2641 | 62.2879 | -122.4655
802.1875 | 122.6028 | -62.0773 | 60.2554 | -0.00022891 | -0.051913 | 0.12508 | 0.033673 | 0.034359 | -0.034878 | -0.025028 | -0.0075532 | -0.011273 | 0.028226 | 0.057697 | -0.019619 | -0.026233 | 60.2875 | -61.972 | 0.045776 | -62.2147 | 60.2692 | -62.0911 | -62.0636 | 0.018311 | 0.022888 | -62.4069 | 60.2371 | 60.1913 | -62.0544 | -62.2238 | -0.013732 | 0.013733 | 0.013733 | 0.10529 | -0.13733 | -0.15106 | 0.032044 | 0.022889 | -0.14648 | -0.01831 | 62.0956 | -0.32959 | -0.1831 | -0.064087 | 122.3465 | 122.3648 | 62.1231 | -122.319 | 122.3145 | 122.2687 | 62.1002 | -122.4792
803.9688 | 122.5204 | -62.0911 | 60.3333 | 0.0074006 | -0.052553 | 0.12679 | 0.033673 | 0.033505 | -0.040219 | -0.027378 | -0.0075532 | -0.015545 | 0.026944 | 0.058338 | -0.02026 | -0.025378 | 60.3973 | -61.8347 | 0.11444 | -62.114 | 60.2234 | -62.0361 | -61.9812 | 0.14191 | 0.16937 | -62.2604 | 60.1776 | 60.1959 | -61.9675 | -62.178 | 0.054931 | 0.10986 | -0.10986 | 0.25635 | -0.022889 | -0.13275 | 0.064087 | 0.1236 | -0.086976 | -0.15564 | 62.233 | -0.16937 | -0.082397 | -0.13733 | 122.3145 | 122.4884 | 62.2055 | -122.3145 | 122.2687 | 122.287 | 62.2604 | -122.5113
805.7656 | 122.5983 | -62.0499 | 60.2783 | -0.00022891 | -0.054049 | 0.12893 | 0.02876 | 0.035214 | -0.03381 | -0.025028 | -0.0075532 | -0.010632 | 0.027372 | 0.061543 | -0.018337 | -0.026019 | 60.2921 | -62.0178 | 0.013733 | -62.2238 | 60.2737 | -62.0911 | -62.027 | 0.032043 | 0.050354 | -62.4344 | 60.2325 | 60.1868 | -62.0178 | -62.2147 | -0.041198 | 0.022888 | -0.004577 | 0.032044 | -0.17395 | -0.19684 | 0.013733 | 0.032044 | -0.16479 | -0.045776 | 62.0819 | -0.38452 | -0.21973 | -0.091552 | 122.3236 | 122.3419 | 62.0636 | -122.3053 | 122.2824 | 122.2366 | 62.1002 | -122.493
807.5781 | 122.6669 | -62.0224 | 60.2921 | -0.0078584 | -0.05469 | 0.12529 | 0.031964 | 0.036709 | -0.036374 | -0.023533 | -0.0075532 | -0.013836 | 0.027799 | 0.058766 | -0.020687 | -0.025592 | 60.3149 | -61.9537 | 0 | -62.1872 | 60.2646 | -62.0773 | -62.0316 | 0.091553 | 0.10071 | -62.3199 | 60.2142 | 60.173 | -61.9949 | -62.178 | -0.054932 | -0.009155 | -0.027466 | 0.068665 | -0.1648 | -0.15564 | 0.022888 | 0.027466 | -0.15564 | -0.07782 | 62.114 | -0.29755 | -0.14191 | -0.11902 | 122.287 | 122.3373 | 62.0224 | -122.3236 | 122.2366 | 122.1954 | 62.1231 | -122.4701
809.2812 | 122.5571 | -62.0224 | 60.347 | -0.0078584 | -0.059389 | 0.12957 | 0.032392 | 0.033718 | -0.044491 | -0.027591 | 7.627e-05 | -0.015332 | 0.025663 | 0.057697 | -0.024532 | -0.024951 | 60.3607 | -61.8668 | 0.073242 | -62.1094 | 60.2783 | -62.0087 | -61.9492 | 0.054932 | 0.11902 | -62.2467 | 60.2142 | 60.228 | -61.9583 | -62.1506 | 0.013733 | 0.073242 | -0.068665 | 0.15564 | -0.086975 | -0.16022 | 0.013733 | 0.064087 | -0.12817 | -0.13275 | 62.0773 | -0.2243 | -0.09613 | -0.11902 | 122.3007 | 122.3831 | 62.0956 | -122.2961 | 122.2366 | 122.2504 | 62.1414 | -122.4976
811.0625 | 122.4884 | -62.0361 | 60.3424 | 0.0074006 | -0.055758 | 0.12807 | 0.036237 | 0.036495 | -0.037869 | -0.027591 | 7.627e-05 | -0.015545 | 0.027372 | 0.060688 | -0.024319 | -0.026233 | 60.4248 | -61.8073 | 0.15564 | -62.0911 | 60.2921 | -61.9766 | -61.9537 | 0.07782 | 0.11902 | -62.2375 | 60.2417 | 60.2142 | -61.9537 | -62.1277 | 0.059509 | 0.082398 | -0.050354 | 0.22888 | -0.054931 | -0.13733 | 0.082398 | 0.082398 | -0.091553 | -0.10071 | 62.114 | -0.20142 | -0.10986 | -0.12817 | 122.3282 | 122.4609 | 62.1918 | -122.2961 | 122.2778 | 122.2504 | 62.1552 | -122.4701
812.875 | 122.5937 | -62.0316 | 60.2692 | -0.0078584 | -0.051485 | 0.12551 | 0.03346 | 0.036923 | -0.031887 | -0.024814 | 0.0077058 | -0.011486 | 0.029081 | 0.061756 | -0.020901 | -0.027087 | 60.3973 | -61.9034 | 0.09613 | -62.1597 | 60.2783 | -62.0728 | -62.0132 | 0.086975 | 0.11444 | -62.3245 | 60.2417 | 60.2142 | -62.0178 | -62.1689 | -0.041199 | 0.01831 | 0.009155 | 0.12817 | -0.12817 | -0.14648 | 0.12817 | 0.013733 | -0.13733 | -0.027466 | 62.1185 | -0.29297 | -0.15564 | -0.054932 | 122.3099 | 122.4289 | 62.1277 | -122.2824 | 122.2733 | 122.2458 | 62.146 | -122.438
814.6562 | 122.5388 | -62.0224 | 60.3882 | 0.0074006 | -0.053194 | 0.12828 | 0.034528 | 0.034146 | -0.038723 | -0.026737 | 7.627e-05 | -0.016613 | 0.025876 | 0.061115 | -0.023892 | -0.02666 | 60.4431 | -61.8027 | 0.10986 | -62.0956 | 60.2692 | -62.0041 | -61.9263 | 0.13733 | 0.15564 | -62.1964 | 60.228 | 60.2005 | -61.9354 | -62.1414 | 0.018311 | 0.09613 | -0.11902 | 0.21973 | -0.073242 | -0.16937 | 0.054931 | 0.086975 | -0.11902 | -0.16022 | 62.1597 | -0.17395 | -0.054932 | -0.18768 | 122.2916 | 122.4655 | 62.1323 | -122.3145 | 122.2504 | 122.2229 | 62.178 | -122.5296
816.4531 | 122.6212 | -62.027 | 60.3058 | -0.00022891 | -0.054476 | 0.12828 | 0.031537 | 0.034573 | -0.033596 | -0.025669 | 7.627e-05 | -0.012982 | 0.025235 | 0.059834 | -0.018337 | -0.02666 | 60.3333 | -61.9675 | -0.022888 | -62.1872 | 60.3195 | -62.027 | -61.9995 | 0.045776 | 0.036621 | -62.3703 | 60.2554 | 60.2325 | -62.0041 | -62.178 | 0 | 0.027466 | 0.013733 | 0.05951 | -0.16022 | -0.18768 | 0.027466 | 0.022889 | -0.15106 | -0.050354 | 62.0728 | -0.34332 | -0.19226 | -0.073242 | 122.3465 | 122.3602 | 62.0041 | -122.3053 | 122.2824 | 122.2595 | 62.0636 | -122.4838
818.2344 | 122.5433 | -62.0178 | 60.3516 | -0.00022891 | -0.05234 | 0.127 | 0.037091 | 0.034573 | -0.039792 | -0.027164 | 7.627e-05 | -0.014477 | 0.030149 | 0.060047 | -0.023037 | -0.027087 | 60.379 | -61.8851 | 0.068665 | -62.1506 | 60.3516 | -62.0087 | -61.9766 | 0.004578 | 0.032043 | -62.3108 | 60.2875 | 60.3195 | -61.9949 | -62.1231 | 0.009155 | 0.041198 | 0 | 0.13275 | -0.13275 | -0.17395 | 0.027466 | 0.022888 | -0.10529 | -0.064086 | 62.0224 | -0.29297 | -0.18768 | -0.032043 | 122.3694 | 122.3969 | 62.0865 | -122.3282 | 122.3053 | 122.3373 | 62.0499 | -122.4747
819.9375 | 122.5891 | -61.9949 | 60.3653 | -0.00022891 | -0.051485 | 0.12551 | 0.032605 | 0.033505 | -0.035519 | -0.025455 | 0.0077058 | -0.0117 | 0.027585 | 0.061543 | -0.01791 | -0.024951 | 60.3653 | -61.9354 | -0.018311 | -62.1414 | 60.3378 | -61.9949 | -61.9446 | 0.045776 | 0.050354 | -62.3383 | 60.2921 | 60.2783 | -61.972 | -62.1597 | 0 | 0.050354 | -0.027465 | 0.059509 | -0.14648 | -0.19684 | 0 | 0.022888 | -0.16479 | -0.073242 | 62.0407 | -0.34332 | -0.17853 | -0.086975 | 122.3328 | 122.3602 | 61.9766 | -122.3099 | 122.287 | 122.2733 | 62.0453 | -122.525
821.7344 | 122.6349 | -61.9492 | 60.3561 | -0.0078584 | -0.052767 | 0.127 | 0.031964 | 0.036923 | -0.035946 | -0.025455 | 0.0077058 | -0.013409 | 0.025876 | 0.060474 | -0.019833 | -0.025165 | 60.3973 | -61.8622 | 0.064087 | -62.1002 | 60.3424 | -61.9949 | -61.972 | 0.050354 | 0.07782 | -62.265 | 60.3104 | 60.2692 | -61.9492 | -62.1231 | -0.045776 | -0.022888 | -0.013733 | 0.086975 | -0.15106 | -0.12817 | 0.041199 | 0 | -0.17395 | -0.045776 | 61.9995 | -0.31586 | -0.14191 | -0.086975 | 122.2916 | 122.3465 | 62.0132 | -122.3282 | 122.2595 | 122.2183 | 62.027 | -122.4792
823.4688 | 122.5525 | -61.9446 | 60.4431 | -0.00022891 | -0.055331 | 0.12764 | 0.03645 | 0.033932 | -0.045132 | -0.027805 | -0.0075532 | -0.016827 | 0.027158 | 0.060047 | -0.026028 | -0.024097 | 60.4752 | -61.7432 | 0.10071 | -62.0224 | 60.3378 | -61.908 | -61.8896 | 0.10071 | 0.15106 | -62.1048 | 60.3104 | 60.3195 | -61.8759 | -62.059 | 0.036621 | 0.054932 | -0.10529 | 0.20142 | -0.07782 | -0.13275 | 0.032044 | 0.068664 | -0.11444 | -0.13275 | 62.0453 | -0.16022 | -0.045776 | -0.1236 | 122.2824 | 122.4197 | 62.0453 | -122.3328 | 122.2549 | 122.2641 | 62.0956 | -122.5021
825.2344 | 122.6349 | -61.9308 | 60.3928 | -0.00022891 | -0.047213 | 0.12423 | 0.038587 | 0.03265 | -0.033596 | -0.024814 | 7.627e-05 | -0.012341 | 0.027799 | 0.063892 | -0.022183 | -0.027087 | 60.4202 | -61.8942 | -0.022888 | -62.1002 | 60.3653 | -61.972 | -61.9354 | 0.068665 | 0.064087 | -62.2421 | 60.3333 | 60.2966 | -61.9308 | -62.1048 | -0.041199 | -0.004578 | -0.027466 | 0.036621 | -0.16937 | -0.16479 | 0.027466 | 0 | -0.17395 | -0.059509 | 61.9995 | -0.31128 | -0.13733 | -0.09613 | 122.2961 | 122.3511 | 61.908 | -122.3282 | 122.2641 | 122.2275 | 61.9949 | -122.4976
827.0312 | 122.5159 | -61.94 | 60.4614 | 0.0074006 | -0.057253 | 0.12615 | 0.030255 | 0.035427 | -0.039578 | -0.025242 | 7.627e-05 | -0.015332 | 0.025022 | 0.058125 | -0.020046 | -0.023029 | 60.498 | -61.7249 | 0.10071 | -62.0041 | 60.347 | -61.9308 | -61.8576 | 0.11444 | 0.15106 | -62.1414 | 60.3149 | 60.2737 | -61.8759 | -62.0407 | 0.009155 | 0.082397 | -0.11444 | 0.21515 | -0.064087 | -0.14648 | 0.036621 | 0.064086 | -0.10071 | -0.14649 | 62.0544 | -0.20142 | -0.10071 | -0.18768 | 122.287 | 122.438 | 62.0407 | -122.319 | 122.2549 | 122.2137 | 62.0911 | -122.5021
828.75 | 122.5571 | -61.908 | 60.4294 | -0.0078584 | -0.05704 | 0.12978 | 0.031751 | 0.034359 | -0.04385 | -0.027805 | 0.0077058 | -0.017682 | 0.025876 | 0.058338 | -0.023464 | -0.025378 | 60.5072 | -61.7294 | 0.09613 | -61.9904 | 60.3745 | -61.908 | -61.8439 | 0.10529 | 0.12817 | -62.0956 | 60.3287 | 60.3241 | -61.853 | -62.0407 | 0 | 0.064087 | -0.054931 | 0.17853 | -0.082397 | -0.14648 | 0.07782 | 0.054932 | -0.13275 | -0.10071 | 62.0132 | -0.18768 | -0.054932 | -0.10528 | 122.2824 | 122.4152 | 62.0041 | -122.2733 | 122.2366 | 122.2321 | 62.0361 | -122.4701
830.5469 | 122.5708 | -61.9125 | 60.434 | -0.0078584 | -0.054476 | 0.12999 | 0.034741 | 0.034786 | -0.041501 | -0.028019 | 7.627e-05 | -0.015973 | 0.026517 | 0.057697 | -0.024105 | -0.025378 | 60.5438 | -61.7111 | 0.15106 | -61.972 | 60.4019 | -61.8713 | -61.821 | 0.11902 | 0.13733 | -62.0773 | 60.3149 | 60.3104 | -61.8393 | -62.0361 | 0.041199 | 0.091553 | -0.032043 | 0.20142 | -0.059509 | -0.15106 | 0.10986 | 0.073243 | -0.1236 | -0.11902 | 62.0316 | -0.16479 | -0.041199 | -0.1236 | 122.3145 | 122.4564 | 62.0636 | -122.2549 | 122.2275 | 122.2229 | 62.0499 | -122.4701
832.2656 | 122.5891 | -61.9217 | 60.3928 | -0.00022891 | -0.051272 | 0.12572 | 0.032819 | 0.034146 | -0.031247 | -0.022892 | -0.0075532 | -0.010846 | 0.029294 | 0.060474 | -0.018978 | -0.027942 | 60.434 | -61.8896 | 0 | -62.0773 | 60.4156 | -61.9583 | -61.9217 | 0.018311 | 0.018311 | -62.2971 | 60.3745 | 60.2875 | -61.9217 | -62.0956 | -0.036621 | 0 | 0.022888 | 0.032044 | -0.15564 | -0.15564 | 0.041199 | 0 | -0.17395 | -0.01831 | 61.94 | -0.37537 | -0.20142 | -0.10529 | 122.3373 | 122.3557 | 61.9217 | -122.3145 | 122.2961 | 122.2092 | 61.94 | -122.4884
834.0625 | 122.58 | -61.9263 | 60.434 | -0.0078584 | -0.053408 | 0.12615 | 0.039868 | 0.034146 | -0.037869 | -0.025028 | -0.0075532 | -0.011486 | 0.029722 | 0.059834 | -0.023678 | -0.026019 | 60.4477 | -61.8164 | 0.082397 | -62.0361 | 60.4156 | -61.9537 | -61.8851 | 0.013733 | 0.022888 | -62.2238 | 60.3699 | 60.3424 | -61.8896 | -62.0728 | -0.027465 | 0.041199 | -0.018311 | 0.10986 | -0.10986 | -0.15106 | 0.013733 | 0.036622 | -0.14648 | -0.064087 | 61.94 | -0.29755 | -0.15106 | -0.091553 | 122.3419 | 122.374 | 62.0087 | -122.319 | 122.2961 | 122.2687 | 61.9492 | -122.5067
835.7812 | 122.5616 | -61.8851 | 60.4752 | -0.00022891 | -0.054903 | 0.12679 | 0.034528 | 0.033932 | -0.04086 | -0.027378 | 0.0077058 | -0.016613 | 0.027799 | 0.058338 | -0.024319 | -0.025806 | 60.5576 | -61.6516 | 0.15564 | -61.9354 | 60.4156 | -61.8759 | -61.8164 | 0.11444 | 0.15564 | -62.0453 | 60.3653 | 60.3378 | -61.8118 | -61.9904 | 0.009155 | 0.068665 | -0.05951 | 0.23346 | -0.050354 | -0.11902 | 0.082397 | 0.073242 | -0.10528 | -0.10986 | 61.9995 | -0.16022 | -0.054932 | -0.13733 | 122.3007 | 122.4426 | 62.0407 | -122.2916 | 122.2504 | 122.2229 | 62.0407 | -122.4655
837.5781 | 122.5891 | -61.9034 | 60.4111 | -0.00022891 | -0.051485 | 0.12615 | 0.031964 | 0.034359 | -0.031033 | -0.023533 | 0.0077058 | -0.011059 | 0.028013 | 0.060474 | -0.017483 | -0.026447 | 60.5209 | -61.7661 | 0.091553 | -62.0224 | 60.3973 | -61.9217 | -61.8851 | 0.09613 | 0.10986 | -62.1918 | 60.3607 | 60.3333 | -61.8576 | -62.0499 | -0.018311 | 0.01831 | -0.013733 | 0.13733 | -0.11902 | -0.13733 | 0.10986 | 0.045776 | -0.14648 | -0.050354 | 61.9995 | -0.28839 | -0.14191 | -0.07782 | 122.3007 | 122.4243 | 61.9949 | -122.2961 | 122.2641 | 122.2366 | 62.0132 | -122.4609
839.2969 | 122.5983 | -61.908 | 60.4523 | 0.0074006 | -0.052126 | 0.12786 | 0.034101 | 0.034573 | -0.038296 | -0.025882 | 7.627e-05 | -0.012127 | 0.029935 | 0.059193 | -0.019619 | -0.025592 | 60.466 | -61.7889 | 0.050354 | -62.0316 | 60.4523 | -61.9125 | -61.8759 | 0.032043 | 0.027466 | -62.2055 | 60.4065 | 60.3653 | -61.8759 | -62.0544 | -0.004578 | 0.032043 | 0 | 0.11902 | -0.1236 | -0.15564 | 0.013732 | 0.032043 | -0.14648 | -0.045777 | 61.94 | -0.29755 | -0.15106 | -0.086976 | 122.3602 | 122.374 | 61.9583 | -122.3282 | 122.3145 | 122.2733 | 61.9354 | -122.5067
841.0781 | 122.5937 | -61.8896 | 60.4431 | -0.015487 | -0.051699 | 0.12679 | 0.032605 | 0.034359 | -0.032528 | -0.024814 | -0.0075532 | -0.0117 | 0.026517 | 0.060261 | -0.018978 | -0.025592 | 60.5392 | -61.7569 | 0.086975 | -61.9949 | 60.4614 | -61.908 | -61.8347 | 0.073242 | 0.091553 | -62.1918 | 60.3928 | 60.3973 | -61.8393 | -62.0224 | -0.018311 | 0.054931 | 0.018311 | 0.13275 | -0.10529 | -0.16022 | 0.096131 | 0.050354 | -0.13275 | -0.050354 | 61.9629 | -0.30212 | -0.16937 | -0.045776 | 122.3511 | 122.4289 | 61.9766 | -122.2778 | 122.2824 | 122.287 | 61.9812 | -122.4655
842.875 | 122.6303 | -61.8301 | 60.4797 | 0.01503 | -0.052126 | 0.12508 | 0.036664 | 0.036068 | -0.036374 | -0.026523 | 0.0077058 | -0.012982 | 0.029294 | 0.057697 | -0.022823 | -0.023883 | 60.498 | -61.7569 | 0.07782 | -61.9675 | 60.4889 | -61.8713 | -61.821 | 0.004578 | 0.050354 | -62.1506 | 60.4065 | 60.4248 | -61.8393 | -61.9904 | -0.041199 | 0.009155 | 0.009156 | 0.073242 | -0.13733 | -0.14648 | 0.018311 | -0.009155 | -0.16022 | -0.073242 | 61.8347 | -0.32043 | -0.16022 | -0.054931 | 122.319 | 122.3282 | 61.908 | -122.3007 | 122.2366 | 122.2549 | 61.8805 | -122.4701
844.6719 | 122.58 | -61.8484 | 60.5118 | -0.00022891 | -0.051913 | 0.127 | 0.032392 | 0.03735 | -0.036374 | -0.02396 | -0.015182 | -0.012555 | 0.025449 | 0.059406 | -0.018124 | -0.023883 | 60.4889 | -61.7935 | 0.009155 | -62.0041 | 60.4752 | -61.8713 | -61.821 | -0.013733 | 0.036621 | -62.1872 | 60.4568 | 60.4202 | -61.8164 | -62.027 | -0.022888 | 0.027466 | -0.036621 | 0.054932 | -0.15564 | -0.1831 | -0.022888 | 0.032044 | -0.17853 | -0.054932 | 61.8347 | -0.33875 | -0.16022 | -0.091553 | 122.3236 | 122.3373 | 61.8576 | -122.3328 | 122.3053 | 122.2687 | 61.8851 | -122.5388
846.4688 | 122.6028 | -61.8118 | 60.5301 | 0.0074006 | -0.050844 | 0.12743 | 0.030469 | 0.035 | -0.038296 | -0.024814 | 7.627e-05 | -0.0117 | 0.025876 | 0.05962 | -0.020474 | -0.024524 | 60.5896 | -61.6882 | 0.091553 | -61.94 | 60.4752 | -61.8622 | -61.8118 | 0.064087 | 0.091553 | -62.114 | 60.4477 | 60.434 | -61.7935 | -61.9766 | -0.050354 | 0 | -0.054931 | 0.1236 | -0.12817 | -0.12817 | 0.05951 | 0.018311 | -0.16479 | -0.082397 | 61.8759 | -0.30212 | -0.13733 | -0.09613 | 122.287 | 122.4014 | 61.9034 | -122.3419 | 122.2595 | 122.2458 | 61.9034 | -122.5067
848.1875 | 122.5983 | -61.7844 | 60.5209 | -0.00022891 | -0.052553 | 0.127 | 0.03346 | 0.034359 | -0.037014 | -0.024387 | 7.627e-05 | -0.012127 | 0.026944 | 0.061543 | -0.02026 | -0.025165 | 60.5896 | -61.6745 | 0.086975 | -61.9263 | 60.5301 | -61.8118 | -61.7798 | 0.068665 | 0.09613 | -62.1048 | 60.466 | 60.466 | -61.7889 | -61.9537 | -0.027466 | 0.004578 | 0.009155 | 0.10986 | -0.14191 | -0.14649 | 0.068665 | -0.004577 | -0.16937 | -0.054932 | 61.853 | -0.32043 | -0.15106 | -0.054932 | 122.3145 | 122.374 | 61.8713 | -122.3007 | 122.2504 | 122.2504 | 61.8805 | -122.4747
849.9688 | 122.4884 | -61.7889 | 60.5988 | -0.00022891 | -0.053622 | 0.12722 | 0.0388 | 0.035 | -0.042141 | -0.026523 | 7.627e-05 | -0.017254 | 0.028867 | 0.060047 | -0.026241 | -0.024097 | 60.6354 | -61.5921 | 0.12817 | -61.8439 | 60.5209 | -61.7706 | -61.7249 | 0.018311 | 0.073242 | -62.027 | 60.498 | 60.4843 | -61.7249 | -61.8988 | 0.01831 | 0.064086 | -0.07782 | 0.19684 | -0.054932 | -0.11902 | 0.036621 | 0.064086 | -0.10986 | -0.10071 | 61.8073 | -0.23804 | -0.12817 | -0.11444 | 122.3099 | 122.4243 | 61.9171 | -122.3236 | 122.287 | 122.2733 | 61.8622 | -122.4976
851.75 | 122.5479 | -61.7477 | 60.6171 | -0.015487 | -0.058108 | 0.12764 | 0.03645 | 0.035427 | -0.044705 | -0.027378 | 7.627e-05 | -0.01875 | 0.027585 | 0.059834 | -0.026028 | -0.023242 | 60.6949 | -61.528 | 0.15564 | -61.7935 | 60.5484 | -61.702 | -61.6791 | 0.11902 | 0.15564 | -61.8942 | 60.5026 | 60.5164 | -61.6653 | -61.8668 | 0.045777 | 0.068665 | -0.068664 | 0.21973 | -0.045776 | -0.11444 | 0.07782 | 0.082398 | -0.11902 | -0.11444 | 61.8668 | -0.14648 | -0.027466 | -0.10071 | 122.2961 | 122.4426 | 61.9034 | -122.2961 | 122.2504 | 122.2641 | 61.9034 | -122.4838
853.5312 | 122.5616 | -61.7523 | 60.6445 | 0.0074006 | -0.055544 | 0.13021 | 0.033246 | 0.033932 | -0.04086 | -0.02866 | 7.627e-05 | -0.01875 | 0.025449 | 0.057911 | -0.022396 | -0.025378 | 60.6857 | -61.5509 | 0.10986 | -61.7981 | 60.5759 | -61.7065 | -61.6745 | 0.086975 | 0.14648 | -61.9034 | 60.5301 | 60.5072 | -61.647 | -61.8439 | 0.045776 | 0.077819 | -0.068664 | 0.20142 | -0.045777 | -0.1236 | 0.041199 | 0.10529 | -0.091553 | -0.11444 | 61.8393 | -0.15106 | -0.059509 | -0.13733 | 122.3282 | 122.438 | 61.8622 | -122.319 | 122.2824 | 122.2595 | 61.8988 | -122.4884
855.3125 | 122.5342 | -61.7294 | 60.6445 | 0.0074006 | -0.056185 | 0.13021 | 0.035169 | 0.03735 | -0.040219 | -0.0293 | 0.0077058 | -0.016613 | 0.025876 | 0.057697 | -0.022823 | -0.026233 | 60.7636 | -61.4594 | 0.1831 | -61.7569 | 60.5759 | -61.6928 | -61.6287 | 0.11444 | 0.16022 | -61.8805 | 60.5118 | 60.5072 | -61.6425 | -61.8164 | 0.036621 | 0.10071 | -0.068664 | 0.27008 | -0.027466 | -0.12817 | 0.11902 | 0.086975 | -0.086975 | -0.13275 | 61.8439 | -0.15106 | -0.064087 | -0.13733 | 122.3053 | 122.493 | 61.9125 | -122.2733 | 122.2412 | 122.2366 | 61.8896 | -122.4609
857.0938 | 122.6257 | -61.7249 | 60.5804 | 0.0074006 | -0.049563 | 0.12615 | 0.032819 | 0.037136 | -0.033383 | -0.027164 | -0.0075532 | -0.011273 | 0.02844 | 0.060474 | -0.020474 | -0.027942 | 60.6766 | -61.6333 | 0.10071 | -61.8256 | 60.6033 | -61.7523 | -61.7157 | 0.073242 | 0.073242 | -62.0132 | 60.5576 | 60.5255 | -61.6974 | -61.8851 | -0.027465 | 0.009156 | 0.022889 | 0.091553 | -0.10071 | -0.10986 | 0.096131 | 0.027466 | -0.16022 | -0.022888 | 61.7981 | -0.28839 | -0.12817 | -0.054931 | 122.3282 | 122.4014 | 61.8256 | -122.2961 | 122.2824 | 122.2504 | 61.7981 | -122.4655
858.875 | 122.5113 | -61.7157 | 60.6995 | -0.00022891 | -0.054049 | 0.12914 | 0.030683 | 0.035427 | -0.041714 | -0.026096 | 0.0077058 | -0.015759 | 0.028226 | 0.058766 | -0.023251 | -0.022815 | 60.7544 | -61.5143 | 0.082397 | -61.7798 | 60.6216 | -61.6699 | -61.6196 | 0.059509 | 0.10986 | -61.9034 | 60.5576 | 60.5713 | -61.6333 | -61.7844 | 0.045776 | 0.09613 | -0.07782 | 0.20142 | -0.064087 | -0.16022 | 0.054932 | 0.082397 | -0.068665 | -0.14191 | 61.7752 | -0.18768 | -0.11902 | -0.12817 | 122.3373 | 122.4701 | 61.7981 | -122.319 | 122.2733 | 122.287 | 61.8256 | -122.4838
860.6719 | 122.6028 | -61.6837 | 60.6354 | -0.00022891 | -0.052767 | 0.12978 | 0.031751 | 0.035641 | -0.032956 | -0.02631 | 7.627e-05 | -0.011273 | 0.027158 | 0.058979 | -0.018124 | -0.026874 | 60.7315 | -61.5738 | 0.10986 | -61.8301 | 60.585 | -61.7157 | -61.6974 | 0.073242 | 0.10529 | -61.9995 | 60.5576 | 60.5438 | -61.6699 | -61.8622 | -0.032043 | -0.013733 | -0.050354 | 0.10986 | -0.14648 | -0.13275 | 0.09613 | 0.013733 | -0.17853 | -0.07782 | 61.7569 | -0.31586 | -0.13733 | -0.091553 | 122.2687 | 122.4152 | 61.7935 | -122.3328 | 122.2412 | 122.2275 | 61.7889 | -122.4976
862.4531 | 122.5616 | -61.6699 | 60.704 | -0.00022891 | -0.058962 | 0.12743 | 0.036664 | 0.036709 | -0.041928 | -0.027805 | 7.627e-05 | -0.017468 | 0.028013 | 0.057911 | -0.024105 | -0.024951 | 60.7727 | -61.4639 | 0.15106 | -61.7386 | 60.6308 | -61.6425 | -61.5967 | 0.11444 | 0.14648 | -61.8393 | 60.553 | 60.5804 | -61.615 | -61.7706 | 0.027466 | 0.073242 | -0.073243 | 0.20599 | -0.068664 | -0.14191 | 0.068664 | 0.054932 | -0.10071 | -0.15106 | 61.7844 | -0.16937 | -0.068664 | -0.1236 | 122.3007 | 122.4426 | 61.821 | -122.3007 | 122.2229 | 122.2504 | 61.8164 | -122.4747
864.1562 | 122.6349 | -61.6791 | 60.6491 | 0.0074006 | -0.052126 | 0.12572 | 0.035169 | 0.035214 | -0.034878 | -0.024173 | -0.0075532 | -0.013623 | 0.028653 | 0.05962 | -0.019619 | -0.027515 | 60.7361 | -61.5509 | 0.10529 | -61.7981 | 60.6537 | -61.7157 | -61.6653 | 0.07782 | 0.086975 | -61.9537 | 60.6033 | 60.5484 | -61.6608 | -61.8256 | -0.036621 | 0.013733 | 0.004578 | 0.12817 | -0.11902 | -0.13275 | 0.086975 | 0.01831 | -0.14648 | -0.045776 | 61.7569 | -0.27466 | -0.12817 | -0.10071 | 122.3328 | 122.4152 | 61.7844 | -122.3145 | 122.2824 | 122.2275 | 61.7661 | -122.4747
865.9375 | 122.5479 | -61.6562 | 60.7132 | -0.0078584 | -0.056612 | 0.1285 | 0.035809 | 0.033077 | -0.041714 | -0.026523 | 7.627e-05 | -0.018963 | 0.027799 | 0.057697 | -0.024532 | -0.024524 | 60.8276 | -61.3998 | 0.19684 | -61.6745 | 60.6445 | -61.615 | -61.5784 | 0.13275 | 0.15106 | -61.8027 | 60.5896 | 60.585 | -61.5692 | -61.7523 | 0.041199 | 0.07782 | -0.068665 | 0.25635 | -0.018311 | -0.096131 | 0.11444 | 0.086975 | -0.09613 | -0.1236 | 61.7889 | -0.14648 | -0.050354 | -0.12817 | 122.3007 | 122.4838 | 61.853 | -122.2916 | 122.2458 | 122.2412 | 61.8073 | -122.4655
867.7188 | 122.6532 | -61.6104 | 60.6766 | -0.0078584 | -0.05469 | 0.1238 | 0.03346 | 0.035427 | -0.034665 | -0.02631 | 0.0077058 | -0.011914 | 0.027372 | 0.061543 | -0.020687 | -0.024738 | 60.7544 | -61.5646 | 0.018311 | -61.7844 | 60.6812 | -61.6379 | -61.647 | 0.086975 | 0.091553 | -61.9217 | 60.6354 | 60.6033 | -61.6104 | -61.7661 | -0.027465 | -0.036621 | 0.004577 | 0.045777 | -0.17395 | -0.13733 | 0.07782 | 0 | -0.15564 | -0.041199 | 61.6974 | -0.31128 | -0.15564 | -0.073242 | 122.2916 | 122.3648 | 61.6287 | -122.3236 | 122.2458 | 122.2137 | 61.702 | -122.4426
869.5156 | 122.5891 | -61.6013 | 60.7498 | -0.015487 | -0.057894 | 0.12722 | 0.032178 | 0.035641 | -0.037228 | -0.024814 | 0.0077058 | -0.015545 | 0.026731 | 0.060474 | -0.019833 | -0.025806 | 60.8505 | -61.3907 | 0.12817 | -61.6516 | 60.6537 | -61.5829 | -61.5372 | 0.15564 | 0.18768 | -61.7844 | 60.6354 | 60.6216 | -61.5555 | -61.7661 | 0.01831 | 0.064087 | -0.09613 | 0.21057 | -0.050354 | -0.11444 | 0.10071 | 0.045776 | -0.1648 | -0.11444 | 61.7569 | -0.18311 | -0.018311 | -0.12817 | 122.2549 | 122.4518 | 61.7294 | -122.287 | 122.2366 | 122.2229 | 61.7889 | -122.5159
871.2969 | 122.6074 | -61.5967 | 60.7361 | -0.00022891 | -0.051058 | 0.12828 | 0.033246 | 0.031368 | -0.033383 | -0.025669 | 7.627e-05 | -0.010846 | 0.029508 | 0.058125 | -0.018337 | -0.025378 | 60.7086 | -61.5875 | 0 | -61.7798 | 60.704 | -61.6425 | -61.5921 | 0.041199 | 0.050354 | -61.9812 | 60.6583 | 60.6171 | -61.6058 | -61.8027 | -0.045776 | 0.004578 | -0.032043 | 0.009156 | -0.1831 | -0.18768 | -0.027466 | -0.009155 | -0.20599 | -0.07782 | 61.6379 | -0.38452 | -0.17853 | -0.11902 | 122.3007 | 122.3053 | 61.5967 | -122.3282 | 122.2549 | 122.2137 | 61.647 | -122.5388
873.0781 | 122.5067 | -61.6058 | 60.7773 | 0.0074006 | -0.052126 | 0.12828 | 0.038587 | 0.034573 | -0.040646 | -0.027164 | 7.627e-05 | -0.015545 | 0.029294 | 0.060261 | -0.023464 | -0.024738 | 60.8597 | -61.3266 | 0.20142 | -61.647 | 60.6995 | -61.5509 | -61.5326 | 0.10529 | 0.17395 | -61.7615 | 60.6491 | 60.6491 | -61.5509 | -61.6974 | 0.054932 | 0.073242 | -0.07782 | 0.27924 | -0.041199 | -0.11444 | 0.082397 | 0.054932 | -0.091553 | -0.12817 | 61.7111 | -0.15564 | -0.064087 | -0.12817 | 122.3053 | 122.4655 | 61.8073 | -122.3099 | 122.2549 | 122.2549 | 61.7798 | -122.4747
874.875 | 122.6532 | -61.6058 | 60.6995 | -0.00022891 | -0.050844 | 0.127 | 0.033032 | 0.034573 | -0.037228 | -0.026523 | -0.0075532 | -0.013195 | 0.02844 | 0.058979 | -0.021542 | -0.027087 | 60.7452 | -61.5051 | 0.054932 | -61.7386 | 60.7224 | -61.6104 | -61.6013 | 0.009155 | 0.050354 | -61.9171 | 60.6766 | 60.6354 | -61.6104 | -61.7844 | -0.004578 | 0.004578 | 0.022888 | 0.10071 | -0.13275 | -0.13733 | 0.045776 | -0.004578 | -0.17853 | -0.022888 | 61.615 | -0.31128 | -0.13275 | -0.064087 | 122.3282 | 122.3511 | 61.6608 | -122.3007 | 122.2824 | 122.2412 | 61.6562 | -122.4838
876.6719 | 122.6028 | -61.5829 | 60.7452 | -0.00022891 | -0.053835 | 0.12273 | 0.030683 | 0.034786 | -0.035519 | -0.026523 | 7.627e-05 | -0.012555 | 0.028653 | 0.060902 | -0.018124 | -0.02132 | 60.7269 | -61.5601 | -0.036621 | -61.7615 | 60.7269 | -61.6196 | -61.5829 | 0.022888 | 0.050354 | -61.9354 | 60.6995 | 60.6674 | -61.5784 | -61.7706 | -0.036621 | 0 | -0.01831 | 0.022888 | -0.17853 | -0.17853 | -0.01831 | 0.004578 | -0.18768 | -0.045776 | 61.6058 | -0.35248 | -0.1648 | -0.07782 | 122.3099 | 122.3099 | 61.5463 | -122.3282 | 122.2824 | 122.2504 | 61.6333 | -122.5159
878.4531 | 122.5021 | -61.615 | 60.7864 | -0.00022891 | -0.053622 | 0.12551 | 0.035169 | 0.036068 | -0.04086 | -0.029728 | -0.015182 | -0.015545 | 0.026517 | 0.057911 | -0.023464 | -0.024097 | 60.8276 | -61.3953 | 0.073242 | -61.6608 | 60.7407 | -61.5784 | -61.5189 | 0 | 0.004578 | -61.8439 | 60.6857 | 60.704 | -61.5326 | -61.7432 | 0.036621 | 0.09613 | -0.045776 | 0.21973 | -0.045777 | -0.14191 | 0.041199 | 0.082397 | -0.12817 | -0.10071 | 61.615 | -0.22888 | -0.10071 | -0.082397 | 122.3557 | 122.4426 | 61.6882 | -122.3053 | 122.3007 | 122.319 | 61.6196 | -122.5296
880.1562 | 122.644 | -61.5692 | 60.7727 | -0.0078584 | -0.05234 | 0.12828 | 0.032392 | 0.033718 | -0.03616 | -0.026737 | 7.627e-05 | -0.014691 | 0.026304 | 0.060902 | -0.019833 | -0.025165 | 60.791 | -61.5189 | -0.032043 | -61.7386 | 60.7636 | -61.6241 | -61.5372 | 0.054932 | 0.054932 | -61.9034 | 60.6857 | 60.704 | -61.528 | -61.7477 | -0.054932 | 0.032044 | -0.009155 | 0.050354 | -0.16937 | -0.20142 | 0.018311 | 0.041199 | -0.17853 | -0.086975 | 61.6241 | -0.33417 | -0.15564 | -0.068664 | 122.3328 | 122.3602 | 61.5372 | -122.3099 | 122.2549 | 122.2733 | 61.6241 | -122.5204
881.9531 | 122.5708 | -61.5967 | 60.7819 | 0.0074006 | -0.052553 | 0.12764 | 0.036237 | 0.036709 | -0.03851 | -0.026737 | 7.627e-05 | -0.012555 | 0.02609 | 0.057911 | -0.021542 | -0.023242 | 60.8002 | -61.4731 | -0.009155 | -61.7111 | 60.759 | -61.5829 | -61.5417 | -0.018311 | -0.013733 | -61.8896 | 60.7224 | 60.7224 | -61.5555 | -61.7157 | 0.013733 | 0.054932 | -0.022888 | 0.1236 | -0.11444 | -0.16937 | 0.018311 | 0.041199 | -0.11902 | -0.059509 | 61.5784 | -0.29297 | -0.17395 | -0.059509 | 122.3557 | 122.3969 | 61.5875 | -122.3236 | 122.319 | 122.319 | 61.5829 | -122.4976
883.7344 | 122.5067 | -61.528 | 60.8551 | -0.0078584 | -0.058108 | 0.12807 | 0.034314 | 0.035 | -0.042355 | -0.028232 | 7.627e-05 | -0.016186 | 0.025022 | 0.058979 | -0.02496 | -0.023456 | 60.9146 | -61.3174 | 0.12817 | -61.5738 | 60.7819 | -61.4822 | -61.4594 | 0.09613 | 0.16022 | -61.6974 | 60.7361 | 60.7086 | -61.4456 | -61.6241 | 0.045776 | 0.068664 | -0.073243 | 0.21057 | -0.045777 | -0.11444 | 0.059509 | 0.082397 | -0.096131 | -0.11902 | 61.6241 | -0.16937 | -0.073242 | -0.14648 | 122.3099 | 122.4426 | 61.6562 | -122.3145 | 122.2641 | 122.2366 | 61.6882 | -122.4792
885.4531 | 122.5342 | -61.5738 | 60.791 | -0.00022891 | -0.052553 | 0.12593 | 0.031751 | 0.037991 | -0.035519 | -0.027805 | -0.0075532 | -0.0117 | 0.024808 | 0.059834 | -0.021542 | -0.026447 | 60.8093 | -61.4685 | -0.018311 | -61.7065 | 60.7773 | -61.5784 | -61.5234 | -0.018311 | -0.018311 | -61.8622 | 60.7269 | 60.7086 | -61.5463 | -61.7157 | -0.004577 | 0.050355 | -0.013733 | 0.10529 | -0.13275 | -0.18311 | 0.01831 | 0.027466 | -0.14191 | -0.064087 | 61.5555 | -0.28839 | -0.14648 | -0.082398 | 122.3511 | 122.3831 | 61.5555 | -122.3145 | 122.3007 | 122.2824 | 61.5555 | -122.5067
887.2344 | 122.5983 | -61.528 | 60.7819 | -0.00022891 | -0.051272 | 0.12487 | 0.030896 | 0.034359 | -0.032528 | -0.025669 | 7.627e-05 | -0.012127 | 0.026944 | 0.060688 | -0.018551 | -0.025592 | 60.8139 | -61.5051 | 0.009155 | -61.7203 | 60.7452 | -61.6013 | -61.5646 | 0.018311 | 0.041199 | -61.9034 | 60.7086 | 60.7544 | -61.5692 | -61.7432 | -0.073242 | -0.036621 | -0.036621 | 0.022888 | -0.19226 | -0.15564 | 0.032044 | -0.041199 | -0.21515 | -0.073242 | 61.5463 | -0.37537 | -0.16022 | -0.027465 | 122.2733 | 122.3419 | 61.5372 | -122.3465 | 122.2366 | 122.2824 | 61.5692 | -122.525
889.0312 | 122.5204 | -61.528 | 60.7864 | -0.00022891 | -0.051485 | 0.12465 | 0.036237 | 0.034786 | -0.037442 | -0.025669 | 7.627e-05 | -0.012127 | 0.029081 | 0.060047 | -0.022183 | -0.023883 | 60.8322 | -61.4319 | 0 | -61.6562 | 60.791 | -61.5829 | -61.5097 | 0.004578 | 0.045776 | -61.8301 | 60.759 | 60.7224 | -61.5097 | -61.6791 | -0.054932 | 0.01831 | 0.004578 | 0.09613 | -0.12817 | -0.14648 | 0.045776 | 0.01831 | -0.15106 | -0.027466 | 61.5326 | -0.30212 | -0.15106 | -0.064087 | 122.319 | 122.3602 | 61.528 | -122.2961 | 122.287 | 122.2504 | 61.5738 | -122.4655
890.7656 | 122.6578 | -61.4456 | 60.8688 | -0.00022891 | -0.054262 | 0.1285 | 0.031751 | 0.033291 | -0.038083 | -0.02631 | 0.0077058 | -0.013836 | 0.025449 | 0.060047 | -0.019192 | -0.023669 | 60.8688 | -61.4227 | 0.018311 | -61.6196 | 60.8047 | -61.4914 | -61.4548 | 0.11444 | 0.1236 | -61.7477 | 60.7681 | 60.791 | -61.4365 | -61.6104 | -0.045776 | -0.009155 | -0.064086 | 0.022889 | -0.17395 | -0.16479 | 0 | 0.009156 | -0.16479 | -0.10071 | 61.5601 | -0.30212 | -0.13733 | -0.077819 | 122.2504 | 122.3145 | 61.4639 | -122.3236 | 122.2137 | 122.2366 | 61.5692 | -122.4792
892.5 | 122.5296 | -61.4685 | 60.8826 | -0.00022891 | -0.053835 | 0.12807 | 0.033032 | 0.035214 | -0.044491 | -0.030796 | 0.0077058 | -0.015973 | 0.026731 | 0.058125 | -0.023464 | -0.024738 | 61.0153 | -61.2259 | 0.16479 | -61.528 | 60.8276 | -61.441 | -61.3815 | 0.09613 | 0.16479 | -61.6287 | 60.7819 | 60.8139 | -61.3998 | -61.5601 | 0.027466 | 0.086975 | -0.054931 | 0.24262 | -0.059509 | -0.14648 | 0.13275 | 0.068665 | -0.091553 | -0.10071 | 61.5646 | -0.16022 | -0.068664 | -0.068664 | 122.2961 | 122.4838 | 61.6333 | -122.2641 | 122.2504 | 122.2824 | 61.6333 | -122.4426
894.2812 | 122.5433 | -61.4273 | 60.9512 | -0.00022891 | -0.053835 | 0.13042 | 0.036664 | 0.033505 | -0.040432 | -0.027164 | 7.627e-05 | -0.018322 | 0.026517 | 0.059834 | -0.025387 | -0.024951 | 60.9924 | -61.2488 | 0.14191 | -61.4868 | 60.8871 | -61.3998 | -61.3358 | 0.091553 | 0.13733 | -61.5738 | 60.8276 | 60.8322 | -61.3449 | -61.5463 | 0.027466 | 0.091553 | -0.064087 | 0.17853 | -0.059509 | -0.15106 | 0.041199 | 0.082397 | -0.11902 | -0.1236 | 61.5189 | -0.14648 | -0.027466 | -0.11902 | 122.3145 | 122.4197 | 61.5692 | -122.287 | 122.2549 | 122.2595 | 61.5646 | -122.4976
896 | 122.58 | -61.4594 | 60.8826 | -0.00022891 | -0.053194 | 0.12658 | 0.029828 | 0.033932 | -0.032742 | -0.026096 | -0.0075532 | -0.012127 | 0.025663 | 0.059193 | -0.01791 | -0.025592 | 60.9329 | -61.3815 | 0.009155 | -61.5875 | 60.8871 | -61.4639 | -61.3998 | 0.027466 | 0.032043 | -61.7981 | 60.8505 | 60.8505 | -61.441 | -61.6058 | -0.004577 | 0.05951 | 0.004578 | 0.07782 | -0.12817 | -0.18768 | 0.050354 | 0.018311 | -0.14648 | -0.032043 | 61.4868 | -0.33875 | -0.19226 | -0.032043 | 122.3465 | 122.3923 | 61.4685 | -122.2824 | 122.3099 | 122.3099 | 61.4914 | -122.4884
897.7969 | 122.5754 | -61.4182 | 60.9238 | -0.00022891 | -0.04999 | 0.12572 | 0.031751 | 0.036495 | -0.032742 | -0.024814 | 0.015335 | -0.012127 | 0.025876 | 0.061115 | -0.018765 | -0.025806 | 60.9604 | -61.3266 | 0.027466 | -61.5601 | 60.91 | -61.441 | -61.3953 | 0.022888 | 0.064087 | -61.7569 | 60.878 | 60.8688 | -61.3678 | -61.5601 | -0.022888 | 0.022888 | -0.013733 | 0.091553 | -0.14191 | -0.1648 | 0.036621 | 0.050354 | -0.14191 | -0.045776 | 61.441 | -0.33875 | -0.19684 | -0.054932 | 122.3282 | 122.3785 | 61.4456 | -122.319 | 122.2961 | 122.287 | 61.4822 | -122.4838
899.5312 | 122.6074 | -61.3541 | 60.9924 | -0.00022891 | -0.053408 | 0.12615 | 0.032605 | 0.035 | -0.033383 | -0.025455 | 0.0077058 | -0.012127 | 0.024381 | 0.061329 | -0.020687 | -0.025592 | 61.0199 | -61.3037 | -0.032043 | -61.5143 | 61.0107 | -61.3815 | -61.3266 | 0.022888 | 0.022888 | -61.6837 | 60.9283 | 60.9421 | -61.3312 | -61.4822 | -0.027466 | 0.027466 | 0.01831 | 0.050354 | -0.16022 | -0.18768 | 0.027465 | 0.022888 | -0.12817 | -0.064087 | 61.377 | -0.32959 | -0.20142 | -0.050354 | 122.3648 | 122.374 | 61.322 | -122.319 | 122.2824 | 122.2961 | 61.377 | -122.4747
901.3125 | 122.5296 | -61.3495 | 61.0703 | -0.0078584 | -0.056826 | 0.12786 | 0.035382 | 0.030728 | -0.042996 | -0.027591 | 0.0077058 | -0.019818 | 0.024808 | 0.056843 | -0.023678 | -0.024738 | 61.1618 | -61.0474 | 0.16937 | -61.3541 | 60.9787 | -61.2854 | -61.2488 | 0.10071 | 0.16479 | -61.4731 | 60.9512 | 60.9467 | -61.2488 | -61.3815 | 0.064087 | 0.10071 | -0.091552 | 0.30212 | -0.004578 | -0.10529 | 0.091553 | 0.10071 | -0.032044 | -0.11902 | 61.4502 | -0.1236 | -0.091552 | -0.1236 | 122.3282 | 122.5113 | 61.5189 | -122.319 | 122.3007 | 122.2961 | 61.5143 | -122.4518
903.0312 | 122.5296 | -61.3724 | 61.0062 | -0.00022891 | -0.055758 | 0.12807 | 0.034955 | 0.034786 | -0.042569 | -0.028232 | -0.015182 | -0.016613 | 0.025022 | 0.057484 | -0.024105 | -0.024738 | 61.0291 | -61.2305 | 0.054932 | -61.4685 | 60.9375 | -61.3266 | -61.2991 | 0.027466 | 0.073242 | -61.6013 | 60.8734 | 60.8826 | -61.3358 | -61.4914 | 0.045776 | 0.073242 | -0.068665 | 0.14191 | -0.096131 | -0.16937 | 0.022888 | 0.036621 | -0.11902 | -0.13275 | 61.3998 | -0.22888 | -0.10986 | -0.1236 | 122.3099 | 122.4014 | 61.4273 | -122.3053 | 122.2458 | 122.2549 | 61.4456 | -122.4976
904.8281 | 122.4792 | -61.4044 | 60.997 | -0.00022891 | -0.051913 | 0.12871 | 0.036878 | 0.034786 | -0.03851 | -0.028873 | 7.627e-05 | -0.016613 | 0.028867 | 0.060474 | -0.025173 | -0.027087 | 61.084 | -61.1572 | 0.17395 | -61.4136 | 60.9055 | -61.3632 | -61.3266 | 0.086975 | 0.15106 | -61.5601 | 60.878 | 60.8688 | -61.29 | -61.4868 | 0.041199 | 0.07782 | -0.091552 | 0.24719 | -0.009155 | -0.086975 | 0.086975 | 0.11444 | -0.082397 | -0.11902 | 61.4914 | -0.15564 | -0.073243 | -0.12817 | 122.3099 | 122.4884 | 61.5784 | -122.3236 | 122.2824 | 122.2733 | 61.5555 | -122.4838
906.5469 | 122.5067 | -61.3586 | 61.0336 | -0.00022891 | -0.057894 | 0.12786 | 0.036237 | 0.034573 | -0.042569 | -0.028232 | 0.0077058 | -0.0164 | 0.026304 | 0.059406 | -0.023678 | -0.027942 | 61.0977 | -61.171 | 0.059509 | -61.4182 | 60.9695 | -61.2991 | -61.2625 | 0.073242 | 0.073242 | -61.5646 | 60.9192 | 60.9055 | -61.2808 | -61.4639 | 0.05951 | 0.096131 | -0.064087 | 0.18768 | -0.059509 | -0.15564 | 0.064087 | 0.07782 | -0.10529 | -0.11444 | 61.4319 | -0.20599 | -0.10071 | -0.12817 | 122.3282 | 122.4564 | 61.4182 | -122.2961 | 122.2778 | 122.2641 | 61.4319 | -122.4976
908.3281 | 122.6166 | -61.3495 | 60.965 | -0.0078584 | -0.050631 | 0.12764 | 0.034314 | 0.032437 | -0.034237 | -0.028446 | 7.627e-05 | -0.015118 | 0.027372 | 0.060261 | -0.02026 | -0.029651 | 61.0336 | -61.2717 | 0.07782 | -61.4639 | 60.997 | -61.3495 | -61.322 | 0.054932 | 0.07782 | -61.6653 | 60.9695 | 60.9146 | -61.3403 | -61.5097 | 0 | 0.027466 | 0.032043 | 0.07782 | -0.11444 | -0.14191 | 0.068664 | 0.009155 | -0.16022 | 0.004577 | 61.4044 | -0.31586 | -0.15564 | -0.050354 | 122.3465 | 122.3831 | 61.4273 | -122.287 | 122.319 | 122.2641 | 61.4273 | -122.4747
910.125 | 122.6028 | -61.3358 | 60.9833 | -0.0078584 | -0.050844 | 0.12658 | 0.036023 | 0.038845 | -0.035733 | -0.025882 | 7.627e-05 | -0.012341 | 0.027158 | 0.060902 | -0.021969 | -0.026874 | 61.0565 | -61.2534 | 0.086975 | -61.4594 | 60.9787 | -61.3449 | -61.3266 | 0.054932 | 0.064087 | -61.6608 | 60.965 | 60.9238 | -61.3037 | -61.5189 | -0.009156 | 0.009155 | -0.004577 | 0.082397 | -0.1236 | -0.13275 | 0.073243 | 0.032043 | -0.18311 | -0.01831 | 61.3907 | -0.32501 | -0.14191 | -0.059509 | 122.3145 | 122.3923 | 61.4227 | -122.3099 | 122.3007 | 122.2595 | 61.3998 | -122.5021
911.9062 | 122.493 | -61.3266 | 61.0611 | -0.0078584 | -0.054049 | 0.12572 | 0.034314 | 0.034146 | -0.040219 | -0.028232 | 7.627e-05 | -0.019177 | 0.026517 | 0.060474 | -0.022396 | -0.02666 | 61.1206 | -61.1252 | 0.064087 | -61.3953 | 60.9512 | -61.2991 | -61.2305 | 0.10986 | 0.11902 | -61.5143 | 60.9238 | 60.9421 | -61.2488 | -61.3998 | 0.027466 | 0.09613 | -0.10986 | 0.20142 | -0.068665 | -0.16479 | 0.059509 | 0.07782 | -0.073242 | -0.13733 | 61.4365 | -0.18768 | -0.11444 | -0.11902 | 122.2778 | 122.4472 | 61.3907 | -122.2916 | 122.2504 | 122.2687 | 61.4456 | -122.4609
913.7031 | 122.5845 | -61.322 | 61.0107 | -0.0078584 | -0.052553 | 0.12316 | 0.031323 | 0.033505 | -0.034665 | -0.026096 | -0.015182 | -0.013623 | 0.028867 | 0.062397 | -0.017056 | -0.027301 | 61.0336 | -61.2717 | -0.022888 | -61.4685 | 61.0245 | -61.3312 | -61.2946 | 0.050354 | 0.041199 | -61.6699 | 60.9695 | 60.9604 | -61.29 | -61.4914 | -0.009156 | 0.027465 | 0.013733 | 0.050354 | -0.14648 | -0.17395 | 0.022888 | 0.032043 | -0.16937 | -0.041199 | 61.3724 | -0.3479 | -0.17853 | -0.050354 | 122.3465 | 122.3557 | 61.2991 | -122.3053 | 122.2916 | 122.2824 | 61.3632 | -122.5021
915.5 | 122.5983 | -61.3129 | 61.0565 | 0.0074006 | -0.058962 | 0.12465 | 0.03346 | 0.036495 | -0.038296 | -0.025669 | 0.015335 | -0.017041 | 0.026304 | 0.060688 | -0.020687 | -0.026019 | 61.1481 | -61.0886 | 0.068665 | -61.3586 | 60.9695 | -61.2854 | -61.2396 | 0.12817 | 0.16937 | -61.5005 | 60.9283 | 60.8963 | -61.2396 | -61.4365 | 0.027466 | 0.073242 | -0.086976 | 0.2243 | -0.045777 | -0.11902 | 0.091552 | 0.073242 | -0.1236 | -0.12817 | 61.441 | -0.18768 | -0.064087 | -0.16022 | 122.2824 | 122.4609 | 61.3815 | -122.2961 | 122.2412 | 122.2092 | 61.4822 | -122.493
917.2031 | 122.493 | -61.2717 | 61.1298 | -0.00022891 | -0.057467 | 0.12828 | 0.03346 | 0.033077 | -0.040432 | -0.026951 | 0.0077058 | -0.015332 | 0.025663 | 0.058552 | -0.021969 | -0.023883 | 61.1252 | -61.0794 | 0.036621 | -61.3678 | 61.0199 | -61.235 | -61.2076 | 0.068665 | 0.073242 | -61.4731 | 61.0016 | 60.9833 | -61.2167 | -61.3861 | 0.036621 | 0.064086 | -0.10986 | 0.19226 | -0.096131 | -0.16022 | -0.004578 | 0.054931 | -0.11444 | -0.12817 | 61.3403 | -0.20142 | -0.086975 | -0.14649 | 122.2916 | 122.3969 | 61.3083 | -122.3373 | 122.2733 | 122.2549 | 61.3449 | -122.5159
919 | 122.6303 | -61.2259 | 61.0886 | 0.0074006 | -0.052981 | 0.12593 | 0.031323 | 0.03265 | -0.034451 | -0.024814 | 7.627e-05 | -0.014904 | 0.025663 | 0.059193 | -0.019192 | -0.028155 | 61.1572 | -61.1069 | 0.013733 | -61.3678 | 61.0474 | -61.2808 | -61.2213 | 0.10986 | 0.14648 | -61.4914 | 60.9879 | 60.9558 | -61.2076 | -61.3678 | -0.054932 | 0.004578 | -0.041199 | 0.11902 | -0.14191 | -0.14648 | 0.068665 | 0.01831 | -0.14191 | -0.10071 | 61.3358 | -0.2655 | -0.1236 | -0.13275 | 122.2733 | 122.3831 | 61.2396 | -122.3099 | 122.2137 | 122.1817 | 61.3724 | -122.4564
920.7812 | 122.6532 | -61.1847 | 61.116 | -0.00022891 | -0.051485 | 0.12636 | 0.033246 | 0.035641 | -0.035305 | -0.02631 | 0.0077058 | -0.014691 | 0.027158 | 0.058979 | -0.019406 | -0.024524 | 61.1481 | -61.1389 | -0.027466 | -61.3678 | 61.1069 | -61.235 | -61.2076 | 0.054932 | 0.054932 | -61.528 | 61.0382 | 61.0199 | -61.1984 | -61.3678 | -0.050354 | -0.022889 | -0.009155 | 0.045776 | -0.18311 | -0.16022 | 0.032043 | -0.013733 | -0.18311 | -0.07782 | 61.2396 | -0.34332 | -0.16022 | -0.096131 | 122.2916 | 122.3328 | 61.1572 | -122.3236 | 122.2229 | 122.2046 | 61.2396 | -122.4838
922.5 | 122.5891 | -61.2076 | 61.1343 | -0.0078584 | -0.054903 | 0.12893 | 0.030896 | 0.033077 | -0.039151 | -0.027378 | 0.0077058 | -0.015118 | 0.024167 | 0.057697 | -0.020901 | -0.026233 | 61.2305 | -61.0016 | 0.073242 | -61.2717 | 61.0519 | -61.1938 | -61.1572 | 0.091553 | 0.15106 | -61.3998 | 61.0016 | 60.997 | -61.1481 | -61.3449 | 0.013733 | 0.050354 | -0.082397 | 0.20599 | -0.064086 | -0.11444 | 0.096131 | 0.05951 | -0.13733 | -0.13275 | 61.2991 | -0.19226 | -0.054931 | -0.13733 | 122.2595 | 122.4381 | 61.2808 | -122.2916 | 122.2092 | 122.2046 | 61.3586 | -122.4792
924.2812 | 122.5342 | -61.171 | 61.2305 | -0.0078584 | -0.058748 | 0.10692 | 0.034528 | 0.035214 | -0.040646 | -0.027805 | -0.0075532 | -0.016186 | 0.023099 | 0.057697 | -0.024319 | -0.024951 | 61.2534 | -60.965 | 0.064087 | -61.2122 | 61.1389 | -61.1206 | -61.084 | 0.059509 | 0.091553 | -61.3449 | 61.116 | 61.084 | -61.0519 | -61.2717 | 0.050354 | 0.086975 | -0.091553 | 0.20599 | -0.041199 | -0.12817 | 0.022888 | 0.11902 | -0.10071 | -0.11444 | 61.2305 | -0.17395 | -0.073243 | -0.14648 | 122.3099 | 122.4243 | 61.235 | -122.3145 | 122.287 | 122.2549 | 61.2625 | -122.5021
926 | 122.6212 | -61.1343 | 61.1847 | -0.00022891 | -0.051058 | 0.12679 | 0.033673 | 0.034573 | -0.036374 | -0.027378 | -0.015182 | -0.012127 | 0.023313 | 0.058338 | -0.019619 | -0.026447 | 61.2717 | -60.9741 | 0.050354 | -61.2442 | 61.1389 | -61.1435 | -61.0931 | 0.10986 | 0.14648 | -61.3678 | 61.0931 | 61.0474 | -61.1206 | -61.2762 | -0.009156 | 0.041198 | -0.045776 | 0.16022 | -0.10986 | -0.15106 | 0.086975 | 0.013733 | -0.14191 | -0.091552 | 61.2442 | -0.23346 | -0.091553 | -0.13733 | 122.2733 | 122.406 | 61.1847 | -122.2778 | 122.2275 | 122.1817 | 61.2808 | -122.4609
927.7812 | 122.5983 | -61.0931 | 61.2442 | -0.00022891 | -0.05469 | 0.12722 | 0.032819 | 0.036495 | -0.034024 | -0.025455 | 7.627e-05 | -0.014477 | 0.028013 | 0.059193 | -0.019619 | -0.025592 | 61.3495 | -60.91 | 0.07782 | -61.1664 | 61.1755 | -61.084 | -61.0519 | 0.11444 | 0.14648 | -61.3266 | 61.1435 | 61.0977 | -61.0565 | -61.2396 | 0.009156 | 0.041199 | -0.068665 | 0.18311 | -0.073242 | -0.11444 | 0.10529 | 0.036621 | -0.14648 | -0.10071 | 61.2076 | -0.23346 | -0.086975 | -0.14648 | 122.2687 | 122.4426 | 61.171 | -122.2961 | 122.2366 | 122.1909 | 61.2396 | -122.4838
929.5 | 122.6257 | -61.0565 | 61.2579 | -0.00022891 | -0.052126 | 0.12551 | 0.034314 | 0.033932 | -0.034237 | -0.025455 | 7.627e-05 | -0.012982 | 0.027372 | 0.056629 | -0.021114 | -0.025165 | 61.2946 | -60.9695 | 0.11902 | -61.1847 | 61.2442 | -61.0703 | -61.0382 | 0.086975 | 0.11444 | -61.3541 | 61.2076 | 61.171 | -61.0382 | -61.2396 | -0.013732 | 0.018311 | -0.013733 | 0.086976 | -0.12817 | -0.14648 | 0.036621 | 0.018311 | -0.1831 | -0.050354 | 61.1435 | -0.29755 | -0.11444 | -0.086976 | 122.3007 | 122.3511 | 61.1755 | -122.2961 | 122.2641 | 122.2275 | 61.171 | -122.4976
931.2969 | 122.4838 | -61.0703 | 61.3174 | -0.00022891 | -0.055331 | 0.12764 | 0.03645 | 0.035855 | -0.037655 | -0.026737 | 7.627e-05 | -0.015973 | 0.028653 | 0.058552 | -0.023892 | -0.025806 | 61.3632 | -60.8322 | 0.16479 | -61.1206 | 61.2396 | -61.0519 | -61.0016 | 0.086975 | 0.11444 | -61.3083 | 61.2213 | 61.1847 | -61.0062 | -61.2076 | 0.01831 | 0.068664 | -0.07782 | 0.23804 | -0.050354 | -0.11902 | 0.045776 | 0.064086 | -0.13733 | -0.096131 | 61.1572 | -0.23804 | -0.10071 | -0.13275 | 122.3099 | 122.4335 | 61.235 | -122.319 | 122.2916 | 122.2549 | 61.1847 | -122.525
933.0312 | 122.6074 | -61.0565 | 61.29 | 0.0074006 | -0.055117 | 0.12764 | 0.036237 | 0.034359 | -0.035946 | -0.026737 | -0.0075532 | -0.013836 | 0.027372 | 0.062397 | -0.022823 | -0.02666 | 61.3449 | -60.9238 | 0.10529 | -61.1435 | 61.322 | -61.0336 | -61.0107 | 0.082397 | 0.064087 | -61.322 | 61.2717 | 61.2579 | -61.0016 | -61.1572 | 0.022889 | 0.045777 | 0.032043 | 0.13275 | -0.086975 | -0.13275 | 0.054932 | 0.054932 | -0.10071 | -0.018311 | 61.1389 | -0.2655 | -0.16479 | -0.032043 | 122.3785 | 122.4014 | 61.1618 | -122.3007 | 122.3282 | 122.3145 | 61.1206 | -122.4472
934.8125 | 122.5754 | -61.0336 | 61.322 | -0.00022891 | -0.052767 | 0.12593 | 0.034741 | 0.036282 | -0.035092 | -0.025669 | 7.627e-05 | -0.010205 | 0.027158 | 0.059834 | -0.02026 | -0.025806 | 61.3266 | -60.9512 | 0.027466 | -61.1572 | 61.3129 | -61.0428 | -61.0016 | 0.050354 | 0.050354 | -61.3678 | 61.2579 | 61.2213 | -61.0153 | -61.1893 | -0.009156 | 0.032043 | -0.009155 | 0.082397 | -0.1236 | -0.15564 | 0.004578 | 0.01831 | -0.15564 | -0.064086 | 61.084 | -0.33417 | -0.17853 | -0.10071 | 122.3465 | 122.3602 | 61.0611 | -122.3236 | 122.2916 | 122.2549 | 61.084 | -122.5113
936.5938 | 122.6532 | -61.0016 | 61.2991 | 0.0074006 | -0.053408 | 0.127 | 0.033673 | 0.035 | -0.037014 | -0.025669 | -0.015182 | -0.015759 | 0.027158 | 0.060902 | -0.022396 | -0.026019 | 61.3403 | -60.9238 | -0.013733 | -61.1526 | 61.2946 | -61.0291 | -60.9787 | 0.073242 | 0.082397 | -61.2854 | 61.2442 | 61.2167 | -60.9924 | -61.1343 | -0.027466 | 0.022888 | -0.004577 | 0.07782 | -0.15106 | -0.17395 | 0.041199 | 0.009155 | -0.13275 | -0.054931 | 61.0748 | -0.28381 | -0.15106 | -0.082397 | 122.2961 | 122.3419 | 60.9879 | -122.2778 | 122.2458 | 122.2183 | 61.084 | -122.4335
938.3125 | 122.5342 | -60.9467 | 61.409 | 0.0074006 | -0.054049 | 0.12679 | 0.035169 | 0.032223 | -0.042782 | -0.02866 | 7.627e-05 | -0.016827 | 0.025022 | 0.05727 | -0.025601 | -0.025592 | 61.4273 | -60.7636 | 0.064087 | -61.0565 | 61.3449 | -60.9329 | -60.878 | 0.050354 | 0.09613 | -61.1526 | 61.322 | 61.2808 | -60.878 | -61.0748 | 0.013733 | 0.068664 | -0.064087 | 0.1831 | -0.10986 | -0.17853 | 0.01831 | 0.068664 | -0.12817 | -0.086976 | 60.997 | -0.20599 | -0.07782 | -0.12817 | 122.2916 | 122.374 | 61.0107 | -122.287 | 122.2687 | 122.2275 | 61.0428 | -122.4838
940.0938 | 122.5433 | -60.9146 | 61.4548 | 0.0074006 | -0.054903 | 0.12743 | 0.036237 | 0.036068 | -0.042569 | -0.026737 | -0.015182 | -0.017041 | 0.026944 | 0.059834 | -0.026028 | -0.027087 | 61.5417 | -60.6583 | 0.15564 | -60.965 | 61.3632 | -60.8963 | -60.8505 | 0.14191 | 0.16937 | -61.0519 | 61.3129 | 61.3037 | -60.8551 | -61.0291 | 0.018311 | 0.064087 | -0.091553 | 0.25635 | -0.050354 | -0.11444 | 0.086975 | 0.059509 | -0.11444 | -0.14191 | 61.0565 | -0.13733 | -0.022888 | -0.15106 | 122.2778 | 122.4564 | 61.0703 | -122.3053 | 122.2275 | 122.2183 | 61.084 | -122.4838
941.8281 | 122.5845 | -60.878 | 61.4822 | -0.00022891 | -0.05469 | 0.12508 | 0.032605 | 0.033718 | -0.037228 | -0.02396 | 0.0077058 | -0.014691 | 0.026304 | 0.061543 | -0.021969 | -0.027942 | 61.5829 | -60.6857 | 0.059509 | -60.9512 | 61.3815 | -60.878 | -60.8185 | 0.11902 | 0.14648 | -61.084 | 61.3586 | 61.3266 | -60.8414 | -61.0107 | 0 | 0.05951 | -0.10071 | 0.19226 | -0.073242 | -0.13275 | 0.10071 | 0.036621 | -0.13275 | -0.1236 | 60.997 | -0.20599 | -0.073242 | -0.15564 | 122.2595 | 122.4609 | 60.9375 | -122.3007 | 122.2366 | 122.2046 | 61.0245 | -122.493
943.6094 | 122.5983 | -60.8002 | 61.5189 | 0.0074006 | -0.051699 | 0.12828 | 0.034101 | 0.034786 | -0.035946 | -0.024601 | 7.627e-05 | -0.013195 | 0.026731 | 0.057484 | -0.020901 | -0.027728 | 61.5784 | -60.7086 | 0.091553 | -60.9467 | 61.5372 | -60.8414 | -60.8093 | 0.059509 | 0.082397 | -61.1206 | 61.4914 | 61.441 | -60.7956 | -60.9604 | -0.041199 | -0.009155 | 0.01831 | 0.091553 | -0.14648 | -0.13733 | 0.059509 | 0.004578 | -0.16022 | -0.027466 | 60.8597 | -0.32043 | -0.16022 | -0.07782 | 122.3373 | 122.3785 | 60.8917 | -122.3282 | 122.2916 | 122.2412 | 60.8826 | -122.4792
945.3906 | 122.4884 | -60.8047 | 61.5738 | -0.00022891 | -0.051058 | 0.12636 | 0.037518 | 0.033932 | -0.038937 | -0.026951 | -0.0075532 | -0.014264 | 0.028653 | 0.05962 | -0.023251 | -0.024738 | 61.5967 | -60.6628 | 0.11444 | -60.9009 | 61.5372 | -60.7864 | -60.7544 | 0.068665 | 0.068665 | -61.0794 | 61.5005 | 61.4731 | -60.7727 | -60.9421 | 0.018311 | 0.050354 | -0.036622 | 0.14191 | -0.09613 | -0.14648 | 0.022888 | 0.032044 | -0.13733 | -0.073243 | 60.8734 | -0.27466 | -0.13733 | -0.10071 | 122.3419 | 122.4014 | 60.9192 | -122.3282 | 122.3053 | 122.2778 | 60.8734 | -122.5159
947.1562 | 122.5021 | -60.8002 | 61.5738 | 0.0074006 | -0.051272 | 0.12679 | 0.037946 | 0.036282 | -0.037228 | -0.026096 | -0.0075532 | -0.017468 | 0.029722 | 0.061543 | -0.025387 | -0.027728 | 61.6058 | -60.6491 | 0.091553 | -60.9192 | 61.5417 | -60.8093 | -60.7407 | 0.059509 | 0.073242 | -61.0748 | 61.4822 | 61.4639 | -60.759 | -60.9512 | -0.009155 | 0.059509 | -0.032044 | 0.15106 | -0.11902 | -0.17853 | 0.032043 | 0.041199 | -0.15106 | -0.091553 | 60.8597 | -0.27466 | -0.1236 | -0.10986 | 122.3419 | 122.406 | 60.8917 | -122.3145 | 122.2824 | 122.2641 | 60.8734 | -122.525
948.875 | 122.5937 | -60.7636 | 61.5875 | -0.0078584 | -0.053408 | 0.12487 | 0.031537 | 0.035 | -0.034665 | -0.026737 | -0.0075532 | -0.012341 | 0.026517 | 0.062397 | -0.018978 | -0.026874 | 61.5967 | -60.6812 | -0.032043 | -60.9055 | 61.5692 | -60.8002 | -60.7224 | 0.036621 | 0.027466 | -61.0794 | 61.5326 | 61.5005 | -60.7178 | -60.9146 | -0.036621 | 0.041199 | -0.01831 | 0.082398 | -0.14191 | -0.18311 | 0.009156 | 0.045777 | -0.15106 | -0.054931 | 60.8002 | -0.31586 | -0.1648 | -0.086975 | 122.3328 | 122.3602 | 60.7315 | -122.3099 | 122.2961 | 122.2641 | 60.791 | -122.5021
950.6562 | 122.5662 | -60.6628 | 61.6699 | -0.00022891 | -0.051485 | 0.12487 | 0.034741 | 0.033291 | -0.035305 | -0.023319 | -0.0075532 | -0.011914 | 0.028226 | 0.061115 | -0.021328 | -0.025165 | 61.7249 | -60.5713 | 0.032043 | -60.8047 | 61.647 | -60.672 | -60.6308 | 0.073242 | 0.082397 | -60.9833 | 61.6241 | 61.5967 | -60.6354 | -60.8139 | -0.009155 | 0.032044 | -0.022888 | 0.091553 | -0.14191 | -0.17395 | 0.054932 | 0.027466 | -0.15106 | -0.045776 | 60.7361 | -0.32043 | -0.16937 | -0.073242 | 122.3099 | 122.3877 | 60.6949 | -122.3007 | 122.287 | 122.2595 | 60.7452 | -122.4838
952.4375 | 122.5937 | -60.5621 | 61.7432 | -0.00022891 | -0.050631 | 0.12572 | 0.039227 | 0.034573 | -0.038296 | -0.027378 | -0.0075532 | -0.015118 | 0.028226 | 0.062397 | -0.021542 | -0.025592 | 61.7981 | -60.4752 | 0.091553 | -60.6995 | 61.7752 | -60.5896 | -60.5392 | 0.068665 | 0.10071 | -60.878 | 61.7249 | 61.7157 | -60.5438 | -60.7361 | -0.027466 | 0.022888 | 0.032044 | 0.086975 | -0.13733 | -0.16022 | 0.054932 | 0.018311 | -0.17395 | -0.01831 | 60.6308 | -0.31586 | -0.14191 | -0.027466 | 122.3373 | 122.3602 | 60.6537 | -122.2824 | 122.287 | 122.2778 | 60.6628 | -122.4792
954.2188 | 122.6257 | -60.585 | 61.7569 | -0.00022891 | -0.052553 | 0.12658 | 0.03346 | 0.034573 | -0.036587 | -0.025669 | 0.0077058 | -0.011914 | 0.027585 | 0.060902 | -0.021755 | -0.024738 | 61.7798 | -60.466 | 0.11902 | -60.6903 | 61.7798 | -60.5896 | -60.553 | 0.09613 | 0.12817 | -60.8643 | 61.702 | 61.7065 | -60.5667 | -60.7498 | -0.004578 | 0.032043 | 0.022888 | 0.11902 | -0.10529 | -0.13733 | 0.022888 | 0.018311 | -0.16479 | -0.054932 | 60.6812 | -0.27924 | -0.11444 | -0.050354 | 122.3648 | 122.3648 | 60.704 | -122.3099 | 122.287 | 122.2916 | 60.7132 | -122.5067
955.9688 | 122.5479 | -60.5255 | 61.8256 | -0.0078584 | -0.053622 | 0.13042 | 0.034314 | 0.033077 | -0.039578 | -0.027591 | 7.627e-05 | -0.012555 | 0.029294 | 0.060902 | -0.023464 | -0.024738 | 61.853 | -60.3973 | 0.10986 | -60.6445 | 61.8256 | -60.498 | -60.4706 | 0.054932 | 0.082397 | -60.8231 | 61.7889 | 61.7706 | -60.4889 | -60.6445 | 0.027466 | 0.054932 | 0 | 0.12817 | -0.11902 | -0.17395 | 0.027465 | 0.036621 | -0.11902 | -0.036622 | 60.5804 | -0.29755 | -0.17853 | -0.054932 | 122.3511 | 122.3785 | 60.6354 | -122.2961 | 122.3145 | 122.2961 | 60.6079 | -122.4701
957.7656 | 122.4976 | -60.5026 | 61.8851 | -0.00022891 | -0.054903 | 0.12465 | 0.033673 | 0.035427 | -0.039792 | -0.027805 | 0.0077058 | -0.015973 | 0.026944 | 0.05962 | -0.024105 | -0.025378 | 61.9308 | -60.3104 | 0.14191 | -60.5804 | 61.8622 | -60.4523 | -60.434 | 0.064087 | 0.073242 | -60.7498 | 61.8393 | 61.8073 | -60.4523 | -60.5988 | 0.050354 | 0.068665 | -0.022888 | 0.19226 | -0.077819 | -0.14648 | 0.045776 | 0.050354 | -0.09613 | -0.045777 | 60.5667 | -0.24719 | -0.15106 | -0.07782 | 122.3648 | 122.4335 | 60.6445 | -122.319 | 122.3419 | 122.3099 | 60.5759 | -122.4838
959.5625 | 122.5159 | -60.4431 | 61.9217 | -0.0078584 | -0.051913 | 0.12615 | 0.038587 | 0.035855 | -0.04321 | -0.027805 | 7.627e-05 | -0.020245 | 0.025449 | 0.057911 | -0.02496 | -0.024951 | 62.027 | -60.1639 | 0.19226 | -60.466 | 61.8851 | -60.4019 | -60.3607 | 0.1236 | 0.17395 | -60.5759 | 61.8027 | 61.821 | -60.3882 | -60.5484 | 0.041198 | 0.082397 | -0.036621 | 0.27924 | -0.022888 | -0.10529 | 0.10529 | 0.054931 | -0.10529 | -0.11902 | 60.5667 | -0.13275 | -0.027466 | -0.10071 | 122.3282 | 122.4701 | 60.6354 | -122.2824 | 122.2458 | 122.2641 | 60.6171 | -122.4701
961.2812 | 122.5113 | -60.466 | 61.972 | -0.0078584 | -0.057253 | 0.13042 | 0.031323 | 0.033718 | -0.042355 | -0.02866 | 7.627e-05 | -0.016827 | 0.023954 | 0.058979 | -0.021114 | -0.02666 | 61.9492 | -60.2829 | 0.068665 | -60.5347 | 61.8622 | -60.434 | -60.3516 | 0.045776 | 0.059509 | -60.6583 | 61.821 | 61.8073 | -60.3882 | -60.5759 | 0.032043 | 0.11444 | -0.10986 | 0.1831 | -0.068665 | -0.18311 | -0.022888 | 0.077819 | -0.10986 | -0.15106 | 60.5118 | -0.19226 | -0.082397 | -0.16479 | 122.3282 | 122.4152 | 60.5347 | -122.3236 | 122.287 | 122.2733 | 60.5255 | -122.5479
963.0781 | 122.5388 | -60.3745 | 62.0087 | -0.00022891 | -0.054262 | 0.12636 | 0.036664 | 0.034359 | -0.042355 | -0.029728 | -0.0075532 | -0.017468 | 0.026944 | 0.058338 | -0.023464 | -0.027301 | 62.0361 | -60.1822 | 0.07782 | -60.4431 | 61.9446 | -60.347 | -60.3149 | 0.059509 | 0.086975 | -60.5667 | 61.9034 | 61.8668 | -60.3104 | -60.4797 | 0.027466 | 0.05951 | -0.064087 | 0.19226 | -0.068664 | -0.12817 | 0.027466 | 0.064087 | -0.10529 | -0.10529 | 60.434 | -0.19226 | -0.086975 | -0.14191 | 122.319 | 122.4106 | 60.4523 | -122.3236 | 122.2778 | 122.2412 | 60.4614 | -122.4884
964.8594 | 122.644 | -60.3195 | 61.9858 | -0.00022891 | -0.052767 | 0.12359 | 0.032605 | 0.032223 | -0.033596 | -0.026096 | 7.627e-05 | -0.0117 | 0.026731 | 0.063679 | -0.020474 | -0.026233 | 62.0316 | -60.2554 | -0.009155 | -60.498 | 62.027 | -60.3333 | -60.3333 | 0.068665 | 0.050354 | -60.6537 | 61.9583 | 61.9263 | -60.3012 | -60.4752 | -0.013733 | -0.013733 | 0.041199 | 0.064087 | -0.17853 | -0.16479 | 0.045776 | 0.018311 | -0.15564 | -0.027466 | 60.3882 | -0.33417 | -0.17853 | -0.059509 | 122.3465 | 122.3511 | 60.3104 | -122.319 | 122.2778 | 122.2458 | 60.3699 | -122.4609
966.6562 | 122.5891 | -60.3195 | 62.0087 | -0.00022891 | -0.052553 | 0.12636 | 0.032178 | 0.035427 | -0.032956 | -0.02631 | 0.015335 | -0.012982 | 0.027372 | 0.059193 | -0.018124 | -0.02666 | 62.0178 | -60.2875 | 0 | -60.4843 | 62.027 | -60.347 | -60.3104 | 0.045776 | 0.041199 | -60.6674 | 61.9858 | 61.9125 | -60.3241 | -60.4797 | -0.027466 | 0.009155 | 0.018311 | 0.032043 | -0.16479 | -0.17395 | 0.009155 | -0.004578 | -0.16022 | -0.022888 | 60.3653 | -0.3479 | -0.18768 | -0.09613 | 122.3465 | 122.3373 | 60.3195 | -122.319 | 122.3053 | 122.2321 | 60.3607 | -122.4884
968.4375 | 122.6303 | -60.2921 | 62.0132 | -0.00022891 | -0.051913 | 0.12529 | 0.035596 | 0.036923 | -0.035733 | -0.024601 | -0.0075532 | -0.01405 | 0.026517 | 0.058766 | -0.02026 | -0.026019 | 62.1185 | -60.141 | 0.12817 | -60.3928 | 62.027 | -60.3149 | -60.2783 | 0.10986 | 0.12817 | -60.5621 | 61.9904 | 61.972 | -60.2692 | -60.434 | -0.022888 | 0.013733 | 0.013733 | 0.15106 | -0.10071 | -0.11444 | 0.10529 | 0.022888 | -0.14191 | -0.022889 | 60.4019 | -0.27008 | -0.12817 | -0.041199 | 122.319 | 122.4106 | 60.4202 | -122.2916 | 122.2824 | 122.2641 | 60.4202 | -122.4472
970.1406 | 122.58 | -60.2646 | 62.0453 | 0.0074006 | -0.05234 | 0.12593 | 0.033032 | 0.036495 | -0.035305 | -0.025455 | 0.0077058 | -0.013195 | 0.027585 | 0.062611 | -0.019406 | -0.025378 | 62.1231 | -60.141 | 0.086975 | -60.4019 | 62.0453 | -60.2829 | -60.2417 | 0.07782 | 0.091553 | -60.5942 | 61.9995 | 62.0178 | -60.2509 | -60.4431 | -0.018311 | 0.022888 | 0 | 0.1236 | -0.13733 | -0.16022 | 0.07782 | 0.013733 | -0.17853 | -0.045776 | 60.3424 | -0.32959 | -0.15106 | -0.027466 | 122.3099 | 122.3877 | 60.3516 | -122.287 | 122.2641 | 122.2824 | 60.3561 | -122.4884
971.9375 | 122.58 | -60.2646 | 62.0636 | -0.0078584 | -0.053835 | 0.12487 | 0.032605 | 0.033932 | -0.037869 | -0.02396 | 7.627e-05 | -0.012555 | 0.02844 | 0.05962 | -0.020046 | -0.025592 | 62.1506 | -60.0906 | 0.13275 | -60.3607 | 62.059 | -60.26 | -60.2005 | 0.13275 | 0.14191 | -60.5255 | 61.9904 | 62.0041 | -60.2417 | -60.4065 | 0.004577 | 0.064087 | -0.004578 | 0.17395 | -0.096131 | -0.16022 | 0.086975 | 0.022888 | -0.14191 | -0.073243 | 60.3973 | -0.26093 | -0.11902 | -0.05951 | 122.3236 | 122.4152 | 60.3973 | -122.2641 | 122.2549 | 122.2687 | 60.4065 | -122.4701
973.7344 | 122.5754 | -60.1364 | 62.1872 | -0.00022891 | -0.050417 | 0.12593 | 0.034955 | 0.034786 | -0.036374 | -0.024814 | 7.627e-05 | -0.011059 | 0.026731 | 0.060261 | -0.018124 | -0.025378 | 62.2192 | -60.0311 | 0.068665 | -60.2783 | 62.1597 | -60.1593 | -60.1135 | 0.068665 | 0.086975 | -60.4706 | 62.1552 | 62.1231 | -60.1135 | -60.3149 | -0.022888 | 0.022889 | -0.027466 | 0.10529 | -0.14191 | -0.16479 | 0.032043 | 0.022889 | -0.17853 | -0.032044 | 60.2051 | -0.33417 | -0.15564 | -0.064087 | 122.2961 | 122.3557 | 60.2051 | -122.3007 | 122.2916 | 122.2595 | 60.2234 | -122.5021
975.4531 | 122.5754 | -60.0403 | 62.2925 | -0.00022891 | -0.051699 | 0.12615 | 0.036023 | 0.035214 | -0.040005 | -0.026523 | 7.627e-05 | -0.013409 | 0.029722 | 0.057484 | -0.02261 | -0.023669 | 62.2971 | -59.9075 | 0.11902 | -60.1593 | 62.2787 | -60.0403 | -60.0357 | 0.054932 | 0.082397 | -60.3424 | 62.2742 | 62.2467 | -60.0266 | -60.2051 | 0 | 0.004577 | -0.013732 | 0.13275 | -0.11902 | -0.1236 | 0.004578 | 0.013733 | -0.16479 | -0.01831 | 60.0952 | -0.30212 | -0.13733 | -0.045776 | 122.319 | 122.3373 | 60.1593 | -122.3282 | 122.3145 | 122.287 | 60.1227 | -122.4976
977.2344 | 122.6349 | -60.022 | 62.3199 | -0.00022891 | -0.052767 | 0.12658 | 0.035382 | 0.03735 | -0.039364 | -0.025882 | 0.0077058 | -0.011486 | 0.023954 | 0.060902 | -0.021755 | -0.024097 | 62.3016 | -59.9304 | -0.027466 | -60.1776 | 62.3062 | -60.0311 | -60.0037 | 0.045776 | 0.059509 | -60.3287 | 62.2696 | 62.2284 | -60.0082 | -60.1868 | -0.009155 | 0.018311 | -0.013733 | 0.091553 | -0.15564 | -0.17395 | -0.01831 | 0.013733 | -0.16479 | -0.050354 | 60.0677 | -0.3067 | -0.14191 | -0.091552 | 122.3282 | 122.3236 | 59.9945 | -122.3236 | 122.2916 | 122.2504 | 60.0815 | -122.5067
978.9688 | 122.644 | -59.9945 | 62.3337 | -0.00022891 | -0.055331 | 0.12359 | 0.036878 | 0.033932 | -0.038083 | -0.028019 | -0.015182 | -0.012982 | 0.026304 | 0.059834 | -0.021755 | -0.02431 | 62.352 | -59.903 | 0.004578 | -60.1364 | 62.3062 | -59.9991 | -59.9579 | 0.082397 | 0.09613 | -60.26 | 62.2604 | 62.2513 | -59.9487 | -60.1364 | -0.004577 | 0.036621 | -0.027466 | 0.091553 | -0.14191 | -0.17853 | 0.018311 | 0.045777 | -0.14191 | -0.073242 | 60.0769 | -0.2655 | -0.1236 | -0.082397 | 122.3007 | 122.3465 | 59.9991 | -122.2916 | 122.2549 | 122.2458 | 60.0906 | -122.4701
980.7656 | 122.5754 | -59.9579 | 62.3932 | -0.0078584 | -0.052981 | 0.12551 | 0.032178 | 0.035 | -0.036587 | -0.029087 | -0.0075532 | -0.015759 | 0.027585 | 0.063252 | -0.019833 | -0.02431 | 62.3566 | -59.8984 | 0.013733 | -60.1181 | 62.3474 | -59.9762 | -59.935 | 0.027466 | 0.041199 | -60.3333 | 62.3154 | 62.3062 | -59.9213 | -60.1273 | -0.01831 | 0.022888 | -0.045776 | 0.05951 | -0.16022 | -0.1831 | -0.036621 | 0.036621 | -0.16937 | -0.077819 | 59.9854 | -0.37537 | -0.20599 | -0.086975 | 122.3053 | 122.3145 | 59.9716 | -122.3282 | 122.2733 | 122.2641 | 59.9991 | -122.5204
982.5625 | 122.5433 | -60.022 | 62.3703 | -0.0078584 | -0.054903 | 0.12743 | 0.037305 | 0.036282 | -0.0462 | -0.02866 | -0.0075532 | -0.018322 | 0.029081 | 0.057484 | -0.025387 | -0.023029 | 62.4115 | -59.7519 | 0.12817 | -60.0494 | 62.2879 | -59.967 | -59.9213 | 0.11444 | 0.13733 | -60.1685 | 62.2421 | 62.2421 | -59.9442 | -60.1227 | 0.054932 | 0.10071 | -0.082397 | 0.27008 | -0.027465 | -0.12817 | 0.041199 | 0.07782 | -0.10071 | -0.12817 | 60.1364 | -0.14648 | -0.045776 | -0.12817 | 122.3099 | 122.4335 | 60.1501 | -122.2916 | 122.2641 | 122.2641 | 60.1593 | -122.493
984.3594 | 122.6257 | -59.8663 | 62.4252 | -0.015487 | -0.049349 | 0.12615 | 0.036023 | 0.035214 | -0.036801 | -0.027378 | 0.0077058 | -0.013623 | 0.028653 | 0.060047 | -0.021328 | -0.025806 | 62.4619 | -59.7656 | 0.10986 | -59.9945 | 62.4298 | -59.9121 | -59.8755 | 0.10071 | 0.11902 | -60.1822 | 62.3795 | 62.352 | -59.8801 | -60.054 | -0.045776 | -0.009155 | 0.004578 | 0.10071 | -0.12817 | -0.11902 | 0.036621 | -0.013733 | -0.18768 | -0.045776 | 59.967 | -0.31586 | -0.12817 | -0.073242 | 122.2961 | 122.3282 | 59.9762 | -122.3007 | 122.2458 | 122.2183 | 59.9854 | -122.4792
986.0625 | 122.612 | -59.9213 | 62.384 | -0.0078584 | -0.053622 | 0.12529 | 0.032178 | 0.036709 | -0.036374 | -0.026523 | 7.627e-05 | -0.017468 | 0.026731 | 0.059406 | -0.02026 | -0.026233 | 62.4664 | -59.7473 | 0.059509 | -60.0311 | 62.3474 | -59.9258 | -59.8709 | 0.1236 | 0.14191 | -60.1639 | 62.3016 | 62.2787 | -59.8846 | -60.054 | -0.004577 | 0.050354 | -0.036621 | 0.17395 | -0.10986 | -0.16022 | 0.082398 | 0.036621 | -0.13275 | -0.082397 | 60.0449 | -0.24261 | -0.10986 | -0.10529 | 122.2687 | 122.3877 | 59.9808 | -122.2549 | 122.2229 | 122.2 | 60.0632 | -122.438
987.8438 | 122.5021 | -59.8251 | 62.5351 | -0.00022891 | -0.051699 | 0.12935 | 0.036237 | 0.035 | -0.041714 | -0.027805 | -0.015182 | -0.017682 | 0.026731 | 0.057911 | -0.02261 | -0.025806 | 62.6175 | -59.5459 | 0.19684 | -59.8709 | 62.4619 | -59.7794 | -59.7427 | 0.14191 | 0.16937 | -59.9945 | 62.4252 | 62.4069 | -59.7382 | -59.9487 | 0.045776 | 0.082397 | -0.073242 | 0.27924 | -0.045777 | -0.12817 | 0.082398 | 0.086975 | -0.1236 | -0.10986 | 59.967 | -0.16937 | -0.045777 | -0.12817 | 122.287 | 122.4426 | 60.022 | -122.2778 | 122.2504 | 122.2321 | 59.9945 | -122.4838
989.6406 | 122.5388 | -59.8114 | 62.5809 | -0.00022891 | -0.054476 | 0.12465 | 0.037091 | 0.033077 | -0.041928 | -0.026951 | 0.0077058 | -0.018322 | 0.02609 | 0.05962 | -0.02496 | -0.026874 | 62.5854 | -59.6237 | 0.086975 | -59.8801 | 62.5305 | -59.7794 | -59.729 | 0.086975 | 0.09613 | -59.9945 | 62.4573 | 62.471 | -59.7198 | -59.8938 | 0.032043 | 0.082397 | -0.050354 | 0.18768 | -0.068665 | -0.15106 | 0.004577 | 0.091552 | -0.082398 | -0.1236 | 59.8984 | -0.18311 | -0.10071 | -0.10986 | 122.3419 | 122.3969 | 59.8984 | -122.3099 | 122.2687 | 122.2824 | 59.9075 | -122.4747
991.3594 | 122.612 | -59.7565 | 62.5763 | -0.0078584 | -0.053835 | 0.12465 | 0.03111 | 0.033718 | -0.037014 | -0.02631 | -0.015182 | -0.014264 | 0.026304 | 0.060688 | -0.020474 | -0.028369 | 62.7045 | -59.5413 | 0.07782 | -59.8068 | 62.5351 | -59.7427 | -59.6878 | 0.12817 | 0.13275 | -59.9716 | 62.4664 | 62.439 | -59.729 | -59.8434 | 0.013733 | 0.068665 | -0.041199 | 0.21515 | -0.050354 | -0.11902 | 0.12817 | 0.027466 | -0.086975 | -0.10986 | 59.8846 | -0.21515 | -0.12817 | -0.13733 | 122.2916 | 122.4609 | 59.8343 | -122.2641 | 122.2229 | 122.1954 | 59.8892 | -122.4197
993.1562 | 122.5204 | -59.729 | 62.6129 | -0.00022891 | -0.051913 | 0.12828 | 0.037732 | 0.034146 | -0.042141 | -0.028019 | 7.627e-05 | -0.01875 | 0.027372 | 0.059193 | -0.023251 | -0.028369 | 62.7319 | -59.4269 | 0.21973 | -59.7702 | 62.5351 | -59.7015 | -59.6741 | 0.16022 | 0.19684 | -59.8938 | 62.4985 | 62.4893 | -59.6649 | -59.8343 | 0.027466 | 0.054932 | -0.07782 | 0.30212 | -0.041199 | -0.096131 | 0.11902 | 0.064087 | -0.10529 | -0.11444 | 59.8892 | -0.16479 | -0.059509 | -0.1236 | 122.2641 | 122.4609 | 59.9487 | -122.287 | 122.2275 | 122.2183 | 59.9258 | -122.4472
994.9531 | 122.5021 | -59.6695 | 62.7365 | -0.00022891 | -0.052126 | 0.12743 | 0.032178 | 0.031582 | -0.037442 | -0.024387 | 7.627e-05 | -0.015545 | 0.026731 | 0.05962 | -0.022183 | -0.027728 | 62.764 | -59.4177 | 0.09613 | -59.7244 | 62.5992 | -59.6512 | -59.6146 | 0.14191 | 0.14191 | -59.8663 | 62.5717 | 62.5397 | -59.6146 | -59.7931 | 0.018311 | 0.054932 | -0.13733 | 0.25177 | -0.054931 | -0.10986 | 0.027466 | 0.054932 | -0.1236 | -0.16479 | 59.8114 | -0.19684 | -0.073242 | -0.19684 | 122.2687 | 122.4335 | 59.7656 | -122.3511 | 122.2412 | 122.2092 | 59.8114 | -122.5296
996.6875 | 122.5891 | -59.6832 | 62.6404 | -0.0078584 | -0.055544 | 0.12615 | 0.031964 | 0.033291 | -0.03616 | -0.025242 | 7.627e-05 | -0.014264 | 0.025876 | 0.058125 | -0.018551 | -0.026233 | 62.7731 | -59.4452 | 0.064087 | -59.7427 | 62.59 | -59.7015 | -59.6146 | 0.1236 | 0.13275 | -59.8755 | 62.5442 | 62.5031 | -59.6329 | -59.8068 | -0.01831 | 0.068665 | -0.050354 | 0.23804 | -0.059509 | -0.12817 | 0.13275 | 0.050354 | -0.1236 | -0.096131 | 59.8068 | -0.19226 | -0.068664 | -0.13733 | 122.2733 | 122.4564 | 59.7473 | -122.2549 | 122.2275 | 122.1863 | 59.816 | -122.4472
998.4844 | 122.58 | -59.523 | 62.7914 | -0.00022891 | -0.050631 | 0.12722 | 0.032605 | 0.033932 | -0.032315 | -0.026737 | -0.0075532 | -0.010846 | 0.027158 | 0.058338 | -0.020046 | -0.027728 | 62.8555 | -59.3536 | 0.10986 | -59.6603 | 62.7686 | -59.5551 | -59.5413 | 0.13733 | 0.12817 | -59.8663 | 62.7182 | 62.6907 | -59.5505 | -59.7061 | -0.032044 | -0.018311 | -0.022888 | 0.16937 | -0.13733 | -0.11902 | 0.064087 | -0.027466 | -0.18311 | -0.073242 | 59.6603 | -0.34332 | -0.16022 | -0.10071 | 122.2916 | 122.3785 | 59.6329 | -122.3328 | 122.2412 | 122.2137 | 59.6512 | -122.4976
1000.2656 | 122.525 | -59.436 | 62.9425 | -0.0078584 | -0.058108 | 0.13042 | 0.031751 | 0.031796 | -0.044064 | -0.025669 | 7.627e-05 | -0.017895 | 0.024381 | 0.060474 | -0.024319 | -0.025165 | 62.9196 | -59.2346 | 0.050354 | -59.5505 | 62.851 | -59.4315 | -59.3765 | 0.054932 | 0.082397 | -59.6832 | 62.8235 | 62.8006 | -59.3811 | -59.5917 | 0.004577 | 0.059509 | -0.091553 | 0.20142 | -0.11444 | -0.17395 | -0.022888 | 0.054931 | -0.15564 | -0.11902 | 59.491 | -0.24719 | -0.091553 | -0.14191 | 122.287 | 122.3557 | 59.4864 | -122.319 | 122.2595 | 122.2366 | 59.5184 | -122.5342
1002.0625 | 122.5983 | -59.5139 | 62.8189 | -0.00022891 | -0.047854 | 0.12529 | 0.03645 | 0.034146 | -0.032742 | -0.028232 | 7.627e-05 | -0.010632 | 0.028867 | 0.060047 | -0.021328 | -0.026233 | 62.8235 | -59.436 | -0.009155 | -59.6924 | 62.8281 | -59.5413 | -59.523 | 0.068665 | 0.032043 | -59.8572 | 62.796 | 62.7274 | -59.5093 | -59.6832 | -0.027466 | -0.009155 | 0.009155 | 0.07782 | -0.17853 | -0.16937 | 0.004577 | 0.004578 | -0.16937 | -0.022888 | 59.5825 | -0.34332 | -0.17395 | -0.091553 | 122.3419 | 122.3373 | 59.5047 | -122.3419 | 122.3099 | 122.2412 | 59.5459 | -122.5021
1003.7812 | 122.4609 | -59.4406 | 62.9562 | -0.00022891 | -0.052126 | 0.12764 | 0.037091 | 0.035 | -0.037442 | -0.028873 | 7.627e-05 | -0.016827 | 0.027799 | 0.060261 | -0.023678 | -0.024951 | 62.9883 | -59.1751 | 0.19684 | -59.5001 | 62.8784 | -59.4315 | -59.3948 | 0.11902 | 0.12817 | -59.6786 | 62.8601 | 62.8372 | -59.3765 | -59.5642 | 0.009155 | 0.045777 | -0.07782 | 0.2655 | -0.059509 | -0.10529 | 0.032043 | 0.064087 | -0.1236 | -0.096131 | 59.5596 | -0.23804 | -0.11444 | -0.11902 | 122.319 | 122.4289 | 59.6375 | -122.3511 | 122.3007 | 122.2778 | 59.5688 | -122.5204
1005.5781 | 122.5021 | -59.2804 | 63.121 | 0.0074006 | -0.053622 | 0.12679 | 0.034741 | 0.034146 | -0.039151 | -0.028232 | 7.627e-05 | -0.015759 | 0.024167 | 0.058552 | -0.021969 | -0.025806 | 63.1393 | -59.0332 | 0.16937 | -59.3582 | 63.0249 | -59.2758 | -59.2255 | 0.091553 | 0.086975 | -59.5505 | 63.0066 | 63.0112 | -59.2392 | -59.4177 | 0.004578 | 0.054932 | -0.096131 | 0.24719 | -0.077819 | -0.13275 | 0.01831 | 0.041199 | -0.13733 | -0.11444 | 59.3719 | -0.27008 | -0.13275 | -0.10986 | 122.3053 | 122.4197 | 59.4498 | -122.3465 | 122.287 | 122.2916 | 59.3674 | -122.5388
1007.375 | 122.5342 | -59.3262 | 63.1027 | -0.0078584 | -0.055971 | 0.12978 | 0.034955 | 0.036923 | -0.040646 | -0.028019 | 7.627e-05 | -0.018322 | 0.024167 | 0.058979 | -0.023678 | -0.025378 | 63.089 | -59.0607 | 0.086975 | -59.3719 | 63.0249 | -59.2667 | -59.2117 | 0.091553 | 0.10529 | -59.4727 | 62.9654 | 62.9654 | -59.2529 | -59.3857 | 0.059509 | 0.11444 | -0.07782 | 0.2655 | -0.045776 | -0.16022 | -0.013733 | 0.073242 | -0.059509 | -0.13733 | 59.4177 | -0.14648 | -0.086975 | -0.13733 | 122.3511 | 122.4152 | 59.4131 | -122.3145 | 122.2916 | 122.2916 | 59.4315 | -122.4884
1009.1719 | 122.5662 | -59.2117 | 63.1119 | -0.00022891 | -0.050417 | 0.12786 | 0.031964 | 0.037777 | -0.03146 | -0.024601 | -0.0075532 | -0.0117 | 0.024167 | 0.061756 | -0.019192 | -0.026447 | 63.1531 | -59.0698 | 0.068665 | -59.3628 | 63.1256 | -59.2346 | -59.2163 | 0.091553 | 0.073242 | -59.5505 | 63.0798 | 63.0478 | -59.1705 | -59.3994 | -0.022888 | -0.004578 | 0.013733 | 0.14191 | -0.15106 | -0.14648 | 0.041199 | 0.041199 | -0.18768 | -0.032043 | 59.3033 | -0.33875 | -0.15106 | -0.064086 | 122.3373 | 122.3648 | 59.2804 | -122.3282 | 122.2916 | 122.2595 | 59.285 | -122.5113
1010.9062 | 122.5342 | -59.166 | 63.2217 | 0.01503 | -0.057253 | 0.12828 | 0.037518 | 0.035427 | -0.041501 | -0.027591 | -0.015182 | -0.018536 | 0.025663 | 0.058552 | -0.025601 | -0.024738 | 63.2996 | -58.8501 | 0.17853 | -59.2072 | 63.1439 | -59.1431 | -59.0973 | 0.16937 | 0.17395 | -59.2896 | 63.0615 | 63.0707 | -59.1019 | -59.2575 | 0.022889 | 0.068665 | -0.07782 | 0.31586 | -0.041198 | -0.10986 | 0.07782 | 0.064087 | -0.091552 | -0.16022 | 59.3353 | -0.1236 | -0.032044 | -0.15106 | 122.3099 | 122.4655 | 59.3445 | -122.319 | 122.2275 | 122.2366 | 59.3399 | -122.4792
1012.6875 | 122.6166 | -59.079 | 63.2263 | -0.00022891 | -0.052126 | 0.12636 | 0.031537 | 0.034786 | -0.033596 | -0.027805 | 7.627e-05 | -0.012341 | 0.028653 | 0.061756 | -0.021328 | -0.026447 | 63.2904 | -58.9005 | 0.12817 | -59.2072 | 63.2538 | -59.079 | -59.0652 | 0.14648 | 0.11444 | -59.3857 | 63.2034 | 63.176 | -59.0698 | -59.2346 | 0 | 0.013732 | 0.027466 | 0.17853 | -0.12817 | -0.14191 | 0.064087 | 0.009155 | -0.15564 | -0.022888 | 59.2255 | -0.3067 | -0.15106 | -0.050354 | 122.3328 | 122.3694 | 59.2072 | -122.2916 | 122.2824 | 122.2549 | 59.1934 | -122.4609
1014.4688 | 122.4838 | -59.0836 | 63.2904 | -0.00022891 | -0.052553 | 0.12786 | 0.037305 | 0.036495 | -0.043423 | -0.024173 | 7.627e-05 | -0.018536 | 0.027372 | 0.060474 | -0.025173 | -0.024951 | 63.3591 | -58.7494 | 0.21057 | -59.1202 | 63.2217 | -59.0424 | -59.0195 | 0.16479 | 0.1831 | -59.2529 | 63.1943 | 63.1668 | -59.0286 | -59.1934 | 0.041199 | 0.064087 | -0.068664 | 0.33417 | -0.036621 | -0.10071 | 0.068665 | 0.054932 | -0.10986 | -0.09613 | 59.2484 | -0.16937 | -0.05951 | -0.1236 | 122.3053 | 122.4426 | 59.2941 | -122.3099 | 122.2778 | 122.2504 | 59.2667 | -122.4838
1016.1719 | 122.4747 | -59.1614 | 63.2492 | -0.0078584 | -0.050631 | 0.127 | 0.035809 | 0.036923 | -0.03851 | -0.025882 | -0.015182 | -0.016186 | 0.026304 | 0.058766 | -0.020687 | -0.026874 | 63.2996 | -58.8318 | 0.20142 | -59.166 | 63.1851 | -59.111 | -59.0698 | 0.13733 | 0.15106 | -59.3536 | 63.1302 | 63.0936 | -59.0881 | -59.2621 | 0.050354 | 0.091553 | -0.064087 | 0.32959 | -0.004578 | -0.096131 | 0.050354 | 0.073242 | -0.10071 | -0.11902 | 59.2987 | -0.19226 | -0.091553 | -0.15564 | 122.3465 | 122.4609 | 59.3628 | -122.319 | 122.2916 | 122.2549 | 59.3124 | -122.5113
1017.9531 | 122.4655 | -59.0515 | 63.3453 | -0.00022891 | -0.052553 | 0.12615 | 0.035809 | 0.033291 | -0.037442 | -0.026951 | 0.0077058 | -0.013195 | 0.030149 | 0.059834 | -0.024105 | -0.026447 | 63.3774 | -58.7311 | 0.19684 | -59.0881 | 63.2858 | -59.0332 | -58.9645 | 0.12817 | 0.11902 | -59.285 | 63.2492 | 63.2217 | -59.0149 | -59.1522 | 0.018311 | 0.086975 | -0.059509 | 0.32043 | -0.036621 | -0.1236 | 0.032043 | 0.036621 | -0.10071 | -0.09613 | 59.1797 | -0.23346 | -0.13275 | -0.1236 | 122.3373 | 122.4289 | 59.2484 | -122.3099 | 122.3007 | 122.2733 | 59.1705 | -122.4976
1019.75 | 122.6028 | -59.0378 | 63.2492 | -0.0078584 | -0.052126 | 0.12551 | 0.031964 | 0.034786 | -0.034878 | -0.025028 | 0.0077058 | -0.013409 | 0.026517 | 0.061329 | -0.020046 | -0.026019 | 63.3224 | -58.8547 | 0.10986 | -59.1568 | 63.3133 | -59.024 | -59.0103 | 0.13275 | 0.10071 | -59.3308 | 63.2355 | 63.2309 | -59.0195 | -59.1934 | 0.013733 | 0.027466 | 0.064086 | 0.18311 | -0.11902 | -0.14648 | 0.073242 | 0.018311 | -0.15564 | -0.013733 | 59.1705 | -0.29297 | -0.13733 | -0.018311 | 122.3511 | 122.3602 | 59.1476 | -122.2595 | 122.2733 | 122.2687 | 59.1385 | -122.4426
1021.4844 | 122.4792 | -58.9966 | 63.4094 | 0.0074006 | -0.054476 | 0.13021 | 0.032392 | 0.034573 | -0.040646 | -0.028232 | 7.627e-05 | -0.016827 | 0.024808 | 0.058338 | -0.022183 | -0.024951 | 63.4872 | -58.6166 | 0.22888 | -59.0103 | 63.3499 | -58.9417 | -58.8867 | 0.16479 | 0.16937 | -59.1156 | 63.3224 | 63.2904 | -58.905 | -59.0652 | 0.054932 | 0.10986 | -0.059509 | 0.37994 | -0.013733 | -0.1236 | 0.07782 | 0.091553 | -0.068665 | -0.086975 | 59.1614 | -0.11902 | -0.050354 | -0.11902 | 122.3465 | 122.4838 | 59.2255 | -122.2961 | 122.319 | 122.287 | 59.166 | -122.4747
1023.2969 | 122.4976 | -58.9645 | 63.414 | 0.0074006 | -0.055971 | 0.127 | 0.033673 | 0.033718 | -0.040432 | -0.026737 | 7.627e-05 | -0.014904 | 0.023954 | 0.057484 | -0.023464 | -0.028155 | 63.4552 | -58.6945 | 0.11902 | -59.0469 | 63.3408 | -58.9096 | -58.905 | 0.086975 | 0.086975 | -59.1705 | 63.295 | 63.295 | -58.8776 | -59.0652 | 0.054932 | 0.05951 | -0.073242 | 0.27008 | -0.082397 | -0.14191 | 0.041199 | 0.086976 | -0.10071 | -0.11902 | 59.0515 | -0.20599 | -0.10529 | -0.11902 | 122.3053 | 122.4197 | 59.0836 | -122.319 | 122.2595 | 122.2595 | 59.0515 | -122.4792
1025.0156 | 122.525 | -58.9279 | 63.4277 | -0.0078584 | -0.054903 | 0.12444 | 0.031964 | 0.034573 | -0.039578 | -0.026951 | 0.0077058 | -0.015545 | 0.026304 | 0.056843 | -0.021755 | -0.026019 | 63.5101 | -58.6349 | 0.16022 | -58.992 | 63.3545 | -58.8959 | -58.8684 | 0.14648 | 0.14191 | -59.1156 | 63.2858 | 63.2858 | -58.8959 | -59.0286 | 0.032043 | 0.059509 | -0.073242 | 0.29297 | -0.064087 | -0.1236 | 0.082398 | 0.032043 | -0.10071 | -0.14191 | 59.0744 | -0.18768 | -0.086976 | -0.14191 | 122.2824 | 122.438 | 59.0881 | -122.2961 | 122.2137 | 122.2137 | 59.0698 | -122.4564
1026.7969 | 122.5983 | -58.7952 | 63.5147 | 0.0074006 | -0.055758 | 0.12593 | 0.034528 | 0.031368 | -0.038083 | -0.025028 | 0.0077058 | -0.017682 | 0.026944 | 0.058552 | -0.02026 | -0.027728 | 63.6154 | -58.548 | 0.14648 | -58.9188 | 63.4415 | -58.8409 | -58.7677 | 0.15564 | 0.13275 | -59.0378 | 63.4048 | 63.3316 | -58.7997 | -58.9691 | -0.045776 | 0.027466 | -0.073242 | 0.24719 | -0.1236 | -0.15106 | 0.10071 | -0.004578 | -0.17395 | -0.10986 | 58.9508 | -0.24262 | -0.068665 | -0.18311 | 122.2366 | 122.4106 | 58.9417 | -122.2824 | 122.2 | 122.1268 | 58.9279 | -122.4838
1028.5938 | 122.5937 | -58.7357 | 63.6063 | -0.00022891 | -0.053194 | 0.12871 | 0.032819 | 0.033291 | -0.038083 | -0.027591 | -0.0075532 | -0.015973 | 0.027585 | 0.058979 | -0.020474 | -0.025806 | 63.6749 | -58.4656 | 0.16937 | -58.8181 | 63.5056 | -58.7631 | -58.699 | 0.14648 | 0.15564 | -58.9737 | 63.4872 | 63.3911 | -58.7448 | -58.8776 | -0.027466 | 0.036621 | -0.10071 | 0.27008 | -0.082397 | -0.11902 | 0.068665 | -0.009155 | -0.14191 | -0.11902 | 58.8821 | -0.23804 | -0.096131 | -0.21515 | 122.2412 | 122.4106 | 58.905 | -122.3053 | 122.2229 | 122.1268 | 58.8913 | -122.4838
1030.375 | 122.4884 | -58.8455 | 63.5925 | -0.0078584 | -0.053622 | 0.12764 | 0.035169 | 0.034146 | -0.039792 | -0.02631 | 7.627e-05 | -0.017041 | 0.026304 | 0.057484 | -0.020901 | -0.027087 | 63.652 | -58.4473 | 0.2655 | -58.8593 | 63.4964 | -58.7677 | -58.7357 | 0.17395 | 0.1831 | -58.9828 | 63.4369 | 63.4369 | -58.754 | -58.9279 | 0.07782 | 0.10986 | -0.09613 | 0.39825 | -0.013733 | -0.1236 | 0.05951 | 0.091553 | -0.082397 | -0.15564 | 59.0195 | -0.13733 | -0.054932 | -0.15564 | 122.3419 | 122.4976 | 59.111 | -122.3282 | 122.2824 | 122.2824 | 59.0286 | -122.5204
1032.1562 | 122.493 | -58.7219 | 63.6566 | -0.00022891 | -0.050417 | 0.12786 | 0.036878 | 0.034573 | -0.039578 | -0.028019 | 7.627e-05 | -0.015759 | 0.026304 | 0.060047 | -0.023037 | -0.025378 | 63.6795 | -58.4839 | 0.18768 | -58.8455 | 63.6108 | -58.7402 | -58.6853 | 0.10986 | 0.068665 | -59.0057 | 63.5788 | 63.5468 | -58.6899 | -58.8638 | -0.01831 | 0.036621 | -0.045776 | 0.23804 | -0.1236 | -0.16022 | 0.022888 | 0.032044 | -0.14191 | -0.07782 | 58.8318 | -0.28381 | -0.14191 | -0.10986 | 122.3328 | 122.4014 | 58.9096 | -122.3419 | 122.3007 | 122.2687 | 58.7906 | -122.5204
1033.875 | 122.5342 | -58.6395 | 63.7115 | -0.0078584 | -0.054049 | 0.12743 | 0.035382 | 0.035 | -0.041287 | -0.026951 | 7.627e-05 | -0.016613 | 0.027158 | 0.058979 | -0.023251 | -0.025806 | 63.7894 | -58.3008 | 0.20142 | -58.699 | 63.6887 | -58.6121 | -58.5663 | 0.16022 | 0.13733 | -58.7906 | 63.6017 | 63.5788 | -58.5617 | -58.7494 | 0.027465 | 0.073242 | -0.022888 | 0.33874 | -0.05951 | -0.13275 | 0.07782 | 0.077819 | -0.10986 | -0.10986 | 58.7997 | -0.15106 | -0.041198 | -0.13275 | 122.3282 | 122.4289 | 58.8409 | -122.2778 | 122.2412 | 122.2183 | 58.7769 | -122.4609
1035.6719 | 122.5616 | -58.5846 | 63.7344 | -0.00022891 | -0.053194 | 0.12743 | 0.037091 | 0.036068 | -0.035519 | -0.025242 | 0.015335 | -0.012127 | 0.025876 | 0.058979 | -0.02026 | -0.028796 | 63.7985 | -58.3694 | 0.16937 | -58.7219 | 63.7665 | -58.5983 | -58.5617 | 0.1236 | 0.07782 | -58.9005 | 63.707 | 63.6795 | -58.5526 | -58.7219 | -0.013733 | 0.022888 | 0.032043 | 0.21515 | -0.13733 | -0.16022 | 0.064087 | 0.032044 | -0.13733 | -0.027466 | 58.7082 | -0.31586 | -0.17853 | -0.054932 | 122.3511 | 122.3831 | 58.754 | -122.2961 | 122.2916 | 122.2641 | 58.6624 | -122.4564
1037.4688 | 122.612 | -58.4702 | 63.8214 | -0.00022891 | -0.049135 | 0.12807 | 0.033673 | 0.034146 | -0.031674 | -0.026737 | -0.0075532 | -0.012555 | 0.027585 | 0.059406 | -0.017697 | -0.028369 | 63.9221 | -58.2138 | 0.17853 | -58.5846 | 63.8535 | -58.5159 | -58.4793 | 0.1831 | 0.13733 | -58.7585 | 63.7619 | 63.7527 | -58.4656 | -58.6533 | -0.045776 | -0.009155 | 0.032044 | 0.25635 | -0.11444 | -0.10529 | 0.10071 | 0.004578 | -0.1831 | -0.059509 | 58.6533 | -0.28839 | -0.10529 | -0.068664 | 122.3236 | 122.3923 | 58.6487 | -122.3007 | 122.2321 | 122.2229 | 58.6075 | -122.4747
1039.25 | 122.525 | -58.4106 | 63.945 | -0.0078584 | -0.057894 | 0.12893 | 0.031751 | 0.033291 | -0.042569 | -0.027805 | -0.0075532 | -0.018963 | 0.025022 | 0.057911 | -0.021114 | -0.024738 | 64.0457 | -57.9941 | 0.27466 | -58.4473 | 63.8901 | -58.4106 | -58.342 | 0.1831 | 0.18768 | -58.5754 | 63.8351 | 63.8168 | -58.3511 | -58.5159 | 0 | 0.068665 | -0.054931 | 0.41657 | -0.036621 | -0.10529 | 0.10071 | 0.05951 | -0.10528 | -0.10986 | 58.5938 | -0.16479 | -0.059509 | -0.12817 | 122.3007 | 122.4564 | 58.6853 | -122.287 | 122.2458 | 122.2275 | 58.5983 | -122.4609
1040.9688 | 122.4884 | -58.4106 | 63.9999 | -0.015487 | -0.050631 | 0.12786 | 0.034314 | 0.034786 | -0.037869 | -0.028873 | -0.0075532 | -0.014477 | 0.026304 | 0.058766 | -0.021114 | -0.026019 | 63.9999 | -58.0902 | 0.19684 | -58.4885 | 63.9862 | -58.3878 | -58.342 | 0.1236 | 0.07782 | -58.6716 | 63.9221 | 63.8763 | -58.3969 | -58.5434 | 0.022889 | 0.068665 | -0.013733 | 0.32044 | -0.077819 | -0.14648 | 0 | 0.013733 | -0.13275 | -0.07782 | 58.5342 | -0.26093 | -0.12817 | -0.1236 | 122.3969 | 122.4106 | 58.6075 | -122.3419 | 122.3328 | 122.287 | 58.4885 | -122.5433
1042.7812 | 122.6212 | -58.2733 | 64.0549 | -0.0078584 | -0.051485 | 0.12593 | 0.034314 | 0.036709 | -0.035519 | -0.024814 | -0.0075532 | -0.013195 | 0.028867 | 0.061115 | -0.017483 | -0.027942 | 64.1144 | -57.9758 | 0.21515 | -58.3832 | 64.0366 | -58.2779 | -58.2458 | 0.20142 | 0.14191 | -58.5434 | 64.0091 | 63.9542 | -58.2687 | -58.4427 | -0.004578 | 0.027465 | -0.018311 | 0.29755 | -0.10986 | -0.13733 | 0.059509 | 0.004577 | -0.16937 | -0.045777 | 58.4747 | -0.27008 | -0.10071 | -0.10071 | 122.3099 | 122.3877 | 58.4885 | -122.3007 | 122.2824 | 122.2275 | 58.4152 | -122.4976
1044.5 | 122.4792 | -58.0811 | 64.2929 | -0.00022891 | -0.051272 | 0.12807 | 0.038587 | 0.034359 | -0.041501 | -0.026523 | -0.0075532 | -0.017254 | 0.028226 | 0.057911 | -0.025601 | -0.026233 | 64.357 | -57.6874 | 0.32044 | -58.136 | 64.2014 | -58.0307 | -58.0078 | 0.19684 | 0.1831 | -58.2596 | 64.1602 | 64.183 | -58.0215 | -58.2047 | 0.050354 | 0.073243 | -0.091553 | 0.39368 | -0.054931 | -0.12817 | 0.064087 | 0.05951 | -0.1236 | -0.13275 | 58.2779 | -0.17853 | -0.054932 | -0.10986 | 122.2824 | 122.4381 | 58.4015 | -122.3007 | 122.2412 | 122.2641 | 58.2642 | -122.4976
1046.2812 | 122.58 | -57.8934 | 64.4394 | -0.00022891 | -0.053408 | 0.12487 | 0.033887 | 0.032864 | -0.033596 | -0.025028 | 7.627e-05 | -0.012982 | 0.02609 | 0.061543 | -0.019619 | -0.026233 | 64.5035 | -57.6004 | 0.21515 | -58.0124 | 64.4531 | -57.9025 | -57.8705 | 0.18768 | 0.11902 | -58.2047 | 64.3936 | 64.3387 | -57.8751 | -58.0399 | -0.009155 | 0.022889 | 0.013733 | 0.29297 | -0.11902 | -0.14191 | 0.064087 | 0.018311 | -0.14648 | -0.045776 | 58.0811 | -0.31128 | -0.16479 | -0.10071 | 122.3465 | 122.3969 | 58.1085 | -122.3099 | 122.287 | 122.2321 | 58.0124 | -122.4792
1048.0938 | 122.5571 | -57.7515 | 64.6042 | 0.0074006 | -0.053194 | 0.12786 | 0.02876 | 0.036282 | -0.040005 | -0.027164 | 0.0077058 | -0.017041 | 0.024381 | 0.059834 | -0.020474 | -0.025592 | 64.6545 | -57.3807 | 0.20142 | -57.8293 | 64.5218 | -57.7377 | -57.6599 | 0.17853 | 0.15564 | -57.9529 | 64.4714 | 64.4669 | -57.7332 | -57.8842 | 0.013733 | 0.091553 | -0.082397 | 0.37079 | -0.07782 | -0.16937 | 0.050354 | 0.018311 | -0.13275 | -0.13275 | 57.93 | -0.20142 | -0.068665 | -0.13733 | 122.2733 | 122.406 | 57.9529 | -122.2641 | 122.2229 | 122.2183 | 57.9071 | -122.4884
1049.8125 | 122.5616 | -57.6279 | 64.7278 | -0.00022891 | -0.05234 | 0.12807 | 0.034955 | 0.033932 | -0.037869 | -0.025669 | -0.0075532 | -0.013195 | 0.02844 | 0.059406 | -0.022183 | -0.025806 | 64.7141 | -57.3578 | 0.19684 | -57.7698 | 64.7232 | -57.6508 | -57.5958 | 0.14191 | 0.07782 | -57.9437 | 64.7003 | 64.65 | -57.6187 | -57.7789 | -0.022888 | 0.032044 | -0.004577 | 0.27008 | -0.14191 | -0.17395 | -0.013733 | 0.009156 | -0.15106 | -0.027466 | 57.7698 | -0.31586 | -0.16479 | -0.07782 | 122.3511 | 122.3419 | 57.8247 | -122.3236 | 122.3282 | 122.2778 | 57.7057 | -122.5067
1051.5938 | 122.4884 | -57.5729 | 64.8376 | 0.0074006 | -0.05704 | 0.12658 | 0.035596 | 0.033291 | -0.04086 | -0.025669 | -0.015182 | -0.017254 | 0.025663 | 0.059406 | -0.025814 | -0.024524 | 64.8285 | -57.2113 | 0.17853 | -57.6553 | 64.7369 | -57.5226 | -57.4997 | 0.12817 | 0.064087 | -57.7789 | 64.6729 | 64.6912 | -57.4997 | -57.6874 | 0.050354 | 0.073242 | -0.10071 | 0.36163 | -0.082397 | -0.15564 | -0.009155 | 0.073242 | -0.11444 | -0.16479 | 57.7011 | -0.20599 | -0.091553 | -0.14648 | 122.3099 | 122.4014 | 57.7515 | -122.3373 | 122.2458 | 122.2641 | 57.637 | -122.525
1053.375 | 122.6212 | -57.4448 | 64.856 | -0.00022891 | -0.053408 | 0.12572 | 0.028974 | 0.031368 | -0.035733 | -0.025882 | -0.015182 | -0.011486 | 0.024381 | 0.059406 | -0.019619 | -0.026233 | 64.9338 | -57.1472 | 0.2243 | -57.5592 | 64.8285 | -57.4539 | -57.4356 | 0.19684 | 0.11902 | -57.7011 | 64.7644 | 64.7461 | -57.4356 | -57.5912 | -0.009155 | 0.009155 | -0.027466 | 0.29755 | -0.11444 | -0.1236 | 0.07782 | 0.009155 | -0.14648 | -0.091553 | 57.6416 | -0.25635 | -0.10986 | -0.10986 | 122.2733 | 122.3785 | 57.6691 | -122.2916 | 122.2092 | 122.1909 | 57.5638 | -122.4472
1055.0938 | 122.4976 | -57.4036 | 65.0391 | 0.0074006 | -0.050417 | 0.12722 | 0.037518 | 0.035855 | -0.037869 | -0.027591 | -0.0075532 | -0.014477 | 0.028013 | 0.059406 | -0.023251 | -0.025165 | 65.0253 | -57.0145 | 0.27924 | -57.4539 | 64.975 | -57.3532 | -57.3166 | 0.14648 | 0.073242 | -57.6416 | 64.9429 | 64.9017 | -57.3395 | -57.4951 | 0.050354 | 0.086975 | -0.064086 | 0.3891 | -0.050354 | -0.13733 | -0.013732 | 0.064086 | -0.091553 | -0.09613 | 57.55 | -0.23804 | -0.14648 | -0.13733 | 122.3785 | 122.4289 | 57.6828 | -122.3557 | 122.3465 | 122.3053 | 57.4768 | -122.5342
1056.8906 | 122.4976 | -57.106 | 65.2679 | -0.0078584 | -0.055544 | 0.12764 | 0.037518 | 0.034573 | -0.041501 | -0.028873 | 7.627e-05 | -0.016186 | 0.026944 | 0.058979 | -0.022396 | -0.026233 | 65.3412 | -56.694 | 0.32959 | -57.1609 | 65.1627 | -57.0877 | -57.0602 | 0.20142 | 0.18768 | -57.2937 | 65.1215 | 65.1123 | -57.0694 | -57.2479 | 0.01831 | 0.045776 | -0.10528 | 0.41199 | -0.054932 | -0.10071 | 0.073243 | 0.036621 | -0.14191 | -0.14648 | 57.3074 | -0.18768 | -0.045776 | -0.15564 | 122.2687 | 122.4472 | 57.4356 | -122.3282 | 122.2275 | 122.2183 | 57.2937 | -122.5159
1058.625 | 122.4884 | -57.0831 | 65.3229 | -0.00022891 | -0.053408 | 0.12914 | 0.034528 | 0.035427 | -0.039364 | -0.028019 | 7.627e-05 | -0.018109 | 0.025663 | 0.05727 | -0.021328 | -0.025378 | 65.3778 | -56.6391 | 0.32501 | -57.1106 | 65.2359 | -57.0374 | -57.019 | 0.20142 | 0.16022 | -57.2662 | 65.2084 | 65.1855 | -57.0236 | -57.193 | 0.045776 | 0.064087 | -0.086975 | 0.44403 | -0.027466 | -0.091553 | 0.054932 | 0.059509 | -0.10986 | -0.11444 | 57.2845 | -0.18311 | -0.073242 | -0.13733 | 122.319 | 122.4609 | 57.4081 | -122.3419 | 122.2916 | 122.2687 | 57.2433 | -122.5159
1060.4062 | 122.612 | -56.9183 | 65.387 | -0.00022891 | -0.048067 | 0.12508 | 0.034101 | 0.033291 | -0.032528 | -0.026737 | 7.627e-05 | -0.013195 | 0.027585 | 0.060261 | -0.01791 | -0.026874 | 65.4648 | -56.5979 | 0.21973 | -57.0419 | 65.4053 | -56.987 | -56.9275 | 0.22888 | 0.14648 | -57.2433 | 65.3229 | 65.2634 | -56.9412 | -57.1152 | -0.068665 | -0.009155 | 0.01831 | 0.32043 | -0.1236 | -0.11444 | 0.07782 | -0.022888 | -0.19684 | -0.064087 | 57.1472 | -0.32501 | -0.12817 | -0.1236 | 122.3236 | 122.3831 | 57.1381 | -122.3145 | 122.2412 | 122.1817 | 57.0648 | -122.5021
1062.125 | 122.493 | -56.8497 | 65.5518 | -0.00022891 | -0.055331 | 0.13021 | 0.034741 | 0.037777 | -0.041928 | -0.026523 | 7.627e-05 | -0.017895 | 0.024595 | 0.058979 | -0.022823 | -0.023883 | 65.5563 | -56.4285 | 0.16479 | -56.9229 | 65.4739 | -56.8268 | -56.7673 | 0.15106 | 0.086975 | -57.0648 | 65.4099 | 65.3641 | -56.7856 | -56.9595 | 0.022888 | 0.082397 | -0.07782 | 0.42114 | -0.073243 | -0.15564 | 0.004577 | 0.064087 | -0.10986 | -0.14191 | 57.0007 | -0.21515 | -0.10529 | -0.18768 | 122.3236 | 122.406 | 57.0145 | -122.319 | 122.2595 | 122.2137 | 56.9366 | -122.5113
1063.9219 | 122.6074 | -56.781 | 65.5655 | -0.00022891 | -0.056826 | 0.127 | 0.03111 | 0.037136 | -0.036801 | -0.024601 | -0.0075532 | -0.015332 | 0.026304 | 0.058979 | -0.020687 | -0.025378 | 65.6662 | -56.3324 | 0.11902 | -56.8222 | 65.4968 | -56.7444 | -56.7215 | 0.19684 | 0.13275 | -56.9824 | 65.4556 | 65.4327 | -56.7261 | -56.8954 | 0.036621 | 0.059509 | -0.068665 | 0.44861 | -0.041199 | -0.10071 | 0.10071 | 0.054932 | -0.11444 | -0.10986 | 56.9778 | -0.20142 | -0.086975 | -0.13275 | 122.2778 | 122.4472 | 56.9 | -122.287 | 122.2366 | 122.2137 | 56.9138 | -122.4609
1065.7188 | 122.5708 | -56.7169 | 65.6021 | -0.0078584 | -0.052767 | 0.12615 | 0.029828 | 0.033077 | -0.033383 | -0.025882 | 0.015335 | -0.013409 | 0.026731 | 0.057484 | -0.017483 | -0.02666 | 65.5975 | -56.4331 | 0.009155 | -56.8726 | 65.6296 | -56.7398 | -56.7261 | 0.13733 | 0.045776 | -57.1014 | 65.5655 | 65.506 | -56.7215 | -56.8817 | -0.022888 | -0.009155 | 0.027466 | 0.28381 | -0.15564 | -0.14649 | -0.004578 | -0.004578 | -0.1648 | -0.036621 | 56.8542 | -0.38452 | -0.21973 | -0.096131 | 122.3465 | 122.3145 | 56.7261 | -122.3282 | 122.2824 | 122.2229 | 56.7627 | -122.4838
1067.5 | 122.5342 | -56.575 | 65.8081 | 0.01503 | -0.050844 | 0.12893 | 0.036023 | 0.036282 | -0.037869 | -0.02631 | 7.627e-05 | -0.015759 | 0.027799 | 0.057911 | -0.022396 | -0.026447 | 65.7715 | -56.1951 | 0.07782 | -56.694 | 65.7761 | -56.5704 | -56.5613 | 0.14191 | 0.054932 | -56.8817 | 65.7532 | 65.6891 | -56.543 | -56.7261 | 0.004577 | 0.013733 | -0.032043 | 0.37994 | -0.11902 | -0.13275 | -0.036621 | 0.032043 | -0.15106 | -0.054931 | 56.7169 | -0.3067 | -0.15564 | -0.11902 | 122.3511 | 122.3465 | 56.6528 | -122.3694 | 122.3282 | 122.2641 | 56.6299 | -122.5342
1069.2031 | 122.5891 | -56.5613 | 65.7852 | -0.00022891 | -0.052553 | 0.12615 | 0.031964 | 0.033932 | -0.034878 | -0.024387 | 0.0077058 | -0.012768 | 0.025876 | 0.060047 | -0.018765 | -0.026019 | 65.7623 | -56.2317 | -0.036621 | -56.7169 | 65.7761 | -56.5887 | -56.5475 | 0.11902 | 0.041199 | -56.9183 | 65.7303 | 65.7028 | -56.543 | -56.7535 | -0.027466 | 0.013733 | -0.009155 | 0.32959 | -0.15564 | -0.16937 | -0.022888 | 0.01831 | -0.19226 | -0.054931 | 56.6803 | -0.35706 | -0.16479 | -0.082397 | 122.3373 | 122.3236 | 56.5247 | -122.3328 | 122.2916 | 122.2641 | 56.6025 | -122.5388
1070.9844 | 122.6166 | -56.337 | 65.9546 | -0.015487 | -0.048922 | 0.12508 | 0.037305 | 0.03265 | -0.034665 | -0.025028 | 7.627e-05 | -0.010846 | 0.027372 | 0.059834 | -0.020474 | -0.02431 | 66.0141 | -55.9525 | 0.059509 | -56.4514 | 65.9775 | -56.3644 | -56.3507 | 0.21057 | 0.10986 | -56.6528 | 65.9042 | 65.863 | -56.3782 | -56.5155 | -0.027466 | -0.013733 | 0.022888 | 0.38452 | -0.11444 | -0.10071 | 0.059509 | -0.041199 | -0.17853 | -0.050354 | 56.5475 | -0.31586 | -0.13733 | -0.091553 | 122.3145 | 122.3511 | 56.3965 | -122.3053 | 122.2412 | 122.2 | 56.4468 | -122.4701
1072.7812 | 122.4884 | -56.2729 | 66.1011 | -0.00022891 | -0.058108 | 0.12593 | 0.031537 | 0.032864 | -0.041501 | -0.026737 | 0.0077058 | -0.017468 | 0.023954 | 0.060047 | -0.025601 | -0.024524 | 66.1331 | -55.7602 | 0.027466 | -56.3278 | 65.9958 | -56.2454 | -56.2088 | 0.16937 | 0.064087 | -56.4743 | 65.9546 | 65.9546 | -56.2225 | -56.3782 | 0.027466 | 0.064087 | -0.10528 | 0.5127 | -0.054932 | -0.11902 | 0.032044 | 0.050354 | -0.10529 | -0.14648 | 56.4423 | -0.20142 | -0.09613 | -0.14648 | 122.2687 | 122.406 | 56.3004 | -122.3099 | 122.2275 | 122.2275 | 56.337 | -122.4792
1074.5469 | 122.493 | -56.131 | 66.2521 | -0.00022891 | -0.054476 | 0.12743 | 0.03645 | 0.033291 | -0.042141 | -0.027164 | -0.0075532 | -0.018963 | 0.026304 | 0.059834 | -0.02496 | -0.025378 | 66.3116 | -55.5862 | 0.091553 | -56.163 | 66.1743 | -56.0898 | -56.0623 | 0.21973 | 0.14191 | -56.3095 | 66.124 | 66.0828 | -56.1081 | -56.25 | 0.041198 | 0.068664 | -0.07782 | 0.54474 | -0.032044 | -0.10071 | 0.05951 | 0.022888 | -0.11902 | -0.12817 | 56.3507 | -0.17853 | -0.059509 | -0.16937 | 122.3053 | 122.4426 | 56.2225 | -122.3145 | 122.2549 | 122.2137 | 56.2729 | -122.5021
1076.3281 | 122.5937 | -56.0028 | 66.3025 | -0.00022891 | -0.052553 | 0.12679 | 0.036664 | 0.033077 | -0.037228 | -0.025028 | 0.0077058 | -0.013195 | 0.030362 | 0.05962 | -0.021755 | -0.026874 | 66.3437 | -55.5908 | -0.022888 | -56.1218 | 66.3528 | -56.0257 | -55.9845 | 0.16022 | 0.073242 | -56.3232 | 66.2888 | 66.2521 | -56.0074 | -56.1584 | -0.022888 | 0.018311 | 0.050354 | 0.41199 | -0.11902 | -0.13733 | 0.041199 | -0.004577 | -0.15564 | -0.013733 | 56.163 | -0.32043 | -0.16479 | -0.050354 | 122.3557 | 122.3465 | 55.9799 | -122.287 | 122.2916 | 122.2549 | 56.0761 | -122.4609
1078.1406 | 122.5662 | -55.9479 | 66.3712 | -0.00022891 | -0.049563 | 0.12444 | 0.033032 | 0.033505 | -0.031887 | -0.025882 | 7.627e-05 | -0.012768 | 0.028867 | 0.060902 | -0.018978 | -0.027515 | 66.3986 | -55.5222 | -0.086975 | -56.0761 | 66.3757 | -55.9753 | -55.925 | 0.14648 | 0.064087 | -56.2775 | 66.3437 | 66.3071 | -55.9341 | -56.1264 | -0.027466 | 0.022888 | 0.004577 | 0.42572 | -0.12817 | -0.15106 | 0.027466 | 0.013733 | -0.17853 | -0.027466 | 56.0944 | -0.32959 | -0.15106 | -0.064087 | 122.3236 | 122.3465 | 55.8609 | -122.2961 | 122.2916 | 122.2549 | 56.012 | -122.4976
1079.8594 | 122.5021 | -55.6732 | 66.7053 | 0.0074006 | -0.052767 | 0.12572 | 0.036664 | 0.033932 | -0.041501 | -0.025882 | 7.627e-05 | -0.017468 | 0.025449 | 0.059834 | -0.023892 | -0.027301 | 66.774 | -55.0781 | 0.11444 | -55.7007 | 66.6412 | -55.6229 | -55.6183 | 0.2243 | 0.1831 | -55.8517 | 66.5863 | 66.6092 | -55.6229 | -55.7648 | 0.050354 | 0.054932 | -0.064087 | 0.59509 | -0.027466 | -0.082398 | 0.068665 | 0.050354 | -0.091553 | -0.11902 | 55.8975 | -0.17853 | -0.086975 | -0.09613 | 122.3145 | 122.4472 | 55.7877 | -122.3236 | 122.2595 | 122.2824 | 55.8563 | -122.4701
1081.6406 | 122.612 | -55.5588 | 66.7419 | -0.015487 | -0.05469 | 0.12529 | 0.032605 | 0.034573 | -0.037228 | -0.027805 | -0.015182 | -0.014904 | 0.026731 | 0.060047 | -0.020474 | -0.028369 | 66.8243 | -55.0644 | -0.045776 | -55.6503 | 66.7419 | -55.5496 | -55.5359 | 0.20599 | 0.14648 | -55.7968 | 66.687 | 66.6641 | -55.5313 | -55.6824 | 0.009155 | 0.022888 | 0 | 0.49439 | -0.091553 | -0.11444 | 0.082398 | 0.027466 | -0.1236 | -0.054931 | 55.7648 | -0.23804 | -0.11444 | -0.077819 | 122.3007 | 122.3831 | 55.513 | -122.2778 | 122.2458 | 122.2229 | 55.7053 | -122.4243
1083.4375 | 122.5159 | -55.3757 | 67.0074 | -0.0078584 | -0.051913 | 0.12572 | 0.03346 | 0.036068 | -0.039578 | -0.026096 | 0.0077058 | -0.016186 | 0.02844 | 0.060261 | -0.023251 | -0.027728 | 67.0807 | -54.7943 | 0.013733 | -55.4306 | 66.9205 | -55.3299 | -55.2704 | 0.17853 | 0.1236 | -55.5634 | 66.8838 | 66.8518 | -55.3024 | -55.5038 | 0.045776 | 0.10528 | -0.086975 | 0.58136 | -0.054932 | -0.16022 | 0.073242 | 0.073242 | -0.12817 | -0.1236 | 55.5542 | -0.18768 | -0.059509 | -0.15564 | 122.2961 | 122.4564 | 55.3894 | -122.2778 | 122.2595 | 122.2275 | 55.4993 | -122.5113
1085.1562 | 122.58 | -55.3207 | 66.9983 | -0.0078584 | -0.051913 | 0.12658 | 0.035596 | 0.035427 | -0.033596 | -0.027378 | -0.015182 | -0.013195 | 0.026731 | 0.061329 | -0.018124 | -0.028583 | 67.0532 | -54.8309 | -0.022888 | -55.4489 | 67.012 | -55.3391 | -55.3024 | 0.16937 | 0.10529 | -55.6686 | 66.9571 | 66.9113 | -55.3116 | -55.4993 | -0.01831 | 0.018311 | 0.013733 | 0.48981 | -0.12817 | -0.14649 | 0.054932 | 0.009156 | -0.17853 | -0.041199 | 55.4901 | -0.3479 | -0.16937 | -0.086975 | 122.3328 | 122.374 | 55.2979 | -122.3007 | 122.2778 | 122.2321 | 55.426 | -122.4976
1086.9375 | 122.4701 | -55.1605 | 67.2318 | -0.00022891 | -0.050417 | 0.12786 | 0.034955 | 0.036282 | -0.039792 | -0.027378 | 7.627e-05 | -0.018322 | 0.028013 | 0.059834 | -0.02261 | -0.026874 | 67.2455 | -54.5288 | 0.10529 | -55.2063 | 67.1539 | -55.1239 | -55.0735 | 0.20142 | 0.17853 | -55.3711 | 67.1036 | 67.0944 | -55.0964 | -55.2658 | 0.036621 | 0.086975 | -0.077819 | 0.63171 | -0.045777 | -0.13275 | 0.013733 | 0.064086 | -0.10529 | -0.12817 | 55.3619 | -0.21057 | -0.10529 | -0.13733 | 122.3145 | 122.406 | 55.2658 | -122.3053 | 122.2641 | 122.2549 | 55.3391 | -122.4976
1088.7344 | 122.58 | -55.1239 | 67.1997 | 0.0074006 | -0.052767 | 0.12508 | 0.031537 | 0.037136 | -0.034665 | -0.02631 | 7.627e-05 | -0.012982 | 0.025022 | 0.058766 | -0.019833 | -0.025592 | 67.2684 | -54.6066 | 0.013733 | -55.2109 | 67.2089 | -55.1651 | -55.1102 | 0.20599 | 0.13733 | -55.4214 | 67.1722 | 67.1219 | -55.1056 | -55.2933 | -0.041199 | 0.013733 | 0.009155 | 0.51727 | -0.086975 | -0.10071 | 0.068665 | 0.01831 | -0.16937 | -0.027466 | 55.3299 | -0.29755 | -0.12817 | -0.07782 | 122.3328 | 122.3923 | 55.1376 | -122.3099 | 122.2961 | 122.2458 | 55.2612 | -122.493
1090.5312 | 122.4884 | -55.1697 | 67.2409 | -0.0078584 | -0.057253 | 0.12743 | 0.03346 | 0.032437 | -0.041928 | -0.026737 | 7.627e-05 | -0.018109 | 0.022458 | 0.05727 | -0.023037 | -0.023029 | 67.2638 | -54.5334 | 0.032043 | -55.2109 | 67.1402 | -55.0919 | -55.0964 | 0.14191 | 0.10071 | -55.3528 | 67.1082 | 67.1219 | -55.069 | -55.2475 | 0.07782 | 0.073242 | -0.10071 | 0.63629 | -0.041198 | -0.11444 | 0.022888 | 0.10071 | -0.07782 | -0.13275 | 55.3116 | -0.18311 | -0.10529 | -0.11902 | 122.3099 | 122.4335 | 55.2017 | -122.3373 | 122.2778 | 122.2916 | 55.2704 | -122.4884
1092.2344 | 122.5342 | -55.014 | 67.3874 | -0.0078584 | -0.055758 | 0.12658 | 0.036023 | 0.036068 | -0.04321 | -0.028232 | -0.0075532 | -0.020459 | 0.024808 | 0.056843 | -0.022823 | -0.023883 | 67.4103 | -54.3732 | 0.16937 | -55.0644 | 67.3141 | -54.9866 | -54.9408 | 0.16937 | 0.1236 | -55.1834 | 67.2272 | 67.2409 | -54.95 | -55.1147 | 0.027466 | 0.073242 | -0.073242 | 0.64087 | -0.050354 | -0.1236 | 0.022888 | 0.064087 | -0.10071 | -0.16022 | 55.1834 | -0.16937 | -0.068665 | -0.14648 | 122.3282 | 122.4243 | 55.1834 | -122.3282 | 122.2412 | 122.2549 | 55.1376 | -122.5021
1094.0156 | 122.6028 | -54.9637 | 67.3279 | 0.0074006 | -0.051913 | 0.12487 | 0.035382 | 0.035214 | -0.032101 | -0.026951 | -0.0075532 | -0.013623 | 0.028013 | 0.060261 | -0.020046 | -0.02901 | 67.4286 | -54.4281 | 0.018311 | -55.0735 | 67.3691 | -54.9866 | -54.9728 | 0.20142 | 0.10529 | -55.275 | 67.2867 | 67.2913 | -54.9957 | -55.1376 | -0.022888 | -0.009155 | 0.041199 | 0.53558 | -0.10986 | -0.10071 | 0.10071 | -0.032044 | -0.17395 | -0.041199 | 55.1651 | -0.31128 | -0.13733 | -0.036621 | 122.3328 | 122.3923 | 54.982 | -122.3007 | 122.2504 | 122.2549 | 55.069 | -122.4655
1095.8125 | 122.5159 | -54.7485 | 67.6117 | -0.00022891 | -0.054476 | 0.12786 | 0.035809 | 0.033077 | -0.042782 | -0.027591 | -0.0075532 | -0.017682 | 0.02609 | 0.058338 | -0.023678 | -0.024951 | 67.6941 | -54.0665 | 0.14191 | -54.7806 | 67.543 | -54.7119 | -54.6753 | 0.17395 | 0.12817 | -54.9271 | 67.5201 | 67.4835 | -54.6982 | -54.8584 | 0.036621 | 0.073242 | -0.068664 | 0.68207 | -0.032044 | -0.10529 | 0.082398 | 0.050354 | -0.10986 | -0.091552 | 54.9225 | -0.17853 | -0.068665 | -0.12817 | 122.2916 | 122.4426 | 54.8904 | -122.287 | 122.2687 | 122.2321 | 54.8767 | -122.4701
1097.6094 | 122.612 | -54.4739 | 67.8497 | -0.00022891 | -0.054262 | 0.12465 | 0.034741 | 0.034359 | -0.036801 | -0.02631 | 7.627e-05 | -0.012768 | 0.028653 | 0.062824 | -0.02026 | -0.026019 | 67.9092 | -53.9246 | -0.013733 | -54.5746 | 67.8452 | -54.4785 | -54.4464 | 0.14648 | 0.086975 | -54.7028 | 67.7902 | 67.7536 | -54.4601 | -54.5929 | -0.004578 | 0.027466 | -0.004577 | 0.54932 | -0.10071 | -0.12817 | 0.05951 | 0.013733 | -0.11902 | -0.059509 | 54.6204 | -0.22888 | -0.10986 | -0.09613 | 122.319 | 122.3831 | 54.4601 | -122.2961 | 122.2641 | 122.2275 | 54.5609 | -122.4426
1099.3281 | 122.4564 | -54.4281 | 67.9413 | -0.0078584 | -0.054476 | 0.12764 | 0.035596 | 0.036495 | -0.038937 | -0.02866 | 0.0077058 | -0.013623 | 0.027158 | 0.058979 | -0.023464 | -0.028583 | 67.9962 | -53.7506 | 0.19226 | -54.4739 | 67.8864 | -54.3915 | -54.3823 | 0.13733 | 0.041199 | -54.6753 | 67.8497 | 67.8314 | -54.4052 | -54.5563 | 0.036622 | 0.045777 | -0.054931 | 0.67749 | -0.045776 | -0.091553 | 0.054932 | 0.022889 | -0.12817 | -0.091553 | 54.5654 | -0.24719 | -0.11902 | -0.10986 | 122.3145 | 122.4243 | 54.6204 | -122.3236 | 122.2778 | 122.2595 | 54.4693 | -122.4976
1101.125 | 122.4701 | -54.6433 | 67.7628 | 0.0074006 | -0.053622 | 0.12743 | 0.033887 | 0.033505 | -0.041287 | -0.027805 | 0.0077058 | -0.018109 | 0.025235 | 0.060047 | -0.021114 | -0.025806 | 67.7948 | -53.9749 | 0.073242 | -54.689 | 67.6941 | -54.5929 | -54.5425 | 0.091553 | -0.013733 | -54.8447 | 67.6437 | 67.662 | -54.5425 | -54.7485 | 0.050354 | 0.10071 | -0.068664 | 0.66833 | -0.045776 | -0.14648 | 0.032044 | 0.10071 | -0.10528 | -0.11902 | 54.7348 | -0.20142 | -0.096131 | -0.10071 | 122.3373 | 122.4381 | 54.7165 | -122.3053 | 122.287 | 122.3053 | 54.6295 | -122.5113
1102.9219 | 122.4655 | -54.3961 | 68.0099 | -0.0078584 | -0.052553 | 0.127 | 0.037091 | 0.034359 | -0.040432 | -0.027378 | -0.0075532 | -0.017468 | 0.027372 | 0.060047 | -0.024532 | -0.028796 | 68.0557 | -53.627 | 0.28839 | -54.4052 | 67.923 | -54.364 | -54.3091 | 0.13275 | 0.068665 | -54.5883 | 67.8818 | 67.868 | -54.3182 | -54.4922 | 0.032043 | 0.086975 | -0.086975 | 0.76904 | -0.009155 | -0.09613 | 0.045776 | 0.07782 | -0.09613 | -0.12817 | 54.5288 | -0.19226 | -0.096131 | -0.14191 | 122.319 | 122.4518 | 54.6844 | -122.319 | 122.2778 | 122.2641 | 54.4647 | -122.5021
1104.7188 | 122.5937 | -54.2679 | 68.042 | -0.0078584 | -0.051058 | 0.12465 | 0.031323 | 0.031796 | -0.03146 | -0.027805 | -0.0075532 | -0.010418 | 0.025022 | 0.062397 | -0.017056 | -0.025378 | 68.129 | -53.6133 | 0.25635 | -54.3549 | 68.0603 | -54.2816 | -54.277 | 0.13733 | 0.050354 | -54.5609 | 68.0008 | 67.9825 | -54.2725 | -54.4235 | -0.013733 | -0.009156 | 0.018311 | 0.6546 | -0.086975 | -0.077819 | 0.086975 | -0.004578 | -0.15564 | -0.041199 | 54.4052 | -0.29297 | -0.13733 | -0.059509 | 122.3282 | 122.3969 | 54.5242 | -122.319 | 122.2687 | 122.2504 | 54.3182 | -122.4655
1106.5 | 122.5754 | -53.6682 | 68.6691 | -0.00022891 | -0.051699 | 0.12615 | 0.03645 | 0.035 | -0.037655 | -0.027591 | -0.0075532 | -0.012341 | 0.028013 | 0.060261 | -0.021542 | -0.026447 | 68.66 | -53.0411 | 0.2655 | -53.7781 | 68.692 | -53.6957 | -53.6453 | 0.009155 | -0.032043 | -53.9886 | 68.6325 | 68.6005 | -53.6591 | -53.8147 | -0.027466 | 0.022888 | 0.022889 | 0.62714 | -0.10986 | -0.13275 | -0.009155 | 0.009155 | -0.14648 | -0.036621 | 53.6774 | -0.32043 | -0.17395 | -0.068664 | 122.3602 | 122.3282 | 53.9337 | -122.3145 | 122.3007 | 122.2687 | 53.6362 | -122.4838
1108.2188 | 122.5296 | -53.4531 | 68.9438 | -0.00022891 | -0.049563 | 0.127 | 0.03645 | 0.035214 | -0.039364 | -0.025028 | 7.627e-05 | -0.013409 | 0.027585 | 0.060688 | -0.02261 | -0.025378 | 68.8934 | -52.7573 | 0.29297 | -53.54 | 68.9392 | -53.4393 | -53.3981 | -0.004578 | 0 | -53.7552 | 68.8751 | 68.8477 | -53.4348 | -53.5675 | 0.013733 | 0.054932 | -0.004578 | 0.6958 | -0.086975 | -0.14191 | -0.050354 | 0.018311 | -0.11444 | -0.068665 | 53.4485 | -0.30212 | -0.18768 | -0.096131 | 122.3923 | 122.3465 | 53.746 | -122.3419 | 122.3282 | 122.3007 | 53.4531 | -122.5113
1110 | 122.4792 | -53.7735 | 68.6325 | -0.015487 | -0.057467 | 0.12914 | 0.034101 | 0.035 | -0.041928 | -0.027164 | 0.0077058 | -0.018322 | 0.024808 | 0.060047 | -0.023251 | -0.02666 | 68.6096 | -53.0136 | 0.27924 | -53.8467 | 68.5181 | -53.7231 | -53.7048 | -0.032043 | -0.045776 | -53.9932 | 68.4814 | 68.4677 | -53.714 | -53.8742 | 0.050354 | 0.068665 | -0.11444 | 0.75989 | -0.073242 | -0.14191 | -0.022888 | 0.05951 | -0.10071 | -0.15106 | 53.7415 | -0.21973 | -0.11902 | -0.16479 | 122.2916 | 122.3831 | 54.0527 | -122.3373 | 122.2549 | 122.2412 | 53.7277 | -122.5067
1111.7656 | 122.4792 | -53.5675 | 68.8339 | -0.0078584 | -0.053835 | 0.12807 | 0.034314 | 0.034786 | -0.038723 | -0.026737 | 7.627e-05 | -0.015545 | 0.026731 | 0.058552 | -0.021969 | -0.026874 | 68.866 | -52.7756 | 0.49439 | -53.5812 | 68.7195 | -53.5492 | -53.5172 | 0.036621 | 0.045776 | -53.7781 | 68.7149 | 68.692 | -53.5126 | -53.6682 | 0.018311 | 0.050354 | -0.11444 | 0.79193 | -0.013733 | -0.064087 | 0.032044 | 0.054932 | -0.10071 | -0.11902 | 53.6041 | -0.21057 | -0.10986 | -0.14191 | 122.287 | 122.4335 | 54.0619 | -122.3511 | 122.2824 | 122.2595 | 53.6133 | -122.5021
1113.5625 | 122.6028 | -53.1967 | 69.104 | -0.00022891 | -0.050417 | 0.12615 | 0.034314 | 0.035 | -0.032956 | -0.025882 | 0.015335 | -0.011486 | 0.025663 | 0.060902 | -0.021114 | -0.026019 | 69.1498 | -52.533 | 0.4303 | -53.3203 | 69.1269 | -53.2196 | -53.1967 | 0.004578 | -0.032043 | -53.5263 | 69.0674 | 69.0628 | -53.2059 | -53.3569 | -0.022888 | 0 | 0.022888 | 0.66376 | -0.1236 | -0.1236 | 0.045776 | -0.009156 | -0.16022 | -0.036621 | 53.2013 | -0.32959 | -0.16937 | -0.041199 | 122.3236 | 122.3465 | 53.627 | -122.3007 | 122.2641 | 122.2595 | 53.1647 | -122.4609
1115.3438 | 122.6303 | -53.0182 | 69.2825 | -0.00022891 | -0.052981 | 0.127 | 0.032178 | 0.03265 | -0.035092 | -0.026523 | 7.627e-05 | -0.011914 | 0.02609 | 0.060474 | -0.020901 | -0.024524 | 69.3192 | -52.3636 | 0.43488 | -53.1509 | 69.2825 | -53.0365 | -53.0045 | -0.027466 | -0.13733 | -53.3295 | 69.2459 | 69.2093 | -53.0136 | -53.1555 | -0.018311 | 0.013732 | 0 | 0.6546 | -0.13275 | -0.14648 | 0.036621 | 0.004577 | -0.13733 | -0.036621 | 52.9907 | -0.31128 | -0.17395 | -0.073242 | 122.3007 | 122.3373 | 53.4531 | -122.287 | 122.2641 | 122.2275 | 52.8809 | -122.4381
1117.0469 | 122.5296 | -52.7115 | 69.6762 | -0.0078584 | -0.056185 | 0.12615 | 0.030683 | 0.034786 | -0.039151 | -0.024814 | 0.0077058 | -0.017041 | 0.025022 | 0.058338 | -0.021755 | -0.026447 | 69.722 | -51.8875 | 0.6546 | -52.7481 | 69.5938 | -52.6611 | -52.6474 | 0.07782 | 0.10071 | -52.9129 | 69.5343 | 69.5114 | -52.6703 | -52.803 | 0.050354 | 0.064087 | -0.082397 | 0.82397 | -0.036621 | -0.10071 | 0.045777 | 0.041199 | -0.091553 | -0.14191 | 52.7893 | -0.20142 | -0.10986 | -0.16479 | 122.3053 | 122.4335 | 53.3661 | -122.3236 | 122.2458 | 122.2229 | 52.8122 | -122.4792
1118.8281 | 122.5021 | -52.4414 | 69.9738 | -0.00022891 | -0.05469 | 0.12807 | 0.036237 | 0.035641 | -0.041928 | -0.028019 | -0.0075532 | -0.018109 | 0.025663 | 0.058766 | -0.022396 | -0.026233 | 70.0287 | -51.5625 | 0.93384 | -52.4368 | 69.8868 | -52.359 | -52.359 | 0.13275 | 0.10529 | -52.6062 | 69.8135 | 69.7952 | -52.3727 | -52.5513 | 0.082397 | 0.082397 | -0.086975 | 0.87891 | 0.004577 | -0.07782 | 0.054932 | 0.068664 | -0.10986 | -0.16022 | 52.5742 | -0.16479 | -0.054931 | -0.17853 | 122.3282 | 122.4701 | 53.3752 | -122.3328 | 122.2549 | 122.2366 | 52.5467 | -122.525
1120.625 | 122.4701 | -52.6245 | 69.7906 | -0.0078584 | -0.054476 | 0.12914 | 0.036664 | 0.034146 | -0.037869 | -0.030155 | 7.627e-05 | -0.0117 | 0.027372 | 0.058552 | -0.024319 | -0.027728 | 69.7861 | -51.8188 | 0.87433 | -52.6657 | 69.7311 | -52.597 | -52.5787 | 0.068665 | 0.018311 | -52.9037 | 69.7083 | 69.6259 | -52.6108 | -52.771 | 0.027466 | 0.045777 | -0.059509 | 0.80566 | -0.041198 | -0.086975 | -0.004577 | 0.013733 | -0.14648 | -0.082397 | 52.6932 | -0.27924 | -0.13275 | -0.16479 | 122.3557 | 122.4106 | 53.4988 | -122.3694 | 122.3328 | 122.2504 | 52.6428 | -122.5616
1122.4062 | 122.6212 | -52.2858 | 70.0607 | -0.0078584 | -0.054262 | 0.127 | 0.030896 | 0.033932 | -0.033169 | -0.024814 | 7.627e-05 | -0.012982 | 0.028226 | 0.060474 | -0.019406 | -0.026447 | 70.0333 | -51.6174 | 0.78278 | -52.4094 | 70.0378 | -52.3132 | -52.2766 | 0.036621 | 0 | -52.6428 | 70.0104 | 69.9509 | -52.2949 | -52.4643 | -0.027465 | 0.009156 | -0.022888 | 0.66833 | -0.1236 | -0.13275 | -0.027466 | -0.009155 | -0.17853 | -0.050354 | 52.3224 | -0.35706 | -0.17853 | -0.10986 | 122.3236 | 122.319 | 53.0685 | -122.3373 | 122.2961 | 122.2366 | 52.2858 | -122.525
1124.1406 | 122.493 | -51.9836 | 70.4178 | -0.00022891 | -0.056399 | 0.12828 | 0.033887 | 0.035 | -0.040005 | -0.029514 | 7.627e-05 | -0.016186 | 0.026304 | 0.057484 | -0.021755 | -0.026019 | 70.4086 | -51.1368 | 1.0162 | -52.0294 | 70.3354 | -51.9196 | -51.8875 | 0.009155 | 0.018311 | -52.1942 | 70.3171 | 70.2896 | -51.9333 | -52.066 | 0.064087 | 0.096131 | -0.082398 | 0.84686 | -0.045776 | -0.14191 | -0.009156 | 0.050354 | -0.082397 | -0.10071 | 51.9928 | -0.21057 | -0.12817 | -0.12817 | 122.319 | 122.3923 | 52.9999 | -122.3053 | 122.3007 | 122.2733 | 52.002 | -122.4838
1125.9375 | 122.5525 | -51.6861 | 70.7062 | -0.00022891 | -0.053408 | 0.12935 | 0.03645 | 0.034146 | -0.039364 | -0.028232 | 7.627e-05 | -0.014904 | 0.027585 | 0.05727 | -0.025173 | -0.027301 | 70.7199 | -50.7935 | 1.0391 | -51.6998 | 70.6421 | -51.6495 | -51.5991 | 0.018311 | -0.009155 | -51.86 | 70.578 | 70.5414 | -51.6083 | -51.7914 | 0.036621 | 0.086975 | -0.064087 | 0.89264 | -0.013733 | -0.10071 | 0.013733 | 0.07782 | -0.10529 | -0.12817 | 51.7044 | -0.17395 | -0.068664 | -0.16479 | 122.3282 | 122.406 | 52.7252 | -122.3053 | 122.2641 | 122.2275 | 51.6769 | -122.4976
1127.7344 | 122.5662 | -51.3702 | 71.0083 | -0.00022891 | -0.051913 | 0.12764 | 0.033673 | 0.034146 | -0.031033 | -0.024601 | 7.627e-05 | -0.010632 | 0.025663 | 0.059406 | -0.019619 | -0.028369 | 71.0037 | -50.6012 | 0.97961 | -51.4664 | 70.9579 | -51.3748 | -51.329 | -0.036621 | -0.082397 | -51.7136 | 70.9396 | 70.8755 | -51.384 | -51.5259 | -0.004578 | 0.041198 | -0.050354 | 0.76904 | -0.096131 | -0.13733 | -0.004578 | -0.013733 | -0.15564 | -0.068665 | 51.3336 | -0.34332 | -0.18768 | -0.13275 | 122.3282 | 122.374 | 52.3499 | -122.3373 | 122.3099 | 122.2458 | 51.2878 | -122.5342
1129.5156 | 122.5983 | -50.9628 | 71.3425 | -0.0078584 | -0.047213 | 0.12807 | 0.03645 | 0.03265 | -0.035092 | -0.025669 | 7.627e-05 | -0.012768 | 0.027799 | 0.059193 | -0.020687 | -0.026019 | 71.3562 | -50.2167 | 0.98877 | -51.0727 | 71.3791 | -50.9949 | -50.9766 | -0.032043 | 0.1236 | -51.3016 | 71.3058 | 71.2509 | -50.9949 | -51.1414 | -0.032043 | -0.013732 | 0.036621 | 0.74615 | -0.10986 | -0.096131 | 0.013733 | -0.032043 | -0.17853 | -0.036621 | 50.9308 | -0.33875 | -0.16022 | -0.091552 | 122.3419 | 122.319 | 51.9516 | -122.319 | 122.2687 | 122.2137 | 51.0864 | -122.4838
1131.2969 | 122.5204 | -50.4044 | 71.9513 | -0.00022891 | -0.057467 | 0.12893 | 0.033032 | 0.034146 | -0.043637 | -0.02631 | -0.0075532 | -0.018109 | 0.026517 | 0.057697 | -0.025173 | -0.024951 | 71.9238 | -49.53 | 0.99335 | -50.4593 | 71.8872 | -50.386 | -50.3952 | -0.004578 | 0.11902 | -50.6149 | 71.8369 | 71.814 | -50.354 | -50.5325 | 0.018311 | 0.009155 | -0.064087 | 0.87433 | -0.054932 | -0.064087 | -0.027466 | 0.050354 | -0.12817 | -0.11444 | 50.3998 | -0.21057 | -0.082397 | -0.13733 | 122.2916 | 122.3282 | 51.3977 | -122.3465 | 122.2412 | 122.2183 | 50.5234 | -122.4838
1133.0938 | 122.5571 | -49.9054 | 72.4319 | -0.00022891 | -0.05234 | 0.12764 | 0.033032 | 0.034573 | -0.033169 | -0.024387 | 7.627e-05 | -0.014264 | 0.028013 | 0.060902 | -0.018978 | -0.025378 | 72.4045 | -49.173 | 0.86517 | -50.0381 | 72.4411 | -49.9283 | -49.9191 | -0.10529 | -0.027466 | -50.3036 | 72.377 | 72.3175 | -49.9191 | -50.0702 | -0.022888 | -0.013732 | 0.009155 | 0.73242 | -0.13275 | -0.11902 | -0.027466 | -0.013732 | -0.16479 | -0.054932 | 49.8001 | -0.39825 | -0.23346 | -0.11444 | 122.3465 | 122.3099 | 50.7706 | -122.3511 | 122.2824 | 122.2229 | 49.8779 | -122.5021
1134.8125 | 122.5021 | -49.6811 | 72.6974 | 0.0074006 | -0.05704 | 0.12551 | 0.036237 | 0.034573 | -0.040432 | -0.025882 | -0.0075532 | -0.016613 | 0.023099 | 0.059193 | -0.023464 | -0.027087 | 72.7341 | -48.761 | 1.0895 | -49.7131 | 72.6151 | -49.6353 | -49.6445 | -0.009155 | -0.10071 | -49.8825 | 72.5693 | 72.5418 | -49.617 | -49.7772 | 0.045776 | 0.036621 | -0.082398 | 0.9201 | -0.032044 | -0.068665 | 0.036621 | 0.064087 | -0.096131 | -0.12817 | 49.6719 | -0.20142 | -0.10528 | -0.15564 | 122.2961 | 122.4152 | 50.7706 | -122.3419 | 122.2504 | 122.2229 | 49.5804 | -122.4747
1136.5938 | 122.5571 | -49.2096 | 73.1461 | -0.00022891 | -0.055117 | 0.12828 | 0.031964 | 0.037136 | -0.038083 | -0.027378 | -0.0075532 | -0.013836 | 0.027372 | 0.059834 | -0.020901 | -0.026233 | 73.1369 | -48.3765 | 1.1032 | -49.2874 | 73.1735 | -49.1959 | -49.1821 | -0.09613 | 0.091553 | -49.5346 | 73.1277 | 73.0682 | -49.1776 | -49.3378 | 0.013733 | 0.027466 | 0.027466 | 0.83313 | -0.07782 | -0.10529 | -0.009155 | 0.032044 | -0.12817 | -0.01831 | 49.1135 | -0.32501 | -0.19684 | -0.07782 | 122.3831 | 122.3465 | 50.3128 | -122.3282 | 122.3373 | 122.2778 | 49.3011 | -122.4838
1138.3125 | 122.5708 | -48.8022 | 73.4711 | -0.00022891 | -0.050631 | 0.12764 | 0.033673 | 0.034786 | -0.033596 | -0.027805 | 7.627e-05 | -0.013836 | 0.024381 | 0.059193 | -0.020046 | -0.026447 | 73.5718 | -47.9874 | 1.3458 | -48.8983 | 73.5214 | -48.8342 | -48.8068 | -0.068665 | 0.07782 | -49.1318 | 73.4711 | 73.4528 | -48.793 | -48.967 | -0.032044 | -0.004578 | 0.050354 | 0.81482 | -0.09613 | -0.091552 | 0.10071 | 0.009155 | -0.16479 | 0 | 48.7335 | -0.32959 | -0.16479 | -0.01831 | 122.3236 | 122.374 | 50.148 | -122.2778 | 122.2733 | 122.2549 | 48.88 | -122.438
1140.1094 | 122.525 | -48.2071 | 74.1943 | -0.00022891 | -0.05469 | 0.12957 | 0.034101 | 0.035 | -0.041928 | -0.026951 | 0.015335 | -0.017254 | 0.025235 | 0.058552 | -0.024746 | -0.02431 | 74.1394 | -47.319 | 1.4328 | -48.2666 | 74.1165 | -48.1567 | -48.1567 | -0.18768 | -0.004578 | -48.4451 | 74.0845 | 74.0707 | -48.143 | -48.3124 | 0.050354 | 0.050354 | -0.07782 | 0.88806 | -0.05951 | -0.10986 | -0.054932 | 0.064087 | -0.10529 | -0.10986 | 48.0194 | -0.23804 | -0.13275 | -0.1236 | 122.3236 | 122.3465 | 49.6399 | -122.3511 | 122.2916 | 122.2778 | 48.2025 | -122.5067
1141.8906 | 122.4518 | -47.7356 | 74.7025 | -0.0078584 | -0.052981 | 0.12807 | 0.0388 | 0.035 | -0.038296 | -0.028232 | 7.627e-05 | -0.015759 | 0.025449 | 0.058979 | -0.024319 | -0.026019 | 74.7025 | -46.7514 | 1.5015 | -47.7356 | 74.6201 | -47.6624 | -47.6532 | -0.15106 | -0.073242 | -47.9553 | 74.6063 | 74.5514 | -47.6761 | -47.7859 | 0.073242 | 0.082398 | -0.082398 | 0.98419 | 0 | -0.082398 | 0 | 0.05951 | -0.050354 | -0.096131 | 47.5845 | -0.21973 | -0.16937 | -0.15106 | 122.3557 | 122.4381 | 49.2371 | -122.3557 | 122.3419 | 122.287 | 47.6624 | -122.4884
1143.625 | 122.5113 | -47.9645 | 74.4232 | -0.0078584 | -0.055117 | 0.12636 | 0.036664 | 0.035855 | -0.042569 | -0.026523 | 7.627e-05 | -0.017041 | 0.026944 | 0.057484 | -0.02496 | -0.028796 | 74.4049 | -47.0673 | 1.2817 | -48.0286 | 74.3774 | -47.9507 | -47.9324 | -0.30212 | -0.14191 | -48.2025 | 74.3042 | 74.295 | -47.9279 | -48.0972 | 0.013733 | 0.032044 | -0.045777 | 0.89722 | -0.064086 | -0.09613 | -0.018311 | 0.036622 | -0.13275 | -0.11902 | 47.6624 | -0.23804 | -0.10529 | -0.12817 | 122.3419 | 122.3694 | 49.2462 | -122.3557 | 122.2687 | 122.2595 | 47.8226 | -122.5204
1145.4219 | 122.525 | -48.3261 | 74.0616 | -0.00022891 | -0.051699 | 0.12978 | 0.034528 | 0.033077 | -0.035946 | -0.025028 | 7.627e-05 | -0.015118 | 0.027158 | 0.060474 | -0.020046 | -0.02666 | 74.025 | -47.4747 | 1.2497 | -48.4085 | 74.0616 | -48.3307 | -48.3078 | -0.31586 | -0.2243 | -48.6465 | 74.025 | 73.9609 | -48.3261 | -48.4543 | -0.004577 | 0.018311 | 0 | 0.85144 | -0.082397 | -0.10071 | -0.036621 | 0 | -0.12817 | -0.036621 | 48.0103 | -0.32043 | -0.19226 | -0.10071 | 122.3877 | 122.3511 | 49.5758 | -122.3694 | 122.3511 | 122.287 | 48.1018 | -122.5159
1147.2031 | 122.5616 | -48.7885 | 73.5535 | -0.00022891 | -0.051485 | 0.12679 | 0.031964 | 0.033718 | -0.036801 | -0.024173 | 7.627e-05 | -0.015759 | 0.025449 | 0.060474 | -0.019192 | -0.027515 | 73.6404 | -47.7951 | 1.3046 | -48.8113 | 73.5168 | -48.7793 | -48.7473 | -0.32044 | -0.25177 | -49.0219 | 73.4528 | 73.4802 | -48.761 | -48.912 | 0.009155 | 0.041199 | -0.036621 | 0.99335 | -0.022888 | -0.064087 | 0.086975 | 0.027466 | -0.1236 | -0.10071 | 48.468 | -0.23346 | -0.10986 | -0.073242 | 122.3053 | 122.4289 | 50.0931 | -122.3007 | 122.2412 | 122.2687 | 48.5367 | -122.4655
1148.9375 | 122.5845 | -47.7585 | 74.5468 | -0.00022891 | -0.051699 | 0.12636 | 0.034528 | 0.033291 | -0.033169 | -0.02396 | 7.627e-05 | -0.014477 | 0.027372 | 0.05962 | -0.018978 | -0.028583 | 74.5193 | -46.962 | 1.1124 | -47.905 | 74.5468 | -47.8043 | -47.7951 | -0.43488 | -0.39368 | -48.1705 | 74.4965 | 74.4873 | -47.7997 | -47.9645 | -0.045776 | -0.036621 | 0 | 0.79651 | -0.14648 | -0.10986 | -0.027466 | -0.041199 | -0.20599 | -0.050354 | 47.3236 | -0.41199 | -0.20599 | -0.059509 | 122.3053 | 122.2778 | 48.8709 | -122.3419 | 122.2549 | 122.2458 | 47.3648 | -122.5113
1150.7344 | 122.5525 | -47.4655 | 74.8764 | -0.0078584 | -0.048495 | 0.12722 | 0.031323 | 0.034786 | -0.034237 | -0.024601 | 0.0077058 | -0.012341 | 0.027372 | 0.061115 | -0.016628 | -0.025806 | 74.8901 | -46.5546 | 1.0712 | -47.5708 | 74.8581 | -47.4701 | -47.4701 | -0.52643 | -0.3891 | -47.8455 | 74.8306 | 74.8077 | -47.4747 | -47.6303 | -0.004578 | -0.004578 | -0.018311 | 0.91095 | -0.10529 | -0.10071 | 0.013733 | -0.009155 | -0.16479 | -0.045777 | 46.9391 | -0.37994 | -0.21515 | -0.068665 | 122.3236 | 122.3557 | 48.5367 | -122.3465 | 122.2961 | 122.2733 | 47.0764 | -122.5067
1152.4531 | 122.6074 | -47.612 | 74.7299 | -0.0078584 | -0.053622 | 0.127 | 0.03346 | 0.033291 | -0.038083 | -0.025242 | 7.627e-05 | -0.013409 | 0.029294 | 0.060047 | -0.020046 | -0.027728 | 74.7986 | -46.6599 | 1.149 | -47.6624 | 74.675 | -47.5891 | -47.5845 | -0.62714 | -0.20142 | -47.8775 | 74.6292 | 74.6017 | -47.5754 | -47.7448 | 0.022889 | 0.027466 | -0.054931 | 0.95215 | -0.050354 | -0.07782 | 0.068665 | 0.036622 | -0.13275 | -0.10071 | 46.9849 | -0.2655 | -0.13275 | -0.12817 | 122.287 | 122.4106 | 48.761 | -122.3145 | 122.2412 | 122.2137 | 47.4106 | -122.4747
1154.25 | 122.5479 | -47.1771 | 75.1877 | -0.0078584 | -0.048281 | 0.12679 | 0.030683 | 0.036709 | -0.033383 | -0.024173 | 0.0077058 | -0.013195 | 0.026517 | 0.05962 | -0.019192 | -0.026019 | 75.1602 | -46.3028 | 0.95673 | -47.2641 | 75.1465 | -47.1725 | -47.1588 | -0.86517 | -0.49439 | -47.5479 | 75.1602 | 75.1099 | -47.1771 | -47.3236 | 0.004578 | 0.018311 | -0.041199 | 0.87433 | -0.086975 | -0.10529 | -0.027466 | 0 | -0.14648 | -0.027466 | 46.312 | -0.37079 | -0.22431 | -0.07782 | 122.3236 | 122.3373 | 48.1339 | -122.3465 | 122.3373 | 122.287 | 46.6827 | -122.5113
1156.0469 | 122.4976 | -46.7926 | 75.6088 | -0.00022891 | -0.057894 | 0.12786 | 0.034528 | 0.035 | -0.043423 | -0.027805 | 0.0077058 | -0.019391 | 0.025663 | 0.057697 | -0.020901 | -0.023242 | 75.6454 | -45.694 | 1.1444 | -46.788 | 75.531 | -46.7331 | -46.7422 | -0.79651 | -0.39825 | -46.9711 | 75.4852 | 75.4486 | -46.7148 | -46.8658 | 0.05951 | 0.050354 | -0.07782 | 1.0986 | 0.004578 | -0.045776 | 0.036621 | 0.07782 | -0.073242 | -0.1236 | 45.9961 | -0.17853 | -0.10529 | -0.16022 | 122.3236 | 122.4381 | 47.937 | -122.3511 | 122.2778 | 122.2412 | 46.3943 | -122.4747
1157.7656 | 122.6074 | -46.6141 | 75.7324 | 0.0074006 | -0.053408 | 0.12722 | 0.03346 | 0.034573 | -0.035519 | -0.025455 | -0.0075532 | -0.015332 | 0.024808 | 0.059406 | -0.016415 | -0.026019 | 75.7507 | -45.6482 | 1.03 | -46.669 | 75.7095 | -46.5683 | -46.582 | -1.03 | -0.97961 | -46.8704 | 75.6409 | 75.5951 | -46.5912 | -46.7285 | 0.045777 | 0.032044 | -0.022888 | 0.96588 | -0.054931 | -0.086975 | 0.01831 | 0.022888 | -0.11444 | -0.091553 | 45.5841 | -0.25635 | -0.14191 | -0.13733 | 122.3236 | 122.3648 | 47.644 | -122.3145 | 122.2549 | 122.2092 | 45.6345 | -122.4609
1159.5469 | 122.6074 | -46.4355 | 75.8698 | -0.00022891 | -0.050204 | 0.12593 | 0.034528 | 0.030941 | -0.034878 | -0.025242 | 7.627e-05 | -0.015332 | 0.028013 | 0.058766 | -0.021969 | -0.02666 | 75.8972 | -45.5246 | 1.0574 | -46.5317 | 75.8972 | -46.4767 | -46.4584 | -1.0025 | -0.737 | -46.7697 | 75.824 | 75.7828 | -46.4722 | -46.6278 | -0.041199 | -0.022888 | 0.027466 | 0.91095 | -0.09613 | -0.073242 | 0.027466 | -0.036621 | -0.19226 | -0.045776 | 45.433 | -0.33417 | -0.14191 | -0.086975 | 122.3328 | 122.3328 | 47.493 | -122.3282 | 122.2595 | 122.2183 | 45.6985 | -122.4976
1161.3281 | 122.4655 | -46.2982 | 76.1078 | -0.00022891 | -0.055331 | 0.12957 | 0.033673 | 0.033505 | -0.041073 | -0.027805 | -0.0075532 | -0.015118 | 0.024808 | 0.058552 | -0.023037 | -0.024524 | 76.1307 | -45.2316 | 1.0574 | -46.3303 | 76.0208 | -46.2341 | -46.225 | -1.1581 | -1.0529 | -46.5042 | 76.0071 | 75.9796 | -46.2296 | -46.3898 | 0.064087 | 0.073242 | -0.086975 | 1.0666 | -0.032043 | -0.10529 | 0.022888 | 0.068665 | -0.091553 | -0.10071 | 45.1401 | -0.20599 | -0.11444 | -0.12817 | 122.319 | 122.4289 | 47.3557 | -122.3328 | 122.3053 | 122.2778 | 45.2454 | -122.4976
1163.0469 | 122.4701 | -46.051 | 76.3275 | -0.0078584 | -0.054262 | 0.13063 | 0.034741 | 0.031155 | -0.040219 | -0.028019 | 7.627e-05 | -0.018536 | 0.025663 | 0.058125 | -0.023251 | -0.025378 | 76.3458 | -44.9844 | 1.1032 | -46.0739 | 76.2451 | -46.0098 | -46.0144 | -1.2451 | -1.0666 | -46.2708 | 76.2268 | 76.1902 | -46.019 | -46.1517 | 0.041198 | 0.036621 | -0.082398 | 1.0666 | -0.022889 | -0.05951 | 0.01831 | 0.032043 | -0.10071 | -0.10071 | 44.8059 | -0.21973 | -0.11902 | -0.13733 | 122.2961 | 122.3969 | 47.1542 | -122.3419 | 122.2778 | 122.2412 | 44.9844 | -122.4792
1164.8438 | 122.525 | -46.9803 | 75.4532 | 0.0074006 | -0.055117 | 0.12999 | 0.035809 | 0.033505 | -0.040432 | -0.027164 | 7.627e-05 | -0.018963 | 0.029081 | 0.056202 | -0.025173 | -0.027728 | 75.3845 | -45.9091 | 0.88348 | -46.994 | 75.3845 | -46.9208 | -46.9025 | -1.4191 | -1.4511 | -47.2137 | 75.3067 | 75.3113 | -46.9162 | -47.0718 | 0.05951 | 0.07782 | -0.068665 | 1.0712 | -0.013733 | -0.091553 | -0.068665 | 0.064087 | -0.091552 | -0.14648 | 45.5612 | -0.23346 | -0.14191 | -0.14191 | 122.3648 | 122.3648 | 47.8638 | -122.3557 | 122.287 | 122.2916 | 45.5292 | -122.525
1166.6406 | 122.4792 | -46.907 | 75.5127 | 0.0074006 | -0.053194 | 0.127 | 0.037305 | 0.033718 | -0.039792 | -0.028446 | 0.015335 | -0.016613 | 0.026944 | 0.05727 | -0.02261 | -0.02901 | 75.5264 | -45.726 | 0.98419 | -46.8933 | 75.4257 | -46.8475 | -46.8246 | -1.5518 | -1.3596 | -47.1085 | 75.3708 | 75.3342 | -46.8704 | -47.0032 | 0.059509 | 0.082397 | -0.086975 | 1.181 | 0.013732 | -0.068665 | 0.013733 | 0.036621 | -0.096131 | -0.14191 | 45.3552 | -0.20142 | -0.10529 | -0.17853 | 122.3328 | 122.4335 | 47.8912 | -122.3373 | 122.2778 | 122.2412 | 45.5475 | -122.5159
1168.4219 | 122.5845 | -42.2287 | 80.1132 | 0.0074006 | -0.04999 | 0.12722 | 0.032605 | 0.036282 | -0.031887 | -0.029087 | 0.0077058 | -0.011486 | 0.026731 | 0.060688 | -0.017697 | -0.028796 | 80.1086 | -41.304 | 1.6067 | -42.3477 | 80.0766 | -42.2516 | -42.2562 | -1.2863 | -0.99792 | -42.5674 | 80.04 | 79.9713 | -42.2424 | -42.4118 | -0.022888 | -0.027466 | -0.036621 | 0.92468 | -0.11902 | -0.091552 | -0.004577 | -0.013733 | -0.1831 | -0.073242 | 40.9424 | -0.33875 | -0.15564 | -0.14191 | 122.3053 | 122.3373 | 43.8354 | -122.3694 | 122.2687 | 122.2 | 41.2308 | -122.525
1170.2031 | 122.4335 | -38.1134 | 84.3475 | -0.00022891 | -0.051272 | 0.12807 | 0.036237 | 0.030941 | -0.036587 | -0.030796 | 0.0077058 | -0.01405 | 0.030362 | 0.059193 | -0.023037 | -0.025165 | 84.2651 | -37.2437 | 2.3163 | -38.1912 | 84.3018 | -38.0447 | -38.0402 | -1.1948 | -1.0345 | -38.4155 | 84.2285 | 84.2148 | -38.0539 | -38.1775 | 0.068664 | 0.073242 | -0.045776 | 0.86975 | -0.07782 | -0.15106 | -0.082397 | 0.059509 | -0.064087 | -0.11902 | 36.9186 | -0.30212 | -0.23804 | -0.13275 | 122.4152 | 122.3785 | 40.4297 | -122.3877 | 122.3419 | 122.3282 | 37.0789 | -122.525
1171.9844 | 122.5845 | -35.7239 | 86.618 | -0.00022891 | -0.053408 | 0.12786 | 0.03346 | 0.035 | -0.037442 | -0.025028 | -0.0075532 | -0.015545 | 0.025449 | 0.057911 | -0.02026 | -0.027087 | 86.6821 | -34.8907 | 2.6321 | -35.8063 | 86.6272 | -35.701 | -35.6918 | -1.0117 | -0.79193 | -35.994 | 86.554 | 86.5356 | -35.701 | -35.82 | 0.022888 | 0.032044 | 0.009155 | 0.83313 | -0.082397 | -0.11444 | 0.064087 | 0.022888 | -0.09613 | -0.064087 | 34.7122 | -0.27008 | -0.17395 | -0.082397 | 122.3511 | 122.406 | 38.356 | -122.3099 | 122.2778 | 122.2595 | 34.9319 | -122.438
1173.7031 | 122.5067 | -34.0347 | 88.3301 | -0.00022891 | -0.051485 | 0.12508 | 0.033246 | 0.033291 | -0.034878 | -0.023746 | 7.627e-05 | -0.012341 | 0.027372 | 0.06197 | -0.019192 | -0.027515 | 88.2935 | -33.3069 | 2.7832 | -34.1949 | 88.3392 | -34.0256 | -34.0485 | -1.1948 | -0.98419 | -34.4421 | 88.2935 | 88.2797 | -34.0164 | -34.1766 | 0.009155 | -0.013733 | 0.009155 | 0.72784 | -0.16022 | -0.14648 | -0.036621 | 0.018311 | -0.14191 | -0.036621 | 32.84 | -0.40741 | -0.2655 | -0.050354 | 122.374 | 122.3282 | 36.8179 | -122.3785 | 122.3282 | 122.3145 | 33.0505 | -122.5067
1175.5 | 122.4976 | -33.2703 | 89.1724 | -0.00022891 | -0.054049 | 0.12828 | 0.037305 | 0.034359 | -0.043423 | -0.027164 | 0.015335 | -0.016827 | 0.025876 | 0.059406 | -0.023892 | -0.026019 | 88.9801 | -32.4738 | 2.9938 | -33.3984 | 89.0625 | -33.2382 | -33.2382 | -1.0162 | -0.98877 | -33.5861 | 88.9755 | 88.9847 | -33.2794 | -33.3939 | 0.032044 | 0.032044 | -0.10986 | 0.79651 | -0.12817 | -0.16022 | -0.19226 | -0.009155 | -0.1236 | -0.19684 | 32.254 | -0.31586 | -0.19226 | -0.18768 | 122.3328 | 122.2504 | 36.264 | -122.4106 | 122.2458 | 122.2549 | 32.2815 | -122.5662
1177.2188 | 122.5479 | -33.2703 | 89.0945 | -0.0078584 | -0.051485 | 0.12786 | 0.031323 | 0.034786 | -0.03381 | -0.02631 | -0.015182 | -0.013623 | 0.024595 | 0.059406 | -0.02026 | -0.025806 | 89.9048 | -33.0185 | 2.1606 | -33.8058 | 88.8336 | -33.4488 | -33.4442 | -0.32044 | 0.013733 | -32.0984 | 89.6713 | 89.4699 | -32.9407 | -33.1604 | -0.17853 | -0.17395 | -0.26093 | 0.25177 | -0.53558 | -0.36163 | 0.81024 | 0.32959 | 0.10986 | 0.57678 | 32.9498 | 1.1719 | 1.062 | 0.37537 | 122.1039 | 123.175 | 35.4309 | -122.5388 | 122.9416 | 122.7402 | 33.284 | -122.2549
1179 | 122.4976 | -45.4102 | 76.9363 | -0.00022891 | -0.054049 | 0.12743 | 0.036878 | 0.036068 | -0.041287 | -0.028232 | -0.022812 | -0.018109 | 0.026944 | 0.055775 | -0.024532 | -0.024524 | 76.9638 | -44.1605 | 1.5564 | -45.433 | 76.8631 | -45.3918 | -45.3644 | -2.3071 | -2.6321 | -45.6253 | 76.8173 | 76.7624 | -45.401 | -45.52 | 0.01831 | 0.045776 | -0.073242 | 1.2497 | -0.022888 | -0.068664 | 0.027466 | 0.009155 | -0.10986 | -0.11902 | 43.103 | -0.21515 | -0.10528 | -0.17395 | 122.2733 | 122.374 | 46.9666 | -122.3007 | 122.2275 | 122.1725 | 42.778 | -122.4564
1180.7969 | 122.5479 | -75.8743 | 46.2341 | -0.00022891 | -0.05234 | 0.12636 | 0.037305 | 0.036495 | -0.037228 | -0.027378 | 7.627e-05 | -0.015118 | 0.027372 | 0.060688 | -0.02261 | -0.028155 | 48.2437 | -72.1298 | -2.3712 | -74.0479 | 48.1476 | -74.2172 | -74.1211 | -5.8044 | -6.1111 | -74.4186 | 48.1247 | 48.0881 | -74.1531 | -74.3317 | 1.6571 | 1.7532 | 1.9135 | 3.7445 | 1.8265 | 0.073242 | 2.0096 | 1.7212 | 1.5427 | 1.8906 | 70.0699 | 1.4557 | -0.086975 | 1.8539 | 124.0219 | 124.118 | 73.5031 | -120.3552 | 123.999 | 123.9624 | 69.7632 | -120.5658
1182.5156 | 122.5388 | -108.4808 | 14.1357 | -0.00022891 | -0.052553 | 0.12658 | 0.034528 | 0.036923 | -0.037442 | -0.024387 | 7.627e-05 | -0.014477 | 0.026517 | 0.058338 | -0.022396 | -0.026874 | 15.0833 | -103.5324 | -6.5048 | -105.011 | 15.8798 | -106.4896 | -106.5857 | -11.3617 | -9.0363 | -105.1987 | 15.2847 | 15.0833 | -107.7438 | -108.5724 | 1.9913 | 1.8951 | 1.7441 | 4.9484 | 3.4698 | 1.5747 | 0.94757 | 0.737 | -0.091553 | 1.149 | 97.1191 | 3.2822 | 3.3737 | 0.94757 | 124.3607 | 123.5641 | 101.976 | -120.7214 | 123.7656 | 123.5641 | 99.4446 | -122.7081
1184.3281 | 122.4518 | -107.0892 | 15.2527 | 0.0074006 | -0.053835 | 0.12722 | 0.035596 | 0.037136 | -0.03851 | -0.027591 | -0.0075532 | -0.014904 | 0.026517 | 0.057057 | -0.023037 | -0.024524 | 15.1657 | -103.9124 | -6.9214 | -106.8146 | 15.1428 | -107.1716 | -107.048 | -9.3521 | -11.9476 | -107.2952 | 15.0925 | 15.1199 | -107.0572 | -107.2861 | -0.082398 | 0.041198 | -0.10986 | 3.1769 | 0.27466 | 0.23346 | -0.086976 | 0.032043 | -0.19684 | -0.16022 | 97.7371 | -0.20599 | -0.009155 | -0.13275 | 122.2321 | 122.2549 | 100.1678 | -122.3007 | 122.1817 | 122.2092 | 95.1416 | -122.5388
1186.0469 | 122.5937 | -118.9499 | 3.3463 | -0.015487 | -0.052126 | 0.12615 | 0.033032 | 0.037991 | -0.034237 | -0.024387 | -0.0075532 | -0.013623 | 0.026731 | 0.061329 | -0.018124 | -0.027728 | 3.3325 | -115.5029 | -8.5693 | -118.6295 | 3.3279 | -119.0369 | -118.9362 | -10.8124 | -13.7924 | -119.0689 | 3.2684 | 3.2593 | -118.9682 | -119.1742 | -0.086975 | 0.013733 | -0.01831 | 3.447 | 0.32043 | 0.3067 | -0.013732 | -0.018311 | -0.2243 | -0.077819 | 108.1375 | -0.11902 | 0.10528 | -0.086975 | 122.2778 | 122.2824 | 110.3806 | -122.2824 | 122.2183 | 122.2092 | 105.1575 | -122.5204
1187.8438 | 122.6852 | -117.6086 | 4.6509 | -0.0078584 | -0.050631 | 0.12423 | 0.033032 | 0.038204 | -0.033169 | -0.025455 | 0.0077058 | -0.012555 | 0.027158 | 0.062183 | -0.018551 | -0.027087 | 4.5685 | -114.4409 | -8.5373 | -117.5217 | 4.6097 | -117.8925 | -117.7963 | -10.2356 | -13.3255 | -118.0206 | 4.4037 | 4.4083 | -117.8329 | -118.0939 | -0.28381 | -0.18768 | -0.041199 | 3.1677 | 0.086976 | 0.27466 | -0.082398 | -0.2243 | -0.48523 | -0.24719 | 107.373 | -0.41199 | 0.073242 | -0.24261 | 122.2183 | 122.1771 | 109.0714 | -122.4472 | 122.0123 | 122.0169 | 104.2831 | -122.7448
1189.5625 | 122.2641 | -115.8188 | 6.2347 | -0.00022891 | -0.053194 | 0.1285 | 0.036878 | 0.036495 | -0.034237 | -0.02631 | -0.015182 | -0.017682 | 0.029722 | 0.060688 | -0.02026 | -0.023242 | 13.3209 | -103.418 | -2.3117 | -108.8287 | 11.3251 | -109.465 | -110.2936 | -7.4844 | -13.9847 | -110.4401 | 7.7591 | 8.67 | -110.0693 | -109.5291 | 6.3538 | 5.5252 | 5.0903 | 12.4008 | 6.9901 | 1.4648 | 7.0862 | 5.7495 | 6.2897 | 1.5244 | 108.3344 | 5.3787 | -0.91095 | 2.4353 | 127.1439 | 129.1397 | 113.5071 | -116.5283 | 123.5779 | 124.4888 | 101.8341 | -115.7639
1191.3594 | 122.5159 | -116.7023 | 5.777 | -0.0078584 | -0.051485 | 0.12828 | 0.031323 | 0.038418 | -0.032956 | -0.023319 | -0.0075532 | -0.014691 | 0.027585 | 0.059834 | -0.016415 | -0.025806 | 4.6371 | -113.5849 | -9.1736 | -115.329 | 5.1682 | -115.7501 | -115.4938 | -11.8195 | -16.2964 | -108.2382 | 8.3221 | 9.4254 | -113.1226 | -114.9628 | 0.95215 | 1.2085 | -0.60883 | 3.1174 | 1.3733 | 0.16479 | -1.1398 | 3.5797 | 1.7395 | 2.5452 | 104.8828 | 8.4641 | 6.7245 | 3.6484 | 121.8704 | 121.3394 | 107.5287 | -121.2708 | 125.0244 | 126.1276 | 100.4059 | -120.7397
1193.0781 | 122.5662 | -119.0231 | 3.2547 | 0.0074006 | -0.048708 | 0.12615 | 0.034955 | 0.03735 | -0.037442 | -0.024387 | -0.015182 | -0.014904 | 0.028226 | 0.060047 | -0.020474 | -0.026019 | 3.154 | -115.4343 | -8.4412 | -118.7073 | 3.273 | -119.1513 | -119.0186 | -10.73 | -15.2756 | -119.2291 | 3.2135 | 3.2181 | -119.0506 | -119.2474 | -0.12817 | 0.004577 | 0.01831 | 3.5889 | 0.31586 | 0.31128 | -0.10071 | -0.027466 | -0.22431 | -0.041199 | 108.2932 | -0.20599 | 0.018311 | -0.036621 | 122.2961 | 122.1771 | 110.582 | -122.2733 | 122.2366 | 122.2412 | 103.7476 | -122.5021
1194.8594 | 122.5616 | -118.8583 | 3.4607 | -0.00022891 | -0.056185 | 0.12444 | 0.032819 | 0.036495 | -0.037442 | -0.023746 | -0.0075532 | -0.015118 | 0.026517 | 0.062611 | -0.021328 | -0.025165 | 3.4332 | -115.1138 | -8.3908 | -118.4921 | 3.4332 | -118.8904 | -118.7759 | -11.0825 | -15.9851 | -118.9545 | 3.3737 | 3.392 | -118.7943 | -119.0414 | -0.032044 | 0.082397 | -0.027465 | 3.7445 | 0.36621 | 0.28381 | -0.027465 | 0.064087 | -0.18311 | -0.086975 | 107.7759 | -0.096131 | 0.086975 | -0.068664 | 122.2916 | 122.2916 | 110.4675 | -122.2366 | 122.2321 | 122.2504 | 102.8732 | -122.5021
1196.6562 | 122.4014 | -118.483 | 3.6896 | -0.015487 | -0.05234 | 0.12615 | 0.034314 | 0.036068 | -0.034237 | -0.026096 | 0.015335 | -0.015118 | 0.026517 | 0.060047 | -0.020046 | -0.02666 | 3.4103 | -115.0818 | -8.5144 | -118.4235 | 3.5156 | -118.84 | -118.7622 | -11.2747 | -15.8615 | -118.9499 | 3.4836 | 3.4698 | -118.7668 | -119.0002 | -0.35706 | -0.27924 | -0.17395 | 3.4012 | 0.059509 | 0.33875 | -0.27924 | -0.28381 | -0.51727 | -0.20599 | 107.2083 | -0.46692 | 0.050354 | -0.21973 | 121.9986 | 121.8933 | 109.9686 | -122.4518 | 121.9666 | 121.9528 | 102.6215 | -122.6898
1198.375 | 122.4426 | -57.1426 | 65.1993 | -0.0078584 | -0.051272 | 0.12444 | 0.036878 | 0.036495 | -0.034878 | -0.025455 | 0.015335 | -0.012127 | 0.029081 | 0.061756 | -0.02261 | -0.026447 | 65.1581 | -55.3894 | 0.33875 | -57.0877 | 65.1764 | -56.9778 | -57.0007 | -2.5681 | -4.66 | -57.3853 | 65.1352 | 65.1077 | -57.019 | -57.1976 | 0.1648 | 0.14191 | -0.022888 | 1.7532 | 0.054931 | -0.086976 | -0.041199 | 0.1236 | -0.054932 | -0.064087 | 54.5746 | -0.24262 | -0.18768 | -0.091553 | 122.319 | 122.3007 | 57.4814 | -122.2 | 122.2778 | 122.2504 | 52.4826 | -122.3969
1200.1719 | 122.3694 | -56.955 | 65.4419 | -0.0078584 | -0.050417 | 0.12722 | 0.03645 | 0.036282 | -0.040005 | -0.027378 | 7.627e-05 | -0.017041 | 0.027158 | 0.058766 | -0.023678 | -0.025165 | 65.3961 | -55.0461 | 0.29297 | -56.8497 | 65.3732 | -56.8222 | -56.7902 | -2.6825 | -5.3925 | -57.1701 | 65.3778 | 65.3412 | -56.8176 | -56.9916 | 0.13275 | 0.1648 | -0.068665 | 1.9089 | 0.10529 | -0.059509 | -0.045777 | 0.13733 | -0.036621 | -0.064087 | 54.2725 | -0.21515 | -0.17853 | -0.10071 | 122.3282 | 122.3511 | 57.2479 | -122.2321 | 122.3328 | 122.2961 | 51.5625 | -122.4335
1201.9062 | 122.3831 | -56.6574 | 65.6982 | 0.0074006 | -0.054476 | 0.12786 | 0.034101 | 0.035427 | -0.041501 | -0.028873 | 0.0077058 | -0.017468 | 0.02609 | 0.057911 | -0.024532 | -0.025806 | 65.7166 | -54.744 | 0.44403 | -56.5796 | 65.5975 | -56.5933 | -56.5659 | -2.6779 | -4.4174 | -56.8817 | 65.5884 | 65.5563 | -56.5979 | -56.7581 | 0.064087 | 0.091553 | -0.10071 | 1.9135 | 0.07782 | -0.013733 | 0.018311 | 0.05951 | -0.10071 | -0.10986 | 53.9795 | -0.2243 | -0.1236 | -0.14191 | 122.2549 | 122.374 | 57.1014 | -122.2641 | 122.2458 | 122.2137 | 52.24 | -122.4564
1203.7031 | 122.4243 | -56.4835 | 65.8905 | -0.0078584 | -0.054262 | 0.12807 | 0.03645 | 0.036282 | -0.040219 | -0.027378 | 0.0077058 | -0.021527 | 0.02374 | 0.056629 | -0.023464 | -0.027087 | 65.9042 | -54.4693 | 0.49896 | -56.369 | 65.7944 | -56.4102 | -56.3736 | -1.9592 | -5.4337 | -56.6528 | 65.7394 | 65.7257 | -56.4148 | -56.5979 | 0.073242 | 0.10986 | -0.09613 | 2.0142 | 0.11444 | 0.004577 | 0.013733 | 0.068664 | -0.11444 | -0.15106 | 54.5242 | -0.16937 | -0.054932 | -0.16479 | 122.2778 | 122.3877 | 56.9824 | -122.2641 | 122.2229 | 122.2092 | 51.0498 | -122.4884
1205.4375 | 122.4609 | -56.369 | 65.9821 | 0.0074006 | -0.049563 | 0.13149 | 0.034955 | 0.03735 | -0.035733 | -0.029087 | 0.0077058 | -0.014691 | 0.025876 | 0.061543 | -0.02261 | -0.027728 | 65.95 | -54.4281 | 0.34332 | -56.3461 | 65.9912 | -56.3553 | -56.3141 | -2.1561 | -5.2597 | -56.6574 | 65.918 | 65.8997 | -56.3232 | -56.4789 | 0.013733 | 0.054932 | 0.009155 | 1.9409 | 0.022889 | -0.032043 | -0.032044 | 0.045777 | -0.10986 | -0.064087 | 54.213 | -0.28839 | -0.17853 | -0.082398 | 122.3602 | 122.319 | 56.7123 | -122.2961 | 122.287 | 122.2687 | 51.1093 | -122.4609
1207.2344 | 122.4289 | -56.2042 | 66.1926 | -0.00022891 | -0.052767 | 0.12764 | 0.033673 | 0.032223 | -0.042782 | -0.029087 | 7.627e-05 | -0.017254 | 0.025022 | 0.060047 | -0.023251 | -0.026874 | 66.1789 | -54.158 | 0.46692 | -56.1218 | 66.124 | -56.1447 | -56.0989 | -2.3438 | -6.0608 | -56.3919 | 66.0599 | 66.0553 | -56.1401 | -56.3049 | 0.05951 | 0.10529 | -0.068665 | 2.0462 | 0.082398 | -0.022888 | -0.013733 | 0.064087 | -0.10071 | -0.13275 | 53.8605 | -0.18768 | -0.086975 | -0.13733 | 122.3282 | 122.3831 | 56.6711 | -122.2916 | 122.2641 | 122.2595 | 50.1434 | -122.4976
1209.0312 | 122.4838 | -56.0394 | 66.3254 | -0.0078584 | -0.054476 | 0.12764 | 0.036664 | 0.037991 | -0.039792 | -0.028873 | 7.627e-05 | -0.017895 | 0.02609 | 0.057057 | -0.023892 | -0.026233 | 66.3757 | -53.9062 | 0.70953 | -55.9479 | 66.2109 | -56.0394 | -55.9753 | -3.0121 | -5.0766 | -56.2088 | 66.1789 | 66.1514 | -55.9982 | -56.163 | 0 | 0.064087 | -0.11444 | 2.1332 | 0.091553 | 0.027466 | 0.050354 | 0.041199 | -0.1236 | -0.14648 | 53.0273 | -0.16937 | -0.045776 | -0.17395 | 122.2504 | 122.4152 | 56.749 | -122.3007 | 122.2183 | 122.1909 | 50.9628 | -122.4884
1210.7656 | 122.4197 | -55.8701 | 66.5405 | 0.0074006 | -0.052767 | 0.12914 | 0.034955 | 0.033932 | -0.037228 | -0.029087 | 0.0077058 | -0.016613 | 0.024808 | 0.05727 | -0.020901 | -0.028369 | 66.5451 | -53.7048 | 0.74616 | -55.7419 | 66.4307 | -55.8334 | -55.8014 | -2.7878 | -5.6671 | -56.0577 | 66.4032 | 66.3574 | -55.8197 | -55.9891 | 0.036621 | 0.068664 | -0.10986 | 2.1652 | 0.12817 | 0.05951 | 0.004578 | 0.050354 | -0.11902 | -0.13733 | 53.0823 | -0.18768 | -0.068664 | -0.1831 | 122.3007 | 122.4152 | 56.6162 | -122.3419 | 122.2733 | 122.2275 | 50.2029 | -122.5296
1212.5625 | 122.5388 | -55.8243 | 66.5359 | 0.0074006 | -0.053408 | 0.1285 | 0.033673 | 0.036068 | -0.032956 | -0.02631 | 7.627e-05 | -0.017254 | 0.025663 | 0.058338 | -0.02026 | -0.026874 | 66.5817 | -53.6774 | 0.75989 | -55.7419 | 66.4536 | -55.806 | -55.7785 | -2.417 | -6.5323 | -56.0349 | 66.4078 | 66.3574 | -55.7922 | -55.957 | 0.018311 | 0.045777 | -0.082398 | 2.1469 | 0.082398 | 0.036621 | 0.045776 | 0.032044 | -0.13275 | -0.12817 | 53.4073 | -0.21057 | -0.07782 | -0.17853 | 122.2778 | 122.406 | 56.5842 | -122.3145 | 122.2321 | 122.1817 | 49.292 | -122.493
1214.3438 | 122.5571 | -55.7373 | 66.5863 | -0.00022891 | -0.048067 | 0.12828 | 0.034101 | 0.035855 | -0.03146 | -0.024387 | 7.627e-05 | -0.013195 | 0.027158 | 0.060902 | -0.01791 | -0.029651 | 66.6367 | -53.5812 | 0.88348 | -55.7098 | 66.5543 | -55.7739 | -55.7281 | -2.6413 | -6.134 | -56.0394 | 66.4948 | 66.4856 | -55.7465 | -55.9113 | -0.036621 | 0.009156 | -0.032044 | 2.1561 | 0.027466 | 0.01831 | 0.050354 | -0.009155 | -0.17395 | -0.091553 | 53.096 | -0.30212 | -0.12817 | -0.10071 | 122.2916 | 122.374 | 56.6208 | -122.3145 | 122.2321 | 122.2229 | 49.6033 | -122.4976
1216.1406 | 122.5708 | -55.7098 | 66.6092 | 0.0074006 | -0.051272 | 0.12807 | 0.035809 | 0.036495 | -0.035305 | -0.027591 | -0.015182 | -0.014477 | 0.025876 | 0.061756 | -0.02026 | -0.026447 | 66.6138 | -53.5538 | 0.85144 | -55.6641 | 66.6138 | -55.7419 | -55.7007 | -2.504 | -6.752 | -56.0303 | 66.5909 | 66.5359 | -55.719 | -55.8701 | -0.032043 | 0.009155 | 0.004578 | 2.1561 | 0.045777 | 0.036622 | 0.004578 | -0.009155 | -0.16022 | -0.018311 | 53.2059 | -0.32043 | -0.16022 | -0.073242 | 122.3236 | 122.3236 | 56.5613 | -122.3099 | 122.3007 | 122.2458 | 48.9578 | -122.4792
1217.8594 | 122.5204 | -55.5817 | 66.7831 | -0.0078584 | -0.053835 | 0.12807 | 0.03645 | 0.035855 | -0.040646 | -0.027591 | 7.627e-05 | -0.018322 | 0.028013 | 0.058338 | -0.026241 | -0.026233 | 66.806 | -53.2516 | 1.1353 | -55.4718 | 66.7328 | -55.5313 | -55.513 | -2.2797 | -6.3538 | -55.7419 | 66.6595 | 66.6412 | -55.5176 | -55.6824 | 0.050354 | 0.068665 | -0.050354 | 2.33 | 0.10986 | 0.041198 | 0.022888 | 0.064087 | -0.10071 | -0.1236 | 53.302 | -0.16022 | -0.059509 | -0.14191 | 122.3145 | 122.3877 | 56.7169 | -122.2961 | 122.2412 | 122.2229 | 49.2279 | -122.4655
1219.6406 | 122.4838 | -55.545 | 66.8472 | -0.0078584 | -0.051058 | 0.12658 | 0.038373 | 0.037777 | -0.03616 | -0.024601 | 7.627e-05 | -0.012982 | 0.027158 | 0.059193 | -0.022183 | -0.025592 | 66.7831 | -53.2288 | 1.1215 | -55.5084 | 66.7923 | -55.5405 | -55.4993 | -2.8931 | -6.0928 | -55.8151 | 66.7648 | 66.7374 | -55.5267 | -55.6824 | 0.004578 | 0.045776 | -0.054932 | 2.3163 | 0.036621 | -0.009155 | -0.064087 | 0.018311 | -0.13733 | -0.082397 | 52.652 | -0.27008 | -0.13275 | -0.10986 | 122.3373 | 122.3282 | 56.6666 | -122.3465 | 122.3099 | 122.2824 | 49.4522 | -122.5296
1221.4219 | 122.5296 | -55.4626 | 66.8976 | -0.0078584 | -0.054262 | 0.12935 | 0.034741 | 0.037564 | -0.04086 | -0.026951 | -0.0075532 | -0.017895 | 0.025449 | 0.05727 | -0.021328 | -0.025378 | 66.925 | -53.0273 | 1.268 | -55.3574 | 66.8198 | -55.426 | -55.4169 | -3.0808 | -6.102 | -55.632 | 66.774 | 66.7511 | -55.426 | -55.5908 | 0.036621 | 0.045776 | -0.07782 | 2.4353 | 0.10529 | 0.059509 | 0.027466 | 0.036621 | -0.12817 | -0.1236 | 52.3819 | -0.16937 | -0.041199 | -0.14648 | 122.2824 | 122.3877 | 56.7307 | -122.3145 | 122.2366 | 122.2137 | 49.3607 | -122.4884
1223.1406 | 122.4655 | -55.4855 | 66.9022 | -0.0078584 | -0.054903 | 0.12871 | 0.03346 | 0.035214 | -0.039792 | -0.029087 | 0.0077058 | -0.015332 | 0.025663 | 0.059193 | -0.022183 | -0.028796 | 66.893 | -53.0319 | 1.1673 | -55.3986 | 66.8198 | -55.4489 | -55.426 | -3.4103 | -6.308 | -55.687 | 66.7969 | 66.7557 | -55.4306 | -55.6 | 0.036621 | 0.05951 | -0.082398 | 2.4536 | 0.086975 | 0.027465 | -0.009156 | 0.054932 | -0.11444 | -0.10529 | 52.0752 | -0.20142 | -0.086975 | -0.14649 | 122.3053 | 122.3785 | 56.6528 | -122.3282 | 122.2824 | 122.2412 | 49.1776 | -122.5021
1224.9219 | 122.6212 | -55.8517 | 66.4856 | -0.015487 | -0.050417 | 0.12636 | 0.035596 | 0.035427 | -0.032742 | -0.025455 | -0.0075532 | -0.012341 | 0.024381 | 0.05962 | -0.019833 | -0.026874 | 66.6321 | -53.2791 | 1.0391 | -55.6549 | 66.6321 | -55.7419 | -55.7327 | -4.303 | -5.658 | -56.0577 | 66.5085 | 66.4627 | -55.8105 | -55.9708 | 0.10986 | 0.11902 | 0.14648 | 2.5726 | 0.19684 | 0.07782 | 0.14648 | 0.041199 | -0.11902 | 0.022888 | 51.5488 | -0.20599 | -0.086975 | -0.022888 | 122.4838 | 122.4838 | 56.8909 | -122.2183 | 122.3602 | 122.3145 | 50.1938 | -122.4564
1226.6562 | 122.6212 | -55.4535 | 66.9067 | -0.00022891 | -0.04999 | 0.12679 | 0.03645 | 0.036495 | -0.033169 | -0.025028 | 7.627e-05 | -0.013195 | 0.026731 | 0.058979 | -0.01791 | -0.026447 | 66.9022 | -52.977 | 1.355 | -55.4031 | 66.8701 | -55.481 | -55.4718 | -4.3808 | -5.2872 | -55.751 | 66.7923 | 66.7557 | -55.4581 | -55.632 | -0.027466 | -0.018311 | -0.036621 | 2.4765 | 0.050354 | 0.068665 | -0.004577 | -0.004578 | -0.17853 | -0.11444 | 51.0727 | -0.29755 | -0.11902 | -0.15106 | 122.3236 | 122.3557 | 56.8085 | -122.3785 | 122.2458 | 122.2092 | 50.1663 | -122.5388
1228.4375 | 122.5433 | -55.22 | 67.1585 | -0.00022891 | -0.056826 | 0.12893 | 0.033246 | 0.035641 | -0.039792 | -0.026951 | 0.015335 | -0.019604 | 0.025235 | 0.058338 | -0.023251 | -0.026874 | 67.1036 | -52.6428 | 1.6617 | -55.1422 | 67.0944 | -55.2246 | -55.188 | -3.6758 | -2.829 | -55.4443 | 67.0166 | 66.9846 | -55.2155 | -55.3711 | -0.004577 | 0.032044 | -0.064087 | 2.5772 | 0.07782 | 0.045776 | -0.054931 | 0.004578 | -0.15106 | -0.14191 | 51.5442 | -0.2243 | -0.073242 | -0.17395 | 122.3145 | 122.3236 | 56.8817 | -122.3465 | 122.2366 | 122.2046 | 52.3911 | -122.5296
1230.1406 | 122.5021 | -55.0964 | 67.3187 | -0.0078584 | -0.051485 | 0.12871 | 0.036664 | 0.035855 | -0.037442 | -0.026096 | 0.0077058 | -0.01405 | 0.024808 | 0.059834 | -0.022823 | -0.026233 | 67.3096 | -52.4506 | 1.6525 | -54.982 | 67.2455 | -55.0735 | -55.0186 | -3.6118 | -2.1927 | -55.3436 | 67.2272 | 67.1997 | -55.101 | -55.2155 | 0.022889 | 0.07782 | -0.073243 | 2.6459 | 0.11444 | 0.036621 | -0.009156 | -0.004577 | -0.11902 | -0.091553 | 51.4847 | -0.24719 | -0.12817 | -0.11902 | 122.3419 | 122.406 | 56.749 | -122.3373 | 122.3236 | 122.2961 | 52.9037 | -122.5342
1231.9219 | 122.5388 | -55.3162 | 67.0395 | -0.0078584 | -0.051913 | 0.12764 | 0.036023 | 0.03735 | -0.040219 | -0.028873 | 7.627e-05 | -0.017468 | 0.02609 | 0.05727 | -0.022183 | -0.024738 | 67.099 | -52.5925 | 1.8356 | -55.1926 | 67.0029 | -55.3207 | -55.2475 | -3.6072 | -2.6962 | -55.4855 | 66.9067 | 66.9205 | -55.2704 | -55.4352 | -0.004578 | 0.068664 | -0.036621 | 2.7237 | 0.1236 | 0.054932 | 0.059509 | 0.045776 | -0.11902 | -0.13275 | 51.709 | -0.16937 | -0.050354 | -0.11902 | 122.319 | 122.4152 | 57.1518 | -122.287 | 122.2229 | 122.2366 | 52.6199 | -122.4747
1233.7031 | 122.5571 | -55.4031 | 66.9342 | -0.00022891 | -0.050204 | 0.12658 | 0.031751 | 0.036709 | -0.031247 | -0.023105 | 7.627e-05 | -0.010632 | 0.026731 | 0.060047 | -0.016842 | -0.026019 | 66.9983 | -52.7115 | 1.7258 | -55.3207 | 66.9891 | -55.3802 | -55.3665 | -3.3188 | -2.3117 | -55.7144 | 66.9067 | 66.8838 | -55.3711 | -55.5496 | 0.022888 | 0.036621 | 0.054932 | 2.6917 | 0.082397 | 0.045776 | 0.064087 | 0.032043 | -0.14648 | -0.027466 | 52.0844 | -0.31128 | -0.16479 | -0.050354 | 122.3923 | 122.4014 | 57.1289 | -122.3007 | 122.3099 | 122.287 | 53.0914 | -122.4838
1235.4062 | 122.5159 | -55.5771 | 66.8106 | -0.00022891 | -0.056185 | 0.13106 | 0.033673 | 0.034146 | -0.041714 | -0.026523 | 0.0077058 | -0.0211 | 0.025449 | 0.056629 | -0.022823 | -0.025378 | 66.7877 | -52.7893 | 1.8951 | -55.4855 | 66.7236 | -55.5588 | -55.5496 | -3.2593 | -2.7145 | -55.7327 | 66.7328 | 66.6962 | -55.4993 | -55.6366 | 0.01831 | 0.027465 | -0.086975 | 2.7878 | 0.091552 | 0.064087 | -0.022888 | 0.077819 | -0.05951 | -0.07782 | 52.3178 | -0.15564 | -0.09613 | -0.11444 | 122.3007 | 122.3648 | 57.4722 | -122.3602 | 122.3099 | 122.2733 | 52.8625 | -122.4472
1237.1875 | 122.5021 | -55.7556 | 66.6321 | -0.00022891 | -0.052981 | 0.12893 | 0.033032 | 0.033077 | -0.036801 | -0.025669 | 7.627e-05 | -0.016186 | 0.024808 | 0.060902 | -0.023037 | -0.025378 | 66.6687 | -52.8717 | 2.0233 | -55.6503 | 66.5085 | -55.7968 | -55.751 | -3.8223 | -2.7237 | -55.9845 | 66.4627 | 66.4444 | -55.7281 | -55.8884 | -0.041199 | 0.004577 | -0.1236 | 2.8839 | 0.10529 | 0.10071 | 0.036621 | 0.027466 | -0.13275 | -0.16937 | 51.9333 | -0.22888 | -0.09613 | -0.18768 | 122.2641 | 122.4243 | 57.7789 | -122.3831 | 122.2183 | 122.2 | 53.0319 | -122.5204
1238.9062 | 122.5159 | -56.1218 | 66.2613 | 0.0074006 | -0.056399 | 0.13128 | 0.032392 | 0.037777 | -0.039364 | -0.02396 | 7.627e-05 | -0.014264 | 0.026517 | 0.058338 | -0.021328 | -0.027301 | 66.3345 | -53.1097 | 2.0554 | -55.9891 | 66.1835 | -56.0761 | -56.0532 | -3.6667 | -2.1698 | -56.2912 | 66.1697 | 66.1377 | -56.0669 | -56.2363 | 0.045776 | 0.068664 | -0.07782 | 3.0121 | 0.13275 | 0.064087 | 0.073242 | 0.054931 | -0.11444 | -0.091553 | 52.4551 | -0.16937 | -0.054932 | -0.1236 | 122.3053 | 122.4564 | 58.1772 | -122.3145 | 122.2916 | 122.2595 | 53.952 | -122.4976
1240.6875 | 122.4884 | -56.0257 | 66.394 | -0.00022891 | -0.053835 | 0.12957 | 0.037732 | 0.035855 | -0.036801 | -0.025669 | -0.0075532 | -0.015332 | 0.025663 | 0.05727 | -0.021114 | -0.026233 | 66.4856 | -52.8763 | 2.1286 | -55.8105 | 66.3345 | -55.9433 | -55.9113 | -3.6987 | -3.0899 | -56.1447 | 66.2796 | 66.2704 | -55.9525 | -56.0989 | 0.082398 | 0.11444 | -0.059509 | 3.1494 | 0.21515 | 0.10071 | 0.091553 | 0.073242 | -0.073242 | -0.11444 | 52.327 | -0.11902 | -0.045776 | -0.1236 | 122.3602 | 122.5113 | 58.1543 | -122.3053 | 122.3053 | 122.2961 | 52.9358 | -122.493
1242.4844 | 122.612 | -56.0623 | 66.2521 | 0.0074006 | -0.051058 | 0.12786 | 0.036878 | 0.037136 | -0.034665 | -0.022464 | -0.0075532 | -0.014264 | 0.027799 | 0.060688 | -0.021542 | -0.027515 | 66.3803 | -52.9633 | 2.1469 | -55.9067 | 66.2704 | -56.0303 | -55.9891 | -3.8818 | -2.5177 | -56.2546 | 66.2155 | 66.1972 | -56.0394 | -56.1813 | 0.032044 | 0.073242 | 0.018311 | 3.0991 | 0.15564 | 0.082398 | 0.12817 | 0.022888 | -0.11902 | -0.036621 | 52.1805 | -0.19226 | -0.073243 | -0.054931 | 122.3328 | 122.4426 | 58.2092 | -122.2412 | 122.2778 | 122.2595 | 53.5446 | -122.4335
1244.2656 | 122.6486 | -56.0394 | 66.3345 | -0.0078584 | -0.04764 | 0.1285 | 0.037946 | 0.035 | -0.03381 | -0.025669 | 7.627e-05 | -0.01405 | 0.026944 | 0.061115 | -0.022183 | -0.027728 | 66.3254 | -53.0228 | 2.2202 | -55.9525 | 66.2933 | -56.0623 | -56.0349 | -3.7262 | -2.5085 | -56.3187 | 66.2338 | 66.2018 | -56.0394 | -56.1722 | -0.022888 | 0.004578 | -0.041199 | 3.0167 | 0.086975 | 0.082397 | -0.009156 | 0 | -0.13275 | -0.10071 | 52.3132 | -0.27924 | -0.14649 | -0.13275 | 122.3328 | 122.3648 | 58.2596 | -122.3694 | 122.2733 | 122.2412 | 53.5309 | -122.5067
1246 | 122.5204 | -56.1584 | 66.2064 | -0.00022891 | -0.052126 | 0.13234 | 0.036664 | 0.036282 | -0.039578 | -0.026737 | -0.015182 | -0.016613 | 0.027585 | 0.060688 | -0.024746 | -0.028583 | 66.2247 | -52.9724 | 2.3254 | -56.0028 | 66.1743 | -56.1218 | -56.1035 | -3.7491 | -1.973 | -56.3278 | 66.1331 | 66.1194 | -56.0852 | -56.2729 | 0.036621 | 0.054931 | -0.032044 | 3.186 | 0.15564 | 0.10071 | 0.01831 | 0.073242 | -0.11444 | -0.073242 | 52.4094 | -0.16937 | -0.054932 | -0.086975 | 122.3328 | 122.3831 | 58.4839 | -122.3099 | 122.2916 | 122.2778 | 54.1855 | -122.4792
1247.7969 | 122.5433 | -56.4514 | 65.9637 | 0.0074006 | -0.051272 | 0.1285 | 0.033673 | 0.035855 | -0.040005 | -0.026951 | 7.627e-05 | -0.016186 | 0.026304 | 0.061756 | -0.023251 | -0.029651 | 66.0004 | -53.0869 | 2.3117 | -56.2592 | 65.8768 | -56.4194 | -56.3644 | -4.2023 | -2.2018 | -56.6025 | 65.7898 | 65.7898 | -56.4056 | -56.575 | 0.032043 | 0.086975 | -0.086975 | 3.3646 | 0.19226 | 0.10529 | 0.036621 | 0.045776 | -0.1236 | -0.17395 | 52.2491 | -0.15106 | -0.027466 | -0.17395 | 122.3282 | 122.4518 | 58.7631 | -122.3282 | 122.2412 | 122.2412 | 54.2496 | -122.5388
1249.5781 | 122.699 | -104.0817 | 18.1595 | 0.0074006 | -0.051913 | 0.15627 | 0.030896 | 0.037564 | -0.031033 | -0.023533 | 7.627e-05 | -0.010632 | 0.026304 | 0.064106 | -0.015988 | -0.028369 | 18.251 | -98.3139 | -7.5485 | -103.7018 | 18.1549 | -104.2969 | -104.1595 | -14.1769 | -14.4791 | -104.3152 | 18.1458 | 18.1183 | -104.2007 | -104.4113 | -0.21515 | -0.07782 | -0.004578 | 5.7678 | 0.37994 | 0.45776 | 0.091553 | -0.11902 | -0.32959 | -0.013733 | 89.9048 | -0.23346 | 0.09613 | -0.041199 | 122.2366 | 122.3328 | 96.5332 | -122.319 | 122.2275 | 122.2 | 89.6027 | -122.5708
1251.3125 | 122.5937 | -105.4138 | 16.9418 | -0.0078584 | -0.056399 | 0.15862 | 0.033887 | 0.040768 | -0.039578 | -0.022678 | 0.0077058 | -0.018963 | 0.026517 | 0.061329 | -0.021542 | -0.024738 | 16.9418 | -99.3439 | -8.0154 | -104.924 | 16.9006 | -105.5008 | -105.3909 | -15.1016 | -16.1224 | -105.5191 | 16.8777 | 16.8686 | -105.3909 | -105.629 | -0.086975 | 0.022888 | -0.041198 | 6.0699 | 0.48981 | 0.46692 | 0 | 0.022888 | -0.21515 | -0.064086 | 90.3122 | -0.10529 | 0.10986 | -0.073242 | 122.3145 | 122.3557 | 97.3984 | -122.3328 | 122.2916 | 122.2824 | 89.2914 | -122.5708
1253.0938 | 122.6715 | -106.3568 | 15.9622 | -0.0078584 | -0.050844 | 0.15905 | 0.034314 | 0.040982 | -0.032101 | -0.023105 | -0.015182 | -0.012555 | 0.027372 | 0.059406 | -0.016201 | -0.026019 | 15.9851 | -100.1999 | -8.7524 | -105.9128 | 15.9851 | -106.4713 | -106.3705 | -16.2643 | -16.7633 | -106.5674 | 15.9302 | 15.921 | -106.3934 | -106.5903 | -0.11444 | -0.013732 | 0.022888 | 6.1569 | 0.44403 | 0.45776 | 0.022888 | -0.036621 | -0.23346 | -0.032043 | 90.0925 | -0.21057 | 0.022888 | -0.041198 | 122.3419 | 122.3419 | 97.6044 | -122.3328 | 122.287 | 122.2778 | 89.5935 | -122.5525
1254.8125 | 122.6624 | -106.7139 | 15.6052 | -0.00022891 | -0.047213 | 0.16118 | 0.036237 | 0.040768 | -0.030179 | -0.023319 | 0.0077058 | -0.01405 | 0.027585 | 0.060688 | -0.017056 | -0.024738 | 15.6555 | -100.2548 | -8.7708 | -106.2103 | 15.6418 | -106.7734 | -106.6956 | -16.2552 | -16.1728 | -106.8695 | 15.5777 | 15.5731 | -106.691 | -106.9519 | -0.059509 | 0.01831 | 0.036621 | 6.459 | 0.50354 | 0.48523 | 0.050354 | 0.022888 | -0.23804 | -0.027466 | 90.4587 | -0.15564 | 0.082397 | -0.032044 | 122.3557 | 122.3694 | 97.9431 | -122.3007 | 122.2916 | 122.287 | 90.5411 | -122.5571
1256.5938 | 122.5433 | -106.9153 | 15.5045 | -0.00022891 | -0.058108 | 0.16182 | 0.038373 | 0.036923 | -0.041501 | -0.024387 | 7.627e-05 | -0.015118 | 0.025876 | 0.063038 | -0.021755 | -0.024738 | 15.4861 | -100.2548 | -8.7524 | -106.3614 | 15.4449 | -106.9244 | -106.8192 | -15.802 | -18.0588 | -106.9748 | 15.4175 | 15.4221 | -106.8054 | -107.0572 | -0.009155 | 0.09613 | -0.05951 | 6.6605 | 0.55389 | 0.45776 | -0.018311 | 0.10986 | -0.14191 | -0.086976 | 91.1133 | -0.059509 | 0.082398 | -0.082398 | 122.3602 | 122.4014 | 98.1628 | -122.3236 | 122.3328 | 122.3373 | 88.8565 | -122.5616
1258.375 | 122.5662 | -107.4371 | 14.9826 | -0.00022891 | -0.05469 | 0.16289 | 0.03645 | 0.039486 | -0.038937 | -0.023319 | 0.0077058 | -0.017041 | 0.024808 | 0.059834 | -0.020474 | -0.025592 | 14.9918 | -100.5798 | -8.6426 | -106.8604 | 14.9277 | -107.4188 | -107.341 | -16.0858 | -16.2552 | -107.4554 | 14.8865 | 14.8773 | -107.3547 | -107.5607 | 0.018311 | 0.096131 | -0.054932 | 6.8573 | 0.57678 | 0.48065 | 0.009155 | 0.082398 | -0.1236 | -0.09613 | 91.3513 | -0.01831 | 0.10529 | -0.10529 | 122.3648 | 122.4289 | 98.7946 | -122.3236 | 122.3236 | 122.3145 | 91.1819 | -122.5433
1260.1562 | 122.58 | -107.46 | 14.9323 | -0.015487 | -0.051913 | 0.16225 | 0.032605 | 0.037991 | -0.026547 | -0.022678 | 7.627e-05 | -0.012982 | 0.026731 | 0.061115 | -0.016201 | -0.026019 | 14.9231 | -100.5203 | -8.725 | -106.9153 | 14.9414 | -107.4738 | -107.3959 | -15.2939 | -19.1803 | -107.6385 | 14.9002 | 14.8911 | -107.4188 | -107.634 | -0.013733 | 0.064087 | 0.009155 | 6.9397 | 0.54474 | 0.48065 | -0.009155 | 0.041199 | -0.17395 | -0.032043 | 92.1661 | -0.17853 | -0.004578 | -0.041199 | 122.4014 | 122.3831 | 98.735 | -122.3282 | 122.3602 | 122.3511 | 88.2797 | -122.5662
1261.875 | 122.6303 | -107.9224 | 14.4516 | -0.0078584 | -0.049776 | 0.16311 | 0.036237 | 0.038418 | -0.033596 | -0.022464 | -0.0075532 | -0.014264 | 0.026731 | 0.062397 | -0.018124 | -0.023669 | 14.4196 | -100.7812 | -9.2331 | -107.3776 | 14.4608 | -107.9636 | -107.8903 | -16.3742 | -16.5298 | -108.0734 | 14.415 | 14.4241 | -107.8949 | -108.0917 | -0.041199 | 0.032043 | 0.009155 | 7.1411 | 0.54474 | 0.5127 | -0.032043 | 0.027466 | -0.16937 | -0.036621 | 91.5482 | -0.15106 | 0.018311 | -0.027466 | 122.3831 | 122.3419 | 98.6893 | -122.3419 | 122.3373 | 122.3465 | 91.3925 | -122.5433
1263.6562 | 122.5067 | -108.1924 | 14.2548 | -0.015487 | -0.056185 | 0.16268 | 0.032819 | 0.0397 | -0.037228 | -0.02396 | 0.0077058 | -0.015973 | 0.025663 | 0.057697 | -0.021114 | -0.024951 | 14.2456 | -100.6897 | -9.2468 | -107.5516 | 14.1815 | -108.1604 | -108.0734 | -16.4429 | -16.5344 | -108.2245 | 14.1174 | 14.1541 | -108.1329 | -108.3435 | 0.032044 | 0.11902 | -0.073242 | 7.5027 | 0.64087 | 0.52185 | -0.009156 | 0.059509 | -0.15106 | -0.13733 | 91.7496 | -0.032043 | 0.11902 | -0.10071 | 122.374 | 122.438 | 98.9456 | -122.3282 | 122.3099 | 122.3465 | 91.658 | -122.5983
1265.4375 | 122.6486 | -108.5907 | 13.765 | -0.00022891 | -0.051272 | 0.16524 | 0.032178 | 0.041836 | -0.031033 | -0.022037 | -0.0075532 | -0.013836 | 0.025663 | 0.062183 | -0.019833 | -0.024524 | 13.7375 | -101.088 | -9.5352 | -108.0643 | 13.7604 | -108.6639 | -108.5587 | -16.6306 | -16.5756 | -108.7601 | 13.7146 | 13.7054 | -108.5678 | -108.8104 | -0.073242 | 0.032043 | -0.004578 | 7.5027 | 0.52643 | 0.49439 | -0.027466 | 0.022888 | -0.21973 | -0.050354 | 91.9601 | -0.16937 | 0.050354 | -0.05951 | 122.3511 | 122.3282 | 99.0555 | -122.3236 | 122.3053 | 122.2961 | 92.0151 | -122.5754
1267.1562 | 122.644 | -108.5037 | 13.8519 | -0.0078584 | -0.052981 | 0.16033 | 0.034741 | 0.041622 | -0.033383 | -0.022892 | 7.627e-05 | -0.014904 | 0.026304 | 0.060688 | -0.021542 | -0.025378 | 13.9023 | -100.6073 | -9.5947 | -107.9086 | 13.8336 | -108.5358 | -108.4396 | -15.8066 | -15.6738 | -108.5587 | 13.765 | 13.7787 | -108.4534 | -108.6411 | -0.032044 | 0.064087 | -0.018311 | 7.8964 | 0.59509 | 0.53101 | 0.050354 | 0.050354 | -0.13733 | -0.086975 | 92.6971 | -0.054932 | 0.082397 | -0.073242 | 122.3373 | 122.406 | 98.909 | -122.2916 | 122.2687 | 122.2824 | 92.8299 | -122.493
1268.9375 | 122.6715 | -108.9661 | 13.4033 | -0.0078584 | -0.050204 | 0.16439 | 0.035169 | 0.039059 | -0.031674 | -0.024173 | 7.627e-05 | -0.015545 | 0.025663 | 0.060474 | -0.018978 | -0.023883 | 13.385 | -100.8682 | -9.8007 | -108.4122 | 13.3667 | -108.989 | -108.9111 | -15.8981 | -16.507 | -109.0805 | 13.3392 | 13.3255 | -108.9249 | -109.1217 | -0.022889 | 0.054931 | -0.036621 | 8.0978 | 0.55389 | 0.49896 | -0.01831 | 0.041198 | -0.15564 | -0.064087 | 93.0679 | -0.11444 | 0.041199 | -0.07782 | 122.3328 | 122.3511 | 99.1653 | -122.3145 | 122.3053 | 122.2916 | 92.4591 | -122.525
1270.75 | 122.5342 | -108.8882 | 13.4949 | 0.0074006 | -0.04999 | 0.16546 | 0.03645 | 0.042904 | -0.035305 | -0.025242 | -0.015182 | -0.016827 | 0.026944 | 0.061115 | -0.023464 | -0.025378 | 13.4445 | -100.4105 | -9.993 | -108.3023 | 13.4903 | -108.9615 | -108.8379 | -15.9714 | -15.8249 | -109.0347 | 13.4491 | 13.4308 | -108.8699 | -109.0805 | -0.073242 | 0.050354 | -0.004578 | 8.4778 | 0.58594 | 0.53558 | -0.050354 | 0.018311 | -0.19226 | -0.045776 | 92.9169 | -0.14648 | 0.045776 | -0.064087 | 122.3785 | 122.3328 | 98.8953 | -122.3328 | 122.3373 | 122.319 | 93.0634 | -122.5754
1272.4688 | 122.5296 | -109.1537 | 13.3026 | 0.0074006 | -0.054903 | 0.16716 | 0.037091 | 0.041622 | -0.038296 | -0.023319 | 0.0077058 | -0.01875 | 0.027158 | 0.060047 | -0.02261 | -0.02431 | 13.2568 | -100.3143 | -10.199 | -108.4808 | 13.2339 | -109.1125 | -109.0164 | -15.77 | -16.5985 | -109.1858 | 13.179 | 13.1927 | -109.0576 | -109.2865 | 0.041199 | 0.13733 | -0.068664 | 8.8394 | 0.67291 | 0.53558 | -0.045776 | 0.096131 | -0.13275 | -0.1236 | 93.3838 | -0.032043 | 0.10071 | -0.10986 | 122.3877 | 122.4106 | 98.9548 | -122.319 | 122.3328 | 122.3465 | 92.5552 | -122.5891
1274.2969 | 122.5571 | -109.2957 | 13.1149 | 0.0074006 | -0.052981 | 0.1661 | 0.036878 | 0.040768 | -0.036801 | -0.025028 | -0.0075532 | -0.017682 | 0.02609 | 0.060047 | -0.021969 | -0.025806 | 13.1241 | -100.0763 | -10.3958 | -108.6227 | 13.0463 | -109.3002 | -109.1949 | -15.6052 | -16.6763 | -109.2819 | 12.9959 | 12.9913 | -109.2178 | -109.4559 | -0.004578 | 0.10071 | -0.068664 | 9.2194 | 0.67291 | 0.5722 | 0.009155 | 0.07782 | -0.16022 | -0.11902 | 93.6905 | 0.013733 | 0.17395 | -0.1236 | 122.3419 | 122.4197 | 98.8998 | -122.3099 | 122.2916 | 122.287 | 92.6193 | -122.5708
1276.0625 | 122.644 | -109.2682 | 13.0783 | -0.00022891 | -0.052553 | 0.16567 | 0.034314 | 0.043331 | -0.029965 | -0.023746 | -0.0075532 | -0.012982 | 0.025876 | 0.061115 | -0.016628 | -0.024097 | 13.1241 | -99.8383 | -10.6842 | -108.6502 | 13.06 | -109.2911 | -109.1858 | -15.8707 | -16.2369 | -109.3552 | 13.0188 | 12.9959 | -109.2133 | -109.4376 | -0.022889 | 0.082397 | -0.01831 | 9.4299 | 0.61798 | 0.53558 | 0.045776 | 0.054931 | -0.16937 | -0.059509 | 93.3975 | -0.086976 | 0.082397 | -0.082397 | 122.3282 | 122.3923 | 98.584 | -122.2641 | 122.287 | 122.2641 | 93.0313 | -122.5159
1277.7656 | 122.5845 | -109.2819 | 13.092 | -0.0078584 | -0.049349 | 0.16417 | 0.034528 | 0.043545 | -0.028897 | -0.022464 | 7.627e-05 | -0.013195 | 0.025235 | 0.064747 | -0.018551 | -0.026233 | 13.1332 | -99.5316 | -10.9497 | -108.6365 | 13.0966 | -109.3277 | -109.1858 | -15.7837 | -16.8549 | -109.4055 | 13.028 | 13.0508 | -109.2224 | -109.4696 | -0.045777 | 0.09613 | 0.004578 | 9.7504 | 0.64545 | 0.54932 | 0.041199 | 0.059509 | -0.18768 | -0.064087 | 93.4982 | -0.1236 | 0.064086 | -0.041199 | 122.3785 | 122.4152 | 98.3322 | -122.2778 | 122.3099 | 122.3328 | 92.4271 | -122.5616
1279.4688 | 122.5021 | -109.4879 | 12.9364 | -0.00022891 | -0.051699 | 0.16823 | 0.03645 | 0.0397 | -0.039792 | -0.023319 | 7.627e-05 | -0.019818 | 0.027158 | 0.06197 | -0.024746 | -0.024524 | 12.8815 | -99.2706 | -11.1191 | -108.8104 | 12.8723 | -109.4604 | -109.3735 | -15.6647 | -17.7933 | -109.5428 | 12.8174 | 12.8128 | -109.4193 | -109.6024 | 0.027466 | 0.11444 | -0.064087 | 10.2173 | 0.67749 | 0.56305 | -0.054931 | 0.068665 | -0.11444 | -0.11902 | 93.8232 | -0.054932 | 0.059509 | -0.1236 | 122.3602 | 122.3694 | 98.3688 | -122.3099 | 122.3053 | 122.3007 | 91.6946 | -122.5388
1281.1719 | 122.58 | -109.5749 | 12.8082 | -0.00022891 | -0.052981 | 0.1708 | 0.033032 | 0.041836 | -0.032956 | -0.020969 | -0.0075532 | -0.015759 | 0.023954 | 0.058979 | -0.019192 | -0.026447 | 12.8632 | -98.7305 | -11.3571 | -108.8745 | 12.7579 | -109.5795 | -109.465 | -15.77 | -16.7541 | -109.6024 | 12.7029 | 12.7029 | -109.5016 | -109.7031 | -0.004578 | 0.10986 | -0.050354 | 10.8444 | 0.70038 | 0.59052 | 0.054931 | 0.073242 | -0.12817 | -0.10529 | 93.8049 | -0.027466 | 0.10071 | -0.10529 | 122.3328 | 122.438 | 98.2178 | -122.2733 | 122.2778 | 122.2778 | 92.8207 | -122.5113
1282.8906 | 122.6212 | -109.227 | 13.1104 | -0.0078584 | -0.051485 | 0.16802 | 0.034955 | 0.044613 | -0.030392 | -0.022464 | 7.627e-05 | -0.012982 | 0.026304 | 0.060474 | -0.017483 | -0.027728 | 13.1012 | -97.9568 | -11.6089 | -108.5999 | 13.1195 | -109.3231 | -109.1995 | -15.9805 | -17.4774 | -109.4101 | 13.1012 | 13.0875 | -109.2407 | -109.4284 | -0.09613 | 0.027466 | 0.009155 | 11.2701 | 0.62714 | 0.59967 | -0.009156 | -0.013733 | -0.20142 | -0.009156 | 93.2465 | -0.1831 | 0.018311 | -0.022889 | 122.3465 | 122.3282 | 97.6181 | -122.3099 | 122.3282 | 122.3145 | 91.7496 | -122.5388
1284.6406 | 122.5342 | -109.4925 | 12.8998 | 0.0074006 | -0.053408 | 0.16973 | 0.038587 | 0.045681 | -0.03851 | -0.023105 | 7.627e-05 | -0.018536 | 0.026731 | 0.060688 | -0.023251 | -0.024738 | 12.9318 | -97.5357 | -11.5997 | -108.7509 | 12.8174 | -109.5245 | -109.4055 | -16.4383 | -16.9144 | -109.5016 | 12.7808 | 12.7945 | -109.465 | -109.6481 | -0.032043 | 0.086975 | -0.082397 | 11.9568 | 0.74158 | 0.6546 | 0.032044 | 0.027466 | -0.15564 | -0.11902 | 93.0542 | -0.009155 | 0.14648 | -0.10529 | 122.3099 | 122.4243 | 97.8928 | -122.3053 | 122.2733 | 122.287 | 92.5781 | -122.5479
1286.4062 | 122.5021 | -109.7992 | 12.6389 | -0.00022891 | -0.057253 | 0.17015 | 0.032178 | 0.043972 | -0.037655 | -0.023533 | 7.627e-05 | -0.018536 | 0.024381 | 0.06197 | -0.018337 | -0.02431 | 12.6617 | -97.2702 | -12.1674 | -109.0347 | 12.5702 | -109.7488 | -109.6573 | -16.3651 | -16.8869 | -109.8221 | 12.5153 | 12.5198 | -109.7031 | -109.9182 | 0.050354 | 0.14191 | -0.068665 | 12.529 | 0.76447 | 0.62256 | 0.022888 | 0.09613 | -0.11902 | -0.1236 | 93.4341 | -0.022889 | 0.09613 | -0.11902 | 122.3694 | 122.4609 | 97.6318 | -122.2961 | 122.3145 | 122.319 | 92.9123 | -122.5571
1288.1562 | 122.6486 | -109.6664 | 12.6709 | -0.00022891 | -0.049135 | 0.17058 | 0.031323 | 0.043331 | -0.029324 | -0.023533 | 7.627e-05 | -0.014691 | 0.027158 | 0.063252 | -0.018124 | -0.025806 | 12.6846 | -96.9864 | -12.4741 | -108.989 | 12.6755 | -109.7305 | -109.6161 | -16.832 | -16.6626 | -109.8267 | 12.6389 | 12.6389 | -109.639 | -109.8587 | -0.064087 | 0.050354 | 0.004578 | 12.6801 | 0.67749 | 0.62714 | 0.013733 | 0.027466 | -0.19226 | -0.032043 | 92.8345 | -0.16022 | 0.032044 | -0.032043 | 122.3419 | 122.3511 | 97.1924 | -122.287 | 122.3053 | 122.3053 | 93.0038 | -122.5296
1289.875 | 122.6532 | -109.9319 | 12.4237 | -0.00022891 | -0.049776 | 0.17186 | 0.032819 | 0.045254 | -0.029965 | -0.024387 | 0.0077058 | -0.01405 | 0.02609 | 0.061543 | -0.01791 | -0.024951 | 12.3917 | -96.9772 | -12.7899 | -109.2453 | 12.41 | -110.0098 | -109.9091 | -16.8091 | -16.7633 | -110.0784 | 12.3596 | 12.3505 | -109.9228 | -110.1196 | -0.07782 | 0.022888 | -0.013733 | 12.9547 | 0.68665 | 0.66376 | -0.032043 | 0.009155 | -0.18768 | -0.064087 | 93.1229 | -0.14648 | 0.041199 | -0.073242 | 122.3419 | 122.3236 | 97.142 | -122.3328 | 122.2916 | 122.2824 | 93.1686 | -122.5433
1291.5938 | 122.5067 | -110.2386 | 12.2086 | -0.00022891 | -0.055544 | 0.1725 | 0.034101 | 0.041409 | -0.037228 | -0.02161 | 7.627e-05 | -0.018536 | 0.02609 | 0.062183 | -0.019619 | -0.023883 | 12.204 | -96.3821 | -13.3118 | -109.4101 | 12.117 | -110.2066 | -110.0876 | -17.1112 | -16.9052 | -110.2524 | 12.0941 | 12.1033 | -110.1608 | -110.3806 | 0.032043 | 0.15106 | -0.091553 | 13.8565 | 0.82855 | 0.67749 | -0.004578 | 0.077819 | -0.14191 | -0.11444 | 93.1274 | -0.013733 | 0.12817 | -0.10529 | 122.3557 | 122.4426 | 96.9269 | -122.2961 | 122.3328 | 122.3419 | 93.3334 | -122.5891
1293.2969 | 122.6212 | -109.7351 | 12.6297 | -0.00022891 | -0.051913 | 0.1708 | 0.032178 | 0.044827 | -0.030819 | -0.021183 | 7.627e-05 | -0.013623 | 0.025235 | 0.063038 | -0.019406 | -0.02431 | 12.6022 | -95.668 | -13.4903 | -108.989 | 12.6205 | -109.7855 | -109.6664 | -17.3401 | -17.9489 | -109.9091 | 12.5885 | 12.5931 | -109.7397 | -109.9136 | -0.050354 | 0.068664 | -0.009156 | 14.0671 | 0.74615 | 0.67749 | -0.027466 | -0.004578 | -0.17853 | -0.041199 | 92.395 | -0.17395 | 0.004577 | -0.036621 | 122.3557 | 122.3373 | 96.2448 | -122.2961 | 122.3236 | 122.3282 | 91.7862 | -122.5433
1295 | 122.6761 | -108.728 | 13.5086 | -0.00022891 | -0.049135 | 0.17101 | 0.037518 | 0.044613 | -0.029965 | -0.022464 | 7.627e-05 | -0.015118 | 0.027372 | 0.06197 | -0.019833 | -0.026874 | 13.5406 | -94.3817 | -13.2202 | -108.0185 | 13.5452 | -108.8745 | -108.7921 | -17.4454 | -17.9489 | -108.9386 | 13.4995 | 13.504 | -108.783 | -109.0256 | -0.14648 | -0.064087 | 0.036621 | 14.3463 | 0.70953 | 0.77362 | 0.032043 | -0.054932 | -0.29755 | -0.009155 | 91.2827 | -0.21057 | 0.086975 | -0.004578 | 122.2733 | 122.2687 | 95.5078 | -122.3007 | 122.2275 | 122.2321 | 90.7791 | -122.5342
1296.7188 | 122.5891 | -109.021 | 13.3255 | -0.00022891 | -0.051699 | 0.17315 | 0.038159 | 0.045254 | -0.039364 | -0.02161 | 7.627e-05 | -0.018109 | 0.028013 | 0.063252 | -0.023892 | -0.02431 | 13.2889 | -93.8644 | -13.7833 | -108.2474 | 13.266 | -109.0805 | -108.9615 | -17.7704 | -18.6035 | -109.108 | 13.2202 | 13.2614 | -109.0073 | -109.2361 | -0.059509 | 0.059509 | -0.059509 | 15.1566 | 0.77362 | 0.71411 | -0.036621 | 0.013733 | -0.21515 | -0.10529 | 91.2506 | -0.086975 | 0.12817 | -0.064086 | 122.287 | 122.3099 | 95.2377 | -122.287 | 122.2412 | 122.2824 | 90.4175 | -122.5616
1298.4375 | 122.6212 | -109.1812 | 13.1699 | -0.00022891 | -0.049776 | 0.17272 | 0.034314 | 0.04504 | -0.02847 | -0.02161 | 7.627e-05 | -0.011059 | 0.027799 | 0.063679 | -0.017269 | -0.028155 | 13.1241 | -93.3014 | -14.1403 | -108.403 | 13.1516 | -109.2453 | -109.1537 | -18.4616 | -19.9127 | -109.3781 | 13.1332 | 13.1378 | -109.1812 | -109.3918 | -0.064087 | 0.027465 | -0.018311 | 15.8798 | 0.7782 | 0.75073 | -0.045777 | 0 | -0.21057 | -0.036621 | 90.7196 | -0.19684 | 0.013733 | -0.032044 | 122.3328 | 122.3053 | 95.0409 | -122.3236 | 122.3145 | 122.319 | 89.2685 | -122.5616
1300.1406 | 122.58 | -109.3643 | 13.028 | 0.0074006 | -0.053408 | 0.17592 | 0.035596 | 0.046108 | -0.038083 | -0.024601 | -0.0075532 | -0.019177 | 0.025663 | 0.060902 | -0.021969 | -0.024738 | 13.0463 | -92.363 | -14.3326 | -108.4396 | 12.9913 | -109.3552 | -109.259 | -18.7912 | -20.3293 | -109.3369 | 12.941 | 12.9364 | -109.2957 | -109.4971 | 0.009155 | 0.10529 | -0.036621 | 17.0013 | 0.92468 | 0.8194 | 0.018311 | 0.068665 | -0.13275 | -0.086975 | 90.5731 | 0.027466 | 0.16022 | -0.091553 | 122.3557 | 122.4106 | 95.0317 | -122.287 | 122.3053 | 122.3007 | 89.035 | -122.525
1301.8438 | 122.6624 | -109.2865 | 13.0142 | -0.0078584 | -0.050631 | 0.17827 | 0.034741 | 0.047604 | -0.028897 | -0.02396 | -0.0075532 | -0.01405 | 0.027799 | 0.063465 | -0.020474 | -0.026233 | 13.0051 | -91.7862 | -14.653 | -108.4625 | 13.0188 | -109.3964 | -109.2865 | -19.1025 | -21.0938 | -109.4696 | 12.973 | 13.0005 | -109.3277 | -109.5428 | -0.10986 | 0 | 0.004578 | 17.5003 | 0.82398 | 0.82398 | -0.009155 | -0.041199 | -0.25635 | -0.041199 | 90.184 | -0.1831 | 0.073243 | -0.013733 | 122.3053 | 122.2916 | 94.6335 | -122.3007 | 122.2595 | 122.287 | 88.1927 | -122.5571
1303.5469 | 122.5891 | -109.053 | 13.3347 | -0.0078584 | -0.052553 | 0.1772 | 0.033032 | 0.051876 | -0.034024 | -0.021396 | -0.0075532 | -0.019818 | 0.025235 | 0.063252 | -0.018978 | -0.024951 | 13.3667 | -90.2435 | -14.653 | -108.0414 | 13.2431 | -109.0622 | -108.934 | -18.7592 | -20.9335 | -109.053 | 13.2248 | 13.2339 | -108.9844 | -109.2087 | -0.009155 | 0.11902 | -0.091553 | 18.8095 | 1.0117 | 0.89264 | 0.032043 | 0.068665 | -0.15564 | -0.10986 | 90.2939 | 0 | 0.15564 | -0.10071 | 122.2961 | 122.4197 | 94.4 | -122.2687 | 122.2778 | 122.287 | 88.1195 | -122.5433
1305.2812 | 122.2458 | -78.7582 | 43.7302 | 0.01503 | -0.051485 | 0.39232 | 0.03645 | 0.04504 | 0.19669 | -0.026096 | 7.627e-05 | -0.020245 | 0.027158 | 0.060902 | -0.022823 | -0.025378 | 43.6066 | -62.1872 | -3.772 | -39.5004 | 43.6203 | -78.5843 | -78.5294 | -10.6384 | -10.5743 | -78.6942 | 43.5699 | 43.5791 | -78.5522 | -78.7445 | 0.17395 | 0.22888 | -0.10986 | 16.571 | 39.2578 | 39.0289 | -0.1236 | 0.20599 | 0.013733 | -0.16022 | 68.1198 | 0.064087 | 0.050354 | -0.15106 | 122.3785 | 122.3648 | 74.9863 | -122.2595 | 122.3282 | 122.3373 | 68.1839 | -122.4747
1307.0312 | 122.4335 | -86.8332 | 35.5453 | -0.0078584 | -0.051913 | 0.59548 | 0.035596 | 0.093106 | 0.35349 | -0.02396 | 0.0077058 | -0.017041 | 0.025449 | 0.06197 | -0.021755 | -0.02666 | 35.5362 | 16.8549 | -4.2297 | -24.7055 | 35.4492 | -86.7325 | -86.6364 | -12.8723 | -13.3713 | -86.8378 | 35.408 | 35.3851 | -86.7371 | -86.9202 | 0.10071 | 0.19684 | -0.09613 | 103.688 | 62.1277 | 61.9308 | -0.009155 | 0.09613 | -0.086975 | -0.13733 | 73.9609 | -0.004578 | 0.082397 | -0.16022 | 122.2824 | 122.3694 | 82.6035 | -122.1817 | 122.2412 | 122.2183 | 73.4619 | -122.4655
1308.7188 | 122.5479 | -81.2805 | 40.9927 | -0.0078584 | -0.051058 | 0.62325 | 0.030255 | 0.095883 | 0.38404 | -0.021396 | 0.0077058 | -0.014264 | 0.026944 | 0.062183 | -0.016842 | -0.02666 | 40.8005 | 26.944 | -2.6459 | -13.2843 | 40.9561 | -81.3126 | -81.2347 | -11.4258 | -11.8011 | -81.4407 | 40.979 | 40.9607 | -81.2622 | -81.4774 | -0.032043 | 0.045777 | -0.036621 | 108.2245 | 67.9962 | 67.9504 | -0.19226 | 0.018311 | -0.19684 | -0.013733 | 69.8547 | -0.16022 | 0.036621 | -0.032044 | 122.2366 | 122.081 | 78.6346 | -122.2275 | 122.2595 | 122.2412 | 69.4794 | -122.4701
1310.4219 | 122.5204 | -91.7221 | 30.5191 | -0.00022891 | -0.044863 | 0.72088 | 0.034741 | 0.097592 | 0.47632 | -0.020542 | 7.627e-05 | -0.013195 | 0.02844 | 0.06197 | -0.018124 | -0.027942 | 30.3818 | 16.5527 | -6.4362 | -10.9543 | 30.5054 | -91.7221 | -91.658 | -13.9252 | -15.5411 | -91.9556 | 30.4825 | 30.4596 | -91.7267 | -91.9373 | 0 | 0.064087 | -0.013733 | 108.2748 | 80.7678 | 80.7037 | -0.13733 | -0.004578 | -0.21515 | -0.036621 | 77.7969 | -0.23346 | -0.01831 | -0.059509 | 122.2275 | 122.1039 | 85.2859 | -122.1771 | 122.2046 | 122.1817 | 76.181 | -122.4564
1312.1406 | 122.5296 | -93.3884 | 28.775 | -0.0078584 | -0.046572 | 0.74202 | 0.035169 | 0.099301 | 0.49662 | -0.020115 | 0.0077058 | -0.014477 | 0.029722 | 0.063252 | -0.017056 | -0.026874 | 28.6789 | 15.239 | -7.3837 | -9.6497 | 28.7659 | -93.457 | -93.3563 | -14.09 | -16.0355 | -93.5532 | 28.7338 | 28.7155 | -93.4296 | -93.6401 | -0.068664 | 0.032044 | -0.009155 | 108.6273 | 83.7387 | 83.7067 | -0.09613 | -0.041198 | -0.25177 | -0.041198 | 79.2984 | -0.16479 | 0.086975 | -0.059509 | 122.1542 | 122.0673 | 86.0046 | -122.1313 | 122.1222 | 122.1039 | 77.3529 | -122.4152
1313.9688 | 122.3877 | -81.4316 | 40.8875 | 0.0074006 | -0.053194 | 0.66982 | 0.037518 | 0.098873 | 0.41907 | -0.022464 | 7.627e-05 | -0.018963 | 0.028013 | 0.061329 | -0.022183 | -0.024524 | 40.892 | 31.9565 | -3.2364 | -8.2077 | 40.7181 | -81.3263 | -81.2759 | -10.7254 | -12.4146 | -81.6834 | 40.6082 | 40.5991 | -81.5643 | -81.9855 | 0.10529 | 0.15564 | -0.16937 | 113.3881 | 73.2239 | 73.0682 | 0.004578 | -0.13275 | -0.55389 | -0.27924 | 70.7062 | -0.25177 | 0.30212 | -0.28839 | 122.1497 | 122.3236 | 78.1952 | -122.1634 | 122.0398 | 122.0306 | 69.017 | -122.8729
1315.7812 | 122.4564 | -87.7716 | 34.4376 | -0.00022891 | -0.048067 | 0.63137 | 0.032605 | 0.10037 | 0.38596 | -0.019901 | 7.627e-05 | -0.01405 | 0.025022 | 0.06197 | -0.016415 | -0.027728 | 34.3918 | 25.914 | -6.0104 | -20.8054 | 34.433 | -87.767 | -87.6892 | -12.0804 | -14.6393 | -87.9684 | 34.3735 | 34.3735 | -87.7716 | -87.9684 | 0.004577 | 0.082397 | -0.004578 | 113.6856 | 66.9662 | 66.8839 | -0.045776 | 0 | -0.19684 | -0.064087 | 75.6912 | -0.19684 | 0 | -0.064087 | 122.2046 | 122.1634 | 81.7612 | -122.1268 | 122.1451 | 122.1451 | 73.1323 | -122.406
1317.5625 | 122.4197 | -88.06 | 34.1949 | -0.0078584 | -0.054049 | 0.69802 | 0.035809 | 0.099728 | 0.43723 | -0.022037 | 7.627e-05 | -0.017682 | 0.02609 | 0.061115 | -0.022823 | -0.023883 | 34.0714 | 25.5386 | -6.0287 | -11.9156 | 34.0805 | -88.028 | -87.9181 | -11.9843 | -15.3488 | -88.0966 | 34.0714 | 34.0347 | -88.0692 | -88.2385 | 0.032044 | 0.14191 | -0.11444 | 113.5986 | 76.1444 | 76.0025 | -0.1236 | -0.009155 | -0.17853 | -0.1236 | 76.0757 | -0.036621 | 0.14191 | -0.16022 | 122.1405 | 122.1313 | 82.0312 | -122.113 | 122.1313 | 122.0947 | 72.7112 | -122.4335
1319.3594 | 122.5067 | -91.7358 | 30.3955 | -0.0078584 | -0.049563 | 0.7275 | 0.033673 | 0.098446 | 0.47568 | -0.02161 | 0.0077058 | -0.012341 | 0.026517 | 0.062397 | -0.018551 | -0.02666 | 30.3589 | 21.5057 | -7.695 | -11.1465 | 30.4321 | -91.7816 | -91.6718 | -13.0463 | -17.2989 | -91.9098 | 30.4092 | 30.3497 | -91.7541 | -91.9556 | -0.045776 | 0.064087 | 0.036621 | 113.2416 | 80.5893 | 80.5252 | -0.036621 | -0.01831 | -0.21973 | 0.013733 | 78.6896 | -0.17395 | 0.045776 | -0.045777 | 122.168 | 122.0947 | 84.0408 | -122.0673 | 122.1451 | 122.0856 | 74.437 | -122.3511
1321.1406 | 122.4014 | -94.7296 | 27.4979 | -0.00022891 | -0.051699 | 0.75313 | 0.034741 | 0.10229 | 0.48871 | -0.024601 | 0.0077058 | -0.019604 | 0.025876 | 0.060474 | -0.019619 | -0.024524 | 27.4246 | 18.8095 | -8.9172 | -10.5698 | 27.3788 | -94.7021 | -94.606 | -13.829 | -18.6905 | -94.7159 | 27.3788 | 27.3834 | -94.7159 | -94.8853 | 0.027466 | 0.1236 | -0.11902 | 113.5391 | 84.1599 | 84.0363 | -0.073242 | 0.013733 | -0.15564 | -0.11902 | 80.9006 | 0.013733 | 0.16937 | -0.11444 | 122.1085 | 122.1542 | 85.8124 | -122.1039 | 122.1085 | 122.113 | 76.0391 | -122.3831
1322.9375 | 122.4152 | -100.4105 | 21.7987 | 0.0074006 | -0.054476 | 0.7918 | 0.037518 | 0.098232 | 0.5246 | -0.022251 | -0.0075532 | -0.019818 | 0.025876 | 0.063679 | -0.021542 | -0.025378 | 21.698 | 10.0983 | -11.1694 | -10.6705 | 21.73 | -100.4013 | -100.2823 | -15.2985 | -21.373 | -100.3967 | 21.698 | 21.7072 | -100.3647 | -100.589 | 0.009155 | 0.12817 | -0.068664 | 110.5087 | 89.74 | 89.6118 | -0.10071 | 0.045776 | -0.17853 | -0.10071 | 85.112 | 0.013732 | 0.19226 | -0.091553 | 122.1405 | 122.1085 | 89.241 | -122.081 | 122.1085 | 122.1176 | 79.0375 | -122.3877
1324.7188 | 122.406 | -80.5801 | 41.748 | -0.0078584 | -0.055758 | 0.63906 | 0.035809 | 0.083279 | 0.39728 | -0.023319 | 7.627e-05 | -0.015118 | 0.025449 | 0.061543 | -0.018337 | -0.026874 | 40.6631 | 7.5211 | -5.4108 | -8.4778 | 40.6357 | -81.4041 | -81.3675 | -10.2173 | -14.3051 | -81.3126 | 40.7227 | 40.7227 | -81.2851 | -81.5186 | -0.82398 | -0.78735 | -1.1124 | 88.1012 | 72.1024 | 72.8897 | -1.0849 | -0.70496 | -0.93842 | -1.0254 | 70.3629 | -0.73242 | 0.20599 | -1.0254 | 121.2158 | 121.2433 | 75.1694 | -123.1155 | 121.3028 | 121.3028 | 66.275 | -123.2666
1326.5 | 122.3282 | -90.6876 | 31.8878 | -0.0078584 | -0.047213 | 1.0691 | 0.037518 | 0.50583 | 0.35627 | -0.019901 | -0.0075532 | -0.010846 | 0.026304 | 0.063252 | -0.017483 | -0.02666 | 30.8487 | 16.9785 | -8.6151 | -26.8387 | 29.2328 | -92.4866 | -91.8274 | -14.2044 | -20.0592 | -92.6743 | 28.3035 | 28.8483 | -92.157 | -92.2348 | -1.799 | -1.1398 | -2.655 | 107.666 | 63.8489 | 64.9887 | -1.0391 | -1.4694 | -1.5472 | -3.5843 | 76.4832 | -1.9867 | -0.43945 | -3.0395 | 119.9203 | 121.5363 | 82.0724 | -123.7152 | 118.9911 | 119.5358 | 70.6284 | -124.1226
1328.2188 | 122.4472 | -71.7316 | 50.5875 | -0.0078584 | -0.04999 | 0.64055 | 0.034101 | 0.10656 | 0.36182 | -0.022251 | 7.627e-05 | -0.014691 | 0.025876 | 0.063679 | -0.016842 | -0.027515 | 49.0997 | -0.059509 | -2.0462 | -11.38 | 48.8892 | -73.2422 | -73.1461 | -6.427 | -11.2335 | -72.908 | 49.4659 | 49.4202 | -72.6929 | -72.8943 | -1.5106 | -1.4145 | -1.6983 | 71.6721 | 60.3516 | 61.7661 | -1.4877 | -0.9613 | -1.1627 | -1.1215 | 65.3046 | -1.1765 | -0.013733 | -1.1673 | 120.6207 | 120.8313 | 69.6854 | -123.7335 | 121.1975 | 121.1517 | 60.498 | -123.4818
1330 | 122.3145 | -73.5077 | 48.5504 | -0.0078584 | -0.052981 | 0.59719 | 0.031751 | 0.096523 | 0.34922 | -0.02161 | -0.0075532 | -0.019604 | 0.027158 | 0.063679 | -0.022183 | -0.024738 | 55.426 | 0.54932 | -4.3488 | -10.73 | 50.592 | -72.6059 | -72.9263 | -8.0109 | -11.8149 | -69.9097 | 49.6857 | 51.1459 | -69.5343 | -68.8431 | 0.90179 | 0.58136 | 2.0416 | 74.057 | 62.7777 | 62.1964 | 6.8756 | 3.9734 | 4.6646 | 1.1353 | 65.4968 | 3.598 | -1.0666 | 2.5955 | 124.0997 | 128.9337 | 69.1589 | -121.4767 | 123.1934 | 124.6536 | 61.6928 | -117.3935
1331.7812 | 122.4106 | -50.4135 | 71.6812 | -0.00022891 | -0.047854 | 1.3481 | 0.034528 | 0.96875 | 0.26975 | -0.022892 | 0.0077058 | -0.013623 | 0.029081 | 0.05962 | -0.019619 | -0.028369 | 72.084 | 26.9852 | 6.9077 | -8.7341 | 72.0428 | -49.9054 | -49.9512 | -2.1835 | -2.3941 | -49.9237 | 72.1893 | 72.1985 | -49.8047 | -49.8962 | 0.50812 | 0.46234 | 0.36163 | 77.3987 | 41.6794 | 41.217 | 0.40283 | 0.60883 | 0.51727 | 0.50812 | 48.23 | 0.48981 | -0.027466 | 0.51727 | 122.4564 | 122.4976 | 57.3212 | -121.6324 | 122.6028 | 122.612 | 48.0194 | -121.5775
1333.5 | 122.081 | -51.3428 | 71.9788 | -0.0078584 | -0.050204 | 0.48183 | 0.035809 | 0.11319 | 0.22959 | -0.023105 | 0.0077058 | -0.018322 | 0.025876 | 0.060474 | -0.022396 | -0.024738 | 72.8165 | -2.1194 | 5.8548 | -7.6813 | 72.7386 | -49.3423 | -49.4156 | -1.68 | -2.536 | -49.8825 | 72.4045 | 73.1644 | -48.5138 | -48.4909 | 2.0004 | 1.9272 | 0.75989 | 49.2233 | 43.6615 | 41.7343 | 0.83771 | 2.829 | 2.8519 | 0.42572 | 49.6628 | 1.4603 | -1.3916 | 1.1856 | 124.0814 | 124.1592 | 57.1976 | -121.3943 | 123.7473 | 124.5071 | 48.8068 | -120.4697
1335.2812 | 122.3648 | -47.7493 | 74.3408 | 0.0074006 | -0.054262 | 1.0296 | 0.034101 | 0.65493 | 0.21485 | -0.025242 | 7.627e-05 | -0.017041 | 0.022886 | 0.059834 | -0.018978 | -0.026874 | 73.819 | -2.3712 | 6.308 | -7.8003 | 74.5422 | -47.5479 | -47.525 | -1.0483 | -1.3458 | -47.58 | 74.3454 | 74.4873 | -47.3694 | -47.3328 | 0.20142 | 0.22431 | 0.20142 | 45.3781 | 39.949 | 39.7247 | -0.52185 | 0.37994 | 0.41657 | 0.004578 | 46.7011 | 0.16937 | -0.24719 | 0.14649 | 122.2916 | 121.5683 | 54.0573 | -121.8658 | 122.0947 | 122.2366 | 46.4035 | -121.6736
1337.0625 | 122.0856 | -63.9542 | 57.8979 | -0.00022891 | -0.048708 | 4.935 | 0.032819 | 4.5157 | 0.29218 | -0.023746 | 0.0077058 | -0.011914 | 0.028226 | 0.064961 | -0.014919 | -0.027728 | 57.2937 | -3.5934 | 0.15564 | -11.348 | 57.9849 | -63.1485 | -63.1577 | -4.9393 | -9.1736 | -63.8214 | 58.1909 | 58.1772 | -63.6932 | -63.7985 | 0.80566 | 0.79651 | 0.086975 | 60.3607 | 52.6062 | 51.8097 | -0.60425 | 0.26093 | 0.15564 | 0.29297 | 59.0149 | 0.13275 | -0.022888 | 0.27924 | 121.9391 | 121.2479 | 64.1098 | -121.0556 | 122.1451 | 122.1313 | 54.7806 | -121.6965
1338.7969 | 121.8246 | -61.4136 | 60.7864 | -0.00022891 | -0.048922 | 5.1583 | 0.037732 | 4.4942 | 0.22574 | 0.27575 | -0.0075532 | -0.014264 | 0.026944 | 0.064961 | -0.015133 | -0.027087 | 56.6162 | -2.948 | -0.17395 | -10.5286 | 57.2021 | -63.7207 | -63.6658 | -4.8019 | -9.2834 | -63.739 | 57.9712 | 57.9529 | -63.652 | -63.6841 | -2.3071 | -2.2522 | -3.5843 | 58.4656 | 50.885 | 53.1372 | -4.1702 | -2.2385 | -2.2705 | -2.8152 | 56.6116 | -2.3254 | -0.054932 | -2.8336 | 118.6157 | 118.0298 | 61.2396 | -124.4522 | 119.3848 | 119.3665 | 52.1301 | -124.4705
1340.5781 | 122.3511 | -65.0162 | 56.7261 | -0.00022891 | -0.048067 | 1.0199 | 0.034741 | 0.24264 | 0.30414 | 0.32019 | 7.627e-05 | -0.01405 | 0.027799 | 0.064961 | -0.018978 | -0.026019 | 60.1868 | 14.6072 | 2.8473 | -7.3837 | 60.1868 | -61.7523 | -61.7523 | -4.2297 | -9.1553 | -62.3474 | 59.7702 | 59.7244 | -62.178 | -62.352 | 3.2639 | 3.2639 | 3.4607 | 79.6234 | 57.6324 | 54.3686 | 3.4607 | 2.8381 | 2.6642 | 3.0441 | 60.7864 | 2.6688 | 0.004578 | 2.9984 | 125.2029 | 125.2029 | 67.8635 | -118.4784 | 124.7864 | 124.7406 | 55.8609 | -119.0781
1342.3594 | 122.2366 | -66.0919 | 55.838 | 0.0074006 | 0.042082 | 0.99987 | 0.034314 | 0.70428 | 0.23172 | -0.019901 | -0.0075532 | -0.019177 | 0.026731 | 0.065815 | -0.020687 | -0.024738 | 56.6025 | 46.2936 | 2.5543 | -5.4794 | 56.5063 | -65.1352 | -64.9338 | -4.6692 | -10.7986 | -64.444 | 57.1793 | 57.1106 | -65.0299 | -65.5014 | 0.95673 | 1.1581 | 0.66834 | 112.3856 | 60.6125 | 59.4543 | 0.76447 | 1.062 | 0.59052 | 1.3412 | 61.4227 | 1.6479 | 1.0574 | 1.2726 | 122.5983 | 122.6944 | 68.6462 | -120.7718 | 123.2712 | 123.2025 | 55.2933 | -121.3394
1344.0625 | 122.4426 | -38.5941 | 83.2581 | 0.0074006 | -0.040804 | 0.42992 | 0.039014 | 0.090969 | 0.22062 | -0.013706 | 7.627e-05 | -0.013623 | 0.028226 | 0.063038 | -0.019619 | -0.027728 | 83.5785 | -1.2039 | 7.6263 | -4.628 | 83.139 | -38.8412 | -38.8916 | 0.1831 | 0.045776 | -39.006 | 83.4274 | 83.6197 | -38.3926 | -38.5574 | -0.24719 | -0.29755 | -0.11902 | 37.3901 | 33.9661 | 34.2636 | 0.32043 | 0.20142 | 0.036621 | 0.16937 | 38.7772 | -0.41199 | -0.44861 | 0.36163 | 121.7331 | 122.1725 | 46.2204 | -122.1497 | 122.0215 | 122.2137 | 38.6398 | -121.8155
1345.8438 | 121.8338 | -33.5678 | 87.7762 | -0.0078584 | -0.033755 | 1.7153 | 0.032392 | 0.095242 | 0.37357 | 1.5569 | -0.015182 | -0.014264 | 0.028653 | 0.060474 | -0.016842 | -0.025592 | 80.6076 | 19.5602 | 8.6288 | -7.37 | 81.1935 | -38.4842 | -37.3352 | 3.6209 | 6.3995 | -37.0789 | 87.8128 | 87.1078 | -34.7992 | -35.1562 | -4.9164 | -3.7674 | -6.5826 | 53.1281 | 26.1978 | 29.9652 | -7.1686 | -1.2314 | -1.5884 | 0.036621 | 37.1887 | -3.511 | -1.9226 | -0.66833 | 114.7614 | 114.1754 | 42.1967 | -125.1114 | 121.3806 | 120.6757 | 39.9673 | -122.9324
1347.625 | 122.3969 | -27.182 | 94.4733 | -0.0078584 | -0.048495 | 0.3496 | 0.031751 | 0.083492 | 0.13132 | 0.0097925 | -0.0075532 | -0.017041 | 0.025022 | 0.063892 | -0.020901 | -0.02666 | 96.6522 | -0.53101 | 11.2701 | -2.8519 | 96.5149 | -25.502 | -25.5524 | -4.5868 | -6.546 | -40.2237 | 82.8873 | 82.489 | -37.9257 | -35.7971 | 1.68 | 1.6296 | 2.0416 | 26.651 | 24.3301 | 22.7005 | 2.179 | -10.7437 | -8.6151 | -11.586 | 22.5952 | -13.0417 | -4.4266 | -11.9843 | 123.6969 | 123.8342 | 38.4521 | -120.0256 | 110.0693 | 109.671 | 20.636 | -130.2704
1349.4062 | 122.5159 | -77.3804 | 44.8288 | -0.0078584 | 0.29394 | 0.28359 | 0.037518 | 0.10678 | 0.35776 | 0.053585 | 0.0077058 | -0.012982 | 0.028013 | 0.066883 | -0.013638 | -0.026874 | 42.2379 | -2.6596 | -0.38452 | -6.5094 | 45.1492 | -77.3438 | -75.6088 | -4.6555 | -17.0471 | -73.8922 | 47.9324 | 47.5479 | -75.3708 | -76.0483 | 0.036621 | 1.7715 | 0.32044 | 74.7208 | 70.871 | 69.0994 | -2.5909 | 2.0096 | 1.3321 | 3.1036 | 72.7249 | 3.4882 | 2.1561 | 2.7191 | 122.5296 | 119.6182 | 76.9958 | -120.4376 | 125.3128 | 124.9283 | 60.3333 | -120.8771
1351.1094 | 122.2458 | -0.43488 | 99.4263 | -0.015487 | -0.021578 | 0.091969 | 0.034955 | 0.0029566 | -0.043423 | 0.020047 | 7.627e-05 | -0.018963 | 0.024808 | 0.058338 | -0.022823 | -0.024524 | 0.054932 | 0.032043 | 0.004578 | -0.31128 | 0.086975 | -0.48065 | -0.58136 | 7.9468 | 16.2918 | -0.44403 | 121.4218 | 121.431 | -0.56305 | -0.59509 | -0.045777 | -0.14648 | -99.3393 | 0.46692 | 0.1236 | 0.27008 | -99.3713 | -0.12817 | -0.16022 | 21.9955 | 8.3817 | -0.009156 | 0.15106 | 22.0047 | 0.52185 | 0.48981 | 0.43945 | -100.0076 | 121.8567 | 121.8658 | 16.7267 | -100.0214
1352.8906 | 121.9666 | -1.1398 | 120.3003 | -0.00022891 | -0.01581 | 0.092396 | 0.031751 | 0.0065882 | -0.033169 | 0.021756 | 0.015335 | -0.015545 | 0.026304 | 0.061115 | -0.019619 | -0.028796 | 0.027466 | -0.10071 | -0.16022 | -1.03 | 0.10986 | -1.062 | -1.1765 | 6.9077 | 16.0904 | -1.1398 | 121.0144 | 121.0007 | -1.1444 | -1.181 | 0.07782 | -0.036621 | -120.1904 | 1.0391 | 0.10986 | 0.14648 | -120.2728 | -0.004577 | -0.041198 | 0.71411 | 8.0475 | 0 | 0.041198 | 0.70038 | 1.2497 | 1.1673 | 0.97961 | -121.4767 | 122.1542 | 122.1405 | 17.2302 | -121.4813
1354.5938 | 106.9336 | -2.504 | 99.1608 | -0.0078584 | -0.019015 | 0.091114 | 0.03645 | 0.006161 | -0.039364 | 0.019192 | 7.627e-05 | -0.017254 | 0.027372 | 0.058125 | -0.023678 | -0.026874 | 0.059509 | 0.018311 | -0.16937 | -2.5131 | 0.032043 | -2.6184 | -2.7328 | 6.1295 | 14.9826 | -2.623 | 119.4214 | 119.4489 | -2.7191 | -2.7832 | -0.11444 | -0.22888 | -99.1287 | 2.5223 | -0.009156 | 0.21973 | -99.1013 | -0.21515 | -0.27924 | 20.2606 | 8.6334 | -0.11902 | 0.16022 | 20.2881 | 2.536 | 2.5635 | 2.3346 | -101.8936 | 121.9254 | 121.9528 | 17.4866 | -101.944
1356.375 | 121.5866 | -3.6804 | 117.7963 | -0.0078584 | -0.017733 | 0.09261 | 0.035809 | 0.020687 | -0.037442 | 0.0006067 | -0.0075532 | -0.017254 | 0.027158 | 0.058766 | -0.022183 | -0.027515 | -0.068665 | -0.14648 | -0.38452 | -3.6163 | 0.064087 | -3.6896 | -3.7811 | 5.4016 | 14.5706 | -3.7765 | 118.483 | 118.4647 | -3.7765 | -3.8406 | -0.009155 | -0.10071 | -117.7322 | 3.5339 | 0.064087 | 0.16479 | -117.865 | -0.09613 | -0.16022 | 0.68665 | 9.082 | -0.09613 | 0.064087 | 0.66834 | 3.7445 | 3.6118 | 3.2959 | -121.5775 | 122.1634 | 122.1451 | 18.251 | -121.637
1358.1094 | 104.8004 | -4.3259 | 117.1143 | -0.00022891 | -0.016878 | 0.095387 | 0.036023 | 0.0087244 | -0.038723 | 0.013424 | 7.627e-05 | -0.017041 | 0.03079 | 0.059406 | -0.022823 | -0.026874 | 0.004578 | -0.013733 | -0.31128 | -4.4586 | 0.009155 | -4.4312 | -4.5319 | 4.66 | 14.0991 | -4.4815 | 117.691 | 117.6727 | -4.454 | -4.5227 | -0.10529 | -0.20599 | -117.1051 | 4.3121 | -0.13275 | 0.073242 | -117.1097 | -0.12817 | -0.19684 | 0.57678 | 8.9859 | -0.15564 | 0.041199 | 0.55847 | 4.335 | 4.3304 | 4.0146 | -121.6461 | 122.0169 | 121.9986 | 18.425 | -121.637
1359.8906 | 122.4243 | -5.9738 | 107.8766 | -0.00022891 | -0.017519 | 0.091755 | 0.034741 | 0.012997 | -0.039364 | 0.0080835 | 7.627e-05 | -0.015759 | 0.025663 | 0.059406 | -0.02261 | -0.026447 | -0.086975 | -0.14191 | -0.50354 | -5.9692 | -0.036621 | -6.0516 | -6.134 | 3.891 | 12.9639 | -6.0974 | 116.0751 | 116.0522 | -6.1386 | -6.1752 | -0.07782 | -0.16022 | -107.9132 | 5.8319 | 0.004578 | 0.16479 | -107.9636 | -0.16479 | -0.20142 | 8.1985 | 9.8648 | -0.1236 | 0.07782 | 8.1757 | 5.9372 | 5.8868 | 5.4703 | -114.0106 | 122.049 | 122.0261 | 18.9377 | -114.0518
1361.6562 | 122.0535 | -3.8681 | 118.5242 | -0.0078584 | -0.019015 | 0.092183 | 0.031751 | 0.010647 | -0.033596 | 0.013424 | 0.0077058 | -0.015545 | 0.02374 | 0.060261 | -0.02026 | -0.028155 | 0.027466 | -0.073242 | -0.25177 | -3.6942 | -0.045776 | -3.7811 | -3.891 | 3.7674 | 14.0808 | -3.7399 | 118.3502 | 118.3502 | -3.8406 | -3.8681 | 0.086975 | -0.022888 | -118.5699 | 3.7949 | 0.17395 | 0.19684 | -118.4967 | 0.027466 | 0 | -0.17395 | 7.6355 | 0.12817 | 0.12817 | -0.17395 | 3.8223 | 3.8956 | 3.6163 | -122.4152 | 122.2183 | 122.2183 | 17.9489 | -122.3923
1363.4531 | 122.438 | -11.4349 | 110.8383 | -0.00022891 | -0.013674 | 0.091114 | 0.032178 | 0.014065 | -0.030392 | 0.0010339 | -0.015182 | -0.012555 | 0.026944 | 0.064747 | -0.01257 | -0.028583 | -0.23804 | -0.35706 | -0.88348 | -11.3342 | -0.20142 | -11.3846 | -11.499 | 2.7512 | 10.3271 | -11.5585 | 110.7605 | 110.7513 | -11.4716 | -11.5448 | 0.050354 | -0.064086 | -111.0397 | 11.0779 | 0.10071 | 0.16479 | -111.0764 | -0.036621 | -0.10986 | -0.07782 | 14.1861 | -0.1236 | -0.013733 | -0.086975 | 11.2335 | 11.1969 | 10.5515 | -122.3373 | 122.1954 | 122.1863 | 21.7621 | -122.3831
1365.1719 | 122.2046 | -11.1832 | 110.8978 | -0.00022891 | -0.018374 | 0.091969 | 0.03645 | 0.010861 | -0.039364 | 0.0014613 | -0.0075532 | -0.017254 | 0.025663 | 0.062183 | -0.018978 | -0.026019 | -0.27008 | -0.31128 | -0.78735 | -11.0275 | -0.25635 | -11.0596 | -11.1511 | 2.5589 | 10.6339 | -11.142 | 111.0077 | 111.0168 | -11.1328 | -11.2106 | 0.1236 | 0.032044 | -111.1542 | 10.8719 | 0.15564 | 0.1236 | -111.1679 | 0.050355 | -0.027465 | 0.10986 | 13.7421 | 0.041199 | 0.068664 | 0.11902 | 10.9268 | 10.9131 | 10.3958 | -122.049 | 122.1909 | 122.2 | 21.817 | -122.1085
1366.9531 | 121.669 | -10.7986 | 111.5662 | -0.00022891 | -0.017733 | 0.093037 | 0.036878 | 0.01257 | -0.039364 | -0.0013159 | 7.627e-05 | -0.01875 | 0.026731 | 0.063892 | -0.019619 | -0.02666 | -0.21973 | -0.27466 | -0.68207 | -10.6705 | -0.22888 | -10.7254 | -10.817 | 2.4948 | 11.0825 | -10.73 | 111.3602 | 111.351 | -10.8078 | -10.8627 | 0.073242 | -0.018311 | -111.795 | 10.524 | 0.12817 | 0.14649 | -111.7859 | -0.009155 | -0.064087 | -0.20599 | 13.2935 | 0.068665 | 0.13275 | -0.21515 | 10.5698 | 10.5789 | 10.1166 | -122.3831 | 122.1588 | 122.1497 | 21.8811 | -122.4289
1368.7344 | 121.5317 | -10.6247 | 111.5112 | -0.00022891 | -0.015383 | 0.091328 | 0.03645 | 0.01022 | -0.034451 | 0.0010339 | 7.627e-05 | -0.01405 | 0.026517 | 0.062824 | -0.017697 | -0.026233 | -0.27008 | -0.35248 | -0.67291 | -10.4782 | -0.24261 | -10.556 | -10.6201 | 2.3621 | 11.5036 | -10.6064 | 111.6531 | 111.5936 | -10.6201 | -10.675 | 0.068665 | 0.004578 | -111.7538 | 10.2722 | 0.14648 | 0.14191 | -111.7813 | 0.004578 | -0.050354 | 0.14191 | 12.9868 | 0.018311 | 0.068665 | 0.082398 | 10.3821 | 10.3546 | 9.9518 | -122.1313 | 122.2778 | 122.2183 | 22.1283 | -122.1863
1370.5156 | 122.3694 | -10.5698 | 111.7401 | -0.00022891 | -0.013674 | 0.093678 | 0.03346 | 0.011074 | -0.029751 | 0.0031703 | 7.627e-05 | -0.0117 | 0.028867 | 0.063892 | -0.013424 | -0.027942 | -0.17853 | -0.30212 | -0.55389 | -10.4416 | -0.16479 | -10.5057 | -10.5835 | 2.0691 | 11.5723 | -10.5652 | 111.676 | 111.6257 | -10.5743 | -10.643 | 0.064087 | -0.013733 | -111.9049 | 10.2676 | 0.12817 | 0.14191 | -111.9186 | -0.004578 | -0.073242 | -0.064087 | 12.6389 | 0.004577 | 0.077819 | -0.11444 | 10.405 | 10.3912 | 10.0159 | -122.3236 | 122.2458 | 122.1954 | 22.142 | -122.3831
1372.2969 | 117.1097 | -9.8282 | 112.4359 | -0.00022891 | -0.022646 | 0.094105 | 0.034528 | 0.0070154 | -0.041287 | 0.0014613 | -0.0075532 | -0.019177 | 0.026731 | 0.061329 | -0.01791 | -0.026019 | -0.16937 | -0.19684 | -0.32959 | -9.7733 | -0.10071 | -9.8053 | -9.9106 | 1.8356 | 12.1536 | -9.8328 | 112.3215 | 112.2803 | -9.8877 | -9.9564 | 0.022888 | -0.082397 | -112.5366 | 9.6313 | 0.054932 | 0.13733 | -112.6053 | -0.059509 | -0.12817 | -0.11444 | 11.6638 | -0.004578 | 0.1236 | -0.15564 | 9.7275 | 9.6588 | 9.4986 | -122.3465 | 122.1497 | 122.1085 | 21.9818 | -122.3923
1374.0781 | 121.8201 | -9.5581 | 112.262 | -0.0078584 | -0.024996 | 0.095601 | 0.034741 | 0.011715 | -0.037869 | 0.0003931 | -0.0075532 | -0.015973 | 0.023526 | 0.062397 | -0.01556 | -0.025378 | -0.10529 | -0.15106 | -0.25635 | -9.4803 | -0.082397 | -9.5352 | -9.6222 | 1.6708 | 13.2797 | -9.5123 | 112.6236 | 112.6053 | -9.5993 | -9.6542 | 0.022888 | -0.064087 | -112.3444 | 9.407 | 0.077819 | 0.14191 | -112.3672 | -0.041199 | -0.096131 | 0.36163 | 11.2289 | 0.045776 | 0.14191 | 0.34332 | 9.4757 | 9.4528 | 9.3018 | -121.8842 | 122.1817 | 122.1634 | 22.8378 | -121.9162
1375.7969 | 122.1268 | -1.5152 | 120.7626 | 0.0074006 | -0.014315 | 0.090474 | 0.033887 | 0.018765 | -0.031247 | 0.0065881 | 7.627e-05 | -0.010846 | 0.028653 | 0.05962 | -0.018551 | -0.02901 | -0.34332 | -0.47607 | -0.34332 | -1.4465 | -0.25177 | -1.4374 | -1.593 | 1.5289 | 17.8116 | -1.5472 | 120.8038 | 120.7672 | -1.5289 | -1.5747 | 0.07782 | -0.07782 | -121.0144 | 1.0391 | 0.068665 | 0.14648 | -121.106 | -0.013733 | -0.059509 | 0.041199 | 3.0441 | -0.032043 | 0.027466 | 0.004578 | 1.2634 | 1.1719 | 1.1719 | -122.3557 | 122.319 | 122.2824 | 19.3268 | -122.3373
1377.5781 | 95.9793 | -1.3367 | 120.3094 | -0.00022891 | -0.017733 | 0.093037 | 0.037732 | 0.017697 | -0.040219 | 0.0072291 | 0.0077058 | -0.017682 | 0.027585 | 0.056202 | -0.022183 | -0.027301 | -0.23804 | -0.24261 | -0.1236 | -1.1993 | -0.27466 | -1.2634 | -1.3916 | 1.5518 | 18.6401 | -1.2268 | 120.8817 | 120.8588 | -1.3641 | -1.4099 | 0.073242 | -0.054932 | -120.5841 | 1.0941 | 0.13733 | 0.19226 | -120.5475 | -0.027466 | -0.073242 | 0.5722 | 2.8885 | 0.10986 | 0.18311 | 0.54932 | 1.062 | 1.0986 | 1.2131 | -121.7011 | 122.2183 | 122.1954 | 19.9768 | -121.7194
1379.2969 | 107.0709 | -1.3779 | 120.1355 | -0.0078584 | -0.024355 | 0.09261 | 0.034528 | 0.018978 | -0.039151 | 0.0063745 | 7.627e-05 | -0.015973 | 0.02609 | 0.05962 | -0.022183 | -0.02666 | -0.27466 | -0.31586 | -0.21057 | -1.4191 | -0.2243 | -1.4465 | -1.5701 | 1.3962 | 19.0704 | -1.4511 | 120.7031 | 120.7306 | -1.561 | -1.5976 | -0.068664 | -0.19226 | -120.3598 | 1.062 | -0.041198 | 0.15106 | -120.4102 | -0.18311 | -0.21973 | 0.56763 | 2.774 | -0.073242 | 0.14648 | 0.59509 | 1.1536 | 1.1032 | 1.1673 | -121.7056 | 122.081 | 122.1085 | 20.4483 | -121.7331
1381.0781 | 121.8658 | -1.8082 | 120.282 | -0.015487 | -0.015169 | 0.091542 | 0.035382 | 0.019833 | -0.032101 | 0.0095789 | 0.0077058 | -0.012768 | 0.026304 | 0.058552 | -0.017483 | -0.028369 | -0.29755 | -0.40283 | -0.33417 | -1.7075 | -0.23346 | -1.7303 | -1.8723 | 1.268 | 19.249 | -1.7853 | 120.4926 | 120.4376 | -1.8402 | -1.886 | 0.07782 | -0.064086 | -120.5154 | 1.4053 | 0.10071 | 0.1648 | -120.5795 | -0.032043 | -0.077819 | 0.21057 | 3.0762 | 0.022889 | 0.10071 | 0.15564 | 1.5747 | 1.5106 | 1.474 | -122.1542 | 122.3007 | 122.2458 | 21.0571 | -122.168
1382.7969 | 122.2229 | -2.7603 | 119.22 | -0.00022891 | -0.0089744 | 0.09026 | 0.038587 | 0.017269 | -0.03146 | 0.0091517 | -0.0075532 | -0.011914 | 0.032285 | 0.062824 | -0.017483 | -0.029224 | -0.43488 | -0.56763 | -0.48981 | -2.6276 | -0.35706 | -2.655 | -2.7969 | 1.1124 | 19.1528 | -2.7466 | 119.5862 | 119.5953 | -2.7649 | -2.8061 | 0.10529 | -0.036621 | -119.577 | 2.1927 | 0.13275 | 0.16937 | -119.6548 | -0.004578 | -0.045776 | 0.36621 | 3.8727 | 0.013733 | 0.059509 | 0.37537 | 2.4033 | 2.3254 | 2.2705 | -122.0169 | 122.3465 | 122.3557 | 21.9131 | -122.0261
1384.5938 | 103.9673 | -2.7145 | 118.7164 | -0.0078584 | -0.016024 | 0.091755 | 0.035596 | 0.017056 | -0.04321 | 0.0059473 | -0.0075532 | -0.017895 | 0.029081 | 0.057484 | -0.023037 | -0.024951 | -0.95673 | -0.9613 | -2.7283 | -2.7649 | -0.9613 | -2.8473 | -2.9709 | 1.1719 | 19.2261 | -2.7603 | 119.3298 | 119.2978 | -2.9343 | -2.9892 | -0.13275 | -0.25635 | -119.6777 | 1.7532 | -0.050354 | 0.20599 | -119.6732 | -0.21973 | -0.27466 | 0.6134 | 3.8864 | -0.045776 | 0.22888 | 0.58136 | 1.7532 | 1.7578 | -0.013732 | -121.6873 | 122.0444 | 122.0123 | 21.9406 | -121.7056
1386.3125 | 122.3877 | -4.0421 | 118.3411 | 0.0074006 | -0.016451 | 0.091328 | 0.03111 | 0.01556 | -0.03381 | 0.0078699 | 7.627e-05 | -0.014904 | 0.02844 | 0.060902 | -0.014279 | -0.027087 | -2.092 | -2.1744 | -3.9276 | -3.891 | -2.0645 | -3.9688 | -4.0878 | 0.96588 | 19.0109 | -3.9047 | 118.2358 | 118.1992 | -4.0283 | -4.0695 | 0.073242 | -0.045777 | -120.4056 | 1.8677 | 0.15106 | 0.19684 | -120.433 | 0.013733 | -0.027466 | -0.10529 | 5.0079 | 0.13733 | 0.16479 | -0.14191 | 1.9775 | 1.9501 | 0.11444 | -122.4289 | 122.2778 | 122.2412 | 23.053 | -122.4106
1388.0781 | 122.4106 | -3.7949 | 118.2449 | -0.00022891 | -0.020083 | 0.092396 | 0.034741 | 0.01791 | -0.038296 | 0.0063745 | -0.0075532 | -0.017254 | 0.026517 | 0.057057 | -0.019192 | -0.026019 | -2.1652 | -2.1652 | -3.7537 | -4.0512 | -2.1652 | -3.8086 | -3.9413 | 1.3779 | 19.3085 | -3.7491 | 118.3411 | 118.2907 | -3.9276 | -3.9642 | -0.013733 | -0.14648 | -120.4102 | 1.6296 | -0.25635 | -0.10986 | -120.4102 | -0.13275 | -0.16937 | 0.09613 | 5.1727 | 0.045777 | 0.21515 | 0.045776 | 1.6296 | 1.6296 | 0.041199 | -122.1863 | 122.1359 | 122.0856 | 23.1033 | -122.2092
1389.875 | 122.168 | -3.4378 | 118.396 | -0.00022891 | -0.015597 | 0.091755 | 0.037946 | 0.012142 | -0.031674 | 0.0040247 | -0.0075532 | -0.014477 | 0.028013 | 0.059406 | -0.019406 | -0.027728 | -2.1286 | -2.1835 | -2.9663 | -2.1606 | -2.0874 | -3.0304 | -3.1494 | 0.85602 | 19.5236 | -3.0121 | 119.2062 | 119.1696 | -3.1265 | -3.186 | 0.40741 | 0.28839 | -120.4834 | 1.2543 | 1.2772 | 0.98877 | -120.5246 | 0.31128 | 0.25177 | 0.81024 | 4.2938 | 0.42572 | 0.17395 | 0.77362 | 1.3504 | 1.3092 | 0.4715 | -121.5454 | 122.644 | 122.6074 | 22.9614 | -121.582
1391.5938 | 122.3007 | -3.3463 | 118.6157 | -0.00022891 | -0.013247 | 0.086842 | 0.035382 | 0.014065 | -0.025692 | 0.0048791 | -0.015182 | -0.011273 | 0.029081 | 0.062397 | -0.01791 | -0.027728 | -1.9821 | -2.0782 | -3.0579 | -2.0416 | -1.9363 | -3.1311 | -3.2318 | 1.1673 | 19.455 | -3.1769 | 119.0369 | 118.9957 | -3.3325 | -3.3829 | 0.21515 | 0.11444 | -120.5521 | 1.268 | 1.3046 | 1.1902 | -120.5978 | 0.013732 | -0.036622 | 0.42114 | 4.5135 | 0.16937 | 0.20599 | 0.37994 | 1.4099 | 1.3641 | 0.28839 | -121.8475 | 122.3831 | 122.3419 | 22.8012 | -121.9986
1393.3281 | 122.0947 | -5.8044 | 116.0934 | -0.00022891 | -0.021792 | 0.095601 | 0.033246 | 0.00787 | -0.037869 | 0.0033839 | 7.627e-05 | -0.015545 | 0.027585 | 0.058338 | -0.015774 | -0.024524 | -5.1453 | -5.1682 | -5.658 | -5.159 | -5.0446 | -5.6717 | -5.7816 | 0.91095 | 18.0771 | -5.5984 | 116.5009 | 116.4917 | -5.7495 | -5.8182 | 0.13275 | 0.022888 | -121.138 | 0.63629 | 0.64545 | 0.62256 | -121.2387 | 0.054931 | -0.013733 | 0.40741 | 6.7154 | 0.20599 | 0.21973 | 0.39825 | 0.75989 | 0.65918 | 0.14648 | -121.875 | 122.3053 | 122.2961 | 23.8815 | -121.9116
1395.0938 | 122.4792 | -5.484 | 116.478 | -0.0078584 | -0.013033 | 0.090901 | 0.034955 | 0.012356 | -0.029324 | 0.0053065 | -0.0075532 | -0.010418 | 0.028867 | 0.063465 | -0.015133 | -0.029651 | -4.8523 | -4.9759 | -5.4153 | -4.9255 | -4.7516 | -5.4062 | -5.5252 | 0.97504 | 17.7246 | -5.3833 | 116.8625 | 116.835 | -5.5023 | -5.5344 | 0.07782 | -0.041199 | -121.2296 | 0.50812 | 0.55847 | 0.59967 | -121.3303 | -0.01831 | -0.050354 | 0.38452 | 6.459 | 0.10071 | 0.15106 | 0.35706 | 0.73242 | 0.63171 | 0.068665 | -122.0032 | 122.3465 | 122.319 | 23.2086 | -122.0123
1396.875 | 121.962 | -5.1132 | 116.89 | -0.0078584 | -0.018374 | 0.093251 | 0.032819 | 0.012142 | -0.041501 | 0.0046655 | 0.0077058 | -0.017254 | 0.025449 | 0.060261 | -0.018551 | -0.024097 | -4.8752 | -4.8981 | -5.0262 | -4.8523 | -4.7287 | -5.0446 | -5.1544 | 0.94299 | 17.7246 | -4.9484 | 117.1692 | 117.1555 | -5.1132 | -5.1682 | 0.068664 | -0.041199 | -121.6187 | 0.21515 | 0.26093 | 0.30212 | -121.7651 | 0 | -0.054932 | 0.27923 | 6.0562 | 0.16479 | 0.21973 | 0.2655 | 0.38452 | 0.23804 | 0.086975 | -122.0444 | 122.2824 | 122.2687 | 22.8378 | -122.0581
1398.5938 | 121.9208 | -4.8843 | 117.5537 | -0.0078584 | -0.017946 | 0.089833 | 0.033887 | 0.012142 | -0.036587 | 0.0046655 | 7.627e-05 | -0.016186 | 0.029508 | 0.058766 | -0.016842 | -0.027728 | -4.6646 | -4.7104 | -4.6967 | -4.7195 | -4.6051 | -4.7424 | -4.8477 | 1.1078 | 17.3264 | -4.6463 | 117.4301 | 117.3889 | -4.8569 | -4.8889 | 0.14191 | 0.036621 | -122.1588 | 0.17395 | 0.16479 | 0.12817 | -122.2183 | 0.027465 | -0.004578 | -0.1236 | 5.9921 | 0.23804 | 0.24261 | -0.1648 | 0.27923 | 0.21973 | 0.18768 | -122.4014 | 122.3145 | 122.2733 | 22.2107 | -122.4426
1400.2969 | 122.4838 | -4.8477 | 117.5766 | -0.0078584 | -0.011538 | 0.08791 | 0.033887 | 0.015133 | -0.032742 | 0.0089381 | 0.0077058 | -0.010632 | 0.031003 | 0.062397 | -0.012356 | -0.027942 | -4.7562 | -4.8889 | -4.8065 | -4.7882 | -4.5639 | -4.7607 | -4.8752 | 0.99792 | 17.0883 | -4.7562 | 117.5079 | 117.4805 | -4.8203 | -4.8981 | 0.086975 | -0.027466 | -122.1405 | -0.041199 | 0.059509 | 0.086975 | -122.3328 | 0.027466 | -0.050354 | -0.068664 | 5.8456 | 0.091552 | 0.14191 | -0.09613 | 0.28381 | 0.091552 | 0.041198 | -122.4518 | 122.3557 | 122.3282 | 21.936 | -122.4747
1402.0781 | 122.5021 | -4.5776 | 117.8101 | -0.0078584 | -0.010256 | 0.087696 | 0.036023 | 0.012356 | -0.035733 | 0.0076563 | -0.015182 | -0.013409 | 0.032071 | 0.063892 | -0.016201 | -0.025378 | -4.5181 | -4.6234 | -4.5639 | -4.5227 | -4.3259 | -4.509 | -4.6326 | 1.0712 | 17.4591 | -4.4815 | 117.7734 | 117.7277 | -4.5868 | -4.6371 | 0.068665 | -0.054931 | -122.1359 | -0.045776 | 0.054932 | 0.10986 | -122.3282 | -0.009155 | -0.059509 | -0.036622 | 5.6488 | 0.096131 | 0.15564 | -0.082398 | 0.25177 | 0.05951 | 0.013733 | -122.4426 | 122.3511 | 122.3053 | 22.0367 | -122.4472
1403.8594 | 122.0032 | -4.7928 | 117.2287 | -0.00022891 | -0.015169 | 0.091755 | 0.037946 | 0.012997 | -0.042996 | 0.0040247 | 7.627e-05 | -0.017895 | 0.026517 | 0.061329 | -0.019619 | -0.024097 | -4.7745 | -4.7928 | -4.7424 | -4.7882 | -4.6875 | -4.7882 | -4.8935 | 1.0025 | 17.3492 | -4.6371 | 117.3843 | 117.3706 | -4.8889 | -4.9393 | 0.004578 | -0.10071 | -121.9162 | 0 | 0.004578 | 0.10529 | -122.0032 | -0.09613 | -0.14648 | 0.15564 | 5.7953 | 0.15564 | 0.30212 | 0.14191 | 0.10529 | 0.018311 | 0.050354 | -122.1222 | 122.1771 | 122.1634 | 22.142 | -122.168
1405.6406 | 121.7926 | -5.6625 | 116.4917 | -0.00022891 | -0.014101 | 0.091969 | 0.034955 | 0.012356 | -0.038937 | 0.0055201 | 7.627e-05 | -0.014264 | 0.027799 | 0.062183 | -0.015988 | -0.02666 | -5.5389 | -5.5618 | -5.5023 | -5.5206 | -5.4199 | -5.5618 | -5.6442 | 0.96588 | 17.5095 | -5.4108 | 116.6336 | 116.6336 | -5.6305 | -5.6992 | 0.10071 | 0.018311 | -121.9116 | 0.10071 | 0.14191 | 0.1236 | -122.0306 | 0.032044 | -0.036621 | 0.14191 | 6.6284 | 0.25177 | 0.28839 | 0.14191 | 0.24262 | 0.1236 | 0.16022 | -122.1359 | 122.2961 | 122.2961 | 23.172 | -122.1909
1407.4219 | 122.3694 | -5.4703 | 116.9449 | -0.015487 | -0.015383 | 0.089619 | 0.033887 | 0.012142 | -0.035305 | 0.0025293 | 7.627e-05 | -0.011914 | 0.028653 | 0.064961 | -0.012142 | -0.025592 | -5.4291 | -5.5206 | -5.4565 | -5.4245 | -5.2231 | -5.4153 | -5.5252 | 0.83771 | 17.688 | -5.3284 | 116.89 | 116.8396 | -5.4794 | -5.5481 | 0.054932 | -0.054932 | -122.168 | -0.050354 | 0.045776 | 0.10071 | -122.374 | -0.009155 | -0.07782 | -0.054931 | 6.308 | 0.14191 | 0.21973 | -0.10528 | 0.24719 | 0.041199 | 0.013733 | -122.4701 | 122.3602 | 122.3099 | 23.1583 | -122.493
1409.1406 | 121.6919 | -5.2368 | 116.5604 | -0.00022891 | -0.015383 | 0.090046 | 0.036023 | 0.011502 | -0.040005 | 0.0063745 | -0.0075532 | -0.018109 | 0.030149 | 0.062397 | -0.016201 | -0.026874 | -5.0949 | -5.1132 | -5.0629 | -5.1224 | -5.0308 | -5.1544 | -5.2597 | 0.91553 | 18.4204 | -4.953 | 117.0502 | 117.0227 | -5.2368 | -5.278 | 0.082397 | -0.022889 | -121.5912 | 0.1236 | 0.11444 | 0.13733 | -121.6553 | 0 | -0.041199 | 0.48981 | 6.1523 | 0.28381 | 0.32501 | 0.46234 | 0.20599 | 0.14191 | 0.17395 | -121.8201 | 122.287 | 122.2595 | 23.6572 | -121.8384
1410.9375 | 122.5479 | -4.985 | 117.3111 | -0.00022891 | -0.013888 | 0.088337 | 0.032605 | 0.010647 | -0.034878 | 0.0059473 | 7.627e-05 | -0.011273 | 0.027372 | 0.063038 | -0.01257 | -0.028369 | -4.9072 | -5.0262 | -4.9301 | -4.9393 | -4.7699 | -4.8981 | -5.0079 | 0.83771 | 18.4021 | -4.7607 | 117.3431 | 117.3431 | -4.9805 | -5.04 | 0.086975 | -0.022889 | -122.081 | -0.041199 | 0.045776 | 0.068665 | -122.2183 | 0.004577 | -0.054932 | 0.032044 | 5.8228 | 0.2243 | 0.27924 | 0.032044 | 0.21515 | 0.077819 | 0.054931 | -122.319 | 122.3282 | 122.3282 | 23.3871 | -122.3511
1412.7188 | 121.6507 | -5.1819 | 116.6977 | 0.0074006 | -0.016665 | 0.090474 | 0.03645 | 0.010006 | -0.03851 | 0.0027429 | -0.0075532 | -0.01405 | 0.029508 | 0.063679 | -0.015774 | -0.026233 | -5.0034 | -5.0491 | -4.9713 | -5.0354 | -4.9438 | -5.0262 | -5.1636 | 0.82855 | 18.0862 | -4.8569 | 117.1783 | 117.1738 | -5.1361 | -5.1865 | 0.15564 | 0.018311 | -121.6415 | 0.13275 | 0.14649 | 0.12817 | -121.701 | 0.045777 | -0.004577 | 0.48065 | 6.0104 | 0.32501 | 0.32959 | 0.47607 | 0.23804 | 0.17853 | 0.21057 | -121.8613 | 122.3602 | 122.3557 | 23.2681 | -121.8842
1414.4531 | 122.4701 | -5.0903 | 117.2333 | -0.00022891 | -0.014529 | 0.089833 | 0.031964 | 0.010647 | -0.032101 | 0.0055201 | 7.627e-05 | -0.011486 | 0.028653 | 0.064961 | -0.011074 | -0.028155 | -4.9713 | -5.1361 | -5.0262 | -5.0262 | -4.8477 | -4.9988 | -5.0995 | 0.6958 | 18.1824 | -4.9026 | 117.2882 | 117.3111 | -5.072 | -5.127 | 0.091553 | -0.009155 | -122.081 | -0.045776 | 0.064087 | 0.073242 | -122.2046 | 0.018311 | -0.036621 | 0.054932 | 5.7861 | 0.18768 | 0.2243 | 0.07782 | 0.24261 | 0.11902 | 0.064087 | -122.3328 | 122.3785 | 122.4014 | 23.2727 | -122.3602
1416.2344 | 122.4838 | -4.7745 | 117.6224 | 0.0074006 | -0.016024 | 0.091755 | 0.032819 | 0.010647 | -0.034024 | 0.0070155 | 7.627e-05 | -0.010846 | 0.028867 | 0.065815 | -0.0093652 | -0.026019 | -4.6921 | -4.7974 | -4.7241 | -4.7333 | -4.5456 | -4.6783 | -4.8019 | 0.64087 | 18.3655 | -4.6234 | 117.5949 | 117.5766 | -4.7928 | -4.8386 | 0.09613 | -0.027466 | -122.168 | -0.022888 | 0.041199 | 0.068665 | -122.3145 | -0.018311 | -0.064087 | -0.027465 | 5.4153 | 0.15106 | 0.21515 | -0.045776 | 0.22888 | 0.082397 | 0.050354 | -122.4243 | 122.3694 | 122.3511 | 23.14 | -122.4609
1418.0312 | 121.6919 | -4.5685 | 117.5949 | -0.0078584 | -0.015169 | 0.090046 | 0.033887 | 0.0093652 | -0.041501 | 0.0063745 | -0.0075532 | -0.015973 | 0.029294 | 0.06197 | -0.015988 | -0.02666 | -4.4266 | -4.454 | -4.3945 | -4.4128 | -4.3488 | -4.4403 | -4.5547 | 0.62714 | 18.4525 | -4.2847 | 117.8055 | 117.8238 | -4.5456 | -4.5731 | 0.12817 | 0.013732 | -121.9437 | 0.11444 | 0.15564 | 0.14191 | -122.0215 | 0.022888 | -0.004578 | 0.21057 | 5.1956 | 0.28381 | 0.28839 | 0.22888 | 0.21973 | 0.14191 | 0.17395 | -122.1497 | 122.374 | 122.3923 | 23.0209 | -122.168
1419.8125 | 121.9666 | -4.1107 | 118.3868 | 0.01503 | -0.018587 | 0.091969 | 0.035596 | 0.008938 | -0.037869 | 0.0035975 | 7.627e-05 | -0.012127 | 0.028226 | 0.063252 | -0.015133 | -0.026874 | -4.0237 | -4.0741 | -4.0192 | -4.0192 | -3.8406 | -4.0009 | -4.1107 | 0.57678 | 19.0704 | -3.8818 | 118.3044 | 118.2678 | -4.0924 | -4.1565 | 0.10986 | 0 | -122.2275 | 0.036621 | 0.091553 | 0.091553 | -122.4106 | 0.018311 | -0.045776 | -0.082398 | 4.6875 | 0.22888 | 0.27466 | -0.11902 | 0.27008 | 0.086975 | 0.091553 | -122.4976 | 122.4152 | 122.3785 | 23.1812 | -122.5433
1421.5312 | 122.5479 | -3.8727 | 118.5242 | 0.0074006 | -0.018587 | 0.092183 | 0.034528 | 0.011502 | -0.034878 | 0.0080835 | 7.627e-05 | -0.01405 | 0.03079 | 0.06667 | -0.014706 | -0.026019 | -3.8132 | -3.8956 | -3.8315 | -3.8132 | -3.6575 | -3.8086 | -3.9413 | 0.58136 | 19.1574 | -3.6758 | 118.5013 | 118.4463 | -3.8864 | -3.9642 | 0.064087 | -0.068664 | -122.1817 | -0.022888 | 0.05951 | 0.12817 | -122.3373 | -0.013733 | -0.091552 | -0.022888 | 4.454 | 0.19684 | 0.28839 | -0.07782 | 0.21515 | 0.05951 | 0.041199 | -122.4655 | 122.374 | 122.319 | 23.0301 | -122.4884
1423.3125 | 121.9437 | -3.9047 | 118.6295 | -0.00022891 | -0.021151 | 0.090687 | 0.033673 | 0.01022 | -0.040646 | 0.0038111 | 7.627e-05 | -0.013623 | 0.029081 | 0.064533 | -0.015988 | -0.025806 | -3.7628 | -3.7765 | -3.6987 | -3.7537 | -3.653 | -3.7262 | -3.8498 | 0.60425 | 19.4458 | -3.5614 | 118.483 | 118.4784 | -3.8177 | -3.9139 | 0.17853 | 0.054932 | -122.2824 | 0.12817 | 0.15106 | 0.09613 | -122.3923 | 0.086975 | -0.009155 | -0.14648 | 4.509 | 0.34332 | 0.35248 | -0.15106 | 0.25177 | 0.14191 | 0.20599 | -122.4792 | 122.3877 | 122.3831 | 23.3505 | -122.5433
1425.0312 | 122.4335 | -3.8956 | 118.4372 | 0.0074006 | -0.022433 | 0.091328 | 0.032605 | 0.013424 | -0.036587 | 0.0061609 | -0.015182 | -0.0097776 | 0.026944 | 0.067524 | -0.01321 | -0.028369 | -3.7125 | -3.7491 | -3.6758 | -3.7262 | -3.6942 | -3.7537 | -3.8635 | 0.63629 | 19.4321 | -3.5019 | 118.4738 | 118.4784 | -3.8452 | -3.9093 | 0.14191 | 0.032044 | -122.1313 | 0.14649 | 0.16937 | 0.13733 | -122.1497 | 0.050354 | -0.013733 | 0.036621 | 4.5319 | 0.39368 | 0.40741 | 0.041199 | 0.20142 | 0.18311 | 0.21973 | -122.3007 | 122.3694 | 122.374 | 23.3276 | -122.3465
1426.7969 | 121.6965 | -56.3004 | 65.1352 | -0.00022891 | 0.76391 | -0.70399 | 0.031323 | 0.56799 | -0.012448 | 0.77328 | 7.627e-05 | 2.1373 | -0.044619 | 0.10982 | 0.51999 | 0.12629 | -51.535 | -51.6907 | -51.7227 | -52.272 | -8.9584 | -54.657 | -54.6936 | -0.41657 | -1.6754 | -33.8287 | 65.4236 | 65.3915 | -55.8334 | -56.012 | 1.6434 | 1.6067 | -74.0936 | 4.6097 | 4.0283 | 2.4216 | -116.6702 | 0.46692 | 0.28839 | 0.28839 | 55.8838 | 22.4716 | 22.1832 | 0.25635 | 47.3419 | 4.7653 | 4.5776 | -119.8288 | 121.7239 | 121.6919 | 54.6249 | -121.1472
1428.5938 | 121.7468 | -61.4685 | 60.0998 | -0.0078584 | -0.01816 | 0.015919 | 0.036023 | -0.008579 | -0.037869 | -0.0015295 | 7.627e-05 | 3.6092 | -0.042483 | 0.24569 | 1.612 | 1.6842 | 0.11902 | 0.064087 | 0.15564 | 0.07782 | 0.082397 | 0.059509 | -0.073242 | 0.20599 | -1.5793 | -6.6513 | 58.9554 | 58.8409 | -62.2192 | -62.439 | 61.528 | 61.3953 | -60.0174 | 61.5326 | 61.5463 | 0.15106 | -59.9808 | -0.75073 | -0.97046 | -1.1444 | 61.6745 | 54.8172 | 55.7877 | -1.2589 | 61.5509 | 61.5875 | 61.6241 | -60.173 | 120.4239 | 120.3094 | 59.8892 | -122.5388
1430.3281 | 121.5134 | -53.8513 | 67.1585 | -0.00022891 | -0.018801 | 0.013356 | 0.039227 | -0.0090062 | -0.03851 | -3.4096e-05 | 7.627e-05 | 7.0022 | -0.0068081 | 0.29973 | 1.3322 | 5.8435 | 0.11902 | 0.068665 | 0.1236 | 0.082397 | 0.082397 | 0.054932 | -0.086975 | 0.24261 | -1.8127 | -4.628 | 69.3329 | 69.0079 | -51.21 | -51.5259 | 53.9062 | 53.7643 | -67.0761 | 53.92 | 53.9337 | 0.16937 | -67.0395 | 2.6413 | 2.3254 | 2.1744 | 54.0939 | 49.2233 | 46.8979 | 1.8494 | 53.9337 | 53.9703 | 53.9749 | -67.2455 | 123.1842 | 122.8592 | 52.0386 | -118.6844
1432.1094 | 119.4031 | -80.4977 | 38.9145 | -0.0078584 | -0.019228 | 0.015492 | 0.034314 | -0.0087926 | -0.037655 | -0.0004613 | -0.0075532 | 7.0022 | -0.010226 | 2.2836 | 2.6 | 7.0077 | 0.11902 | 0.032043 | 0.10986 | 0.059509 | 0.09613 | 0.054932 | -0.068665 | 2.0279 | -12.9822 | 14.8773 | 34.7809 | 34.8221 | -77.5543 | -76.9684 | 80.5527 | 80.4291 | -38.8184 | 80.5298 | 80.5573 | 0.12817 | -38.7955 | 2.9434 | 3.5294 | -4.1336 | 82.5256 | 95.3751 | 91.8457 | -4.0924 | 80.5939 | 80.6168 | 80.6076 | -38.9832 | 115.2786 | 115.3198 | 67.5156 | -115.8829
1433.8281 | 121.0281 | -66.7511 | 54.0894 | -0.015487 | -0.02521 | 0.015492 | 0.032819 | -0.010502 | -0.039364 | -0.0013159 | 7.627e-05 | 7.0022 | -0.016207 | 3.0683 | 1.979 | 2.6028 | 0.14648 | 0.091553 | 0.14191 | 0.086975 | 0.086975 | 0.041199 | -0.07782 | 0.14648 | -3.9185 | -4.3304 | 52.1622 | 52.1805 | -67.4515 | -67.6529 | 66.7923 | 66.6733 | -54.0024 | 66.8427 | 66.8381 | 0.16479 | -53.9429 | -0.70038 | -0.90179 | -1.9272 | 66.8976 | 62.4207 | 63.3224 | -1.9089 | 66.8381 | 66.8976 | 66.893 | -54.1672 | 118.9133 | 118.9316 | 62.8326 | -121.7422
1435.625 | 121.3028 | -63.6246 | 57.3578 | -0.0078584 | -0.016238 | 0.015919 | 0.035596 | -0.012638 | -0.038937 | 0.0006067 | -0.0075532 | 5.2691 | -0.014285 | 3.8183 | 1.4971 | 0.028455 | 0.068665 | 0.013733 | 0.068665 | 0.045776 | 0.09613 | 0.045776 | -0.086975 | 0.11902 | -2.6642 | -5.9601 | 56.4926 | 56.4789 | -63.858 | -64.1876 | 63.6703 | 63.5376 | -57.2617 | 63.6383 | 63.6703 | 0.13275 | -57.2891 | -0.23346 | -0.56305 | -0.86517 | 63.7436 | 57.6645 | 58.2275 | -0.87891 | 63.7207 | 63.6932 | 63.6932 | -57.4448 | 120.1172 | 120.1035 | 60.9604 | -121.5454
1437.3594 | 121.312 | -120.0439 | 0.82855 | 0.0074006 | -0.016451 | 0.013142 | 0.034314 | -0.011143 | -0.030606 | 0.0006067 | -0.0075532 | 0.034656 | -0.042697 | -0.00019431 | -0.0091516 | 4.2822e-05 | 0.064087 | -0.086975 | -0.009155 | 0.009155 | 0.13275 | 0.018311 | -0.12817 | 0.004578 | -0.29297 | -0.07782 | 0.82398 | 0.82855 | -0.013733 | -0.10071 | 120.0623 | 119.9158 | -0.6958 | 119.957 | 120.0531 | 0.13733 | -0.76446 | 120.0302 | 119.9432 | -0.004577 | 120.0485 | 119.9661 | 0.022888 | 0 | 120.1767 | 120.108 | 120.0348 | -0.95673 | 120.8679 | 120.8725 | 119.751 | -0.92926
1439.1406 | 121.4539 | -120.3644 | 0.84686 | 0.0074006 | -0.015597 | 0.01421 | 0.037732 | -0.00922 | -0.034024 | -3.4096e-05 | 0.0077058 | 0.031879 | -0.044192 | -0.0019033 | -0.013851 | 0.00068362 | 0.054932 | -0.054932 | -0.004578 | 0.004578 | 0.13733 | 0.009155 | -0.14648 | -0.009155 | -0.18768 | -0.068665 | 0.85602 | 0.83313 | -0.045776 | -0.10529 | 120.3735 | 120.2179 | -0.70953 | 120.3094 | 120.369 | 0.15106 | -0.79193 | 120.3186 | 120.2591 | 0.009155 | 120.3552 | 120.2957 | 0.036621 | -0.013733 | 120.5017 | 120.4193 | 120.3598 | -0.99335 | 121.2204 | 121.1975 | 120.1767 | -0.95215
1440.875 | 121.5866 | -120.3598 | 0.92468 | 0.0074006 | -0.015383 | 0.012501 | 0.032178 | -0.0096472 | -0.033383 | 0.0040247 | -0.015182 | 0.034229 | -0.043338 | -0.0016897 | -0.011715 | 0.0036744 | 0.073242 | -0.068665 | 0.013733 | -0.004578 | 0.13733 | 0.027466 | -0.10986 | 0.050354 | -0.1831 | -0.045776 | 0.91095 | 0.90637 | -0.018311 | -0.11444 | 120.3873 | 120.2499 | -0.78735 | 120.2911 | 120.3552 | 0.10529 | -0.85144 | 120.3415 | 120.2454 | -0.013733 | 120.4102 | 120.314 | 0.068665 | -0.018311 | 120.4971 | 120.433 | 120.3735 | -1.0345 | 121.2708 | 121.2662 | 120.1767 | -1.0391
1442.6562 | 121.463 | -120.1401 | 1.3275 | -0.00022891 | -0.019228 | 0.012501 | 0.035596 | -0.01157 | -0.038937 | 0.0006067 | 7.627e-05 | 0.029102 | -0.043978 | -0.0040395 | -0.015774 | 0.0036744 | 0.11444 | 0.045776 | 0.10529 | 0.050354 | 0.091553 | 0.041199 | -0.07782 | 0.086975 | -0.054932 | 0.022888 | 1.2451 | 1.2497 | -0.032043 | -0.068665 | 120.1813 | 120.0623 | -1.236 | 120.1859 | 120.1904 | 0.12817 | -1.2131 | 120.108 | 120.0714 | -0.082398 | 120.2271 | 120.163 | 0.091553 | -0.07782 | 120.2316 | 120.2545 | 120.2454 | -1.4053 | 121.3852 | 121.3898 | 120.0851 | -1.3962
1444.3906 | 121.5454 | -119.9158 | 1.506 | -0.00022891 | -0.013888 | 0.012715 | 0.039014 | -0.011143 | -0.036801 | 0.0003931 | 7.627e-05 | 0.034442 | -0.042697 | -0.0016897 | -0.014492 | -0.00017078 | 0.036621 | -0.050354 | 0 | 0.004578 | 0.12817 | 0.004578 | -0.10529 | 0.004578 | -0.086975 | -0.091553 | 1.5015 | 1.4786 | -0.068665 | -0.10986 | 119.9203 | 119.8105 | -1.3779 | 119.8654 | 119.9203 | 0.10986 | -1.4694 | 119.8471 | 119.8059 | -0.004577 | 119.9203 | 119.8242 | 0.01831 | -0.027465 | 120.0439 | 119.9524 | 119.9158 | -1.6113 | 121.4172 | 121.3943 | 119.8288 | -1.6159
1446.1562 | 121.6415 | -119.7464 | 1.6479 | 0.0074006 | -0.012606 | 0.012074 | 0.037091 | -0.008579 | -0.03616 | 0.0038111 | -0.0075532 | 0.032306 | -0.044192 | -0.0016897 | -0.010647 | 0.0023926 | 0.050354 | -0.045776 | 0.018311 | 0.032043 | 0.13733 | 0.004578 | -0.12817 | 0.027466 | -0.009155 | -0.045776 | 1.6434 | 1.6342 | -0.050354 | -0.11902 | 119.751 | 119.6182 | -1.5106 | 119.7006 | 119.7784 | 0.16022 | -1.5976 | 119.696 | 119.6274 | -0.004577 | 119.7739 | 119.7006 | 0.073243 | -0.013733 | 119.8837 | 119.7968 | 119.7647 | -1.7761 | 121.3898 | 121.3806 | 119.7372 | -1.767
1447.9375 | 121.6187 | -118.2312 | 3.2043 | 0.0074006 | -0.014101 | 0.012501 | 0.032178 | -0.0098608 | -0.032315 | 0.0029565 | 7.627e-05 | 0.033161 | -0.043124 | -0.0012625 | -0.0093652 | 0.003247 | 0.013733 | -0.082397 | -0.009155 | 0.004578 | 0.11902 | 0.013733 | -0.1236 | -0.045776 | -0.022888 | -0.10071 | 3.1815 | 3.1815 | -0.045776 | -0.10986 | 118.2449 | 118.1076 | -3.0853 | 118.1488 | 118.2358 | 0.12817 | -3.1906 | 118.1854 | 118.1213 | -0.022888 | 118.1854 | 118.1305 | 0.009155 | -0.022888 | 118.3502 | 118.2449 | 118.222 | -3.3279 | 121.4127 | 121.4127 | 118.2083 | -3.3142
1449.6562 | 121.6507 | -117.9565 | 3.5385 | -0.00022891 | -0.014315 | 0.013142 | 0.032819 | -0.0079382 | -0.036374 | 0.0040247 | -0.0075532 | 0.031452 | -0.044619 | -0.0021169 | -0.008938 | 0.0026062 | 0.10071 | 0.013733 | 0.054932 | 0.050354 | 0.11444 | 0.022888 | -0.11444 | 0.036621 | 0.11444 | -0.018311 | 3.4973 | 3.479 | -0.022888 | -0.09613 | 117.9794 | 117.8421 | -3.4241 | 117.9703 | 118.0069 | 0.16479 | -3.4378 | 117.9337 | 117.8604 | -0.041199 | 117.9932 | 117.9382 | 0.077819 | -0.059509 | 118.071 | 118.0573 | 118.0115 | -3.653 | 121.4539 | 121.4355 | 118.071 | -3.6346
1451.4375 | 121.5866 | -115.5991 | 5.9647 | -0.0078584 | -0.017946 | 0.015492 | 0.036878 | -0.010288 | -0.04385 | 0.0014613 | -0.0075532 | 0.026325 | -0.043124 | -0.0044669 | -0.013851 | 0.0023926 | 0.10529 | 0.10529 | 0.15106 | 0.091553 | 0.091553 | 0.041199 | -0.07782 | 0.10071 | 0.28381 | 0.082397 | 5.8868 | 5.8502 | -0.004578 | -0.091553 | 115.6403 | 115.5212 | -5.8731 | 115.7043 | 115.6906 | 0.16937 | -5.8594 | 115.5945 | 115.5075 | -0.07782 | 115.6998 | 115.6815 | 0.17395 | -0.11444 | 115.6906 | 115.7043 | 115.7501 | -6.0425 | 121.4859 | 121.4493 | 115.8829 | -6.0562
1453.1562 | 121.6049 | -120.3552 | 1.2314 | 0.0074006 | -0.018801 | 0.012074 | 0.035382 | -0.0083654 | -0.039578 | -0.0002477 | 7.627e-05 | 0.032947 | -0.04526 | -0.0027579 | -0.014919 | 0.004956 | 0.12817 | 0.068665 | 0.1236 | 0.073242 | 0.068665 | 0.041199 | -0.07782 | 0.09613 | 0.13275 | 0.054932 | 1.1307 | 1.1124 | -0.018311 | -0.10529 | 120.3964 | 120.2774 | -1.1627 | 120.4239 | 120.4285 | 0.15106 | -1.1032 | 120.3369 | 120.2499 | -0.10071 | 120.4514 | 120.4102 | 0.16022 | -0.11902 | 120.4239 | 120.4834 | 120.4788 | -1.3092 | 121.4859 | 121.4676 | 120.488 | -1.3367
1454.9531 | 121.6553 | -120.282 | 1.268 | -0.015487 | -0.020296 | 0.016987 | 0.033887 | -0.0083654 | -0.041073 | -0.0015295 | 0.0077058 | 0.029316 | -0.045047 | -0.0036123 | -0.014492 | 0.0026062 | 0.054932 | 0.018311 | 0.086975 | 0.054932 | 0.10986 | 0.041199 | -0.091553 | 0.059509 | 0.12817 | 0.045776 | 1.1993 | 1.1719 | -0.032043 | -0.086975 | 120.3232 | 120.1904 | -1.1581 | 120.3003 | 120.3369 | 0.14649 | -1.2131 | 120.2499 | 120.195 | -0.068664 | 120.3415 | 120.3278 | 0.13275 | -0.09613 | 120.3918 | 120.3369 | 120.369 | -1.3596 | 121.4813 | 121.4539 | 120.4102 | -1.355
1456.6562 | 121.7194 | -120.2362 | 1.3 | 0.0074006 | -0.015169 | 0.011433 | 0.033887 | -0.008579 | -0.031674 | 0.0035975 | -0.0075532 | 0.035297 | -0.042483 | -0.0033987 | -0.0082972 | 0.0019654 | 0.082397 | -0.027466 | 0.036621 | 0.041199 | 0.13275 | 0.009155 | -0.1236 | 0 | 0.036621 | -0.050354 | 1.2863 | 1.2497 | -0.027466 | -0.11444 | 120.2454 | 120.1126 | -1.1673 | 120.2087 | 120.2774 | 0.16479 | -1.2177 | 120.2087 | 120.1218 | -0.013733 | 120.2362 | 120.1859 | 0.064087 | -0.050354 | 120.369 | 120.3186 | 120.2728 | -1.4236 | 121.5225 | 121.4859 | 120.2728 | -1.4145
1458.4375 | 121.7834 | -120.8176 | 0.73242 | -0.0078584 | -0.017092 | 0.011433 | 0.035809 | -0.010288 | -0.034237 | 0.0023157 | 7.627e-05 | 0.024616 | -0.034579 | -0.0016897 | -0.0095788 | 0.00068362 | 0.036621 | -0.068665 | -0.004578 | 0.009155 | 0.13275 | 0.013733 | -0.11444 | 0.018311 | 0.032043 | 0.032043 | 0.72327 | 0.69122 | -0.009155 | -0.073242 | 120.8313 | 120.7031 | -0.59967 | 120.7489 | 120.8267 | 0.1236 | -0.6958 | 120.8084 | 120.7443 | -0.009155 | 120.8359 | 120.8496 | 0.10529 | -0.041199 | 120.9503 | 120.8542 | 120.813 | -0.84686 | 121.5408 | 121.5088 | 120.8496 | -0.80566
1460.1719 | 121.7834 | -120.9412 | 0.61798 | -0.00022891 | -0.016024 | 0.013142 | 0.033673 | -0.012211 | -0.034451 | 0.0018885 | -0.0075532 | 0.019702 | -0.030734 | -0.0036123 | -0.0093652 | 0.0017518 | 0.036621 | -0.032043 | 0.018311 | 0.041199 | 0.1236 | 0.009155 | -0.1236 | 0.027466 | 0.11444 | 0.073242 | 0.62256 | 0.59052 | -0.009155 | -0.068665 | 120.9503 | 120.8176 | -0.49439 | 120.9091 | 120.9824 | 0.16479 | -0.58136 | 120.932 | 120.8725 | 0.004578 | 120.9686 | 121.0144 | 0.14191 | -0.027466 | 121.0648 | 120.9778 | 120.9595 | -0.74158 | 121.5637 | 121.5317 | 121.0556 | -0.68665
1461.9531 | 121.669 | -121.0831 | 0.58594 | -0.00022891 | -0.020724 | 0.013142 | 0.036664 | -0.012211 | -0.040219 | -0.0006751 | 7.627e-05 | 0.013935 | -0.032656 | -0.0051077 | -0.011288 | 0.0036744 | 0.050354 | 0.036621 | 0.091553 | 0.036621 | 0.086975 | 0.045776 | -0.091553 | 0.068665 | 0.11902 | 0.17853 | 0.50354 | 0.48065 | 0.027466 | -0.050354 | 121.1288 | 120.9915 | -0.49896 | 121.1197 | 121.1197 | 0.12817 | -0.53558 | 121.1105 | 121.0327 | -0.082397 | 121.1517 | 121.2616 | 0.22888 | -0.10529 | 121.17 | 121.1334 | 121.1746 | -0.67749 | 121.5866 | 121.5637 | 121.2021 | -0.63629
1463.7188 | 121.7514 | -121.2433 | 0.3891 | -0.00022891 | -0.019869 | 0.011647 | 0.032392 | -0.010929 | -0.039364 | 0.0010339 | -0.0075532 | 0.01308 | -0.027316 | -0.0040395 | -0.0095788 | 4.2822e-05 | 0.1236 | 0.064087 | 0.14191 | 0.091553 | 0.064087 | 0.050354 | -0.082397 | 0.13275 | 0.17395 | 0.24261 | 0.32959 | 0.31586 | 0.050354 | -0.018311 | 121.2936 | 121.1609 | -0.32501 | 121.3074 | 121.3348 | 0.17395 | -0.2655 | 121.2936 | 121.225 | -0.059509 | 121.376 | 121.4859 | 0.26093 | -0.073242 | 121.3074 | 121.3669 | 121.3852 | -0.4715 | 121.5729 | 121.5591 | 121.4172 | -0.40741
1465.4375 | 121.7331 | -121.2753 | 0.40283 | -0.00022891 | -0.017946 | 0.012928 | 0.038159 | -0.015201 | -0.039792 | -0.0015295 | -0.0075532 | 0.010517 | -0.024966 | -0.0044669 | -0.011715 | 0.00068362 | 0.032043 | 0.004578 | 0.064087 | 0.050354 | 0.11444 | 0.036621 | -0.073242 | 0.059509 | 0.12817 | 0.23346 | 0.33875 | 0.31128 | 0.032043 | -0.009155 | 121.312 | 121.2021 | -0.28839 | 121.2799 | 121.3257 | 0.1236 | -0.37079 | 121.3074 | 121.2662 | -0.064087 | 121.3348 | 121.5088 | 0.24261 | -0.091553 | 121.3898 | 121.3074 | 121.3394 | -0.47607 | 121.6141 | 121.5866 | 121.4035 | -0.41199
1467.2031 | 121.701 | -121.2845 | 0.39825 | -0.0078584 | -0.016451 | 0.01421 | 0.036237 | -0.0094336 | -0.037655 | 0.0012477 | -0.0075532 | 0.013294 | -0.02582 | -0.0063895 | -0.0080834 | -0.0031616 | 0.086975 | 0.027466 | 0.082397 | 0.07782 | 0.09613 | 0.018311 | -0.11902 | 0.036621 | 0.086975 | 0.17853 | 0.36163 | 0.33417 | 0.022888 | -0.054932 | 121.3028 | 121.1655 | -0.30212 | 121.312 | 121.3623 | 0.19684 | -0.31128 | 121.3074 | 121.2296 | -0.036621 | 121.3211 | 121.463 | 0.23346 | -0.064087 | 121.3806 | 121.3715 | 121.3669 | -0.51727 | 121.6461 | 121.6187 | 121.3715 | -0.45319
1468.9844 | 121.7697 | -121.2433 | 0.41657 | -0.00022891 | -0.019869 | 0.011647 | 0.034101 | -0.010288 | -0.040432 | 0.0003931 | 7.627e-05 | 0.011371 | -0.028811 | -0.0033987 | -0.010861 | -0.002948 | 0.064087 | 0.013733 | 0.086975 | 0.045776 | 0.09613 | 0.027466 | -0.091553 | 0.091553 | 0.1236 | 0.28381 | 0.34332 | 0.32501 | 0.050354 | -0.018311 | 121.2708 | 121.1517 | -0.32044 | 121.257 | 121.2891 | 0.13733 | -0.35248 | 121.2936 | 121.225 | -0.073242 | 121.3348 | 121.5271 | 0.30212 | -0.091553 | 121.3394 | 121.3074 | 121.3303 | -0.50812 | 121.5866 | 121.5683 | 121.3669 | -0.43488
1470.7656 | 121.7377 | -121.2753 | 0.43488 | -0.00022891 | -0.016878 | 0.012928 | 0.037091 | -0.0070836 | -0.038296 | 0.0001795 | 0.0077058 | 0.016712 | -0.029238 | -0.0023305 | -0.0074426 | -0.0059386 | 0.036621 | -0.041199 | 0.018311 | 0.004578 | 0.1236 | 0.004578 | -0.10986 | 0.027466 | 0.064087 | 0.19684 | 0.39368 | 0.37537 | 0.018311 | -0.041199 | 121.2799 | 121.1655 | -0.31128 | 121.2341 | 121.2799 | 0.11444 | -0.39825 | 121.2936 | 121.2341 | -0.041198 | 121.3028 | 121.4722 | 0.23804 | -0.059509 | 121.3989 | 121.312 | 121.2936 | -0.54474 | 121.669 | 121.6507 | 121.3394 | -0.47607
1472.4844 | 121.7239 | -121.2799 | 0.46234 | 0.0074006 | -0.020296 | 0.013997 | 0.035382 | -0.0072974 | -0.037014 | -0.0011023 | 0.015335 | 0.010303 | -0.02817 | -0.0021169 | -0.0074426 | -0.001239 | 0.091553 | 0.045776 | 0.091553 | 0.059509 | 0.082397 | 0.045776 | -0.07782 | 0.09613 | 0.11444 | 0.29297 | 0.37994 | 0.3479 | 0.064087 | 0.004578 | 121.3257 | 121.2021 | -0.37994 | 121.3257 | 121.3394 | 0.13733 | -0.37079 | 121.344 | 121.2845 | -0.082397 | 121.376 | 121.5729 | 0.28839 | -0.11444 | 121.3623 | 121.3715 | 121.3715 | -0.54016 | 121.6599 | 121.6278 | 121.3943 | -0.45776
1474.2656 | 121.875 | -121.2387 | 0.42114 | -0.00022891 | -0.01047 | 0.011647 | 0.03346 | -0.010929 | -0.031247 | 0.0003931 | 0.0077058 | 0.01543 | -0.026461 | -0.0025443 | -0.0042382 | -0.0033752 | 0.068665 | -0.027466 | 0.022888 | 0.045776 | 0.11444 | 0.013733 | -0.10986 | 0.036621 | 0.11902 | 0.21057 | 0.41199 | 0.38452 | 0.054932 | -0.013733 | 121.2524 | 121.1288 | -0.3067 | 121.2112 | 121.2845 | 0.15564 | -0.35248 | 121.2936 | 121.225 | -0.009156 | 121.2753 | 121.4493 | 0.2243 | -0.036622 | 121.3531 | 121.3074 | 121.2616 | -0.53101 | 121.6507 | 121.6232 | 121.3577 | -0.43488
1476 | 121.8887 | -121.2799 | 0.40283 | -0.0078584 | -0.014742 | 0.012928 | 0.032605 | -0.01157 | -0.034024 | 0.0038111 | -0.0075532 | 0.016498 | -0.024325 | -0.0036123 | -0.0042382 | -0.002948 | 0.032043 | -0.086975 | -0.022888 | 0 | 0.11444 | 0.018311 | -0.12817 | 0.013733 | 0.022888 | 0.16022 | 0.40741 | 0.38452 | 0.054932 | 0 | 121.2982 | 121.1517 | -0.28839 | 121.1929 | 121.2799 | 0.12817 | -0.37079 | 121.3348 | 121.2799 | 0.004578 | 121.2936 | 121.4401 | 0.16022 | -0.018311 | 121.3943 | 121.3119 | 121.257 | -0.53101 | 121.6873 | 121.6644 | 121.3028 | -0.40283
1477.7656 | 121.7651 | -121.344 | 0.46234 | -0.0078584 | -0.022219 | 0.014637 | 0.034314 | -0.01157 | -0.040646 | 0.0001795 | 7.627e-05 | 0.010303 | -0.026034 | -0.0048941 | -0.0085108 | 0.00089722 | 0.073242 | 0.041199 | 0.086975 | 0.045776 | 0.07782 | 0.041199 | -0.07782 | 0.073242 | 0.14191 | 0.26093 | 0.35706 | 0.35248 | 0.068665 | -0.004578 | 121.3852 | 121.2662 | -0.38452 | 121.3852 | 121.3898 | 0.1236 | -0.3891 | 121.4127 | 121.3394 | -0.10529 | 121.4172 | 121.6049 | 0.2655 | -0.10986 | 121.4218 | 121.4172 | 121.431 | -0.54016 | 121.701 | 121.6965 | 121.4859 | -0.46692
1479.4844 | 121.907 | -121.2936 | 0.38452 | -0.00022891 | -0.019655 | 0.013783 | 0.035169 | -0.0094336 | -0.03381 | 0.0010339 | 0.0077058 | 0.012867 | -0.023684 | -0.0029715 | -0.0070154 | -0.00017078 | 0.14191 | 0.050354 | 0.1236 | 0.086975 | 0.086975 | 0.054932 | -0.073242 | 0.11902 | 0.18768 | 0.30212 | 0.33875 | 0.33417 | 0.07782 | 0.013733 | 121.3486 | 121.2204 | -0.29755 | 121.344 | 121.3806 | 0.16022 | -0.24261 | 121.3715 | 121.3074 | -0.045776 | 121.4127 | 121.5958 | 0.28839 | -0.050354 | 121.3806 | 121.4355 | 121.4172 | -0.45776 | 121.6324 | 121.6278 | 121.4813 | -0.37079
1481.2656 | 121.7834 | -121.3257 | 0.42572 | -0.0078584 | -0.016238 | 0.014851 | 0.037518 | -0.010502 | -0.03616 | -0.0017431 | 0.0077058 | 0.011585 | -0.024966 | -0.0021169 | -0.0093652 | 4.2822e-05 | 0.032043 | -0.004578 | 0.027466 | 0.018311 | 0.10986 | -0.009155 | -0.10986 | 0.013733 | 0.13733 | 0.19226 | 0.39368 | 0.37079 | 0.050354 | -0.013733 | 121.3165 | 121.2158 | -0.31586 | 121.3211 | 121.344 | 0.12817 | -0.39368 | 121.376 | 121.312 | -0.032043 | 121.3394 | 121.5179 | 0.20599 | -0.054931 | 121.4355 | 121.3577 | 121.3531 | -0.53558 | 121.7194 | 121.6965 | 121.463 | -0.43945
1482.9844 | 121.9208 | -121.3165 | 0.38452 | -0.00022891 | -0.019015 | 0.010151 | 0.03346 | -0.00922 | -0.037014 | 0.0008203 | -0.0075532 | 0.012012 | -0.025393 | -0.0027579 | -0.0042382 | -0.00081178 | 0.11444 | 0 | 0.09613 | 0.091553 | 0.09613 | 0.050354 | -0.07782 | 0.10986 | 0.18768 | 0.29755 | 0.35706 | 0.32501 | 0.10529 | 0.018311 | 121.3669 | 121.2387 | -0.28839 | 121.3165 | 121.4081 | 0.16937 | -0.27008 | 121.4218 | 121.3348 | -0.027465 | 121.4264 | 121.6141 | 0.27923 | -0.059509 | 121.4127 | 121.431 | 121.4127 | -0.46234 | 121.6736 | 121.6415 | 121.5042 | -0.36621
1484.7656 | 121.8521 | -121.0327 | 0.76446 | -0.0078584 | -0.016451 | 0.016774 | 0.035169 | -0.0096472 | -0.040005 | 0.0012477 | 7.627e-05 | 0.015644 | -0.031161 | -0.0066031 | -0.012356 | 4.2822e-05 | 0.064087 | -0.009155 | 0.07782 | 0.050354 | 0.09613 | 0.054932 | -0.082397 | 0.068665 | 0.16937 | 0.20599 | 0.70038 | 0.6958 | 0.054932 | -0.013733 | 121.0876 | 120.9503 | -0.66833 | 121.0236 | 121.0831 | 0.13275 | -0.70038 | 121.0876 | 121.019 | -0.064087 | 121.1014 | 121.2387 | 0.21973 | -0.068664 | 121.1288 | 121.0968 | 121.1105 | -0.84686 | 121.7331 | 121.7285 | 121.2021 | -0.7782
1486.5625 | 121.8246 | -121.0236 | 0.79193 | -0.00022891 | -0.018587 | 0.012928 | 0.03346 | -0.011356 | -0.039792 | -0.0034521 | -0.0075532 | 0.017139 | -0.032443 | -0.0046805 | -0.010861 | -0.00059818 | 0.07782 | -0.004578 | 0.068665 | 0.041199 | 0.086975 | 0.036621 | -0.082397 | 0.054932 | 0.16937 | 0.16479 | 0.71411 | 0.70496 | 0.068665 | -0.009155 | 121.0602 | 120.9412 | -0.70496 | 121.019 | 121.0648 | 0.1236 | -0.71411 | 121.0922 | 121.0144 | -0.07782 | 121.0785 | 121.1884 | 0.17395 | -0.086975 | 121.1105 | 121.1014 | 121.0922 | -0.87433 | 121.7377 | 121.7285 | 121.1929 | -0.80109
1488.2969 | 121.8292 | -120.9183 | 0.88348 | -0.0078584 | -0.018374 | 0.014637 | 0.035596 | -0.010929 | -0.037442 | 0.0014613 | -0.015182 | 0.018848 | -0.030307 | -0.0061757 | -0.0095788 | 0.0013244 | 0.036621 | -0.036621 | 0.018311 | 0.004578 | 0.1236 | 0.009155 | -0.12817 | -0.013733 | 0.13275 | 0.082397 | 0.85602 | 0.84686 | 0.013733 | -0.050354 | 120.9274 | 120.7901 | -0.75989 | 120.8817 | 120.9229 | 0.13275 | -0.84686 | 120.932 | 120.8679 | -0.027466 | 120.9045 | 121.0007 | 0.13275 | -0.036621 | 121.0419 | 120.9549 | 120.9366 | -1.0117 | 121.7743 | 121.7651 | 121.051 | -0.93384
1490.0781 | 121.9666 | -120.7993 | 0.97046 | 0.0074006 | -0.01816 | 0.011433 | 0.035596 | -0.00922 | -0.03381 | 0.0046655 | -0.015182 | 0.018848 | -0.034152 | -0.0048941 | -0.0068018 | 0.00047002 | 0.10071 | 0.013733 | 0.082397 | 0.059509 | 0.091553 | 0.045776 | -0.091553 | 0.10529 | 0.20142 | 0.17853 | 0.90179 | 0.87891 | 0.068665 | 0.004578 | 120.845 | 120.7077 | -0.87891 | 120.813 | 120.8588 | 0.15106 | -0.86975 | 120.8679 | 120.8038 | -0.068665 | 120.9045 | 120.9778 | 0.17395 | -0.091553 | 120.8908 | 120.9 | 120.8817 | -1.062 | 121.701 | 121.6782 | 121.0007 | -0.96588
1491.8594 | 121.994 | -120.7535 | 0.99792 | -0.0078584 | -0.017092 | 0.011647 | 0.035809 | -0.0098608 | -0.034878 | 0.0021021 | 0.0077058 | 0.019489 | -0.029238 | -0.0016897 | -0.0091516 | 0.0011108 | 0.054932 | -0.059509 | -0.018311 | 0 | 0.13275 | 0.018311 | -0.10529 | 0.018311 | 0.11444 | 0.09613 | 0.98419 | 0.94299 | 0.045776 | -0.018311 | 120.7718 | 120.6482 | -0.86517 | 120.694 | 120.7535 | 0.10529 | -0.94299 | 120.7993 | 120.7352 | -0.013733 | 120.7718 | 120.8496 | 0.11444 | -0.054932 | 120.8862 | 120.8084 | 120.7352 | -1.1032 | 121.7377 | 121.6965 | 120.8679 | -1.0162
1493.6406 | 121.907 | -120.7123 | 1.0941 | -0.00022891 | -0.017946 | 0.014851 | 0.033246 | -0.012211 | -0.043423 | -0.0015295 | -0.0075532 | 0.014576 | -0.028384 | -0.0055349 | -0.01321 | 0.0015382 | 0.11902 | 0.10071 | 0.13733 | 0.082397 | 0.086975 | 0.041199 | -0.082397 | 0.13275 | 0.27008 | 0.24719 | 1.0117 | 1.0208 | 0.07782 | 0.018311 | 120.7535 | 120.6299 | -1.0071 | 120.813 | 120.7947 | 0.16479 | -0.97504 | 120.7901 | 120.7306 | -0.082397 | 120.845 | 120.9595 | 0.22888 | -0.073242 | 120.7993 | 120.8313 | 120.8496 | -1.1765 | 121.7239 | 121.7331 | 120.9824 | -1.0757
1495.4219 | 121.9666 | -120.6985 | 1.0574 | -0.0078584 | -0.017519 | 0.013356 | 0.033887 | -0.010502 | -0.034451 | 0.0008203 | 7.627e-05 | 0.014789 | -0.029452 | -0.0031851 | -0.0068018 | 0.00047002 | 0.12817 | 0.068665 | 0.11444 | 0.10529 | 0.073242 | 0.045776 | -0.082397 | 0.11444 | 0.20599 | 0.21515 | 1.0117 | 0.98419 | 0.09613 | -0.004578 | 120.7443 | 120.6162 | -0.98419 | 120.7672 | 120.8038 | 0.18768 | -0.92926 | 120.7947 | 120.694 | -0.045776 | 120.813 | 120.9137 | 0.21973 | -0.073242 | 120.7718 | 120.8267 | 120.813 | -1.1398 | 121.7102 | 121.6827 | 120.9045 | -1.062
1497.1875 | 121.9528 | -120.6757 | 1.1169 | 0.0074006 | -0.016665 | 0.010151 | 0.035596 | -0.0096472 | -0.037014 | 0.0027429 | 7.627e-05 | 0.016925 | -0.032229 | -0.0038259 | -0.010433 | 0.00089722 | 0.14648 | 0.068665 | 0.12817 | 0.091553 | 0.07782 | 0.045776 | -0.082397 | 0.10986 | 0.23346 | 0.20599 | 1.0574 | 1.0529 | 0.073242 | -0.004578 | 120.7214 | 120.5933 | -1.0391 | 120.7443 | 120.7672 | 0.17395 | -0.97046 | 120.7489 | 120.6711 | -0.059509 | 120.7855 | 120.8817 | 0.21057 | -0.064087 | 120.7535 | 120.8221 | 120.8038 | -1.1993 | 121.7331 | 121.7285 | 120.9091 | -1.1215
1498.9688 | 121.8979 | -120.6024 | 1.2543 | -0.00022891 | -0.01581 | 0.013783 | 0.038587 | -0.0098608 | -0.04086 | 0.0001795 | 7.627e-05 | 0.012226 | -0.03052 | -0.0033987 | -0.014492 | 0.00089722 | 0.1236 | 0.10529 | 0.15106 | 0.086975 | 0.082397 | 0.036621 | -0.064087 | 0.11444 | 0.27008 | 0.21973 | 1.1719 | 1.1444 | 0.07782 | 0.018311 | 120.639 | 120.5383 | -1.1719 | 120.7077 | 120.6894 | 0.15106 | -1.1307 | 120.6802 | 120.6207 | -0.082397 | 120.7169 | 120.8221 | 0.20142 | -0.10986 | 120.6848 | 120.726 | 120.7535 | -1.3184 | 121.7743 | 121.7468 | 120.8725 | -1.236
1500.75 | 121.9894 | -120.4422 | 1.3412 | -0.00022891 | -0.011111 | 0.011647 | 0.037305 | -0.011997 | -0.031247 | 0.0031703 | 0.0077058 | 0.018848 | -0.03052 | -0.0010489 | -0.0087244 | -0.0027344 | 0.10529 | 0.009155 | 0.054932 | 0.045776 | 0.11902 | 0.013733 | -0.091553 | 0.059509 | 0.15564 | 0.10071 | 1.3184 | 1.2955 | 0.050354 | -0.041199 | 120.4559 | 120.3506 | -1.2222 | 120.4514 | 120.488 | 0.13733 | -1.236 | 120.4926 | 120.401 | -0.022889 | 120.5017 | 120.5429 | 0.14191 | -0.045777 | 120.5612 | 120.5475 | 120.4971 | -1.4328 | 121.7606 | 121.7377 | 120.5978 | -1.3824
1502.5156 | 122.0352 | -120.4514 | 1.3367 | -0.0078584 | -0.014101 | 0.010365 | 0.036664 | -0.0087926 | -0.033169 | 0.0021021 | 0.0077058 | 0.019275 | -0.028598 | -0.0016897 | -0.0093652 | 0.0015382 | 0.064087 | -0.018311 | 0.036621 | 0.054932 | 0.12817 | 0.013733 | -0.1236 | 0.041199 | 0.15564 | 0.068665 | 1.3412 | 1.3092 | 0.018311 | -0.036621 | 120.4651 | 120.3278 | -1.2085 | 120.433 | 120.5063 | 0.17853 | -1.2726 | 120.4697 | 120.4147 | 0.004578 | 120.4926 | 120.52 | 0.10529 | -0.027466 | 120.5795 | 120.5154 | 120.488 | -1.4603 | 121.7926 | 121.7606 | 120.607 | -1.3733
1504.2344 | 121.9254 | -120.3369 | 1.5335 | -0.0078584 | -0.016024 | 0.016133 | 0.038159 | -0.010288 | -0.037442 | 0.0012477 | -0.015182 | 0.019489 | -0.032443 | -0.0036123 | -0.011501 | 0.0011108 | 0.013733 | -0.054932 | 0.013733 | -0.013733 | 0.14191 | 0.009155 | -0.11902 | -0.009155 | 0.10986 | 0.059509 | 1.5106 | 1.474 | 0.009155 | -0.050354 | 120.3461 | 120.2179 | -1.3916 | 120.282 | 120.3232 | 0.10529 | -1.5198 | 120.3461 | 120.2866 | -0.022888 | 120.3278 | 120.3964 | 0.10986 | -0.059509 | 120.4788 | 120.3506 | 120.3506 | -1.6525 | 121.8475 | 121.8109 | 120.4468 | -1.5839
1506.0156 | 122.0352 | -120.1996 | 1.6296 | -0.015487 | -0.019655 | 0.01421 | 0.032819 | -0.0096472 | -0.038296 | 0.0035975 | 7.627e-05 | 0.020771 | -0.035006 | -0.0038259 | -0.0087244 | 0.00089722 | 0.11444 | 0.064087 | 0.1236 | 0.09613 | 0.086975 | 0.073242 | -0.064087 | 0.11444 | 0.18768 | 0.15106 | 1.5564 | 1.5472 | 0.036621 | -0.027466 | 120.2728 | 120.1355 | -1.5427 | 120.2637 | 120.2957 | 0.16022 | -1.5152 | 120.2362 | 120.1721 | -0.073243 | 120.314 | 120.3506 | 0.17853 | -0.082398 | 120.2866 | 120.314 | 120.3232 | -1.6937 | 121.756 | 121.7468 | 120.3873 | -1.6571
1507.7969 | 121.9757 | -119.957 | 1.8951 | -0.00022891 | -0.020296 | 0.015065 | 0.034955 | -0.010288 | -0.042782 | -0.0015295 | 0.0077058 | 0.016071 | -0.03522 | -0.0051077 | -0.013638 | 0.0028198 | 0.11444 | 0.082397 | 0.12817 | 0.09613 | 0.09613 | 0.045776 | -0.091553 | 0.10986 | 0.2243 | 0.18768 | 1.8356 | 1.8127 | 0.059509 | -0.027466 | 120.0027 | 119.8654 | -1.799 | 120.0394 | 120.0531 | 0.18768 | -1.7807 | 120.0165 | 119.9295 | -0.05951 | 120.0668 | 120.1447 | 0.21515 | -0.082398 | 120.0531 | 120.0714 | 120.0851 | -1.9867 | 121.7926 | 121.7697 | 120.1813 | -1.9226
1509.5156 | 121.9437 | -119.8563 | 2.0279 | -0.015487 | -0.016238 | 0.013783 | 0.039441 | -0.012424 | -0.040219 | 0.0006067 | -0.0075532 | 0.02312 | -0.036929 | -0.0046805 | -0.01321 | 0.0013244 | 0.1236 | 0.10071 | 0.15106 | 0.091553 | 0.091553 | 0.054932 | -0.091553 | 0.10529 | 0.22888 | 0.16022 | 1.9684 | 1.918 | 0.009155 | -0.041199 | 119.9112 | 119.7647 | -1.9363 | 119.957 | 119.9478 | 0.18311 | -1.9043 | 119.8654 | 119.8151 | -0.059509 | 119.9615 | 120.0165 | 0.20142 | -0.10986 | 119.9478 | 119.9799 | 120.0073 | -2.1194 | 121.8246 | 121.7743 | 120.0851 | -2.0691
1511.2969 | 122.0764 | -119.7556 | 2.1103 | -0.0078584 | -0.017733 | 0.012928 | 0.034741 | -0.010715 | -0.035092 | 0.0001795 | -0.0075532 | 0.021839 | -0.036502 | -0.0042531 | -0.010861 | 0.00025642 | 0.091553 | -0.013733 | 0.050354 | 0.041199 | 0.10986 | 0.032043 | -0.10986 | 0.11444 | 0.16022 | 0.086975 | 2.0416 | 2.037 | 0.027466 | -0.045776 | 119.7876 | 119.6457 | -2.0004 | 119.7418 | 119.7968 | 0.15106 | -2.0187 | 119.783 | 119.7098 | -0.068665 | 119.87 | 119.8425 | 0.13275 | -0.073243 | 119.8654 | 119.8471 | 119.8059 | -2.2202 | 121.7972 | 121.7926 | 119.9158 | -2.1561
1513.0781 | 121.9208 | -119.8563 | 2.0828 | -0.00022891 | -0.015169 | 0.014424 | 0.034528 | -0.0081518 | -0.036587 | -0.0006751 | 7.627e-05 | 0.020557 | -0.037997 | -0.0044669 | -0.011501 | -0.00081178 | 0.09613 | 0.07782 | 0.1236 | 0.086975 | 0.09613 | 0.041199 | -0.09613 | 0.059509 | 0.17395 | 0.086975 | 2.0004 | 1.9867 | 0.022888 | -0.054932 | 119.8975 | 119.7601 | -1.9867 | 119.9341 | 119.9432 | 0.1831 | -1.9867 | 119.8791 | 119.8013 | -0.082398 | 119.9158 | 119.9432 | 0.14191 | -0.096131 | 119.9524 | 119.9524 | 119.9799 | -2.179 | 121.8567 | 121.843 | 120.0302 | -2.1378
1514.8594 | 122.0901 | -119.7601 | 2.0737 | 0.0074006 | -0.014956 | 0.012928 | 0.032178 | -0.014133 | -0.035092 | 0.0035975 | 7.627e-05 | 0.023334 | -0.039279 | -0.0048941 | -0.0082972 | 0.0015382 | 0.07782 | 0.009155 | 0.068665 | 0.045776 | 0.09613 | 0.027466 | -0.09613 | 0.091553 | 0.14191 | 0.10529 | 2.0096 | 2.0096 | 0.050354 | -0.050354 | 119.7876 | 119.664 | -1.9775 | 119.7693 | 119.8059 | 0.14191 | -1.9958 | 119.8105 | 119.7098 | -0.064086 | 119.8517 | 119.8654 | 0.15564 | -0.064086 | 119.8563 | 119.838 | 119.8288 | -2.1698 | 121.7697 | 121.7697 | 119.902 | -2.124
1516.5781 | 121.9986 | -119.6503 | 2.2751 | -0.00022891 | -0.020296 | 0.014424 | 0.040082 | -0.011997 | -0.040219 | -0.0015295 | -0.0075532 | 0.021839 | -0.041201 | -0.0059621 | -0.013424 | 0.0011108 | 0.1236 | 0.11902 | 0.14648 | 0.09613 | 0.082397 | 0.064087 | -0.086975 | 0.13733 | 0.24719 | 0.16937 | 2.1881 | 2.1698 | 0.018311 | -0.054932 | 119.7144 | 119.5633 | -2.1927 | 119.7693 | 119.7464 | 0.1831 | -2.1515 | 119.6686 | 119.5953 | -0.086975 | 119.7876 | 119.8196 | 0.22431 | -0.10528 | 119.7327 | 119.7739 | 119.7968 | -2.3621 | 121.8384 | 121.8201 | 119.8975 | -2.33
1518.375 | 121.9574 | -119.6274 | 2.3346 | -0.0078584 | -0.014315 | 0.013356 | 0.037946 | -0.011143 | -0.036587 | -0.0002477 | -0.0075532 | 0.024402 | -0.037997 | -0.0051077 | -0.011929 | 0.00025642 | 0.07782 | 0.018311 | 0.07782 | 0.045776 | 0.11444 | 0.027466 | -0.1236 | 0.013733 | 0.10529 | 0.018311 | 2.2751 | 2.243 | -0.013733 | -0.082397 | 119.6548 | 119.5038 | -2.2202 | 119.6457 | 119.6732 | 0.16937 | -2.2568 | 119.6136 | 119.545 | -0.05951 | 119.6411 | 119.6457 | 0.10071 | -0.091553 | 119.7418 | 119.7052 | 119.7052 | -2.4582 | 121.9025 | 121.8704 | 119.7327 | -2.417
1520.1562 | 121.9803 | -119.577 | 2.3621 | -0.00022891 | -0.016024 | 0.013997 | 0.038373 | -0.0079382 | -0.036587 | -0.0008887 | 0.015335 | 0.02547 | -0.039492 | -0.0042531 | -0.010861 | 0.0011108 | 0.059509 | 0.013733 | 0.041199 | 0.022888 | 0.12817 | 0.009155 | -0.12817 | 0 | 0.091553 | -0.004578 | 2.3117 | 2.3026 | -0.036621 | -0.091553 | 119.5862 | 119.4489 | -2.2339 | 119.5908 | 119.5999 | 0.15106 | -2.3026 | 119.5404 | 119.4855 | -0.050354 | 119.577 | 119.5724 | 0.086975 | -0.05951 | 119.7052 | 119.6365 | 119.6182 | -2.4902 | 121.8887 | 121.8796 | 119.6686 | -2.4536
1521.875 | 121.9757 | -119.5038 | 2.4857 | -0.00022891 | -0.021578 | 0.014637 | 0.032819 | -0.011356 | -0.038296 | 0.0012477 | 7.627e-05 | 0.022693 | -0.039706 | -0.0029715 | -0.010433 | 0.00089722 | 0.1236 | 0.068665 | 0.13275 | 0.07782 | 0.07782 | 0.054932 | -0.082397 | 0.082397 | 0.14191 | 0.086975 | 2.3666 | 2.3575 | 0.018311 | -0.045776 | 119.5587 | 119.4214 | -2.4078 | 119.5724 | 119.5816 | 0.16022 | -2.3621 | 119.5221 | 119.458 | -0.11902 | 119.5862 | 119.5908 | 0.13275 | -0.12817 | 119.5816 | 119.6274 | 119.6365 | -2.5681 | 121.8704 | 121.8613 | 119.6457 | -2.5314
1523.6562 | 122.1039 | -119.7372 | 2.1835 | -0.00022891 | -0.01581 | 0.013356 | 0.034741 | -0.0098608 | -0.034237 | 0.0021021 | 7.627e-05 | 0.022052 | -0.034579 | -0.00040791 | -0.010006 | 0.00047002 | 0.045776 | -0.082397 | -0.027466 | -0.004578 | 0.1236 | 0.009155 | -0.12817 | 0.004578 | 0.045776 | 0 | 2.1606 | 2.1423 | -0.022888 | -0.064087 | 119.7464 | 119.6091 | -2.0599 | 119.6548 | 119.7327 | 0.1236 | -2.1378 | 119.7144 | 119.6732 | -0.022888 | 119.7418 | 119.7372 | 0.064087 | -0.041199 | 119.8608 | 119.783 | 119.7098 | -2.3117 | 121.8979 | 121.8796 | 119.783 | -2.2476
1525.4531 | 122.0215 | -119.9707 | 2.005 | -0.0078584 | -0.017092 | 0.013569 | 0.032605 | -0.0087926 | -0.041073 | -0.0008887 | -0.0075532 | 0.019489 | -0.036715 | -0.0042531 | -0.013424 | 0.0026062 | 0.059509 | 0.009155 | 0.082397 | 0.050354 | 0.10529 | 0.004578 | -0.091553 | 0.050354 | 0.13733 | 0.086975 | 1.9089 | 1.8951 | 0.009155 | -0.073242 | 119.9753 | 119.8791 | -1.8997 | 119.9799 | 120.0211 | 0.14191 | -1.9455 | 119.9799 | 119.8975 | -0.09613 | 120.0211 | 120.0577 | 0.16022 | -0.10986 | 120.076 | 120.0302 | 120.0531 | -2.0966 | 121.8796 | 121.8658 | 120.108 | -2.0782
1527.1719 | 122.0856 | -120.0073 | 1.9089 | -0.00022891 | -0.014956 | 0.010792 | 0.035596 | -0.007511 | -0.032101 | 0.0027429 | 0.0077058 | 0.026111 | -0.033297 | -0.0029715 | -0.0087244 | -0.001239 | 0.11444 | 0.022888 | 0.050354 | 0.050354 | 0.10071 | 0.013733 | -0.10986 | 0.050354 | 0.1236 | 0.018311 | 1.9089 | 1.8677 | 0.004578 | -0.059509 | 120.0211 | 119.8975 | -1.8082 | 120.0302 | 120.0577 | 0.16022 | -1.7944 | 120.0119 | 119.9478 | 0 | 120.0577 | 120.0256 | 0.07782 | -0.041199 | 120.108 | 120.1218 | 120.0577 | -2.0187 | 121.9162 | 121.875 | 120.1309 | -1.9684
1528.9531 | 122.1313 | -119.9982 | 1.9135 | -0.0078584 | -0.016665 | 0.012715 | 0.032819 | -0.00922 | -0.036587 | 0.0023157 | -0.0075532 | 0.022266 | -0.038638 | -0.0033987 | -0.0053064 | 0.0019654 | 0.064087 | 0.009155 | 0.064087 | 0.050354 | 0.091553 | 0.027466 | -0.086975 | 0.086975 | 0.16937 | 0.082397 | 1.8677 | 1.8448 | 0.036621 | -0.054932 | 120.0256 | 119.9112 | -1.8219 | 120.0073 | 120.0485 | 0.13733 | -1.8494 | 120.0348 | 119.9432 | -0.045776 | 120.0851 | 120.0806 | 0.13733 | -0.068664 | 120.0897 | 120.0623 | 120.0623 | -2.0004 | 121.8658 | 121.843 | 120.1675 | -1.9684
1530.7344 | 122.0123 | -120.0714 | 1.8951 | -0.0078584 | -0.016878 | 0.01186 | 0.036878 | -0.012424 | -0.042782 | -0.0006751 | 7.627e-05 | 0.020557 | -0.036288 | -0.0036123 | -0.016415 | 4.2822e-05 | 0.064087 | 0.013733 | 0.091553 | 0.041199 | 0.091553 | 0.027466 | -0.10071 | 0.059509 | 0.12817 | 0.07782 | 1.7944 | 1.7899 | 0.013733 | -0.073242 | 120.0989 | 119.9707 | -1.8036 | 120.0851 | 120.1126 | 0.14191 | -1.8311 | 120.0851 | 119.9982 | -0.10071 | 120.1309 | 120.1492 | 0.15106 | -0.10529 | 120.163 | 120.1355 | 120.163 | -1.9959 | 121.8658 | 121.8613 | 120.1996 | -1.9684
1532.4688 | 122.1634 | -120.0485 | 1.8539 | -0.00022891 | -0.017092 | 0.01421 | 0.032392 | -0.012638 | -0.036374 | 0.0014613 | 0.0077058 | 0.024616 | -0.03992 | -0.0016897 | -0.0087244 | 0.00047002 | 0.068665 | -0.027466 | 0.027466 | 0.027466 | 0.1236 | 0.009155 | -0.12817 | 0.068665 | 0.091553 | 0.059509 | 1.8219 | 1.7944 | 0.041199 | -0.018311 | 120.0577 | 119.9203 | -1.7303 | 120.0211 | 120.076 | 0.15564 | -1.7853 | 120.0897 | 120.0302 | -0.032044 | 120.1172 | 120.108 | 0.07782 | -0.059509 | 120.1721 | 120.1172 | 120.076 | -1.9821 | 121.8704 | 121.843 | 120.1401 | -1.8723
1534.25 | 122.168 | -120.2133 | 1.7441 | -0.0078584 | -0.01581 | 0.012715 | 0.035596 | -0.011356 | -0.034237 | -0.0004613 | 7.627e-05 | 0.021625 | -0.034365 | -0.0010489 | -0.01022 | 0.0036744 | 0.045776 | -0.059509 | 0.004578 | 0.009155 | 0.12817 | 0 | -0.13733 | 0.018311 | 0.10071 | -0.013733 | 1.7075 | 1.6983 | 0.022888 | -0.054932 | 120.2133 | 120.076 | -1.6159 | 120.1538 | 120.2225 | 0.14648 | -1.6983 | 120.2362 | 120.1584 | -0.036622 | 120.2316 | 120.1996 | 0.041199 | -0.045777 | 120.3415 | 120.2591 | 120.2179 | -1.8814 | 121.9208 | 121.9116 | 120.314 | -1.799
1536.0469 | 122.1863 | -120.163 | 1.7487 | -0.00022891 | -0.016451 | 0.012928 | 0.035382 | -0.01157 | -0.034451 | 0.0031703 | -0.0075532 | 0.022907 | -0.037783 | -0.0016897 | -0.010861 | 0.0034608 | 0.036621 | -0.082397 | -0.018311 | -0.004578 | 0.12817 | -0.009155 | -0.1236 | -0.004578 | 0.036621 | 0.004578 | 1.7899 | 1.7578 | 0.013733 | -0.054932 | 120.1538 | 120.0394 | -1.6205 | 120.0806 | 120.1584 | 0.11902 | -1.712 | 120.1767 | 120.108 | 0.041199 | 120.1584 | 120.1675 | 0.05951 | 0.009155 | 120.2911 | 120.1996 | 120.1447 | -1.8723 | 121.9528 | 121.9208 | 120.1996 | -1.8036
1537.7656 | 122.0581 | -120.0897 | 1.8906 | -0.0078584 | -0.020083 | 0.012928 | 0.036664 | -0.0081518 | -0.04385 | -0.0006751 | 0.0077058 | 0.016925 | -0.033725 | -0.0063895 | -0.016201 | 0.003888 | 0.054932 | 0.027466 | 0.091553 | 0.054932 | 0.10071 | 0.004578 | -0.1236 | 0.050354 | 0.13733 | 0.10986 | 1.8448 | 1.8127 | 0.064087 | -0.013733 | 120.0943 | 119.9661 | -1.7899 | 120.1172 | 120.1447 | 0.17853 | -1.8356 | 120.1538 | 120.076 | -0.045776 | 120.1401 | 120.1996 | 0.1236 | -0.07782 | 120.1904 | 120.1447 | 120.1813 | -2.0142 | 121.9345 | 121.9025 | 120.2271 | -1.9043
1539.5469 | 122.1451 | -120.076 | 1.8906 | -0.00022891 | -0.015169 | 0.01186 | 0.032819 | -0.010502 | -0.032742 | 0.0012477 | 7.627e-05 | 0.02248 | -0.03287 | -0.0046805 | -0.0087244 | 0.0015382 | 0.027466 | -0.09613 | -0.022888 | 0.004578 | 0.10986 | 0.013733 | -0.1236 | -0.009155 | 0.022888 | -0.018311 | 1.8906 | 1.8539 | 0 | -0.050354 | 120.0897 | 119.9524 | -1.7807 | 119.9799 | 120.0806 | 0.12817 | -1.8631 | 120.076 | 120.0256 | 0 | 120.0668 | 120.0577 | 0.032043 | -0.036621 | 120.1859 | 120.1035 | 120.0531 | -2.0142 | 121.9666 | 121.9299 | 120.0989 | -1.9409
1541.2812 | 122.0261 | -120.1859 | 1.8585 | -0.0078584 | -0.020937 | 0.012715 | 0.035596 | -0.011143 | -0.042141 | 0.0033839 | -0.0075532 | 0.018421 | -0.034365 | -0.0029715 | -0.01556 | 0.003247 | 0.064087 | 0.032043 | 0.086975 | 0.041199 | 0.082397 | 0.036621 | -0.07782 | 0.045776 | 0.10986 | 0.091553 | 1.7624 | 1.7578 | 0.041199 | -0.032043 | 120.2225 | 120.108 | -1.7761 | 120.2179 | 120.2271 | 0.11902 | -1.7944 | 120.2271 | 120.1538 | -0.096131 | 120.2316 | 120.2774 | 0.1236 | -0.10071 | 120.2682 | 120.2499 | 120.2728 | -1.9363 | 121.9482 | 121.9437 | 120.2957 | -1.8906
1543.0469 | 122.049 | -120.1492 | 1.8677 | -0.00022891 | -0.021578 | 0.015278 | 0.034528 | -0.010715 | -0.040219 | -0.0023839 | 7.627e-05 | 0.019702 | -0.033297 | -0.0025443 | -0.013851 | 0.0036744 | 0.091553 | 0.032043 | 0.032043 | 0.045776 | 0.07782 | 0.027466 | -0.10529 | 0.041199 | 0.10071 | 0.091553 | 1.7899 | 1.7761 | 0.054932 | -0.032043 | 120.1767 | 120.0439 | -1.7899 | 120.1813 | 120.195 | 0.15106 | -1.7761 | 120.2042 | 120.1172 | -0.07782 | 120.1904 | 120.2408 | 0.1236 | -0.091553 | 120.2271 | 120.2408 | 120.1813 | -1.973 | 121.9391 | 121.9254 | 120.2499 | -1.8997
1544.8125 | 122.0535 | -120.2179 | 1.8585 | -0.00022891 | -0.020296 | 0.013783 | 0.035596 | -0.010502 | -0.037442 | 0.0003931 | 7.627e-05 | 0.019702 | -0.036074 | -0.0033987 | -0.014065 | 0.0019654 | 0.082397 | 0.022888 | 0.068665 | 0.059509 | 0.082397 | 0.027466 | -0.091553 | 0.041199 | 0.10986 | 0.091553 | 1.7578 | 1.7487 | 0.054932 | -0.013733 | 120.2454 | 120.1263 | -1.7761 | 120.2408 | 120.2774 | 0.15106 | -1.7761 | 120.2728 | 120.2042 | -0.10071 | 120.2591 | 120.3094 | 0.10529 | -0.10986 | 120.3003 | 120.3003 | 120.2866 | -1.9501 | 121.9757 | 121.9666 | 120.3278 | -1.8723
1546.5938 | 122.1817 | -120.163 | 1.8127 | 0.01503 | -0.018801 | 0.012501 | 0.034314 | -0.011783 | -0.034237 | -0.0004613 | -0.0075532 | 0.021411 | -0.033297 | -0.0029715 | -0.0095788 | -0.00038438 | 0.14648 | 0.041199 | 0.059509 | 0.07782 | 0.082397 | 0.041199 | -0.082397 | 0.10529 | 0.15564 | 0.11444 | 1.7487 | 1.7212 | 0.045776 | -0.009155 | 120.2042 | 120.0806 | -1.7303 | 120.2042 | 120.2408 | 0.16022 | -1.6663 | 120.2087 | 120.1538 | -0.064087 | 120.2683 | 120.2774 | 0.1236 | -0.091553 | 120.2454 | 120.3094 | 120.2225 | -1.8951 | 121.9116 | 121.8842 | 120.3186 | -1.8219
1548.3125 | 122.1451 | -120.108 | 1.918 | -0.00022891 | -0.019869 | 0.014637 | 0.031751 | -0.010074 | -0.037014 | 0.0016749 | 0.0077058 | 0.01778 | -0.036715 | -0.0029715 | -0.0093652 | 0.0013244 | 0.15106 | 0.082397 | 0.1236 | 0.082397 | 0.07782 | 0.059509 | -0.082397 | 0.11902 | 0.16479 | 0.15106 | 1.8494 | 1.8127 | 0.068665 | -0.022888 | 120.1675 | 120.0256 | -1.8402 | 120.1904 | 120.1904 | 0.16479 | -1.767 | 120.1767 | 120.0851 | -0.068665 | 120.2271 | 120.2591 | 0.17395 | -0.10529 | 120.1859 | 120.2591 | 120.2316 | -2.0004 | 121.9574 | 121.9208 | 120.2728 | -1.9409
1550.0781 | 122.2137 | -119.9982 | 1.9775 | -0.0078584 | -0.01346 | 0.012501 | 0.037732 | -0.013492 | -0.035519 | 0.0008203 | 7.627e-05 | 0.019489 | -0.031161 | -0.0019033 | -0.010433 | 0.00025642 | 0.059509 | -0.082397 | -0.009155 | -0.013733 | 0.11444 | -0.004578 | -0.13275 | 0.013733 | 0.022888 | 0.018311 | 1.9775 | 1.9638 | 0.009155 | -0.041199 | 119.9936 | 119.8654 | -1.8631 | 119.9158 | 119.9844 | 0.11902 | -1.918 | 120.0073 | 119.957 | 0 | 120.0119 | 120.0165 | 0.05951 | -0.013733 | 120.1126 | 120.0577 | 119.989 | -2.1103 | 121.9757 | 121.962 | 120.0211 | -2.0187
1551.8438 | 122.1085 | -119.9615 | 2.0691 | -0.00022891 | -0.020296 | 0.016133 | 0.036023 | -0.010502 | -0.040646 | 0.0016749 | 0.0077058 | 0.014789 | -0.03287 | -0.0033987 | -0.013424 | 0.0036744 | 0.068665 | 0.027466 | -0.004578 | 0.045776 | 0.10071 | 0.036621 | -0.10986 | 0.050354 | 0.091553 | 0.11444 | 1.9913 | 2.0004 | 0.054932 | -0.004578 | 119.9982 | 119.8517 | -1.9684 | 119.989 | 120.0073 | 0.15564 | -2.0004 | 120.0165 | 119.957 | -0.07782 | 120.0119 | 120.076 | 0.11902 | -0.068665 | 120.0623 | 120.0302 | 119.957 | -2.179 | 121.9528 | 121.962 | 120.0531 | -2.0737
1553.6406 | 122.1451 | -120.0302 | 1.9775 | -0.00022891 | -0.01282 | 0.013997 | 0.036664 | -0.00922 | -0.036587 | -3.4096e-05 | 7.627e-05 | 0.020771 | -0.031802 | -0.0038259 | -0.012142 | 0.0015382 | 0.054932 | -0.054932 | -0.068665 | 0 | 0.1236 | -0.018311 | -0.13275 | -0.013733 | 0.045776 | 0.032043 | 1.9638 | 1.9409 | 0.018311 | -0.036621 | 120.0119 | 119.8975 | -1.8539 | 119.9753 | 120.0302 | 0.13275 | -1.9226 | 120.0485 | 119.9936 | -0.013733 | 120.0165 | 120.0623 | 0.068664 | -0.036621 | 120.1538 | 120.0851 | 119.9615 | -2.1103 | 121.994 | 121.9711 | 120.076 | -2.0142
1555.3594 | 122.0947 | -120.0668 | 1.9821 | -0.0078584 | -0.017092 | 0.015919 | 0.035169 | -0.010288 | -0.040005 | -3.4096e-05 | 7.627e-05 | 0.016712 | -0.030947 | -0.0046805 | -0.012997 | 0.00089722 | 0.12817 | 0.091553 | 0.073242 | 0.091553 | 0.07782 | 0.022888 | -0.11444 | 0.09613 | 0.20599 | 0.16022 | 1.9135 | 1.8997 | 0.064087 | 0 | 120.0897 | 119.9524 | -1.9043 | 120.1584 | 120.1584 | 0.20599 | -1.8539 | 120.1309 | 120.0668 | -0.068665 | 120.163 | 120.2271 | 0.16022 | -0.082398 | 120.1447 | 120.195 | 120.1401 | -2.0966 | 121.9803 | 121.9666 | 120.2728 | -1.9821
1557.1562 | 122.2412 | -120.0027 | 2.0004 | 0.0074006 | -0.016665 | 0.013142 | 0.035169 | -0.012211 | -0.031887 | 0.0008203 | -0.0075532 | 0.02013 | -0.029025 | -0.0029715 | -0.011501 | -0.00017078 | 0.073242 | -0.073242 | -0.073242 | 0 | 0.11902 | 0.013733 | -0.11444 | 0.032043 | 0.027466 | 0.032043 | 1.9958 | 1.9775 | 0.041199 | -0.032043 | 120.0165 | 119.8883 | -1.8814 | 119.9295 | 120.0027 | 0.11444 | -1.9272 | 120.0439 | 119.9707 | -0.004577 | 120.0348 | 120.0348 | 0.064086 | -0.022888 | 120.1218 | 120.076 | 119.9295 | -2.1149 | 121.9986 | 121.9803 | 120.0302 | -2.0325
1558.875 | 122.2092 | -120.1035 | 1.8951 | -0.00022891 | -0.013247 | 0.01186 | 0.034101 | -0.010288 | -0.033383 | 0.0021021 | -0.0075532 | 0.019062 | -0.030093 | -0.0027579 | -0.010006 | -0.00017078 | 0.091553 | -0.018311 | -0.022888 | 0.045776 | 0.11444 | -0.009155 | -0.12817 | 0.036621 | 0.10071 | 0.064087 | 1.8906 | 1.886 | 0.045776 | -0.018311 | 120.0943 | 119.9753 | -1.7807 | 120.0851 | 120.1492 | 0.17395 | -1.8036 | 120.1492 | 120.0851 | -0.004578 | 120.1401 | 120.1675 | 0.082398 | -0.009156 | 120.2179 | 120.195 | 120.0806 | -2.0233 | 121.994 | 121.9894 | 120.2042 | -1.9135
1560.6562 | 122.2321 | -119.9341 | 2.0782 | -0.0078584 | -0.014742 | 0.013997 | 0.035382 | -0.0055884 | -0.035946 | 0.0010339 | 7.627e-05 | 0.018421 | -0.029666 | -0.00083531 | -0.012997 | 0.0011108 | 0.018311 | -0.068665 | -0.045776 | 0.004578 | 0.11902 | -0.018311 | -0.14648 | -0.022888 | 0.073242 | 0.041199 | 2.0691 | 2.0416 | 0.045776 | -0.022888 | 119.9158 | 119.7876 | -1.9592 | 119.8654 | 119.9387 | 0.15106 | -2.0599 | 119.9799 | 119.9112 | -0.009155 | 119.9112 | 119.9753 | 0.064087 | -0.036621 | 120.0531 | 119.9524 | 119.8883 | -2.2247 | 122.0032 | 121.9757 | 120.0073 | -2.1011
1562.4375 | 122.0901 | -119.9661 | 2.1149 | -0.00022891 | -0.015169 | 0.015706 | 0.036878 | -0.0094336 | -0.039578 | 0.0014613 | -0.0075532 | 0.016925 | -0.029666 | -0.0023305 | -0.01257 | 0.0015382 | 0.07782 | 0.009155 | 0.009155 | 0.041199 | 0.10529 | 0.004578 | -0.10071 | -0.009155 | 0.11444 | 0.082397 | 2.0828 | 2.0462 | 0.041199 | -0.022888 | 119.9707 | 119.8654 | -2.0096 | 119.9753 | 120.0073 | 0.14191 | -2.037 | 120.0073 | 119.9432 | -0.032043 | 119.957 | 120.0485 | 0.10528 | -0.068664 | 120.0714 | 120.0439 | 119.9753 | -2.2156 | 122.049 | 122.0123 | 120.0806 | -2.1378
1564.1562 | 122.0993 | -120.0211 | 2.0828 | -0.00022891 | -0.016024 | 0.010579 | 0.035169 | -0.010288 | -0.040646 | 0.0016749 | 0.0077058 | 0.01543 | -0.027529 | -0.0019033 | -0.015133 | 0.002179 | 0.11902 | 0.050354 | 0.059509 | 0.064087 | 0.086975 | 0.045776 | -0.07782 | 0.086975 | 0.15564 | 0.16937 | 1.9958 | 1.9913 | 0.11902 | 0.036621 | 120.0668 | 119.9432 | -1.9959 | 120.0714 | 120.0851 | 0.14191 | -1.9638 | 120.1401 | 120.0577 | -0.086975 | 120.108 | 120.1904 | 0.13275 | -0.091553 | 120.108 | 120.1401 | 120.0806 | -2.1606 | 122.0169 | 122.0123 | 120.1767 | -2.0462
1565.9375 | 122.2504 | -119.9661 | 2.0508 | -0.015487 | -0.014956 | 0.012928 | 0.038159 | -0.0081518 | -0.034878 | 0.0008203 | -0.015182 | 0.020343 | -0.026034 | -0.0016897 | -0.011715 | -0.00017078 | 0.045776 | -0.068665 | -0.036621 | 0.022888 | 0.10529 | 0.009155 | -0.14191 | 0.018311 | 0.10986 | 0.091553 | 2.0187 | 2.0233 | 0.07782 | 0.022888 | 119.9753 | 119.8242 | -1.9455 | 119.8975 | 119.989 | 0.16479 | -2.005 | 120.0439 | 119.989 | -0.032043 | 119.9844 | 120.0577 | 0.068665 | -0.027466 | 120.0714 | 120.0119 | 119.9295 | -2.1927 | 121.9849 | 121.9894 | 120.076 | -2.0279
1567.6719 | 122.2504 | -119.6274 | 2.417 | -0.00022891 | -0.016665 | 0.01421 | 0.031751 | -0.011356 | -0.034237 | 0.0016749 | 0.0077058 | 0.021625 | -0.021334 | -0.00019431 | -0.0087244 | 0.0023926 | 0.036621 | -0.10071 | -0.10071 | -0.022888 | 0.10986 | 0 | -0.11444 | -0.009155 | 0.050354 | 0.10529 | 2.417 | 2.3666 | 0.10529 | 0.045776 | 119.6274 | 119.5129 | -2.3071 | 119.5267 | 119.6045 | 0.091553 | -2.3804 | 119.7327 | 119.6732 | 0 | 119.6182 | 119.7327 | 0.05951 | -0.050354 | 119.7372 | 119.664 | 119.5267 | -2.5314 | 122.0444 | 121.994 | 119.6777 | -2.3712
1569.4531 | 122.2275 | -120.4742 | 1.5839 | 0.0074006 | -0.016024 | 0.013997 | 0.035382 | -0.010715 | -0.034665 | 0.0025293 | 7.627e-05 | 0.015644 | -0.030307 | -0.0025443 | -0.010006 | 0.00089722 | 0.082397 | -0.004578 | 0.027466 | 0.045776 | 0.1236 | 0.032043 | -0.10986 | 0.004578 | 0.086975 | 0.041199 | 1.5747 | 1.5747 | 0.054932 | -0.018311 | 120.5063 | 120.3644 | -1.4603 | 120.4697 | 120.52 | 0.15564 | -1.5015 | 120.5292 | 120.4559 | -0.009155 | 120.4788 | 120.5154 | 0.05951 | -0.009155 | 120.5978 | 120.5566 | 120.5017 | -1.6937 | 122.049 | 122.049 | 120.5612 | -1.6022
1571.2344 | 122.1634 | -120.0302 | 2.1103 | -0.00022891 | -0.021792 | 0.012501 | 0.036023 | -0.010929 | -0.041501 | 0.0021021 | -0.0075532 | 0.01543 | -0.036288 | -0.0027579 | -0.012997 | 0.0023926 | 0.09613 | 0.07782 | 0.14648 | 0.064087 | 0.086975 | 0.064087 | -0.082397 | 0.09613 | 0.19684 | 0.13275 | 2.0004 | 1.9958 | 0.082397 | 0 | 120.0943 | 119.9478 | -2.0233 | 120.108 | 120.0943 | 0.14648 | -2.0142 | 120.1126 | 120.0302 | -0.10986 | 120.1263 | 120.163 | 0.13275 | -0.11444 | 120.1172 | 120.1263 | 120.1767 | -2.1927 | 122.0306 | 122.0261 | 120.2271 | -2.1103
1573.0156 | 122.2229 | -120.0302 | 2.0782 | -0.0078584 | -0.02051 | 0.014637 | 0.035169 | -0.011356 | -0.037869 | 0.0016749 | 0.0077058 | 0.013294 | -0.035861 | -0.0021169 | -0.010861 | 0.0013244 | 0.11902 | 0.086975 | 0.15106 | 0.082397 | 0.073242 | 0.064087 | -0.050354 | 0.10529 | 0.22888 | 0.16022 | 1.9913 | 1.973 | 0.059509 | 0.032043 | 120.0943 | 119.9799 | -2.005 | 120.1172 | 120.1126 | 0.13275 | -1.9592 | 120.0897 | 120.0623 | -0.086975 | 120.1355 | 120.1904 | 0.12817 | -0.10529 | 120.1035 | 120.1492 | 120.1813 | -2.1286 | 122.0215 | 122.0032 | 120.2591 | -2.0462
1574.7188 | 122.1771 | -119.9524 | 2.1286 | -0.0078584 | -0.017946 | 0.015919 | 0.037091 | -0.01157 | -0.04086 | -0.0028113 | 0.0077058 | 0.01073 | -0.035434 | -0.0051077 | -0.013424 | 0.00047002 | 0.10986 | 0.10529 | 0.14648 | 0.09613 | 0.082397 | 0.059509 | -0.07782 | 0.1236 | 0.31128 | 0.21057 | 2.0554 | 2.0462 | 0.086975 | 0.018311 | 120.0119 | 119.8746 | -2.0462 | 120.0577 | 120.0485 | 0.17395 | -2.0187 | 120.0394 | 119.9707 | -0.073242 | 120.076 | 120.163 | 0.19226 | -0.082397 | 120.0348 | 120.0623 | 120.0989 | -2.2064 | 122.0078 | 121.9986 | 120.2637 | -2.1103
1576.5 | 122.1725 | -119.8608 | 2.2614 | -0.0078584 | -0.019015 | 0.013142 | 0.03111 | -0.0098608 | -0.03851 | 0.0014613 | 0.0077058 | 0.012867 | -0.038638 | -0.0029715 | -0.012997 | -0.0016662 | 0.13275 | 0.073242 | 0.14191 | 0.073242 | 0.082397 | 0.050354 | -0.073242 | 0.10071 | 0.23346 | 0.14648 | 2.179 | 2.1606 | 0.091553 | 0.018311 | 119.9112 | 119.7876 | -2.179 | 119.9341 | 119.9341 | 0.14648 | -2.1286 | 119.9524 | 119.8792 | -0.082398 | 119.9615 | 120.0073 | 0.12817 | -0.10071 | 119.9432 | 119.9936 | 120.0027 | -2.3346 | 122.0398 | 122.0215 | 120.0943 | -2.243
1578.2812 | 122.2366 | -119.9982 | 2.0828 | 0.0074006 | -0.011324 | 0.011219 | 0.038587 | -0.0096472 | -0.028683 | 0.0018885 | 7.627e-05 | 0.014789 | -0.031588 | -0.00040791 | -0.0087244 | -0.0018798 | 0.082397 | -0.068665 | 0.013733 | 0.009155 | 0.11902 | 0.027466 | -0.10986 | 0 | 0.1236 | 0.027466 | 2.0599 | 2.0462 | 0.068665 | 0.013733 | 120.0256 | 119.8883 | -1.9638 | 119.9295 | 120.0073 | 0.11902 | -2.0004 | 120.0668 | 120.0119 | -0.022888 | 119.9982 | 120.0256 | 0.013733 | -0.036621 | 120.1172 | 120.0806 | 120.0119 | -2.1927 | 122.0581 | 122.0444 | 120.1218 | -2.0691
1580.0469 | 122.1497 | -120.0531 | 2.0691 | -0.0078584 | -0.020937 | 0.015706 | 0.033032 | -0.013065 | -0.042782 | -0.0008887 | 0.0077058 | 0.010517 | -0.032656 | -0.00062151 | -0.014065 | 0.0028198 | 0.073242 | 0.032043 | 0.073242 | 0.059509 | 0.10071 | 0.073242 | -0.09613 | 0.045776 | 0.21057 | 0.1236 | 1.9913 | 2.0004 | 0.10071 | 0.022888 | 120.1263 | 119.957 | -1.9684 | 120.0851 | 120.1126 | 0.15564 | -1.9958 | 120.1538 | 120.076 | -0.07782 | 120.0989 | 120.1767 | 0.10071 | -0.068665 | 120.1538 | 120.1263 | 120.1263 | -2.1652 | 122.0444 | 122.0535 | 120.2637 | -2.0462
1581.7656 | 122.2458 | -120.0394 | 2.0737 | -0.00022891 | -0.014101 | 0.013997 | 0.035382 | -0.01157 | -0.03381 | 0.0003931 | 0.0077058 | 0.014362 | -0.032443 | -0.00062151 | -0.0082972 | -0.00081178 | 0.064087 | -0.064087 | 0.004578 | 0.018311 | 0.12817 | 0.045776 | -0.11444 | -0.013733 | 0.14191 | 0.027466 | 2.0279 | 2.0279 | 0.073242 | 0.004578 | 120.0851 | 119.9249 | -1.9455 | 119.9753 | 120.0577 | 0.13275 | -2.0096 | 120.1126 | 120.0439 | -0.045776 | 120.0256 | 120.0668 | 0.022888 | -0.045776 | 120.1675 | 120.1035 | 120.0439 | -2.1881 | 122.0673 | 122.0673 | 120.1813 | -2.0691
1583.5469 | 122.2137 | -120.2637 | 1.8951 | -0.0078584 | -0.019015 | 0.01421 | 0.037946 | -0.012211 | -0.042355 | -0.0028113 | -0.0075532 | 0.0088076 | -0.031588 | -0.0053213 | -0.016415 | 0.0026062 | 0.045776 | 0 | 0.091553 | 0.050354 | 0.086975 | 0.041199 | -0.09613 | 0.045776 | 0.22888 | 0.17395 | 1.8356 | 1.7944 | 0.091553 | 0.027466 | 120.3049 | 120.1675 | -1.8082 | 120.2637 | 120.314 | 0.14648 | -1.8494 | 120.3552 | 120.2911 | -0.05951 | 120.3094 | 120.4376 | 0.14648 | -0.10071 | 120.3506 | 120.3094 | 120.3552 | -1.9913 | 122.0993 | 122.0581 | 120.4926 | -1.8677
1585.3281 | 122.2641 | -120.0394 | 2.0782 | -0.00022891 | -0.01346 | 0.010792 | 0.035809 | -0.012211 | -0.031247 | 0.0027429 | 7.627e-05 | 0.01308 | -0.030947 | 0.00087369 | -0.011501 | -0.00017078 | 0.11444 | 0.004578 | 0.054932 | 0.041199 | 0.12817 | 0.022888 | -0.09613 | 0.045776 | 0.21515 | 0.07782 | 2.0325 | 2.037 | 0.10529 | 0.022888 | 120.0623 | 119.9432 | -1.9501 | 120.0439 | 120.0806 | 0.13733 | -1.9638 | 120.1447 | 120.0623 | -0.045776 | 120.0851 | 120.1172 | 0.054932 | -0.041199 | 120.1675 | 120.1538 | 120.0943 | -2.1744 | 122.0718 | 122.0764 | 120.2545 | -2.0554
1587.0469 | 122.2366 | -120.1126 | 2.005 | -0.0078584 | -0.015383 | 0.012715 | 0.037091 | -0.010715 | -0.038083 | -0.0002477 | 7.627e-05 | 0.013935 | -0.029879 | -0.0031851 | -0.013424 | 0.0015382 | 0.018311 | -0.036621 | -0.004578 | 0.004578 | 0.1236 | 0.013733 | -0.11902 | -0.018311 | 0.19684 | 0.064087 | 1.9958 | 1.9867 | 0.082397 | 0.027466 | 120.1263 | 119.9936 | -1.8814 | 120.076 | 120.1172 | 0.1236 | -1.9867 | 120.195 | 120.1401 | -0.009155 | 120.0943 | 120.1767 | 0.036621 | -0.018311 | 120.2362 | 120.1309 | 120.108 | -2.124 | 122.1085 | 122.0993 | 120.3094 | -1.9775
1588.8125 | 122.2641 | -120.5521 | 1.5472 | -0.00022891 | -0.016451 | 0.011219 | 0.035809 | -0.0098608 | -0.035092 | 0.0016749 | 7.627e-05 | 0.020557 | -0.036502 | 0.0060007 | -0.017056 | -0.0025208 | 0.054932 | -0.027466 | 0.018311 | 0.022888 | 0.13733 | 0.032043 | -0.13733 | 0.004578 | 0.38452 | 0.054932 | 1.5335 | 1.5198 | 0.31128 | 0.23346 | 120.5841 | 120.4147 | -1.4099 | 120.5246 | 120.575 | 0.16022 | -1.4923 | 120.8633 | 120.7855 | -0.013733 | 120.5566 | 120.607 | -0.17853 | -0.027466 | 120.6894 | 120.607 | 120.5704 | -1.6846 | 122.0856 | 122.0718 | 120.9366 | -1.3138
1590.5312 | 122.3282 | -121.376 | 0.737 | -0.00022891 | -0.015169 | 0.013356 | 0.03645 | -0.011143 | -0.035946 | 0.0021021 | 7.627e-05 | 0.024402 | -0.042697 | 0.014973 | -0.025173 | -0.002948 | 0.045776 | -0.009155 | 0.032043 | 0.050354 | 0.13275 | 0.013733 | -0.10529 | 0.045776 | 0.65918 | 0.12817 | 0.71411 | 0.6958 | 0.51727 | 0.44403 | 121.3898 | 121.2708 | -0.60425 | 121.3669 | 121.4264 | 0.15564 | -0.69122 | 121.8933 | 121.8201 | -0.022889 | 121.4218 | 121.5042 | -0.31586 | -0.041199 | 121.5088 | 121.4218 | 121.4081 | -0.84229 | 122.0901 | 122.0718 | 122.0352 | -0.29297
1592.25 | 122.3282 | -121.3989 | 0.70496 | 0.0074006 | -0.012606 | 0.011006 | 0.033673 | -0.0094336 | -0.035519 | 0.0025293 | -0.0075532 | 0.02547 | -0.044619 | 0.01305 | -0.023464 | -0.0031616 | 0.068665 | 0.022888 | 0.059509 | 0.045776 | 0.11902 | 0.027466 | -0.10986 | 0.064087 | 0.6958 | 0.15106 | 0.70038 | 0.69122 | 0.54932 | 0.48065 | 121.4264 | 121.2891 | -0.58594 | 121.4218 | 121.4447 | 0.15564 | -0.63629 | 121.9482 | 121.8796 | -0.004578 | 121.463 | 121.55 | -0.32959 | -0.013733 | 121.5179 | 121.4676 | 121.4584 | -0.81482 | 122.0993 | 122.0901 | 122.0947 | -0.2243
1594.0156 | 122.3373 | -121.3989 | 0.70496 | -0.00022891 | -0.017306 | 0.012501 | 0.035382 | -0.010929 | -0.034878 | 0.0014613 | 7.627e-05 | 0.024616 | -0.043551 | 0.014546 | -0.025814 | -0.0044434 | 0.050354 | 0.004578 | 0.050354 | 0.050354 | 0.10071 | 0.009155 | -0.09613 | 0.041199 | 0.69122 | 0.14648 | 0.67291 | 0.67291 | 0.56763 | 0.49439 | 121.4081 | 121.3028 | -0.60425 | 121.4035 | 121.4493 | 0.14648 | -0.6546 | 121.9666 | 121.8933 | -0.032043 | 121.4401 | 121.5454 | -0.3479 | -0.032043 | 121.4996 | 121.4493 | 121.4493 | -0.80109 | 122.0718 | 122.0718 | 122.0901 | -0.21057
1595.7812 | 122.2916 | -121.431 | 0.72327 | 0.0074006 | -0.01346 | 0.011433 | 0.03645 | -0.012852 | -0.035305 | 0.0018885 | -0.0075532 | 0.027179 | -0.042269 | 0.015614 | -0.023464 | -0.00038438 | 0.032043 | -0.036621 | 0.032043 | 0.027466 | 0.12817 | 0.032043 | -0.11902 | 0.009155 | 0.61798 | 0.073242 | 0.71411 | 0.69122 | 0.52643 | 0.48065 | 121.463 | 121.312 | -0.59509 | 121.3943 | 121.4584 | 0.14649 | -0.69122 | 121.9574 | 121.9116 | -0.009156 | 121.4401 | 121.5042 | -0.40741 | -0.032044 | 121.5591 | 121.463 | 121.463 | -0.84229 | 122.1451 | 122.1222 | 122.049 | -0.24261
1597.5781 | 122.3419 | -121.3943 | 0.71869 | -0.00022891 | -0.016665 | 0.011433 | 0.033887 | -0.0096472 | -0.03616 | 0.0016749 | 7.627e-05 | 0.02312 | -0.045901 | 0.013905 | -0.026241 | -0.0014526 | 0.07782 | 0.059509 | 0.10529 | 0.073242 | 0.091553 | 0.064087 | -0.091553 | 0.086975 | 0.737 | 0.2243 | 0.67749 | 0.6546 | 0.59052 | 0.53558 | 121.4584 | 121.3028 | -0.62714 | 121.4539 | 121.4676 | 0.16479 | -0.64087 | 121.9849 | 121.9299 | -0.041199 | 121.4813 | 121.6187 | -0.31128 | -0.064087 | 121.4859 | 121.4722 | 121.4996 | -0.81024 | 122.0718 | 122.0489 | 122.1313 | -0.18311
1599.2969 | 122.3419 | -121.4127 | 0.70953 | -0.0078584 | -0.014742 | 0.012928 | 0.039655 | -0.010715 | -0.03381 | 0.0023157 | 0.0077058 | 0.027607 | -0.04526 | 0.013691 | -0.023251 | -0.0031616 | 0.054932 | 0.013733 | 0.050354 | 0.054932 | 0.1236 | 0.036621 | -0.10986 | 0.027466 | 0.67749 | 0.15564 | 0.68665 | 0.6958 | 0.55847 | 0.49896 | 121.4493 | 121.3028 | -0.58594 | 121.4264 | 121.4676 | 0.16479 | -0.6546 | 121.9711 | 121.9116 | -0.022888 | 121.4401 | 121.5683 | -0.34332 | -0.013733 | 121.5363 | 121.4676 | 121.463 | -0.8194 | 122.0993 | 122.1085 | 122.0901 | -0.21057
1601.0625 | 122.3557 | -121.3943 | 0.73242 | -0.0078584 | -0.01282 | 0.011647 | 0.037732 | -0.0098608 | -0.035092 | 0.0010339 | 7.627e-05 | 0.026752 | -0.043765 | 0.016041 | -0.023464 | -0.0035888 | 0.054932 | -0.004578 | 0.045776 | 0.050354 | 0.12817 | 0.027466 | -0.10986 | 0.050354 | 0.67749 | 0.15564 | 0.70038 | 0.68665 | 0.54932 | 0.48981 | 121.4218 | 121.2845 | -0.60425 | 121.3898 | 121.4447 | 0.16022 | -0.67749 | 121.9437 | 121.8842 | -0.032044 | 121.4447 | 121.55 | -0.33417 | -0.045776 | 121.5225 | 121.4493 | 121.4401 | -0.84229 | 122.0947 | 122.081 | 122.0718 | -0.24262
1602.8438 | 122.2733 | -121.3943 | 0.80109 | -0.0078584 | -0.021792 | 0.013569 | 0.034528 | -0.0094336 | -0.045987 | -0.0015295 | -0.0075532 | 0.024189 | -0.049105 | 0.01305 | -0.02731 | -0.00017078 | 0.036621 | 0.036621 | 0.086975 | 0.059509 | 0.086975 | 0.050354 | -0.07782 | 0.064087 | 0.67749 | 0.21515 | 0.72784 | 0.737 | 0.53558 | 0.48523 | 121.4447 | 121.3165 | -0.71411 | 121.431 | 121.4539 | 0.13733 | -0.76446 | 121.9299 | 121.8796 | -0.073242 | 121.4584 | 121.6095 | -0.27008 | -0.064086 | 121.4813 | 121.431 | 121.4813 | -0.87891 | 122.1222 | 122.1313 | 122.0718 | -0.31586
1604.625 | 122.3602 | -121.3623 | 0.80109 | -0.0078584 | -0.019655 | 0.013142 | 0.034955 | -0.012638 | -0.037014 | -0.0004613 | 0.0077058 | 0.024402 | -0.046115 | 0.012623 | -0.023892 | -0.0018798 | 0.10986 | 0.013733 | 0.11444 | 0.09613 | 0.09613 | 0.050354 | -0.07782 | 0.10529 | 0.70496 | 0.22888 | 0.737 | 0.73242 | 0.54932 | 0.49896 | 121.4127 | 121.2845 | -0.70496 | 121.376 | 121.4584 | 0.17395 | -0.69122 | 121.9116 | 121.8613 | -0.064086 | 121.4676 | 121.5912 | -0.27008 | -0.068664 | 121.4584 | 121.4722 | 121.4767 | -0.87891 | 122.0993 | 122.0947 | 122.0673 | -0.30212
1606.4062 | 122.2733 | -121.4813 | 0.71869 | -0.00022891 | -0.017946 | 0.014851 | 0.037732 | -0.0081518 | -0.038937 | -0.0013159 | -0.015182 | 0.026752 | -0.045687 | 0.011555 | -0.025601 | -0.004016 | 0.022888 | -0.041199 | 0.013733 | 0.009155 | 0.13275 | 0.004578 | -0.1236 | -0.009155 | 0.6134 | 0.1236 | 0.70953 | 0.69122 | 0.53558 | 0.48523 | 121.4859 | 121.3577 | -0.58594 | 121.4401 | 121.4905 | 0.13275 | -0.6958 | 122.0169 | 121.9666 | -0.009155 | 121.4722 | 121.6049 | -0.36163 | -0.027466 | 121.6141 | 121.5042 | 121.4951 | -0.84229 | 122.1909 | 122.1725 | 122.0947 | -0.23346
1608.1875 | 122.3648 | -121.4493 | 0.70496 | 0.0074006 | -0.017306 | 0.011433 | 0.03346 | -0.0077246 | -0.036587 | 0.0006067 | -0.0075532 | 0.025043 | -0.047824 | 0.012623 | -0.022183 | -0.0023072 | 0.10071 | 0.050354 | 0.091553 | 0.064087 | 0.082397 | 0.054932 | -0.073242 | 0.12817 | 0.70953 | 0.23346 | 0.66834 | 0.6546 | 0.57678 | 0.49896 | 121.5042 | 121.376 | -0.62256 | 121.4996 | 121.5134 | 0.13733 | -0.60425 | 122.0261 | 121.9482 | -0.036621 | 121.5775 | 121.6827 | -0.2655 | -0.050354 | 121.5317 | 121.55 | 121.5408 | -0.7782 | 122.1176 | 122.1039 | 122.1588 | -0.20599
1609.9062 | 122.2778 | -121.4951 | 0.71869 | -0.0078584 | -0.019228 | 0.015065 | 0.035596 | -0.012852 | -0.042355 | -3.4096e-05 | 0.0077058 | 0.024402 | -0.044833 | 0.011555 | -0.025387 | -0.0042298 | 0.041199 | 0.009155 | 0.082397 | 0.054932 | 0.086975 | 0.064087 | -0.086975 | 0.054932 | 0.65002 | 0.18768 | 0.67291 | 0.64545 | 0.54932 | 0.4715 | 121.5591 | 121.4081 | -0.63171 | 121.5042 | 121.55 | 0.14191 | -0.67749 | 122.0444 | 121.9666 | -0.045776 | 121.55 | 121.6827 | -0.28381 | -0.073242 | 121.582 | 121.5363 | 121.5775 | -0.80566 | 122.168 | 122.1405 | 122.1451 | -0.24719
1611.6875 | 122.2412 | -121.5363 | 0.70953 | -0.00022891 | -0.017519 | 0.014851 | 0.036878 | -0.010715 | -0.039792 | -0.0013159 | -0.015182 | 0.023334 | -0.044833 | 0.011982 | -0.024532 | -0.0020934 | 0.12817 | 0.07782 | 0.13275 | 0.064087 | 0.091553 | 0.050354 | -0.068665 | 0.13275 | 0.66376 | 0.21515 | 0.65002 | 0.62256 | 0.5127 | 0.48065 | 121.5866 | 121.4676 | -0.61798 | 121.6141 | 121.6003 | 0.13275 | -0.58136 | 122.0489 | 122.0169 | -0.05951 | 121.669 | 121.7514 | -0.2655 | -0.086975 | 121.6278 | 121.6644 | 121.669 | -0.7782 | 122.1863 | 122.1588 | 122.2 | -0.22888
1613.4688 | 122.3648 | -121.5042 | 0.69122 | -0.00022891 | -0.014956 | 0.0099378 | 0.039441 | -0.0081518 | -0.037655 | -0.0002477 | -0.0075532 | 0.026325 | -0.043765 | 0.012837 | -0.022396 | -0.0050842 | 0.041199 | -0.064087 | -0.004578 | 0.018311 | 0.1236 | 0.009155 | -0.1236 | 0.009155 | 0.59509 | 0.082397 | 0.66834 | 0.6546 | 0.48981 | 0.43488 | 121.5134 | 121.3806 | -0.56763 | 121.4401 | 121.5225 | 0.14191 | -0.65002 | 121.994 | 121.9391 | -0.022888 | 121.5134 | 121.5866 | -0.35248 | -0.036621 | 121.6278 | 121.5454 | 121.4996 | -0.81482 | 122.1725 | 122.1588 | 122.0993 | -0.25635
1615.1875 | 122.3465 | -121.5317 | 0.6546 | -0.00022891 | -0.014742 | 0.012501 | 0.034955 | -0.01157 | -0.035305 | 0.0010339 | 0.0077058 | 0.027179 | -0.043765 | 0.01305 | -0.021328 | -0.0033752 | 0.032043 | -0.054932 | -0.013733 | 0.018311 | 0.14191 | 0.009155 | -0.10986 | -0.004578 | 0.58136 | 0.091553 | 0.65002 | 0.63171 | 0.49439 | 0.42114 | 121.5408 | 121.4218 | -0.5127 | 121.4767 | 121.55 | 0.12817 | -0.62256 | 122.0261 | 121.9528 | -0.004578 | 121.5271 | 121.6232 | -0.32959 | -0.022888 | 121.6736 | 121.5637 | 121.5179 | -0.76447 | 122.1817 | 122.1634 | 122.113 | -0.23346
1616.9531 | 122.406 | -121.5225 | 0.66376 | -0.00022891 | -0.017519 | 0.011219 | 0.034101 | -0.010929 | -0.03616 | 0.0008203 | 7.627e-05 | 0.022266 | -0.044833 | 0.014118 | -0.021969 | -0.00059818 | 0.054932 | -0.041199 | 0.009155 | 0.013733 | 0.1236 | 0.032043 | -0.10071 | 0.064087 | 0.59967 | 0.14191 | 0.6546 | 0.63171 | 0.53101 | 0.46692 | 121.5546 | 121.4218 | -0.54016 | 121.4813 | 121.5363 | 0.11444 | -0.60883 | 122.0535 | 121.9894 | -0.009155 | 121.5866 | 121.6644 | -0.32501 | -0.032043 | 121.6461 | 121.5775 | 121.5317 | -0.76447 | 122.1771 | 122.1542 | 122.1222 | -0.19684
1618.7344 | 122.2961 | -121.5408 | 0.6958 | -0.0078584 | -0.014529 | 0.013997 | 0.037946 | -0.0087926 | -0.035733 | -0.0025977 | -0.0075532 | 0.023975 | -0.042483 | 0.012196 | -0.026028 | -0.00017078 | 0.013733 | -0.045776 | -0.004578 | 0.018311 | 0.13275 | 0.022888 | -0.11444 | 0 | 0.59052 | 0.07782 | 0.68207 | 0.65918 | 0.49896 | 0.44861 | 121.5637 | 121.4264 | -0.56305 | 121.4951 | 121.5591 | 0.13275 | -0.68207 | 122.0398 | 121.9894 | -0.013733 | 121.5408 | 121.6187 | -0.37079 | -0.036621 | 121.6736 | 121.5546 | 121.5363 | -0.81024 | 122.2229 | 122.2 | 122.1313 | -0.24719
1620.5312 | 122.3923 | -121.5134 | 0.6546 | -0.00022891 | -0.017519 | 0.015278 | 0.032605 | -0.0081518 | -0.039364 | 0.0027429 | 7.627e-05 | 0.023548 | -0.046542 | 0.013905 | -0.023892 | -0.0023072 | 0.1236 | 0.054932 | 0.10986 | 0.09613 | 0.07782 | 0.068665 | -0.082397 | 0.12817 | 0.67749 | 0.19684 | 0.59052 | 0.58594 | 0.54016 | 0.47607 | 121.582 | 121.431 | -0.57678 | 121.5683 | 121.6095 | 0.17853 | -0.53101 | 122.0535 | 121.9894 | -0.064087 | 121.6415 | 121.7102 | -0.27924 | -0.068665 | 121.5912 | 121.637 | 121.6232 | -0.737 | 122.1039 | 122.0993 | 122.1909 | -0.17853
1622.2812 | 122.3557 | -121.5775 | 0.62714 | -0.0078584 | -0.013674 | 0.010151 | 0.035596 | -0.010074 | -0.035946 | 0.0035975 | 7.627e-05 | 0.027179 | -0.043765 | 0.011982 | -0.019619 | -0.0014526 | 0.050354 | -0.054932 | 0.013733 | 0.018311 | 0.1236 | 0.018311 | -0.10071 | -0.018311 | 0.53558 | 0.054932 | 0.65002 | 0.6134 | 0.48981 | 0.41199 | 121.5958 | 121.4767 | -0.50354 | 121.5225 | 121.5958 | 0.11902 | -0.57678 | 122.0673 | 121.9894 | 0.022888 | 121.5591 | 121.6324 | -0.35706 | -0.013733 | 121.7011 | 121.6278 | 121.5912 | -0.72784 | 122.2275 | 122.1909 | 122.113 | -0.21515
1624.0625 | 122.2961 | -121.5866 | 0.68207 | -0.0078584 | -0.022219 | 0.015278 | 0.032605 | -0.011143 | -0.040432 | -0.0013159 | -0.0075532 | 0.022052 | -0.046969 | 0.0098459 | -0.023892 | -0.00038438 | 0.10071 | 0.10529 | 0.15106 | 0.10071 | 0.082397 | 0.041199 | -0.068665 | 0.10071 | 0.71869 | 0.2243 | 0.61798 | 0.59509 | 0.53101 | 0.46692 | 121.6278 | 121.5179 | -0.59967 | 121.6919 | 121.6873 | 0.16937 | -0.58136 | 122.1176 | 122.0535 | -0.064087 | 121.6873 | 121.8109 | -0.24261 | -0.086975 | 121.669 | 121.6873 | 121.7377 | -0.75073 | 122.2046 | 122.1817 | 122.3053 | -0.21515
1625.8281 | 122.3373 | -121.6049 | 0.66834 | 0.0074006 | -0.018801 | 0.01656 | 0.035169 | -0.01157 | -0.041928 | -0.0002477 | 7.627e-05 | 0.022052 | -0.046756 | 0.0107 | -0.026455 | -0.0016662 | 0.07782 | 0.036621 | 0.11444 | 0.068665 | 0.10529 | 0.054932 | -0.064087 | 0.10071 | 0.66376 | 0.21515 | 0.6134 | 0.59967 | 0.52185 | 0.46234 | 121.6599 | 121.5408 | -0.56305 | 121.6415 | 121.6736 | 0.13275 | -0.59052 | 122.1268 | 122.0673 | -0.054932 | 121.7056 | 121.8201 | -0.24719 | -0.068665 | 121.7102 | 121.6827 | 121.7194 | -0.73242 | 122.2183 | 122.2046 | 122.2687 | -0.20599
1627.6094 | 122.3053 | -121.5775 | 0.68207 | -0.0078584 | -0.015597 | 0.013783 | 0.037091 | -0.010288 | -0.035733 | -0.0011023 | 7.627e-05 | 0.025898 | -0.043978 | 0.011341 | -0.025601 | 0.00068362 | 0.054932 | -0.050354 | 0.018311 | 0.009155 | 0.13733 | 0.009155 | -0.1236 | 0.004578 | 0.32501 | 0.09613 | 0.65918 | 0.64087 | 0.48981 | 0.42114 | 121.5866 | 121.4539 | -0.54474 | 121.5271 | 121.5866 | 0.13275 | -0.62714 | 122.0673 | 121.9986 | -0.022888 | 121.582 | 121.6736 | -0.32501 | -0.041199 | 121.7148 | 121.6324 | 121.5958 | -0.80566 | 122.2366 | 122.2183 | 121.9025 | -0.26093
1629.3906 | 122.4472 | -121.5042 | 0.6958 | -0.00022891 | -0.018374 | 0.012928 | 0.033032 | -0.010929 | -0.032956 | 0.0012477 | 7.627e-05 | 0.02547 | -0.042483 | 0.010914 | -0.023464 | -0.00059818 | 0.050354 | -0.064087 | 0.004578 | 0.022888 | 0.11444 | 0.018311 | -0.10986 | 0.082397 | 0.21057 | 0.1236 | 0.67749 | 0.67749 | 0.54016 | 0.48981 | 121.5225 | 121.3943 | -0.58136 | 121.4401 | 121.5271 | 0.13275 | -0.64545 | 122.0444 | 121.994 | -0.018311 | 121.5866 | 121.6278 | -0.36621 | -0.018311 | 121.6187 | 121.5546 | 121.5088 | -0.80566 | 122.1817 | 122.1817 | 121.7148 | -0.20599
1631.1562 | 122.374 | -121.5225 | 0.71869 | -0.0078584 | -0.018374 | 0.012928 | 0.033673 | -0.011356 | -0.037442 | 0.0012477 | 0.0077058 | 0.022907 | -0.044619 | 0.0085641 | -0.023678 | 0.0019654 | 0.15564 | 0.064087 | 0.13275 | 0.086975 | 0.073242 | 0.091553 | -0.059509 | 0.12817 | 0.32044 | 0.21515 | 0.63171 | 0.65002 | 0.57678 | 0.49896 | 121.6141 | 121.463 | -0.64545 | 121.5866 | 121.6095 | 0.14648 | -0.56305 | 122.0993 | 122.0215 | -0.086975 | 121.6507 | 121.7377 | -0.28381 | -0.068665 | 121.5958 | 121.6782 | 121.6553 | -0.7782 | 122.1542 | 122.1725 | 121.843 | -0.21973
1632.9375 | 122.4472 | -121.5042 | 0.70038 | -0.00022891 | -0.013674 | 0.012928 | 0.040296 | -0.0087926 | -0.03616 | 0.0021021 | -0.0075532 | 0.024402 | -0.042269 | 0.0094187 | -0.023678 | 0.0011108 | 0.086975 | -0.027466 | 0.045776 | 0.050354 | 0.12817 | 0.018311 | -0.10529 | 0.041199 | 0.2655 | 0.13733 | 0.68207 | 0.66376 | 0.5127 | 0.45319 | 121.5225 | 121.3989 | -0.5722 | 121.4767 | 121.5546 | 0.15564 | -0.6134 | 122.0169 | 121.9574 | -0.01831 | 121.5454 | 121.6415 | -0.31586 | -0.036621 | 121.6324 | 121.5912 | 121.55 | -0.80566 | 122.1863 | 122.168 | 121.7697 | -0.24719
1634.7188 | 122.3282 | -121.5454 | 0.71869 | -0.00022891 | -0.017946 | 0.015706 | 0.0388 | -0.011783 | -0.042996 | 0.0012477 | 7.627e-05 | 0.020557 | -0.044406 | 0.0087779 | -0.027737 | 0.0028198 | 0.14191 | 0.10529 | 0.16479 | 0.09613 | 0.073242 | 0.045776 | -0.064087 | 0.12817 | 0.32044 | 0.23804 | 0.63629 | 0.64545 | 0.5722 | 0.50354 | 121.5912 | 121.4813 | -0.64545 | 121.6507 | 121.6415 | 0.16022 | -0.57678 | 122.1176 | 122.049 | -0.082397 | 121.6736 | 121.7834 | -0.2655 | -0.073242 | 121.6187 | 121.6873 | 121.7102 | -0.78278 | 122.1817 | 122.1909 | 121.8658 | -0.21515
1636.5 | 122.4472 | -121.5271 | 0.70953 | -0.0078584 | -0.015169 | 0.012288 | 0.032605 | -0.012424 | -0.036374 | 0.0003931 | -0.0075532 | 0.022266 | -0.043978 | 0.013264 | -0.023037 | -0.00059818 | 0.082397 | 0.009155 | 0.064087 | 0.059509 | 0.091553 | 0.059509 | -0.073242 | 0.10986 | 0.19684 | 0.20599 | 0.66834 | 0.65918 | 0.58136 | 0.52643 | 121.5866 | 121.4539 | -0.61798 | 121.5363 | 121.5866 | 0.13275 | -0.62714 | 122.1085 | 122.0535 | -0.041199 | 121.637 | 121.7331 | -0.32043 | -0.050354 | 121.6187 | 121.6095 | 121.5912 | -0.78278 | 122.1954 | 122.1863 | 121.7239 | -0.18311
1638.2188 | 122.3328 | -121.6141 | 0.6958 | -0.00022891 | -0.018587 | 0.015492 | 0.035382 | -0.013492 | -0.042569 | -0.0019567 | -0.0075532 | 0.019275 | -0.044406 | 0.0081369 | -0.023678 | 0.0019654 | 0.054932 | 0.018311 | 0.086975 | 0.054932 | 0.091553 | 0.041199 | -0.07782 | 0.068665 | 0.58594 | 0.17395 | 0.61798 | 0.58594 | 0.49896 | 0.44861 | 121.6553 | 121.5363 | -0.60425 | 121.6324 | 121.669 | 0.13275 | -0.64087 | 122.113 | 122.0627 | -0.07782 | 121.6827 | 121.788 | -0.27466 | -0.10986 | 121.7056 | 121.669 | 121.701 | -0.77362 | 122.2321 | 122.2 | 122.2 | -0.24719
1640 | 122.4564 | -121.6415 | 0.62714 | 0.0074006 | -0.016665 | 0.012501 | 0.03346 | -0.010074 | -0.034024 | 0.0016749 | 7.627e-05 | 0.022693 | -0.041842 | 0.0089915 | -0.019192 | 0.0023926 | 0.11444 | 0.054932 | 0.10071 | 0.068665 | 0.059509 | 0.050354 | -0.086975 | 0.1236 | 0.65002 | 0.1831 | 0.5722 | 0.56763 | 0.49896 | 0.43488 | 121.6919 | 121.5546 | -0.56763 | 121.6965 | 121.7102 | 0.15564 | -0.5127 | 122.1405 | 122.0764 | -0.054931 | 121.7651 | 121.8246 | -0.25177 | -0.059509 | 121.7011 | 121.756 | 121.7422 | -0.71411 | 122.2137 | 122.2092 | 122.2916 | -0.19226
1641.7344 | 122.4106 | -121.6278 | 0.63629 | -0.0078584 | -0.015383 | 0.014424 | 0.035169 | -0.01157 | -0.031033 | 0.0027429 | -0.0075532 | 0.024189 | -0.040133 | 0.0079233 | -0.020687 | 0.0015382 | 0.032043 | -0.086975 | -0.013733 | 0.013733 | 0.11902 | 0.027466 | -0.11444 | 0.004578 | 0.5127 | 0.050354 | 0.62714 | 0.6134 | 0.46692 | 0.39825 | 121.6553 | 121.5134 | -0.51727 | 121.5408 | 121.6415 | 0.12817 | -0.60425 | 122.0947 | 122.0261 | -0.009156 | 121.6324 | 121.6782 | -0.3479 | -0.022889 | 121.7468 | 121.6599 | 121.6141 | -0.75073 | 122.2549 | 122.2412 | 122.1405 | -0.23804
1643.5312 | 122.3053 | -121.6553 | 0.67291 | -0.0078584 | -0.015597 | 0.012715 | 0.04115 | -0.0064428 | -0.039364 | 0.0006067 | 7.627e-05 | 0.02013 | -0.040347 | 0.0057871 | -0.023892 | 0.0026062 | 0.09613 | 0.054932 | 0.10986 | 0.064087 | 0.086975 | 0.032043 | -0.09613 | 0.045776 | 0.62256 | 0.13733 | 0.58594 | 0.59967 | 0.4715 | 0.39368 | 121.6873 | 121.5591 | -0.58594 | 121.7102 | 121.7194 | 0.16022 | -0.57678 | 122.1268 | 122.0489 | -0.086976 | 121.701 | 121.7926 | -0.25635 | -0.073243 | 121.7422 | 121.7514 | 121.7651 | -0.76904 | 122.2412 | 122.2549 | 122.2778 | -0.27924
1645.2656 | 122.406 | -121.6278 | 0.61798 | 0.0074006 | -0.016451 | 0.012715 | 0.034314 | -0.01157 | -0.032315 | -3.4096e-05 | -0.015182 | 0.024402 | -0.040988 | 0.011128 | -0.018337 | 0.00047002 | 0.086975 | -0.041199 | 0.013733 | 0.032043 | 0.13733 | 0.018311 | -0.10529 | 0.022888 | 0.54016 | 0.073242 | 0.59509 | 0.59967 | 0.46234 | 0.39368 | 121.6461 | 121.5225 | -0.48065 | 121.5866 | 121.6599 | 0.13733 | -0.53101 | 122.0901 | 122.0215 | -0.022888 | 121.6507 | 121.701 | -0.32044 | -0.018311 | 121.7651 | 121.7148 | 121.6415 | -0.72327 | 122.2229 | 122.2275 | 122.168 | -0.2243
1647.0469 | 122.3831 | -121.6553 | 0.65918 | -0.0078584 | -0.023287 | -0.0067248 | 0.033032 | -0.010929 | -0.042355 | -0.0017431 | -0.015182 | 0.016925 | -0.04526 | 0.0057871 | -0.024532 | 0.0019654 | 0.064087 | 0.032043 | 0.09613 | 0.073242 | 0.10529 | 0.059509 | -0.07782 | 0.086975 | 0.65918 | 0.19226 | 0.58136 | 0.56763 | 0.48981 | 0.42572 | 121.7148 | 121.5775 | -0.55389 | 121.6873 | 121.7285 | 0.15106 | -0.59509 | 122.1451 | 122.081 | -0.07782 | 121.7422 | 121.8475 | -0.23346 | -0.091553 | 121.7606 | 121.7194 | 121.7514 | -0.737 | 122.2366 | 122.2229 | 122.3145 | -0.23346
1648.7812 | 122.4701 | -121.5729 | 0.64545 | 0.0074006 | -0.014529 | 0.011433 | 0.037518 | -0.010074 | -0.033596 | 0.0012477 | 0.0077058 | 0.023334 | -0.041629 | 0.0053599 | -0.021755 | -0.0016662 | 0.068665 | -0.054932 | 0.013733 | 0.036621 | 0.12817 | 0.018311 | -0.10529 | 0.041199 | 0.64087 | 0.10529 | 0.63171 | 0.61798 | 0.49896 | 0.42572 | 121.5912 | 121.4676 | -0.51727 | 121.5179 | 121.6095 | 0.14191 | -0.57678 | 122.0718 | 121.9986 | -0.013733 | 121.6141 | 121.6782 | -0.32043 | -0.027466 | 121.701 | 121.6415 | 121.5866 | -0.75073 | 122.2046 | 122.1909 | 122.2137 | -0.21973
1650.5156 | 122.4564 | -121.5958 | 0.64545 | -0.0078584 | -0.014315 | 0.010792 | 0.035596 | -0.0094336 | -0.032956 | 0.0006067 | -0.0075532 | 0.024829 | -0.040774 | 0.0107 | -0.02261 | -0.00081178 | 0.09613 | 0.013733 | 0.054932 | 0.045776 | 0.11902 | 0.036621 | -0.11444 | 0.064087 | 0.65918 | 0.13275 | 0.62714 | 0.62714 | 0.49896 | 0.4303 | 121.6324 | 121.4813 | -0.52643 | 121.6095 | 121.6415 | 0.16022 | -0.54932 | 122.0947 | 122.0261 | -0.018311 | 121.6599 | 121.7285 | -0.29755 | -0.018311 | 121.7148 | 121.6919 | 121.6507 | -0.75989 | 122.2229 | 122.2229 | 122.2549 | -0.21515
1652.2969 | 122.4289 | -121.6049 | 0.67291 | -0.0078584 | -0.016024 | 0.012288 | 0.034741 | -0.0098608 | -0.035305 | -0.0002477 | 7.627e-05 | 0.02248 | -0.040988 | 0.010059 | -0.024105 | 0.0017518 | 0.091553 | 0.009155 | 0.041199 | 0.036621 | 0.11444 | 0.036621 | -0.11902 | 0.041199 | 0.61798 | 0.10071 | 0.63171 | 0.63171 | 0.48065 | 0.42572 | 121.6415 | 121.4859 | -0.55847 | 121.6141 | 121.6415 | 0.15564 | -0.58136 | 122.0856 | 122.0306 | -0.041199 | 121.6461 | 121.7056 | -0.32501 | -0.041199 | 121.7194 | 121.6965 | 121.6461 | -0.79193 | 122.2366 | 122.2366 | 122.2229 | -0.24719
1654.0156 | 122.3511 | -121.6232 | 0.71869 | -0.0078584 | -0.021792 | 0.016987 | 0.033673 | -0.010502 | -0.041928 | 0.0003931 | 7.627e-05 | 0.017139 | -0.042697 | 0.0098459 | -0.024319 | 0.003888 | 0.091553 | 0.064087 | 0.10986 | 0.073242 | 0.082397 | 0.064087 | -0.091553 | 0.082397 | 0.69122 | 0.17395 | 0.64087 | 0.61798 | 0.50812 | 0.45319 | 121.6873 | 121.5317 | -0.63629 | 121.6873 | 121.6965 | 0.16479 | -0.62714 | 122.1313 | 122.0764 | -0.07782 | 121.7056 | 121.7972 | -0.27924 | -0.10071 | 121.7056 | 121.7148 | 121.7331 | -0.81024 | 122.2641 | 122.2412 | 122.3145 | -0.2655
1655.7969 | 122.3969 | -120.9183 | 1.4008 | -0.0078584 | -0.018374 | 0.012715 | 0.035169 | -0.011783 | -0.03851 | -0.0006751 | -0.0075532 | 0.015857 | -0.034579 | -0.0025443 | -0.014492 | 0.0041016 | 0.027466 | -0.041199 | -0.013733 | 0.004578 | 0.13733 | -0.013733 | -0.13275 | -0.013733 | 1.2863 | 0.032043 | 1.355 | 1.3641 | 0.10529 | 0.064087 | 120.9045 | 120.7855 | -1.2634 | 120.8771 | 120.9229 | 0.13733 | -1.3733 | 121.0236 | 120.9824 | -0.045777 | 120.9045 | 120.9503 | -0.032044 | -0.036621 | 121.0556 | 120.9457 | 120.9045 | -1.5335 | 122.2733 | 122.2824 | 122.2046 | -1.3367
1657.5938 | 122.438 | -120.9732 | 1.3138 | -0.0078584 | -0.014315 | 0.013356 | 0.035596 | -0.011997 | -0.035519 | -0.0002477 | 7.627e-05 | 0.016284 | -0.03757 | 0.0010873 | -0.011501 | 0.00089722 | 0.082397 | -0.027466 | 0.054932 | 0.032043 | 0.11902 | 0.027466 | -0.10529 | -0.009155 | 1.2131 | 0.018311 | 1.3046 | 1.2817 | 0.11444 | 0.054932 | 121.0007 | 120.8679 | -1.1948 | 120.9457 | 121.0052 | 0.13733 | -1.2314 | 121.0876 | 121.0281 | -0.009156 | 120.9641 | 120.9915 | -0.036621 | -0.032044 | 121.0922 | 121.0556 | 121.0281 | -1.4191 | 122.2778 | 122.2549 | 122.1863 | -1.2589
1659.3125 | 122.3511 | -121.019 | 1.3184 | -0.00022891 | -0.016451 | 0.014424 | 0.036878 | -0.010929 | -0.041073 | 0.0001795 | 7.627e-05 | 0.015857 | -0.037143 | -0.0014761 | -0.016201 | 0.00068362 | 0.10529 | 0.068665 | 0.14648 | 0.09613 | 0.082397 | 0.054932 | -0.073242 | 0.082397 | 1.3458 | 0.16937 | 1.2222 | 1.2222 | 0.14191 | 0.068665 | 121.0739 | 120.9457 | -1.236 | 121.0876 | 121.1151 | 0.16937 | -1.2131 | 121.1609 | 121.0876 | -0.09613 | 121.1014 | 121.1884 | 0.10071 | -0.09613 | 121.1014 | 121.1243 | 121.1655 | -1.3916 | 122.2412 | 122.2412 | 122.3648 | -1.2497
1661.0938 | 122.438 | -120.9869 | 1.3 | -0.00022891 | -0.01816 | 0.013356 | 0.032392 | -0.0098608 | -0.037869 | -0.0021703 | 0.0077058 | 0.019916 | -0.043978 | -0.0027579 | -0.012356 | 0.0028198 | 0.14648 | 0.068665 | 0.13733 | 0.10529 | 0.07782 | 0.068665 | -0.082397 | 0.16937 | 1.3321 | 0.15564 | 1.2222 | 1.2268 | 0.15564 | 0.091553 | 121.0556 | 120.9045 | -1.2222 | 121.0556 | 121.0922 | 0.18768 | -1.1536 | 121.1426 | 121.0785 | -0.07782 | 121.1563 | 121.1426 | 0.064087 | -0.073242 | 121.0648 | 121.1334 | 121.1243 | -1.3824 | 122.2092 | 122.2137 | 122.319 | -1.2085
1662.875 | 122.4243 | -121.051 | 1.2726 | -0.00022891 | -0.015169 | 0.012928 | 0.037305 | -0.010502 | -0.037228 | 0.0021021 | 7.627e-05 | 0.020557 | -0.041201 | -0.0019033 | -0.014706 | 0.0028198 | 0.045776 | -0.059509 | -0.004578 | 0.013733 | 0.11902 | -0.004578 | -0.11444 | 0.045776 | 1.1719 | 0.036621 | 1.2405 | 1.236 | 0.09613 | 0.022888 | 121.0464 | 120.9366 | -1.1536 | 120.9915 | 121.0648 | 0.12817 | -1.2268 | 121.1472 | 121.0739 | -0.032043 | 121.0968 | 121.0876 | 0.013733 | -0.036621 | 121.17 | 121.0968 | 121.0464 | -1.387 | 122.2916 | 122.287 | 122.2229 | -1.2497
1664.5938 | 122.3877 | -122.0123 | 0.33875 | -0.015487 | -0.017092 | 0.014637 | 0.037091 | -0.011997 | -0.037869 | 0.0012477 | 0.0077058 | 0.0066714 | -0.028598 | -0.0061757 | -0.013638 | 0.0015382 | 0.13275 | 0.07782 | 0.13275 | 0.086975 | 0.10529 | 0.054932 | -0.054932 | 0.3067 | 0.36163 | 0.24261 | 0.2655 | 0.25177 | 0.13733 | 0.068665 | 122.0673 | 121.9574 | -0.23346 | 122.0901 | 122.0993 | 0.14191 | -0.20599 | 122.1497 | 122.081 | -0.073242 | 122.319 | 122.2549 | 0.17395 | -0.086975 | 122.1176 | 122.1451 | 122.1451 | -0.39368 | 122.2778 | 122.2641 | 122.374 | -0.27008
1666.3125 | 122.3877 | -122.0306 | 0.37537 | 0.01503 | -0.017733 | 0.013783 | 0.036023 | -0.011356 | -0.041714 | -0.0006751 | -0.0075532 | 0.0036808 | -0.028811 | -0.0046805 | -0.013638 | 0.0019654 | 0.082397 | 0.018311 | 0.10529 | 0.059509 | 0.10071 | 0.059509 | -0.068665 | 0.24261 | 0.31128 | 0.21057 | 0.27008 | 0.24719 | 0.15106 | 0.073242 | 122.0901 | 121.962 | -0.27466 | 122.049 | 122.0901 | 0.12817 | -0.29297 | 122.1817 | 122.1039 | -0.10528 | 122.2733 | 122.2412 | 0.13733 | -0.12817 | 122.1313 | 122.113 | 122.1359 | -0.44403 | 122.3007 | 122.2778 | 122.3419 | -0.30212
1668.0938 | 122.4243 | -121.9391 | 0.40283 | -0.00022891 | -0.021578 | 0.013356 | 0.034955 | -0.011356 | -0.041073 | -0.0021703 | -0.0075532 | 0.010089 | -0.033297 | 0.0010873 | -0.017269 | 0.00068362 | 0.11902 | 0.068665 | 0.1236 | 0.082397 | 0.11444 | 0.054932 | -0.059509 | 0.36163 | 0.45776 | 0.24261 | 0.33417 | 0.32959 | 0.25635 | 0.20142 | 121.994 | 121.8796 | -0.28839 | 122.0078 | 122.0215 | 0.14191 | -0.28381 | 122.1954 | 122.1405 | -0.068665 | 122.3007 | 122.1817 | 0.041199 | -0.073242 | 122.0535 | 122.0581 | 122.0627 | -0.46234 | 122.2733 | 122.2687 | 122.3969 | -0.20142
1669.875 | 122.3648 | -121.8521 | 0.53101 | -0.015487 | -0.018801 | 0.015278 | 0.036664 | -0.0090062 | -0.037655 | -0.0004613 | 7.627e-05 | 0.018207 | -0.037783 | 0.0047189 | -0.019833 | -0.00038438 | 0.10986 | 0.013733 | 0.086975 | 0.068665 | 0.09613 | 0.068665 | -0.073242 | 0.42114 | 0.4715 | 0.14191 | 0.43945 | 0.43488 | 0.33417 | 0.27924 | 121.9208 | 121.7789 | -0.43488 | 121.8658 | 121.9208 | 0.14191 | -0.42114 | 122.1863 | 122.1313 | -0.091553 | 122.2733 | 121.994 | -0.13733 | -0.096131 | 121.9482 | 121.962 | 121.9391 | -0.60425 | 122.2916 | 122.287 | 122.3236 | -0.25177
1671.6562 | 122.5067 | -121.9757 | 0.31586 | -0.00022891 | -0.012392 | 0.01186 | 0.033887 | -0.0094336 | -0.03381 | 0.0001795 | 7.627e-05 | 0.01073 | -0.03052 | -0.0016897 | -0.011715 | -0.00017078 | 0.091553 | -0.050354 | 0 | 0.013733 | 0.13275 | 0.018311 | -0.12817 | 0.21515 | 0.30212 | 0.13275 | 0.32959 | 0.3067 | 0.15106 | 0.086975 | 121.994 | 121.8475 | -0.18311 | 121.9254 | 121.9894 | 0.14191 | -0.2243 | 122.1268 | 122.0627 | 0.013733 | 122.1909 | 122.1085 | 0.045776 | -0.009155 | 122.1085 | 122.0673 | 121.9757 | -0.44403 | 122.3053 | 122.2824 | 122.2778 | -0.22888
1673.3906 | 122.5204 | -121.8063 | 0.4715 | -0.023117 | -0.015169 | 0.014637 | 0.035169 | -0.0090062 | -0.032742 | 0.0010339 | -0.0075532 | 0.017566 | -0.036074 | 0.0017283 | -0.014279 | -0.0010254 | 0.064087 | -0.064087 | 0.009155 | 0.018311 | 0.14191 | 0.018311 | -0.10986 | 0.38452 | 0.39368 | 0.07782 | 0.47607 | 0.45319 | 0.31586 | 0.2655 | 121.8246 | 121.6965 | -0.32959 | 121.7422 | 121.8246 | 0.12817 | -0.40741 | 122.1222 | 122.0718 | 0.004577 | 122.1909 | 121.8842 | -0.18768 | -0.018311 | 121.9482 | 121.8704 | 121.8155 | -0.58136 | 122.2824 | 122.2595 | 122.2 | -0.20599
1675.1719 | 122.5113 | -121.7651 | 0.52185 | -0.00022891 | -0.014742 | 0.011433 | 0.036023 | -0.010288 | -0.037014 | 0.0025293 | -0.015182 | 0.020557 | -0.034365 | 0.0032237 | -0.014492 | -0.00038438 | 0.050354 | -0.036621 | 0.018311 | 0.036621 | 0.11902 | 0.009155 | -0.10071 | 0.41657 | 0.49896 | 0.073242 | 0.52185 | 0.5127 | 0.2243 | 0.16479 | 121.7743 | 121.6644 | -0.40283 | 121.7285 | 121.8018 | 0.13733 | -0.4715 | 121.9894 | 121.9299 | 0 | 122.1817 | 121.8384 | -0.091553 | -0.009156 | 121.8842 | 121.8155 | 121.7834 | -0.62256 | 122.287 | 122.2778 | 122.2641 | -0.35706
1676.9531 | 122.4701 | -121.8475 | 0.50354 | -0.015487 | -0.017519 | 0.011006 | 0.031323 | -0.012211 | -0.033596 | 0.0029565 | 0.0077058 | 0.019275 | -0.035861 | 0.0060007 | -0.016201 | -0.00017078 | 0.11902 | 0.004578 | 0.064087 | 0.050354 | 0.11902 | 0.027466 | -0.10986 | 0.39368 | 0.46234 | 0.073242 | 0.47607 | 0.46234 | 0.28381 | 0.21057 | 121.875 | 121.7377 | -0.38452 | 121.8521 | 121.8979 | 0.16022 | -0.38452 | 122.1313 | 122.0581 | -0.027466 | 122.2412 | 121.9208 | -0.13733 | -0.041199 | 121.9666 | 121.9666 | 121.9116 | -0.6134 | 122.3236 | 122.3099 | 122.3099 | -0.29297
1678.7656 | 122.3969 | -121.8567 | 0.51727 | -0.00022891 | -0.016665 | 0.013997 | 0.0388 | -0.010288 | -0.042569 | -0.0002477 | 0.015335 | 0.014362 | -0.037143 | 0.0036509 | -0.020046 | 0.0023926 | 0.10986 | 0.064087 | 0.13733 | 0.073242 | 0.09613 | 0.059509 | -0.064087 | 0.43945 | 0.50354 | 0.16022 | 0.42572 | 0.42572 | 0.32044 | 0.24719 | 121.9162 | 121.7926 | -0.42114 | 121.9208 | 121.9299 | 0.13733 | -0.40741 | 122.1771 | 122.1039 | -0.091553 | 122.2961 | 122.0169 | -0.086975 | -0.091553 | 121.9528 | 121.9666 | 121.994 | -0.58136 | 122.2824 | 122.2824 | 122.3602 | -0.27008
1680.4844 | 122.5067 | -121.6782 | 0.65002 | -0.00022891 | -0.015169 | 0.013142 | 0.034741 | -0.011143 | -0.034451 | 0.0021021 | -0.0075532 | 0.01543 | -0.033084 | -0.0031851 | -0.01022 | 0.0026062 | 0.036621 | -0.086975 | -0.013733 | 0.013733 | 0.14191 | 0.022888 | -0.09613 | 0.49896 | 0.52643 | 0.004578 | 0.64545 | 0.62714 | 0.059509 | 0 | 121.701 | 121.582 | -0.50812 | 121.5912 | 121.6919 | 0.10986 | -0.6134 | 121.7377 | 121.6782 | -0.004577 | 122.1771 | 121.6827 | 0.004578 | -0.022888 | 121.8201 | 121.7148 | 121.6644 | -0.74615 | 122.3236 | 122.3053 | 122.2046 | -0.65002
1682.25 | 122.5342 | -121.701 | 0.63171 | -0.00022891 | -0.016665 | 0.013356 | 0.036023 | -0.010288 | -0.035092 | 0.0038111 | 7.627e-05 | 0.013294 | -0.030947 | -0.0023305 | -0.0095788 | 0.0017518 | 0.045776 | -0.050354 | 0.009155 | 0.022888 | 0.13275 | 0.013733 | -0.11444 | 0.5127 | 0.53558 | 0.027466 | 0.6134 | 0.60883 | 0.064087 | -0.004578 | 121.7148 | 121.5866 | -0.49896 | 121.6507 | 121.7239 | 0.13733 | -0.58594 | 121.7651 | 121.6965 | -0.018311 | 122.2137 | 121.7285 | 0.032044 | -0.022888 | 121.8338 | 121.7468 | 121.7102 | -0.74616 | 122.3145 | 122.3099 | 122.2366 | -0.63629
1683.9688 | 122.438 | -121.7422 | 0.63629 | -0.0078584 | -0.019869 | 0.013783 | 0.036878 | -0.011143 | -0.043423 | -0.0019567 | -0.0075532 | 0.0096622 | -0.033084 | -0.0053213 | -0.01791 | 0.003247 | 0.064087 | 0.041199 | 0.10986 | 0.07782 | 0.10986 | 0.041199 | -0.073242 | 0.56763 | 0.67749 | 0.16022 | 0.58594 | 0.58594 | 0.082397 | 0.013733 | 121.7834 | 121.669 | -0.52643 | 121.7834 | 121.8201 | 0.15106 | -0.5722 | 121.8246 | 121.756 | -0.050355 | 122.3099 | 121.9025 | 0.14648 | -0.050355 | 121.8521 | 121.8063 | 121.8521 | -0.70953 | 122.3282 | 122.3282 | 122.4197 | -0.62256
1685.7656 | 122.4472 | -121.7194 | 0.6546 | -0.00022891 | -0.017519 | 0.012928 | 0.039014 | -0.011356 | -0.041714 | -0.0036657 | 7.627e-05 | 0.0096622 | -0.035006 | -0.0021169 | -0.017483 | 0.00068362 | 0.10529 | 0.059509 | 0.12817 | 0.091553 | 0.09613 | 0.045776 | -0.082397 | 0.6134 | 0.70496 | 0.16937 | 0.59052 | 0.57678 | 0.10071 | 0.041199 | 121.7651 | 121.637 | -0.55847 | 121.7789 | 121.8109 | 0.17395 | -0.54932 | 121.8201 | 121.7606 | -0.064087 | 122.3328 | 121.8887 | 0.12817 | -0.07782 | 121.8155 | 121.8246 | 121.8475 | -0.737 | 122.3099 | 122.2961 | 122.4243 | -0.6134
1687.5625 | 122.3923 | -121.7468 | 0.64545 | 0.0074006 | -0.015597 | 0.014637 | 0.038159 | -0.0098608 | -0.038296 | -0.0011023 | 0.0077058 | 0.011798 | -0.031588 | -0.0027579 | -0.014492 | 0.00047002 | 0.13733 | 0.07782 | 0.14191 | 0.10529 | 0.10529 | 0.054932 | -0.082397 | 0.56763 | 0.67291 | 0.15564 | 0.55847 | 0.54932 | 0.091553 | 0.022888 | 121.8018 | 121.6644 | -0.54016 | 121.8246 | 121.8521 | 0.18768 | -0.50812 | 121.8384 | 121.7697 | -0.086975 | 122.3145 | 121.9025 | 0.13275 | -0.096131 | 121.8521 | 121.8842 | 121.8887 | -0.72784 | 122.3053 | 122.2961 | 122.4197 | -0.62256
1689.3281 | 122.4106 | -121.7468 | 0.64087 | -0.00022891 | -0.01581 | 0.013569 | 0.036023 | -0.00922 | -0.037014 | 0.0006067 | -0.0075532 | 0.011158 | -0.03052 | -0.0016897 | -0.011929 | -0.00081178 | 0.10529 | 0.036621 | 0.073242 | 0.059509 | 0.11444 | 0.036621 | -0.091553 | 0.48981 | 0.56763 | 0.082397 | 0.58136 | 0.57678 | 0.07782 | 0 | 121.7834 | 121.6553 | -0.52643 | 121.7834 | 121.8063 | 0.15106 | -0.53558 | 121.8246 | 121.7468 | -0.059509 | 122.2366 | 121.8292 | 0.082397 | -0.064087 | 121.8613 | 121.8521 | 121.8201 | -0.73242 | 122.3282 | 122.3236 | 122.3145 | -0.64087
1691.0938 | 122.5204 | -121.6965 | 0.61798 | -0.0078584 | -0.011751 | 0.01186 | 0.039014 | -0.0098608 | -0.034451 | -0.0004613 | -0.0075532 | 0.014362 | -0.028384 | -0.0014761 | -0.011501 | -0.00059818 | 0.050354 | -0.045776 | -0.004578 | 0.027466 | 0.12817 | 0 | -0.10529 | 0.46692 | 0.56305 | 0.032043 | 0.58594 | 0.58594 | 0.073242 | 0 | 121.6965 | 121.5912 | -0.48981 | 121.6507 | 121.7239 | 0.13275 | -0.56763 | 121.7697 | 121.6965 | -0.032044 | 122.1634 | 121.7285 | 0.032043 | -0.032044 | 121.8246 | 121.7468 | 121.6919 | -0.72327 | 122.2824 | 122.2824 | 122.2595 | -0.61798
1692.8125 | 122.5525 | -121.7331 | 0.59052 | -0.00022891 | -0.010683 | 0.01421 | 0.033673 | -0.0083654 | -0.034451 | -0.0004613 | 7.627e-05 | 0.012439 | -0.03052 | -0.0023305 | -0.010006 | 0.00089722 | 0.073242 | -0.009155 | 0.018311 | 0.041199 | 0.1236 | 0.022888 | -0.09613 | 0.48981 | 0.57678 | 0.073242 | 0.59052 | 0.58136 | 0.054932 | 0 | 121.756 | 121.637 | -0.46692 | 121.7239 | 121.7743 | 0.13733 | -0.51727 | 121.788 | 121.7331 | 0 | 122.2229 | 121.8063 | 0.073242 | -0.009155 | 121.8567 | 121.8063 | 121.7514 | -0.68664 | 122.3236 | 122.3145 | 122.3099 | -0.59052
1694.5312 | 122.5296 | -121.7331 | 0.59967 | -0.015487 | -0.014101 | 0.012501 | 0.034528 | -0.010074 | -0.034451 | 0.0010339 | 7.627e-05 | 0.014789 | -0.031802 | -0.0040395 | -0.0093652 | 0.0019654 | 0.082397 | 0.009155 | 0.050354 | 0.050354 | 0.11444 | 0.018311 | -0.10529 | 0.54474 | 0.60883 | 0.073242 | 0.5722 | 0.55847 | 0.082397 | 0 | 121.7514 | 121.6278 | -0.48523 | 121.7422 | 121.7834 | 0.15564 | -0.51727 | 121.8155 | 121.7331 | -0.027465 | 122.2778 | 121.8063 | 0.073242 | -0.041198 | 121.8475 | 121.8155 | 121.7834 | -0.70496 | 122.3053 | 122.2916 | 122.3419 | -0.59967
1696.2969 | 122.4884 | -121.7422 | 0.61798 | -0.0078584 | -0.013888 | 0.012501 | 0.03346 | -0.0087926 | -0.033383 | 0.0018885 | -0.0075532 | 0.01543 | -0.030734 | -0.0019033 | -0.0093652 | 0.0019654 | 0.059509 | -0.036621 | 0.013733 | 0.013733 | 0.091553 | 0.013733 | -0.1236 | 0.46692 | 0.53558 | 0.022888 | 0.59509 | 0.59052 | 0.068665 | -0.018311 | 121.756 | 121.6187 | -0.52643 | 121.7056 | 121.756 | 0.13733 | -0.55847 | 121.8109 | 121.7239 | -0.022888 | 122.2092 | 121.7651 | 0.041199 | -0.027466 | 121.8338 | 121.8018 | 121.756 | -0.74158 | 122.3373 | 122.3328 | 122.2778 | -0.63629
1698.0781 | 122.5525 | -121.7239 | 0.6134 | -0.0078584 | -0.014956 | 0.012928 | 0.035596 | -0.010929 | -0.036801 | 0.0012477 | 0.0077058 | 0.012226 | -0.032656 | -0.0025443 | -0.010433 | 0.002179 | 0.032043 | -0.041199 | 0.013733 | 0.050354 | 0.13275 | 0.022888 | -0.10529 | 0.48981 | 0.60883 | 0.068665 | 0.59967 | 0.56763 | 0.073242 | -0.004578 | 121.7468 | 121.6187 | -0.48065 | 121.6827 | 121.7743 | 0.15564 | -0.58136 | 121.7972 | 121.7194 | -0.013733 | 122.2137 | 121.7926 | 0.073243 | -0.045776 | 121.8567 | 121.756 | 121.7377 | -0.71869 | 122.3236 | 122.2916 | 122.3328 | -0.61798
1699.8594 | 122.4335 | -121.7606 | 0.64545 | -0.00022891 | -0.018801 | 0.013783 | 0.036237 | -0.010929 | -0.038723 | -0.0004613 | 7.627e-05 | 0.010303 | -0.029666 | -0.0042531 | -0.014706 | 0.0047424 | 0.013733 | -0.027466 | 0.018311 | 0.009155 | 0.13733 | 0.022888 | -0.10071 | 0.45319 | 0.57678 | 0.045776 | 0.61798 | 0.60883 | 0.091553 | 0.009155 | 121.7834 | 121.6599 | -0.50812 | 121.7331 | 121.7697 | 0.10986 | -0.63171 | 121.8521 | 121.7697 | -0.027466 | 122.2137 | 121.8063 | 0.036621 | -0.036621 | 121.8979 | 121.7743 | 121.7789 | -0.74616 | 122.3785 | 122.3694 | 122.3373 | -0.63629
1701.6406 | 122.4655 | -121.7651 | 0.62714 | -0.0078584 | -0.01581 | 0.016133 | 0.036023 | -0.012211 | -0.041073 | 0.0006067 | -0.0075532 | 0.0088076 | -0.03287 | -0.0044669 | -0.015347 | 0.0011108 | 0.14191 | 0.12817 | 0.16479 | 0.10986 | 0.09613 | 0.059509 | -0.07782 | 0.56763 | 0.6958 | 0.19226 | 0.55847 | 0.53558 | 0.10986 | 0.022888 | 121.8246 | 121.6873 | -0.53101 | 121.8933 | 121.875 | 0.18768 | -0.48523 | 121.875 | 121.788 | -0.068664 | 122.3328 | 121.9574 | 0.16937 | -0.091553 | 121.8613 | 121.907 | 121.9299 | -0.70496 | 122.3236 | 122.3007 | 122.4609 | -0.60425
1703.375 | 122.5525 | -121.7285 | 0.59967 | -0.00022891 | -0.014529 | 0.012715 | 0.03645 | -0.010715 | -0.035733 | -0.0006751 | -0.0075532 | 0.01308 | -0.030093 | -0.0033987 | -0.011501 | -0.00059818 | 0.050354 | -0.054932 | 0 | 0.032043 | 0.12817 | 0.022888 | -0.11444 | 0.44861 | 0.55389 | 0.036621 | 0.59052 | 0.56763 | 0.086975 | 0.013733 | 121.7514 | 121.6141 | -0.4715 | 121.6736 | 121.7606 | 0.14648 | -0.54932 | 121.8155 | 121.7422 | -0.009155 | 122.1771 | 121.7651 | 0.022888 | -0.032043 | 121.8567 | 121.7789 | 121.7285 | -0.71411 | 122.319 | 122.2961 | 122.2824 | -0.58594
1705.1406 | 122.5479 | -121.7422 | 0.59967 | 0.0074006 | -0.016024 | 0.012928 | 0.036237 | -0.011997 | -0.035946 | -0.0008887 | 7.627e-05 | 0.011798 | -0.030093 | -0.0025443 | -0.012356 | -0.00081178 | 0.022888 | -0.054932 | 0.009155 | 0.013733 | 0.14191 | 0.013733 | -0.10986 | 0.4303 | 0.55389 | 0.027466 | 0.59509 | 0.58136 | 0.073242 | -0.018311 | 121.756 | 121.6324 | -0.45776 | 121.6873 | 121.756 | 0.1236 | -0.57678 | 121.8155 | 121.7239 | -0.004577 | 122.1725 | 121.7697 | 0.045777 | -0.01831 | 121.8842 | 121.7651 | 121.7514 | -0.70953 | 122.3373 | 122.3236 | 122.2961 | -0.61798
1706.8594 | 122.4701 | -121.8109 | 0.62256 | -0.00022891 | -0.021364 | 0.018055 | 0.034741 | -0.010502 | -0.042996 | -0.0011023 | 7.627e-05 | 0.0081668 | -0.032443 | -0.0029715 | -0.014706 | 0.002179 | 0.050354 | 0.027466 | 0.086975 | 0.045776 | 0.10529 | 0.041199 | -0.07782 | 0.50354 | 0.58136 | 0.14191 | 0.54932 | 0.53558 | 0.09613 | 0.036621 | 121.8521 | 121.7331 | -0.51727 | 121.8384 | 121.8567 | 0.1236 | -0.5722 | 121.907 | 121.8475 | -0.073243 | 122.3145 | 121.9528 | 0.10529 | -0.086976 | 121.9162 | 121.8613 | 121.8979 | -0.70038 | 122.3602 | 122.3465 | 122.3923 | -0.58594
1708.6406 | 122.4838 | -121.8018 | 0.62256 | -0.00022891 | -0.019015 | 0.015492 | 0.034314 | -0.012638 | -0.041287 | -0.0019567 | -0.0075532 | 0.0083804 | -0.032656 | -0.0057485 | -0.01257 | 0.0028198 | 0.045776 | 0.013733 | 0.086975 | 0.050354 | 0.082397 | 0.059509 | -0.073242 | 0.50812 | 0.57678 | 0.15564 | 0.56305 | 0.52643 | 0.10529 | 0.041199 | 121.8613 | 121.7285 | -0.54016 | 121.8155 | 121.8521 | 0.1236 | -0.57678 | 121.907 | 121.843 | -0.05951 | 122.3099 | 121.9574 | 0.11444 | -0.096131 | 121.8842 | 121.8475 | 121.8887 | -0.6958 | 122.3648 | 122.3282 | 122.3785 | -0.58136
1710.3594 | 122.4472 | -121.8292 | 0.61798 | -0.00022891 | -0.01581 | 0.014424 | 0.039227 | -0.011783 | -0.03851 | -0.0017431 | 7.627e-05 | 0.0096622 | -0.030947 | -0.0025443 | -0.015133 | -0.00081178 | 0.13275 | 0.10986 | 0.14648 | 0.10529 | 0.091553 | 0.059509 | -0.082397 | 0.53558 | 0.64087 | 0.16479 | 0.54932 | 0.52185 | 0.091553 | 0.045776 | 121.8887 | 121.7468 | -0.52643 | 121.9391 | 121.9345 | 0.18768 | -0.48523 | 121.9208 | 121.875 | -0.068665 | 122.3648 | 121.994 | 0.11902 | -0.09613 | 121.9208 | 121.962 | 121.9757 | -0.70038 | 122.3785 | 122.3511 | 122.4701 | -0.5722
1712.125 | 122.4976 | -121.8109 | 0.62256 | -0.00022891 | -0.026278 | 0.015706 | 0.031964 | -0.011143 | -0.043423 | -0.0028113 | 0.0077058 | 0.0083804 | -0.034793 | -0.0019033 | -0.012997 | 4.2822e-05 | 0.10529 | 0.073242 | 0.10986 | 0.082397 | 0.10529 | 0.045776 | -0.07782 | 0.55389 | 0.65918 | 0.1831 | 0.54474 | 0.53101 | 0.1236 | 0.054932 | 121.8567 | 121.7331 | -0.51727 | 121.8842 | 121.8933 | 0.16022 | -0.51727 | 121.9345 | 121.8658 | -0.07782 | 122.3648 | 121.994 | 0.12817 | -0.091553 | 121.9162 | 121.9162 | 121.9208 | -0.70038 | 122.3557 | 122.3419 | 122.4701 | -0.56763
1713.9062 | 122.4655 | -121.8018 | 0.63171 | 0.0074006 | -0.01581 | 0.014637 | 0.036878 | -0.008579 | -0.035946 | -0.0032385 | 0.0077058 | 0.011158 | -0.032016 | -0.0038259 | -0.013424 | -0.0023072 | 0.14191 | 0.07782 | 0.13733 | 0.10529 | 0.082397 | 0.050354 | -0.07782 | 0.55389 | 0.64545 | 0.15564 | 0.56305 | 0.53558 | 0.11902 | 0.050354 | 121.8521 | 121.7239 | -0.54932 | 121.8796 | 121.907 | 0.18311 | -0.48981 | 121.9208 | 121.8521 | -0.068665 | 122.3557 | 121.9574 | 0.10529 | -0.096131 | 121.8842 | 121.9437 | 121.9391 | -0.70953 | 122.3648 | 122.3373 | 122.4472 | -0.58136
1715.6406 | 122.4472 | -121.8018 | 0.62714 | -0.00022891 | -0.016024 | 0.012501 | 0.037732 | -0.008579 | -0.036587 | -0.0021703 | 7.627e-05 | 0.011371 | -0.029025 | -0.0014761 | -0.013638 | -0.0014526 | 0.073242 | -0.018311 | 0.041199 | 0.022888 | 0.10986 | 0.013733 | -0.10986 | 0.46692 | 0.53558 | 0.045776 | 0.59967 | 0.59052 | 0.086975 | 0.004578 | 121.8155 | 121.6919 | -0.51727 | 121.7834 | 121.8246 | 0.13275 | -0.55389 | 121.8887 | 121.8063 | -0.027466 | 122.2687 | 121.8475 | 0.041198 | -0.036621 | 121.9116 | 121.875 | 121.843 | -0.737 | 122.4014 | 122.3923 | 122.3373 | -0.62256
1717.4375 | 122.4609 | -121.8521 | 0.62256 | -0.00022891 | -0.019015 | 0.012501 | 0.034528 | -0.011997 | -0.037228 | -0.0011023 | -0.0075532 | 0.0098758 | -0.029025 | -0.0010489 | -0.014279 | 0.00047002 | 0.086975 | 0.059509 | 0.07782 | 0.059509 | 0.09613 | 0.059509 | -0.068665 | 0.53558 | 0.57678 | 0.1236 | 0.53101 | 0.53558 | 0.11444 | 0.045776 | 121.9116 | 121.7834 | -0.52643 | 121.9116 | 121.9116 | 0.12817 | -0.53558 | 121.9666 | 121.8979 | -0.091553 | 122.3877 | 121.9757 | 0.07782 | -0.086976 | 121.9482 | 121.9391 | 121.9299 | -0.69122 | 122.3831 | 122.3877 | 122.4289 | -0.57678
1719.2188 | 122.5754 | -121.7834 | 0.5722 | -0.00022891 | -0.019655 | 0.013997 | 0.034741 | -0.011356 | -0.034878 | 0.0001795 | 7.627e-05 | 0.010944 | -0.03287 | -0.0031851 | -0.0082972 | -0.001239 | 0.16479 | 0.064087 | 0.1236 | 0.086975 | 0.086975 | 0.059509 | -0.068665 | 0.58136 | 0.60425 | 0.16479 | 0.52185 | 0.50812 | 0.12817 | 0.050354 | 121.843 | 121.7148 | -0.48523 | 121.8475 | 121.8704 | 0.15564 | -0.40741 | 121.9116 | 121.8338 | -0.050354 | 122.3648 | 121.9482 | 0.11444 | -0.064087 | 121.8704 | 121.9482 | 121.907 | -0.64087 | 122.3053 | 122.2916 | 122.3877 | -0.52185
1721.0156 | 122.5296 | -121.8292 | 0.58136 | -0.00022891 | -0.017519 | 0.012715 | 0.034955 | -0.011356 | -0.03381 | 0.0025293 | 7.627e-05 | 0.0098758 | -0.030734 | -0.0025443 | -0.0097924 | 0.00089722 | 0.14191 | 0.09613 | 0.14191 | 0.09613 | 0.07782 | 0.054932 | -0.064087 | 0.58594 | 0.62714 | 0.17395 | 0.52643 | 0.50812 | 0.10529 | 0.050354 | 121.8842 | 121.7651 | -0.50354 | 121.9254 | 121.9254 | 0.16022 | -0.43945 | 121.9345 | 121.8796 | -0.054932 | 122.4152 | 122.0032 | 0.1236 | -0.073242 | 121.907 | 121.9711 | 121.9711 | -0.64545 | 122.3557 | 122.3373 | 122.4564 | -0.53101
1722.75 | 122.493 | -121.8613 | 0.59052 | -0.00022891 | -0.01816 | 0.013569 | 0.032819 | -0.010288 | -0.03851 | -3.4096e-05 | 0.0077058 | 0.0090214 | -0.03287 | -0.0021169 | -0.010861 | -0.00038438 | 0.14191 | 0.09613 | 0.13733 | 0.086975 | 0.07782 | 0.059509 | -0.059509 | 0.56763 | 0.59967 | 0.17395 | 0.53101 | 0.54932 | 0.10071 | 0.050354 | 121.9208 | 121.8018 | -0.5127 | 121.9574 | 121.9482 | 0.14648 | -0.44861 | 121.962 | 121.9116 | -0.059509 | 122.4289 | 122.0352 | 0.1236 | -0.041199 | 121.9391 | 122.0032 | 121.9986 | -0.65002 | 122.3923 | 122.4106 | 122.4609 | -0.54016
1724.5312 | 122.4792 | -121.8384 | 0.58136 | -0.00022891 | -0.014101 | 0.013783 | 0.037732 | -0.011143 | -0.036374 | 0.0010339 | 7.627e-05 | 0.014148 | -0.029452 | -0.0016897 | -0.012356 | -0.00017078 | 0.041199 | -0.032043 | 0.027466 | 0.009155 | 0.13733 | 0.036621 | -0.10529 | 0.4303 | 0.5127 | 0.054932 | 0.55847 | 0.54474 | 0.064087 | 0.013733 | 121.875 | 121.7331 | -0.44403 | 121.8063 | 121.8475 | 0.11444 | -0.54016 | 121.9025 | 121.8521 | -0.022888 | 122.2687 | 121.8933 | 0.041199 | -0.036621 | 121.9757 | 121.8796 | 121.8658 | -0.68665 | 122.3969 | 122.3831 | 122.3511 | -0.56763
1726.2969 | 122.5754 | -121.8109 | 0.55389 | -0.00022891 | -0.015383 | 0.015278 | 0.037091 | -0.0094336 | -0.037655 | -3.4096e-05 | -0.0075532 | 0.010944 | -0.030947 | 0.00087369 | -0.011715 | 0.00089722 | 0.050354 | -0.036621 | 0 | 0.022888 | 0.11902 | 0.013733 | -0.11444 | 0.43488 | 0.50354 | 0.054932 | 0.56305 | 0.54932 | 0.086975 | 0.013733 | 121.8246 | 121.6965 | -0.43488 | 121.7743 | 121.8338 | 0.13733 | -0.50354 | 121.8979 | 121.8246 | 0.009155 | 122.2458 | 121.8658 | 0.041199 | -0.004578 | 121.9299 | 121.8613 | 121.8109 | -0.66834 | 122.374 | 122.3602 | 122.3145 | -0.54016
1728.0625 | 122.4792 | -121.8567 | 0.58136 | -0.00022891 | -0.016451 | 0.013783 | 0.040082 | -0.010502 | -0.037655 | -0.0004613 | -0.015182 | 0.0094486 | -0.03052 | -0.00040791 | -0.013424 | 4.2822e-05 | 0.032043 | -0.027466 | 0.027466 | 0.018311 | 0.14191 | 0.022888 | -0.11444 | 0.41657 | 0.49896 | 0.064087 | 0.57678 | 0.53558 | 0.068665 | 0.018311 | 121.8796 | 121.7422 | -0.43945 | 121.8292 | 121.875 | 0.13275 | -0.54932 | 121.9254 | 121.875 | -0.004578 | 122.2733 | 121.9208 | 0.045776 | -0.045777 | 121.9986 | 121.8887 | 121.8842 | -0.6958 | 122.4335 | 122.3923 | 122.3557 | -0.56305
1729.7812 | 122.612 | -121.8109 | 0.55847 | 0.0074006 | -0.013888 | 0.011006 | 0.036664 | -0.010929 | -0.034665 | 0.0025293 | 7.627e-05 | 0.012653 | -0.029666 | -0.0023305 | -0.012783 | -0.00059818 | 0.073242 | -0.027466 | 0.018311 | 0.041199 | 0.13275 | 0.022888 | -0.11902 | 0.4715 | 0.54932 | 0.09613 | 0.54932 | 0.54016 | 0.10529 | 0.032043 | 121.8338 | 121.6919 | -0.42572 | 121.7834 | 121.8521 | 0.16022 | -0.48523 | 121.9162 | 121.843 | -0.009156 | 122.2824 | 121.907 | 0.064087 | -0.018311 | 121.9437 | 121.8842 | 121.8292 | -0.67749 | 122.3602 | 122.3511 | 122.3602 | -0.52643
1731.5625 | 122.493 | -121.8887 | 0.58594 | 0.0074006 | -0.021792 | 0.012715 | 0.034528 | -0.011356 | -0.042141 | -0.0002477 | -0.0075532 | 0.0081668 | -0.033084 | -0.00083531 | -0.014492 | 0.002179 | 0.073242 | 0.045776 | 0.091553 | 0.054932 | 0.091553 | 0.054932 | -0.07782 | 0.48981 | 0.55389 | 0.13275 | 0.5127 | 0.5127 | 0.12817 | 0.036621 | 121.9437 | 121.8109 | -0.49438 | 121.9345 | 121.9437 | 0.13275 | -0.5127 | 122.0169 | 121.9254 | -0.073242 | 122.3785 | 122.0215 | 0.09613 | -0.073242 | 121.9803 | 121.962 | 121.9803 | -0.66376 | 122.4014 | 122.4014 | 122.4426 | -0.54932
1733.3438 | 122.4792 | -121.8704 | 0.58136 | -0.0078584 | -0.016024 | 0.013997 | 0.035382 | -0.008579 | -0.037228 | 0.0010339 | -0.0075532 | 0.0096622 | -0.033297 | -0.0033987 | -0.011501 | 0.0017518 | 0.082397 | 0.036621 | 0.059509 | 0.050354 | 0.12817 | 0.027466 | -0.10986 | 0.44403 | 0.53101 | 0.064087 | 0.53558 | 0.54016 | 0.086975 | 0.022888 | 121.8979 | 121.7606 | -0.45319 | 121.907 | 121.9208 | 0.16022 | -0.49896 | 121.9574 | 121.8933 | -0.045777 | 122.3145 | 121.9345 | 0.041199 | -0.041199 | 121.9986 | 121.9528 | 121.9299 | -0.69122 | 122.406 | 122.4106 | 122.4014 | -0.55847
1735.125 | 122.5662 | -121.8246 | 0.56305 | 0.0074006 | -0.013888 | 0.011433 | 0.034314 | -0.012424 | -0.034665 | 0.0018885 | 7.627e-05 | 0.014576 | -0.03052 | -0.0023305 | -0.0095788 | -0.0025208 | 0.11902 | 0.013733 | 0.059509 | 0.045776 | 0.11902 | 0.032043 | -0.10071 | 0.4715 | 0.53558 | 0.082397 | 0.55389 | 0.52185 | 0.09613 | 0.013733 | 121.8567 | 121.7239 | -0.44403 | 121.8384 | 121.8704 | 0.14648 | -0.44403 | 121.9208 | 121.8384 | -0.009155 | 122.2961 | 121.907 | 0.068664 | -0.041198 | 121.9437 | 121.9437 | 121.8842 | -0.66376 | 122.3785 | 122.3465 | 122.3602 | -0.54932
1736.8594 | 122.5021 | -121.8842 | 0.59509 | 0.0074006 | -0.02286 | 0.013142 | 0.035169 | -0.010929 | -0.044278 | -0.0004613 | -0.0075532 | 0.008594 | -0.032229 | -0.0021169 | -0.013638 | 0.0026062 | 0.064087 | 0.036621 | 0.09613 | 0.054932 | 0.086975 | 0.036621 | -0.086975 | 0.46234 | 0.56305 | 0.12817 | 0.50812 | 0.50812 | 0.10986 | 0.041199 | 121.9208 | 121.7972 | -0.50812 | 121.9208 | 121.9391 | 0.14191 | -0.53101 | 121.994 | 121.9254 | -0.086975 | 122.3465 | 122.0123 | 0.086975 | -0.086975 | 121.9711 | 121.9482 | 121.9803 | -0.68207 | 122.3923 | 122.3923 | 122.4472 | -0.55389
1738.6406 | 122.5845 | -121.8338 | 0.55847 | -0.015487 | -0.014315 | 0.013356 | 0.035596 | -0.0077246 | -0.035305 | -0.0013159 | 0.0077058 | 0.011585 | -0.030093 | -0.0027579 | -0.010861 | -0.0014526 | 0.045776 | -0.041199 | 0.004578 | 0.004578 | 0.13733 | 0.018311 | -0.11902 | 0.39368 | 0.49896 | 0.059509 | 0.55389 | 0.54474 | 0.091553 | 0.013733 | 121.8521 | 121.7148 | -0.42114 | 121.7926 | 121.8384 | 0.1236 | -0.5127 | 121.9254 | 121.8475 | -0.004578 | 122.2275 | 121.8933 | 0.045776 | -0.013733 | 121.9711 | 121.8796 | 121.8384 | -0.67749 | 122.3877 | 122.3785 | 122.3328 | -0.54474
1740.4375 | 122.4838 | -121.9025 | 0.60883 | 0.0074006 | -0.018587 | 0.015065 | 0.037305 | -0.010715 | -0.040005 | -0.0011023 | 7.627e-05 | 0.0094486 | -0.033511 | -0.0044669 | -0.015347 | 4.2822e-05 | 0.1236 | 0.10071 | 0.15106 | 0.091553 | 0.086975 | 0.045776 | -0.073242 | 0.49896 | 0.63629 | 0.1831 | 0.51727 | 0.50354 | 0.1236 | 0.041199 | 121.9482 | 121.8292 | -0.52185 | 122.0032 | 121.994 | 0.16479 | -0.48523 | 122.0261 | 121.9437 | -0.091553 | 122.4014 | 122.0856 | 0.14191 | -0.10529 | 121.9894 | 122.0261 | 122.0535 | -0.68207 | 122.4197 | 122.406 | 122.5388 | -0.56763
1742.1562 | 122.644 | -121.843 | 0.56763 | -0.00022891 | -0.011111 | 0.01186 | 0.039227 | -0.011356 | -0.034665 | -3.4096e-05 | 7.627e-05 | 0.01308 | -0.02817 | -0.0019033 | -0.01257 | 0.002179 | 0.054932 | -0.054932 | 0.013733 | 0.013733 | 0.12817 | 0.027466 | -0.11444 | 0.48523 | 0.5127 | 0.082397 | 0.54474 | 0.53558 | 0.09613 | 0.027466 | 121.8704 | 121.7285 | -0.43945 | 121.788 | 121.8567 | 0.12817 | -0.5127 | 121.9391 | 121.8704 | -0.022888 | 122.3282 | 121.9254 | 0.054931 | -0.032044 | 121.9711 | 121.8979 | 121.8567 | -0.68207 | 122.3877 | 122.3785 | 122.3557 | -0.54016
1743.9375 | 122.6074 | -121.8567 | 0.5722 | -0.0078584 | -0.014742 | 0.013783 | 0.037091 | -0.012424 | -0.03381 | 0.0021021 | -0.0075532 | 0.01308 | -0.031161 | -0.0014761 | -0.011074 | -0.0010254 | 0.086975 | 0.027466 | 0.050354 | 0.050354 | 0.11444 | 0.036621 | -0.12817 | 0.47607 | 0.55847 | 0.086975 | 0.55389 | 0.51727 | 0.091553 | 0.027466 | 121.8933 | 121.7285 | -0.45776 | 121.8842 | 121.907 | 0.17853 | -0.48523 | 121.9482 | 121.8842 | -0.018311 | 122.3328 | 121.9437 | 0.059509 | -0.054932 | 121.9711 | 121.9437 | 121.907 | -0.70038 | 122.4106 | 122.374 | 122.4152 | -0.54474
1745.7031 | 122.6624 | -121.8613 | 0.54932 | -0.00022891 | -0.01581 | 0.01421 | 0.034528 | -0.010929 | -0.036801 | 0.0003931 | 7.627e-05 | 0.010089 | -0.031161 | -0.0027579 | -0.011074 | 0.00025642 | 0.036621 | -0.013733 | 0.032043 | 0.018311 | 0.1236 | 0.041199 | -0.10986 | 0.47607 | 0.5127 | 0.10529 | 0.51727 | 0.51727 | 0.10071 | 0.018311 | 121.9025 | 121.7514 | -0.42572 | 121.8475 | 121.8796 | 0.12817 | -0.5127 | 121.962 | 121.8796 | -0.032043 | 122.3373 | 121.9666 | 0.086975 | -0.032043 | 121.9849 | 121.8979 | 121.8933 | -0.65918 | 122.3785 | 122.3785 | 122.374 | -0.53101
1747.4844 | 122.5296 | -121.875 | 0.59052 | -0.0078584 | -0.014742 | 0.01421 | 0.036878 | -0.010074 | -0.038723 | -3.4096e-05 | -0.0075532 | 0.012867 | -0.030734 | -0.0029715 | -0.014706 | 0.00047002 | 0.004578 | -0.022888 | 0.009155 | 0.009155 | 0.13733 | 0.009155 | -0.11902 | 0.39368 | 0.50354 | 0.045776 | 0.54932 | 0.53558 | 0.086975 | 0.004578 | 121.8842 | 121.756 | -0.45319 | 121.8521 | 121.8842 | 0.12817 | -0.58594 | 121.962 | 121.8796 | -0.041199 | 122.2687 | 121.9208 | 0.041198 | -0.054932 | 122.0123 | 121.8796 | 121.8842 | -0.70953 | 122.4243 | 122.4106 | 122.3785 | -0.58594
1749.2031 | 122.5479 | -121.8979 | 0.60425 | -0.0078584 | -0.017519 | 0.016774 | 0.03645 | -0.01157 | -0.041073 | -0.0004613 | -0.0075532 | 0.0090214 | -0.033084 | -0.0025443 | -0.01556 | 0.003888 | 0.073242 | 0.041199 | 0.086975 | 0.073242 | 0.10071 | 0.045776 | -0.064087 | 0.48065 | 0.55847 | 0.16022 | 0.51727 | 0.49439 | 0.10529 | 0.050354 | 121.9437 | 121.8338 | -0.50354 | 121.9391 | 121.9711 | 0.13733 | -0.53101 | 122.0032 | 121.9482 | -0.086975 | 122.3785 | 122.0581 | 0.10986 | -0.10986 | 121.9986 | 121.9711 | 121.9849 | -0.66834 | 122.4152 | 122.3923 | 122.4564 | -0.55389
1750.9844 | 122.5296 | -121.9162 | 0.5722 | -0.0078584 | -0.016878 | 0.014637 | 0.037946 | -0.00922 | -0.040219 | 0.0001795 | -0.0075532 | 0.010944 | -0.033084 | -0.0044669 | -0.015988 | 0.0011108 | 0.082397 | 0.009155 | 0.086975 | 0.059509 | 0.10529 | 0.045776 | -0.068665 | 0.44861 | 0.53101 | 0.15106 | 0.50354 | 0.49439 | 0.12817 | 0.041199 | 121.962 | 121.8475 | -0.46692 | 121.9254 | 121.9757 | 0.12817 | -0.48981 | 122.0444 | 121.9574 | -0.068665 | 122.3648 | 122.0673 | 0.10986 | -0.07782 | 122.0215 | 121.9986 | 122.0032 | -0.64087 | 122.4197 | 122.4106 | 122.4472 | -0.53101
1752.7812 | 122.6212 | -121.8567 | 0.52643 | -0.00022891 | -0.016451 | 0.013142 | 0.034955 | -0.010288 | -0.032742 | 0.0003931 | 7.627e-05 | 0.014789 | -0.035647 | -0.0029715 | -0.0093652 | -0.00038438 | 0.11902 | 0.009155 | 0.041199 | 0.059509 | 0.11444 | 0.032043 | -0.1236 | 0.43945 | 0.52643 | 0.086975 | 0.52643 | 0.49439 | 0.10986 | 0.022888 | 121.8887 | 121.7331 | -0.41199 | 121.8658 | 121.9162 | 0.1831 | -0.40741 | 121.9666 | 121.8796 | 0 | 122.2961 | 121.9437 | 0.064087 | -0.032043 | 121.9711 | 121.9757 | 121.8979 | -0.65002 | 122.3831 | 122.3511 | 122.3831 | -0.50354
1754.5781 | 122.6669 | -121.8613 | 0.53101 | -0.00022891 | -0.016024 | 0.012715 | 0.033673 | -0.011356 | -0.035305 | 0.0016749 | 7.627e-05 | 0.012653 | -0.034579 | -0.0019033 | -0.0085108 | 0.00047002 | 0.059509 | -0.050354 | -0.004578 | 0.018311 | 0.13733 | 0.027466 | -0.1236 | 0.43945 | 0.44403 | 0.073242 | 0.50812 | 0.49896 | 0.11902 | 0.032043 | 121.8887 | 121.7377 | -0.39368 | 121.8109 | 121.8796 | 0.14191 | -0.4715 | 121.9803 | 121.8933 | -0.022888 | 122.3007 | 121.9345 | 0.041199 | -0.032044 | 121.9986 | 121.9208 | 121.8567 | -0.6546 | 122.3694 | 122.3602 | 122.3053 | -0.49896
1756.2812 | 122.4747 | -121.9299 | 0.5722 | -0.00022891 | -0.019228 | 0.014424 | 0.036237 | -0.012211 | -0.039792 | -0.0019567 | -0.0075532 | 0.011371 | -0.03522 | -0.0038259 | -0.01257 | 0.0013244 | 0.11902 | 0.086975 | 0.1236 | 0.09613 | 0.082397 | 0.045776 | -0.064087 | 0.44403 | 0.56305 | 0.12817 | 0.48523 | 0.49896 | 0.10986 | 0.041199 | 121.9757 | 121.8658 | -0.48981 | 122.0169 | 122.0261 | 0.16022 | -0.45319 | 122.0398 | 121.9711 | -0.086976 | 122.374 | 122.0581 | 0.086975 | -0.073243 | 122.0123 | 122.049 | 122.0535 | -0.63629 | 122.4152 | 122.4289 | 122.493 | -0.53101
1758.0469 | 122.493 | -121.9574 | 0.56305 | -0.015487 | -0.019442 | 0.014637 | 0.035596 | -0.0083654 | -0.038723 | -0.0015295 | 7.627e-05 | 0.011158 | -0.030307 | -0.0040395 | -0.013638 | -0.0016662 | 0.12817 | 0.082397 | 0.13733 | 0.10986 | 0.09613 | 0.059509 | -0.082397 | 0.46692 | 0.5722 | 0.16937 | 0.48523 | 0.46692 | 0.10529 | 0.036621 | 122.0169 | 121.875 | -0.46692 | 122.0398 | 122.0673 | 0.19226 | -0.43488 | 122.0627 | 121.994 | -0.07782 | 122.4243 | 122.1268 | 0.13275 | -0.09613 | 122.0535 | 122.0856 | 122.0947 | -0.64545 | 122.4426 | 122.4243 | 122.5296 | -0.52643
1759.8281 | 122.5525 | -121.962 | 0.53101 | -0.00022891 | -0.019228 | 0.013356 | 0.034741 | -0.0098608 | -0.037014 | 0.0010339 | -0.0075532 | 0.011158 | -0.034579 | -0.0044669 | -0.010861 | -0.0014526 | 0.14648 | 0.068665 | 0.13733 | 0.09613 | 0.073242 | 0.073242 | -0.050354 | 0.50354 | 0.56763 | 0.18768 | 0.4715 | 0.45776 | 0.1236 | 0.059509 | 122.0352 | 121.9116 | -0.45776 | 122.0306 | 122.0581 | 0.14648 | -0.38452 | 122.0856 | 122.0215 | -0.059509 | 122.4655 | 122.1497 | 0.12817 | -0.073242 | 122.0352 | 122.1085 | 122.0993 | -0.58136 | 122.4335 | 122.4197 | 122.5296 | -0.4715
1761.6094 | 122.5891 | -121.9391 | 0.52643 | -0.00022891 | -0.013888 | 0.013569 | 0.03346 | -0.0094336 | -0.031887 | 0.0001795 | -0.030441 | 0.014789 | -0.033725 | -0.0010489 | -0.007229 | -0.0010254 | 0.10529 | -0.009155 | 0.027466 | 0.036621 | 0.1236 | 0.022888 | -0.11444 | 0.37994 | 0.42114 | 0.041199 | 0.48981 | 0.49439 | 0.091553 | 0.027466 | 121.962 | 121.8246 | -0.40283 | 121.9299 | 121.9757 | 0.15106 | -0.42114 | 122.0306 | 121.9666 | -0.036621 | 122.319 | 121.9803 | 0.013733 | -0.032043 | 122.0627 | 122.0444 | 121.9666 | -0.64087 | 122.4289 | 122.4335 | 122.3602 | -0.49896
1763.3906 | 122.5388 | -121.9711 | 0.52643 | 0.0074006 | -0.017946 | 0.013142 | 0.037091 | -0.0081518 | -0.03851 | -0.0013159 | 7.627e-05 | 0.008594 | -0.032229 | -0.0016897 | -0.014492 | 0.00068362 | 0.13733 | 0.07782 | 0.14648 | 0.07782 | 0.10071 | 0.050354 | -0.073242 | 0.48981 | 0.54474 | 0.19226 | 0.45776 | 0.43945 | 0.13275 | 0.068665 | 122.0215 | 121.8979 | -0.42572 | 122.049 | 122.049 | 0.15106 | -0.3891 | 122.1039 | 122.0398 | -0.068664 | 122.4609 | 122.1634 | 0.1236 | -0.086975 | 122.0718 | 122.1085 | 122.1176 | -0.59967 | 122.4289 | 122.4106 | 122.5159 | -0.45776
1765.1719 | 122.5571 | -121.9574 | 0.56763 | -0.0078584 | -0.022219 | 0.013783 | 0.032819 | -0.014133 | -0.037869 | 0.0012477 | 7.627e-05 | 0.0090214 | -0.030093 | -0.0031851 | -0.011715 | 0.00089722 | 0.14191 | 0.091553 | 0.12817 | 0.091553 | 0.086975 | 0.068665 | -0.064087 | 0.5127 | 0.55389 | 0.16022 | 0.46234 | 0.45319 | 0.13733 | 0.064087 | 122.0261 | 121.8933 | -0.48065 | 122.049 | 122.049 | 0.15564 | -0.42572 | 122.0947 | 122.0215 | -0.10529 | 122.4701 | 122.1176 | 0.09613 | -0.11444 | 122.0444 | 122.0993 | 122.0856 | -0.63171 | 122.4197 | 122.4106 | 122.5113 | -0.50354
1766.8906 | 122.6486 | -121.8796 | 0.58136 | -0.0078584 | -0.016024 | 0.013356 | 0.033673 | -0.010929 | -0.037014 | -0.0013159 | 0.0077058 | 0.010089 | -0.030307 | -0.0019033 | -0.010647 | 0.00068362 | 0.14191 | 0.082397 | 0.11444 | 0.10986 | 0.091553 | 0.073242 | -0.054932 | 0.54474 | 0.19226 | 0.17853 | 0.49439 | 0.48065 | 0.14648 | 0.064087 | 121.9528 | 121.8246 | -0.48981 | 121.962 | 121.9894 | 0.16479 | -0.43945 | 122.0261 | 121.9437 | -0.086975 | 122.4243 | 122.0581 | 0.11444 | -0.10071 | 121.9711 | 122.0215 | 121.994 | -0.63629 | 122.374 | 122.3602 | 122.0718 | -0.51727
1768.6719 | 122.6303 | -121.8933 | 0.54474 | -0.00022891 | -0.014956 | 0.012074 | 0.037732 | -0.010074 | -0.034878 | 0.0003931 | 7.627e-05 | 0.012226 | -0.031802 | -0.0025443 | -0.01022 | -0.0023072 | 0.10986 | 0.009155 | 0.064087 | 0.054932 | 0.10529 | 0.050354 | -0.11444 | 0.47607 | 0.15564 | 0.10071 | 0.56305 | 0.5127 | 0.11902 | 0.036621 | 121.9437 | 121.7789 | -0.43945 | 121.9025 | 121.9482 | 0.16937 | -0.43488 | 122.0123 | 121.9299 | 0.01831 | 122.3694 | 121.994 | 0.064087 | -0.032044 | 121.9986 | 122.0032 | 121.9574 | -0.65918 | 122.4564 | 122.406 | 122.049 | -0.50812
1770.3906 | 122.5937 | -121.9116 | 0.57678 | -0.00022891 | -0.014315 | 0.012715 | 0.035596 | -0.010074 | -0.033596 | 0.0018885 | -0.0075532 | 0.012439 | -0.029666 | -0.0031851 | -0.0091516 | 0.00047002 | 0.041199 | -0.068665 | 0.009155 | 0.018311 | 0.10071 | 0.027466 | -0.12817 | 0.39368 | 0.068665 | 0.027466 | 0.56305 | 0.56305 | 0.10529 | 0.032043 | 121.9391 | 121.7834 | -0.47607 | 121.843 | 121.9299 | 0.14649 | -0.53558 | 122.0169 | 121.9437 | -0.013733 | 122.3053 | 121.9391 | -0.004577 | -0.013733 | 122.0123 | 121.9528 | 121.9208 | -0.70496 | 122.4747 | 122.4747 | 121.9803 | -0.54474
1772.1562 | 122.5342 | -121.9345 | 0.59052 | -0.023117 | -0.015383 | 0.01421 | 0.040296 | -0.0079382 | -0.040646 | 0.0001795 | 0.0077058 | 0.0079532 | -0.02817 | -0.0016897 | -0.014919 | 0.0028198 | 0.036621 | -0.004578 | 0.050354 | 0.022888 | 0.13275 | 0.032043 | -0.10986 | 0.41657 | 0.12817 | 0.073242 | 0.54932 | 0.51727 | 0.10071 | 0.018311 | 121.9666 | 121.8246 | -0.45776 | 121.9299 | 121.9574 | 0.13275 | -0.55389 | 122.0352 | 121.9528 | -0.041199 | 122.3511 | 122.0078 | 0.054931 | -0.073242 | 122.0673 | 121.9711 | 121.9849 | -0.70038 | 122.4838 | 122.4518 | 122.0627 | -0.5722
1773.875 | 122.6074 | -121.9116 | 0.55389 | -0.00022891 | -0.015169 | 0.012288 | 0.032819 | -0.010715 | -0.032315 | 0.0006067 | 7.627e-05 | 0.012226 | -0.029879 | -0.0010489 | -0.008938 | -0.00038438 | 0.054932 | -0.013733 | 0.027466 | 0.032043 | 0.14191 | 0.027466 | -0.10529 | 0.41657 | 0.10529 | 0.032043 | 0.53101 | 0.53558 | 0.10071 | 0.018311 | 121.9391 | 121.8063 | -0.41199 | 121.8979 | 121.9437 | 0.13733 | -0.49896 | 122.0123 | 121.9299 | -0.022888 | 122.3282 | 121.9437 | 0.013732 | -0.018311 | 122.0535 | 121.9666 | 121.9391 | -0.65918 | 122.4426 | 122.4472 | 122.0169 | -0.53558
1775.6719 | 122.6166 | -121.9162 | 0.5722 | -0.0078584 | -0.014315 | 0.013783 | 0.035169 | -0.01157 | -0.036374 | 0.0010339 | -0.0075532 | 0.012226 | -0.029879 | -0.00083531 | -0.010647 | 0.0019654 | 0.036621 | -0.059509 | 0.018311 | 0.009155 | 0.13275 | 0.018311 | -0.11444 | 0.37537 | 0.068665 | 0.022888 | 0.54016 | 0.52643 | 0.091553 | 0.009155 | 121.9345 | 121.8018 | -0.43945 | 121.8567 | 121.9254 | 0.1236 | -0.53558 | 122.0078 | 121.9254 | -0.032044 | 122.2916 | 121.9391 | 0.013733 | -0.045777 | 122.049 | 121.9528 | 121.9345 | -0.68665 | 122.4564 | 122.4426 | 121.9849 | -0.56305
1777.4531 | 122.6212 | -121.9208 | 0.53558 | -0.0078584 | -0.013247 | 0.013783 | 0.039655 | -0.012211 | -0.037228 | 0.0014613 | 0.0077058 | 0.010517 | -0.026889 | -0.00019431 | -0.01556 | 0.0011108 | 0.018311 | -0.045776 | 0 | 0.036621 | 0.1236 | 0.004578 | -0.10986 | 0.37994 | 0.10529 | 0.054932 | 0.52185 | 0.51727 | 0.091553 | 0.009155 | 121.9254 | 121.8109 | -0.41199 | 121.875 | 121.9574 | 0.14648 | -0.51727 | 122.0123 | 121.9299 | -0.013732 | 122.3007 | 121.9757 | 0.045777 | -0.01831 | 122.0444 | 121.9391 | 121.9208 | -0.64545 | 122.4426 | 122.438 | 122.0261 | -0.52643
1779.2188 | 122.5433 | -121.9849 | 0.56305 | -0.00022891 | -0.015597 | 0.015278 | 0.036664 | -0.0083654 | -0.038296 | 0.0003931 | 7.627e-05 | 0.0083804 | -0.029452 | -0.0027579 | -0.014706 | -0.0010254 | 0.018311 | -0.009155 | 0.032043 | 0.027466 | 0.12817 | 0.022888 | -0.10529 | 0.38452 | 0.11444 | 0.082397 | 0.51727 | 0.50812 | 0.091553 | 0.004578 | 122.0078 | 121.8796 | -0.43488 | 121.9757 | 122.0123 | 0.13275 | -0.54474 | 122.0764 | 121.9894 | -0.045776 | 122.3694 | 122.0673 | 0.077819 | -0.054931 | 122.113 | 122.0032 | 122.0169 | -0.66834 | 122.5021 | 122.493 | 122.0993 | -0.55847
1780.9531 | 122.6669 | -121.9574 | 0.48523 | 0.0074006 | -0.016238 | 0.013997 | 0.035809 | -0.012424 | -0.036587 | 0.0003931 | -0.0075532 | 0.013507 | -0.032656 | -0.00083531 | -0.011715 | -0.0018798 | 0.068665 | 0.022888 | 0.050354 | 0.054932 | 0.13275 | 0.036621 | -0.09613 | 0.40741 | 0.45319 | 0.09613 | 0.45776 | 0.46692 | 0.073242 | 0 | 121.994 | 121.8613 | -0.35248 | 121.9803 | 122.0123 | 0.15106 | -0.41656 | 122.0306 | 121.9574 | -0.027465 | 122.3648 | 122.0535 | 0.09613 | -0.01831 | 122.0901 | 122.0261 | 122.0078 | -0.58136 | 122.4152 | 122.4243 | 122.4106 | -0.48523
1782.7344 | 122.6166 | -121.9849 | 0.51727 | -0.0078584 | -0.013674 | 0.013356 | 0.032178 | -0.012638 | -0.035946 | 0.0006067 | 7.627e-05 | 0.013294 | -0.032443 | -0.0012625 | -0.0093652 | 0.002179 | 0.086975 | 0.013733 | 0.045776 | 0.050354 | 0.12817 | 0.032043 | -0.09613 | 0.38452 | 0.31128 | 0.054932 | 0.49439 | 0.48065 | 0.073242 | 0.018311 | 122.0169 | 121.8887 | -0.3891 | 121.9986 | 122.0352 | 0.14648 | -0.4303 | 122.0581 | 122.0032 | -0.022888 | 122.3694 | 122.0398 | 0.036621 | -0.036621 | 122.113 | 122.0718 | 122.0306 | -0.6134 | 122.4792 | 122.4655 | 122.2961 | -0.49896
1784.5156 | 122.5754 | -121.9849 | 0.55389 | -0.015487 | -0.019015 | 0.015278 | 0.035596 | -0.011783 | -0.043637 | -0.0011023 | 7.627e-05 | 0.0062442 | -0.03287 | -0.0029715 | -0.014919 | 0.0011108 | 0.045776 | 0.022888 | 0.073242 | 0.059509 | 0.10071 | 0.050354 | -0.073242 | 0.42114 | 0.16479 | 0.15106 | 0.4715 | 0.4715 | 0.10529 | 0.027466 | 122.0352 | 121.9116 | -0.45319 | 122.0078 | 122.0444 | 0.13275 | -0.50812 | 122.0901 | 122.0123 | -0.082397 | 122.406 | 122.1359 | 0.1236 | -0.082397 | 122.0856 | 122.0306 | 122.0581 | -0.62714 | 122.4564 | 122.4564 | 122.1497 | -0.52643
1786.2344 | 122.5525 | -122.0261 | 0.50812 | -0.0078584 | -0.021792 | 0.013356 | 0.034955 | -0.01157 | -0.038937 | -0.0011023 | -0.015182 | 0.012867 | -0.033725 | -0.0025443 | -0.01321 | 0.00068362 | 0.14191 | 0.068665 | 0.13733 | 0.082397 | 0.082397 | 0.068665 | -0.054932 | 0.43945 | 0.47607 | 0.15564 | 0.42572 | 0.40741 | 0.10986 | 0.027466 | 122.0947 | 121.9711 | -0.42572 | 122.0947 | 122.1085 | 0.13733 | -0.36621 | 122.1359 | 122.0535 | -0.082398 | 122.4655 | 122.1817 | 0.12817 | -0.10071 | 122.1085 | 122.168 | 122.1634 | -0.56305 | 122.4518 | 122.4335 | 122.5021 | -0.48065
1788 | 122.5845 | -122.0306 | 0.50354 | -0.0078584 | -0.017519 | 0.013569 | 0.037946 | -0.0079382 | -0.041287 | -0.0017431 | 7.627e-05 | 0.012226 | -0.03522 | -0.0014761 | -0.01556 | -0.00059818 | 0.13275 | 0.09613 | 0.14648 | 0.09613 | 0.082397 | 0.054932 | -0.068665 | 0.48523 | 0.54474 | 0.19226 | 0.42572 | 0.40741 | 0.10986 | 0.032043 | 122.0856 | 121.962 | -0.42114 | 122.1268 | 122.1268 | 0.16479 | -0.37079 | 122.1405 | 122.0627 | -0.07782 | 122.5159 | 122.2229 | 0.16022 | -0.09613 | 122.113 | 122.1634 | 122.1771 | -0.5722 | 122.4564 | 122.4381 | 122.5754 | -0.4715
1789.7812 | 122.6486 | -121.9986 | 0.48065 | 0.01503 | -0.015383 | 0.01421 | 0.032605 | -0.01392 | -0.032315 | 0.0006067 | 7.627e-05 | 0.016712 | -0.036074 | -0.00062151 | -0.0087244 | 0.00025642 | 0.054932 | -0.086975 | -0.009155 | 0.013733 | 0.1236 | 0.027466 | -0.091553 | 0.31586 | 0.34332 | 0.013733 | 0.46234 | 0.44403 | 0.073242 | -0.013733 | 122.0261 | 121.907 | -0.35706 | 121.9116 | 122.0123 | 0.10529 | -0.42572 | 122.0718 | 121.9849 | -0.018311 | 122.3145 | 122.0123 | 0.027466 | -0.036621 | 122.1222 | 122.0535 | 121.9894 | -0.57221 | 122.4609 | 122.4426 | 122.3419 | -0.49439
1791.5625 | 122.5937 | -122.0444 | 0.48065 | -0.00022891 | -0.016878 | 0.015492 | 0.039227 | -0.011783 | -0.039364 | -0.0021703 | 7.627e-05 | 0.011798 | -0.035434 | -0.0036123 | -0.015347 | -0.0020934 | 0.12817 | 0.068665 | 0.1236 | 0.086975 | 0.09613 | 0.054932 | -0.064087 | 0.43488 | 0.53101 | 0.18768 | 0.41657 | 0.41199 | 0.091553 | 0.032043 | 122.0993 | 121.9803 | -0.38452 | 122.113 | 122.1313 | 0.15106 | -0.35248 | 122.1359 | 122.0764 | -0.064087 | 122.4792 | 122.2321 | 0.15564 | -0.068665 | 122.1405 | 122.1725 | 122.168 | -0.54474 | 122.4609 | 122.4564 | 122.5754 | -0.44861
1793.3438 | 122.6761 | -122.0032 | 0.45776 | -0.0078584 | -0.014529 | 0.015065 | 0.035809 | -0.011143 | -0.031887 | 0.0003931 | -0.0075532 | 0.016071 | -0.035647 | -0.0044669 | -0.010006 | -0.002948 | 0.1236 | -0.022888 | 0.064087 | 0.059509 | 0.11902 | 0.009155 | -0.11444 | 0.36163 | 0.44403 | 0.068665 | 0.43945 | 0.42114 | 0.073242 | -0.004578 | 122.0123 | 121.8887 | -0.33875 | 121.9803 | 122.0627 | 0.17395 | -0.33417 | 122.0764 | 121.9986 | -0.018311 | 122.3648 | 122.0718 | 0.073243 | -0.036621 | 122.1222 | 122.1268 | 122.0673 | -0.5722 | 122.4426 | 122.4243 | 122.4472 | -0.46234
1795.125 | 122.6303 | -122.0444 | 0.46234 | -0.0078584 | -0.019869 | 0.014424 | 0.034741 | -0.010715 | -0.039792 | 0.0023157 | -0.0075532 | 0.014576 | -0.037356 | -0.0048941 | -0.010433 | 0.00068362 | 0.13733 | 0.073242 | 0.13275 | 0.10071 | 0.073242 | 0.07782 | -0.068665 | 0.43488 | 0.49896 | 0.15564 | 0.37994 | 0.39368 | 0.091553 | 0.032043 | 122.1222 | 121.9757 | -0.3891 | 122.1176 | 122.1451 | 0.16937 | -0.32501 | 122.1359 | 122.0764 | -0.082397 | 122.4792 | 122.2 | 0.1236 | -0.068664 | 122.1176 | 122.1817 | 122.1771 | -0.53101 | 122.4243 | 122.438 | 122.5433 | -0.4303
1796.8594 | 122.6074 | -122.0306 | 0.48981 | 0.0074006 | -0.014315 | 0.012074 | 0.036664 | -0.015201 | -0.038296 | -3.4096e-05 | 0.0077058 | 0.013507 | -0.03052 | -0.0023305 | -0.012356 | 0.00025642 | 0.041199 | -0.036621 | 0.004578 | 0.032043 | 0.13275 | 0.013733 | -0.11444 | 0.29755 | 0.3891 | 0.027466 | 0.4715 | 0.45776 | 0.050354 | -0.009155 | 122.0444 | 121.9162 | -0.35706 | 121.994 | 122.0627 | 0.14648 | -0.44861 | 122.081 | 122.0215 | -0.01831 | 122.3282 | 122.0581 | 0.036621 | -0.032043 | 122.1634 | 122.0718 | 122.0352 | -0.60425 | 122.5021 | 122.4884 | 122.4197 | -0.49896
1798.6406 | 122.6395 | -122.0581 | 0.4715 | -0.00022891 | -0.016024 | 0.014637 | 0.033673 | -0.0094336 | -0.036801 | -3.4096e-05 | -0.0075532 | 0.016284 | -0.039279 | -0.0027579 | -0.012783 | 0.0013244 | 0.14191 | 0.07782 | 0.14648 | 0.09613 | 0.086975 | 0.073242 | -0.059509 | 0.42572 | 0.48523 | 0.15106 | 0.3891 | 0.37994 | 0.082397 | 0.013733 | 122.1313 | 121.9986 | -0.38452 | 122.1359 | 122.1542 | 0.15564 | -0.32959 | 122.1405 | 122.0718 | -0.082398 | 122.4838 | 122.2092 | 0.13733 | -0.091553 | 122.1451 | 122.2 | 122.2046 | -0.53101 | 122.4472 | 122.438 | 122.5433 | -0.45776
1800.375 | 122.6807 | -122.0078 | 0.45319 | -0.0078584 | -0.014315 | 0.013569 | 0.033887 | -0.0096472 | -0.034665 | 0.0016749 | 7.627e-05 | 0.017566 | -0.03757 | -0.0014761 | -0.010006 | 0.00025642 | 0.086975 | -0.022888 | 0.036621 | 0.045776 | 0.11902 | 0.022888 | -0.07782 | 0.38452 | 0.44861 | 0.10071 | 0.43945 | 0.41657 | 0.091553 | 0.022888 | 122.0306 | 121.9299 | -0.33417 | 121.9849 | 122.0535 | 0.1236 | -0.36621 | 122.0993 | 122.0306 | -0.013733 | 122.3923 | 122.1085 | 0.07782 | -0.036621 | 122.1268 | 122.0947 | 122.0444 | -0.53101 | 122.4472 | 122.4243 | 122.4564 | -0.4303
1802.1562 | 122.6486 | -122.081 | 0.43945 | -0.00022891 | -0.014101 | 0.013997 | 0.033032 | -0.011143 | -0.032956 | 0.0025293 | -0.0075532 | 0.018207 | -0.038211 | -0.00062151 | -0.0095788 | 0.00068362 | 0.054932 | -0.054932 | 0 | 0.022888 | 0.13733 | 0.022888 | -0.10986 | 0.27924 | 0.35248 | 0.004578 | 0.4303 | 0.43488 | 0.059509 | -0.009155 | 122.1039 | 121.9711 | -0.30212 | 122.0261 | 122.1039 | 0.13275 | -0.38452 | 122.1405 | 122.0718 | -0.009155 | 122.3602 | 122.0856 | 0.013733 | -0.004578 | 122.2183 | 122.1359 | 122.081 | -0.54932 | 122.5113 | 122.5159 | 122.4335 | -0.44861
1803.8906 | 122.7081 | -122.0398 | 0.43488 | -0.00022891 | -0.016024 | 0.012074 | 0.036237 | -0.011783 | -0.037655 | -3.4096e-05 | 7.627e-05 | 0.023548 | -0.042056 | 1.9292e-05 | -0.011929 | -0.0016662 | 0.041199 | -0.086975 | -0.004578 | 0.004578 | 0.12817 | 0.009155 | -0.10986 | 0.31128 | 0.35706 | 0.027466 | 0.42572 | 0.40741 | 0.059509 | -0.013733 | 122.049 | 121.9299 | -0.3067 | 121.9528 | 122.0444 | 0.11444 | -0.39368 | 122.0993 | 122.0261 | -0.009155 | 122.3511 | 122.0673 | 0.041199 | -0.027465 | 122.168 | 122.081 | 122.0352 | -0.54474 | 122.4655 | 122.4472 | 122.3969 | -0.44861
1805.6875 | 122.5754 | -122.0993 | 0.48523 | -0.00022891 | -0.020083 | 0.017415 | 0.035382 | -0.012424 | -0.041287 | 0.0010339 | -0.0075532 | 0.019275 | -0.043765 | -0.0012625 | -0.015133 | 0.0015382 | 0.07782 | 0.013733 | 0.10071 | 0.054932 | 0.086975 | 0.059509 | -0.068665 | 0.35706 | 0.44403 | 0.10529 | 0.39368 | 0.40283 | 0.07782 | 0.004578 | 122.1588 | 122.0306 | -0.39825 | 122.113 | 122.1542 | 0.1236 | -0.40741 | 122.1771 | 122.1039 | -0.091552 | 122.4564 | 122.2046 | 0.10071 | -0.082397 | 122.1863 | 122.1771 | 122.2 | -0.55389 | 122.493 | 122.5021 | 122.5433 | -0.48065
1807.4688 | 122.6624 | -122.0673 | 0.45776 | -0.015487 | -0.014529 | 0.013569 | 0.03645 | -0.00922 | -0.033169 | 0.0023157 | 7.627e-05 | 0.025898 | -0.041415 | -0.0010489 | -0.010006 | -0.0020934 | 0.059509 | -0.032043 | -0.004578 | 0.018311 | 0.14648 | 0.027466 | -0.11444 | 0.27008 | 0.35706 | 0.004578 | 0.42114 | 0.4303 | 0.050354 | -0.027466 | 122.0947 | 121.9528 | -0.31128 | 122.0352 | 122.0856 | 0.13275 | -0.39826 | 122.1176 | 122.0398 | -0.036621 | 122.3373 | 122.0718 | 0.032044 | -0.027466 | 122.2137 | 122.1268 | 122.0627 | -0.5722 | 122.4884 | 122.4976 | 122.4243 | -0.48523
1809.1875 | 122.5571 | -122.0947 | 0.48981 | -0.00022891 | -0.020083 | 0.016346 | 0.033673 | -0.011997 | -0.041501 | 0.0006067 | -0.0075532 | 0.019489 | -0.044833 | -0.0051077 | -0.01257 | 0.00089722 | 0.09613 | 0.064087 | 0.10529 | 0.059509 | 0.091553 | 0.054932 | -0.073242 | 0.37537 | 0.45776 | 0.11444 | 0.40741 | 0.38452 | 0.082397 | 0.009155 | 122.1497 | 122.0215 | -0.39825 | 122.1588 | 122.1542 | 0.13275 | -0.39368 | 122.1771 | 122.1039 | -0.082397 | 122.4701 | 122.2092 | 0.10529 | -0.10529 | 122.1863 | 122.1909 | 122.2 | -0.56305 | 122.5021 | 122.4792 | 122.5525 | -0.48065
1810.9844 | 122.6532 | -122.0947 | 0.46692 | -0.00022891 | -0.019869 | 0.013569 | 0.033673 | -0.010929 | -0.039792 | -0.0008887 | -0.0075532 | 0.019062 | -0.043551 | -0.0016897 | -0.012783 | -0.00017078 | 0.15106 | 0.064087 | 0.14191 | 0.09613 | 0.082397 | 0.059509 | -0.050354 | 0.39825 | 0.48981 | 0.15564 | 0.37994 | 0.37994 | 0.07782 | 0.013733 | 122.1542 | 122.0444 | -0.38452 | 122.1588 | 122.1909 | 0.14648 | -0.31586 | 122.1725 | 122.1085 | -0.086975 | 122.493 | 122.2504 | 0.14191 | -0.086975 | 122.1771 | 122.2458 | 122.2366 | -0.51727 | 122.4747 | 122.4747 | 122.5845 | -0.45319
1812.7656 | 122.7173 | -122.0215 | 0.45776 | -0.0078584 | -0.016024 | 0.012928 | 0.036878 | -0.010929 | -0.033596 | 0.0035975 | 7.627e-05 | 0.025043 | -0.04291 | -0.00083531 | -0.01257 | -0.00081178 | 0.091553 | 0.004578 | 0.045776 | 0.054932 | 0.12817 | 0.036621 | -0.10986 | 0.32501 | 0.43945 | 0.059509 | 0.43945 | 0.40741 | 0.041199 | -0.009155 | 122.0581 | 121.9116 | -0.32959 | 122.0261 | 122.0764 | 0.16479 | -0.36621 | 122.0627 | 122.0123 | -0.018311 | 122.3465 | 122.081 | 0.068664 | -0.050354 | 122.1497 | 122.113 | 122.0673 | -0.56763 | 122.4609 | 122.4289 | 122.4609 | -0.46692
1814.5 | 122.7127 | -122.0581 | 0.43488 | -0.0078584 | -0.016024 | 0.011006 | 0.033887 | -0.011356 | -0.03616 | 0.0012477 | 0.0077058 | 0.025043 | -0.042697 | -0.00040791 | -0.010433 | 0.0015382 | 0.045776 | -0.064087 | -0.004578 | 0.013733 | 0.14648 | 0.022888 | -0.10529 | 0.28839 | 0.34332 | 0.036621 | 0.42114 | 0.40283 | 0.041199 | -0.018311 | 122.081 | 121.9528 | -0.28839 | 121.994 | 122.0718 | 0.11902 | -0.3891 | 122.0993 | 122.0398 | -0.013732 | 122.3465 | 122.0947 | 0.054932 | -0.032043 | 122.2046 | 122.1039 | 122.0535 | -0.54016 | 122.4792 | 122.4609 | 122.4014 | -0.45319
1816.2812 | 122.58 | -122.1405 | 0.46234 | -0.0078584 | -0.022219 | 0.016987 | 0.03645 | -0.010502 | -0.04321 | -0.0017431 | 7.627e-05 | 0.017993 | -0.043765 | -0.0031851 | -0.012783 | 0.00047002 | 0.068665 | 0.050354 | 0.091553 | 0.054932 | 0.10529 | 0.059509 | -0.064087 | 0.32044 | 0.44403 | 0.10071 | 0.39368 | 0.38452 | 0.073242 | 0.013733 | 122.2 | 122.0764 | -0.35706 | 122.1909 | 122.1954 | 0.11902 | -0.39368 | 122.2137 | 122.1542 | -0.068664 | 122.4609 | 122.2412 | 0.086975 | -0.07782 | 122.2458 | 122.2092 | 122.2321 | -0.52643 | 122.5342 | 122.525 | 122.5845 | -0.44861
1818.0469 | 122.6349 | -122.1268 | 0.46234 | 0.0074006 | -0.021578 | 0.018483 | 0.035382 | -0.012211 | -0.042782 | -0.0030249 | 7.627e-05 | 0.019062 | -0.044406 | -0.0051077 | -0.013851 | 0.00047002 | 0.068665 | 0.018311 | 0.073242 | 0.054932 | 0.10071 | 0.036621 | -0.082397 | 0.32501 | 0.42572 | 0.10529 | 0.36621 | 0.36163 | 0.082397 | 0.009155 | 122.1634 | 122.0444 | -0.36163 | 122.1451 | 122.1817 | 0.13733 | -0.39368 | 122.2092 | 122.1359 | -0.09613 | 122.4518 | 122.2321 | 0.096131 | -0.10071 | 122.2275 | 122.1954 | 122.2 | -0.54474 | 122.493 | 122.4884 | 122.5525 | -0.45319
1819.7656 | 122.7036 | -122.0764 | 0.42114 | 0.01503 | -0.016451 | 0.013569 | 0.037946 | -0.012852 | -0.033596 | 0.0003931 | -0.0075532 | 0.025043 | -0.041201 | -0.0012625 | -0.01257 | -0.002948 | 0.091553 | -0.032043 | 0.041199 | 0.059509 | 0.1236 | 0.018311 | -0.11444 | 0.29755 | 0.39368 | 0.041199 | 0.3891 | 0.37537 | 0.045776 | -0.045776 | 122.0947 | 121.962 | -0.29755 | 122.0444 | 122.1359 | 0.17395 | -0.32959 | 122.1222 | 122.0306 | -0.032044 | 122.374 | 122.1176 | 0.086975 | -0.045777 | 122.2 | 122.168 | 122.1176 | -0.53558 | 122.4655 | 122.4518 | 122.4701 | -0.46692
1821.5625 | 122.7356 | -122.0947 | 0.42114 | 0.0074006 | -0.016238 | 0.012501 | 0.037305 | -0.012638 | -0.035946 | 0.0006067 | -0.015182 | 0.022052 | -0.04056 | 0.0010873 | -0.010861 | -0.00038438 | 0.059509 | -0.032043 | 0.027466 | 0.041199 | 0.13733 | 0.032043 | -0.09613 | 0.3067 | 0.37994 | 0.07782 | 0.40283 | 0.35248 | 0.059509 | 0.004578 | 122.1268 | 121.9986 | -0.28381 | 122.0627 | 122.1359 | 0.13733 | -0.36163 | 122.1542 | 122.0993 | -0.018311 | 122.4014 | 122.1725 | 0.073242 | -0.068665 | 122.2321 | 122.1542 | 122.1222 | -0.51727 | 122.4976 | 122.4472 | 122.4747 | -0.41656
1823.2656 | 122.699 | -122.0901 | 0.40283 | -0.00022891 | -0.016024 | 0.015706 | 0.036237 | -0.0077246 | -0.034665 | 0.0012477 | 7.627e-05 | 0.022693 | -0.042697 | -0.0023305 | -0.011288 | 0.00047002 | 0.032043 | -0.045776 | -0.009155 | 0.018311 | 0.13733 | 0.032043 | -0.1236 | 0.25635 | 0.3479 | 0.022888 | 0.41199 | 0.3891 | 0.032043 | -0.032043 | 122.1222 | 121.9666 | -0.2655 | 122.0444 | 122.1085 | 0.14191 | -0.37079 | 122.1222 | 122.0581 | 0.009155 | 122.3465 | 122.113 | 0.054931 | -0.013733 | 122.2275 | 122.1222 | 122.081 | -0.52643 | 122.5021 | 122.4792 | 122.438 | -0.43488
1825.0469 | 122.699 | -122.1268 | 0.3891 | -0.00022891 | -0.014529 | 0.014851 | 0.034101 | -0.010715 | -0.03381 | 0.0012477 | 0.0077058 | 0.025043 | -0.039706 | -0.0019033 | -0.012142 | 0.0019654 | 0.022888 | -0.086975 | -0.009155 | 0.009155 | 0.13275 | 0.013733 | -0.11444 | 0.22888 | 0.27466 | 0 | 0.37537 | 0.36621 | 0.068665 | 0.032043 | 122.1405 | 122.0123 | -0.25635 | 122.0398 | 122.1359 | 0.1236 | -0.36621 | 122.1954 | 122.1588 | -0.013733 | 122.3557 | 122.1268 | -0.032043 | -0.022888 | 122.2595 | 122.1497 | 122.1176 | -0.50354 | 122.5021 | 122.493 | 122.4014 | -0.35706
1826.7656 | 122.7173 | -122.1176 | 0.36163 | -0.0078584 | -0.016451 | 0.014851 | 0.034955 | -0.010074 | -0.037014 | 0.0014613 | 7.627e-05 | 0.022693 | -0.043551 | -0.0036123 | -0.013638 | 0.0064514 | 0.068665 | 0.022888 | 0.068665 | 0.050354 | 0.10071 | 0.059509 | -0.068665 | 0.27924 | 0.39825 | 0.11902 | 0.33417 | 0.32501 | 0.17395 | 0.11444 | 122.1771 | 122.049 | -0.26092 | 122.1405 | 122.168 | 0.11902 | -0.29297 | 122.2916 | 122.2321 | -0.027466 | 122.3969 | 122.2366 | 0.004578 | -0.036621 | 122.2183 | 122.1863 | 122.1863 | -0.4303 | 122.4518 | 122.4426 | 122.5159 | -0.24719
1828.5625 | 122.6395 | -122.1588 | 0.41657 | 0.0074006 | -0.019442 | 0.015492 | 0.039655 | -0.012852 | -0.04321 | 0.0006067 | 7.627e-05 | 0.018848 | -0.042697 | -0.0072439 | -0.019619 | 0.0075196 | 0.041199 | 0.022888 | 0.091553 | 0.054932 | 0.091553 | 0.041199 | -0.09613 | 0.20142 | 0.39825 | 0.13275 | 0.3479 | 0.32501 | 0.23804 | 0.1831 | 122.2 | 122.0627 | -0.32501 | 122.1817 | 122.2137 | 0.15106 | -0.37537 | 122.3969 | 122.3419 | -0.068665 | 122.3602 | 122.2916 | -0.050354 | -0.091553 | 122.2504 | 122.2 | 122.2504 | -0.5127 | 122.5067 | 122.4838 | 122.5571 | -0.23346
1830.2812 | 122.7081 | -122.0947 | 0.4303 | -0.00022891 | -0.013888 | 0.01421 | 0.033887 | -0.011356 | -0.034024 | 0.0001795 | -0.015182 | 0.022052 | -0.038851 | -0.0055349 | -0.017483 | 0.007306 | 0.041199 | -0.086975 | -0.027466 | 0.018311 | 0.1236 | 0.022888 | -0.09613 | 0.027466 | 0.31586 | 0.009155 | 0.42114 | 0.41199 | 0.26093 | 0.20599 | 122.1176 | 121.9986 | -0.3067 | 122.0078 | 122.113 | 0.11444 | -0.3891 | 122.3557 | 122.3007 | -0.009155 | 122.1222 | 122.1039 | -0.19684 | -0.018311 | 122.2183 | 122.1359 | 122.0673 | -0.52643 | 122.5159 | 122.5067 | 122.4106 | -0.2243
1832.0469 | 122.6028 | -122.1405 | 0.45776 | -0.00022891 | -0.021151 | 0.013997 | 0.032819 | -0.010288 | -0.041287 | -0.0011023 | -0.0075532 | 0.019489 | -0.043978 | -0.0059621 | -0.018337 | 0.011365 | 0.1236 | 0.068665 | 0.1236 | 0.059509 | 0.091553 | 0.054932 | -0.064087 | 0.1236 | 0.43945 | 0.14191 | 0.3891 | 0.38452 | 0.29755 | 0.23804 | 122.1954 | 122.0764 | -0.36621 | 122.2092 | 122.2 | 0.1236 | -0.33417 | 122.438 | 122.3785 | -0.068665 | 122.2641 | 122.2824 | -0.09613 | -0.073243 | 122.2321 | 122.2641 | 122.2641 | -0.52185 | 122.5296 | 122.525 | 122.58 | -0.21973
1833.8281 | 122.6028 | -122.1313 | 0.45776 | 0.0074006 | -0.016238 | 0.012715 | 0.040082 | -0.010715 | -0.040219 | -0.0011023 | -0.0075532 | 0.020343 | -0.040988 | -0.0061757 | -0.021969 | 0.0081604 | 0.12817 | 0.082397 | 0.14648 | 0.09613 | 0.091553 | 0.059509 | -0.091553 | 0.11902 | 0.49896 | 0.16022 | 0.36163 | 0.35706 | 0.29297 | 0.23804 | 122.1909 | 122.0398 | -0.36621 | 122.2137 | 122.2275 | 0.18768 | -0.32959 | 122.4243 | 122.3694 | -0.096131 | 122.2504 | 122.2916 | -0.07782 | -0.10071 | 122.2229 | 122.2595 | 122.2778 | -0.54932 | 122.493 | 122.4884 | 122.6303 | -0.21973
1835.6094 | 122.7264 | -122.0993 | 0.42114 | -0.00022891 | -0.011538 | 0.012074 | 0.04115 | -0.010502 | -0.034665 | -0.0011023 | 0.0077058 | 0.022052 | -0.039706 | -0.0019033 | -0.01791 | 0.0068786 | 0.045776 | -0.054932 | 0.013733 | 0.022888 | 0.13733 | 0.004578 | -0.11902 | 0.036621 | 0.37079 | 0.027466 | 0.43488 | 0.39368 | 0.27008 | 0.20142 | 122.1039 | 121.9803 | -0.28381 | 122.0444 | 122.1222 | 0.14191 | -0.37537 | 122.3694 | 122.3007 | 0.013732 | 122.1359 | 122.1268 | -0.17395 | -0.027466 | 122.2366 | 122.1451 | 122.113 | -0.54016 | 122.5342 | 122.493 | 122.4701 | -0.21973
1837.3906 | 122.6074 | -122.1497 | 0.45776 | -0.00022891 | -0.019228 | 0.014424 | 0.035382 | -0.0096472 | -0.041501 | 0.0006067 | -0.0075532 | 0.017353 | -0.040988 | -0.0068167 | -0.02026 | 0.010724 | 0.091553 | 0.068665 | 0.10986 | 0.050354 | 0.091553 | 0.050354 | -0.068665 | 0.11444 | 0.41657 | 0.11444 | 0.35706 | 0.36621 | 0.27924 | 0.21057 | 122.2 | 122.081 | -0.36621 | 122.2183 | 122.2 | 0.11902 | -0.36621 | 122.4289 | 122.3602 | -0.10071 | 122.2641 | 122.2641 | -0.09613 | -0.091553 | 122.2412 | 122.2412 | 122.2595 | -0.52643 | 122.5067 | 122.5159 | 122.5662 | -0.24719
1839.0938 | 122.7219 | -122.0901 | 0.41199 | -0.00022891 | -0.01282 | 0.013142 | 0.038587 | -0.011143 | -0.035305 | 0.0008203 | 7.627e-05 | 0.021198 | -0.04056 | -0.0033987 | -0.017269 | 0.0043152 | 0.041199 | -0.041199 | 0 | 0.036621 | 0.12817 | 0.018311 | -0.11444 | 0.036621 | 0.37537 | 0.045776 | 0.41199 | 0.40283 | 0.24719 | 0.1831 | 122.1085 | 121.9757 | -0.28381 | 122.0489 | 122.1268 | 0.15106 | -0.37079 | 122.3373 | 122.2733 | 0 | 122.1268 | 122.1359 | -0.13733 | -0.009155 | 122.2183 | 122.1313 | 122.0901 | -0.52643 | 122.5021 | 122.493 | 122.4655 | -0.22888
1840.875 | 122.7356 | -122.0947 | 0.44403 | -0.00022891 | -0.013247 | 0.012074 | 0.036878 | -0.011356 | -0.034024 | 0.0008203 | -0.0075532 | 0.02248 | -0.037783 | -0.0031851 | -0.016415 | 0.0075196 | 0.054932 | -0.013733 | 0.036621 | 0.041199 | 0.11902 | 0.018311 | -0.11444 | 0.050354 | 0.40283 | 0.059509 | 0.40741 | 0.3891 | 0.23346 | 0.1831 | 122.113 | 121.9803 | -0.32501 | 122.081 | 122.1359 | 0.15564 | -0.3891 | 122.3282 | 122.2778 | -0.036621 | 122.1451 | 122.1542 | -0.1236 | -0.054932 | 122.2137 | 122.1497 | 122.1313 | -0.55847 | 122.5021 | 122.4838 | 122.4976 | -0.26093
1842.6719 | 122.6807 | -122.1176 | 0.42572 | -0.00022891 | -0.014101 | 0.011433 | 0.035169 | -0.011783 | -0.036801 | 0.0001795 | 7.627e-05 | 0.02248 | -0.041415 | -0.0044669 | -0.014919 | 0.0060242 | 0.082397 | 0.022888 | 0.050354 | 0.050354 | 0.13733 | 0.032043 | -0.086975 | 0.073242 | 0.39368 | 0.041199 | 0.3891 | 0.3891 | 0.24261 | 0.19226 | 122.1497 | 122.0306 | -0.28839 | 122.1405 | 122.168 | 0.13733 | -0.34332 | 122.3602 | 122.3099 | -0.036621 | 122.1909 | 122.1588 | -0.15106 | -0.036621 | 122.2549 | 122.2 | 122.168 | -0.5127 | 122.5067 | 122.5067 | 122.5113 | -0.23346
1844.3906 | 122.7402 | -122.0947 | 0.40741 | -0.0078584 | -0.014101 | 0.014424 | 0.036023 | -0.012424 | -0.037014 | -0.0006751 | -0.0075532 | 0.020343 | -0.040347 | -0.0048941 | -0.015774 | 0.0081604 | 0.022888 | -0.022888 | 0.018311 | 0.032043 | 0.13275 | 0.009155 | -0.10986 | 0.041199 | 0.3891 | 0.064087 | 0.42114 | 0.3891 | 0.23346 | 0.17395 | 122.1039 | 121.9849 | -0.27466 | 122.0718 | 122.1268 | 0.14191 | -0.38452 | 122.3282 | 122.2687 | 0.013733 | 122.1359 | 122.1588 | -0.10986 | -0.018311 | 122.2275 | 122.1176 | 122.113 | -0.51727 | 122.5159 | 122.4838 | 122.4838 | -0.23346
1846.1719 | 122.699 | -122.1222 | 0.40283 | -0.0078584 | -0.014315 | 0.013356 | 0.034101 | -0.010715 | -0.034024 | 0.0012477 | 7.627e-05 | 0.022052 | -0.039279 | -0.0031851 | -0.017056 | 0.0079468 | 0.073242 | 0.027466 | 0.050354 | 0.054932 | 0.12817 | 0.027466 | -0.10529 | 0.082397 | 0.39825 | 0.068665 | 0.37994 | 0.37079 | 0.22888 | 0.1831 | 122.1497 | 122.0169 | -0.27466 | 122.1497 | 122.1771 | 0.16022 | -0.32959 | 122.3511 | 122.3053 | -0.022888 | 122.2046 | 122.1909 | -0.11444 | -0.032043 | 122.2504 | 122.1954 | 122.1725 | -0.50812 | 122.5021 | 122.493 | 122.5204 | -0.21973
1847.9688 | 122.7219 | -122.113 | 0.41657 | -0.00022891 | -0.019228 | 0.014424 | 0.033673 | -0.010929 | -0.038723 | 0.0012477 | -0.015182 | 0.02013 | -0.043765 | -0.0048941 | -0.018337 | 0.010083 | 0.11902 | 0.073242 | 0.11902 | 0.11444 | 0.07782 | 0.068665 | -0.045776 | 0.14191 | 0.46692 | 0.14648 | 0.35706 | 0.33875 | 0.27924 | 0.21057 | 122.1817 | 122.0673 | -0.33875 | 122.1863 | 122.2275 | 0.16022 | -0.29755 | 122.3923 | 122.3236 | -0.059509 | 122.2549 | 122.2595 | -0.064087 | -0.07782 | 122.1909 | 122.2321 | 122.2321 | -0.46234 | 122.4701 | 122.4518 | 122.58 | -0.20599
1849.6875 | 122.7402 | -122.113 | 0.41657 | 0.0074006 | -0.020296 | 0.014851 | 0.032392 | -0.0081518 | -0.037442 | -0.0017431 | 7.627e-05 | 0.022052 | -0.041415 | -0.0059621 | -0.016628 | 0.0085876 | 0.050354 | 0 | 0.07782 | 0.050354 | 0.11444 | 0.041199 | -0.091553 | 0.11444 | 0.42114 | 0.10529 | 0.35706 | 0.35248 | 0.25635 | 0.20142 | 122.1542 | 122.0215 | -0.30212 | 122.113 | 122.1634 | 0.14191 | -0.36621 | 122.3694 | 122.3145 | -0.059509 | 122.2275 | 122.2183 | -0.09613 | -0.064087 | 122.2275 | 122.1634 | 122.1909 | -0.50812 | 122.4701 | 122.4655 | 122.5342 | -0.21515
1851.4688 | 122.6395 | -122.1588 | 0.4303 | -0.0078584 | -0.016024 | 0.015492 | 0.037091 | -0.012424 | -0.038083 | -0.0017431 | 7.627e-05 | 0.021625 | -0.041201 | -0.0051077 | -0.01791 | 0.0088012 | 0.018311 | -0.045776 | 0.009155 | 0.009155 | 0.12817 | 0.018311 | -0.11902 | 0 | 0.34332 | 0.018311 | 0.40741 | 0.40283 | 0.21515 | 0.15106 | 122.1771 | 122.0398 | -0.30212 | 122.113 | 122.168 | 0.12817 | -0.41199 | 122.374 | 122.3099 | -0.022888 | 122.1588 | 122.1771 | -0.13275 | -0.027466 | 122.287 | 122.1771 | 122.168 | -0.54932 | 122.5662 | 122.5616 | 122.5021 | -0.27924
1853.25 | 122.6212 | -122.168 | 0.43945 | -0.00022891 | -0.017306 | 0.01421 | 0.04115 | -0.013279 | -0.04086 | -0.0019567 | 7.627e-05 | 0.019062 | -0.040774 | -0.0063895 | -0.02261 | 0.0098694 | 0.11444 | 0.10529 | 0.16022 | 0.10529 | 0.091553 | 0.041199 | -0.07782 | 0.11902 | 0.48981 | 0.16937 | 0.33875 | 0.32959 | 0.27466 | 0.21973 | 122.2092 | 122.0901 | -0.3479 | 122.2733 | 122.2733 | 0.18311 | -0.32501 | 122.4426 | 122.3877 | -0.10071 | 122.287 | 122.3373 | -0.050354 | -0.10986 | 122.2595 | 122.2824 | 122.3282 | -0.51727 | 122.5067 | 122.4976 | 122.6578 | -0.21973
1854.9844 | 122.5891 | -122.1725 | 0.42572 | 0.0074006 | -0.016024 | 0.013569 | 0.038159 | -0.010502 | -0.038723 | -0.0030249 | 7.627e-05 | 0.019489 | -0.040133 | -0.0051077 | -0.020901 | 0.0077332 | 0.086975 | 0.068665 | 0.11444 | 0.086975 | 0.086975 | 0.032043 | -0.073242 | 0.050354 | 0.39825 | 0.07782 | 0.36621 | 0.36621 | 0.22888 | 0.19684 | 122.2046 | 122.0993 | -0.33874 | 122.2412 | 122.2595 | 0.16022 | -0.33874 | 122.4014 | 122.3694 | -0.059509 | 122.2229 | 122.2504 | -0.11902 | -0.059509 | 122.2595 | 122.2595 | 122.287 | -0.49896 | 122.5388 | 122.5388 | 122.5708 | -0.22888
1856.7812 | 122.7448 | -122.1771 | 0.37537 | -0.00022891 | -0.014956 | 0.012928 | 0.034955 | -0.011356 | -0.033596 | -0.0006751 | 7.627e-05 | 0.022907 | -0.04291 | -0.0044669 | -0.016842 | 0.0045288 | 0.09613 | -0.009155 | 0.022888 | 0.054932 | 0.13733 | 0.032043 | -0.12817 | 0.054932 | 0.38452 | 0.059509 | 0.37994 | 0.35706 | 0.24261 | 0.17853 | 122.2092 | 122.049 | -0.23804 | 122.168 | 122.2321 | 0.18311 | -0.27924 | 122.4197 | 122.3557 | 0.004578 | 122.2321 | 122.2366 | -0.11902 | -0.01831 | 122.3145 | 122.2733 | 122.2 | -0.50354 | 122.5571 | 122.5342 | 122.5616 | -0.19684
1858.5 | 122.7127 | -122.1588 | 0.37994 | -0.0078584 | -0.014315 | 0.012715 | 0.034741 | -0.011783 | -0.035092 | 0.0001795 | 7.627e-05 | 0.022266 | -0.039706 | -0.0074575 | -0.015988 | 0.010297 | 0.041199 | -0.07782 | -0.004578 | 0.013733 | 0.12817 | 0.027466 | -0.10986 | -0.027466 | 0.27924 | -0.004578 | 0.37079 | 0.37079 | 0.24261 | 0.16479 | 122.1863 | 122.0489 | -0.25177 | 122.081 | 122.1725 | 0.1236 | -0.33875 | 122.4014 | 122.3236 | -0.009155 | 122.1313 | 122.1542 | -0.16937 | -0.009155 | 122.287 | 122.2 | 122.1542 | -0.48981 | 122.5296 | 122.5296 | 122.438 | -0.21515
1860.2812 | 122.7448 | -122.1497 | 0.38452 | -0.00022891 | -0.011538 | 0.012928 | 0.037732 | -0.0096472 | -0.034665 | 0.0003931 | 7.627e-05 | 0.020557 | -0.038638 | -0.0042531 | -0.017483 | 0.0068786 | 0.073242 | 0.004578 | 0.027466 | 0.054932 | 0.14648 | 0.027466 | -0.13275 | 0.054932 | 0.37994 | 0.064087 | 0.38452 | 0.36163 | 0.21973 | 0.17853 | 122.1771 | 122.0169 | -0.23804 | 122.1542 | 122.2046 | 0.18768 | -0.31128 | 122.3694 | 122.3282 | 0 | 122.2046 | 122.2137 | -0.11444 | -0.022888 | 122.2961 | 122.2229 | 122.1771 | -0.51727 | 122.5342 | 122.5113 | 122.5296 | -0.20599
1862.0781 | 122.6212 | -122.2046 | 0.43488 | -0.00022891 | -0.019655 | 0.016346 | 0.034528 | -0.012424 | -0.041501 | -0.0006751 | -0.0075532 | 0.017353 | -0.042056 | -0.0059621 | -0.020901 | 0.0085876 | 0.050354 | 0.041199 | 0.082397 | 0.054932 | 0.09613 | 0.050354 | -0.073242 | 0.059509 | 0.38452 | 0.10529 | 0.35706 | 0.34332 | 0.2655 | 0.1831 | 122.2549 | 122.1313 | -0.33875 | 122.2458 | 122.2595 | 0.12817 | -0.38452 | 122.4701 | 122.3877 | -0.077819 | 122.2641 | 122.3099 | -0.077819 | -0.091552 | 122.3007 | 122.2549 | 122.287 | -0.50812 | 122.5616 | 122.5479 | 122.5891 | -0.25177
1863.875 | 122.6761 | -122.1909 | 0.4303 | -0.00022891 | -0.019228 | 0.015065 | 0.039014 | -0.012424 | -0.042355 | -0.0025977 | 7.627e-05 | 0.017139 | -0.041842 | -0.0078847 | -0.019619 | 0.0070924 | 0.09613 | 0.064087 | 0.1236 | 0.09613 | 0.091553 | 0.059509 | -0.073242 | 0.12817 | 0.46692 | 0.17395 | 0.33875 | 0.33417 | 0.24261 | 0.19684 | 122.2504 | 122.1176 | -0.33875 | 122.2549 | 122.287 | 0.16937 | -0.33417 | 122.4335 | 122.3877 | -0.091553 | 122.319 | 122.3648 | -0.022888 | -0.096131 | 122.2824 | 122.287 | 122.3145 | -0.50354 | 122.5296 | 122.525 | 122.6578 | -0.23346
1865.6562 | 122.6807 | -122.1817 | 0.4303 | 0.0074006 | -0.017519 | 0.015278 | 0.036023 | -0.011997 | -0.039151 | -0.0019567 | 7.627e-05 | 0.017566 | -0.043124 | -0.0057485 | -0.01791 | 0.006665 | 0.07782 | 0.032043 | 0.082397 | 0.064087 | 0.10986 | 0.050354 | -0.068665 | 0.10529 | 0.4303 | 0.13275 | 0.37079 | 0.36163 | 0.23804 | 0.16937 | 122.2321 | 122.113 | -0.32044 | 122.2137 | 122.2458 | 0.13275 | -0.35248 | 122.4197 | 122.3511 | -0.059509 | 122.287 | 122.3145 | -0.036622 | -0.068665 | 122.2916 | 122.2595 | 122.2641 | -0.49896 | 122.5525 | 122.5433 | 122.612 | -0.26093
1867.375 | 122.6898 | -122.168 | 0.41199 | -0.0078584 | -0.014956 | 0.013356 | 0.033887 | -0.008579 | -0.034878 | -0.0034521 | -0.0075532 | 0.02312 | -0.042056 | -0.0066031 | -0.018765 | 0.005597 | 0.054932 | -0.050354 | 0 | 0.013733 | 0.13733 | -0.004578 | -0.13275 | 0.004578 | 0.32959 | 0.018311 | 0.41199 | 0.37537 | 0.19684 | 0.1236 | 122.1634 | 122.0352 | -0.27466 | 122.1176 | 122.1817 | 0.14648 | -0.35706 | 122.3648 | 122.2916 | 0 | 122.1725 | 122.1863 | -0.10528 | -0.036621 | 122.3053 | 122.2229 | 122.168 | -0.54474 | 122.58 | 122.5433 | 122.4976 | -0.28839
1869.1406 | 122.6303 | -122.1634 | 0.45319 | 0.0074006 | -0.018587 | 0.015065 | 0.038587 | -0.011783 | -0.038723 | -0.0013159 | 0.0077058 | 0.018848 | -0.037997 | -0.0057485 | -0.019192 | 0.004956 | 0.1236 | 0.086975 | 0.14191 | 0.086975 | 0.086975 | 0.050354 | -0.064087 | 0.10529 | 0.45776 | 0.12817 | 0.33875 | 0.3479 | 0.24719 | 0.16937 | 122.2137 | 122.0993 | -0.36621 | 122.2504 | 122.2504 | 0.15106 | -0.32959 | 122.4106 | 122.3328 | -0.11444 | 122.2687 | 122.2916 | -0.041199 | -0.10529 | 122.2504 | 122.287 | 122.3053 | -0.51727 | 122.5021 | 122.5113 | 122.6212 | -0.28381
1870.875 | 122.7219 | -122.1588 | 0.40283 | -0.015487 | -0.014529 | 0.011647 | 0.034101 | -0.0096472 | -0.029324 | 0.0014613 | 0.0077058 | 0.02312 | -0.039706 | -0.0033987 | -0.013851 | 0.0062378 | 0.073242 | -0.054932 | 0 | 0.032043 | 0.13275 | 0.032043 | -0.11444 | 0.018311 | 0.3067 | -0.009155 | 0.37994 | 0.37537 | 0.20599 | 0.12817 | 122.1909 | 122.0444 | -0.27008 | 122.1039 | 122.1909 | 0.14648 | -0.32959 | 122.3648 | 122.287 | -0.022888 | 122.1771 | 122.1497 | -0.13733 | -0.027466 | 122.2916 | 122.2321 | 122.1588 | -0.51727 | 122.5388 | 122.5342 | 122.4655 | -0.27466
1872.6719 | 122.7585 | -121.9299 | 0.59052 | 0.0074006 | -0.017946 | 0.014424 | 0.034314 | -0.010502 | -0.036587 | 0.0023157 | 0.0077058 | 0.016712 | -0.035647 | -0.0029715 | -0.0097924 | 4.2822e-05 | 0.10986 | 0.018311 | 0.086975 | 0.073242 | 0.091553 | 0.041199 | -0.082397 | 0.11902 | 0.61798 | 0.10071 | 0.54932 | 0.54016 | 0.073242 | 0 | 121.9711 | 121.8475 | -0.49896 | 121.9482 | 122.0032 | 0.15564 | -0.48065 | 122.0032 | 121.9299 | -0.041199 | 122.049 | 122.0306 | 0.10071 | -0.050354 | 122.0215 | 122.0398 | 122.0169 | -0.67291 | 122.4792 | 122.4701 | 122.5479 | -0.59052
1874.4375 | 122.6669 | -122.0032 | 0.6134 | -0.0078584 | -0.02051 | 0.015065 | 0.03645 | -0.010929 | -0.042782 | -0.0025977 | -0.0075532 | 0.012012 | -0.038851 | -0.0038259 | -0.013424 | 0.0023926 | 0.050354 | 0.009155 | 0.086975 | 0.054932 | 0.082397 | 0.041199 | -0.09613 | 0.073242 | 0.56763 | 0.10529 | 0.53558 | 0.53101 | 0.059509 | -0.027466 | 122.0444 | 121.907 | -0.53101 | 122.0123 | 122.0581 | 0.15106 | -0.56305 | 122.0627 | 121.9757 | -0.07782 | 122.0764 | 122.1085 | 0.13275 | -0.082397 | 122.0856 | 122.0535 | 122.0901 | -0.70953 | 122.5388 | 122.5342 | 122.5708 | -0.64087
1876.1406 | 122.6212 | -122.0123 | 0.61798 | -0.0078584 | -0.01581 | 0.015706 | 0.038373 | -0.013065 | -0.039792 | -0.0017431 | -0.0075532 | 0.014576 | -0.036074 | -0.0023305 | -0.01321 | -0.00017078 | 0.12817 | 0.091553 | 0.13275 | 0.10071 | 0.10529 | 0.064087 | -0.073242 | 0.12817 | 0.65002 | 0.12817 | 0.51727 | 0.52643 | 0.068665 | -0.009155 | 122.0764 | 121.9391 | -0.5127 | 122.1039 | 122.113 | 0.17395 | -0.48981 | 122.081 | 122.0032 | -0.10071 | 122.1405 | 122.1405 | 0.13733 | -0.091553 | 122.1176 | 122.1405 | 122.1451 | -0.69122 | 122.5296 | 122.5388 | 122.6624 | -0.62714
1877.9375 | 122.6532 | -122.0261 | 0.60425 | -0.0078584 | -0.020937 | 0.014637 | 0.03111 | -0.0094336 | -0.037655 | -0.0008887 | -0.0075532 | 0.014148 | -0.03757 | -0.0040395 | -0.011074 | -0.0014526 | 0.13275 | 0.073242 | 0.13275 | 0.086975 | 0.09613 | 0.059509 | -0.07782 | 0.14191 | 0.6134 | 0.13733 | 0.53101 | 0.5127 | 0.064087 | -0.009155 | 122.0856 | 121.9482 | -0.50812 | 122.0993 | 122.113 | 0.16479 | -0.4715 | 122.0901 | 122.0169 | -0.073242 | 122.168 | 122.1634 | 0.14648 | -0.091553 | 122.1222 | 122.1588 | 122.1588 | -0.68207 | 122.5571 | 122.5388 | 122.6395 | -0.6134
1879.7188 | 122.6715 | -122.0444 | 0.60425 | -0.00022891 | -0.019442 | 0.013356 | 0.034314 | -0.012424 | -0.040646 | -0.0002477 | -0.0075532 | 0.014148 | -0.037356 | -0.0044669 | -0.013424 | -0.00017078 | 0.073242 | 0.018311 | 0.07782 | 0.054932 | 0.11902 | 0.050354 | -0.091553 | 0.091553 | 0.56305 | 0.091553 | 0.54016 | 0.51727 | 0.064087 | -0.022888 | 122.0947 | 121.9528 | -0.48523 | 122.0627 | 122.0993 | 0.14649 | -0.53101 | 122.1085 | 122.0215 | -0.064087 | 122.1359 | 122.1359 | 0.11444 | -0.086975 | 122.1634 | 122.1176 | 122.1222 | -0.6958 | 122.5845 | 122.5616 | 122.6074 | -0.62714
1881.5156 | 122.6395 | -122.0352 | 0.62256 | -0.00022891 | -0.01816 | 0.013997 | 0.039014 | -0.010715 | -0.039364 | -0.0015295 | -0.0075532 | 0.01308 | -0.033297 | -0.0021169 | -0.013851 | 0.00047002 | 0.091553 | 0.036621 | 0.091553 | 0.050354 | 0.10071 | 0.059509 | -0.091553 | 0.091553 | 0.57678 | 0.09613 | 0.54474 | 0.51727 | 0.059509 | -0.022888 | 122.0947 | 121.9437 | -0.52185 | 122.0718 | 122.0856 | 0.14191 | -0.53101 | 122.0947 | 122.0123 | -0.07782 | 122.1268 | 122.1313 | 0.11902 | -0.10529 | 122.1359 | 122.1268 | 122.1268 | -0.71411 | 122.58 | 122.5525 | 122.612 | -0.64545
1883.2344 | 122.6303 | -122.0169 | 0.60883 | -0.00022891 | -0.017519 | 0.013569 | 0.040509 | -0.0096472 | -0.040005 | -0.0008887 | 0.0077058 | 0.013294 | -0.035006 | -0.0031851 | -0.01321 | -0.0020934 | 0.14648 | 0.10529 | 0.15564 | 0.086975 | 0.086975 | 0.050354 | -0.091553 | 0.1236 | 0.65002 | 0.1236 | 0.53558 | 0.54474 | 0.068665 | 0.009155 | 122.0673 | 121.9254 | -0.52185 | 122.1222 | 122.1039 | 0.17853 | -0.46234 | 122.0856 | 122.0261 | -0.073243 | 122.1405 | 122.1405 | 0.11444 | -0.064087 | 122.1039 | 122.1634 | 122.1725 | -0.70038 | 122.5525 | 122.5616 | 122.6669 | -0.59967
1885.0156 | 122.7768 | -121.9849 | 0.59052 | 0.0074006 | -0.011965 | 0.011219 | 0.034101 | -0.0066564 | -0.03146 | 0.0014613 | -0.0075532 | 0.016498 | -0.036074 | -0.0010489 | -0.0091516 | -0.0025208 | 0.09613 | 0.018311 | 0.050354 | 0.050354 | 0.11444 | 0.022888 | -0.10986 | 0.082397 | 0.56763 | 0.041199 | 0.55389 | 0.54016 | 0.054932 | -0.054932 | 122.0078 | 121.875 | -0.47607 | 122.0032 | 122.0352 | 0.16022 | -0.49439 | 122.0398 | 121.9299 | -0.036621 | 122.0673 | 122.0261 | 0.096131 | -0.050354 | 122.0993 | 122.081 | 122.0352 | -0.70038 | 122.5388 | 122.525 | 122.5525 | -0.64545
1886.7969 | 122.7539 | -122.0123 | 0.58594 | -0.00022891 | -0.014315 | 0.014424 | 0.040509 | -0.010502 | -0.032742 | -0.0008887 | -0.0075532 | 0.018207 | -0.033725 | -0.0010489 | -0.011715 | 4.2822e-05 | 0.045776 | -0.036621 | 0.004578 | 0.013733 | 0.14648 | 0 | -0.13275 | 0.022888 | 0.50354 | 0 | 0.56305 | 0.53101 | 0.009155 | -0.032043 | 122.0123 | 121.8796 | -0.43945 | 121.9757 | 122.0261 | 0.14648 | -0.54016 | 122.0215 | 121.9803 | -0.022888 | 122.0352 | 122.0123 | 0.032043 | -0.054931 | 122.1588 | 122.0581 | 122.0169 | -0.71869 | 122.5754 | 122.5433 | 122.5159 | -0.61798
1888.5156 | 122.6212 | -122.0398 | 0.59509 | -0.0078584 | -0.013888 | 0.012928 | 0.037946 | -0.0072974 | -0.039364 | 0.0001795 | 7.627e-05 | 0.01543 | -0.035861 | -0.0031851 | -0.014065 | -0.0010254 | 0.10071 | 0.091553 | 0.13275 | 0.091553 | 0.086975 | 0.041199 | -0.07782 | 0.068665 | 0.60883 | 0.091553 | 0.54474 | 0.53101 | 0.050354 | -0.004578 | 122.081 | 121.962 | -0.50812 | 122.1313 | 122.1313 | 0.16937 | -0.49438 | 122.0901 | 122.0352 | -0.050354 | 122.1085 | 122.1313 | 0.096131 | -0.064087 | 122.1268 | 122.1405 | 122.1725 | -0.67291 | 122.5845 | 122.5708 | 122.6486 | -0.59967
1890.2812 | 122.7264 | -122.0032 | 0.56305 | -0.00022891 | -0.009188 | 0.010579 | 0.03645 | -0.010929 | -0.030819 | 0.0021021 | 7.627e-05 | 0.017139 | -0.03287 | 0.0013011 | -0.0085108 | -0.0033752 | 0.041199 | -0.027466 | 0.004578 | 0.032043 | 0.11902 | 0.027466 | -0.10529 | 0.022888 | 0.48523 | -0.004578 | 0.55389 | 0.52185 | 0.036621 | -0.054932 | 122.0306 | 121.8979 | -0.44403 | 121.9757 | 122.0352 | 0.13733 | -0.52185 | 122.0398 | 121.9482 | -0.009155 | 122.0261 | 121.9986 | 0.050354 | -0.041198 | 122.1222 | 122.0444 | 122.0078 | -0.66834 | 122.5571 | 122.525 | 122.4884 | -0.61798
1892.0781 | 122.6852 | -122.0444 | 0.58594 | 0.0074006 | -0.023714 | 0.018269 | 0.03346 | -0.0090062 | -0.041073 | -0.0006751 | 7.627e-05 | 0.012867 | -0.040988 | -0.0042531 | -0.01257 | 0.0026062 | 0.10529 | 0.14191 | 0.15564 | 0.09613 | 0.091553 | 0.050354 | -0.09613 | 0.12817 | 0.64545 | 0.16479 | 0.51727 | 0.49896 | 0.050354 | -0.004578 | 122.0947 | 121.9482 | -0.49438 | 122.1863 | 122.1405 | 0.19226 | -0.48065 | 122.0947 | 122.0398 | -0.068664 | 122.1725 | 122.2092 | 0.16937 | -0.086975 | 122.1359 | 122.1497 | 122.2 | -0.68207 | 122.5616 | 122.5433 | 122.6898 | -0.59052
1893.8594 | 122.6257 | -122.0215 | 0.62256 | -0.00022891 | -0.017519 | 0.015706 | 0.039441 | -0.011997 | -0.039151 | -0.0002477 | -0.015182 | 0.014148 | -0.034152 | -0.0029715 | -0.01321 | -0.00059818 | 0.10986 | 0.10529 | 0.13275 | 0.11444 | 0.10529 | 0.054932 | -0.082397 | 0.10071 | 0.64087 | 0.12817 | 0.50812 | 0.50812 | 0.059509 | -0.004578 | 122.0764 | 121.9391 | -0.51727 | 122.1268 | 122.1359 | 0.19684 | -0.5127 | 122.081 | 122.0169 | -0.11444 | 122.1222 | 122.1497 | 0.13275 | -0.11444 | 122.1268 | 122.1313 | 122.1542 | -0.70496 | 122.5296 | 122.5296 | 122.6624 | -0.62714
1895.5938 | 122.6486 | -122.0306 | 0.61798 | -0.00022891 | -0.014101 | 0.012288 | 0.037946 | -0.00922 | -0.038083 | -0.0004613 | -0.0075532 | 0.017353 | -0.035434 | -0.0016897 | -0.013638 | -0.0025208 | 0.041199 | 0.013733 | 0.045776 | 0.045776 | 0.11902 | 0.013733 | -0.13275 | 0.018311 | 0.52185 | 0.018311 | 0.56305 | 0.55389 | 0.032043 | -0.032043 | 122.0444 | 121.8979 | -0.49896 | 122.0444 | 122.0764 | 0.17853 | -0.57678 | 122.0627 | 121.9986 | -0.054932 | 122.049 | 122.049 | 0.050354 | -0.064087 | 122.1497 | 122.0718 | 122.0764 | -0.75073 | 122.5937 | 122.5845 | 122.5525 | -0.65002
1897.375 | 122.6532 | -122.0581 | 0.6134 | -0.023117 | -0.022646 | 0.011647 | 0.034741 | -0.010929 | -0.040219 | -0.0015295 | 7.627e-05 | 0.016498 | -0.038424 | -0.00062151 | -0.011929 | -0.00081178 | 0.086975 | 0.082397 | 0.082397 | 0.054932 | 0.09613 | 0.054932 | -0.07782 | 0.11444 | 0.54474 | 0.10986 | 0.53101 | 0.50812 | 0.064087 | -0.009155 | 122.113 | 121.9803 | -0.51727 | 122.1405 | 122.113 | 0.13275 | -0.52643 | 122.1222 | 122.0489 | -0.082397 | 122.1725 | 122.168 | 0.11902 | -0.10529 | 122.1542 | 122.1451 | 122.1405 | -0.69122 | 122.5891 | 122.5662 | 122.6028 | -0.62256
1899.1406 | 122.6578 | -122.2504 | 0.40741 | -0.00022891 | -0.020083 | 0.015492 | 0.037305 | -0.011783 | -0.038937 | -0.0013159 | 7.627e-05 | 0.010303 | -0.03287 | -0.0044669 | -0.012356 | -0.0010254 | 0.068665 | 0.027466 | 0.082397 | 0.064087 | 0.11444 | 0.050354 | -0.068665 | 0.19684 | 0.3479 | 0.10071 | 0.34332 | 0.32044 | 0.045776 | -0.032043 | 122.3007 | 122.1817 | -0.29297 | 122.2778 | 122.3145 | 0.13275 | -0.33874 | 122.2961 | 122.2183 | -0.064087 | 122.4472 | 122.3511 | 0.13275 | -0.086975 | 122.3648 | 122.319 | 122.3328 | -0.47608 | 122.5937 | 122.5708 | 122.5983 | -0.43945
1900.9375 | 122.6578 | -122.2595 | 0.41657 | 0.0074006 | -0.013888 | 0.015278 | 0.037305 | -0.012424 | -0.03851 | -0.0028113 | 7.627e-05 | 0.012653 | -0.030307 | -0.0033987 | -0.011501 | -0.0014526 | 0.091553 | 0.045776 | 0.09613 | 0.059509 | 0.10071 | 0.054932 | -0.082397 | 0.21515 | 0.32959 | 0.09613 | 0.32501 | 0.31586 | 0.027466 | -0.041199 | 122.3145 | 122.1771 | -0.31586 | 122.3053 | 122.319 | 0.14191 | -0.32501 | 122.287 | 122.2183 | -0.091553 | 122.4747 | 122.3557 | 0.13733 | -0.10071 | 122.3602 | 122.3511 | 122.3557 | -0.49896 | 122.5845 | 122.5754 | 122.5891 | -0.45776
1902.75 | 122.7997 | -122.2 | 0.36621 | 0.0074006 | -0.015169 | 0.012288 | 0.033887 | -0.011783 | -0.035305 | -0.0011023 | 0.0077058 | 0.012439 | -0.033938 | -0.0016897 | -0.0097924 | -0.0010254 | 0.10071 | -0.027466 | 0.045776 | 0.045776 | 0.13275 | 0.036621 | -0.10071 | 0.2655 | 0.16937 | 0.09613 | 0.33417 | 0.32501 | 0.036621 | -0.022888 | 122.2366 | 122.0993 | -0.23346 | 122.1725 | 122.2458 | 0.14648 | -0.2655 | 122.2366 | 122.1771 | -0.032044 | 122.4655 | 122.2961 | 0.11902 | -0.041199 | 122.3328 | 122.3007 | 122.2458 | -0.46692 | 122.5342 | 122.525 | 122.3694 | -0.3891
1904.4688 | 122.7722 | -122.1176 | 0.46692 | -0.00022891 | -0.013033 | 0.015706 | 0.036664 | -0.012638 | -0.034451 | 0.0001795 | 0.0077058 | 0.015003 | -0.034365 | -0.0021169 | -0.011074 | -0.0025208 | 0.064087 | -0.036621 | -0.004578 | 0.027466 | 0.12817 | 0 | -0.1236 | 0.10071 | 0.32501 | 0.004578 | 0.45319 | 0.44403 | 0.018311 | -0.054932 | 122.1176 | 121.994 | -0.33874 | 122.081 | 122.1451 | 0.15106 | -0.40283 | 122.1359 | 122.0627 | -0.013733 | 122.2183 | 122.1222 | 0.05951 | -0.022888 | 122.2458 | 122.1817 | 122.113 | -0.59052 | 122.5708 | 122.5616 | 122.4426 | -0.52185
1906.2344 | 122.6852 | -122.2733 | 0.39825 | -0.0078584 | -0.016878 | 0.018055 | 0.037518 | -0.0087926 | -0.039151 | 0.0006067 | 7.627e-05 | 0.0073124 | -0.029025 | -0.0042531 | -0.011715 | -0.00038438 | 0.15564 | 0.13733 | 0.14191 | 0.10986 | 0.086975 | 0.068665 | -0.086975 | 0.28381 | 0.24719 | 0.15564 | 0.30212 | 0.27924 | 0.050354 | -0.036621 | 122.3419 | 122.1863 | -0.31128 | 122.4106 | 122.3831 | 0.19684 | -0.24261 | 122.3236 | 122.2366 | -0.09613 | 122.5571 | 122.4289 | 0.19226 | -0.11902 | 122.3602 | 122.4289 | 122.4152 | -0.48523 | 122.5754 | 122.5525 | 122.5204 | -0.43488
1908.0469 | 122.7631 | -121.994 | 0.55389 | -0.0078584 | -0.015597 | 0.01186 | 0.034314 | -0.012638 | -0.032315 | 0.0001795 | 7.627e-05 | 0.017566 | -0.034365 | 0.00044649 | -0.010861 | -0.0033752 | 0.12817 | 0.004578 | 0.041199 | 0.045776 | 0.11444 | 0.013733 | -0.091553 | 0.091553 | 0.19684 | 0.050354 | 0.60425 | 0.58136 | 0.050354 | -0.027466 | 122.0078 | 121.9025 | -0.43945 | 121.9986 | 122.0398 | 0.13733 | -0.42572 | 122.0444 | 121.9666 | 0.050354 | 122.0856 | 122.0444 | 0.07782 | 0.027466 | 122.1085 | 122.1222 | 122.0352 | -0.64545 | 122.5983 | 122.5754 | 122.1909 | -0.58136
1909.7656 | 122.7219 | -122.2595 | 0.40283 | -0.00022891 | -0.021792 | 0.014851 | 0.036878 | -0.011783 | -0.041714 | -0.0028113 | -0.0075532 | 0.0062442 | -0.030947 | -0.0033987 | -0.014919 | 4.2822e-05 | 0.091553 | 0.059509 | 0.11444 | 0.082397 | 0.09613 | 0.045776 | -0.082397 | 0.25177 | 0.22888 | 0.14191 | 0.31128 | 0.31128 | 0.054932 | -0.036621 | 122.3053 | 122.1771 | -0.3067 | 122.319 | 122.3419 | 0.16479 | -0.31128 | 122.3145 | 122.2229 | -0.091553 | 122.5113 | 122.4014 | 0.17853 | -0.091553 | 122.3557 | 122.3511 | 122.374 | -0.48523 | 122.5708 | 122.5708 | 122.4884 | -0.43945
1911.5469 | 122.7448 | -122.2366 | 0.36621 | -0.0078584 | -0.016024 | 0.011647 | 0.033887 | -0.010502 | -0.032315 | 0.0027429 | 7.627e-05 | 0.01308 | -0.029452 | -0.0029715 | -0.0091516 | -0.0020934 | 0.041199 | -0.073242 | -0.018311 | 0.018311 | 0.1236 | 0.018311 | -0.11902 | 0.11902 | 0.050354 | -0.036621 | 0.36163 | 0.35248 | 0.022888 | -0.068665 | 122.2549 | 122.1176 | -0.24262 | 122.1634 | 122.2549 | 0.13733 | -0.32501 | 122.2595 | 122.168 | -0.004578 | 122.3557 | 122.2 | 0.032044 | -0.013733 | 122.3602 | 122.2778 | 122.2183 | -0.48523 | 122.5983 | 122.5891 | 122.287 | -0.43488
1913.3438 | 122.6578 | -122.2824 | 0.39825 | -0.00022891 | -0.022219 | 0.016987 | 0.037305 | -0.015201 | -0.042782 | -0.0008887 | 7.627e-05 | 0.006885 | -0.032016 | -0.0012625 | -0.012356 | 0.0026062 | 0.10986 | 0.054932 | 0.10071 | 0.054932 | 0.091553 | 0.059509 | -0.07782 | 0.22888 | 0.16022 | 0.091553 | 0.3067 | 0.31128 | 0.036621 | -0.045776 | 122.3419 | 122.2046 | -0.3067 | 122.3373 | 122.3373 | 0.13275 | -0.28839 | 122.319 | 122.2366 | -0.091552 | 122.5113 | 122.374 | 0.13733 | -0.086975 | 122.374 | 122.3923 | 122.3831 | -0.47607 | 122.5891 | 122.5937 | 122.4426 | -0.44403
1915.0469 | 122.7127 | -122.1451 | 0.50812 | -0.00022891 | -0.020083 | 0.016987 | 0.037518 | -0.012211 | -0.041073 | -0.0015295 | -0.0075532 | 0.010303 | -0.034793 | -0.0014761 | -0.014492 | -0.0020934 | 0.091553 | 0.07782 | 0.1236 | 0.07782 | 0.091553 | 0.050354 | -0.09613 | 0.19684 | 0.2655 | 0.13733 | 0.45319 | 0.43945 | 0.059509 | -0.004578 | 122.1954 | 122.049 | -0.41656 | 122.2229 | 122.2229 | 0.17395 | -0.41656 | 122.2046 | 122.1405 | -0.054932 | 122.3419 | 122.2824 | 0.14191 | -0.068665 | 122.2366 | 122.2366 | 122.2687 | -0.60425 | 122.5983 | 122.5845 | 122.4106 | -0.5127
1916.8281 | 122.7676 | -121.9437 | 0.63171 | -0.00022891 | -0.015169 | 0.015278 | 0.033887 | -0.00922 | -0.032315 | 0.0006067 | 7.627e-05 | 0.019916 | -0.035434 | -0.0021169 | -0.0080834 | -0.0023072 | 0.10986 | 0.022888 | 0.050354 | 0.054932 | 0.11444 | 0.027466 | -0.11444 | 0.064087 | 0.18768 | 0.013733 | 0.61798 | 0.59509 | 0.050354 | -0.018311 | 121.9711 | 121.8292 | -0.51727 | 121.9666 | 121.9986 | 0.16937 | -0.52185 | 121.994 | 121.9254 | -0.013733 | 122.0078 | 121.9574 | 0.032044 | -0.036621 | 122.0581 | 122.0535 | 121.994 | -0.74616 | 122.5616 | 122.5388 | 122.1313 | -0.65002
1918.5625 | 122.6761 | -122.0627 | 0.60425 | -0.00022891 | -0.017306 | 0.015492 | 0.038587 | -0.011783 | -0.041928 | -0.0008887 | -0.0075532 | 0.012653 | -0.037356 | -0.0029715 | -0.012783 | -0.0016662 | 0.12817 | 0.086975 | 0.13733 | 0.10071 | 0.086975 | 0.054932 | -0.086975 | 0.11902 | 0.27924 | 0.11444 | 0.54016 | 0.54016 | 0.041199 | -0.027466 | 122.1176 | 121.9757 | -0.51727 | 122.1497 | 122.1634 | 0.18768 | -0.47607 | 122.1039 | 122.0352 | -0.064087 | 122.1817 | 122.1771 | 0.14191 | -0.064087 | 122.1497 | 122.1909 | 122.2 | -0.69122 | 122.6028 | 122.6028 | 122.3419 | -0.63171
1920.3438 | 122.6807 | -122.0627 | 0.62714 | -0.00022891 | -0.02521 | 0.015919 | 0.035596 | -0.012852 | -0.040005 | -0.0015295 | -0.0075532 | 0.012653 | -0.037143 | -0.0016897 | -0.012356 | -0.0010254 | 0.1236 | 0.11902 | 0.15106 | 0.10071 | 0.086975 | 0.045776 | -0.086975 | 0.13733 | 0.29297 | 0.13733 | 0.51727 | 0.51727 | 0.064087 | 0.004578 | 122.1085 | 121.9757 | -0.54016 | 122.1817 | 122.1634 | 0.18768 | -0.50354 | 122.1268 | 122.0673 | -0.10986 | 122.2 | 122.2 | 0.13275 | -0.10986 | 122.1497 | 122.1863 | 122.2137 | -0.71411 | 122.58 | 122.58 | 122.3557 | -0.62256
1922.1406 | 122.8134 | -122.2412 | 0.36621 | -0.00022891 | -0.012392 | 0.013569 | 0.036237 | -0.008579 | -0.033596 | -0.0008887 | 7.627e-05 | 0.011798 | -0.032016 | -0.00040791 | -0.0080834 | -0.0044434 | 0.054932 | -0.022888 | 0.018311 | 0.045776 | 0.14191 | 0.009155 | -0.10529 | 0.16937 | 0.14191 | 0.036621 | 0.37079 | 0.34332 | 0.009155 | -0.054932 | 122.2504 | 122.1359 | -0.2243 | 122.2183 | 122.287 | 0.15106 | -0.31128 | 122.2504 | 122.1863 | 0.004578 | 122.4106 | 122.2778 | 0.091553 | -0.022888 | 122.3831 | 122.2961 | 122.2595 | -0.4715 | 122.612 | 122.5845 | 122.3831 | -0.42114
1923.8594 | 122.6715 | -122.2229 | 0.43945 | -0.00022891 | -0.019015 | 0.016133 | 0.037518 | -0.010502 | -0.040005 | -0.0006751 | 7.627e-05 | 0.0083804 | -0.02817 | -0.0014761 | -0.01321 | -0.001239 | 0.13275 | 0.11444 | 0.15564 | 0.10986 | 0.10071 | 0.059509 | -0.086975 | 0.22888 | 0.24719 | 0.1236 | 0.36163 | 0.35248 | 0.054932 | -0.032043 | 122.2824 | 122.1359 | -0.33874 | 122.3373 | 122.3328 | 0.19684 | -0.3067 | 122.2778 | 122.1909 | -0.07782 | 122.4518 | 122.3465 | 0.15564 | -0.086975 | 122.3236 | 122.3557 | 122.3785 | -0.52643 | 122.5845 | 122.5754 | 122.4701 | -0.4715
1925.6562 | 122.7493 | -121.9437 | 0.66834 | -0.0078584 | -0.014956 | 0.014851 | 0.033673 | -0.011997 | -0.032315 | 0.0016749 | -0.015182 | 0.020343 | -0.03757 | -0.00062151 | -0.0087244 | -0.0025208 | 0.10529 | 0.018311 | 0.045776 | 0.054932 | 0.12817 | 0.027466 | -0.10986 | 0.045776 | 0.20142 | 0.009155 | 0.64545 | 0.63629 | 0.036621 | -0.013733 | 121.9711 | 121.8338 | -0.54016 | 121.962 | 121.9986 | 0.16479 | -0.56305 | 121.9803 | 121.9299 | -0.022888 | 121.9894 | 121.9528 | 0.022888 | -0.032043 | 122.0718 | 122.049 | 121.9894 | -0.7782 | 122.5891 | 122.58 | 122.1451 | -0.68207
1927.375 | 122.7539 | -122.2 | 0.4303 | -0.00022891 | -0.011324 | 0.013142 | 0.034955 | -0.012211 | -0.033596 | 0.0006067 | -0.0075532 | 0.017139 | -0.033938 | -0.0025443 | -0.0097924 | -0.0014526 | 0.050354 | -0.091553 | -0.004578 | 0.018311 | 0.12817 | 0 | -0.12817 | 0.07782 | 0.30212 | -0.022888 | 0.40283 | 0.39825 | 0.013733 | -0.045776 | 122.2 | 122.0718 | -0.30212 | 122.1085 | 122.2183 | 0.14649 | -0.37994 | 122.2137 | 122.1542 | -0.027466 | 122.2778 | 122.1771 | 0.022888 | -0.032044 | 122.3282 | 122.2504 | 122.1954 | -0.55847 | 122.6028 | 122.5983 | 122.5021 | -0.47607
1929.1406 | 122.7905 | -122.0581 | 0.56763 | -0.00022891 | -0.017306 | 0.013569 | 0.034955 | -0.010074 | -0.037869 | 0.0014613 | 7.627e-05 | 0.017993 | -0.03757 | -0.00083531 | -0.012142 | -0.00081178 | 0.13733 | 0.073242 | 0.1236 | 0.09613 | 0.10529 | 0.064087 | -0.082397 | 0.10986 | 0.56305 | 0.09613 | 0.52185 | 0.53101 | 0.050354 | 0 | 122.1222 | 121.9757 | -0.46234 | 122.1313 | 122.1542 | 0.17853 | -0.4303 | 122.1085 | 122.0581 | -0.045776 | 122.168 | 122.1542 | 0.09613 | -0.036621 | 122.1634 | 122.1954 | 122.1817 | -0.65002 | 122.58 | 122.5891 | 122.6212 | -0.56763
1930.8594 | 122.7951 | -122.2916 | 0.33875 | -0.00022891 | -0.016024 | 0.015706 | 0.033032 | -0.015415 | -0.035946 | 0.0023157 | 7.627e-05 | 0.013294 | -0.030734 | -0.0012625 | -0.010006 | 0.00089722 | 0.022888 | -0.07782 | -0.013733 | 0.013733 | 0.12817 | 0.032043 | -0.10529 | 0.14191 | 0.18768 | -0.009155 | 0.32044 | 0.31586 | 0.004578 | -0.064087 | 122.3236 | 122.1863 | -0.21057 | 122.2137 | 122.3053 | 0.11902 | -0.31586 | 122.2961 | 122.2275 | -0.01831 | 122.4335 | 122.2824 | 0.054932 | -0.022888 | 122.4197 | 122.3145 | 122.2778 | -0.44403 | 122.612 | 122.6074 | 122.4792 | -0.40283
1932.6562 | 122.7402 | -122.0261 | 0.64087 | -0.00022891 | -0.018587 | 0.014637 | 0.037946 | -0.010929 | -0.044705 | -0.0023839 | -0.0075532 | 0.014148 | -0.040774 | -0.0025443 | -0.016201 | -0.0014526 | 0.068665 | 0.054932 | 0.11444 | 0.082397 | 0.09613 | 0.059509 | -0.07782 | 0.10986 | 0.44861 | 0.13733 | 0.57678 | 0.54932 | 0.050354 | -0.027466 | 122.0856 | 121.9482 | -0.54474 | 122.081 | 122.1085 | 0.16022 | -0.5722 | 122.0764 | 121.9986 | -0.064087 | 122.1359 | 122.1634 | 0.16479 | -0.091553 | 122.1222 | 122.0947 | 122.1405 | -0.71869 | 122.6028 | 122.5754 | 122.4747 | -0.66834
1934.4531 | 122.8088 | -122.2366 | 0.36621 | -0.0078584 | -0.015597 | 0.016133 | 0.034955 | -0.01392 | -0.037228 | -0.0006751 | -0.0075532 | 0.013935 | -0.032443 | -0.0012625 | -0.008938 | -0.00017078 | 0.045776 | -0.073242 | -0.013733 | 0.004578 | 0.14648 | 0.032043 | -0.11902 | 0.11444 | 0.25177 | -0.004578 | 0.33875 | 0.32044 | 0.004578 | -0.050354 | 122.2687 | 122.1176 | -0.21973 | 122.1634 | 122.2412 | 0.1236 | -0.32044 | 122.2412 | 122.1863 | -0.027466 | 122.3511 | 122.2321 | 0.045776 | -0.045776 | 122.3831 | 122.2824 | 122.2229 | -0.48523 | 122.5754 | 122.5571 | 122.4884 | -0.41657
1936.2344 | 122.6852 | -122.2549 | 0.45319 | -0.015487 | -0.019228 | 0.016987 | 0.036023 | -0.013065 | -0.041073 | -0.0011023 | -0.0075532 | 0.012653 | -0.035647 | -0.0021169 | -0.01321 | 0.00068362 | 0.091553 | 0.041199 | 0.10071 | 0.068665 | 0.082397 | 0.059509 | -0.07782 | 0.14648 | 0.39825 | 0.086975 | 0.37994 | 0.35706 | 0.009155 | -0.022888 | 122.3145 | 122.1771 | -0.37079 | 122.2961 | 122.3236 | 0.14649 | -0.36163 | 122.2641 | 122.2321 | -0.073242 | 122.4014 | 122.3419 | 0.10986 | -0.09613 | 122.3373 | 122.3465 | 122.3557 | -0.53101 | 122.6349 | 122.612 | 122.6532 | -0.47607
1938.0312 | 122.7448 | -122.1497 | 0.49439 | -0.0078584 | -0.020724 | 0.016133 | 0.038159 | -0.011356 | -0.039578 | 0.0008203 | 7.627e-05 | 0.016284 | -0.037356 | -0.0036123 | -0.015347 | -0.00017078 | 0.12817 | 0.082397 | 0.13275 | 0.086975 | 0.091553 | 0.045776 | -0.082397 | 0.16479 | 0.53558 | 0.13733 | 0.41657 | 0.40283 | 0.041199 | -0.022888 | 122.1954 | 122.0673 | -0.40283 | 122.2321 | 122.2366 | 0.16937 | -0.36621 | 122.1909 | 122.1268 | -0.07782 | 122.3145 | 122.287 | 0.16022 | -0.091553 | 122.2412 | 122.2778 | 122.2824 | -0.57678 | 122.5662 | 122.5525 | 122.6852 | -0.51727
1939.75 | 122.6944 | -122.0856 | 0.59052 | 0.0074006 | -0.022219 | 0.015706 | 0.037305 | -0.0098608 | -0.040219 | -0.0017431 | -0.0075532 | 0.017139 | -0.040133 | -0.0016897 | -0.013638 | -0.0016662 | 0.091553 | 0.032043 | 0.07782 | 0.054932 | 0.10529 | 0.041199 | -0.082397 | 0.050354 | 0.49439 | 0.059509 | 0.52643 | 0.50812 | 0.045776 | -0.036621 | 122.1268 | 122.0032 | -0.48523 | 122.1176 | 122.1405 | 0.13733 | -0.49896 | 122.1313 | 122.049 | -0.064087 | 122.1359 | 122.1451 | 0.09613 | -0.082397 | 122.1909 | 122.1771 | 122.1634 | -0.67291 | 122.612 | 122.5937 | 122.58 | -0.62714
1941.5312 | 122.818 | -122.1313 | 0.50354 | -0.00022891 | -0.017733 | 0.012501 | 0.034955 | -0.010502 | -0.037228 | -0.0015295 | 0.0077058 | 0.017993 | -0.038424 | -0.0042531 | -0.010861 | -0.0010254 | 0.14648 | 0.054932 | 0.10529 | 0.068665 | 0.10986 | 0.041199 | -0.086975 | 0.12817 | 0.50354 | 0.086975 | 0.44861 | 0.45776 | 0.041199 | -0.009155 | 122.1725 | 122.0444 | -0.39368 | 122.1863 | 122.2 | 0.15564 | -0.35706 | 122.1725 | 122.1222 | -0.054932 | 122.2595 | 122.2183 | 0.09613 | -0.045776 | 122.2412 | 122.2778 | 122.2366 | -0.59052 | 122.58 | 122.5891 | 122.6349 | -0.5127
1943.3125 | 122.8363 | -122.1222 | 0.47607 | -0.00022891 | -0.018587 | 0.014424 | 0.034314 | -0.01157 | -0.033383 | 0.0027429 | 0.0077058 | 0.02013 | -0.037783 | 1.9292e-05 | -0.010433 | -0.00081178 | 0.10071 | -0.013733 | 0.045776 | 0.041199 | 0.11902 | 0.027466 | -0.10529 | 0.12817 | 0.4715 | 0.068665 | 0.4303 | 0.41657 | 0.041199 | -0.036621 | 122.1497 | 122.0169 | -0.35706 | 122.1085 | 122.1634 | 0.14649 | -0.37537 | 122.1634 | 122.0856 | -0.045776 | 122.2504 | 122.1909 | 0.10529 | -0.059509 | 122.2412 | 122.2229 | 122.168 | -0.58136 | 122.5525 | 122.5388 | 122.5937 | -0.5127
1945.0938 | 122.8043 | -122.168 | 0.42572 | -0.0078584 | -0.018587 | 0.017415 | 0.034528 | -0.010715 | -0.034878 | 0.0018885 | 7.627e-05 | 0.016498 | -0.03757 | -0.0016897 | -0.007229 | -0.002948 | 0.12817 | 0.064087 | 0.10071 | 0.09613 | 0.09613 | 0.045776 | -0.07782 | 0.16479 | 0.45776 | 0.086975 | 0.37537 | 0.36163 | 0.036621 | -0.027466 | 122.2137 | 122.0901 | -0.32959 | 122.2321 | 122.2641 | 0.17395 | -0.29755 | 122.2046 | 122.1405 | -0.050354 | 122.3328 | 122.2549 | 0.11444 | -0.064087 | 122.2641 | 122.2961 | 122.2687 | -0.50354 | 122.5433 | 122.5296 | 122.6257 | -0.45319
1946.875 | 122.7585 | -122.2137 | 0.42114 | -0.00022891 | -0.013888 | 0.015706 | 0.035809 | -0.0098608 | -0.03146 | 0.0008203 | 7.627e-05 | 0.019275 | -0.034579 | -0.00040791 | -0.0093652 | -0.0010254 | 0.059509 | -0.027466 | 0.022888 | 0.013733 | 0.14191 | 0.009155 | -0.11444 | 0.059509 | 0.32501 | -0.032043 | 0.37994 | 0.38452 | -0.004578 | -0.064087 | 122.2229 | 122.0993 | -0.27924 | 122.1863 | 122.2275 | 0.12817 | -0.36163 | 122.2092 | 122.1497 | -0.041199 | 122.2733 | 122.1817 | 0.032044 | -0.036622 | 122.3557 | 122.2733 | 122.2366 | -0.53558 | 122.5937 | 122.5983 | 122.5388 | -0.48523
1948.6094 | 122.7036 | -122.2046 | 0.48065 | -0.0078584 | -0.020083 | 0.012715 | 0.039014 | -0.014133 | -0.041714 | -0.0032385 | 7.627e-05 | 0.0094486 | -0.031588 | -0.0023305 | -0.01556 | 0.00025642 | 0.068665 | 0.022888 | 0.07782 | 0.045776 | 0.09613 | 0.050354 | -0.073242 | 0.13275 | 0.15564 | 0.091553 | 0.39368 | 0.3891 | 0.050354 | -0.045776 | 122.2549 | 122.1313 | -0.38452 | 122.2275 | 122.2504 | 0.11902 | -0.41199 | 122.2549 | 122.1588 | -0.086975 | 122.3373 | 122.2961 | 0.13733 | -0.091553 | 122.3007 | 122.2733 | 122.2824 | -0.55389 | 122.5983 | 122.5937 | 122.3602 | -0.52643
1950.3906 | 122.7127 | -122.287 | 0.40283 | -0.00022891 | -0.018374 | 0.015492 | 0.038587 | -0.012852 | -0.039578 | -0.0004613 | 7.627e-05 | 0.0079532 | -0.033938 | -0.0046805 | -0.012997 | -0.0010254 | 0.11444 | 0.11902 | 0.15106 | 0.10529 | 0.11902 | 0.041199 | -0.082397 | 0.21973 | 0.22888 | 0.12817 | 0.32044 | 0.29297 | 0.045776 | -0.041199 | 122.3282 | 122.2046 | -0.28381 | 122.406 | 122.3923 | 0.18768 | -0.28839 | 122.3328 | 122.2458 | -0.082397 | 122.5067 | 122.4152 | 0.16937 | -0.10986 | 122.406 | 122.4014 | 122.438 | -0.48523 | 122.6074 | 122.58 | 122.5159 | -0.44403
1952.1094 | 122.7814 | -122.2778 | 0.36163 | 0.0074006 | -0.015383 | 0.013142 | 0.035596 | -0.0098608 | -0.033596 | 0.0014613 | -0.0075532 | 0.014148 | -0.031375 | -0.00083531 | -0.0095788 | -0.0018798 | 0.036621 | -0.07782 | -0.018311 | 0.018311 | 0.1236 | 0.013733 | -0.11444 | 0.086975 | 0.19226 | -0.041199 | 0.3479 | 0.35248 | 0 | -0.068665 | 122.2916 | 122.1634 | -0.23804 | 122.2 | 122.2961 | 0.13275 | -0.32501 | 122.2778 | 122.2092 | -0.013733 | 122.3648 | 122.2366 | 0.027466 | -0.009155 | 122.4014 | 122.3145 | 122.2595 | -0.47607 | 122.6257 | 122.6303 | 122.4701 | -0.4303
1953.9062 | 122.8271 | -122.2641 | 0.34332 | -0.00022891 | -0.018587 | 0.013997 | 0.035169 | -0.0090062 | -0.037869 | 0.0027429 | 7.627e-05 | 0.011158 | -0.032656 | -0.0025443 | -0.0095788 | -0.00059818 | 0.10986 | 0.004578 | 0.091553 | 0.086975 | 0.10071 | 0.054932 | -0.07782 | 0.21973 | 0.33875 | 0.09613 | 0.28381 | 0.29755 | 0.041199 | -0.032043 | 122.319 | 122.1863 | -0.24261 | 122.2687 | 122.3511 | 0.16479 | -0.23346 | 122.3053 | 122.2321 | -0.05951 | 122.4838 | 122.3602 | 0.12817 | -0.045777 | 122.3648 | 122.374 | 122.3557 | -0.42114 | 122.5479 | 122.5616 | 122.6028 | -0.37537
1955.7031 | 122.7127 | -122.3007 | 0.42114 | 0.0074006 | -0.016665 | 0.013569 | 0.039014 | -0.011997 | -0.041287 | -0.0013159 | 7.627e-05 | 0.01073 | -0.032443 | -0.0016897 | -0.014706 | 0.00025642 | 0.11444 | 0.13275 | 0.15106 | 0.09613 | 0.086975 | 0.041199 | -0.073242 | 0.18768 | 0.43488 | 0.13733 | 0.31128 | 0.31128 | 0.050354 | -0.027466 | 122.3419 | 122.2275 | -0.33417 | 122.4335 | 122.3969 | 0.16937 | -0.3067 | 122.3511 | 122.2733 | -0.10986 | 122.4884 | 122.438 | 0.16479 | -0.10986 | 122.3877 | 122.4152 | 122.4518 | -0.49438 | 122.612 | 122.612 | 122.7356 | -0.44861
1957.4844 | 122.7997 | -122.1817 | 0.44403 | -0.0078584 | -0.015597 | 0.014424 | 0.031964 | -0.010502 | -0.034237 | 0.0029565 | 7.627e-05 | 0.019275 | -0.03522 | -0.00083531 | -0.0078698 | 4.2822e-05 | 0.032043 | -0.068665 | -0.018311 | 0.022888 | 0.13275 | 0.004578 | -0.12817 | 0.059509 | 0.27008 | -0.045776 | 0.45319 | 0.42114 | 0.013733 | -0.054932 | 122.1863 | 122.0535 | -0.31128 | 122.113 | 122.2046 | 0.15106 | -0.41199 | 122.1954 | 122.1268 | 0.009155 | 122.2412 | 122.1359 | 0.009156 | -0.022888 | 122.3145 | 122.2137 | 122.1634 | -0.57221 | 122.6349 | 122.6028 | 122.4518 | -0.49896
1959.2031 | 122.6852 | -122.2183 | 0.46234 | -0.00022891 | -0.017092 | 0.013783 | 0.038587 | -0.011997 | -0.041287 | -0.0006751 | -0.015182 | 0.013935 | -0.032443 | -0.0036123 | -0.015988 | 0.00025642 | 0.086975 | 0.09613 | 0.12817 | 0.091553 | 0.10071 | 0.054932 | -0.091553 | 0.13275 | 0.37537 | 0.07782 | 0.3891 | 0.3891 | 0.018311 | -0.045776 | 122.2733 | 122.1268 | -0.36163 | 122.3145 | 122.3099 | 0.18311 | -0.37537 | 122.2366 | 122.1725 | -0.073242 | 122.3511 | 122.2961 | 0.1236 | -0.073242 | 122.319 | 122.3053 | 122.3465 | -0.55389 | 122.6074 | 122.6074 | 122.5937 | -0.50812
1961 | 122.8134 | -122.0581 | 0.54016 | -0.0078584 | -0.014956 | 0.013783 | 0.036664 | -0.010502 | -0.035946 | -0.0015295 | 7.627e-05 | 0.019916 | -0.034152 | -0.0019033 | -0.0097924 | -0.0027344 | 0.032043 | -0.036621 | 0.004578 | 0.018311 | 0.13733 | 0.004578 | -0.1236 | 0.022888 | 0.13275 | -0.004578 | 0.53101 | 0.52643 | 0.009155 | -0.054932 | 122.0627 | 121.9345 | -0.40283 | 122.0215 | 122.0764 | 0.14191 | -0.50812 | 122.0673 | 122.0032 | -0.009155 | 122.081 | 122.0535 | 0.050354 | -0.013733 | 122.1954 | 122.0901 | 122.0627 | -0.66376 | 122.5891 | 122.5845 | 122.1909 | -0.59509
1962.7344 | 122.8317 | -121.9986 | 0.60425 | -0.0078584 | -0.015597 | 0.011647 | 0.037091 | -0.013279 | -0.035092 | -3.4096e-05 | -0.0075532 | 0.022266 | -0.038424 | -0.00040791 | -0.010861 | -0.0020934 | 0.091553 | 0.009155 | 0.045776 | 0.059509 | 0.14648 | 0.018311 | -0.10986 | 0.064087 | 0.19684 | 0.041199 | 0.60425 | 0.60883 | 0.036621 | -0.050354 | 122.0169 | 121.8887 | -0.45776 | 122.0078 | 122.0581 | 0.16937 | -0.5127 | 122.0352 | 121.9482 | 0 | 122.0627 | 122.0398 | 0.091553 | 0.004578 | 122.1451 | 122.0901 | 122.0444 | -0.71411 | 122.6028 | 122.6074 | 122.1954 | -0.6546
1964.5312 | 122.7997 | -122.0718 | 0.56763 | -0.00022891 | -0.015169 | 0.013569 | 0.034101 | -0.0083654 | -0.033596 | -3.4096e-05 | 0.0077058 | 0.021625 | -0.036929 | 1.9292e-05 | -0.0093652 | -0.0020934 | 0.059509 | -0.009155 | 0.004578 | 0.036621 | 0.1236 | 0.027466 | -0.1236 | 0.022888 | 0.12817 | -0.018311 | 0.54474 | 0.54474 | 0.022888 | -0.045776 | 122.0993 | 121.9482 | -0.44403 | 122.0627 | 122.1085 | 0.16022 | -0.50812 | 122.0947 | 122.0261 | -0.022888 | 122.0947 | 122.0535 | 0.027465 | -0.022888 | 122.1954 | 122.1313 | 122.0764 | -0.69122 | 122.6166 | 122.6166 | 122.2 | -0.6134
1966.25 | 122.7539 | -122.0764 | 0.6134 | -0.0078584 | -0.020937 | 0.014637 | 0.037946 | -0.011997 | -0.044491 | -0.0011023 | 7.627e-05 | 0.014789 | -0.038424 | -0.0021169 | -0.014919 | 0.0011108 | 0.082397 | 0.059509 | 0.11902 | 0.091553 | 0.11444 | 0.050354 | -0.068665 | 0.11902 | 0.27008 | 0.12817 | 0.53558 | 0.5127 | 0.07782 | -0.013733 | 122.1268 | 122.0078 | -0.49896 | 122.1359 | 122.168 | 0.16022 | -0.53101 | 122.1542 | 122.0627 | -0.07782 | 122.1954 | 122.2046 | 0.14191 | -0.10071 | 122.1909 | 122.1588 | 122.1954 | -0.68207 | 122.612 | 122.5891 | 122.3465 | -0.62714
1968.0469 | 122.7448 | -122.168 | 0.52643 | -0.0078584 | -0.023501 | 0.017628 | 0.036664 | -0.01392 | -0.04385 | -0.0030249 | 7.627e-05 | 0.013721 | -0.038211 | -0.0046805 | -0.012142 | 0.0026062 | 0.059509 | 0.027466 | 0.07782 | 0.054932 | 0.10986 | 0.050354 | -0.064087 | 0.086975 | 0.17853 | 0.07782 | 0.46692 | 0.46234 | 0.022888 | -0.036621 | 122.2183 | 122.1039 | -0.41657 | 122.1954 | 122.2229 | 0.11902 | -0.46692 | 122.1909 | 122.1313 | -0.059509 | 122.2549 | 122.2458 | 0.11444 | -0.064087 | 122.2778 | 122.2275 | 122.2458 | -0.59052 | 122.6349 | 122.6303 | 122.3465 | -0.56305
1969.8281 | 122.731 | -122.1497 | 0.53558 | -0.0078584 | -0.014529 | 0.013997 | 0.038587 | -0.013492 | -0.036374 | -0.0006751 | -0.0075532 | 0.01543 | -0.036074 | 1.9292e-05 | -0.012783 | -0.001239 | 0.041199 | -0.041199 | 0 | 0.018311 | 0.13275 | 0.018311 | -0.12817 | 0.027466 | 0.1236 | 0 | 0.5127 | 0.49896 | 0 | -0.045776 | 122.168 | 122.0215 | -0.40283 | 122.1085 | 122.168 | 0.14649 | -0.49438 | 122.1497 | 122.1039 | -0.022888 | 122.1771 | 122.1497 | 0.045776 | -0.036621 | 122.2824 | 122.1909 | 122.1497 | -0.66376 | 122.6624 | 122.6486 | 122.2733 | -0.58136
1971.5625 | 122.7493 | -122.0581 | 0.66376 | -0.0078584 | -0.020724 | 0.015065 | 0.035596 | -0.012424 | -0.040219 | -0.0021703 | -0.0075532 | 0.015216 | -0.04056 | -0.0014761 | -0.014919 | -0.0010254 | 0.073242 | 0.027466 | 0.09613 | 0.059509 | 0.10529 | 0.045776 | -0.10071 | 0.073242 | 0.20142 | 0.11444 | 0.58594 | 0.58136 | 0.059509 | -0.018311 | 122.1039 | 121.9574 | -0.55847 | 122.0856 | 122.1176 | 0.16022 | -0.59052 | 122.1176 | 122.0398 | -0.07782 | 122.1313 | 122.1725 | 0.13275 | -0.082397 | 122.1634 | 122.1313 | 122.1542 | -0.76447 | 122.644 | 122.6395 | 122.2595 | -0.68207
1973.3594 | 122.7676 | -122.0581 | 0.65002 | -0.00022891 | -0.020083 | 0.015278 | 0.037946 | -0.0094336 | -0.040219 | -0.0038793 | -0.0075532 | 0.017139 | -0.038851 | -0.0010489 | -0.014919 | -0.0014526 | 0.10529 | 0.045776 | 0.09613 | 0.073242 | 0.10071 | 0.041199 | -0.073242 | 0.10529 | 0.25635 | 0.11444 | 0.56305 | 0.56305 | 0.059509 | -0.004578 | 122.0993 | 121.9849 | -0.54932 | 122.1039 | 122.1313 | 0.14648 | -0.54474 | 122.1176 | 122.0535 | -0.086975 | 122.1634 | 122.1725 | 0.11902 | -0.086975 | 122.1588 | 122.1634 | 122.1542 | -0.72327 | 122.6212 | 122.6212 | 122.3145 | -0.6546
1975.1562 | 122.731 | -122.0673 | 0.63171 | -0.00022891 | -0.017519 | 0.014851 | 0.036878 | -0.014133 | -0.03851 | -0.0011023 | 7.627e-05 | 0.015857 | -0.036715 | -0.0023305 | -0.012997 | -0.0020934 | 0.10986 | 0.018311 | 0.086975 | 0.050354 | 0.091553 | 0.041199 | -0.073242 | 0.059509 | 0.18768 | 0.059509 | 0.57678 | 0.56305 | 0.045776 | -0.032043 | 122.1085 | 121.994 | -0.54016 | 122.0856 | 122.1176 | 0.1236 | -0.52185 | 122.113 | 122.0352 | -0.054932 | 122.1268 | 122.1268 | 0.091552 | -0.068665 | 122.1588 | 122.1771 | 122.1542 | -0.70496 | 122.644 | 122.6303 | 122.2549 | -0.66376
1976.9531 | 122.7539 | -122.0764 | 0.60883 | -0.00022891 | -0.018374 | 0.015278 | 0.037518 | -0.012211 | -0.040005 | -0.0032385 | 7.627e-05 | 0.017353 | -0.038638 | -0.0027579 | -0.015347 | -0.0025208 | 0.15106 | 0.10529 | 0.13733 | 0.10529 | 0.10529 | 0.041199 | -0.082397 | 0.15106 | 0.2655 | 0.13733 | 0.54474 | 0.52643 | 0.059509 | -0.018311 | 122.1176 | 121.994 | -0.50354 | 122.1817 | 122.1817 | 0.18768 | -0.45776 | 122.1359 | 122.0581 | -0.064087 | 122.2275 | 122.2137 | 0.15564 | -0.082398 | 122.1817 | 122.2275 | 122.2137 | -0.69122 | 122.6212 | 122.6028 | 122.3419 | -0.62714
1978.6875 | 122.8455 | -122.0535 | 0.58594 | -0.0078584 | -0.01581 | 0.01421 | 0.031323 | -0.010929 | -0.034024 | -3.4096e-05 | -0.0075532 | 0.02013 | -0.038638 | -0.00083531 | -0.011074 | -0.0042298 | 0.091553 | -0.059509 | 0 | 0.013733 | 0.14648 | 0.009155 | -0.10986 | 0.041199 | 0.11444 | 0.013733 | 0.5722 | 0.55389 | 0.013733 | -0.050354 | 122.0627 | 121.9437 | -0.43945 | 121.994 | 122.0673 | 0.1236 | -0.49438 | 122.0673 | 122.0032 | -0.013732 | 122.0947 | 122.0673 | 0.064087 | -0.032043 | 122.2 | 122.1451 | 122.0535 | -0.6958 | 122.6257 | 122.6074 | 122.168 | -0.63629
1980.4844 | 122.8088 | -122.0444 | 0.59967 | -0.0078584 | -0.014529 | 0.012074 | 0.033673 | -0.0090062 | -0.032101 | 0.0008203 | -0.0075532 | 0.023334 | -0.039065 | -0.00019431 | -0.0068018 | -0.0016662 | 0.10986 | -0.022888 | 0.022888 | 0.045776 | 0.13275 | 0.022888 | -0.1236 | 0 | 0.1236 | -0.027466 | 0.57678 | 0.56305 | 0.018311 | -0.050354 | 122.0673 | 121.9208 | -0.46692 | 122.0215 | 122.0901 | 0.16937 | -0.48981 | 122.0627 | 121.994 | -0.022888 | 122.0444 | 122.0169 | 0.022888 | -0.036621 | 122.1771 | 122.1542 | 122.0673 | -0.72327 | 122.6212 | 122.6074 | 122.168 | -0.65002
1982.2031 | 122.8638 | -122.0581 | 0.58136 | -0.00022891 | -0.014956 | 0.013142 | 0.03346 | -0.011783 | -0.034665 | -3.4096e-05 | -0.0075532 | 0.020557 | -0.038638 | -0.0021169 | -0.011715 | -0.0020934 | 0.073242 | -0.054932 | 0.013733 | 0.018311 | 0.1236 | 0.018311 | -0.10986 | 0.041199 | 0.13733 | 0.022888 | 0.55847 | 0.54474 | 0.027466 | -0.018311 | 122.0764 | 121.9482 | -0.45776 | 122.0032 | 122.0764 | 0.12817 | -0.50812 | 122.0856 | 122.0398 | -0.022888 | 122.0993 | 122.081 | 0.041199 | -0.036621 | 122.1817 | 122.1313 | 122.0718 | -0.69122 | 122.6166 | 122.6028 | 122.1954 | -0.59967
1984 | 122.7264 | -122.1085 | 0.62256 | -0.0078584 | -0.02051 | 0.01656 | 0.03645 | -0.011997 | -0.042355 | -0.0008887 | 7.627e-05 | 0.013721 | -0.038638 | -0.0038259 | -0.015347 | 0.00089722 | 0.07782 | 0.022888 | 0.082397 | 0.050354 | 0.10071 | 0.036621 | -0.073242 | 0.050354 | 0.18768 | 0.068665 | 0.53101 | 0.51727 | 0.050354 | -0.032043 | 122.1451 | 122.0352 | -0.52185 | 122.1313 | 122.1588 | 0.1236 | -0.54474 | 122.1588 | 122.0764 | -0.091553 | 122.1588 | 122.1771 | 0.10071 | -0.10529 | 122.2092 | 122.1863 | 122.1909 | -0.6958 | 122.6395 | 122.6257 | 122.2961 | -0.6546
1985.7812 | 122.7264 | -122.1405 | 0.59052 | -0.0078584 | -0.022005 | 0.017842 | 0.037732 | -0.010715 | -0.039792 | -0.0017431 | 0.0077058 | 0.019062 | -0.037783 | -0.0016897 | -0.014919 | -0.0023072 | 0.1236 | 0.036621 | 0.10986 | 0.045776 | 0.10071 | 0.050354 | -0.073242 | 0.086975 | 0.20142 | 0.07782 | 0.51727 | 0.5127 | 0.036621 | -0.018311 | 122.1909 | 122.0673 | -0.48981 | 122.1771 | 122.1863 | 0.11902 | -0.46692 | 122.1771 | 122.1222 | -0.073242 | 122.2275 | 122.2183 | 0.096131 | -0.07782 | 122.2412 | 122.2641 | 122.2504 | -0.66376 | 122.6578 | 122.6532 | 122.3419 | -0.60883
1987.5625 | 122.8455 | -122.0718 | 0.55389 | -0.0078584 | -0.013247 | 0.014637 | 0.03346 | -0.012211 | -0.031887 | -0.0008887 | 7.627e-05 | 0.019916 | -0.036929 | -0.00040791 | -0.011715 | -0.0010254 | 0.064087 | -0.036621 | -0.009155 | 0.004578 | 0.13733 | 0.013733 | -0.11444 | 0.022888 | 0.10986 | -0.018311 | 0.54016 | 0.53558 | 0.009155 | -0.045776 | 122.0856 | 121.9574 | -0.41656 | 122.0352 | 122.0764 | 0.11902 | -0.48981 | 122.081 | 122.0261 | -0.013733 | 122.0947 | 122.0535 | 0.027465 | -0.018311 | 122.2092 | 122.1359 | 122.0627 | -0.66834 | 122.612 | 122.6074 | 122.1817 | -0.59967
1989.3438 | 122.7127 | -122.1588 | 0.59509 | -0.0078584 | -0.017519 | 0.012928 | 0.036664 | -0.00922 | -0.040646 | -0.0028113 | 7.627e-05 | 0.01543 | -0.03757 | -0.0025443 | -0.011715 | -0.00038438 | 0.091553 | 0.068665 | 0.09613 | 0.050354 | 0.091553 | 0.054932 | -0.073242 | 0.068665 | 0.20142 | 0.068665 | 0.52185 | 0.49439 | 0.036621 | -0.045776 | 122.2137 | 122.0856 | -0.50354 | 122.2275 | 122.2092 | 0.1236 | -0.50354 | 122.1954 | 122.113 | -0.073242 | 122.2275 | 122.2275 | 0.11444 | -0.10071 | 122.2504 | 122.2504 | 122.2549 | -0.66834 | 122.6807 | 122.6532 | 122.3602 | -0.64087
1991.1406 | 122.8271 | -122.1176 | 0.54932 | -0.00022891 | -0.017733 | 0.010579 | 0.033032 | -0.012211 | -0.034878 | 0.0003931 | 7.627e-05 | 0.01778 | -0.038638 | -0.0014761 | -0.012142 | -0.00059818 | 0.16479 | 0.059509 | 0.10986 | 0.10071 | 0.09613 | 0.082397 | -0.068665 | 0.13733 | 0.21973 | 0.10529 | 0.49439 | 0.46234 | 0.027466 | -0.013733 | 122.2 | 122.049 | -0.45319 | 122.1771 | 122.2183 | 0.16937 | -0.38452 | 122.1451 | 122.1039 | -0.054931 | 122.2549 | 122.2229 | 0.11902 | -0.086975 | 122.2137 | 122.2824 | 122.2275 | -0.61798 | 122.612 | 122.58 | 122.3373 | -0.56305
1992.8906 | 122.7997 | -122.1268 | 0.54932 | -0.00022891 | -0.014956 | 0.01421 | 0.035382 | -0.011783 | -0.032528 | 0.0016749 | -0.0075532 | 0.02013 | -0.03757 | 0.00044649 | -0.010861 | -0.001239 | 0.050354 | -0.059509 | -0.009155 | 0.022888 | 0.1236 | 0.022888 | -0.1236 | -0.018311 | 0.091553 | -0.045776 | 0.54474 | 0.49896 | -0.004578 | -0.068665 | 122.1497 | 122.0032 | -0.42572 | 122.0673 | 122.1497 | 0.14648 | -0.49896 | 122.1222 | 122.0581 | -0.004577 | 122.1085 | 122.081 | 0.022889 | -0.050354 | 122.2504 | 122.1771 | 122.1176 | -0.67291 | 122.6715 | 122.6257 | 122.2183 | -0.61798
1994.6875 | 122.7951 | -122.0901 | 0.55389 | -0.00022891 | -0.014101 | 0.012288 | 0.035169 | -0.013706 | -0.034451 | 0.0027429 | -0.0075532 | 0.021198 | -0.036929 | -0.0019033 | -0.0085108 | -0.0014526 | 0.054932 | -0.032043 | 0.009155 | 0.018311 | 0.13733 | 0.022888 | -0.10529 | -0.013733 | 0.11444 | -0.041199 | 0.53558 | 0.53558 | 0.027466 | -0.045776 | 122.113 | 121.9849 | -0.41656 | 122.0581 | 122.1085 | 0.1236 | -0.49896 | 122.1176 | 122.0444 | -0.018311 | 122.0764 | 122.0489 | 0.004577 | -0.018311 | 122.2275 | 122.1451 | 122.0993 | -0.65918 | 122.6257 | 122.6257 | 122.2046 | -0.59967
1996.4688 | 122.7631 | -122.1451 | 0.55389 | -0.00022891 | -0.020937 | 0.015919 | 0.035382 | -0.015842 | -0.04321 | 0.0001795 | 7.627e-05 | 0.013721 | -0.037356 | -0.0014761 | -0.015774 | 0.00089722 | 0.091553 | 0.059509 | 0.11444 | 0.073242 | 0.10529 | 0.054932 | -0.091553 | 0.10986 | 0.2655 | 0.12817 | 0.47607 | 0.48523 | 0.050354 | -0.032043 | 122.2 | 122.0535 | -0.44861 | 122.2046 | 122.2183 | 0.16479 | -0.46234 | 122.1954 | 122.113 | -0.07782 | 122.2549 | 122.2733 | 0.16022 | -0.068665 | 122.2504 | 122.2366 | 122.2595 | -0.64545 | 122.6212 | 122.6303 | 122.4106 | -0.58594
1998.1875 | 122.8409 | -122.1268 | 0.54016 | -0.00022891 | -0.015597 | 0.011647 | 0.034741 | -0.010074 | -0.035092 | -0.0017431 | 7.627e-05 | 0.022693 | -0.038424 | -0.00083531 | -0.010647 | -0.0023072 | 0.054932 | -0.091553 | -0.004578 | 0.022888 | 0.14191 | 0.013733 | -0.10529 | 0.018311 | 0.10071 | -0.036621 | 0.51727 | 0.50354 | 0.013733 | -0.059509 | 122.1405 | 122.0215 | -0.39825 | 122.0352 | 122.1497 | 0.12817 | -0.48523 | 122.1405 | 122.0673 | -0.022888 | 122.1451 | 122.0901 | 0.022888 | -0.036621 | 122.2687 | 122.1817 | 122.1222 | -0.64545 | 122.644 | 122.6303 | 122.2275 | -0.59967
1999.9844 | 122.8592 | -122.1176 | 0.49896 | -0.00022891 | -0.016024 | 0.013142 | 0.036878 | -0.010929 | -0.036587 | 0.0001795 | -0.0075532 | 0.019062 | -0.035434 | 0.00066009 | -0.012142 | -0.0023072 | 0.07782 | -0.013733 | 0.027466 | 0.054932 | 0.13275 | 0.022888 | -0.11902 | 0.018311 | 0.16937 | 0.009155 | 0.50354 | 0.48523 | 0 | -0.054932 | 122.1405 | 121.9986 | -0.36621 | 122.1039 | 122.1725 | 0.17395 | -0.42114 | 122.1176 | 122.0627 | 0.004578 | 122.1359 | 122.1268 | 0.064087 | -0.013733 | 122.2504 | 122.1954 | 122.1451 | -0.61798 | 122.6212 | 122.6028 | 122.287 | -0.55389
2001.7188 | 122.8546 | -122.1405 | 0.5127 | -0.00022891 | -0.014529 | 0.013997 | 0.035809 | -0.011143 | -0.035092 | -0.0002477 | 0.0077058 | 0.018634 | -0.036074 | -0.00040791 | -0.01257 | -0.0010254 | 0.091553 | 0 | 0.036621 | 0.050354 | 0.13733 | 0.004578 | -0.11444 | 0.059509 | 0.18768 | 0.022888 | 0.50812 | 0.50812 | 0.013733 | -0.054932 | 122.1451 | 122.0261 | -0.37537 | 122.1405 | 122.1909 | 0.16479 | -0.42114 | 122.1542 | 122.0856 | -0.004577 | 122.2 | 122.1634 | 0.07782 | -0.004577 | 122.2778 | 122.2321 | 122.1771 | -0.62714 | 122.6486 | 122.6486 | 122.3282 | -0.56763
2003.5156 | 122.7631 | -122.1634 | 0.54932 | -0.0078584 | -0.01581 | 0.017201 | 0.036878 | -0.010074 | -0.045559 | -0.0004613 | 0.0077058 | 0.015216 | -0.038851 | -0.0040395 | -0.014706 | 0.0013244 | 0.059509 | 0.009155 | 0.082397 | 0.054932 | 0.12817 | 0.036621 | -0.073242 | 0.059509 | 0.20599 | 0.09613 | 0.46234 | 0.48065 | 0.059509 | -0.032043 | 122.2 | 122.0901 | -0.42114 | 122.1725 | 122.2183 | 0.12817 | -0.48981 | 122.2229 | 122.1313 | -0.086975 | 122.2229 | 122.2595 | 0.12817 | -0.068664 | 122.2916 | 122.2229 | 122.2458 | -0.62256 | 122.6257 | 122.644 | 122.3694 | -0.58136
2005.2344 | 122.731 | -122.1634 | 0.54932 | -0.0078584 | -0.018801 | 0.014424 | 0.039441 | -0.01157 | -0.040005 | -0.0030249 | -0.0075532 | 0.015216 | -0.036288 | -0.00083531 | -0.015774 | -0.00038438 | 0.13275 | 0.09613 | 0.14191 | 0.091553 | 0.10071 | 0.027466 | -0.091553 | 0.10529 | 0.29297 | 0.12817 | 0.46234 | 0.45776 | 0.041199 | -0.018311 | 122.1909 | 122.0718 | -0.44861 | 122.2595 | 122.2549 | 0.18311 | -0.41657 | 122.2046 | 122.1451 | -0.086975 | 122.2687 | 122.2916 | 0.14649 | -0.091552 | 122.2641 | 122.2961 | 122.3053 | -0.64087 | 122.6257 | 122.6212 | 122.4564 | -0.56763
2007.0156 | 122.7631 | -122.1817 | 0.54932 | -0.015487 | -0.019442 | 0.016346 | 0.034955 | -0.0090062 | -0.042141 | -0.0038793 | 7.627e-05 | 0.01543 | -0.038851 | -0.00083531 | -0.01321 | -0.00017078 | 0.054932 | 0.004578 | 0.082397 | 0.054932 | 0.09613 | 0.045776 | -0.10071 | 0.054932 | 0.20142 | 0.07782 | 0.46234 | 0.46234 | 0.036621 | -0.032043 | 122.2275 | 122.081 | -0.45319 | 122.1863 | 122.2366 | 0.15564 | -0.49438 | 122.2183 | 122.1497 | -0.086975 | 122.2366 | 122.2595 | 0.10986 | -0.086975 | 122.2778 | 122.2366 | 122.2641 | -0.65002 | 122.644 | 122.644 | 122.3831 | -0.58136
2008.7969 | 122.8729 | -122.1451 | 0.50354 | -0.0078584 | -0.014742 | 0.012288 | 0.032178 | -0.010288 | -0.035519 | -0.0002477 | -0.015182 | 0.020343 | -0.040347 | 0.0017283 | -0.01022 | -0.0031616 | 0.073242 | -0.073242 | -0.018311 | 0.013733 | 0.13275 | 0.004578 | -0.1236 | 0.027466 | 0.10529 | -0.004578 | 0.50812 | 0.48065 | 0 | -0.059509 | 122.1497 | 122.0215 | -0.37079 | 122.0718 | 122.1588 | 0.13733 | -0.4303 | 122.1451 | 122.0856 | 0.004578 | 122.1725 | 122.1405 | 0.054931 | -0.022888 | 122.2778 | 122.2183 | 122.1268 | -0.62714 | 122.6532 | 122.6257 | 122.2504 | -0.56305
2010.5938 | 122.8317 | -122.1542 | 0.50354 | -0.00022891 | -0.017519 | 0.013783 | 0.036878 | -0.010715 | -0.035305 | 0.0008203 | 7.627e-05 | 0.017566 | -0.037783 | -0.0021169 | -0.010861 | -0.001239 | 0.14191 | 0.068665 | 0.12817 | 0.10529 | 0.086975 | 0.050354 | -0.086975 | 0.11444 | 0.24261 | 0.10529 | 0.44403 | 0.43488 | 0.027466 | -0.022888 | 122.2046 | 122.0673 | -0.41656 | 122.2229 | 122.2595 | 0.19226 | -0.36163 | 122.1817 | 122.1313 | -0.059509 | 122.2687 | 122.2595 | 0.12817 | -0.068665 | 122.2412 | 122.2961 | 122.2824 | -0.59052 | 122.5983 | 122.5891 | 122.3969 | -0.52643
2012.3125 | 122.7585 | -122.1817 | 0.52643 | -0.00022891 | -0.016024 | 0.017628 | 0.036237 | -0.011356 | -0.042569 | -0.0025977 | 7.627e-05 | 0.017139 | -0.040988 | -0.0042531 | -0.013851 | -0.00017078 | 0.14191 | 0.10071 | 0.14191 | 0.091553 | 0.082397 | 0.054932 | -0.068665 | 0.10529 | 0.29755 | 0.1236 | 0.46234 | 0.43945 | 0.045776 | -0.036621 | 122.2366 | 122.113 | -0.44403 | 122.2824 | 122.2733 | 0.16022 | -0.38452 | 122.2275 | 122.1451 | -0.064087 | 122.287 | 122.3053 | 0.16022 | -0.086975 | 122.2641 | 122.3236 | 122.3236 | -0.59509 | 122.644 | 122.6212 | 122.4792 | -0.56305
2014.125 | 122.8683 | -122.1725 | 0.5127 | 0.0074006 | -0.015169 | 0.011006 | 0.035809 | -0.010502 | -0.033596 | 0.0018885 | -0.0075532 | 0.019489 | -0.036929 | -0.0019033 | -0.01257 | -0.0033752 | 0.059509 | -0.059509 | -0.013733 | 0.032043 | 0.13733 | 0.022888 | -0.10071 | 0.022888 | 0.13275 | -0.032043 | 0.49896 | 0.4715 | -0.004578 | -0.073242 | 122.1954 | 122.0718 | -0.37537 | 122.113 | 122.2046 | 0.13275 | -0.45319 | 122.168 | 122.0993 | -0.013733 | 122.1954 | 122.1405 | 0.041199 | -0.041198 | 122.3099 | 122.2321 | 122.1588 | -0.6134 | 122.6715 | 122.644 | 122.3053 | -0.58594
2015.8438 | 122.7402 | -122.2137 | 0.53101 | -0.00022891 | -0.018801 | 0.015065 | 0.036237 | -0.014988 | -0.038723 | 0.0001795 | -0.0075532 | 0.016925 | -0.037997 | -0.0027579 | -0.012356 | -0.0018798 | 0.1236 | 0.064087 | 0.1236 | 0.068665 | 0.07782 | 0.036621 | -0.073242 | 0.082397 | 0.20599 | 0.064087 | 0.45319 | 0.43945 | 0.036621 | -0.022888 | 122.2504 | 122.1405 | -0.45319 | 122.2778 | 122.2824 | 0.14191 | -0.40741 | 122.2504 | 122.1909 | -0.07782 | 122.2961 | 122.2778 | 0.086975 | -0.091553 | 122.2916 | 122.3373 | 122.3373 | -0.60425 | 122.6669 | 122.6532 | 122.4197 | -0.55389
2017.6406 | 122.8592 | -122.1542 | 0.5127 | -0.0078584 | -0.01346 | 0.010792 | 0.03645 | -0.0094336 | -0.036801 | 0.0003931 | 7.627e-05 | 0.01778 | -0.036929 | -0.0014761 | -0.012997 | -0.001239 | 0.14648 | 0.059509 | 0.10529 | 0.09613 | 0.10529 | 0.054932 | -0.091553 | 0.12817 | 0.24261 | 0.091553 | 0.45319 | 0.43488 | 0.050354 | -0.032043 | 122.2092 | 122.0627 | -0.40741 | 122.2137 | 122.2504 | 0.18768 | -0.36621 | 122.2046 | 122.1222 | -0.059509 | 122.2824 | 122.2458 | 0.1236 | -0.07782 | 122.2595 | 122.3007 | 122.2595 | -0.60425 | 122.6074 | 122.5891 | 122.3969 | -0.54474
2019.4219 | 122.8592 | -122.1497 | 0.5127 | -0.0078584 | -0.017519 | 0.013142 | 0.036023 | -0.01157 | -0.032956 | 0.0006067 | -0.0075532 | 0.022052 | -0.036288 | -0.00083531 | -0.010433 | -0.0018798 | 0.11444 | 0.022888 | 0.050354 | 0.045776 | 0.11444 | 0.022888 | -0.10529 | 0.050354 | 0.17853 | 0.022888 | 0.48523 | 0.46234 | 0.018311 | -0.059509 | 122.1725 | 122.0444 | -0.39825 | 122.1725 | 122.1954 | 0.15106 | -0.39825 | 122.168 | 122.0901 | -0.027466 | 122.2 | 122.1725 | 0.082397 | -0.050354 | 122.2641 | 122.2641 | 122.2 | -0.61798 | 122.6349 | 122.612 | 122.3282 | -0.5722
2021.1562 | 122.8043 | -122.1771 | 0.5127 | -0.00022891 | -0.016238 | 0.013569 | 0.040296 | -0.011143 | -0.038723 | 0.0010339 | -0.015182 | 0.019702 | -0.035861 | -0.00062151 | -0.014279 | -0.0010254 | 0.041199 | -0.041199 | -0.013733 | 0.018311 | 0.1236 | 0.009155 | -0.1236 | 0 | 0.14191 | -0.018311 | 0.49896 | 0.49439 | -0.004578 | -0.073242 | 122.1863 | 122.0535 | -0.3891 | 122.1359 | 122.1954 | 0.14191 | -0.4715 | 122.1725 | 122.1039 | -0.013733 | 122.1771 | 122.1588 | 0.054931 | -0.01831 | 122.3007 | 122.2183 | 122.1634 | -0.63629 | 122.6761 | 122.6715 | 122.319 | -0.58594
2022.9375 | 122.8821 | -122.1588 | 0.50354 | -0.0078584 | -0.017946 | 0.012501 | 0.034955 | -0.010074 | -0.037014 | 0.0008203 | -0.0075532 | 0.017353 | -0.038424 | 0.00044649 | -0.011715 | 0.00025642 | 0.082397 | -0.027466 | 0.041199 | 0.041199 | 0.11444 | 0.009155 | -0.10529 | 0.082397 | 0.18768 | 0.050354 | 0.46692 | 0.45776 | 0.041199 | -0.027466 | 122.168 | 122.0535 | -0.3891 | 122.1313 | 122.2 | 0.14649 | -0.42114 | 122.2 | 122.1313 | -0.036621 | 122.2412 | 122.2092 | 0.07782 | -0.045776 | 122.2733 | 122.2412 | 122.2 | -0.60883 | 122.6257 | 122.6166 | 122.3465 | -0.53101
2024.7344 | 122.8317 | -122.1954 | 0.49439 | -0.00022891 | -0.014101 | 0.014637 | 0.032605 | -0.011356 | -0.034665 | 0.0031703 | 7.627e-05 | 0.021411 | -0.038424 | -0.0021169 | -0.010433 | -0.0010254 | 0.036621 | -0.09613 | -0.022888 | 0.004578 | 0.14191 | 0.004578 | -0.11444 | -0.036621 | 0.10071 | -0.050354 | 0.48523 | 0.4715 | -0.013733 | -0.082397 | 122.2 | 122.081 | -0.35248 | 122.0993 | 122.2 | 0.11902 | -0.45776 | 122.1817 | 122.113 | -0.009156 | 122.1588 | 122.1451 | 0.032043 | -0.022888 | 122.3373 | 122.2321 | 122.1725 | -0.60883 | 122.6807 | 122.6669 | 122.2961 | -0.57678
2026.5156 | 122.7814 | -122.2092 | 0.53558 | -0.0078584 | -0.018801 | 0.014424 | 0.034101 | -0.011997 | -0.041073 | -0.0019567 | -0.0075532 | 0.014789 | -0.038211 | -0.0038259 | -0.01321 | -0.00017078 | 0.11444 | 0.091553 | 0.1236 | 0.09613 | 0.082397 | 0.064087 | -0.073242 | 0.10071 | 0.26093 | 0.10986 | 0.44861 | 0.43488 | 0.032043 | -0.032043 | 122.2733 | 122.1359 | -0.45319 | 122.3007 | 122.3053 | 0.16937 | -0.42114 | 122.2412 | 122.1771 | -0.086975 | 122.3099 | 122.319 | 0.14191 | -0.10071 | 122.2916 | 122.3236 | 122.3328 | -0.60883 | 122.6578 | 122.644 | 122.4701 | -0.56763
2028.2812 | 122.7905 | -122.2046 | 0.50812 | -0.00022891 | -0.024782 | 0.017201 | 0.036664 | -0.011356 | -0.040432 | 0.0003931 | 0.0077058 | 0.01543 | -0.04056 | -0.0033987 | -0.013424 | 4.2822e-05 | 0.11902 | 0.1236 | 0.14648 | 0.10071 | 0.10071 | 0.041199 | -0.068665 | 0.12817 | 0.3067 | 0.15564 | 0.45319 | 0.44403 | 0.032043 | -0.050354 | 122.2458 | 122.1359 | -0.40741 | 122.3282 | 122.3053 | 0.16937 | -0.3891 | 122.2366 | 122.1542 | -0.054932 | 122.3328 | 122.3602 | 0.20599 | -0.064087 | 122.3053 | 122.3236 | 122.3511 | -0.57678 | 122.6578 | 122.6486 | 122.5113 | -0.55847
2030.0625 | 122.7768 | -122.2046 | 0.5127 | -0.00022891 | -0.020083 | 0.016133 | 0.037305 | -0.012424 | -0.041073 | -0.0017431 | -0.0075532 | 0.016712 | -0.041629 | -0.0038259 | -0.014279 | -0.0016662 | 0.14648 | 0.11444 | 0.13733 | 0.09613 | 0.082397 | 0.041199 | -0.091553 | 0.10071 | 0.29297 | 0.1236 | 0.43945 | 0.4303 | 0.027466 | -0.054932 | 122.2458 | 122.113 | -0.4303 | 122.319 | 122.3007 | 0.18768 | -0.36621 | 122.2321 | 122.1497 | -0.073242 | 122.3053 | 122.3282 | 0.17853 | -0.082397 | 122.287 | 122.3511 | 122.3419 | -0.60425 | 122.644 | 122.6349 | 122.4976 | -0.56763
2031.8438 | 122.8958 | -122.1771 | 0.47607 | -0.0078584 | -0.017306 | 0.012715 | 0.034741 | -0.012424 | -0.034878 | -0.0006751 | 7.627e-05 | 0.017353 | -0.038851 | -0.0012625 | -0.0095788 | -0.0031616 | 0.11444 | 0.018311 | 0.091553 | 0.068665 | 0.09613 | 0.054932 | -0.059509 | 0.10529 | 0.2243 | 0.073242 | 0.45319 | 0.44403 | 0.036621 | -0.041199 | 122.2321 | 122.1176 | -0.37994 | 122.1954 | 122.2458 | 0.12817 | -0.36163 | 122.2137 | 122.1359 | -0.022888 | 122.2824 | 122.2504 | 0.11444 | -0.032043 | 122.2733 | 122.2916 | 122.2687 | -0.53558 | 122.6303 | 122.6212 | 122.4014 | -0.51727
2033.5625 | 122.7448 | -122.2504 | 0.53101 | -0.0078584 | -0.020296 | 0.015919 | 0.036237 | -0.013065 | -0.039578 | -0.0028113 | 0.0077058 | 0.015857 | -0.039279 | -0.0014761 | -0.014279 | -0.00017078 | 0.13275 | 0.068665 | 0.11902 | 0.073242 | 0.091553 | 0.054932 | -0.091553 | 0.086975 | 0.20599 | 0.082397 | 0.43488 | 0.42572 | 0.032043 | -0.041199 | 122.3053 | 122.1588 | -0.43945 | 122.319 | 122.3236 | 0.16479 | -0.39825 | 122.2824 | 122.2092 | -0.096131 | 122.3373 | 122.3328 | 0.1236 | -0.10529 | 122.3419 | 122.3831 | 122.3694 | -0.62256 | 122.6852 | 122.6761 | 122.4564 | -0.5722
2035.3438 | 122.8775 | -122.1725 | 0.48065 | 0.0074006 | -0.013674 | 0.012501 | 0.036237 | -0.01157 | -0.031674 | 0.0029565 | 0.0077058 | 0.020984 | -0.037783 | 1.9292e-05 | -0.010861 | -0.004016 | 0.082397 | -0.004578 | 0.041199 | 0.059509 | 0.14191 | 0.013733 | -0.10986 | 0.032043 | 0.1831 | 0.009155 | 0.45319 | 0.46234 | 0.004578 | -0.068665 | 122.1863 | 122.0627 | -0.33875 | 122.168 | 122.2321 | 0.16937 | -0.39826 | 122.1771 | 122.1039 | -0.027466 | 122.2046 | 122.1817 | 0.07782 | -0.018311 | 122.3145 | 122.2549 | 122.2137 | -0.59052 | 122.6257 | 122.6349 | 122.3557 | -0.54932
2037.125 | 122.7493 | -122.2321 | 0.53101 | -0.00022891 | -0.020937 | 0.014424 | 0.036237 | -0.013706 | -0.039578 | 0.0006067 | -0.015182 | 0.016925 | -0.038851 | -0.0023305 | -0.014065 | -0.00038438 | 0.07782 | 0.036621 | 0.086975 | 0.050354 | 0.10529 | 0.054932 | -0.068665 | 0.064087 | 0.20599 | 0.054932 | 0.43488 | 0.41657 | 0.013733 | -0.041199 | 122.287 | 122.1634 | -0.42572 | 122.2687 | 122.2824 | 0.11902 | -0.45319 | 122.2458 | 122.1909 | -0.096131 | 122.2961 | 122.287 | 0.096131 | -0.11444 | 122.3373 | 122.3099 | 122.319 | -0.59967 | 122.6669 | 122.6486 | 122.4381 | -0.5722
2038.8438 | 122.8775 | -122.1909 | 0.48065 | -0.0078584 | -0.017306 | 0.012928 | 0.037518 | -0.008579 | -0.035733 | -0.0013159 | 7.627e-05 | 0.019489 | -0.034793 | -0.00062151 | -0.008938 | -0.0027344 | 0.036621 | -0.068665 | -0.013733 | 0.004578 | 0.13275 | 0.032043 | -0.11902 | 0.009155 | 0.091553 | -0.045776 | 0.48523 | 0.44861 | -0.004578 | -0.064087 | 122.2229 | 122.0718 | -0.3479 | 122.1222 | 122.1954 | 0.1236 | -0.44403 | 122.1863 | 122.1268 | 0.004577 | 122.2 | 122.1451 | 0.018311 | -0.032044 | 122.3236 | 122.2275 | 122.1771 | -0.59967 | 122.6761 | 122.6395 | 122.2824 | -0.54474
2040.6406 | 122.818 | -122.2321 | 0.50354 | -0.00022891 | -0.016024 | 0.017415 | 0.037946 | -0.012852 | -0.041073 | -0.0043065 | -0.015182 | 0.014148 | -0.037997 | -0.0044669 | -0.014279 | -0.00017078 | 0.10529 | 0.10986 | 0.15106 | 0.086975 | 0.11902 | 0.036621 | -0.07782 | 0.1236 | 0.27924 | 0.12817 | 0.4303 | 0.41199 | 0.018311 | -0.032043 | 122.2687 | 122.1542 | -0.38452 | 122.3419 | 122.319 | 0.16479 | -0.39825 | 122.2504 | 122.2 | -0.073242 | 122.3557 | 122.3602 | 0.16022 | -0.091553 | 122.3511 | 122.3373 | 122.3831 | -0.58136 | 122.6624 | 122.644 | 122.5113 | -0.53558
2042.4219 | 122.8592 | -122.2321 | 0.48065 | -0.0078584 | -0.01581 | 0.010792 | 0.037305 | -0.013706 | -0.032528 | 0.0001795 | 7.627e-05 | 0.019702 | -0.035861 | -0.0027579 | -0.01022 | -0.0025208 | 0.045776 | -0.068665 | -0.013733 | 0.027466 | 0.12817 | 0.027466 | -0.10986 | -0.004578 | 0.082397 | -0.059509 | 0.4715 | 0.45319 | 0 | -0.064087 | 122.2595 | 122.1222 | -0.35248 | 122.1634 | 122.2595 | 0.13733 | -0.43488 | 122.2321 | 122.168 | -0.009155 | 122.2275 | 122.1725 | 0.004578 | -0.027466 | 122.3602 | 122.2778 | 122.2183 | -0.59052 | 122.7036 | 122.6852 | 122.3145 | -0.54474
2044.1562 | 122.7676 | -122.2595 | 0.48523 | -0.0078584 | -0.017092 | 0.016133 | 0.039014 | -0.01157 | -0.040646 | -0.0006751 | -0.015182 | 0.01543 | -0.036288 | -0.0036123 | -0.016842 | -0.0016662 | 0.11902 | 0.11444 | 0.16479 | 0.086975 | 0.086975 | 0.045776 | -0.091553 | 0.082397 | 0.29297 | 0.11902 | 0.41657 | 0.39825 | 0.036621 | -0.045776 | 122.3053 | 122.168 | -0.39825 | 122.374 | 122.3465 | 0.17853 | -0.36621 | 122.2961 | 122.2137 | -0.068664 | 122.3419 | 122.3785 | 0.16479 | -0.086975 | 122.3465 | 122.3785 | 122.4243 | -0.57678 | 122.6761 | 122.6578 | 122.5525 | -0.53101
2045.9531 | 122.7951 | -122.2549 | 0.48981 | -0.00022891 | -0.018374 | 0.013569 | 0.037946 | -0.012852 | -0.040219 | -0.0017431 | 7.627e-05 | 0.016284 | -0.03757 | -0.0016897 | -0.01321 | 4.2822e-05 | 0.068665 | 0.032043 | 0.09613 | 0.050354 | 0.10529 | 0.045776 | -0.10071 | 0.073242 | 0.22888 | 0.082397 | 0.41657 | 0.40741 | 0.032043 | -0.036621 | 122.3007 | 122.1542 | -0.38452 | 122.287 | 122.3053 | 0.15106 | -0.42114 | 122.287 | 122.2183 | -0.073242 | 122.3282 | 122.3373 | 0.11902 | -0.082397 | 122.3602 | 122.3236 | 122.3511 | -0.59052 | 122.6715 | 122.6624 | 122.4838 | -0.52643
2047.7344 | 122.8363 | -122.2275 | 0.44403 | 0.0074006 | -0.01282 | 0.01421 | 0.032392 | -0.00922 | -0.029538 | 0.0003931 | 7.627e-05 | 0.023975 | -0.039065 | 1.9292e-05 | -0.007229 | -0.004016 | 0.11902 | 0.004578 | 0.041199 | 0.045776 | 0.13275 | 0.041199 | -0.10986 | 0.045776 | 0.16937 | -0.009155 | 0.43945 | 0.41199 | -0.004578 | -0.073242 | 122.2687 | 122.1176 | -0.31128 | 122.2321 | 122.2733 | 0.15564 | -0.32501 | 122.2229 | 122.1542 | -0.004578 | 122.2733 | 122.2183 | 0.064087 | -0.032044 | 122.3602 | 122.3465 | 122.2687 | -0.55389 | 122.6669 | 122.6395 | 122.3969 | -0.51727
2049.4531 | 122.8912 | -122.2092 | 0.45776 | 0.0074006 | -0.01047 | 0.013997 | 0.033887 | -0.0098608 | -0.036801 | 0.0003931 | -0.0075532 | 0.020343 | -0.038424 | -0.0021169 | -0.0097924 | -0.0016662 | 0.07782 | -0.036621 | 0.013733 | 0.045776 | 0.1236 | 0.022888 | -0.12817 | 0.022888 | 0.17853 | -0.004578 | 0.44861 | 0.4303 | 0.009155 | -0.09613 | 122.2321 | 122.081 | -0.33417 | 122.1725 | 122.2549 | 0.17395 | -0.37994 | 122.2183 | 122.113 | -0.009156 | 122.2321 | 122.2046 | 0.091552 | -0.027466 | 122.3328 | 122.287 | 122.2229 | -0.58594 | 122.6578 | 122.6395 | 122.3877 | -0.55389
2051.2188 | 122.8775 | -122.2321 | 0.45319 | -0.0078584 | -0.012606 | 0.01656 | 0.034955 | -0.011356 | -0.034024 | 0.0031703 | -0.0075532 | 0.019916 | -0.037356 | -0.0012625 | -0.0097924 | 0.00047002 | 0.041199 | -0.073242 | -0.018311 | 0 | 0.14648 | 0.009155 | -0.13275 | 0 | 0.11902 | -0.022888 | 0.44861 | 0.4303 | 0 | -0.073242 | 122.2412 | 122.0993 | -0.3067 | 122.1588 | 122.2321 | 0.13275 | -0.41199 | 122.2321 | 122.1588 | -0.004578 | 122.2321 | 122.2092 | 0.050354 | -0.022888 | 122.3785 | 122.2733 | 122.2137 | -0.58594 | 122.6807 | 122.6624 | 122.3511 | -0.52643
2052.9531 | 122.8775 | -122.2412 | 0.44861 | -0.0078584 | -0.020296 | 0.01421 | 0.036237 | -0.010074 | -0.037014 | 0.0016749 | -0.0075532 | 0.012867 | -0.036929 | -0.0019033 | -0.010433 | 0.0015382 | 0.10529 | 0.018311 | 0.091553 | 0.068665 | 0.10529 | 0.059509 | -0.068665 | 0.09613 | 0.23346 | 0.086975 | 0.39825 | 0.38452 | 0.032043 | -0.050354 | 122.3007 | 122.1725 | -0.34332 | 122.2595 | 122.3099 | 0.13733 | -0.34332 | 122.2733 | 122.1909 | -0.050354 | 122.3373 | 122.3282 | 0.13733 | -0.064087 | 122.3465 | 122.3465 | 122.3328 | -0.51727 | 122.6395 | 122.6257 | 122.4747 | -0.49896
2054.7344 | 122.8455 | -122.2412 | 0.42572 | -0.00022891 | -0.016238 | 0.014424 | 0.034741 | -0.013706 | -0.033169 | 0.0018885 | -0.0075532 | 0.019489 | -0.037143 | -0.00062151 | -0.011288 | -0.00038438 | 0.1236 | 0.022888 | 0.054932 | 0.050354 | 0.1236 | 0.032043 | -0.1236 | 0.041199 | 0.18768 | 0 | 0.42572 | 0.41657 | -0.004578 | -0.064087 | 122.2733 | 122.1176 | -0.30212 | 122.2641 | 122.2916 | 0.17395 | -0.30212 | 122.2366 | 122.1771 | 0 | 122.2824 | 122.2412 | 0.064087 | -0.009155 | 122.3648 | 122.3648 | 122.2961 | -0.54932 | 122.6669 | 122.6578 | 122.4289 | -0.48981
2056.5156 | 122.8546 | -122.2595 | 0.45776 | -0.00022891 | -0.016024 | 0.013997 | 0.035596 | -0.011783 | -0.035092 | -0.0004613 | 7.627e-05 | 0.019275 | -0.037356 | -0.0014761 | -0.011074 | -0.00038438 | 0.018311 | -0.07782 | -0.018311 | 0.009155 | 0.12817 | 0.032043 | -0.11902 | -0.045776 | 0.082397 | -0.054932 | 0.42572 | 0.40741 | -0.009155 | -0.073242 | 122.2916 | 122.1405 | -0.32959 | 122.1817 | 122.2687 | 0.12817 | -0.43945 | 122.2504 | 122.1863 | -0.032044 | 122.2137 | 122.2046 | 0.01831 | -0.050354 | 122.3877 | 122.2778 | 122.2412 | -0.57678 | 122.6852 | 122.6669 | 122.3419 | -0.53101
2058.2969 | 122.9004 | -122.2275 | 0.44403 | -0.0078584 | -0.015597 | 0.013142 | 0.03645 | -0.014133 | -0.038296 | 0.0027429 | 7.627e-05 | 0.019916 | -0.036929 | 0.0015147 | -0.01257 | -0.00038438 | 0.041199 | -0.064087 | -0.004578 | 0.018311 | 0.10529 | 0.032043 | -0.10071 | 0.032043 | 0.13733 | 0.004578 | 0.41199 | 0.42572 | 0.004578 | -0.064087 | 122.2595 | 122.1268 | -0.33875 | 122.1634 | 122.2458 | 0.11902 | -0.40283 | 122.2321 | 122.1634 | -0.032044 | 122.2595 | 122.2321 | 0.068665 | -0.018311 | 122.3328 | 122.2687 | 122.2229 | -0.54474 | 122.6395 | 122.6532 | 122.3648 | -0.50812
2060.0938 | 122.9004 | -122.2595 | 0.43945 | -0.00022891 | -0.016238 | 0.013142 | 0.035809 | -0.012424 | -0.037442 | 0.0008203 | 7.627e-05 | 0.018848 | -0.037997 | -0.0036123 | -0.012783 | -0.002948 | 0.045776 | -0.041199 | 0.018311 | 0.041199 | 0.11902 | 0.018311 | -0.11444 | 0.009155 | 0.17853 | 0.004578 | 0.40741 | 0.40741 | -0.018311 | -0.073242 | 122.2778 | 122.1451 | -0.32043 | 122.2183 | 122.3007 | 0.15564 | -0.39368 | 122.2412 | 122.1863 | -0.032043 | 122.2687 | 122.2641 | 0.07782 | -0.032043 | 122.3785 | 122.3053 | 122.2778 | -0.55389 | 122.6669 | 122.6669 | 122.438 | -0.5127
2061.8125 | 122.7722 | -122.287 | 0.46692 | -0.00022891 | -0.015383 | 0.013783 | 0.038159 | -0.011356 | -0.041073 | 0.0016749 | 7.627e-05 | 0.015216 | -0.037356 | -0.0025443 | -0.014279 | -0.00017078 | 0.027466 | -0.045776 | 0.004578 | 0.004578 | 0.13733 | 0.022888 | -0.11902 | -0.036621 | 0.13733 | -0.027466 | 0.44861 | 0.40283 | -0.027466 | -0.086975 | 122.3099 | 122.168 | -0.32959 | 122.2412 | 122.2916 | 0.1236 | -0.43945 | 122.2595 | 122.2 | -0.018311 | 122.2504 | 122.2595 | 0.059509 | -0.064087 | 122.4243 | 122.3145 | 122.2916 | -0.58594 | 122.7356 | 122.6898 | 122.4243 | -0.55389
2063.5938 | 122.8683 | -122.2504 | 0.45319 | -0.00022891 | -0.014315 | 0.015278 | 0.034741 | -0.010715 | -0.035305 | -0.0017431 | -0.0075532 | 0.021839 | -0.035434 | -0.0019033 | -0.0082972 | -0.00017078 | -0.009155 | -0.091553 | -0.027466 | 0.009155 | 0.14191 | 0.018311 | -0.10986 | -0.018311 | 0.09613 | -0.050354 | 0.42114 | 0.42114 | -0.009155 | -0.082397 | 122.2687 | 122.1405 | -0.31128 | 122.1588 | 122.2595 | 0.11902 | -0.46234 | 122.2412 | 122.168 | -0.032043 | 122.2321 | 122.2 | 0.032043 | -0.032043 | 122.3923 | 122.2412 | 122.2229 | -0.56305 | 122.6715 | 122.6715 | 122.3465 | -0.53558
2065.3906 | 122.7585 | -122.2824 | 0.47607 | -0.015487 | -0.015169 | 0.013142 | 0.039655 | -0.0079382 | -0.041287 | -0.0011023 | 7.627e-05 | 0.01543 | -0.035647 | -0.0038259 | -0.016201 | -0.00017078 | 0.041199 | 0 | 0.032043 | 0.045776 | 0.11902 | 0.004578 | -0.10529 | -0.022888 | 0.14648 | -0.013733 | 0.40283 | 0.41657 | -0.036621 | -0.09613 | 122.287 | 122.1771 | -0.35706 | 122.2824 | 122.3282 | 0.15106 | -0.43488 | 122.2458 | 122.1863 | -0.073242 | 122.2595 | 122.2687 | 0.082397 | -0.059509 | 122.4014 | 122.3236 | 122.3145 | -0.58136 | 122.6852 | 122.699 | 122.4289 | -0.5722
2067.1719 | 122.8317 | -122.2733 | 0.45776 | -0.0078584 | -0.012179 | 0.013356 | 0.034741 | -0.011783 | -0.033169 | 0.0014613 | 7.627e-05 | 0.018634 | -0.037356 | -0.00083531 | -0.0095788 | 0.00068362 | 0.050354 | -0.036621 | 0.009155 | 0.022888 | 0.14191 | 0.027466 | -0.11444 | -0.032043 | 0.11902 | -0.045776 | 0.4303 | 0.40283 | -0.036621 | -0.082397 | 122.3007 | 122.1588 | -0.31586 | 122.2366 | 122.2961 | 0.13733 | -0.40741 | 122.2366 | 122.1909 | -0.027466 | 122.2412 | 122.2275 | 0.036621 | -0.054932 | 122.4152 | 122.3236 | 122.2824 | -0.5722 | 122.7036 | 122.6761 | 122.3923 | -0.54016
2068.8906 | 122.8546 | -122.2595 | 0.45319 | -0.00022891 | -0.014742 | 0.011433 | 0.03346 | -0.011997 | -0.037869 | -0.0008887 | -0.015182 | 0.019062 | -0.036715 | -0.00062151 | -0.010861 | -0.00038438 | 0.009155 | -0.082397 | -0.018311 | 0.004578 | 0.14191 | 0.009155 | -0.11902 | -0.027466 | 0.082397 | -0.027466 | 0.43945 | 0.41657 | 0 | -0.07782 | 122.2687 | 122.1405 | -0.31128 | 122.1771 | 122.2641 | 0.1236 | -0.44403 | 122.2595 | 122.1817 | -0.013733 | 122.2321 | 122.2321 | 0.050354 | -0.036621 | 122.4014 | 122.2687 | 122.2412 | -0.5722 | 122.699 | 122.6761 | 122.3419 | -0.53101
2070.6719 | 122.8363 | -122.3007 | 0.4303 | -0.0078584 | -0.016238 | 0.014851 | 0.037732 | -0.011356 | -0.037442 | -0.0006751 | 0.0077058 | 0.019702 | -0.03757 | -0.00062151 | -0.015347 | 0.00047002 | 0.013733 | -0.054932 | -0.013733 | 0.004578 | 0.15106 | 0.018311 | -0.11444 | -0.050354 | 0.13733 | -0.032043 | 0.42572 | 0.42572 | -0.022888 | -0.09613 | 122.319 | 122.1863 | -0.27924 | 122.2458 | 122.3053 | 0.11902 | -0.41657 | 122.2778 | 122.2046 | -0.004578 | 122.2504 | 122.2687 | 0.064087 | -0.004578 | 122.4518 | 122.3145 | 122.287 | -0.54474 | 122.7264 | 122.7264 | 122.438 | -0.52643
2072.4531 | 122.905 | -122.2733 | 0.3891 | 0.0074006 | -0.015383 | 0.012928 | 0.037305 | -0.010074 | -0.039364 | -0.0011023 | 7.627e-05 | 0.017139 | -0.034579 | -0.0010489 | -0.012356 | -0.001239 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.13733 | 0.013733 | -0.11902 | 0.018311 | 0.09613 | -0.013733 | 0.37079 | 0.35248 | -0.004578 | -0.073242 | 122.287 | 122.1542 | -0.25177 | 122.2137 | 122.2916 | 0.13733 | -0.35248 | 122.2687 | 122.2 | -0.01831 | 122.2916 | 122.2595 | 0.059509 | -0.036621 | 122.4106 | 122.3099 | 122.2595 | -0.50812 | 122.644 | 122.6257 | 122.3694 | -0.46234
2074.1719 | 122.7722 | -122.3328 | 0.41199 | -0.00022891 | -0.014956 | 0.012288 | 0.038587 | -0.013706 | -0.040005 | 0.0006067 | -0.0075532 | 0.015857 | -0.036074 | -0.0036123 | -0.015347 | 0.00068362 | 0.027466 | -0.041199 | 0.009155 | 0.013733 | 0.15106 | 0.013733 | -0.13275 | -0.018311 | 0.1236 | -0.013733 | 0.39825 | 0.38452 | -0.032043 | -0.086975 | 122.3465 | 122.2 | -0.26092 | 122.2916 | 122.3465 | 0.14648 | -0.38452 | 122.3007 | 122.2458 | -0.013733 | 122.3145 | 122.319 | 0.073242 | -0.027466 | 122.4838 | 122.3602 | 122.3419 | -0.54474 | 122.731 | 122.7173 | 122.4564 | -0.49896
2075.9688 | 122.905 | -122.2687 | 0.42572 | -0.00022891 | -0.017519 | 0.011219 | 0.036023 | -0.01456 | -0.034451 | -0.0013159 | 0.0077058 | 0.017566 | -0.037997 | 0.00044649 | -0.012783 | -0.0010254 | 0.041199 | -0.091553 | -0.022888 | 0.013733 | 0.16022 | 0.027466 | -0.11902 | 0 | 0.10529 | -0.045776 | 0.41199 | 0.42114 | -0.022888 | -0.07782 | 122.2961 | 122.1497 | -0.2655 | 122.1771 | 122.2824 | 0.13275 | -0.38452 | 122.2458 | 122.1909 | -0.013733 | 122.2687 | 122.2229 | 0.032044 | -0.004577 | 122.4289 | 122.3099 | 122.2458 | -0.54474 | 122.6807 | 122.6898 | 122.374 | -0.50354
2077.75 | 122.8867 | -122.287 | 0.42114 | -0.00022891 | -0.013674 | 0.01186 | 0.037518 | -0.013279 | -0.03616 | -0.0036657 | 7.627e-05 | 0.019275 | -0.036502 | -0.00062151 | -0.012997 | -0.00059818 | 0.018311 | -0.045776 | 0.018311 | 0.032043 | 0.11902 | 0.004578 | -0.13275 | -0.013733 | 0.16022 | -0.018311 | 0.40741 | 0.40741 | -0.013733 | -0.07782 | 122.2916 | 122.1542 | -0.30212 | 122.2412 | 122.319 | 0.16479 | -0.40283 | 122.2733 | 122.2092 | -0.013733 | 122.2733 | 122.2687 | 0.059509 | -0.013733 | 122.406 | 122.3053 | 122.3053 | -0.55389 | 122.6944 | 122.6944 | 122.4472 | -0.49896
2079.5156 | 122.8683 | -122.2824 | 0.41657 | -0.015487 | -0.012392 | 0.011647 | 0.040082 | -0.011143 | -0.034024 | 0.0001795 | -0.0075532 | 0.020343 | -0.035861 | -0.0014761 | -0.012356 | -0.0025208 | 0.054932 | -0.022888 | 0.036621 | 0.041199 | 0.1236 | 0.022888 | -0.13733 | -0.022888 | 0.1236 | -0.050354 | 0.40741 | 0.38452 | -0.013733 | -0.086975 | 122.3053 | 122.1451 | -0.29297 | 122.2595 | 122.3236 | 0.17853 | -0.36163 | 122.2687 | 122.1954 | -0.009155 | 122.2595 | 122.2321 | 0.036621 | -0.032044 | 122.406 | 122.3373 | 122.319 | -0.55389 | 122.6898 | 122.6669 | 122.406 | -0.50354
2081.3125 | 122.7722 | -122.319 | 0.44403 | -0.0078584 | -0.016238 | 0.012501 | 0.038587 | -0.010074 | -0.039792 | -3.4096e-05 | 0.015335 | 0.018421 | -0.037997 | -0.0012625 | -0.013638 | 0.00025642 | -0.013733 | -0.027466 | 0.022888 | 0.013733 | 0.1236 | 0.032043 | -0.10529 | -0.027466 | 0.14191 | -0.018311 | 0.39825 | 0.3891 | -0.018311 | -0.07782 | 122.3511 | 122.2137 | -0.32044 | 122.2916 | 122.3328 | 0.11902 | -0.45776 | 122.3007 | 122.2412 | -0.045777 | 122.2916 | 122.3007 | 0.059509 | -0.054932 | 122.4426 | 122.3053 | 122.3419 | -0.54932 | 122.7173 | 122.7081 | 122.4609 | -0.52185
2083.0938 | 122.8226 | -122.3145 | 0.43488 | -0.015487 | -0.021151 | 0.013569 | 0.037091 | -0.013279 | -0.043423 | -0.0030249 | 7.627e-05 | 0.016498 | -0.039279 | -0.0048941 | -0.016628 | 0.00068362 | 0.059509 | 0.045776 | 0.10529 | 0.073242 | 0.11444 | 0.036621 | -0.07782 | 0.091553 | 0.24261 | 0.10986 | 0.36621 | 0.36163 | 0.045776 | -0.054932 | 122.3511 | 122.2366 | -0.32043 | 122.3602 | 122.3877 | 0.15106 | -0.37537 | 122.3602 | 122.2595 | -0.068664 | 122.406 | 122.4243 | 0.16479 | -0.073242 | 122.4289 | 122.374 | 122.4197 | -0.5127 | 122.6807 | 122.6761 | 122.5571 | -0.48981
2084.8125 | 122.8363 | -122.4792 | 0.27924 | -0.0078584 | -0.016238 | 0.014851 | 0.038373 | -0.014347 | -0.039578 | -0.0015295 | 0.0077058 | 0.0088076 | -0.029452 | -0.0036123 | -0.014065 | -0.0025208 | 0.1236 | 0.11444 | 0.15564 | 0.09613 | 0.10986 | 0.054932 | -0.082397 | 0.16022 | 0.24261 | 0.1236 | 0.21515 | 0.17395 | 0.018311 | -0.059509 | 122.5342 | 122.3969 | -0.16937 | 122.5937 | 122.5754 | 0.17853 | -0.15564 | 122.4976 | 122.4197 | -0.064087 | 122.6395 | 122.6028 | 0.1831 | -0.10529 | 122.5891 | 122.6028 | 122.6349 | -0.36163 | 122.6944 | 122.6532 | 122.7219 | -0.33874
2086.5938 | 122.8958 | -122.4655 | 0.2243 | -0.00022891 | -0.018587 | 0.015706 | 0.033246 | -0.012852 | -0.03616 | -0.0034521 | -0.0075532 | 0.012439 | -0.030093 | -0.0023305 | -0.0068018 | -0.0023072 | 0.059509 | -0.045776 | -0.032043 | 0.022888 | 0.12817 | 0.018311 | -0.13275 | 0.041199 | 0.086975 | -0.004578 | 0.22888 | 0.21057 | -0.041199 | -0.10071 | 122.4838 | 122.3328 | -0.09613 | 122.4197 | 122.4884 | 0.15564 | -0.16479 | 122.4243 | 122.3648 | 0.004578 | 122.5067 | 122.4609 | 0.09613 | -0.013733 | 122.5937 | 122.525 | 122.4335 | -0.35706 | 122.6944 | 122.6761 | 122.5525 | -0.32501
2088.375 | 122.8271 | -122.3145 | 0.41657 | -0.0078584 | -0.016665 | 0.015278 | 0.037946 | -0.010929 | -0.037014 | -0.0023839 | -0.0075532 | 0.020557 | -0.038211 | -0.0046805 | -0.012783 | -0.0016662 | 0.045776 | -0.054932 | -0.018311 | 0.013733 | 0.15106 | 0.009155 | -0.11902 | -0.032043 | 0.13275 | -0.045776 | 0.38452 | 0.39825 | -0.036621 | -0.091553 | 122.3236 | 122.1954 | -0.2655 | 122.2595 | 122.3282 | 0.13275 | -0.37079 | 122.2778 | 122.2229 | -0.032044 | 122.2824 | 122.2687 | 0.045777 | -0.018311 | 122.4655 | 122.3602 | 122.2961 | -0.53558 | 122.699 | 122.7127 | 122.4472 | -0.50812
2090.1719 | 122.7631 | -122.3419 | 0.4303 | -0.015487 | -0.017519 | 0.018696 | 0.036023 | -0.00922 | -0.040219 | -0.0034521 | 7.627e-05 | 0.017139 | -0.038211 | -0.0048941 | -0.012142 | -0.00017078 | 0.10529 | 0.09613 | 0.13733 | 0.10529 | 0.10986 | 0.050354 | -0.064087 | 0.064087 | 0.26093 | 0.082397 | 0.3479 | 0.33875 | 0.004578 | -0.041199 | 122.3923 | 122.2778 | -0.32044 | 122.438 | 122.4472 | 0.16937 | -0.32501 | 122.3465 | 122.3007 | -0.082398 | 122.406 | 122.4243 | 0.1236 | -0.091553 | 122.4518 | 122.4472 | 122.4792 | -0.49439 | 122.6898 | 122.6807 | 122.6028 | -0.4715
2091.9062 | 122.8271 | -122.438 | 0.32959 | -0.015487 | -0.019442 | 0.018483 | 0.038373 | -0.014133 | -0.040432 | -0.0015295 | 7.627e-05 | 0.0081668 | -0.032016 | -0.0053213 | -0.014706 | -0.001239 | 0.068665 | 0.045776 | 0.086975 | 0.064087 | 0.10529 | 0.064087 | -0.091553 | 0.11444 | 0.18768 | 0.09613 | 0.25177 | 0.24261 | 0 | -0.064087 | 122.5021 | 122.3465 | -0.2243 | 122.4838 | 122.5021 | 0.15564 | -0.26092 | 122.438 | 122.374 | -0.07782 | 122.5525 | 122.5342 | 0.16022 | -0.086975 | 122.5433 | 122.5067 | 122.525 | -0.42114 | 122.6898 | 122.6807 | 122.6257 | -0.39368
2093.6875 | 122.9141 | -122.2961 | 0.3891 | -0.00022891 | -0.016024 | 0.013569 | 0.037091 | -0.011783 | -0.032956 | -0.0017431 | -0.0075532 | 0.019489 | -0.036929 | -0.00019431 | -0.011288 | -0.00038438 | 0.050354 | -0.041199 | 0 | 0.013733 | 0.12817 | 0.013733 | -0.1236 | 0.027466 | 0.10986 | -0.018311 | 0.36163 | 0.36621 | -0.009155 | -0.07782 | 122.3099 | 122.1725 | -0.26092 | 122.2549 | 122.3099 | 0.13733 | -0.33874 | 122.287 | 122.2183 | -0.027466 | 122.3236 | 122.2778 | 0.059509 | -0.022888 | 122.4243 | 122.3465 | 122.2961 | -0.5127 | 122.6578 | 122.6624 | 122.406 | -0.46692
2095.4688 | 122.9004 | -122.2961 | 0.3891 | 0.0074006 | -0.014956 | 0.016133 | 0.037518 | -0.010074 | -0.032528 | -3.4096e-05 | -0.0075532 | 0.021198 | -0.037783 | -0.00083531 | -0.011715 | -0.0044434 | 0.07782 | -0.013733 | 0.032043 | 0.045776 | 0.13275 | 0.013733 | -0.11902 | 0.022888 | 0.16479 | -0.009155 | 0.39368 | 0.37994 | -0.009155 | -0.09613 | 122.3099 | 122.1771 | -0.25635 | 122.2824 | 122.3419 | 0.16479 | -0.31128 | 122.287 | 122.2 | 0.004578 | 122.319 | 122.287 | 0.086975 | -0.009155 | 122.4289 | 122.374 | 122.3282 | -0.50812 | 122.6898 | 122.6761 | 122.4609 | -0.48523
2097.25 | 122.8638 | -122.3465 | 0.40283 | 0.0074006 | -0.012179 | 0.012501 | 0.034955 | -0.0098608 | -0.035092 | 0.0018885 | 0.0077058 | 0.022266 | -0.038211 | -0.0040395 | -0.0076562 | 0.0013244 | 0.050354 | -0.018311 | 0.013733 | 0.018311 | 0.11902 | 0.018311 | -0.11902 | -0.027466 | 0.09613 | -0.041199 | 0.37079 | 0.35248 | -0.018311 | -0.09613 | 122.3648 | 122.2275 | -0.28381 | 122.3282 | 122.3648 | 0.13733 | -0.35248 | 122.3282 | 122.2504 | -0.032043 | 122.319 | 122.3053 | 0.054931 | -0.050354 | 122.4655 | 122.3969 | 122.3602 | -0.52185 | 122.7173 | 122.699 | 122.4426 | -0.49896
2098.9844 | 122.7814 | -122.3923 | 0.39368 | -0.00022891 | -0.017519 | 0.014851 | 0.035169 | -0.010929 | -0.040646 | -0.0023839 | 0.0077058 | 0.014362 | -0.039279 | -0.0038259 | -0.014919 | 0.00068362 | 0.09613 | 0.091553 | 0.12817 | 0.091553 | 0.086975 | 0.045776 | -0.082397 | 0.091553 | 0.20599 | 0.068665 | 0.33417 | 0.32044 | 0.004578 | -0.054932 | 122.438 | 122.3099 | -0.3067 | 122.4838 | 122.4838 | 0.17395 | -0.29755 | 122.3969 | 122.3373 | -0.05951 | 122.4838 | 122.4609 | 0.1236 | -0.073242 | 122.4792 | 122.4884 | 122.5204 | -0.47607 | 122.7264 | 122.7127 | 122.5983 | -0.44861
2100.7812 | 122.7951 | -122.4655 | 0.32044 | -0.00022891 | -0.016451 | 0.015706 | 0.040509 | -0.01157 | -0.040646 | -0.0008887 | 0.0077058 | 0.012439 | -0.033938 | -0.0016897 | -0.015133 | -0.0014526 | 0.13275 | 0.10986 | 0.15564 | 0.10529 | 0.091553 | 0.064087 | -0.091553 | 0.13733 | 0.24719 | 0.11444 | 0.21515 | 0.22888 | 0.013733 | -0.054932 | 122.5296 | 122.374 | -0.22888 | 122.5754 | 122.5708 | 0.19684 | -0.18768 | 122.4792 | 122.4106 | -0.10529 | 122.6028 | 122.58 | 0.16937 | -0.091553 | 122.5571 | 122.5983 | 122.6212 | -0.41199 | 122.6807 | 122.6944 | 122.7127 | -0.37537
2102.5625 | 122.818 | -122.5113 | 0.27466 | -0.0078584 | -0.024996 | 0.015065 | 0.036664 | -0.01157 | -0.041501 | -0.0013159 | -0.0075532 | 0.0081668 | -0.033084 | -0.0055349 | -0.013638 | -0.0014526 | 0.064087 | 0.018311 | 0.068665 | 0.050354 | 0.091553 | 0.050354 | -0.09613 | 0.10986 | 0.14648 | 0.064087 | 0.19226 | 0.18768 | -0.009155 | -0.07782 | 122.5616 | 122.4152 | -0.18311 | 122.5296 | 122.5616 | 0.14648 | -0.21057 | 122.5021 | 122.4335 | -0.082397 | 122.6212 | 122.5754 | 0.14191 | -0.086975 | 122.6028 | 122.5754 | 122.58 | -0.37079 | 122.7036 | 122.699 | 122.6578 | -0.35248
2104.2812 | 122.9233 | -122.4289 | 0.27924 | -0.0078584 | -0.018374 | 0.013142 | 0.034314 | -0.011356 | -0.035946 | 0.0003931 | -0.0075532 | 0.013721 | -0.033938 | -0.0046805 | -0.008938 | -0.0042298 | 0.14648 | 0.050354 | 0.10986 | 0.086975 | 0.09613 | 0.045776 | -0.073242 | 0.13733 | 0.1831 | 0.086975 | 0.21515 | 0.20142 | 0.018311 | -0.054932 | 122.4747 | 122.3557 | -0.18311 | 122.4792 | 122.5159 | 0.16022 | -0.13275 | 122.4472 | 122.374 | -0.064087 | 122.5662 | 122.5159 | 0.14191 | -0.07782 | 122.525 | 122.5754 | 122.5388 | -0.35248 | 122.644 | 122.6303 | 122.612 | -0.33417
2106.0781 | 122.8592 | -122.3969 | 0.32501 | -0.00022891 | -0.012392 | 0.01186 | 0.039655 | -0.010502 | -0.03146 | 0.0010339 | -0.0075532 | 0.01778 | -0.033938 | -0.0019033 | -0.0093652 | -0.0031616 | 0.050354 | -0.07782 | 0.004578 | 0.004578 | 0.13275 | 0.013733 | -0.11444 | -0.013733 | 0.082397 | -0.064087 | 0.32959 | 0.29755 | -0.036621 | -0.10529 | 122.4106 | 122.2824 | -0.19226 | 122.319 | 122.4014 | 0.11902 | -0.27466 | 122.3602 | 122.2916 | 0.004578 | 122.3831 | 122.3328 | 0.041199 | -0.027466 | 122.5296 | 122.4472 | 122.4014 | -0.43945 | 122.7264 | 122.6944 | 122.4792 | -0.4303
2107.8594 | 122.7859 | -122.5571 | 0.25177 | -0.015487 | -0.02051 | 0.015919 | 0.037732 | -0.012211 | -0.040219 | -0.0011023 | -0.0075532 | 0.007526 | -0.032016 | -0.0033987 | -0.011288 | 0.0013244 | 0.09613 | 0.086975 | 0.10986 | 0.073242 | 0.091553 | 0.064087 | -0.086975 | 0.15106 | 0.15564 | 0.07782 | 0.19684 | 0.19226 | 0 | -0.059509 | 122.6212 | 122.4701 | -0.16022 | 122.644 | 122.6303 | 0.16022 | -0.15564 | 122.5571 | 122.4976 | -0.054932 | 122.7081 | 122.6349 | 0.13733 | -0.059509 | 122.6486 | 122.6532 | 122.6669 | -0.33874 | 122.7539 | 122.7493 | 122.7127 | -0.31128
2109.6406 | 122.8638 | -122.3969 | 0.3479 | -0.00022891 | -0.016024 | 0.012715 | 0.032392 | -0.013065 | -0.032956 | 0.0008203 | -0.015182 | 0.019702 | -0.036074 | -0.0019033 | -0.0093652 | -0.0031616 | 0.064087 | -0.036621 | 0.027466 | 0.013733 | 0.12817 | 0.022888 | -0.10986 | 0 | 0.10071 | -0.054932 | 0.32044 | 0.31128 | -0.004578 | -0.091553 | 122.4197 | 122.287 | -0.21973 | 122.3602 | 122.4106 | 0.1236 | -0.28381 | 122.3923 | 122.3053 | -0.027465 | 122.3969 | 122.3419 | 0.036621 | -0.036621 | 122.525 | 122.4609 | 122.4243 | -0.45776 | 122.7173 | 122.7081 | 122.4976 | -0.43945
2111.4219 | 122.9141 | -122.4792 | 0.21057 | -0.0078584 | -0.014101 | 0.013783 | 0.038587 | -0.013492 | -0.037228 | -3.4096e-05 | 7.627e-05 | 0.013294 | -0.027743 | -0.0025443 | -0.010861 | -0.0016662 | 0.068665 | -0.009155 | 0.032043 | 0.045776 | 0.13733 | 0.018311 | -0.10071 | 0.10071 | 0.1236 | 0.004578 | 0.20142 | 0.18768 | -0.032043 | -0.09613 | 122.4976 | 122.3785 | -0.073242 | 122.4701 | 122.525 | 0.14648 | -0.14191 | 122.4472 | 122.3831 | -0.009155 | 122.58 | 122.4838 | 0.10071 | -0.022888 | 122.6166 | 122.5479 | 122.5113 | -0.31128 | 122.6807 | 122.6669 | 122.6028 | -0.3067
2113.2031 | 122.9187 | -122.3923 | 0.28839 | -0.00022891 | -0.013247 | 0.013569 | 0.039014 | -0.0083654 | -0.035733 | 0.0018885 | 7.627e-05 | 0.01778 | -0.031375 | 0.00023289 | -0.011929 | -0.0023072 | 0.022888 | -0.036621 | 0.009155 | 0.032043 | 0.13275 | 0.004578 | -0.13275 | 0.018311 | 0.1236 | -0.004578 | 0.28381 | 0.28381 | -0.013733 | -0.09613 | 122.3969 | 122.2595 | -0.15564 | 122.3557 | 122.4243 | 0.16479 | -0.2655 | 122.3785 | 122.2961 | -0.004578 | 122.4106 | 122.3877 | 0.091552 | -0.004578 | 122.525 | 122.4152 | 122.4014 | -0.42114 | 122.6761 | 122.6761 | 122.5159 | -0.38452
2114.9844 | 122.7722 | -122.5204 | 0.25177 | -0.023117 | -0.015169 | 0.014851 | 0.037946 | -0.0094336 | -0.042569 | -0.0015295 | 0.0077058 | 0.0098758 | -0.030093 | -0.0040395 | -0.016842 | 0.00025642 | 0.07782 | 0.054932 | 0.10071 | 0.059509 | 0.10071 | 0.036621 | -0.10071 | 0.068665 | 0.13733 | 0.032043 | 0.16937 | 0.19226 | -0.018311 | -0.09613 | 122.5571 | 122.4197 | -0.15106 | 122.5754 | 122.58 | 0.16022 | -0.17395 | 122.5021 | 122.4243 | -0.082397 | 122.5891 | 122.5525 | 0.12817 | -0.059509 | 122.6212 | 122.5983 | 122.6212 | -0.35248 | 122.6898 | 122.7127 | 122.6578 | -0.3479
2116.7656 | 122.9141 | -122.4884 | 0.23804 | -0.0078584 | -0.019655 | 0.014424 | 0.034955 | -0.010929 | -0.035519 | -0.0006751 | -0.0075532 | 0.014789 | -0.030307 | -0.0023305 | -0.008938 | -0.00081178 | 0.064087 | -0.004578 | 0.045776 | 0.045776 | 0.1236 | 0.022888 | -0.10529 | 0.13733 | 0.14648 | 0.068665 | 0.19684 | 0.1831 | 0.013733 | -0.068665 | 122.5113 | 122.3831 | -0.11444 | 122.4838 | 122.5342 | 0.15106 | -0.17395 | 122.5021 | 122.4197 | -0.041199 | 122.6257 | 122.5571 | 0.13733 | -0.054932 | 122.612 | 122.5525 | 122.5342 | -0.34332 | 122.6852 | 122.6715 | 122.6349 | -0.3067
2118.5469 | 122.85 | -122.4838 | 0.23346 | -0.0078584 | -0.01047 | 0.0095104 | 0.039655 | -0.012211 | -0.034237 | 0.0008203 | 0.0077058 | 0.01543 | -0.028598 | -0.0023305 | -0.010433 | -0.0023072 | 0.027466 | -0.068665 | -0.013733 | 0.027466 | 0.13275 | 0.018311 | -0.12817 | 0.013733 | 0.041199 | -0.054932 | 0.21973 | 0.2243 | -0.036621 | -0.10071 | 122.5021 | 122.3557 | -0.10071 | 122.4152 | 122.5113 | 0.15564 | -0.20599 | 122.4472 | 122.3831 | -0.013732 | 122.4976 | 122.4289 | 0.045776 | -0.009155 | 122.6166 | 122.5113 | 122.4701 | -0.36163 | 122.7036 | 122.7081 | 122.525 | -0.33417
2120.2656 | 122.8683 | -122.4792 | 0.22888 | -0.0078584 | -0.011538 | 0.010579 | 0.036878 | -0.0094336 | -0.035305 | 0.0023157 | 0.0077058 | 0.014362 | -0.027743 | -0.00040791 | -0.01022 | -0.0018798 | 0.07782 | -0.004578 | 0.032043 | 0.036621 | 0.11902 | 0.022888 | -0.1236 | 0.073242 | 0.086975 | -0.013733 | 0.21057 | 0.1831 | -0.018311 | -0.09613 | 122.5021 | 122.3557 | -0.10986 | 122.4747 | 122.5159 | 0.16022 | -0.15106 | 122.4609 | 122.3831 | -0.018311 | 122.5525 | 122.4655 | 0.082397 | -0.045777 | 122.5983 | 122.5571 | 122.5113 | -0.35248 | 122.6898 | 122.6624 | 122.5662 | -0.32501
2122.0469 | 122.9095 | -122.4106 | 0.27008 | -0.015487 | -0.01282 | 0.014637 | 0.03645 | -0.011356 | -0.038723 | -0.0019567 | 0.0077058 | 0.014576 | -0.030734 | -0.0038259 | -0.011501 | 0.00025642 | 0.027466 | -0.036621 | -0.004578 | 0.022888 | 0.13733 | 0.027466 | -0.11902 | 0.036621 | 0.13275 | -0.009155 | 0.27008 | 0.27008 | -0.027466 | -0.091553 | 122.438 | 122.2916 | -0.13275 | 122.374 | 122.4335 | 0.14191 | -0.24262 | 122.3831 | 122.319 | 0 | 122.4472 | 122.4014 | 0.082398 | 0 | 122.5479 | 122.438 | 122.406 | -0.3891 | 122.6807 | 122.6807 | 122.5433 | -0.36163
2123.8281 | 122.7722 | -122.4289 | 0.37079 | -0.00022891 | -0.01581 | 0.01891 | 0.036237 | -0.010074 | -0.041287 | 0.0006067 | -0.0075532 | 0.015216 | -0.036074 | -0.0040395 | -0.014706 | 0.0011108 | 0.091553 | 0.073242 | 0.091553 | 0.091553 | 0.09613 | 0.036621 | -0.082397 | 0.050354 | 0.20142 | 0.045776 | 0.31128 | 0.3067 | -0.027466 | -0.082397 | 122.4655 | 122.3465 | -0.27466 | 122.5021 | 122.5204 | 0.17395 | -0.27924 | 122.4014 | 122.3465 | -0.05951 | 122.4792 | 122.4747 | 0.12817 | -0.064087 | 122.525 | 122.5204 | 122.5204 | -0.45319 | 122.7402 | 122.7356 | 122.6303 | -0.45319
2125.5625 | 122.8226 | -122.3831 | 0.37994 | -0.0078584 | -0.018587 | 0.015706 | 0.036237 | -0.012424 | -0.043637 | -0.0021703 | 0.0077058 | 0.016284 | -0.038851 | -0.0053213 | -0.015347 | 4.2822e-05 | 0.064087 | 0.013733 | 0.073242 | 0.054932 | 0.11902 | 0.045776 | -0.09613 | 0.041199 | 0.19226 | 0.073242 | 0.31586 | 0.31586 | 0.013733 | -0.059509 | 122.4289 | 122.287 | -0.26093 | 122.3969 | 122.438 | 0.15106 | -0.31586 | 122.3969 | 122.3236 | -0.064087 | 122.4243 | 122.4564 | 0.13275 | -0.064087 | 122.5021 | 122.4472 | 122.4564 | -0.47607 | 122.699 | 122.699 | 122.5754 | -0.43945
2127.3281 | 122.8409 | -122.3694 | 0.39368 | -0.00022891 | -0.018801 | 0.014851 | 0.036023 | -0.012638 | -0.04086 | -0.0025977 | 7.627e-05 | 0.016925 | -0.04056 | -0.0038259 | -0.013424 | -0.001239 | 0.14191 | 0.11902 | 0.14191 | 0.10529 | 0.10529 | 0.050354 | -0.082397 | 0.091553 | 0.27466 | 0.11444 | 0.32959 | 0.29755 | 0.032043 | -0.054932 | 122.4197 | 122.287 | -0.28839 | 122.4884 | 122.4747 | 0.18768 | -0.25177 | 122.4014 | 122.3145 | -0.064087 | 122.4609 | 122.4838 | 0.16937 | -0.096131 | 122.4747 | 122.5113 | 122.5113 | -0.47607 | 122.699 | 122.6669 | 122.644 | -0.44861
2129.1094 | 122.9416 | -122.3373 | 0.36163 | 0.0074006 | -0.017306 | 0.015065 | 0.035596 | -0.013279 | -0.034878 | -3.4096e-05 | 7.627e-05 | 0.02013 | -0.039065 | -0.0019033 | -0.011715 | -0.0031616 | 0.064087 | -0.050354 | 0 | 0.022888 | 0.12817 | 0.032043 | -0.11444 | 0.032043 | 0.11902 | -0.004578 | 0.33875 | 0.31586 | -0.009155 | -0.068665 | 122.3694 | 122.2229 | -0.23346 | 122.287 | 122.3602 | 0.13733 | -0.29755 | 122.3282 | 122.2687 | -0.022888 | 122.3694 | 122.3328 | 0.064087 | -0.045776 | 122.4655 | 122.4014 | 122.3373 | -0.47607 | 122.6761 | 122.6532 | 122.4564 | -0.4303
2130.8906 | 122.8043 | -122.4655 | 0.3067 | -0.00022891 | -0.018587 | 0.015065 | 0.035169 | -0.013065 | -0.038083 | -3.4096e-05 | 7.627e-05 | 0.014148 | -0.035861 | -0.0031851 | -0.011288 | -0.00081178 | 0.15564 | 0.07782 | 0.12817 | 0.07782 | 0.091553 | 0.064087 | -0.091553 | 0.13275 | 0.20142 | 0.086975 | 0.24719 | 0.24261 | 0.004578 | -0.054932 | 122.5296 | 122.374 | -0.21515 | 122.5433 | 122.5433 | 0.16937 | -0.15106 | 122.4701 | 122.4106 | -0.05951 | 122.5983 | 122.5525 | 0.14191 | -0.064087 | 122.5571 | 122.6212 | 122.5937 | -0.39825 | 122.7127 | 122.7081 | 122.6669 | -0.36163
2132.6094 | 122.8317 | -122.3831 | 0.39368 | -0.0078584 | -0.01581 | 0.015492 | 0.033673 | -0.010929 | -0.036587 | -3.4096e-05 | -0.0075532 | 0.017566 | -0.040988 | -0.0044669 | -0.0095788 | -0.0018798 | 0.14191 | 0.09613 | 0.13275 | 0.086975 | 0.10071 | 0.064087 | -0.073242 | 0.10529 | 0.22888 | 0.082397 | 0.3067 | 0.28839 | 0.004578 | -0.050354 | 122.4472 | 122.3099 | -0.29297 | 122.4792 | 122.4701 | 0.16022 | -0.25177 | 122.3877 | 122.3328 | -0.086975 | 122.4884 | 122.4655 | 0.13275 | -0.10529 | 122.4838 | 122.525 | 122.5159 | -0.46692 | 122.6898 | 122.6715 | 122.612 | -0.44403
2134.375 | 122.7997 | -122.4014 | 0.40283 | -0.0078584 | -0.020296 | 0.014424 | 0.036664 | -0.011783 | -0.038083 | -0.0021703 | 7.627e-05 | 0.017993 | -0.038638 | -0.0042531 | -0.012356 | 4.2822e-05 | 0.1236 | 0.068665 | 0.11902 | 0.07782 | 0.091553 | 0.059509 | -0.041199 | 0.07782 | 0.17853 | 0.059509 | 0.3067 | 0.29755 | 0.018311 | -0.064087 | 122.4609 | 122.3602 | -0.31128 | 122.4701 | 122.4792 | 0.11902 | -0.27924 | 122.4197 | 122.3373 | -0.09613 | 122.4792 | 122.4609 | 0.1236 | -0.10529 | 122.493 | 122.525 | 122.5204 | -0.44403 | 122.7081 | 122.699 | 122.58 | -0.46692
2136.0938 | 122.937 | -122.3465 | 0.3479 | -0.0078584 | -0.015169 | 0.013356 | 0.034528 | -0.010929 | -0.035092 | 0.0008203 | -0.0075532 | 0.02248 | -0.038851 | -0.0019033 | -0.0097924 | -0.004016 | 0.054932 | -0.045776 | -0.004578 | 0.022888 | 0.13275 | 0.032043 | -0.10529 | 0.022888 | 0.10529 | -0.013733 | 0.32501 | 0.32501 | -0.004578 | -0.09613 | 122.3785 | 122.2412 | -0.21515 | 122.3007 | 122.3694 | 0.12817 | -0.29297 | 122.3419 | 122.2504 | -0.022888 | 122.3694 | 122.3328 | 0.082397 | -0.022888 | 122.4792 | 122.4014 | 122.3419 | -0.45319 | 122.6715 | 122.6715 | 122.4518 | -0.44403
2137.875 | 122.85 | -122.406 | 0.37079 | 0.0074006 | -0.018587 | 0.015919 | 0.039441 | -0.011143 | -0.043423 | -0.0004613 | 7.627e-05 | 0.014362 | -0.039065 | -0.0027579 | -0.01556 | -0.001239 | 0.12817 | 0.07782 | 0.13733 | 0.07782 | 0.10529 | 0.036621 | -0.086975 | 0.10986 | 0.26093 | 0.09613 | 0.30212 | 0.29297 | -0.013733 | -0.050354 | 122.4426 | 122.319 | -0.2655 | 122.4838 | 122.4838 | 0.16479 | -0.24261 | 122.3923 | 122.3557 | -0.068665 | 122.5159 | 122.5021 | 0.14648 | -0.07782 | 122.5113 | 122.5342 | 122.5433 | -0.45776 | 122.7081 | 122.699 | 122.6669 | -0.42114
2139.5938 | 122.9279 | -122.3511 | 0.35706 | -0.00022891 | -0.012606 | 0.013142 | 0.039655 | -0.010502 | -0.034237 | -0.0011023 | 7.627e-05 | 0.019702 | -0.036288 | -0.0010489 | -0.010647 | -0.0027344 | 0.050354 | -0.059509 | -0.004578 | 0.027466 | 0.15106 | 0 | -0.13733 | -0.009155 | 0.1236 | -0.036621 | 0.3479 | 0.33417 | -0.041199 | -0.082397 | 122.3511 | 122.2137 | -0.20599 | 122.2916 | 122.3785 | 0.16479 | -0.3067 | 122.3099 | 122.2687 | -0.009156 | 122.3419 | 122.3145 | 0.045776 | -0.022889 | 122.5021 | 122.4014 | 122.3465 | -0.49438 | 122.699 | 122.6852 | 122.4747 | -0.43945
2141.375 | 122.8134 | -122.4197 | 0.3891 | -0.00022891 | -0.019655 | 0.01421 | 0.037518 | -0.011356 | -0.041714 | -0.0002477 | 7.627e-05 | 0.016925 | -0.039492 | -0.0012625 | -0.014706 | 0.0013244 | 0.07782 | 0.032043 | 0.07782 | 0.059509 | 0.10071 | 0.045776 | -0.073242 | 0.054932 | 0.1831 | 0.045776 | 0.30212 | 0.31128 | 0.013733 | -0.054932 | 122.4655 | 122.3465 | -0.28839 | 122.4518 | 122.4792 | 0.13275 | -0.31128 | 122.4335 | 122.3648 | -0.086975 | 122.4747 | 122.4655 | 0.10071 | -0.07782 | 122.5204 | 122.4976 | 122.4976 | -0.46234 | 122.7219 | 122.731 | 122.6028 | -0.44403
2143.1562 | 122.7951 | -122.3923 | 0.39825 | -0.0078584 | -0.016665 | 0.016987 | 0.036878 | -0.012638 | -0.040646 | -0.0013159 | 7.627e-05 | 0.019489 | -0.038851 | -0.0021169 | -0.013638 | 0.00047002 | 0.13733 | 0.10529 | 0.15564 | 0.10071 | 0.10071 | 0.050354 | -0.091553 | 0.09613 | 0.2655 | 0.091553 | 0.32044 | 0.28381 | 0.027466 | -0.045776 | 122.4426 | 122.3007 | -0.29755 | 122.4976 | 122.493 | 0.19226 | -0.26092 | 122.4197 | 122.3465 | -0.077819 | 122.4884 | 122.4838 | 0.13733 | -0.11444 | 122.493 | 122.5296 | 122.5479 | -0.48981 | 122.7127 | 122.6761 | 122.6578 | -0.44403
2144.8906 | 122.8043 | -122.406 | 0.39368 | -0.0078584 | -0.015597 | 0.016987 | 0.036664 | -0.012852 | -0.03616 | -0.0008887 | -0.0075532 | 0.016925 | -0.038211 | -0.0023305 | -0.01257 | -0.0016662 | 0.14648 | 0.086975 | 0.1236 | 0.091553 | 0.10071 | 0.036621 | -0.091553 | 0.086975 | 0.25177 | 0.068665 | 0.32044 | 0.32501 | -0.013733 | -0.045776 | 122.4426 | 122.3145 | -0.29297 | 122.493 | 122.4976 | 0.18311 | -0.24719 | 122.3923 | 122.3602 | -0.073242 | 122.493 | 122.4747 | 0.11444 | -0.068665 | 122.5067 | 122.5525 | 122.5296 | -0.48523 | 122.7264 | 122.731 | 122.6578 | -0.43945
2146.6719 | 122.9416 | -122.3877 | 0.34332 | -0.0078584 | -0.015383 | 0.013783 | 0.034741 | -0.01157 | -0.033169 | -0.0008887 | -0.015182 | 0.02312 | -0.037356 | -0.00019431 | -0.011715 | -0.004016 | 0.064087 | -0.082397 | -0.022888 | 0.032043 | 0.15106 | 0.009155 | -0.10986 | -0.004578 | 0.086975 | -0.059509 | 0.34332 | 0.32501 | -0.027466 | -0.091553 | 122.3969 | 122.2778 | -0.19226 | 122.3053 | 122.4197 | 0.14191 | -0.27924 | 122.3602 | 122.2961 | 0 | 122.3831 | 122.3282 | 0.032044 | -0.018311 | 122.5388 | 122.4518 | 122.3648 | -0.45319 | 122.731 | 122.7127 | 122.4747 | -0.43488
2148.4531 | 122.8455 | -122.4243 | 0.37537 | -0.015487 | -0.019442 | 0.01656 | 0.039227 | -0.013706 | -0.041501 | -0.0023839 | 7.627e-05 | 0.015857 | -0.03992 | -0.0048941 | -0.015133 | -0.00081178 | 0.10529 | 0.059509 | 0.10986 | 0.082397 | 0.11444 | 0.045776 | -0.10071 | 0.09613 | 0.23346 | 0.10986 | 0.3067 | 0.28839 | 0.013733 | -0.050354 | 122.4701 | 122.3236 | -0.26092 | 122.4838 | 122.5067 | 0.18311 | -0.27008 | 122.438 | 122.374 | -0.068664 | 122.5204 | 122.5342 | 0.16022 | -0.086975 | 122.5388 | 122.5296 | 122.5342 | -0.47607 | 122.731 | 122.7127 | 122.6578 | -0.42572
2150.2656 | 122.8409 | -122.4106 | 0.36621 | 0.0074006 | -0.020724 | 0.01656 | 0.037091 | -0.012852 | -0.039364 | -0.0013159 | 7.627e-05 | 0.018421 | -0.039065 | -0.00019431 | -0.014706 | -0.00017078 | 0.16022 | 0.10529 | 0.14191 | 0.10071 | 0.09613 | 0.054932 | -0.082397 | 0.10986 | 0.26093 | 0.10529 | 0.30212 | 0.27466 | -0.004578 | -0.041199 | 122.4655 | 122.3282 | -0.27008 | 122.5159 | 122.5113 | 0.18311 | -0.20599 | 122.406 | 122.3694 | -0.064087 | 122.5204 | 122.5159 | 0.14649 | -0.091553 | 122.5067 | 122.5708 | 122.5525 | -0.44861 | 122.7127 | 122.6852 | 122.6715 | -0.40741
2152.0469 | 122.7859 | -122.4152 | 0.37079 | -0.00022891 | -0.019655 | 0.014851 | 0.036237 | -0.011997 | -0.037014 | -0.0025977 | 0.0077058 | 0.018634 | -0.040347 | -0.0048941 | -0.011929 | -0.0018798 | 0.13275 | 0.068665 | 0.11444 | 0.086975 | 0.09613 | 0.050354 | -0.086975 | 0.064087 | 0.20142 | 0.032043 | 0.32501 | 0.31586 | -0.004578 | -0.07782 | 122.4655 | 122.3282 | -0.27466 | 122.4838 | 122.5021 | 0.17395 | -0.23804 | 122.4106 | 122.3373 | -0.045777 | 122.4792 | 122.4472 | 0.10986 | -0.054932 | 122.5113 | 122.5479 | 122.5296 | -0.45776 | 122.7402 | 122.731 | 122.6166 | -0.44861
2153.8281 | 122.8134 | -122.4152 | 0.37994 | -0.0078584 | -0.020937 | 0.017842 | 0.034741 | -0.010288 | -0.039151 | -0.0032385 | 7.627e-05 | 0.018207 | -0.04056 | -0.0042531 | -0.01257 | -0.00017078 | 0.10529 | 0.022888 | 0.07782 | 0.045776 | 0.091553 | 0.045776 | -0.07782 | 0.073242 | 0.16022 | 0.036621 | 0.29755 | 0.29297 | 0.013733 | -0.064087 | 122.4609 | 122.3373 | -0.28839 | 122.438 | 122.4609 | 0.1236 | -0.27466 | 122.4289 | 122.3511 | -0.082398 | 122.4884 | 122.4518 | 0.10071 | -0.086975 | 122.5067 | 122.5204 | 122.493 | -0.45776 | 122.7127 | 122.7081 | 122.5754 | -0.44403
2155.5469 | 122.8363 | -122.4014 | 0.37537 | -0.0078584 | -0.021151 | 0.017201 | 0.036664 | -0.013706 | -0.039364 | 0.0003931 | 0.0077058 | 0.017353 | -0.038424 | -0.0036123 | -0.012997 | -0.002948 | 0.11902 | 0.027466 | 0.10986 | 0.082397 | 0.091553 | 0.050354 | -0.082397 | 0.07782 | 0.21515 | 0.073242 | 0.30212 | 0.29297 | 0.009155 | -0.064087 | 122.4518 | 122.319 | -0.28381 | 122.4289 | 122.4838 | 0.16479 | -0.25635 | 122.4106 | 122.3373 | -0.073242 | 122.4792 | 122.4747 | 0.13733 | -0.082397 | 122.493 | 122.5204 | 122.5113 | -0.45776 | 122.7036 | 122.6944 | 122.6166 | -0.43945
2157.3438 | 122.8912 | -122.406 | 0.37079 | -0.015487 | -0.008547 | 0.011006 | 0.036237 | -0.010502 | -0.031674 | 0.0025293 | 7.627e-05 | 0.024402 | -0.037783 | -0.0038259 | -0.0074426 | -0.0020934 | 0.073242 | -0.086975 | -0.009155 | 0.013733 | 0.14648 | 0.004578 | -0.1236 | -0.027466 | 0.068665 | -0.091553 | 0.32959 | 0.32959 | -0.032043 | -0.082397 | 122.4106 | 122.2824 | -0.2243 | 122.319 | 122.4197 | 0.13733 | -0.29755 | 122.374 | 122.3236 | -0.041199 | 122.3785 | 122.3145 | -0.009156 | -0.041199 | 122.5525 | 122.4792 | 122.3969 | -0.49438 | 122.7356 | 122.7356 | 122.4747 | -0.45319
2159.125 | 122.7905 | -122.4426 | 0.39368 | -0.0078584 | -0.018801 | 0.017201 | 0.03346 | -0.011783 | -0.040219 | -0.0002477 | -0.0075532 | 0.01778 | -0.038424 | -0.0036123 | -0.014279 | 0.0015382 | 0.1236 | 0.050354 | 0.10071 | 0.054932 | 0.091553 | 0.041199 | -0.073242 | 0.064087 | 0.17853 | 0.045776 | 0.30212 | 0.28839 | -0.009155 | -0.045776 | 122.4838 | 122.3694 | -0.30212 | 122.493 | 122.4976 | 0.12817 | -0.27008 | 122.4335 | 122.3969 | -0.091553 | 122.5067 | 122.4884 | 0.091552 | -0.10529 | 122.5342 | 122.5662 | 122.5433 | -0.46692 | 122.7448 | 122.731 | 122.6212 | -0.43945
2160.8438 | 122.9233 | -122.3923 | 0.36621 | -0.00022891 | -0.017092 | 0.013142 | 0.034741 | -0.010288 | -0.03381 | 0.0014613 | 7.627e-05 | 0.019275 | -0.040133 | -0.0040395 | -0.011074 | -0.0020934 | 0.14648 | 0.064087 | 0.09613 | 0.082397 | 0.10986 | 0.036621 | -0.09613 | 0.10529 | 0.21057 | 0.064087 | 0.29755 | 0.27466 | 0.018311 | -0.041199 | 122.4289 | 122.2961 | -0.25635 | 122.4564 | 122.4747 | 0.17853 | -0.21973 | 122.4106 | 122.3511 | -0.068665 | 122.4976 | 122.4564 | 0.10529 | -0.091553 | 122.5021 | 122.5388 | 122.4884 | -0.46234 | 122.6898 | 122.6669 | 122.6028 | -0.40741
2162.625 | 122.8592 | -122.3969 | 0.37079 | 0.01503 | -0.022219 | 0.015706 | 0.037305 | -0.011356 | -0.041501 | -0.0017431 | 7.627e-05 | 0.015003 | -0.039065 | -0.0040395 | -0.01321 | 0.00025642 | 0.09613 | 0.068665 | 0.11444 | 0.07782 | 0.09613 | 0.050354 | -0.082397 | 0.091553 | 0.24261 | 0.091553 | 0.30212 | 0.29297 | 0 | -0.059509 | 122.4472 | 122.3145 | -0.27466 | 122.4655 | 122.4747 | 0.16022 | -0.27466 | 122.3969 | 122.3373 | -0.068665 | 122.4884 | 122.4884 | 0.15106 | -0.07782 | 122.493 | 122.493 | 122.5113 | -0.45319 | 122.699 | 122.6898 | 122.6395 | -0.4303
2164.3438 | 122.85 | -122.4197 | 0.35706 | -0.00022891 | -0.020724 | 0.012501 | 0.035809 | -0.012211 | -0.035946 | 0.0003931 | -0.015182 | 0.018634 | -0.036288 | -0.0016897 | -0.011929 | -0.0023072 | 0.15564 | 0.082397 | 0.15564 | 0.082397 | 0.09613 | 0.064087 | -0.050354 | 0.11902 | 0.20599 | 0.086975 | 0.29297 | 0.28839 | 0.013733 | -0.059509 | 122.4838 | 122.3694 | -0.26093 | 122.5021 | 122.5021 | 0.13275 | -0.20142 | 122.4335 | 122.3602 | -0.064087 | 122.5388 | 122.5067 | 0.14648 | -0.068665 | 122.5159 | 122.5754 | 122.5754 | -0.40741 | 122.7127 | 122.7081 | 122.6257 | -0.41656
2166.125 | 122.818 | -122.406 | 0.37079 | -0.0078584 | -0.016878 | 0.015706 | 0.036664 | -0.012852 | -0.038083 | 0.0006067 | 7.627e-05 | 0.017139 | -0.035861 | -0.0019033 | -0.011715 | -0.00017078 | 0.13275 | 0.10529 | 0.14191 | 0.10529 | 0.086975 | 0.050354 | -0.09613 | 0.09613 | 0.24261 | 0.082397 | 0.28381 | 0.27466 | 0 | -0.050354 | 122.4564 | 122.3099 | -0.28381 | 122.5113 | 122.5113 | 0.20142 | -0.23804 | 122.406 | 122.3557 | -0.086976 | 122.5021 | 122.4884 | 0.13275 | -0.096131 | 122.493 | 122.5388 | 122.5479 | -0.46692 | 122.6898 | 122.6807 | 122.6486 | -0.42114
2167.8438 | 122.8409 | -122.4335 | 0.37079 | -0.00022891 | -0.01346 | 0.015919 | 0.039441 | -0.0094336 | -0.035946 | 0.0006067 | 7.627e-05 | 0.022052 | -0.036074 | -0.0023305 | -0.011501 | -0.0033752 | 0.054932 | -0.041199 | 0.013733 | 0.009155 | 0.1236 | 0.018311 | -0.13275 | -0.009155 | 0.11444 | -0.032043 | 0.35248 | 0.33875 | -0.036621 | -0.10529 | 122.4518 | 122.3007 | -0.24719 | 122.3923 | 122.4426 | 0.14191 | -0.31586 | 122.3969 | 122.3282 | -0.018311 | 122.4243 | 122.4014 | 0.073243 | -0.032044 | 122.5571 | 122.4884 | 122.4472 | -0.50354 | 122.7859 | 122.7722 | 122.5479 | -0.47607
2169.625 | 122.9462 | -122.4152 | 0.3479 | -0.0078584 | -0.014315 | 0.010365 | 0.038159 | -0.00922 | -0.033596 | -0.0006751 | 7.627e-05 | 0.022052 | -0.036288 | -0.0021169 | -0.010861 | -0.0027344 | 0.082397 | 0 | 0.027466 | 0.050354 | 0.14648 | 0.022888 | -0.13275 | 0.032043 | 0.16022 | 0 | 0.33417 | 0.31128 | -0.027466 | -0.068665 | 122.438 | 122.2824 | -0.20142 | 122.4152 | 122.4655 | 0.18311 | -0.2655 | 122.3877 | 122.3465 | -0.013733 | 122.4472 | 122.4152 | 0.068665 | -0.036621 | 122.5616 | 122.4976 | 122.4426 | -0.48065 | 122.7493 | 122.7264 | 122.5754 | -0.41656
2171.4062 | 122.8271 | -122.4243 | 0.41199 | -0.00022891 | -0.020724 | 0.013356 | 0.036023 | -0.0096472 | -0.042355 | -0.0006751 | 7.627e-05 | 0.017139 | -0.038211 | -0.0044669 | -0.01556 | 0.00089722 | 0.045776 | 0.027466 | 0.07782 | 0.064087 | 0.10986 | 0.041199 | -0.10071 | 0.036621 | 0.1831 | 0.032043 | 0.30212 | 0.28381 | 0 | -0.054932 | 122.4655 | 122.3236 | -0.30212 | 122.4518 | 122.4884 | 0.1648 | -0.36621 | 122.4243 | 122.3694 | -0.10986 | 122.4609 | 122.4564 | 0.086975 | -0.12817 | 122.5342 | 122.4701 | 122.5021 | -0.5127 | 122.7264 | 122.7081 | 122.6074 | -0.46692
2173.1719 | 122.8592 | -122.4197 | 0.37537 | -0.00022891 | -0.019655 | 0.015919 | 0.036664 | -0.01157 | -0.041714 | -0.0011023 | 7.627e-05 | 0.017139 | -0.037356 | -0.0038259 | -0.012997 | 0.00025642 | 0.07782 | 0.045776 | 0.086975 | 0.07782 | 0.11444 | 0.032043 | -0.082397 | 0.091553 | 0.2243 | 0.091553 | 0.29297 | 0.29755 | 0.018311 | -0.054932 | 122.4518 | 122.3373 | -0.26092 | 122.4655 | 122.4976 | 0.16022 | -0.29755 | 122.4381 | 122.3648 | -0.082397 | 122.5113 | 122.5113 | 0.14649 | -0.07782 | 122.5342 | 122.4976 | 122.5067 | -0.45776 | 122.7127 | 122.7173 | 122.644 | -0.4303
2174.9688 | 122.937 | -122.3694 | 0.34332 | 0.0074006 | -0.013888 | 0.011006 | 0.03645 | -0.0096472 | -0.035519 | -0.0002477 | 0.0077058 | 0.021411 | -0.036074 | -0.00019431 | -0.010006 | -0.00059818 | 0.073242 | -0.041199 | 0 | 0.041199 | 0.13733 | 0.018311 | -0.11444 | 0 | 0.12817 | -0.045776 | 0.32959 | 0.32044 | -0.009155 | -0.10529 | 122.3877 | 122.2549 | -0.20599 | 122.3282 | 122.4106 | 0.15564 | -0.27008 | 122.3602 | 122.2641 | -0.013733 | 122.3694 | 122.3236 | 0.05951 | -0.022888 | 122.5067 | 122.4426 | 122.3694 | -0.45776 | 122.699 | 122.6898 | 122.4976 | -0.44861
2176.75 | 122.9507 | -122.3923 | 0.32959 | -0.0078584 | -0.012392 | 0.013142 | 0.034314 | -0.011143 | -0.034024 | 0.0016749 | -0.0075532 | 0.021411 | -0.038851 | -0.0036123 | -0.0080834 | -0.004016 | 0.073242 | -0.018311 | 0.013733 | 0.050354 | 0.13733 | 0.013733 | -0.11444 | 0.018311 | 0.15564 | -0.022888 | 0.33417 | 0.32959 | -0.018311 | -0.082397 | 122.406 | 122.2778 | -0.19226 | 122.374 | 122.4426 | 0.16479 | -0.25635 | 122.374 | 122.3099 | 0.004577 | 122.4106 | 122.3694 | 0.059509 | 0 | 122.5296 | 122.4655 | 122.406 | -0.44403 | 122.7264 | 122.7219 | 122.5479 | -0.41199
2178.4688 | 122.8683 | -122.438 | 0.37079 | -0.00022891 | -0.018374 | 0.017628 | 0.037091 | -0.012211 | -0.042355 | -0.0017431 | 7.627e-05 | 0.016498 | -0.036502 | -0.0053213 | -0.012997 | 0.0015382 | 0.054932 | 0.018311 | 0.082397 | 0.064087 | 0.10986 | 0.036621 | -0.091553 | 0.054932 | 0.19684 | 0.082397 | 0.30212 | 0.29297 | 0.009155 | -0.07782 | 122.4747 | 122.3465 | -0.26093 | 122.4564 | 122.5021 | 0.15564 | -0.31586 | 122.4472 | 122.3602 | -0.068665 | 122.493 | 122.5204 | 0.16022 | -0.07782 | 122.5479 | 122.493 | 122.5204 | -0.46234 | 122.7402 | 122.731 | 122.6349 | -0.44861
2180.2656 | 122.85 | -122.4289 | 0.36163 | -0.015487 | -0.022433 | 0.015278 | 0.034741 | -0.01392 | -0.041714 | -0.0019567 | -0.0075532 | 0.018207 | -0.039065 | -0.0038259 | -0.014919 | -0.0014526 | 0.073242 | 0.022888 | 0.07782 | 0.045776 | 0.10071 | 0.032043 | -0.10986 | 0.064087 | 0.18768 | 0.050354 | 0.29297 | 0.29297 | 0.004578 | -0.050354 | 122.4609 | 122.319 | -0.26092 | 122.4518 | 122.4747 | 0.15564 | -0.28839 | 122.4335 | 122.3785 | -0.068664 | 122.493 | 122.4792 | 0.10071 | -0.068664 | 122.5296 | 122.5021 | 122.5067 | -0.4715 | 122.7219 | 122.7219 | 122.6166 | -0.41199
2182.0625 | 122.8363 | -122.4426 | 0.37537 | -0.00022891 | -0.019442 | 0.014637 | 0.035169 | -0.012424 | -0.038937 | -0.0004613 | -0.0075532 | 0.017993 | -0.038424 | -0.0014761 | -0.013424 | -0.001239 | 0.13733 | 0.13275 | 0.13733 | 0.10071 | 0.10071 | 0.036621 | -0.07782 | 0.09613 | 0.25635 | 0.082397 | 0.29755 | 0.27008 | -0.004578 | -0.054932 | 122.4792 | 122.3648 | -0.27466 | 122.5754 | 122.5433 | 0.17853 | -0.23804 | 122.438 | 122.3877 | -0.07782 | 122.5388 | 122.525 | 0.13733 | -0.10528 | 122.5433 | 122.58 | 122.58 | -0.45319 | 122.7402 | 122.7127 | 122.699 | -0.4303
2183.8438 | 122.9782 | -122.4106 | 0.32959 | -0.0078584 | -0.014529 | 0.01421 | 0.036664 | -0.012852 | -0.030606 | -0.0013159 | 7.627e-05 | 0.020557 | -0.035434 | -0.0021169 | -0.011288 | -0.0018798 | 0.07782 | -0.036621 | 0.009155 | 0.022888 | 0.12817 | 0.022888 | -0.11444 | 0.050354 | 0.13275 | -0.004578 | 0.3067 | 0.27924 | -0.004578 | -0.073242 | 122.4335 | 122.2961 | -0.20142 | 122.374 | 122.4335 | 0.13733 | -0.25177 | 122.406 | 122.3373 | -0.022888 | 122.4609 | 122.406 | 0.068664 | -0.050354 | 122.5388 | 122.4884 | 122.4197 | -0.44403 | 122.7173 | 122.6898 | 122.5433 | -0.40283
2185.625 | 122.8043 | -122.4564 | 0.36163 | -0.00022891 | -0.017306 | 0.015065 | 0.038373 | -0.010074 | -0.038083 | -0.0008887 | 0.0077058 | 0.016925 | -0.037783 | -0.0023305 | -0.014706 | -0.0016662 | 0.12817 | 0.10071 | 0.13733 | 0.086975 | 0.09613 | 0.041199 | -0.086975 | 0.054932 | 0.21973 | 0.045776 | 0.30212 | 0.28381 | -0.009155 | -0.073242 | 122.4976 | 122.3694 | -0.2655 | 122.5571 | 122.5433 | 0.17395 | -0.23346 | 122.4472 | 122.3831 | -0.059509 | 122.5113 | 122.5021 | 0.11902 | -0.07782 | 122.5525 | 122.5845 | 122.5937 | -0.44861 | 122.7585 | 122.7402 | 122.6761 | -0.43488
2187.4219 | 122.9645 | -122.3923 | 0.31128 | -0.00022891 | -0.012392 | 0.014424 | 0.037305 | -0.0081518 | -0.034024 | -3.4096e-05 | -0.0075532 | 0.022907 | -0.035861 | -0.00062151 | -0.011074 | -0.0027344 | 0.059509 | -0.045776 | 0.013733 | 0.022888 | 0.14191 | 0.013733 | -0.1236 | 0.041199 | 0.10986 | -0.027466 | 0.30212 | 0.30212 | -0.022888 | -0.068665 | 122.406 | 122.2687 | -0.16937 | 122.3465 | 122.4152 | 0.14648 | -0.25177 | 122.3694 | 122.3236 | -0.009155 | 122.4335 | 122.3648 | 0.041199 | -0.009155 | 122.5342 | 122.4518 | 122.406 | -0.43487 | 122.6944 | 122.6944 | 122.5021 | -0.37994
2189.125 | 122.8043 | -122.4335 | 0.37537 | -0.0078584 | -0.01581 | 0.017628 | 0.037305 | -0.010074 | -0.03851 | 0.0003931 | 7.627e-05 | 0.018207 | -0.040133 | -0.0019033 | -0.012997 | -0.0014526 | 0.09613 | 0.082397 | 0.10986 | 0.073242 | 0.11444 | 0.032043 | -0.10071 | 0.036621 | 0.20599 | 0.022888 | 0.31128 | 0.3067 | 0 | -0.07782 | 122.4655 | 122.3328 | -0.26092 | 122.5159 | 122.5067 | 0.17395 | -0.27924 | 122.4335 | 122.3557 | -0.064087 | 122.4701 | 122.4564 | 0.10071 | -0.068664 | 122.5479 | 122.5296 | 122.5433 | -0.47607 | 122.7448 | 122.7402 | 122.6395 | -0.45319
2190.9062 | 122.8592 | -122.4289 | 0.36163 | -0.00022891 | -0.017946 | 0.015706 | 0.036664 | -0.0090062 | -0.041073 | -0.0025977 | -0.0075532 | 0.01778 | -0.036715 | -0.0048941 | -0.011929 | -0.00059818 | 0.13275 | 0.12817 | 0.15564 | 0.10986 | 0.09613 | 0.045776 | -0.086975 | 0.11444 | 0.27008 | 0.10986 | 0.29297 | 0.2655 | -0.009155 | -0.050354 | 122.4747 | 122.3419 | -0.2655 | 122.5571 | 122.5388 | 0.19684 | -0.22888 | 122.4197 | 122.3785 | -0.068664 | 122.5433 | 122.5388 | 0.16022 | -0.09613 | 122.525 | 122.5616 | 122.5845 | -0.44861 | 122.7219 | 122.6944 | 122.699 | -0.41199
2192.6406 | 122.9141 | -122.406 | 0.32044 | -0.0078584 | -0.010897 | 0.014637 | 0.036878 | -0.0098608 | -0.034878 | 0.0008203 | 7.627e-05 | 0.02312 | -0.036288 | -0.0023305 | -0.012997 | -0.0016662 | 0.068665 | -0.054932 | -0.009155 | 0.032043 | 0.12817 | 0 | -0.12817 | -0.022888 | 0.13275 | -0.041199 | 0.32044 | 0.31128 | -0.032043 | -0.10071 | 122.406 | 122.2778 | -0.19226 | 122.3511 | 122.438 | 0.16022 | -0.25177 | 122.374 | 122.3053 | 0 | 122.3831 | 122.3648 | 0.059509 | -0.009156 | 122.5342 | 122.4747 | 122.3969 | -0.44861 | 122.7264 | 122.7173 | 122.5388 | -0.42114
2194.4219 | 122.8455 | -122.4243 | 0.36163 | 0.0074006 | -0.018801 | 0.013997 | 0.036664 | -0.010502 | -0.041501 | -0.0036657 | -0.0075532 | 0.016712 | -0.036074 | -0.0038259 | -0.014065 | 0.00047002 | 0.050354 | 0.041199 | 0.086975 | 0.068665 | 0.10529 | 0.050354 | -0.07782 | 0.059509 | 0.19684 | 0.073242 | 0.28381 | 0.25635 | 0.009155 | -0.064087 | 122.4747 | 122.3465 | -0.25635 | 122.4655 | 122.493 | 0.14649 | -0.31128 | 122.4335 | 122.3602 | -0.07782 | 122.4838 | 122.4976 | 0.13733 | -0.10528 | 122.5296 | 122.4747 | 122.5113 | -0.43945 | 122.7081 | 122.6807 | 122.6212 | -0.42572
2196.2031 | 122.8409 | -122.4518 | 0.35248 | -0.0078584 | -0.016878 | 0.016133 | 0.036664 | -0.011783 | -0.039364 | -0.0015295 | 7.627e-05 | 0.016071 | -0.037997 | -0.0033987 | -0.013424 | -0.001239 | 0.14191 | 0.11902 | 0.14648 | 0.09613 | 0.09613 | 0.027466 | -0.073242 | 0.10071 | 0.27466 | 0.10529 | 0.28381 | 0.28839 | 0.022888 | -0.059509 | 122.4792 | 122.3785 | -0.25635 | 122.5708 | 122.5479 | 0.16937 | -0.21057 | 122.4747 | 122.3923 | -0.068665 | 122.5525 | 122.5571 | 0.16479 | -0.064087 | 122.5479 | 122.5937 | 122.5983 | -0.42572 | 122.7356 | 122.7402 | 122.7264 | -0.41199
2198.0156 | 122.9095 | -122.406 | 0.32501 | -0.015487 | -0.014742 | 0.011433 | 0.033887 | -0.011997 | -0.031033 | 0.0023157 | -0.0075532 | 0.022693 | -0.038851 | 0.00066009 | -0.0091516 | -0.0031616 | 0.13733 | 0.009155 | 0.045776 | 0.050354 | 0.1236 | 0.022888 | -0.091553 | 0.018311 | 0.12817 | -0.050354 | 0.31128 | 0.30212 | -0.032043 | -0.091553 | 122.4289 | 122.3145 | -0.20142 | 122.4152 | 122.4564 | 0.14191 | -0.18768 | 122.374 | 122.3145 | -0.013733 | 122.4243 | 122.3557 | 0.041199 | -0.022888 | 122.5296 | 122.5433 | 122.4518 | -0.41657 | 122.7173 | 122.7081 | 122.5342 | -0.41657
2199.7344 | 122.8912 | -122.4335 | 0.32501 | -0.0078584 | -0.014529 | 0.01186 | 0.035809 | -0.0096472 | -0.031674 | -0.0006751 | -0.0075532 | 0.021839 | -0.039492 | -0.0016897 | -0.0082972 | 0.00025642 | 0.068665 | -0.036621 | 0.013733 | 0.018311 | 0.13275 | 0.009155 | -0.12817 | -0.022888 | 0.086975 | -0.07782 | 0.31586 | 0.29755 | -0.018311 | -0.091553 | 122.4426 | 122.3053 | -0.19226 | 122.3969 | 122.4518 | 0.14649 | -0.25635 | 122.4152 | 122.3419 | -0.009155 | 122.4106 | 122.3557 | 0.013733 | -0.027466 | 122.5662 | 122.5021 | 122.4472 | -0.45319 | 122.7493 | 122.731 | 122.5204 | -0.41657
2201.4531 | 122.8134 | -122.4701 | 0.37994 | 0.0074006 | -0.017733 | 0.014637 | 0.037518 | -0.012424 | -0.041928 | -0.0002477 | 7.627e-05 | 0.017993 | -0.036288 | -0.0038259 | -0.015347 | -0.00059818 | 0.082397 | 0.054932 | 0.09613 | 0.041199 | 0.082397 | 0.036621 | -0.086975 | 0.073242 | 0.17395 | 0.045776 | 0.27466 | 0.25635 | 0.004578 | -0.045776 | 122.5067 | 122.3831 | -0.29755 | 122.525 | 122.5113 | 0.12817 | -0.29755 | 122.4747 | 122.4243 | -0.10529 | 122.5433 | 122.5159 | 0.091552 | -0.1236 | 122.5525 | 122.5525 | 122.5662 | -0.46692 | 122.7448 | 122.7264 | 122.644 | -0.42572
2203.2344 | 122.8958 | -122.4472 | 0.31128 | 0.0074006 | -0.014956 | 0.013356 | 0.036878 | -0.010288 | -0.034024 | 0.0014613 | -0.0075532 | 0.020984 | -0.034793 | -0.00083531 | -0.0097924 | -0.0038024 | 0.1236 | 0.004578 | 0.036621 | 0.050354 | 0.11444 | 0.036621 | -0.10986 | 0.013733 | 0.15564 | -0.022888 | 0.32044 | 0.28839 | -0.022888 | -0.09613 | 122.4838 | 122.3373 | -0.19684 | 122.4518 | 122.4976 | 0.16022 | -0.18768 | 122.4243 | 122.3511 | 0.009156 | 122.4609 | 122.4243 | 0.073242 | -0.022888 | 122.5616 | 122.5708 | 122.4838 | -0.42114 | 122.7676 | 122.7356 | 122.6028 | -0.40741
2205.0312 | 122.905 | -122.4289 | 0.31586 | -0.00022891 | -0.013888 | 0.012074 | 0.037091 | -0.01157 | -0.033169 | 0.0023157 | -0.015182 | 0.02248 | -0.034793 | -0.00083531 | -0.010433 | -0.0014526 | 0.11444 | 0.004578 | 0.041199 | 0.050354 | 0.11444 | 0.027466 | -0.10986 | 0.022888 | 0.16479 | 0 | 0.28381 | 0.29755 | -0.013733 | -0.082397 | 122.4564 | 122.319 | -0.20142 | 122.4335 | 122.4792 | 0.16022 | -0.20142 | 122.4152 | 122.3465 | -0.032044 | 122.4518 | 122.4289 | 0.082397 | -0.018311 | 122.5433 | 122.5433 | 122.4701 | -0.42572 | 122.7127 | 122.7264 | 122.5937 | -0.39825
2206.8125 | 122.8226 | -122.4701 | 0.33875 | -0.00022891 | -0.02286 | 0.013569 | 0.036878 | -0.011143 | -0.044064 | -0.0019567 | -0.0075532 | 0.018634 | -0.039492 | -0.0019033 | -0.015988 | -0.00038438 | 0.10071 | 0.059509 | 0.10986 | 0.059509 | 0.07782 | 0.036621 | -0.082397 | 0.059509 | 0.17853 | 0.064087 | 0.28381 | 0.2655 | -0.004578 | -0.068665 | 122.5067 | 122.3877 | -0.26093 | 122.5296 | 122.5296 | 0.14191 | -0.23804 | 122.4655 | 122.4014 | -0.054932 | 122.5296 | 122.5342 | 0.13275 | -0.073242 | 122.5479 | 122.5708 | 122.58 | -0.42114 | 122.7539 | 122.7356 | 122.6486 | -0.40741
2208.5938 | 122.9095 | -122.4197 | 0.32044 | -0.00022891 | -0.014101 | 0.014851 | 0.036237 | -0.010715 | -0.034665 | 0.0016749 | 0.0077058 | 0.020984 | -0.036715 | -0.0014761 | -0.011074 | -0.0023072 | 0.10986 | 0 | 0.027466 | 0.041199 | 0.11444 | 0.013733 | -0.11444 | 0.009155 | 0.10986 | -0.027466 | 0.30212 | 0.28839 | -0.027466 | -0.082397 | 122.4335 | 122.3053 | -0.20599 | 122.4197 | 122.4609 | 0.15564 | -0.21057 | 122.3923 | 122.3373 | -0.018311 | 122.4289 | 122.3923 | 0.054931 | -0.032044 | 122.5342 | 122.5296 | 122.4472 | -0.43488 | 122.7219 | 122.7081 | 122.5296 | -0.40283
2210.3438 | 122.9233 | -122.438 | 0.31128 | -0.00022891 | -0.016665 | 0.014851 | 0.034101 | -0.010715 | -0.039364 | 0.0006067 | 7.627e-05 | 0.017993 | -0.039706 | -0.0025443 | -0.0093652 | 0.0015382 | 0.12817 | 0.082397 | 0.1236 | 0.09613 | 0.082397 | 0.050354 | -0.086975 | 0.10529 | 0.21057 | 0.07782 | 0.25635 | 0.23804 | 0.009155 | -0.064087 | 122.4884 | 122.3511 | -0.22888 | 122.5204 | 122.5342 | 0.1831 | -0.1831 | 122.4472 | 122.374 | -0.054931 | 122.5433 | 122.5159 | 0.14191 | -0.073242 | 122.5204 | 122.5662 | 122.5616 | -0.39825 | 122.6944 | 122.6761 | 122.6486 | -0.37537
2212.125 | 122.9645 | -122.4106 | 0.29755 | -0.0078584 | -0.012179 | 0.014424 | 0.034528 | -0.011997 | -0.036587 | -0.0017431 | 0.0077058 | 0.020771 | -0.038851 | 0.0013011 | -0.0095788 | 0.00089722 | 0.054932 | -0.050354 | -0.004578 | 0.027466 | 0.1236 | 0.027466 | -0.11902 | 0.004578 | 0.082397 | -0.009155 | 0.3067 | 0.29297 | -0.032043 | -0.091553 | 122.438 | 122.2916 | -0.17395 | 122.3602 | 122.438 | 0.14649 | -0.24261 | 122.3785 | 122.319 | 0.009156 | 122.4152 | 122.4014 | 0.082398 | -0.004577 | 122.5342 | 122.4655 | 122.406 | -0.41656 | 122.7173 | 122.7036 | 122.493 | -0.3891
2213.8906 | 122.8226 | -122.4701 | 0.36163 | 0.0074006 | -0.018374 | 0.015492 | 0.034741 | -0.012852 | -0.041073 | -0.0017431 | 7.627e-05 | 0.016284 | -0.040347 | -0.0021169 | -0.013424 | 0.00089722 | 0.12817 | 0.054932 | 0.11444 | 0.07782 | 0.086975 | 0.036621 | -0.086975 | 0.073242 | 0.18768 | 0.054932 | 0.28381 | 0.2655 | 0.004578 | -0.064087 | 122.5067 | 122.3831 | -0.27466 | 122.525 | 122.5479 | 0.16479 | -0.23346 | 122.4747 | 122.406 | -0.07782 | 122.5433 | 122.525 | 0.11902 | -0.09613 | 122.5571 | 122.5983 | 122.5845 | -0.44861 | 122.7539 | 122.7356 | 122.6578 | -0.42572
2215.6719 | 122.9187 | -122.4655 | 0.3067 | -0.0078584 | -0.016665 | 0.013783 | 0.038373 | -0.011143 | -0.03616 | 0.0008203 | -0.0075532 | 0.018848 | -0.035006 | -0.0025443 | -0.014065 | -0.0016662 | 0.14191 | 0.050354 | 0.13733 | 0.10529 | 0.10071 | 0.068665 | -0.073242 | 0.10529 | 0.20599 | 0.091553 | 0.26093 | 0.26093 | 0.027466 | -0.068665 | 122.5342 | 122.3923 | -0.20599 | 122.5159 | 122.5708 | 0.17853 | -0.16479 | 122.493 | 122.3969 | -0.045777 | 122.5708 | 122.5571 | 0.16022 | -0.045777 | 122.5662 | 122.6074 | 122.6028 | -0.37994 | 122.7264 | 122.7264 | 122.6715 | -0.37537
2217.3906 | 122.8317 | -122.4792 | 0.3479 | 0.0074006 | -0.019442 | 0.013783 | 0.037946 | -0.01392 | -0.040432 | -0.0028113 | 7.627e-05 | 0.015857 | -0.036929 | -0.0038259 | -0.014919 | -0.00017078 | 0.07782 | 0.013733 | 0.091553 | 0.064087 | 0.086975 | 0.027466 | -0.09613 | 0.045776 | 0.16022 | 0.041199 | 0.27466 | 0.26093 | -0.009155 | -0.064087 | 122.5067 | 122.3831 | -0.26092 | 122.493 | 122.5433 | 0.16022 | -0.27008 | 122.4701 | 122.4152 | -0.073242 | 122.525 | 122.5204 | 0.10529 | -0.086975 | 122.5662 | 122.5571 | 122.5708 | -0.44403 | 122.7539 | 122.7402 | 122.6395 | -0.41199
2219.1562 | 122.8638 | -122.4701 | 0.35706 | -0.0078584 | -0.019442 | 0.015492 | 0.038373 | -0.014774 | -0.040219 | -0.0040929 | -0.0075532 | 0.018634 | -0.037997 | -0.0023305 | -0.013424 | 4.2822e-05 | 0.086975 | 0.027466 | 0.10071 | 0.054932 | 0.10986 | 0.045776 | -0.068665 | 0.068665 | 0.19226 | 0.07782 | 0.25177 | 0.26093 | 0 | -0.064087 | 122.5159 | 122.4014 | -0.24719 | 122.4976 | 122.525 | 0.1236 | -0.27008 | 122.4701 | 122.406 | -0.10529 | 122.5388 | 122.5479 | 0.14191 | -0.096131 | 122.58 | 122.5571 | 122.5708 | -0.42572 | 122.7219 | 122.731 | 122.6624 | -0.42114
2220.9375 | 122.9416 | -122.4609 | 0.31586 | -0.00022891 | -0.016238 | 0.016346 | 0.033246 | -0.010502 | -0.03616 | 0.0006067 | -0.015182 | 0.021839 | -0.038851 | -0.0031851 | -0.007229 | -0.0023072 | 0.16022 | 0.036621 | 0.09613 | 0.07782 | 0.09613 | 0.07782 | -0.068665 | 0.091553 | 0.18768 | 0.059509 | 0.26093 | 0.23804 | -0.004578 | -0.045776 | 122.5388 | 122.3923 | -0.21973 | 122.4976 | 122.5388 | 0.14649 | -0.15564 | 122.4564 | 122.4152 | -0.054932 | 122.5525 | 122.5204 | 0.10528 | -0.07782 | 122.5571 | 122.6212 | 122.5571 | -0.38452 | 122.7219 | 122.699 | 122.6486 | -0.36163
2222.7344 | 122.9233 | -122.438 | 0.30212 | -0.00022891 | -0.014529 | 0.014851 | 0.037518 | -0.011143 | -0.035946 | 0.0008203 | 0.0077058 | 0.019916 | -0.035434 | -0.0038259 | -0.011501 | -0.0014526 | 0.054932 | -0.064087 | -0.013733 | 0.018311 | 0.15106 | 0.004578 | -0.11902 | -0.018311 | 0.11902 | -0.050354 | 0.31586 | 0.28381 | -0.041199 | -0.10986 | 122.4426 | 122.319 | -0.15106 | 122.374 | 122.4564 | 0.13733 | -0.24719 | 122.3969 | 122.3282 | 0.013733 | 122.4197 | 122.3877 | 0.059509 | -0.018311 | 122.5891 | 122.493 | 122.4243 | -0.42114 | 122.7539 | 122.7219 | 122.5571 | -0.41199
2224.4531 | 122.9187 | -122.4564 | 0.29755 | -0.0078584 | -0.012392 | 0.012501 | 0.0388 | -0.0081518 | -0.031674 | 0.0006067 | 7.627e-05 | 0.02312 | -0.033297 | -0.00062151 | -0.01022 | -0.0016662 | 0.12817 | 0.018311 | 0.045776 | 0.050354 | 0.12817 | 0.018311 | -0.10529 | 0.050354 | 0.14648 | -0.018311 | 0.30212 | 0.27466 | -0.018311 | -0.10529 | 122.4747 | 122.3511 | -0.16937 | 122.4747 | 122.5067 | 0.15564 | -0.16937 | 122.438 | 122.3511 | 0.004578 | 122.5067 | 122.438 | 0.086975 | -0.022888 | 122.5845 | 122.5845 | 122.5021 | -0.40283 | 122.7585 | 122.731 | 122.6028 | -0.40283
2226.2344 | 122.8134 | -122.5021 | 0.34332 | -0.0078584 | -0.019442 | 0.016987 | 0.037305 | -0.012638 | -0.041287 | -0.0025977 | 7.627e-05 | 0.015003 | -0.03757 | -0.0031851 | -0.014279 | 0.00025642 | 0.082397 | 0.022888 | 0.091553 | 0.041199 | 0.09613 | 0.050354 | -0.086975 | 0.032043 | 0.14191 | 0.045776 | 0.26093 | 0.2655 | 0.009155 | -0.059509 | 122.5525 | 122.4152 | -0.24719 | 122.525 | 122.5433 | 0.12817 | -0.26093 | 122.5113 | 122.4426 | -0.082398 | 122.5342 | 122.5479 | 0.10528 | -0.07782 | 122.5983 | 122.5845 | 122.5937 | -0.4303 | 122.7631 | 122.7676 | 122.644 | -0.40283
2227.9688 | 122.9416 | -122.4289 | 0.3067 | -0.00022891 | -0.016451 | 0.015065 | 0.033673 | -0.0098608 | -0.035733 | -0.0006751 | -0.0075532 | 0.020771 | -0.037356 | -0.0016897 | -0.01022 | -0.0014526 | 0.10986 | -0.004578 | 0.059509 | 0.041199 | 0.11444 | 0.050354 | -0.09613 | 0.068665 | 0.19226 | 0.036621 | 0.2655 | 0.24719 | -0.004578 | -0.073242 | 122.4792 | 122.3328 | -0.19226 | 122.4243 | 122.4701 | 0.13733 | -0.19684 | 122.4243 | 122.3557 | -0.041199 | 122.4976 | 122.4655 | 0.10986 | -0.05951 | 122.5433 | 122.5388 | 122.4884 | -0.40283 | 122.6944 | 122.6761 | 122.6212 | -0.37994
2229.75 | 122.9279 | -122.4426 | 0.31128 | -0.0078584 | -0.013674 | 0.012928 | 0.040509 | -0.011143 | -0.035519 | 0.0006067 | -0.0075532 | 0.021625 | -0.035647 | -0.0036123 | -0.01321 | -0.0014526 | 0.045776 | -0.041199 | 0.009155 | 0.018311 | 0.14648 | 0.009155 | -0.11902 | -0.036621 | 0.11444 | -0.045776 | 0.30212 | 0.28839 | -0.018311 | -0.10071 | 122.4518 | 122.3236 | -0.16479 | 122.4014 | 122.4609 | 0.13733 | -0.2655 | 122.4243 | 122.3419 | -0.009155 | 122.406 | 122.3969 | 0.054932 | -0.022888 | 122.5891 | 122.4884 | 122.4518 | -0.4303 | 122.7448 | 122.731 | 122.5571 | -0.41199
2231.4688 | 122.8821 | -122.4701 | 0.32501 | -0.00022891 | -0.016024 | 0.015065 | 0.037518 | -0.012852 | -0.044491 | -0.0004613 | -0.0075532 | 0.016925 | -0.036288 | -0.0027579 | -0.014492 | 0.00089722 | 0.12817 | 0.091553 | 0.13275 | 0.09613 | 0.091553 | 0.032043 | -0.091553 | 0.11444 | 0.25177 | 0.11444 | 0.24719 | 0.24261 | 0 | -0.064087 | 122.5021 | 122.3785 | -0.23346 | 122.5616 | 122.5662 | 0.18768 | -0.19684 | 122.4701 | 122.406 | -0.07782 | 122.5845 | 122.5845 | 0.17853 | -0.082397 | 122.5616 | 122.5983 | 122.6028 | -0.41657 | 122.7173 | 122.7127 | 122.7219 | -0.3891
2233.2656 | 122.8226 | -122.5159 | 0.33875 | -0.015487 | -0.017092 | 0.013356 | 0.037946 | -0.011783 | -0.038937 | 0.0018885 | -0.0075532 | 0.02013 | -0.035434 | -0.0033987 | -0.01321 | 4.2822e-05 | 0.13275 | 0.064087 | 0.11444 | 0.07782 | 0.086975 | 0.064087 | -0.064087 | 0.091553 | 0.17853 | 0.059509 | 0.26093 | 0.26093 | 0.018311 | -0.082397 | 122.58 | 122.4518 | -0.25177 | 122.58 | 122.5937 | 0.14191 | -0.20599 | 122.5342 | 122.4335 | -0.07782 | 122.6074 | 122.5754 | 0.14191 | -0.07782 | 122.6028 | 122.6486 | 122.6303 | -0.40283 | 122.7768 | 122.7768 | 122.6944 | -0.42114
2235.0625 | 122.9187 | -122.4976 | 0.3067 | -0.0078584 | -0.01346 | 0.013356 | 0.03346 | -0.008579 | -0.033383 | 0.0001795 | 7.627e-05 | 0.02312 | -0.035434 | -0.0023305 | -0.010433 | -0.0042298 | 0.12817 | 0.009155 | 0.036621 | 0.054932 | 0.1236 | 0.022888 | -0.10529 | 0.022888 | 0.12817 | -0.027466 | 0.27924 | 0.25177 | -0.022888 | -0.09613 | 122.5204 | 122.3923 | -0.18311 | 122.5067 | 122.5525 | 0.16022 | -0.17853 | 122.4747 | 122.4014 | -0.027466 | 122.5204 | 122.4701 | 0.068664 | -0.054932 | 122.6212 | 122.6257 | 122.5342 | -0.41199 | 122.7768 | 122.7493 | 122.6257 | -0.40283
2236.7812 | 122.85 | -122.4747 | 0.33417 | -0.0078584 | -0.016238 | 0.015919 | 0.037518 | -0.011997 | -0.04086 | -0.0013159 | -0.0075532 | 0.016712 | -0.037356 | -0.0031851 | -0.01257 | -0.0016662 | 0.12817 | 0.11902 | 0.15106 | 0.09613 | 0.09613 | 0.041199 | -0.073242 | 0.082397 | 0.26093 | 0.10529 | 0.25177 | 0.24261 | 0.013733 | -0.059509 | 122.5159 | 122.4014 | -0.23804 | 122.5937 | 122.5708 | 0.16937 | -0.20599 | 122.4884 | 122.4152 | -0.082397 | 122.5571 | 122.58 | 0.16479 | -0.091552 | 122.5708 | 122.6028 | 122.6257 | -0.40741 | 122.7264 | 122.7173 | 122.7356 | -0.39368
2238.5625 | 122.8683 | -122.4976 | 0.32044 | 0.0074006 | -0.016878 | 0.015492 | 0.036023 | -0.01157 | -0.042782 | -0.0002477 | 7.627e-05 | 0.018421 | -0.037997 | -0.0042531 | -0.014919 | -0.0016662 | 0.14191 | 0.13275 | 0.16022 | 0.11902 | 0.09613 | 0.050354 | -0.082397 | 0.10071 | 0.25635 | 0.09613 | 0.24261 | 0.24719 | 0.004578 | -0.064087 | 122.5479 | 122.4152 | -0.22431 | 122.6303 | 122.6166 | 0.20142 | -0.17853 | 122.5021 | 122.4335 | -0.07782 | 122.5983 | 122.5937 | 0.16022 | -0.073243 | 122.5937 | 122.6395 | 122.6578 | -0.40283 | 122.7402 | 122.7448 | 122.7539 | -0.38452
2240.3594 | 122.9553 | -122.4518 | 0.27924 | 0.0074006 | -0.013674 | 0.013997 | 0.033887 | -0.011143 | -0.031247 | 0.0012477 | 7.627e-05 | 0.021839 | -0.039279 | -0.0023305 | -0.0093652 | -0.002948 | 0.11902 | 0.013733 | 0.041199 | 0.045776 | 0.1236 | 0.009155 | -0.12817 | 0.036621 | 0.16022 | -0.009155 | 0.28381 | 0.27008 | -0.027466 | -0.086975 | 122.4609 | 122.3236 | -0.15564 | 122.4655 | 122.4976 | 0.17395 | -0.16022 | 122.4243 | 122.3648 | 0.004577 | 122.4884 | 122.4426 | 0.07782 | -0.009155 | 122.5754 | 122.5708 | 122.493 | -0.40741 | 122.7356 | 122.7219 | 122.612 | -0.36621
2242.1406 | 122.8683 | -122.493 | 0.32959 | -0.00022891 | -0.021578 | 0.013997 | 0.035169 | -0.010288 | -0.042141 | -0.0008887 | -0.0075532 | 0.017353 | -0.038638 | -0.0044669 | -0.014279 | 0.0019654 | 0.059509 | 0.013733 | 0.082397 | 0.068665 | 0.086975 | 0.032043 | -0.09613 | 0.050354 | 0.19226 | 0.050354 | 0.25635 | 0.25635 | -0.009155 | -0.068665 | 122.525 | 122.3969 | -0.24261 | 122.5067 | 122.5616 | 0.16479 | -0.27008 | 122.4838 | 122.4243 | -0.073242 | 122.5433 | 122.5433 | 0.11902 | -0.073242 | 122.58 | 122.5525 | 122.5754 | -0.42572 | 122.7493 | 122.7493 | 122.6852 | -0.39826
2243.9375 | 122.8775 | -122.4884 | 0.32959 | -0.00022891 | -0.016878 | 0.016774 | 0.040936 | -0.011143 | -0.041073 | -0.0011023 | -0.0075532 | 0.016498 | -0.036074 | -0.0025443 | -0.015988 | -0.00081178 | 0.10986 | 0.059509 | 0.11444 | 0.082397 | 0.10071 | 0.045776 | -0.086975 | 0.086975 | 0.23804 | 0.11444 | 0.25177 | 0.23804 | 0 | -0.073242 | 122.5342 | 122.4014 | -0.22888 | 122.5479 | 122.5708 | 0.16937 | -0.21973 | 122.4884 | 122.4152 | -0.07782 | 122.5754 | 122.6028 | 0.18768 | -0.091553 | 122.5891 | 122.5983 | 122.6028 | -0.41656 | 122.7402 | 122.7264 | 122.7264 | -0.40283
2245.6562 | 122.9691 | -122.4655 | 0.32044 | -0.00022891 | -0.017092 | 0.013783 | 0.033032 | -0.010502 | -0.035092 | 0.0006067 | -0.0075532 | 0.020557 | -0.035861 | -0.0014761 | -0.010647 | -0.0023072 | 0.14648 | 0.045776 | 0.10071 | 0.059509 | 0.082397 | 0.041199 | -0.064087 | 0.10529 | 0.19684 | 0.068665 | 0.25177 | 0.2243 | 0.004578 | -0.059509 | 122.5067 | 122.4014 | -0.23804 | 122.5113 | 122.525 | 0.1236 | -0.17395 | 122.4701 | 122.406 | -0.068665 | 122.5708 | 122.5342 | 0.12817 | -0.096131 | 122.5479 | 122.612 | 122.5662 | -0.38452 | 122.7173 | 122.6898 | 122.6624 | -0.37994
2247.4375 | 122.9233 | -122.4701 | 0.31128 | -0.00022891 | -0.01346 | 0.014424 | 0.037091 | -0.010715 | -0.03146 | 0.0008203 | 7.627e-05 | 0.02013 | -0.035006 | -0.0021169 | -0.0082972 | -0.0020934 | 0.054932 | -0.082397 | -0.022888 | 0.022888 | 0.13275 | 0.032043 | -0.12817 | -0.022888 | 0.073242 | -0.068665 | 0.29297 | 0.28839 | -0.036621 | -0.10529 | 122.5021 | 122.3419 | -0.17853 | 122.3877 | 122.493 | 0.15106 | -0.25635 | 122.4335 | 122.3648 | -0.01831 | 122.4472 | 122.4014 | 0.036621 | -0.022888 | 122.6028 | 122.525 | 122.4472 | -0.43945 | 122.7631 | 122.7585 | 122.5433 | -0.41656
2249.2188 | 122.9553 | -122.4655 | 0.29297 | -0.00022891 | -0.012392 | 0.012288 | 0.037946 | -0.010929 | -0.033383 | 0.0012477 | 7.627e-05 | 0.022907 | -0.03522 | -0.00062151 | -0.01022 | -0.00059818 | 0.086975 | 0.022888 | 0.054932 | 0.054932 | 0.1236 | 0.013733 | -0.13733 | 0.045776 | 0.16937 | -0.018311 | 0.27924 | 0.27008 | -0.032043 | -0.09613 | 122.4792 | 122.3282 | -0.16937 | 122.4884 | 122.5204 | 0.19226 | -0.20599 | 122.4335 | 122.3694 | -0.013733 | 122.5113 | 122.4472 | 0.077819 | -0.022888 | 122.5891 | 122.5525 | 122.5204 | -0.4303 | 122.7448 | 122.7356 | 122.6349 | -0.3891
2250.9375 | 122.9187 | -122.4747 | 0.29297 | 0.0074006 | -0.015383 | 0.012928 | 0.033673 | -0.011356 | -0.032956 | 0.0001795 | -0.0075532 | 0.020557 | -0.036715 | -0.00062151 | -0.010647 | 0.00025642 | 0.027466 | -0.041199 | 0 | 0 | 0.14191 | 0.004578 | -0.10986 | -0.045776 | 0.07782 | -0.082397 | 0.27466 | 0.28381 | -0.032043 | -0.10529 | 122.4792 | 122.3648 | -0.15106 | 122.4335 | 122.4747 | 0.10986 | -0.2655 | 122.4426 | 122.3694 | -0.018311 | 122.4289 | 122.3923 | 0.022889 | -0.009156 | 122.6166 | 122.5021 | 122.4747 | -0.40283 | 122.7493 | 122.7585 | 122.5525 | -0.39825
2252.7188 | 122.85 | -122.4884 | 0.31128 | -0.0078584 | -0.018374 | 0.013142 | 0.0388 | -0.011783 | -0.041714 | 0.0010339 | 7.627e-05 | 0.017993 | -0.036929 | -0.0016897 | -0.015347 | 0.00025642 | 0.09613 | 0.10071 | 0.1236 | 0.068665 | 0.086975 | 0.050354 | -0.064087 | 0.10071 | 0.21057 | 0.07782 | 0.23346 | 0.21973 | 0.013733 | -0.059509 | 122.5388 | 122.4243 | -0.2243 | 122.5891 | 122.5571 | 0.13275 | -0.21515 | 122.5021 | 122.4289 | -0.07782 | 122.5891 | 122.5662 | 0.13733 | -0.091552 | 122.5754 | 122.5845 | 122.612 | -0.37537 | 122.7219 | 122.7081 | 122.699 | -0.37079
2254.5 | 122.8775 | -122.4747 | 0.32501 | -0.00022891 | -0.017306 | 0.016346 | 0.037518 | -0.011997 | -0.041928 | -0.0002477 | -0.0075532 | 0.016498 | -0.037143 | -0.0051077 | -0.015133 | -0.0014526 | 0.11444 | 0.1236 | 0.13733 | 0.10986 | 0.086975 | 0.027466 | -0.073242 | 0.086975 | 0.2655 | 0.10529 | 0.24261 | 0.25635 | 0.018311 | -0.068665 | 122.5021 | 122.4014 | -0.23804 | 122.5983 | 122.5845 | 0.18311 | -0.21057 | 122.493 | 122.406 | -0.082397 | 122.5616 | 122.58 | 0.17395 | -0.068664 | 122.5616 | 122.5891 | 122.612 | -0.39825 | 122.7173 | 122.731 | 122.7402 | -0.39368
2256.2812 | 122.9187 | -122.4838 | 0.31128 | -0.00022891 | -0.014956 | 0.013997 | 0.034101 | -0.013279 | -0.031674 | -0.0015295 | 7.627e-05 | 0.022266 | -0.037356 | -0.00040791 | -0.0082972 | -0.00038438 | 0.064087 | -0.064087 | -0.009155 | 0.018311 | 0.13733 | 0.018311 | -0.11902 | -0.027466 | 0.059509 | -0.082397 | 0.29755 | 0.28839 | -0.027466 | -0.10986 | 122.5021 | 122.3648 | -0.17395 | 122.4197 | 122.5021 | 0.13733 | -0.24719 | 122.4564 | 122.374 | -0.013733 | 122.4564 | 122.4014 | 0.027466 | -0.022888 | 122.6212 | 122.5479 | 122.4747 | -0.4303 | 122.7814 | 122.7722 | 122.5433 | -0.42114
2258.0156 | 122.8546 | -122.4701 | 0.31128 | -0.0078584 | -0.016665 | 0.015919 | 0.039441 | -0.013492 | -0.045346 | -0.0032385 | 0.0077058 | 0.01778 | -0.03522 | -0.0040395 | -0.015347 | 0.00025642 | 0.10071 | 0.045776 | 0.10986 | 0.082397 | 0.10529 | 0.054932 | -0.064087 | 0.086975 | 0.21515 | 0.10071 | 0.25635 | 0.2655 | -0.013733 | -0.059509 | 122.525 | 122.406 | -0.20599 | 122.5159 | 122.5525 | 0.14648 | -0.21057 | 122.4564 | 122.4106 | -0.054931 | 122.5571 | 122.5708 | 0.16022 | -0.045776 | 122.5754 | 122.5708 | 122.58 | -0.37537 | 122.7264 | 122.7356 | 122.6852 | -0.37079
2259.7969 | 122.9507 | -122.4289 | 0.29755 | -0.00022891 | -0.012606 | 0.014637 | 0.034314 | -0.011143 | -0.034024 | -0.0028113 | 7.627e-05 | 0.02248 | -0.036074 | -0.0014761 | -0.01022 | -0.00038438 | 0.09613 | 0.009155 | 0.041199 | 0.050354 | 0.13275 | 0.022888 | -0.13733 | 0.032043 | 0.16479 | -0.009155 | 0.28381 | 0.26093 | -0.041199 | -0.082397 | 122.4518 | 122.2916 | -0.16479 | 122.438 | 122.4792 | 0.18768 | -0.20142 | 122.3877 | 122.3465 | -0.013733 | 122.4609 | 122.4197 | 0.073242 | -0.036621 | 122.5616 | 122.525 | 122.4701 | -0.43488 | 122.7127 | 122.6898 | 122.5937 | -0.37994
2261.5 | 122.937 | -122.4838 | 0.30212 | -0.00022891 | -0.017733 | 0.015278 | 0.034314 | -0.010288 | -0.037869 | 0.0006067 | -0.015182 | 0.019489 | -0.03757 | -0.0029715 | -0.01321 | -0.0010254 | 0.1236 | 0.073242 | 0.13275 | 0.091553 | 0.082397 | 0.041199 | -0.082397 | 0.10071 | 0.21973 | 0.091553 | 0.25635 | 0.24719 | 0.004578 | -0.064087 | 122.525 | 122.4014 | -0.21973 | 122.5571 | 122.5754 | 0.17395 | -0.17853 | 122.4884 | 122.4197 | -0.045776 | 122.5845 | 122.5754 | 0.15564 | -0.054932 | 122.5662 | 122.6074 | 122.6166 | -0.38452 | 122.7402 | 122.731 | 122.7036 | -0.36621
2263.2812 | 122.9462 | -122.4655 | 0.31128 | -0.0078584 | -0.013033 | 0.013997 | 0.035809 | -0.01157 | -0.034024 | -0.0008887 | 7.627e-05 | 0.022693 | -0.033511 | -0.0023305 | -0.010433 | 0.00068362 | 0.027466 | -0.11902 | -0.027466 | -0.009155 | 0.14191 | 0.004578 | -0.12817 | -0.018311 | 0.054932 | -0.064087 | 0.28839 | 0.28839 | -0.032043 | -0.091553 | 122.4701 | 122.3373 | -0.16937 | 122.3465 | 122.4564 | 0.11902 | -0.28381 | 122.4335 | 122.374 | -0.022888 | 122.4472 | 122.4014 | 0.027466 | -0.022888 | 122.6074 | 122.493 | 122.438 | -0.43945 | 122.7539 | 122.7539 | 122.5204 | -0.40283
2265.0625 | 122.9095 | -122.5113 | 0.30212 | -0.0078584 | -0.014315 | 0.014424 | 0.033673 | -0.010502 | -0.03616 | 0.0003931 | 7.627e-05 | 0.020557 | -0.034152 | 0.00023289 | -0.008938 | -0.00059818 | 0.073242 | -0.027466 | 0.027466 | 0.022888 | 0.14648 | 0.027466 | -0.11444 | -0.022888 | 0.09613 | -0.068665 | 0.29755 | 0.25635 | -0.036621 | -0.10071 | 122.5388 | 122.3969 | -0.15564 | 122.4838 | 122.5342 | 0.13733 | -0.22888 | 122.4747 | 122.4106 | -0.004578 | 122.4884 | 122.4426 | 0.032043 | -0.045776 | 122.6578 | 122.5845 | 122.5388 | -0.41657 | 122.8088 | 122.7676 | 122.6074 | -0.40283
2266.7812 | 122.9645 | -122.4564 | 0.2655 | -0.00022891 | -0.011538 | 0.012715 | 0.040296 | -0.011783 | -0.037655 | 0.0001795 | -0.015182 | 0.021625 | -0.034579 | -0.0014761 | -0.012142 | -0.0016662 | 0.041199 | -0.041199 | 0.004578 | 0.032043 | 0.13733 | 0.018311 | -0.1236 | 0.009155 | 0.13733 | -0.022888 | 0.27466 | 0.27924 | -0.032043 | -0.09613 | 122.4747 | 122.3328 | -0.12817 | 122.4152 | 122.4884 | 0.15564 | -0.2243 | 122.4243 | 122.3602 | 0.009155 | 122.4655 | 122.4335 | 0.073242 | 0.013733 | 122.5937 | 122.4976 | 122.4609 | -0.3891 | 122.731 | 122.7356 | 122.5937 | -0.36163
2268.5469 | 123.0011 | -122.4884 | 0.28839 | -0.015487 | -0.016451 | 0.014851 | 0.036237 | -0.012211 | -0.034237 | -3.4096e-05 | -0.015182 | 0.016498 | -0.035434 | -0.0014761 | -0.010647 | 0.00025642 | 0.059509 | -0.032043 | 0.036621 | 0.018311 | 0.14191 | 0.018311 | -0.11444 | 0.022888 | 0.13733 | 0.009155 | 0.27008 | 0.24719 | -0.013733 | -0.07782 | 122.5067 | 122.374 | -0.14648 | 122.4564 | 122.5067 | 0.13275 | -0.22888 | 122.4747 | 122.4106 | -0.01831 | 122.5113 | 122.4976 | 0.086975 | -0.041199 | 122.6303 | 122.5479 | 122.525 | -0.40283 | 122.7585 | 122.7356 | 122.6257 | -0.36621
2270.3281 | 122.8867 | -122.525 | 0.33417 | -0.00022891 | -0.017733 | 0.01656 | 0.035169 | -0.010715 | -0.044278 | -0.0028113 | 0.0077058 | 0.016071 | -0.036074 | -0.0051077 | -0.016201 | 0.00047002 | 0.050354 | 0.018311 | 0.082397 | 0.054932 | 0.09613 | 0.041199 | -0.091553 | 0.022888 | 0.17395 | 0.059509 | 0.25177 | 0.24719 | -0.009155 | -0.086975 | 122.5662 | 122.4335 | -0.23804 | 122.5433 | 122.58 | 0.14649 | -0.28381 | 122.5159 | 122.438 | -0.082397 | 122.5479 | 122.5845 | 0.14648 | -0.086975 | 122.6212 | 122.5754 | 122.6074 | -0.42572 | 122.7768 | 122.7722 | 122.699 | -0.42114
2272.0469 | 122.9462 | -122.4792 | 0.29755 | 0.0074006 | -0.017306 | 0.013569 | 0.034955 | -0.010502 | -0.036374 | -0.0006751 | -0.0075532 | 0.019062 | -0.034579 | -0.0033987 | -0.010647 | -0.0023072 | 0.1236 | 0.059509 | 0.10071 | 0.07782 | 0.10986 | 0.073242 | -0.073242 | 0.082397 | 0.1831 | 0.068665 | 0.24261 | 0.2243 | 0.032043 | -0.064087 | 122.5525 | 122.406 | -0.18768 | 122.5388 | 122.5571 | 0.15106 | -0.17395 | 122.5113 | 122.4152 | -0.054931 | 122.5616 | 122.5479 | 0.13275 | -0.073242 | 122.5891 | 122.6028 | 122.58 | -0.37079 | 122.7219 | 122.7036 | 122.6624 | -0.36163
2273.8438 | 122.9416 | -122.4701 | 0.28381 | 0.0074006 | -0.012179 | 0.012288 | 0.035382 | -0.008579 | -0.034665 | 0.0010339 | 0.015335 | 0.022907 | -0.035434 | -0.0029715 | -0.0087244 | -0.0016662 | 0.009155 | -0.091553 | -0.018311 | 0 | 0.12817 | 0.027466 | -0.11444 | -0.022888 | 0.059509 | -0.064087 | 0.27466 | 0.27466 | -0.027466 | -0.086975 | 122.4976 | 122.3557 | -0.15564 | 122.3785 | 122.4701 | 0.11444 | -0.27466 | 122.4426 | 122.3831 | -0.009155 | 122.4472 | 122.406 | 0.022888 | -0.009155 | 122.5983 | 122.4792 | 122.4518 | -0.39825 | 122.7448 | 122.7448 | 122.5296 | -0.37079
2275.625 | 122.9553 | -122.493 | 0.27924 | -0.00022891 | -0.017519 | 0.013569 | 0.033673 | -0.012424 | -0.038083 | 0.0006067 | 7.627e-05 | 0.017566 | -0.036715 | -0.0025443 | -0.011288 | 0.00025642 | 0.09613 | 0.054932 | 0.10986 | 0.09613 | 0.09613 | 0.054932 | -0.091553 | 0.10071 | 0.17853 | 0.073242 | 0.21973 | 0.21515 | 0.004578 | -0.050354 | 122.5479 | 122.4014 | -0.18311 | 122.5479 | 122.5891 | 0.18768 | -0.18311 | 122.4976 | 122.4426 | -0.059509 | 122.5937 | 122.5662 | 0.1236 | -0.064087 | 122.5891 | 122.5891 | 122.6028 | -0.37079 | 122.7127 | 122.7081 | 122.6715 | -0.32959
2277.3594 | 122.85 | -122.5159 | 0.32501 | -0.00022891 | -0.01581 | 0.013783 | 0.037305 | -0.012424 | -0.039151 | 0.0003931 | -0.015182 | 0.01778 | -0.034579 | -0.00062151 | -0.012783 | -0.0020934 | 0.11444 | 0.07782 | 0.13733 | 0.09613 | 0.086975 | 0.059509 | -0.082397 | 0.086975 | 0.21057 | 0.082397 | 0.22888 | 0.2243 | 0.004578 | -0.059509 | 122.5754 | 122.4335 | -0.23804 | 122.5937 | 122.612 | 0.17853 | -0.21057 | 122.5204 | 122.4564 | -0.09613 | 122.6028 | 122.5983 | 0.14191 | -0.10071 | 122.6028 | 122.6303 | 122.6532 | -0.40741 | 122.7448 | 122.7402 | 122.7264 | -0.38452
2279.1406 | 122.8592 | -122.5113 | 0.3067 | -0.0078584 | -0.013888 | 0.01421 | 0.040936 | -0.00922 | -0.039792 | -0.0017431 | -0.0075532 | 0.01778 | -0.034152 | -0.0036123 | -0.013424 | -0.0014526 | 0.022888 | 0 | 0.032043 | 0.013733 | 0.14191 | 0.009155 | -0.11902 | -0.022888 | 0.11444 | -0.027466 | 0.28381 | 0.27924 | -0.032043 | -0.13733 | 122.5204 | 122.3923 | -0.16479 | 122.5113 | 122.525 | 0.13275 | -0.28381 | 122.4792 | 122.374 | -0.022889 | 122.4884 | 122.4838 | 0.10986 | -0.027466 | 122.6532 | 122.5342 | 122.5433 | -0.42572 | 122.7951 | 122.7905 | 122.6257 | -0.44403
2280.9219 | 122.8363 | -122.5296 | 0.32501 | -0.00022891 | -0.021151 | 0.01421 | 0.03645 | -0.010502 | -0.042782 | -0.0021703 | 7.627e-05 | 0.019062 | -0.037997 | -0.0042531 | -0.015133 | -0.0010254 | 0.073242 | 0.045776 | 0.068665 | 0.059509 | 0.086975 | 0.041199 | -0.068665 | 0.054932 | 0.16022 | 0.045776 | 0.22888 | 0.23346 | -0.018311 | -0.07782 | 122.5708 | 122.4609 | -0.23804 | 122.5754 | 122.5891 | 0.12817 | -0.25177 | 122.5113 | 122.4518 | -0.09613 | 122.5845 | 122.5754 | 0.1236 | -0.091553 | 122.6166 | 122.6028 | 122.5983 | -0.39368 | 122.7585 | 122.7631 | 122.6898 | -0.40283
2282.6406 | 122.9141 | -122.5113 | 0.28381 | -0.00022891 | -0.01282 | 0.012288 | 0.035169 | -0.011356 | -0.031674 | 0.0003931 | 7.627e-05 | 0.022266 | -0.038211 | -0.0016897 | -0.0097924 | -0.0031616 | 0.10071 | 0.013733 | 0.036621 | 0.036621 | 0.13275 | 0.018311 | -0.12817 | 0.013733 | 0.10529 | -0.036621 | 0.25177 | 0.25635 | -0.032043 | -0.10071 | 122.5296 | 122.3831 | -0.15106 | 122.525 | 122.5479 | 0.1648 | -0.1831 | 122.4792 | 122.4106 | -0.032043 | 122.525 | 122.4747 | 0.064087 | -0.027465 | 122.644 | 122.612 | 122.5479 | -0.41199 | 122.7631 | 122.7676 | 122.6166 | -0.38452
2284.4375 | 122.8912 | -122.4976 | 0.29297 | -0.0078584 | -0.017946 | 0.014851 | 0.034314 | -0.011356 | -0.040005 | 0.0003931 | 7.627e-05 | 0.017353 | -0.037997 | -0.0040395 | -0.01257 | 4.2822e-05 | 0.12817 | 0.082397 | 0.13733 | 0.091553 | 0.082397 | 0.054932 | -0.073242 | 0.09613 | 0.2243 | 0.064087 | 0.23346 | 0.21973 | 0.018311 | -0.050354 | 122.5525 | 122.4243 | -0.21057 | 122.58 | 122.5891 | 0.16479 | -0.16479 | 122.5159 | 122.4472 | -0.05951 | 122.5937 | 122.5616 | 0.11444 | -0.073242 | 122.58 | 122.6257 | 122.6349 | -0.36621 | 122.731 | 122.7173 | 122.7219 | -0.34332
2286.1562 | 122.9279 | -122.4747 | 0.27008 | -0.00022891 | -0.014529 | 0.013783 | 0.034101 | -0.013065 | -0.035092 | -0.0004613 | 7.627e-05 | 0.021198 | -0.036288 | -0.0038259 | -0.0097924 | -0.0025208 | 0.11444 | 0.027466 | 0.050354 | 0.050354 | 0.12817 | 0.027466 | -0.11444 | 0.045776 | 0.15564 | -0.009155 | 0.25177 | 0.24261 | -0.013733 | -0.086975 | 122.5021 | 122.3602 | -0.14191 | 122.5021 | 122.525 | 0.16479 | -0.15564 | 122.4609 | 122.3877 | -0.018311 | 122.5204 | 122.4655 | 0.07782 | -0.027466 | 122.6028 | 122.5891 | 122.525 | -0.38452 | 122.7264 | 122.7173 | 122.6303 | -0.35706
2287.9531 | 122.9233 | -122.493 | 0.28381 | 0.0074006 | -0.012179 | 0.013997 | 0.034101 | -0.012638 | -0.035946 | 0.0023157 | -0.0075532 | 0.019275 | -0.037143 | -0.0010489 | -0.0085108 | -0.00017078 | 0.036621 | -0.07782 | -0.004578 | 0.009155 | 0.11902 | 0.013733 | -0.13275 | -0.050354 | 0.045776 | -0.07782 | 0.28381 | 0.24719 | -0.018311 | -0.10071 | 122.5067 | 122.3602 | -0.16479 | 122.4152 | 122.5021 | 0.14191 | -0.24719 | 122.4747 | 122.3923 | 0 | 122.4426 | 122.4152 | 0.022888 | -0.036621 | 122.612 | 122.5296 | 122.4884 | -0.41656 | 122.7768 | 122.7402 | 122.5388 | -0.38452
2289.7344 | 122.9874 | -122.4747 | 0.27924 | -0.00022891 | -0.012606 | 0.012074 | 0.036664 | -0.010929 | -0.037655 | 0.0012477 | 0.0077058 | 0.021198 | -0.035647 | -0.0033987 | -0.010006 | 0.0011108 | 0.045776 | -0.032043 | -0.004578 | 0.018311 | 0.12817 | 0.009155 | -0.09613 | 0.045776 | 0.10986 | -0.004578 | 0.25635 | 0.23346 | -0.022888 | -0.073242 | 122.4838 | 122.3785 | -0.15106 | 122.4426 | 122.493 | 0.11444 | -0.23346 | 122.4518 | 122.4014 | -0.022888 | 122.5204 | 122.4701 | 0.068664 | -0.045777 | 122.6028 | 122.5204 | 122.4701 | -0.37537 | 122.731 | 122.7081 | 122.5845 | -0.35248
2291.4688 | 122.8867 | -122.5204 | 0.31128 | 0.0074006 | -0.016451 | 0.013356 | 0.037946 | -0.013279 | -0.038723 | 0.0006067 | -0.0075532 | 0.019275 | -0.033511 | -0.0033987 | -0.014065 | -0.0010254 | 0.027466 | -0.036621 | 0.009155 | 0.013733 | 0.13733 | 0.018311 | -0.13733 | -0.045776 | 0.10071 | -0.036621 | 0.27466 | 0.24719 | -0.032043 | -0.09613 | 122.5388 | 122.3831 | -0.17395 | 122.4838 | 122.5342 | 0.15106 | -0.28381 | 122.4884 | 122.4243 | -0.036621 | 122.4747 | 122.4838 | 0.059509 | -0.064087 | 122.6578 | 122.5479 | 122.5296 | -0.44861 | 122.7951 | 122.7676 | 122.6212 | -0.40741
2293.25 | 122.9691 | -122.5021 | 0.26093 | 0.0074006 | -0.016451 | 0.013142 | 0.03645 | -0.010288 | -0.039364 | 0.0018885 | -0.0075532 | 0.017993 | -0.034579 | -0.0040395 | -0.012997 | -0.0014526 | 0.11444 | 0.045776 | 0.10986 | 0.068665 | 0.09613 | 0.041199 | -0.10071 | 0.07782 | 0.19684 | 0.068665 | 0.21973 | 0.19684 | 0.013733 | -0.073242 | 122.5433 | 122.4014 | -0.1648 | 122.5479 | 122.5708 | 0.16937 | -0.14648 | 122.5159 | 122.4289 | -0.041198 | 122.58 | 122.5708 | 0.14191 | -0.064087 | 122.5983 | 122.6166 | 122.612 | -0.36163 | 122.7219 | 122.699 | 122.699 | -0.33417
2295.0312 | 122.9279 | -122.525 | 0.2655 | -0.0078584 | -0.014101 | 0.012928 | 0.037091 | -0.010715 | -0.03381 | -0.0002477 | 7.627e-05 | 0.019275 | -0.03522 | -0.00083531 | -0.01022 | -0.0014526 | 0.082397 | 0.004578 | 0.032043 | 0.064087 | 0.13275 | 0.022888 | -0.11902 | 0.009155 | 0.1236 | -0.036621 | 0.26093 | 0.23346 | -0.032043 | -0.091553 | 122.5479 | 122.406 | -0.13275 | 122.5296 | 122.5891 | 0.18311 | -0.18311 | 122.493 | 122.4335 | -0.004578 | 122.5342 | 122.4884 | 0.054932 | -0.032044 | 122.6578 | 122.6074 | 122.5571 | -0.38452 | 122.7859 | 122.7585 | 122.6486 | -0.35706
2296.7344 | 122.9828 | -122.4884 | 0.29297 | -0.00022891 | -0.016665 | 0.015492 | 0.035596 | -0.010929 | -0.037869 | 0.0010339 | 7.627e-05 | 0.020984 | -0.037997 | -0.00019431 | -0.0097924 | -0.00059818 | 0.068665 | -0.018311 | 0.036621 | 0.027466 | 0.1236 | 0.041199 | -0.11444 | 0.050354 | 0.14648 | 0.032043 | 0.23804 | 0.23804 | 0.009155 | -0.07782 | 122.5296 | 122.374 | -0.16937 | 122.4701 | 122.5159 | 0.14191 | -0.2243 | 122.4976 | 122.4106 | -0.054932 | 122.5388 | 122.5204 | 0.10986 | -0.054932 | 122.612 | 122.5571 | 122.525 | -0.40741 | 122.7264 | 122.7264 | 122.6349 | -0.37079
2298.5312 | 122.8455 | -122.5296 | 0.32044 | -0.015487 | -0.017946 | 0.011647 | 0.039441 | -0.011143 | -0.04086 | 0.0003931 | 7.627e-05 | 0.016925 | -0.035006 | -0.0021169 | -0.014706 | -0.00059818 | 0.10071 | 0.07782 | 0.13275 | 0.073242 | 0.086975 | 0.050354 | -0.073242 | 0.07782 | 0.17853 | 0.064087 | 0.2243 | 0.21515 | -0.009155 | -0.073242 | 122.58 | 122.4564 | -0.23346 | 122.6074 | 122.6028 | 0.14648 | -0.21973 | 122.5204 | 122.4564 | -0.096131 | 122.6074 | 122.5937 | 0.13733 | -0.10529 | 122.6166 | 122.6303 | 122.6624 | -0.39368 | 122.7539 | 122.7448 | 122.7081 | -0.39368
2300.2656 | 122.9599 | -122.5159 | 0.27466 | -0.00022891 | -0.015597 | 0.014637 | 0.033673 | -0.012424 | -0.036587 | -0.0015295 | 7.627e-05 | 0.022693 | -0.037356 | -0.00062151 | -0.0091516 | -0.00081178 | 0.036621 | -0.082397 | -0.027466 | 0.009155 | 0.1236 | 0.013733 | -0.11902 | -0.022888 | 0.050354 | -0.064087 | 0.2655 | 0.25635 | -0.036621 | -0.07782 | 122.5296 | 122.3969 | -0.15106 | 122.4335 | 122.525 | 0.12817 | -0.23804 | 122.4792 | 122.438 | -0.009155 | 122.493 | 122.4518 | 0.013733 | -0.01831 | 122.6395 | 122.5525 | 122.4884 | -0.39368 | 122.7814 | 122.7722 | 122.5662 | -0.35248
2302.0312 | 122.9645 | -122.493 | 0.26093 | 0.0074006 | -0.012392 | 0.01186 | 0.039227 | -0.012852 | -0.034878 | -0.0004613 | 7.627e-05 | 0.022693 | -0.03287 | -0.0029715 | -0.012356 | -0.0020934 | 0.045776 | -0.027466 | 0.022888 | 0.045776 | 0.12817 | 0.018311 | -0.10986 | 0.013733 | 0.14191 | -0.013733 | 0.25177 | 0.24719 | -0.032043 | -0.09613 | 122.5113 | 122.3831 | -0.13275 | 122.4655 | 122.5388 | 0.15564 | -0.21515 | 122.4609 | 122.3969 | -0.009155 | 122.5067 | 122.4792 | 0.082397 | -0.013733 | 122.6212 | 122.5388 | 122.5159 | -0.37079 | 122.7448 | 122.7402 | 122.6349 | -0.35706
2303.8125 | 122.8912 | -122.525 | 0.3067 | -0.0078584 | -0.020724 | 0.016774 | 0.03645 | -0.012852 | -0.044491 | -0.0028113 | 7.627e-05 | 0.017353 | -0.036074 | -0.0029715 | -0.01321 | 0.002179 | 0.091553 | 0.073242 | 0.12817 | 0.082397 | 0.11444 | 0.036621 | -0.09613 | 0.082397 | 0.22888 | 0.10071 | 0.2243 | 0.22888 | 0.013733 | -0.064087 | 122.5616 | 122.4289 | -0.19226 | 122.5983 | 122.6074 | 0.17853 | -0.21515 | 122.5388 | 122.4609 | -0.082398 | 122.6074 | 122.6257 | 0.1648 | -0.07782 | 122.6395 | 122.6166 | 122.6532 | -0.40283 | 122.7493 | 122.7539 | 122.7539 | -0.37079
2305.5312 | 123.0148 | -122.4655 | 0.25177 | -0.0078584 | -0.016451 | 0.013569 | 0.033246 | -0.011143 | -0.034878 | -0.0013159 | 0.0077058 | 0.021198 | -0.034793 | -0.0023305 | -0.011501 | -0.0033752 | 0.059509 | -0.041199 | 0.009155 | 0.013733 | 0.12817 | 0.036621 | -0.12817 | 0.027466 | 0.10986 | -0.013733 | 0.24719 | 0.22888 | -0.013733 | -0.082397 | 122.5021 | 122.3373 | -0.1236 | 122.4243 | 122.4792 | 0.14191 | -0.19226 | 122.4518 | 122.3831 | -0.004578 | 122.493 | 122.4518 | 0.068664 | -0.022888 | 122.5937 | 122.525 | 122.4747 | -0.37994 | 122.7127 | 122.6944 | 122.5754 | -0.33417
2307.3125 | 122.8409 | -122.5204 | 0.3067 | -0.015487 | -0.016665 | 0.01656 | 0.035169 | -0.010288 | -0.039792 | -0.0015295 | -0.0075532 | 0.019062 | -0.038424 | -0.0036123 | -0.01257 | 0.00025642 | 0.1236 | 0.086975 | 0.13275 | 0.086975 | 0.10071 | 0.036621 | -0.091553 | 0.050354 | 0.22888 | 0.059509 | 0.21973 | 0.21057 | 0.009155 | -0.068665 | 122.5571 | 122.4289 | -0.20599 | 122.6074 | 122.6074 | 0.17853 | -0.18311 | 122.5296 | 122.4518 | -0.086975 | 122.5708 | 122.58 | 0.12817 | -0.096131 | 122.6212 | 122.644 | 122.6532 | -0.39825 | 122.7402 | 122.731 | 122.7493 | -0.37537
2309.0938 | 122.8729 | -122.525 | 0.29755 | 0.0074006 | -0.017092 | 0.015065 | 0.035809 | -0.01157 | -0.040005 | -0.0013159 | -0.0075532 | 0.016712 | -0.036502 | -0.0014761 | -0.015133 | -0.0020934 | 0.14191 | 0.09613 | 0.13275 | 0.091553 | 0.10986 | 0.041199 | -0.082397 | 0.07782 | 0.24719 | 0.10071 | 0.22888 | 0.21973 | 0.009155 | -0.073242 | 122.5662 | 122.4426 | -0.18768 | 122.6212 | 122.6166 | 0.17395 | -0.15564 | 122.5342 | 122.4518 | -0.068664 | 122.6028 | 122.6257 | 0.17395 | -0.077819 | 122.6349 | 122.6669 | 122.6578 | -0.37994 | 122.7539 | 122.7448 | 122.7722 | -0.37079
2310.875 | 122.9553 | -122.4838 | 0.26093 | -0.0078584 | -0.013888 | 0.013783 | 0.036237 | -0.010929 | -0.03146 | 0.0001795 | 7.627e-05 | 0.022266 | -0.035434 | 1.9292e-05 | -0.0093652 | -0.002948 | 0.11444 | 0.018311 | 0.059509 | 0.059509 | 0.14191 | 0.013733 | -0.12817 | 0.045776 | 0.13275 | -0.022888 | 0.25177 | 0.2243 | -0.036621 | -0.091553 | 122.4976 | 122.3557 | -0.11902 | 122.5021 | 122.5433 | 0.18768 | -0.14648 | 122.4472 | 122.3923 | -0.009155 | 122.5296 | 122.4609 | 0.068665 | -0.036621 | 122.6257 | 122.5983 | 122.5433 | -0.3891 | 122.7356 | 122.7081 | 122.6166 | -0.35248
2312.6719 | 122.8638 | -122.5525 | 0.29755 | -0.0078584 | -0.017306 | 0.016133 | 0.039227 | -0.012211 | -0.042569 | -0.0011023 | 7.627e-05 | 0.017353 | -0.035861 | -0.0046805 | -0.014492 | -0.00059818 | 0.07782 | 0.018311 | 0.07782 | 0.059509 | 0.086975 | 0.054932 | -0.091553 | 0.045776 | 0.15106 | 0.032043 | 0.22888 | 0.21057 | 0.009155 | -0.091553 | 122.6074 | 122.4609 | -0.21057 | 122.5708 | 122.612 | 0.15106 | -0.21973 | 122.5616 | 122.4609 | -0.068664 | 122.5983 | 122.5845 | 0.1236 | -0.086975 | 122.6395 | 122.6303 | 122.6303 | -0.3891 | 122.7814 | 122.7631 | 122.7036 | -0.3891
2314.4062 | 122.9416 | -122.5342 | 0.27008 | -0.00022891 | -0.014742 | 0.012928 | 0.031964 | -0.010929 | -0.033169 | -0.0019567 | -0.0075532 | 0.02248 | -0.036502 | -0.0021169 | -0.01022 | -0.0018798 | 0.045776 | -0.09613 | -0.018311 | 0.004578 | 0.14191 | 0.032043 | -0.11902 | -0.032043 | 0.036621 | -0.086975 | 0.24261 | 0.24261 | -0.022888 | -0.10529 | 122.5662 | 122.4152 | -0.12817 | 122.4381 | 122.5388 | 0.1236 | -0.22431 | 122.5113 | 122.4289 | -0.027466 | 122.5021 | 122.4472 | 0.018311 | -0.027466 | 122.6761 | 122.58 | 122.5159 | -0.3891 | 122.7768 | 122.7768 | 122.5708 | -0.37537
2316.1719 | 122.8729 | -122.5525 | 0.28839 | -0.0078584 | -0.021364 | 0.014851 | 0.035596 | -0.012424 | -0.038083 | 0.0018885 | -0.015182 | 0.017139 | -0.035006 | -0.0042531 | -0.012142 | 4.2822e-05 | 0.13733 | 0.086975 | 0.13275 | 0.07782 | 0.091553 | 0.045776 | -0.07782 | 0.086975 | 0.20599 | 0.068665 | 0.19226 | 0.20142 | 0.004578 | -0.064087 | 122.5983 | 122.4747 | -0.19684 | 122.6395 | 122.6303 | 0.15564 | -0.15106 | 122.5571 | 122.4884 | -0.09613 | 122.6395 | 122.6212 | 0.13275 | -0.086975 | 122.644 | 122.6898 | 122.6852 | -0.36621 | 122.7448 | 122.7539 | 122.7585 | -0.35248
2317.9688 | 122.9553 | -122.5021 | 0.26093 | -0.00022891 | -0.013247 | 0.012501 | 0.039441 | -0.011356 | -0.033596 | 0.0008203 | -0.0075532 | 0.022693 | -0.033511 | -0.0010489 | -0.0093652 | -0.0016662 | 0.10071 | 0 | 0.041199 | 0.041199 | 0.13733 | 0.018311 | -0.11444 | 0.041199 | 0.15564 | -0.022888 | 0.25177 | 0.21973 | -0.018311 | -0.10529 | 122.5204 | 122.3877 | -0.1236 | 122.5021 | 122.5433 | 0.15564 | -0.16022 | 122.4838 | 122.3968 | -0.009155 | 122.5433 | 122.4792 | 0.082398 | -0.041198 | 122.6395 | 122.6028 | 122.5433 | -0.37537 | 122.7539 | 122.7219 | 122.6578 | -0.36621
2319.6875 | 122.9279 | -122.5296 | 0.2655 | 0.0074006 | -0.015597 | 0.010365 | 0.035169 | -0.01157 | -0.033383 | 0.0021021 | -0.0075532 | 0.021198 | -0.035006 | -0.0014761 | -0.011288 | -0.0020934 | 0.027466 | -0.054932 | 0.009155 | 0.004578 | 0.13275 | 0.022888 | -0.12817 | -0.041199 | 0.059509 | -0.07782 | 0.2655 | 0.23346 | -0.036621 | -0.10986 | 122.5525 | 122.4014 | -0.13275 | 122.4747 | 122.5342 | 0.13275 | -0.23804 | 122.493 | 122.4197 | 0 | 122.4884 | 122.4518 | 0.032043 | -0.032044 | 122.6624 | 122.5571 | 122.5388 | -0.39368 | 122.7951 | 122.7631 | 122.5891 | -0.37537
2321.4688 | 123.0148 | -122.5159 | 0.24261 | -0.00022891 | -0.015383 | 0.014851 | 0.035809 | -0.0096472 | -0.03616 | 0.0012477 | -0.0075532 | 0.018207 | -0.036074 | -0.00062151 | -0.0087244 | 0.0013244 | 0.045776 | -0.032043 | 0.022888 | 0.027466 | 0.13733 | 0.009155 | -0.11902 | 0.032043 | 0.13275 | 0.004578 | 0.23804 | 0.23346 | -0.013733 | -0.091553 | 122.525 | 122.3969 | -0.10529 | 122.4838 | 122.5433 | 0.14649 | -0.19684 | 122.5021 | 122.4243 | -0.004578 | 122.5479 | 122.5204 | 0.096131 | -0.009156 | 122.6532 | 122.5616 | 122.5388 | -0.36163 | 122.7539 | 122.7493 | 122.6486 | -0.33417
2323.25 | 122.8409 | -122.5616 | 0.29297 | -0.00022891 | -0.017092 | 0.012928 | 0.034314 | -0.011356 | -0.041501 | -3.4096e-05 | 7.627e-05 | 0.017139 | -0.035861 | -0.0040395 | -0.014279 | 0.0015382 | 0.091553 | 0.050354 | 0.10071 | 0.059509 | 0.09613 | 0.036621 | -0.082397 | 0.054932 | 0.16937 | 0.027466 | 0.21515 | 0.21515 | -0.009155 | -0.07782 | 122.5983 | 122.4792 | -0.19684 | 122.612 | 122.6212 | 0.14191 | -0.20142 | 122.5525 | 122.4838 | -0.07782 | 122.6166 | 122.5891 | 0.10529 | -0.07782 | 122.6578 | 122.6532 | 122.6624 | -0.37537 | 122.7768 | 122.7768 | 122.731 | -0.37079
2324.9844 | 122.9279 | -122.5571 | 0.26093 | 0.0074006 | -0.017306 | 0.010579 | 0.035596 | -0.012211 | -0.033383 | 0.0016749 | 0.0077058 | 0.02312 | -0.033938 | -0.00062151 | -0.010861 | -0.0018798 | 0.064087 | -0.059509 | 0.013733 | 0.032043 | 0.1236 | 0.013733 | -0.10529 | -0.018311 | 0.082397 | -0.07782 | 0.25177 | 0.22888 | -0.027466 | -0.11444 | 122.5708 | 122.4518 | -0.13733 | 122.4976 | 122.5891 | 0.13733 | -0.19684 | 122.5296 | 122.4426 | -0.009155 | 122.5388 | 122.4792 | 0.036621 | -0.032043 | 122.6807 | 122.6212 | 122.5708 | -0.36621 | 122.8088 | 122.7859 | 122.6395 | -0.37537
2326.75 | 122.9416 | -122.525 | 0.24261 | -0.0078584 | -0.013247 | 0.012288 | 0.039441 | -0.011783 | -0.035305 | -0.0002477 | -0.0075532 | 0.022693 | -0.033297 | -0.0010489 | -0.0091516 | 0.00025642 | 0.09613 | 0.013733 | 0.045776 | 0.050354 | 0.1236 | 0.022888 | -0.13275 | 0.041199 | 0.16022 | -0.032043 | 0.22888 | 0.23346 | -0.027466 | -0.086975 | 122.5479 | 122.3923 | -0.11902 | 122.5388 | 122.5754 | 0.18311 | -0.14649 | 122.4976 | 122.438 | -0.013733 | 122.5662 | 122.493 | 0.054932 | -0.009156 | 122.6486 | 122.6212 | 122.5708 | -0.37537 | 122.7539 | 122.7585 | 122.6852 | -0.32959
2328.5469 | 122.8683 | -122.5571 | 0.28839 | -0.015487 | -0.02286 | 0.013142 | 0.037091 | -0.013279 | -0.043637 | -0.0015295 | -0.0075532 | 0.014576 | -0.035434 | -0.0033987 | -0.014706 | 0.0011108 | 0.073242 | 0.022888 | 0.086975 | 0.054932 | 0.09613 | 0.045776 | -0.082397 | 0.027466 | 0.15564 | 0.050354 | 0.21973 | 0.20142 | 0.013733 | -0.059509 | 122.6028 | 122.4747 | -0.19226 | 122.58 | 122.612 | 0.13733 | -0.21515 | 122.5708 | 122.4976 | -0.068664 | 122.5845 | 122.6074 | 0.10986 | -0.086975 | 122.6532 | 122.6303 | 122.644 | -0.37079 | 122.7768 | 122.7585 | 122.7127 | -0.3479
2330.2656 | 122.9279 | -122.525 | 0.27008 | -0.0078584 | -0.0096152 | 0.010365 | 0.038373 | -0.012211 | -0.032528 | -0.0013159 | -0.0075532 | 0.022693 | -0.033511 | 0.00066009 | -0.011715 | -0.0048706 | 0.086975 | -0.022888 | 0.027466 | 0.041199 | 0.13733 | 0.013733 | -0.10529 | 0 | 0.091553 | -0.050354 | 0.23346 | 0.22888 | -0.036621 | -0.10071 | 122.5388 | 122.4197 | -0.13275 | 122.5021 | 122.5662 | 0.14649 | -0.18311 | 122.4884 | 122.4243 | -0.036622 | 122.525 | 122.4747 | 0.050354 | -0.041199 | 122.6624 | 122.612 | 122.5525 | -0.37537 | 122.7585 | 122.7539 | 122.6166 | -0.37079
2332.0469 | 122.8729 | -122.5433 | 0.29297 | 0.0074006 | -0.02286 | 0.015706 | 0.034741 | -0.011356 | -0.042782 | -0.0028113 | -0.0075532 | 0.016925 | -0.036715 | -0.0010489 | -0.015988 | -0.00017078 | 0.11444 | 0.12817 | 0.14191 | 0.10529 | 0.10071 | 0.045776 | -0.09613 | 0.086975 | 0.24261 | 0.10986 | 0.19684 | 0.20599 | 0.004578 | -0.064087 | 122.5891 | 122.4472 | -0.19226 | 122.6715 | 122.6486 | 0.20142 | -0.17853 | 122.5479 | 122.4792 | -0.096131 | 122.6303 | 122.6532 | 0.17395 | -0.086975 | 122.644 | 122.6578 | 122.6852 | -0.3891 | 122.7402 | 122.7493 | 122.7859 | -0.35706
2333.8281 | 122.8638 | -122.5479 | 0.31128 | -0.00022891 | -0.014956 | 0.013997 | 0.038373 | -0.012211 | -0.040432 | 0.0023157 | 7.627e-05 | 0.017353 | -0.036502 | -0.0023305 | -0.0093652 | 0.00068362 | 0.11444 | 0.07782 | 0.1236 | 0.091553 | 0.07782 | 0.064087 | -0.09613 | 0.091553 | 0.20142 | 0.082397 | 0.20599 | 0.19684 | -0.004578 | -0.073242 | 122.612 | 122.4518 | -0.23346 | 122.6257 | 122.6395 | 0.18768 | -0.19684 | 122.5433 | 122.4747 | -0.10528 | 122.6395 | 122.6303 | 0.15564 | -0.11444 | 122.6257 | 122.6624 | 122.6715 | -0.40741 | 122.7539 | 122.7448 | 122.7493 | -0.38452
2335.6094 | 122.8638 | -122.5388 | 0.29297 | -0.00022891 | -0.016024 | 0.017415 | 0.037946 | -0.0098608 | -0.04086 | -0.0032385 | -0.022812 | 0.017353 | -0.035006 | -0.0016897 | -0.014706 | -0.00038438 | 0.10529 | 0.10529 | 0.15564 | 0.082397 | 0.091553 | 0.036621 | -0.091553 | 0.073242 | 0.25635 | 0.086975 | 0.21057 | 0.19226 | -0.004578 | -0.068665 | 122.5754 | 122.4472 | -0.20142 | 122.644 | 122.6212 | 0.17395 | -0.18768 | 122.5342 | 122.4701 | -0.082398 | 122.612 | 122.6257 | 0.15564 | -0.10071 | 122.6303 | 122.644 | 122.6944 | -0.38452 | 122.7493 | 122.731 | 122.7951 | -0.36163
2337.3906 | 122.9782 | -122.5342 | 0.27466 | -0.00022891 | -0.011324 | 0.012501 | 0.037091 | -0.012424 | -0.033169 | -0.0006751 | 7.627e-05 | 0.022907 | -0.034579 | -0.0014761 | -0.011715 | -0.0014526 | 0.041199 | -0.082397 | -0.013733 | 0 | 0.15564 | 0.013733 | -0.12817 | 0 | 0.050354 | -0.054932 | 0.24719 | 0.22888 | -0.027466 | -0.09613 | 122.5479 | 122.406 | -0.11902 | 122.4518 | 122.5342 | 0.12817 | -0.23346 | 122.5067 | 122.4381 | -0.027466 | 122.5342 | 122.4792 | 0.041198 | -0.045776 | 122.6898 | 122.5754 | 122.5204 | -0.40283 | 122.7814 | 122.7631 | 122.5845 | -0.37079
2339.1094 | 122.8546 | -122.5479 | 0.27924 | 0.0074006 | -0.022219 | 0.014424 | 0.033887 | -0.013279 | -0.037869 | -0.0008887 | -0.0075532 | 0.017993 | -0.037143 | -0.00062151 | -0.011288 | 4.2822e-05 | 0.11902 | 0.091553 | 0.14191 | 0.086975 | 0.086975 | 0.050354 | -0.064087 | 0.10986 | 0.19226 | 0.064087 | 0.21057 | 0.20142 | 0 | -0.064087 | 122.5983 | 122.4838 | -0.19226 | 122.6395 | 122.6349 | 0.15106 | -0.16022 | 122.5479 | 122.4838 | -0.068665 | 122.6578 | 122.612 | 0.12817 | -0.07782 | 122.6349 | 122.6669 | 122.6898 | -0.34332 | 122.7585 | 122.7493 | 122.7402 | -0.34332
2340.8906 | 122.9233 | -122.5479 | 0.24719 | -0.00022891 | -0.013888 | 0.011433 | 0.038587 | -0.0098608 | -0.033596 | 0.0016749 | -0.0075532 | 0.02248 | -0.034793 | -0.0012625 | -0.010861 | -0.0025208 | 0.082397 | -0.027466 | 0.009155 | 0.022888 | 0.12817 | 0.009155 | -0.11444 | -0.022888 | 0.086975 | -0.086975 | 0.23804 | 0.23804 | -0.022888 | -0.10986 | 122.5571 | 122.4335 | -0.11902 | 122.5204 | 122.5708 | 0.13733 | -0.16479 | 122.525 | 122.438 | -0.009155 | 122.525 | 122.4609 | 0.022888 | -0.009155 | 122.6761 | 122.6303 | 122.5571 | -0.36163 | 122.7859 | 122.7859 | 122.6349 | -0.35706
2342.6719 | 122.9965 | -122.5113 | 0.24261 | -0.0078584 | -0.017092 | 0.012288 | 0.033246 | -0.0096472 | -0.037869 | 0.0003931 | -0.0075532 | 0.022266 | -0.036074 | -0.0038259 | -0.010861 | -0.00059818 | 0.064087 | 0 | 0.059509 | 0.032043 | 0.10986 | 0.036621 | -0.091553 | 0.068665 | 0.16937 | 0.041199 | 0.21973 | 0.19684 | 0.009155 | -0.068665 | 122.5479 | 122.4197 | -0.13275 | 122.5113 | 122.5433 | 0.1236 | -0.17853 | 122.5204 | 122.4426 | -0.022888 | 122.58 | 122.5525 | 0.10986 | -0.045777 | 122.6212 | 122.5754 | 122.5708 | -0.33417 | 122.731 | 122.7081 | 122.6807 | -0.31128
2344.4844 | 122.8638 | -122.5479 | 0.27924 | -0.0078584 | -0.017733 | 0.014851 | 0.035382 | -0.012852 | -0.039578 | -0.0034521 | 7.627e-05 | 0.018421 | -0.037997 | -0.0033987 | -0.011929 | 0.0011108 | 0.027466 | -0.027466 | 0.004578 | 0.009155 | 0.13733 | -0.013733 | -0.1236 | -0.054932 | 0.09613 | -0.050354 | 0.24719 | 0.23804 | -0.050354 | -0.1236 | 122.5342 | 122.4243 | -0.14191 | 122.5204 | 122.5571 | 0.13275 | -0.25177 | 122.4976 | 122.4243 | -0.032044 | 122.493 | 122.4976 | 0.073242 | -0.041199 | 122.6852 | 122.5754 | 122.5525 | -0.40283 | 122.7951 | 122.7859 | 122.644 | -0.40283
2346.2031 | 122.8958 | -122.5662 | 0.30212 | 0.0074006 | -0.017519 | 0.015065 | 0.040509 | -0.012211 | -0.04086 | -0.0015295 | 7.627e-05 | 0.016498 | -0.036288 | -0.0023305 | -0.014706 | -0.00059818 | 0.064087 | 0.041199 | 0.09613 | 0.068665 | 0.091553 | 0.050354 | -0.086975 | 0.054932 | 0.19226 | 0.073242 | 0.21057 | 0.20142 | 0.004578 | -0.059509 | 122.6166 | 122.4792 | -0.21057 | 122.6074 | 122.6349 | 0.15564 | -0.23804 | 122.5708 | 122.5067 | -0.091553 | 122.6212 | 122.6395 | 0.13275 | -0.10071 | 122.6578 | 122.6303 | 122.6624 | -0.3891 | 122.7768 | 122.7676 | 122.7585 | -0.36163
2348 | 122.8363 | -122.5662 | 0.27924 | 0.0074006 | -0.014315 | 0.013569 | 0.038587 | -0.00922 | -0.038296 | 0.0006067 | 0.015335 | 0.022052 | -0.036074 | -0.0027579 | -0.014065 | 0.0011108 | 0.086975 | 0.059509 | 0.091553 | 0.07782 | 0.11902 | 0.036621 | -0.10529 | 0.013733 | 0.14648 | 0 | 0.2243 | 0.20142 | -0.022888 | -0.09613 | 122.6028 | 122.4609 | -0.16022 | 122.6257 | 122.644 | 0.18311 | -0.19226 | 122.5433 | 122.4701 | -0.054932 | 122.58 | 122.5662 | 0.09613 | -0.07782 | 122.6852 | 122.6532 | 122.6578 | -0.38452 | 122.7905 | 122.7676 | 122.7127 | -0.37537
2349.7812 | 122.9507 | -122.5159 | 0.24719 | -0.00022891 | -0.013247 | 0.015065 | 0.035169 | -0.010502 | -0.033169 | -0.0025977 | 7.627e-05 | 0.02312 | -0.036929 | -0.0016897 | -0.011288 | -0.0035888 | 0.09613 | 0.009155 | 0.045776 | 0.045776 | 0.11902 | 0.018311 | -0.11902 | 0.045776 | 0.15564 | -0.018311 | 0.24261 | 0.21973 | -0.022888 | -0.10529 | 122.5342 | 122.3969 | -0.12817 | 122.525 | 122.5616 | 0.16479 | -0.15106 | 122.493 | 122.4106 | -0.004577 | 122.5616 | 122.4976 | 0.086975 | -0.027465 | 122.6349 | 122.612 | 122.5616 | -0.36621 | 122.7585 | 122.7356 | 122.6715 | -0.35248
2351.5781 | 122.9095 | -122.5388 | 0.27466 | -0.0078584 | -0.020083 | 0.01421 | 0.033887 | -0.011356 | -0.037228 | -0.0008887 | -0.0075532 | 0.018207 | -0.03757 | -0.0031851 | -0.011715 | 4.2822e-05 | 0.14191 | 0.082397 | 0.1236 | 0.091553 | 0.086975 | 0.054932 | -0.064087 | 0.09613 | 0.21057 | 0.082397 | 0.20599 | 0.16937 | 0.009155 | -0.073242 | 122.5937 | 122.4747 | -0.18768 | 122.6212 | 122.6303 | 0.15564 | -0.13275 | 122.5479 | 122.4655 | -0.068664 | 122.6349 | 122.6212 | 0.15564 | -0.10529 | 122.6257 | 122.6807 | 122.6624 | -0.33875 | 122.7448 | 122.7081 | 122.7493 | -0.3479
2353.3594 | 122.9782 | -122.5296 | 0.24719 | -0.015487 | -0.015169 | 0.013997 | 0.035169 | -0.012211 | -0.036374 | 0.0001795 | -0.0075532 | 0.020557 | -0.034152 | -0.0016897 | -0.011074 | -0.0023072 | 0.032043 | -0.073242 | -0.022888 | 0.004578 | 0.16479 | 0.032043 | -0.11902 | -0.027466 | 0.054932 | -0.059509 | 0.25635 | 0.23346 | -0.022888 | -0.09613 | 122.5616 | 122.4106 | -0.082397 | 122.4564 | 122.5342 | 0.1236 | -0.21515 | 122.5067 | 122.4335 | 0.009156 | 122.5021 | 122.4701 | 0.036621 | -0.013733 | 122.6944 | 122.5616 | 122.5067 | -0.36621 | 122.7859 | 122.7631 | 122.5845 | -0.34332
2355.1562 | 122.9599 | -122.5342 | 0.25177 | -0.00022891 | -0.013888 | 0.012715 | 0.033032 | -0.015201 | -0.033596 | 0.0014613 | 0.0077058 | 0.018421 | -0.034793 | -0.0019033 | -0.0095788 | -0.00059818 | 0.018311 | -0.086975 | -0.041199 | -0.013733 | 0.13275 | 0.018311 | -0.11902 | -0.027466 | 0.050354 | -0.073242 | 0.25177 | 0.23346 | -0.041199 | -0.09613 | 122.5525 | 122.4152 | -0.11902 | 122.4472 | 122.5204 | 0.10529 | -0.23346 | 122.493 | 122.4381 | 0 | 122.5067 | 122.4609 | 0.022888 | -0.018311 | 122.6669 | 122.5525 | 122.493 | -0.37079 | 122.7859 | 122.7676 | 122.5845 | -0.3479
2356.9531 | 122.8821 | -122.5754 | 0.27924 | 0.0074006 | -0.016024 | 0.017628 | 0.039655 | -0.012638 | -0.040646 | -0.0002477 | -0.015182 | 0.019702 | -0.036288 | -0.0021169 | -0.013638 | 0.00025642 | 0.027466 | -0.036621 | 0 | 0.013733 | 0.13733 | 0.013733 | -0.12817 | -0.032043 | 0.10071 | -0.041199 | 0.25177 | 0.23346 | -0.054932 | -0.10986 | 122.5891 | 122.4472 | -0.14191 | 122.5388 | 122.5891 | 0.14191 | -0.25177 | 122.5204 | 122.4655 | -0.027466 | 122.5433 | 122.5342 | 0.068664 | -0.045777 | 122.7127 | 122.6028 | 122.5754 | -0.40741 | 122.8271 | 122.8088 | 122.6761 | -0.3891
2358.7344 | 122.9828 | -122.5204 | 0.25177 | 0.0074006 | -0.015383 | 0.012928 | 0.035809 | -0.011997 | -0.037655 | 0.0010339 | 7.627e-05 | 0.018421 | -0.034152 | -0.0014761 | -0.01257 | -0.0014526 | 0.11902 | 0.041199 | 0.10529 | 0.09613 | 0.10529 | 0.045776 | -0.086975 | 0.082397 | 0.19226 | 0.068665 | 0.19684 | 0.19684 | -0.018311 | -0.064087 | 122.5662 | 122.4335 | -0.14648 | 122.5616 | 122.6166 | 0.1831 | -0.13275 | 122.5021 | 122.4564 | -0.054932 | 122.6028 | 122.5891 | 0.13275 | -0.054932 | 122.6257 | 122.6395 | 122.6257 | -0.33874 | 122.7173 | 122.7173 | 122.7127 | -0.31586
2360.4688 | 122.9187 | -122.5433 | 0.25635 | 0.0074006 | -0.013247 | 0.013783 | 0.036878 | -0.010502 | -0.032315 | 0.0021021 | 0.0077058 | 0.019916 | -0.035434 | -0.00019431 | -0.008938 | -0.00081178 | 0.045776 | -0.032043 | 0.004578 | 0.004578 | 0.1236 | 0.032043 | -0.10986 | -0.045776 | 0.073242 | -0.07782 | 0.23346 | 0.2243 | -0.036621 | -0.10071 | 122.5754 | 122.4335 | -0.13275 | 122.5113 | 122.5479 | 0.11444 | -0.21057 | 122.5067 | 122.4426 | -0.022889 | 122.4976 | 122.4655 | 0.022888 | -0.032044 | 122.6669 | 122.5891 | 122.5479 | -0.36621 | 122.7768 | 122.7676 | 122.6166 | -0.35706
2362.25 | 122.8867 | -122.5571 | 0.27924 | -0.00022891 | -0.018374 | 0.015492 | 0.037732 | -0.012211 | -0.042996 | -0.0013159 | 7.627e-05 | 0.01543 | -0.036074 | -0.0029715 | -0.015133 | -0.0010254 | 0.11444 | 0.1236 | 0.15564 | 0.10071 | 0.09613 | 0.045776 | -0.09613 | 0.091553 | 0.25177 | 0.10071 | 0.20599 | 0.1831 | 0 | -0.082397 | 122.6028 | 122.4609 | -0.18311 | 122.6807 | 122.6578 | 0.19684 | -0.16479 | 122.5571 | 122.4747 | -0.073242 | 122.6486 | 122.6578 | 0.18311 | -0.096131 | 122.6532 | 122.6715 | 122.7127 | -0.37537 | 122.7631 | 122.7402 | 122.8088 | -0.36163
2363.9844 | 122.8638 | -122.5342 | 0.27466 | 0.0074006 | -0.014315 | 0.015919 | 0.038587 | -0.011143 | -0.039578 | -0.0015295 | -0.0075532 | 0.01543 | -0.037143 | -0.0040395 | -0.014706 | -0.001239 | 0.10986 | 0.10529 | 0.14648 | 0.10986 | 0.09613 | 0.045776 | -0.068665 | 0.073242 | 0.24719 | 0.10529 | 0.20142 | 0.20599 | 0.009155 | -0.073242 | 122.58 | 122.4655 | -0.17853 | 122.6395 | 122.644 | 0.17853 | -0.1648 | 122.5433 | 122.4609 | -0.073242 | 122.6074 | 122.6395 | 0.17853 | -0.068664 | 122.6303 | 122.644 | 122.6807 | -0.34332 | 122.7356 | 122.7402 | 122.7814 | -0.3479
2365.7656 | 122.9507 | -122.58 | 0.25177 | -0.015487 | -0.016024 | 0.011647 | 0.033887 | -0.013279 | -0.034237 | -0.0030249 | -0.0075532 | 0.020771 | -0.036074 | -0.00062151 | -0.011288 | -0.0038024 | 0.032043 | -0.07782 | -0.036621 | 0.013733 | 0.15106 | 0.027466 | -0.11902 | -0.041199 | 0.050354 | -0.07782 | 0.23346 | 0.24261 | -0.050354 | -0.09613 | 122.6074 | 122.4609 | -0.10071 | 122.5021 | 122.5937 | 0.13275 | -0.21973 | 122.5296 | 122.4838 | -0.018311 | 122.5388 | 122.5021 | 0.01831 | -0.009155 | 122.731 | 122.612 | 122.5433 | -0.37079 | 122.8134 | 122.8226 | 122.6303 | -0.3479
2367.5625 | 122.9233 | -122.5388 | 0.25177 | 0.01503 | -0.01581 | 0.013142 | 0.032605 | -0.011997 | -0.034237 | 0.0018885 | -0.015182 | 0.022266 | -0.034579 | -0.0023305 | -0.010647 | -0.00038438 | 0.027466 | -0.073242 | -0.027466 | 0.022888 | 0.13733 | 0.009155 | -0.11444 | -0.064087 | 0.041199 | -0.082397 | 0.24719 | 0.23346 | -0.050354 | -0.10986 | 122.5479 | 122.4243 | -0.11444 | 122.4655 | 122.5616 | 0.13733 | -0.2243 | 122.4884 | 122.4289 | -0.004578 | 122.4747 | 122.4564 | 0.027466 | -0.018311 | 122.6761 | 122.5662 | 122.5113 | -0.36621 | 122.7859 | 122.7722 | 122.58 | -0.36163
2369.3438 | 122.8546 | -122.5708 | 0.27466 | -0.0078584 | -0.015383 | 0.015706 | 0.037305 | -0.010288 | -0.039792 | -0.0023839 | 7.627e-05 | 0.019916 | -0.034152 | -0.0048941 | -0.015774 | 0.0013244 | 0.032043 | -0.004578 | 0.018311 | 0.036621 | 0.12817 | 0.018311 | -0.1236 | -0.032043 | 0.11902 | -0.022888 | 0.25177 | 0.23804 | -0.027466 | -0.11902 | 122.5891 | 122.4472 | -0.14648 | 122.5662 | 122.6074 | 0.16022 | -0.24262 | 122.5433 | 122.4518 | -0.022888 | 122.5388 | 122.5479 | 0.096131 | -0.036621 | 122.699 | 122.6028 | 122.5891 | -0.39825 | 122.8226 | 122.8088 | 122.6898 | -0.39368
2371.0625 | 122.9416 | -122.5479 | 0.25177 | -0.00022891 | -0.014101 | 0.014851 | 0.037305 | -0.0096472 | -0.034237 | -0.0002477 | 7.627e-05 | 0.022266 | -0.034579 | 0.00023289 | -0.013424 | -0.0042298 | 0.054932 | -0.041199 | 0 | 0.018311 | 0.12817 | 0.013733 | -0.13275 | -0.045776 | 0.064087 | -0.082397 | 0.24261 | 0.21057 | -0.050354 | -0.10986 | 122.5616 | 122.4152 | -0.1236 | 122.5067 | 122.5662 | 0.15106 | -0.19684 | 122.4976 | 122.438 | -0.009155 | 122.5021 | 122.4655 | 0.027466 | -0.041199 | 122.6761 | 122.6028 | 122.5479 | -0.38452 | 122.7905 | 122.7585 | 122.612 | -0.36163
2372.8281 | 122.905 | -122.5433 | 0.25635 | -0.0078584 | -0.02051 | 0.017842 | 0.035596 | -0.013279 | -0.043423 | -0.0025977 | 0.0077058 | 0.016498 | -0.036074 | -0.0025443 | -0.01321 | 0.00025642 | 0.11444 | 0.11902 | 0.13733 | 0.10529 | 0.10986 | 0.045776 | -0.086975 | 0.09613 | 0.24719 | 0.10529 | 0.21057 | 0.20142 | -0.004578 | -0.059509 | 122.5891 | 122.4564 | -0.14649 | 122.6624 | 122.6486 | 0.19226 | -0.14191 | 122.5388 | 122.4838 | -0.045777 | 122.6395 | 122.6486 | 0.16479 | -0.054932 | 122.6532 | 122.6578 | 122.6807 | -0.34332 | 122.7539 | 122.7448 | 122.7905 | -0.31586
2374.625 | 122.9782 | -122.5433 | 0.24261 | -0.0078584 | -0.020296 | 0.011219 | 0.036664 | -0.0090062 | -0.035092 | -0.0006751 | -0.0075532 | 0.02013 | -0.034793 | -0.0021169 | -0.011288 | -0.0016662 | 0.032043 | -0.045776 | 0 | 0.027466 | 0.1236 | 0.018311 | -0.12817 | -0.032043 | 0.11444 | -0.045776 | 0.22888 | 0.22888 | -0.022888 | -0.10529 | 122.5616 | 122.4152 | -0.11902 | 122.4976 | 122.5708 | 0.15564 | -0.21057 | 122.5204 | 122.438 | -0.013733 | 122.5113 | 122.4976 | 0.05951 | -0.013733 | 122.6669 | 122.5754 | 122.5433 | -0.37079 | 122.7722 | 122.7722 | 122.6578 | -0.3479
2376.4062 | 122.8409 | -122.5754 | 0.29297 | -0.00022891 | -0.021792 | 0.013356 | 0.034955 | -0.012638 | -0.040005 | -0.0017431 | 7.627e-05 | 0.01778 | -0.035647 | -0.0021169 | -0.013424 | -0.00081178 | 0.022888 | -0.009155 | 0.022888 | 0.027466 | 0.12817 | 0.018311 | -0.11444 | -0.027466 | 0.11444 | -0.041199 | 0.23346 | 0.23804 | -0.050354 | -0.10529 | 122.5937 | 122.4609 | -0.16479 | 122.5662 | 122.6028 | 0.14191 | -0.27008 | 122.525 | 122.4701 | -0.05951 | 122.5479 | 122.5342 | 0.064087 | -0.054932 | 122.7036 | 122.5983 | 122.5983 | -0.40741 | 122.8088 | 122.8134 | 122.6898 | -0.39825
2378.125 | 122.9187 | -122.5525 | 0.26093 | -0.0078584 | -0.019015 | 0.012715 | 0.037518 | -0.011783 | -0.038723 | -0.0013159 | 7.627e-05 | 0.02013 | -0.034152 | -0.0033987 | -0.014492 | -0.0023072 | 0.027466 | -0.059509 | -0.004578 | 0 | 0.14191 | 0 | -0.11902 | -0.041199 | 0.091553 | -0.059509 | 0.24261 | 0.23804 | -0.045776 | -0.10529 | 122.5525 | 122.4335 | -0.11902 | 122.493 | 122.5525 | 0.11902 | -0.23346 | 122.5067 | 122.4472 | -0.01831 | 122.5113 | 122.493 | 0.045777 | -0.022888 | 122.6944 | 122.58 | 122.5479 | -0.37994 | 122.7951 | 122.7905 | 122.644 | -0.36621
2379.9062 | 122.9691 | -122.5479 | 0.23346 | -0.00022891 | -0.010042 | 0.013997 | 0.033887 | -0.01392 | -0.034878 | 0.0010339 | -0.0075532 | 0.021839 | -0.034365 | -0.0025443 | -0.010647 | -0.0020934 | 0.054932 | -0.07782 | -0.027466 | 0.013733 | 0.14191 | 0.009155 | -0.13733 | -0.018311 | 0.041199 | -0.073242 | 0.24261 | 0.23804 | -0.041199 | -0.11444 | 122.5571 | 122.4106 | -0.091552 | 122.4701 | 122.5616 | 0.15106 | -0.17853 | 122.5067 | 122.4335 | 0.009156 | 122.5296 | 122.4747 | 0.041199 | 0.004578 | 122.6898 | 122.6028 | 122.5204 | -0.37079 | 122.7905 | 122.7859 | 122.5891 | -0.3479
2381.6875 | 122.8409 | -122.5708 | 0.29755 | 0.01503 | -0.017733 | 0.014637 | 0.037732 | -0.011997 | -0.041928 | -3.4096e-05 | 7.627e-05 | 0.016071 | -0.035861 | -0.0044669 | -0.01257 | -0.0014526 | 0.10986 | 0.091553 | 0.13275 | 0.082397 | 0.10071 | 0.041199 | -0.086975 | 0.064087 | 0.23804 | 0.07782 | 0.21515 | 0.20599 | -0.004578 | -0.07782 | 122.612 | 122.4838 | -0.19684 | 122.6624 | 122.6532 | 0.16937 | -0.18768 | 122.5662 | 122.493 | -0.082397 | 122.6349 | 122.6486 | 0.15564 | -0.091552 | 122.6715 | 122.6807 | 122.7036 | -0.38452 | 122.7859 | 122.7768 | 122.8088 | -0.37537
2383.4688 | 122.9782 | -122.525 | 0.25635 | -0.0078584 | -0.014101 | 0.01891 | 0.031537 | -0.011783 | -0.036374 | 0.0001795 | -0.0075532 | 0.019916 | -0.036502 | -0.0021169 | -0.011715 | -0.002948 | 0.13733 | 0.064087 | 0.10986 | 0.09613 | 0.10529 | 0.07782 | -0.09613 | 0.086975 | 0.19684 | 0.068665 | 0.20142 | 0.21057 | 0.004578 | -0.041199 | 122.6028 | 122.4289 | -0.15106 | 122.5891 | 122.6212 | 0.19226 | -0.11902 | 122.5296 | 122.4838 | -0.054932 | 122.612 | 122.5937 | 0.10986 | -0.045777 | 122.6303 | 122.6624 | 122.6349 | -0.35248 | 122.7264 | 122.7356 | 122.7219 | -0.29755
2385.1875 | 122.9004 | -122.5616 | 0.2655 | -0.00022891 | -0.015169 | 0.01656 | 0.03645 | -0.010502 | -0.04321 | -0.0021703 | -0.022812 | 0.014789 | -0.034579 | -0.0031851 | -0.01556 | -0.00081178 | 0.082397 | 0.018311 | 0.091553 | 0.064087 | 0.11444 | 0.032043 | -0.09613 | 0.041199 | 0.17395 | 0.054932 | 0.21057 | 0.20599 | -0.004578 | -0.086975 | 122.5937 | 122.4655 | -0.15106 | 122.58 | 122.6257 | 0.16022 | -0.18311 | 122.5571 | 122.4747 | -0.054932 | 122.6028 | 122.6166 | 0.14191 | -0.059509 | 122.6761 | 122.644 | 122.6532 | -0.36163 | 122.7722 | 122.7676 | 122.7356 | -0.35248
2386.9688 | 122.9965 | -122.5479 | 0.24719 | -0.0078584 | -0.018374 | 0.013356 | 0.038587 | -0.01157 | -0.034024 | -0.0008887 | -0.015182 | 0.021625 | -0.033084 | -0.0027579 | -0.011715 | -0.0031616 | 0.059509 | -0.036621 | 0.013733 | 0.032043 | 0.11902 | 0.027466 | -0.12817 | 0.004578 | 0.13733 | -0.027466 | 0.24261 | 0.21973 | -0.027466 | -0.10986 | 122.5754 | 122.4197 | -0.12817 | 122.5113 | 122.58 | 0.16022 | -0.18768 | 122.5204 | 122.438 | -0.004577 | 122.5525 | 122.5204 | 0.082397 | -0.027465 | 122.6669 | 122.6074 | 122.5616 | -0.37537 | 122.7905 | 122.7676 | 122.6852 | -0.35706
2388.75 | 122.9324 | -122.5388 | 0.24261 | -0.0078584 | -0.015169 | 0.013142 | 0.032819 | -0.012211 | -0.03381 | 0.0001795 | -0.0075532 | 0.021411 | -0.034365 | -0.0051077 | -0.0080834 | -0.0020934 | 0.041199 | -0.059509 | -0.013733 | 0.022888 | 0.14648 | 0 | -0.11902 | -0.050354 | 0.050354 | -0.09613 | 0.25177 | 0.25177 | -0.050354 | -0.11444 | 122.5388 | 122.4197 | -0.096131 | 122.4792 | 122.5616 | 0.14191 | -0.20142 | 122.4884 | 122.4243 | 0.009155 | 122.4884 | 122.4426 | 0.018311 | 0.009155 | 122.6852 | 122.58 | 122.525 | -0.36163 | 122.7905 | 122.7905 | 122.5891 | -0.35706
2390.5625 | 122.9095 | -122.5616 | 0.27924 | -0.00022891 | -0.015597 | 0.015706 | 0.034314 | -0.011997 | -0.04086 | 0.0018885 | -0.0075532 | 0.016712 | -0.035647 | -0.0040395 | -0.01257 | -0.0010254 | 0.15106 | 0.068665 | 0.13275 | 0.086975 | 0.086975 | 0.064087 | -0.07782 | 0.082397 | 0.19684 | 0.068665 | 0.19684 | 0.18768 | -0.004578 | -0.050354 | 122.6257 | 122.4838 | -0.19226 | 122.6303 | 122.6486 | 0.16479 | -0.12817 | 122.5571 | 122.5113 | -0.082398 | 122.644 | 122.6303 | 0.11902 | -0.091553 | 122.6486 | 122.7127 | 122.6944 | -0.35706 | 122.7585 | 122.7493 | 122.7585 | -0.32959
2392.2812 | 122.8729 | -122.58 | 0.27466 | -0.00022891 | -0.018801 | 0.013997 | 0.034101 | -0.016056 | -0.037655 | -3.4096e-05 | -0.0075532 | 0.01778 | -0.037997 | -0.0027579 | -0.012997 | -0.0010254 | 0.12817 | 0.086975 | 0.13733 | 0.07782 | 0.091553 | 0.059509 | -0.086975 | 0.10071 | 0.19226 | 0.059509 | 0.20599 | 0.18768 | 0.004578 | -0.059509 | 122.6395 | 122.493 | -0.18311 | 122.6669 | 122.6578 | 0.16479 | -0.14648 | 122.5845 | 122.5204 | -0.068664 | 122.6807 | 122.6395 | 0.11902 | -0.086975 | 122.6715 | 122.7081 | 122.7173 | -0.36163 | 122.7859 | 122.7676 | 122.7722 | -0.33417
2394.0625 | 122.9324 | -122.5296 | 0.24719 | -0.0078584 | -0.010256 | 0.015278 | 0.036878 | -0.012211 | -0.032315 | -0.0002477 | -0.0075532 | 0.019489 | -0.03287 | 1.9292e-05 | -0.0095788 | -0.0035888 | 0.1236 | 0 | 0.050354 | 0.045776 | 0.12817 | 0.032043 | -0.1236 | 0.009155 | 0.11902 | -0.050354 | 0.2243 | 0.21515 | -0.013733 | -0.086975 | 122.5616 | 122.406 | -0.11902 | 122.5296 | 122.5754 | 0.16937 | -0.1236 | 122.5159 | 122.4426 | -0.022888 | 122.5388 | 122.4792 | 0.036621 | -0.032043 | 122.6578 | 122.6532 | 122.58 | -0.37079 | 122.7539 | 122.7448 | 122.6486 | -0.33417
2395.8438 | 122.9507 | -122.5342 | 0.25635 | -0.0078584 | -0.015383 | 0.01421 | 0.037732 | -0.010715 | -0.038083 | 0.0010339 | 7.627e-05 | 0.016071 | -0.032016 | -0.0036123 | -0.011501 | -0.00038438 | 0.12817 | 0.073242 | 0.1236 | 0.10071 | 0.07782 | 0.054932 | -0.086975 | 0.10529 | 0.18768 | 0.082397 | 0.20599 | 0.17853 | 0.004578 | -0.059509 | 122.5891 | 122.4472 | -0.17853 | 122.6074 | 122.6349 | 0.18768 | -0.12817 | 122.5388 | 122.4747 | -0.050354 | 122.6395 | 122.6166 | 0.14191 | -0.07782 | 122.612 | 122.6624 | 122.6578 | -0.34332 | 122.7402 | 122.7127 | 122.7219 | -0.31586
2397.6406 | 122.937 | -122.5433 | 0.2655 | -0.0078584 | -0.01346 | 0.013997 | 0.034314 | -0.0090062 | -0.032315 | 0.0016749 | -0.0075532 | 0.02248 | -0.03757 | -0.0012625 | -0.0095788 | -0.0010254 | 0.068665 | 0.009155 | 0.018311 | 0.041199 | 0.13275 | 0.022888 | -0.1236 | -0.018311 | 0.086975 | -0.073242 | 0.25177 | 0.2243 | -0.050354 | -0.091553 | 122.5662 | 122.4197 | -0.13275 | 122.5525 | 122.5845 | 0.16479 | -0.19684 | 122.493 | 122.4518 | -0.013733 | 122.525 | 122.4701 | 0.018311 | -0.041199 | 122.6761 | 122.612 | 122.5616 | -0.3891 | 122.7951 | 122.7676 | 122.6303 | -0.35706
2399.375 | 122.9324 | -122.5388 | 0.23804 | -0.0078584 | -0.01282 | 0.012501 | 0.032178 | -0.010288 | -0.035733 | -0.0006751 | 7.627e-05 | 0.020771 | -0.033511 | -0.0029715 | -0.0097924 | -0.0010254 | 0.036621 | -0.082397 | -0.018311 | 0.013733 | 0.12817 | 0.009155 | -0.10071 | -0.050354 | 0.050354 | -0.091553 | 0.24261 | 0.2243 | -0.032043 | -0.10071 | 122.5479 | 122.438 | -0.10986 | 122.4564 | 122.5525 | 0.11444 | -0.20142 | 122.5067 | 122.438 | 0.004578 | 122.4884 | 122.4472 | 0.009155 | -0.013733 | 122.6669 | 122.5754 | 122.5204 | -0.33875 | 122.7814 | 122.7631 | 122.5891 | -0.33875
2401.1719 | 122.9691 | -122.5616 | 0.26093 | -0.00022891 | -0.01346 | 0.014851 | 0.036023 | -0.011356 | -0.035733 | 0.0008203 | 7.627e-05 | 0.022907 | -0.033084 | 0.00023289 | -0.013424 | 0.00047002 | 0.027466 | -0.07782 | -0.013733 | 0.004578 | 0.15106 | 0.009155 | -0.12817 | -0.022888 | 0.036621 | -0.068665 | 0.23346 | 0.22888 | -0.041199 | -0.10529 | 122.5708 | 122.4335 | -0.10986 | 122.4838 | 122.5662 | 0.13275 | -0.23346 | 122.5204 | 122.4564 | -0.027466 | 122.5388 | 122.493 | 0.036621 | -0.032043 | 122.7127 | 122.5891 | 122.5479 | -0.3891 | 122.7951 | 122.7905 | 122.5983 | -0.36621
2402.9062 | 122.9141 | -122.5296 | 0.2655 | 0.0074006 | -0.014101 | 0.013569 | 0.039441 | -0.0096472 | -0.038296 | -0.0011023 | -0.0075532 | 0.018848 | -0.032656 | -0.0012625 | -0.016201 | -0.00017078 | 0.018311 | -0.050354 | -0.004578 | 0.018311 | 0.15106 | 0.004578 | -0.1236 | -0.041199 | 0.086975 | -0.064087 | 0.25177 | 0.2243 | -0.050354 | -0.10071 | 122.5342 | 122.406 | -0.11444 | 122.4792 | 122.5479 | 0.14191 | -0.24719 | 122.4792 | 122.4289 | -0.013733 | 122.4884 | 122.4655 | 0.036621 | -0.041199 | 122.6807 | 122.5479 | 122.525 | -0.3891 | 122.7814 | 122.7539 | 122.6166 | -0.36621
2404.6875 | 122.8958 | -122.5983 | 0.28839 | -0.00022891 | -0.019015 | 0.015065 | 0.035809 | -0.010929 | -0.04385 | -0.0023839 | -0.0075532 | 0.016925 | -0.036502 | -0.0027579 | -0.015347 | -0.00081178 | 0.041199 | 0.022888 | 0.07782 | 0.045776 | 0.12817 | 0.041199 | -0.091553 | 0.004578 | 0.16022 | 0.050354 | 0.20142 | 0.21057 | -0.013733 | -0.086975 | 122.6395 | 122.5067 | -0.16022 | 122.6212 | 122.644 | 0.13733 | -0.24719 | 122.5845 | 122.5113 | -0.086975 | 122.6028 | 122.6486 | 0.13733 | -0.07782 | 122.7264 | 122.6395 | 122.6761 | -0.37994 | 122.7997 | 122.8088 | 122.7585 | -0.37537
2406.4688 | 122.8546 | -122.5754 | 0.27466 | -0.0078584 | -0.017733 | 0.01656 | 0.037305 | -0.012852 | -0.040646 | -0.0004613 | 7.627e-05 | 0.017566 | -0.03522 | -0.0051077 | -0.013424 | -0.00038438 | 0.12817 | 0.07782 | 0.11444 | 0.091553 | 0.10071 | 0.050354 | -0.082397 | 0.041199 | 0.21973 | 0.041199 | 0.21057 | 0.21515 | 0.004578 | -0.091553 | 122.6257 | 122.493 | -0.17395 | 122.6532 | 122.6669 | 0.17395 | -0.14648 | 122.58 | 122.4838 | -0.064087 | 122.6166 | 122.6166 | 0.13275 | -0.059509 | 122.6761 | 122.7036 | 122.6898 | -0.35706 | 122.7859 | 122.7905 | 122.7951 | -0.36621
2408.1875 | 122.8363 | -122.58 | 0.28381 | -0.00022891 | -0.014315 | 0.015706 | 0.036878 | -0.010074 | -0.041073 | -0.0019567 | 7.627e-05 | 0.018848 | -0.033511 | -0.0033987 | -0.012783 | -0.001239 | 0.11902 | 0.059509 | 0.10986 | 0.091553 | 0.10071 | 0.027466 | -0.09613 | 0.018311 | 0.1831 | 0.027466 | 0.2243 | 0.21973 | -0.009155 | -0.086975 | 122.6074 | 122.4838 | -0.1831 | 122.6395 | 122.6715 | 0.18768 | -0.16479 | 122.5708 | 122.493 | -0.059509 | 122.5983 | 122.6074 | 0.11444 | -0.064086 | 122.6807 | 122.699 | 122.6898 | -0.37994 | 122.8043 | 122.7997 | 122.7631 | -0.37079
2409.9688 | 122.8409 | -122.58 | 0.27008 | -0.00022891 | -0.017946 | 0.013997 | 0.036023 | -0.011997 | -0.040432 | -0.0036657 | -0.015182 | 0.017993 | -0.034365 | -0.0048941 | -0.013851 | -0.0018798 | 0.13733 | 0.091553 | 0.13275 | 0.086975 | 0.10071 | 0.059509 | -0.086975 | 0.068665 | 0.22888 | 0.064087 | 0.21515 | 0.1831 | -0.013733 | -0.073242 | 122.6395 | 122.493 | -0.16937 | 122.6715 | 122.6669 | 0.17395 | -0.13275 | 122.5662 | 122.5067 | -0.054932 | 122.6486 | 122.644 | 0.13733 | -0.086976 | 122.6807 | 122.7173 | 122.7127 | -0.35706 | 122.7951 | 122.7631 | 122.8088 | -0.34332
2411.7656 | 122.8317 | -122.58 | 0.27924 | -0.00022891 | -0.014956 | 0.014424 | 0.039655 | -0.012211 | -0.039578 | -0.0019567 | 7.627e-05 | 0.017566 | -0.034579 | -0.0031851 | -0.015347 | -0.0027344 | 0.13733 | 0.091553 | 0.14648 | 0.091553 | 0.07782 | 0.036621 | -0.10529 | 0.086975 | 0.22888 | 0.091553 | 0.21515 | 0.19684 | 0 | -0.068665 | 122.6166 | 122.4747 | -0.20142 | 122.6715 | 122.6715 | 0.19684 | -0.14191 | 122.58 | 122.5113 | -0.064087 | 122.6669 | 122.6715 | 0.16022 | -0.082398 | 122.6578 | 122.7173 | 122.7264 | -0.38452 | 122.7951 | 122.7768 | 122.8088 | -0.3479
2413.4844 | 122.8592 | -122.5937 | 0.27008 | 0.01503 | -0.019442 | 0.015919 | 0.034741 | -0.012638 | -0.038296 | -0.0004613 | 0.0077058 | 0.017353 | -0.03522 | -0.0021169 | -0.01321 | -0.0031616 | 0.13275 | 0.07782 | 0.10529 | 0.082397 | 0.086975 | 0.059509 | -0.068665 | 0.10071 | 0.17853 | 0.050354 | 0.21057 | 0.20599 | -0.032043 | -0.073242 | 122.6532 | 122.525 | -0.18311 | 122.6715 | 122.6761 | 0.15106 | -0.13733 | 122.5616 | 122.5204 | -0.05951 | 122.6944 | 122.644 | 0.1236 | -0.064087 | 122.6807 | 122.7264 | 122.699 | -0.33875 | 122.8043 | 122.7997 | 122.7722 | -0.34332
2415.2812 | 122.937 | -122.5388 | 0.2655 | -0.00022891 | -0.014742 | 0.013783 | 0.036023 | -0.015201 | -0.036374 | -0.0023839 | -0.015182 | 0.021411 | -0.033511 | -0.00083531 | -0.012142 | -0.00038438 | 0.045776 | -0.045776 | -0.013733 | -0.004578 | 0.14648 | 0 | -0.14191 | -0.027466 | 0.091553 | -0.059509 | 0.24261 | 0.23804 | -0.050354 | -0.11902 | 122.5388 | 122.3969 | -0.11902 | 122.493 | 122.5342 | 0.13733 | -0.21973 | 122.4884 | 122.4197 | -0.022888 | 122.5113 | 122.4792 | 0.05951 | -0.027466 | 122.6852 | 122.5845 | 122.525 | -0.40741 | 122.7814 | 122.7768 | 122.6303 | -0.38452
2417.0156 | 122.9874 | -122.5479 | 0.24261 | -0.0078584 | -0.016451 | 0.014424 | 0.033887 | -0.01157 | -0.034878 | -0.0002477 | -0.0075532 | 0.020771 | -0.033938 | 0.00023289 | -0.01022 | 0.00025642 | 0.050354 | -0.050354 | 0 | 0.013733 | 0.15564 | 0.018311 | -0.13275 | 0.004578 | 0.064087 | -0.050354 | 0.21973 | 0.21515 | -0.036621 | -0.10529 | 122.5662 | 122.4152 | -0.086975 | 122.4976 | 122.5616 | 0.14648 | -0.19226 | 122.5113 | 122.4426 | -0.022888 | 122.5525 | 122.4976 | 0.054932 | -0.027466 | 122.7036 | 122.5983 | 122.5479 | -0.37537 | 122.7676 | 122.7631 | 122.612 | -0.3479
2418.7969 | 122.8409 | -122.5891 | 0.28381 | -0.0078584 | -0.017306 | 0.013142 | 0.037091 | -0.01157 | -0.039364 | -0.0002477 | -0.015182 | 0.019062 | -0.033297 | -0.0031851 | -0.01321 | -0.00038438 | 0.045776 | 0.022888 | 0.059509 | 0.022888 | 0.10529 | 0.027466 | -0.10529 | -0.027466 | 0.11444 | -0.032043 | 0.23804 | 0.22888 | -0.045776 | -0.091553 | 122.6166 | 122.4838 | -0.17853 | 122.612 | 122.612 | 0.12817 | -0.23804 | 122.5433 | 122.4976 | -0.045776 | 122.5616 | 122.5571 | 0.05951 | -0.054931 | 122.6944 | 122.6349 | 122.6486 | -0.3891 | 122.8271 | 122.818 | 122.7036 | -0.37537
2420.6094 | 122.8821 | -122.5937 | 0.28381 | -0.015487 | -0.014956 | 0.013142 | 0.039441 | -0.010502 | -0.038296 | -0.0025977 | 7.627e-05 | 0.019062 | -0.033725 | -0.0027579 | -0.011288 | -0.00038438 | 0.018311 | -0.013733 | 0.009155 | 0.013733 | 0.13275 | -0.009155 | -0.12817 | -0.022888 | 0.091553 | -0.045776 | 0.21515 | 0.2243 | -0.032043 | -0.11444 | 122.5845 | 122.4655 | -0.15106 | 122.58 | 122.6074 | 0.14191 | -0.2655 | 122.5616 | 122.4792 | -0.068664 | 122.5708 | 122.5479 | 0.068665 | -0.059509 | 122.7264 | 122.612 | 122.6028 | -0.41199 | 122.8088 | 122.818 | 122.6852 | -0.39825
2422.3281 | 122.8912 | -122.58 | 0.27008 | -0.0078584 | -0.018587 | 0.015919 | 0.038373 | -0.0096472 | -0.042141 | -0.0021703 | -0.015182 | 0.015216 | -0.03287 | -0.0027579 | -0.014065 | -0.0010254 | 0.12817 | 0.15106 | 0.16022 | 0.09613 | 0.086975 | 0.022888 | -0.10529 | 0.086975 | 0.26093 | 0.09613 | 0.19226 | 0.18768 | 0 | -0.068665 | 122.6028 | 122.4747 | -0.18311 | 122.731 | 122.6761 | 0.20142 | -0.14191 | 122.58 | 122.5113 | -0.07782 | 122.6669 | 122.6761 | 0.16479 | -0.082398 | 122.6669 | 122.7081 | 122.7402 | -0.37537 | 122.7722 | 122.7676 | 122.8409 | -0.33875
2424.125 | 122.8455 | -122.5937 | 0.27924 | -0.0078584 | -0.016665 | 0.016346 | 0.037518 | -0.011997 | -0.040432 | -0.0011023 | -0.0075532 | 0.017566 | -0.034365 | -0.0042531 | -0.01257 | 0.00025642 | 0.091553 | 0.064087 | 0.10071 | 0.041199 | 0.091553 | 0.045776 | -0.082397 | 0.050354 | 0.16022 | 0.036621 | 0.18768 | 0.17853 | -0.009155 | -0.07782 | 122.6395 | 122.5113 | -0.18768 | 122.6578 | 122.6349 | 0.1236 | -0.18768 | 122.5845 | 122.5159 | -0.091553 | 122.644 | 122.6303 | 0.11444 | -0.10071 | 122.6852 | 122.6852 | 122.6944 | -0.36163 | 122.7814 | 122.7722 | 122.7539 | -0.35706
2425.9219 | 122.8592 | -122.5983 | 0.27466 | -0.00022891 | -0.022646 | 0.01656 | 0.035169 | -0.010288 | -0.039578 | -0.0017431 | -0.015182 | 0.016071 | -0.035434 | -0.0068167 | -0.01257 | -0.00038438 | 0.07782 | 0.054932 | 0.082397 | 0.050354 | 0.10529 | 0.032043 | -0.082397 | 0.050354 | 0.15564 | 0.036621 | 0.20599 | 0.20599 | 0 | -0.10071 | 122.6303 | 122.5159 | -0.16937 | 122.6532 | 122.6486 | 0.13275 | -0.19684 | 122.5983 | 122.4976 | -0.068664 | 122.6486 | 122.6349 | 0.13733 | -0.068664 | 122.7036 | 122.6761 | 122.6807 | -0.35706 | 122.8043 | 122.8043 | 122.7539 | -0.37537
2427.7031 | 122.8546 | -122.5845 | 0.27924 | -0.015487 | -0.016024 | 0.015492 | 0.037946 | -0.010715 | -0.037655 | -0.0019567 | 7.627e-05 | 0.018634 | -0.033725 | -0.0036123 | -0.01257 | -0.0014526 | 0.064087 | 0 | 0.045776 | 0.041199 | 0.1236 | 0.004578 | -0.1236 | -0.013733 | 0.09613 | -0.041199 | 0.22888 | 0.2243 | -0.027466 | -0.10071 | 122.5891 | 122.4609 | -0.15564 | 122.5845 | 122.6257 | 0.16479 | -0.21515 | 122.5571 | 122.4838 | -0.050354 | 122.5708 | 122.5433 | 0.059509 | -0.054932 | 122.7081 | 122.6486 | 122.6303 | -0.40283 | 122.8134 | 122.8088 | 122.6807 | -0.37994
2429.4219 | 122.8363 | -122.5891 | 0.29297 | -0.0078584 | -0.015383 | 0.015919 | 0.037091 | -0.012211 | -0.039151 | -0.0004613 | -0.0075532 | 0.015857 | -0.033511 | -0.0031851 | -0.013424 | -0.0035888 | 0.13275 | 0.09613 | 0.1236 | 0.10986 | 0.09613 | 0.032043 | -0.10529 | 0.068665 | 0.21057 | 0.050354 | 0.21057 | 0.19226 | 0.004578 | -0.086975 | 122.6212 | 122.4838 | -0.19684 | 122.6852 | 122.699 | 0.21515 | -0.16022 | 122.5937 | 122.5021 | -0.082398 | 122.6578 | 122.6395 | 0.13733 | -0.10071 | 122.6852 | 122.7219 | 122.7127 | -0.39825 | 122.7997 | 122.7814 | 122.7997 | -0.37994
2431.2188 | 122.9095 | -122.5754 | 0.27466 | -0.00022891 | -0.01816 | 0.015492 | 0.035382 | -0.013065 | -0.04086 | -0.0006751 | -0.0075532 | 0.016712 | -0.037997 | -0.0021169 | -0.015133 | -0.0023072 | 0.16022 | 0.12817 | 0.13733 | 0.10529 | 0.086975 | 0.036621 | -0.082397 | 0.10071 | 0.23804 | 0.086975 | 0.1831 | 0.16937 | 0 | -0.073242 | 122.612 | 122.493 | -0.18768 | 122.7036 | 122.6807 | 0.18768 | -0.11444 | 122.5754 | 122.5021 | -0.091553 | 122.6761 | 122.6624 | 0.16022 | -0.10529 | 122.6624 | 122.7356 | 122.7127 | -0.35706 | 122.7585 | 122.7448 | 122.8134 | -0.3479
2433.0156 | 122.905 | -122.58 | 0.25177 | -0.00022891 | -0.018587 | 0.013356 | 0.031964 | -0.013065 | -0.034237 | 0.0001795 | -0.0075532 | 0.018421 | -0.036715 | -0.0021169 | -0.010647 | -0.0020934 | 0.16937 | 0.073242 | 0.11902 | 0.091553 | 0.10071 | 0.059509 | -0.091553 | 0.10986 | 0.19226 | 0.059509 | 0.20142 | 0.17853 | -0.013733 | -0.068665 | 122.6395 | 122.4884 | -0.15106 | 122.6532 | 122.6715 | 0.18311 | -0.082397 | 122.5662 | 122.5113 | -0.050354 | 122.6898 | 122.6395 | 0.12817 | -0.073242 | 122.6807 | 122.7493 | 122.699 | -0.34332 | 122.7814 | 122.7585 | 122.7722 | -0.32044
2434.7344 | 122.8683 | -122.5662 | 0.27466 | -0.00022891 | -0.018587 | 0.015492 | 0.037091 | -0.00922 | -0.039151 | -0.0034521 | 7.627e-05 | 0.015216 | -0.03287 | -0.0048941 | -0.013424 | -0.0018798 | 0.14648 | 0.11444 | 0.15564 | 0.09613 | 0.086975 | 0.027466 | -0.091553 | 0.082397 | 0.27008 | 0.082397 | 0.19684 | 0.16022 | -0.013733 | -0.073242 | 122.5937 | 122.4747 | -0.18768 | 122.6807 | 122.6624 | 0.18768 | -0.12817 | 122.5525 | 122.493 | -0.07782 | 122.6486 | 122.6486 | 0.15564 | -0.11444 | 122.6532 | 122.7127 | 122.7219 | -0.36621 | 122.7631 | 122.7264 | 122.8363 | -0.3479
2436.5469 | 122.8729 | -122.58 | 0.2655 | 0.0074006 | -0.01816 | 0.015492 | 0.036023 | -0.013279 | -0.039151 | -0.0011023 | 7.627e-05 | 0.018634 | -0.03522 | -0.0046805 | -0.011715 | -0.0020934 | 0.17395 | 0.10986 | 0.14648 | 0.09613 | 0.09613 | 0.054932 | -0.082397 | 0.086975 | 0.24719 | 0.082397 | 0.19684 | 0.1831 | -0.013733 | -0.073242 | 122.6349 | 122.4976 | -0.16937 | 122.6898 | 122.6761 | 0.17853 | -0.091553 | 122.5662 | 122.5067 | -0.068665 | 122.6669 | 122.6624 | 0.15564 | -0.082398 | 122.6761 | 122.7539 | 122.7264 | -0.3479 | 122.7768 | 122.7631 | 122.8271 | -0.33874
2438.3281 | 122.9919 | -122.5479 | 0.2243 | -0.00022891 | -0.014742 | 0.012715 | 0.032605 | -0.010074 | -0.032315 | -0.0006751 | 7.627e-05 | 0.021625 | -0.034365 | -0.0023305 | -0.0087244 | -0.0010254 | 0.073242 | -0.059509 | 0 | 0.013733 | 0.15106 | 0.004578 | -0.11444 | 0.018311 | 0.07782 | -0.032043 | 0.25177 | 0.20599 | -0.054932 | -0.09613 | 122.5525 | 122.4335 | -0.073242 | 122.4884 | 122.5616 | 0.12817 | -0.15106 | 122.493 | 122.4518 | 0.027466 | 122.5662 | 122.5159 | 0.064087 | -0.01831 | 122.699 | 122.6212 | 122.5479 | -0.33875 | 122.7997 | 122.7539 | 122.6257 | -0.32043
2440.1094 | 122.9416 | -122.5662 | 0.23804 | -0.00022891 | -0.01346 | 0.013569 | 0.035382 | -0.010288 | -0.031887 | 0.0014613 | -0.0075532 | 0.02312 | -0.032656 | -0.0029715 | -0.0078698 | -0.00059818 | 0.10071 | -0.022888 | 0.027466 | 0.036621 | 0.10986 | 0.013733 | -0.11902 | -0.013733 | 0.082397 | -0.054932 | 0.21515 | 0.21515 | -0.036621 | -0.11444 | 122.58 | 122.4472 | -0.12817 | 122.5433 | 122.6028 | 0.15564 | -0.13733 | 122.5296 | 122.4518 | -0.022888 | 122.5525 | 122.5113 | 0.059509 | -0.022888 | 122.6761 | 122.6669 | 122.5937 | -0.35706 | 122.7814 | 122.7814 | 122.6486 | -0.35248
2441.8906 | 122.9233 | -122.6028 | 0.28381 | -0.0078584 | -0.016238 | 0.017415 | 0.0388 | -0.012424 | -0.041287 | -0.0006751 | 7.627e-05 | 0.015857 | -0.034365 | -0.0031851 | -0.015774 | -0.0016662 | 0.07782 | 0.050354 | 0.091553 | 0.073242 | 0.11902 | 0.032043 | -0.091553 | 0.082397 | 0.20599 | 0.082397 | 0.20599 | 0.18768 | -0.022888 | -0.086975 | 122.6349 | 122.5113 | -0.16479 | 122.6532 | 122.6761 | 0.16479 | -0.20599 | 122.58 | 122.5159 | -0.077819 | 122.6852 | 122.6852 | 0.16937 | -0.09613 | 122.7219 | 122.6807 | 122.6944 | -0.37537 | 122.8088 | 122.7905 | 122.8088 | -0.37079
2443.6719 | 123.0057 | -122.5388 | 0.24261 | -0.015487 | -0.017733 | 0.014851 | 0.037091 | -0.010929 | -0.034878 | -3.4096e-05 | -0.0075532 | 0.020557 | -0.033297 | -0.0021169 | -0.0076562 | -0.0023072 | 0.10071 | -0.009155 | 0.027466 | 0.041199 | 0.13275 | 0.041199 | -0.10071 | 0.082397 | 0.16022 | 0.022888 | 0.19684 | 0.19684 | -0.022888 | -0.073242 | 122.58 | 122.438 | -0.10986 | 122.5296 | 122.58 | 0.14191 | -0.14191 | 122.5159 | 122.4655 | -0.045777 | 122.6212 | 122.5616 | 0.09613 | -0.045777 | 122.6715 | 122.6395 | 122.5662 | -0.34332 | 122.7356 | 122.7356 | 122.699 | -0.31586
2445.4062 | 122.9095 | -122.58 | 0.27008 | -0.0078584 | -0.01581 | 0.012928 | 0.036237 | -0.01456 | -0.039364 | 0.0012477 | -0.015182 | 0.016925 | -0.033725 | -0.0033987 | -0.012997 | 0.00047002 | 0.13733 | 0.091553 | 0.14191 | 0.09613 | 0.07782 | 0.064087 | -0.073242 | 0.10071 | 0.19226 | 0.064087 | 0.19684 | 0.17853 | -0.018311 | -0.064087 | 122.644 | 122.5067 | -0.19226 | 122.6715 | 122.6761 | 0.16937 | -0.13275 | 122.5616 | 122.5159 | -0.073243 | 122.6807 | 122.644 | 0.12817 | -0.091553 | 122.6578 | 122.7173 | 122.7219 | -0.34332 | 122.7768 | 122.7585 | 122.7722 | -0.33417
2447.2031 | 122.9187 | -122.5662 | 0.27008 | -0.0078584 | -0.019655 | 0.019123 | 0.037305 | -0.010288 | -0.04321 | -0.0013159 | -0.0075532 | 0.016071 | -0.036288 | -0.0023305 | -0.015347 | -0.00081178 | 0.11444 | 0.068665 | 0.11444 | 0.073242 | 0.09613 | 0.032043 | -0.07782 | 0.086975 | 0.21515 | 0.091553 | 0.19684 | 0.16479 | -0.018311 | -0.07782 | 122.5983 | 122.4884 | -0.17395 | 122.6349 | 122.6395 | 0.15106 | -0.15564 | 122.5479 | 122.4884 | -0.073243 | 122.6532 | 122.6578 | 0.16937 | -0.10529 | 122.6624 | 122.6807 | 122.6807 | -0.3479 | 122.7631 | 122.731 | 122.7814 | -0.3479
2448.9844 | 122.8912 | -122.5983 | 0.27466 | -0.00022891 | -0.019655 | 0.015706 | 0.036023 | -0.012852 | -0.040432 | -0.0043065 | -0.0075532 | 0.01778 | -0.035647 | -0.0031851 | -0.014279 | -0.0010254 | 0.091553 | 0.013733 | 0.082397 | 0.054932 | 0.1236 | 0.045776 | -0.091553 | 0.027466 | 0.13733 | 0.036621 | 0.20142 | 0.19226 | -0.004578 | -0.073242 | 122.644 | 122.5067 | -0.15106 | 122.612 | 122.6532 | 0.14649 | -0.18311 | 122.5937 | 122.525 | -0.073242 | 122.6257 | 122.6349 | 0.10986 | -0.082397 | 122.7219 | 122.6898 | 122.6807 | -0.36621 | 122.7997 | 122.7905 | 122.7356 | -0.3479
2450.6875 | 122.9187 | -122.5479 | 0.25635 | -0.0078584 | -0.01346 | 0.014851 | 0.038587 | -0.010074 | -0.033383 | -0.0008887 | 7.627e-05 | 0.02248 | -0.031161 | -0.0010489 | -0.011288 | -0.004016 | 0.059509 | -0.041199 | -0.009155 | 0.022888 | 0.14648 | -0.009155 | -0.12817 | -0.022888 | 0.086975 | -0.050354 | 0.23346 | 0.20599 | -0.041199 | -0.10986 | 122.5388 | 122.4197 | -0.10986 | 122.5067 | 122.5708 | 0.15106 | -0.19684 | 122.5067 | 122.438 | -0.022889 | 122.525 | 122.4976 | 0.059509 | -0.050354 | 122.6944 | 122.6074 | 122.5388 | -0.38452 | 122.7814 | 122.7539 | 122.6349 | -0.36621
2452.6875 | 122.9828 | -122.5571 | 0.24261 | -0.015487 | -0.011538 | 0.015706 | 0.034741 | -0.010929 | -0.034024 | -0.0011023 | 7.627e-05 | 0.018848 | -0.033297 | -0.0025443 | -0.010647 | -0.00059818 | 0.15564 | 0.068665 | 0.1236 | 0.10529 | 0.10071 | 0.073242 | -0.082397 | 0.10071 | 0.19684 | 0.054932 | 0.17853 | 0.16022 | 0.004578 | -0.068665 | 122.6303 | 122.4747 | -0.14191 | 122.6257 | 122.6624 | 0.18768 | -0.086975 | 122.5616 | 122.4884 | -0.064087 | 122.6578 | 122.612 | 0.1236 | -0.082398 | 122.6578 | 122.7127 | 122.6807 | -0.32501 | 122.7356 | 122.7173 | 122.7539 | -0.31128
2456.5938 | 122.9691 | -122.5845 | 0.24261 | -0.00022891 | -0.016665 | 0.014851 | 0.03346 | -0.0083654 | -0.034237 | 0.0008203 | -0.0075532 | 0.020557 | -0.034152 | -0.00040791 | -0.010647 | -0.001239 | 0.054932 | -0.054932 | -0.027466 | 0.004578 | 0.13733 | 0.018311 | -0.1236 | 0 | 0.045776 | -0.07782 | 0.2243 | 0.21515 | -0.041199 | -0.09613 | 122.6028 | 122.4609 | -0.10529 | 122.5296 | 122.5891 | 0.12817 | -0.18768 | 122.5433 | 122.4884 | -0.018311 | 122.5845 | 122.5067 | 0.01831 | -0.027466 | 122.7219 | 122.6395 | 122.5571 | -0.36621 | 122.8088 | 122.7997 | 122.6303 | -0.33874
2460.1719 | 122.8683 | -122.5845 | 0.27466 | -0.0078584 | -0.013033 | 0.013997 | 0.039868 | -0.012211 | -0.038723 | 0.0008203 | -0.0075532 | 0.018848 | -0.031375 | -0.0012625 | -0.013851 | -0.0018798 | 0.10071 | 0.041199 | 0.07782 | 0.064087 | 0.10986 | 0.027466 | -0.11902 | 0 | 0.12817 | -0.018311 | 0.2243 | 0.20599 | -0.032043 | -0.10986 | 122.612 | 122.4655 | -0.1648 | 122.6257 | 122.6486 | 0.18311 | -0.17395 | 122.5525 | 122.4747 | -0.050354 | 122.5845 | 122.5662 | 0.091552 | -0.068664 | 122.6944 | 122.6852 | 122.6624 | -0.39368 | 122.8088 | 122.7905 | 122.7127 | -0.38452
2465.9375 | 122.8683 | -122.5891 | 0.27008 | -0.00022891 | -0.024569 | 0.015278 | 0.035596 | -0.013279 | -0.041073 | -0.0011023 | -0.0075532 | 0.018634 | -0.033938 | -0.0025443 | -0.013851 | -0.001239 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.10529 | 0.045776 | -0.082397 | 0.07782 | 0.23804 | 0.082397 | 0.18768 | 0.16937 | -0.018311 | -0.082397 | 122.6349 | 122.5067 | -0.1648 | 122.699 | 122.6898 | 0.18311 | -0.13733 | 122.5708 | 122.5067 | -0.082398 | 122.6669 | 122.6715 | 0.16479 | -0.10071 | 122.6944 | 122.7219 | 122.731 | -0.35248 | 122.7768 | 122.7585 | 122.8271 | -0.35248
2467.7344 | 122.8729 | -122.6257 | 0.26093 | -0.00022891 | -0.021151 | 0.017415 | 0.034955 | -0.01157 | -0.042569 | 0.0010339 | -0.0075532 | 0.016071 | -0.034365 | -0.0033987 | -0.011288 | -0.00059818 | 0.064087 | 0.032043 | 0.07782 | 0.054932 | 0.10529 | 0.032043 | -0.091553 | 0.032043 | 0.14648 | 0.036621 | 0.19226 | 0.18768 | 0 | -0.082397 | 122.6578 | 122.5342 | -0.15564 | 122.6578 | 122.6807 | 0.14649 | -0.19684 | 122.6257 | 122.5433 | -0.068664 | 122.6578 | 122.6624 | 0.11902 | -0.073242 | 122.731 | 122.6898 | 122.7036 | -0.35248 | 122.818 | 122.8134 | 122.7722 | -0.34332
2469.5156 | 122.8638 | -122.612 | 0.25177 | -0.00022891 | -0.020937 | 0.014424 | 0.034314 | -0.014133 | -0.037869 | -0.0038793 | -0.015182 | 0.016498 | -0.033511 | -0.0029715 | -0.011929 | 0.0013244 | 0.12817 | 0.073242 | 0.12817 | 0.064087 | 0.09613 | 0.054932 | -0.082397 | 0.073242 | 0.16022 | 0.036621 | 0.16022 | 0.1831 | 0 | -0.073242 | 122.6669 | 122.5296 | -0.15564 | 122.6852 | 122.6761 | 0.14648 | -0.1236 | 122.612 | 122.5388 | -0.091553 | 122.6852 | 122.6486 | 0.10986 | -0.068665 | 122.7081 | 122.7402 | 122.7402 | -0.33417 | 122.7722 | 122.7951 | 122.7722 | -0.32501
2471.2344 | 122.9736 | -122.5937 | 0.21973 | 0.0074006 | -0.016024 | 0.01421 | 0.034314 | -0.011997 | -0.032315 | -0.0004613 | 7.627e-05 | 0.021625 | -0.034365 | -0.0019033 | -0.0093652 | -0.00038438 | 0.064087 | -0.073242 | -0.013733 | 0.022888 | 0.12817 | 0.022888 | -0.13275 | -0.009155 | 0.036621 | -0.068665 | 0.21515 | 0.2243 | -0.032043 | -0.10529 | 122.6166 | 122.4609 | -0.091553 | 122.5204 | 122.6166 | 0.15564 | -0.15564 | 122.5616 | 122.4884 | -0.004578 | 122.5845 | 122.525 | 0.036621 | 0.004577 | 122.7219 | 122.6578 | 122.58 | -0.35248 | 122.8088 | 122.818 | 122.6303 | -0.32501
2473.0469 | 122.8683 | -122.6349 | 0.26093 | -0.00022891 | -0.017946 | 0.015919 | 0.034955 | -0.010502 | -0.037442 | -0.0011023 | 7.627e-05 | 0.019062 | -0.032656 | -0.0033987 | -0.013638 | -0.00081178 | 0.12817 | 0.082397 | 0.1236 | 0.073242 | 0.10529 | 0.059509 | -0.07782 | 0.09613 | 0.18768 | 0.054932 | 0.18768 | 0.16479 | -0.022888 | -0.07782 | 122.6944 | 122.5571 | -0.15564 | 122.7173 | 122.7081 | 0.15106 | -0.13275 | 122.612 | 122.5571 | -0.073242 | 122.731 | 122.6898 | 0.13275 | -0.09613 | 122.7402 | 122.7631 | 122.7585 | -0.33875 | 122.8226 | 122.7997 | 122.8226 | -0.33875
2474.8281 | 122.9462 | -122.58 | 0.23346 | -0.0078584 | -0.014956 | 0.010365 | 0.031751 | -0.013706 | -0.03381 | 0.0014613 | 7.627e-05 | 0.020771 | -0.031802 | -0.0014761 | -0.0080834 | -0.0027344 | 0.050354 | -0.059509 | -0.013733 | 0.018311 | 0.14191 | 0.013733 | -0.11444 | -0.036621 | 0.050354 | -0.09613 | 0.2243 | 0.21057 | -0.032043 | -0.11444 | 122.5937 | 122.4655 | -0.091552 | 122.5204 | 122.5983 | 0.13275 | -0.1831 | 122.5479 | 122.4655 | -0.009155 | 122.5433 | 122.4838 | 0.018311 | -0.022888 | 122.7219 | 122.6303 | 122.5662 | -0.3479 | 122.8043 | 122.7905 | 122.6303 | -0.3479
2476.6094 | 122.8638 | -122.6074 | 0.2655 | -0.00022891 | -0.017733 | 0.014851 | 0.035596 | -0.011783 | -0.041928 | -0.0017431 | -0.015182 | 0.016712 | -0.033725 | -0.0040395 | -0.013638 | -0.00059818 | 0.12817 | 0.091553 | 0.11902 | 0.07782 | 0.086975 | 0.050354 | -0.091553 | 0.059509 | 0.17395 | 0.041199 | 0.16937 | 0.17853 | 0 | -0.086975 | 122.6578 | 122.5159 | -0.17853 | 122.699 | 122.6852 | 0.16937 | -0.13733 | 122.6074 | 122.5204 | -0.09613 | 122.6669 | 122.6486 | 0.12817 | -0.086975 | 122.6944 | 122.7356 | 122.7264 | -0.35706 | 122.7768 | 122.7859 | 122.7814 | -0.35248
2478.3438 | 122.9874 | -122.5662 | 0.2243 | -0.0078584 | -0.014742 | 0.014851 | 0.039014 | -0.0094336 | -0.036801 | -0.0019567 | -0.0075532 | 0.019489 | -0.031375 | -0.0033987 | -0.012997 | -0.00017078 | 0.054932 | -0.045776 | 0 | 0.013733 | 0.14648 | 0 | -0.12817 | -0.022888 | 0.11902 | -0.050354 | 0.22888 | 0.19684 | -0.045776 | -0.11444 | 122.5662 | 122.438 | -0.07782 | 122.5204 | 122.58 | 0.14191 | -0.16937 | 122.5204 | 122.4518 | 0.004578 | 122.5433 | 122.5159 | 0.064087 | -0.027466 | 122.7127 | 122.6212 | 122.5662 | -0.35248 | 122.7951 | 122.7631 | 122.6852 | -0.33875
2480.0625 | 122.9233 | -122.5845 | 0.24261 | -0.00022891 | -0.022219 | 0.015492 | 0.034741 | -0.0098608 | -0.04321 | -0.0004613 | 7.627e-05 | 0.015216 | -0.034793 | -0.0023305 | -0.011929 | -0.00017078 | 0.07782 | 0.045776 | 0.07782 | 0.059509 | 0.10071 | 0.041199 | -0.086975 | 0.045776 | 0.18768 | 0.064087 | 0.1831 | 0.17853 | -0.009155 | -0.091553 | 122.6257 | 122.4976 | -0.14191 | 122.6303 | 122.644 | 0.14648 | -0.16479 | 122.5754 | 122.493 | -0.05951 | 122.6303 | 122.6486 | 0.15564 | -0.064087 | 122.6852 | 122.6624 | 122.6624 | -0.32959 | 122.7676 | 122.7631 | 122.7722 | -0.33417
2481.7812 | 122.9828 | -122.5525 | 0.21515 | -0.0078584 | -0.011965 | 0.015065 | 0.037732 | -0.0087926 | -0.035519 | 0.0016749 | 7.627e-05 | 0.018634 | -0.030947 | -0.0016897 | -0.012142 | -0.004657 | 0.041199 | -0.054932 | -0.013733 | 0.032043 | 0.16022 | 0.009155 | -0.1236 | -0.022888 | 0.10071 | -0.059509 | 0.23346 | 0.19226 | -0.050354 | -0.10071 | 122.5616 | 122.4289 | -0.054932 | 122.4976 | 122.5845 | 0.15564 | -0.17395 | 122.5021 | 122.4518 | 0.01831 | 122.5296 | 122.493 | 0.041199 | -0.022888 | 122.7127 | 122.5937 | 122.5388 | -0.33875 | 122.7859 | 122.7448 | 122.6532 | -0.31586
2483.5 | 122.9965 | -122.5983 | 0.21973 | -0.0078584 | -0.014742 | 0.01421 | 0.033887 | -0.012211 | -0.034024 | -0.0002477 | -0.0075532 | 0.019702 | -0.029452 | -0.00062151 | -0.011501 | -0.001239 | 0.036621 | -0.073242 | -0.022888 | 0.004578 | 0.14191 | 0.018311 | -0.11444 | -0.022888 | 0.054932 | -0.068665 | 0.21515 | 0.19684 | -0.027466 | -0.10986 | 122.6166 | 122.4838 | -0.07782 | 122.525 | 122.6028 | 0.11902 | -0.18311 | 122.5708 | 122.4884 | -0.004578 | 122.5754 | 122.5296 | 0.041198 | -0.022889 | 122.7402 | 122.6349 | 122.5754 | -0.33417 | 122.8134 | 122.7951 | 122.6532 | -0.32959
2485.2188 | 122.8821 | -122.612 | 0.25635 | -0.00022891 | -0.018801 | 0.015706 | 0.037946 | -0.010074 | -0.041501 | -0.0017431 | 7.627e-05 | 0.013935 | -0.033725 | -0.0031851 | -0.015133 | -0.00059818 | 0.050354 | 0.036621 | 0.082397 | 0.059509 | 0.10986 | 0.032043 | -0.07782 | 0.050354 | 0.16022 | 0.036621 | 0.20142 | 0.1831 | -0.018311 | -0.07782 | 122.644 | 122.5342 | -0.14649 | 122.6486 | 122.6715 | 0.13733 | -0.20599 | 122.5937 | 122.5342 | -0.054932 | 122.6624 | 122.6486 | 0.11444 | -0.073243 | 122.7219 | 122.6624 | 122.6944 | -0.33417 | 122.8134 | 122.7951 | 122.7722 | -0.33417
2487 | 122.8821 | -122.6212 | 0.26093 | -0.0078584 | -0.014956 | 0.013356 | 0.037732 | -0.011143 | -0.037655 | -0.0002477 | 7.627e-05 | 0.017353 | -0.029452 | -0.0025443 | -0.012356 | -0.002948 | 0.032043 | -0.022888 | 0.004578 | 0.009155 | 0.12817 | 0.009155 | -0.15106 | -0.032043 | 0.091553 | -0.054932 | 0.21973 | 0.21973 | -0.054932 | -0.10986 | 122.6303 | 122.4701 | -0.13275 | 122.5983 | 122.6303 | 0.16022 | -0.22888 | 122.5662 | 122.5113 | -0.041198 | 122.5891 | 122.5662 | 0.054931 | -0.041198 | 122.7493 | 122.6532 | 122.6257 | -0.41199 | 122.8409 | 122.8409 | 122.7127 | -0.37079
2488.7188 | 122.937 | -122.58 | 0.2243 | -0.0078584 | -0.017519 | 0.015065 | 0.033887 | -0.012638 | -0.037442 | 0.0008203 | 7.627e-05 | 0.018421 | -0.034152 | -0.0033987 | -0.0093652 | -0.0014526 | 0.1236 | 0.086975 | 0.1236 | 0.10986 | 0.082397 | 0.045776 | -0.073242 | 0.11902 | 0.21515 | 0.073242 | 0.16937 | 0.14648 | -0.013733 | -0.068665 | 122.6257 | 122.5067 | -0.14191 | 122.6669 | 122.6898 | 0.18311 | -0.10071 | 122.5662 | 122.5113 | -0.054931 | 122.699 | 122.6532 | 0.14191 | -0.07782 | 122.6624 | 122.7036 | 122.7036 | -0.29755 | 122.7493 | 122.7264 | 122.7951 | -0.29297
2490.5156 | 122.8867 | -122.6028 | 0.26093 | -0.00022891 | -0.017946 | 0.015919 | 0.038373 | -0.012424 | -0.042141 | -0.0032385 | 7.627e-05 | 0.016712 | -0.03287 | -0.0044669 | -0.014919 | -0.00038438 | 0.064087 | 0.009155 | 0.07782 | 0.054932 | 0.086975 | 0.050354 | -0.091553 | 0.036621 | 0.14191 | 0.036621 | 0.19684 | 0.19226 | -0.022888 | -0.09613 | 122.6532 | 122.5113 | -0.17395 | 122.612 | 122.6578 | 0.14649 | -0.19684 | 122.58 | 122.5067 | -0.064087 | 122.6395 | 122.6395 | 0.13275 | -0.068664 | 122.6898 | 122.6669 | 122.6807 | -0.35248 | 122.7997 | 122.7951 | 122.7448 | -0.35706
2492.2969 | 122.9599 | -122.58 | 0.24261 | -0.00022891 | -0.0076926 | 0.013783 | 0.036237 | -0.011143 | -0.032101 | -0.0008887 | 7.627e-05 | 0.022052 | -0.028811 | -0.0012625 | -0.0093652 | -0.002948 | 0.054932 | -0.091553 | -0.013733 | 0.018311 | 0.13733 | 0.009155 | -0.13733 | -0.045776 | 0.036621 | -0.09613 | 0.21515 | 0.19226 | -0.036621 | -0.11444 | 122.5891 | 122.4426 | -0.10529 | 122.4884 | 122.5983 | 0.15564 | -0.18768 | 122.5433 | 122.4655 | -0.027466 | 122.5342 | 122.4838 | 0.018311 | -0.050354 | 122.7173 | 122.6349 | 122.5662 | -0.37994 | 122.7951 | 122.7722 | 122.6166 | -0.35706
2494.0781 | 122.9874 | -122.5616 | 0.21515 | -0.00022891 | -0.009188 | 0.011647 | 0.036878 | -0.0098608 | -0.034024 | -0.0002477 | 7.627e-05 | 0.02013 | -0.03052 | -0.00019431 | -0.012356 | -0.0027344 | 0.059509 | -0.018311 | 0.013733 | 0.032043 | 0.14191 | 0.009155 | -0.12817 | 0.009155 | 0.12817 | -0.018311 | 0.20599 | 0.19684 | -0.041199 | -0.11902 | 122.5708 | 122.4335 | -0.073242 | 122.5433 | 122.5937 | 0.16022 | -0.15564 | 122.5204 | 122.4426 | -0.009155 | 122.5708 | 122.5433 | 0.10071 | -0.018311 | 122.7036 | 122.6212 | 122.5754 | -0.34332 | 122.7676 | 122.7585 | 122.6898 | -0.33417
2495.8438 | 122.9645 | -122.6028 | 0.22888 | -0.0078584 | -0.013033 | 0.012928 | 0.03346 | -0.011356 | -0.034665 | 0.0008203 | -0.0075532 | 0.019702 | -0.032656 | 0.0010873 | -0.010433 | 0.0011108 | 0.027466 | -0.068665 | -0.022888 | 0.004578 | 0.14191 | 0.018311 | -0.12817 | -0.054932 | 0.050354 | -0.086975 | 0.21057 | 0.21057 | -0.041199 | -0.10529 | 122.6212 | 122.4747 | -0.086975 | 122.5342 | 122.6074 | 0.13275 | -0.20142 | 122.5616 | 122.4976 | -0.018311 | 122.5479 | 122.5159 | 0.018311 | -0.018311 | 122.7448 | 122.6303 | 122.58 | -0.35706 | 122.8134 | 122.8134 | 122.6532 | -0.33417
2497.6562 | 123.0148 | -122.5891 | 0.21973 | -0.0078584 | -0.013888 | 0.012928 | 0.039014 | -0.013706 | -0.03381 | 0.0018885 | -0.0075532 | 0.018634 | -0.031588 | -0.0031851 | -0.011288 | -0.00038438 | 0.018311 | -0.054932 | 0 | 0.013733 | 0.13733 | 0.004578 | -0.1236 | -0.013733 | 0.07782 | -0.045776 | 0.21515 | 0.20142 | -0.041199 | -0.10529 | 122.5937 | 122.4655 | -0.082398 | 122.5342 | 122.6028 | 0.13733 | -0.20142 | 122.5479 | 122.4838 | -0.004578 | 122.5754 | 122.5433 | 0.05951 | -0.018311 | 122.7264 | 122.6074 | 122.5891 | -0.34332 | 122.8043 | 122.7905 | 122.6669 | -0.32501
2499.3906 | 122.9095 | -122.5937 | 0.25177 | -0.0078584 | -0.018587 | 0.015492 | 0.037091 | -0.015415 | -0.044064 | -0.0015295 | -0.0075532 | 0.014789 | -0.033084 | -0.0031851 | -0.01556 | -0.00059818 | 0.027466 | 0.036621 | 0.091553 | 0.054932 | 0.09613 | 0.022888 | -0.091553 | 0.032043 | 0.16937 | 0.064087 | 0.17395 | 0.16022 | -0.018311 | -0.07782 | 122.6166 | 122.5021 | -0.15564 | 122.6303 | 122.6486 | 0.14649 | -0.2243 | 122.5754 | 122.5159 | -0.07782 | 122.6257 | 122.6578 | 0.14191 | -0.091553 | 122.6898 | 122.6212 | 122.6852 | -0.34332 | 122.7676 | 122.7539 | 122.7631 | -0.32959
2501.1562 | 122.85 | -122.612 | 0.25635 | -0.00022891 | -0.012392 | 0.01656 | 0.039014 | -0.013492 | -0.041714 | -0.0013159 | -0.015182 | 0.019062 | -0.031802 | -0.0019033 | -0.013424 | -0.00038438 | 0.11902 | 0.064087 | 0.10071 | 0.091553 | 0.10529 | 0.027466 | -0.09613 | 0.009155 | 0.17395 | 0.013733 | 0.19226 | 0.18768 | -0.027466 | -0.11444 | 122.6395 | 122.5159 | -0.15106 | 122.6761 | 122.7036 | 0.18768 | -0.13733 | 122.5845 | 122.4976 | -0.064087 | 122.6212 | 122.6257 | 0.12817 | -0.068665 | 122.7173 | 122.731 | 122.7127 | -0.35248 | 122.8043 | 122.7997 | 122.7859 | -0.37079
2502.9531 | 122.9874 | -122.58 | 0.21515 | -0.0078584 | -0.012606 | 0.013142 | 0.034101 | -0.010502 | -0.03381 | 0.0001795 | 7.627e-05 | 0.021839 | -0.032656 | -0.0033987 | -0.01022 | -0.004016 | 0.073242 | -0.027466 | 0.022888 | 0.059509 | 0.1236 | 0.004578 | -0.1236 | 0.009155 | 0.13733 | -0.022888 | 0.20142 | 0.19226 | -0.032043 | -0.10986 | 122.5845 | 122.4564 | -0.091553 | 122.5525 | 122.6395 | 0.1831 | -0.14191 | 122.5479 | 122.4701 | -0.013733 | 122.5891 | 122.5571 | 0.086975 | -0.022888 | 122.7036 | 122.6532 | 122.6028 | -0.33875 | 122.7814 | 122.7722 | 122.7173 | -0.32501
2504.7344 | 122.9233 | -122.6074 | 0.27008 | -0.00022891 | -0.020296 | 0.015278 | 0.037732 | -0.012211 | -0.046414 | -0.0008887 | 0.0077058 | 0.015644 | -0.032443 | -0.0051077 | -0.015347 | -0.0010254 | 0.064087 | 0.050354 | 0.10986 | 0.073242 | 0.10529 | 0.050354 | -0.10529 | 0.064087 | 0.19684 | 0.082397 | 0.18768 | 0.16479 | 0 | -0.054932 | 122.6578 | 122.5021 | -0.1648 | 122.6578 | 122.6807 | 0.17853 | -0.20599 | 122.6074 | 122.5525 | -0.082398 | 122.6715 | 122.6898 | 0.13733 | -0.10529 | 122.7127 | 122.6715 | 122.7173 | -0.37537 | 122.7951 | 122.7722 | 122.8043 | -0.32501
2506.4531 | 122.9187 | -122.5891 | 0.24261 | 0.0074006 | -0.016238 | 0.013783 | 0.037732 | -0.012852 | -0.041928 | -0.0021703 | -0.0075532 | 0.01778 | -0.032443 | -0.0046805 | -0.016842 | -0.0020934 | 0.10986 | 0.068665 | 0.13275 | 0.10071 | 0.10986 | 0.032043 | -0.09613 | 0.091553 | 0.2243 | 0.09613 | 0.16479 | 0.15564 | -0.009155 | -0.07782 | 122.6212 | 122.493 | -0.13275 | 122.6578 | 122.6898 | 0.19684 | -0.13275 | 122.58 | 122.5113 | -0.07782 | 122.6807 | 122.6852 | 0.17395 | -0.086975 | 122.699 | 122.699 | 122.7219 | -0.33874 | 122.7539 | 122.7448 | 122.8134 | -0.32044
2508.1719 | 122.8683 | -122.6028 | 0.24719 | -0.015487 | -0.014956 | 0.014637 | 0.0388 | -0.00922 | -0.036801 | -0.0036657 | 0.0077058 | 0.017139 | -0.032016 | -0.0014761 | -0.013424 | -0.00038438 | 0.13275 | 0.10986 | 0.13733 | 0.09613 | 0.10071 | 0.045776 | -0.082397 | 0.082397 | 0.23346 | 0.07782 | 0.18768 | 0.16022 | -0.004578 | -0.068665 | 122.6486 | 122.5204 | -0.14648 | 122.7127 | 122.699 | 0.17853 | -0.11444 | 122.5983 | 122.5342 | -0.059509 | 122.6852 | 122.6807 | 0.14649 | -0.086975 | 122.7036 | 122.7356 | 122.7402 | -0.32959 | 122.7905 | 122.7631 | 122.8363 | -0.31586
2509.8906 | 123.0331 | -122.5708 | 0.23346 | -0.00022891 | -0.01581 | 0.012715 | 0.032178 | -0.011143 | -0.033596 | 0.0025293 | -0.0075532 | 0.019275 | -0.034152 | -0.0027579 | -0.0091516 | -0.002948 | 0.059509 | -0.032043 | 0.009155 | 0.022888 | 0.14191 | 0 | -0.10529 | 0.036621 | 0.10529 | -0.009155 | 0.18768 | 0.16937 | -0.009155 | -0.086975 | 122.5708 | 122.4655 | -0.091552 | 122.5388 | 122.5937 | 0.12817 | -0.17395 | 122.5616 | 122.4838 | -0.045776 | 122.6074 | 122.5616 | 0.07782 | -0.064086 | 122.7127 | 122.6303 | 122.58 | -0.33875 | 122.7585 | 122.7402 | 122.6761 | -0.32043
2511.6875 | 122.9874 | -122.5937 | 0.2243 | -0.0078584 | -0.016024 | 0.011647 | 0.033673 | -0.012638 | -0.033596 | 0.0001795 | -0.0075532 | 0.02013 | -0.033725 | -0.0019033 | -0.01022 | -0.00038438 | 0.041199 | -0.068665 | -0.027466 | 0 | 0.15106 | -0.004578 | -0.12817 | -0.009155 | 0.054932 | -0.050354 | 0.21515 | 0.21057 | -0.036621 | -0.10986 | 122.5891 | 122.4655 | -0.073242 | 122.525 | 122.5937 | 0.12817 | -0.18311 | 122.5571 | 122.4838 | -0.009155 | 122.5845 | 122.5433 | 0.059509 | -0.013733 | 122.7448 | 122.6349 | 122.5662 | -0.35248 | 122.8088 | 122.8043 | 122.6486 | -0.33417
2513.4844 | 122.9782 | -122.5708 | 0.19684 | -0.00022891 | -0.015383 | 0.014851 | 0.036237 | -0.011783 | -0.033596 | 0.0001795 | 0.0077058 | 0.022266 | -0.033511 | -0.0021169 | -0.0093652 | -0.0020934 | 0.09613 | 0.009155 | 0.041199 | 0.050354 | 0.13733 | 0.018311 | -0.11902 | 0.013733 | 0.14191 | -0.013733 | 0.20599 | 0.18768 | -0.027466 | -0.10071 | 122.5891 | 122.4518 | -0.059509 | 122.58 | 122.6212 | 0.16937 | -0.10071 | 122.5433 | 122.4701 | 0.009156 | 122.5845 | 122.5571 | 0.086975 | -0.009155 | 122.7081 | 122.6669 | 122.612 | -0.31586 | 122.7768 | 122.7585 | 122.7127 | -0.29755
2515.2656 | 122.9141 | -122.6257 | 0.23346 | -0.0078584 | -0.023073 | 0.015919 | 0.035809 | -0.012211 | -0.044278 | -0.0011023 | -0.0075532 | 0.014789 | -0.031375 | -0.0036123 | -0.01556 | -0.00017078 | 0.1236 | 0.13733 | 0.14191 | 0.10986 | 0.10071 | 0.041199 | -0.10071 | 0.082397 | 0.24719 | 0.091553 | 0.14191 | 0.15564 | -0.018311 | -0.07782 | 122.6669 | 122.525 | -0.13275 | 122.7631 | 122.7356 | 0.21057 | -0.10986 | 122.6074 | 122.5479 | -0.091552 | 122.7081 | 122.7173 | 0.16937 | -0.077819 | 122.7264 | 122.7493 | 122.7676 | -0.33417 | 122.7676 | 122.7814 | 122.8729 | -0.31128
2516.9844 | 122.9141 | -122.6303 | 0.2655 | -0.0078584 | -0.019869 | -0.0062976 | 0.035809 | -0.012852 | -0.042996 | -0.0025977 | 0.0077058 | 0.012653 | -0.035006 | -0.0046805 | -0.012142 | 0.00068362 | 0.050354 | 0.050354 | 0.082397 | 0.064087 | 0.10071 | 0.036621 | -0.10071 | 0.073242 | 0.18768 | 0.064087 | 0.17853 | 0.16479 | -0.036621 | -0.073242 | 122.6669 | 122.5296 | -0.16479 | 122.6807 | 122.6944 | 0.1648 | -0.21515 | 122.5937 | 122.5571 | -0.086975 | 122.7036 | 122.6944 | 0.13733 | -0.10071 | 122.731 | 122.6807 | 122.7127 | -0.36621 | 122.8088 | 122.7951 | 122.818 | -0.33874
2518.7656 | 122.9599 | -122.5616 | 0.21515 | -0.00022891 | -0.014101 | 0.013997 | 0.035382 | -0.011143 | -0.032956 | -0.0011023 | 7.627e-05 | 0.020771 | -0.032016 | -0.0025443 | -0.01022 | -0.0027344 | 0.10986 | 0.041199 | 0.045776 | 0.059509 | 0.14191 | 0.013733 | -0.11902 | 0.036621 | 0.1236 | -0.027466 | 0.19684 | 0.17395 | -0.032043 | -0.10529 | 122.5754 | 122.4426 | -0.073242 | 122.6028 | 122.6212 | 0.17853 | -0.10529 | 122.5296 | 122.4564 | -0.018311 | 122.5983 | 122.5342 | 0.07782 | -0.041199 | 122.7036 | 122.6715 | 122.6074 | -0.33417 | 122.7585 | 122.7356 | 122.6852 | -0.32044
2520.5625 | 122.9919 | -122.612 | 0.21057 | -0.00022891 | -0.01581 | 0.014851 | 0.034741 | -0.013279 | -0.035305 | 0.0008203 | -0.0075532 | 0.022266 | -0.033084 | -0.0023305 | -0.011715 | -0.00059818 | 0.041199 | -0.082397 | -0.018311 | 0.004578 | 0.15106 | -0.004578 | -0.10986 | -0.032043 | 0.036621 | -0.068665 | 0.21057 | 0.19684 | -0.045776 | -0.10529 | 122.6074 | 122.5021 | -0.059509 | 122.5296 | 122.6166 | 0.11444 | -0.16937 | 122.5662 | 122.5067 | 0 | 122.58 | 122.5433 | 0.036621 | -0.013733 | 122.7631 | 122.6532 | 122.5937 | -0.32043 | 122.8226 | 122.8088 | 122.6486 | -0.31586
2522.2812 | 122.9782 | -122.6166 | 0.2243 | 0.0074006 | -0.013247 | 0.014851 | 0.037091 | -0.013706 | -0.037442 | 0.0010339 | 7.627e-05 | 0.022052 | -0.029238 | -0.0019033 | -0.0097924 | 4.2822e-05 | 0.027466 | -0.082397 | -0.022888 | 0.004578 | 0.14191 | 0 | -0.11902 | -0.041199 | 0.045776 | -0.07782 | 0.19684 | 0.19684 | -0.041199 | -0.10071 | 122.6166 | 122.4976 | -0.082397 | 122.5342 | 122.6212 | 0.1236 | -0.19684 | 122.5754 | 122.5159 | -0.027466 | 122.5754 | 122.5388 | 0.022888 | -0.027466 | 122.7585 | 122.644 | 122.5937 | -0.34332 | 122.8134 | 122.8134 | 122.6624 | -0.32501
2524.0625 | 122.8638 | -122.6212 | 0.24719 | 0.0074006 | -0.016451 | 0.013783 | 0.038159 | -0.011997 | -0.040005 | -0.0017431 | 7.627e-05 | 0.01778 | -0.032016 | -0.00062151 | -0.014492 | 0.00047002 | 0.068665 | 0.013733 | 0.059509 | 0.068665 | 0.10986 | 0.013733 | -0.10529 | -0.027466 | 0.11444 | -0.041199 | 0.19684 | 0.20142 | -0.018311 | -0.11444 | 122.6349 | 122.5159 | -0.13733 | 122.6349 | 122.6898 | 0.17395 | -0.17853 | 122.6028 | 122.5067 | -0.050354 | 122.5937 | 122.58 | 0.073242 | -0.045776 | 122.731 | 122.6898 | 122.6807 | -0.35248 | 122.818 | 122.8226 | 122.7356 | -0.36163
2525.8438 | 122.9141 | -122.6303 | 0.22888 | -0.00022891 | -0.020083 | 0.017201 | 0.038587 | -0.012852 | -0.044278 | -0.0028113 | 0.0077058 | 0.015857 | -0.032656 | -0.0048941 | -0.015133 | -0.00017078 | 0.082397 | 0.045776 | 0.091553 | 0.07782 | 0.10986 | 0.032043 | -0.086975 | 0.054932 | 0.20599 | 0.059509 | 0.16937 | 0.16937 | -0.022888 | -0.086975 | 122.6624 | 122.5433 | -0.11902 | 122.6761 | 122.7081 | 0.16479 | -0.14649 | 122.6074 | 122.5433 | -0.059509 | 122.6852 | 122.6898 | 0.14648 | -0.059509 | 122.7402 | 122.7127 | 122.7219 | -0.31586 | 122.7997 | 122.7997 | 122.8363 | -0.31586
2527.6406 | 122.9874 | -122.5754 | 0.21057 | -0.00022891 | -0.01346 | 0.016346 | 0.03645 | -0.011143 | -0.037014 | -0.0034521 | 0.0077058 | 0.019062 | -0.029452 | -0.0016897 | -0.01257 | -0.0035888 | 0.054932 | -0.064087 | 0.013733 | 0.032043 | 0.13275 | 0.009155 | -0.11902 | -0.027466 | 0.091553 | -0.050354 | 0.19226 | 0.19226 | -0.041199 | -0.09613 | 122.5845 | 122.4564 | -0.07782 | 122.5113 | 122.6074 | 0.15106 | -0.15564 | 122.5342 | 122.4792 | -0.01831 | 122.5479 | 122.525 | 0.045776 | -0.01831 | 122.7081 | 122.6303 | 122.5891 | -0.32959 | 122.7676 | 122.7676 | 122.6669 | -0.3067
2529.4219 | 122.9599 | -122.5937 | 0.19684 | -0.00022891 | -0.012606 | 0.013569 | 0.034101 | -0.012211 | -0.036374 | -0.0004613 | 7.627e-05 | 0.022052 | -0.03052 | -0.0016897 | -0.0087244 | -0.0031616 | 0.13275 | 0.004578 | 0.041199 | 0.054932 | 0.1236 | 0.009155 | -0.1236 | 0.004578 | 0.1236 | -0.032043 | 0.20142 | 0.1831 | -0.045776 | -0.10071 | 122.6028 | 122.4701 | -0.073242 | 122.5983 | 122.6486 | 0.17853 | -0.064087 | 122.5479 | 122.493 | 0.004578 | 122.5983 | 122.5616 | 0.068665 | -0.013733 | 122.7173 | 122.7264 | 122.6349 | -0.32043 | 122.7951 | 122.7768 | 122.7173 | -0.29755
2531.2031 | 123.0011 | -122.6212 | 0.20599 | -0.0078584 | -0.01346 | 0.015278 | 0.033887 | -0.012852 | -0.035519 | -0.0011023 | -0.0075532 | 0.019702 | -0.033511 | -0.0021169 | -0.011074 | -0.00017078 | 0.027466 | -0.082397 | -0.032043 | 0.018311 | 0.12817 | 0.004578 | -0.11444 | -0.036621 | 0.050354 | -0.068665 | 0.19226 | 0.19226 | -0.032043 | -0.086975 | 122.6257 | 122.5067 | -0.07782 | 122.5388 | 122.6395 | 0.13275 | -0.17853 | 122.5891 | 122.5342 | -0.013733 | 122.5845 | 122.5525 | 0.01831 | -0.013733 | 122.7493 | 122.6486 | 122.5891 | -0.32044 | 122.8134 | 122.8134 | 122.6715 | -0.29297
2533 | 123.0103 | -122.5937 | 0.20599 | -0.00022891 | -0.013888 | 0.016133 | 0.035169 | -0.0096472 | -0.035092 | -0.0017431 | -0.0075532 | 0.020343 | -0.03052 | -0.0023305 | -0.014279 | -0.0018798 | 0.054932 | -0.045776 | 0.004578 | 0.032043 | 0.16022 | 0.018311 | -0.14648 | -0.018311 | 0.13275 | -0.018311 | 0.18768 | 0.19684 | -0.032043 | -0.1236 | 122.612 | 122.4472 | -0.045777 | 122.5479 | 122.6257 | 0.17853 | -0.15106 | 122.5616 | 122.4701 | -0.018311 | 122.5754 | 122.5754 | 0.10528 | -0.009156 | 122.7539 | 122.6486 | 122.5983 | -0.35248 | 122.7814 | 122.7905 | 122.7264 | -0.32959
2534.7812 | 122.9279 | -122.6074 | 0.23804 | -0.00022891 | -0.018374 | 0.013997 | 0.039227 | -0.013065 | -0.043423 | -0.0025977 | 7.627e-05 | 0.013507 | -0.032016 | -0.0029715 | -0.018551 | 0.0011108 | 0.12817 | 0.10071 | 0.13275 | 0.09613 | 0.09613 | 0.045776 | -0.09613 | 0.10071 | 0.26093 | 0.10529 | 0.16479 | 0.17395 | 0 | -0.073242 | 122.6532 | 122.5113 | -0.14191 | 122.7081 | 122.7036 | 0.19226 | -0.10986 | 122.6074 | 122.5342 | -0.073242 | 122.7081 | 122.7127 | 0.17853 | -0.064087 | 122.7036 | 122.7356 | 122.7402 | -0.33417 | 122.7722 | 122.7814 | 122.8683 | -0.31128
2536.5 | 122.8958 | -122.6395 | 0.23346 | -0.00022891 | -0.019228 | 0.01421 | 0.038587 | -0.01157 | -0.042996 | -0.0040929 | -0.0075532 | 0.014362 | -0.032656 | -0.0042531 | -0.014919 | -0.00017078 | 0.050354 | 0.013733 | 0.07782 | 0.059509 | 0.10986 | 0.059509 | -0.10071 | 0.009155 | 0.15564 | 0.032043 | 0.1831 | 0.16022 | -0.013733 | -0.09613 | 122.699 | 122.5388 | -0.1236 | 122.6532 | 122.699 | 0.16022 | -0.1831 | 122.6257 | 122.5433 | -0.050354 | 122.6486 | 122.6715 | 0.12817 | -0.073242 | 122.7493 | 122.6898 | 122.7173 | -0.33417 | 122.8226 | 122.7997 | 122.7951 | -0.32959
2538.2656 | 122.9507 | -122.6257 | 0.21973 | -0.0078584 | -0.0081198 | 0.012715 | 0.035169 | -0.013492 | -0.031887 | -0.0006751 | 7.627e-05 | 0.020343 | -0.030947 | -0.00083531 | -0.0093652 | -0.0025208 | 0.07782 | -0.045776 | 0.009155 | 0.013733 | 0.13733 | 0.009155 | -0.12817 | -0.036621 | 0.054932 | -0.09613 | 0.20599 | 0.1831 | -0.050354 | -0.11902 | 122.6349 | 122.4976 | -0.082398 | 122.58 | 122.6395 | 0.14191 | -0.14191 | 122.5754 | 122.5067 | -0.013733 | 122.5891 | 122.5296 | 0.022889 | -0.036622 | 122.7631 | 122.7036 | 122.6349 | -0.3479 | 122.8317 | 122.8088 | 122.6807 | -0.33875
2539.9844 | 122.9004 | -122.6166 | 0.22888 | -0.0078584 | -0.021792 | 0.015065 | 0.0388 | -0.013065 | -0.041928 | -0.0019567 | 7.627e-05 | 0.014148 | -0.031588 | -0.0025443 | -0.015133 | 4.2822e-05 | 0.050354 | 0.013733 | 0.082397 | 0.064087 | 0.10071 | 0.036621 | -0.09613 | 0.036621 | 0.16937 | 0.054932 | 0.1831 | 0.16022 | -0.013733 | -0.07782 | 122.6532 | 122.5204 | -0.12817 | 122.6303 | 122.6807 | 0.16022 | -0.17853 | 122.6028 | 122.5388 | -0.045777 | 122.6532 | 122.6715 | 0.13275 | -0.068665 | 122.7173 | 122.6669 | 122.699 | -0.32501 | 122.7997 | 122.7768 | 122.7859 | -0.3067
2541.7656 | 122.9919 | -122.5891 | 0.21515 | -0.0078584 | -0.019869 | 0.011433 | 0.034528 | -0.01157 | -0.034878 | -0.0023839 | -0.015182 | 0.018634 | -0.032016 | -0.0012625 | -0.010433 | -0.0010254 | 0.13733 | 0.059509 | 0.11902 | 0.091553 | 0.091553 | 0.041199 | -0.086975 | 0.086975 | 0.17395 | 0.054932 | 0.14191 | 0.15106 | 0 | -0.059509 | 122.6303 | 122.5021 | -0.1236 | 122.6486 | 122.6807 | 0.17853 | -0.07782 | 122.5891 | 122.5296 | -0.073242 | 122.6761 | 122.644 | 0.11444 | -0.064087 | 122.6807 | 122.7264 | 122.7081 | -0.30212 | 122.731 | 122.7402 | 122.7631 | -0.27466
2543.4844 | 122.9874 | -122.5891 | 0.21057 | -0.00022891 | -0.015383 | 0.014637 | 0.035382 | -0.010288 | -0.036587 | -0.0021703 | 7.627e-05 | 0.021625 | -0.032016 | -0.0031851 | -0.010433 | -0.0023072 | 0.045776 | -0.045776 | -0.009155 | 0.036621 | 0.14191 | -0.009155 | -0.13275 | -0.032043 | 0.10529 | -0.059509 | 0.19226 | 0.19226 | -0.050354 | -0.10986 | 122.58 | 122.4564 | -0.068664 | 122.5433 | 122.6257 | 0.16937 | -0.1648 | 122.5388 | 122.4792 | -0.01831 | 122.5571 | 122.5296 | 0.050354 | -0.01831 | 122.731 | 122.6349 | 122.58 | -0.34332 | 122.7814 | 122.7814 | 122.6944 | -0.32043
2545.2812 | 122.9599 | -122.6166 | 0.21515 | -0.0078584 | -0.011751 | 0.013997 | 0.037946 | -0.010715 | -0.035519 | -0.0015295 | 0.0077058 | 0.024829 | -0.032443 | -0.0023305 | -0.008938 | -0.0027344 | 0.041199 | -0.086975 | -0.022888 | 0.013733 | 0.14648 | 0.009155 | -0.12817 | -0.041199 | 0.022888 | -0.082397 | 0.1831 | 0.19226 | -0.054932 | -0.10071 | 122.6257 | 122.4884 | -0.068665 | 122.5296 | 122.6303 | 0.14191 | -0.17395 | 122.5616 | 122.5159 | -0.032044 | 122.5754 | 122.5342 | 0.018311 | -0.022888 | 122.7631 | 122.6578 | 122.5937 | -0.34332 | 122.7997 | 122.8088 | 122.6395 | -0.31586
2547.0625 | 122.9324 | -122.6349 | 0.21515 | -0.015487 | -0.017092 | 0.016346 | 0.039227 | -0.0096472 | -0.043423 | -0.0028113 | -0.0075532 | 0.016071 | -0.035006 | -0.0044669 | -0.015988 | 0.00047002 | 0.10986 | 0.10529 | 0.13733 | 0.09613 | 0.10986 | 0.041199 | -0.082397 | 0.10071 | 0.21973 | 0.09613 | 0.14191 | 0.13733 | -0.009155 | -0.068665 | 122.6761 | 122.5525 | -0.10529 | 122.7402 | 122.731 | 0.17853 | -0.10529 | 122.6257 | 122.5662 | -0.073242 | 122.7356 | 122.731 | 0.16479 | -0.07782 | 122.7448 | 122.7448 | 122.7722 | -0.29755 | 122.7768 | 122.7722 | 122.8546 | -0.28381
2548.8594 | 122.9095 | -122.6303 | 0.22888 | -0.0078584 | -0.01816 | 0.013997 | 0.036023 | -0.010715 | -0.040646 | -0.0055883 | -0.0075532 | 0.016498 | -0.03287 | -0.0059621 | -0.014706 | -0.001239 | 0.086975 | 0.050354 | 0.10986 | 0.073242 | 0.091553 | 0.045776 | -0.10071 | 0.073242 | 0.19684 | 0.07782 | 0.15564 | 0.16937 | 0.004578 | -0.073242 | 122.6761 | 122.5296 | -0.13733 | 122.6807 | 122.7036 | 0.17395 | -0.14191 | 122.6349 | 122.5571 | -0.073242 | 122.7036 | 122.7081 | 0.15106 | -0.059509 | 122.7219 | 122.7173 | 122.7402 | -0.32959 | 122.7859 | 122.7997 | 122.8271 | -0.30212
2550.6562 | 122.9919 | -122.5983 | 0.1831 | 0.01503 | -0.012392 | 0.01421 | 0.037091 | -0.010502 | -0.034451 | 0.0001795 | -0.0075532 | 0.02312 | -0.030307 | -0.0025443 | -0.012356 | -0.0035888 | 0.082397 | -0.022888 | 0.022888 | 0.054932 | 0.13733 | 0.009155 | -0.10529 | 0.004578 | 0.12817 | -0.027466 | 0.18768 | 0.1831 | -0.045776 | -0.091553 | 122.6074 | 122.493 | -0.045776 | 122.5754 | 122.6532 | 0.16022 | -0.10071 | 122.5525 | 122.5067 | 0.004578 | 122.6028 | 122.5708 | 0.064087 | 0 | 122.7356 | 122.6807 | 122.6212 | -0.28839 | 122.786 | 122.7814 | 122.7264 | -0.27466
2552.4375 | 122.9004 | -122.6395 | 0.21973 | -0.00022891 | -0.022433 | 0.022328 | 0.03346 | -0.010502 | -0.04385 | -0.0013159 | -0.015182 | 0.018207 | -0.03522 | -0.0029715 | -0.013851 | 0.0015382 | 0.09613 | 0.082397 | 0.10071 | 0.07782 | 0.11444 | 0.032043 | -0.09613 | 0.07782 | 0.20599 | 0.07782 | 0.15106 | 0.14648 | 0.018311 | -0.07782 | 122.6715 | 122.5433 | -0.10529 | 122.7219 | 122.7173 | 0.17395 | -0.1236 | 122.6578 | 122.5616 | -0.068665 | 122.7173 | 122.7173 | 0.15564 | -0.073243 | 122.7539 | 122.7356 | 122.7402 | -0.31586 | 122.7905 | 122.7859 | 122.8455 | -0.29755
2554.1562 | 122.8409 | -122.6715 | 0.23346 | -0.00022891 | -0.014315 | 0.013569 | 0.039868 | -0.011143 | -0.039151 | -0.0025977 | 7.627e-05 | 0.014789 | -0.030093 | -0.0042531 | -0.012356 | -0.004657 | 0.10529 | 0.082397 | 0.11902 | 0.091553 | 0.11902 | 0.041199 | -0.082397 | 0.041199 | 0.16022 | 0.022888 | 0.14191 | 0.15564 | -0.032043 | -0.10986 | 122.7127 | 122.5891 | -0.11444 | 122.7539 | 122.7631 | 0.17395 | -0.12817 | 122.6395 | 122.5616 | -0.091552 | 122.7127 | 122.6944 | 0.13275 | -0.077819 | 122.7905 | 122.7768 | 122.7905 | -0.31586 | 122.8134 | 122.8271 | 122.8317 | -0.34332
2555.9375 | 122.9553 | -122.6166 | 0.16022 | -0.00022891 | -0.014956 | 0.01186 | 0.032605 | -0.011143 | -0.03381 | -0.0015295 | 7.627e-05 | 0.017566 | -0.027529 | -0.0019033 | -0.01022 | -0.0014526 | 0.09613 | 0.018311 | 0.036621 | 0.054932 | 0.13733 | 0.013733 | -0.11444 | 0.027466 | 0.082397 | -0.059509 | 0.15564 | 0.15106 | -0.036621 | -0.12817 | 122.6303 | 122.5021 | -0.022888 | 122.6349 | 122.6715 | 0.16937 | -0.064087 | 122.58 | 122.4884 | -0.004577 | 122.644 | 122.5571 | 0.068665 | -0.009155 | 122.7539 | 122.7127 | 122.6532 | -0.27466 | 122.7722 | 122.7676 | 122.699 | -0.28839
2557.7188 | 122.8775 | -122.6257 | 0.21057 | -0.00022891 | -0.013888 | 0.017201 | 0.038159 | -0.012211 | -0.042569 | 0.0008203 | -0.0075532 | 0.014148 | -0.03052 | -0.0042531 | -0.014279 | -0.0016662 | 0.10986 | 0.12817 | 0.15106 | 0.10986 | 0.091553 | 0.036621 | -0.10071 | 0.068665 | 0.2243 | 0.082397 | 0.11902 | 0.11902 | 0 | -0.07782 | 122.6624 | 122.525 | -0.11902 | 122.7539 | 122.7356 | 0.21057 | -0.10071 | 122.6257 | 122.5479 | -0.091552 | 122.6944 | 122.7081 | 0.16022 | -0.091552 | 122.7173 | 122.7356 | 122.7768 | -0.31128 | 122.7448 | 122.7448 | 122.85 | -0.28839
2559.5156 | 122.8821 | -122.6944 | 0.20142 | -0.0078584 | -0.018374 | 0.017628 | 0.034528 | -0.010929 | -0.037869 | -0.0004613 | 7.627e-05 | 0.01308 | -0.027529 | -0.0031851 | -0.012997 | -0.001239 | 0.11444 | 0.082397 | 0.12817 | 0.073242 | 0.091553 | 0.054932 | -0.073242 | 0.07782 | 0.13275 | 0.036621 | 0.12817 | 0.10529 | -0.022888 | -0.07782 | 122.7493 | 122.6212 | -0.10986 | 122.7768 | 122.7676 | 0.14648 | -0.086975 | 122.6715 | 122.6166 | -0.073242 | 122.7722 | 122.731 | 0.11444 | -0.09613 | 122.7859 | 122.8088 | 122.8226 | -0.27466 | 122.8226 | 122.7997 | 122.8271 | -0.27924
2561.2344 | 122.9782 | -122.6761 | 0.14648 | -0.0078584 | -0.016451 | 0.014851 | 0.036023 | -0.012211 | -0.034451 | 0.0003931 | -0.022812 | 0.016071 | -0.026034 | -0.0027579 | -0.011074 | -0.0033752 | 0.045776 | -0.041199 | -0.004578 | 0.013733 | 0.15106 | 0.009155 | -0.13733 | -0.022888 | 0.064087 | -0.054932 | 0.16022 | 0.15106 | -0.054932 | -0.1236 | 122.6852 | 122.5388 | 0.004578 | 122.6349 | 122.6898 | 0.15106 | -0.10071 | 122.6212 | 122.5525 | 0.013733 | 122.6532 | 122.6212 | 0.068664 | 0.004578 | 122.8271 | 122.7219 | 122.6715 | -0.28381 | 122.8363 | 122.8271 | 122.7402 | -0.27008
2563.0156 | 123.0103 | -122.6395 | 0.15106 | -0.00022891 | -0.01581 | 0.016133 | 0.03346 | -0.013492 | -0.035733 | -0.0011023 | -0.0075532 | 0.016284 | -0.025607 | -0.0027579 | -0.010006 | -0.001239 | 0.045776 | -0.054932 | -0.018311 | 0 | 0.13733 | 0.013733 | -0.13275 | -0.004578 | 0.050354 | -0.036621 | 0.15106 | 0.13733 | -0.045776 | -0.091553 | 122.6532 | 122.5067 | -0.013733 | 122.5845 | 122.6395 | 0.13275 | -0.10529 | 122.5937 | 122.5479 | 0 | 122.6349 | 122.6028 | 0.054932 | -0.013733 | 122.7768 | 122.6852 | 122.6212 | -0.28381 | 122.7905 | 122.7768 | 122.6898 | -0.24261
2564.7969 | 123.0194 | -122.6578 | 0.12817 | -0.0078584 | -0.013033 | 0.015065 | 0.036023 | -0.010929 | -0.034665 | 0.0003931 | -0.015182 | 0.015216 | -0.023684 | -0.00019431 | -0.0097924 | 0.0019654 | 0.032043 | -0.041199 | -0.009155 | 0 | 0.13733 | 0.018311 | -0.10986 | 0.004578 | 0.059509 | -0.045776 | 0.14648 | 0.1236 | -0.050354 | -0.086975 | 122.6761 | 122.5479 | 0.009155 | 122.6166 | 122.6578 | 0.10986 | -0.096131 | 122.6074 | 122.5708 | 0.01831 | 122.6624 | 122.612 | 0.041199 | -0.004578 | 122.7951 | 122.6898 | 122.6486 | -0.23804 | 122.8043 | 122.7814 | 122.7173 | -0.21515
2566.5781 | 122.9507 | -122.6578 | 0.14191 | -0.015487 | -0.015383 | 0.010365 | 0.037305 | -0.01157 | -0.035519 | 0.0018885 | 7.627e-05 | 0.015216 | -0.023257 | -0.0029715 | -0.010433 | -0.00081178 | 0.050354 | -0.045776 | 0.009155 | 0.027466 | 0.1236 | 0.013733 | -0.12817 | -0.032043 | 0.054932 | -0.07782 | 0.12817 | 0.13733 | -0.045776 | -0.1236 | 122.6715 | 122.5296 | -0.018311 | 122.612 | 122.6852 | 0.15564 | -0.091553 | 122.612 | 122.5342 | -0.013733 | 122.6257 | 122.58 | 0.045776 | -0.004578 | 122.7814 | 122.7081 | 122.6669 | -0.27008 | 122.7859 | 122.7951 | 122.7127 | -0.2655
2568.2969 | 122.9782 | -122.6624 | 0.16022 | -0.0078584 | -0.010256 | 0.011433 | 0.037305 | -0.013065 | -0.034665 | 0.0010339 | 7.627e-05 | 0.011798 | -0.024112 | 0.00066009 | -0.012783 | -0.0025208 | 0.018311 | -0.07782 | -0.009155 | 0 | 0.13275 | 0.013733 | -0.13275 | -0.022888 | 0.022888 | -0.073242 | 0.15106 | 0.1236 | -0.045776 | -0.11902 | 122.6761 | 122.5296 | -0.027466 | 122.5845 | 122.6624 | 0.13275 | -0.14191 | 122.6166 | 122.5433 | -0.009155 | 122.6395 | 122.5891 | 0.045777 | -0.036621 | 122.7951 | 122.6807 | 122.6532 | -0.29297 | 122.8134 | 122.7859 | 122.6852 | -0.27924
2570.0938 | 122.9874 | -122.6761 | 0.14191 | 0.0074006 | -0.01581 | 0.01421 | 0.036664 | -0.011143 | -0.03616 | 0.0018885 | 0.0077058 | 0.013935 | -0.023043 | -0.0019033 | -0.01022 | -0.0014526 | 0.032043 | -0.07782 | -0.018311 | 0 | 0.15106 | 0.004578 | -0.11444 | -0.018311 | 0.004578 | -0.07782 | 0.13733 | 0.11902 | -0.041199 | -0.10529 | 122.6807 | 122.5616 | 0.009155 | 122.5983 | 122.6761 | 0.11444 | -0.10986 | 122.6349 | 122.5708 | -0.004578 | 122.6578 | 122.5983 | 0.027466 | -0.022888 | 122.8271 | 122.7081 | 122.6578 | -0.25635 | 122.8134 | 122.7951 | 122.6807 | -0.24719
2571.875 | 122.9279 | -122.7264 | 0.18768 | -0.0078584 | -0.019655 | 0.019764 | 0.037091 | -0.011783 | -0.044491 | -0.0017431 | 7.627e-05 | 0.0090214 | -0.02518 | -0.0029715 | -0.016415 | 0.00025642 | 0.045776 | 0.013733 | 0.07782 | 0.064087 | 0.086975 | 0.036621 | -0.09613 | 0.032043 | 0.11444 | 0.050354 | 0.11444 | 0.091553 | -0.013733 | -0.086975 | 122.7631 | 122.6303 | -0.10071 | 122.7402 | 122.7905 | 0.16022 | -0.14191 | 122.7127 | 122.6395 | -0.073242 | 122.7585 | 122.7768 | 0.13733 | -0.09613 | 122.8134 | 122.7722 | 122.8043 | -0.28381 | 122.8409 | 122.818 | 122.8409 | -0.27466
2573.6562 | 122.9553 | -122.644 | 0.13733 | 0.0074006 | -0.014101 | 0.012715 | 0.035596 | -0.010929 | -0.03381 | -0.0004613 | 7.627e-05 | 0.012653 | -0.023471 | -0.0012625 | -0.011074 | -0.0042298 | 0.09613 | 0.022888 | 0.045776 | 0.050354 | 0.14191 | 0.013733 | -0.12817 | 0.059509 | 0.10986 | -0.009155 | 0.11902 | 0.11444 | -0.036621 | -0.10529 | 122.6578 | 122.5159 | 0.004578 | 122.6669 | 122.6944 | 0.17853 | -0.041199 | 122.6074 | 122.5388 | -0.01831 | 122.7036 | 122.6349 | 0.096131 | -0.022888 | 122.7859 | 122.7402 | 122.6898 | -0.2655 | 122.7631 | 122.7585 | 122.7539 | -0.24262
2575.3906 | 122.8867 | -122.7219 | 0.17395 | -0.0078584 | -0.021364 | 0.01421 | 0.038159 | -0.011997 | -0.044918 | -0.0047339 | 7.627e-05 | 0.006885 | -0.024966 | -0.0036123 | -0.015988 | 0.00068362 | 0.054932 | 0.036621 | 0.082397 | 0.050354 | 0.10986 | 0.054932 | -0.082397 | 0.045776 | 0.10986 | 0.050354 | 0.091553 | 0.10071 | -0.009155 | -0.082397 | 122.7768 | 122.6395 | -0.064087 | 122.7585 | 122.7722 | 0.13275 | -0.11902 | 122.7127 | 122.6395 | -0.082397 | 122.7676 | 122.7722 | 0.13275 | -0.073242 | 122.8317 | 122.7768 | 122.8043 | -0.25635 | 122.8134 | 122.8226 | 122.8317 | -0.25635
2577.1562 | 122.8867 | -122.699 | 0.1831 | -0.0078584 | -0.015383 | 0.013356 | 0.038373 | -0.0094336 | -0.038937 | -0.0021703 | 7.627e-05 | 0.0081668 | -0.023257 | -0.0036123 | -0.014706 | -0.0020934 | 0.10071 | 0.086975 | 0.13275 | 0.09613 | 0.11444 | 0.022888 | -0.09613 | 0.068665 | 0.19226 | 0.054932 | 0.10529 | 0.086975 | -0.036621 | -0.086975 | 122.7219 | 122.6028 | -0.068664 | 122.7859 | 122.7951 | 0.19226 | -0.082397 | 122.6624 | 122.612 | -0.077819 | 122.7676 | 122.7539 | 0.14191 | -0.09613 | 122.8134 | 122.7997 | 122.8317 | -0.27924 | 122.8043 | 122.7859 | 122.8912 | -0.27008
2578.9375 | 122.9462 | -122.6669 | 0.16937 | -0.0078584 | -0.016665 | 0.016346 | 0.037946 | -0.011356 | -0.035946 | -0.0013159 | 7.627e-05 | 0.01308 | -0.025393 | -0.0033987 | -0.012783 | -0.0042298 | 0.050354 | -0.045776 | -0.013733 | 0.018311 | 0.14191 | -0.013733 | -0.13275 | -0.032043 | 0.059509 | -0.041199 | 0.14191 | 0.13275 | -0.041199 | -0.11444 | 122.6532 | 122.5342 | -0.027466 | 122.6212 | 122.6852 | 0.15106 | -0.11902 | 122.6257 | 122.5525 | -0.027466 | 122.6349 | 122.6257 | 0.073242 | -0.036622 | 122.8088 | 122.7173 | 122.6532 | -0.30212 | 122.8088 | 122.7997 | 122.7264 | -0.28381
2580.75 | 123.0011 | -122.6349 | 0.14191 | 0.0074006 | -0.011965 | 0.013783 | 0.036023 | -0.0096472 | -0.033169 | -0.0002477 | -0.0075532 | 0.013721 | -0.026034 | -0.0040395 | -0.01022 | -0.0023072 | 0.091553 | 0.018311 | 0.050354 | 0.068665 | 0.14191 | 0 | -0.11444 | 0.022888 | 0.12817 | -0.013733 | 0.13275 | 0.1236 | -0.036621 | -0.10529 | 122.6349 | 122.5204 | 0 | 122.6532 | 122.7036 | 0.18311 | -0.050354 | 122.5983 | 122.5296 | -0.009156 | 122.6578 | 122.6212 | 0.091553 | -0.018311 | 122.7768 | 122.7264 | 122.6852 | -0.25635 | 122.7676 | 122.7585 | 122.7631 | -0.24719
2582.4688 | 122.9462 | -122.6578 | 0.15564 | -0.00022891 | -0.01581 | 0.012288 | 0.036023 | -0.013279 | -0.034237 | -3.4096e-05 | -0.0075532 | 0.017139 | -0.026461 | -0.0033987 | -0.010647 | -0.0023072 | 0.11444 | 0.004578 | 0.036621 | 0.054932 | 0.11444 | 0.009155 | -0.10986 | 0.013733 | 0.10071 | -0.032043 | 0.12817 | 0.11902 | -0.041199 | -0.10071 | 122.6669 | 122.5479 | -0.041199 | 122.6624 | 122.7127 | 0.16479 | -0.041199 | 122.6166 | 122.5571 | -0.027466 | 122.6715 | 122.6257 | 0.068665 | -0.036621 | 122.7722 | 122.7722 | 122.6944 | -0.2655 | 122.7859 | 122.7768 | 122.7585 | -0.25635
2584.2344 | 122.8867 | -122.6852 | 0.1831 | -0.00022891 | -0.016451 | 0.01656 | 0.038159 | -0.0098608 | -0.038083 | -0.0008887 | -0.0075532 | 0.013294 | -0.024112 | 0.00023289 | -0.015133 | -0.0010254 | 0.009155 | -0.041199 | 0.009155 | 0.004578 | 0.12817 | -0.004578 | -0.14648 | -0.027466 | 0.07782 | -0.045776 | 0.14191 | 0.11902 | -0.045776 | -0.11444 | 122.6807 | 122.5388 | -0.054931 | 122.644 | 122.6898 | 0.15106 | -0.17395 | 122.6395 | 122.5708 | -0.041198 | 122.6578 | 122.6395 | 0.068665 | -0.064086 | 122.8134 | 122.6944 | 122.6944 | -0.32959 | 122.8271 | 122.8043 | 122.7631 | -0.29755
2586.0312 | 122.8729 | -122.6761 | 0.19226 | -0.0078584 | -0.015169 | 0.013783 | 0.040723 | -0.013279 | -0.039578 | -0.0004613 | -0.015182 | 0.013507 | -0.02518 | -0.0025443 | -0.016415 | -0.00017078 | 0.041199 | -0.032043 | 0.041199 | 0.027466 | 0.12817 | 0.004578 | -0.11444 | -0.022888 | 0.09613 | -0.032043 | 0.15106 | 0.1236 | -0.064087 | -0.11444 | 122.6807 | 122.5616 | -0.064087 | 122.644 | 122.7036 | 0.14191 | -0.15106 | 122.612 | 122.5616 | -0.041199 | 122.6532 | 122.644 | 0.082398 | -0.068665 | 122.8043 | 122.7173 | 122.7173 | -0.3067 | 122.8271 | 122.7997 | 122.7722 | -0.3067
2587.75 | 122.9462 | -122.6395 | 0.1831 | -0.00022891 | -0.013888 | 0.011433 | 0.036023 | -0.015201 | -0.033383 | 0.0012477 | -0.0075532 | 0.020343 | -0.028598 | -0.00019431 | -0.011929 | -0.0023072 | 0.050354 | -0.054932 | -0.013733 | 0.027466 | 0.15564 | 0.004578 | -0.1236 | -0.041199 | 0.050354 | -0.073242 | 0.17853 | 0.14191 | -0.054932 | -0.11444 | 122.644 | 122.5159 | -0.027465 | 122.5845 | 122.6669 | 0.15106 | -0.13275 | 122.5845 | 122.525 | -0.004577 | 122.5983 | 122.5662 | 0.041199 | -0.041198 | 122.7951 | 122.6898 | 122.6257 | -0.3067 | 122.818 | 122.7814 | 122.6898 | -0.29755
2589.4688 | 122.8821 | -122.6624 | 0.21973 | 0.0074006 | -0.021792 | 0.01656 | 0.035382 | -0.012211 | -0.04385 | -0.0011023 | -0.0075532 | 0.015003 | -0.032656 | -0.0029715 | -0.015133 | -0.00038438 | 0.059509 | 0.027466 | 0.07782 | 0.045776 | 0.10986 | 0.022888 | -0.086975 | 0.036621 | 0.13275 | 0.036621 | 0.15106 | 0.13275 | -0.036621 | -0.07782 | 122.6852 | 122.5754 | -0.10986 | 122.6898 | 122.7081 | 0.13275 | -0.16022 | 122.6257 | 122.5845 | -0.068665 | 122.699 | 122.699 | 0.11444 | -0.086976 | 122.7722 | 122.7219 | 122.7402 | -0.3067 | 122.8134 | 122.7951 | 122.7951 | -0.29755
2591.25 | 122.905 | -122.6578 | 0.21515 | 0.0074006 | -0.016451 | 0.018483 | 0.035382 | -0.013065 | -0.040219 | -0.0036657 | 0.0077058 | 0.015216 | -0.030947 | -0.0033987 | -0.015347 | -0.0014526 | 0.064087 | 0.018311 | 0.07782 | 0.050354 | 0.11444 | 0.032043 | -0.086975 | 0.027466 | 0.14648 | 0.045776 | 0.13275 | 0.14191 | -0.013733 | -0.086975 | 122.6898 | 122.5708 | -0.10071 | 122.6761 | 122.7081 | 0.13733 | -0.15106 | 122.644 | 122.5708 | -0.082398 | 122.6852 | 122.7036 | 0.13275 | -0.073242 | 122.7722 | 122.7219 | 122.7356 | -0.30212 | 122.7905 | 122.7997 | 122.8043 | -0.30212
2592.9844 | 122.9279 | -122.6257 | 0.21057 | 0.0074006 | -0.01816 | 0.015492 | 0.039868 | -0.010074 | -0.041287 | -0.0051611 | 7.627e-05 | 0.019062 | -0.033725 | -0.0019033 | -0.01556 | -0.0020934 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.11444 | 0.041199 | -0.086975 | 0.11444 | 0.23346 | 0.11444 | 0.13733 | 0.12817 | -0.004578 | -0.068665 | 122.6669 | 122.5388 | -0.09613 | 122.7356 | 122.7264 | 0.18768 | -0.07782 | 122.6212 | 122.5571 | -0.073242 | 122.7402 | 122.7402 | 0.18311 | -0.082397 | 122.7402 | 122.7585 | 122.7676 | -0.29755 | 122.7631 | 122.7539 | 122.8592 | -0.27924
2594.7812 | 122.9874 | -122.6303 | 0.1831 | -0.0078584 | -0.014101 | 0.011219 | 0.036237 | -0.011356 | -0.036801 | -0.0013159 | -0.0075532 | 0.019275 | -0.029666 | -0.0021169 | -0.013638 | -0.0042298 | 0.15564 | 0.059509 | 0.11444 | 0.11902 | 0.091553 | 0.050354 | -0.086975 | 0.10529 | 0.1831 | 0.073242 | 0.11902 | 0.10071 | 0.004578 | -0.064087 | 122.6807 | 122.5433 | -0.091552 | 122.6898 | 122.7493 | 0.20599 | -0.027465 | 122.6349 | 122.5662 | -0.064086 | 122.7356 | 122.7036 | 0.13733 | -0.082397 | 122.7219 | 122.7859 | 122.7448 | -0.27008 | 122.7493 | 122.731 | 122.8134 | -0.24719
2596.5625 | 122.9279 | -122.6578 | 0.20142 | -0.00022891 | -0.017306 | 0.017628 | 0.037305 | -0.010288 | -0.041287 | -0.0023839 | 7.627e-05 | 0.014576 | -0.028384 | -0.0036123 | -0.014919 | -0.0020934 | 0.11444 | 0.073242 | 0.13275 | 0.091553 | 0.11444 | 0.036621 | -0.091553 | 0.11902 | 0.20599 | 0.091553 | 0.1236 | 0.10986 | -0.004578 | -0.064087 | 122.6944 | 122.5662 | -0.086975 | 122.731 | 122.7493 | 0.18311 | -0.086975 | 122.6532 | 122.5937 | -0.07782 | 122.7768 | 122.7493 | 0.15564 | -0.091553 | 122.7722 | 122.7722 | 122.7905 | -0.29297 | 122.7814 | 122.7676 | 122.8638 | -0.2655
2598.3594 | 122.9782 | -122.6166 | 0.16937 | -0.0078584 | -0.012392 | 0.013569 | 0.033887 | -0.01157 | -0.032101 | -0.0002477 | -0.0075532 | 0.021411 | -0.034579 | 0.0010873 | -0.0091516 | -0.0020934 | 0.041199 | -0.073242 | -0.022888 | 0.009155 | 0.16022 | 0.009155 | -0.11902 | -0.013733 | 0.022888 | -0.07782 | 0.18768 | 0.15564 | -0.045776 | -0.10986 | 122.6257 | 122.4976 | -0.009156 | 122.5433 | 122.6257 | 0.12817 | -0.12817 | 122.5708 | 122.5067 | 0.01831 | 122.6028 | 122.5388 | 0.032043 | -0.013733 | 122.7768 | 122.6578 | 122.5937 | -0.28839 | 122.8043 | 122.7722 | 122.6395 | -0.27924
2600.0781 | 122.9919 | -122.6303 | 0.16022 | -0.0078584 | -0.008547 | 0.013997 | 0.035169 | -0.011997 | -0.033169 | 0.0001795 | 0.0077058 | 0.020557 | -0.027957 | 0.00023289 | -0.0097924 | -0.0016662 | 0.045776 | -0.082397 | -0.009155 | -0.004578 | 0.15106 | 0 | -0.11444 | -0.013733 | 0.027466 | -0.082397 | 0.17395 | 0.14648 | -0.054932 | -0.11444 | 122.6303 | 122.5159 | -0.009155 | 122.5479 | 122.6257 | 0.10986 | -0.11444 | 122.5754 | 122.5159 | 0.013733 | 122.6166 | 122.5479 | 0.032044 | -0.013733 | 122.7814 | 122.6761 | 122.6212 | -0.27466 | 122.8043 | 122.7768 | 122.6578 | -0.27466
2601.8594 | 122.9965 | -122.6532 | 0.15564 | -0.00022891 | -0.016238 | 0.013356 | 0.035382 | -0.010074 | -0.03381 | 0.0006067 | -0.0075532 | 0.02248 | -0.028598 | -0.00083531 | -0.0097924 | -0.0018798 | 0.050354 | -0.064087 | -0.013733 | 0.013733 | 0.14191 | -0.004578 | -0.1236 | -0.027466 | 0.036621 | -0.073242 | 0.17395 | 0.16022 | -0.050354 | -0.11444 | 122.6486 | 122.5296 | -0.013733 | 122.5891 | 122.6669 | 0.13733 | -0.10529 | 122.6028 | 122.5388 | 0.01831 | 122.6257 | 122.58 | 0.041199 | 0.004577 | 122.7951 | 122.7036 | 122.6395 | -0.27924 | 122.8271 | 122.8134 | 122.6898 | -0.27008
2603.6406 | 123.024 | -122.6212 | 0.1831 | -0.00022891 | -0.015169 | 0.015919 | 0.035809 | -0.012211 | -0.036801 | 0.0012477 | 7.627e-05 | 0.020557 | -0.029025 | -0.0016897 | -0.011715 | 0.00025642 | 0.068665 | -0.004578 | 0.050354 | 0.045776 | 0.10529 | 0.041199 | -0.10529 | 0.073242 | 0.14648 | 0.036621 | 0.15106 | 0.10986 | -0.009155 | -0.073242 | 122.6624 | 122.5159 | -0.077819 | 122.6166 | 122.6669 | 0.15106 | -0.11444 | 122.612 | 122.5479 | -0.032043 | 122.6944 | 122.6578 | 0.10986 | -0.073242 | 122.7264 | 122.6898 | 122.6715 | -0.28839 | 122.7722 | 122.731 | 122.7676 | -0.25635
2605.4375 | 122.9279 | -122.6624 | 0.19684 | 0.0074006 | -0.017519 | 0.016346 | 0.040082 | -0.011997 | -0.042355 | 0.0006067 | -0.0075532 | 0.016712 | -0.031802 | -0.0031851 | -0.013851 | -0.00017078 | 0.10529 | 0.1236 | 0.16022 | 0.10071 | 0.09613 | 0.050354 | -0.10071 | 0.086975 | 0.23346 | 0.086975 | 0.11902 | 0.11444 | -0.013733 | -0.07782 | 122.7127 | 122.5616 | -0.10071 | 122.7859 | 122.7631 | 0.20142 | -0.091552 | 122.6486 | 122.5845 | -0.077819 | 122.7493 | 122.7493 | 0.16479 | -0.082397 | 122.7585 | 122.7676 | 122.8226 | -0.29755 | 122.7814 | 122.7768 | 122.8958 | -0.27466
2607.1562 | 122.9965 | -122.644 | 0.1831 | -0.0078584 | -0.014101 | 0.01656 | 0.035382 | -0.012424 | -0.034878 | -0.0004613 | 7.627e-05 | 0.020557 | -0.030307 | -0.0027579 | -0.010433 | -0.0016662 | 0.027466 | -0.07782 | -0.041199 | 0.009155 | 0.14191 | 0.004578 | -0.13275 | -0.018311 | 0.032043 | -0.082397 | 0.17853 | 0.15106 | -0.032043 | -0.10986 | 122.6486 | 122.5113 | -0.041198 | 122.5662 | 122.6532 | 0.14191 | -0.15564 | 122.612 | 122.5342 | -0.004577 | 122.6257 | 122.5616 | 0.027466 | -0.032043 | 122.7859 | 122.6715 | 122.6028 | -0.31586 | 122.8226 | 122.7951 | 122.6761 | -0.29297
2608.9375 | 122.9187 | -122.6578 | 0.19226 | -0.00022891 | -0.018587 | 0.016346 | 0.039441 | -0.013065 | -0.041287 | -0.0023839 | 0.0077058 | 0.016498 | -0.028811 | -0.0019033 | -0.016628 | -0.0020934 | 0.12817 | 0.12817 | 0.15106 | 0.10071 | 0.10529 | 0.054932 | -0.09613 | 0.07782 | 0.23346 | 0.086975 | 0.13275 | 0.12817 | 0.004578 | -0.091553 | 122.7127 | 122.5616 | -0.086975 | 122.7859 | 122.7585 | 0.19684 | -0.064087 | 122.6624 | 122.5662 | -0.05951 | 122.7356 | 122.7448 | 0.17853 | -0.064087 | 122.7631 | 122.7859 | 122.8088 | -0.28839 | 122.7905 | 122.7859 | 122.8912 | -0.28381
2610.7344 | 122.8867 | -122.6624 | 0.21057 | -0.015487 | -0.017733 | 0.015492 | 0.0388 | -0.011783 | -0.038083 | -0.0028113 | -0.0075532 | 0.020984 | -0.033297 | -0.0025443 | -0.011501 | -0.0027344 | 0.050354 | 0 | 0.027466 | 0.036621 | 0.13733 | 0.004578 | -0.13733 | -0.032043 | 0.10986 | -0.045776 | 0.17395 | 0.15106 | -0.041199 | -0.09613 | 122.6669 | 122.525 | -0.073242 | 122.6624 | 122.699 | 0.17395 | -0.16022 | 122.6212 | 122.5662 | -0.036621 | 122.6303 | 122.6166 | 0.050354 | -0.059509 | 122.7997 | 122.7127 | 122.6898 | -0.3479 | 122.8363 | 122.8134 | 122.7722 | -0.3067
2612.5312 | 122.9874 | -122.6303 | 0.1831 | -0.00022891 | -0.013888 | 0.014424 | 0.034955 | -0.012852 | -0.035092 | -0.0015295 | 7.627e-05 | 0.022693 | -0.03287 | -0.0031851 | -0.01022 | -0.00081178 | 0.050354 | -0.082397 | -0.041199 | 0 | 0.13733 | 0.018311 | -0.11902 | -0.022888 | 0.022888 | -0.073242 | 0.16022 | 0.16937 | -0.032043 | -0.10986 | 122.6486 | 122.5113 | -0.045776 | 122.5479 | 122.6303 | 0.11902 | -0.13275 | 122.5983 | 122.5204 | -0.022888 | 122.6074 | 122.5571 | 0.036621 | -0.013732 | 122.7676 | 122.6807 | 122.5891 | -0.30212 | 122.7905 | 122.7997 | 122.6532 | -0.29297
2614.2656 | 122.9874 | -122.6349 | 0.18768 | -0.0078584 | -0.012392 | 0.015065 | 0.035382 | -0.011997 | -0.036801 | -0.0006751 | 7.627e-05 | 0.02312 | -0.031588 | -0.0012625 | -0.012356 | 0.00068362 | 0.050354 | -0.064087 | -0.009155 | 0.013733 | 0.13733 | 0 | -0.14648 | -0.036621 | 0.082397 | -0.059509 | 0.17853 | 0.15106 | -0.036621 | -0.09613 | 122.6349 | 122.4884 | -0.050354 | 122.5708 | 122.6486 | 0.16022 | -0.13733 | 122.5983 | 122.5388 | -0.009155 | 122.5983 | 122.5754 | 0.036621 | -0.036621 | 122.7722 | 122.6852 | 122.6257 | -0.33417 | 122.8134 | 122.7859 | 122.7173 | -0.28381
2616.0312 | 122.9874 | -122.6624 | 0.16937 | -0.00022891 | -0.014315 | 0.015065 | 0.038159 | -0.011783 | -0.037442 | -0.0023839 | 7.627e-05 | 0.023548 | -0.031161 | -0.0029715 | -0.013638 | -0.0014526 | 0.027466 | -0.045776 | -0.013733 | 0.013733 | 0.15564 | 0.004578 | -0.14648 | -0.022888 | 0.082397 | -0.045776 | 0.16022 | 0.16479 | -0.059509 | -0.10071 | 122.6669 | 122.5159 | -0.013733 | 122.6166 | 122.6761 | 0.16022 | -0.14191 | 122.6028 | 122.5616 | -0.009156 | 122.6395 | 122.6166 | 0.054932 | -0.004578 | 122.818 | 122.6898 | 122.6486 | -0.31586 | 122.8226 | 122.8271 | 122.7448 | -0.27008
2617.8125 | 123.0011 | -122.6578 | 0.15106 | 0.0074006 | -0.017306 | 0.013356 | 0.035382 | -0.012211 | -0.037869 | -0.0006751 | -0.0075532 | 0.023548 | -0.035006 | -0.0016897 | -0.011501 | -0.0018798 | 0.1236 | 0.059509 | 0.10071 | 0.091553 | 0.10529 | 0.054932 | -0.07782 | 0.09613 | 0.16479 | 0.064087 | 0.09613 | 0.10071 | 0.013733 | -0.068665 | 122.7127 | 122.58 | -0.045776 | 122.7173 | 122.7493 | 0.16937 | -0.027466 | 122.6715 | 122.5891 | -0.054932 | 122.7539 | 122.7219 | 0.13275 | -0.050354 | 122.7631 | 122.7814 | 122.7585 | -0.22888 | 122.7539 | 122.7585 | 122.8226 | -0.21973
2619.6094 | 123.0148 | -122.6532 | 0.14648 | -0.00022891 | -0.015597 | 0.013142 | 0.036023 | -0.0094336 | -0.035733 | -0.0004613 | 7.627e-05 | 0.026752 | -0.034793 | -0.00083531 | -0.01257 | -0.0023072 | 0.091553 | 0.027466 | 0.036621 | 0.059509 | 0.13733 | 0.004578 | -0.12817 | 0.036621 | 0.11902 | -0.027466 | 0.13733 | 0.11444 | -0.045776 | -0.10529 | 122.6578 | 122.525 | -0.009155 | 122.6807 | 122.7127 | 0.18768 | -0.054931 | 122.6074 | 122.5479 | -0.009155 | 122.6898 | 122.6257 | 0.07782 | -0.032043 | 122.7905 | 122.7448 | 122.6898 | -0.27466 | 122.7905 | 122.7676 | 122.7722 | -0.25177
2621.3438 | 122.9279 | -122.6715 | 0.17395 | -0.00022891 | -0.019228 | 0.014424 | 0.038587 | -0.0096472 | -0.04385 | -0.0021703 | -0.0075532 | 0.024402 | -0.038424 | -0.0029715 | -0.013638 | 4.2822e-05 | 0.073242 | 0.059509 | 0.11444 | 0.073242 | 0.10986 | 0.032043 | -0.10529 | 0.068665 | 0.1831 | 0.091553 | 0.1236 | 0.091553 | -0.022888 | -0.086975 | 122.7036 | 122.5662 | -0.064087 | 122.731 | 122.7448 | 0.17853 | -0.10071 | 122.6486 | 122.5845 | -0.050354 | 122.7402 | 122.7631 | 0.17853 | -0.082397 | 122.7814 | 122.7448 | 122.7859 | -0.27924 | 122.7951 | 122.7631 | 122.8546 | -0.26092
2623.125 | 122.9141 | -122.6761 | 0.1831 | 0.0074006 | -0.02051 | 0.016774 | 0.035382 | -0.013279 | -0.042782 | -0.0011023 | 7.627e-05 | 0.024402 | -0.039279 | -0.0025443 | -0.013638 | -0.0010254 | 0.064087 | 0.022888 | 0.082397 | 0.068665 | 0.11444 | 0.045776 | -0.10071 | 0.050354 | 0.13275 | 0.059509 | 0.10986 | 0.10986 | 0 | -0.091553 | 122.7219 | 122.5754 | -0.068664 | 122.699 | 122.7448 | 0.16937 | -0.11902 | 122.6761 | 122.5845 | -0.073242 | 122.7264 | 122.7356 | 0.15106 | -0.073242 | 122.7905 | 122.7402 | 122.7585 | -0.28381 | 122.7859 | 122.7859 | 122.8088 | -0.27466
2624.8438 | 123.0057 | -122.6257 | 0.15106 | -0.00022891 | -0.015169 | 0.012288 | 0.034741 | -0.010502 | -0.032956 | -0.0011023 | 7.627e-05 | 0.031024 | -0.03757 | -0.00062151 | -0.0097924 | -0.0027344 | 0.091553 | 0 | 0.022888 | 0.054932 | 0.14191 | 0.013733 | -0.11902 | 0.027466 | 0.11444 | -0.018311 | 0.13275 | 0.1236 | -0.050354 | -0.1236 | 122.6395 | 122.5067 | -0.009155 | 122.6257 | 122.6807 | 0.17395 | -0.059509 | 122.5754 | 122.5021 | -0.018311 | 122.6532 | 122.6074 | 0.10528 | -0.027466 | 122.7676 | 122.7173 | 122.6486 | -0.27008 | 122.7585 | 122.7493 | 122.7402 | -0.27466
2626.6406 | 122.9645 | -122.6532 | 0.16022 | 0.0074006 | -0.013247 | 0.014424 | 0.034955 | -0.0087926 | -0.034665 | -0.0036657 | 7.627e-05 | 0.026966 | -0.039492 | -0.0016897 | -0.0074426 | -0.0031616 | 0.059509 | -0.004578 | 0.013733 | 0.041199 | 0.1236 | 0.032043 | -0.11444 | -0.004578 | 0.041199 | -0.064087 | 0.14648 | 0.11902 | -0.050354 | -0.12817 | 122.6852 | 122.5388 | -0.036621 | 122.6486 | 122.6944 | 0.15564 | -0.10071 | 122.6028 | 122.525 | -0.013733 | 122.6486 | 122.5891 | 0.064087 | -0.041198 | 122.7768 | 122.7127 | 122.6669 | -0.27466 | 122.7997 | 122.7722 | 122.6944 | -0.28839
2628.4219 | 122.85 | -122.7081 | 0.19226 | 0.0074006 | -0.015169 | 0.015706 | 0.037732 | -0.012211 | -0.042355 | -0.0017431 | -0.015182 | 0.023761 | -0.036502 | -0.0044669 | -0.01257 | 0.00025642 | 0.10071 | 0.073242 | 0.10529 | 0.086975 | 0.091553 | 0.032043 | -0.091553 | 0.018311 | 0.15106 | 0.032043 | 0.10986 | 0.11444 | -0.022888 | -0.10071 | 122.7402 | 122.6166 | -0.10071 | 122.7814 | 122.7951 | 0.17853 | -0.091553 | 122.6852 | 122.6074 | -0.082398 | 122.7264 | 122.7402 | 0.13275 | -0.07782 | 122.7997 | 122.8088 | 122.8134 | -0.28381 | 122.818 | 122.8226 | 122.8592 | -0.29297
2630.1562 | 122.9599 | -122.6486 | 0.13275 | -0.0078584 | -0.014529 | 0.012501 | 0.03645 | -0.011356 | -0.033383 | -0.0006751 | 0.0077058 | 0.028247 | -0.034579 | -0.0031851 | -0.010433 | -0.0010254 | 0.10529 | 0.018311 | 0.054932 | 0.054932 | 0.12817 | 0.013733 | -0.1236 | 0.036621 | 0.11444 | -0.013733 | 0.1236 | 0.12817 | -0.027466 | -0.10986 | 122.6624 | 122.525 | -0.004577 | 122.6669 | 122.7036 | 0.17853 | -0.027465 | 122.6212 | 122.5388 | -0.009155 | 122.6852 | 122.6349 | 0.09613 | -0.004577 | 122.7768 | 122.7539 | 122.7036 | -0.25635 | 122.7722 | 122.7768 | 122.7631 | -0.24261
2631.9375 | 122.9828 | -122.6852 | 0.16022 | -0.00022891 | -0.01581 | 0.013997 | 0.034314 | -0.011997 | -0.034451 | 0.0001795 | 7.627e-05 | 0.028461 | -0.03757 | 0.00066009 | -0.0095788 | -0.0016662 | 0.082397 | 0.018311 | 0.050354 | 0.054932 | 0.14191 | 0.018311 | -0.11902 | 0.032043 | 0.12817 | -0.009155 | 0.13275 | 0.10529 | -0.050354 | -0.086975 | 122.7036 | 122.5662 | -0.01831 | 122.7036 | 122.7402 | 0.17395 | -0.07782 | 122.6349 | 122.5983 | -0.027466 | 122.7173 | 122.6761 | 0.07782 | -0.054931 | 122.8271 | 122.7676 | 122.7356 | -0.27924 | 122.818 | 122.7905 | 122.8134 | -0.24719
2633.7344 | 123.0011 | -122.6578 | 0.12817 | -0.00022891 | -0.011965 | 0.012501 | 0.038159 | -0.011143 | -0.035092 | -3.4096e-05 | -0.022812 | 0.026966 | -0.036074 | -0.0014761 | -0.011074 | -0.0023072 | 0.07782 | 0.013733 | 0.045776 | 0.041199 | 0.13733 | 0.013733 | -0.13275 | 0.022888 | 0.12817 | -0.009155 | 0.1236 | 0.10986 | -0.041199 | -0.1236 | 122.6715 | 122.525 | 0.009155 | 122.6715 | 122.699 | 0.17395 | -0.050354 | 122.6166 | 122.5342 | -0.004578 | 122.6807 | 122.6486 | 0.11444 | -0.018311 | 122.7951 | 122.7356 | 122.7036 | -0.26093 | 122.7814 | 122.7676 | 122.7859 | -0.25177
2635.5312 | 122.9965 | -122.6807 | 0.14648 | -0.00022891 | -0.016878 | 0.015065 | 0.037732 | -0.010288 | -0.039151 | 0.0012477 | 0.0077058 | 0.025684 | -0.035861 | -0.0016897 | -0.012142 | -0.001239 | 0.10529 | 0.07782 | 0.12817 | 0.10071 | 0.09613 | 0.068665 | -0.091553 | 0.09613 | 0.16479 | 0.086975 | 0.09613 | 0.082397 | -0.009155 | -0.082397 | 122.7493 | 122.5891 | -0.050354 | 122.7585 | 122.7814 | 0.19226 | -0.041198 | 122.6715 | 122.5983 | -0.050354 | 122.7768 | 122.7676 | 0.16937 | -0.064087 | 122.7768 | 122.7859 | 122.8088 | -0.23804 | 122.7768 | 122.7631 | 122.8455 | -0.22888
2637.25 | 122.9507 | -122.6486 | 0.13733 | -0.00022891 | -0.012392 | 0.013997 | 0.035382 | -0.010502 | -0.03616 | 0.0014613 | 7.627e-05 | 0.028888 | -0.037356 | -0.0016897 | -0.010647 | -0.002948 | 0.10071 | 0.013733 | 0.041199 | 0.054932 | 0.14191 | 0.004578 | -0.1236 | 0.018311 | 0.07782 | -0.032043 | 0.1236 | 0.11902 | -0.027466 | -0.10529 | 122.6532 | 122.525 | 0.004578 | 122.6624 | 122.7036 | 0.17853 | -0.036621 | 122.6212 | 122.5433 | -0.013733 | 122.6669 | 122.6166 | 0.073243 | -0.01831 | 122.7905 | 122.7493 | 122.6898 | -0.26093 | 122.7722 | 122.7676 | 122.7264 | -0.24262
2639.0156 | 123.024 | -122.6624 | 0.14648 | 0.0074006 | -0.017092 | 0.015706 | 0.035382 | -0.011997 | -0.039364 | -0.0006751 | -0.0075532 | 0.026111 | -0.037997 | -0.0014761 | -0.011501 | -0.0016662 | 0.082397 | 0.032043 | 0.07782 | 0.068665 | 0.12817 | 0.041199 | -0.10071 | 0.082397 | 0.14191 | 0.054932 | 0.10529 | 0.10071 | -0.018311 | -0.073242 | 122.7036 | 122.5616 | -0.01831 | 122.6944 | 122.731 | 0.16937 | -0.064087 | 122.644 | 122.5891 | -0.041198 | 122.7448 | 122.7173 | 0.12817 | -0.045776 | 122.7905 | 122.7448 | 122.7402 | -0.24719 | 122.7676 | 122.7631 | 122.8043 | -0.21973
2640.7656 | 123.0194 | -122.6669 | 0.12817 | 0.0074006 | -0.015169 | 0.012288 | 0.034741 | -0.011997 | -0.03851 | -0.0028113 | 7.627e-05 | 0.029316 | -0.03757 | -0.0014761 | -0.011501 | -0.001239 | 0.082397 | -0.013733 | 0.064087 | 0.045776 | 0.12817 | 0.027466 | -0.11444 | 0.059509 | 0.12817 | 0.050354 | 0.09613 | 0.09613 | -0.022888 | -0.073242 | 122.6944 | 122.5525 | 0 | 122.6532 | 122.7127 | 0.16022 | -0.045777 | 122.644 | 122.5937 | -0.032044 | 122.7264 | 122.7173 | 0.1236 | -0.032044 | 122.7951 | 122.7493 | 122.731 | -0.24262 | 122.7631 | 122.7631 | 122.7951 | -0.20142
2642.5625 | 123.0103 | -122.6761 | 0.13733 | -0.00022891 | -0.01816 | 0.015065 | 0.033673 | -0.012852 | -0.038937 | -0.0011023 | -0.015182 | 0.027179 | -0.039492 | -0.0033987 | -0.011074 | -0.0027344 | 0.13733 | 0.059509 | 0.10071 | 0.09613 | 0.091553 | 0.045776 | -0.086975 | 0.09613 | 0.16022 | 0.082397 | 0.082397 | 0.073242 | -0.013733 | -0.073242 | 122.7219 | 122.5891 | -0.045776 | 122.7356 | 122.7722 | 0.1831 | 0 | 122.6624 | 122.6028 | -0.054932 | 122.7722 | 122.7585 | 0.15564 | -0.064087 | 122.7676 | 122.8134 | 122.7768 | -0.2243 | 122.7585 | 122.7493 | 122.8363 | -0.21057
2644.3438 | 122.8867 | -122.7127 | 0.16022 | -0.00022891 | -0.016451 | 0.015065 | 0.034955 | -0.012211 | -0.040432 | -0.0013159 | 7.627e-05 | 0.026325 | -0.039492 | -0.0040395 | -0.012142 | -0.00081178 | 0.10986 | 0.082397 | 0.13275 | 0.086975 | 0.086975 | 0.041199 | -0.091553 | 0.091553 | 0.15564 | 0.082397 | 0.091553 | 0.07782 | -0.004578 | -0.073242 | 122.7539 | 122.6212 | -0.073242 | 122.7951 | 122.7997 | 0.17853 | -0.050354 | 122.7081 | 122.6395 | -0.068664 | 122.8043 | 122.7951 | 0.15564 | -0.082397 | 122.7997 | 122.8226 | 122.8455 | -0.25177 | 122.8043 | 122.7905 | 122.8683 | -0.23346
2646.1406 | 122.8775 | -122.6944 | 0.1831 | -0.00022891 | -0.017092 | 0.014637 | 0.038587 | -0.011356 | -0.041501 | -0.0028113 | -0.015182 | 0.024829 | -0.038851 | -0.0059621 | -0.014919 | -0.0035888 | 0.11444 | 0.091553 | 0.14191 | 0.09613 | 0.091553 | 0.041199 | -0.10529 | 0.068665 | 0.19226 | 0.086975 | 0.10071 | 0.091553 | -0.027466 | -0.091553 | 122.7356 | 122.5891 | -0.091552 | 122.7859 | 122.7905 | 0.20142 | -0.068664 | 122.6669 | 122.6028 | -0.082397 | 122.7631 | 122.7814 | 0.17853 | -0.091552 | 122.7859 | 122.8088 | 122.8363 | -0.28839 | 122.7951 | 122.7859 | 122.8867 | -0.27466
2647.9219 | 122.937 | -122.6761 | 0.16937 | -0.00022891 | -0.02051 | 0.013356 | 0.037305 | -0.011997 | -0.042996 | -0.0030249 | 7.627e-05 | 0.025257 | -0.038424 | -0.0040395 | -0.014065 | -0.0014526 | 0.064087 | 0.009155 | 0.07782 | 0.064087 | 0.11444 | 0.032043 | -0.10529 | 0.054932 | 0.13733 | 0.073242 | 0.091553 | 0.10071 | -0.018311 | -0.086975 | 122.7081 | 122.5708 | -0.054932 | 122.6852 | 122.7402 | 0.16937 | -0.10529 | 122.6578 | 122.5891 | -0.07782 | 122.731 | 122.7493 | 0.16022 | -0.068665 | 122.7905 | 122.7402 | 122.7539 | -0.27466 | 122.7676 | 122.7768 | 122.8134 | -0.25635
2649.7031 | 123.0011 | -122.6669 | 0.11444 | -0.0078584 | -0.01346 | 0.013783 | 0.036878 | -0.011783 | -0.034451 | -0.0008887 | 7.627e-05 | 0.032093 | -0.03992 | -0.0012625 | -0.010861 | -0.0076476 | 0.059509 | -0.041199 | -0.013733 | 0.032043 | 0.13275 | -0.004578 | -0.15106 | -0.009155 | 0.086975 | -0.036621 | 0.12817 | 0.10986 | -0.045776 | -0.10986 | 122.6624 | 122.5159 | 0.01831 | 122.6257 | 122.699 | 0.18311 | -0.054932 | 122.6212 | 122.5571 | 0.013733 | 122.6578 | 122.6303 | 0.073242 | -0.004578 | 122.7997 | 122.7264 | 122.6532 | -0.2655 | 122.7951 | 122.7768 | 122.7539 | -0.2243
2651.4375 | 123.0148 | -122.6807 | 0.1236 | 0.0074006 | -0.01282 | 0.013356 | 0.037518 | -0.014774 | -0.035733 | -0.0008887 | -0.0075532 | 0.030811 | -0.038638 | 0.00066009 | -0.011288 | -0.0061524 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.1236 | 0.027466 | -0.13275 | 0 | 0.013733 | -0.054932 | 0.13275 | 0.11902 | -0.045776 | -0.11444 | 122.7081 | 122.5479 | 0 | 122.6212 | 122.699 | 0.15106 | -0.086975 | 122.6349 | 122.5662 | 0.009155 | 122.6807 | 122.6257 | 0.059509 | -0.004577 | 122.8043 | 122.7173 | 122.6669 | -0.25635 | 122.8134 | 122.7997 | 122.6944 | -0.23804
2653.2031 | 122.8821 | -122.731 | 0.16937 | -0.015487 | -0.020083 | 0.014637 | 0.033887 | -0.010502 | -0.041287 | -0.0030249 | -0.022812 | 0.026752 | -0.040133 | -0.0029715 | -0.01321 | -0.00081178 | 0.082397 | 0.045776 | 0.07782 | 0.050354 | 0.10529 | 0.041199 | -0.091553 | 0.050354 | 0.12817 | 0.045776 | 0.07782 | 0.091553 | 0.009155 | -0.068665 | 122.7722 | 122.6395 | -0.064087 | 122.7768 | 122.7814 | 0.14191 | -0.086976 | 122.7402 | 122.6624 | -0.091553 | 122.7814 | 122.7768 | 0.11444 | -0.07782 | 122.8363 | 122.8134 | 122.8088 | -0.26093 | 122.8088 | 122.8226 | 122.8592 | -0.23804
2654.9375 | 122.8043 | -122.7127 | 0.17853 | -0.00022891 | -0.01581 | 0.015065 | 0.040296 | -0.011997 | -0.042355 | -0.0017431 | 7.627e-05 | 0.027607 | -0.036288 | 0.00044649 | -0.01556 | -0.0035888 | 0.068665 | 0.018311 | 0.068665 | 0.068665 | 0.11902 | 0.054932 | -0.09613 | 0.032043 | 0.10986 | 0.050354 | 0.091553 | 0.10071 | -0.013733 | -0.086975 | 122.7676 | 122.6166 | -0.059509 | 122.731 | 122.7814 | 0.16479 | -0.10986 | 122.699 | 122.6257 | -0.086975 | 122.7448 | 122.7631 | 0.13733 | -0.07782 | 122.8317 | 122.7814 | 122.7814 | -0.27466 | 122.8043 | 122.8134 | 122.8226 | -0.2655
2656.7188 | 123.0194 | -122.6761 | 0.13275 | -0.00022891 | -0.014742 | 0.013783 | 0.034955 | -0.012424 | -0.035305 | -0.0006751 | 7.627e-05 | 0.033374 | -0.040347 | 0.00023289 | -0.0097924 | -0.004016 | 0.073242 | -0.054932 | -0.009155 | 0.018311 | 0.13275 | 0.022888 | -0.13733 | 0.009155 | 0.036621 | -0.041199 | 0.11444 | 0.091553 | -0.036621 | -0.09613 | 122.699 | 122.5388 | 0 | 122.6212 | 122.6944 | 0.15564 | -0.059509 | 122.6395 | 122.58 | -0.01831 | 122.6852 | 122.6349 | 0.054931 | -0.041198 | 122.8088 | 122.7493 | 122.6669 | -0.27008 | 122.7905 | 122.7676 | 122.7127 | -0.22888
2658.4375 | 122.9141 | -122.7402 | 0.1831 | -0.0078584 | -0.018374 | 0.01421 | 0.034101 | -0.015415 | -0.041928 | -0.0030249 | -0.0075532 | 0.028461 | -0.040774 | -0.00019431 | -0.013851 | -0.0014526 | 0.068665 | 0.018311 | 0.068665 | 0.054932 | 0.10986 | 0.032043 | -0.082397 | 0.036621 | 0.11902 | 0.050354 | 0.10986 | 0.073242 | -0.018311 | -0.09613 | 122.7722 | 122.6578 | -0.073242 | 122.7585 | 122.7951 | 0.13733 | -0.11444 | 122.7219 | 122.644 | -0.073242 | 122.7768 | 122.7905 | 0.14648 | -0.10986 | 122.85 | 122.8088 | 122.8088 | -0.2655 | 122.85 | 122.8134 | 122.8592 | -0.27924
2660.2188 | 123.0011 | -122.6669 | 0.13275 | -0.00022891 | -0.0096152 | 0.015278 | 0.034955 | -0.010288 | -0.031887 | -0.0006751 | -0.0075532 | 0.031238 | -0.037783 | -0.0016897 | -0.008938 | -0.004657 | 0.1236 | 0 | 0.045776 | 0.059509 | 0.14648 | 0.027466 | -0.12817 | 0.032043 | 0.11444 | -0.022888 | 0.14191 | 0.13733 | -0.045776 | -0.11444 | 122.6944 | 122.5388 | 0.013733 | 122.6669 | 122.7264 | 0.18768 | -0.009155 | 122.6212 | 122.5525 | 0.009156 | 122.699 | 122.644 | 0.091553 | 0.004578 | 122.8134 | 122.7905 | 122.7127 | -0.26093 | 122.8088 | 122.8043 | 122.7814 | -0.24719
2662.0156 | 123.0331 | -122.6852 | 0.13733 | 0.0074006 | -0.015597 | 0.013783 | 0.035169 | -0.012424 | -0.035519 | 0.0003931 | 0.0077058 | 0.031238 | -0.039706 | 0.00044649 | -0.0095788 | -0.0031616 | 0.073242 | -0.041199 | 0.018311 | 0.027466 | 0.14191 | 0.027466 | -0.10986 | 0.045776 | 0.09613 | 0.009155 | 0.10071 | 0.086975 | -0.013733 | -0.091553 | 122.7127 | 122.5754 | 0.004578 | 122.644 | 122.7127 | 0.13733 | -0.064087 | 122.6715 | 122.5937 | -0.036621 | 122.731 | 122.6944 | 0.10071 | -0.050354 | 122.8271 | 122.7585 | 122.7036 | -0.24719 | 122.7859 | 122.7722 | 122.7814 | -0.22888
2663.75 | 123.0011 | -122.6669 | 0.13275 | -0.0078584 | -0.017092 | 0.01421 | 0.035809 | -0.010074 | -0.039151 | -0.0011023 | 7.627e-05 | 0.031024 | -0.036929 | -0.0014761 | -0.010433 | -0.0014526 | 0.13733 | 0.068665 | 0.11902 | 0.10071 | 0.10529 | 0.041199 | -0.091553 | 0.09613 | 0.15106 | 0.064087 | 0.086975 | 0.07782 | -0.018311 | -0.064087 | 122.7081 | 122.5754 | -0.027465 | 122.7356 | 122.7676 | 0.19226 | 0.004578 | 122.6486 | 122.6028 | -0.045776 | 122.7631 | 122.731 | 0.12817 | -0.054931 | 122.7722 | 122.8043 | 122.7859 | -0.2243 | 122.7539 | 122.7448 | 122.818 | -0.19684
2665.5469 | 122.9233 | -122.6898 | 0.16479 | -0.0078584 | -0.021792 | -0.0067248 | 0.034955 | -0.0098608 | -0.042782 | -0.0019567 | 0.0077058 | 0.02547 | -0.042697 | -0.0027579 | -0.014919 | 4.2822e-05 | 0.082397 | 0.045776 | 0.09613 | 0.068665 | 0.10529 | 0.041199 | -0.10071 | 0.073242 | 0.17853 | 0.082397 | 0.09613 | 0.082397 | -0.018311 | -0.073242 | 122.731 | 122.5891 | -0.059509 | 122.7356 | 122.7585 | 0.16937 | -0.082398 | 122.6715 | 122.6166 | -0.068665 | 122.7631 | 122.7722 | 0.15564 | -0.082398 | 122.7951 | 122.7722 | 122.7859 | -0.2655 | 122.7859 | 122.7722 | 122.8683 | -0.23804
2667.3281 | 122.9095 | -122.6852 | 0.17395 | -0.0078584 | -0.017733 | 0.015706 | 0.038587 | -0.013279 | -0.041501 | -0.0023839 | -0.0075532 | 0.026325 | -0.036288 | -0.0027579 | -0.01556 | -0.004016 | 0.14191 | 0.1236 | 0.14191 | 0.091553 | 0.10986 | 0.050354 | -0.10071 | 0.086975 | 0.21973 | 0.086975 | 0.091553 | 0.073242 | 0.013733 | -0.082397 | 122.7356 | 122.5845 | -0.064087 | 122.8088 | 122.7768 | 0.19226 | -0.032043 | 122.699 | 122.6028 | -0.082397 | 122.7722 | 122.7722 | 0.16937 | -0.10071 | 122.7951 | 122.8271 | 122.8271 | -0.27466 | 122.7768 | 122.7585 | 122.905 | -0.25635
2669.0938 | 122.8729 | -122.731 | 0.16937 | 0.0074006 | -0.016665 | 0.012715 | 0.039868 | -0.010502 | -0.04086 | -0.0051611 | 7.627e-05 | 0.028247 | -0.035861 | -0.0012625 | -0.014492 | -0.0027344 | 0.10986 | 0.045776 | 0.086975 | 0.073242 | 0.11444 | 0.018311 | -0.10529 | 0 | 0.12817 | -0.009155 | 0.12817 | 0.11902 | -0.036621 | -0.11444 | 122.7493 | 122.6257 | -0.054932 | 122.7768 | 122.8043 | 0.17853 | -0.05951 | 122.6944 | 122.6166 | -0.041199 | 122.731 | 122.7219 | 0.10529 | -0.050354 | 122.8455 | 122.8409 | 122.818 | -0.27466 | 122.8592 | 122.85 | 122.8592 | -0.28381
2670.9219 | 122.9233 | -122.6898 | 0.16022 | 0.0074006 | -0.01581 | 0.013783 | 0.0388 | -0.010929 | -0.034665 | -0.0008887 | 7.627e-05 | 0.029529 | -0.036288 | -0.00083531 | -0.012356 | -0.0038024 | 0.045776 | -0.041199 | -0.009155 | 0.004578 | 0.13733 | 0.004578 | -0.13733 | -0.041199 | 0.068665 | -0.068665 | 0.14648 | 0.1236 | -0.050354 | -0.12817 | 122.6944 | 122.5525 | -0.022888 | 122.6486 | 122.6944 | 0.14191 | -0.11444 | 122.6395 | 122.5616 | -0.013733 | 122.6486 | 122.6212 | 0.059509 | -0.036621 | 122.8271 | 122.7356 | 122.6807 | -0.29755 | 122.8363 | 122.8134 | 122.7585 | -0.28839
2672.7188 | 123.0148 | -122.644 | 0.1236 | -0.00022891 | -0.016665 | 0.014424 | 0.032178 | -0.01157 | -0.035305 | 0.0001795 | 7.627e-05 | 0.030384 | -0.039065 | -0.0012625 | -0.010647 | -0.004016 | 0.064087 | -0.036621 | -0.004578 | 0.018311 | 0.15106 | 0.027466 | -0.11902 | 0.022888 | 0.059509 | -0.027466 | 0.11902 | 0.10986 | -0.032043 | -0.10071 | 122.6715 | 122.525 | 0.027466 | 122.6074 | 122.6624 | 0.13733 | -0.059509 | 122.612 | 122.5433 | -0.004577 | 122.6669 | 122.6166 | 0.073242 | -0.013733 | 122.7951 | 122.7081 | 122.6395 | -0.24261 | 122.7631 | 122.7539 | 122.7036 | -0.2243
2674.5 | 122.9187 | -122.7173 | 0.16022 | -0.0078584 | -0.016665 | 0.015278 | 0.0388 | -0.013706 | -0.037014 | -0.0017431 | -0.015182 | 0.029743 | -0.034365 | -0.00062151 | -0.012356 | -0.0031616 | 0.041199 | -0.045776 | 0.004578 | 0.013733 | 0.13733 | 0.004578 | -0.13275 | -0.032043 | 0.07782 | -0.068665 | 0.13733 | 0.11902 | -0.045776 | -0.10986 | 122.7219 | 122.5845 | -0.022888 | 122.6715 | 122.731 | 0.14648 | -0.11902 | 122.6715 | 122.6074 | -0.022888 | 122.6852 | 122.6486 | 0.041198 | -0.041198 | 122.8546 | 122.7585 | 122.7219 | -0.29297 | 122.8546 | 122.8363 | 122.7951 | -0.27008
2676.2188 | 123.0011 | -122.6715 | 0.12817 | -0.00022891 | -0.012392 | 0.014637 | 0.037305 | -0.0090062 | -0.038937 | -0.0013159 | 0.0077058 | 0.029316 | -0.036288 | -0.0016897 | -0.013424 | -0.0044434 | 0.045776 | -0.041199 | 0.004578 | 0.036621 | 0.13733 | 0.004578 | -0.13733 | -0.009155 | 0.07782 | -0.032043 | 0.13275 | 0.11902 | -0.022888 | -0.10071 | 122.6761 | 122.5342 | 0.009155 | 122.6303 | 122.7081 | 0.17395 | -0.082398 | 122.6486 | 122.5708 | 0.004577 | 122.6624 | 122.6395 | 0.068665 | -0.009155 | 122.8088 | 122.7173 | 122.6761 | -0.2655 | 122.8043 | 122.7905 | 122.7493 | -0.22888
2678 | 122.9965 | -122.6761 | 0.13275 | -0.0078584 | -0.015597 | 0.015706 | 0.033246 | -0.011783 | -0.039364 | 0.0008203 | -0.0075532 | 0.028675 | -0.036929 | 0.00023289 | -0.0097924 | -0.0018798 | 0.11444 | 0.054932 | 0.10986 | 0.073242 | 0.09613 | 0.045776 | -0.082397 | 0.091553 | 0.16022 | 0.045776 | 0.07782 | 0.07782 | -0.004578 | -0.054932 | 122.7219 | 122.5937 | -0.036621 | 122.731 | 122.7493 | 0.15564 | -0.01831 | 122.6715 | 122.6212 | -0.054931 | 122.7676 | 122.7219 | 0.10071 | -0.054931 | 122.7722 | 122.7905 | 122.7859 | -0.21515 | 122.7539 | 122.7539 | 122.8363 | -0.18768
2679.7812 | 122.9645 | -122.6898 | 0.14191 | -0.00022891 | -0.015383 | 0.012501 | 0.035382 | -0.010929 | -0.034024 | 0.0014613 | -0.015182 | 0.033802 | -0.036074 | -0.00083531 | -0.0091516 | -0.0033752 | 0.073242 | -0.018311 | 0.009155 | 0.032043 | 0.12817 | 0.013733 | -0.11902 | -0.018311 | 0.064087 | -0.059509 | 0.13275 | 0.10986 | -0.013733 | -0.091553 | 122.7036 | 122.5708 | -0.013733 | 122.6715 | 122.7219 | 0.15106 | -0.068665 | 122.6761 | 122.5983 | -0.009156 | 122.6715 | 122.6303 | 0.032044 | -0.032044 | 122.818 | 122.7631 | 122.699 | -0.26093 | 122.8226 | 122.7997 | 122.7539 | -0.23346
2681.5781 | 122.8912 | -122.699 | 0.17853 | -0.00022891 | -0.020937 | 0.015706 | 0.033032 | -0.015201 | -0.044064 | -0.0013159 | 7.627e-05 | 0.027179 | -0.037997 | -0.0019033 | -0.015133 | -0.0027344 | 0.059509 | 0.054932 | 0.086975 | 0.054932 | 0.091553 | 0.036621 | -0.091553 | 0.022888 | 0.12817 | 0.027466 | 0.086975 | 0.10529 | 0 | -0.082397 | 122.7356 | 122.6074 | -0.086975 | 122.7539 | 122.7539 | 0.14649 | -0.11902 | 122.699 | 122.6166 | -0.091553 | 122.7219 | 122.7264 | 0.10986 | -0.073242 | 122.7905 | 122.7585 | 122.7859 | -0.27008 | 122.7859 | 122.8043 | 122.8271 | -0.26092
2683.2969 | 122.9416 | -122.6944 | 0.15106 | -0.00022891 | -0.023501 | 0.01656 | 0.033673 | -0.014133 | -0.040219 | -0.0030249 | 0.0077058 | 0.028034 | -0.042269 | -0.00040791 | -0.013851 | -0.002948 | 0.09613 | 0.086975 | 0.12817 | 0.086975 | 0.10529 | 0.050354 | -0.082397 | 0.09613 | 0.19226 | 0.09613 | 0.10529 | 0.073242 | -0.018311 | -0.059509 | 122.7448 | 122.612 | -0.045776 | 122.7814 | 122.7814 | 0.16937 | -0.054932 | 122.6761 | 122.6349 | -0.045776 | 122.7905 | 122.7905 | 0.15564 | -0.07782 | 122.7997 | 122.7905 | 122.8226 | -0.23346 | 122.7997 | 122.7676 | 122.8867 | -0.21057
2685.0625 | 122.8638 | -122.699 | 0.16937 | -0.0078584 | -0.015383 | 0.016133 | 0.040082 | -0.01392 | -0.039578 | -0.0015295 | -0.015182 | 0.029529 | -0.037783 | -0.0012625 | -0.013851 | -0.0061524 | 0.11444 | 0.086975 | 0.11902 | 0.10071 | 0.11444 | 0.054932 | -0.09613 | 0.050354 | 0.17853 | 0.068665 | 0.091553 | 0.073242 | -0.013733 | -0.068665 | 122.7539 | 122.6028 | -0.054932 | 122.7859 | 122.7997 | 0.19684 | -0.054932 | 122.6852 | 122.6303 | -0.07782 | 122.7493 | 122.7676 | 0.13733 | -0.096131 | 122.8134 | 122.8134 | 122.818 | -0.2655 | 122.7905 | 122.7722 | 122.8775 | -0.23804
2686.8594 | 123.0057 | -122.644 | 0.13275 | -0.015487 | -0.01282 | 0.012715 | 0.038373 | -0.011997 | -0.032956 | -0.0013159 | 7.627e-05 | 0.035083 | -0.036929 | 0.0030099 | -0.0095788 | -0.0065796 | 0.09613 | -0.018311 | 0.036621 | 0.045776 | 0.15106 | 0.013733 | -0.11444 | -0.004578 | 0.10529 | -0.027466 | 0.10986 | 0.11444 | -0.036621 | -0.091553 | 122.6578 | 122.5296 | 0.018311 | 122.6257 | 122.6898 | 0.16022 | -0.036621 | 122.6074 | 122.5525 | -0.022888 | 122.6395 | 122.6166 | 0.064087 | -0.01831 | 122.7951 | 122.7402 | 122.6807 | -0.24719 | 122.7539 | 122.7585 | 122.7493 | -0.2243
2688.5938 | 122.8867 | -122.7219 | 0.18768 | -0.015487 | -0.019869 | 0.015919 | 0.035809 | -0.0096472 | -0.041928 | -3.4096e-05 | -0.0075532 | 0.028675 | -0.03992 | -0.00019431 | -0.014919 | -0.0020934 | 0.07782 | 0.018311 | 0.082397 | 0.073242 | 0.10986 | 0.045776 | -0.09613 | 0.032043 | 0.10529 | 0.036621 | 0.082397 | 0.09613 | 0.009155 | -0.09613 | 122.7676 | 122.6257 | -0.07782 | 122.7402 | 122.7951 | 0.16937 | -0.10986 | 122.731 | 122.6257 | -0.10529 | 122.7539 | 122.7585 | 0.13275 | -0.091553 | 122.8317 | 122.7997 | 122.8043 | -0.28381 | 122.8043 | 122.818 | 122.8271 | -0.28381
2690.375 | 122.9919 | -122.6715 | 0.13733 | -0.015487 | -0.013888 | 0.012288 | 0.037305 | -0.011143 | -0.032315 | -0.0008887 | -0.015182 | 0.034229 | -0.036715 | 0.0010873 | -0.0093652 | -0.0093566 | 0.10529 | 0.022888 | 0.022888 | 0.059509 | 0.14191 | 0.022888 | -0.13275 | 0.032043 | 0.11444 | -0.018311 | 0.11444 | 0.09613 | -0.041199 | -0.091553 | 122.6944 | 122.5388 | 0.004578 | 122.6944 | 122.731 | 0.19226 | -0.032043 | 122.6303 | 122.58 | -0.022888 | 122.7036 | 122.6532 | 0.073242 | -0.041199 | 122.8134 | 122.7768 | 122.6944 | -0.27008 | 122.7859 | 122.7676 | 122.7859 | -0.22888
2692.1562 | 122.8867 | -122.7081 | 0.16479 | 0.0074006 | -0.020083 | 0.018483 | 0.03645 | -0.010074 | -0.03851 | -0.0025977 | 7.627e-05 | 0.029956 | -0.039492 | 0.0017283 | -0.011715 | -0.0042298 | 0.068665 | 0.045776 | 0.059509 | 0.054932 | 0.091553 | 0.022888 | -0.11902 | -0.018311 | 0.10986 | -0.022888 | 0.1236 | 0.10986 | -0.045776 | -0.1236 | 122.731 | 122.5891 | -0.073242 | 122.7539 | 122.7631 | 0.17395 | -0.09613 | 122.6624 | 122.5845 | -0.041199 | 122.6898 | 122.6852 | 0.10071 | -0.054932 | 122.7997 | 122.7768 | 122.7676 | -0.28381 | 122.8317 | 122.818 | 122.818 | -0.28839
2693.9531 | 122.8775 | -122.7081 | 0.16937 | -0.015487 | -0.019655 | 0.016774 | 0.035596 | -0.012852 | -0.041714 | -0.0011023 | -0.015182 | 0.028461 | -0.037783 | -0.0010489 | -0.01257 | -0.0033752 | 0.082397 | 0.059509 | 0.09613 | 0.064087 | 0.10986 | 0.041199 | -0.09613 | 0.054932 | 0.1236 | 0.054932 | 0.09613 | 0.091553 | -0.004578 | -0.091553 | 122.7493 | 122.612 | -0.05951 | 122.7676 | 122.7722 | 0.16022 | -0.086976 | 122.7036 | 122.6166 | -0.073243 | 122.7631 | 122.7631 | 0.14649 | -0.07782 | 122.818 | 122.7905 | 122.8043 | -0.2655 | 122.8043 | 122.7997 | 122.8317 | -0.26093
2695.75 | 122.9279 | -122.699 | 0.17395 | -0.0078584 | -0.01816 | 0.01421 | 0.039655 | -0.011783 | -0.041928 | -0.0017431 | 0.0077058 | 0.028675 | -0.038424 | -0.0014761 | -0.015347 | -0.0031616 | 0.11444 | 0.07782 | 0.13733 | 0.073242 | 0.10986 | 0.022888 | -0.086975 | 0.091553 | 0.18768 | 0.09613 | 0.09613 | 0.09613 | -0.018311 | -0.064087 | 122.7219 | 122.612 | -0.064087 | 122.7768 | 122.7722 | 0.16022 | -0.059509 | 122.6807 | 122.6349 | -0.07782 | 122.7905 | 122.7951 | 0.16022 | -0.07782 | 122.8088 | 122.8134 | 122.8363 | -0.26092 | 122.7951 | 122.7951 | 122.8867 | -0.23804
2697.4844 | 122.9965 | -122.6578 | 0.11902 | 0.0074006 | -0.012606 | 0.014851 | 0.035596 | -0.010288 | -0.032956 | -0.0017431 | 0.0077058 | 0.032093 | -0.036288 | -0.0014761 | -0.0095788 | -0.0070068 | 0.073242 | -0.009155 | 0.018311 | 0.050354 | 0.13275 | 0.004578 | -0.11902 | 0.004578 | 0.091553 | -0.013733 | 0.13275 | 0.10529 | -0.054932 | -0.10071 | 122.6624 | 122.5388 | 0.013732 | 122.6486 | 122.7081 | 0.16937 | -0.045777 | 122.6028 | 122.5571 | 0.013732 | 122.6624 | 122.644 | 0.086975 | -0.013733 | 122.7905 | 122.731 | 122.6761 | -0.23804 | 122.7905 | 122.7631 | 122.7493 | -0.21973
2699.25 | 123.0194 | -122.6715 | 0.12817 | -0.00022891 | -0.01346 | 0.013569 | 0.03346 | -0.011997 | -0.034665 | -0.0015295 | -0.015182 | 0.031238 | -0.035006 | -0.0051077 | -0.010433 | -0.00059818 | 0.045776 | -0.059509 | -0.022888 | 0.018311 | 0.12817 | -0.004578 | -0.14191 | 0.004578 | 0.032043 | -0.027466 | 0.13275 | 0.1236 | -0.050354 | -0.10071 | 122.6669 | 122.5296 | 0 | 122.612 | 122.6898 | 0.16022 | -0.082398 | 122.6212 | 122.5708 | 0.004577 | 122.6761 | 122.644 | 0.073242 | -0.004578 | 122.7997 | 122.7173 | 122.6486 | -0.27008 | 122.8043 | 122.7951 | 122.7036 | -0.22888
2701.0469 | 122.9782 | -122.6486 | 0.14191 | -0.0078584 | -0.015383 | 0.013997 | 0.03645 | -0.014347 | -0.035305 | 0.0001795 | 7.627e-05 | 0.032947 | -0.038211 | -0.0048941 | -0.01022 | 0.0019654 | 0.032043 | -0.054932 | -0.009155 | 0.004578 | 0.13275 | 0.004578 | -0.12817 | -0.018311 | 0.013733 | -0.068665 | 0.13275 | 0.10071 | -0.045776 | -0.11444 | 122.6532 | 122.5204 | -0.009156 | 122.5937 | 122.6532 | 0.13275 | -0.10986 | 122.6028 | 122.5342 | -0.009156 | 122.6303 | 122.58 | 0.045776 | -0.041199 | 122.7814 | 122.6807 | 122.6395 | -0.27008 | 122.7814 | 122.7493 | 122.6624 | -0.25635
2702.7812 | 122.8867 | -122.6578 | 0.16022 | -0.00022891 | -0.017733 | 0.015278 | 0.0388 | -0.0090062 | -0.043637 | -0.0034521 | 7.627e-05 | 0.02782 | -0.035861 | -0.0059621 | -0.013424 | 0.0026062 | 0.11902 | 0.11444 | 0.14191 | 0.09613 | 0.10529 | 0.050354 | -0.07782 | 0.054932 | 0.20142 | 0.091553 | 0.091553 | 0.09613 | 0 | -0.086975 | 122.7081 | 122.58 | -0.054931 | 122.7722 | 122.7539 | 0.17395 | -0.041198 | 122.6578 | 122.5708 | -0.068664 | 122.7127 | 122.7493 | 0.17853 | -0.064087 | 122.7631 | 122.7768 | 122.7997 | -0.23804 | 122.7493 | 122.7539 | 122.8592 | -0.24719
2704.5 | 122.8729 | -122.7081 | 0.20142 | -0.00022891 | -0.016451 | 0.016346 | 0.038587 | -0.013492 | -0.041928 | -0.0030249 | 7.627e-05 | 0.028247 | -0.035434 | -0.0031851 | -0.016842 | -0.00017078 | 0.082397 | 0.054932 | 0.09613 | 0.050354 | 0.09613 | 0.022888 | -0.091553 | 0.036621 | 0.13275 | 0.050354 | 0.10529 | 0.086975 | -0.018311 | -0.082397 | 122.731 | 122.6166 | -0.10529 | 122.7631 | 122.7585 | 0.14191 | -0.11902 | 122.6898 | 122.6257 | -0.09613 | 122.7448 | 122.7585 | 0.13275 | -0.11444 | 122.8043 | 122.7905 | 122.8043 | -0.29297 | 122.8134 | 122.7951 | 122.8409 | -0.28381
2706.2969 | 122.9004 | -122.6944 | 0.19684 | -0.0078584 | -0.022646 | 0.018483 | 0.035596 | -0.014133 | -0.041073 | -0.0021703 | -0.015182 | 0.029743 | -0.03757 | -0.0076711 | -0.010647 | 0.00047002 | 0.073242 | 0.036621 | 0.07782 | 0.064087 | 0.10529 | 0.027466 | -0.10071 | 0.022888 | 0.11902 | 0.045776 | 0.10529 | 0.091553 | -0.009155 | -0.073242 | 122.7219 | 122.5937 | -0.091552 | 122.731 | 122.7585 | 0.1648 | -0.1236 | 122.6852 | 122.6212 | -0.091552 | 122.7173 | 122.7402 | 0.11902 | -0.10529 | 122.7997 | 122.7676 | 122.7722 | -0.29755 | 122.7997 | 122.7859 | 122.8134 | -0.27008
2708.0156 | 122.9736 | -122.6852 | 0.15564 | -0.015487 | -0.014315 | 0.014637 | 0.034955 | -0.012638 | -0.032528 | -0.0002477 | 7.627e-05 | 0.033802 | -0.036502 | -0.0051077 | -0.0078698 | -0.0025208 | 0.1236 | 0.022888 | 0.032043 | 0.050354 | 0.12817 | 0.018311 | -0.10986 | 0.022888 | 0.10071 | -0.041199 | 0.11902 | 0.11444 | -0.036621 | -0.10986 | 122.7036 | 122.5754 | -0.027466 | 122.7081 | 122.7356 | 0.16022 | -0.032044 | 122.6486 | 122.5754 | -0.036621 | 122.7081 | 122.644 | 0.068664 | -0.041199 | 122.8134 | 122.8088 | 122.7173 | -0.2655 | 122.8043 | 122.7997 | 122.7859 | -0.2655
2709.7969 | 122.8958 | -122.7081 | 0.19684 | -0.00022891 | -0.018374 | 0.015706 | 0.037732 | -0.01392 | -0.040646 | 0.0008203 | 7.627e-05 | 0.024402 | -0.032229 | -0.0087393 | -0.015347 | 0.0036744 | 0.064087 | 0.041199 | 0.082397 | 0.054932 | 0.10071 | 0.032043 | -0.09613 | 0.004578 | 0.11444 | 0.022888 | 0.13275 | 0.09613 | -0.022888 | -0.073242 | 122.7402 | 122.612 | -0.09613 | 122.7493 | 122.7631 | 0.15106 | -0.13275 | 122.6852 | 122.6349 | -0.064087 | 122.7127 | 122.731 | 0.09613 | -0.10071 | 122.8088 | 122.7722 | 122.7905 | -0.29297 | 122.8409 | 122.8043 | 122.8226 | -0.27008
2711.5781 | 122.8821 | -122.6898 | 0.18768 | -0.00022891 | -0.020083 | 0.016346 | 0.035809 | -0.012638 | -0.038937 | -0.0019567 | 7.627e-05 | 0.023975 | -0.031802 | -0.0051077 | -0.01321 | 0.002179 | 0.10071 | 0.041199 | 0.09613 | 0.059509 | 0.09613 | 0.045776 | -0.086975 | 0.045776 | 0.13733 | 0.022888 | 0.1236 | 0.10071 | -0.027466 | -0.07782 | 122.7356 | 122.6028 | -0.091553 | 122.731 | 122.7493 | 0.14648 | -0.086975 | 122.6624 | 122.612 | -0.064087 | 122.7356 | 122.7127 | 0.10071 | -0.086975 | 122.7859 | 122.7905 | 122.7859 | -0.27466 | 122.8134 | 122.7905 | 122.8271 | -0.2655
2713.3594 | 122.8821 | -122.699 | 0.17395 | -0.0078584 | -0.016878 | 0.014851 | 0.035596 | -0.012424 | -0.037869 | -0.0015295 | 7.627e-05 | 0.024402 | -0.032656 | -0.0048941 | -0.013851 | 0.0023926 | 0.13733 | 0.07782 | 0.13275 | 0.086975 | 0.09613 | 0.036621 | -0.09613 | 0.086975 | 0.14648 | 0.050354 | 0.10529 | 0.09613 | 0 | -0.073242 | 122.7356 | 122.6028 | -0.07782 | 122.7768 | 122.7859 | 0.1831 | -0.036621 | 122.699 | 122.6257 | -0.068664 | 122.7859 | 122.7493 | 0.1236 | -0.07782 | 122.7951 | 122.8363 | 122.8317 | -0.27008 | 122.8043 | 122.7951 | 122.8455 | -0.24719
2715.125 | 123.0286 | -122.6349 | 0.16937 | -0.0078584 | -0.014101 | 0.016987 | 0.033673 | -0.010929 | -0.035733 | -0.0011023 | 7.627e-05 | 0.029102 | -0.033511 | -0.0044669 | -0.0085108 | 0.0026062 | 0.10071 | -0.027466 | 0.032043 | 0.032043 | 0.12817 | 0.018311 | -0.10529 | 0.068665 | 0.1236 | 0.013733 | 0.11444 | 0.11444 | -0.004578 | -0.07782 | 122.6532 | 122.5296 | -0.041199 | 122.6074 | 122.6669 | 0.13733 | -0.068665 | 122.6303 | 122.5571 | -0.054932 | 122.7036 | 122.6486 | 0.091553 | -0.054932 | 122.7631 | 122.7356 | 122.6669 | -0.27466 | 122.7493 | 122.7493 | 122.7585 | -0.24719
2716.8594 | 123.0103 | -122.6212 | 0.13733 | -0.00022891 | -0.013888 | 0.014424 | 0.035169 | -0.010502 | -0.034024 | 0.0003931 | 7.627e-05 | 0.027179 | -0.032443 | -0.0055349 | -0.0087244 | 0.0013244 | 0.045776 | -0.059509 | -0.013733 | 0.004578 | 0.15106 | 0.018311 | -0.13275 | -0.009155 | 0.045776 | -0.068665 | 0.14191 | 0.11902 | -0.027466 | -0.10529 | 122.6395 | 122.4884 | 0.013733 | 122.5616 | 122.6257 | 0.13733 | -0.091553 | 122.5937 | 122.5159 | 0.004578 | 122.612 | 122.5525 | 0.036621 | -0.01831 | 122.7722 | 122.6669 | 122.6074 | -0.27008 | 122.7631 | 122.7402 | 122.6669 | -0.24262
2718.6406 | 123.0011 | -122.6486 | 0.16479 | -0.00022891 | -0.011751 | 0.013997 | 0.0388 | -0.01157 | -0.033596 | -0.0008887 | 0.0077058 | 0.029529 | -0.031375 | -0.0063895 | -0.012356 | 0.003247 | 0.10529 | 0 | 0.036621 | 0.059509 | 0.13733 | 0 | -0.10986 | 0.009155 | 0.1236 | -0.018311 | 0.13733 | 0.11902 | -0.027466 | -0.091553 | 122.6486 | 122.5388 | -0.027466 | 122.6486 | 122.7081 | 0.16937 | -0.059509 | 122.6212 | 122.5571 | -0.027466 | 122.6578 | 122.6303 | 0.073242 | -0.045776 | 122.7859 | 122.7539 | 122.6852 | -0.27466 | 122.7859 | 122.7676 | 122.7722 | -0.25635
2720.3594 | 122.8775 | -122.7081 | 0.17853 | -0.0078584 | -0.021151 | 0.01656 | 0.034101 | -0.0087926 | -0.042569 | -0.0013159 | 0.0077058 | 0.024616 | -0.033511 | -0.0068167 | -0.014065 | 0.003247 | 0.10529 | 0.073242 | 0.11444 | 0.07782 | 0.091553 | 0.041199 | -0.10529 | 0.036621 | 0.14191 | 0.041199 | 0.10071 | 0.09613 | 0 | -0.091553 | 122.7493 | 122.6028 | -0.086975 | 122.7814 | 122.7859 | 0.18311 | -0.073242 | 122.7081 | 122.6166 | -0.07782 | 122.7448 | 122.7493 | 0.13275 | -0.082398 | 122.7997 | 122.8134 | 122.8226 | -0.28381 | 122.8088 | 122.8043 | 122.85 | -0.27008
2722.1562 | 122.9965 | -122.6395 | 0.16479 | -0.015487 | -0.014529 | 0.013783 | 0.037732 | -0.012424 | -0.034878 | -0.0006751 | 0.0077058 | 0.028675 | -0.033084 | -0.0055349 | -0.010647 | -0.00081178 | 0.068665 | -0.009155 | 0.032043 | 0.041199 | 0.11902 | 0.022888 | -0.086975 | 0.041199 | 0.13275 | 0.022888 | 0.1236 | 0.10529 | 0.004578 | -0.073242 | 122.6624 | 122.5525 | -0.045776 | 122.6303 | 122.6807 | 0.12817 | -0.09613 | 122.644 | 122.5662 | -0.041199 | 122.6807 | 122.6624 | 0.09613 | -0.059509 | 122.7585 | 122.7081 | 122.6715 | -0.25177 | 122.7631 | 122.7448 | 122.7722 | -0.23804
2723.8906 | 122.9141 | -122.6944 | 0.16479 | 0.0074006 | -0.016024 | 0.013356 | 0.040082 | -0.010288 | -0.039151 | -0.0004613 | 7.627e-05 | 0.029956 | -0.029238 | -0.0021169 | -0.014706 | -0.00081178 | 0.041199 | -0.036621 | 0.018311 | 0.004578 | 0.14648 | -0.004578 | -0.14648 | -0.050354 | 0.064087 | -0.054932 | 0.15106 | 0.14191 | -0.050354 | -0.10986 | 122.6898 | 122.5479 | -0.018311 | 122.6578 | 122.699 | 0.15106 | -0.1236 | 122.644 | 122.5845 | -0.013733 | 122.644 | 122.6395 | 0.054931 | -0.022888 | 122.8409 | 122.7356 | 122.7127 | -0.31128 | 122.8455 | 122.8363 | 122.7585 | -0.27466
2725.6719 | 123.0011 | -122.6486 | 0.14191 | -0.0078584 | -0.011538 | 0.015492 | 0.040723 | -0.015629 | -0.035305 | -0.0008887 | 0.015335 | 0.031879 | -0.029879 | -0.0027579 | -0.01257 | -0.0033752 | 0.091553 | 0.022888 | 0.041199 | 0.054932 | 0.14191 | 0.009155 | -0.12817 | 0 | 0.1236 | -0.027466 | 0.14191 | 0.12817 | -0.022888 | -0.09613 | 122.6578 | 122.5204 | 0 | 122.6715 | 122.7036 | 0.18311 | -0.050354 | 122.6257 | 122.5525 | 0 | 122.6486 | 122.6212 | 0.068664 | -0.013733 | 122.7905 | 122.7402 | 122.6898 | -0.27008 | 122.7905 | 122.7768 | 122.7722 | -0.23804
2727.4688 | 122.9507 | -122.6486 | 0.16479 | -0.00022891 | -0.014315 | 0.013142 | 0.033032 | -0.011356 | -0.033383 | -0.0002477 | 7.627e-05 | 0.03017 | -0.032656 | -0.00083531 | -0.011074 | -0.00081178 | 0.036621 | -0.064087 | -0.009155 | 0.018311 | 0.13733 | -0.004578 | -0.13733 | -0.054932 | 0.045776 | -0.091553 | 0.12817 | 0.14648 | -0.022888 | -0.10071 | 122.644 | 122.5113 | -0.027466 | 122.5845 | 122.6669 | 0.15564 | -0.12817 | 122.6257 | 122.5479 | -0.036621 | 122.5937 | 122.5571 | 0.009155 | -0.018311 | 122.7859 | 122.6852 | 122.6395 | -0.30212 | 122.7768 | 122.7951 | 122.6944 | -0.2655
2729.25 | 122.905 | -122.6715 | 0.1831 | -0.00022891 | -0.016878 | 0.015278 | 0.038373 | -0.01157 | -0.044278 | -0.0019567 | 7.627e-05 | 0.028461 | -0.034579 | -0.0055349 | -0.015988 | 0.0019654 | 0.13275 | 0.11902 | 0.13733 | 0.10986 | 0.11444 | 0.032043 | -0.10529 | 0.068665 | 0.21973 | 0.09613 | 0.091553 | 0.091553 | -0.009155 | -0.064087 | 122.7036 | 122.5662 | -0.068664 | 122.7905 | 122.7814 | 0.21515 | -0.050354 | 122.6624 | 122.6074 | -0.091552 | 122.7402 | 122.7676 | 0.16022 | -0.091552 | 122.7859 | 122.8043 | 122.8088 | -0.28839 | 122.7631 | 122.7631 | 122.8912 | -0.24719
2730.9688 | 123.0057 | -122.6257 | 0.15106 | -0.0078584 | -0.01581 | 0.015065 | 0.037091 | -0.011997 | -0.037442 | -0.0025977 | -0.015182 | 0.03017 | -0.034152 | -0.0029715 | -0.011929 | 0.00047002 | 0.054932 | -0.041199 | 0.013733 | 0.022888 | 0.12817 | 0 | -0.12817 | 0.009155 | 0.059509 | -0.027466 | 0.14648 | 0.12817 | -0.018311 | -0.07782 | 122.6257 | 122.4976 | -0.022888 | 122.5845 | 122.6486 | 0.15106 | -0.09613 | 122.6074 | 122.5479 | -0.004578 | 122.6349 | 122.5983 | 0.050354 | -0.022888 | 122.7539 | 122.6807 | 122.6395 | -0.27924 | 122.7722 | 122.7539 | 122.6852 | -0.22888
2732.7656 | 122.9004 | -122.6807 | 0.16479 | -0.0078584 | -0.018801 | 0.015706 | 0.03346 | -0.011783 | -0.041073 | -0.0021703 | 0.0077058 | 0.02782 | -0.033511 | -0.0053213 | -0.013424 | 0.0013244 | 0.14191 | 0.073242 | 0.11902 | 0.09613 | 0.10071 | 0.036621 | -0.086975 | 0.07782 | 0.1831 | 0.073242 | 0.10529 | 0.09613 | 0.009155 | -0.059509 | 122.7173 | 122.5937 | -0.064087 | 122.7539 | 122.7768 | 0.1831 | -0.022888 | 122.6898 | 122.6212 | -0.059509 | 122.7585 | 122.7539 | 0.13275 | -0.068665 | 122.7814 | 122.8226 | 122.7997 | -0.25177 | 122.7859 | 122.7768 | 122.8638 | -0.2243
2734.5469 | 122.9691 | -122.6532 | 0.17395 | 0.01503 | -0.018374 | 0.016774 | 0.038373 | -0.00922 | -0.035519 | -0.0047339 | -0.0075532 | 0.031665 | -0.029025 | -0.0066031 | -0.013424 | 0.002179 | 0.045776 | -0.054932 | 0 | 0.027466 | 0.16479 | 0.009155 | -0.13275 | -0.050354 | 0.073242 | -0.064087 | 0.14191 | 0.14191 | -0.036621 | -0.10986 | 122.6624 | 122.5204 | -0.009155 | 122.5983 | 122.6807 | 0.16022 | -0.12817 | 122.6166 | 122.5433 | -0.032043 | 122.6028 | 122.5891 | 0.045776 | -0.032043 | 122.818 | 122.699 | 122.6532 | -0.3067 | 122.7951 | 122.7951 | 122.7264 | -0.28381
2736.2656 | 123.0057 | -122.6349 | 0.13733 | -0.00022891 | -0.011111 | 0.015278 | 0.040296 | -0.011143 | -0.037655 | -0.0023839 | 7.627e-05 | 0.028034 | -0.03052 | -0.0087393 | -0.011288 | 0.0023926 | 0.068665 | -0.041199 | 0.004578 | 0.036621 | 0.11902 | -0.009155 | -0.1236 | -0.009155 | 0.09613 | -0.036621 | 0.14648 | 0.13275 | -0.013733 | -0.1236 | 122.6257 | 122.5113 | -0.01831 | 122.5937 | 122.6715 | 0.16022 | -0.068664 | 122.6212 | 122.5113 | 0.009155 | 122.6257 | 122.5983 | 0.086975 | -0.004578 | 122.7539 | 122.7036 | 122.6395 | -0.26093 | 122.7814 | 122.7676 | 122.731 | -0.26093
2738.0625 | 122.9416 | -122.6532 | 0.17853 | 0.02266 | -0.019015 | 0.016346 | 0.031964 | -0.013065 | -0.039364 | 0.0014613 | -0.015182 | 0.028461 | -0.031588 | -0.0057485 | -0.01257 | 0.0028198 | 0.14648 | 0.07782 | 0.13275 | 0.10071 | 0.09613 | 0.054932 | -0.082397 | 0.09613 | 0.18768 | 0.068665 | 0.09613 | 0.091553 | -0.004578 | -0.073242 | 122.7081 | 122.5708 | -0.082398 | 122.731 | 122.7539 | 0.18311 | -0.032044 | 122.6486 | 122.58 | -0.082398 | 122.7493 | 122.7219 | 0.14191 | -0.086975 | 122.7493 | 122.7997 | 122.7859 | -0.26092 | 122.7493 | 122.7448 | 122.8409 | -0.25177
2739.8438 | 122.8867 | -122.6944 | 0.19226 | -0.00022891 | -0.016451 | 0.015706 | 0.039655 | -0.011143 | -0.042996 | -0.0032385 | 7.627e-05 | 0.026966 | -0.028811 | -0.0070303 | -0.016628 | 0.0041016 | 0.086975 | 0.009155 | 0.09613 | 0.059509 | 0.10529 | 0.045776 | -0.086975 | 0.009155 | 0.14191 | 0.032043 | 0.12817 | 0.10986 | 0 | -0.082397 | 122.7402 | 122.6074 | -0.086975 | 122.7036 | 122.7539 | 0.14648 | -0.10529 | 122.6944 | 122.612 | -0.064087 | 122.7036 | 122.7264 | 0.11444 | -0.082398 | 122.7997 | 122.7814 | 122.7905 | -0.27924 | 122.8226 | 122.8043 | 122.8363 | -0.27466
2741.5781 | 122.8683 | -122.6898 | 0.1831 | -0.0078584 | -0.019015 | 0.012501 | 0.034528 | -0.012424 | -0.040432 | -0.0008887 | -0.0075532 | 0.027179 | -0.029666 | -0.0061757 | -0.014065 | 0.0026062 | 0.15106 | 0.073242 | 0.13275 | 0.07782 | 0.10071 | 0.032043 | -0.082397 | 0.086975 | 0.16937 | 0.064087 | 0.10986 | 0.10071 | 0 | -0.064087 | 122.7219 | 122.6074 | -0.082397 | 122.7631 | 122.7676 | 0.16022 | -0.032043 | 122.6898 | 122.6257 | -0.073242 | 122.7768 | 122.7539 | 0.12817 | -0.082397 | 122.7905 | 122.8409 | 122.8226 | -0.2655 | 122.7997 | 122.7905 | 122.8592 | -0.24719
2743.375 | 122.9416 | -122.6303 | 0.16022 | -0.00022891 | -0.013674 | 0.013142 | 0.035596 | -0.010929 | -0.032956 | 0.0001795 | -0.0075532 | 0.032093 | -0.029238 | -0.0048941 | -0.0093652 | 4.2822e-05 | 0.086975 | -0.036621 | 0 | 0.022888 | 0.13275 | 0 | -0.13733 | -0.036621 | 0.054932 | -0.07782 | 0.13275 | 0.13275 | -0.059509 | -0.10986 | 122.6303 | 122.493 | -0.027466 | 122.5937 | 122.6532 | 0.16022 | -0.073242 | 122.5708 | 122.5204 | -0.027466 | 122.5937 | 122.5525 | 0.032043 | -0.027466 | 122.7631 | 122.7173 | 122.6303 | -0.29755 | 122.7631 | 122.7631 | 122.6852 | -0.27008
2745.0938 | 122.905 | -122.6807 | 0.21515 | -0.015487 | -0.016878 | 0.014637 | 0.036237 | -0.013065 | -0.042569 | -0.0034521 | 0.0077058 | 0.02547 | -0.030307 | -0.0063895 | -0.014919 | 0.0034608 | 0.059509 | 0.018311 | 0.086975 | 0.064087 | 0.11444 | 0.032043 | -0.10529 | 0.018311 | 0.13275 | 0.054932 | 0.13733 | 0.10986 | -0.013733 | -0.07782 | 122.7127 | 122.5754 | -0.10071 | 122.699 | 122.7448 | 0.16937 | -0.15564 | 122.6669 | 122.6028 | -0.07782 | 122.699 | 122.7356 | 0.13275 | -0.10529 | 122.7951 | 122.7402 | 122.7676 | -0.32044 | 122.818 | 122.7905 | 122.8134 | -0.29297
2746.8906 | 122.8867 | -122.6669 | 0.19226 | -0.015487 | -0.014742 | 0.013997 | 0.039014 | -0.011356 | -0.037442 | -0.0017431 | 7.627e-05 | 0.027393 | -0.027316 | -0.0046805 | -0.014279 | 0.0017518 | 0.036621 | 0 | 0.032043 | 0.018311 | 0.13275 | 0.013733 | -0.13733 | -0.013733 | 0.086975 | -0.045776 | 0.16937 | 0.14648 | -0.045776 | -0.10986 | 122.6807 | 122.5296 | -0.05951 | 122.6669 | 122.6852 | 0.15564 | -0.15564 | 122.6212 | 122.5571 | -0.022888 | 122.6532 | 122.6212 | 0.064087 | -0.045777 | 122.7997 | 122.7036 | 122.699 | -0.32959 | 122.8363 | 122.8134 | 122.7539 | -0.30212
2748.6719 | 122.9233 | -122.6028 | 0.11902 | -0.00022891 | -0.013033 | 0.012501 | 0.037946 | -0.010715 | -0.032956 | -0.0066565 | 7.627e-05 | 0.027393 | -0.018344 | -0.088634 | -0.0093652 | 0.003247 | 0.1236 | 0.018311 | 0.050354 | 0.054932 | 0.14191 | 0.032043 | -0.13275 | 0.022888 | 0.11444 | -0.041199 | 0.10986 | 0.09613 | -0.032043 | -0.10071 | 122.6349 | 122.4701 | 0.022888 | 122.6212 | 122.6578 | 0.18768 | 0.004577 | 122.5708 | 122.5021 | -0.009156 | 122.6257 | 122.5616 | 0.059509 | -0.022889 | 122.7448 | 122.7264 | 122.6532 | -0.25177 | 122.7127 | 122.699 | 122.7173 | -0.21973
2750.4688 | 122.8546 | -122.7036 | 0.15564 | -0.00022891 | -0.022005 | 0.016987 | 0.036664 | -0.011997 | -0.041714 | -0.0060155 | -0.0075532 | 0.021839 | -0.021334 | -0.089489 | -0.013851 | 0.003888 | 0.082397 | 0.036621 | 0.09613 | 0.050354 | 0.086975 | 0.054932 | -0.09613 | 0.013733 | 0.11444 | 0.036621 | 0.07782 | 0.07782 | -0.013733 | -0.086975 | 122.7585 | 122.6074 | -0.068665 | 122.7402 | 122.7539 | 0.14648 | -0.073243 | 122.6898 | 122.6166 | -0.07782 | 122.7173 | 122.7402 | 0.1236 | -0.07782 | 122.7905 | 122.7859 | 122.7997 | -0.25177 | 122.7814 | 122.7814 | 122.818 | -0.24261
2752.1875 | 123.0103 | -122.6486 | 0.10529 | -0.0078584 | -0.017306 | 0.01186 | 0.036878 | -0.008579 | -0.035733 | -0.0064429 | -0.015182 | 0.023334 | -0.020694 | -0.089703 | -0.014065 | 0.003888 | 0.082397 | 0.004578 | 0.050354 | 0.045776 | 0.10529 | 0.032043 | -0.09613 | 0.054932 | 0.10986 | 0.032043 | 0.073242 | 0.068665 | -0.018311 | -0.068665 | 122.6807 | 122.5525 | 0 | 122.6532 | 122.6944 | 0.14191 | -0.022889 | 122.6303 | 122.58 | -0.032044 | 122.7036 | 122.6807 | 0.10071 | -0.036621 | 122.7539 | 122.731 | 122.699 | -0.20142 | 122.7219 | 122.7173 | 122.7585 | -0.17395
2753.9844 | 122.9553 | -122.6669 | 0.11902 | -0.00022891 | -0.016665 | 0.017201 | 0.036664 | -0.0098608 | -0.034451 | -0.0021703 | -0.015182 | 0.026538 | -0.020907 | -0.088421 | -0.012356 | 0.0041016 | 0.10529 | 0.013733 | 0.041199 | 0.045776 | 0.1236 | 0.018311 | -0.12817 | 0.013733 | 0.091553 | -0.041199 | 0.086975 | 0.091553 | -0.036621 | -0.10529 | 122.6852 | 122.5388 | 0.004577 | 122.6807 | 122.7127 | 0.17395 | -0.013733 | 122.6303 | 122.5616 | -0.032044 | 122.6807 | 122.6257 | 0.064087 | -0.027466 | 122.7905 | 122.7722 | 122.7081 | -0.24719 | 122.7539 | 122.7585 | 122.7585 | -0.22431
2755.7656 | 122.8775 | -122.7036 | 0.14191 | -0.0078584 | -0.020724 | 0.016133 | 0.038373 | -0.01157 | -0.042782 | -0.0066565 | 7.627e-05 | 0.019916 | -0.018344 | -0.089062 | -0.016842 | 0.0062378 | 0.032043 | 0.027466 | 0.082397 | 0.045776 | 0.11902 | 0.022888 | -0.086975 | 0.009155 | 0.10071 | 0.032043 | 0.073242 | 0.059509 | -0.027466 | -0.07782 | 122.7264 | 122.6166 | -0.022888 | 122.731 | 122.7493 | 0.13275 | -0.10986 | 122.6761 | 122.6257 | -0.068665 | 122.7127 | 122.7356 | 0.10986 | -0.082398 | 122.8226 | 122.7356 | 122.7859 | -0.22888 | 122.7768 | 122.7631 | 122.8043 | -0.21973
2757.5 | 122.9599 | -122.6944 | 0.13733 | -0.00022891 | -0.015169 | 0.014851 | 0.038159 | -0.010929 | -0.034237 | -0.0045203 | -0.015182 | 0.02547 | -0.021334 | -0.089703 | -0.010861 | 0.0034608 | 0.032043 | -0.059509 | -0.018311 | 0.009155 | 0.13275 | 0 | -0.11902 | -0.068665 | -0.009155 | -0.11444 | 0.10071 | 0.09613 | -0.054932 | -0.11444 | 122.6944 | 122.5754 | -0.004578 | 122.6349 | 122.7036 | 0.12817 | -0.10529 | 122.6395 | 122.58 | -0.036621 | 122.6257 | 122.58 | 0 | -0.041199 | 122.8271 | 122.7264 | 122.6761 | -0.25635 | 122.7951 | 122.7905 | 122.6852 | -0.25177
2759.2812 | 122.8821 | -122.7402 | 0.13275 | -0.00022891 | -0.020296 | 0.016774 | 0.034314 | -0.011783 | -0.041501 | -0.0053747 | 7.627e-05 | 0.02013 | -0.021762 | -0.09248 | -0.01321 | 0.006665 | 0.091553 | 0.073242 | 0.10529 | 0.050354 | 0.10071 | 0.054932 | -0.07782 | 0.054932 | 0.10986 | 0.027466 | 0.064087 | 0.064087 | -0.013733 | -0.073242 | 122.7951 | 122.6624 | -0.032043 | 122.8134 | 122.7905 | 0.12817 | -0.041198 | 122.7264 | 122.6669 | -0.068664 | 122.7951 | 122.7676 | 0.10071 | -0.068664 | 122.8409 | 122.8317 | 122.8455 | -0.21057 | 122.8043 | 122.8043 | 122.85 | -0.20599
2761 | 122.9782 | -122.6807 | 0.10986 | -0.0078584 | -0.012606 | 0.013783 | 0.036023 | -0.012211 | -0.035092 | -0.0058019 | 0.0077058 | 0.026752 | -0.019839 | -0.088207 | -0.011501 | 0.0053834 | 0.018311 | -0.07782 | -0.045776 | -0.004578 | 0.15564 | 0.013733 | -0.10986 | -0.045776 | 0.004578 | -0.073242 | 0.11902 | 0.086975 | -0.054932 | -0.1236 | 122.6944 | 122.5708 | 0.045777 | 122.6028 | 122.6761 | 0.10529 | -0.091552 | 122.6257 | 122.5571 | 0.009156 | 122.6349 | 122.6074 | 0.050354 | -0.022888 | 122.8363 | 122.699 | 122.6349 | -0.21973 | 122.7997 | 122.7676 | 122.6852 | -0.23346
2762.7969 | 122.8867 | -122.7356 | 0.15564 | -0.00022891 | -0.020937 | 0.016987 | 0.035382 | -0.012638 | -0.042569 | -0.0053747 | 7.627e-05 | 0.021198 | -0.02048 | -0.089703 | -0.014492 | 0.0058106 | 0.054932 | 0.045776 | 0.091553 | 0.045776 | 0.09613 | 0.045776 | -0.086975 | 0.009155 | 0.10529 | 0.027466 | 0.064087 | 0.068665 | -0.004578 | -0.10071 | 122.7814 | 122.6486 | -0.05951 | 122.7814 | 122.7814 | 0.13275 | -0.10071 | 122.731 | 122.6349 | -0.091553 | 122.7448 | 122.7631 | 0.12817 | -0.086975 | 122.8317 | 122.7905 | 122.8271 | -0.24261 | 122.7997 | 122.8043 | 122.8409 | -0.25635
2764.5156 | 122.8775 | -122.7631 | 0.15564 | -0.0078584 | -0.019228 | 0.015919 | 0.036237 | -0.012424 | -0.039792 | -0.0064429 | 7.627e-05 | 0.020343 | -0.022616 | -0.091411 | -0.015133 | 0.003888 | 0.13733 | 0.07782 | 0.12817 | 0.082397 | 0.09613 | 0.059509 | -0.09613 | 0.054932 | 0.11444 | 0.041199 | 0.082397 | 0.036621 | -0.009155 | -0.09613 | 122.8226 | 122.6669 | -0.05951 | 122.8409 | 122.8455 | 0.17853 | -0.018311 | 122.7539 | 122.6669 | -0.073243 | 122.818 | 122.8043 | 0.13733 | -0.11902 | 122.8592 | 122.9004 | 122.8912 | -0.25177 | 122.8455 | 122.7997 | 122.8775 | -0.25177
2766.3125 | 122.9279 | -122.7493 | 0.13733 | -0.015487 | -0.022646 | 0.018055 | 0.039014 | -0.0096472 | -0.040219 | -0.0075109 | -0.0075532 | 0.019062 | -0.022616 | -0.09013 | -0.015988 | 0.0036744 | 0.07782 | 0.032043 | 0.07782 | 0.045776 | 0.11444 | 0.041199 | -0.10071 | 0.022888 | 0.091553 | 0.018311 | 0.073242 | 0.064087 | -0.022888 | -0.10071 | 122.7905 | 122.6486 | -0.022888 | 122.7814 | 122.7951 | 0.14648 | -0.059509 | 122.7264 | 122.6486 | -0.064087 | 122.7722 | 122.7676 | 0.11902 | -0.073242 | 122.8638 | 122.8271 | 122.8271 | -0.23804 | 122.8226 | 122.8134 | 122.8409 | -0.23804
2768.1094 | 122.9462 | -122.7539 | 0.14191 | -0.0078584 | -0.017733 | 0.017201 | 0.040936 | -0.0094336 | -0.039792 | -0.0087927 | -0.0075532 | 0.020984 | -0.020266 | -0.090771 | -0.017056 | 0.0026062 | 0.064087 | 0.027466 | 0.07782 | 0.050354 | 0.10529 | 0.032043 | -0.10071 | 0.036621 | 0.11444 | 0.050354 | 0.073242 | 0.073242 | -0.018311 | -0.091553 | 122.7859 | 122.6532 | -0.036621 | 122.7814 | 122.8043 | 0.15106 | -0.07782 | 122.7356 | 122.6624 | -0.068665 | 122.7905 | 122.8043 | 0.14191 | -0.068665 | 122.8592 | 122.818 | 122.8317 | -0.24262 | 122.8271 | 122.8271 | 122.8683 | -0.23346
2769.8281 | 122.9736 | -122.7219 | 0.15106 | 0.01503 | -0.019015 | 0.013783 | 0.036237 | -0.0098608 | -0.034237 | -0.0060155 | 7.627e-05 | 0.023548 | -0.020053 | -0.090343 | -0.013638 | 0.003888 | 0.15106 | 0.10071 | 0.13733 | 0.09613 | 0.10071 | 0.036621 | -0.068665 | 0.09613 | 0.16022 | 0.059509 | 0.059509 | 0.041199 | -0.013733 | -0.073242 | 122.7585 | 122.6532 | -0.050354 | 122.8226 | 122.818 | 0.16479 | 0 | 122.7081 | 122.6486 | -0.091553 | 122.818 | 122.7814 | 0.13275 | -0.10986 | 122.8226 | 122.8729 | 122.8592 | -0.21973 | 122.7814 | 122.7631 | 122.8821 | -0.2243
2771.625 | 122.8867 | -122.7448 | 0.14648 | -0.0078584 | -0.019655 | 0.018055 | 0.039014 | -0.010929 | -0.037869 | -0.0066565 | -0.015182 | 0.023334 | -0.019625 | -0.091625 | -0.014706 | 0.0058106 | 0.091553 | 0.064087 | 0.091553 | 0.064087 | 0.091553 | 0.050354 | -0.07782 | 0.045776 | 0.10986 | 0.009155 | 0.07782 | 0.050354 | 0.004578 | -0.073242 | 122.7951 | 122.6669 | -0.054931 | 122.8088 | 122.8088 | 0.14191 | -0.054931 | 122.7493 | 122.6715 | -0.068664 | 122.7905 | 122.7539 | 0.082397 | -0.09613 | 122.8363 | 122.8363 | 122.8363 | -0.2243 | 122.8226 | 122.7951 | 122.8546 | -0.21973
2773.4219 | 122.8958 | -122.7493 | 0.13275 | -0.00022891 | -0.020083 | 0.019337 | 0.034955 | -0.0081518 | -0.037655 | -0.0070837 | -0.0075532 | 0.020984 | -0.023898 | -0.090343 | -0.013424 | 0.0034608 | 0.13275 | 0.1236 | 0.12817 | 0.10529 | 0.086975 | 0.041199 | -0.09613 | 0.068665 | 0.16937 | 0.054932 | 0.064087 | 0.07782 | -0.032043 | -0.07782 | 122.7905 | 122.6532 | -0.045776 | 122.8729 | 122.8546 | 0.20142 | 0 | 122.7173 | 122.6715 | -0.068664 | 122.818 | 122.8043 | 0.13275 | -0.054931 | 122.8363 | 122.8821 | 122.8775 | -0.22888 | 122.8134 | 122.8271 | 122.9187 | -0.21057
2775.125 | 123.0103 | -122.731 | 0.11444 | -0.0078584 | -0.014956 | 0.016133 | 0.035596 | -0.0098608 | -0.030819 | -0.0068701 | -0.0075532 | 0.027393 | -0.020694 | -0.088848 | -0.0095788 | 0.00068362 | 0.073242 | -0.068665 | -0.018311 | 0.009155 | 0.14191 | 0.009155 | -0.13275 | -0.022888 | 0 | -0.07782 | 0.09613 | 0.086975 | -0.045776 | -0.11902 | 122.7402 | 122.5983 | 0.027466 | 122.6624 | 122.7402 | 0.14191 | -0.041199 | 122.6852 | 122.612 | -0.018311 | 122.7081 | 122.6532 | 0.041199 | -0.027466 | 122.8729 | 122.8043 | 122.7127 | -0.24719 | 122.8271 | 122.818 | 122.731 | -0.23346
2776.9219 | 123.0194 | -122.699 | 0.10529 | -0.015487 | -0.013674 | 0.014637 | 0.036664 | -0.00922 | -0.033169 | -0.0058019 | 7.627e-05 | 0.02782 | -0.021548 | -0.089703 | -0.011501 | 0.0036744 | 0.10529 | 0.013733 | 0.032043 | 0.068665 | 0.15106 | 0 | -0.12817 | 0.004578 | 0.10986 | -0.041199 | 0.091553 | 0.07782 | -0.050354 | -0.10986 | 122.699 | 122.5708 | 0.045776 | 122.7127 | 122.7676 | 0.19684 | 0 | 122.6486 | 122.5891 | -0.013733 | 122.7036 | 122.6578 | 0.068664 | -0.027466 | 122.85 | 122.8043 | 122.731 | -0.23346 | 122.7905 | 122.7768 | 122.8088 | -0.21515
2778.7031 | 122.9416 | -122.7173 | 0.12817 | -0.0078584 | -0.01346 | 0.013997 | 0.039441 | -0.010715 | -0.036587 | -0.0064429 | -0.0075532 | 0.022907 | -0.019412 | -0.09013 | -0.014919 | 0.0041016 | 0.027466 | -0.041199 | -0.004578 | 0.018311 | 0.13733 | 0.009155 | -0.13275 | -0.041199 | 0.050354 | -0.068665 | 0.11444 | 0.09613 | -0.064087 | -0.11444 | 122.7264 | 122.5845 | 0.009155 | 122.6761 | 122.7356 | 0.15106 | -0.10071 | 122.6532 | 122.6028 | -0.013733 | 122.6761 | 122.6486 | 0.045776 | -0.032044 | 122.8546 | 122.7448 | 122.7127 | -0.26093 | 122.8317 | 122.8134 | 122.7676 | -0.24262
2780.4844 | 122.612 | -122.3831 | 0.1236 | -0.015487 | -0.017519 | 0.01891 | 0.040296 | -0.011783 | -0.04321 | -0.0064429 | 0.0077058 | 0.018421 | -0.019839 | -0.089275 | -0.018551 | 0.004956 | 0.1236 | 0.1236 | 0.14648 | 0.09613 | 0.10986 | 0.027466 | -0.09613 | 0.091553 | 0.21057 | 0.10986 | 0.054932 | 0.059509 | -0.022888 | -0.086975 | 122.4106 | 122.287 | -0.013733 | 122.5067 | 122.4792 | 0.19226 | 0 | 122.3602 | 122.2961 | -0.068664 | 122.4747 | 122.493 | 0.19684 | -0.064087 | 122.493 | 122.5067 | 122.5296 | -0.21973 | 122.438 | 122.4426 | 122.5937 | -0.21057
2782.25 | 122.8134 | -122.4655 | 0.10071 | -0.015487 | -0.013247 | 0.016987 | 0.037732 | -0.01157 | -0.034024 | -0.0075109 | -0.0075532 | 0.026111 | -0.019625 | -0.08778 | -0.012356 | 0.003247 | 0.059509 | -0.036621 | -0.013733 | 0.032043 | 0.14191 | -0.009155 | -0.12817 | -0.036621 | 0.073242 | -0.036621 | 0.10986 | 0.09613 | -0.068665 | -0.10986 | 122.4564 | 122.3373 | 0.041199 | 122.4289 | 122.4976 | 0.16022 | -0.041199 | 122.3969 | 122.3557 | 0.009155 | 122.4289 | 122.4289 | 0.073242 | -0.004578 | 122.6074 | 122.525 | 122.4518 | -0.22888 | 122.5754 | 122.5616 | 122.5388 | -0.21057
2784.0469 | 122.7951 | -122.5204 | 0.11444 | 0.0074006 | -0.016665 | 0.014851 | 0.033673 | -0.0094336 | -0.038723 | -0.0036657 | -0.0075532 | 0.023548 | -0.023471 | -0.09013 | -0.012356 | 0.003247 | 0.15564 | 0.073242 | 0.1236 | 0.09613 | 0.09613 | 0.032043 | -0.082397 | 0.09613 | 0.16479 | 0.064087 | 0.054932 | 0.054932 | -0.022888 | -0.073242 | 122.5525 | 122.4381 | -0.018311 | 122.5937 | 122.6166 | 0.17853 | 0.041199 | 122.4976 | 122.4472 | -0.059509 | 122.6166 | 122.5845 | 0.13733 | -0.059509 | 122.6166 | 122.6761 | 122.644 | -0.19684 | 122.5754 | 122.5754 | 122.6852 | -0.18768
2785.8281 | 122.8134 | -122.5342 | 0.09613 | -0.00022891 | -0.013033 | 0.013997 | 0.037091 | -0.011356 | -0.032956 | -0.0051611 | 7.627e-05 | 0.026966 | -0.017276 | -0.088634 | -0.011715 | 0.0034608 | 0.10529 | 0.027466 | 0.045776 | 0.045776 | 0.13275 | 0.004578 | -0.12817 | 0.022888 | 0.10071 | -0.032043 | 0.082397 | 0.082397 | -0.032043 | -0.1236 | 122.5388 | 122.406 | 0.036621 | 122.5616 | 122.58 | 0.17395 | 0.009156 | 122.5021 | 122.4106 | -0.013733 | 122.5571 | 122.5021 | 0.091553 | -0.013733 | 122.6669 | 122.6395 | 122.58 | -0.2243 | 122.6166 | 122.6166 | 122.6349 | -0.21973
2787.5469 | 122.8912 | -122.5525 | 0.086975 | -0.0078584 | -0.017092 | 0.016346 | 0.036237 | -0.012638 | -0.03616 | -0.0058019 | 7.627e-05 | 0.025898 | -0.020266 | -0.088848 | -0.01257 | 0.005597 | 0.050354 | -0.036621 | -0.013733 | -0.004578 | 0.13275 | 0.004578 | -0.12817 | 0.009155 | 0.054932 | -0.022888 | 0.09613 | 0.073242 | -0.018311 | -0.11444 | 122.5571 | 122.4243 | 0.045776 | 122.5159 | 122.5479 | 0.1236 | -0.036621 | 122.5342 | 122.438 | 0.009155 | 122.5616 | 122.5296 | 0.091553 | -0.013733 | 122.6852 | 122.6028 | 122.5388 | -0.21515 | 122.6486 | 122.6257 | 122.6074 | -0.20142
2789.3438 | 122.8638 | -122.5662 | 0.1236 | -0.0078584 | -0.015169 | 0.014637 | 0.035382 | -0.010502 | -0.034237 | -0.0055883 | 0.0077058 | 0.025898 | -0.018344 | -0.087139 | -0.012142 | 0.0062378 | 0.032043 | -0.073242 | -0.018311 | 0 | 0.13733 | 0.009155 | -0.13275 | -0.041199 | 0.018311 | -0.059509 | 0.082397 | 0.091553 | -0.054932 | -0.11444 | 122.5754 | 122.4335 | 0.013733 | 122.493 | 122.5662 | 0.13275 | -0.091553 | 122.5113 | 122.4518 | -0.041199 | 122.525 | 122.5067 | 0.054932 | -0.032043 | 122.7036 | 122.5983 | 122.5479 | -0.25635 | 122.6486 | 122.6578 | 122.5845 | -0.23804
2791.125 | 122.8729 | -122.58 | 0.10529 | -0.00022891 | -0.01346 | 0.014424 | 0.037091 | -0.010929 | -0.035305 | -0.0058019 | -0.0075532 | 0.024829 | -0.018985 | -0.089275 | -0.01321 | 0.0060242 | 0.036621 | -0.073242 | -0.027466 | 0.009155 | 0.12817 | -0.004578 | -0.13275 | -0.041199 | 0.013733 | -0.073242 | 0.091553 | 0.10071 | -0.064087 | -0.11444 | 122.5754 | 122.4472 | 0.022888 | 122.5067 | 122.5891 | 0.14191 | -0.068665 | 122.5159 | 122.4655 | -0.013733 | 122.5388 | 122.5067 | 0.041199 | -0.004578 | 122.7081 | 122.6166 | 122.5525 | -0.23804 | 122.6715 | 122.6807 | 122.5937 | -0.21973
2792.8594 | 122.8867 | -122.58 | 0.11444 | -0.015487 | -0.014742 | 0.012501 | 0.038373 | -0.010288 | -0.035733 | -0.0043065 | 7.627e-05 | 0.024402 | -0.016848 | -0.089275 | -0.014492 | 0.004956 | 0.09613 | 0.022888 | 0.045776 | 0.045776 | 0.1236 | 0.004578 | -0.13733 | 0.027466 | 0.10986 | -0.022888 | 0.09613 | 0.091553 | -0.041199 | -0.10986 | 122.5845 | 122.4426 | 0.009155 | 122.6028 | 122.6257 | 0.18311 | -0.018311 | 122.5388 | 122.4701 | -0.018311 | 122.6074 | 122.5571 | 0.086975 | -0.022888 | 122.7036 | 122.6761 | 122.6257 | -0.25177 | 122.6761 | 122.6715 | 122.6898 | -0.2243
2794.6406 | 122.7402 | -122.6212 | 0.14191 | 0.0074006 | -0.013674 | 0.015492 | 0.041577 | -0.011783 | -0.042569 | -0.0079381 | -0.0075532 | 0.02248 | -0.01813 | -0.091198 | -0.017056 | 0.003888 | 0.086975 | 0.064087 | 0.10986 | 0.086975 | 0.10071 | 0.018311 | -0.10986 | -0.004578 | 0.12817 | 0.018311 | 0.07782 | 0.086975 | -0.036621 | -0.10986 | 122.6395 | 122.5113 | -0.041199 | 122.6852 | 122.7081 | 0.19684 | -0.054932 | 122.5845 | 122.5113 | -0.064087 | 122.6166 | 122.6395 | 0.12817 | -0.054932 | 122.7219 | 122.7081 | 122.731 | -0.25177 | 122.699 | 122.7081 | 122.7493 | -0.25177
2796.3594 | 122.0627 | -121.9254 | 0.14191 | -0.0078584 | -0.015169 | 0.016774 | 0.037305 | -0.0096472 | -0.039792 | -0.0060155 | -0.0075532 | 0.021411 | -0.023471 | -0.089916 | -0.015774 | 0.0034608 | 0.036621 | 0 | 0.032043 | 0.027466 | 0.11902 | 0.009155 | -0.13733 | -0.036621 | 0.064087 | -0.059509 | 0.10986 | 0.086975 | -0.064087 | -0.11902 | 121.9345 | 121.788 | -0.022888 | 121.9254 | 121.9528 | 0.16479 | -0.10529 | 121.8613 | 121.8063 | -0.032044 | 121.8887 | 121.8658 | 0.05951 | -0.054932 | 122.0444 | 121.962 | 121.9574 | -0.27924 | 122.0352 | 122.0123 | 121.9894 | -0.26093
2798.1406 | 122.3419 | -122.0764 | 0.11902 | -0.00022891 | -0.013247 | 0.016987 | 0.032605 | -0.012424 | -0.034237 | -0.0045203 | 7.627e-05 | 0.024402 | -0.022189 | -0.090343 | -0.010861 | 0.0030334 | 0.082397 | -0.022888 | 0.004578 | 0.036621 | 0.12817 | 0.013733 | -0.1236 | -0.032043 | 0.022888 | -0.086975 | 0.082397 | 0.10529 | -0.045776 | -0.12817 | 122.0901 | 121.9528 | 0.009155 | 122.0535 | 122.113 | 0.16022 | -0.036622 | 122.0306 | 121.9482 | -0.036622 | 122.0444 | 121.9894 | 0.041199 | -0.013733 | 122.2046 | 122.1588 | 122.081 | -0.24261 | 122.1588 | 122.1817 | 122.0993 | -0.24719
2799.9219 | 121.8933 | -121.6324 | 0.14191 | -0.0078584 | -0.020937 | 0.016987 | 0.037305 | -0.011356 | -0.045773 | -0.0083655 | -0.015182 | 0.020984 | -0.020907 | -0.089275 | -0.017697 | 0.004956 | 0.050354 | 0.022888 | 0.073242 | 0.050354 | 0.11902 | 0.027466 | -0.11444 | 0.027466 | 0.1236 | 0.045776 | 0.064087 | 0.059509 | -0.027466 | -0.10529 | 121.6599 | 121.5179 | -0.022888 | 121.6553 | 121.6827 | 0.16479 | -0.091553 | 121.6049 | 121.5271 | -0.07782 | 121.6599 | 121.6782 | 0.15106 | -0.082398 | 121.7514 | 121.6827 | 121.7056 | -0.25635 | 121.6965 | 121.6919 | 121.756 | -0.24719
2801.7188 | 122.1909 | -122.0215 | 0.15106 | -0.00022891 | -0.016024 | 0.017201 | 0.037518 | -0.010288 | -0.039151 | -0.0085791 | 7.627e-05 | 0.019916 | -0.021548 | -0.091198 | -0.016201 | 0.003247 | 0.11444 | 0.09613 | 0.13275 | 0.086975 | 0.10071 | 0.022888 | -0.09613 | 0.036621 | 0.17395 | 0.041199 | 0.068665 | 0.059509 | -0.018311 | -0.09613 | 122.0444 | 121.9254 | -0.050354 | 122.1176 | 122.1085 | 0.1831 | -0.036621 | 122.0032 | 121.9254 | -0.082397 | 122.0581 | 122.0627 | 0.13733 | -0.091553 | 122.1222 | 122.1359 | 122.1542 | -0.24719 | 122.0901 | 122.081 | 122.1954 | -0.24719
2803.4531 | 121.8475 | -121.6049 | 0.16022 | -0.00022891 | -0.022646 | 0.016346 | 0.034101 | -0.012424 | -0.039578 | -0.0072973 | -0.0075532 | 0.026966 | -0.015353 | -0.090771 | -0.014279 | 0.0045288 | 0.14191 | 0.054932 | 0.10986 | 0.054932 | 0.09613 | 0.050354 | -0.086975 | 0.045776 | 0.13733 | 0.036621 | 0.086975 | 0.064087 | -0.022888 | -0.091553 | 121.6553 | 121.5179 | -0.064087 | 121.6599 | 121.6599 | 0.14191 | -0.01831 | 121.582 | 121.5134 | -0.073242 | 121.6507 | 121.6415 | 0.12817 | -0.09613 | 121.701 | 121.7468 | 121.7148 | -0.24719 | 121.6919 | 121.669 | 121.7422 | -0.25177
2805.2344 | 122.0261 | -121.7697 | 0.15106 | 0.0074006 | -0.018587 | 0.015278 | 0.038587 | -0.008579 | -0.042569 | -0.0072973 | 0.0077058 | 0.027393 | -0.010867 | -0.092052 | -0.015774 | 0.0060242 | 0.073242 | 0.018311 | 0.086975 | 0.059509 | 0.11902 | 0.027466 | -0.10986 | 0.045776 | 0.13275 | 0.059509 | 0.07782 | 0.07782 | -0.022888 | -0.082397 | 121.7972 | 121.6599 | -0.032043 | 121.788 | 121.8292 | 0.16937 | -0.07782 | 121.7468 | 121.6873 | -0.073242 | 121.8155 | 121.8292 | 0.14191 | -0.073242 | 121.8887 | 121.843 | 121.8567 | -0.26093 | 121.8475 | 121.8475 | 121.9025 | -0.23346
2806.9688 | 117.366 | -117.0273 | 0.086975 | -0.00022891 | -0.016878 | 0.016133 | 0.035169 | -0.011143 | -0.03616 | -0.0066565 | 7.627e-05 | 0.029956 | -0.01813 | -0.090343 | -0.010861 | 0.0047424 | 0.073242 | -0.050354 | 0.009155 | 0.009155 | 0.14191 | 0.018311 | -0.11444 | 0.032043 | 0.041199 | -0.032043 | 0.086975 | 0.086975 | -0.022888 | -0.073242 | 117.0456 | 116.9128 | 0.054932 | 116.9769 | 117.0364 | 0.1236 | -0.013733 | 117.0044 | 116.954 | 0 | 117.0593 | 116.9952 | 0.041199 | 0 | 117.1692 | 117.1005 | 117.0364 | -0.20142 | 117.1143 | 117.1143 | 117.0685 | -0.16022
2808.75 | 121.8933 | -121.5088 | 0.13733 | -0.00022891 | -0.01346 | 0.017628 | 0.033673 | -0.0079382 | -0.035519 | -0.0070837 | 0.0077058 | 0.032093 | -0.01108 | -0.091198 | -0.012783 | 0.0060242 | 0.064087 | -0.045776 | 0.013733 | 0.018311 | 0.14648 | 0.013733 | -0.13275 | 0.013733 | 0.054932 | -0.013733 | 0.091553 | 0.091553 | -0.027466 | -0.10071 | 121.5225 | 121.376 | 0.009155 | 121.463 | 121.5271 | 0.15106 | -0.073242 | 121.4813 | 121.4081 | -0.045776 | 121.5225 | 121.4951 | 0.086975 | -0.045776 | 121.6553 | 121.5729 | 121.5225 | -0.27008 | 121.6003 | 121.6003 | 121.5637 | -0.23804
2810.5469 | 121.8567 | -121.6873 | 0.14191 | -0.00022891 | -0.014742 | 0.015065 | 0.040723 | -0.0079382 | -0.040432 | -0.0068701 | 7.627e-05 | 0.03487 | -0.0076627 | -0.091839 | -0.015133 | 0.0058106 | 0.082397 | 0.027466 | 0.059509 | 0.045776 | 0.13275 | 0.004578 | -0.13275 | -0.018311 | 0.082397 | -0.036621 | 0.11902 | 0.11444 | -0.045776 | -0.10529 | 121.6919 | 121.5546 | -0.009156 | 121.7148 | 121.7331 | 0.17853 | -0.05951 | 121.6415 | 121.582 | -0.022888 | 121.669 | 121.6507 | 0.068665 | -0.027466 | 121.8201 | 121.7697 | 121.7468 | -0.27466 | 121.8063 | 121.8018 | 121.7697 | -0.24719
2812.2656 | 121.9437 | -121.7148 | 0.15106 | -0.0078584 | -0.024355 | 0.017415 | 0.033246 | -0.010288 | -0.042996 | -0.0077245 | -0.0075532 | 0.031879 | -0.011721 | -0.093761 | -0.015347 | 0.0068786 | 0.14191 | 0.11444 | 0.14191 | 0.09613 | 0.10529 | 0.054932 | -0.10529 | 0.082397 | 0.19684 | 0.10529 | 0.073242 | 0.082397 | -0.009155 | -0.068665 | 121.7697 | 121.6095 | -0.045776 | 121.8292 | 121.8109 | 0.20142 | -0.009155 | 121.7056 | 121.6461 | -0.07782 | 121.7972 | 121.8201 | 0.17395 | -0.068665 | 121.8201 | 121.8567 | 121.8567 | -0.25635 | 121.788 | 121.7972 | 121.9116 | -0.21973
2814.0312 | 122.049 | -121.7285 | 0.12817 | -0.00022891 | -0.013888 | 0.014637 | 0.035809 | -0.0079382 | -0.032742 | -0.0064429 | -0.0075532 | 0.038074 | -0.0061673 | -0.090984 | -0.011501 | 0.0064514 | 0.10529 | 0.013733 | 0.054932 | 0.054932 | 0.14648 | 0.013733 | -0.11902 | 0.013733 | 0.10529 | -0.009155 | 0.1236 | 0.09613 | -0.022888 | -0.09613 | 121.7422 | 121.6095 | 0.01831 | 121.7422 | 121.7834 | 0.17395 | -0.022888 | 121.7056 | 121.6324 | -0.004578 | 121.7422 | 121.7194 | 0.086975 | -0.032044 | 121.875 | 121.8338 | 121.7834 | -0.24719 | 121.8521 | 121.8246 | 121.8338 | -0.2243
2815.8281 | 121.994 | -121.2753 | 0.41199 | -0.0078584 | -0.019442 | 0.019123 | 0.035382 | -0.0079382 | -0.037014 | -0.0081519 | -0.0075532 | 0.2549 | 0.27838 | -0.14695 | -0.013638 | 0.05943 | 0.068665 | 0.013733 | 0.032043 | 0.059509 | 0.18768 | 0.036621 | -0.10529 | 0.13275 | 0.2243 | 0.16022 | 0.37994 | 0.36621 | 0.14648 | 0.091553 | 121.312 | 121.17 | -0.2243 | 121.2891 | 121.3348 | 0.16479 | -0.34332 | 121.4218 | 121.3669 | -0.032043 | 121.4081 | 121.4355 | 0.068664 | -0.045776 | 121.463 | 121.344 | 121.3074 | -0.51727 | 121.6553 | 121.6415 | 121.4996 | -0.32043
2817.5625 | 120.7718 | -120.4605 | 0.10529 | -0.00022891 | -0.019442 | 0.017628 | 0.033673 | -0.0094336 | -0.035305 | -0.018833 | 7.627e-05 | 0.01308 | 0.0060093 | -0.10252 | 0.013706 | -0.019397 | 0.054932 | -0.045776 | -0.004578 | 0.009155 | 0.14191 | 0.032043 | -0.1236 | 0.018311 | 0.050354 | -0.050354 | 0.09613 | 0.10071 | -0.032043 | -0.10529 | 120.4926 | 120.3369 | 0.036621 | 120.4147 | 120.4697 | 0.13275 | -0.050354 | 120.4285 | 120.3552 | -0.009156 | 120.4788 | 120.4102 | 0.054932 | -0.004578 | 120.6024 | 120.5154 | 120.4559 | -0.22888 | 120.5566 | 120.5612 | 120.5109 | -0.21057
2819.3594 | 121.3852 | -121.0464 | 0.11444 | -0.00022891 | -0.017733 | 0.016346 | 0.037518 | -0.0098608 | -0.034024 | -0.019474 | 7.627e-05 | 0.026966 | -0.0076627 | -0.097393 | -0.014065 | 0.0017518 | 0.086975 | -0.022888 | 0.036621 | 0.064087 | 0.13733 | 0.022888 | -0.1236 | -0.018311 | 0.086975 | -0.027466 | 0.091553 | 0.10986 | -0.050354 | -0.10529 | 121.0693 | 120.9229 | 0.022888 | 121.0236 | 121.1105 | 0.18768 | -0.027466 | 120.9961 | 120.9412 | -0.022888 | 121.0281 | 121.019 | 0.07782 | -0.004578 | 121.1838 | 121.1334 | 121.0831 | -0.23804 | 121.138 | 121.1563 | 121.1334 | -0.21973
2821.1406 | 121.4447 | -121.1746 | 0.11902 | -0.00022891 | -0.018801 | 0.019337 | 0.036237 | -0.0066564 | -0.035519 | -0.018619 | 7.627e-05 | 0.026325 | -0.0078763 | -0.1006 | -0.011288 | 0.003247 | 0.027466 | -0.10071 | -0.004578 | 0.004578 | 0.16022 | 0.004578 | -0.11902 | -0.041199 | -0.013733 | -0.091553 | 0.10071 | 0.10071 | -0.041199 | -0.11902 | 121.1792 | 121.0556 | 0.041198 | 121.0739 | 121.1792 | 0.1236 | -0.091553 | 121.1334 | 121.0556 | -0.018311 | 121.1334 | 121.0831 | 0.027466 | -0.018311 | 121.3348 | 121.2021 | 121.17 | -0.23804 | 121.2753 | 121.2753 | 121.1609 | -0.23804
2822.875 | 121.4676 | -121.2616 | 0.13733 | -0.00022891 | -0.022005 | 0.019978 | 0.037732 | -0.010288 | -0.04385 | -0.020328 | 7.627e-05 | 0.020984 | -0.0072353 | -0.10337 | -0.019406 | 0.0047424 | 0.068665 | 0.036621 | 0.10071 | 0.082397 | 0.12817 | 0.022888 | -0.10529 | 0.032043 | 0.15564 | 0.073242 | 0.073242 | 0.059509 | -0.032043 | -0.082397 | 121.2845 | 121.1563 | -0.009155 | 121.2982 | 121.344 | 0.18768 | -0.068664 | 121.2296 | 121.1792 | -0.064087 | 121.2936 | 121.3348 | 0.15564 | -0.07782 | 121.3898 | 121.3303 | 121.3623 | -0.24262 | 121.3348 | 121.3211 | 121.4172 | -0.21973
2824.6719 | 121.5912 | -121.2845 | 0.10529 | -0.0078584 | -0.01816 | 0.016133 | 0.037091 | -0.0096472 | -0.031887 | -0.020115 | 7.627e-05 | 0.02782 | -0.0048855 | -0.099956 | -0.013851 | 0.00089722 | 0.10071 | 0.004578 | 0.041199 | 0.064087 | 0.14648 | 0.009155 | -0.11444 | 0.004578 | 0.09613 | -0.018311 | 0.091553 | 0.073242 | -0.054932 | -0.11444 | 121.2936 | 121.17 | 0.041198 | 121.2891 | 121.3486 | 0.17853 | -0.004578 | 121.2296 | 121.17 | -0.013733 | 121.2891 | 121.2662 | 0.09613 | -0.032044 | 121.431 | 121.3852 | 121.3257 | -0.21973 | 121.376 | 121.3577 | 121.3806 | -0.21973
2826.3906 | 121.5958 | -121.344 | 0.12817 | 0.0074006 | -0.015597 | 0.016987 | 0.035169 | -0.0049474 | -0.034237 | -0.01926 | -0.0075532 | 0.026538 | -0.0059537 | -0.098034 | -0.01321 | 0.0013244 | 0.11444 | 0.027466 | 0.041199 | 0.050354 | 0.16022 | -0.004578 | -0.11444 | 0.018311 | 0.09613 | -0.027466 | 0.086975 | 0.073242 | -0.050354 | -0.10071 | 121.3394 | 121.2296 | 0.032043 | 121.3715 | 121.3943 | 0.16479 | -0.013733 | 121.2936 | 121.2433 | -0.041199 | 121.3623 | 121.3165 | 0.073242 | -0.054932 | 121.5042 | 121.4584 | 121.3852 | -0.24262 | 121.431 | 121.4172 | 121.4401 | -0.22888
2828.1719 | 121.6599 | -121.3577 | 0.11444 | -0.015487 | -0.020296 | 0.016987 | 0.036237 | -0.0083654 | -0.039151 | -0.019474 | -0.0075532 | 0.023548 | -0.0061673 | -0.10231 | -0.013638 | 0.0036744 | 0.13733 | 0.082397 | 0.12817 | 0.086975 | 0.10071 | 0.036621 | -0.064087 | 0.068665 | 0.14648 | 0.068665 | 0.050354 | 0.041199 | -0.027466 | -0.07782 | 121.3943 | 121.2936 | -0.013733 | 121.4401 | 121.4447 | 0.15106 | 0.022888 | 121.3303 | 121.2799 | -0.064087 | 121.4264 | 121.4264 | 0.14649 | -0.073242 | 121.4584 | 121.4951 | 121.4859 | -0.17853 | 121.4081 | 121.3989 | 121.5042 | -0.19226
2829.9062 | 121.6507 | -121.3669 | 0.12817 | -0.00022891 | -0.017306 | 0.018055 | 0.035809 | -0.0081518 | -0.033596 | -0.018192 | 7.627e-05 | 0.026325 | -0.0065945 | -0.10102 | -0.011288 | 0.0023926 | 0.059509 | -0.027466 | -0.004578 | 0.022888 | 0.1236 | 0.004578 | -0.12817 | -0.045776 | 0.027466 | -0.086975 | 0.10529 | 0.09613 | -0.045776 | -0.11902 | 121.3715 | 121.2387 | -0.004578 | 121.3394 | 121.3898 | 0.15106 | -0.068665 | 121.3211 | 121.2479 | -0.022888 | 121.3211 | 121.2799 | 0.032044 | -0.032044 | 121.4905 | 121.4264 | 121.3623 | -0.25635 | 121.4722 | 121.463 | 121.3943 | -0.24719
2831.6875 | 121.6049 | -121.4401 | 0.12817 | -0.0078584 | -0.019869 | 0.017842 | 0.035596 | -0.0077246 | -0.039578 | -0.022892 | 7.627e-05 | 0.023975 | -0.0068081 | -0.10038 | -0.01556 | 0.0030334 | 0.022888 | -0.022888 | 0.013733 | 0.009155 | 0.11902 | 0.013733 | -0.13733 | -0.041199 | 0.054932 | -0.045776 | 0.11902 | 0.10986 | -0.059509 | -0.1236 | 121.4539 | 121.3028 | -0.009155 | 121.4172 | 121.4493 | 0.14648 | -0.10529 | 121.3806 | 121.3165 | -0.009155 | 121.3989 | 121.3943 | 0.07782 | -0.018311 | 121.5591 | 121.463 | 121.4539 | -0.2655 | 121.5591 | 121.55 | 121.4951 | -0.25177
2833.4844 | 121.6553 | -121.463 | 0.13275 | -0.00022891 | -0.024996 | 0.022114 | 0.035382 | -0.010288 | -0.042996 | -0.021824 | -0.015182 | 0.021625 | -0.0074491 | -0.10145 | -0.017697 | 0.0045288 | 0.10986 | 0.073242 | 0.11902 | 0.091553 | 0.11902 | 0.045776 | -0.07782 | 0.064087 | 0.18768 | 0.086975 | 0.068665 | 0.054932 | -0.004578 | -0.082397 | 121.5088 | 121.3852 | -0.013732 | 121.5363 | 121.5546 | 0.16937 | -0.022888 | 121.4584 | 121.3806 | -0.064086 | 121.5271 | 121.55 | 0.16937 | -0.077819 | 121.582 | 121.5729 | 121.582 | -0.21057 | 121.5317 | 121.5179 | 121.6507 | -0.21515
2835.1875 | 121.7194 | -121.463 | 0.1236 | -0.00022891 | -0.016878 | 0.017842 | 0.031537 | -0.0098608 | -0.033383 | -0.020542 | 7.627e-05 | 0.027179 | -0.0025357 | -0.10124 | -0.01257 | 0.0028198 | 0.064087 | -0.068665 | -0.013733 | 0.018311 | 0.13275 | 0 | -0.14191 | -0.073242 | 0.009155 | -0.091553 | 0.10529 | 0.091553 | -0.059509 | -0.11444 | 121.463 | 121.3211 | 0.009155 | 121.3943 | 121.4813 | 0.16022 | -0.059509 | 121.4035 | 121.3486 | -0.01831 | 121.3898 | 121.3715 | 0.022888 | -0.032043 | 121.5958 | 121.5271 | 121.4493 | -0.2655 | 121.5683 | 121.5546 | 121.4722 | -0.23804
2836.9844 | 121.7606 | -121.4584 | 0.13275 | -0.00022891 | -0.016024 | 0.017415 | 0.035596 | -0.0096472 | -0.034878 | -0.020115 | -0.0075532 | 0.026538 | -0.0042447 | -0.10081 | -0.01257 | 0.0041016 | 0.027466 | -0.10529 | -0.036621 | -0.013733 | 0.15106 | 0.018311 | -0.1236 | -0.054932 | -0.013733 | -0.082397 | 0.10986 | 0.10986 | -0.050354 | -0.11444 | 121.4767 | 121.3348 | 0.018311 | 121.3531 | 121.4447 | 0.10986 | -0.10529 | 121.4081 | 121.344 | -0.022888 | 121.4035 | 121.376 | 0.032044 | -0.022888 | 121.6095 | 121.4859 | 121.4218 | -0.25635 | 121.5683 | 121.5683 | 121.4447 | -0.24719
2838.7812 | 121.7422 | -121.4905 | 0.11902 | -0.00022891 | -0.016878 | 0.015706 | 0.034101 | -0.0077246 | -0.035305 | -0.018833 | 7.627e-05 | 0.028247 | -0.0023221 | -0.099316 | -0.011074 | 0.0036744 | 0.07782 | -0.004578 | 0.013733 | 0.027466 | 0.13733 | 0 | -0.11902 | -0.032043 | 0.045776 | -0.07782 | 0.10071 | 0.086975 | -0.050354 | -0.1236 | 121.4905 | 121.3715 | 0.01831 | 121.4859 | 121.5179 | 0.14649 | -0.041199 | 121.4401 | 121.3669 | -0.018311 | 121.4584 | 121.4127 | 0.045776 | -0.032044 | 121.6278 | 121.5683 | 121.5042 | -0.23804 | 121.5912 | 121.5775 | 121.5363 | -0.24261
2840.5781 | 121.7926 | -121.5088 | 0.11902 | -0.00022891 | -0.01816 | 0.020192 | 0.034101 | -0.008579 | -0.040219 | -0.018406 | -0.0075532 | 0.023334 | -0.0044583 | -0.10359 | -0.013851 | 0.0058106 | 0.12817 | 0.073242 | 0.11444 | 0.10071 | 0.10071 | 0.050354 | -0.068665 | 0.086975 | 0.14648 | 0.059509 | 0.059509 | 0.064087 | -0.004578 | -0.082397 | 121.5591 | 121.4401 | -0.018311 | 121.582 | 121.6095 | 0.16937 | 0.009155 | 121.5042 | 121.4264 | -0.05951 | 121.5958 | 121.5683 | 0.14191 | -0.054932 | 121.6095 | 121.637 | 121.6232 | -0.18768 | 121.5683 | 121.5729 | 121.6553 | -0.20142
2842.3125 | 121.8018 | -121.5363 | 0.11444 | -0.00022891 | -0.014315 | 0.018696 | 0.040296 | -0.0079382 | -0.034451 | -0.018619 | 7.627e-05 | 0.027393 | -0.00018589 | -0.10124 | -0.01257 | 0.0036744 | 0.045776 | -0.054932 | 0 | 0.018311 | 0.14648 | 0.022888 | -0.11902 | -0.054932 | 0.013733 | -0.09613 | 0.10529 | 0.10071 | -0.064087 | -0.10986 | 121.5591 | 121.4172 | 0.032043 | 121.4813 | 121.5546 | 0.13733 | -0.068665 | 121.4722 | 121.4264 | -0.009155 | 121.4813 | 121.4401 | 0.013733 | -0.013733 | 121.6827 | 121.582 | 121.5363 | -0.23346 | 121.6415 | 121.637 | 121.55 | -0.2243
2844.0938 | 121.8155 | -121.5546 | 0.11444 | -0.00022891 | -0.016238 | 0.016346 | 0.036237 | -0.0090062 | -0.035305 | -0.01926 | 0.0077058 | 0.027393 | -0.0023221 | -0.10081 | -0.013424 | 0.0045288 | 0.018311 | -0.082397 | -0.036621 | 0.004578 | 0.1236 | 0.009155 | -0.12817 | -0.073242 | -0.009155 | -0.10071 | 0.10071 | 0.10986 | -0.041199 | -0.11444 | 121.5637 | 121.4264 | 0.009155 | 121.4722 | 121.5591 | 0.13275 | -0.09613 | 121.5134 | 121.4401 | -0.013733 | 121.4813 | 121.4539 | 0.013733 | -0.004578 | 121.6782 | 121.5729 | 121.5179 | -0.24262 | 121.6553 | 121.6644 | 121.5454 | -0.22888
2845.875 | 121.7285 | -121.6049 | 0.16022 | -0.00022891 | -0.021792 | 0.019337 | 0.039441 | -0.0079382 | -0.041928 | -0.020328 | 0.0077058 | 0.022693 | 0.00024151 | -0.10252 | -0.017697 | 0.0058106 | 0.082397 | 0.018311 | 0.10071 | 0.064087 | 0.09613 | 0.050354 | -0.091553 | 0.036621 | 0.10529 | 0.041199 | 0.073242 | 0.064087 | -0.018311 | -0.091553 | 121.6553 | 121.5134 | -0.064087 | 121.6232 | 121.669 | 0.15564 | -0.07782 | 121.5866 | 121.5134 | -0.086975 | 121.6415 | 121.6461 | 0.13275 | -0.09613 | 121.701 | 121.6873 | 121.7056 | -0.25177 | 121.6782 | 121.669 | 121.7102 | -0.25177
2847.6719 | 121.8842 | -121.5637 | 0.11902 | -0.00022891 | -0.022005 | 0.015919 | 0.034955 | -0.00922 | -0.037442 | -0.020328 | 7.627e-05 | 0.024829 | 0.00024151 | -0.10167 | -0.015347 | 0.0051698 | 0.11902 | 0.050354 | 0.11444 | 0.09613 | 0.10529 | 0.041199 | -0.09613 | 0.064087 | 0.13733 | 0.054932 | 0.068665 | 0.059509 | -0.004578 | -0.07782 | 121.6049 | 121.4676 | -0.013733 | 121.6141 | 121.6599 | 0.19226 | 0 | 121.5591 | 121.4859 | -0.050354 | 121.6278 | 121.6187 | 0.13275 | -0.05951 | 121.669 | 121.6827 | 121.6782 | -0.21515 | 121.6324 | 121.6232 | 121.701 | -0.19684
2849.4062 | 121.7743 | -121.6187 | 0.16479 | -0.00022891 | -0.018587 | 0.017842 | 0.040936 | -0.010715 | -0.041287 | -0.021824 | -0.015182 | 0.023334 | 0.00066871 | -0.10295 | -0.015347 | 0.0053834 | 0.050354 | 0.032043 | 0.064087 | 0.054932 | 0.13275 | 0 | -0.12817 | -0.022888 | 0.059509 | -0.032043 | 0.10986 | 0.09613 | -0.054932 | -0.11444 | 121.6187 | 121.4905 | -0.032044 | 121.6507 | 121.6736 | 0.18311 | -0.11444 | 121.5637 | 121.5042 | -0.054932 | 121.5958 | 121.5866 | 0.082398 | -0.068665 | 121.7514 | 121.669 | 121.6827 | -0.29297 | 121.7285 | 121.7148 | 121.6782 | -0.27924
2851.1719 | 121.8613 | -121.6003 | 0.1236 | -0.00022891 | -0.017946 | 0.018483 | 0.034741 | -0.008579 | -0.03616 | -0.020542 | -0.015182 | 0.029316 | 2.7914e-05 | -0.10252 | -0.01257 | 0.0030334 | 0.036621 | -0.07782 | -0.032043 | 0 | 0.15106 | 0 | -0.14648 | -0.064087 | -0.018311 | -0.086975 | 0.10986 | 0.10529 | -0.041199 | -0.10529 | 121.6003 | 121.4539 | 0.027466 | 121.5225 | 121.6003 | 0.14648 | -0.086975 | 121.5591 | 121.4951 | -0.013733 | 121.5363 | 121.5134 | 0.018311 | -0.01831 | 121.7514 | 121.637 | 121.5683 | -0.27008 | 121.7102 | 121.7056 | 121.582 | -0.22888
2852.9062 | 121.9208 | -121.5866 | 0.12817 | -0.00022891 | -0.019228 | 0.018696 | 0.033673 | -0.0081518 | -0.03851 | -0.020755 | 7.627e-05 | 0.026111 | -0.00061309 | -0.10102 | -0.014492 | 0.0051698 | 0.10986 | 0.068665 | 0.1236 | 0.09613 | 0.10071 | 0.054932 | -0.09613 | 0.07782 | 0.15106 | 0.068665 | 0.064087 | 0.054932 | -0.013733 | -0.068665 | 121.6415 | 121.4905 | -0.027466 | 121.6553 | 121.6827 | 0.19226 | -0.018311 | 121.5729 | 121.5179 | -0.064087 | 121.6644 | 121.6553 | 0.13733 | -0.073242 | 121.6873 | 121.6965 | 121.7102 | -0.2243 | 121.6507 | 121.6415 | 121.7377 | -0.19684
2854.7031 | 121.8796 | -121.6232 | 0.11902 | 0.0074006 | -0.015169 | 0.016346 | 0.032178 | -0.00922 | -0.033383 | -0.018406 | 7.627e-05 | 0.029956 | 0.0023777 | -0.10316 | -0.010433 | 0.003247 | 0.054932 | -0.064087 | -0.018311 | 0.009155 | 0.14648 | 0.009155 | -0.14191 | -0.045776 | 0.018311 | -0.091553 | 0.1236 | 0.10529 | -0.045776 | -0.10529 | 121.6324 | 121.4813 | 0.027465 | 121.5591 | 121.6324 | 0.15106 | -0.064087 | 121.5775 | 121.5179 | 0.004577 | 121.5775 | 121.5317 | 0.013733 | -0.013733 | 121.7697 | 121.6782 | 121.6049 | -0.26093 | 121.7468 | 121.7285 | 121.6415 | -0.22431
2856.5 | 121.8658 | -121.6553 | 0.13733 | -0.0078584 | -0.020724 | 0.019551 | 0.037518 | -0.0064428 | -0.039578 | -0.021824 | 7.627e-05 | 0.030811 | 0.0025913 | -0.10402 | -0.016415 | 0.0077332 | 0.032043 | -0.054932 | -0.004578 | 0.009155 | 0.14191 | 0 | -0.13733 | -0.045776 | 0.045776 | -0.064087 | 0.11902 | 0.10071 | -0.045776 | -0.11444 | 121.6553 | 121.5179 | 0.004578 | 121.6003 | 121.6644 | 0.14648 | -0.10529 | 121.6095 | 121.5408 | -0.01831 | 121.6095 | 121.5912 | 0.050354 | -0.036621 | 121.7972 | 121.6873 | 121.6507 | -0.27466 | 121.7743 | 121.756 | 121.701 | -0.25177
2858.2188 | 121.9849 | -121.5912 | 0.16937 | -0.00022891 | -0.019655 | 0.016987 | 0.032605 | -0.007511 | -0.035733 | -0.021183 | -0.0075532 | 0.065204 | 0.045957 | -0.1147 | -0.013424 | 0.016919 | 0.073242 | -0.018311 | 0.022888 | 0.027466 | 0.14648 | 0.032043 | -0.082397 | 0.041199 | 0.10071 | 0.036621 | 0.13275 | 0.12817 | 0.018311 | -0.041199 | 121.6232 | 121.5088 | -0.022889 | 121.5729 | 121.6187 | 0.10986 | -0.096131 | 121.6095 | 121.55 | -0.036622 | 121.6324 | 121.6278 | 0.07782 | -0.041199 | 121.7377 | 121.6644 | 121.6141 | -0.25177 | 121.7239 | 121.7194 | 121.6919 | -0.21057
2860.0156 | 121.9574 | -121.6003 | 0.1831 | -0.00022891 | -0.017733 | 0.018269 | 0.033887 | -0.0064428 | -0.038083 | -0.021824 | -0.0075532 | 0.064991 | 0.049802 | -0.11384 | -0.012997 | 0.018628 | 0.13275 | 0.064087 | 0.13275 | 0.10071 | 0.10071 | 0.054932 | -0.073242 | 0.10529 | 0.1831 | 0.10986 | 0.10529 | 0.10529 | 0.027466 | -0.050354 | 121.6553 | 121.5271 | -0.082397 | 121.6644 | 121.701 | 0.17395 | -0.050354 | 121.6278 | 121.55 | -0.077819 | 121.7056 | 121.7102 | 0.16022 | -0.077819 | 121.701 | 121.7331 | 121.7331 | -0.25635 | 121.7056 | 121.7056 | 121.7834 | -0.23346
2861.7969 | 121.8475 | -121.6507 | 0.20599 | -0.0078584 | -0.020296 | 0.019123 | 0.036023 | -0.0077246 | -0.040432 | -0.022678 | -0.0075532 | 0.065845 | 0.051084 | -0.11662 | -0.016415 | 0.016919 | 0.09613 | 0.045776 | 0.086975 | 0.064087 | 0.11902 | 0.032043 | -0.11444 | 0.004578 | 0.11444 | 0.018311 | 0.13733 | 0.13733 | -0.018311 | -0.07782 | 121.6827 | 121.5363 | -0.086975 | 121.6965 | 121.7148 | 0.17853 | -0.10986 | 121.6324 | 121.5729 | -0.068665 | 121.6553 | 121.669 | 0.096131 | -0.068665 | 121.7697 | 121.7468 | 121.7377 | -0.32044 | 121.788 | 121.788 | 121.7651 | -0.28381
2863.5938 | 121.9711 | -121.6049 | 0.17853 | 0.0074006 | -0.015169 | 0.017842 | 0.037732 | -0.0087926 | -0.037228 | -0.022037 | 7.627e-05 | 0.069049 | 0.05322 | -0.11747 | -0.014279 | 0.017773 | 0.064087 | -0.041199 | 0.022888 | 0.050354 | 0.16022 | 0.013733 | -0.1236 | 0 | 0.091553 | 0.004578 | 0.17853 | 0.15106 | 0.004578 | -0.07782 | 121.6187 | 121.4813 | -0.018311 | 121.5637 | 121.6553 | 0.17395 | -0.11444 | 121.6095 | 121.5271 | 0 | 121.6049 | 121.6095 | 0.082398 | -0.027466 | 121.7651 | 121.669 | 121.6278 | -0.30212 | 121.7834 | 121.756 | 121.6965 | -0.25635
2865.3125 | 121.9711 | -121.6324 | 0.19684 | -0.015487 | -0.019442 | 0.017415 | 0.037305 | -0.0094336 | -0.032315 | -0.019687 | 7.627e-05 | 0.06969 | 0.052366 | -0.11555 | -0.013424 | 0.017773 | 0.032043 | -0.07782 | -0.022888 | 0.022888 | 0.16479 | 0.022888 | -0.12817 | -0.009155 | 0.036621 | -0.050354 | 0.15564 | 0.13733 | -0.013733 | -0.082397 | 121.6553 | 121.5042 | -0.032043 | 121.5546 | 121.6553 | 0.15106 | -0.1648 | 121.6187 | 121.55 | -0.041198 | 121.6232 | 121.582 | 0.032043 | -0.059509 | 121.7972 | 121.6644 | 121.6095 | -0.32501 | 121.788 | 121.7697 | 121.669 | -0.27924
2867.0938 | 121.9757 | -121.6324 | 0.1831 | -0.00022891 | -0.015383 | 0.017201 | 0.040296 | -0.0060156 | -0.037442 | -0.022037 | -0.0075532 | 0.069477 | 0.055356 | -0.11406 | -0.016415 | 0.01991 | 0.022888 | -0.032043 | -0.004578 | 0.022888 | 0.17395 | 0.004578 | -0.10986 | -0.018311 | 0.086975 | -0.018311 | 0.17853 | 0.14191 | -0.009155 | -0.073242 | 121.637 | 121.5225 | -0.009155 | 121.6003 | 121.6553 | 0.13275 | -0.16022 | 121.6232 | 121.5591 | -0.004577 | 121.6141 | 121.6141 | 0.054931 | -0.041198 | 121.8063 | 121.6553 | 121.6278 | -0.29297 | 121.8109 | 121.7743 | 121.7194 | -0.25635
2868.8906 | 122.0398 | -121.6553 | 0.1831 | -0.0078584 | -0.017946 | 0.015706 | 0.034955 | -0.0081518 | -0.03616 | -0.020969 | -0.0075532 | 0.069477 | 0.052793 | -0.11555 | -0.011929 | 0.016919 | 0.036621 | -0.032043 | 0.004578 | 0.022888 | 0.14648 | 0.013733 | -0.12817 | 0.013733 | 0.068665 | -0.013733 | 0.16479 | 0.13733 | -0.009155 | -0.073242 | 121.669 | 121.5271 | -0.036621 | 121.6232 | 121.6782 | 0.15106 | -0.14648 | 121.6461 | 121.582 | -0.01831 | 121.669 | 121.6415 | 0.059509 | -0.045776 | 121.8018 | 121.6919 | 121.6599 | -0.31128 | 121.8201 | 121.7926 | 121.7239 | -0.25635
2870.7031 | 121.994 | -121.6736 | 0.17853 | 0.0074006 | -0.019015 | 0.017415 | 0.033246 | -0.0079382 | -0.036374 | -0.020328 | 7.627e-05 | 0.070758 | 0.05792 | -0.11576 | -0.011715 | 0.019482 | 0.068665 | 0.009155 | 0.009155 | 0.041199 | 0.16022 | 0.027466 | -0.10529 | -0.004578 | 0.073242 | -0.032043 | 0.15564 | 0.17853 | 0.004578 | -0.059509 | 121.7011 | 121.5683 | -0.018311 | 121.6827 | 121.7148 | 0.14649 | -0.10986 | 121.6782 | 121.6141 | -0.022888 | 121.669 | 121.6415 | 0.027466 | 0 | 121.8338 | 121.7422 | 121.6827 | -0.28381 | 121.8292 | 121.8521 | 121.7468 | -0.23804
2872.5 | 121.9208 | -121.6644 | 0.21057 | -0.015487 | -0.021364 | 0.021687 | 0.037732 | -0.0096472 | -0.040219 | -0.023746 | 7.627e-05 | 0.068409 | 0.055997 | -0.11961 | -0.018337 | 0.019482 | 0.022888 | -0.027466 | 0.032043 | 0.027466 | 0.14648 | 0.022888 | -0.13275 | -0.018311 | 0.10986 | -0.004578 | 0.17853 | 0.17395 | -0.022888 | -0.07782 | 121.6873 | 121.5317 | -0.064087 | 121.637 | 121.6919 | 0.16022 | -0.18768 | 121.6415 | 121.5866 | -0.032043 | 121.6461 | 121.6599 | 0.073242 | -0.036621 | 121.8109 | 121.6873 | 121.6965 | -0.34332 | 121.843 | 121.8384 | 121.7743 | -0.28839
2874.2188 | 121.9482 | -121.7331 | 0.20599 | -0.00022891 | -0.024996 | 0.019551 | 0.033887 | -0.0077246 | -0.044705 | -0.023105 | 7.627e-05 | 0.066272 | 0.053647 | -0.11876 | -0.016415 | 0.019482 | 0.07782 | 0.022888 | 0.086975 | 0.068665 | 0.11902 | 0.032043 | -0.091553 | 0.041199 | 0.15106 | 0.068665 | 0.13275 | 0.12817 | 0.027466 | -0.045776 | 121.7651 | 121.6415 | -0.086975 | 121.756 | 121.8018 | 0.16022 | -0.12817 | 121.7606 | 121.6873 | -0.073243 | 121.7743 | 121.8018 | 0.11444 | -0.07782 | 121.8521 | 121.8109 | 121.8201 | -0.29755 | 121.8658 | 121.8613 | 121.8842 | -0.25177
2876.0312 | 121.962 | -121.6965 | 0.20599 | -0.00022891 | -0.020937 | 0.019551 | 0.038159 | -0.0081518 | -0.041928 | -0.020115 | 0.0077058 | 0.067127 | 0.05557 | -0.11961 | -0.016415 | 0.018628 | 0.15564 | 0.10986 | 0.15106 | 0.10529 | 0.11902 | 0.054932 | -0.091553 | 0.09613 | 0.23346 | 0.14191 | 0.12817 | 0.11902 | 0.032043 | -0.032043 | 121.7514 | 121.6049 | -0.086975 | 121.8063 | 121.8018 | 0.19684 | -0.050354 | 121.7285 | 121.6644 | -0.07782 | 121.7926 | 121.8384 | 0.17395 | -0.086975 | 121.8155 | 121.8521 | 121.8475 | -0.29755 | 121.8246 | 121.8155 | 121.9299 | -0.23804
2877.8281 | 121.9849 | -121.7331 | 0.19684 | -0.015487 | -0.019869 | 0.020405 | 0.0388 | -0.010715 | -0.041501 | -0.021396 | -0.0075532 | 0.06734 | 0.056424 | -0.1179 | -0.018551 | 0.01991 | 0.10071 | 0.050354 | 0.11902 | 0.082397 | 0.14191 | 0.041199 | -0.091553 | 0.09613 | 0.17395 | 0.10986 | 0.13275 | 0.12817 | 0.032043 | -0.054932 | 121.7743 | 121.6415 | -0.054931 | 121.7834 | 121.8155 | 0.17395 | -0.09613 | 121.7651 | 121.6782 | -0.064087 | 121.8292 | 121.843 | 0.16479 | -0.068664 | 121.875 | 121.8338 | 121.8521 | -0.28839 | 121.8658 | 121.8613 | 121.907 | -0.25177
2879.6406 | 122.1085 | -121.6873 | 0.17395 | -0.0078584 | -0.019442 | 0.018269 | 0.034314 | -0.0087926 | -0.035092 | -0.02161 | -0.0075532 | 0.070545 | 0.05557 | -0.11833 | -0.01257 | 0.018201 | 0.082397 | -0.041199 | 0.027466 | 0.036621 | 0.15564 | 0.032043 | -0.12817 | 0.064087 | 0.086975 | 0.027466 | 0.14191 | 0.15106 | 0.004578 | -0.059509 | 121.7194 | 121.5591 | -0.01831 | 121.6461 | 121.7239 | 0.1648 | -0.091553 | 121.6919 | 121.6278 | -0.032043 | 121.7514 | 121.7148 | 0.086975 | -0.022888 | 121.843 | 121.7697 | 121.7148 | -0.30212 | 121.8292 | 121.8384 | 121.7743 | -0.23346
2881.3594 | 122.0352 | -121.7056 | 0.20599 | -0.00022891 | -0.01282 | 0.015492 | 0.039014 | -0.00687 | -0.03146 | -0.017338 | 7.627e-05 | 0.073535 | 0.058561 | -0.11598 | -0.013851 | 0.017133 | 0.082397 | -0.045776 | 0.004578 | 0.027466 | 0.14191 | 0.032043 | -0.11902 | -0.013733 | 0.050354 | -0.036621 | 0.16479 | 0.14191 | -0.009155 | -0.07782 | 121.7377 | 121.5866 | -0.064087 | 121.6599 | 121.7331 | 0.14649 | -0.1236 | 121.6965 | 121.6278 | -0.041199 | 121.6919 | 121.669 | 0.041199 | -0.064087 | 121.8475 | 121.788 | 121.7102 | -0.32501 | 121.8704 | 121.8475 | 121.756 | -0.28381
2883.1406 | 122.0306 | -121.7285 | 0.17853 | -0.015487 | -0.016878 | 0.018269 | 0.040509 | -0.0087926 | -0.037869 | -0.020328 | -0.0075532 | 0.071613 | 0.06091 | -0.11598 | -0.016628 | 0.016492 | 0.041199 | -0.027466 | -0.004578 | 0.022888 | 0.16937 | 0 | -0.11444 | 0 | 0.073242 | -0.027466 | 0.16937 | 0.15564 | -0.027466 | -0.064087 | 121.7285 | 121.6141 | -0.009155 | 121.701 | 121.7514 | 0.13733 | -0.13733 | 121.701 | 121.6644 | -0.009155 | 121.7285 | 121.701 | 0.036621 | -0.022888 | 121.8979 | 121.7697 | 121.7239 | -0.29297 | 121.8979 | 121.8842 | 121.8018 | -0.24261
2884.875 | 122.0306 | -121.7331 | 0.20142 | -0.0078584 | -0.023287 | 0.018055 | 0.034101 | -0.0098608 | -0.042996 | -0.021183 | 0.0077058 | 0.067554 | 0.055997 | -0.11769 | -0.018551 | 0.021619 | 0.07782 | 0.050354 | 0.09613 | 0.068665 | 0.10529 | 0.064087 | -0.086975 | 0.082397 | 0.16937 | 0.10986 | 0.15106 | 0.14191 | 0.036621 | -0.041199 | 121.7972 | 121.6461 | -0.09613 | 121.7834 | 121.8018 | 0.15564 | -0.1236 | 121.7697 | 121.6919 | -0.050354 | 121.8155 | 121.843 | 0.15106 | -0.059509 | 121.8384 | 121.8109 | 121.8292 | -0.28839 | 121.8842 | 121.875 | 121.9025 | -0.24262
2886.6719 | 121.9711 | -121.7789 | 0.21057 | -0.00022891 | -0.024142 | 0.015919 | 0.03645 | -0.0072974 | -0.040646 | -0.023533 | -0.0075532 | 0.06969 | 0.055997 | -0.11619 | -0.016201 | 0.020337 | 0.10529 | 0.054932 | 0.09613 | 0.073242 | 0.1236 | 0.045776 | -0.064087 | 0.07782 | 0.15106 | 0.068665 | 0.1236 | 0.11902 | 0.036621 | -0.032043 | 121.8246 | 121.7148 | -0.086975 | 121.8338 | 121.8521 | 0.13733 | -0.10529 | 121.8155 | 121.7468 | -0.086975 | 121.8567 | 121.8475 | 0.10071 | -0.091552 | 121.9025 | 121.8842 | 121.875 | -0.27466 | 121.9025 | 121.8979 | 121.9299 | -0.24261
2888.4688 | 121.994 | -121.7468 | 0.20599 | -0.00022891 | -0.021792 | 0.017201 | 0.0388 | -0.0064428 | -0.039151 | -0.022037 | -0.0075532 | 0.06969 | 0.060483 | -0.11769 | -0.017056 | 0.019482 | 0.082397 | 0.018311 | 0.10071 | 0.064087 | 0.12817 | 0.022888 | -0.086975 | 0.068665 | 0.13275 | 0.068665 | 0.12817 | 0.11444 | 0.022888 | -0.041199 | 121.7697 | 121.6599 | -0.07782 | 121.7651 | 121.8109 | 0.15106 | -0.1236 | 121.7697 | 121.7056 | -0.07782 | 121.8155 | 121.8155 | 0.10986 | -0.091553 | 121.875 | 121.8292 | 121.8475 | -0.29297 | 121.875 | 121.8613 | 121.8796 | -0.24719
2890.2656 | 122.0032 | -121.7834 | 0.21515 | -0.00022891 | -0.022433 | 0.018269 | 0.032605 | -0.00922 | -0.034665 | -0.021396 | 7.627e-05 | 0.07204 | 0.056211 | -0.11833 | -0.012356 | 0.019696 | 0.15106 | 0.10071 | 0.1236 | 0.091553 | 0.11444 | 0.059509 | -0.073242 | 0.12817 | 0.17853 | 0.10071 | 0.1236 | 0.11902 | 0.018311 | -0.018311 | 121.843 | 121.7102 | -0.10071 | 121.8842 | 121.875 | 0.16479 | -0.064087 | 121.8018 | 121.7651 | -0.091553 | 121.9116 | 121.8842 | 0.11902 | -0.09613 | 121.8979 | 121.9345 | 121.907 | -0.28839 | 121.907 | 121.9025 | 121.962 | -0.23346
2891.9844 | 122.1268 | -121.7285 | 0.19226 | 0.0074006 | -0.02051 | 0.017201 | 0.033887 | -0.0043066 | -0.034665 | -0.019474 | 0.015335 | 0.07439 | 0.059415 | -0.11747 | -0.011929 | 0.019269 | 0.14648 | 0.059509 | 0.091553 | 0.073242 | 0.11902 | 0.050354 | -0.09613 | 0.11902 | 0.17853 | 0.10529 | 0.13275 | 0.1236 | 0.041199 | -0.032043 | 121.7789 | 121.6324 | -0.073242 | 121.788 | 121.8018 | 0.16937 | -0.045777 | 121.7697 | 121.6965 | -0.05951 | 121.8475 | 121.8338 | 0.13733 | -0.068665 | 121.8475 | 121.875 | 121.8201 | -0.28839 | 121.8613 | 121.8521 | 121.907 | -0.2243
2893.7812 | 122.0947 | -121.7606 | 0.19226 | -0.0078584 | -0.019442 | 0.018269 | 0.034528 | -0.0072974 | -0.037228 | -0.020969 | -0.0075532 | 0.075885 | 0.058133 | -0.11811 | -0.013851 | 0.019269 | 0.16479 | 0.082397 | 0.14191 | 0.11444 | 0.10071 | 0.064087 | -0.086975 | 0.13275 | 0.21057 | 0.10529 | 0.1236 | 0.11902 | 0.045776 | -0.036621 | 121.8246 | 121.6736 | -0.091553 | 121.843 | 121.875 | 0.20142 | -0.027466 | 121.8063 | 121.7239 | -0.068665 | 121.8933 | 121.8658 | 0.14191 | -0.073242 | 121.8613 | 121.9254 | 121.9025 | -0.27924 | 121.8842 | 121.8796 | 121.9711 | -0.22888
2895.5781 | 122.0718 | -121.7514 | 0.19226 | -0.0078584 | -0.019228 | 0.019764 | 0.040509 | -0.0083654 | -0.035946 | -0.02161 | 7.627e-05 | 0.073963 | 0.062833 | -0.1179 | -0.015774 | 0.020978 | 0.059509 | -0.032043 | 0.009155 | 0.032043 | 0.17395 | 0 | -0.13275 | -0.004578 | 0.07782 | -0.027466 | 0.1831 | 0.15564 | 0.004578 | -0.064087 | 121.7514 | 121.6187 | -0.018311 | 121.7194 | 121.7834 | 0.16479 | -0.13275 | 121.756 | 121.6873 | -0.009156 | 121.7468 | 121.7239 | 0.036621 | -0.036621 | 121.9254 | 121.8109 | 121.7606 | -0.32501 | 121.9345 | 121.907 | 121.8292 | -0.25635
2897.3594 | 122.0215 | -121.8018 | 0.21515 | -0.00022891 | -0.023073 | 0.020405 | 0.036023 | -0.00922 | -0.041287 | -0.020755 | 7.627e-05 | 0.072895 | 0.061551 | -0.11897 | -0.014919 | 0.020764 | 0.14191 | 0.10071 | 0.14191 | 0.10071 | 0.11444 | 0.064087 | -0.07782 | 0.10529 | 0.21973 | 0.11444 | 0.12817 | 0.11444 | 0.041199 | -0.054932 | 121.8658 | 121.7239 | -0.10071 | 121.9025 | 121.9025 | 0.17853 | -0.073242 | 121.843 | 121.7468 | -0.086975 | 121.907 | 121.9162 | 0.16937 | -0.10071 | 121.9162 | 121.9437 | 121.9437 | -0.29297 | 121.9299 | 121.9162 | 122.0215 | -0.27008
2899.0781 | 122.0169 | -121.8063 | 0.2243 | -0.00022891 | -0.019869 | 0.020192 | 0.041577 | -0.0077246 | -0.037442 | -0.019901 | -0.015182 | 0.075672 | 0.063901 | -0.11876 | -0.017269 | 0.019696 | 0.15106 | 0.10529 | 0.13733 | 0.09613 | 0.09613 | 0.041199 | -0.082397 | 0.09613 | 0.21057 | 0.10071 | 0.13733 | 0.13275 | 0.009155 | -0.022888 | 121.8475 | 121.7239 | -0.12817 | 121.9116 | 121.9025 | 0.17853 | -0.073242 | 121.8155 | 121.7834 | -0.086975 | 121.9025 | 121.907 | 0.1236 | -0.091553 | 121.9025 | 121.9574 | 121.9437 | -0.3067 | 121.9437 | 121.9391 | 122.0169 | -0.24719
2900.8906 | 122.0993 | -121.8246 | 0.17853 | 0.0074006 | -0.019228 | 0.01656 | 0.0388 | -0.0047338 | -0.036587 | -0.022464 | -0.0075532 | 0.056446 | 0.038694 | -0.11128 | -0.013638 | 0.013074 | 0.036621 | -0.027466 | 0.009155 | 0.022888 | 0.16022 | 0.018311 | -0.13733 | -0.009155 | 0.073242 | -0.045776 | 0.15564 | 0.15564 | -0.022888 | -0.10529 | 121.843 | 121.6873 | -0.018311 | 121.7972 | 121.8475 | 0.16022 | -0.14191 | 121.8018 | 121.7194 | -0.022888 | 121.8155 | 121.7789 | 0.05951 | -0.022888 | 121.9849 | 121.8613 | 121.8338 | -0.31586 | 121.9803 | 121.9803 | 121.8979 | -0.28381
2902.6875 | 122.0673 | -121.8521 | 0.17395 | -0.00022891 | -0.019869 | 0.02126 | 0.038373 | -0.0083654 | -0.039578 | -0.021396 | 7.627e-05 | 0.039783 | 0.022672 | -0.11021 | -0.016415 | 0.0085876 | 0.12817 | 0.13733 | 0.13733 | 0.10071 | 0.10529 | 0.036621 | -0.086975 | 0.09613 | 0.2243 | 0.10529 | 0.086975 | 0.068665 | 0.027466 | -0.064087 | 121.8887 | 121.7651 | -0.068664 | 121.9894 | 121.9528 | 0.18768 | -0.045776 | 121.8796 | 121.788 | -0.086975 | 121.9482 | 121.9574 | 0.16937 | -0.10528 | 121.9574 | 121.9803 | 121.9894 | -0.26092 | 121.9391 | 121.9208 | 122.0764 | -0.23804
2904.4844 | 122.0627 | -121.8842 | 0.16479 | 0.01503 | -0.020724 | 0.016133 | 0.037305 | -0.0081518 | -0.036587 | -0.020755 | 0.0077058 | 0.041492 | 0.024595 | -0.1085 | -0.01321 | 0.012647 | 0.11902 | 0.091553 | 0.11444 | 0.07782 | 0.10529 | 0.059509 | -0.091553 | 0.09613 | 0.15564 | 0.068665 | 0.091553 | 0.07782 | 0.013733 | -0.054932 | 121.9437 | 121.7926 | -0.059509 | 121.9757 | 121.962 | 0.16937 | -0.045776 | 121.8979 | 121.8292 | -0.073242 | 121.9803 | 121.9528 | 0.1236 | -0.086975 | 121.9894 | 122.0032 | 121.9986 | -0.25635 | 121.9757 | 121.962 | 122.0398 | -0.21973
2906.2188 | 122.1863 | -121.8567 | 0.14191 | -0.0078584 | -0.020083 | 0.016774 | 0.033246 | -0.010929 | -0.031887 | -0.018833 | 7.627e-05 | 0.043842 | 0.019468 | -0.10637 | -0.011929 | 0.0070924 | 0.050354 | -0.036621 | 0 | 0.013733 | 0.13733 | 0.032043 | -0.12817 | -0.009155 | 0.032043 | -0.050354 | 0.11902 | 0.11444 | -0.036621 | -0.11444 | 121.8887 | 121.7285 | -0.004578 | 121.8201 | 121.8704 | 0.14191 | -0.091553 | 121.8201 | 121.7422 | -0.022888 | 121.8475 | 121.8063 | 0.064087 | -0.027466 | 121.994 | 121.907 | 121.8567 | -0.27008 | 121.9757 | 121.9711 | 121.8887 | -0.25635
2908.0156 | 122.0856 | -121.8887 | 0.15564 | -0.0078584 | -0.018374 | 0.018269 | 0.038159 | -0.0087926 | -0.037869 | -0.020542 | -0.015182 | 0.039783 | 0.021177 | -0.10615 | -0.018337 | 0.008374 | 0.041199 | -0.018311 | 0.004578 | 0.009155 | 0.13733 | 0.018311 | -0.12817 | -0.018311 | 0.07782 | -0.027466 | 0.14191 | 0.11444 | -0.050354 | -0.10986 | 121.907 | 121.7606 | -0.018311 | 121.8704 | 121.8979 | 0.13733 | -0.11444 | 121.8384 | 121.7789 | -0.013733 | 121.8704 | 121.8613 | 0.082397 | -0.041199 | 122.0261 | 121.9299 | 121.8933 | -0.28381 | 122.0306 | 122.0032 | 121.9666 | -0.2655
2909.8125 | 122.2 | -121.8887 | 0.14191 | -0.0078584 | -0.018587 | 0.015919 | 0.034741 | -0.0098608 | -0.037869 | -0.017551 | -0.0075532 | 0.041919 | 0.017972 | -0.10722 | -0.01321 | 0.0075196 | 0.09613 | 0.022888 | 0.064087 | 0.064087 | 0.10529 | 0.045776 | -0.091553 | 0.091553 | 0.11902 | 0.054932 | 0.091553 | 0.09613 | 0.018311 | -0.073242 | 121.9345 | 121.7972 | -0.036621 | 121.9116 | 121.9528 | 0.15564 | -0.045777 | 121.907 | 121.8155 | -0.050354 | 121.9803 | 121.9437 | 0.12817 | -0.045777 | 121.994 | 121.9849 | 121.9528 | -0.23346 | 121.9803 | 121.9849 | 122.0078 | -0.21515
2911.5312 | 122.081 | -121.8979 | 0.17853 | 0.0074006 | -0.022646 | 0.017201 | 0.035382 | -0.0098608 | -0.039792 | -0.022037 | 0.0077058 | 0.040851 | 0.017972 | -0.10658 | -0.01556 | 0.010724 | 0.10529 | 0.082397 | 0.11444 | 0.068665 | 0.10529 | 0.054932 | -0.082397 | 0.068665 | 0.13275 | 0.059509 | 0.10071 | 0.07782 | 0.004578 | -0.059509 | 121.9528 | 121.8155 | -0.073242 | 121.9803 | 121.9666 | 0.15106 | -0.073242 | 121.9025 | 121.8384 | -0.07782 | 121.9666 | 121.9574 | 0.11902 | -0.10071 | 122.0032 | 122.0032 | 122.0123 | -0.26092 | 121.9986 | 121.9757 | 122.0306 | -0.23804
2913.3281 | 122.1954 | -121.8567 | 0.13733 | -0.00022891 | -0.021151 | 0.01656 | 0.03346 | -0.0064428 | -0.034878 | -0.020755 | 7.627e-05 | 0.043628 | 0.019254 | -0.10807 | -0.012356 | 0.0096558 | 0.1236 | 0.054932 | 0.10986 | 0.082397 | 0.12817 | 0.045776 | -0.086975 | 0.086975 | 0.16022 | 0.059509 | 0.091553 | 0.091553 | 0.009155 | -0.054932 | 121.9025 | 121.7697 | -0.009155 | 121.9116 | 121.9391 | 0.16937 | -0.013733 | 121.8658 | 121.8018 | -0.045776 | 121.9437 | 121.9162 | 0.11444 | -0.045776 | 121.9849 | 121.9803 | 121.9666 | -0.2243 | 121.9482 | 121.9482 | 122.0169 | -0.19226
2915.125 | 122.0718 | -121.9025 | 0.18768 | -0.00022891 | -0.022005 | 0.017201 | 0.035596 | -0.007511 | -0.041287 | -0.018833 | 7.627e-05 | 0.041065 | 0.020749 | -0.1085 | -0.01556 | 0.011151 | 0.10529 | 0.086975 | 0.13733 | 0.082397 | 0.10986 | 0.07782 | -0.091553 | 0.07782 | 0.13275 | 0.059509 | 0.086975 | 0.09613 | 0.009155 | -0.054932 | 121.9803 | 121.8109 | -0.07782 | 121.9894 | 121.9849 | 0.17395 | -0.082397 | 121.9116 | 121.8475 | -0.10071 | 121.9803 | 121.962 | 0.11444 | -0.091553 | 122.0123 | 122.0078 | 122.0398 | -0.27924 | 121.9894 | 121.9986 | 122.0352 | -0.24261
2916.9219 | 122.1313 | -121.9299 | 0.13733 | -0.00022891 | -0.017306 | 0.020619 | 0.039014 | -0.0087926 | -0.038723 | -0.020969 | 7.627e-05 | 0.017566 | -0.0014675 | -0.099102 | -0.017483 | 0.0019654 | 0.027466 | -0.032043 | -0.004578 | 0.004578 | 0.15106 | 0.004578 | -0.15106 | -0.050354 | 0.036621 | -0.068665 | 0.10986 | 0.091553 | -0.054932 | -0.12817 | 121.9345 | 121.7789 | 0.013733 | 121.8979 | 121.9345 | 0.15564 | -0.10986 | 121.875 | 121.8018 | -0.027466 | 121.8796 | 121.8613 | 0.059509 | -0.045776 | 122.081 | 121.9574 | 121.9254 | -0.28839 | 122.0398 | 122.0215 | 121.9666 | -0.2655
2918.7188 | 122.1909 | -121.9482 | 0.10071 | -0.00022891 | -0.017092 | 0.016346 | 0.036237 | -0.010929 | -0.032101 | -0.017124 | -0.0075532 | 0.021411 | -0.0010403 | -0.10102 | -0.011501 | 0.0011108 | 0.11444 | 0.032043 | 0.050354 | 0.064087 | 0.11902 | 0.022888 | -0.12817 | 0.013733 | 0.091553 | -0.054932 | 0.091553 | 0.068665 | -0.041199 | -0.11902 | 121.9711 | 121.8201 | 0.018311 | 121.9803 | 122.0123 | 0.19226 | 0.013733 | 121.907 | 121.8292 | -0.009155 | 121.962 | 121.8933 | 0.064087 | -0.032043 | 122.0673 | 122.0627 | 121.9986 | -0.22888 | 122.0398 | 122.0169 | 122.0398 | -0.21973
2920.4531 | 122.168 | -121.9528 | 0.13275 | -0.00022891 | -0.022219 | 0.021046 | 0.037732 | -0.0077246 | -0.041501 | -0.021396 | -0.0075532 | 0.014789 | -0.0012539 | -0.10167 | -0.017697 | 0.0023926 | 0.09613 | 0.050354 | 0.10071 | 0.073242 | 0.10986 | 0.018311 | -0.11444 | 0.054932 | 0.15106 | 0.073242 | 0.068665 | 0.054932 | -0.027466 | -0.086975 | 121.9711 | 121.8384 | -0.022888 | 122.0032 | 122.0261 | 0.18768 | -0.036621 | 121.9254 | 121.8658 | -0.064086 | 122.0078 | 122.0261 | 0.16022 | -0.077819 | 122.0627 | 122.049 | 122.0535 | -0.24719 | 122.0215 | 122.0078 | 122.1039 | -0.21973
2922.2344 | 122.2366 | -121.962 | 0.09613 | -0.00022891 | -0.019655 | 0.017415 | 0.040723 | -0.0090062 | -0.033596 | -0.021396 | -0.0075532 | 0.019702 | -0.00039949 | -0.099956 | -0.01321 | 0.0019654 | 0.036621 | -0.054932 | 0.004578 | 0.032043 | 0.15564 | 0 | -0.12817 | -0.041199 | 0.064087 | -0.07782 | 0.10986 | 0.082397 | -0.064087 | -0.1236 | 121.962 | 121.8338 | 0.05951 | 121.907 | 121.994 | 0.16022 | -0.059509 | 121.8979 | 121.8384 | 0.013733 | 121.9208 | 121.8842 | 0.045776 | -0.013733 | 122.1176 | 121.9986 | 121.9666 | -0.2243 | 122.0718 | 122.0444 | 122.0261 | -0.21973
2924.0469 | 122.2 | -121.9803 | 0.14191 | -0.0078584 | -0.022646 | 0.018483 | 0.033032 | -0.0087926 | -0.039364 | -0.017124 | -0.0075532 | 0.016498 | -0.0023221 | -0.099529 | -0.011074 | 0.0041016 | 0.14648 | 0.07782 | 0.11902 | 0.082397 | 0.10071 | 0.045776 | -0.086975 | 0.086975 | 0.14648 | 0.059509 | 0.054932 | 0.041199 | -0.032043 | -0.086975 | 122.0261 | 121.8933 | -0.041199 | 122.0581 | 122.0627 | 0.16937 | 0.004577 | 121.9482 | 121.8933 | -0.086975 | 122.0673 | 122.0398 | 0.14648 | -0.10071 | 122.081 | 122.1268 | 122.0993 | -0.22888 | 122.0352 | 122.0215 | 122.1268 | -0.22888
2925.8438 | 122.1451 | -122.0078 | 0.12817 | -0.0078584 | -0.019015 | 0.021687 | 0.0388 | -0.008579 | -0.040219 | -0.018619 | -0.0075532 | 0.019702 | 0.0019505 | -0.099102 | -0.014919 | 0.0053834 | 0.050354 | -0.013733 | 0.022888 | 0.013733 | 0.13733 | 0.009155 | -0.13733 | -0.036621 | 0.064087 | -0.050354 | 0.1236 | 0.10071 | -0.045776 | -0.11444 | 122.0169 | 121.8704 | 0.009155 | 121.994 | 122.0215 | 0.15106 | -0.07782 | 121.962 | 121.8933 | -0.004578 | 121.9711 | 121.9574 | 0.064087 | -0.027466 | 122.1451 | 122.0581 | 122.0306 | -0.2655 | 122.1313 | 122.1085 | 122.0718 | -0.24262
2927.6406 | 122.2183 | -122.0078 | 0.12817 | -0.0078584 | -0.022433 | 0.020192 | 0.040082 | -0.0077246 | -0.039792 | -0.019901 | 0.0077058 | 0.016925 | 0.0036593 | -0.10231 | -0.015774 | 0.002179 | 0.11444 | 0.091553 | 0.1236 | 0.086975 | 0.10986 | 0.022888 | -0.091553 | 0.082397 | 0.17853 | 0.10986 | 0.064087 | 0.059509 | -0.022888 | -0.064087 | 122.0306 | 121.9162 | -0.018311 | 122.0993 | 122.0947 | 0.17853 | -0.013733 | 121.9849 | 121.9437 | -0.064087 | 122.0901 | 122.1176 | 0.17395 | -0.068665 | 122.1176 | 122.1222 | 122.1313 | -0.21973 | 122.0718 | 122.0673 | 122.1863 | -0.19226
2929.3594 | 122.3007 | -121.9757 | 0.091553 | -0.00022891 | -0.020296 | 0.017415 | 0.033032 | -0.0094336 | -0.034665 | -0.018619 | 7.627e-05 | 0.022907 | 0.0010959 | -0.10231 | -0.011501 | 0.0023926 | 0.086975 | -0.004578 | 0.027466 | 0.032043 | 0.12817 | 0.022888 | -0.10071 | 0.045776 | 0.11444 | 0.018311 | 0.068665 | 0.064087 | -0.018311 | -0.086975 | 121.9986 | 121.875 | 0.036621 | 121.9711 | 122.0078 | 0.13275 | -0.004578 | 121.9574 | 121.8887 | -0.022888 | 122.0215 | 121.994 | 0.10529 | -0.027466 | 122.1039 | 122.0627 | 122.0032 | -0.19226 | 122.0444 | 122.0398 | 122.0901 | -0.17853
2931.1562 | 122.3145 | -121.9803 | 0.10986 | -0.00022891 | -0.017733 | 0.017415 | 0.033887 | -0.010074 | -0.03381 | -0.018406 | 0.0077058 | 0.025898 | 0.0036593 | -0.099316 | -0.010006 | 0.0034608 | 0.068665 | -0.045776 | 0.004578 | 0.022888 | 0.15106 | 0.022888 | -0.12817 | 0.009155 | 0.059509 | -0.032043 | 0.091553 | 0.073242 | -0.045776 | -0.09613 | 122.0032 | 121.8521 | 0.041199 | 121.9345 | 122.0032 | 0.15106 | -0.041198 | 121.9345 | 121.8842 | -0.01831 | 121.9894 | 121.9482 | 0.064087 | -0.036621 | 122.1313 | 122.049 | 121.9849 | -0.23804 | 122.0718 | 122.0535 | 122.0398 | -0.20599
2932.9531 | 122.1725 | -122.0306 | 0.15106 | -0.00022891 | -0.024142 | 0.021046 | 0.035169 | -0.010715 | -0.04086 | -0.021824 | 7.627e-05 | 0.023548 | 0.0047275 | -0.10145 | -0.015988 | 0.0047424 | 0.10071 | 0.064087 | 0.10986 | 0.050354 | 0.10986 | 0.041199 | -0.09613 | 0.054932 | 0.11444 | 0.036621 | 0.068665 | 0.050354 | -0.032043 | -0.091553 | 122.0718 | 121.9345 | -0.041199 | 122.0947 | 122.081 | 0.14648 | -0.050354 | 121.9986 | 121.9391 | -0.082397 | 122.0856 | 122.0673 | 0.12817 | -0.10071 | 122.1405 | 122.1313 | 122.1405 | -0.24719 | 122.0993 | 122.081 | 122.1451 | -0.24261
2934.7344 | 122.2733 | -122.0032 | 0.13733 | 0.0074006 | -0.023073 | 0.017842 | 0.036878 | -0.010074 | -0.036801 | -0.019901 | 7.627e-05 | 0.024616 | 0.0094273 | -0.1038 | -0.012142 | 0.0041016 | 0.13275 | 0.086975 | 0.12817 | 0.10986 | 0.10071 | 0.059509 | -0.091553 | 0.086975 | 0.15106 | 0.054932 | 0.082397 | 0.068665 | -0.018311 | -0.054932 | 122.0627 | 121.9116 | -0.036621 | 122.0901 | 122.113 | 0.20142 | -0.004578 | 121.9849 | 121.9482 | -0.054932 | 122.0901 | 122.0581 | 0.10986 | -0.068664 | 122.1039 | 122.1359 | 122.1313 | -0.22888 | 122.0856 | 122.0718 | 122.1542 | -0.19226
2936.4688 | 122.2916 | -121.962 | 0.12817 | -0.00022891 | -0.020083 | 0.019978 | 0.037732 | -0.0072974 | -0.034451 | -0.019901 | -0.015182 | 0.03252 | 0.013913 | -0.10359 | -0.012142 | 0.004956 | 0.045776 | -0.022888 | -0.004578 | 0.022888 | 0.14648 | 0.004578 | -0.13275 | -0.041199 | 0.073242 | -0.050354 | 0.11902 | 0.086975 | -0.054932 | -0.10071 | 121.9666 | 121.8292 | 0.01831 | 121.9391 | 121.9849 | 0.15564 | -0.082398 | 121.907 | 121.8613 | -0.009155 | 121.9208 | 121.9116 | 0.050354 | -0.041199 | 122.1085 | 122.0078 | 121.9574 | -0.26093 | 122.081 | 122.0489 | 122.0352 | -0.22888
2938.25 | 122.2504 | -121.9711 | 0.16022 | -0.0078584 | -0.018374 | 0.01891 | 0.039227 | -0.0070836 | -0.03851 | -0.021183 | 0.0077058 | 0.044483 | 0.032712 | -0.10786 | -0.014706 | 0.010083 | 0.036621 | -0.036621 | -0.004578 | 0.013733 | 0.14191 | -0.004578 | -0.14191 | -0.032043 | 0.054932 | -0.045776 | 0.12817 | 0.1236 | -0.032043 | -0.11444 | 121.9666 | 121.8292 | -0.01831 | 121.9345 | 121.9849 | 0.15564 | -0.1236 | 121.9391 | 121.8567 | -0.032043 | 121.9391 | 121.9254 | 0.068665 | -0.036621 | 122.113 | 122.0078 | 121.9666 | -0.30212 | 122.0993 | 122.0947 | 122.0261 | -0.27466
2940.0469 | 121.8887 | -120.5383 | 1.3229 | -0.00022891 | -0.024782 | 0.020832 | 0.035169 | 0.0014612 | -0.04321 | -0.031223 | -0.022812 | 0.85155 | 1.1004 | -0.3751 | -0.015774 | 0.27476 | 0.20599 | 0.19684 | 0.2243 | 0.22888 | 0.26093 | 0.19684 | 0.045776 | 0.66376 | 0.78735 | 0.85602 | 1.1581 | 1.1444 | 0.81482 | 0.75989 | 120.7352 | 120.5841 | -1.062 | 120.7352 | 120.7672 | 0.18311 | -1.1169 | 121.3531 | 121.2982 | -0.1648 | 121.2021 | 121.3943 | 0.09613 | -0.17853 | 120.7993 | 120.7443 | 120.7626 | -1.2772 | 121.6965 | 121.6827 | 121.3257 | -0.56305
2941.8438 | 122.0901 | -121.7834 | 0.09613 | -0.0078584 | -0.014956 | 0.018269 | 0.036023 | -0.00922 | -0.034024 | -0.020969 | 7.627e-05 | 0.012439 | -0.010653 | -0.096538 | -0.011715 | -0.0018798 | 0.10529 | 0.018311 | 0.022888 | 0.054932 | 0.13275 | 0.004578 | -0.13275 | 0.018311 | 0.09613 | -0.045776 | 0.09613 | 0.073242 | -0.059509 | -0.1236 | 121.788 | 121.6507 | 0.036621 | 121.8018 | 121.8384 | 0.18768 | 0.009156 | 121.7239 | 121.6599 | 0 | 121.8018 | 121.7377 | 0.07782 | -0.022888 | 121.9162 | 121.8887 | 121.8063 | -0.22888 | 121.8796 | 121.8567 | 121.8796 | -0.21973
2943.6406 | 122.1954 | -121.8979 | 0.086975 | -0.0078584 | -0.017306 | 0.017628 | 0.034955 | -0.010288 | -0.033596 | -0.020328 | 7.627e-05 | 0.01308 | -0.012362 | -0.094189 | -0.014492 | 0.00089722 | 0.041199 | -0.050354 | -0.022888 | 0.009155 | 0.14648 | 0.004578 | -0.13733 | -0.032043 | 0.009155 | -0.059509 | 0.073242 | 0.073242 | -0.064087 | -0.13275 | 121.9025 | 121.7606 | 0.059509 | 121.8475 | 121.907 | 0.14648 | -0.045776 | 121.8338 | 121.7651 | -0.013733 | 121.8658 | 121.8384 | 0.073242 | -0.013733 | 122.0444 | 121.9391 | 121.875 | -0.2243 | 121.9711 | 121.9711 | 121.907 | -0.21973
2945.375 | 122.0993 | -121.9894 | 0.15106 | -0.00022891 | -0.026491 | 0.017842 | 0.040082 | -0.0070836 | -0.04321 | -0.021396 | 7.627e-05 | 0.0064578 | -0.012789 | -0.096752 | -0.017483 | 0.0017518 | 0.054932 | 0.036621 | 0.082397 | 0.036621 | 0.1236 | 0.032043 | -0.10986 | 0.009155 | 0.10529 | 0.022888 | 0.050354 | 0.036621 | -0.041199 | -0.10986 | 122.0215 | 121.8796 | -0.027466 | 122.0261 | 122.0261 | 0.14648 | -0.09613 | 121.9482 | 121.8796 | -0.10071 | 121.9986 | 122.0123 | 0.13275 | -0.11444 | 122.113 | 122.0444 | 122.0718 | -0.26093 | 122.0398 | 122.0261 | 122.0947 | -0.26093
2947.1719 | 122.2366 | -121.9528 | 0.091553 | -0.00022891 | -0.017306 | 0.01656 | 0.03645 | -0.007511 | -0.034451 | -0.019901 | -0.015182 | 0.011798 | -0.010867 | -0.098461 | -0.011501 | -0.00038438 | 0.086975 | 0.004578 | 0.041199 | 0.045776 | 0.13733 | 0.022888 | -0.13733 | -0.004578 | 0.086975 | -0.041199 | 0.082397 | 0.07782 | -0.050354 | -0.11444 | 121.9757 | 121.8155 | 0.045776 | 121.9574 | 121.9986 | 0.18311 | -0.004578 | 121.9025 | 121.8384 | -0.009156 | 121.9482 | 121.9116 | 0.073242 | -0.013733 | 122.0901 | 122.0398 | 121.994 | -0.22888 | 122.0352 | 122.0306 | 122.0398 | -0.20599
2948.9688 | 122.2824 | -121.9711 | 0.10529 | -0.00022891 | -0.019442 | 0.020192 | 0.035382 | -0.011143 | -0.035733 | -0.018833 | -0.0075532 | 0.011371 | -0.010653 | -0.095684 | -0.011929 | 0.0023926 | 0.054932 | -0.027466 | 0.009155 | 0.013733 | 0.13275 | -0.004578 | -0.11902 | 0 | 0.036621 | -0.032043 | 0.073242 | 0.059509 | -0.036621 | -0.10529 | 121.9666 | 121.8521 | 0.027465 | 121.9437 | 121.9849 | 0.13275 | -0.050354 | 121.9345 | 121.8658 | -0.032044 | 121.9711 | 121.9391 | 0.073243 | -0.045777 | 122.1039 | 122.0261 | 121.9803 | -0.22431 | 122.0444 | 122.0306 | 122.0078 | -0.21057
2950.6875 | 122.1542 | -122.0215 | 0.13733 | -0.00022891 | -0.017733 | 0.017842 | 0.039227 | -0.0081518 | -0.042141 | -0.020328 | -0.015182 | 0.0098758 | -0.01044 | -0.096966 | -0.017483 | 0.0013244 | 0.10071 | 0.082397 | 0.13275 | 0.091553 | 0.10529 | 0.036621 | -0.10529 | 0.018311 | 0.16937 | 0.027466 | 0.073242 | 0.032043 | -0.045776 | -0.09613 | 122.0581 | 121.9162 | -0.032043 | 122.1039 | 122.113 | 0.19684 | -0.036621 | 121.9757 | 121.9254 | -0.064087 | 122.0398 | 122.049 | 0.1236 | -0.10529 | 122.1268 | 122.1222 | 122.1542 | -0.24262 | 122.0947 | 122.0535 | 122.1909 | -0.23346
2952.4688 | 122.2 | -122.0169 | 0.11444 | -0.00022891 | -0.021364 | 0.02126 | 0.040509 | -0.010715 | -0.043423 | -0.020969 | -0.0075532 | 0.007526 | -0.0093717 | -0.099102 | -0.017697 | 0.00068362 | 0.11902 | 0.11902 | 0.14648 | 0.10529 | 0.10071 | 0.041199 | -0.09613 | 0.086975 | 0.19684 | 0.091553 | 0.050354 | 0.032043 | -0.036621 | -0.091553 | 122.0581 | 121.9208 | -0.013733 | 122.1359 | 122.1222 | 0.20142 | 0.004578 | 121.9803 | 121.9254 | -0.064087 | 122.1039 | 122.1085 | 0.18311 | -0.082398 | 122.1176 | 122.1359 | 122.1634 | -0.21057 | 122.0673 | 122.049 | 122.2137 | -0.20599
2954.2344 | 122.2321 | -122.049 | 0.1236 | -0.00022891 | -0.02051 | 0.021901 | 0.036023 | -0.008579 | -0.04086 | -0.022678 | 7.627e-05 | 0.009235 | -0.013217 | -0.099529 | -0.016842 | -0.00038438 | 0.13733 | 0.1236 | 0.14648 | 0.10986 | 0.10986 | 0.041199 | -0.091553 | 0.082397 | 0.19684 | 0.07782 | 0.041199 | 0.036621 | -0.018311 | -0.10071 | 122.0901 | 121.9574 | -0.013733 | 122.1725 | 122.1588 | 0.20142 | 0.013733 | 122.0306 | 121.9482 | -0.082397 | 122.1313 | 122.1268 | 0.17853 | -0.086975 | 122.1588 | 122.1863 | 122.1954 | -0.21515 | 122.0901 | 122.0856 | 122.2458 | -0.2243
2956.0312 | 122.1954 | -122.0352 | 0.11902 | -0.00022891 | -0.019442 | 0.017415 | 0.036664 | -0.00922 | -0.039151 | -0.02161 | -0.0075532 | 0.007526 | -0.0089443 | -0.099956 | -0.015133 | -0.0016662 | 0.14191 | 0.10986 | 0.13733 | 0.091553 | 0.10986 | 0.032043 | -0.10071 | 0.054932 | 0.19226 | 0.059509 | 0.045776 | 0.041199 | -0.022888 | -0.086975 | 122.0673 | 121.9345 | -0.009156 | 122.1451 | 122.1268 | 0.19226 | 0.022888 | 122.0123 | 121.9482 | -0.073243 | 122.0901 | 122.0947 | 0.14648 | -0.07782 | 122.1451 | 122.1771 | 122.1725 | -0.21973 | 122.081 | 122.0764 | 122.2275 | -0.20599
2957.8281 | 122.2 | -122.0627 | 0.13733 | -0.00022891 | -0.021792 | 0.018269 | 0.039655 | -0.01157 | -0.037869 | -0.021396 | -0.0075532 | 0.0073124 | -0.0095853 | -0.098675 | -0.015347 | -0.0014526 | 0.082397 | 0.045776 | 0.07782 | 0.041199 | 0.11444 | 0.032043 | -0.10529 | 0.032043 | 0.091553 | 0.004578 | 0.07782 | 0.032043 | -0.032043 | -0.086975 | 122.0947 | 121.9574 | -0.022888 | 122.1085 | 122.1039 | 0.14649 | -0.054932 | 122.0306 | 121.9757 | -0.059509 | 122.0947 | 122.0673 | 0.091553 | -0.10529 | 122.1771 | 122.1451 | 122.1405 | -0.24262 | 122.1405 | 122.0947 | 122.1542 | -0.2243
2959.625 | 122.3145 | -122.0169 | 0.10529 | -0.00022891 | -0.02051 | 0.017201 | 0.035169 | -0.0096472 | -0.035305 | -0.019687 | 7.627e-05 | 0.010944 | -0.010867 | -0.098888 | -0.011288 | 0.00068362 | 0.16022 | 0.091553 | 0.10986 | 0.10071 | 0.086975 | 0.041199 | -0.09613 | 0.10071 | 0.13733 | 0.041199 | 0.041199 | 0.013733 | -0.032043 | -0.091553 | 122.0581 | 121.9208 | -0.018311 | 122.1085 | 122.1176 | 0.19684 | 0.054931 | 121.9849 | 121.9254 | -0.064087 | 122.1176 | 122.0581 | 0.13275 | -0.091553 | 122.1039 | 122.1771 | 122.1268 | -0.20142 | 122.0581 | 122.0306 | 122.1542 | -0.19684
2961.3594 | 122.2092 | -122.0901 | 0.12817 | -0.00022891 | -0.020083 | 0.019123 | 0.035596 | -0.0094336 | -0.04086 | -0.021396 | 7.627e-05 | 0.0088076 | -0.0085171 | -0.10017 | -0.014065 | -0.00059818 | 0.09613 | 0.036621 | 0.082397 | 0.050354 | 0.11902 | 0.041199 | -0.09613 | 0.018311 | 0.091553 | 0.018311 | 0.059509 | 0.054932 | -0.036621 | -0.091553 | 122.1313 | 121.994 | -0.009155 | 122.1268 | 122.1405 | 0.14648 | -0.032044 | 122.0535 | 121.9986 | -0.068665 | 122.1085 | 122.1085 | 0.10986 | -0.073242 | 122.2092 | 122.1863 | 122.1725 | -0.2243 | 122.1497 | 122.1451 | 122.1817 | -0.21973
2963.1406 | 122.3557 | -122.0261 | 0.082397 | -0.0078584 | -0.015597 | 0.017201 | 0.039227 | -0.0081518 | -0.030819 | -0.019687 | 7.627e-05 | 0.014148 | -0.0080899 | -0.098247 | -0.013638 | -0.001239 | 0.10986 | -0.009155 | 0.036621 | 0.059509 | 0.15564 | 0.009155 | -0.12817 | -0.004578 | 0.068665 | -0.050354 | 0.07782 | 0.059509 | -0.041199 | -0.1236 | 122.0352 | 121.8979 | 0.073243 | 122.0169 | 122.0856 | 0.18768 | 0.027466 | 121.9849 | 121.9025 | -0.004577 | 122.0215 | 121.9757 | 0.073242 | -0.022888 | 122.1817 | 122.1359 | 122.0627 | -0.21057 | 122.1039 | 122.0856 | 122.0947 | -0.20599
2964.8594 | 122.2916 | -122.0627 | 0.10529 | -0.015487 | -0.017306 | 0.017201 | 0.032605 | -0.010074 | -0.032742 | -0.01926 | -0.0075532 | 0.016284 | -0.0068081 | -0.095684 | -0.010433 | 4.2822e-05 | 0.054932 | -0.073242 | -0.027466 | 0.013733 | 0.12817 | 0.018311 | -0.13275 | -0.064087 | 0.004578 | -0.1236 | 0.09613 | 0.09613 | -0.054932 | -0.1236 | 122.081 | 121.9299 | 0.022888 | 121.9894 | 122.0764 | 0.14648 | -0.050354 | 122.0078 | 121.9391 | -0.009156 | 121.9986 | 121.9391 | 0 | -0.009156 | 122.1909 | 122.1176 | 122.0352 | -0.23804 | 122.1588 | 122.1588 | 122.0673 | -0.22888
2966.5938 | 122.3373 | -122.0627 | 0.091553 | -0.00022891 | -0.016024 | 0.016987 | 0.039868 | -0.00922 | -0.037228 | -0.019687 | 7.627e-05 | 0.012653 | -0.0070217 | -0.098247 | -0.014279 | 0.0017518 | 0.036621 | -0.036621 | -0.009155 | 0.022888 | 0.14191 | 0 | -0.14191 | -0.036621 | 0.068665 | -0.059509 | 0.091553 | 0.082397 | -0.068665 | -0.13733 | 122.0627 | 121.9208 | 0.050354 | 122.0261 | 122.0856 | 0.16479 | -0.054932 | 121.994 | 121.9254 | 0 | 122.0261 | 122.0032 | 0.07782 | -0.009156 | 122.2046 | 122.0993 | 122.0535 | -0.23346 | 122.1542 | 122.1451 | 122.1313 | -0.22888
2968.375 | 122.3328 | -122.0581 | 0.11902 | -0.00022891 | -0.01816 | 0.016774 | 0.037091 | -0.008579 | -0.035946 | -0.018192 | 7.627e-05 | 0.016712 | -0.0059537 | -0.09547 | -0.013424 | -0.0014526 | 0.10071 | 0.027466 | 0.054932 | 0.041199 | 0.13275 | 0.022888 | -0.11444 | 0.018311 | 0.082397 | -0.036621 | 0.082397 | 0.068665 | -0.068665 | -0.11902 | 122.081 | 121.9437 | 0.013732 | 122.0856 | 122.0993 | 0.15564 | -0.018311 | 121.9894 | 121.9391 | -0.036622 | 122.0764 | 122.0215 | 0.082398 | -0.050354 | 122.1909 | 122.1588 | 122.113 | -0.23346 | 122.1405 | 122.1268 | 122.1405 | -0.23804
2970.1562 | 122.2412 | -122.1313 | 0.12817 | -0.00022891 | -0.023073 | 0.019978 | 0.033673 | -0.0094336 | -0.042355 | -0.018833 | -0.0075532 | 0.0090214 | -0.010226 | -0.099743 | -0.016415 | 0.004956 | 0.036621 | 0.036621 | 0.082397 | 0.064087 | 0.10529 | 0.018311 | -0.09613 | -0.004578 | 0.086975 | 0.013733 | 0.059509 | 0.059509 | -0.032043 | -0.09613 | 122.1497 | 122.0352 | -0.022888 | 122.168 | 122.1954 | 0.16022 | -0.091553 | 122.0993 | 122.0352 | -0.068665 | 122.1268 | 122.1451 | 0.10986 | -0.068665 | 122.2366 | 122.168 | 122.2137 | -0.2243 | 122.1909 | 122.1909 | 122.2183 | -0.2243
2971.9531 | 122.3877 | -122.0627 | 0.091553 | -0.00022891 | -0.018801 | 0.017201 | 0.034741 | -0.010288 | -0.034665 | -0.019474 | 7.627e-05 | 0.014789 | -0.0085171 | -0.098034 | -0.011074 | 0.00068362 | 0.082397 | 0.009155 | 0.054932 | 0.045776 | 0.11902 | 0.027466 | -0.10529 | 0.045776 | 0.10071 | 0.027466 | 0.068665 | 0.041199 | -0.027466 | -0.082397 | 122.0901 | 121.9574 | 0.027466 | 122.0718 | 122.1085 | 0.15106 | -0.009156 | 122.0352 | 121.9803 | -0.022888 | 122.1085 | 122.0901 | 0.10986 | -0.050354 | 122.1817 | 122.1451 | 122.1176 | -0.19684 | 122.1313 | 122.1039 | 122.1634 | -0.17395
2973.6719 | 122.3648 | -122.0718 | 0.1236 | -0.0078584 | -0.021151 | 0.017201 | 0.036023 | -0.011143 | -0.037869 | -0.018833 | 7.627e-05 | 0.012439 | -0.0065945 | -0.098034 | -0.014279 | 0.0023926 | 0.1236 | 0.064087 | 0.11902 | 0.091553 | 0.082397 | 0.054932 | -0.07782 | 0.064087 | 0.15106 | 0.050354 | 0.054932 | 0.045776 | -0.027466 | -0.09613 | 122.1268 | 121.994 | -0.041199 | 122.1359 | 122.1634 | 0.16937 | 0 | 122.0444 | 121.9757 | -0.068664 | 122.1359 | 122.1222 | 0.14648 | -0.07782 | 122.1542 | 122.1954 | 122.1909 | -0.20142 | 122.1268 | 122.1176 | 122.2229 | -0.21973
2975.4531 | 122.3465 | -122.0993 | 0.091553 | -0.0078584 | -0.016024 | 0.015919 | 0.039441 | -0.0083654 | -0.037228 | -0.018192 | 0.0077058 | 0.01308 | -0.0046719 | -0.10167 | -0.015133 | -0.00038438 | 0.1236 | 0.073242 | 0.1236 | 0.10986 | 0.091553 | 0.054932 | -0.10071 | 0.086975 | 0.13275 | 0.054932 | 0.054932 | 0.032043 | -0.018311 | -0.09613 | 122.1542 | 121.9986 | 0 | 122.1725 | 122.2092 | 0.21057 | 0.032043 | 122.081 | 122.0032 | -0.036621 | 122.1863 | 122.1542 | 0.15106 | -0.05951 | 122.1909 | 122.2229 | 122.2229 | -0.19226 | 122.1542 | 122.1313 | 122.2321 | -0.18768
2977.1719 | 122.3648 | -122.0535 | 0.10071 | -0.0078584 | -0.016878 | 0.01656 | 0.036878 | -0.0083654 | -0.034878 | -0.020542 | 0.0077058 | 0.016925 | -0.0046719 | -0.099956 | -0.011288 | 0.00089722 | 0.10071 | 0.022888 | 0.032043 | 0.045776 | 0.15564 | 0.004578 | -0.15106 | 0.004578 | 0.10071 | -0.032043 | 0.082397 | 0.068665 | -0.064087 | -0.09613 | 122.0581 | 121.9025 | 0.054932 | 122.0764 | 122.0993 | 0.19684 | 0 | 121.9894 | 121.9574 | -0.018311 | 122.0581 | 122.0215 | 0.064087 | -0.032043 | 122.2092 | 122.1542 | 122.0856 | -0.25177 | 122.1359 | 122.1222 | 122.1542 | -0.19684
2978.9688 | 122.3969 | -122.0901 | 0.10986 | 0.01503 | -0.017092 | 0.017201 | 0.035382 | -0.0081518 | -0.037228 | -0.020755 | -0.0075532 | 0.016071 | -0.0042447 | -0.099956 | -0.014065 | 0.0015382 | 0.018311 | -0.013733 | 0.004578 | 0.032043 | 0.13733 | 0.013733 | -0.15106 | -0.050354 | 0.059509 | -0.041199 | 0.09613 | 0.091553 | -0.059509 | -0.12817 | 122.1039 | 121.9391 | 0.027466 | 122.0764 | 122.1222 | 0.18311 | -0.091552 | 122.0306 | 121.962 | -0.013733 | 122.0398 | 122.0489 | 0.086975 | -0.01831 | 122.2275 | 122.1085 | 122.0947 | -0.26093 | 122.1863 | 122.1817 | 122.1497 | -0.23804
2980.7656 | 122.3145 | -122.1039 | 0.1236 | -0.0078584 | -0.019655 | 0.021473 | 0.037518 | -0.011356 | -0.042569 | -0.019901 | 0.0077058 | 0.0096622 | -0.0036037 | -0.10124 | -0.016628 | 0.002179 | 0.11444 | 0.13275 | 0.14648 | 0.09613 | 0.10529 | 0.036621 | -0.10071 | 0.064087 | 0.18768 | 0.073242 | 0.054932 | 0.059509 | -0.022888 | -0.082397 | 122.1405 | 122.0032 | -0.01831 | 122.2366 | 122.2 | 0.19684 | -0.009155 | 122.081 | 122.0215 | -0.068664 | 122.168 | 122.1771 | 0.15564 | -0.064087 | 122.2092 | 122.2183 | 122.2504 | -0.2243 | 122.1588 | 122.1634 | 122.2916 | -0.20599
2982.5 | 122.4106 | -122.1085 | 0.10529 | -0.00022891 | -0.019655 | 0.016133 | 0.034314 | -0.0070836 | -0.034237 | -0.018619 | -0.0075532 | 0.018634 | -0.0029629 | -0.10102 | -0.01321 | 4.2822e-05 | 0.032043 | -0.041199 | -0.004578 | -0.004578 | 0.13733 | 0.009155 | -0.15106 | -0.018311 | 0.009155 | -0.059509 | 0.07782 | 0.073242 | -0.041199 | -0.11444 | 122.1176 | 121.9574 | 0.032043 | 122.0673 | 122.1039 | 0.14648 | -0.073243 | 122.0673 | 121.994 | -0.027466 | 122.0901 | 122.0489 | 0.054932 | -0.032044 | 122.2458 | 122.1405 | 122.1039 | -0.25635 | 122.1863 | 122.1817 | 122.1176 | -0.21973
2984.2812 | 122.2824 | -122.1451 | 0.13733 | -0.0078584 | -0.020296 | 0.019978 | 0.038373 | -0.010074 | -0.041501 | -0.01926 | 0.022965 | 0.016071 | -0.0046719 | -0.10081 | -0.01556 | 0.0023926 | 0.036621 | -0.032043 | 0.022888 | 0.009155 | 0.1236 | 0.009155 | -0.13733 | -0.045776 | 0.054932 | -0.059509 | 0.09613 | 0.086975 | -0.073242 | -0.12817 | 122.1542 | 122.0078 | -0.013733 | 122.113 | 122.1542 | 0.14648 | -0.10071 | 122.0718 | 122.0169 | -0.041199 | 122.0993 | 122.0856 | 0.068665 | -0.050354 | 122.2687 | 122.1817 | 122.168 | -0.27466 | 122.2412 | 122.2321 | 122.2 | -0.2655
2986.0625 | 122.4289 | -122.0947 | 0.11444 | -0.0078584 | -0.018374 | 0.01656 | 0.03645 | -0.007511 | -0.038296 | -0.020115 | 7.627e-05 | 0.016925 | -0.00082669 | -0.098461 | -0.014492 | 0.0013244 | 0.10986 | 0.041199 | 0.09613 | 0.082397 | 0.09613 | 0.036621 | -0.10071 | 0.064087 | 0.11444 | 0.032043 | 0.054932 | 0.032043 | -0.009155 | -0.082397 | 122.1313 | 121.994 | -0.018311 | 122.1359 | 122.1771 | 0.18311 | -0.004578 | 122.0856 | 122.0123 | -0.059509 | 122.1588 | 122.1268 | 0.11444 | -0.082398 | 122.1909 | 122.2046 | 122.1909 | -0.21515 | 122.1497 | 122.1268 | 122.2092 | -0.19684
2987.8438 | 122.3877 | -122.1085 | 0.10986 | -0.0078584 | -0.017092 | 0.016346 | 0.037305 | -0.0077246 | -0.037014 | -0.019901 | -0.0075532 | 0.016925 | -0.00018589 | -0.099102 | -0.017269 | -0.0016662 | 0.032043 | -0.054932 | -0.004578 | 0.018311 | 0.14648 | 0 | -0.14191 | -0.036621 | 0.041199 | -0.064087 | 0.10529 | 0.091553 | -0.073242 | -0.14191 | 122.1085 | 121.9666 | 0.036621 | 122.0535 | 122.1268 | 0.16022 | -0.07782 | 122.0352 | 121.9666 | -0.004577 | 122.0718 | 122.0444 | 0.07782 | -0.01831 | 122.2549 | 122.1405 | 122.1039 | -0.25177 | 122.2137 | 122.2 | 122.1497 | -0.25177
2989.5625 | 122.4289 | -122.1176 | 0.11444 | -0.0078584 | -0.018374 | 0.017628 | 0.037091 | -0.0070836 | -0.036374 | -0.020328 | 7.627e-05 | 0.018207 | -0.0016811 | -0.098247 | -0.014279 | 0.0011108 | 0.064087 | -0.027466 | 0.009155 | 0.045776 | 0.13733 | 0.013733 | -0.14191 | -0.004578 | 0.082397 | -0.032043 | 0.09613 | 0.073242 | -0.050354 | -0.1236 | 122.1313 | 121.9757 | 0.022888 | 122.0901 | 122.1634 | 0.18768 | -0.050354 | 122.0673 | 121.994 | -0.018311 | 122.113 | 122.0856 | 0.091553 | -0.041199 | 122.2549 | 122.1817 | 122.1268 | -0.25635 | 122.2137 | 122.1909 | 122.2 | -0.23804
2991.3438 | 122.4243 | -122.0947 | 0.10529 | -0.015487 | -0.015169 | 0.015065 | 0.036237 | -0.00922 | -0.035946 | -0.018406 | -0.015182 | 0.018421 | 0.00088231 | -0.098675 | -0.013424 | 0.0019654 | 0.073242 | -0.018311 | 0.036621 | 0.036621 | 0.13733 | 0.013733 | -0.13275 | -0.022888 | 0.086975 | -0.041199 | 0.086975 | 0.07782 | -0.064087 | -0.1236 | 122.1085 | 121.962 | 0.032043 | 122.0764 | 122.1313 | 0.16937 | -0.032044 | 122.0306 | 121.9711 | -0.018311 | 122.0718 | 122.0535 | 0.082397 | -0.027466 | 122.2321 | 122.168 | 122.1313 | -0.23804 | 122.1817 | 122.1725 | 122.1817 | -0.22888
2993.0625 | 122.3831 | -122.1451 | 0.10071 | 0.0074006 | -0.016238 | 0.01656 | 0.035596 | -0.0083654 | -0.034451 | -0.018833 | -0.0075532 | 0.019916 | 0.0015231 | -0.097607 | -0.010861 | 0.00047002 | 0.086975 | 0.013733 | 0.027466 | 0.050354 | 0.12817 | 0 | -0.11444 | -0.013733 | 0.059509 | -0.059509 | 0.091553 | 0.07782 | -0.050354 | -0.11444 | 122.1451 | 122.0306 | 0.027466 | 122.1588 | 122.1954 | 0.16479 | -0.013733 | 122.0947 | 122.0306 | -0.009155 | 122.1313 | 122.0856 | 0.054932 | -0.022888 | 122.2733 | 122.2321 | 122.1725 | -0.21515 | 122.2366 | 122.2229 | 122.2046 | -0.21515
2994.8438 | 122.3465 | -122.1588 | 0.15106 | -0.00022891 | -0.023714 | 0.019123 | 0.032605 | -0.0098608 | -0.044705 | -0.020115 | -0.015182 | 0.015857 | 0.0010959 | -0.10102 | -0.016201 | 0.0058106 | 0.032043 | 0.009155 | 0.073242 | 0.050354 | 0.13275 | 0.022888 | -0.09613 | 0.013733 | 0.11444 | 0.036621 | 0.064087 | 0.073242 | -0.041199 | -0.086975 | 122.1817 | 122.0627 | -0.018311 | 122.168 | 122.2092 | 0.14648 | -0.11902 | 122.1176 | 122.0718 | -0.086975 | 122.1725 | 122.1954 | 0.1236 | -0.07782 | 122.2916 | 122.1909 | 122.2321 | -0.24719 | 122.2229 | 122.2321 | 122.2733 | -0.23804
2996.6406 | 122.3145 | -122.1588 | 0.14191 | -0.00022891 | -0.019228 | 0.021473 | 0.038587 | -0.0072974 | -0.038083 | -0.021183 | -0.0075532 | 0.021839 | 0.0068637 | -0.10209 | -0.015988 | 0.003888 | 0.059509 | 0.013733 | 0.064087 | 0.050354 | 0.13275 | 0.018311 | -0.11902 | -0.041199 | 0.082397 | -0.036621 | 0.10071 | 0.091553 | -0.054932 | -0.11444 | 122.1771 | 122.0398 | -0.009156 | 122.1725 | 122.2092 | 0.16937 | -0.082398 | 122.1039 | 122.0444 | -0.041199 | 122.1176 | 122.1222 | 0.07782 | -0.050354 | 122.2916 | 122.2183 | 122.2229 | -0.26093 | 122.2595 | 122.2504 | 122.2412 | -0.25635
2998.3594 | 122.319 | -122.1771 | 0.16022 | -0.00022891 | -0.024142 | 0.019551 | 0.035809 | -0.0079382 | -0.041928 | -0.020115 | 7.627e-05 | 0.016498 | 0.0051547 | -0.10295 | -0.01791 | 0.006665 | 0.068665 | 0.041199 | 0.091553 | 0.059509 | 0.10529 | 0.041199 | -0.10071 | 0.022888 | 0.10529 | 0.013733 | 0.086975 | 0.045776 | -0.045776 | -0.10071 | 122.2183 | 122.0764 | -0.054931 | 122.2183 | 122.2366 | 0.16022 | -0.091552 | 122.1313 | 122.0764 | -0.073242 | 122.2 | 122.1909 | 0.11444 | -0.11444 | 122.2824 | 122.2458 | 122.2687 | -0.26093 | 122.2641 | 122.2229 | 122.2824 | -0.26093
3000.1406 | 122.4152 | -122.168 | 0.10529 | -0.0078584 | -0.020937 | 0.01656 | 0.035596 | -0.0083654 | -0.037442 | -0.019901 | -0.0075532 | 0.026111 | 0.0062229 | -0.10337 | -0.010433 | 0.0028198 | 0.12817 | 0.073242 | 0.11902 | 0.09613 | 0.10986 | 0.036621 | -0.082397 | 0.07782 | 0.14191 | 0.073242 | 0.073242 | 0.064087 | -0.022888 | -0.054932 | 122.2046 | 122.0856 | 0.004577 | 122.2412 | 122.2641 | 0.17853 | 0.022888 | 122.1451 | 122.113 | -0.032044 | 122.2458 | 122.2412 | 0.12817 | -0.041199 | 122.2778 | 122.2961 | 122.287 | -0.18768 | 122.2412 | 122.2321 | 122.3099 | -0.16022
3001.875 | 122.3465 | -122.1771 | 0.14648 | -0.00022891 | -0.01816 | 0.019978 | 0.040509 | -0.0087926 | -0.037655 | -0.022037 | -0.0075532 | 0.03252 | 0.019895 | -0.10551 | -0.016201 | 0.0058106 | 0.041199 | -0.041199 | 0.018311 | 0.009155 | 0.14191 | -0.004578 | -0.13275 | -0.036621 | 0.064087 | -0.059509 | 0.1236 | 0.1236 | -0.054932 | -0.10529 | 122.1725 | 122.0444 | -0.004577 | 122.1359 | 122.1863 | 0.14191 | -0.10529 | 122.1222 | 122.0718 | -0.022888 | 122.1405 | 122.1176 | 0.045777 | -0.022888 | 122.319 | 122.2183 | 122.1954 | -0.27924 | 122.3007 | 122.3007 | 122.2412 | -0.25177
3003.6719 | 122.3236 | -122.1863 | 0.17395 | 0.0074006 | -0.017092 | 0.018269 | 0.039227 | -0.0064428 | -0.038937 | -0.020328 | 7.627e-05 | 0.036365 | 0.026517 | -0.10829 | -0.015347 | 0.0079468 | 0.07782 | 0.027466 | 0.064087 | 0.064087 | 0.1236 | 0.018311 | -0.11902 | -0.018311 | 0.10071 | -0.018311 | 0.11902 | 0.10529 | -0.045776 | -0.11444 | 122.2046 | 122.0673 | -0.050354 | 122.2137 | 122.2504 | 0.18311 | -0.09613 | 122.1405 | 122.0718 | -0.054931 | 122.168 | 122.168 | 0.09613 | -0.068664 | 122.3099 | 122.2641 | 122.2504 | -0.29297 | 122.3053 | 122.2916 | 122.287 | -0.28839
3005.4688 | 122.4792 | -122.0947 | 0.15564 | -0.00022891 | -0.016238 | 0.016774 | 0.036237 | -0.0079382 | -0.036587 | -0.020115 | -0.015182 | 0.04491 | 0.03613 | -0.10487 | -0.012356 | 0.0092286 | 0.09613 | -0.009155 | 0.036621 | 0.064087 | 0.15106 | -0.009155 | -0.13275 | 0.032043 | 0.11444 | -0.013733 | 0.13275 | 0.10529 | -0.013733 | -0.10071 | 122.0856 | 121.962 | -0.004578 | 122.0856 | 122.1588 | 0.19684 | -0.05951 | 122.081 | 121.994 | -0.022889 | 122.1268 | 122.081 | 0.086975 | -0.050354 | 122.2458 | 122.1909 | 122.1313 | -0.28839 | 122.2275 | 122.2 | 122.2092 | -0.25635
3007.2656 | 122.374 | -122.1405 | 0.17853 | -0.00022891 | -0.026278 | 0.021901 | 0.034314 | -0.0090062 | -0.042141 | -0.021824 | -0.022812 | 0.044269 | 0.039121 | -0.10871 | -0.015347 | 0.012433 | 0.082397 | 0.032043 | 0.086975 | 0.068665 | 0.11902 | 0.045776 | -0.091553 | 0.045776 | 0.14191 | 0.07782 | 0.10529 | 0.10529 | 0.013733 | -0.068665 | 122.1863 | 122.0489 | -0.059509 | 122.1725 | 122.2092 | 0.16022 | -0.096131 | 122.1542 | 122.0718 | -0.073242 | 122.1863 | 122.2183 | 0.14649 | -0.073242 | 122.2595 | 122.2229 | 122.2275 | -0.27008 | 122.2458 | 122.2458 | 122.2824 | -0.24719
3008.9844 | 122.4472 | -122.0947 | 0.17853 | 0.0074006 | -0.017946 | 0.017842 | 0.035169 | -0.0060156 | -0.034024 | -0.020755 | -0.0075532 | 0.062641 | 0.05792 | -0.11534 | -0.01022 | 0.012647 | 0.1236 | 0.022888 | 0.050354 | 0.054932 | 0.14191 | 0.018311 | -0.11902 | 0.032043 | 0.11444 | 0 | 0.15106 | 0.13733 | -0.018311 | -0.073242 | 122.113 | 121.9757 | -0.036621 | 122.1176 | 122.1497 | 0.17395 | -0.054932 | 122.0764 | 122.0215 | -0.027466 | 122.1268 | 122.0947 | 0.073242 | -0.041199 | 122.2366 | 122.2183 | 122.1451 | -0.29755 | 122.2458 | 122.2321 | 122.2092 | -0.25177
3010.7656 | 122.3602 | -121.7789 | 0.51727 | -0.00022891 | -0.024142 | 0.018055 | 0.03645 | -0.0064428 | -0.043637 | -0.023746 | 0.0077058 | 0.26943 | 0.34289 | -0.18434 | -0.017697 | 0.083997 | 0.09613 | 0.07782 | 0.13275 | 0.10986 | 0.14648 | 0.068665 | -0.054932 | 0.21057 | 0.32501 | 0.28839 | 0.38452 | 0.3891 | 0.2243 | 0.16022 | 121.8475 | 121.7239 | -0.37079 | 121.8567 | 121.8887 | 0.16479 | -0.42114 | 122.0032 | 121.9391 | -0.13275 | 121.9894 | 122.0673 | 0.12817 | -0.12817 | 121.9254 | 121.875 | 121.9116 | -0.5722 | 122.1634 | 122.168 | 122.1039 | -0.35706
3012.4844 | 122.4426 | -121.6507 | 0.58136 | -0.0078584 | -0.014529 | 0.016987 | 0.037091 | -0.003452 | -0.035519 | -0.020755 | 0.0077058 | 0.20171 | 0.24505 | -0.15486 | -0.010433 | 0.083356 | 0.09613 | -0.018311 | 0.045776 | 0.054932 | 0.17853 | 0.045776 | -0.10071 | 0.27008 | 0.29755 | 0.28381 | 0.41657 | 0.39368 | 0.24261 | 0.18768 | 121.6965 | 121.55 | -0.40283 | 121.6324 | 121.7056 | 0.15564 | -0.48523 | 121.8933 | 121.8384 | -0.16479 | 121.9208 | 121.9345 | 0.09613 | -0.18768 | 121.8292 | 121.7468 | 121.6965 | -0.68207 | 122.0673 | 122.0444 | 121.9482 | -0.39368
3014.2656 | 122.2595 | -120.5246 | 1.5793 | -0.0078584 | -0.018374 | 0.017628 | 0.03645 | 0.003811 | -0.03616 | -0.030155 | 7.627e-05 | 1.0504 | 1.3779 | -0.42552 | -0.012356 | 0.32817 | 0.21515 | 0.11902 | 0.15106 | 0.19226 | 0.32044 | 0.17853 | 0.032043 | 0.72327 | 0.78735 | 0.92468 | 1.3916 | 1.3824 | 0.95215 | 0.89264 | 120.7031 | 120.5566 | -1.2589 | 120.6436 | 120.7169 | 0.16022 | -1.3641 | 121.4767 | 121.4172 | -0.18768 | 121.2479 | 121.4493 | 0.032044 | -0.19684 | 120.845 | 120.7397 | 120.6757 | -1.5472 | 121.9162 | 121.907 | 121.312 | -0.68665
3015.9844 | 122.2549 | -121.4859 | 0.54474 | -0.015487 | -0.017733 | 0.017415 | 0.038587 | -0.0055884 | -0.037228 | -0.023533 | 0.0077058 | 0.3051 | 0.37686 | -0.18434 | -0.012356 | 0.086987 | 0.086975 | 0.027466 | 0.054932 | 0.091553 | 0.18768 | 0.050354 | -0.09613 | 0.16022 | 0.28381 | 0.21057 | 0.46234 | 0.4303 | 0.21973 | 0.15106 | 121.5363 | 121.3898 | -0.35706 | 121.5134 | 121.5775 | 0.18768 | -0.45776 | 121.7056 | 121.637 | -0.082398 | 121.6461 | 121.6965 | 0.059509 | -0.11444 | 121.6736 | 121.5729 | 121.5408 | -0.64087 | 121.9482 | 121.9162 | 121.7697 | -0.39368
3017.7812 | 121.9528 | -120.6665 | 1.2909 | -0.00022891 | -0.022219 | 0.017842 | 0.035809 | -0.0019568 | -0.042141 | -0.027378 | 0.0077058 | 0.80626 | 1.0617 | -0.34776 | -0.016842 | 0.25297 | 0.24261 | 0.20599 | 0.24261 | 0.22888 | 0.24261 | 0.17853 | 0.054932 | 0.61798 | 0.71869 | 0.80109 | 1.0574 | 1.0437 | 0.75989 | 0.68665 | 120.845 | 120.7214 | -1.0483 | 120.8725 | 120.8954 | 0.17395 | -1.0483 | 121.4264 | 121.3531 | -0.23346 | 121.2845 | 121.4676 | 0.11444 | -0.24719 | 120.9091 | 120.9091 | 120.9091 | -1.236 | 121.7239 | 121.7102 | 121.3852 | -0.60425
3019.5625 | 122.3099 | -122.0764 | 0.11902 | -0.0078584 | -0.021792 | 0.01656 | 0.033887 | -0.00687 | -0.038937 | -0.019474 | -0.0075532 | 0.012012 | -0.0046719 | -0.097179 | -0.015347 | 0.00025642 | 0.11902 | 0.091553 | 0.12817 | 0.082397 | 0.091553 | 0.045776 | -0.09613 | 0.054932 | 0.14648 | 0.045776 | 0.032043 | 0.036621 | -0.018311 | -0.09613 | 122.1222 | 121.9803 | -0.027466 | 122.168 | 122.1588 | 0.17853 | 0 | 122.0581 | 121.9803 | -0.086976 | 122.1313 | 122.1222 | 0.14191 | -0.082398 | 122.168 | 122.1954 | 122.2046 | -0.21515 | 122.1085 | 122.113 | 122.2229 | -0.21515
3021.2656 | 122.3831 | -122.049 | 0.13733 | -0.00022891 | -0.012606 | 0.017628 | 0.039441 | -0.0096472 | -0.034878 | -0.020542 | 7.627e-05 | 0.040424 | 0.028867 | -0.10295 | -0.015133 | 0.0045288 | 0.10071 | 0 | 0.041199 | 0.045776 | 0.14191 | 0.004578 | -0.1236 | 0.018311 | 0.11444 | -0.022888 | 0.11902 | 0.09613 | -0.041199 | -0.086975 | 122.0535 | 121.9254 | 0.004578 | 122.049 | 122.0947 | 0.16937 | -0.036621 | 122.0078 | 121.962 | -0.01831 | 122.0673 | 122.0261 | 0.064087 | -0.041199 | 122.1909 | 122.1497 | 122.0901 | -0.26093 | 122.168 | 122.1451 | 122.1634 | -0.2243
3023.0625 | 122.4152 | -122.0901 | 0.1236 | -0.00022891 | -0.019015 | 0.016774 | 0.037732 | -0.008579 | -0.035733 | -0.019901 | -0.0075532 | 0.029529 | 0.015836 | -0.10252 | -0.01556 | 0.0064514 | 0.054932 | -0.004578 | 0.027466 | 0.054932 | 0.14191 | -0.004578 | -0.1236 | -0.004578 | 0.091553 | -0.009155 | 0.11444 | 0.07782 | -0.041199 | -0.10529 | 122.0856 | 121.9666 | 0.018311 | 122.0856 | 122.1451 | 0.17853 | -0.068664 | 122.0489 | 121.9849 | -0.009155 | 122.0856 | 122.081 | 0.096131 | -0.045776 | 122.2321 | 122.1451 | 122.1176 | -0.24719 | 122.2046 | 122.168 | 122.1817 | -0.22888
3024.8594 | 122.3465 | -122.0947 | 0.18768 | -0.00022891 | -0.02051 | 0.020405 | 0.040082 | -0.0096472 | -0.042996 | -0.02161 | -0.015182 | 0.040424 | 0.035917 | -0.10936 | -0.017697 | 0.010938 | 0.032043 | 0.050354 | 0.086975 | 0.059509 | 0.10529 | 0.041199 | -0.11902 | 0.045776 | 0.15106 | 0.091553 | 0.09613 | 0.086975 | -0.009155 | -0.073242 | 122.1359 | 121.9757 | -0.082397 | 122.1451 | 122.1542 | 0.17853 | -0.15564 | 122.0856 | 122.0215 | -0.091553 | 122.1405 | 122.1863 | 0.16479 | -0.10071 | 122.2 | 122.1268 | 122.1817 | -0.3067 | 122.1909 | 122.1817 | 122.2458 | -0.26092
3026.6406 | 122.438 | -122.1451 | 0.09613 | -0.00022891 | -0.017946 | 0.018696 | 0.032819 | -0.0079382 | -0.035946 | -0.021183 | -0.0075532 | 0.015216 | -0.0055263 | -0.098888 | -0.011074 | 0.00025642 | 0.13275 | 0.054932 | 0.10071 | 0.10071 | 0.10986 | 0.050354 | -0.11902 | 0.068665 | 0.14191 | 0.041199 | 0.050354 | 0.041199 | -0.013733 | -0.073242 | 122.1954 | 122.0261 | 0.013733 | 122.2 | 122.2458 | 0.21973 | 0.036621 | 122.1313 | 122.0718 | -0.045776 | 122.2137 | 122.1863 | 0.11444 | -0.054931 | 122.2549 | 122.2778 | 122.2458 | -0.21515 | 122.1954 | 122.1863 | 122.287 | -0.16937
3028.3594 | 122.4518 | -122.1451 | 0.10986 | -0.00022891 | -0.018587 | 0.019123 | 0.034741 | -0.00922 | -0.036587 | -0.018619 | 7.627e-05 | 0.01543 | -0.0036037 | -0.10017 | -0.012997 | 0.002179 | 0.12817 | 0.050354 | 0.10071 | 0.091553 | 0.10071 | 0.054932 | -0.09613 | 0.073242 | 0.13275 | 0.032043 | 0.054932 | 0.041199 | -0.027466 | -0.091553 | 122.2 | 122.049 | -0.009155 | 122.1954 | 122.2366 | 0.18768 | 0.018311 | 122.1176 | 122.0535 | -0.054931 | 122.2183 | 122.1771 | 0.1236 | -0.068664 | 122.2458 | 122.2733 | 122.2458 | -0.20599 | 122.2 | 122.1863 | 122.2778 | -0.20142
3030.1406 | 122.4609 | -122.0718 | 0.16479 | -0.015487 | -0.016238 | 0.018269 | 0.039441 | -0.0060156 | -0.038937 | -0.020755 | -0.0075532 | 0.068622 | 0.068815 | -0.11406 | -0.014706 | 0.016919 | 0.041199 | -0.036621 | 0 | 0.032043 | 0.14191 | 0.013733 | -0.13733 | -0.004578 | 0.073242 | -0.022888 | 0.18768 | 0.12817 | -0.018311 | -0.068665 | 122.0856 | 121.9345 | -0.022888 | 122.0352 | 122.1039 | 0.16937 | -0.1236 | 122.0535 | 122.0032 | 0.022888 | 122.0673 | 122.049 | 0.045777 | -0.036621 | 122.2137 | 122.113 | 122.0718 | -0.30212 | 122.2595 | 122.2 | 122.1451 | -0.23346
3031.875 | 122.2549 | -121.9299 | 0.37079 | -0.00022891 | -0.021792 | 0.018483 | 0.037091 | -0.0053746 | -0.041928 | -0.021183 | 7.627e-05 | 0.16475 | 0.20468 | -0.14674 | -0.017056 | 0.051312 | 0.12817 | 0.10071 | 0.13733 | 0.09613 | 0.13275 | 0.073242 | -0.07782 | 0.13733 | 0.2243 | 0.17395 | 0.23804 | 0.23346 | 0.10071 | 0.059509 | 122.0032 | 121.8521 | -0.23804 | 122.0306 | 122.0261 | 0.17395 | -0.24261 | 122.0306 | 121.9894 | -0.13275 | 122.0673 | 122.1039 | 0.11444 | -0.13733 | 122.0627 | 122.0581 | 122.0673 | -0.44861 | 122.168 | 122.1634 | 122.1542 | -0.31128
3033.6719 | 122.4564 | -122.1542 | 0.09613 | -0.0078584 | -0.017306 | 0.014851 | 0.038159 | -0.0081518 | -0.035519 | -0.021396 | 7.627e-05 | 0.043842 | 0.036985 | -0.10701 | -0.013424 | 0.0094422 | 0.082397 | 0.004578 | 0.054932 | 0.050354 | 0.11902 | 0.050354 | -0.11444 | 0.073242 | 0.11902 | 0.054932 | 0.09613 | 0.086975 | 0.004578 | -0.073242 | 122.2046 | 122.0398 | 0.022889 | 122.1588 | 122.2046 | 0.16479 | -0.013733 | 122.1588 | 122.081 | 0 | 122.2275 | 122.2092 | 0.12817 | -0.009155 | 122.2733 | 122.2366 | 122.2092 | -0.21057 | 122.2504 | 122.2412 | 122.2733 | -0.16937
3035.3906 | 122.4655 | -122.1359 | 0.086975 | -0.015487 | -0.013888 | 0.016346 | 0.039014 | -0.0098608 | -0.036801 | -0.017551 | -0.0075532 | 0.016284 | -0.0029629 | -0.097393 | -0.012783 | -0.00081178 | 0.073242 | 0.013733 | 0.032043 | 0.045776 | 0.13733 | 0.004578 | -0.13733 | -0.013733 | 0.086975 | -0.032043 | 0.073242 | 0.064087 | -0.059509 | -0.13733 | 122.1405 | 121.9986 | 0.050354 | 122.1497 | 122.1817 | 0.18311 | -0.013733 | 122.0764 | 121.9986 | -0.013733 | 122.1222 | 122.1039 | 0.10529 | -0.022888 | 122.2733 | 122.2092 | 122.168 | -0.2243 | 122.2092 | 122.2 | 122.2229 | -0.2243
3037.1875 | 122.3557 | -122.2366 | 0.14191 | 0.0074006 | -0.021151 | 0.01656 | 0.035382 | -0.0083654 | -0.039792 | -0.021824 | -0.0075532 | 0.011371 | -0.0053127 | -0.097607 | -0.015774 | 0.0026062 | 0.10071 | 0.086975 | 0.1236 | 0.07782 | 0.10529 | 0.045776 | -0.09613 | 0.054932 | 0.10986 | 0.032043 | 0.050354 | 0.059509 | -0.022888 | -0.10986 | 122.2824 | 122.1405 | -0.036621 | 122.3236 | 122.3145 | 0.17395 | -0.041199 | 122.2137 | 122.1268 | -0.091553 | 122.2916 | 122.2687 | 0.14191 | -0.082398 | 122.3419 | 122.3373 | 122.3602 | -0.23804 | 122.287 | 122.2961 | 122.3465 | -0.25177
3038.9219 | 122.4747 | -122.1817 | 0.07782 | 0.01503 | -0.016024 | 0.017201 | 0.035596 | -0.00922 | -0.035946 | -0.020755 | 0.0077058 | 0.014789 | -0.0055263 | -0.09782 | -0.011501 | -0.0031616 | 0.054932 | 0.009155 | 0.018311 | 0.036621 | 0.13275 | 0.018311 | -0.14191 | 0 | 0.073242 | -0.032043 | 0.10071 | 0.073242 | -0.041199 | -0.12817 | 122.2 | 122.0398 | 0.054931 | 122.1909 | 122.2183 | 0.17853 | -0.022888 | 122.1405 | 122.0535 | 0.022888 | 122.1817 | 122.1497 | 0.096131 | -0.004578 | 122.3145 | 122.2366 | 122.2 | -0.21973 | 122.2824 | 122.2549 | 122.2549 | -0.20599
3040.7031 | 122.406 | -122.2183 | 0.16937 | -0.0078584 | -0.019869 | 0.019123 | 0.041364 | -0.0072974 | -0.041287 | -0.021396 | 0.0077058 | 0.025043 | 0.019895 | -0.1006 | -0.017483 | 0.0068786 | 0.10071 | 0.091553 | 0.13275 | 0.10071 | 0.10529 | 0.032043 | -0.086975 | 0.059509 | 0.1831 | 0.054932 | 0.064087 | 0.07782 | -0.018311 | -0.073242 | 122.2504 | 122.1313 | -0.064087 | 122.3099 | 122.319 | 0.18768 | -0.068665 | 122.2 | 122.1451 | -0.10529 | 122.2778 | 122.2733 | 0.12817 | -0.091553 | 122.3236 | 122.319 | 122.3511 | -0.25635 | 122.2824 | 122.2961 | 122.4014 | -0.24261
3042.5 | 122.4426 | -122.2046 | 0.11444 | -0.00022891 | -0.019228 | 0.019337 | 0.039655 | -0.0070836 | -0.03616 | -0.020969 | 7.627e-05 | 0.01543 | -0.0053127 | -0.098675 | -0.014279 | 0.00068362 | 0.022888 | -0.045776 | -0.013733 | 0.009155 | 0.14648 | -0.018311 | -0.14648 | -0.064087 | 0.045776 | -0.073242 | 0.10071 | 0.073242 | -0.07782 | -0.12817 | 122.1863 | 122.0581 | 0.032043 | 122.1588 | 122.2137 | 0.15564 | -0.091553 | 122.1268 | 122.0764 | -0.013733 | 122.1405 | 122.1313 | 0.054932 | -0.041199 | 122.3511 | 122.2275 | 122.1909 | -0.26093 | 122.3053 | 122.2778 | 122.2504 | -0.24262
3044.2344 | 122.3877 | -122.2458 | 0.13733 | -0.023117 | -0.022646 | 0.020405 | 0.033246 | -0.0096472 | -0.041073 | -0.020115 | -0.015182 | 0.012439 | -0.0068081 | -0.099743 | -0.012356 | 0.0019654 | 0.10071 | 0.091553 | 0.1236 | 0.082397 | 0.09613 | 0.045776 | -0.091553 | 0.07782 | 0.14191 | 0.050354 | 0.041199 | 0.032043 | -0.022888 | -0.091553 | 122.2916 | 122.1542 | -0.041199 | 122.3373 | 122.3282 | 0.17395 | -0.036621 | 122.2229 | 122.1542 | -0.09613 | 122.3236 | 122.2961 | 0.14191 | -0.10529 | 122.3419 | 122.3465 | 122.3694 | -0.22888 | 122.287 | 122.2778 | 122.3877 | -0.22888
3046.0156 | 122.4976 | -121.9299 | 0.32501 | 0.0074006 | -0.018801 | 0.01891 | 0.0388 | -0.0077246 | -0.035092 | -0.023746 | 7.627e-05 | 0.17864 | 0.21258 | -0.15037 | -0.013851 | 0.050885 | 0.068665 | -0.004578 | 0.027466 | 0.050354 | 0.16479 | 0.032043 | -0.10986 | 0.064087 | 0.17395 | 0.082397 | 0.3067 | 0.29297 | 0.10071 | 0.036621 | 121.962 | 121.8201 | -0.16022 | 121.9254 | 121.9803 | 0.16022 | -0.25635 | 122.0306 | 121.9666 | -0.01831 | 121.994 | 122.0123 | 0.045776 | -0.032043 | 122.0947 | 121.9986 | 121.9574 | -0.43488 | 122.2366 | 122.2229 | 122.1039 | -0.28839
3047.8125 | 122.3923 | -121.7743 | 0.43488 | -0.00022891 | -0.01581 | 0.016774 | 0.036878 | -0.0083654 | -0.032528 | -0.022037 | 7.627e-05 | 0.23867 | 0.29013 | -0.16725 | -0.011715 | 0.07182 | 0.073242 | 0 | 0.045776 | 0.054932 | 0.15564 | 0.036621 | -0.091553 | 0.1236 | 0.16937 | 0.12817 | 0.37994 | 0.35706 | 0.17395 | 0.10071 | 121.8109 | 121.6827 | -0.27924 | 121.7743 | 121.8292 | 0.14649 | -0.36163 | 121.9482 | 121.875 | -0.054931 | 121.8979 | 121.9025 | 0.027466 | -0.077819 | 121.9299 | 121.8475 | 121.8201 | -0.52643 | 122.1542 | 122.1313 | 121.9437 | -0.33417
3049.5938 | 122.3099 | -121.669 | 0.45776 | -0.00022891 | -0.017946 | 0.017842 | 0.039014 | -0.0043066 | -0.038083 | -0.023105 | 7.627e-05 | 0.2769 | 0.34845 | -0.17921 | -0.013424 | 0.08122 | 0.10529 | 0.027466 | 0.068665 | 0.10986 | 0.17853 | 0.054932 | -0.082397 | 0.16937 | 0.27924 | 0.21973 | 0.41657 | 0.41657 | 0.20599 | 0.15106 | 121.7239 | 121.5866 | -0.27924 | 121.6965 | 121.7789 | 0.19226 | -0.35248 | 121.875 | 121.8201 | -0.041199 | 121.8384 | 121.8887 | 0.068665 | -0.041199 | 121.8475 | 121.7743 | 121.7377 | -0.54016 | 122.0856 | 122.0856 | 121.9482 | -0.3067
3051.375 | 122.3145 | -121.4493 | 0.6546 | -0.0078584 | -0.01816 | 0.019551 | 0.034528 | -0.0036658 | -0.039151 | -0.025455 | -0.0075532 | 0.39354 | 0.50995 | -0.21595 | -0.011715 | 0.12074 | 0.11902 | 0.059509 | 0.10986 | 0.10529 | 0.20142 | 0.082397 | -0.064087 | 0.28381 | 0.37079 | 0.37537 | 0.56305 | 0.55389 | 0.34332 | 0.28839 | 121.5317 | 121.3852 | -0.45319 | 121.5088 | 121.5546 | 0.16937 | -0.53558 | 121.7926 | 121.7377 | -0.091553 | 121.7331 | 121.8246 | 0.086975 | -0.10071 | 121.6507 | 121.5683 | 121.5591 | -0.71869 | 122.0123 | 122.0032 | 121.8201 | -0.36621
3053.1719 | 122.2 | -121.3531 | 0.71411 | -0.00022891 | -0.016238 | 0.016346 | 0.036237 | -0.0060156 | -0.032528 | -0.025669 | -0.0075532 | 0.45058 | 0.58108 | -0.23497 | -0.011501 | 0.13826 | 0.14648 | 0.07782 | 0.091553 | 0.11902 | 0.21057 | 0.10071 | -0.064087 | 0.27924 | 0.38452 | 0.34332 | 0.62256 | 0.61798 | 0.36621 | 0.32044 | 121.4539 | 121.2891 | -0.50354 | 121.431 | 121.4722 | 0.18311 | -0.56763 | 121.7194 | 121.6736 | -0.091552 | 121.6324 | 121.6965 | 0.022888 | -0.09613 | 121.5637 | 121.4996 | 121.4447 | -0.7782 | 121.9757 | 121.9711 | 121.7377 | -0.39368
3054.9688 | 122.0764 | -121.2524 | 0.76446 | -0.0078584 | -0.01816 | 0.016774 | 0.036237 | -0.0025976 | -0.040432 | -0.028019 | -0.015182 | 0.46788 | 0.61163 | -0.24116 | -0.016842 | 0.14595 | 0.086975 | 0.050354 | 0.091553 | 0.09613 | 0.20142 | 0.091553 | -0.068665 | 0.2655 | 0.39825 | 0.3891 | 0.67291 | 0.6546 | 0.39368 | 0.31586 | 121.344 | 121.1838 | -0.56305 | 121.3028 | 121.3486 | 0.16479 | -0.67749 | 121.6461 | 121.5683 | -0.091552 | 121.5179 | 121.6415 | 0.073242 | -0.10986 | 121.4539 | 121.3394 | 121.344 | -0.83313 | 121.9254 | 121.907 | 121.6507 | -0.44861
3056.7656 | 122.0123 | -121.0602 | 0.90179 | -0.015487 | -0.019655 | 0.018696 | 0.039441 | 0.0016748 | -0.04385 | -0.029941 | -0.0075532 | 0.54757 | 0.72015 | -0.26616 | -0.019192 | 0.17137 | 0.21515 | 0.19226 | 0.23346 | 0.20599 | 0.20599 | 0.13275 | 0.009155 | 0.42572 | 0.59967 | 0.57678 | 0.737 | 0.72327 | 0.50812 | 0.42572 | 121.1929 | 121.0693 | -0.6958 | 121.2524 | 121.2662 | 0.19684 | -0.68664 | 121.5683 | 121.4859 | -0.16479 | 121.4859 | 121.637 | 0.15106 | -0.17853 | 121.2662 | 121.2753 | 121.2936 | -0.89264 | 121.7972 | 121.7834 | 121.6599 | -0.47607
3058.5625 | 122.0856 | -120.9412 | 0.89264 | -0.00022891 | -0.017519 | 0.015919 | 0.0388 | 0.00039316 | -0.034237 | -0.028232 | -0.0075532 | 0.57491 | 0.75027 | -0.27171 | -0.013638 | 0.17457 | 0.15564 | 0.032043 | 0.09613 | 0.10529 | 0.22888 | 0.086975 | -0.032043 | 0.37994 | 0.46234 | 0.5127 | 0.80566 | 0.76904 | 0.5127 | 0.43488 | 121.0281 | 120.9091 | -0.66376 | 120.9732 | 121.0464 | 0.13733 | -0.737 | 121.4539 | 121.376 | -0.086975 | 121.3211 | 121.4539 | 0.07782 | -0.1236 | 121.17 | 121.0968 | 121.0373 | -0.92468 | 121.7468 | 121.7102 | 121.4035 | -0.45776
3060.2812 | 122.0306 | -121.17 | 0.60425 | -0.0078584 | -0.014529 | 0.014851 | 0.037732 | -0.0030248 | -0.034878 | -0.023105 | -0.0075532 | 0.36043 | 0.45077 | -0.20036 | -0.01257 | 0.10664 | 0.086975 | -0.022888 | 0.050354 | 0.073242 | 0.20142 | 0.059509 | -0.068665 | 0.18768 | 0.24261 | 0.21973 | 0.53101 | 0.5127 | 0.27466 | 0.21057 | 121.2296 | 121.1014 | -0.40283 | 121.1472 | 121.2433 | 0.14191 | -0.51727 | 121.4447 | 121.3806 | -0.073242 | 121.3577 | 121.3898 | 0.009156 | -0.091553 | 121.3715 | 121.257 | 121.2204 | -0.67291 | 121.7011 | 121.6827 | 121.4127 | -0.39368
3062.0625 | 122.0078 | -120.8176 | 0.94299 | 0.0074006 | -0.015597 | 0.015919 | 0.038159 | -3.424e-05 | -0.035305 | -0.028232 | 7.627e-05 | 0.60781 | 0.78979 | -0.28154 | -0.014065 | 0.18376 | 0.18768 | 0.09613 | 0.12817 | 0.16022 | 0.25177 | 0.10071 | -0.050354 | 0.39825 | 0.53101 | 0.53101 | 0.82398 | 0.82398 | 0.53101 | 0.45776 | 120.9183 | 120.7672 | -0.69122 | 120.9137 | 120.9778 | 0.21057 | -0.75531 | 121.3486 | 121.2753 | -0.11902 | 121.2158 | 121.3486 | 0.073242 | -0.11902 | 121.0693 | 121.0052 | 120.9457 | -0.99335 | 121.6415 | 121.6415 | 121.3486 | -0.48523
3063.8594 | 121.843 | -120.3186 | 1.3184 | -0.00022891 | -0.01816 | 0.017201 | 0.036237 | 0.0059474 | -0.03851 | -0.032718 | -0.015182 | 0.87484 | 1.1643 | -0.3672 | -0.015988 | 0.26921 | 0.24261 | 0.19684 | 0.23804 | 0.22888 | 0.26093 | 0.17395 | 0.045776 | 0.64087 | 0.79651 | 0.86517 | 1.1307 | 1.1261 | 0.82398 | 0.74616 | 120.4926 | 120.3644 | -1.0574 | 120.5154 | 120.5475 | 0.18311 | -1.0757 | 121.1426 | 121.0648 | -0.18768 | 120.9595 | 121.1838 | 0.11902 | -0.19226 | 120.5795 | 120.5612 | 120.5566 | -1.2726 | 121.4493 | 121.4447 | 121.1151 | -0.5722
3065.6562 | 121.756 | -120.7764 | 0.86517 | -0.00022891 | -0.014956 | 0.015492 | 0.035596 | -0.0011022 | -0.035092 | -0.026523 | -0.0075532 | 0.59179 | 0.76843 | -0.2732 | -0.012997 | 0.1765 | 0.11444 | 0.018311 | 0.064087 | 0.10986 | 0.23804 | 0.10986 | -0.022888 | 0.34332 | 0.43945 | 0.44861 | 0.79651 | 0.80109 | 0.48981 | 0.4303 | 120.8862 | 120.7535 | -0.62714 | 120.7947 | 120.8862 | 0.13275 | -0.75073 | 121.2662 | 121.2067 | -0.068664 | 121.1197 | 121.225 | 0.01831 | -0.064087 | 121.0144 | 120.8908 | 120.8405 | -0.88806 | 121.5729 | 121.5775 | 121.2158 | -0.43487
3067.375 | 121.7285 | -120.7672 | 0.93384 | 0.0074006 | -0.018801 | 0.019551 | 0.038373 | -0.0015294 | -0.042996 | -0.028019 | 7.627e-05 | 0.59093 | 0.78018 | -0.28047 | -0.015133 | 0.18098 | 0.16937 | 0.14191 | 0.17395 | 0.1831 | 0.20599 | 0.1236 | -0.022888 | 0.3891 | 0.50354 | 0.49439 | 0.81482 | 0.79193 | 0.51727 | 0.43945 | 120.8908 | 120.7443 | -0.72784 | 120.9091 | 120.9503 | 0.20599 | -0.76446 | 121.2845 | 121.2067 | -0.11902 | 121.1563 | 121.2616 | 0.054932 | -0.14191 | 120.9732 | 120.9366 | 120.9412 | -0.95673 | 121.582 | 121.5591 | 121.2708 | -0.49438
3069.1719 | 121.5134 | -118.602 | 2.7878 | -0.015487 | -0.020937 | 0.017628 | 0.036664 | 0.016415 | -0.042569 | -0.04639 | 7.627e-05 | 1.9071 | 2.5392 | -0.67909 | -0.018337 | 0.58174 | 0.37079 | 0.36163 | 0.40741 | 0.40283 | 0.4303 | 0.35248 | 0.19684 | 1.3229 | 1.5656 | 1.8585 | 2.3987 | 2.3987 | 1.7853 | 1.7258 | 118.9545 | 118.7988 | -2.3575 | 118.9636 | 119.0048 | 0.20599 | -2.417 | 120.3873 | 120.3278 | -0.3891 | 119.9249 | 120.4605 | 0.13275 | -0.3891 | 119.0323 | 118.9728 | 119.0094 | -2.5909 | 121.0007 | 121.0007 | 120.1675 | -1.062
3070.9531 | 121.3898 | -120.3232 | 0.99335 | -0.00022891 | -0.019015 | 0.018055 | 0.037732 | -0.002384 | -0.042141 | -0.031223 | 7.627e-05 | 0.63494 | 0.84128 | -0.29072 | -0.017269 | 0.19359 | 0.1831 | 0.16022 | 0.20599 | 0.18768 | 0.21057 | 0.14191 | 0.004578 | 0.48981 | 0.62714 | 0.64545 | 0.85144 | 0.82855 | 0.54932 | 0.50812 | 120.4651 | 120.3278 | -0.78278 | 120.4834 | 120.5109 | 0.1831 | -0.81024 | 120.8725 | 120.8313 | -0.14191 | 120.813 | 120.9686 | 0.13733 | -0.1648 | 120.5338 | 120.5063 | 120.5292 | -0.98877 | 121.1746 | 121.1517 | 120.9503 | -0.48523
3072.75 | 121.6507 | -120.6665 | 0.70953 | -0.0078584 | -0.017092 | 0.018483 | 0.034101 | -0.0019568 | -0.033383 | -0.028019 | -0.0075532 | 0.45784 | 0.58514 | -0.23262 | -0.011501 | 0.13441 | 0.12817 | 0.041199 | 0.086975 | 0.11444 | 0.21515 | 0.07782 | -0.064087 | 0.28839 | 0.42114 | 0.36621 | 0.63629 | 0.60883 | 0.36621 | 0.29297 | 120.7443 | 120.6024 | -0.49438 | 120.7077 | 120.7809 | 0.17853 | -0.58136 | 121.0327 | 120.9595 | -0.073242 | 120.9549 | 121.0327 | 0.073242 | -0.10071 | 120.8817 | 120.7947 | 120.7535 | -0.77362 | 121.3028 | 121.2753 | 121.0876 | -0.41657
3074.4844 | 121.5866 | -121.5408 | 0.10529 | -0.0078584 | -0.018801 | 0.017628 | 0.034741 | -0.0070836 | -0.03616 | -0.019901 | -0.0075532 | 0.014789 | -0.0046719 | -0.096752 | -0.011929 | 0.0013244 | 0.032043 | -0.041199 | -0.009155 | 0.027466 | 0.15564 | -0.022888 | -0.16937 | -0.050354 | 0.054932 | -0.073242 | 0.07782 | 0.082397 | -0.045776 | -0.11444 | 121.5179 | 121.3715 | 0.050354 | 121.4996 | 121.5683 | 0.19684 | -0.073243 | 121.4951 | 121.4264 | -0.027466 | 121.4905 | 121.4676 | 0.041199 | -0.022889 | 121.6965 | 121.5729 | 121.5317 | -0.27466 | 121.6187 | 121.6232 | 121.5958 | -0.21973
3076.2656 | 121.8109 | -121.5317 | 0.091553 | -0.0078584 | -0.017092 | 0.015706 | 0.035596 | -0.0079382 | -0.034665 | -0.016483 | -0.0075532 | 0.041492 | 0.026517 | -0.10487 | -0.013424 | 0.0060242 | 0.09613 | 0.013733 | 0.050354 | 0.050354 | 0.14648 | 0.027466 | -0.13275 | 0.036621 | 0.09613 | -0.009155 | 0.1236 | 0.10529 | -0.045776 | -0.10071 | 121.5591 | 121.3989 | 0.054931 | 121.5454 | 121.582 | 0.18311 | 0.004577 | 121.4859 | 121.431 | 0.032043 | 121.5683 | 121.5225 | 0.091553 | 0.013733 | 121.6782 | 121.6278 | 121.582 | -0.2243 | 121.6553 | 121.637 | 121.6278 | -0.19226
3078 | 121.7651 | -121.4218 | 0.2243 | -0.0078584 | -0.017946 | 0.01656 | 0.034314 | -0.0070836 | -0.037442 | -0.019901 | 0.0077058 | 0.10665 | 0.12051 | -0.12388 | -0.012783 | 0.0276 | 0.10529 | 0.027466 | 0.059509 | 0.059509 | 0.15564 | 0.027466 | -0.11444 | 0.068665 | 0.14648 | 0.045776 | 0.1831 | 0.17853 | 0.027466 | -0.009155 | 121.4493 | 121.3074 | -0.068664 | 121.4493 | 121.4813 | 0.17395 | -0.11902 | 121.4493 | 121.4127 | -0.041199 | 121.4905 | 121.4676 | 0.054931 | -0.045776 | 121.5775 | 121.5271 | 121.4813 | -0.33875 | 121.6049 | 121.6003 | 121.5683 | -0.23346
3079.7969 | 121.7285 | -121.6232 | 0.14191 | -0.015487 | -0.019442 | 0.020192 | 0.036664 | -0.0096472 | -0.042569 | -0.020542 | 0.0077058 | 0.0070988 | -0.0078763 | -0.10017 | -0.016201 | 0.0019654 | 0.09613 | 0.10529 | 0.13733 | 0.082397 | 0.091553 | 0.027466 | -0.09613 | 0.027466 | 0.17853 | 0.059509 | 0.050354 | 0.068665 | -0.032043 | -0.10986 | 121.6507 | 121.5271 | -0.050354 | 121.7285 | 121.7056 | 0.17853 | -0.045777 | 121.5912 | 121.5134 | -0.091553 | 121.6507 | 121.6827 | 0.16937 | -0.073242 | 121.7148 | 121.7194 | 121.7606 | -0.23804 | 121.6736 | 121.6919 | 121.8018 | -0.25177
3081.5938 | 121.907 | -121.756 | 0.13733 | 0.0074006 | -0.01816 | 0.019978 | 0.037732 | -0.0094336 | -0.042996 | -0.020328 | 7.627e-05 | 0.007526 | -0.0091579 | -0.098461 | -0.016415 | 0.0023926 | 0.036621 | 0.027466 | 0.068665 | 0.054932 | 0.086975 | 0.032043 | -0.086975 | -0.013733 | 0.10071 | 0.009155 | 0.059509 | 0.054932 | -0.036621 | -0.10529 | 121.788 | 121.669 | -0.050354 | 121.7834 | 121.8109 | 0.14191 | -0.10071 | 121.7194 | 121.6507 | -0.07782 | 121.7422 | 121.7651 | 0.11444 | -0.082397 | 121.843 | 121.7926 | 121.8246 | -0.2243 | 121.8155 | 121.8109 | 121.8567 | -0.24262
3083.375 | 121.907 | -121.5637 | 0.1236 | -0.0078584 | -0.015597 | 0.016346 | 0.036878 | -0.010074 | -0.03381 | -0.019687 | -0.0075532 | 0.025684 | 0.0085727 | -0.10145 | -0.011929 | 0.0017518 | 0.11444 | 0.009155 | 0.036621 | 0.059509 | 0.11444 | 0.013733 | -0.12817 | -0.004578 | 0.09613 | -0.013733 | 0.091553 | 0.09613 | -0.036621 | -0.10071 | 121.5775 | 121.4355 | -0.009155 | 121.5729 | 121.6232 | 0.18768 | -0.009155 | 121.5271 | 121.463 | -0.032043 | 121.5591 | 121.55 | 0.086975 | -0.027466 | 121.6782 | 121.6782 | 121.6003 | -0.25177 | 121.6553 | 121.6599 | 121.6599 | -0.2243
3085.1562 | 121.6003 | -121.3028 | 0.13275 | -0.0078584 | -0.014956 | 0.018483 | 0.03645 | -0.0077246 | -0.038083 | -0.022251 | 7.627e-05 | 0.050251 | 0.04083 | -0.10978 | -0.015133 | 0.010083 | 0.045776 | -0.036621 | -0.004578 | 0.027466 | 0.15106 | 0.004578 | -0.12817 | -0.022888 | 0.082397 | -0.013733 | 0.13733 | 0.13275 | -0.032043 | -0.091553 | 121.3074 | 121.1746 | 0.018311 | 121.2662 | 121.3303 | 0.15564 | -0.086975 | 121.2708 | 121.2112 | 0.004578 | 121.2799 | 121.2891 | 0.07782 | 0 | 121.4539 | 121.3486 | 121.2982 | -0.26093 | 121.4401 | 121.4355 | 121.3852 | -0.2243
3086.8906 | 118.3273 | -118.2953 | 0.21057 | -0.015487 | -0.017733 | 0.020619 | 0.038159 | -0.008579 | -0.041928 | -0.021396 | 7.627e-05 | 0.087635 | 0.089536 | -0.12388 | -0.014919 | 0.023755 | 0.10071 | 0.091553 | 0.10071 | 0.10986 | 0.11902 | 0.054932 | -0.09613 | 0.022888 | 0.17853 | 0.091553 | 0.15564 | 0.15564 | 0.027466 | -0.041199 | 118.3502 | 118.1992 | -0.091552 | 118.3868 | 118.4052 | 0.20599 | -0.10986 | 118.3228 | 118.2541 | -0.054931 | 118.3182 | 118.3868 | 0.13275 | -0.054931 | 118.4143 | 118.396 | 118.396 | -0.3067 | 118.4509 | 118.4509 | 118.4738 | -0.25177
3088.6875 | 121.5134 | -120.726 | 0.55847 | -0.00022891 | -0.018587 | 0.018055 | 0.032392 | -0.0030248 | -0.036587 | -0.024814 | 7.627e-05 | 0.34676 | 0.44265 | -0.19758 | -0.013424 | 0.10045 | 0.11902 | 0.045776 | 0.091553 | 0.10986 | 0.17853 | 0.073242 | -0.054932 | 0.27008 | 0.36163 | 0.33875 | 0.47607 | 0.45776 | 0.29297 | 0.2243 | 120.7993 | 120.6711 | -0.37994 | 120.7718 | 120.8359 | 0.16479 | -0.43945 | 121.019 | 120.9503 | -0.082398 | 120.9961 | 121.0648 | 0.11444 | -0.10071 | 120.9045 | 120.845 | 120.8176 | -0.6134 | 121.2021 | 121.1838 | 121.0876 | -0.33417
3090.4062 | 121.3257 | -120.7031 | 0.39825 | 0.0074006 | -0.016878 | 0.015278 | 0.037091 | -0.005802 | -0.034878 | -0.022037 | -0.015182 | 0.22799 | 0.28628 | -0.16191 | -0.012356 | 0.064557 | 0.15564 | 0.054932 | 0.086975 | 0.082397 | 0.15564 | 0.054932 | -0.091553 | 0.14648 | 0.23346 | 0.14191 | 0.36163 | 0.34332 | 0.13275 | 0.091553 | 120.7581 | 120.6116 | -0.24261 | 120.7581 | 120.7855 | 0.17395 | -0.24261 | 120.8359 | 120.7947 | -0.036621 | 120.8496 | 120.845 | 0.050354 | -0.054931 | 120.8588 | 120.8588 | 120.7901 | -0.48981 | 121.0648 | 121.0464 | 120.9366 | -0.3067
3092.1875 | 121.138 | -120.8679 | 0.2243 | -0.0078584 | -0.023287 | 0.019764 | 0.034528 | -0.0062292 | -0.04321 | -0.021183 | 7.627e-05 | 0.07674 | 0.08975 | -0.12474 | -0.017697 | 0.024609 | 0.10986 | 0.11444 | 0.15564 | 0.11444 | 0.11902 | 0.050354 | -0.091553 | 0.11902 | 0.24719 | 0.14648 | 0.12817 | 0.14191 | 0.041199 | -0.022888 | 120.9183 | 120.7764 | -0.10529 | 120.9824 | 120.9824 | 0.20599 | -0.11444 | 120.9091 | 120.845 | -0.09613 | 120.9869 | 121.0144 | 0.16937 | -0.082397 | 120.9869 | 120.9778 | 121.0236 | -0.31586 | 120.9961 | 121.0098 | 121.1151 | -0.24719
3093.9844 | 121.4447 | -121.2799 | 0.11444 | -0.0078584 | -0.018374 | 0.018055 | 0.0388 | -0.011997 | -0.037655 | -0.019901 | 0.0077058 | 0.016925 | -0.0018949 | -0.09782 | -0.015774 | -0.00059818 | 0.027466 | -0.041199 | -0.009155 | 0.018311 | 0.15564 | 0.013733 | -0.15564 | -0.064087 | 0.018311 | -0.07782 | 0.10071 | 0.10529 | -0.059509 | -0.13275 | 121.2936 | 121.1243 | 0.041199 | 121.2387 | 121.2982 | 0.17395 | -0.086975 | 121.2204 | 121.1472 | -0.013733 | 121.2158 | 121.2021 | 0.054931 | -0.009155 | 121.4355 | 121.3074 | 121.2708 | -0.27008 | 121.3806 | 121.3852 | 121.2982 | -0.24719
3095.7188 | 121.2524 | -120.9641 | 0.09613 | -0.0078584 | -0.017092 | 0.016133 | 0.035596 | -0.0066564 | -0.034451 | -0.019046 | -0.015182 | 0.023761 | 0.0043003 | -0.098461 | -0.01257 | 0.0041016 | 0.13275 | 0.013733 | 0.027466 | 0.054932 | 0.14191 | 0.022888 | -0.1236 | 0.009155 | 0.082397 | -0.041199 | 0.086975 | 0.091553 | -0.059509 | -0.10986 | 120.9869 | 120.8405 | 0.045777 | 120.9778 | 121.019 | 0.17853 | 0.036621 | 120.9045 | 120.8542 | -0.009155 | 120.9732 | 120.9229 | 0.068664 | -0.004577 | 121.106 | 121.0968 | 120.9915 | -0.21973 | 121.051 | 121.0556 | 121.0464 | -0.20599
3097.5156 | 121.0007 | -120.845 | 0.14191 | -0.00022891 | -0.022219 | 0.016987 | 0.0388 | -0.00922 | -0.044064 | -0.019687 | -0.015182 | 0.0098758 | -0.0076627 | -0.099529 | -0.018765 | 0.0030334 | 0.050354 | 0.013733 | 0.07782 | 0.059509 | 0.10986 | 0.045776 | -0.11444 | 0.009155 | 0.086975 | 0.018311 | 0.073242 | 0.054932 | -0.027466 | -0.086975 | 120.8908 | 120.7306 | -0.032044 | 120.8588 | 120.9045 | 0.17395 | -0.091553 | 120.8176 | 120.7581 | -0.068665 | 120.8542 | 120.8633 | 0.10529 | -0.086975 | 120.9549 | 120.8954 | 120.9229 | -0.25635 | 120.9183 | 120.9 | 120.932 | -0.22888
3099.25 | 121.2708 | -121.0968 | 0.12817 | -0.0078584 | -0.026705 | 0.01891 | 0.036237 | -0.0094336 | -0.040005 | -0.020115 | 7.627e-05 | 0.008594 | -0.012149 | -0.097179 | -0.017483 | -0.00038438 | 0.086975 | 0.032043 | 0.082397 | 0.050354 | 0.09613 | 0.045776 | -0.091553 | 0.027466 | 0.10529 | 0.018311 | 0.064087 | 0.050354 | -0.036621 | -0.10071 | 121.1426 | 121.0052 | -0.032044 | 121.1288 | 121.1472 | 0.14191 | -0.041199 | 121.0602 | 120.9961 | -0.064087 | 121.1243 | 121.1151 | 0.11902 | -0.07782 | 121.1929 | 121.1838 | 121.1792 | -0.21973 | 121.1609 | 121.1472 | 121.2021 | -0.22888
3101.0312 | 121.4905 | -121.3303 | 0.09613 | -0.00022891 | -0.017733 | 0.017842 | 0.040082 | -0.0098608 | -0.037655 | -0.021183 | 7.627e-05 | 0.010089 | -0.0091579 | -0.097607 | -0.014492 | -0.001239 | 0.036621 | -0.036621 | 0.013733 | 0.004578 | 0.15106 | -0.004578 | -0.15564 | -0.064087 | 0.032043 | -0.068665 | 0.091553 | 0.082397 | -0.073242 | -0.13275 | 121.3257 | 121.1746 | 0.054932 | 121.2936 | 121.3348 | 0.16022 | -0.059509 | 121.257 | 121.1975 | -0.004577 | 121.2662 | 121.2616 | 0.064086 | -0.013733 | 121.4813 | 121.3669 | 121.344 | -0.25177 | 121.4218 | 121.4127 | 121.3623 | -0.22888
3102.8281 | 121.5134 | -121.3898 | 0.11902 | -0.00022891 | -0.017092 | 0.017415 | 0.036023 | -0.0083654 | -0.040432 | -0.02396 | 7.627e-05 | 0.0094486 | -0.0080899 | -0.099529 | -0.015347 | -0.00038438 | 0.091553 | 0.059509 | 0.07782 | 0.064087 | 0.11444 | 0.022888 | -0.10529 | -0.013733 | 0.086975 | -0.013733 | 0.059509 | 0.068665 | -0.064087 | -0.1236 | 121.4127 | 121.2845 | -0.004578 | 121.4493 | 121.4539 | 0.16937 | -0.027466 | 121.3257 | 121.2662 | -0.05951 | 121.376 | 121.376 | 0.10986 | -0.050354 | 121.5042 | 121.4813 | 121.4676 | -0.22431 | 121.4493 | 121.4584 | 121.4767 | -0.24261
3104.5469 | 121.7285 | -121.3852 | 0.091553 | -0.0078584 | -0.019228 | 0.015919 | 0.034741 | -0.011997 | -0.034665 | -0.017978 | 0.0077058 | 0.010517 | -0.0093717 | -0.096111 | -0.010861 | -0.0016662 | 0.059509 | -0.050354 | -0.013733 | 0.013733 | 0.16479 | 0.009155 | -0.1236 | -0.022888 | 0.009155 | -0.054932 | 0.073242 | 0.068665 | -0.059509 | -0.13733 | 121.3943 | 121.2616 | 0.073242 | 121.3348 | 121.3989 | 0.13733 | -0.032044 | 121.3257 | 121.2479 | -0.018311 | 121.3623 | 121.3303 | 0.082397 | -0.022888 | 121.55 | 121.4447 | 121.3715 | -0.21515 | 121.4584 | 121.4539 | 121.3943 | -0.22888
3106.3281 | 121.7514 | -121.4172 | 0.086975 | -0.0078584 | -0.016024 | 0.01656 | 0.037518 | -0.0072974 | -0.03616 | -0.019474 | 7.627e-05 | 0.012439 | -0.01044 | -0.096966 | -0.01257 | -0.0023072 | 0.045776 | -0.041199 | 0.004578 | 0.032043 | 0.14191 | -0.004578 | -0.14191 | -0.032043 | 0.064087 | -0.041199 | 0.086975 | 0.073242 | -0.068665 | -0.1236 | 121.4127 | 121.2753 | 0.054932 | 121.376 | 121.4493 | 0.17395 | -0.041199 | 121.3486 | 121.2936 | 0 | 121.3852 | 121.376 | 0.082397 | -0.013733 | 121.5591 | 121.463 | 121.4218 | -0.22888 | 121.5042 | 121.4905 | 121.4813 | -0.21057
3108.1094 | 121.7514 | -121.4447 | 0.07782 | 0.01503 | -0.016238 | 0.016346 | 0.035596 | -0.0060156 | -0.035519 | -0.017765 | -0.0075532 | 0.012867 | -0.0095853 | -0.094189 | -0.011501 | -0.0027344 | 0.09613 | 0.013733 | 0.050354 | 0.032043 | 0.1236 | 0.009155 | -0.13733 | 0 | 0.086975 | -0.045776 | 0.086975 | 0.082397 | -0.059509 | -0.12817 | 121.4539 | 121.3074 | 0.045776 | 121.4584 | 121.4767 | 0.16937 | 0.01831 | 121.3852 | 121.3165 | 0.009155 | 121.4447 | 121.3989 | 0.082398 | 0.004577 | 121.5683 | 121.5408 | 121.4951 | -0.21515 | 121.5317 | 121.5271 | 121.5317 | -0.20599
3109.9062 | 121.7194 | -121.5271 | 0.1236 | -0.00022891 | -0.023073 | 0.020192 | 0.037091 | -0.0096472 | -0.042355 | -0.020969 | 7.627e-05 | 0.0060306 | -0.011935 | -0.095898 | -0.018337 | 0.002179 | 0.022888 | 0.022888 | 0.07782 | 0.045776 | 0.1236 | 0.032043 | -0.10529 | 0.013733 | 0.10986 | 0.018311 | 0.064087 | 0.064087 | -0.041199 | -0.11444 | 121.5591 | 121.4218 | 0 | 121.55 | 121.5729 | 0.15106 | -0.10071 | 121.4859 | 121.4127 | -0.059509 | 121.5408 | 121.5454 | 0.13275 | -0.059509 | 121.6507 | 121.55 | 121.6049 | -0.22888 | 121.5912 | 121.5912 | 121.637 | -0.23804
3111.6875 | 121.6965 | -121.5546 | 0.12817 | -0.00022891 | -0.024355 | 0.021901 | 0.035169 | -0.0083654 | -0.04321 | -0.021183 | 7.627e-05 | 0.0073124 | -0.013003 | -0.095043 | -0.017056 | 0.0015382 | 0.054932 | 0.027466 | 0.086975 | 0.041199 | 0.11902 | 0.027466 | -0.10529 | -0.009155 | 0.082397 | 0.022888 | 0.041199 | 0.050354 | -0.032043 | -0.091553 | 121.582 | 121.4493 | -0.009155 | 121.582 | 121.5958 | 0.14649 | -0.073242 | 121.5225 | 121.463 | -0.086975 | 121.5454 | 121.5775 | 0.11444 | -0.07782 | 121.6736 | 121.6095 | 121.6415 | -0.23346 | 121.5958 | 121.6049 | 121.637 | -0.21973
3113.4062 | 121.7606 | -121.5546 | 0.13275 | -0.0078584 | -0.023714 | 0.018269 | 0.035596 | -0.0096472 | -0.041501 | -0.021824 | -0.0075532 | 0.0079532 | -0.011508 | -0.098888 | -0.015133 | -0.0014526 | 0.10529 | 0.059509 | 0.11444 | 0.050354 | 0.10986 | 0.027466 | -0.10071 | 0.064087 | 0.14191 | 0.064087 | 0.050354 | 0.045776 | -0.022888 | -0.10071 | 121.582 | 121.4539 | -0.022888 | 121.6141 | 121.6049 | 0.15106 | -0.027465 | 121.5317 | 121.4539 | -0.082397 | 121.6187 | 121.6187 | 0.1648 | -0.086975 | 121.6644 | 121.6599 | 121.669 | -0.23346 | 121.6049 | 121.6003 | 121.6965 | -0.23346
3115.1875 | 121.7789 | -121.582 | 0.09613 | -0.015487 | -0.023073 | 0.018055 | 0.037732 | -0.0083654 | -0.041073 | -0.020969 | 7.627e-05 | 0.006885 | -0.012362 | -0.099743 | -0.017269 | 0.00047002 | 0.073242 | 0.032043 | 0.091553 | 0.064087 | 0.11902 | 0.036621 | -0.10986 | 0.032043 | 0.11444 | 0.036621 | 0.054932 | 0.045776 | -0.041199 | -0.11902 | 121.6187 | 121.4722 | 0.022889 | 121.6141 | 121.6461 | 0.17395 | -0.022888 | 121.5408 | 121.463 | -0.041198 | 121.6141 | 121.6187 | 0.15564 | -0.050354 | 121.701 | 121.6553 | 121.6736 | -0.20599 | 121.637 | 121.6278 | 121.6965 | -0.21515
3116.9531 | 121.7972 | -121.6187 | 0.12817 | -0.0078584 | -0.025637 | 0.020192 | 0.034314 | -0.013065 | -0.040219 | -0.02161 | 0.0077058 | 0.007526 | -0.012789 | -0.096538 | -0.016628 | -0.0018798 | 0.07782 | 0.036621 | 0.086975 | 0.050354 | 0.12817 | 0.022888 | -0.10071 | 0.032043 | 0.10986 | 0.027466 | 0.073242 | 0.050354 | -0.041199 | -0.10986 | 121.6415 | 121.5179 | 0 | 121.6553 | 121.669 | 0.15106 | -0.050354 | 121.5775 | 121.5088 | -0.054932 | 121.6507 | 121.6461 | 0.13733 | -0.07782 | 121.7468 | 121.6965 | 121.7056 | -0.22888 | 121.6919 | 121.669 | 121.7285 | -0.23804
3118.7344 | 121.7834 | -121.6278 | 0.11902 | -0.00022891 | -0.020937 | 0.020405 | 0.031537 | -0.00922 | -0.036801 | -0.02161 | 0.015335 | 0.0088076 | -0.014071 | -0.098247 | -0.011501 | -0.0025208 | 0.15106 | 0.073242 | 0.11902 | 0.07782 | 0.09613 | 0.032043 | -0.07782 | 0.073242 | 0.13275 | 0.027466 | 0.045776 | 0.045776 | -0.022888 | -0.086975 | 121.6599 | 121.55 | -0.022889 | 121.701 | 121.7056 | 0.15564 | 0.032043 | 121.6049 | 121.5408 | -0.073243 | 121.701 | 121.6553 | 0.11444 | -0.073243 | 121.7239 | 121.7789 | 121.7468 | -0.19684 | 121.6736 | 121.6736 | 121.7606 | -0.20599
3120.5312 | 121.788 | -121.6599 | 0.14648 | -0.00022891 | -0.020296 | 0.018269 | 0.037518 | -0.0062292 | -0.040432 | -0.021396 | 7.627e-05 | 0.0077396 | -0.011935 | -0.098247 | -0.014492 | -0.00081178 | 0.12817 | 0.059509 | 0.10529 | 0.068665 | 0.091553 | 0.027466 | -0.10529 | 0.050354 | 0.086975 | -0.009155 | 0.059509 | 0.036621 | -0.027466 | -0.10986 | 121.6873 | 121.5546 | -0.054931 | 121.7194 | 121.7285 | 0.17395 | -0.01831 | 121.6324 | 121.55 | -0.086975 | 121.7102 | 121.6507 | 0.10071 | -0.10986 | 121.7514 | 121.788 | 121.7651 | -0.25177 | 121.7194 | 121.6965 | 121.7468 | -0.25635
3122.2656 | 121.9299 | -121.6049 | 0.086975 | -0.00022891 | -0.015597 | 0.016987 | 0.039227 | -0.0079382 | -0.034878 | -0.021183 | -0.015182 | 0.014148 | -0.0095853 | -0.09782 | -0.011929 | -0.004016 | 0.059509 | -0.036621 | 0.004578 | 0.036621 | 0.14648 | 0 | -0.11902 | -0.018311 | 0.082397 | -0.068665 | 0.07782 | 0.064087 | -0.082397 | -0.13275 | 121.6049 | 121.4859 | 0.059509 | 121.5683 | 121.6415 | 0.15564 | -0.027466 | 121.5225 | 121.4722 | -0.009155 | 121.5866 | 121.5363 | 0.064086 | -0.022888 | 121.7514 | 121.6644 | 121.6095 | -0.20599 | 121.6827 | 121.669 | 121.6873 | -0.21973
3124.0469 | 121.8842 | -121.6507 | 0.10986 | -0.00022891 | -0.012179 | 0.016133 | 0.037091 | -0.0087926 | -0.030392 | -0.018833 | -0.015182 | 0.013294 | -0.0085171 | -0.096325 | -0.010433 | -0.0010254 | 0.032043 | -0.054932 | -0.022888 | 0.018311 | 0.15106 | -0.009155 | -0.14191 | -0.068665 | 0 | -0.11444 | 0.082397 | 0.064087 | -0.07782 | -0.13275 | 121.6415 | 121.5088 | 0.041199 | 121.5958 | 121.669 | 0.16022 | -0.07782 | 121.5729 | 121.5179 | -0.027466 | 121.582 | 121.5363 | 0.01831 | -0.045776 | 121.8018 | 121.6827 | 121.6278 | -0.25177 | 121.7331 | 121.7148 | 121.6507 | -0.24261
3125.8281 | 121.8246 | -121.7102 | 0.1236 | -0.0078584 | -0.022219 | 0.018483 | 0.038587 | -0.008579 | -0.041928 | -0.018833 | 7.627e-05 | 0.007526 | -0.0074491 | -0.097393 | -0.016842 | 0.0019654 | 0.073242 | 0.086975 | 0.10071 | 0.054932 | 0.11444 | 0.050354 | -0.091553 | 0.045776 | 0.1236 | 0.013733 | 0.050354 | 0.041199 | -0.032043 | -0.082397 | 121.7606 | 121.6187 | -0.009155 | 121.7972 | 121.7651 | 0.14649 | -0.050354 | 121.6782 | 121.6278 | -0.073242 | 121.756 | 121.7239 | 0.09613 | -0.082397 | 121.8246 | 121.7834 | 121.8109 | -0.21515 | 121.7606 | 121.7514 | 121.8338 | -0.20599
3127.6094 | 121.9299 | -121.6736 | 0.10986 | 0.0074006 | -0.01282 | 0.015278 | 0.034314 | -0.0090062 | -0.034024 | -0.018619 | 7.627e-05 | 0.012867 | -0.0085171 | -0.096966 | -0.013638 | -0.0020934 | 0.041199 | -0.041199 | -0.018311 | 0.018311 | 0.12817 | 0.004578 | -0.12817 | -0.027466 | 0.018311 | -0.11444 | 0.07782 | 0.068665 | -0.068665 | -0.12817 | 121.6782 | 121.5454 | 0.018311 | 121.6324 | 121.6919 | 0.14649 | -0.068664 | 121.6049 | 121.5454 | -0.032043 | 121.6461 | 121.5591 | 0.013733 | -0.041198 | 121.8018 | 121.7148 | 121.6553 | -0.23804 | 121.7514 | 121.7422 | 121.6919 | -0.23804
3129.4062 | 121.9849 | -121.6782 | 0.09613 | -0.0078584 | -0.01816 | 0.015706 | 0.03645 | -0.005802 | -0.037869 | -0.017551 | 0.0077058 | 0.010303 | -0.012149 | -0.095257 | -0.012356 | -0.00038438 | 0.1236 | 0.064087 | 0.10071 | 0.091553 | 0.10986 | 0.041199 | -0.091553 | 0.068665 | 0.14191 | 0.036621 | 0.041199 | 0.036621 | -0.032043 | -0.09613 | 121.7194 | 121.5866 | 0.013733 | 121.7422 | 121.7697 | 0.18311 | 0.027466 | 121.6461 | 121.582 | -0.054931 | 121.7468 | 121.7148 | 0.13275 | -0.059509 | 121.788 | 121.8018 | 121.7789 | -0.18768 | 121.7194 | 121.7148 | 121.8201 | -0.19226
3131.1875 | 121.8567 | -121.7148 | 0.11902 | -0.015487 | -0.017519 | 0.018696 | 0.039227 | -0.0094336 | -0.042141 | -0.018406 | 7.627e-05 | 0.0043216 | -0.013858 | -0.10038 | -0.015347 | -0.00081178 | 0.11444 | 0.11444 | 0.14191 | 0.10986 | 0.10529 | 0.036621 | -0.10986 | 0.045776 | 0.19226 | 0.064087 | 0.050354 | 0.045776 | -0.032043 | -0.10986 | 121.7514 | 121.6049 | -0.013733 | 121.8292 | 121.8246 | 0.21973 | -0.004578 | 121.6827 | 121.6049 | -0.068665 | 121.7606 | 121.7789 | 0.17395 | -0.073243 | 121.8201 | 121.8292 | 121.8567 | -0.22888 | 121.7651 | 121.7606 | 121.907 | -0.22888
3132.9844 | 121.9711 | -121.7285 | 0.10071 | -0.0078584 | -0.019655 | 0.015278 | 0.036237 | -0.0098608 | -0.032315 | -0.017765 | 7.627e-05 | 0.013721 | -0.0093717 | -0.096752 | -0.0095788 | -0.0016662 | 0.09613 | -0.009155 | 0.009155 | 0.041199 | 0.12817 | 0.027466 | -0.11444 | -0.018311 | 0.041199 | -0.07782 | 0.07782 | 0.064087 | -0.073242 | -0.1236 | 121.756 | 121.6141 | 0.027466 | 121.7194 | 121.7697 | 0.15564 | -0.004578 | 121.6553 | 121.6049 | -0.022888 | 121.7102 | 121.6507 | 0.045776 | -0.036621 | 121.8567 | 121.8246 | 121.7377 | -0.21515 | 121.8063 | 121.7926 | 121.7697 | -0.2243
3134.7656 | 122.0444 | -121.7056 | 0.10529 | -0.00022891 | -0.018374 | 0.016346 | 0.034528 | -0.0077246 | -0.034237 | -0.021183 | -0.0075532 | 0.010517 | -0.011294 | -0.095043 | -0.01321 | -0.00038438 | 0.064087 | -0.032043 | 0.013733 | 0.022888 | 0.12817 | 0.018311 | -0.12817 | 0.018311 | 0.073242 | -0.018311 | 0.07782 | 0.054932 | -0.054932 | -0.11444 | 121.7239 | 121.5775 | 0.022888 | 121.6736 | 121.7285 | 0.15106 | -0.041199 | 121.6507 | 121.5912 | -0.027466 | 121.7239 | 121.6873 | 0.09613 | -0.050354 | 121.8338 | 121.7697 | 121.7194 | -0.23346 | 121.7834 | 121.7606 | 121.7789 | -0.21973
3136.4844 | 121.9345 | -121.7606 | 0.12817 | 0.0074006 | -0.022433 | 0.017415 | 0.034101 | -0.0079382 | -0.039792 | -0.018619 | -0.0075532 | 0.0096622 | -0.01108 | -0.097179 | -0.014706 | 0.00047002 | 0.1236 | 0.064087 | 0.1236 | 0.091553 | 0.082397 | 0.032043 | -0.09613 | 0.073242 | 0.14648 | 0.054932 | 0.032043 | 0.041199 | -0.018311 | -0.09613 | 121.7926 | 121.6644 | -0.045777 | 121.8246 | 121.8521 | 0.18768 | -0.004578 | 121.7422 | 121.6644 | -0.096131 | 121.8338 | 121.8155 | 0.15106 | -0.086975 | 121.843 | 121.8842 | 121.8842 | -0.2243 | 121.7926 | 121.8018 | 121.907 | -0.2243
3138.2656 | 121.9299 | -121.7743 | 0.1236 | 0.0074006 | -0.02051 | 0.016133 | 0.035809 | -0.010074 | -0.039578 | -0.019474 | 7.627e-05 | 0.0098758 | -0.0089443 | -0.096538 | -0.014706 | 0.0011108 | 0.1236 | 0.082397 | 0.13275 | 0.07782 | 0.091553 | 0.036621 | -0.09613 | 0.07782 | 0.13733 | 0.050354 | 0.036621 | 0.036621 | -0.050354 | -0.10529 | 121.8109 | 121.6782 | -0.032043 | 121.8567 | 121.8521 | 0.17395 | 0 | 121.7239 | 121.669 | -0.086975 | 121.8521 | 121.8246 | 0.15564 | -0.086975 | 121.8658 | 121.8979 | 121.907 | -0.21973 | 121.8109 | 121.8109 | 121.9116 | -0.22888
3140 | 121.9391 | -121.8018 | 0.11444 | -0.00022891 | -0.019015 | 0.017842 | 0.037091 | -0.00922 | -0.04086 | -0.021183 | 7.627e-05 | 0.0079532 | -0.011935 | -0.098675 | -0.011929 | -0.00081178 | 0.12817 | 0.10071 | 0.11902 | 0.082397 | 0.086975 | 0.041199 | -0.10071 | 0.064087 | 0.12817 | 0.022888 | 0.041199 | 0.041199 | -0.022888 | -0.09613 | 121.843 | 121.7011 | -0.027466 | 121.9025 | 121.8842 | 0.18311 | 0.013733 | 121.7789 | 121.7056 | -0.073242 | 121.8658 | 121.8246 | 0.11902 | -0.073242 | 121.8887 | 121.9299 | 121.9208 | -0.21515 | 121.843 | 121.843 | 121.9299 | -0.21057
3141.7812 | 122.0398 | -121.7697 | 0.082397 | -0.0078584 | -0.016238 | 0.019123 | 0.034314 | -0.0090062 | -0.034878 | -0.018406 | -0.0075532 | 0.01308 | -0.01108 | -0.099102 | -0.010861 | -0.00081178 | 0.054932 | -0.068665 | -0.022888 | 0.009155 | 0.14648 | 0.004578 | -0.13275 | -0.036621 | -0.013733 | -0.10529 | 0.07782 | 0.073242 | -0.064087 | -0.13733 | 121.7743 | 121.637 | 0.064087 | 121.701 | 121.7789 | 0.14191 | -0.027465 | 121.7056 | 121.6324 | -0.004577 | 121.7331 | 121.6644 | 0.032043 | -0.009155 | 121.9162 | 121.8246 | 121.7468 | -0.21515 | 121.8475 | 121.843 | 121.756 | -0.21973
3143.5625 | 122.0627 | -121.7606 | 0.09613 | -0.015487 | -0.019442 | 0.014851 | 0.03645 | -0.00922 | -0.034878 | -0.017978 | -0.0075532 | 0.011798 | -0.0085171 | -0.09782 | -0.013638 | -0.0016662 | 0.086975 | 0.018311 | 0.054932 | 0.054932 | 0.13275 | 0.013733 | -0.12817 | 0 | 0.086975 | -0.036621 | 0.091553 | 0.082397 | -0.073242 | -0.11444 | 121.7743 | 121.6324 | 0.036621 | 121.7789 | 121.8155 | 0.18311 | -0.009155 | 121.6873 | 121.6461 | -0.004577 | 121.7606 | 121.7239 | 0.07782 | -0.013733 | 121.8933 | 121.8475 | 121.8155 | -0.2243 | 121.8521 | 121.843 | 121.8475 | -0.21057
3145.2969 | 122.0306 | -121.7834 | 0.10529 | -0.0078584 | -0.016024 | 0.015706 | 0.0388 | -0.0081518 | -0.034878 | -0.017551 | -0.0075532 | 0.011585 | -0.0070217 | -0.097179 | -0.012997 | -0.0014526 | 0.07782 | 0.009155 | 0.027466 | 0.032043 | 0.10529 | 0.018311 | -0.12817 | -0.013733 | 0.059509 | -0.068665 | 0.082397 | 0.068665 | -0.059509 | -0.10986 | 121.8018 | 121.6553 | 0 | 121.7926 | 121.8155 | 0.16022 | -0.027466 | 121.7239 | 121.6736 | -0.022889 | 121.7697 | 121.7148 | 0.041198 | -0.036621 | 121.8887 | 121.8613 | 121.8109 | -0.23346 | 121.8658 | 121.8521 | 121.843 | -0.21515
3147.0938 | 122.081 | -121.7789 | 0.086975 | -0.0078584 | -0.019015 | 0.015919 | 0.03645 | -0.010074 | -0.038723 | -0.017124 | 7.627e-05 | 0.013721 | -0.0083035 | -0.09782 | -0.012783 | 0.0011108 | 0 | -0.054932 | -0.027466 | 0.013733 | 0.14648 | 0.004578 | -0.13275 | -0.050354 | 0 | -0.068665 | 0.07782 | 0.082397 | -0.064087 | -0.11902 | 121.7834 | 121.6461 | 0.059509 | 121.7239 | 121.7926 | 0.14648 | -0.086975 | 121.7148 | 121.6599 | -0.009155 | 121.7285 | 121.7102 | 0.050354 | -0.004578 | 121.9254 | 121.7789 | 121.7514 | -0.21973 | 121.8567 | 121.8613 | 121.7789 | -0.20599
3148.9062 | 122.0993 | -121.8063 | 0.10071 | -0.00022891 | -0.013888 | 0.017842 | 0.042218 | -0.00687 | -0.036374 | -0.020328 | -0.0075532 | 0.012012 | -0.0053127 | -0.098247 | -0.016415 | -0.00017078 | 0.045776 | -0.004578 | 0.041199 | 0.054932 | 0.14648 | -0.004578 | -0.12817 | -0.027466 | 0.07782 | -0.036621 | 0.10986 | 0.082397 | -0.050354 | -0.13275 | 121.8018 | 121.6782 | 0.045776 | 121.8018 | 121.8613 | 0.18311 | -0.054932 | 121.756 | 121.6736 | 0.009155 | 121.7789 | 121.7697 | 0.09613 | -0.018311 | 121.9528 | 121.8521 | 121.8475 | -0.22888 | 121.9162 | 121.8887 | 121.8842 | -0.23346
3150.6406 | 121.9803 | -121.843 | 0.10529 | -0.0078584 | -0.020083 | 0.017628 | 0.037305 | -0.0070836 | -0.041714 | -0.021396 | -0.0075532 | 0.006885 | -0.0083035 | -0.098247 | -0.016201 | 0.00025642 | 0.091553 | 0.10529 | 0.14648 | 0.10071 | 0.091553 | 0.027466 | -0.10071 | 0.032043 | 0.17853 | 0.064087 | 0.064087 | 0.041199 | -0.041199 | -0.11444 | 121.8704 | 121.7422 | -0.013733 | 121.9482 | 121.9437 | 0.20142 | -0.013733 | 121.8018 | 121.7285 | -0.041199 | 121.875 | 121.907 | 0.17853 | -0.064087 | 121.9345 | 121.9345 | 121.9894 | -0.20599 | 121.907 | 121.8842 | 122.0215 | -0.21973
3152.4219 | 122.0078 | -121.8796 | 0.14191 | -0.0078584 | -0.022433 | 0.020619 | 0.034101 | -0.0072974 | -0.04086 | -0.022464 | 7.627e-05 | 0.0081668 | -0.010012 | -0.098888 | -0.014706 | -0.00081178 | 0.09613 | 0.09613 | 0.11902 | 0.082397 | 0.09613 | 0.032043 | -0.11902 | 0.045776 | 0.11902 | 0.045776 | 0.059509 | 0.059509 | -0.036621 | -0.091553 | 121.9116 | 121.7606 | -0.045777 | 121.9757 | 121.962 | 0.20142 | -0.045777 | 121.843 | 121.788 | -0.082398 | 121.9254 | 121.9254 | 0.13733 | -0.082398 | 121.9757 | 121.9757 | 121.9986 | -0.26093 | 121.9391 | 121.9391 | 121.9986 | -0.23346
3154.2031 | 122.0856 | -121.8475 | 0.10529 | -0.0078584 | -0.019869 | 0.018269 | 0.033887 | -0.00687 | -0.038083 | -0.020755 | -0.0075532 | 0.0098758 | -0.013003 | -0.098247 | -0.011715 | -0.0016662 | 0.1236 | 0.086975 | 0.1236 | 0.10071 | 0.10071 | 0.045776 | -0.086975 | 0.068665 | 0.13733 | 0.064087 | 0.041199 | 0.027466 | -0.027466 | -0.091553 | 121.8933 | 121.7606 | -0.004578 | 121.9345 | 121.9482 | 0.18768 | 0.01831 | 121.8201 | 121.756 | -0.064087 | 121.9162 | 121.9116 | 0.15564 | -0.07782 | 121.9482 | 121.9711 | 121.9711 | -0.19226 | 121.8887 | 121.875 | 121.9849 | -0.19684
3155.9219 | 122.1588 | -121.843 | 0.09613 | -0.00022891 | -0.018374 | 0.015278 | 0.034101 | -0.011356 | -0.037442 | -0.017765 | 7.627e-05 | 0.013721 | -0.010653 | -0.097393 | -0.0095788 | -0.00017078 | 0.07782 | -0.018311 | 0.027466 | 0.036621 | 0.13733 | 0.032043 | -0.10986 | 0.045776 | 0.09613 | 0.004578 | 0.054932 | 0.032043 | -0.018311 | -0.091553 | 121.875 | 121.7331 | 0.041199 | 121.8246 | 121.8796 | 0.14648 | -0.01831 | 121.8246 | 121.7514 | -0.041198 | 121.8887 | 121.8475 | 0.096131 | -0.064087 | 121.9803 | 121.9208 | 121.8704 | -0.20599 | 121.8979 | 121.875 | 121.9391 | -0.18768
3157.7031 | 122.1405 | -121.8521 | 0.091553 | 0.0074006 | -0.016238 | 0.018483 | 0.039441 | -0.010074 | -0.034878 | -0.021183 | -0.0075532 | 0.012439 | -0.0087307 | -0.096325 | -0.014706 | -0.0014526 | 0.054932 | -0.054932 | 0.004578 | 0.022888 | 0.13275 | 0.009155 | -0.12817 | -0.064087 | 0.054932 | -0.068665 | 0.091553 | 0.07782 | -0.064087 | -0.14191 | 121.8613 | 121.7239 | 0.041198 | 121.7972 | 121.875 | 0.15106 | -0.036621 | 121.788 | 121.7102 | 0 | 121.788 | 121.7834 | 0.073242 | -0.013733 | 121.9849 | 121.907 | 121.8567 | -0.21973 | 121.9437 | 121.9299 | 121.907 | -0.23346
3159.4844 | 122.1542 | -121.8521 | 0.07782 | -0.0078584 | -0.015383 | 0.017842 | 0.039014 | -0.0083654 | -0.036801 | -0.020755 | 0.0077058 | 0.014362 | -0.0050991 | -0.095684 | -0.013638 | 4.2822e-05 | 0.082397 | -0.004578 | 0.022888 | 0.045776 | 0.15106 | 0.018311 | -0.12817 | -0.009155 | 0.07782 | -0.059509 | 0.068665 | 0.086975 | -0.041199 | -0.14191 | 121.8704 | 121.7239 | 0.073242 | 121.8475 | 121.8979 | 0.17395 | 0.004577 | 121.8109 | 121.7102 | -0.009155 | 121.843 | 121.7926 | 0.082398 | 0.009155 | 122.0032 | 121.9345 | 121.875 | -0.20599 | 121.9208 | 121.9391 | 121.9299 | -0.21973
3161.2031 | 122.1268 | -121.8613 | 0.09613 | -0.0078584 | -0.016665 | 0.015706 | 0.037518 | -0.008579 | -0.034451 | -0.019901 | 0.0077058 | 0.011585 | -0.0074491 | -0.097179 | -0.014919 | -0.001239 | 0.10986 | 0.018311 | 0.041199 | 0.050354 | 0.14191 | 0 | -0.11902 | 0.013733 | 0.073242 | -0.045776 | 0.068665 | 0.086975 | -0.059509 | -0.11444 | 121.8613 | 121.7422 | 0.045777 | 121.8796 | 121.9116 | 0.16937 | 0.013733 | 121.8018 | 121.7468 | -0.027465 | 121.875 | 121.8155 | 0.068665 | -0.009155 | 122.0032 | 121.9711 | 121.9025 | -0.21515 | 121.9299 | 121.9482 | 121.9345 | -0.21057
3162.9844 | 122.1222 | -121.8933 | 0.068665 | -0.0078584 | -0.01581 | 0.018483 | 0.037518 | -0.011356 | -0.035092 | -0.018619 | -0.0075532 | 0.011371 | -0.0083035 | -0.093975 | -0.012997 | -0.0016662 | 0.10529 | 0.004578 | 0.045776 | 0.050354 | 0.13275 | 0.036621 | -0.12817 | 0 | 0.082397 | -0.054932 | 0.073242 | 0.073242 | -0.054932 | -0.11902 | 121.9299 | 121.7651 | 0.064086 | 121.8979 | 121.9437 | 0.17853 | 0.036621 | 121.8384 | 121.7743 | 0.004577 | 121.8933 | 121.8384 | 0.064087 | 0.004577 | 122.0261 | 121.9986 | 121.9391 | -0.19684 | 121.9666 | 121.9666 | 121.9757 | -0.18768
3164.7812 | 122.1725 | -121.8704 | 0.091553 | -0.015487 | -0.019228 | 0.016987 | 0.034955 | -0.0081518 | -0.039578 | -0.018192 | 7.627e-05 | 0.0098758 | -0.0095853 | -0.09547 | -0.013638 | 0.0015382 | 0.086975 | 0.064087 | 0.091553 | 0.082397 | 0.12817 | 0.022888 | -0.10986 | 0.059509 | 0.1236 | 0.036621 | 0.045776 | 0.045776 | -0.022888 | -0.073242 | 121.8933 | 121.7606 | 0.036621 | 121.9345 | 121.9528 | 0.19226 | -0.004578 | 121.8475 | 121.7972 | -0.045777 | 121.9299 | 121.907 | 0.10986 | -0.045777 | 121.9986 | 121.9574 | 121.962 | -0.20142 | 121.9162 | 121.9162 | 121.994 | -0.16479
3166.5156 | 122.2 | -121.8979 | 0.10071 | -0.00022891 | -0.018374 | 0.017842 | 0.036237 | -0.0098608 | -0.039578 | -0.021396 | 7.627e-05 | 0.0096622 | -0.0076627 | -0.096966 | -0.016628 | 0.00047002 | 0.11444 | 0.041199 | 0.10986 | 0.086975 | 0.086975 | 0.050354 | -0.10529 | 0.059509 | 0.13275 | 0.041199 | 0.050354 | 0.036621 | -0.022888 | -0.091553 | 121.9482 | 121.7926 | -0.013733 | 121.9391 | 121.9849 | 0.19226 | 0.013733 | 121.875 | 121.8063 | -0.050354 | 121.9574 | 121.9391 | 0.13275 | -0.064087 | 121.9849 | 122.0123 | 122.0078 | -0.20599 | 121.9482 | 121.9345 | 122.0306 | -0.19226
3168.3125 | 122.1222 | -121.9254 | 0.11444 | 0.0074006 | -0.018374 | 0.019551 | 0.039014 | -0.00687 | -0.042782 | -0.022251 | -0.0075532 | 0.0064578 | -0.0076627 | -0.097393 | -0.01791 | 0.00025642 | 0.10071 | 0.082397 | 0.10986 | 0.086975 | 0.10071 | 0.027466 | -0.091553 | 0.07782 | 0.1831 | 0.082397 | 0.054932 | 0.045776 | -0.041199 | -0.091553 | 121.9528 | 121.8338 | -0.013733 | 122.0078 | 122.0123 | 0.17853 | -0.013733 | 121.8842 | 121.8338 | -0.059509 | 122.0032 | 122.0078 | 0.17395 | -0.068665 | 122.0261 | 122.0261 | 122.0352 | -0.20599 | 121.9803 | 121.9711 | 122.1085 | -0.20599
3170.0312 | 122.1268 | -121.9345 | 0.10071 | -0.0078584 | -0.021364 | 0.020832 | 0.036237 | -0.00922 | -0.04385 | -0.021824 | 7.627e-05 | 0.0081668 | -0.010653 | -0.098461 | -0.016842 | -0.00059818 | 0.10986 | 0.068665 | 0.1236 | 0.082397 | 0.10071 | 0.027466 | -0.10529 | 0.068665 | 0.16479 | 0.082397 | 0.059509 | 0.050354 | -0.022888 | -0.10071 | 121.962 | 121.8292 | 0 | 122.0032 | 122.0169 | 0.18768 | 0.009155 | 121.9116 | 121.8338 | -0.041199 | 122.0032 | 122.0169 | 0.18311 | -0.050354 | 122.0352 | 122.0444 | 122.0581 | -0.20599 | 121.994 | 121.9849 | 122.0993 | -0.20142
3171.8281 | 122.1359 | -121.9116 | 0.1236 | -0.0078584 | -0.019442 | 0.016987 | 0.037946 | -0.0087926 | -0.036587 | -0.020969 | -0.0075532 | 0.01308 | -0.0089443 | -0.099102 | -0.013638 | -0.0016662 | 0.032043 | -0.045776 | -0.018311 | 0.004578 | 0.16022 | 0 | -0.13733 | -0.064087 | 0.022888 | -0.091553 | 0.09613 | 0.07782 | -0.068665 | -0.13733 | 121.9116 | 121.7743 | 0.036621 | 121.8658 | 121.9162 | 0.14191 | -0.091553 | 121.843 | 121.7743 | -0.027466 | 121.8475 | 121.8201 | 0.045776 | -0.045776 | 122.0718 | 121.9437 | 121.8933 | -0.26093 | 122.0078 | 121.9894 | 121.9345 | -0.26093
3173.5625 | 122.1497 | -121.9528 | 0.10986 | -0.0078584 | -0.020937 | 0.017415 | 0.035596 | -0.0096472 | -0.043423 | -0.022251 | 7.627e-05 | 0.0077396 | -0.011294 | -0.097607 | -0.016628 | -0.001239 | 0.13275 | 0.09613 | 0.13733 | 0.091553 | 0.11902 | 0.050354 | -0.09613 | 0.086975 | 0.16937 | 0.082397 | 0.050354 | 0.064087 | -0.027466 | -0.091553 | 122.0032 | 121.8567 | 0.009156 | 122.049 | 122.0444 | 0.18768 | 0.022888 | 121.9254 | 121.8613 | -0.059509 | 122.0398 | 122.0352 | 0.17395 | -0.045776 | 122.0718 | 122.0856 | 122.0901 | -0.20599 | 122.0032 | 122.0169 | 122.1222 | -0.20142
3175.3594 | 122.1359 | -121.9849 | 0.13275 | -0.00022891 | -0.021151 | 0.020192 | 0.032392 | -0.0096472 | -0.037014 | -0.02161 | 0.0077058 | 0.011371 | -0.01108 | -0.09782 | -0.010861 | -0.00081178 | 0.15106 | 0.07782 | 0.12817 | 0.073242 | 0.10071 | 0.041199 | -0.086975 | 0.068665 | 0.11902 | 0.041199 | 0.050354 | 0.045776 | -0.045776 | -0.10986 | 122.0261 | 121.8979 | -0.032043 | 122.0627 | 122.0581 | 0.16022 | 0.018311 | 121.9391 | 121.875 | -0.082397 | 122.0535 | 122.0261 | 0.15106 | -0.086975 | 122.0856 | 122.1359 | 122.113 | -0.21973 | 122.0352 | 122.0306 | 122.1039 | -0.24261
3177.1406 | 122.2458 | -121.9666 | 0.086975 | -0.00022891 | -0.017306 | 0.018269 | 0.033032 | -0.0072974 | -0.035519 | -0.020115 | 7.627e-05 | 0.011798 | -0.0080899 | -0.097179 | -0.012356 | -0.0020934 | 0.07782 | -0.032043 | 0.013733 | 0.018311 | 0.12817 | 0.022888 | -0.11444 | 0.018311 | 0.054932 | -0.018311 | 0.068665 | 0.036621 | -0.041199 | -0.10529 | 121.9894 | 121.8521 | 0.041199 | 121.9345 | 121.9849 | 0.13275 | -0.009155 | 121.9254 | 121.8613 | -0.01831 | 121.9849 | 121.9482 | 0.086975 | -0.050354 | 122.0947 | 122.0444 | 121.9803 | -0.20142 | 122.0352 | 122.0032 | 122.0215 | -0.19226
3178.9375 | 122.2137 | -121.9666 | 0.09613 | -0.00022891 | -0.017306 | 0.01421 | 0.035596 | -0.0083654 | -0.033383 | -0.018192 | 0.0077058 | 0.012012 | -0.0083035 | -0.093761 | -0.011288 | 0.00025642 | 0.045776 | -0.086975 | -0.032043 | 0.004578 | 0.12817 | 0.013733 | -0.14648 | -0.054932 | -0.022888 | -0.10529 | 0.09613 | 0.082397 | -0.054932 | -0.12817 | 121.9803 | 121.8201 | 0.032044 | 121.8796 | 121.9711 | 0.15106 | -0.050354 | 121.9116 | 121.8384 | 0 | 121.9116 | 121.8613 | 0.022888 | -0.013733 | 122.0947 | 122.0123 | 121.9345 | -0.24261 | 122.0627 | 122.049 | 121.9437 | -0.2243
3180.6719 | 122.0993 | -121.9986 | 0.12817 | -0.00022891 | -0.021792 | 0.015706 | 0.039441 | -0.0096472 | -0.041501 | -0.021396 | 7.627e-05 | 0.0064578 | -0.0085171 | -0.099743 | -0.014492 | -0.0010254 | 0.091553 | 0.068665 | 0.091553 | 0.07782 | 0.11444 | 0.013733 | -0.11902 | -0.009155 | 0.11444 | -0.027466 | 0.050354 | 0.064087 | -0.073242 | -0.11444 | 122.0123 | 121.8796 | -0.013733 | 122.0673 | 122.0764 | 0.19684 | -0.036621 | 121.9254 | 121.8842 | -0.07782 | 121.9894 | 121.9711 | 0.086975 | -0.064087 | 122.113 | 122.0901 | 122.0901 | -0.24719 | 122.049 | 122.0627 | 122.113 | -0.24262
3182.4531 | 122.2183 | -121.9894 | 0.11444 | -0.00022891 | -0.015597 | 0.015919 | 0.035596 | -0.0094336 | -0.032956 | -0.01691 | -0.0075532 | 0.012653 | -0.0063809 | -0.096752 | -0.010861 | -0.00038438 | 0.041199 | -0.041199 | 0 | 0.009155 | 0.14191 | 0.009155 | -0.10529 | -0.064087 | 0.009155 | -0.10529 | 0.073242 | 0.07782 | -0.045776 | -0.14191 | 121.9986 | 121.8842 | 0.027466 | 121.9482 | 121.9986 | 0.11444 | -0.073242 | 121.9437 | 121.8475 | -0.041199 | 121.9254 | 121.8842 | 0.036621 | -0.036621 | 122.1313 | 122.0306 | 121.9894 | -0.21973 | 122.0627 | 122.0673 | 121.9986 | -0.25635
3184.25 | 122.2183 | -121.9894 | 0.09613 | -0.023117 | -0.016024 | 0.015706 | 0.033887 | -0.0090062 | -0.035092 | -0.017765 | -0.0075532 | 0.011798 | -0.0095853 | -0.09547 | -0.011074 | -0.00081178 | 0.036621 | -0.045776 | -0.013733 | 0.004578 | 0.13733 | -0.004578 | -0.13275 | -0.064087 | 0.018311 | -0.11444 | 0.09613 | 0.082397 | -0.050354 | -0.15564 | 121.9849 | 121.8567 | 0.041199 | 121.9437 | 121.994 | 0.13733 | -0.059509 | 121.9391 | 121.8338 | 0 | 121.9254 | 121.875 | 0.041199 | -0.013733 | 122.1268 | 122.0261 | 121.9757 | -0.22888 | 122.0856 | 122.0718 | 122.0078 | -0.25177
3186 | 122.2641 | -121.9849 | 0.082397 | -0.0078584 | -0.018374 | 0.019123 | 0.034741 | -0.0090062 | -0.037442 | -0.01926 | -0.0075532 | 0.012867 | -0.01108 | -0.098247 | -0.013851 | 0.00047002 | 0.059509 | -0.013733 | 0.013733 | 0.045776 | 0.12817 | 0.004578 | -0.14191 | -0.032043 | 0.091553 | -0.036621 | 0.068665 | 0.086975 | -0.054932 | -0.12817 | 121.9894 | 121.843 | 0.045777 | 121.9711 | 122.0306 | 0.18768 | -0.022888 | 121.9299 | 121.8567 | -0.013732 | 121.9528 | 121.9482 | 0.091553 | 0.004578 | 122.113 | 122.0444 | 121.9986 | -0.2243 | 122.0535 | 122.0718 | 122.0764 | -0.21057
3187.7812 | 122.1954 | -122.0215 | 0.11902 | -0.0078584 | -0.024355 | 0.018696 | 0.038373 | -0.010074 | -0.044918 | -0.020969 | -0.0075532 | 0.0062442 | -0.010653 | -0.098247 | -0.016201 | 0.0026062 | 0.032043 | 0.027466 | 0.086975 | 0.050354 | 0.10986 | 0.022888 | -0.11902 | -0.009155 | 0.10071 | 0.022888 | 0.068665 | 0.041199 | -0.036621 | -0.10986 | 122.0444 | 121.9025 | -0.009156 | 122.049 | 122.0718 | 0.16937 | -0.086976 | 121.9849 | 121.9116 | -0.050354 | 122.0123 | 122.0444 | 0.13275 | -0.07782 | 122.1313 | 122.0535 | 122.1085 | -0.23804 | 122.0901 | 122.0627 | 122.1222 | -0.22888
3189.5781 | 122.2824 | -121.9849 | 0.10529 | -0.00022891 | -0.014742 | 0.01656 | 0.039868 | -0.00687 | -0.037014 | -0.021183 | -0.015182 | 0.01308 | -0.0085171 | -0.096752 | -0.017483 | -0.001239 | 0.041199 | -0.059509 | 0 | 0.022888 | 0.14191 | 0.004578 | -0.14648 | -0.059509 | 0.027466 | -0.073242 | 0.082397 | 0.10529 | -0.064087 | -0.1236 | 121.9894 | 121.8384 | 0.036621 | 121.9254 | 122.0078 | 0.16937 | -0.064087 | 121.9208 | 121.8613 | -0.022889 | 121.9254 | 121.9116 | 0.050354 | 0 | 122.1268 | 122.0261 | 121.9849 | -0.25177 | 122.0673 | 122.0901 | 122.0123 | -0.22888
3191.2969 | 122.2321 | -122.0078 | 0.10986 | -0.0078584 | -0.011538 | 0.015492 | 0.037305 | -0.011997 | -0.035092 | -0.020755 | -0.0075532 | 0.014148 | -0.0065945 | -0.096111 | -0.012356 | -0.0010254 | 0.036621 | -0.068665 | -0.013733 | 0.009155 | 0.13733 | 0.022888 | -0.13275 | -0.073242 | 0.004578 | -0.11444 | 0.091553 | 0.091553 | -0.068665 | -0.12817 | 122.0306 | 121.875 | 0.027466 | 121.9391 | 122.0169 | 0.14191 | -0.073242 | 121.9391 | 121.8796 | -0.01831 | 121.9345 | 121.8933 | 0.013733 | -0.01831 | 122.1451 | 122.0444 | 121.994 | -0.24261 | 122.0993 | 122.0993 | 122.0123 | -0.23804
3193.0625 | 122.2733 | -122.0261 | 0.091553 | -0.00022891 | -0.021151 | 0.017415 | 0.034314 | -0.008579 | -0.039578 | -0.017978 | 0.0077058 | 0.0096622 | -0.01044 | -0.097179 | -0.012997 | -0.0018798 | 0.11902 | 0.086975 | 0.12817 | 0.09613 | 0.09613 | 0.041199 | -0.082397 | 0.068665 | 0.14191 | 0.059509 | 0.036621 | 0.027466 | -0.022888 | -0.086975 | 122.0673 | 121.9437 | 0.004577 | 122.113 | 122.1222 | 0.17853 | 0.027466 | 122.0032 | 121.9391 | -0.054932 | 122.0947 | 122.0856 | 0.14648 | -0.064087 | 122.1222 | 122.1451 | 122.1542 | -0.17395 | 122.0627 | 122.0535 | 122.168 | -0.17853
3194.8594 | 122.1863 | -122.0398 | 0.14648 | -0.00022891 | -0.020083 | 0.019551 | 0.0388 | -0.00922 | -0.04086 | -0.021824 | -0.0075532 | 0.0081668 | -0.0091579 | -0.099316 | -0.017483 | -0.0014526 | 0.10529 | 0.10071 | 0.14191 | 0.086975 | 0.09613 | 0.050354 | -0.10071 | 0.027466 | 0.16937 | 0.050354 | 0.045776 | 0.045776 | -0.032043 | -0.09613 | 122.0901 | 121.9391 | -0.050354 | 122.1405 | 122.1268 | 0.18768 | -0.041198 | 122.0078 | 121.9437 | -0.10071 | 122.0673 | 122.0901 | 0.14648 | -0.10071 | 122.1359 | 122.1451 | 122.1817 | -0.24719 | 122.0856 | 122.0856 | 122.2092 | -0.24261
3196.5781 | 122.1725 | -122.0673 | 0.12817 | -0.0078584 | -0.018587 | 0.017628 | 0.040509 | -0.00922 | -0.040219 | -0.020755 | -0.0075532 | 0.0088076 | -0.0080899 | -0.097607 | -0.014919 | -0.0018798 | 0.086975 | 0.07782 | 0.10529 | 0.086975 | 0.11444 | 0.027466 | -0.10986 | -0.013733 | 0.11902 | -0.004578 | 0.073242 | 0.073242 | -0.054932 | -0.12817 | 122.0947 | 121.9574 | -0.013733 | 122.1451 | 122.1542 | 0.19684 | -0.041199 | 122.0123 | 121.9391 | -0.054932 | 122.0535 | 122.0627 | 0.1236 | -0.054932 | 122.1817 | 122.1542 | 122.1725 | -0.23804 | 122.1405 | 122.1405 | 122.1863 | -0.25635
3198.3594 | 122.2183 | -122.0444 | 0.11444 | -0.00022891 | -0.019015 | 0.020619 | 0.037732 | -0.0094336 | -0.036801 | -0.021824 | -0.015182 | 0.010517 | -0.010653 | -0.099102 | -0.015774 | -0.00059818 | 0.013733 | -0.018311 | 0 | 0.009155 | 0.14648 | -0.009155 | -0.15564 | -0.059509 | 0.041199 | -0.064087 | 0.091553 | 0.09613 | -0.09613 | -0.14191 | 122.0352 | 121.8887 | 0.032043 | 122.0261 | 122.0535 | 0.16479 | -0.10071 | 121.9482 | 121.9025 | -0.022888 | 121.9849 | 121.9803 | 0.07782 | -0.018311 | 122.1909 | 122.0581 | 122.0444 | -0.27008 | 122.1359 | 122.1405 | 122.0856 | -0.25635
3200.1406 | 122.3099 | -122.0169 | 0.10071 | 0.0074006 | -0.018587 | 0.016774 | 0.033887 | -0.012211 | -0.034665 | -0.019687 | 7.627e-05 | 0.012226 | -0.0083035 | -0.099529 | -0.011715 | 0.0017518 | 0.036621 | -0.07782 | -0.032043 | 0.009155 | 0.14191 | -0.004578 | -0.14191 | -0.036621 | 0 | -0.091553 | 0.10071 | 0.082397 | -0.086975 | -0.14191 | 122.0123 | 121.875 | 0.041199 | 121.9391 | 122.0261 | 0.15106 | -0.064087 | 121.9299 | 121.875 | 0 | 121.9803 | 121.9254 | 0.050354 | -0.018311 | 122.1588 | 122.0535 | 121.9849 | -0.24262 | 122.1176 | 122.0993 | 122.0169 | -0.24262
3201.8906 | 122.3328 | -122.0398 | 0.086975 | -0.00022891 | -0.017519 | 0.017201 | 0.037091 | -0.0079382 | -0.03616 | -0.021396 | -0.015182 | 0.012653 | -0.01044 | -0.094402 | -0.015133 | -0.002948 | 0.032043 | -0.027466 | 0 | 0.032043 | 0.14191 | -0.009155 | -0.16479 | -0.036621 | 0.07782 | -0.045776 | 0.09613 | 0.07782 | -0.054932 | -0.11444 | 122.0306 | 121.875 | 0.054932 | 122.0123 | 122.0718 | 0.19684 | -0.054932 | 121.9849 | 121.9254 | 0.009155 | 122.0032 | 121.994 | 0.068665 | -0.009155 | 122.1817 | 122.0718 | 122.0398 | -0.25177 | 122.1359 | 122.1176 | 122.1176 | -0.20142
3203.6719 | 122.2275 | -122.1085 | 0.13275 | 0.0074006 | -0.024142 | 0.017842 | 0.035596 | -0.0079382 | -0.041501 | -0.019687 | 7.627e-05 | 0.010517 | -0.0089443 | -0.097179 | -0.01556 | 0.002179 | 0.10529 | 0.091553 | 0.1236 | 0.07782 | 0.091553 | 0.041199 | -0.086975 | 0.068665 | 0.13275 | 0.045776 | 0.050354 | 0.045776 | -0.032043 | -0.10071 | 122.1497 | 122.0215 | -0.041198 | 122.2 | 122.1863 | 0.16479 | -0.027465 | 122.0764 | 122.0078 | -0.082397 | 122.1771 | 122.1542 | 0.14648 | -0.086975 | 122.2 | 122.2137 | 122.2321 | -0.21973 | 122.1588 | 122.1542 | 122.2412 | -0.23346
3205.4062 | 122.2961 | -122.0718 | 0.10529 | -0.0078584 | -0.01581 | 0.015919 | 0.034314 | -0.008579 | -0.034237 | -0.019901 | 0.0077058 | 0.014789 | -0.0083035 | -0.097179 | -0.011074 | 0.00047002 | 0.022888 | -0.068665 | -0.009155 | 0.009155 | 0.16479 | 0.009155 | -0.15106 | -0.068665 | -0.009155 | -0.10529 | 0.10071 | 0.073242 | -0.068665 | -0.13275 | 122.081 | 121.9208 | 0.059509 | 122.0032 | 122.081 | 0.16022 | -0.082398 | 122.0032 | 121.9391 | -0.004578 | 122.0032 | 121.9666 | 0.027465 | -0.032044 | 122.2366 | 122.0947 | 122.0627 | -0.25635 | 122.1725 | 122.1451 | 122.0627 | -0.23804
3207.1875 | 122.2549 | -122.0856 | 0.14191 | -0.00022891 | -0.019869 | 0.019764 | 0.039441 | -0.0098608 | -0.041501 | -0.021396 | 7.627e-05 | 0.0079532 | -0.0091579 | -0.097393 | -0.017483 | 0.00047002 | 0.11902 | 0.11444 | 0.13275 | 0.091553 | 0.10071 | 0.032043 | -0.10529 | 0.059509 | 0.20142 | 0.068665 | 0.050354 | 0.027466 | -0.032043 | -0.091553 | 122.1176 | 121.9803 | -0.041199 | 122.2 | 122.1771 | 0.19684 | -0.022888 | 122.0535 | 121.994 | -0.091553 | 122.1451 | 122.1542 | 0.16022 | -0.11444 | 122.1863 | 122.2046 | 122.2183 | -0.24719 | 122.1359 | 122.113 | 122.287 | -0.23346
3208.9844 | 122.2366 | -122.0993 | 0.11902 | -0.00022891 | -0.022219 | 0.017842 | 0.035596 | -0.0083654 | -0.040219 | -0.019687 | 7.627e-05 | 0.011371 | -0.01044 | -0.098034 | -0.015133 | -0.00081178 | 0.13275 | 0.091553 | 0.11902 | 0.082397 | 0.086975 | 0.059509 | -0.09613 | 0.064087 | 0.13275 | 0.032043 | 0.032043 | 0.036621 | -0.022888 | -0.091553 | 122.1588 | 122.0032 | -0.032044 | 122.1909 | 122.1817 | 0.17853 | 0.013732 | 122.0764 | 122.0078 | -0.086976 | 122.1634 | 122.1313 | 0.1236 | -0.082398 | 122.1863 | 122.2321 | 122.2183 | -0.21515 | 122.1313 | 122.1359 | 122.2321 | -0.21057
3210.7656 | 122.374 | -122.0856 | 0.10071 | 0.0074006 | -0.017733 | 0.017415 | 0.034528 | -0.0096472 | -0.035946 | -0.017765 | 7.627e-05 | 0.012439 | -0.010653 | -0.099316 | -0.011929 | -0.0025208 | 0.10071 | 0.036621 | 0.082397 | 0.064087 | 0.11902 | 0.027466 | -0.10986 | 0.045776 | 0.10529 | 0.022888 | 0.059509 | 0.036621 | -0.018311 | -0.09613 | 122.113 | 121.9757 | 0.018311 | 122.1222 | 122.1497 | 0.17395 | 0 | 122.0673 | 121.9894 | -0.041199 | 122.1313 | 122.1085 | 0.11902 | -0.064087 | 122.2046 | 122.1863 | 122.168 | -0.21057 | 122.1451 | 122.1222 | 122.1909 | -0.19684
3212.5469 | 122.3557 | -122.081 | 0.086975 | -0.015487 | -0.014742 | 0.016133 | 0.038373 | -0.010715 | -0.033169 | -0.01926 | -0.0075532 | 0.013721 | -0.0076627 | -0.09547 | -0.014706 | -0.0014526 | 0.10986 | 0.013733 | 0.027466 | 0.054932 | 0.14191 | 0.009155 | -0.1236 | 0.018311 | 0.10071 | -0.036621 | 0.07782 | 0.050354 | -0.059509 | -0.12817 | 122.0901 | 121.9574 | 0.054932 | 122.0947 | 122.1359 | 0.17853 | 0.022888 | 122.0215 | 121.9528 | -0.009155 | 122.0993 | 122.0444 | 0.091553 | -0.036621 | 122.2229 | 122.1909 | 122.1085 | -0.21057 | 122.1588 | 122.1313 | 122.1817 | -0.21515
3214.2656 | 122.2916 | -122.1039 | 0.10986 | 0.0074006 | -0.026919 | 0.023396 | 0.035809 | -0.008579 | -0.043637 | -0.021396 | 7.627e-05 | 0.009235 | -0.011935 | -0.098247 | -0.01791 | 0.002179 | 0.10529 | 0.068665 | 0.10529 | 0.073242 | 0.11444 | 0.032043 | -0.11444 | 0.050354 | 0.17395 | 0.068665 | 0.050354 | 0.050354 | -0.027466 | -0.10071 | 122.1359 | 121.9894 | 0.004578 | 122.1725 | 122.1771 | 0.18768 | -0.004577 | 122.0764 | 122.0032 | -0.059509 | 122.1542 | 122.1725 | 0.16937 | -0.059509 | 122.2183 | 122.2092 | 122.2092 | -0.2243 | 122.1542 | 122.1542 | 122.2778 | -0.21057
3216.0469 | 122.3877 | -122.0993 | 0.091553 | -0.0078584 | -0.020083 | 0.017415 | 0.034741 | -0.0096472 | -0.037869 | -0.021824 | -0.0075532 | 0.011371 | -0.0087307 | -0.097179 | -0.012997 | -0.0016662 | 0.14191 | 0.064087 | 0.10986 | 0.10071 | 0.10529 | 0.045776 | -0.10071 | 0.064087 | 0.13733 | 0.036621 | 0.032043 | 0.022888 | -0.018311 | -0.091553 | 122.1451 | 121.9986 | 0.013733 | 122.1634 | 122.2 | 0.20142 | 0.050354 | 122.081 | 122.0078 | -0.05951 | 122.1634 | 122.1359 | 0.12817 | -0.068665 | 122.2046 | 122.2412 | 122.2092 | -0.19226 | 122.1313 | 122.1222 | 122.2366 | -0.18311
3217.8281 | 122.3557 | -122.0856 | 0.082397 | -0.00022891 | -0.016878 | 0.017201 | 0.036878 | -0.0087926 | -0.033169 | -0.020115 | -0.015182 | 0.012867 | -0.0074491 | -0.096966 | -0.011929 | -0.00059818 | 0.10986 | 0.013733 | 0.041199 | 0.054932 | 0.13733 | 0 | -0.12817 | 0.022888 | 0.073242 | -0.054932 | 0.082397 | 0.073242 | -0.054932 | -0.1236 | 122.0856 | 121.9574 | 0.054932 | 122.0993 | 122.1405 | 0.18311 | 0.027466 | 122.0306 | 121.962 | 0 | 122.1085 | 122.0306 | 0.068664 | -0.009155 | 122.2229 | 122.1954 | 122.1268 | -0.21057 | 122.168 | 122.1588 | 122.1588 | -0.20599
3219.5469 | 122.2961 | -122.1085 | 0.11902 | -0.0078584 | -0.019442 | 0.017415 | 0.040296 | -0.0098608 | -0.03851 | -0.022037 | -0.0075532 | 0.011585 | -0.0089443 | -0.095684 | -0.016628 | -0.00059818 | 0.041199 | -0.054932 | 0 | -0.009155 | 0.1236 | 0.004578 | -0.15106 | -0.068665 | 0.041199 | -0.07782 | 0.09613 | 0.086975 | -0.082397 | -0.14648 | 122.113 | 121.9574 | 0.004577 | 122.0535 | 122.0993 | 0.14191 | -0.07782 | 122.0261 | 121.962 | -0.022889 | 122.0398 | 122.0306 | 0.068664 | -0.032044 | 122.2321 | 122.1497 | 122.1085 | -0.27008 | 122.2046 | 122.1954 | 122.1497 | -0.2655
3221.3281 | 122.2504 | -122.1268 | 0.12817 | -0.0078584 | -0.018801 | 0.019337 | 0.038587 | -0.0083654 | -0.041501 | -0.018192 | 0.0077058 | 0.010089 | -0.0080899 | -0.1006 | -0.015988 | 0.0015382 | 0.11444 | 0.09613 | 0.11902 | 0.091553 | 0.10529 | 0.045776 | -0.10986 | 0.027466 | 0.17853 | 0.036621 | 0.054932 | 0.045776 | -0.059509 | -0.10986 | 122.1725 | 122.0169 | -0.022888 | 122.2229 | 122.2183 | 0.20142 | -0.013733 | 122.0673 | 122.0169 | -0.073242 | 122.1542 | 122.1634 | 0.14648 | -0.082398 | 122.2321 | 122.2412 | 122.2458 | -0.23804 | 122.1817 | 122.1725 | 122.3053 | -0.23804
3223.1094 | 122.2916 | -122.1359 | 0.13733 | 0.0074006 | -0.022646 | 0.018055 | 0.036023 | -0.007511 | -0.041928 | -0.022037 | 0.015335 | 0.0094486 | -0.010226 | -0.098888 | -0.01791 | 0.0011108 | 0.07782 | 0.018311 | 0.068665 | 0.064087 | 0.10986 | 0.036621 | -0.10986 | 0.013733 | 0.086975 | 0.004578 | 0.064087 | 0.059509 | -0.041199 | -0.10071 | 122.1725 | 122.0261 | -0.027466 | 122.1542 | 122.2 | 0.17395 | -0.059509 | 122.0947 | 122.0352 | -0.073242 | 122.1497 | 122.1405 | 0.10529 | -0.07782 | 122.2458 | 122.2137 | 122.2046 | -0.24719 | 122.2 | 122.1954 | 122.2229 | -0.23804
3224.8281 | 122.3328 | -122.1405 | 0.12817 | -0.00022891 | -0.022219 | 0.018483 | 0.037305 | -0.010929 | -0.040219 | -0.024173 | 7.627e-05 | 0.0096622 | -0.01108 | -0.098675 | -0.016842 | 0.00089722 | 0.13275 | 0.09613 | 0.11902 | 0.082397 | 0.11902 | 0.036621 | -0.10071 | 0.064087 | 0.16937 | 0.07782 | 0.045776 | 0.036621 | -0.032043 | -0.10071 | 122.1771 | 122.0398 | -0.009155 | 122.2366 | 122.2229 | 0.18311 | 0.004577 | 122.1085 | 122.0398 | -0.082398 | 122.2046 | 122.2183 | 0.17853 | -0.091553 | 122.2595 | 122.2733 | 122.2595 | -0.22888 | 122.1863 | 122.1771 | 122.3099 | -0.22888
3226.6094 | 122.4243 | -122.0947 | 0.082397 | -0.00022891 | -0.020724 | 0.01891 | 0.035169 | -0.0079382 | -0.03381 | -0.019687 | -0.0075532 | 0.013294 | -0.0076627 | -0.095684 | -0.011929 | -0.0018798 | 0.050354 | -0.068665 | -0.013733 | -0.004578 | 0.15106 | 0.013733 | -0.12817 | -0.009155 | 0.022888 | -0.068665 | 0.091553 | 0.068665 | -0.068665 | -0.13733 | 122.1085 | 121.9666 | 0.068665 | 122.0261 | 122.0901 | 0.1236 | -0.032043 | 122.0261 | 121.9574 | 0.009156 | 122.0856 | 122.0261 | 0.068664 | -0.013732 | 122.2458 | 122.1451 | 122.081 | -0.21057 | 122.1863 | 122.1634 | 122.1176 | -0.21973
3228.4062 | 122.3969 | -122.0947 | 0.068665 | -0.023117 | -0.018374 | 0.016133 | 0.036237 | -0.005802 | -0.035092 | -0.019687 | 0.0077058 | 0.012226 | -0.0089443 | -0.097393 | -0.011715 | -0.002948 | 0.10071 | 0.032043 | 0.041199 | 0.064087 | 0.13733 | 0.013733 | -0.13733 | 0.013733 | 0.09613 | -0.036621 | 0.086975 | 0.068665 | -0.068665 | -0.12817 | 122.1085 | 121.9574 | 0.068664 | 122.1268 | 122.1588 | 0.20142 | 0.032043 | 122.0261 | 121.9666 | 0.01831 | 122.1085 | 122.0581 | 0.091553 | 0 | 122.2321 | 122.1954 | 122.1359 | -0.20599 | 122.1817 | 122.1634 | 122.1909 | -0.19684
3230.1875 | 122.2916 | -122.1954 | 0.14191 | 0.0074006 | -0.023287 | 0.018483 | 0.035809 | -0.010715 | -0.043423 | -0.023319 | 7.627e-05 | 0.007526 | -0.0087307 | -0.10124 | -0.016628 | 0.00025642 | 0.059509 | 0.050354 | 0.082397 | 0.054932 | 0.10986 | 0.036621 | -0.10986 | 0.022888 | 0.10071 | 0.009155 | 0.054932 | 0.054932 | -0.013733 | -0.10071 | 122.2321 | 122.0856 | -0.032044 | 122.2458 | 122.2504 | 0.16479 | -0.082398 | 122.1817 | 122.0947 | -0.086975 | 122.2183 | 122.2046 | 0.10986 | -0.086975 | 122.3053 | 122.2549 | 122.2778 | -0.25177 | 122.2504 | 122.2504 | 122.2961 | -0.24262
3231.9219 | 122.3145 | -122.1863 | 0.12817 | -0.00022891 | -0.024782 | 0.018055 | 0.037518 | -0.008579 | -0.041501 | -0.020542 | 7.627e-05 | 0.0088076 | -0.011294 | -0.098461 | -0.014279 | -0.001239 | 0.073242 | 0.041199 | 0.086975 | 0.041199 | 0.10071 | 0.036621 | -0.082397 | 0.022888 | 0.09613 | 0.013733 | 0.086975 | 0.050354 | -0.036621 | -0.10071 | 122.2229 | 122.1039 | -0.027466 | 122.2275 | 122.2275 | 0.1236 | -0.054932 | 122.1497 | 122.0856 | -0.041199 | 122.2092 | 122.2 | 0.11444 | -0.07782 | 122.287 | 122.2595 | 122.2733 | -0.21057 | 122.2733 | 122.2366 | 122.2824 | -0.22888
3233.7031 | 122.4243 | -122.1588 | 0.10071 | -0.00022891 | -0.018374 | 0.016774 | 0.035169 | -0.0094336 | -0.032315 | -0.019474 | -0.015182 | 0.016284 | -0.0085171 | -0.094829 | -0.011501 | -0.0023072 | 0.032043 | -0.073242 | -0.009155 | 0.013733 | 0.14191 | 0 | -0.14648 | -0.036621 | -0.009155 | -0.10529 | 0.10071 | 0.068665 | -0.068665 | -0.14191 | 122.1588 | 122.0123 | 0.041199 | 122.0856 | 122.1725 | 0.16022 | -0.068665 | 122.0901 | 122.0169 | 0 | 122.1222 | 122.0535 | 0.036621 | -0.032043 | 122.3007 | 122.1909 | 122.1497 | -0.24719 | 122.2595 | 122.2275 | 122.1497 | -0.24262
3235.5 | 122.4472 | -122.1268 | 0.10529 | -0.00022891 | -0.019228 | 0.018269 | 0.032605 | -0.01157 | -0.036374 | -0.018192 | -0.0075532 | 0.011798 | -0.0089443 | -0.098675 | -0.011288 | -0.00038438 | 0.12817 | 0.082397 | 0.10529 | 0.082397 | 0.1236 | 0.036621 | -0.10529 | 0.086975 | 0.12817 | 0.022888 | 0.041199 | 0.018311 | -0.045776 | -0.10071 | 122.1634 | 122.0215 | 0.01831 | 122.2092 | 122.2092 | 0.18768 | 0.022888 | 122.081 | 122.0261 | -0.064087 | 122.2137 | 122.1497 | 0.1236 | -0.086975 | 122.2504 | 122.2549 | 122.2321 | -0.21057 | 122.168 | 122.1451 | 122.2549 | -0.20599
3237.2969 | 122.4701 | -122.1451 | 0.086975 | 0.0074006 | -0.018374 | 0.016774 | 0.037305 | -0.012211 | -0.035305 | -0.017765 | 7.627e-05 | 0.014148 | -0.0068081 | -0.098461 | -0.013424 | 0.00068362 | 0.036621 | -0.059509 | -0.013733 | 0.018311 | 0.17395 | -0.004578 | -0.13275 | -0.036621 | 0.018311 | -0.068665 | 0.09613 | 0.073242 | -0.064087 | -0.12817 | 122.1405 | 122.0123 | 0.086975 | 122.0856 | 122.1634 | 0.15106 | -0.050354 | 122.081 | 122.0169 | 0.009155 | 122.1085 | 122.0764 | 0.059509 | -0.013733 | 122.319 | 122.1817 | 122.1313 | -0.21973 | 122.2412 | 122.2183 | 122.1634 | -0.21515
3239.0938 | 122.4472 | -122.1359 | 0.091553 | -0.015487 | -0.016878 | 0.016774 | 0.036878 | -0.00687 | -0.035519 | -0.019046 | 0.0077058 | 0.014362 | -0.0097989 | -0.094829 | -0.010006 | -0.00059818 | 0.018311 | -0.07782 | -0.018311 | 0.009155 | 0.14648 | 0.009155 | -0.1236 | -0.064087 | -0.009155 | -0.086975 | 0.082397 | 0.086975 | -0.073242 | -0.13275 | 122.1451 | 122.0123 | 0.054931 | 122.0581 | 122.1451 | 0.13275 | -0.073242 | 122.0627 | 122.0032 | -0.009156 | 122.0718 | 122.049 | 0.045776 | -0.004578 | 122.2824 | 122.1542 | 122.1176 | -0.21515 | 122.2183 | 122.2229 | 122.1268 | -0.2243
3240.8906 | 122.3557 | -122.1725 | 0.12817 | -0.0078584 | -0.022219 | 0.019551 | 0.040509 | -0.010929 | -0.042996 | -0.020542 | -0.0075532 | 0.0081668 | -0.0087307 | -0.098461 | -0.019192 | -0.00017078 | 0.036621 | 0.032043 | 0.086975 | 0.054932 | 0.11902 | 0.036621 | -0.10071 | 0.018311 | 0.1236 | 0.032043 | 0.064087 | 0.054932 | -0.041199 | -0.11444 | 122.2092 | 122.0718 | -0.009155 | 122.2046 | 122.2275 | 0.15564 | -0.091553 | 122.1313 | 122.0581 | -0.064087 | 122.1909 | 122.2046 | 0.14648 | -0.073242 | 122.2916 | 122.2092 | 122.2595 | -0.22888 | 122.2366 | 122.2275 | 122.2961 | -0.24262
3242.6719 | 122.406 | -122.1588 | 0.091553 | 0.0074006 | -0.016665 | 0.014851 | 0.037732 | -0.010288 | -0.032101 | -0.018619 | 7.627e-05 | 0.013935 | -0.0078763 | -0.09312 | -0.012997 | -0.0042298 | 0.09613 | -0.013733 | 0.022888 | 0.022888 | 0.1236 | 0.013733 | -0.13733 | -0.032043 | 0.045776 | -0.082397 | 0.068665 | 0.073242 | -0.054932 | -0.11902 | 122.1725 | 122.0215 | 0.032043 | 122.1451 | 122.1817 | 0.16022 | 0.004577 | 122.1039 | 122.0398 | -0.022888 | 122.1268 | 122.0764 | 0.036622 | -0.018311 | 122.2824 | 122.2549 | 122.1817 | -0.22888 | 122.2275 | 122.2321 | 122.2046 | -0.21057
3244.4062 | 122.406 | -122.1725 | 0.11444 | -0.00022891 | -0.019442 | 0.02126 | 0.038373 | -0.0064428 | -0.037442 | -0.020755 | 7.627e-05 | 0.011158 | -0.0083035 | -0.098888 | -0.014919 | 0.0026062 | 0.022888 | -0.054932 | 0 | 0.009155 | 0.14648 | 0 | -0.11902 | -0.064087 | 0.032043 | -0.07782 | 0.09613 | 0.091553 | -0.073242 | -0.13275 | 122.1725 | 122.0535 | 0.032043 | 122.1176 | 122.1817 | 0.12817 | -0.091553 | 122.0993 | 122.0398 | -0.018311 | 122.1085 | 122.0947 | 0.054931 | -0.022888 | 122.319 | 122.1954 | 122.1725 | -0.23346 | 122.2687 | 122.2641 | 122.2046 | -0.24719
3246.2031 | 122.4564 | -122.1771 | 0.10071 | -0.00022891 | -0.015383 | 0.019551 | 0.039868 | -0.0087926 | -0.037442 | -0.019901 | 0.0077058 | 0.011798 | -0.0068081 | -0.094829 | -0.015774 | -0.00059818 | 0.027466 | -0.050354 | -0.009155 | 0.009155 | 0.14648 | 0.004578 | -0.14648 | -0.059509 | 0.032043 | -0.073242 | 0.09613 | 0.091553 | -0.059509 | -0.14191 | 122.1817 | 122.0306 | 0.045776 | 122.1268 | 122.1863 | 0.15564 | -0.073242 | 122.1176 | 122.0352 | -0.004578 | 122.1176 | 122.1039 | 0.068665 | -0.009155 | 122.3236 | 122.2046 | 122.168 | -0.24719 | 122.2733 | 122.2687 | 122.2092 | -0.24262
3247.9219 | 122.4838 | -122.1954 | 0.09613 | -0.0078584 | -0.01816 | 0.018696 | 0.035169 | -0.0072974 | -0.036801 | -0.019046 | 0.0077058 | 0.012226 | -0.0093717 | -0.094829 | -0.015347 | 0.00047002 | 0.11902 | 0.045776 | 0.10071 | 0.09613 | 0.11444 | 0.050354 | -0.091553 | 0.045776 | 0.13733 | 0.022888 | 0.041199 | 0.032043 | -0.022888 | -0.07782 | 122.2458 | 122.1039 | 0.018311 | 122.2412 | 122.2916 | 0.18768 | 0.022889 | 122.1725 | 122.1176 | -0.054931 | 122.2412 | 122.2183 | 0.10071 | -0.064087 | 122.3099 | 122.3145 | 122.2961 | -0.18768 | 122.2366 | 122.2275 | 122.3328 | -0.17395
3249.7031 | 122.4335 | -122.1817 | 0.10529 | -0.0078584 | -0.017519 | 0.015919 | 0.037305 | -0.0090062 | -0.034665 | -0.020115 | 7.627e-05 | 0.015644 | -0.0070217 | -0.096538 | -0.011715 | -0.0025208 | 0.022888 | -0.07782 | -0.027466 | 0 | 0.13733 | 0.009155 | -0.13275 | -0.091553 | -0.009155 | -0.12817 | 0.073242 | 0.07782 | -0.054932 | -0.13275 | 122.1909 | 122.049 | 0.032043 | 122.1039 | 122.1817 | 0.13275 | -0.082398 | 122.1268 | 122.049 | -0.032044 | 122.0901 | 122.0535 | 0.004577 | -0.027466 | 122.319 | 122.2046 | 122.1542 | -0.23804 | 122.2549 | 122.2595 | 122.1725 | -0.23804
3251.5156 | 122.4792 | -122.1588 | 0.07782 | -0.00022891 | -0.01581 | 0.017201 | 0.037305 | -0.010715 | -0.037014 | -0.021183 | 7.627e-05 | 0.014789 | -0.0061673 | -0.09547 | -0.012997 | 0.00025642 | 0.059509 | -0.004578 | 0.032043 | 0.064087 | 0.14648 | 0.013733 | -0.1236 | -0.018311 | 0.086975 | -0.041199 | 0.091553 | 0.068665 | -0.059509 | -0.13275 | 122.1725 | 122.0352 | 0.068664 | 122.1542 | 122.2229 | 0.18768 | -0.018311 | 122.0993 | 122.0261 | 0.013733 | 122.1405 | 122.1176 | 0.091552 | -0.009155 | 122.3053 | 122.2183 | 122.1909 | -0.20142 | 122.2504 | 122.2275 | 122.2458 | -0.21057
3253.2344 | 122.493 | -122.1634 | 0.082397 | -0.0078584 | -0.015383 | 0.016774 | 0.036664 | -0.0070836 | -0.035946 | -0.018406 | 7.627e-05 | 0.014362 | -0.0050991 | -0.09547 | -0.012997 | 0.0011108 | 0.050354 | -0.013733 | 0.027466 | 0.050354 | 0.12817 | -0.004578 | -0.15106 | -0.027466 | 0.07782 | -0.032043 | 0.082397 | 0.064087 | -0.054932 | -0.12817 | 122.1588 | 122.0123 | 0.045777 | 122.1497 | 122.2137 | 0.20142 | -0.032043 | 122.1085 | 122.0352 | 0 | 122.1359 | 122.1313 | 0.096131 | -0.01831 | 122.2916 | 122.2137 | 122.1909 | -0.23346 | 122.2458 | 122.2275 | 122.2412 | -0.21057
3255.0156 | 122.3648 | -122.2137 | 0.11444 | -0.00022891 | -0.01816 | 0.018483 | 0.039868 | -0.0077246 | -0.041073 | -0.020969 | -0.0075532 | 0.013721 | -0.0072353 | -0.098034 | -0.017056 | 0.0015382 | 0.050354 | 0.018311 | 0.045776 | 0.045776 | 0.11902 | 0 | -0.13275 | -0.050354 | 0.054932 | -0.059509 | 0.091553 | 0.07782 | -0.064087 | -0.13733 | 122.2137 | 122.081 | 0.004578 | 122.2321 | 122.2595 | 0.17853 | -0.064087 | 122.1497 | 122.0764 | -0.022888 | 122.1634 | 122.1542 | 0.07782 | -0.036621 | 122.3328 | 122.2641 | 122.2595 | -0.24719 | 122.3053 | 122.2916 | 122.2687 | -0.25177
3256.8125 | 122.406 | -122.2275 | 0.13733 | -0.00022891 | -0.020724 | 0.019337 | 0.037946 | -0.010288 | -0.042996 | -0.022892 | -0.0075532 | 0.012226 | -0.0029629 | -0.099102 | -0.017483 | 0.00025642 | 0.11444 | 0.10529 | 0.14648 | 0.10071 | 0.11444 | 0.041199 | -0.091553 | 0.068665 | 0.20599 | 0.091553 | 0.050354 | 0.068665 | -0.013733 | -0.10986 | 122.2687 | 122.1359 | -0.022888 | 122.3328 | 122.3282 | 0.19226 | -0.022888 | 122.2137 | 122.1176 | -0.086975 | 122.2961 | 122.319 | 0.20142 | -0.068664 | 122.3419 | 122.3419 | 122.374 | -0.22888 | 122.2778 | 122.2961 | 122.4335 | -0.24719
3258.5312 | 122.493 | -122.1817 | 0.10071 | -0.00022891 | -0.019442 | 0.016346 | 0.036878 | -0.010288 | -0.035092 | -0.020328 | -0.015182 | 0.015216 | -0.0040311 | -0.099316 | -0.011929 | 0.00025642 | 0.045776 | -0.050354 | 0.004578 | 0 | 0.15564 | 0.009155 | -0.11902 | -0.022888 | 0.018311 | -0.068665 | 0.086975 | 0.064087 | -0.068665 | -0.11902 | 122.1909 | 122.0627 | 0.054932 | 122.1313 | 122.1817 | 0.11902 | -0.054932 | 122.113 | 122.0627 | -0.013733 | 122.1588 | 122.113 | 0.050354 | -0.036621 | 122.3373 | 122.2275 | 122.1863 | -0.21973 | 122.2687 | 122.2458 | 122.2 | -0.21973
3260.3281 | 122.374 | -122.2275 | 0.12817 | -0.00022891 | -0.019869 | 0.019123 | 0.038587 | -0.0087926 | -0.042355 | -0.020328 | 0.0077058 | 0.012439 | -0.0042447 | -0.1006 | -0.015988 | 0.00089722 | 0.10071 | 0.10529 | 0.13733 | 0.091553 | 0.09613 | 0.045776 | -0.10986 | 0.027466 | 0.16479 | 0.041199 | 0.068665 | 0.036621 | -0.041199 | -0.10071 | 122.2733 | 122.1176 | -0.032044 | 122.3328 | 122.319 | 0.20142 | -0.027466 | 122.1863 | 122.1268 | -0.059509 | 122.2549 | 122.2687 | 0.14191 | -0.091553 | 122.3236 | 122.3282 | 122.3648 | -0.23804 | 122.2961 | 122.2641 | 122.3923 | -0.22888
3262.125 | 122.3969 | -122.2549 | 0.13275 | -0.00022891 | -0.020724 | 0.018696 | 0.03645 | -0.0087926 | -0.038937 | -0.020328 | -0.0075532 | 0.0094486 | -0.011508 | -0.097393 | -0.01556 | 0.00089722 | 0.13275 | 0.082397 | 0.11902 | 0.086975 | 0.091553 | 0.050354 | -0.086975 | 0.073242 | 0.13275 | 0.036621 | 0.073242 | 0.054932 | -0.009155 | -0.07782 | 122.3053 | 122.168 | -0.041198 | 122.3373 | 122.3419 | 0.17395 | 0 | 122.2458 | 122.1771 | -0.059509 | 122.3282 | 122.2916 | 0.11444 | -0.077819 | 122.3465 | 122.3877 | 122.374 | -0.21973 | 122.3282 | 122.3099 | 122.3877 | -0.21057
3263.8438 | 122.493 | -122.1909 | 0.086975 | -0.015487 | -0.017092 | 0.01891 | 0.036664 | -0.0087926 | -0.034878 | -0.01926 | 7.627e-05 | 0.013721 | -0.010867 | -0.096325 | -0.014065 | -0.0014526 | 0.054932 | -0.032043 | -0.004578 | 0.027466 | 0.16479 | 0.004578 | -0.14648 | -0.050354 | 0.064087 | -0.064087 | 0.09613 | 0.073242 | -0.064087 | -0.11444 | 122.1954 | 122.0444 | 0.07782 | 122.1588 | 122.2183 | 0.17395 | -0.032043 | 122.1268 | 122.0764 | 0.009155 | 122.1405 | 122.1268 | 0.050354 | -0.013733 | 122.3557 | 122.2458 | 122.1863 | -0.23346 | 122.287 | 122.2641 | 122.2549 | -0.20142
3265.625 | 122.3831 | -122.2366 | 0.14648 | -0.015487 | -0.024142 | 0.021046 | 0.035596 | -0.010288 | -0.040219 | -0.019046 | 0.0077058 | 0.010089 | -0.01108 | -0.097607 | -0.015133 | 0.0015382 | 0.091553 | 0.064087 | 0.09613 | 0.059509 | 0.10529 | 0.036621 | -0.10529 | 0.036621 | 0.09613 | 0.013733 | 0.041199 | 0.050354 | -0.050354 | -0.10071 | 122.2733 | 122.1313 | -0.041198 | 122.3007 | 122.2961 | 0.16479 | -0.054931 | 122.1863 | 122.1359 | -0.10529 | 122.2733 | 122.2504 | 0.11444 | -0.09613 | 122.3419 | 122.3282 | 122.3328 | -0.25177 | 122.2778 | 122.287 | 122.3328 | -0.24719
3267.4219 | 122.4564 | -122.2 | 0.091553 | -0.0078584 | -0.01581 | 0.019337 | 0.037518 | -0.007511 | -0.03616 | -0.019687 | 7.627e-05 | 0.011371 | -0.0085171 | -0.097179 | -0.015988 | -0.0014526 | 0.036621 | -0.045776 | -0.013733 | 0.009155 | 0.15564 | -0.013733 | -0.14191 | -0.054932 | 0.036621 | -0.086975 | 0.10071 | 0.082397 | -0.091553 | -0.14191 | 122.1863 | 122.0581 | 0.064087 | 122.1542 | 122.2092 | 0.15106 | -0.054932 | 122.1085 | 122.0581 | 0.009155 | 122.1451 | 122.113 | 0.054932 | -0.009156 | 122.3557 | 122.2366 | 122.1863 | -0.23346 | 122.3007 | 122.2824 | 122.2366 | -0.23346
3269.2031 | 122.525 | -122.2229 | 0.091553 | -0.0078584 | -0.020083 | 0.015278 | 0.034528 | -0.0070836 | -0.036374 | -0.018406 | -0.0075532 | 0.012439 | -0.0080899 | -0.096111 | -0.013851 | -0.00017078 | 0.09613 | 0.018311 | 0.082397 | 0.073242 | 0.12817 | 0.054932 | -0.10071 | 0.064087 | 0.11902 | 0.022888 | 0.050354 | 0.045776 | -0.041199 | -0.07782 | 122.2778 | 122.1222 | 0.036621 | 122.2412 | 122.2961 | 0.17395 | 0.004577 | 122.1817 | 122.1451 | -0.041199 | 122.287 | 122.2458 | 0.10071 | -0.045777 | 122.3511 | 122.319 | 122.3053 | -0.19226 | 122.2733 | 122.2687 | 122.3419 | -0.16937
3271 | 122.4838 | -122.2229 | 0.086975 | -0.00022891 | -0.016238 | 0.016774 | 0.033887 | -0.0070836 | -0.035092 | -0.017978 | 7.627e-05 | 0.012867 | -0.0076627 | -0.097607 | -0.011501 | 0.00089722 | 0.009155 | -0.068665 | -0.022888 | 0 | 0.14648 | 0 | -0.13733 | -0.064087 | -0.036621 | -0.1236 | 0.082397 | 0.086975 | -0.054932 | -0.13733 | 122.2229 | 122.0856 | 0.059509 | 122.1542 | 122.2229 | 0.13733 | -0.07782 | 122.168 | 122.0856 | -0.004578 | 122.1588 | 122.0993 | 0.013733 | 0 | 122.3694 | 122.2321 | 122.2 | -0.2243 | 122.3053 | 122.3099 | 122.1863 | -0.2243
3272.7344 | 122.525 | -122.2183 | 0.091553 | 0.0074006 | -0.016024 | 0.017628 | 0.033887 | -0.010074 | -0.03616 | -0.018406 | 0.0077058 | 0.012867 | -0.0068081 | -0.095898 | -0.012783 | -0.00017078 | 0.022888 | -0.059509 | -0.013733 | 0 | 0.14191 | 0 | -0.1236 | -0.036621 | -0.009155 | -0.082397 | 0.09613 | 0.059509 | -0.050354 | -0.1236 | 122.2183 | 122.0947 | 0.050354 | 122.1588 | 122.2183 | 0.1236 | -0.068665 | 122.168 | 122.0947 | 0.004577 | 122.1817 | 122.1359 | 0.041199 | -0.032044 | 122.3602 | 122.2412 | 122.2046 | -0.21515 | 122.3145 | 122.2778 | 122.2092 | -0.21515
3274.4844 | 122.5113 | -122.2641 | 0.10071 | 0.0074006 | -0.019655 | 0.019764 | 0.033673 | -0.0081518 | -0.04086 | -0.017978 | 7.627e-05 | 0.010944 | -0.0091579 | -0.099956 | -0.013851 | 0.00089722 | 0.12817 | 0.07782 | 0.11902 | 0.09613 | 0.091553 | 0.059509 | -0.09613 | 0.073242 | 0.14648 | 0.054932 | 0.036621 | 0.050354 | -0.022888 | -0.082397 | 122.3236 | 122.168 | -0.009155 | 122.3419 | 122.3602 | 0.19226 | 0.027466 | 122.2412 | 122.1817 | -0.064087 | 122.3373 | 122.319 | 0.13733 | -0.050354 | 122.3557 | 122.3923 | 122.3831 | -0.19684 | 122.3007 | 122.3145 | 122.4106 | -0.18311
3276.2812 | 122.4838 | -122.2595 | 0.09613 | -0.0078584 | -0.01581 | 0.015919 | 0.036878 | -0.0079382 | -0.035946 | -0.020328 | 0.0077058 | 0.014148 | -0.0076627 | -0.095898 | -0.012783 | -0.0010254 | 0.032043 | -0.068665 | -0.004578 | 0.004578 | 0.13733 | 0 | -0.13733 | -0.091553 | -0.013733 | -0.10071 | 0.082397 | 0.086975 | -0.050354 | -0.13733 | 122.2595 | 122.1222 | 0.041199 | 122.1909 | 122.2641 | 0.14191 | -0.064087 | 122.2092 | 122.1222 | -0.013733 | 122.168 | 122.1588 | 0.036621 | -0.009155 | 122.3969 | 122.2916 | 122.2549 | -0.23346 | 122.3419 | 122.3465 | 122.2458 | -0.23346
3278.0156 | 122.525 | -122.2275 | 0.091553 | -0.00022891 | -0.019228 | 0.018483 | 0.037732 | -0.0055884 | -0.037014 | -0.020115 | 0.0077058 | 0.010944 | -0.0078763 | -0.09547 | -0.014919 | -0.00017078 | 0.027466 | -0.045776 | -0.022888 | 0.022888 | 0.15106 | -0.009155 | -0.15106 | -0.073242 | 0.054932 | -0.068665 | 0.10986 | 0.09613 | -0.091553 | -0.13275 | 122.2183 | 122.0764 | 0.059509 | 122.1817 | 122.2504 | 0.17395 | -0.064087 | 122.1359 | 122.0947 | 0.01831 | 122.1542 | 122.1588 | 0.064086 | 0.004577 | 122.3785 | 122.2549 | 122.2046 | -0.24261 | 122.3373 | 122.3236 | 122.2824 | -0.2243
3279.75 | 122.438 | -122.287 | 0.11444 | -0.015487 | -0.01816 | 0.017415 | 0.039227 | -0.0077246 | -0.040219 | -0.01926 | -0.0075532 | 0.011585 | -0.0074491 | -0.09782 | -0.016628 | 0.00068362 | 0.027466 | -0.054932 | -0.009155 | -0.009155 | 0.14191 | 0.004578 | -0.14191 | -0.068665 | 0.054932 | -0.091553 | 0.10529 | 0.10529 | -0.073242 | -0.12817 | 122.2916 | 122.1451 | 0.027466 | 122.2321 | 122.2778 | 0.13275 | -0.086975 | 122.2137 | 122.1588 | -0.009155 | 122.2183 | 122.1954 | 0.036621 | -0.009155 | 122.4289 | 122.3145 | 122.2778 | -0.25635 | 122.3923 | 122.3923 | 122.3419 | -0.24262
3281.5469 | 122.5937 | -122.2595 | 0.091553 | -0.015487 | -0.018801 | 0.018055 | 0.032392 | -0.010074 | -0.037442 | -0.017338 | -0.015182 | 0.011371 | -0.0078763 | -0.099743 | -0.012997 | -0.0010254 | 0.059509 | -0.036621 | 0.018311 | 0.009155 | 0.14648 | 0.027466 | -0.11444 | 0.004578 | 0.050354 | -0.009155 | 0.073242 | 0.059509 | -0.018311 | -0.1236 | 122.287 | 122.1451 | 0.054931 | 122.2229 | 122.2687 | 0.1236 | -0.032044 | 122.2412 | 122.1359 | -0.018311 | 122.2641 | 122.2504 | 0.11444 | -0.032044 | 122.406 | 122.319 | 122.2778 | -0.20599 | 122.3328 | 122.319 | 122.3099 | -0.21515
3283.3281 | 122.4152 | -122.2504 | 0.11902 | -0.00022891 | -0.019228 | 0.017628 | 0.039441 | -0.011356 | -0.04086 | -0.02161 | 7.627e-05 | 0.0088076 | -0.0095853 | -0.096752 | -0.017269 | 0.00089722 | 0.10529 | 0.07782 | 0.11902 | 0.10071 | 0.10071 | 0.041199 | -0.10071 | 0 | 0.15106 | 0.013733 | 0.050354 | 0.059509 | -0.036621 | -0.12817 | 122.2916 | 122.1497 | -0.018311 | 122.3282 | 122.3511 | 0.20142 | -0.013733 | 122.2137 | 122.1222 | -0.068665 | 122.2504 | 122.2641 | 0.14191 | -0.05951 | 122.3511 | 122.3557 | 122.3694 | -0.21973 | 122.3007 | 122.3099 | 122.4014 | -0.24719
3285.0625 | 122.4976 | -122.2961 | 0.10986 | -0.0078584 | -0.019869 | 0.019978 | 0.037946 | -0.0090062 | -0.042782 | -0.020542 | 7.627e-05 | 0.007526 | -0.0080899 | -0.098247 | -0.016415 | 4.2822e-05 | 0.12817 | 0.10071 | 0.12817 | 0.086975 | 0.10071 | 0.045776 | -0.082397 | 0.082397 | 0.1831 | 0.09613 | 0.054932 | 0.054932 | -0.036621 | -0.10529 | 122.3419 | 122.2137 | -0.009155 | 122.3969 | 122.3831 | 0.16937 | 0.018311 | 122.2595 | 122.1909 | -0.054931 | 122.3785 | 122.3923 | 0.20142 | -0.054931 | 122.3969 | 122.4243 | 122.4243 | -0.19226 | 122.3511 | 122.3511 | 122.4792 | -0.21515
3286.8594 | 122.5662 | -122.2687 | 0.082397 | 0.0074006 | -0.017519 | 0.017415 | 0.033673 | -0.00922 | -0.034451 | -0.020755 | 0.0077058 | 0.013721 | -0.0083035 | -0.098247 | -0.01257 | -0.0018798 | 0.054932 | -0.054932 | -0.018311 | 0.009155 | 0.14648 | 0.013733 | -0.13733 | -0.032043 | 0.009155 | -0.07782 | 0.091553 | 0.082397 | -0.050354 | -0.12817 | 122.2824 | 122.1313 | 0.064087 | 122.2137 | 122.2778 | 0.14648 | -0.027465 | 122.2183 | 122.1405 | 0.009156 | 122.2366 | 122.1909 | 0.050354 | 0 | 122.4152 | 122.3236 | 122.2504 | -0.21973 | 122.3602 | 122.3511 | 122.2778 | -0.21057
3288.6406 | 122.4884 | -122.2733 | 0.11902 | -0.00022891 | -0.015383 | 0.019551 | 0.036023 | -0.010502 | -0.037228 | -0.020115 | 7.627e-05 | 0.012012 | -0.0072353 | -0.095684 | -0.013851 | -0.0014526 | 0.022888 | -0.036621 | -0.009155 | 0.009155 | 0.12817 | -0.018311 | -0.14648 | -0.073242 | 0.032043 | -0.091553 | 0.09613 | 0.09613 | -0.07782 | -0.14648 | 122.2549 | 122.1268 | 0.009155 | 122.2366 | 122.2824 | 0.15564 | -0.096131 | 122.1954 | 122.1268 | -0.022889 | 122.2 | 122.1817 | 0.054931 | -0.022889 | 122.4014 | 122.2961 | 122.2641 | -0.2655 | 122.3694 | 122.3694 | 122.3053 | -0.2655
3290.4219 | 122.4792 | -122.3099 | 0.11444 | -0.00022891 | -0.02051 | 0.018483 | 0.033887 | -0.010502 | -0.039151 | -0.021396 | -0.015182 | 0.01073 | -0.01108 | -0.098675 | -0.014065 | 0.00047002 | 0.032043 | -0.041199 | -0.009155 | 0.009155 | 0.15564 | -0.013733 | -0.16022 | -0.059509 | 0.036621 | -0.07782 | 0.086975 | 0.082397 | -0.073242 | -0.14191 | 122.2961 | 122.1497 | 0.041199 | 122.2687 | 122.319 | 0.16937 | -0.082398 | 122.2366 | 122.168 | -0.027466 | 122.2504 | 122.2321 | 0.064087 | -0.032044 | 122.4655 | 122.3419 | 122.3007 | -0.27466 | 122.3969 | 122.3923 | 122.3465 | -0.25635
3292.1562 | 122.58 | -122.2778 | 0.07782 | -0.00022891 | -0.018801 | 0.015492 | 0.03645 | -0.010502 | -0.035092 | -0.020542 | -0.0075532 | 0.013935 | -0.0078763 | -0.094616 | -0.014706 | -0.00081178 | 0.045776 | -0.082397 | -0.041199 | 0.013733 | 0.14648 | 0.009155 | -0.14648 | -0.045776 | 0.009155 | -0.073242 | 0.082397 | 0.086975 | -0.059509 | -0.12817 | 122.287 | 122.1313 | 0.068664 | 122.1954 | 122.2916 | 0.16022 | -0.032044 | 122.2183 | 122.1497 | 0.004577 | 122.2321 | 122.2046 | 0.054932 | 0.009155 | 122.4243 | 122.3236 | 122.2366 | -0.2243 | 122.3602 | 122.3648 | 122.287 | -0.20599
3293.9531 | 122.4289 | -122.3236 | 0.1236 | -0.00022891 | -0.020937 | 0.017628 | 0.037305 | -0.0090062 | -0.041501 | -0.017338 | 7.627e-05 | 0.011158 | -0.0072353 | -0.098247 | -0.017056 | 0.00068362 | 0.10529 | 0.09613 | 0.1236 | 0.082397 | 0.10529 | 0.022888 | -0.11902 | 0.009155 | 0.13733 | 0.022888 | 0.050354 | 0.050354 | -0.041199 | -0.10529 | 122.3465 | 122.2046 | -0.01831 | 122.4197 | 122.406 | 0.20142 | -0.01831 | 122.2824 | 122.2183 | -0.073242 | 122.3328 | 122.3465 | 0.12817 | -0.073242 | 122.4289 | 122.4289 | 122.4472 | -0.24261 | 122.374 | 122.374 | 122.4609 | -0.22888
3295.6719 | 122.4564 | -122.3282 | 0.10986 | -0.00022891 | -0.022433 | 0.01891 | 0.034528 | -0.012638 | -0.040219 | -0.021824 | -0.0075532 | 0.0079532 | -0.0085171 | -0.099529 | -0.016415 | 0.00068362 | 0.059509 | 0.041199 | 0.082397 | 0.059509 | 0.10986 | 0.036621 | -0.10071 | -0.004578 | 0.091553 | 0.009155 | 0.050354 | 0.050354 | -0.054932 | -0.1236 | 122.3648 | 122.2275 | 0 | 122.3694 | 122.3877 | 0.16022 | -0.050354 | 122.2733 | 122.2046 | -0.059509 | 122.3236 | 122.3373 | 0.13275 | -0.059509 | 122.438 | 122.3877 | 122.4106 | -0.21057 | 122.3785 | 122.3785 | 122.4197 | -0.23346
3297.4531 | 122.5342 | -122.2961 | 0.10986 | -0.00022891 | -0.020724 | 0.019764 | 0.033887 | -0.0070836 | -0.037228 | -0.020755 | 7.627e-05 | 0.0098758 | -0.0095853 | -0.098034 | -0.014065 | -0.001239 | 0.15106 | 0.059509 | 0.13275 | 0.086975 | 0.10529 | 0.041199 | -0.10986 | 0.068665 | 0.16022 | 0.045776 | 0.045776 | 0.045776 | -0.022888 | -0.07782 | 122.3373 | 122.1863 | -0.004577 | 122.3557 | 122.3831 | 0.19684 | 0.041199 | 122.2733 | 122.2183 | -0.064087 | 122.3648 | 122.3419 | 0.1236 | -0.064087 | 122.4014 | 122.4472 | 122.4289 | -0.21973 | 122.3419 | 122.3419 | 122.4564 | -0.18768
3299.1719 | 122.5021 | -122.3053 | 0.13275 | -0.00022891 | -0.020724 | 0.020192 | 0.038159 | -0.0083654 | -0.042782 | -0.021183 | 0.0077058 | 0.0081668 | -0.0078763 | -0.096111 | -0.017697 | -0.001239 | 0.14191 | 0.10529 | 0.15564 | 0.10529 | 0.086975 | 0.027466 | -0.09613 | 0.054932 | 0.17853 | 0.064087 | 0.041199 | 0.054932 | -0.041199 | -0.09613 | 122.3328 | 122.2092 | -0.045776 | 122.4106 | 122.4106 | 0.20142 | 0.009156 | 122.2641 | 122.2092 | -0.091552 | 122.3602 | 122.3694 | 0.16022 | -0.077819 | 122.3923 | 122.4472 | 122.4609 | -0.22888 | 122.3465 | 122.3602 | 122.4838 | -0.22888
3300.9688 | 122.4747 | -122.3419 | 0.11902 | -0.015487 | -0.019869 | 0.019978 | 0.040509 | -0.01157 | -0.040646 | -0.023105 | 7.627e-05 | 0.008594 | -0.0089443 | -0.098888 | -0.016415 | -0.0016662 | 0.14648 | 0.11902 | 0.14191 | 0.10986 | 0.082397 | 0.032043 | -0.10529 | 0.068665 | 0.19684 | 0.064087 | 0.064087 | 0.032043 | -0.036621 | -0.10529 | 122.374 | 122.2366 | -0.036622 | 122.4609 | 122.4518 | 0.21515 | 0.027465 | 122.3053 | 122.2366 | -0.054932 | 122.4106 | 122.406 | 0.16937 | -0.086976 | 122.4243 | 122.4884 | 122.4838 | -0.22431 | 122.406 | 122.374 | 122.5388 | -0.22431
3302.7656 | 122.4884 | -122.3373 | 0.13733 | -0.0078584 | -0.021364 | 0.020192 | 0.036664 | -0.00922 | -0.03851 | -0.022892 | 7.627e-05 | 0.011371 | -0.0059537 | -0.099743 | -0.013424 | 4.2822e-05 | 0.068665 | 0.022888 | 0.082397 | 0.073242 | 0.11444 | 0.041199 | -0.10529 | 0.004578 | 0.07782 | 0.022888 | 0.059509 | 0.045776 | -0.032043 | -0.10529 | 122.3785 | 122.2321 | -0.022888 | 122.3602 | 122.4106 | 0.17853 | -0.068664 | 122.3053 | 122.2321 | -0.07782 | 122.3419 | 122.3602 | 0.12817 | -0.091553 | 122.4518 | 122.406 | 122.4197 | -0.24262 | 122.3969 | 122.3831 | 122.4152 | -0.24262
3304.5781 | 122.5525 | -122.287 | 0.10529 | -0.0078584 | -0.015169 | 0.017842 | 0.035169 | -0.0079382 | -0.031887 | -0.018406 | 0.0077058 | 0.017353 | -0.0040311 | -0.09782 | -0.010647 | -0.0033752 | 0.045776 | -0.064087 | -0.013733 | 0.009155 | 0.15564 | -0.009155 | -0.14648 | -0.059509 | -0.013733 | -0.11902 | 0.086975 | 0.068665 | -0.054932 | -0.12817 | 122.2778 | 122.1405 | 0.050354 | 122.2229 | 122.2961 | 0.15564 | -0.05951 | 122.2321 | 122.1588 | -0.018311 | 122.2275 | 122.168 | 0.009155 | -0.036621 | 122.4426 | 122.3328 | 122.2733 | -0.25177 | 122.374 | 122.3557 | 122.2733 | -0.23346
3306.2969 | 122.5479 | -122.3145 | 0.12817 | -0.0078584 | -0.024142 | 0.024037 | 0.036237 | -0.008579 | -0.042569 | -0.020755 | -0.0075532 | 0.008594 | -0.01108 | -0.10017 | -0.01321 | 0.0013244 | 0.059509 | 0.045776 | 0.07782 | 0.064087 | 0.12817 | 0.013733 | -0.11444 | 0.022888 | 0.1236 | 0.032043 | 0.054932 | 0.059509 | -0.027466 | -0.10986 | 122.3282 | 122.2 | 0 | 122.3602 | 122.3785 | 0.17853 | -0.068665 | 122.287 | 122.2046 | -0.073242 | 122.3373 | 122.3465 | 0.14191 | -0.068665 | 122.4426 | 122.374 | 122.3923 | -0.24262 | 122.3694 | 122.374 | 122.438 | -0.23804
3308.0938 | 122.6074 | -122.3145 | 0.086975 | -0.0078584 | -0.017946 | 0.017415 | 0.036878 | -0.00922 | -0.034878 | -0.019046 | -0.0075532 | 0.011798 | -0.0046719 | -0.098034 | -0.01321 | -0.001239 | 0.09613 | 0.004578 | 0.045776 | 0.041199 | 0.10986 | 0.022888 | -0.11902 | 0.050354 | 0.11444 | -0.004578 | 0.045776 | 0.054932 | -0.022888 | -0.10986 | 122.3373 | 122.1954 | 0.022888 | 122.319 | 122.3557 | 0.16022 | 0.009155 | 122.2916 | 122.2046 | -0.041199 | 122.3648 | 122.3099 | 0.10529 | -0.032043 | 122.4243 | 122.4106 | 122.3602 | -0.20599 | 122.3602 | 122.3694 | 122.4289 | -0.19684
3309.8906 | 122.5067 | -122.3282 | 0.1236 | 0.0074006 | -0.023073 | 0.021687 | 0.037305 | -0.011356 | -0.041714 | -0.022037 | 7.627e-05 | 0.007526 | -0.0070217 | -0.099316 | -0.015133 | 0.00068362 | 0.13275 | 0.13733 | 0.14648 | 0.086975 | 0.10071 | 0.032043 | -0.082397 | 0.059509 | 0.19684 | 0.050354 | 0.045776 | 0.032043 | -0.036621 | -0.091553 | 122.3602 | 122.2458 | -0.022888 | 122.4655 | 122.4152 | 0.16937 | 0.009155 | 122.2916 | 122.2366 | -0.07782 | 122.3877 | 122.3785 | 0.14191 | -0.091553 | 122.4289 | 122.4609 | 122.4747 | -0.20599 | 122.374 | 122.3602 | 122.525 | -0.21515
3311.6094 | 122.5891 | -122.3053 | 0.10071 | -0.0078584 | -0.013247 | 0.015278 | 0.039227 | -0.0087926 | -0.035946 | -0.020755 | 7.627e-05 | 0.016071 | -0.0065945 | -0.095898 | -0.014492 | -0.0014526 | 0.059509 | -0.059509 | -0.013733 | 0.018311 | 0.13733 | 0.009155 | -0.13733 | -0.032043 | 0.050354 | -0.064087 | 0.09613 | 0.10071 | -0.064087 | -0.1236 | 122.3145 | 122.168 | 0.036621 | 122.2458 | 122.3236 | 0.15564 | -0.041199 | 122.2412 | 122.1817 | -0.004578 | 122.2733 | 122.2412 | 0.059509 | 0 | 122.4426 | 122.3648 | 122.2916 | -0.23804 | 122.4014 | 122.406 | 122.3557 | -0.2243
3313.4062 | 122.5021 | -122.3877 | 0.11902 | -0.015487 | -0.019869 | 0.017415 | 0.036023 | -0.0096472 | -0.038083 | -0.020328 | 0.0077058 | 0.012867 | -0.0097989 | -0.096752 | -0.01791 | 0.0017518 | 0.041199 | -0.009155 | 0.022888 | 0.004578 | 0.13275 | 0.013733 | -0.13733 | -0.045776 | 0.041199 | -0.068665 | 0.10529 | 0.082397 | -0.064087 | -0.13733 | 122.4014 | 122.2504 | 0.013732 | 122.3785 | 122.3923 | 0.14191 | -0.07782 | 122.3236 | 122.2504 | -0.013733 | 122.3419 | 122.319 | 0.068664 | -0.036622 | 122.5204 | 122.4289 | 122.4106 | -0.25635 | 122.493 | 122.4701 | 122.4289 | -0.25635
3315.1875 | 122.5845 | -122.3373 | 0.09613 | 0.0074006 | -0.01816 | 0.018269 | 0.038159 | -0.0083654 | -0.037228 | -0.019901 | -0.0075532 | 0.012867 | -0.0074491 | -0.095898 | -0.014279 | -0.0010254 | 0.059509 | -0.050354 | -0.009155 | 0.004578 | 0.15564 | -0.013733 | -0.13275 | -0.054932 | 0.045776 | -0.086975 | 0.10986 | 0.086975 | -0.059509 | -0.15106 | 122.3236 | 122.2046 | 0.05951 | 122.287 | 122.3419 | 0.13733 | -0.036621 | 122.2778 | 122.1863 | 0.013733 | 122.2824 | 122.2504 | 0.064087 | -0.009155 | 122.493 | 122.3969 | 122.3282 | -0.22888 | 122.4472 | 122.4243 | 122.3831 | -0.24719
3316.9375 | 122.6166 | -122.3282 | 0.10071 | -0.00022891 | -0.019869 | 0.017201 | 0.034314 | -0.0077246 | -0.034878 | -0.017978 | 7.627e-05 | 0.013294 | -0.0065945 | -0.094402 | -0.013851 | 0.00047002 | 0.064087 | -0.07782 | -0.036621 | 0.018311 | 0.15106 | 0.013733 | -0.13733 | -0.041199 | 0.013733 | -0.091553 | 0.086975 | 0.073242 | -0.050354 | -0.12817 | 122.3419 | 122.1909 | 0.050354 | 122.2504 | 122.3465 | 0.15564 | -0.036621 | 122.2778 | 122.2 | -0.013733 | 122.287 | 122.2366 | 0.036621 | -0.027466 | 122.4792 | 122.3923 | 122.2916 | -0.23804 | 122.4152 | 122.4014 | 122.3419 | -0.22888
3318.7188 | 122.493 | -122.3877 | 0.10986 | -0.00022891 | -0.017946 | 0.020192 | 0.0388 | -0.010715 | -0.040005 | -0.020115 | -0.015182 | 0.012653 | -0.010012 | -0.098034 | -0.016201 | -0.001239 | 0.032043 | -0.009155 | 0.018311 | 0.013733 | 0.13733 | -0.009155 | -0.15106 | -0.045776 | 0.050354 | -0.07782 | 0.091553 | 0.10071 | -0.091553 | -0.15106 | 122.3785 | 122.2366 | 0.027466 | 122.3785 | 122.4014 | 0.16479 | -0.07782 | 122.2961 | 122.2366 | -0.01831 | 122.3419 | 122.3099 | 0.073242 | -0.009155 | 122.525 | 122.4197 | 122.406 | -0.26093 | 122.4792 | 122.4884 | 122.438 | -0.26093
3320.4531 | 122.644 | -122.3145 | 0.091553 | -0.00022891 | -0.017733 | 0.019551 | 0.035382 | -0.0087926 | -0.034665 | -0.019474 | 0.015335 | 0.015644 | -0.0078763 | -0.094616 | -0.012142 | 0.00068362 | 0.054932 | -0.059509 | -0.018311 | 0.004578 | 0.13275 | 0 | -0.13275 | -0.013733 | 0.013733 | -0.059509 | 0.07782 | 0.068665 | -0.073242 | -0.1236 | 122.3145 | 122.1817 | 0.041198 | 122.2549 | 122.319 | 0.13733 | -0.036621 | 122.2412 | 122.1909 | -0.013733 | 122.3007 | 122.2549 | 0.064087 | -0.022888 | 122.4472 | 122.3694 | 122.2961 | -0.2243 | 122.3923 | 122.3831 | 122.3282 | -0.21515
3322.2344 | 122.6166 | -122.3511 | 0.091553 | -0.00022891 | -0.01581 | 0.015706 | 0.035169 | -0.00922 | -0.032742 | -0.018406 | -0.0075532 | 0.01308 | -0.0093717 | -0.096538 | -0.011501 | 0.0017518 | 0.054932 | -0.086975 | -0.022888 | 0.022888 | 0.15106 | 0.013733 | -0.13733 | -0.059509 | 0 | -0.10071 | 0.086975 | 0.07782 | -0.07782 | -0.14648 | 122.3648 | 122.2137 | 0.059509 | 122.2641 | 122.374 | 0.16022 | -0.036621 | 122.2733 | 122.2046 | -0.004578 | 122.2916 | 122.2504 | 0.045776 | -0.013733 | 122.5021 | 122.406 | 122.3282 | -0.22888 | 122.438 | 122.4289 | 122.3511 | -0.23804
3323.9531 | 122.612 | -122.3328 | 0.09613 | 0.0074006 | -0.018374 | 0.018696 | 0.033673 | -0.0090062 | -0.038723 | -0.017124 | 7.627e-05 | 0.011798 | -0.0083035 | -0.097393 | -0.013851 | 4.2822e-05 | 0.13275 | 0.059509 | 0.12817 | 0.10986 | 0.07782 | 0.036621 | -0.11444 | 0.068665 | 0.15564 | 0.054932 | 0.036621 | 0.041199 | -0.027466 | -0.086975 | 122.3694 | 122.2183 | -0.01831 | 122.3923 | 122.4426 | 0.2243 | 0.036621 | 122.3053 | 122.2458 | -0.059509 | 122.4014 | 122.3877 | 0.14191 | -0.054931 | 122.4106 | 122.4655 | 122.4609 | -0.21057 | 122.3694 | 122.374 | 122.4884 | -0.1831
3325.7344 | 122.6074 | -122.3373 | 0.10071 | 0.0074006 | -0.01581 | 0.015919 | 0.037305 | -0.0079382 | -0.035733 | -0.01926 | -0.015182 | 0.014362 | -0.0078763 | -0.095684 | -0.012997 | 4.2822e-05 | 0.059509 | -0.068665 | -0.004578 | 0.018311 | 0.14648 | 0.009155 | -0.13733 | -0.068665 | -0.004578 | -0.09613 | 0.091553 | 0.082397 | -0.068665 | -0.14191 | 122.3465 | 122.2 | 0.045776 | 122.2687 | 122.3557 | 0.15564 | -0.041199 | 122.2687 | 122.1954 | -0.009155 | 122.2687 | 122.2412 | 0.045777 | -0.018311 | 122.4838 | 122.3969 | 122.3328 | -0.23804 | 122.4289 | 122.4197 | 122.3328 | -0.24262
3327.5469 | 122.5388 | -122.3557 | 0.10986 | -0.0078584 | -0.021364 | 0.019123 | 0.04115 | -0.010074 | -0.043423 | -0.017551 | 7.627e-05 | 0.009235 | -0.0072353 | -0.099743 | -0.018765 | -0.001239 | 0.12817 | 0.10986 | 0.12817 | 0.10529 | 0.10529 | 0.027466 | -0.11444 | 0.054932 | 0.20142 | 0.064087 | 0.054932 | 0.045776 | -0.032043 | -0.10529 | 122.3831 | 122.2412 | -0.004577 | 122.4655 | 122.4609 | 0.21973 | 0.018311 | 122.3236 | 122.2504 | -0.054931 | 122.4106 | 122.4197 | 0.16937 | -0.064087 | 122.4609 | 122.4838 | 122.4838 | -0.2243 | 122.4106 | 122.4014 | 122.5571 | -0.21515
3329.2656 | 122.6303 | -122.3465 | 0.091553 | -0.015487 | -0.016238 | 0.015065 | 0.037091 | -0.0079382 | -0.035946 | -0.018619 | -0.0075532 | 0.015216 | -0.0097989 | -0.098034 | -0.014279 | -0.0025208 | 0.036621 | -0.054932 | -0.009155 | 0.032043 | 0.15106 | 0 | -0.13275 | -0.054932 | 0.059509 | -0.059509 | 0.086975 | 0.091553 | -0.064087 | -0.13275 | 122.3465 | 122.2137 | 0.059509 | 122.2916 | 122.3785 | 0.16479 | -0.054932 | 122.2824 | 122.2137 | -0.004578 | 122.2916 | 122.287 | 0.073242 | 0 | 122.4976 | 122.3831 | 122.3373 | -0.2243 | 122.4335 | 122.4381 | 122.406 | -0.2243
3331.0469 | 122.644 | -122.3373 | 0.091553 | -0.00022891 | -0.016665 | 0.019337 | 0.038159 | -0.011997 | -0.038296 | -0.019687 | -0.015182 | 0.013507 | -0.0080899 | -0.098888 | -0.014492 | -0.0031616 | 0.036621 | -0.041199 | 0.009155 | 0.041199 | 0.14191 | 0 | -0.12817 | -0.050354 | 0.059509 | -0.054932 | 0.064087 | 0.082397 | -0.059509 | -0.11902 | 122.3373 | 122.2092 | 0.050354 | 122.2961 | 122.3785 | 0.16937 | -0.054932 | 122.2778 | 122.2183 | -0.027466 | 122.287 | 122.2824 | 0.064087 | -0.009156 | 122.4792 | 122.374 | 122.3465 | -0.21973 | 122.4014 | 122.4197 | 122.3969 | -0.21057
3332.7812 | 122.6669 | -122.3465 | 0.073242 | -0.015487 | -0.021151 | 0.01656 | 0.035596 | -0.00922 | -0.035946 | -0.018619 | 7.627e-05 | 0.014362 | -0.0091579 | -0.097179 | -0.013638 | -0.00059818 | 0.054932 | -0.059509 | -0.013733 | 0.009155 | 0.15106 | 0.009155 | -0.13733 | -0.022888 | 0.027466 | -0.050354 | 0.068665 | 0.07782 | -0.027466 | -0.11902 | 122.3557 | 122.2092 | 0.07782 | 122.287 | 122.3557 | 0.14648 | -0.01831 | 122.319 | 122.2275 | -0.004577 | 122.3236 | 122.2961 | 0.068665 | 0.004578 | 122.4976 | 122.4014 | 122.3328 | -0.21057 | 122.4152 | 122.4243 | 122.374 | -0.19226
3334.5938 | 122.5204 | -122.4014 | 0.13275 | 0.0074006 | -0.016878 | 0.017842 | 0.040509 | -0.0077246 | -0.041501 | -0.020542 | 7.627e-05 | 0.012653 | -0.0074491 | -0.09782 | -0.018124 | -0.00081178 | 0.041199 | -0.004578 | 0.027466 | 0.027466 | 0.14191 | 0 | -0.16479 | -0.059509 | 0.054932 | -0.059509 | 0.091553 | 0.091553 | -0.073242 | -0.14191 | 122.4014 | 122.2366 | 0.009156 | 122.3969 | 122.4289 | 0.19226 | -0.091552 | 122.3282 | 122.2595 | -0.041198 | 122.3419 | 122.3419 | 0.082398 | -0.041198 | 122.5433 | 122.4426 | 122.4289 | -0.29755 | 122.493 | 122.493 | 122.4564 | -0.27466
3336.3906 | 122.644 | -122.3877 | 0.082397 | 0.0074006 | -0.01282 | 0.017415 | 0.034314 | -0.010074 | -0.032742 | -0.020755 | 7.627e-05 | 0.013721 | -0.0068081 | -0.098247 | -0.013424 | -0.001239 | 0.032043 | -0.09613 | -0.022888 | 0.018311 | 0.14648 | 0.004578 | -0.11444 | -0.050354 | -0.004578 | -0.091553 | 0.091553 | 0.073242 | -0.059509 | -0.13733 | 122.3923 | 122.2733 | 0.064087 | 122.2916 | 122.406 | 0.13275 | -0.050354 | 122.3282 | 122.2504 | 0.009156 | 122.3373 | 122.2961 | 0.045776 | -0.009155 | 122.5342 | 122.4197 | 122.3648 | -0.19684 | 122.4792 | 122.4609 | 122.3831 | -0.21973
3338.125 | 122.6257 | -122.3648 | 0.07782 | -0.00022891 | -0.014529 | 0.016987 | 0.033887 | -0.010288 | -0.036374 | -0.018833 | 7.627e-05 | 0.015644 | -0.0046719 | -0.096111 | -0.010647 | -0.001239 | 0.10071 | 0.018311 | 0.050354 | 0.032043 | 0.14191 | 0.027466 | -0.1236 | -0.009155 | 0.086975 | -0.041199 | 0.073242 | 0.086975 | -0.064087 | -0.11444 | 122.3923 | 122.2412 | 0.064087 | 122.3831 | 122.3969 | 0.15564 | 0.022888 | 122.3007 | 122.2504 | -0.004578 | 122.3557 | 122.3236 | 0.073242 | 0.009155 | 122.5067 | 122.4655 | 122.4152 | -0.20142 | 122.438 | 122.4518 | 122.4518 | -0.19226
3339.9219 | 122.6349 | -122.3373 | 0.11444 | -0.015487 | -0.015597 | 0.016133 | 0.039441 | -0.011143 | -0.037869 | -0.020755 | 7.627e-05 | 0.012653 | -0.0050991 | -0.095898 | -0.016415 | 0.00089722 | 0.027466 | -0.054932 | -0.013733 | 0.036621 | 0.16022 | 0 | -0.14191 | -0.073242 | 0.050354 | -0.064087 | 0.091553 | 0.07782 | -0.07782 | -0.12817 | 122.3373 | 122.1954 | 0.045776 | 122.2824 | 122.374 | 0.17853 | -0.086975 | 122.2595 | 122.2092 | -0.022888 | 122.2641 | 122.2733 | 0.064087 | -0.036621 | 122.4976 | 122.3648 | 122.3236 | -0.25635 | 122.4289 | 122.4152 | 122.3877 | -0.24262
3341.6562 | 122.6578 | -122.3969 | 0.086975 | -0.00022891 | -0.016024 | 0.017842 | 0.035382 | -0.010074 | -0.035733 | -0.017551 | 0.015335 | 0.012653 | -0.0078763 | -0.093548 | -0.011929 | -0.00017078 | 0.027466 | -0.09613 | -0.027466 | -0.004578 | 0.14191 | 0.004578 | -0.12817 | -0.050354 | 0 | -0.09613 | 0.073242 | 0.07782 | -0.054932 | -0.15106 | 122.4014 | 122.2687 | 0.054932 | 122.3007 | 122.3923 | 0.1236 | -0.059509 | 122.3419 | 122.2458 | -0.013733 | 122.3465 | 122.3007 | 0.054932 | -0.009155 | 122.5388 | 122.4243 | 122.3694 | -0.21515 | 122.4701 | 122.4747 | 122.3969 | -0.23804
3343.4531 | 122.6578 | -122.3969 | 0.086975 | 0.0074006 | -0.016665 | 0.017628 | 0.03346 | -0.00922 | -0.03616 | -0.019046 | 7.627e-05 | 0.012226 | -0.0072353 | -0.096111 | -0.012783 | -0.00081178 | 0.041199 | -0.082397 | -0.027466 | 0.009155 | 0.15564 | 0.009155 | -0.12817 | -0.041199 | 0.009155 | -0.064087 | 0.073242 | 0.073242 | -0.068665 | -0.13733 | 122.406 | 122.2687 | 0.068665 | 122.3145 | 122.406 | 0.13733 | -0.045776 | 122.3282 | 122.2595 | -0.013733 | 122.3557 | 122.3328 | 0.073242 | -0.013733 | 122.5525 | 122.4381 | 122.3694 | -0.21515 | 122.4701 | 122.4701 | 122.406 | -0.2243
3345.1719 | 122.6486 | -122.3923 | 0.082397 | -0.0078584 | -0.01581 | 0.018269 | 0.036878 | -0.0079382 | -0.036801 | -0.020115 | 7.627e-05 | 0.013721 | -0.0074491 | -0.096325 | -0.012783 | 0.0013244 | 0.004578 | -0.10071 | -0.027466 | 0.013733 | 0.13733 | 0 | -0.13275 | -0.07782 | -0.004578 | -0.10071 | 0.09613 | 0.073242 | -0.059509 | -0.13275 | 122.3923 | 122.2595 | 0.054932 | 122.2916 | 122.406 | 0.14648 | -0.077819 | 122.3328 | 122.2595 | 0.013733 | 122.3145 | 122.2916 | 0.032043 | -0.009155 | 122.5296 | 122.3969 | 122.3648 | -0.21515 | 122.4884 | 122.4655 | 122.3877 | -0.21515
3346.9688 | 122.5296 | -122.4289 | 0.12817 | -0.00022891 | -0.022219 | 0.017842 | 0.038373 | -0.010502 | -0.042141 | -0.020755 | -0.0075532 | 0.0096622 | -0.0076627 | -0.097393 | -0.01791 | 0.002179 | 0.10071 | 0.068665 | 0.10986 | 0.082397 | 0.091553 | 0.036621 | -0.09613 | 0.022888 | 0.10071 | 0.036621 | 0.059509 | 0.041199 | -0.041199 | -0.11444 | 122.4655 | 122.3328 | -0.036621 | 122.4976 | 122.5113 | 0.17853 | -0.027466 | 122.3877 | 122.3145 | -0.068665 | 122.4518 | 122.4655 | 0.15106 | -0.086975 | 122.5204 | 122.5296 | 122.5388 | -0.2243 | 122.4884 | 122.4701 | 122.5296 | -0.24262
3348.7656 | 122.6852 | -122.4014 | 0.082397 | -0.00022891 | -0.017733 | 0.01891 | 0.034955 | -0.010288 | -0.035946 | -0.019687 | -0.0075532 | 0.012012 | -0.0057401 | -0.095257 | -0.013424 | 0.00068362 | 0.032043 | -0.050354 | -0.022888 | 0.018311 | 0.15564 | 0.009155 | -0.12817 | -0.045776 | 0.004578 | -0.086975 | 0.09613 | 0.073242 | -0.054932 | -0.1236 | 122.4106 | 122.2733 | 0.073243 | 122.3511 | 122.4197 | 0.14649 | -0.050354 | 122.3465 | 122.2778 | 0.013733 | 122.3557 | 122.3145 | 0.036621 | -0.009155 | 122.5571 | 122.4335 | 122.3785 | -0.21057 | 122.4976 | 122.4747 | 122.406 | -0.20599
3350.5 | 122.5204 | -121.9482 | 0.36163 | -0.0078584 | -0.017519 | 0.016133 | 0.035596 | -0.0049474 | -0.037442 | -0.023746 | 0.0077058 | 0.22948 | 0.23886 | -0.1461 | -0.011929 | 0.046399 | 0.068665 | -0.045776 | 0 | 0.036621 | 0.18768 | 0.022888 | -0.11902 | 0.10071 | 0.20599 | 0.10986 | 0.35706 | 0.32959 | 0.11444 | 0.054932 | 121.9711 | 121.8292 | -0.17395 | 121.9025 | 121.9849 | 0.15564 | -0.29297 | 122.0627 | 122.0032 | -0.004577 | 122.0489 | 122.0581 | 0.054931 | -0.032043 | 122.1359 | 122.0169 | 121.9482 | -0.48065 | 122.3053 | 122.2778 | 122.1542 | -0.3067
3352.2812 | 119.7144 | -91.1819 | 28.3218 | -0.00022891 | 0.035032 | -0.032573 | 0.037732 | -0.17478 | -0.038083 | 0.13433 | -0.0075532 | 7.0022 | 7.0137 | -1.0798 | -0.16424 | 1.1218 | 0.28381 | 0.25177 | 0.32959 | 0.24261 | 0.27008 | 0.16022 | 0.018311 | 0.20599 | 18.1503 | 14.5477 | 23.0804 | 22.9156 | 8.963 | 8.8486 | 91.3422 | 91.2003 | -28.0518 | 91.4337 | 91.4246 | 0.2243 | -28.038 | 100.145 | 100.0305 | -5.2414 | 91.3879 | 105.7297 | 5.6992 | -5.4062 | 91.452 | 91.4658 | 91.5115 | -28.3035 | 114.2624 | 114.0976 | 109.3323 | -19.4733
3354.0781 | 122.1451 | -121.6003 | 0.24261 | 0.0074006 | -0.012179 | 0.01421 | 0.036237 | -0.033359 | -0.035519 | -0.011356 | 7.627e-05 | 0.17073 | 0.27646 | -0.11128 | -0.013424 | 0.013501 | 0.086975 | 0.004578 | 0.045776 | 0.054932 | 0.14648 | 0.009155 | -0.13733 | -0.009155 | 0.16937 | 0.027466 | 0.21973 | 0.21057 | 0.045776 | -0.027466 | 121.6095 | 121.463 | -0.096131 | 121.6049 | 121.6553 | 0.19226 | -0.15564 | 121.6461 | 121.5729 | -0.022888 | 121.5912 | 121.6278 | 0.054932 | -0.032044 | 121.7468 | 121.6873 | 121.6461 | -0.37994 | 121.8201 | 121.8109 | 121.7697 | -0.27008
3355.7969 | 122.0673 | -121.3898 | 0.50354 | -0.0078584 | -0.020296 | 0.017415 | 0.037518 | -0.036136 | -0.045132 | -0.0077245 | 0.0077058 | 0.3568 | 0.6159 | -0.1288 | -0.016842 | 0.032941 | 0.09613 | 0.073242 | 0.10986 | 0.073242 | 0.11902 | 0.032043 | -0.10986 | 0.059509 | 0.35706 | 0.25177 | 0.35706 | 0.36163 | 0.21515 | 0.12817 | 121.4218 | 121.2799 | -0.38452 | 121.463 | 121.463 | 0.18311 | -0.40741 | 121.6049 | 121.5179 | -0.14648 | 121.4493 | 121.6415 | 0.1236 | -0.14191 | 121.5088 | 121.4859 | 121.4996 | -0.6134 | 121.7468 | 121.7514 | 121.7468 | -0.37537
3357.5938 | 122.2137 | -122.0123 | 0.1236 | -0.0078584 | -0.017306 | 0.01656 | 0.037732 | -0.027591 | -0.039364 | -0.01392 | 0.0077058 | 0.019275 | 0.0083591 | -0.099316 | -0.01556 | 0.0011108 | 0.027466 | -0.054932 | -0.018311 | 0 | 0.16022 | -0.013733 | -0.15106 | -0.082397 | 0.027466 | -0.082397 | 0.091553 | 0.082397 | -0.073242 | -0.13275 | 121.9986 | 121.8613 | 0.036621 | 121.9574 | 122.0123 | 0.15106 | -0.09613 | 121.9391 | 121.8796 | -0.032043 | 121.9299 | 121.9299 | 0.050354 | -0.041199 | 122.1725 | 122.0398 | 121.994 | -0.27466 | 122.1039 | 122.0947 | 122.0398 | -0.25635
3359.3906 | 122.1176 | -121.8933 | 0.21057 | -0.0078584 | -0.019228 | 0.018055 | 0.040936 | -0.030369 | -0.042569 | -0.011142 | 0.015335 | 0.070758 | 0.10598 | -0.10658 | -0.017269 | 0.0064514 | 0.050354 | 0.018311 | 0.082397 | 0.050354 | 0.11444 | 0.032043 | -0.10529 | -0.009155 | 0.1236 | 0.041199 | 0.11902 | 0.10529 | 0 | -0.068665 | 121.9254 | 121.788 | -0.09613 | 121.9116 | 121.9437 | 0.15564 | -0.16022 | 121.8933 | 121.8246 | -0.091552 | 121.8842 | 121.9345 | 0.10986 | -0.10529 | 122.0078 | 121.9437 | 121.9757 | -0.31586 | 122.0123 | 121.9986 | 122.0169 | -0.27924
3361.1719 | 122.3145 | -121.9803 | 0.09613 | -0.00022891 | -0.014742 | 0.015706 | 0.037305 | -0.03165 | -0.035305 | -0.014133 | 7.627e-05 | 0.024829 | 0.012632 | -0.099529 | -0.012356 | -0.00081178 | 0.045776 | -0.059509 | -0.009155 | 0.027466 | 0.15106 | -0.013733 | -0.13733 | -0.068665 | 0.041199 | -0.059509 | 0.10529 | 0.09613 | -0.073242 | -0.12817 | 121.9666 | 121.843 | 0.054932 | 121.9208 | 122.0078 | 0.16479 | -0.050354 | 121.907 | 121.8521 | 0.009156 | 121.9116 | 121.9208 | 0.068665 | 0 | 122.1313 | 122.0261 | 121.9711 | -0.23346 | 122.0856 | 122.0764 | 122.0215 | -0.2243
3362.9062 | 122.2595 | -122.049 | 0.10986 | -0.0078584 | -0.023501 | 0.017628 | 0.037305 | -0.029514 | -0.045346 | -0.014774 | -0.0075532 | 0.017353 | 0.0070773 | -0.10081 | -0.017056 | 0.0034608 | 0.064087 | 0.013733 | 0.073242 | 0.073242 | 0.11902 | 0.018311 | -0.10529 | 0.018311 | 0.12817 | 0.041199 | 0.054932 | 0.050354 | -0.041199 | -0.09613 | 122.0673 | 121.9437 | 0.009156 | 122.0627 | 122.1222 | 0.17853 | -0.045776 | 122.0078 | 121.9528 | -0.054931 | 122.0673 | 122.0901 | 0.13733 | -0.059509 | 122.168 | 122.113 | 122.1222 | -0.21515 | 122.1039 | 122.0993 | 122.1771 | -0.20599
3364.6875 | 122.3419 | -122.0261 | 0.07782 | -0.00022891 | -0.016024 | 0.015706 | 0.037518 | -0.030582 | -0.034024 | -0.013492 | 7.627e-05 | 0.024402 | 0.0081455 | -0.099316 | -0.013638 | 0.00068362 | 0.086975 | -0.027466 | 0.013733 | 0.041199 | 0.16022 | -0.009155 | -0.12817 | -0.004578 | 0.068665 | -0.045776 | 0.07782 | 0.086975 | -0.068665 | -0.11902 | 122.0169 | 121.8979 | 0.082397 | 121.9986 | 122.0673 | 0.16937 | 0.009155 | 121.9574 | 121.907 | 0 | 122.0215 | 121.9803 | 0.073243 | 0.009155 | 122.1863 | 122.113 | 122.0398 | -0.20599 | 122.1039 | 122.113 | 122.0947 | -0.19684
3366.4688 | 122.2183 | -122.0444 | 0.15564 | -0.015487 | -0.017946 | 0.017842 | 0.039227 | -0.030582 | -0.040005 | -0.014347 | 7.627e-05 | 0.061145 | 0.079496 | -0.10081 | -0.016842 | 0.0070924 | 0.045776 | -0.045776 | 0.013733 | 0.009155 | 0.13275 | -0.013733 | -0.12817 | -0.059509 | 0.073242 | -0.036621 | 0.14191 | 0.15564 | -0.045776 | -0.10071 | 122.0306 | 121.9162 | -0.022889 | 121.9986 | 122.0535 | 0.13733 | -0.10986 | 121.9986 | 121.9437 | -0.013733 | 121.9849 | 122.0078 | 0.064087 | 0 | 122.1771 | 122.0901 | 122.0581 | -0.28381 | 122.1863 | 122.2 | 122.1176 | -0.25635
3368.25 | 122.2549 | -122.1176 | 0.13733 | -0.0078584 | -0.022219 | 0.017842 | 0.035382 | -0.032291 | -0.042569 | -0.011997 | 7.627e-05 | 0.017353 | 0.0068637 | -0.098675 | -0.016842 | 0.0047424 | 0.073242 | 0.009155 | 0.068665 | 0.050354 | 0.11444 | 0.022888 | -0.10071 | -0.004578 | 0.091553 | 0.009155 | 0.059509 | 0.050354 | -0.045776 | -0.09613 | 122.1405 | 122.0169 | -0.022888 | 122.1268 | 122.168 | 0.15106 | -0.064087 | 122.0718 | 122.0215 | -0.07782 | 122.113 | 122.1268 | 0.10528 | -0.086975 | 122.2321 | 122.1909 | 122.1863 | -0.23804 | 122.1771 | 122.168 | 122.2092 | -0.23346
3370.0469 | 122.1817 | -122.0901 | 0.10071 | -0.0078584 | -0.017946 | 0.016987 | 0.0388 | -0.030369 | -0.039151 | -0.013492 | 0.0077058 | 0.019702 | 0.010495 | -0.1038 | -0.014492 | 0.0030334 | 0.045776 | -0.045776 | 0.018311 | 0.004578 | 0.16022 | -0.004578 | -0.13733 | -0.059509 | 0.036621 | -0.07782 | 0.10529 | 0.086975 | -0.082397 | -0.13733 | 122.0856 | 121.9528 | 0.059509 | 122.0444 | 122.0947 | 0.14191 | -0.054932 | 122.0078 | 121.9528 | 0.004578 | 122.0306 | 122.0123 | 0.059509 | -0.013733 | 122.2504 | 122.1359 | 122.1085 | -0.23804 | 122.1954 | 122.1771 | 122.1268 | -0.23804
3371.7812 | 122.2687 | -122.1268 | 0.13733 | 0.0074006 | -0.018801 | 0.018055 | 0.039868 | -0.02866 | -0.04086 | -0.016697 | 7.627e-05 | 0.01778 | 0.0079319 | -0.10466 | -0.015133 | 0.0026062 | 0.11902 | 0.10986 | 0.13275 | 0.073242 | 0.086975 | 0.027466 | -0.09613 | 0.059509 | 0.18768 | 0.064087 | 0.036621 | 0.041199 | -0.045776 | -0.10071 | 122.1542 | 122.0306 | -0.050354 | 122.2366 | 122.2 | 0.16937 | -0.01831 | 122.081 | 122.0261 | -0.10071 | 122.1863 | 122.1909 | 0.1648 | -0.09613 | 122.2137 | 122.2458 | 122.2595 | -0.23346 | 122.1634 | 122.168 | 122.3145 | -0.23804
3373.5781 | 122.3602 | -122.1222 | 0.12817 | -0.0078584 | -0.018374 | 0.013783 | 0.035596 | -0.028019 | -0.03616 | -0.011142 | 7.627e-05 | 0.019916 | 0.0064365 | -0.10038 | -0.010861 | 0.00068362 | 0.16022 | 0.059509 | 0.11444 | 0.10071 | 0.09613 | 0.045776 | -0.082397 | 0.07782 | 0.12817 | 0.064087 | 0.050354 | 0.045776 | -0.022888 | -0.10071 | 122.168 | 122.0398 | -0.032044 | 122.1817 | 122.2229 | 0.18311 | 0.032043 | 122.0993 | 122.0215 | -0.07782 | 122.2 | 122.1863 | 0.1648 | -0.082398 | 122.2183 | 122.2824 | 122.2366 | -0.21057 | 122.1725 | 122.168 | 122.2504 | -0.22888
3375.3594 | 122.4152 | -122.1039 | 0.10986 | -0.00022891 | -0.018801 | 0.015706 | 0.033032 | -0.031437 | -0.034665 | -0.010502 | -0.0075532 | 0.020984 | 0.0066501 | -0.10017 | -0.011715 | 0.0013244 | 0.10986 | 0.032043 | 0.07782 | 0.064087 | 0.11444 | 0.036621 | -0.09613 | 0.050354 | 0.12817 | 0.036621 | 0.073242 | 0.036621 | -0.032043 | -0.086975 | 122.1405 | 122.0078 | 0.004578 | 122.1359 | 122.168 | 0.16022 | 0 | 122.0718 | 122.0169 | -0.036621 | 122.1542 | 122.1405 | 0.1236 | -0.073242 | 122.2183 | 122.2137 | 122.1817 | -0.20599 | 122.1771 | 122.1405 | 122.2321 | -0.19684
3377.0781 | 122.438 | -122.1313 | 0.09613 | 0.01503 | -0.018374 | 0.016133 | 0.034528 | -0.032932 | -0.036374 | -0.012638 | -0.015182 | 0.022693 | 0.010495 | -0.10188 | -0.0097924 | 0.0026062 | 0.068665 | -0.013733 | 0.018311 | 0.027466 | 0.13275 | 0.018311 | -0.11902 | 0.041199 | 0.082397 | 0.004578 | 0.054932 | 0.050354 | -0.027466 | -0.10986 | 122.1497 | 122.0123 | 0.036621 | 122.1176 | 122.1588 | 0.14649 | -0.027465 | 122.1039 | 122.0215 | -0.041198 | 122.1725 | 122.1359 | 0.11444 | -0.045776 | 122.2641 | 122.2 | 122.1497 | -0.21515 | 122.1863 | 122.1817 | 122.2137 | -0.20599
3378.875 | 122.2778 | -122.1588 | 0.14191 | -0.0078584 | -0.015597 | 0.01891 | 0.040723 | -0.032291 | -0.039364 | -0.014347 | 7.627e-05 | 0.02013 | 0.010068 | -0.1006 | -0.016628 | 0.003247 | 0.10071 | 0.086975 | 0.11444 | 0.10071 | 0.10529 | 0.022888 | -0.1236 | 0.018311 | 0.14648 | 0.013733 | 0.073242 | 0.059509 | -0.032043 | -0.11444 | 122.1817 | 122.0352 | -0.036621 | 122.2458 | 122.2595 | 0.2243 | -0.041199 | 122.1268 | 122.0444 | -0.068665 | 122.1771 | 122.1725 | 0.12817 | -0.082398 | 122.2641 | 122.2595 | 122.2733 | -0.2655 | 122.2321 | 122.2183 | 122.3053 | -0.25635
3380.6562 | 122.4106 | -122.1268 | 0.086975 | -0.0078584 | -0.014315 | 0.016346 | 0.036664 | -0.030369 | -0.033169 | -0.010502 | 7.627e-05 | 0.022052 | 0.011564 | -0.097179 | -0.011929 | -0.00059818 | 0.11444 | 0.027466 | 0.059509 | 0.050354 | 0.13275 | 0.004578 | -0.13275 | -0.018311 | 0.064087 | -0.054932 | 0.07782 | 0.059509 | -0.064087 | -0.13733 | 122.1313 | 121.994 | 0.045776 | 122.1542 | 122.1771 | 0.18311 | 0.027466 | 122.0627 | 121.9894 | -0.009155 | 122.1085 | 122.0718 | 0.082397 | -0.027466 | 122.2595 | 122.2412 | 122.1863 | -0.21973 | 122.2046 | 122.1863 | 122.1909 | -0.2243
3382.4531 | 122.3785 | -121.6187 | 0.54016 | -0.0078584 | -0.01816 | 0.015492 | 0.035596 | -0.033573 | -0.034024 | -0.011142 | -0.0075532 | 0.39504 | 0.7052 | -0.14119 | -0.015133 | 0.047894 | 0.09613 | 0.022888 | 0.036621 | 0.054932 | 0.15564 | -0.009155 | -0.10986 | -0.022888 | 0.27466 | 0.16479 | 0.46234 | 0.44403 | 0.21973 | 0.15106 | 121.6095 | 121.5088 | -0.38452 | 121.6415 | 121.6736 | 0.16479 | -0.44403 | 121.8384 | 121.7697 | -0.07782 | 121.5958 | 121.7834 | 0.013733 | -0.09613 | 121.7743 | 121.7148 | 121.6553 | -0.65002 | 122.081 | 122.0627 | 121.8933 | -0.3891
3384.1875 | 122.4335 | -122.1497 | 0.09613 | -0.00022891 | -0.016238 | 0.016346 | 0.034955 | -0.030369 | -0.035946 | -0.01157 | 7.627e-05 | 0.025043 | 0.0094273 | -0.10038 | -0.011715 | 0.004956 | 0.036621 | -0.091553 | -0.036621 | 0.004578 | 0.15106 | 0 | -0.14648 | -0.054932 | 0 | -0.091553 | 0.082397 | 0.086975 | -0.059509 | -0.14191 | 122.1497 | 122.0032 | 0.054932 | 122.0581 | 122.1542 | 0.15106 | -0.059509 | 122.0901 | 122.0078 | -0.013733 | 122.0947 | 122.0581 | 0.050354 | -0.009155 | 122.3007 | 122.1863 | 122.113 | -0.24261 | 122.2321 | 122.2366 | 122.1497 | -0.23804
3385.9688 | 122.3419 | -122.2321 | 0.13733 | -0.00022891 | -0.020296 | 0.018696 | 0.034955 | -0.0293 | -0.043423 | -0.016056 | -0.0075532 | 0.018634 | 0.0070773 | -0.10295 | -0.015774 | 0.0051698 | 0.086975 | 0.064087 | 0.09613 | 0.073242 | 0.09613 | 0.032043 | -0.10071 | 0.018311 | 0.10986 | 0.018311 | 0.041199 | 0.054932 | -0.041199 | -0.10071 | 122.2641 | 122.1313 | -0.041199 | 122.2961 | 122.3053 | 0.17395 | -0.050354 | 122.1909 | 122.1313 | -0.09613 | 122.2504 | 122.2504 | 0.11902 | -0.082397 | 122.3282 | 122.319 | 122.3282 | -0.23804 | 122.2733 | 122.287 | 122.3419 | -0.23804
3387.75 | 122.4747 | -122.1588 | 0.10529 | -0.015487 | -0.016878 | 0.015919 | 0.036237 | -0.028873 | -0.037442 | -0.012211 | 7.627e-05 | 0.021839 | 0.0087863 | -0.10081 | -0.014706 | 0.0017518 | 0.032043 | -0.022888 | 0 | 0.027466 | 0.15106 | 0 | -0.14648 | -0.050354 | 0.064087 | -0.054932 | 0.10986 | 0.068665 | -0.073242 | -0.11902 | 122.1588 | 122.0123 | 0.045776 | 122.1359 | 122.1863 | 0.17395 | -0.073243 | 122.0856 | 122.0398 | 0.004577 | 122.1085 | 122.1039 | 0.064087 | -0.036621 | 122.3099 | 122.1909 | 122.1588 | -0.25177 | 122.2687 | 122.2275 | 122.2229 | -0.22431
3389.4844 | 122.4197 | -122.1313 | 0.16937 | -0.0078584 | -0.020937 | 0.017628 | 0.035169 | -0.028019 | -0.039151 | -0.014347 | 7.627e-05 | 0.089771 | 0.14785 | -0.10978 | -0.015133 | 0.013715 | 0.11444 | 0.09613 | 0.14191 | 0.10071 | 0.09613 | 0.045776 | -0.09613 | 0.050354 | 0.15564 | 0.091553 | 0.12817 | 0.10986 | 0.032043 | -0.041199 | 122.1771 | 122.0352 | -0.073243 | 122.2275 | 122.2321 | 0.19684 | -0.054932 | 122.1634 | 122.0901 | -0.041199 | 122.1817 | 122.2229 | 0.13275 | -0.05951 | 122.2275 | 122.2458 | 122.2733 | -0.2655 | 122.2595 | 122.2412 | 122.287 | -0.21057
3391.2656 | 122.3785 | -122.2046 | 0.12817 | -0.0078584 | -0.01816 | 0.018269 | 0.040082 | -0.026523 | -0.037655 | -0.015842 | 0.0077058 | 0.022907 | 0.011136 | -0.10124 | -0.015133 | 0.0017518 | 0.027466 | -0.059509 | -0.004578 | 0 | 0.13733 | 0.004578 | -0.14648 | -0.082397 | 0.022888 | -0.091553 | 0.11444 | 0.091553 | -0.09613 | -0.11902 | 122.2092 | 122.0581 | 0.009155 | 122.1451 | 122.2046 | 0.14648 | -0.10071 | 122.1085 | 122.0856 | -0.013733 | 122.1222 | 122.113 | 0.027466 | -0.036621 | 122.3419 | 122.2321 | 122.2 | -0.27466 | 122.319 | 122.2961 | 122.2275 | -0.24719
3393 | 122.374 | -122.2229 | 0.14191 | -0.00022891 | -0.019228 | 0.015706 | 0.038587 | -0.029514 | -0.039364 | -0.014347 | 7.627e-05 | 0.020557 | 0.0096409 | -0.097607 | -0.016415 | 0.00047002 | 0.07782 | 0 | 0.041199 | 0.073242 | 0.13275 | 0.018311 | -0.1236 | -0.050354 | 0.064087 | -0.054932 | 0.068665 | 0.086975 | -0.054932 | -0.11444 | 122.2412 | 122.0993 | -0.009156 | 122.2229 | 122.2961 | 0.19684 | -0.064087 | 122.168 | 122.1085 | -0.073242 | 122.1725 | 122.168 | 0.059509 | -0.054932 | 122.3557 | 122.3007 | 122.2641 | -0.2655 | 122.2916 | 122.3099 | 122.287 | -0.25635
3394.7969 | 122.4884 | -122.1909 | 0.09613 | -0.00022891 | -0.013888 | 0.015706 | 0.0388 | -0.026737 | -0.037014 | -0.014774 | -0.0075532 | 0.020984 | 0.013059 | -0.098034 | -0.014279 | 0.00047002 | 0.054932 | -0.059509 | -0.013733 | 0.004578 | 0.15564 | -0.004578 | -0.13275 | -0.054932 | 0.054932 | -0.082397 | 0.10529 | 0.082397 | -0.073242 | -0.13275 | 122.1863 | 122.0581 | 0.05951 | 122.1313 | 122.1954 | 0.13733 | -0.041198 | 122.1176 | 122.0581 | 0.009156 | 122.1359 | 122.1085 | 0.050354 | -0.013733 | 122.3465 | 122.2458 | 122.1771 | -0.22888 | 122.2961 | 122.2733 | 122.2458 | -0.22888
3396.5938 | 122.5159 | -122.2183 | 0.07782 | 0.0074006 | -0.017519 | 0.015278 | 0.03346 | -0.028446 | -0.034665 | -0.013065 | 7.627e-05 | 0.02013 | 0.013059 | -0.099102 | -0.011288 | 0.0013244 | 0.032043 | -0.054932 | -0.013733 | 0.013733 | 0.15106 | 0.004578 | -0.12817 | -0.032043 | 0.004578 | -0.07782 | 0.091553 | 0.064087 | -0.054932 | -0.1236 | 122.2229 | 122.0901 | 0.073242 | 122.1634 | 122.2321 | 0.14191 | -0.045777 | 122.1634 | 122.0947 | 0.013733 | 122.1863 | 122.1405 | 0.045776 | -0.013733 | 122.3694 | 122.2504 | 122.2046 | -0.20599 | 122.3099 | 122.2824 | 122.2229 | -0.20142
3398.3906 | 122.3465 | -122.2229 | 0.17395 | -0.0078584 | -0.015169 | 0.017842 | 0.039227 | -0.031223 | -0.042141 | -0.012851 | -0.015182 | 0.019275 | 0.031217 | -0.09782 | -0.015988 | 0.003888 | 0.1236 | 0.064087 | 0.11444 | 0.091553 | 0.082397 | 0.041199 | -0.086975 | 0.068665 | 0.13733 | 0.027466 | 0.054932 | 0.054932 | -0.027466 | -0.09613 | 122.2641 | 122.1359 | -0.091553 | 122.287 | 122.3145 | 0.17853 | -0.050354 | 122.1954 | 122.1268 | -0.11902 | 122.2916 | 122.2504 | 0.1236 | -0.11902 | 122.3053 | 122.3465 | 122.3373 | -0.26092 | 122.2778 | 122.2778 | 122.3602 | -0.27008
3400.1094 | 122.4243 | -121.8887 | 0.32501 | -0.0078584 | -0.019228 | 0.016987 | 0.03346 | -0.027164 | -0.036587 | -0.013706 | 0.0077058 | 0.33821 | 0.74472 | -0.11705 | -0.015774 | 0.020978 | 0.10071 | 0.032043 | 0.073242 | 0.073242 | 0.11444 | 0.022888 | -0.09613 | 0.054932 | 0.16022 | 0.036621 | 0.22888 | 0.20599 | 0.064087 | -0.004578 | 121.9116 | 121.7926 | -0.21057 | 121.9208 | 121.962 | 0.16937 | -0.2243 | 121.9528 | 121.8842 | -0.09613 | 121.9437 | 121.9254 | 0.041199 | -0.11902 | 122.0032 | 121.9894 | 121.962 | -0.42114 | 122.1176 | 122.0947 | 122.049 | -0.32959
3401.9062 | 122.2641 | -121.6736 | 0.47607 | -0.015487 | -0.016024 | 0.016987 | 0.035169 | -0.029941 | -0.032956 | -0.013279 | 7.627e-05 | 0.32412 | 1.1707 | -0.13563 | -0.013851 | 0.042767 | 0.09613 | 0.013733 | 0.018311 | 0.045776 | 0.12817 | 0.004578 | -0.1236 | -0.018311 | 0.07782 | -0.068665 | 0.3479 | 0.32959 | 0.11444 | 0.045776 | 121.6782 | 121.55 | -0.3479 | 121.6873 | 121.7194 | 0.16937 | -0.37994 | 121.788 | 121.7194 | -0.12817 | 121.6553 | 121.6049 | -0.11444 | -0.14648 | 121.8018 | 121.7697 | 121.6919 | -0.59967 | 122.0215 | 122.0032 | 121.7514 | -0.4303
3403.6562 | 122.2229 | -121.2936 | 0.72784 | -0.00022891 | -0.016024 | 0.015065 | 0.034955 | -0.026523 | -0.037655 | -0.012638 | -0.015182 | 0.54821 | 2.0641 | -0.16298 | -0.018978 | 0.070111 | 0.10986 | 0.045776 | 0.041199 | 0.054932 | 0.15106 | 0.013733 | -0.11902 | 0.004578 | 0.16937 | -0.032043 | 0.51727 | 0.5127 | 0.27008 | 0.20599 | 121.3074 | 121.1746 | -0.57678 | 121.3394 | 121.3486 | 0.17395 | -0.61798 | 121.5637 | 121.4996 | -0.21057 | 121.2982 | 121.2616 | -0.23804 | -0.21515 | 121.4447 | 121.4035 | 121.3348 | -0.84686 | 121.8109 | 121.8063 | 121.463 | -0.52185
3405.4531 | 121.8842 | -120.9137 | 1.0437 | -0.00022891 | -0.01816 | 0.016346 | 0.042218 | -0.027378 | -0.040219 | -0.016269 | -0.0075532 | 0.83361 | 2.854 | -0.179 | -0.028805 | 0.10237 | 0.027466 | -0.022888 | 0.036621 | 0.018311 | 0.15106 | -0.004578 | -0.13275 | -0.073242 | 0.14191 | -0.032043 | 0.737 | 0.69122 | 0.3479 | 0.30212 | 120.9091 | 120.7809 | -0.89264 | 120.8908 | 120.932 | 0.15106 | -1.0162 | 121.2616 | 121.2158 | -0.3067 | 120.8405 | 120.8817 | -0.33417 | -0.35248 | 121.0648 | 120.9412 | 120.9503 | -1.1765 | 121.6507 | 121.6049 | 121.0556 | -0.74158
3407.2344 | 121.788 | -121.3348 | 0.15564 | -0.0078584 | -0.01816 | 0.015706 | 0.038587 | -0.029941 | -0.035092 | -0.014133 | -0.0075532 | 0.047046 | 0.12201 | -0.10188 | -0.014492 | 0.010724 | 0.009155 | -0.091553 | -0.045776 | -0.013733 | 0.14191 | 0.009155 | -0.14191 | -0.013733 | 0.004578 | -0.12817 | 0.11444 | 0.1236 | -0.036621 | -0.11444 | 121.344 | 121.1929 | -0.013733 | 121.2433 | 121.3211 | 0.12817 | -0.14649 | 121.2982 | 121.2204 | -0.041199 | 121.3211 | 121.2067 | -0.013733 | -0.032044 | 121.4767 | 121.344 | 121.2891 | -0.29755 | 121.4493 | 121.4584 | 121.3394 | -0.27008
3409.0469 | 121.8796 | -121.7148 | 0.11902 | -0.015487 | -0.022219 | 0.019551 | 0.035382 | -0.030796 | -0.045132 | -0.01392 | 7.627e-05 | 0.013507 | 0.010282 | -0.10231 | -0.014492 | 0.0030334 | 0.10071 | 0.11444 | 0.13733 | 0.10071 | 0.09613 | 0.022888 | -0.10986 | 0.036621 | 0.19226 | 0.073242 | 0.050354 | 0.045776 | -0.032043 | -0.086975 | 121.7377 | 121.6049 | -0.022889 | 121.8292 | 121.8155 | 0.21057 | -0.018311 | 121.6827 | 121.6278 | -0.068665 | 121.7514 | 121.788 | 0.16022 | -0.073243 | 121.8109 | 121.8155 | 121.8521 | -0.22888 | 121.7651 | 121.7606 | 121.907 | -0.20599
3410.8281 | 122.1222 | -121.8155 | 0.091553 | -0.0078584 | -0.016878 | 0.016774 | 0.038373 | -0.030369 | -0.034237 | -0.015201 | 7.627e-05 | 0.019275 | 0.013059 | -0.098888 | -0.011715 | 0.0030334 | 0.036621 | -0.064087 | -0.022888 | 0.018311 | 0.15106 | 0.009155 | -0.14648 | -0.041199 | 0 | -0.086975 | 0.10071 | 0.064087 | -0.064087 | -0.12817 | 121.8246 | 121.669 | 0.059509 | 121.7514 | 121.8338 | 0.16479 | -0.054932 | 121.7514 | 121.6873 | 0.009155 | 121.7743 | 121.7285 | 0.041199 | -0.027466 | 121.9666 | 121.8521 | 121.7926 | -0.23804 | 121.9162 | 121.8796 | 121.8155 | -0.21973
3412.5625 | 122.1634 | -121.8567 | 0.086975 | -0.00022891 | -0.017519 | 0.016346 | 0.037946 | -0.028019 | -0.037442 | -0.012211 | 7.627e-05 | 0.01778 | 0.01135 | -0.099743 | -0.015133 | 0.0026062 | 0.091553 | 0.009155 | 0.073242 | 0.059509 | 0.13733 | 0.032043 | -0.11902 | 0.041199 | 0.1236 | 0.027466 | 0.054932 | 0.050354 | -0.036621 | -0.10529 | 121.8887 | 121.7377 | 0.050354 | 121.8658 | 121.9162 | 0.17853 | 0.004578 | 121.8201 | 121.7514 | -0.032043 | 121.8979 | 121.8842 | 0.13275 | -0.036621 | 121.994 | 121.9482 | 121.9299 | -0.20599 | 121.9116 | 121.907 | 121.9803 | -0.19226
3414.3594 | 122.1909 | -121.9162 | 0.10071 | -0.00022891 | -0.020083 | 0.018055 | 0.03645 | -0.027591 | -0.037869 | -0.012424 | -0.0075532 | 0.016925 | 0.011564 | -0.10167 | -0.014492 | 0.0015382 | 0.11444 | 0.054932 | 0.086975 | 0.073242 | 0.10986 | 0.045776 | -0.086975 | 0.064087 | 0.11902 | 0.032043 | 0.036621 | 0.050354 | -0.027466 | -0.091553 | 121.962 | 121.8292 | 0.009155 | 121.9711 | 121.9894 | 0.16022 | 0.013733 | 121.8887 | 121.8246 | -0.064087 | 121.9803 | 121.9482 | 0.1236 | -0.050354 | 122.0261 | 122.0306 | 122.0032 | -0.18768 | 121.9528 | 121.9666 | 122.0352 | -0.19226
3416.0781 | 122.1313 | -121.9345 | 0.1236 | 0.0074006 | -0.027346 | 0.019551 | 0.0388 | -0.029087 | -0.044064 | -0.014774 | 0.0077058 | 0.014576 | 0.011991 | -0.10017 | -0.016842 | 0.004956 | 0.027466 | 0.027466 | 0.073242 | 0.064087 | 0.1236 | 0.018311 | -0.11444 | 0.004578 | 0.10071 | 0.018311 | 0.054932 | 0.059509 | -0.032043 | -0.10071 | 121.9528 | 121.8201 | 0 | 121.962 | 121.9986 | 0.17853 | -0.09613 | 121.9025 | 121.8338 | -0.068664 | 121.9391 | 121.9528 | 0.11902 | -0.064087 | 122.0581 | 121.962 | 122.0078 | -0.23804 | 121.9894 | 121.994 | 122.0352 | -0.2243
3417.8438 | 122.1542 | -121.962 | 0.13275 | -0.023117 | -0.019228 | 0.019551 | 0.038373 | -0.029087 | -0.040646 | -0.016269 | 0.0077058 | 0.015216 | 0.014554 | -0.10316 | -0.017697 | 0.0041016 | 0.15106 | 0.11444 | 0.15106 | 0.10071 | 0.09613 | 0.036621 | -0.091553 | 0.059509 | 0.17395 | 0.068665 | 0.036621 | 0.032043 | -0.027466 | -0.091553 | 121.9986 | 121.8704 | -0.036621 | 122.0764 | 122.0627 | 0.19226 | 0.018311 | 121.9345 | 121.8704 | -0.09613 | 122.0215 | 122.0306 | 0.16022 | -0.10071 | 122.0581 | 122.113 | 122.113 | -0.2243 | 121.9986 | 121.994 | 122.1359 | -0.2243
3419.6562 | 122.1909 | -121.994 | 0.11902 | -0.00022891 | -0.019442 | 0.019551 | 0.040082 | -0.028873 | -0.04086 | -0.015842 | -0.0075532 | 0.01543 | 0.016263 | -0.10017 | -0.015347 | 0.00089722 | 0.10529 | 0.054932 | 0.10529 | 0.09613 | 0.10071 | 0.027466 | -0.11902 | 0.064087 | 0.15106 | 0.054932 | 0.068665 | 0.045776 | -0.027466 | -0.10529 | 122.0215 | 121.875 | -0.018311 | 122.049 | 122.0901 | 0.21515 | -0.013733 | 121.9666 | 121.8887 | -0.050354 | 122.0581 | 122.049 | 0.16022 | -0.073243 | 122.0947 | 122.0993 | 122.0993 | -0.23804 | 122.0627 | 122.0398 | 122.1451 | -0.22431
3421.3906 | 122.1313 | -121.994 | 0.13275 | -0.00022891 | -0.018374 | 0.016774 | 0.036664 | -0.02631 | -0.03851 | -0.015842 | 7.627e-05 | 0.014576 | 0.01605 | -0.10081 | -0.013638 | 0.0015382 | 0.11902 | 0.09613 | 0.12817 | 0.10986 | 0.10986 | 0.050354 | -0.10986 | 0.022888 | 0.14648 | 0.004578 | 0.059509 | 0.045776 | -0.036621 | -0.10529 | 122.0444 | 121.8842 | -0.022888 | 122.0901 | 122.1039 | 0.21973 | -0.013732 | 121.9574 | 121.8887 | -0.073242 | 122.0169 | 121.9986 | 0.10986 | -0.086975 | 122.1039 | 122.113 | 122.1222 | -0.24261 | 122.0535 | 122.0398 | 122.1405 | -0.23804
3423.1875 | 122.2137 | -122.0032 | 0.10071 | -0.015487 | -0.019015 | 0.017201 | 0.037946 | -0.029514 | -0.040432 | -0.015629 | 0.0077058 | 0.01778 | 0.0137 | -0.10359 | -0.014492 | 0.00068362 | 0.10529 | 0.064087 | 0.10986 | 0.10071 | 0.10529 | 0.036621 | -0.10529 | 0.064087 | 0.15564 | 0.064087 | 0.059509 | 0.045776 | -0.032043 | -0.082397 | 122.0398 | 121.8979 | 0.004578 | 122.0673 | 122.1039 | 0.20599 | 0.004578 | 121.9711 | 121.9208 | -0.041199 | 122.0673 | 122.0673 | 0.14648 | -0.054932 | 122.1085 | 122.1085 | 122.113 | -0.20599 | 122.0627 | 122.049 | 122.1588 | -0.18311
3424.9219 | 122.2961 | -122.0169 | 0.091553 | -0.00022891 | -0.01581 | 0.017842 | 0.031964 | -0.029728 | -0.035519 | -0.016269 | 7.627e-05 | 0.020984 | 0.015836 | -0.098888 | -0.010861 | 0.00047002 | 0.14648 | 0.07782 | 0.091553 | 0.082397 | 0.10071 | 0.045776 | -0.11902 | 0.082397 | 0.1236 | 0.018311 | 0.064087 | 0.027466 | -0.032043 | -0.10529 | 122.0627 | 121.8979 | 0.009155 | 122.0947 | 122.0993 | 0.20142 | 0.054931 | 121.9849 | 121.9116 | -0.027466 | 122.0993 | 122.0352 | 0.1236 | -0.064087 | 122.1176 | 122.1634 | 122.1085 | -0.21057 | 122.081 | 122.0444 | 122.1405 | -0.19684
3426.7188 | 122.2321 | -122.0169 | 0.11444 | -0.0078584 | -0.020724 | 0.01891 | 0.040723 | -0.028873 | -0.040219 | -0.01456 | -0.0075532 | 0.015003 | 0.016477 | -0.10209 | -0.019406 | 0.00047002 | 0.10986 | 0.091553 | 0.10986 | 0.082397 | 0.10529 | 0.027466 | -0.10071 | 0.073242 | 0.15106 | 0.050354 | 0.059509 | 0.041199 | -0.027466 | -0.10529 | 122.0444 | 121.9162 | -0.009155 | 122.1085 | 122.0993 | 0.18311 | -0.004578 | 121.9894 | 121.9116 | -0.054932 | 122.0901 | 122.0673 | 0.15564 | -0.073242 | 122.1222 | 122.1268 | 122.1268 | -0.21515 | 122.0764 | 122.0581 | 122.168 | -0.21973
3428.5156 | 122.3419 | -122.0352 | 0.091553 | 0.0074006 | -0.018801 | 0.014424 | 0.035809 | -0.02866 | -0.034665 | -0.011997 | -0.0075532 | 0.019062 | 0.013913 | -0.098888 | -0.010861 | -0.00038438 | 0.10071 | -0.013733 | 0.032043 | 0.032043 | 0.11902 | 0.032043 | -0.11902 | 0.064087 | 0.10986 | -0.009155 | 0.054932 | 0.045776 | -0.022888 | -0.09613 | 122.0673 | 121.9162 | 0.027466 | 122.0215 | 122.0673 | 0.15106 | 0.009155 | 122.0123 | 121.9391 | -0.036621 | 122.0993 | 122.0261 | 0.086975 | -0.045777 | 122.1542 | 122.1359 | 122.0673 | -0.21057 | 122.0901 | 122.081 | 122.1451 | -0.18768
3430.3125 | 122.2137 | -122.081 | 0.11902 | 0.0074006 | -0.023073 | 0.01656 | 0.036664 | -0.026951 | -0.039792 | -0.013706 | 7.627e-05 | 0.017139 | 0.015622 | -0.098888 | -0.01791 | 0.0011108 | 0.091553 | 0.027466 | 0.068665 | 0.054932 | 0.11902 | 0.022888 | -0.09613 | 0.022888 | 0.10071 | 0 | 0.059509 | 0.050354 | -0.036621 | -0.10071 | 122.1039 | 121.9849 | 0 | 122.1085 | 122.1359 | 0.15106 | -0.027466 | 122.0444 | 121.9803 | -0.05951 | 122.1039 | 122.081 | 0.10071 | -0.068665 | 122.2 | 122.1725 | 122.1497 | -0.21515 | 122.1405 | 122.1313 | 122.1817 | -0.21973
3432.0938 | 122.3648 | -122.049 | 0.09613 | 0.0074006 | -0.019869 | 0.015919 | 0.033246 | -0.02866 | -0.03616 | -0.013065 | 0.0077058 | 0.019275 | 0.016904 | -0.098888 | -0.011288 | 0.00068362 | 0.15106 | 0.07782 | 0.10529 | 0.091553 | 0.09613 | 0.050354 | -0.10071 | 0.082397 | 0.14191 | 0.036621 | 0.041199 | 0.036621 | -0.018311 | -0.09613 | 122.0993 | 121.9482 | 0 | 122.1268 | 122.1405 | 0.19226 | 0.054932 | 122.0306 | 121.9528 | -0.054931 | 122.1313 | 122.0856 | 0.13275 | -0.059509 | 122.1451 | 122.2 | 122.1542 | -0.19684 | 122.0901 | 122.0856 | 122.1909 | -0.19226
3433.8125 | 122.2824 | -121.9666 | 0.14648 | -0.015487 | -0.016451 | 0.016133 | 0.038373 | -0.029728 | -0.032528 | -0.012851 | 7.627e-05 | 0.088916 | 0.24933 | -0.10466 | -0.014279 | 0.0085876 | 0.059509 | -0.054932 | 0.013733 | 0.041199 | 0.14648 | -0.018311 | -0.14648 | -0.027466 | 0.086975 | -0.059509 | 0.14191 | 0.10529 | -0.032043 | -0.091553 | 121.9482 | 121.8201 | 0 | 121.9116 | 122.0078 | 0.18768 | -0.086975 | 121.9345 | 121.875 | -0.004577 | 121.9391 | 121.907 | 0.032044 | -0.041198 | 122.113 | 122.0261 | 121.9803 | -0.29297 | 122.1085 | 122.0718 | 122.0535 | -0.23804
3435.6094 | 122.3877 | -122.0627 | 0.07782 | -0.0078584 | -0.017092 | 0.016133 | 0.037946 | -0.0293 | -0.035946 | -0.012851 | 7.627e-05 | 0.021411 | 0.014341 | -0.099102 | -0.013424 | 0.0015382 | 0.10071 | 0.013733 | 0.036621 | 0.054932 | 0.14191 | 0.004578 | -0.13733 | 0.018311 | 0.07782 | -0.050354 | 0.068665 | 0.068665 | -0.07782 | -0.1236 | 122.0673 | 121.9254 | 0.064087 | 122.0764 | 122.1176 | 0.19226 | 0.022888 | 121.9849 | 121.9391 | -0.009155 | 122.081 | 122.0123 | 0.073242 | -0.009155 | 122.2046 | 122.1634 | 122.0993 | -0.21515 | 122.1313 | 122.1313 | 122.1405 | -0.20142
3437.4062 | 122.3465 | -122.0856 | 0.091553 | -0.00022891 | -0.014529 | 0.01656 | 0.037091 | -0.029728 | -0.036587 | -0.012211 | -0.015182 | 0.020343 | 0.014554 | -0.098247 | -0.012997 | 0.002179 | 0.10071 | -0.009155 | 0.032043 | 0.027466 | 0.13275 | 0.013733 | -0.13733 | -0.018311 | 0.050354 | -0.10071 | 0.082397 | 0.050354 | -0.068665 | -0.11902 | 122.0993 | 121.9482 | 0.041198 | 122.0764 | 122.113 | 0.16479 | 0.009155 | 122.0169 | 121.9666 | -0.009156 | 122.0673 | 121.9849 | 0.018311 | -0.041199 | 122.2183 | 122.1863 | 122.1176 | -0.22888 | 122.168 | 122.1359 | 122.1359 | -0.21057
3439.2031 | 122.406 | -122.081 | 0.11444 | -0.00022891 | -0.013888 | 0.01421 | 0.036664 | -0.028019 | -0.037869 | -0.01456 | -0.0075532 | 0.019702 | 0.014341 | -0.099956 | -0.016201 | 0.0015382 | 0.059509 | -0.027466 | 0.009155 | 0.041199 | 0.13733 | -0.013733 | -0.14648 | -0.032043 | 0.091553 | -0.041199 | 0.09613 | 0.07782 | -0.059509 | -0.14648 | 122.0673 | 121.9345 | 0.022888 | 122.0535 | 122.1222 | 0.18768 | -0.054932 | 122.0215 | 121.9345 | -0.018311 | 122.049 | 122.0398 | 0.10529 | -0.036621 | 122.2183 | 122.1405 | 122.0901 | -0.26093 | 122.1771 | 122.1588 | 122.1725 | -0.26093
3440.9219 | 122.374 | -122.0993 | 0.082397 | 0.0074006 | -0.016451 | 0.015706 | 0.036664 | -0.0293 | -0.034665 | -0.012851 | 0.0077058 | 0.019275 | 0.015622 | -0.098247 | -0.014919 | 0.0026062 | 0.10071 | -0.013733 | 0.018311 | 0.045776 | 0.11444 | 0.013733 | -0.14648 | -0.022888 | 0.059509 | -0.068665 | 0.07782 | 0.07782 | -0.068665 | -0.12817 | 122.113 | 121.9528 | 0.032044 | 122.0856 | 122.1451 | 0.19226 | 0.018311 | 122.0306 | 121.9711 | -0.004577 | 122.0764 | 122.0306 | 0.059509 | -0.004577 | 122.2137 | 122.2 | 122.1176 | -0.22888 | 122.1771 | 122.1771 | 122.1588 | -0.21057
3442.7031 | 122.2824 | -122.1451 | 0.13733 | -0.0078584 | -0.018374 | 0.019337 | 0.038159 | -0.029087 | -0.041287 | -0.016269 | 7.627e-05 | 0.016284 | 0.014768 | -0.099102 | -0.018551 | 0.0023926 | 0.082397 | 0.086975 | 0.11444 | 0.09613 | 0.10071 | 0.036621 | -0.10071 | -0.009155 | 0.13733 | 0.013733 | 0.059509 | 0.050354 | -0.050354 | -0.11902 | 122.1817 | 122.0444 | -0.036621 | 122.2321 | 122.2412 | 0.19684 | -0.054932 | 122.0947 | 122.0261 | -0.07782 | 122.1359 | 122.1588 | 0.13275 | -0.086975 | 122.2458 | 122.2275 | 122.2595 | -0.23804 | 122.2046 | 122.1954 | 122.2824 | -0.25635
3444.5156 | 122.4197 | -122.113 | 0.11444 | -0.0078584 | -0.018374 | 0.015919 | 0.034314 | -0.028019 | -0.035519 | -0.011997 | 0.0077058 | 0.018848 | 0.017545 | -0.098675 | -0.012356 | 0.0026062 | 0.022888 | -0.036621 | -0.013733 | 0 | 0.14648 | 0.013733 | -0.12817 | -0.036621 | 0.027466 | -0.064087 | 0.09613 | 0.073242 | -0.082397 | -0.13275 | 122.1268 | 121.9849 | 0.032043 | 122.0764 | 122.113 | 0.12817 | -0.091553 | 122.0306 | 121.9803 | -0.018311 | 122.0764 | 122.049 | 0.068664 | -0.041199 | 122.2595 | 122.1359 | 122.0993 | -0.24262 | 122.2092 | 122.1863 | 122.1405 | -0.24719
3446.2969 | 122.4106 | -122.1313 | 0.09613 | -0.00022891 | -0.012179 | 0.016346 | 0.0388 | -0.029087 | -0.034878 | -0.013706 | 0.0077058 | 0.02013 | 0.019254 | -0.099316 | -0.013424 | 0.00025642 | 0.064087 | 0.032043 | 0.036621 | 0.050354 | 0.13733 | 0.004578 | -0.11902 | 0.013733 | 0.09613 | -0.036621 | 0.091553 | 0.064087 | -0.059509 | -0.11902 | 122.1359 | 122.0123 | 0.041199 | 122.1634 | 122.1817 | 0.16937 | -0.032043 | 122.0718 | 122.0123 | -0.004577 | 122.1451 | 122.0947 | 0.082398 | -0.032043 | 122.2687 | 122.1954 | 122.168 | -0.21515 | 122.2229 | 122.1954 | 122.2275 | -0.21515
3448.0781 | 122.3465 | -122.1588 | 0.10071 | 0.01503 | -0.020296 | 0.018055 | 0.03645 | -0.030582 | -0.039151 | -0.014133 | -0.0075532 | 0.017566 | 0.014127 | -0.10102 | -0.01556 | 0.0023926 | 0.009155 | -0.036621 | -0.018311 | 0.013733 | 0.14648 | -0.009155 | -0.15106 | -0.091553 | 0.036621 | -0.068665 | 0.10529 | 0.10071 | -0.07782 | -0.13733 | 122.1497 | 122.0078 | 0.045776 | 122.1222 | 122.1725 | 0.16479 | -0.091553 | 122.081 | 122.0215 | 0.004578 | 122.0673 | 122.0901 | 0.068664 | 0 | 122.3053 | 122.168 | 122.1405 | -0.25177 | 122.2641 | 122.2595 | 122.1954 | -0.23804
3449.875 | 122.3419 | -122.1817 | 0.11902 | 0.0074006 | -0.019228 | 0.017415 | 0.040509 | -0.028873 | -0.04321 | -0.016056 | 7.627e-05 | 0.01308 | 0.016904 | -0.10167 | -0.016842 | 0.0030334 | 0.10986 | 0.11902 | 0.13733 | 0.10986 | 0.086975 | 0.032043 | -0.10071 | 0.050354 | 0.19226 | 0.054932 | 0.050354 | 0.054932 | -0.032043 | -0.082397 | 122.2137 | 122.081 | -0.032044 | 122.3007 | 122.2916 | 0.21057 | -0.009156 | 122.1497 | 122.0993 | -0.068665 | 122.2321 | 122.2366 | 0.13733 | -0.064087 | 122.2687 | 122.2916 | 122.319 | -0.21973 | 122.2321 | 122.2366 | 122.374 | -0.20142
3451.6719 | 122.4106 | -122.1771 | 0.086975 | -0.0078584 | -0.016451 | 0.015278 | 0.03645 | -0.02866 | -0.032956 | -0.012851 | 7.627e-05 | 0.021625 | 0.016263 | -0.098675 | -0.010861 | 0.0019654 | 0.091553 | -0.022888 | 0.018311 | 0.041199 | 0.12817 | 0.018311 | -0.12817 | -0.032043 | 0.050354 | -0.082397 | 0.091553 | 0.082397 | -0.073242 | -0.13275 | 122.1954 | 122.049 | 0.041199 | 122.1542 | 122.2183 | 0.16937 | 0.004578 | 122.1039 | 122.0444 | 0.004578 | 122.1451 | 122.0947 | 0.050354 | -0.004578 | 122.3053 | 122.2687 | 122.1954 | -0.21515 | 122.2687 | 122.2595 | 122.2275 | -0.21973
3453.3906 | 122.3282 | -122.2229 | 0.14648 | -0.00022891 | -0.021151 | 0.018269 | 0.03645 | -0.030582 | -0.041928 | -0.014133 | -0.0075532 | 0.014362 | 0.014554 | -0.099956 | -0.01556 | 0.0028198 | 0.11902 | 0.054932 | 0.10529 | 0.07782 | 0.086975 | 0.045776 | -0.091553 | 0.018311 | 0.11902 | 0.027466 | 0.050354 | 0.050354 | -0.032043 | -0.073242 | 122.2687 | 122.1313 | -0.059509 | 122.2778 | 122.3007 | 0.16937 | -0.027465 | 122.1909 | 122.1497 | -0.09613 | 122.2412 | 122.2504 | 0.10071 | -0.09613 | 122.3099 | 122.3419 | 122.3282 | -0.23804 | 122.2733 | 122.2733 | 122.3419 | -0.21973
3455.1719 | 122.4747 | -122.1542 | 0.086975 | 0.0074006 | -0.019228 | 0.015706 | 0.034955 | -0.031437 | -0.03851 | -0.013492 | -0.0075532 | 0.019062 | 0.013486 | -0.097607 | -0.013851 | 0.0023926 | 0.091553 | -0.022888 | 0.032043 | 0.032043 | 0.1236 | 0.018311 | -0.1236 | 0.027466 | 0.10071 | 0.009155 | 0.082397 | 0.045776 | -0.036621 | -0.10071 | 122.1725 | 122.0306 | 0.036621 | 122.1313 | 122.1863 | 0.15564 | 0.004578 | 122.1176 | 122.0535 | -0.004578 | 122.1817 | 122.1634 | 0.10986 | -0.041199 | 122.2778 | 122.2458 | 122.1863 | -0.21057 | 122.2366 | 122.2 | 122.2549 | -0.18768
3456.9688 | 122.4014 | -122.1909 | 0.11902 | -0.0078584 | -0.019228 | 0.02126 | 0.039655 | -0.02866 | -0.041287 | -0.016483 | -0.0075532 | 0.014148 | 0.014768 | -0.10295 | -0.015988 | 0.0041016 | 0.045776 | 0.027466 | 0.091553 | 0.054932 | 0.11444 | 0.036621 | -0.091553 | 0.022888 | 0.12817 | 0.050354 | 0.073242 | 0.045776 | -0.064087 | -0.10529 | 122.2275 | 122.0993 | -0.004578 | 122.2183 | 122.2458 | 0.14649 | -0.073243 | 122.1268 | 122.0856 | -0.045777 | 122.2137 | 122.2412 | 0.15564 | -0.073243 | 122.3053 | 122.2366 | 122.2824 | -0.21057 | 122.2641 | 122.2366 | 122.319 | -0.22431
3458.7031 | 122.3648 | -122.2275 | 0.13275 | -0.015487 | -0.018587 | 0.018055 | 0.036237 | -0.029941 | -0.039578 | -0.014774 | 7.627e-05 | 0.016071 | 0.012845 | -0.10124 | -0.012997 | 0.0013244 | 0.1236 | 0.082397 | 0.11902 | 0.07782 | 0.07782 | 0.050354 | -0.09613 | 0.059509 | 0.12817 | 0.027466 | 0.041199 | 0.045776 | -0.027466 | -0.10529 | 122.2778 | 122.1313 | -0.054931 | 122.3099 | 122.3053 | 0.17395 | -0.009155 | 122.2 | 122.1222 | -0.091552 | 122.287 | 122.2549 | 0.13275 | -0.086975 | 122.3053 | 122.3511 | 122.3465 | -0.22888 | 122.2687 | 122.2733 | 122.3557 | -0.23804
3460.5 | 122.4609 | -122.1909 | 0.082397 | -0.0078584 | -0.01581 | 0.016133 | 0.034955 | -0.025669 | -0.032101 | -0.013065 | 0.0077058 | 0.020984 | 0.016904 | -0.099529 | -0.012997 | 4.2822e-05 | 0.11902 | 0.018311 | 0.050354 | 0.059509 | 0.13275 | -0.004578 | -0.13275 | 0.004578 | 0.07782 | -0.054932 | 0.07782 | 0.073242 | -0.054932 | -0.12817 | 122.1863 | 122.0581 | 0.050354 | 122.2092 | 122.2504 | 0.19226 | 0.036622 | 122.1359 | 122.0627 | -0.004577 | 122.1954 | 122.1359 | 0.073242 | -0.009155 | 122.3236 | 122.3099 | 122.2412 | -0.21515 | 122.2687 | 122.2641 | 122.2687 | -0.21057
3462.2969 | 122.4701 | -122.1954 | 0.068665 | 0.01503 | -0.014742 | 0.014424 | 0.038373 | -0.029941 | -0.034237 | -0.012424 | 0.0077058 | 0.019062 | 0.017759 | -0.099316 | -0.014706 | -0.00038438 | 0.11444 | 0.013733 | 0.036621 | 0.059509 | 0.12817 | -0.009155 | -0.13275 | -0.004578 | 0.09613 | -0.045776 | 0.073242 | 0.073242 | -0.068665 | -0.1236 | 122.1863 | 122.0627 | 0.059509 | 122.2092 | 122.2549 | 0.19226 | 0.045776 | 122.1268 | 122.0718 | 0.004577 | 122.1909 | 122.1497 | 0.07782 | 0.004577 | 122.3236 | 122.3099 | 122.2321 | -0.20142 | 122.2687 | 122.2687 | 122.2916 | -0.19226
3464.0781 | 122.3785 | -122.2458 | 0.13275 | -0.00022891 | -0.022646 | 0.018483 | 0.035596 | -0.03165 | -0.044064 | -0.016269 | 0.0077058 | 0.013507 | 0.012632 | -0.10038 | -0.01556 | 0.0051698 | 0.068665 | 0.027466 | 0.064087 | 0.059509 | 0.10529 | 0.036621 | -0.09613 | -0.009155 | 0.086975 | 0.022888 | 0.068665 | 0.050354 | -0.045776 | -0.086975 | 122.2824 | 122.1497 | -0.027465 | 122.2733 | 122.3053 | 0.15564 | -0.064086 | 122.2 | 122.1588 | -0.064086 | 122.2366 | 122.2687 | 0.10986 | -0.082397 | 122.3511 | 122.3145 | 122.3099 | -0.22888 | 122.3145 | 122.2961 | 122.3328 | -0.21973
3465.8125 | 122.4426 | -122.2092 | 0.091553 | -0.0078584 | -0.016451 | 0.016774 | 0.034955 | -0.028446 | -0.034451 | -0.013706 | -0.0075532 | 0.020557 | 0.015622 | -0.09782 | -0.011501 | 0.0015382 | 0.11902 | 0.018311 | 0.036621 | 0.041199 | 0.13733 | 0.022888 | -0.1236 | 0 | 0.068665 | -0.059509 | 0.082397 | 0.064087 | -0.045776 | -0.11444 | 122.2321 | 122.0856 | 0.045776 | 122.2275 | 122.2504 | 0.16479 | 0.027466 | 122.1634 | 122.0947 | -0.009156 | 122.2092 | 122.1497 | 0.054932 | -0.027466 | 122.3465 | 122.3282 | 122.2458 | -0.21515 | 122.2916 | 122.2733 | 122.2778 | -0.20599
3467.6094 | 122.4243 | -122.2412 | 0.09613 | -0.00022891 | -0.019655 | 0.017415 | 0.040509 | -0.029728 | -0.042569 | -0.014774 | 7.627e-05 | 0.014148 | 0.014768 | -0.10081 | -0.021114 | 0.00089722 | 0.091553 | 0.07782 | 0.1236 | 0.082397 | 0.12817 | 0.045776 | -0.11444 | 0.059509 | 0.15106 | 0.059509 | 0.041199 | 0.045776 | -0.036621 | -0.09613 | 122.287 | 122.1268 | 0.032044 | 122.319 | 122.3236 | 0.19684 | -0.004577 | 122.2046 | 122.1451 | -0.054931 | 122.3007 | 122.3007 | 0.15564 | -0.050354 | 122.3694 | 122.3328 | 122.3648 | -0.21057 | 122.2824 | 122.287 | 122.3923 | -0.19226
3469.3438 | 122.4426 | -122.2275 | 0.086975 | 0.0074006 | -0.018801 | 0.019551 | 0.036664 | -0.028232 | -0.039151 | -0.016483 | 7.627e-05 | 0.016925 | 0.01605 | -0.098675 | -0.014492 | 0.0013244 | 0.036621 | -0.045776 | -0.018311 | 0.004578 | 0.14191 | -0.022888 | -0.14648 | -0.068665 | 0.032043 | -0.086975 | 0.09613 | 0.082397 | -0.073242 | -0.14191 | 122.2046 | 122.081 | 0.054932 | 122.1817 | 122.2321 | 0.15106 | -0.050354 | 122.1542 | 122.0856 | 0.009155 | 122.1588 | 122.1405 | 0.054932 | -0.004578 | 122.3694 | 122.2641 | 122.2092 | -0.23346 | 122.3236 | 122.3099 | 122.2595 | -0.22888
3471.125 | 122.4335 | -122.2549 | 0.12817 | -0.00022891 | -0.020937 | 0.02126 | 0.037091 | -0.032291 | -0.04321 | -0.013279 | 0.0077058 | 0.013507 | 0.013913 | -0.10231 | -0.017483 | 0.0034608 | 0.064087 | 0.045776 | 0.10071 | 0.064087 | 0.1236 | 0.032043 | -0.1236 | 0.022888 | 0.13733 | 0.054932 | 0.07782 | 0.036621 | -0.045776 | -0.10529 | 122.287 | 122.1313 | -0.004578 | 122.3007 | 122.319 | 0.18768 | -0.064087 | 122.2092 | 122.1497 | -0.050354 | 122.2778 | 122.3099 | 0.16022 | -0.091553 | 122.3785 | 122.319 | 122.3557 | -0.25177 | 122.3328 | 122.2916 | 122.3923 | -0.23346
3472.9062 | 122.525 | -122.2092 | 0.086975 | -0.0078584 | -0.017306 | 0.014851 | 0.038373 | -0.02866 | -0.035092 | -0.012211 | -0.0075532 | 0.02013 | 0.014982 | -0.099529 | -0.012142 | 4.2822e-05 | 0.041199 | -0.045776 | -0.022888 | 0.009155 | 0.14191 | -0.009155 | -0.14648 | -0.036621 | 0.009155 | -0.068665 | 0.073242 | 0.064087 | -0.059509 | -0.12817 | 122.2 | 122.0627 | 0.054932 | 122.1634 | 122.2183 | 0.15564 | -0.045776 | 122.1497 | 122.081 | -0.013733 | 122.1725 | 122.1405 | 0.059509 | -0.022888 | 122.3511 | 122.2504 | 122.1863 | -0.23346 | 122.2824 | 122.2733 | 122.2183 | -0.21515
3474.7031 | 122.5296 | -122.2092 | 0.086975 | -0.0078584 | -0.014529 | 0.013142 | 0.04115 | -0.029941 | -0.03381 | -0.013279 | -0.0075532 | 0.018421 | 0.020322 | -0.096966 | -0.015774 | -0.00038438 | 0.073242 | -0.018311 | 0.022888 | 0.050354 | 0.13733 | 0 | -0.14648 | -0.018311 | 0.073242 | -0.041199 | 0.07782 | 0.073242 | -0.068665 | -0.11902 | 122.2092 | 122.0627 | 0.050354 | 122.1909 | 122.2595 | 0.19684 | -0.013733 | 122.1405 | 122.0901 | -0.009155 | 122.1909 | 122.168 | 0.07782 | -0.013733 | 122.3465 | 122.2824 | 122.2321 | -0.23346 | 122.287 | 122.2824 | 122.2824 | -0.20599
3476.4375 | 122.5296 | -122.2275 | 0.10529 | -0.0078584 | -0.017519 | 0.017415 | 0.036237 | -0.027805 | -0.038937 | -0.012638 | 7.627e-05 | 0.018634 | 0.017972 | -0.10145 | -0.011288 | 0.0043152 | 0.1236 | 0.041199 | 0.10529 | 0.082397 | 0.11902 | 0.027466 | -0.10071 | 0.050354 | 0.12817 | 0.018311 | 0.064087 | 0.027466 | -0.018311 | -0.091553 | 122.2549 | 122.1268 | 0.013733 | 122.2687 | 122.3099 | 0.18311 | 0.01831 | 122.2092 | 122.1359 | -0.041199 | 122.2778 | 122.2458 | 0.10986 | -0.07782 | 122.3465 | 122.3511 | 122.3328 | -0.20599 | 122.2916 | 122.2549 | 122.3557 | -0.19684
3478.2188 | 122.3648 | -122.0718 | 0.22888 | -0.015487 | -0.019228 | 0.016774 | 0.037946 | -0.029941 | -0.038723 | -0.01392 | 7.627e-05 | 0.15065 | 0.60501 | -0.11961 | -0.017483 | 0.017987 | 0.1236 | 0.07782 | 0.13733 | 0.091553 | 0.10071 | 0.032043 | -0.091553 | 0.10986 | 0.24719 | 0.091553 | 0.17853 | 0.16479 | 0.073242 | 0.022888 | 122.1039 | 121.9803 | -0.12817 | 122.1497 | 122.1634 | 0.18311 | -0.10529 | 122.1451 | 122.0947 | -0.050354 | 122.1817 | 122.1634 | 0.068665 | -0.064087 | 122.1725 | 122.1954 | 122.2092 | -0.32044 | 122.2504 | 122.2366 | 122.319 | -0.20599
3480.0156 | 122.3099 | -122.1313 | 0.20599 | -0.0078584 | -0.017092 | 0.015919 | 0.040296 | -0.0293 | -0.042355 | -0.013706 | -0.022812 | 0.08678 | 0.31512 | -0.11042 | -0.018551 | 0.012647 | 0.10071 | 0.086975 | 0.12817 | 0.09613 | 0.10529 | 0.032043 | -0.10986 | 0.018311 | 0.15106 | 0.009155 | 0.13275 | 0.1236 | -0.004578 | -0.073242 | 122.1634 | 122.0215 | -0.10071 | 122.2183 | 122.2275 | 0.20599 | -0.10529 | 122.1268 | 122.0581 | -0.073243 | 122.1497 | 122.1405 | 0.082397 | -0.082398 | 122.2366 | 122.2321 | 122.2595 | -0.31586 | 122.2641 | 122.2549 | 122.2824 | -0.27924
3481.8125 | 122.4792 | -122.1313 | 0.10529 | 0.0074006 | -0.015597 | 0.015278 | 0.037732 | -0.028019 | -0.035305 | -0.014347 | 7.627e-05 | 0.033374 | 0.071592 | -0.10124 | -0.013638 | 0.002179 | 0.07782 | -0.013733 | 0.022888 | 0.050354 | 0.15106 | 0.004578 | -0.13275 | -0.027466 | 0.091553 | -0.050354 | 0.091553 | 0.09613 | -0.045776 | -0.11444 | 122.1359 | 121.9986 | 0.045776 | 122.1176 | 122.1817 | 0.18311 | -0.027466 | 122.0856 | 122.0169 | -0.013733 | 122.1039 | 122.081 | 0.064087 | -0.009156 | 122.2824 | 122.2092 | 122.1542 | -0.23804 | 122.2229 | 122.2275 | 122.2229 | -0.21973
3483.6094 | 121.8201 | -121.5683 | 0.15564 | -0.00022891 | -0.01581 | 0.01891 | 0.038373 | -0.02631 | -0.038937 | -0.013279 | 7.627e-05 | 0.065418 | 0.14316 | -0.099956 | -0.018765 | 0.0015382 | 0.032043 | -0.045776 | -0.013733 | 0.009155 | 0.14191 | 0 | -0.15564 | -0.036621 | 0.032043 | -0.086975 | 0.11902 | 0.10986 | -0.050354 | -0.1236 | 121.5683 | 121.4127 | -0.013733 | 121.5225 | 121.5775 | 0.16479 | -0.1236 | 121.5179 | 121.4447 | -0.036621 | 121.5317 | 121.4813 | 0.036621 | -0.045777 | 121.7102 | 121.6003 | 121.5546 | -0.31128 | 121.6873 | 121.6782 | 121.6003 | -0.27924
3485.4062 | 122.1863 | -121.8796 | 0.073242 | 0.0074006 | -0.017519 | 0.017201 | 0.035169 | -0.027805 | -0.035305 | -0.016483 | -0.015182 | 0.018421 | 0.013273 | -0.099743 | -0.015133 | -0.00017078 | 0.054932 | -0.036621 | 0 | 0.032043 | 0.14191 | -0.004578 | -0.13275 | -0.032043 | 0.073242 | -0.050354 | 0.086975 | 0.082397 | -0.054932 | -0.11902 | 121.875 | 121.7468 | 0.068665 | 121.843 | 121.9116 | 0.16479 | -0.01831 | 121.8246 | 121.7606 | 0.013733 | 121.8475 | 121.8292 | 0.068665 | 0.009155 | 122.0215 | 121.9345 | 121.8796 | -0.20599 | 121.9666 | 121.962 | 121.9528 | -0.19226
3487.125 | 122.2321 | -121.9482 | 0.091553 | 0.0074006 | -0.013888 | 0.014424 | 0.040082 | -0.0293 | -0.032528 | -0.011356 | -0.0075532 | 0.017566 | 0.015409 | -0.098675 | -0.014065 | 0.00068362 | 0.018311 | -0.11444 | -0.027466 | 0.009155 | 0.14648 | 0 | -0.13275 | -0.050354 | -0.004578 | -0.10529 | 0.07782 | 0.068665 | -0.064087 | -0.13733 | 121.9482 | 121.8155 | 0.054931 | 121.8338 | 121.9574 | 0.14191 | -0.073242 | 121.8842 | 121.8109 | -0.013733 | 121.8979 | 121.843 | 0.032043 | -0.022888 | 122.0947 | 121.9666 | 121.9208 | -0.2243 | 122.0261 | 122.0169 | 121.9437 | -0.22888
3488.9062 | 122.1634 | -122.0261 | 0.13733 | 0.0074006 | -0.018587 | 0.018483 | 0.038159 | -0.0293 | -0.042782 | -0.013492 | 7.627e-05 | 0.0090214 | 0.012845 | -0.10081 | -0.020687 | 0.0047424 | 0.045776 | 0.036621 | 0.07782 | 0.050354 | 0.10986 | 0.032043 | -0.10529 | 0.013733 | 0.10071 | 0 | 0.045776 | 0.059509 | -0.054932 | -0.12817 | 122.0581 | 121.9208 | -0.027466 | 122.0627 | 122.0764 | 0.15564 | -0.091553 | 121.9711 | 121.8979 | -0.091553 | 122.0398 | 122.0261 | 0.12817 | -0.07782 | 122.1359 | 122.0718 | 122.1039 | -0.24262 | 122.0718 | 122.0856 | 122.1268 | -0.2655
3490.6406 | 122.2824 | -122.0261 | 0.082397 | -0.0078584 | -0.015169 | 0.01656 | 0.035382 | -0.030796 | -0.032956 | -0.012851 | -0.0075532 | 0.017566 | 0.013273 | -0.099102 | -0.012356 | 0.0015382 | 0.027466 | -0.064087 | -0.009155 | 0.004578 | 0.15106 | -0.004578 | -0.13733 | -0.086975 | -0.018311 | -0.12817 | 0.082397 | 0.07782 | -0.068665 | -0.15106 | 122.0215 | 121.8887 | 0.068665 | 121.962 | 122.0306 | 0.14191 | -0.054931 | 121.9574 | 121.875 | 0 | 121.9391 | 121.8979 | 0.022888 | -0.004577 | 122.1771 | 122.0535 | 122.0169 | -0.21973 | 122.1085 | 122.1039 | 122.0078 | -0.23346
3492.3594 | 122.2275 | -122.081 | 0.12817 | -0.0078584 | -0.024996 | 0.017628 | 0.035596 | -0.027164 | -0.042355 | -0.01456 | -0.0075532 | 0.01308 | 0.012632 | -0.099956 | -0.01556 | 0.0034608 | 0.050354 | 0.036621 | 0.091553 | 0.041199 | 0.10071 | 0.041199 | -0.086975 | 0.018311 | 0.09613 | 0.009155 | 0.054932 | 0.050354 | -0.036621 | -0.09613 | 122.1222 | 121.994 | -0.027466 | 122.1176 | 122.1222 | 0.12817 | -0.07782 | 122.0444 | 121.9849 | -0.073242 | 122.0993 | 122.0901 | 0.10528 | -0.07782 | 122.1817 | 122.1313 | 122.1725 | -0.21515 | 122.1359 | 122.1313 | 122.1771 | -0.2243
3494.1406 | 122.3282 | -122.0581 | 0.09613 | -0.015487 | -0.014101 | 0.016133 | 0.037305 | -0.0293 | -0.031674 | -0.010502 | 0.0077058 | 0.018634 | 0.014982 | -0.099743 | -0.011929 | -0.0010254 | 0.09613 | -0.013733 | 0.018311 | 0.045776 | 0.13275 | 0.018311 | -0.13733 | -0.018311 | 0.054932 | -0.07782 | 0.07782 | 0.068665 | -0.082397 | -0.11902 | 122.0764 | 121.9208 | 0.036621 | 122.0444 | 122.1039 | 0.18311 | 0 | 121.9757 | 121.9391 | -0.01831 | 122.0398 | 121.9803 | 0.041199 | -0.027465 | 122.1909 | 122.1542 | 122.0764 | -0.23346 | 122.1359 | 122.1268 | 122.113 | -0.21515
3495.8594 | 122.2366 | -122.0535 | 0.15106 | -0.00022891 | -0.017092 | 0.018055 | 0.038159 | -0.028232 | -0.042996 | -0.016483 | 7.627e-05 | 0.017566 | 0.092099 | -0.1006 | -0.019833 | 0.011151 | 0.09613 | 0.054932 | 0.082397 | 0.082397 | 0.10986 | 0.009155 | -0.11444 | 0.082397 | -0.064087 | -0.086975 | 0.10071 | 0.091553 | -0.050354 | -0.10529 | 122.0627 | 121.9391 | -0.041199 | 122.1085 | 122.1359 | 0.19684 | -0.054932 | 122.0032 | 121.9482 | -0.050354 | 122.1359 | 121.9666 | 0.018311 | -0.059509 | 122.1634 | 122.1497 | 122.1359 | -0.2655 | 122.1542 | 122.1451 | 121.9894 | -0.25635
3497.6562 | 122.3145 | -121.8109 | 0.28839 | -0.00022891 | -0.020296 | 0.016133 | 0.034741 | -0.029087 | -0.034665 | -0.011997 | -0.0075532 | 0.1451 | 0.57873 | -0.11641 | -0.016201 | 0.019482 | 0.11902 | 0.050354 | 0.091553 | 0.086975 | 0.091553 | 0.032043 | -0.082397 | 0.059509 | 0.25177 | 0.07782 | 0.18768 | 0.18768 | 0.07782 | 0.013733 | 121.843 | 121.7285 | -0.19684 | 121.8613 | 121.8979 | 0.16937 | -0.16937 | 121.8887 | 121.8246 | -0.10071 | 121.8704 | 121.8887 | 0.064087 | -0.10071 | 121.9025 | 121.9299 | 121.9025 | -0.37079 | 121.9986 | 121.9986 | 122.0627 | -0.27466
3499.4531 | 122.2046 | -122.0718 | 0.11444 | -0.015487 | -0.019015 | 0.017842 | 0.036878 | -0.030796 | -0.043423 | -0.016697 | 7.627e-05 | 0.016712 | 0.031858 | -0.099956 | -0.017483 | 0.0030334 | 0.086975 | 0.07782 | 0.1236 | 0.082397 | 0.10529 | 0.036621 | -0.10529 | 0.050354 | 0.17395 | 0.073242 | 0.054932 | 0.032043 | -0.013733 | -0.082397 | 122.1085 | 121.9666 | -0.009155 | 122.1497 | 122.1542 | 0.18768 | -0.027466 | 122.0581 | 121.9894 | -0.059509 | 122.1222 | 122.1451 | 0.15564 | -0.082398 | 122.1771 | 122.1588 | 122.1954 | -0.21973 | 122.1268 | 122.1039 | 122.2458 | -0.19684
3501.1719 | 122.3785 | -122.2137 | 0.086975 | -0.0078584 | -0.015169 | 0.015492 | 0.037305 | -0.028873 | -0.032528 | -0.013065 | 7.627e-05 | 0.030384 | 0.037626 | -0.095684 | -0.01257 | 4.2822e-05 | 0.041199 | -0.086975 | -0.027466 | 0.013733 | 0.13733 | 0.004578 | -0.14191 | 0.013733 | 0.082397 | -0.036621 | 0.11444 | 0.11444 | -0.054932 | -0.10529 | 122.2183 | 122.0718 | 0.050354 | 122.1268 | 122.2275 | 0.15564 | -0.045776 | 122.1588 | 122.1085 | 0.027466 | 122.2275 | 122.1771 | 0.068665 | 0.027466 | 122.3511 | 122.2549 | 122.1863 | -0.22888 | 122.3282 | 122.3282 | 122.2961 | -0.19226
3502.9531 | 122.2916 | -122.0261 | 0.18768 | -0.00022891 | -0.017733 | 0.01656 | 0.040723 | -0.030155 | -0.03851 | -0.013492 | -0.0075532 | 0.085712 | 0.28949 | -0.1038 | -0.019192 | 0.008374 | 0.018311 | -0.041199 | -0.004578 | -0.004578 | 0.15564 | -0.013733 | -0.14191 | -0.054932 | 0.054932 | -0.050354 | 0.15106 | 0.15106 | -0.018311 | -0.041199 | 122.0123 | 121.8842 | -0.032043 | 121.9849 | 122.0215 | 0.13733 | -0.16937 | 122.0078 | 121.9849 | -0.036621 | 121.9711 | 121.9757 | -0.009155 | -0.036621 | 122.1817 | 122.0444 | 122.0215 | -0.32959 | 122.1771 | 122.1771 | 122.081 | -0.22888
3504.6875 | 122.3511 | -122.0169 | 0.16479 | -0.0078584 | -0.017946 | 0.016987 | 0.034314 | -0.029514 | -0.035092 | -0.012851 | 7.627e-05 | 0.088916 | 0.2474 | -0.10594 | -0.010861 | 0.0077332 | 0.045776 | -0.059509 | 0.032043 | 0.018311 | 0.13733 | 0.018311 | -0.12817 | -0.018311 | 0.064087 | -0.018311 | 0.12817 | 0.10529 | 0 | -0.082397 | 122.0352 | 121.8887 | -0.027466 | 121.9574 | 122.0352 | 0.14649 | -0.11902 | 122.0169 | 121.9345 | -0.036621 | 121.9986 | 121.9986 | 0.064086 | -0.059509 | 122.1542 | 122.0627 | 122.049 | -0.29297 | 122.1451 | 122.1222 | 122.081 | -0.24719
3506.4844 | 122.1542 | -121.9482 | 0.21973 | -0.0078584 | -0.017519 | 0.016987 | 0.038159 | -0.029728 | -0.041073 | -0.015842 | 7.627e-05 | 0.12886 | 0.44928 | -0.11085 | -0.018337 | 0.012647 | 0.09613 | 0.11444 | 0.13275 | 0.09613 | 0.086975 | 0.018311 | -0.1236 | 0.004578 | 0.14191 | 0.10529 | 0.16022 | 0.11902 | 0.018311 | -0.041199 | 121.9666 | 121.8246 | -0.13275 | 122.0627 | 122.0444 | 0.21973 | -0.1236 | 121.9666 | 121.907 | -0.05951 | 121.9528 | 122.0535 | 0.14649 | -0.10071 | 122.0352 | 122.0444 | 122.081 | -0.34332 | 122.1085 | 122.0673 | 122.0901 | -0.26093
3508.2656 | 121.0236 | -120.5887 | 0.16022 | 0.0074006 | -0.016451 | 0.015278 | 0.036023 | -0.029728 | -0.034665 | -0.012638 | 7.627e-05 | 0.16646 | 0.16836 | -0.065136 | -0.17749 | 0.13377 | 0.059509 | -0.045776 | -0.013733 | 0.013733 | 0.14648 | 0.013733 | -0.12817 | 0.013733 | 0.11444 | -0.041199 | 0.09613 | 0.086975 | -0.068665 | -0.15106 | 120.6024 | 120.4605 | -0.013733 | 120.5429 | 120.6024 | 0.14191 | -0.10071 | 120.52 | 120.4376 | -0.064087 | 120.6024 | 120.5475 | 0.10986 | -0.073242 | 120.7352 | 120.6482 | 120.575 | -0.28839 | 120.6848 | 120.6757 | 120.7031 | -0.31128
3510.0469 | 121.2158 | -116.8213 | 4.6097 | -0.00022891 | -0.021578 | 0.019123 | 0.033032 | -0.030369 | -0.040646 | -0.010288 | -0.0075532 | 2.1153 | 7.0137 | -0.31657 | -0.084347 | 0.29463 | 0.1831 | 0.13275 | 0.16479 | 0.12817 | 0.13733 | 0.064087 | -0.064087 | 0.34332 | 0.69122 | 0.10529 | 2.8336 | 2.7328 | 2.2476 | 2.2018 | 116.8854 | 116.7572 | -4.4724 | 116.954 | 116.9495 | 0.19226 | -4.4266 | 119.0689 | 119.0231 | -1.7761 | 117.1646 | 116.9266 | -2.0966 | -1.8768 | 116.9586 | 117.0044 | 116.9861 | -4.6738 | 119.6548 | 119.5541 | 117.5125 | -2.4078
3511.8438 | 121.756 | -121.6599 | 0.12817 | -0.00022891 | -0.020083 | 0.018696 | 0.037091 | -0.029087 | -0.040219 | -0.014988 | -0.0075532 | 0.0049624 | 0.027585 | -0.098247 | -0.017483 | 0.0028198 | 0.082397 | 0.032043 | 0.073242 | 0.041199 | 0.10529 | 0.041199 | -0.10986 | 0.009155 | 0.09613 | 0.009155 | 0.064087 | 0.050354 | -0.050354 | -0.10529 | 121.7011 | 121.55 | -0.022888 | 121.6919 | 121.7011 | 0.15106 | -0.045777 | 121.6095 | 121.5546 | -0.064087 | 121.669 | 121.669 | 0.11444 | -0.07782 | 121.7651 | 121.7422 | 121.7331 | -0.23804 | 121.7239 | 121.7102 | 121.756 | -0.23346
3513.5781 | 122.0535 | -121.6415 | 0.13275 | -0.0078584 | -0.015597 | 0.015492 | 0.036237 | -0.027378 | -0.034237 | -0.015415 | -0.0075532 | 0.035511 | 0.18139 | -0.10167 | -0.012142 | 0.0026062 | 0.10986 | -0.009155 | 0.045776 | 0.059509 | 0.13275 | -0.009155 | -0.13733 | 0 | 0.059509 | -0.041199 | 0.10529 | 0.11902 | -0.036621 | -0.10529 | 121.6324 | 121.5042 | 0 | 121.6324 | 121.7011 | 0.19684 | -0.022888 | 121.6049 | 121.5363 | -0.027465 | 121.6415 | 121.6003 | 0.064087 | -0.013732 | 121.7743 | 121.7514 | 121.6873 | -0.27008 | 121.7468 | 121.7606 | 121.7011 | -0.23804
3515.375 | 122.0123 | -121.7926 | 0.086975 | -0.0078584 | -0.015169 | 0.017201 | 0.033887 | -0.029728 | -0.035946 | -0.013279 | -0.015182 | 0.0073124 | 0.018186 | -0.096538 | -0.012997 | -0.00059818 | 0.022888 | -0.086975 | -0.036621 | -0.004578 | 0.14648 | 0.018311 | -0.14191 | -0.050354 | 0 | -0.10071 | 0.09613 | 0.073242 | -0.068665 | -0.13733 | 121.8109 | 121.6507 | 0.059509 | 121.7056 | 121.788 | 0.13733 | -0.064087 | 121.7239 | 121.6553 | 0.009155 | 121.7422 | 121.6919 | 0.036621 | -0.013733 | 121.9391 | 121.8155 | 121.756 | -0.22888 | 121.8887 | 121.8658 | 121.7926 | -0.2243
3517.1562 | 121.9894 | -121.8018 | 0.12817 | -0.00022891 | -0.023714 | 0.019123 | 0.033673 | -0.029728 | -0.043423 | -0.016269 | 0.015335 | 0.0028262 | 0.013486 | -0.10038 | -0.016201 | 0.0026062 | 0.1236 | 0.10986 | 0.11902 | 0.086975 | 0.11444 | 0.022888 | -0.11444 | 0.068665 | 0.18768 | 0.073242 | 0.064087 | 0.045776 | -0.032043 | -0.10071 | 121.8246 | 121.6873 | -0.013733 | 121.9116 | 121.8887 | 0.20142 | -0.004578 | 121.7697 | 121.7011 | -0.064087 | 121.8704 | 121.875 | 0.17395 | -0.082398 | 121.9162 | 121.9254 | 121.9208 | -0.24262 | 121.8658 | 121.8475 | 121.9894 | -0.22888
3518.9375 | 121.2296 | -118.0618 | 3.2501 | -0.00022891 | -0.02286 | 0.019123 | 0.037732 | -0.03165 | -0.045346 | -0.016483 | -0.0075532 | 2.5499 | 7.0137 | -0.3907 | -0.057644 | 0.30851 | 0.10071 | 0.07782 | 0.11444 | 0.15564 | 0.16937 | 0.07782 | -0.059509 | 0.58136 | 0.93384 | -0.036621 | 2.774 | 2.6733 | 2.124 | 2.0737 | 118.1396 | 118.0023 | -3.0807 | 118.1396 | 118.2175 | 0.21515 | -3.1494 | 120.1859 | 120.1355 | -0.47607 | 118.6432 | 118.0252 | -2.1103 | -0.57678 | 118.2312 | 118.1625 | 118.1763 | -3.3096 | 120.8359 | 120.7352 | 118.9957 | -1.1765
3520.6719 | 121.6141 | -121.4355 | 0.11902 | -0.0078584 | -0.024142 | 0.016987 | 0.035596 | -0.028019 | -0.039364 | -0.017978 | 7.627e-05 | 0.0079532 | 0.010282 | -0.098675 | -0.016628 | 0.0015382 | 0.11444 | 0.068665 | 0.11444 | 0.073242 | 0.091553 | 0.050354 | -0.10529 | 0.045776 | 0.10986 | 0.022888 | 0.054932 | 0.041199 | -0.036621 | -0.09613 | 121.4859 | 121.3303 | -0.027466 | 121.5042 | 121.5088 | 0.17853 | -0.004578 | 121.3989 | 121.3394 | -0.064087 | 121.4813 | 121.4584 | 0.11902 | -0.07782 | 121.5271 | 121.55 | 121.55 | -0.22431 | 121.4905 | 121.4767 | 121.5454 | -0.21515
3522.4531 | 121.8887 | -121.6049 | 0.086975 | -0.0078584 | -0.01581 | 0.01656 | 0.037732 | -0.028446 | -0.030392 | -0.013279 | -0.0075532 | 0.01308 | 0.015622 | -0.096966 | -0.011929 | -0.00081178 | 0.1236 | 0.013733 | 0.041199 | 0.045776 | 0.11444 | 0 | -0.15564 | 0 | 0.064087 | -0.054932 | 0.073242 | 0.073242 | -0.050354 | -0.10986 | 121.6049 | 121.4493 | 0.027466 | 121.6187 | 121.6507 | 0.20142 | 0.036621 | 121.5546 | 121.4951 | -0.013733 | 121.6049 | 121.55 | 0.054931 | -0.013733 | 121.7194 | 121.7285 | 121.6461 | -0.24261 | 121.6782 | 121.6782 | 121.669 | -0.19684
3524.25 | 121.8933 | -121.637 | 0.09613 | -0.0078584 | -0.014315 | 0.018055 | 0.035169 | -0.030369 | -0.035733 | -0.0096471 | 0.0077058 | 0.010517 | 0.015622 | -0.096538 | -0.01321 | 0.0017518 | 0.022888 | -0.082397 | -0.032043 | 0 | 0.14191 | -0.018311 | -0.14191 | -0.064087 | 0.009155 | -0.11444 | 0.091553 | 0.07782 | -0.064087 | -0.14191 | 121.6187 | 121.4951 | 0.045777 | 121.5546 | 121.637 | 0.14191 | -0.073242 | 121.5729 | 121.4951 | -0.004577 | 121.5729 | 121.5225 | 0.027466 | -0.01831 | 121.7789 | 121.6599 | 121.6049 | -0.23804 | 121.7285 | 121.7148 | 121.6461 | -0.23804
3525.9688 | 121.8704 | -121.7377 | 0.12817 | -0.0078584 | -0.023073 | 0.017842 | 0.035809 | -0.032291 | -0.042782 | -0.014133 | 0.0077058 | 0.0094486 | 0.014341 | -0.097179 | -0.014492 | 0.0015382 | 0.09613 | 0.059509 | 0.11444 | 0.054932 | 0.10986 | 0.027466 | -0.11902 | 0.041199 | 0.09613 | 0.009155 | 0.054932 | 0.050354 | -0.041199 | -0.091553 | 121.7651 | 121.6187 | -0.018311 | 121.7972 | 121.7926 | 0.17395 | -0.032044 | 121.6965 | 121.6461 | -0.073242 | 121.7789 | 121.7468 | 0.10071 | -0.07782 | 121.8475 | 121.8338 | 121.8521 | -0.24719 | 121.7926 | 121.788 | 121.8338 | -0.21973
3527.75 | 121.5317 | -121.3486 | 0.11902 | -0.00022891 | -0.022433 | 0.017842 | 0.036664 | -0.028019 | -0.03851 | -0.012211 | 7.627e-05 | 0.013294 | 0.012204 | -0.096966 | -0.017269 | 0.0030334 | 0.14191 | 0.073242 | 0.12817 | 0.086975 | 0.10529 | 0.041199 | -0.09613 | 0.068665 | 0.12817 | 0.032043 | 0.032043 | 0.054932 | -0.041199 | -0.086975 | 121.3898 | 121.2524 | -0.013733 | 121.4218 | 121.4355 | 0.1831 | 0.022888 | 121.3074 | 121.2616 | -0.086976 | 121.4172 | 121.3806 | 0.11902 | -0.064087 | 121.4539 | 121.4905 | 121.4767 | -0.21515 | 121.3806 | 121.4035 | 121.4767 | -0.20599
3529.5469 | 121.7743 | -121.5775 | 0.10529 | -0.0078584 | -0.017733 | 0.015065 | 0.037518 | -0.0293 | -0.036587 | -0.01392 | 0.0077058 | 0.02013 | 0.031644 | -0.095043 | -0.022396 | 0.006665 | 0.15564 | 0.068665 | 0.1236 | 0.091553 | 0.07782 | 0.054932 | -0.086975 | 0.073242 | 0.12817 | 0.032043 | 0.027466 | 0.022888 | -0.041199 | -0.091553 | 121.6324 | 121.4905 | -0.027466 | 121.6461 | 121.669 | 0.17853 | 0.050354 | 121.5363 | 121.4859 | -0.07782 | 121.6507 | 121.6095 | 0.1236 | -0.082398 | 121.6553 | 121.7331 | 121.7011 | -0.19226 | 121.6049 | 121.6003 | 121.7056 | -0.19684
3531.3438 | 121.5042 | -121.4767 | 0.12817 | -0.00022891 | -0.01581 | 0.017201 | 0.037518 | -0.031009 | -0.03851 | -0.013065 | 7.627e-05 | -0.0052914 | 0.0025913 | -0.093334 | -0.015347 | -0.0010254 | 0.13733 | 0.082397 | 0.11902 | 0.086975 | 0.10529 | 0.050354 | -0.09613 | 0.073242 | 0.1236 | 0.032043 | 0.073242 | 0.045776 | -0.036621 | -0.068665 | 121.5271 | 121.3806 | -0.022888 | 121.5591 | 121.5637 | 0.1831 | 0.009155 | 121.4401 | 121.4081 | -0.054932 | 121.55 | 121.5088 | 0.10071 | -0.082398 | 121.582 | 121.6141 | 121.5958 | -0.2243 | 121.55 | 121.5225 | 121.6003 | -0.19684
3533.125 | 121.6553 | -121.5546 | 0.12817 | -0.00022891 | -0.018374 | 0.015919 | 0.035809 | -0.028873 | -0.041073 | -0.014774 | -0.0075532 | -0.0059322 | 0.0028049 | -0.092693 | -0.016842 | -0.0010254 | 0.15106 | 0.09613 | 0.13733 | 0.09613 | 0.1236 | 0.027466 | -0.10529 | 0.045776 | 0.17853 | 0.045776 | 0.036621 | 0.041199 | -0.041199 | -0.11444 | 121.582 | 121.4493 | -0.004578 | 121.6507 | 121.6507 | 0.20142 | 0.022888 | 121.5134 | 121.4401 | -0.091553 | 121.6003 | 121.6003 | 0.16022 | -0.086975 | 121.6782 | 121.7056 | 121.6919 | -0.23346 | 121.5912 | 121.5958 | 121.7331 | -0.24262
3534.8594 | 121.6827 | -121.6232 | 0.12817 | -0.00022891 | -0.01816 | 0.018696 | 0.038587 | -0.028232 | -0.039578 | -0.01456 | 7.627e-05 | -0.0070004 | 0.0034457 | -0.091411 | -0.015347 | -0.0020934 | 0.13733 | 0.086975 | 0.13275 | 0.10071 | 0.10986 | 0.027466 | -0.10071 | 0.050354 | 0.16022 | 0.050354 | 0.059509 | 0.054932 | -0.059509 | -0.09613 | 121.6507 | 121.5225 | -0.018311 | 121.7102 | 121.7239 | 0.20142 | 0.009155 | 121.5637 | 121.5271 | -0.068665 | 121.6736 | 121.6736 | 0.14648 | -0.073242 | 121.7331 | 121.7606 | 121.756 | -0.22888 | 121.6827 | 121.6782 | 121.7834 | -0.2243
3536.6562 | 121.8384 | -121.6095 | 0.11444 | -0.015487 | -0.016238 | 0.015278 | 0.035382 | -0.029728 | -0.031887 | -0.012638 | 7.627e-05 | -0.0014462 | 0.0045139 | -0.090771 | -0.011074 | -0.0025208 | 0.13275 | 0.018311 | 0.041199 | 0.041199 | 0.13733 | 0.013733 | -0.11444 | 0.009155 | 0.050354 | -0.059509 | 0.07782 | 0.073242 | -0.086975 | -0.13733 | 121.6232 | 121.4951 | 0.022888 | 121.6278 | 121.6507 | 0.15564 | 0.01831 | 121.5225 | 121.4722 | -0.036621 | 121.6187 | 121.55 | 0.07782 | -0.041199 | 121.7468 | 121.7422 | 121.6507 | -0.22888 | 121.6873 | 121.6827 | 121.6599 | -0.25177
3538.4531 | 121.843 | -121.6599 | 0.1236 | -0.00022891 | -0.020083 | 0.020832 | 0.036878 | -0.029514 | -0.044064 | -0.013706 | 7.627e-05 | -0.0070004 | 0.0032321 | -0.095898 | -0.016415 | 0.0011108 | 0.10529 | 0.09613 | 0.11902 | 0.082397 | 0.11444 | 0.027466 | -0.11444 | 0.064087 | 0.17853 | 0.082397 | 0.050354 | 0.045776 | -0.013733 | -0.10986 | 121.6873 | 121.5454 | -0.009155 | 121.756 | 121.7422 | 0.19684 | -0.01831 | 121.6461 | 121.55 | -0.073242 | 121.7239 | 121.7422 | 0.19226 | -0.07782 | 121.7743 | 121.7651 | 121.7789 | -0.23804 | 121.7102 | 121.7056 | 121.8384 | -0.23346
3540.2344 | 121.9345 | -121.6415 | 0.09613 | -0.0078584 | -0.016878 | 0.01656 | 0.036023 | -0.029941 | -0.032742 | -0.01392 | 0.0077058 | -0.001019 | 0.0036593 | -0.092266 | -0.012356 | -0.0023072 | 0.050354 | -0.068665 | -0.018311 | 0.004578 | 0.14648 | 0 | -0.12817 | -0.036621 | 0.004578 | -0.073242 | 0.10071 | 0.07782 | -0.059509 | -0.14191 | 121.6415 | 121.5134 | 0.050354 | 121.5729 | 121.6461 | 0.13275 | -0.045776 | 121.582 | 121.4996 | 0.004578 | 121.6049 | 121.5683 | 0.068665 | -0.01831 | 121.788 | 121.6919 | 121.6232 | -0.2243 | 121.7422 | 121.7194 | 121.6461 | -0.23804
3542.0469 | 121.8384 | -121.7056 | 0.14191 | -0.023117 | -0.02051 | 0.017628 | 0.032392 | -0.031009 | -0.040432 | -0.012211 | -0.0075532 | -0.0057186 | 0.0028049 | -0.095043 | -0.015988 | -0.00017078 | 0.09613 | 0.073242 | 0.10071 | 0.064087 | 0.10529 | 0.045776 | -0.10529 | 0.032043 | 0.11444 | 0.013733 | 0.059509 | 0.041199 | -0.022888 | -0.10986 | 121.7514 | 121.6003 | -0.036621 | 121.7789 | 121.7697 | 0.16937 | -0.045777 | 121.6827 | 121.5958 | -0.082398 | 121.7377 | 121.7194 | 0.1236 | -0.10071 | 121.8109 | 121.8018 | 121.8063 | -0.24719 | 121.7651 | 121.7468 | 121.8201 | -0.25177
3543.8438 | 121.9803 | -121.669 | 0.07782 | -0.00022891 | -0.017092 | 0.015492 | 0.037518 | -0.027805 | -0.03381 | -0.012211 | -0.0075532 | -0.00059177 | 0.0036593 | -0.090984 | -0.013638 | -0.00081178 | 0.10071 | 0.009155 | 0.041199 | 0.059509 | 0.12817 | 0.013733 | -0.15106 | 0.013733 | 0.086975 | -0.050354 | 0.09613 | 0.064087 | -0.064087 | -0.13275 | 121.6827 | 121.5179 | 0.050354 | 121.6782 | 121.7285 | 0.21057 | 0.022888 | 121.6049 | 121.5363 | 0.01831 | 121.6827 | 121.6187 | 0.082397 | -0.013733 | 121.7972 | 121.7697 | 121.7102 | -0.22888 | 121.7651 | 121.7331 | 121.756 | -0.21057
3545.5781 | 121.9711 | -121.7285 | 0.09613 | 0.0074006 | -0.014101 | 0.013569 | 0.036023 | -0.028019 | -0.034024 | -0.012638 | 7.627e-05 | -0.0025144 | 0.0023777 | -0.088848 | -0.011929 | -0.0027344 | 0.09613 | 0.004578 | 0.032043 | 0.054932 | 0.12817 | 0.004578 | -0.14191 | -0.022888 | 0.050354 | -0.082397 | 0.082397 | 0.073242 | -0.059509 | -0.12817 | 121.7331 | 121.5866 | 0.032044 | 121.7331 | 121.7834 | 0.19684 | 0 | 121.669 | 121.6003 | -0.013733 | 121.7056 | 121.6461 | 0.045777 | -0.022888 | 121.8567 | 121.8246 | 121.7606 | -0.23804 | 121.8109 | 121.8018 | 121.7789 | -0.2243
3547.375 | 121.9757 | -121.7422 | 0.10529 | -0.0078584 | -0.018587 | 0.016987 | 0.035169 | -0.028446 | -0.034451 | -0.013065 | 0.0077058 | -0.0025144 | 0.0064365 | -0.09312 | -0.013424 | 0.00047002 | 0.09613 | 0.036621 | 0.045776 | 0.054932 | 0.1236 | 0.009155 | -0.12817 | 0 | 0.082397 | -0.064087 | 0.073242 | 0.073242 | -0.059509 | -0.13733 | 121.7514 | 121.6141 | 0.01831 | 121.7789 | 121.7972 | 0.18311 | -0.009156 | 121.6827 | 121.6049 | -0.032044 | 121.7422 | 121.6782 | 0.073242 | -0.032044 | 121.8658 | 121.8384 | 121.788 | -0.23346 | 121.8155 | 121.8155 | 121.8246 | -0.24262
3549.0938 | 121.9208 | -121.7834 | 0.11902 | -0.0078584 | -0.017092 | 0.016346 | 0.042432 | -0.025669 | -0.040005 | -0.01456 | -0.0075532 | -0.0033688 | 0.0055821 | -0.094829 | -0.019406 | 0.0015382 | 0.041199 | 0.022888 | 0.050354 | 0.054932 | 0.14191 | 0.009155 | -0.1236 | -0.064087 | 0.082397 | -0.059509 | 0.091553 | 0.073242 | -0.064087 | -0.14191 | 121.7926 | 121.6599 | 0.022888 | 121.8063 | 121.8384 | 0.17853 | -0.07782 | 121.7194 | 121.6415 | -0.027466 | 121.7194 | 121.7239 | 0.082398 | -0.045777 | 121.9254 | 121.8246 | 121.8338 | -0.24261 | 121.875 | 121.8567 | 121.8658 | -0.26093
3550.8906 | 122.0123 | -121.7514 | 0.086975 | -0.00022891 | -0.01816 | 0.017201 | 0.037305 | -0.029087 | -0.034451 | -0.012424 | 7.627e-05 | -0.00080537 | 0.0051547 | -0.09248 | -0.012997 | -0.00017078 | 0.09613 | 0.018311 | 0.027466 | 0.041199 | 0.15106 | 0.018311 | -0.14191 | -0.018311 | 0.068665 | -0.059509 | 0.10986 | 0.059509 | -0.041199 | -0.13733 | 121.7697 | 121.6095 | 0.064087 | 121.7697 | 121.7926 | 0.18311 | 0.009155 | 121.7102 | 121.6141 | 0.022888 | 121.7331 | 121.6919 | 0.07782 | -0.027466 | 121.9025 | 121.8475 | 121.7789 | -0.22888 | 121.8613 | 121.8109 | 121.8201 | -0.2243
3552.6406 | 121.9437 | -121.8018 | 0.11444 | -0.00022891 | -0.020083 | 0.019337 | 0.037091 | -0.030155 | -0.041287 | -0.016056 | -0.015182 | -0.0065732 | 0.0043003 | -0.094189 | -0.017697 | -0.0014526 | 0.054932 | 0.054932 | 0.082397 | 0.050354 | 0.11902 | 0.022888 | -0.13733 | -0.032043 | 0.086975 | -0.036621 | 0.07782 | 0.082397 | -0.059509 | -0.13733 | 121.8246 | 121.6644 | 0.004578 | 121.8567 | 121.8521 | 0.18768 | -0.059509 | 121.7422 | 121.6644 | -0.036621 | 121.7697 | 121.7651 | 0.10071 | -0.032044 | 121.9208 | 121.8567 | 121.8842 | -0.25177 | 121.8796 | 121.8842 | 121.8887 | -0.25177
3554.4375 | 121.9849 | -121.7926 | 0.1236 | -0.0078584 | -0.018374 | 0.021046 | 0.038373 | -0.028446 | -0.041928 | -0.018192 | 0.0077058 | -0.0046506 | 0.0038731 | -0.095043 | -0.017056 | -0.00017078 | 0.09613 | 0.11902 | 0.14648 | 0.09613 | 0.091553 | 0.032043 | -0.10986 | 0.041199 | 0.18768 | 0.073242 | 0.045776 | 0.041199 | -0.027466 | -0.10529 | 121.8246 | 121.6827 | -0.032043 | 121.9116 | 121.8887 | 0.20599 | -0.027466 | 121.7651 | 121.6873 | -0.07782 | 121.8338 | 121.8658 | 0.17853 | -0.082397 | 121.8842 | 121.8887 | 121.9391 | -0.23346 | 121.8384 | 121.8338 | 121.9803 | -0.22888
3556.1719 | 122.0306 | -121.8201 | 0.10071 | 0.0074006 | -0.016451 | 0.017628 | 0.034741 | -0.027164 | -0.03381 | -0.014347 | -0.0075532 | -0.0016598 | 0.0019505 | -0.094189 | -0.011715 | 4.2822e-05 | 0.07782 | -0.018311 | 0.018311 | 0.036621 | 0.13275 | -0.004578 | -0.13275 | -0.050354 | 0.022888 | -0.10071 | 0.082397 | 0.064087 | -0.068665 | -0.15106 | 121.8155 | 121.6873 | 0.032043 | 121.8018 | 121.8567 | 0.16937 | -0.022888 | 121.7514 | 121.669 | -0.018311 | 121.7697 | 121.7194 | 0.050354 | -0.036621 | 121.9528 | 121.8979 | 121.8384 | -0.23346 | 121.9025 | 121.8842 | 121.843 | -0.25177
3557.9531 | 121.9849 | -121.8475 | 0.10986 | -0.00022891 | -0.019655 | 0.014637 | 0.040509 | -0.025669 | -0.038937 | -0.013492 | -0.015182 | -0.0029416 | 0.0023777 | -0.094189 | -0.017697 | -0.0014526 | 0.013733 | -0.013733 | 0.009155 | 0.009155 | 0.1236 | -0.009155 | -0.15564 | -0.059509 | 0.054932 | -0.064087 | 0.09613 | 0.073242 | -0.07782 | -0.14191 | 121.8384 | 121.6919 | 0.013733 | 121.8338 | 121.8567 | 0.16479 | -0.09613 | 121.7697 | 121.7056 | -0.013733 | 121.788 | 121.7834 | 0.07782 | -0.036621 | 121.9711 | 121.8613 | 121.8567 | -0.2655 | 121.9437 | 121.9208 | 121.9025 | -0.25177
3559.75 | 122.1085 | -121.8292 | 0.091553 | -0.0078584 | -0.014315 | 0.017201 | 0.03645 | -0.030369 | -0.034024 | -0.015201 | 0.0077058 | -0.0023008 | 0.0043003 | -0.09547 | -0.012997 | -0.0014526 | 0.09613 | 0.018311 | 0.036621 | 0.050354 | 0.13733 | 0.009155 | -0.13733 | -0.009155 | 0.082397 | -0.036621 | 0.07782 | 0.064087 | -0.073242 | -0.1236 | 121.8384 | 121.6919 | 0.045776 | 121.8475 | 121.8796 | 0.18768 | 0.004577 | 121.756 | 121.7056 | -0.013733 | 121.8201 | 121.7926 | 0.086975 | -0.027466 | 121.9666 | 121.9254 | 121.8658 | -0.22888 | 121.907 | 121.8933 | 121.9116 | -0.21515
3561.4844 | 122.1039 | -121.8338 | 0.091553 | 0.01503 | -0.014529 | 0.015492 | 0.038587 | -0.029941 | -0.037869 | -0.01392 | -0.015182 | -0.0016598 | 0.0038731 | -0.094189 | -0.016201 | -0.00038438 | 0.036621 | -0.050354 | -0.013733 | 0.027466 | 0.15106 | 0 | -0.16022 | -0.064087 | 0.032043 | -0.068665 | 0.10071 | 0.091553 | -0.082397 | -0.13733 | 121.8338 | 121.6736 | 0.059509 | 121.7834 | 121.8613 | 0.18768 | -0.054932 | 121.7514 | 121.6965 | 0.009155 | 121.7697 | 121.7651 | 0.068664 | 0 | 121.9849 | 121.8704 | 121.8201 | -0.25177 | 121.9345 | 121.9254 | 121.8658 | -0.22888
3563.2656 | 122.0169 | -121.8796 | 0.14191 | -0.00022891 | -0.021792 | 0.01656 | 0.034955 | -0.030582 | -0.044064 | -0.016056 | 7.627e-05 | -0.0082822 | 0.0025913 | -0.094616 | -0.017056 | 0.0028198 | 0.059509 | 0.036621 | 0.073242 | 0.064087 | 0.11444 | 0.036621 | -0.10071 | 0.013733 | 0.10529 | 0.004578 | 0.054932 | 0.064087 | -0.059509 | -0.11444 | 121.9162 | 121.7789 | -0.027466 | 121.9162 | 121.9437 | 0.1648 | -0.082398 | 121.8201 | 121.7651 | -0.086975 | 121.8933 | 121.8842 | 0.11902 | -0.07782 | 121.994 | 121.9391 | 121.9528 | -0.24262 | 121.9345 | 121.9437 | 121.9849 | -0.25635
3565.0625 | 122.1085 | -121.875 | 0.086975 | -0.00022891 | -0.014315 | 0.014637 | 0.035596 | -0.029728 | -0.032742 | -0.01157 | -0.0075532 | -0.001019 | 0.00088231 | -0.093548 | -0.013424 | 0.00025642 | 0.10071 | 0 | 0.022888 | 0.022888 | 0.13733 | 0.004578 | -0.10986 | -0.050354 | 0.036621 | -0.086975 | 0.082397 | 0.073242 | -0.059509 | -0.12817 | 121.8796 | 121.7651 | 0.050354 | 121.875 | 121.8979 | 0.13275 | 0.013733 | 121.8155 | 121.7468 | -0.004578 | 121.8246 | 121.788 | 0.041199 | -0.013733 | 122.0123 | 121.9757 | 121.8979 | -0.19684 | 121.9574 | 121.9482 | 121.9116 | -0.21515
3566.875 | 122.168 | -121.843 | 0.07782 | -0.0078584 | -0.016451 | 0.016774 | 0.035809 | -0.028873 | -0.035092 | -0.014347 | -0.015182 | -0.004437 | 0.0030185 | -0.092907 | -0.013638 | -0.0010254 | 0.082397 | 0 | 0.036621 | 0.045776 | 0.12817 | 0 | -0.13275 | -0.013733 | 0.09613 | -0.050354 | 0.068665 | 0.082397 | -0.059509 | -0.13733 | 121.843 | 121.7102 | 0.050354 | 121.843 | 121.8887 | 0.17853 | 0.004577 | 121.7834 | 121.7056 | -0.009155 | 121.8292 | 121.7926 | 0.086975 | 0.004577 | 121.9711 | 121.9254 | 121.8796 | -0.21057 | 121.9116 | 121.9254 | 121.9391 | -0.21515
3568.6094 | 122.0398 | -121.9299 | 0.11902 | 0.0074006 | -0.022005 | 0.017842 | 0.037305 | -0.028019 | -0.042141 | -0.015842 | -0.0075532 | -0.006146 | 0.0023777 | -0.09312 | -0.017483 | 0.0023926 | 0.09613 | 0.050354 | 0.10071 | 0.073242 | 0.10986 | 0.041199 | -0.10529 | 0.036621 | 0.10071 | 0.004578 | 0.064087 | 0.041199 | -0.054932 | -0.10986 | 121.9711 | 121.8246 | -0.009156 | 121.9803 | 122.0032 | 0.17853 | -0.022889 | 121.875 | 121.8201 | -0.054932 | 121.9666 | 121.9345 | 0.11444 | -0.07782 | 122.0398 | 122.0261 | 122.0306 | -0.22431 | 121.994 | 121.9711 | 122.0306 | -0.22888
3570.3906 | 122.2046 | -121.8887 | 0.091553 | 0.0074006 | -0.018587 | 0.01656 | 0.035169 | -0.028873 | -0.034451 | -0.01392 | 7.627e-05 | -0.002087 | 0.0019505 | -0.09248 | -0.013851 | 0.0019654 | 0.059509 | -0.041199 | 0.004578 | 0.009155 | 0.15106 | 0.027466 | -0.13733 | -0.009155 | 0.036621 | -0.041199 | 0.068665 | 0.073242 | -0.054932 | -0.10986 | 121.9162 | 121.7514 | 0.059509 | 121.8475 | 121.8979 | 0.14648 | -0.032044 | 121.8338 | 121.7789 | -0.022888 | 121.8796 | 121.8475 | 0.068664 | -0.018311 | 122.0398 | 121.9482 | 121.8933 | -0.22888 | 121.9574 | 121.962 | 121.9254 | -0.20142
3572.1719 | 122.1909 | -121.8933 | 0.07782 | -0.0078584 | -0.014315 | 0.015706 | 0.038587 | -0.028232 | -0.035519 | -0.014774 | 7.627e-05 | -0.001019 | 0.0036593 | -0.091411 | -0.01556 | -0.00038438 | 0.064087 | -0.032043 | 0.009155 | 0.036621 | 0.13733 | 0 | -0.13275 | -0.032043 | 0.073242 | -0.032043 | 0.086975 | 0.073242 | -0.059509 | -0.12817 | 121.8933 | 121.7606 | 0.059509 | 121.8613 | 121.9299 | 0.16937 | -0.013733 | 121.8338 | 121.7651 | 0.009155 | 121.8613 | 121.8613 | 0.096131 | -0.004578 | 122.0306 | 121.9574 | 121.9025 | -0.21057 | 121.9803 | 121.9666 | 121.9666 | -0.20599
3573.8906 | 122.2275 | -121.8933 | 0.11444 | -0.00022891 | -0.017946 | 0.01656 | 0.036878 | -0.030369 | -0.034878 | -0.013279 | -0.0075532 | -0.0057186 | 0.0036593 | -0.093975 | -0.013424 | 0.00047002 | 0.064087 | -0.041199 | 0.018311 | 0.027466 | 0.13733 | 0.004578 | -0.1236 | -0.004578 | 0.054932 | -0.022888 | 0.07782 | 0.064087 | -0.045776 | -0.10529 | 121.8979 | 121.7697 | 0.022888 | 121.8521 | 121.9208 | 0.15106 | -0.050354 | 121.8475 | 121.788 | -0.036621 | 121.8887 | 121.8704 | 0.082398 | -0.050354 | 122.0306 | 121.9574 | 121.9116 | -0.23804 | 121.9711 | 121.9574 | 121.9482 | -0.21973
3575.6875 | 122.2046 | -121.9391 | 0.10071 | 0.01503 | -0.018801 | 0.01656 | 0.034741 | -0.029087 | -0.039364 | -0.01456 | 7.627e-05 | -0.004437 | 0.00088231 | -0.092266 | -0.017269 | 0.0011108 | 0.13275 | 0.059509 | 0.11902 | 0.086975 | 0.082397 | 0.045776 | -0.09613 | 0.059509 | 0.1236 | 0.032043 | 0.041199 | 0.041199 | -0.050354 | -0.086975 | 121.9849 | 121.843 | -0.018311 | 121.9986 | 122.0261 | 0.1831 | 0.032043 | 121.8887 | 121.8521 | -0.059509 | 121.9986 | 121.9711 | 0.11902 | -0.059509 | 122.0215 | 122.0718 | 122.0581 | -0.19684 | 121.9803 | 121.9803 | 122.0627 | -0.18768
3577.4844 | 122.1451 | -121.9299 | 0.10986 | -0.00022891 | -0.019015 | 0.016133 | 0.04115 | -0.029728 | -0.042355 | -0.016697 | 0.0077058 | -0.0091366 | 0.0030185 | -0.094829 | -0.019192 | 0.00025642 | 0.12817 | 0.11444 | 0.15106 | 0.09613 | 0.10071 | 0.045776 | -0.091553 | 0.050354 | 0.18768 | 0.064087 | 0.041199 | 0.041199 | -0.036621 | -0.086975 | 121.9757 | 121.8384 | -0.009155 | 122.0444 | 122.0261 | 0.18768 | 0.018311 | 121.8933 | 121.843 | -0.068664 | 121.9803 | 121.994 | 0.15106 | -0.068664 | 122.0306 | 122.0581 | 122.081 | -0.20142 | 121.9711 | 121.9711 | 122.1176 | -0.19684
3579.2656 | 122.1542 | -121.9528 | 0.12817 | -0.00022891 | -0.024782 | 0.020405 | 0.037946 | -0.032078 | -0.041287 | -0.014133 | 0.0077058 | -0.0063596 | 0.0019505 | -0.093975 | -0.017697 | 0.00089722 | 0.13275 | 0.10986 | 0.14191 | 0.10071 | 0.10986 | 0.036621 | -0.10071 | 0.073242 | 0.19226 | 0.068665 | 0.045776 | 0.032043 | -0.050354 | -0.10529 | 121.9894 | 121.8521 | -0.018311 | 122.0627 | 122.0535 | 0.20142 | 0.004577 | 121.9025 | 121.8475 | -0.082398 | 122.0261 | 122.0215 | 0.17395 | -0.096131 | 122.0627 | 122.0856 | 122.0947 | -0.22888 | 121.9986 | 121.9849 | 122.1451 | -0.23346
3580.9844 | 122.1222 | -121.994 | 0.10529 | -0.0078584 | -0.023714 | 0.020192 | 0.033887 | -0.030582 | -0.041073 | -0.016056 | 7.627e-05 | -0.0063596 | -0.00018589 | -0.094402 | -0.016628 | 0.0015382 | 0.07782 | 0.027466 | 0.068665 | 0.054932 | 0.10986 | 0.036621 | -0.086975 | 0.004578 | 0.082397 | 0.004578 | 0.050354 | 0.050354 | -0.032043 | -0.10986 | 122.0306 | 121.907 | 0.004577 | 122.0215 | 122.049 | 0.14191 | -0.027466 | 121.962 | 121.8842 | -0.054932 | 121.9986 | 121.9986 | 0.11444 | -0.054932 | 122.1039 | 122.0718 | 122.0627 | -0.19226 | 122.0444 | 122.0444 | 122.0764 | -0.21515
3582.7812 | 122.2366 | -121.9528 | 0.09613 | 0.0074006 | -0.019869 | 0.017628 | 0.03346 | -0.030582 | -0.035092 | -0.016269 | -0.0075532 | -0.0012326 | 0.00045511 | -0.093975 | -0.01257 | -0.0014526 | 0.041199 | -0.045776 | -0.013733 | 0.018311 | 0.14191 | -0.004578 | -0.13733 | -0.064087 | 0.036621 | -0.073242 | 0.091553 | 0.086975 | -0.059509 | -0.13733 | 121.9482 | 121.8155 | 0.045777 | 121.907 | 121.9711 | 0.15564 | -0.054931 | 121.8933 | 121.8155 | -0.004577 | 121.8887 | 121.8796 | 0.064087 | -0.009155 | 122.0947 | 121.994 | 121.9391 | -0.23346 | 122.0444 | 122.0398 | 121.9894 | -0.23346
3584.5781 | 122.2366 | -121.9757 | 0.091553 | -0.0078584 | -0.014742 | 0.013783 | 0.035596 | -0.029941 | -0.034451 | -0.011142 | -0.0075532 | -0.0042234 | 0.0017367 | -0.092907 | -0.011929 | -0.00017078 | 0.10071 | 0.036621 | 0.027466 | 0.041199 | 0.14648 | -0.009155 | -0.13733 | 0.013733 | 0.07782 | -0.050354 | 0.073242 | 0.064087 | -0.064087 | -0.12817 | 121.9666 | 121.8384 | 0.054931 | 122.0123 | 122.0169 | 0.17853 | 0.009155 | 121.9116 | 121.8475 | -0.018311 | 121.9894 | 121.9254 | 0.07782 | -0.027466 | 122.1222 | 122.0764 | 122.0032 | -0.22888 | 122.0489 | 122.0398 | 122.0535 | -0.21973
3586.2969 | 122.2687 | -121.9574 | 0.086975 | -0.00022891 | -0.014315 | 0.018483 | 0.038373 | -0.028446 | -0.036374 | -0.012851 | -0.0075532 | -0.0035824 | 0.0036593 | -0.092693 | -0.015133 | 0.00068362 | 0.036621 | -0.059509 | -0.013733 | -0.009155 | 0.13733 | 0.018311 | -0.12817 | -0.041199 | 0.009155 | -0.091553 | 0.09613 | 0.091553 | -0.082397 | -0.1236 | 121.9757 | 121.8292 | 0.050354 | 121.8979 | 121.9482 | 0.11902 | -0.050354 | 121.875 | 121.8338 | 0.009155 | 121.9162 | 121.8658 | 0.032043 | 0.004578 | 122.0947 | 121.994 | 121.9437 | -0.21515 | 122.0535 | 122.049 | 121.9666 | -0.21057
3588.0781 | 122.2275 | -121.9666 | 0.082397 | -0.00022891 | -0.010256 | 0.015065 | 0.040723 | -0.030369 | -0.032101 | -0.011783 | -0.0075532 | -0.0018734 | 0.0057957 | -0.091839 | -0.013638 | -0.0023072 | 0.073242 | 0 | 0.036621 | 0.041199 | 0.13733 | -0.018311 | -0.13275 | -0.036621 | 0.032043 | -0.086975 | 0.086975 | 0.07782 | -0.068665 | -0.1236 | 121.9482 | 121.8338 | 0.054932 | 121.9666 | 122.0078 | 0.17395 | -0.009155 | 121.8979 | 121.843 | 0.004578 | 121.9299 | 121.8796 | 0.036621 | -0.004577 | 122.1039 | 122.0398 | 122.0032 | -0.21515 | 122.0535 | 122.0444 | 121.9986 | -0.20599
3589.875 | 122.2549 | -121.9894 | 0.09613 | -0.00022891 | -0.019442 | 0.017415 | 0.034955 | -0.028873 | -0.039578 | -0.013492 | 7.627e-05 | -0.0040096 | 0.0013095 | -0.091198 | -0.015988 | 0.0013244 | 0.13733 | 0.07782 | 0.10529 | 0.082397 | 0.10529 | 0.041199 | -0.091553 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.054932 | -0.022888 | -0.091553 | 122.0306 | 121.8979 | 0.009156 | 122.0673 | 122.0718 | 0.17395 | 0.041199 | 121.9666 | 121.8979 | -0.059509 | 122.0581 | 122.0352 | 0.13733 | -0.041198 | 122.0947 | 122.1268 | 122.0947 | -0.18768 | 122.0261 | 122.0444 | 122.1359 | -0.18768
3591.625 | 122.2229 | -121.994 | 0.091553 | -0.0078584 | -0.014315 | 0.01656 | 0.034314 | -0.028019 | -0.035946 | -0.014988 | 7.627e-05 | -0.0018734 | 0.0025913 | -0.091411 | -0.01257 | -0.0014526 | 0.032043 | -0.036621 | -0.013733 | 0.018311 | 0.13733 | -0.004578 | -0.12817 | -0.068665 | 0.004578 | -0.11444 | 0.086975 | 0.07782 | -0.086975 | -0.14191 | 121.9894 | 121.8658 | 0.045776 | 121.9574 | 122.0123 | 0.14649 | -0.05951 | 121.907 | 121.8521 | -0.004578 | 121.9254 | 121.8796 | 0.027466 | -0.013733 | 122.1313 | 122.0261 | 121.9803 | -0.21973 | 122.081 | 122.0718 | 121.9986 | -0.23346
3593.4219 | 122.3007 | -121.9803 | 0.091553 | -0.0078584 | -0.014956 | 0.018055 | 0.033673 | -0.027805 | -0.036587 | -0.013706 | -0.0075532 | -0.0016598 | 0.00024151 | -0.094189 | -0.014065 | -0.00038438 | 0.050354 | -0.004578 | 0.013733 | 0.041199 | 0.13733 | 0.004578 | -0.14191 | -0.027466 | 0.082397 | -0.036621 | 0.07782 | 0.073242 | -0.059509 | -0.1236 | 121.9849 | 121.8384 | 0.045776 | 121.9757 | 122.0215 | 0.18311 | -0.041199 | 121.9208 | 121.8567 | -0.013733 | 121.9528 | 121.9437 | 0.086975 | -0.018311 | 122.1176 | 122.0306 | 121.994 | -0.23346 | 122.0581 | 122.0535 | 122.0627 | -0.21515
3595.2031 | 122.3099 | -121.9986 | 0.086975 | -0.00022891 | -0.016024 | 0.018055 | 0.035169 | -0.02866 | -0.036801 | -0.014774 | -0.0075532 | -0.0029416 | 0.0015231 | -0.092266 | -0.014279 | 0.0011108 | 0.027466 | -0.059509 | -0.013733 | 0.009155 | 0.13733 | -0.004578 | -0.1236 | -0.045776 | 0 | -0.068665 | 0.091553 | 0.07782 | -0.073242 | -0.11902 | 121.994 | 121.875 | 0.050354 | 121.9391 | 122.0078 | 0.13275 | -0.059509 | 121.9254 | 121.8796 | 0.004578 | 121.9528 | 121.9299 | 0.050354 | -0.009155 | 122.1359 | 122.0261 | 121.9849 | -0.21057 | 122.0901 | 122.0764 | 121.9986 | -0.20599
3597.0156 | 122.2 | -122.0398 | 0.10529 | -0.00022891 | -0.021151 | 0.019978 | 0.037305 | -0.031009 | -0.044918 | -0.014988 | -0.015182 | -0.0065732 | 0.0030185 | -0.095684 | -0.016201 | 0.002179 | 0.041199 | 0.027466 | 0.07782 | 0.059509 | 0.10071 | 0.045776 | -0.091553 | -0.013733 | 0.086975 | 0.027466 | 0.068665 | 0.054932 | -0.032043 | -0.10529 | 122.0856 | 121.9482 | -0.004578 | 122.0673 | 122.0993 | 0.15106 | -0.064087 | 122.0078 | 121.9345 | -0.036621 | 122.0261 | 122.0673 | 0.13275 | -0.050354 | 122.1405 | 122.081 | 122.1176 | -0.19684 | 122.1085 | 122.0947 | 122.1268 | -0.21057
3598.75 | 122.2275 | -122.0398 | 0.11902 | -0.0078584 | -0.020296 | 0.017201 | 0.040296 | -0.030582 | -0.042355 | -0.015629 | 7.627e-05 | -0.0067868 | 0.0030185 | -0.094829 | -0.018337 | -0.0010254 | 0.045776 | 0.041199 | 0.11444 | 0.073242 | 0.11444 | 0.036621 | -0.09613 | 0.036621 | 0.12817 | 0.050354 | 0.054932 | 0.041199 | -0.045776 | -0.10071 | 122.0764 | 121.9437 | -0.004578 | 122.081 | 122.113 | 0.16937 | -0.073243 | 121.994 | 121.9391 | -0.064087 | 122.0764 | 122.0901 | 0.15106 | -0.07782 | 122.1542 | 122.0856 | 122.1542 | -0.21515 | 122.0947 | 122.081 | 122.168 | -0.21973
3600.5469 | 122.1909 | -122.0581 | 0.1236 | -0.00022891 | -0.019869 | 0.017842 | 0.038587 | -0.028873 | -0.040646 | -0.015201 | 7.627e-05 | -0.007214 | 0.00088231 | -0.094402 | -0.016415 | -0.00081178 | 0.11902 | 0.068665 | 0.1236 | 0.07782 | 0.10071 | 0.036621 | -0.09613 | 0.064087 | 0.10529 | 0.013733 | 0.045776 | 0.045776 | -0.036621 | -0.10986 | 122.0947 | 121.962 | -0.022888 | 122.1268 | 122.1359 | 0.17395 | -0.004577 | 122.0215 | 121.9482 | -0.07782 | 122.1222 | 122.0718 | 0.1236 | -0.07782 | 122.1588 | 122.1771 | 122.1817 | -0.21973 | 122.1039 | 122.1039 | 122.1634 | -0.23346
3602.3438 | 122.2458 | -122.0535 | 0.11902 | -0.0078584 | -0.016238 | 0.015919 | 0.040296 | -0.028232 | -0.036801 | -0.014133 | -0.015182 | -0.0018734 | 0.0038731 | -0.09248 | -0.018551 | -0.001239 | 0.041199 | -0.054932 | -0.013733 | 0.018311 | 0.13733 | 0.004578 | -0.14191 | -0.054932 | 0.041199 | -0.086975 | 0.11444 | 0.082397 | -0.082397 | -0.13275 | 122.0581 | 121.9116 | 0.01831 | 121.9986 | 122.0718 | 0.16022 | -0.07782 | 121.9711 | 121.9208 | -0.004578 | 121.9986 | 121.9666 | 0.045776 | -0.036622 | 122.1909 | 122.0947 | 122.0398 | -0.26093 | 122.168 | 122.1359 | 122.0947 | -0.25177
3604.0625 | 122.2504 | -122.0627 | 0.11444 | -0.015487 | -0.023287 | 0.01656 | 0.034955 | -0.02866 | -0.041714 | -0.015842 | 7.627e-05 | -0.006146 | 0.0017367 | -0.095043 | -0.014919 | 0.0013244 | 0.086975 | 0.036621 | 0.086975 | 0.068665 | 0.11902 | 0.032043 | -0.10986 | 0.027466 | 0.12817 | 0.050354 | 0.059509 | 0.041199 | -0.050354 | -0.082397 | 122.0947 | 121.9528 | 0.004578 | 122.0993 | 122.1313 | 0.17853 | -0.027466 | 122.0123 | 121.9803 | -0.054932 | 122.0901 | 122.113 | 0.13275 | -0.073242 | 122.1817 | 122.1497 | 122.1497 | -0.2243 | 122.1222 | 122.1039 | 122.1909 | -0.19684
3605.8594 | 122.2595 | -122.0627 | 0.12817 | -0.00022891 | -0.018587 | 0.018483 | 0.037732 | -0.032505 | -0.041501 | -0.016697 | -0.015182 | -0.0057186 | 0.0036593 | -0.094829 | -0.018978 | -0.0020934 | 0.073242 | 0.009155 | 0.082397 | 0.059509 | 0.11444 | 0.036621 | -0.11902 | 0.013733 | 0.086975 | 0.004578 | 0.059509 | 0.059509 | -0.018311 | -0.11444 | 122.0993 | 121.9437 | -0.013733 | 122.0718 | 122.1222 | 0.17853 | -0.054932 | 122.0444 | 121.9482 | -0.068665 | 122.0764 | 122.0673 | 0.11902 | -0.068665 | 122.1771 | 122.1359 | 122.1451 | -0.24719 | 122.1222 | 122.1222 | 122.1497 | -0.24262
3607.5938 | 122.2366 | -122.0856 | 0.13733 | -0.00022891 | -0.019442 | 0.016987 | 0.035382 | -0.027805 | -0.036801 | -0.013706 | -0.0075532 | -0.003796 | 0.00066871 | -0.09312 | -0.015347 | -0.001239 | 0.16022 | 0.064087 | 0.1236 | 0.091553 | 0.10071 | 0.050354 | -0.091553 | 0.07782 | 0.11902 | 0.041199 | 0.045776 | 0.041199 | -0.027466 | -0.09613 | 122.1359 | 121.994 | -0.036621 | 122.1497 | 122.1771 | 0.18311 | 0.022888 | 122.0581 | 121.9894 | -0.091553 | 122.1634 | 122.1268 | 0.13733 | -0.09613 | 122.1863 | 122.2458 | 122.2092 | -0.22888 | 122.1313 | 122.1268 | 122.2046 | -0.23346
3609.3906 | 122.3236 | -122.0398 | 0.091553 | -0.0078584 | -0.017946 | 0.017415 | 0.037305 | -0.031009 | -0.033169 | -0.01456 | -0.0075532 | 0.00047643 | 0.0015231 | -0.093334 | -0.015133 | -0.0018798 | 0.068665 | -0.068665 | -0.009155 | 0.013733 | 0.15106 | 0.004578 | -0.15106 | -0.036621 | 0.032043 | -0.086975 | 0.10529 | 0.07782 | -0.073242 | -0.1236 | 122.0444 | 121.8887 | 0.059509 | 121.9711 | 122.0535 | 0.16479 | -0.022888 | 121.9666 | 121.9162 | 0.013733 | 122.0032 | 121.9528 | 0.036621 | -0.013733 | 122.1909 | 122.1085 | 122.0306 | -0.24261 | 122.1451 | 122.1176 | 122.0718 | -0.21515
3611.1719 | 122.3557 | -122.049 | 0.068665 | -0.0078584 | -0.014742 | 0.01656 | 0.037732 | -0.027805 | -0.034024 | -0.015629 | 7.627e-05 | -0.0018734 | 0.0047275 | -0.09312 | -0.012997 | -0.0031616 | 0.045776 | -0.036621 | -0.009155 | 0.027466 | 0.14648 | -0.022888 | -0.13733 | -0.050354 | 0.059509 | -0.07782 | 0.09613 | 0.073242 | -0.091553 | -0.11902 | 122.0261 | 121.9116 | 0.077819 | 122.0123 | 122.0764 | 0.16479 | -0.022889 | 121.9574 | 121.9299 | 0.027465 | 121.9986 | 121.9711 | 0.041199 | 0.004577 | 122.1954 | 122.0947 | 122.0398 | -0.20599 | 122.1451 | 122.1222 | 122.1085 | -0.18768
3612.9688 | 122.2778 | -122.113 | 0.1236 | -0.00022891 | -0.016451 | 0.017628 | 0.0388 | -0.027591 | -0.039151 | -0.014133 | -0.0075532 | -0.003796 | 0.0015231 | -0.093761 | -0.013638 | 0.00047002 | 0.036621 | -0.018311 | 0 | 0.004578 | 0.14191 | -0.013733 | -0.15106 | -0.068665 | 0.050354 | -0.07782 | 0.10529 | 0.082397 | -0.091553 | -0.13733 | 122.0993 | 121.962 | 0.018311 | 122.0947 | 122.1176 | 0.15564 | -0.086975 | 122.0215 | 121.9757 | -0.01831 | 122.0444 | 122.0352 | 0.059509 | -0.041199 | 122.2549 | 122.1497 | 122.113 | -0.27466 | 122.2183 | 122.1954 | 122.1634 | -0.26093
3614.7031 | 122.287 | -122.0947 | 0.10071 | -0.00022891 | -0.017946 | 0.018055 | 0.033887 | -0.029728 | -0.038937 | -0.013706 | 0.0077058 | -0.0025144 | 0.0010959 | -0.093761 | -0.015988 | 0.00089722 | 0.1236 | 0.091553 | 0.13275 | 0.086975 | 0.082397 | 0.050354 | -0.07782 | 0.07782 | 0.14648 | 0.050354 | 0.032043 | 0.027466 | -0.022888 | -0.082397 | 122.1451 | 122.0169 | -0.018311 | 122.1863 | 122.1817 | 0.16479 | 0.022888 | 122.0718 | 122.0123 | -0.068665 | 122.1725 | 122.1451 | 0.13275 | -0.073242 | 122.1771 | 122.2183 | 122.2275 | -0.17853 | 122.1268 | 122.1222 | 122.2412 | -0.18311
3616.5 | 122.2458 | -122.1222 | 0.1236 | -0.015487 | -0.019869 | 0.018483 | 0.03645 | -0.027378 | -0.042569 | -0.012851 | 7.627e-05 | -0.0046506 | 0.0010959 | -0.094829 | -0.016842 | 0.0011108 | 0.064087 | 0.022888 | 0.082397 | 0.059509 | 0.10071 | 0.045776 | -0.10986 | 0.027466 | 0.091553 | 0.018311 | 0.059509 | 0.059509 | -0.018311 | -0.10529 | 122.168 | 122.0123 | -0.022888 | 122.1451 | 122.1817 | 0.16937 | -0.059509 | 122.1039 | 122.0169 | -0.064087 | 122.1497 | 122.1405 | 0.1236 | -0.064087 | 122.2229 | 122.1863 | 122.2046 | -0.23346 | 122.1817 | 122.1817 | 122.2137 | -0.22888
3618.2344 | 122.287 | -122.1176 | 0.1236 | -0.015487 | -0.019015 | 0.020192 | 0.036664 | -0.028019 | -0.039792 | -0.016056 | 7.627e-05 | -0.006146 | 0.00066871 | -0.094189 | -0.017056 | 0.00047002 | 0.073242 | 0.036621 | 0.082397 | 0.068665 | 0.11902 | 0.036621 | -0.11444 | 0.036621 | 0.13275 | 0.041199 | 0.068665 | 0.045776 | -0.041199 | -0.086975 | 122.1542 | 122.0032 | -0.004577 | 122.1542 | 122.1863 | 0.18311 | -0.050354 | 122.0764 | 122.0306 | -0.054931 | 122.1542 | 122.1588 | 0.12817 | -0.07782 | 122.2366 | 122.1909 | 122.2 | -0.23804 | 122.1863 | 122.1634 | 122.2504 | -0.21057
3620.0156 | 122.3923 | -122.0764 | 0.091553 | -0.0078584 | -0.015169 | 0.015919 | 0.038159 | -0.029941 | -0.032742 | -0.013492 | 7.627e-05 | -0.0025144 | 0.0023777 | -0.091839 | -0.012997 | -0.004016 | 0.11902 | 0 | 0.036621 | 0.050354 | 0.13733 | 0.009155 | -0.13733 | 0.009155 | 0.091553 | -0.064087 | 0.082397 | 0.073242 | -0.073242 | -0.14191 | 122.0856 | 121.9391 | 0.045776 | 122.0764 | 122.1268 | 0.18768 | 0.027466 | 122.0032 | 121.9345 | -0.009156 | 122.0856 | 122.0123 | 0.07782 | -0.018311 | 122.2137 | 122.1954 | 122.113 | -0.22888 | 122.1588 | 122.1497 | 122.168 | -0.23346
3621.8125 | 122.4014 | -122.0856 | 0.07782 | -0.00022891 | -0.014101 | 0.017415 | 0.037518 | -0.027805 | -0.033383 | -0.011142 | -0.0075532 | -0.00080537 | 0.0017367 | -0.091411 | -0.011288 | 0.0019654 | 0.054932 | -0.059509 | -0.027466 | 0 | 0.14191 | 0.004578 | -0.12817 | -0.041199 | -0.004578 | -0.086975 | 0.086975 | 0.059509 | -0.064087 | -0.13275 | 122.0901 | 121.9574 | 0.064087 | 122.0261 | 122.0856 | 0.12817 | -0.022888 | 122.0215 | 121.9528 | 0.009155 | 122.0444 | 121.9986 | 0.045776 | -0.018311 | 122.2275 | 122.1405 | 122.0581 | -0.20599 | 122.1725 | 122.1451 | 122.081 | -0.21057
3623.5469 | 122.3328 | -122.168 | 0.11444 | -0.00022891 | -0.017946 | 0.016987 | 0.034741 | -0.026523 | -0.038296 | -0.015842 | 7.627e-05 | -0.005505 | 0.0032321 | -0.094829 | -0.012997 | 0.0011108 | 0.022888 | -0.013733 | -0.004578 | 0.013733 | 0.16937 | -0.004578 | -0.15106 | -0.068665 | 0.041199 | -0.091553 | 0.10529 | 0.068665 | -0.07782 | -0.12817 | 122.1634 | 122.0169 | 0.054932 | 122.1542 | 122.1817 | 0.16479 | -0.091553 | 122.0901 | 122.0398 | -0.009155 | 122.0993 | 122.0764 | 0.036621 | -0.045776 | 122.3373 | 122.1909 | 122.1634 | -0.2655 | 122.2733 | 122.2366 | 122.2092 | -0.24262
3625.3281 | 122.2687 | -122.1588 | 0.12817 | -0.00022891 | -0.021364 | 0.017842 | 0.035596 | -0.026523 | -0.041714 | -0.013492 | 0.0077058 | -0.0048642 | -0.00039949 | -0.096325 | -0.014492 | 0.00089722 | 0.10071 | 0.091553 | 0.10529 | 0.091553 | 0.091553 | 0.036621 | -0.10986 | -0.004578 | 0.13733 | 0.013733 | 0.064087 | 0.054932 | -0.054932 | -0.11902 | 122.1954 | 122.0489 | -0.036621 | 122.2504 | 122.2504 | 0.20142 | -0.027466 | 122.1039 | 122.0398 | -0.064087 | 122.1542 | 122.1725 | 0.13275 | -0.073242 | 122.2504 | 122.2595 | 122.2641 | -0.23804 | 122.2229 | 122.2137 | 122.2961 | -0.24719
3627.1094 | 122.4243 | -122.1039 | 0.091553 | -0.00022891 | -0.016665 | 0.017842 | 0.035596 | -0.030796 | -0.035305 | -0.013492 | 7.627e-05 | -0.0018734 | 0.0030185 | -0.092693 | -0.01257 | -0.0014526 | 0.054932 | -0.054932 | -0.009155 | 0.009155 | 0.15564 | 0.022888 | -0.11902 | -0.009155 | 0.027466 | -0.045776 | 0.082397 | 0.059509 | -0.045776 | -0.11902 | 122.1268 | 121.9849 | 0.064087 | 122.049 | 122.113 | 0.12817 | -0.036621 | 122.0581 | 121.9849 | -0.009156 | 122.0947 | 122.0581 | 0.073243 | -0.032044 | 122.2595 | 122.1588 | 122.0947 | -0.21057 | 122.1863 | 122.1634 | 122.1313 | -0.21057
3628.8594 | 122.319 | -122.1725 | 0.10071 | -0.00022891 | -0.019015 | 0.019764 | 0.036664 | -0.027805 | -0.039364 | -0.01392 | -0.015182 | -0.0033688 | 0.0010959 | -0.095898 | -0.016415 | 0.0019654 | 0.041199 | -0.036621 | -0.018311 | 0.004578 | 0.14191 | 0.004578 | -0.14648 | -0.068665 | 0.036621 | -0.068665 | 0.091553 | 0.091553 | -0.068665 | -0.13733 | 122.1771 | 122.0261 | 0.041199 | 122.1359 | 122.1771 | 0.15106 | -0.059509 | 122.1039 | 122.0352 | -0.009155 | 122.1039 | 122.1039 | 0.068664 | -0.009155 | 122.3145 | 122.2137 | 122.1542 | -0.24719 | 122.2641 | 122.2641 | 122.2092 | -0.23804
3630.6562 | 122.4106 | -122.168 | 0.082397 | -0.00022891 | -0.02051 | 0.01656 | 0.03346 | -0.027378 | -0.034024 | -0.011783 | -0.0075532 | -0.00059177 | 0.0034457 | -0.093548 | -0.013424 | -0.00017078 | 0.032043 | -0.068665 | -0.013733 | 0.004578 | 0.14648 | 0 | -0.14191 | -0.050354 | -0.004578 | -0.082397 | 0.091553 | 0.068665 | -0.059509 | -0.11902 | 122.168 | 122.0261 | 0.064087 | 122.0993 | 122.1725 | 0.14649 | -0.050354 | 122.1085 | 122.049 | 0.009156 | 122.1176 | 122.0856 | 0.036622 | -0.013732 | 122.3145 | 122.2 | 122.1542 | -0.2243 | 122.2595 | 122.2366 | 122.1634 | -0.20142
3632.4375 | 122.3465 | -122.1588 | 0.11902 | -0.00022891 | -0.024569 | 0.026173 | 0.034528 | -0.028446 | -0.045773 | -0.01456 | -0.0075532 | -0.0059322 | 2.7914e-05 | -0.093548 | -0.018978 | 0.00089722 | 0.050354 | 0.036621 | 0.091553 | 0.086975 | 0.10986 | 0.036621 | -0.1236 | 0.013733 | 0.11902 | 0.032043 | 0.054932 | 0.050354 | -0.032043 | -0.10986 | 122.1954 | 122.0352 | -0.009156 | 122.1954 | 122.2458 | 0.21057 | -0.068665 | 122.1268 | 122.0489 | -0.064087 | 122.1725 | 122.1909 | 0.14191 | -0.068665 | 122.2687 | 122.2092 | 122.2504 | -0.24261 | 122.2137 | 122.2092 | 122.2778 | -0.22888
3634.2188 | 122.3145 | -122.1909 | 0.10529 | -0.00022891 | -0.019228 | 0.017628 | 0.040082 | -0.028446 | -0.039792 | -0.015415 | -0.0075532 | -0.0059322 | 0.0010959 | -0.094829 | -0.019833 | 0.0011108 | 0.14191 | 0.10986 | 0.12817 | 0.09613 | 0.10529 | 0.027466 | -0.10071 | 0.064087 | 0.20142 | 0.068665 | 0.050354 | 0.045776 | -0.027466 | -0.10071 | 122.2183 | 122.0901 | 0 | 122.3007 | 122.287 | 0.19684 | 0.036621 | 122.1634 | 122.0901 | -0.054932 | 122.2549 | 122.2595 | 0.16937 | -0.05951 | 122.2961 | 122.3328 | 122.319 | -0.20599 | 122.2412 | 122.2366 | 122.3923 | -0.20599
3635.9688 | 122.4518 | -122.1497 | 0.082397 | -0.015487 | -0.016238 | 0.014851 | 0.039441 | -0.030155 | -0.033383 | -0.013706 | 7.627e-05 | 0.00047643 | 0.0047275 | -0.090984 | -0.014279 | -0.0025208 | 0.10071 | -0.018311 | 0.027466 | 0.054932 | 0.13275 | 0 | -0.14191 | 0 | 0.086975 | -0.045776 | 0.09613 | 0.07782 | -0.059509 | -0.12817 | 122.1497 | 122.0078 | 0.050354 | 122.1313 | 122.2046 | 0.19684 | 0.018311 | 122.0901 | 122.0215 | 0.013733 | 122.1497 | 122.1039 | 0.082398 | -0.004577 | 122.2824 | 122.2504 | 122.1771 | -0.2243 | 122.2458 | 122.2275 | 122.2366 | -0.21057
3637.75 | 122.4106 | -122.1359 | 0.091553 | -0.00022891 | -0.014529 | 0.015065 | 0.036664 | -0.028232 | -0.032956 | -0.011997 | 7.627e-05 | -0.0025144 | 0.0043003 | -0.091411 | -0.013424 | -0.0023072 | 0.07782 | -0.022888 | 0.009155 | 0.036621 | 0.14191 | 0.013733 | -0.14191 | -0.036621 | 0.027466 | -0.091553 | 0.07782 | 0.059509 | -0.050354 | -0.12817 | 122.1497 | 121.994 | 0.050354 | 122.113 | 122.1725 | 0.17853 | -0.013733 | 122.0856 | 122.0078 | -0.013733 | 122.0993 | 122.0444 | 0.036621 | -0.032044 | 122.2778 | 122.2137 | 122.1451 | -0.23346 | 122.2137 | 122.1954 | 122.1634 | -0.21973
3639.5469 | 122.3328 | -122.1863 | 0.13275 | -0.0078584 | -0.016451 | 0.016133 | 0.037518 | -0.029941 | -0.040646 | -0.013706 | 7.627e-05 | -0.0050778 | 0.0017367 | -0.092907 | -0.017269 | 0.00025642 | 0.027466 | -0.004578 | 0.022888 | 0.032043 | 0.12817 | 0.009155 | -0.14191 | -0.045776 | 0.045776 | -0.054932 | 0.082397 | 0.073242 | -0.068665 | -0.14191 | 122.1954 | 122.0444 | -0.004577 | 122.1817 | 122.2183 | 0.17395 | -0.10529 | 122.1176 | 122.0444 | -0.050354 | 122.1405 | 122.1313 | 0.086975 | -0.059509 | 122.3145 | 122.2137 | 122.2092 | -0.27466 | 122.2687 | 122.2595 | 122.2321 | -0.27466
3641.2656 | 122.3557 | -122.1542 | 0.10529 | -0.00022891 | -0.017733 | 0.017628 | 0.037091 | -0.029941 | -0.040005 | -0.013492 | -0.0075532 | -0.0016598 | 0.0023777 | -0.09248 | -0.016415 | -0.0016662 | 0.022888 | -0.032043 | -0.009155 | 0.009155 | 0.14191 | 0.004578 | -0.15106 | -0.068665 | 0.054932 | -0.064087 | 0.10529 | 0.10986 | -0.09613 | -0.13733 | 122.1588 | 122.0032 | 0.036621 | 122.1222 | 122.1634 | 0.16022 | -0.082398 | 122.0581 | 122.0169 | 0 | 122.0856 | 122.0901 | 0.073242 | 0.004577 | 122.2961 | 122.1771 | 122.1451 | -0.25635 | 122.2595 | 122.2641 | 122.2092 | -0.24262
3643.0625 | 122.3511 | -122.2 | 0.1236 | -0.0078584 | -0.020296 | 0.01891 | 0.038587 | -0.027805 | -0.038296 | -0.014988 | -0.0075532 | -0.0035824 | 0.00024151 | -0.092693 | -0.015347 | 0.00025642 | 0.050354 | -0.004578 | 0.027466 | 0.022888 | 0.13733 | 0.009155 | -0.13733 | -0.064087 | 0.068665 | -0.059509 | 0.09613 | 0.091553 | -0.064087 | -0.13733 | 122.2092 | 122.0627 | 0.013733 | 122.1954 | 122.2229 | 0.16022 | -0.073242 | 122.1359 | 122.0627 | -0.027466 | 122.1359 | 122.1405 | 0.07782 | -0.032043 | 122.3373 | 122.2504 | 122.2275 | -0.26093 | 122.2961 | 122.2916 | 122.2687 | -0.26093
3644.8438 | 122.4014 | -122.2046 | 0.11444 | -0.00022891 | -0.024569 | 0.019123 | 0.037305 | -0.032078 | -0.042569 | -0.014774 | -0.0075532 | -0.007855 | 0.00045511 | -0.093548 | -0.018337 | -0.0010254 | 0.091553 | 0.10529 | 0.11902 | 0.086975 | 0.10529 | 0.036621 | -0.09613 | 0.07782 | 0.17853 | 0.091553 | 0.050354 | 0.036621 | -0.032043 | -0.10986 | 122.2412 | 122.1085 | -0.009155 | 122.3099 | 122.2916 | 0.1831 | -0.022888 | 122.1725 | 122.0947 | -0.064087 | 122.2824 | 122.2961 | 0.20142 | -0.07782 | 122.3099 | 122.2961 | 122.3236 | -0.21057 | 122.2549 | 122.2412 | 122.3831 | -0.2243
3646.6406 | 122.3236 | -122.2 | 0.12817 | -0.00022891 | -0.018587 | 0.015706 | 0.038373 | -0.029514 | -0.038937 | -0.01456 | 0.0077058 | -0.004437 | 0.0034457 | -0.094829 | -0.016201 | -0.0023072 | 0.086975 | 0.064087 | 0.10071 | 0.064087 | 0.11444 | 0.009155 | -0.10986 | 0.004578 | 0.10529 | -0.022888 | 0.064087 | 0.059509 | -0.059509 | -0.12817 | 122.2092 | 122.0901 | -0.013733 | 122.2641 | 122.2641 | 0.17395 | -0.041199 | 122.1405 | 122.0718 | -0.064087 | 122.2046 | 122.1771 | 0.10529 | -0.068665 | 122.3145 | 122.287 | 122.3007 | -0.23804 | 122.2641 | 122.2595 | 122.3053 | -0.25635
3648.4531 | 122.3648 | -122.2366 | 0.12817 | -0.023117 | -0.02286 | 0.018696 | 0.035809 | -0.027805 | -0.039792 | -0.01456 | -0.0075532 | -0.003796 | 0.0028049 | -0.094402 | -0.015133 | 4.2822e-05 | 0.082397 | 0.050354 | 0.091553 | 0.050354 | 0.10986 | 0.041199 | -0.10529 | 0.036621 | 0.10071 | 0.004578 | 0.036621 | 0.036621 | -0.036621 | -0.09613 | 122.2778 | 122.1313 | -0.018311 | 122.287 | 122.287 | 0.15564 | -0.045777 | 122.2 | 122.1405 | -0.091553 | 122.2733 | 122.2412 | 0.10071 | -0.091553 | 122.3465 | 122.319 | 122.3282 | -0.23346 | 122.2733 | 122.2733 | 122.3373 | -0.2243
3650.2344 | 122.3602 | -122.2137 | 0.11902 | -0.00022891 | -0.016238 | 0.015706 | 0.0388 | -0.028232 | -0.037228 | -0.016056 | 7.627e-05 | -0.0040096 | 0.0010959 | -0.091411 | -0.016628 | -0.0020934 | 0.11902 | 0.07782 | 0.10529 | 0.091553 | 0.10071 | 0.036621 | -0.11444 | 0.013733 | 0.15564 | 0.027466 | 0.054932 | 0.054932 | -0.041199 | -0.11902 | 122.2504 | 122.0993 | -0.018311 | 122.2916 | 122.3053 | 0.20599 | 0 | 122.1725 | 122.0947 | -0.064087 | 122.2275 | 122.2412 | 0.14649 | -0.064087 | 122.3145 | 122.3328 | 122.319 | -0.23346 | 122.2687 | 122.2687 | 122.3694 | -0.23804
3651.9844 | 122.4472 | -122.2092 | 0.10986 | -0.00022891 | -0.015383 | 0.015492 | 0.034314 | -0.028873 | -0.034024 | -0.01456 | 7.627e-05 | -0.0016598 | 0.0015231 | -0.095257 | -0.011501 | -0.0016662 | 0.059509 | -0.050354 | -0.027466 | 0.009155 | 0.13733 | -0.004578 | -0.13275 | -0.068665 | -0.013733 | -0.1236 | 0.09613 | 0.07782 | -0.082397 | -0.11902 | 122.2046 | 122.0764 | 0.027466 | 122.1588 | 122.2183 | 0.14191 | -0.050354 | 122.1268 | 122.0901 | -0.013733 | 122.1405 | 122.0856 | -0.004577 | -0.032043 | 122.3465 | 122.2687 | 122.1817 | -0.24261 | 122.3053 | 122.287 | 122.1954 | -0.22888
3653.7812 | 122.374 | -122.2412 | 0.11444 | 0.0074006 | -0.021792 | 0.01891 | 0.036237 | -0.028873 | -0.042355 | -0.013279 | 0.015335 | -0.003796 | 2.7914e-05 | -0.092693 | -0.016628 | -0.00038438 | 0.068665 | 0.032043 | 0.073242 | 0.059509 | 0.11444 | 0.032043 | -0.10071 | 0.009155 | 0.09613 | 0.004578 | 0.045776 | 0.045776 | -0.027466 | -0.09613 | 122.2733 | 122.1405 | 0 | 122.2733 | 122.3007 | 0.16022 | -0.045776 | 122.2137 | 122.1451 | -0.068665 | 122.2504 | 122.2458 | 0.10071 | -0.068665 | 122.3557 | 122.3099 | 122.3145 | -0.21515 | 122.287 | 122.287 | 122.3373 | -0.21057
3655.5781 | 122.3557 | -122.2458 | 0.14648 | -0.00022891 | -0.018587 | 0.017201 | 0.039655 | -0.029941 | -0.039364 | -0.014347 | 7.627e-05 | -0.0052914 | 0.00066871 | -0.093761 | -0.016628 | -0.001239 | 0.09613 | 0.091553 | 0.10529 | 0.091553 | 0.10986 | 0.036621 | -0.10986 | 0.013733 | 0.13733 | -0.009155 | 0.068665 | 0.059509 | -0.050354 | -0.11444 | 122.2824 | 122.1359 | -0.036621 | 122.3373 | 122.3373 | 0.20142 | -0.050354 | 122.1954 | 122.1313 | -0.077819 | 122.2595 | 122.2366 | 0.10529 | -0.086975 | 122.3557 | 122.3419 | 122.3511 | -0.25635 | 122.3145 | 122.3053 | 122.3831 | -0.26093
3657.3281 | 122.5204 | -122.2092 | 0.091553 | -0.0078584 | -0.016451 | 0.013356 | 0.036237 | -0.02631 | -0.035092 | -0.01456 | 7.627e-05 | -0.0014462 | 0.0028049 | -0.091625 | -0.012142 | -0.0016662 | 0.07782 | -0.041199 | -0.009155 | 0.022888 | 0.15106 | 0 | -0.1236 | -0.013733 | 0.022888 | -0.064087 | 0.086975 | 0.068665 | -0.064087 | -0.11444 | 122.2092 | 122.0856 | 0.059509 | 122.168 | 122.2321 | 0.14648 | -0.013733 | 122.1451 | 122.0947 | -0.004578 | 122.1954 | 122.1451 | 0.050354 | -0.022888 | 122.3602 | 122.287 | 122.2 | -0.21515 | 122.2961 | 122.2778 | 122.2321 | -0.20599
3659.1094 | 122.3831 | -122.2687 | 0.10071 | -0.00022891 | -0.016878 | 0.016987 | 0.04115 | -0.02631 | -0.039151 | -0.013065 | 7.627e-05 | -0.0042234 | 0.0030185 | -0.09248 | -0.014492 | -0.0010254 | 0.09613 | 0.041199 | 0.07782 | 0.059509 | 0.11902 | 0.027466 | -0.13275 | -0.036621 | 0.068665 | -0.036621 | 0.07782 | 0.068665 | -0.059509 | -0.1236 | 122.2961 | 122.1359 | 0.018311 | 122.3099 | 122.3282 | 0.19226 | -0.004578 | 122.2092 | 122.1451 | -0.022888 | 122.2321 | 122.2321 | 0.086975 | -0.032043 | 122.3877 | 122.3648 | 122.3465 | -0.23346 | 122.3465 | 122.3373 | 122.3373 | -0.2243
3660.8594 | 122.4014 | -122.2687 | 0.12817 | -0.0078584 | -0.021578 | 0.017628 | 0.03645 | -0.029514 | -0.041073 | -0.016056 | -0.015182 | -0.005505 | 0.0017367 | -0.091411 | -0.016201 | -0.00038438 | 0.09613 | 0.027466 | 0.082397 | 0.059509 | 0.11444 | 0.027466 | -0.11444 | 0.013733 | 0.09613 | 0.009155 | 0.054932 | 0.054932 | -0.054932 | -0.086975 | 122.2961 | 122.1542 | -0.013733 | 122.2961 | 122.3282 | 0.17395 | -0.032044 | 122.2137 | 122.1817 | -0.073242 | 122.2824 | 122.2778 | 0.09613 | -0.073242 | 122.3831 | 122.3648 | 122.3511 | -0.24262 | 122.3236 | 122.3236 | 122.3648 | -0.21515
3662.6562 | 122.4197 | -122.2321 | 0.11444 | -0.015487 | -0.014315 | 0.014851 | 0.038373 | -0.02866 | -0.037228 | -0.01456 | -0.0075532 | -0.0016598 | 0.0034457 | -0.092266 | -0.016415 | -0.0018798 | 0.054932 | -0.054932 | 0.009155 | -0.009155 | 0.12817 | -0.009155 | -0.12817 | -0.059509 | 0.036621 | -0.082397 | 0.09613 | 0.073242 | -0.054932 | -0.13733 | 122.2229 | 122.1039 | 0.013733 | 122.1771 | 122.2229 | 0.11902 | -0.059509 | 122.1771 | 122.0947 | -0.018311 | 122.1725 | 122.1497 | 0.054932 | -0.041199 | 122.3602 | 122.287 | 122.2412 | -0.24262 | 122.3282 | 122.3053 | 122.2687 | -0.25177
3664.4531 | 122.4518 | -122.2412 | 0.10071 | -0.00022891 | -0.021792 | 0.017842 | 0.038587 | -0.027164 | -0.042355 | -0.01456 | 7.627e-05 | -0.0057186 | 0.0032321 | -0.094829 | -0.016842 | 0.0011108 | 0.082397 | 0.045776 | 0.07782 | 0.054932 | 0.11902 | -0.009155 | -0.10529 | 0.036621 | 0.12817 | 0.054932 | 0.059509 | 0.068665 | -0.032043 | -0.11444 | 122.2321 | 122.1359 | 0.018311 | 122.287 | 122.2961 | 0.16022 | -0.018311 | 122.2092 | 122.1268 | -0.041199 | 122.2778 | 122.2961 | 0.16937 | -0.032043 | 122.3602 | 122.3236 | 122.319 | -0.20599 | 122.3007 | 122.3099 | 122.3694 | -0.21515
3666.2344 | 122.4152 | -122.2504 | 0.1236 | -0.0078584 | -0.022219 | 0.01891 | 0.03645 | -0.027805 | -0.038083 | -0.014988 | 7.627e-05 | -0.0029416 | -0.00018589 | -0.095257 | -0.014706 | -0.00081178 | 0.082397 | 0.022888 | 0.07782 | 0.059509 | 0.11902 | 0.032043 | -0.09613 | 0.004578 | 0.10071 | 0.013733 | 0.068665 | 0.050354 | -0.027466 | -0.086975 | 122.2824 | 122.1542 | -0.004577 | 122.2733 | 122.3099 | 0.15564 | -0.041199 | 122.2229 | 122.1634 | -0.054931 | 122.2549 | 122.2641 | 0.10071 | -0.073242 | 122.3694 | 122.3328 | 122.3282 | -0.21973 | 122.319 | 122.3007 | 122.3511 | -0.21057
3667.9688 | 122.3923 | -122.2733 | 0.12817 | 0.0074006 | -0.022005 | 0.017415 | 0.029828 | -0.027805 | -0.036587 | -0.014774 | 7.627e-05 | -0.0059322 | -0.0010403 | -0.09547 | -0.015774 | 0.00068362 | 0.13733 | 0.082397 | 0.10986 | 0.064087 | 0.10529 | 0.018311 | -0.09613 | 0.050354 | 0.10529 | 0.013733 | 0.050354 | 0.027466 | -0.045776 | -0.10529 | 122.2916 | 122.1771 | -0.022888 | 122.3557 | 122.3373 | 0.16022 | 0.009155 | 122.2275 | 122.168 | -0.07782 | 122.3236 | 122.287 | 0.11902 | -0.10071 | 122.3785 | 122.4106 | 122.3831 | -0.2243 | 122.3236 | 122.3007 | 122.3785 | -0.23346
3669.75 | 122.5342 | -122.2275 | 0.07782 | -0.0078584 | -0.020083 | 0.018483 | 0.036237 | -0.030155 | -0.034451 | -0.011997 | 7.627e-05 | -0.00059177 | 0.0010959 | -0.093334 | -0.013424 | -0.001239 | 0.14191 | 0.027466 | 0.086975 | 0.082397 | 0.11444 | 0.041199 | -0.09613 | 0.07782 | 0.12817 | 0.032043 | 0.032043 | 0.022888 | -0.027466 | -0.09613 | 122.2687 | 122.1313 | 0.036621 | 122.2549 | 122.3099 | 0.17853 | 0.064087 | 122.2 | 122.1313 | -0.045777 | 122.3053 | 122.2595 | 0.12817 | -0.054932 | 122.3419 | 122.3694 | 122.3145 | -0.17395 | 122.2595 | 122.2504 | 122.3557 | -0.17395
3671.5469 | 122.4106 | -122.3007 | 0.12817 | -0.0078584 | -0.01816 | 0.018269 | 0.036878 | -0.028446 | -0.039364 | -0.013065 | -0.0075532 | -0.0040096 | 0.00066871 | -0.095043 | -0.016415 | -0.001239 | 0.11444 | 0.086975 | 0.12817 | 0.09613 | 0.10071 | 0.032043 | -0.11902 | 0.036621 | 0.16479 | 0.022888 | 0.068665 | 0.041199 | -0.027466 | -0.10529 | 122.3328 | 122.1817 | -0.027466 | 122.3877 | 122.3969 | 0.21515 | -0.013733 | 122.2733 | 122.1954 | -0.059509 | 122.3373 | 122.3236 | 0.12817 | -0.086975 | 122.4014 | 122.4152 | 122.4289 | -0.24719 | 122.3694 | 122.3419 | 122.4655 | -0.23346
3673.3438 | 122.438 | -122.3053 | 0.12817 | 0.0074006 | -0.025423 | 0.016774 | 0.034314 | -0.031009 | -0.040646 | -0.016056 | 0.0077058 | -0.0040096 | -0.0018949 | -0.095898 | -0.017269 | 0.0015382 | 0.064087 | 0.045776 | 0.073242 | 0.059509 | 0.10529 | 0.032043 | -0.10986 | 0.009155 | 0.09613 | 0.004578 | 0.050354 | 0.045776 | -0.032043 | -0.09613 | 122.3373 | 122.1954 | -0.022888 | 122.3511 | 122.3648 | 0.16937 | -0.064087 | 122.2733 | 122.2092 | -0.07782 | 122.3145 | 122.3099 | 0.10071 | -0.082398 | 122.4106 | 122.3694 | 122.3785 | -0.23804 | 122.3557 | 122.3511 | 122.4014 | -0.2243
3675.1406 | 122.4197 | -122.3053 | 0.1236 | -0.00022891 | -0.019015 | 0.018055 | 0.039441 | -0.027591 | -0.040432 | -0.014774 | -0.0075532 | -0.0016598 | 0.0025913 | -0.09312 | -0.014919 | -0.00081178 | 0.10986 | 0.091553 | 0.11902 | 0.086975 | 0.10071 | 0.027466 | -0.10529 | 0.018311 | 0.14191 | 0.018311 | 0.045776 | 0.045776 | -0.059509 | -0.11902 | 122.3328 | 122.2 | -0.022888 | 122.3969 | 122.3923 | 0.19226 | -0.013733 | 122.2458 | 122.1863 | -0.07782 | 122.3236 | 122.3236 | 0.13733 | -0.07782 | 122.406 | 122.4152 | 122.4243 | -0.22888 | 122.3511 | 122.3511 | 122.4472 | -0.24261
3676.9375 | 122.4747 | -122.3007 | 0.11902 | -0.00022891 | -0.021151 | 0.018696 | 0.034314 | -0.026096 | -0.041501 | -0.01456 | -0.0075532 | -0.0042234 | 0.0019505 | -0.094616 | -0.013424 | 4.2822e-05 | 0.07782 | 0.050354 | 0.09613 | 0.068665 | 0.11902 | 0.036621 | -0.09613 | 0.050354 | 0.13275 | 0.036621 | 0.054932 | 0.054932 | -0.036621 | -0.10529 | 122.3373 | 122.2046 | 0 | 122.3511 | 122.3694 | 0.16479 | -0.041199 | 122.2641 | 122.1954 | -0.064087 | 122.3511 | 122.3373 | 0.14191 | -0.064087 | 122.4197 | 122.3785 | 122.3969 | -0.21515 | 122.3557 | 122.3557 | 122.4335 | -0.22431
3678.6719 | 122.4747 | -122.287 | 0.09613 | -0.0078584 | -0.015383 | 0.018483 | 0.036237 | -0.03165 | -0.034665 | -0.014774 | 7.627e-05 | -0.00037797 | 0.0038731 | -0.09547 | -0.015347 | -0.0025208 | 0.041199 | -0.022888 | -0.013733 | 0.009155 | 0.14191 | -0.004578 | -0.16479 | -0.036621 | 0.036621 | -0.091553 | 0.07782 | 0.091553 | -0.064087 | -0.14648 | 122.2824 | 122.1222 | 0.045777 | 122.2641 | 122.2961 | 0.17395 | -0.054931 | 122.2229 | 122.1405 | -0.01831 | 122.2504 | 122.1954 | 0.054931 | -0.004577 | 122.4289 | 122.3282 | 122.2733 | -0.26092 | 122.3648 | 122.3785 | 122.3236 | -0.24261
3680.4688 | 122.5616 | -122.2412 | 0.07782 | -0.0078584 | -0.018374 | 0.019123 | 0.035382 | -0.025883 | -0.034665 | -0.014347 | 7.627e-05 | -0.001019 | 0.0017367 | -0.094189 | -0.011288 | -0.00059818 | 0.050354 | -0.013733 | 0.004578 | 0.036621 | 0.12817 | 0.013733 | -0.13733 | -0.041199 | 0.068665 | -0.050354 | 0.09613 | 0.073242 | -0.054932 | -0.12817 | 122.2549 | 122.1039 | 0.050354 | 122.2275 | 122.2778 | 0.17395 | -0.027466 | 122.1863 | 122.113 | 0.01831 | 122.2 | 122.1909 | 0.07782 | -0.004578 | 122.3694 | 122.2916 | 122.2458 | -0.21515 | 122.3373 | 122.3145 | 122.3099 | -0.20599
3682.2031 | 122.5571 | -122.2778 | 0.07782 | -0.0078584 | -0.017519 | 0.016346 | 0.038159 | -0.028232 | -0.035946 | -0.013706 | -0.0075532 | -0.00080537 | 0.0034457 | -0.09013 | -0.013424 | -0.002948 | 0.050354 | -0.013733 | -0.013733 | 0.022888 | 0.15106 | -0.009155 | -0.15106 | -0.041199 | 0.059509 | -0.07782 | 0.073242 | 0.073242 | -0.054932 | -0.13733 | 122.2687 | 122.1268 | 0.073242 | 122.2641 | 122.3007 | 0.17395 | -0.027466 | 122.2229 | 122.1405 | -0.004578 | 122.2366 | 122.2 | 0.059509 | -0.004578 | 122.4289 | 122.3282 | 122.2641 | -0.22888 | 122.3511 | 122.3511 | 122.3373 | -0.21515
3684.0156 | 122.4792 | -122.2687 | 0.11444 | -0.00022891 | -0.019655 | 0.020619 | 0.040509 | -0.031009 | -0.041928 | -0.015842 | -0.0075532 | -0.0065732 | 0.0047275 | -0.094616 | -0.01791 | 0.0026062 | 0.11902 | 0.12817 | 0.14191 | 0.09613 | 0.10529 | 0.032043 | -0.11444 | 0.091553 | 0.18768 | 0.091553 | 0.041199 | 0.041199 | -0.022888 | -0.086975 | 122.3007 | 122.1542 | -0.009155 | 122.3969 | 122.3648 | 0.21057 | 0.004578 | 122.2458 | 122.1817 | -0.073242 | 122.3602 | 122.3602 | 0.17853 | -0.073242 | 122.374 | 122.3877 | 122.4106 | -0.22888 | 122.3099 | 122.3099 | 122.4564 | -0.20142
3685.75 | 122.4426 | -122.3099 | 0.12817 | -0.00022891 | -0.023714 | 0.017415 | 0.033032 | -0.030796 | -0.041073 | -0.01157 | 7.627e-05 | -0.005505 | 0.0017367 | -0.09547 | -0.016201 | 0.0013244 | 0.10071 | 0.082397 | 0.10529 | 0.064087 | 0.10986 | 0.036621 | -0.091553 | 0.027466 | 0.10529 | 0.022888 | 0.050354 | 0.022888 | -0.041199 | -0.10071 | 122.3465 | 122.2183 | -0.018311 | 122.3923 | 122.374 | 0.15564 | -0.027466 | 122.2687 | 122.2092 | -0.07782 | 122.3373 | 122.3328 | 0.1236 | -0.10529 | 122.4197 | 122.4106 | 122.4152 | -0.21973 | 122.3602 | 122.3328 | 122.4152 | -0.22888
3687.5469 | 122.4426 | -122.3145 | 0.12817 | -0.0078584 | -0.017946 | 0.020192 | 0.037518 | -0.029728 | -0.038083 | -0.013279 | -0.0075532 | -0.0057186 | 0.00088231 | -0.09547 | -0.014279 | -0.0018798 | 0.11902 | 0.10529 | 0.1236 | 0.09613 | 0.10986 | 0.041199 | -0.10071 | 0.032043 | 0.16937 | 0.036621 | 0.045776 | 0.032043 | -0.045776 | -0.091553 | 122.3557 | 122.2137 | -0.018311 | 122.4197 | 122.4106 | 0.19684 | -0.009155 | 122.2687 | 122.2229 | -0.082398 | 122.3465 | 122.3511 | 0.12817 | -0.096131 | 122.4243 | 122.4335 | 122.438 | -0.22888 | 122.3602 | 122.3465 | 122.4838 | -0.21973
3689.2656 | 122.6028 | -122.2778 | 0.091553 | -0.00022891 | -0.016878 | 0.016346 | 0.035382 | -0.029087 | -0.036374 | -0.012851 | -0.015182 | 4.9234e-05 | 0.0025913 | -0.092266 | -0.013851 | -0.0033752 | 0.091553 | 0.018311 | 0.059509 | 0.045776 | 0.10529 | 0.027466 | -0.10986 | 0.054932 | 0.11444 | 0.013733 | 0.050354 | 0.041199 | -0.036621 | -0.10071 | 122.3053 | 122.168 | 0.013733 | 122.2961 | 122.3236 | 0.15564 | 0 | 122.2412 | 122.1771 | -0.041199 | 122.3328 | 122.2916 | 0.11444 | -0.050354 | 122.3831 | 122.3694 | 122.3373 | -0.20142 | 122.3282 | 122.319 | 122.3923 | -0.19226
3691.0781 | 122.5983 | -122.2916 | 0.091553 | -0.0078584 | -0.017946 | 0.016987 | 0.036023 | -0.029514 | -0.034237 | -0.014347 | 7.627e-05 | -0.0016598 | 0.0034457 | -0.092907 | -0.011715 | -0.00059818 | 0.045776 | -0.027466 | 0.009155 | 0.022888 | 0.16022 | 0.004578 | -0.13275 | 0 | 0.022888 | -0.054932 | 0.086975 | 0.045776 | -0.050354 | -0.11902 | 122.2961 | 122.1588 | 0.068664 | 122.2641 | 122.3145 | 0.15564 | -0.045777 | 122.2412 | 122.1725 | -0.004578 | 122.2916 | 122.2366 | 0.064087 | -0.045777 | 122.4518 | 122.3373 | 122.3007 | -0.2243 | 122.3785 | 122.3373 | 122.3145 | -0.21057
3692.875 | 122.4747 | -122.3236 | 0.1236 | 0.0074006 | -0.017519 | 0.015278 | 0.03645 | -0.026951 | -0.039578 | -0.015415 | -0.0075532 | -0.0059322 | 0.00088231 | -0.096325 | -0.016415 | -0.00038438 | 0.11444 | 0.1236 | 0.14648 | 0.09613 | 0.10071 | 0.045776 | -0.11444 | 0.050354 | 0.18768 | 0.054932 | 0.050354 | 0.022888 | -0.041199 | -0.10529 | 122.3694 | 122.2092 | -0.022888 | 122.4472 | 122.4197 | 0.21057 | -0.009155 | 122.2824 | 122.2183 | -0.073242 | 122.374 | 122.3785 | 0.16022 | -0.10071 | 122.4243 | 122.438 | 122.4701 | -0.23804 | 122.374 | 122.3465 | 122.5113 | -0.22888
3694.6719 | 122.4747 | -122.3282 | 0.12817 | -0.0078584 | -0.02286 | 0.019123 | 0.033673 | -0.02631 | -0.040646 | -0.014347 | 0.0077058 | -0.0050778 | 0.00024151 | -0.094402 | -0.017483 | -0.00059818 | 0.086975 | 0.045776 | 0.086975 | 0.050354 | 0.09613 | 0.018311 | -0.1236 | 0.027466 | 0.10986 | 0.013733 | 0.054932 | 0.041199 | -0.027466 | -0.10529 | 122.3465 | 122.2046 | -0.032044 | 122.374 | 122.3785 | 0.17395 | -0.041199 | 122.3007 | 122.2229 | -0.073242 | 122.3557 | 122.3419 | 0.11902 | -0.086975 | 122.4243 | 122.4152 | 122.4152 | -0.25177 | 122.3831 | 122.3694 | 122.438 | -0.23346
3696.4688 | 122.5708 | -122.3145 | 0.07782 | -0.0078584 | -0.01816 | 0.014851 | 0.035382 | -0.026523 | -0.030606 | -0.013706 | 7.627e-05 | 0.0017582 | 2.7914e-05 | -0.091839 | -0.012783 | -0.00081178 | 0.050354 | -0.082397 | -0.036621 | 0.022888 | 0.13275 | 0.004578 | -0.11902 | -0.045776 | 0.013733 | -0.086975 | 0.091553 | 0.091553 | -0.07782 | -0.14191 | 122.319 | 122.1954 | 0.054931 | 122.2321 | 122.3373 | 0.14191 | -0.027466 | 122.2366 | 122.1725 | 0.013733 | 122.2687 | 122.2275 | 0.054932 | 0.013733 | 122.4472 | 122.3648 | 122.2778 | -0.19684 | 122.406 | 122.406 | 122.3282 | -0.21973
3698.1875 | 122.5159 | -122.3282 | 0.11902 | -0.00022891 | -0.018374 | 0.018269 | 0.038373 | -0.027164 | -0.042355 | -0.013492 | 7.627e-05 | -0.0057186 | 0.00045511 | -0.095684 | -0.017697 | 0.00047002 | 0.14648 | 0.13275 | 0.15564 | 0.10071 | 0.10071 | 0.027466 | -0.10529 | 0.068665 | 0.1831 | 0.073242 | 0.064087 | 0.036621 | -0.027466 | -0.10071 | 122.3557 | 122.2229 | -0.018311 | 122.4609 | 122.4289 | 0.20599 | 0.027465 | 122.3007 | 122.2275 | -0.054932 | 122.3969 | 122.4014 | 0.17395 | -0.082398 | 122.4289 | 122.4747 | 122.4838 | -0.22431 | 122.3923 | 122.3648 | 122.5113 | -0.21973
3700 | 122.4747 | -122.3419 | 0.11902 | -0.0078584 | -0.017092 | 0.017628 | 0.034955 | -0.0293 | -0.039578 | -0.01456 | -0.015182 | -0.0040096 | 0.0013095 | -0.095257 | -0.014065 | -0.00038438 | 0.1236 | 0.059509 | 0.10071 | 0.064087 | 0.10071 | 0.041199 | -0.091553 | 0.050354 | 0.10071 | 0.013733 | 0.050354 | 0.022888 | -0.036621 | -0.091553 | 122.3831 | 122.2504 | -0.018311 | 122.4014 | 122.406 | 0.15564 | 0.004577 | 122.3053 | 122.2504 | -0.068665 | 122.3923 | 122.3557 | 0.10529 | -0.096131 | 122.4426 | 122.4655 | 122.4426 | -0.21057 | 122.3923 | 122.3648 | 122.4426 | -0.21057
3701.7969 | 122.4701 | -122.3328 | 0.1236 | -0.0078584 | -0.018587 | 0.017628 | 0.038587 | -0.027591 | -0.037442 | -0.014774 | -0.0075532 | -0.0035824 | 0.0034457 | -0.094829 | -0.014492 | -0.00038438 | 0.086975 | 0.041199 | 0.064087 | 0.059509 | 0.11902 | 0.009155 | -0.12817 | -0.036621 | 0.09613 | -0.050354 | 0.09613 | 0.068665 | -0.054932 | -0.13733 | 122.3419 | 122.2046 | -0.004577 | 122.374 | 122.3923 | 0.18768 | -0.036621 | 122.2778 | 122.1954 | -0.027466 | 122.2961 | 122.2824 | 0.086975 | -0.054931 | 122.4518 | 122.4197 | 122.3969 | -0.25177 | 122.4289 | 122.4014 | 122.4289 | -0.26093
3703.6094 | 122.493 | -122.3328 | 0.12817 | -0.0078584 | -0.017092 | 0.016774 | 0.039441 | -0.028019 | -0.040646 | -0.015842 | -0.015182 | -0.0035824 | 0.0023777 | -0.09312 | -0.017483 | -0.0025208 | 0.13733 | 0.1236 | 0.13275 | 0.091553 | 0.10071 | 0.027466 | -0.11444 | 0.054932 | 0.20142 | 0.050354 | 0.036621 | 0.045776 | -0.009155 | -0.091553 | 122.3602 | 122.2183 | -0.027466 | 122.4564 | 122.4243 | 0.20599 | 0.009155 | 122.3236 | 122.2412 | -0.091553 | 122.3877 | 122.3831 | 0.14191 | -0.082398 | 122.4335 | 122.4701 | 122.4655 | -0.24262 | 122.3694 | 122.3785 | 122.5342 | -0.21973
3705.3906 | 122.5571 | -122.3694 | 0.10529 | -0.0078584 | -0.016238 | 0.016133 | 0.034741 | -0.025669 | -0.037869 | -0.010715 | 7.627e-05 | -0.0033688 | 0.0010959 | -0.094402 | -0.01257 | -0.00059818 | 0.15106 | 0.091553 | 0.11902 | 0.086975 | 0.091553 | 0.059509 | -0.07782 | 0.082397 | 0.14648 | 0.041199 | 0.041199 | 0.018311 | -0.032043 | -0.086975 | 122.4289 | 122.2916 | -0.013733 | 122.4609 | 122.4564 | 0.16479 | 0.045776 | 122.3373 | 122.2824 | -0.064087 | 122.4518 | 122.4106 | 0.12817 | -0.086975 | 122.4609 | 122.5204 | 122.4884 | -0.18311 | 122.4106 | 122.3877 | 122.5159 | -0.19226
3707.125 | 122.5342 | -122.3602 | 0.10986 | -0.00022891 | -0.019442 | 0.016346 | 0.038159 | -0.029941 | -0.040432 | -0.015415 | 7.627e-05 | -0.003796 | 0.0025913 | -0.095043 | -0.018551 | -0.0018798 | 0.11444 | 0.054932 | 0.10529 | 0.07782 | 0.10986 | 0.045776 | -0.10986 | 0.054932 | 0.14191 | 0.064087 | 0.059509 | 0.050354 | -0.032043 | -0.091553 | 122.406 | 122.2504 | 0 | 122.4152 | 122.438 | 0.18768 | 0.004578 | 122.3282 | 122.2687 | -0.050354 | 122.4152 | 122.4243 | 0.15564 | -0.059509 | 122.4701 | 122.4747 | 122.4655 | -0.21973 | 122.4197 | 122.4106 | 122.5021 | -0.20142
3708.9375 | 122.6074 | -122.3236 | 0.091553 | -0.00022891 | -0.016665 | 0.017842 | 0.032605 | -0.028873 | -0.031674 | -0.012638 | 7.627e-05 | -0.00016437 | 0.00088231 | -0.093761 | -0.012142 | -0.0010254 | 0.064087 | -0.064087 | -0.036621 | -0.009155 | 0.13733 | 0.018311 | -0.1236 | -0.032043 | -0.004578 | -0.091553 | 0.091553 | 0.07782 | -0.068665 | -0.1236 | 122.3419 | 122.2 | 0.045776 | 122.2595 | 122.3145 | 0.11444 | -0.027466 | 122.2549 | 122.2 | 0 | 122.2916 | 122.2321 | 0.032043 | -0.013733 | 122.4609 | 122.3877 | 122.287 | -0.21515 | 122.4152 | 122.4014 | 122.319 | -0.21515
3710.6719 | 122.5021 | -122.374 | 0.1236 | -0.00022891 | -0.017946 | 0.015919 | 0.039014 | -0.029941 | -0.035733 | -0.014133 | 7.627e-05 | -0.002087 | 0.0025913 | -0.092907 | -0.017269 | -0.00038438 | 0.054932 | -0.022888 | 0.032043 | 0.018311 | 0.14191 | 0.013733 | -0.13275 | -0.045776 | 0.054932 | -0.068665 | 0.082397 | 0.086975 | -0.082397 | -0.12817 | 122.3877 | 122.2412 | 0.018311 | 122.3511 | 122.3923 | 0.15106 | -0.068664 | 122.2916 | 122.2458 | -0.041199 | 122.3282 | 122.3053 | 0.059509 | -0.036621 | 122.5159 | 122.4289 | 122.406 | -0.25635 | 122.4564 | 122.4609 | 122.4289 | -0.25177
3712.4531 | 122.6303 | -122.3145 | 0.086975 | -0.00022891 | -0.015597 | 0.017842 | 0.0388 | -0.029514 | -0.034024 | -0.013065 | 7.627e-05 | -0.0016598 | 0.0036593 | -0.094829 | -0.015774 | -0.0016662 | 0.073242 | -0.027466 | 0 | 0.027466 | 0.13733 | -0.009155 | -0.14191 | -0.032043 | 0.07782 | -0.064087 | 0.086975 | 0.054932 | -0.07782 | -0.13275 | 122.3053 | 122.1725 | 0.050354 | 122.287 | 122.3419 | 0.16937 | -0.013733 | 122.2366 | 122.1817 | 0 | 122.2824 | 122.2504 | 0.068664 | -0.032043 | 122.4518 | 122.3877 | 122.3145 | -0.22888 | 122.4014 | 122.3694 | 122.3923 | -0.21973
3714.1719 | 122.5204 | -122.3557 | 0.11902 | 0.01503 | -0.018587 | 0.019551 | 0.037946 | -0.029087 | -0.037442 | -0.01392 | -0.0075532 | -0.0012326 | 0.0023777 | -0.09312 | -0.016201 | -0.00081178 | 0.022888 | -0.027466 | -0.004578 | 0.009155 | 0.16022 | -0.018311 | -0.14191 | -0.045776 | 0.045776 | -0.07782 | 0.10071 | 0.086975 | -0.07782 | -0.12817 | 122.3373 | 122.2137 | 0.041198 | 122.3282 | 122.3648 | 0.15106 | -0.096131 | 122.2778 | 122.2275 | -0.018311 | 122.3099 | 122.2778 | 0.050354 | -0.032044 | 122.5159 | 122.3785 | 122.3511 | -0.26093 | 122.4564 | 122.4426 | 122.4014 | -0.24719
3715.9688 | 122.6395 | -122.3053 | 0.086975 | -0.00022891 | -0.014956 | 0.014851 | 0.035596 | -0.025028 | -0.034024 | -0.013065 | 7.627e-05 | -0.0023008 | 0.0038731 | -0.092907 | -0.012142 | -0.0010254 | 0.086975 | 0.018311 | 0.022888 | 0.054932 | 0.15106 | -0.004578 | -0.12817 | 0 | 0.086975 | -0.041199 | 0.073242 | 0.073242 | -0.050354 | -0.12817 | 122.3007 | 122.1771 | 0.064087 | 122.3236 | 122.3602 | 0.18311 | 0 | 122.2549 | 122.1771 | -0.013733 | 122.3053 | 122.2641 | 0.086975 | -0.013733 | 122.4564 | 122.3923 | 122.3282 | -0.21515 | 122.3785 | 122.3785 | 122.3923 | -0.21515
3717.7656 | 122.4747 | -122.3831 | 0.13733 | -0.0078584 | -0.020724 | 0.015492 | 0.035382 | -0.026737 | -0.042569 | -0.015629 | 0.0077058 | -0.0040096 | 0.0019505 | -0.096325 | -0.016201 | 0.0019654 | 0.082397 | 0.086975 | 0.10529 | 0.091553 | 0.10986 | 0.041199 | -0.10529 | 0.013733 | 0.14648 | 0.009155 | 0.054932 | 0.059509 | -0.036621 | -0.10986 | 122.4243 | 122.2778 | -0.027466 | 122.4701 | 122.4747 | 0.19684 | -0.054932 | 122.3465 | 122.2733 | -0.082397 | 122.3969 | 122.3923 | 0.11902 | -0.07782 | 122.493 | 122.4655 | 122.4884 | -0.24262 | 122.438 | 122.4426 | 122.5296 | -0.24719
3719.5 | 122.5525 | -122.3785 | 0.11444 | 0.0074006 | -0.021364 | 0.017201 | 0.034101 | -0.030582 | -0.037442 | -0.014988 | 7.627e-05 | -0.0031552 | 0.0021641 | -0.095898 | -0.014706 | 0.00047002 | 0.11902 | 0.10071 | 0.13275 | 0.091553 | 0.091553 | 0.032043 | -0.091553 | 0.068665 | 0.13733 | 0.054932 | 0.059509 | 0.022888 | -0.045776 | -0.073242 | 122.4106 | 122.287 | -0.022888 | 122.4792 | 122.4701 | 0.18311 | 0.004578 | 122.3328 | 122.3053 | -0.054932 | 122.4472 | 122.4335 | 0.12817 | -0.091553 | 122.4701 | 122.4976 | 122.5113 | -0.20599 | 122.438 | 122.4014 | 122.5159 | -0.18768
3721.2969 | 122.5571 | -122.3831 | 0.13275 | -0.00022891 | -0.023714 | 0.018483 | 0.035169 | -0.031223 | -0.041501 | -0.014133 | 7.627e-05 | -0.0023008 | -0.0016811 | -0.095684 | -0.015347 | 0.0017518 | 0.054932 | 0.036621 | 0.07782 | 0.045776 | 0.11902 | 0.022888 | -0.10071 | -0.022888 | 0.082397 | 0.018311 | 0.059509 | 0.041199 | -0.036621 | -0.10529 | 122.406 | 122.2824 | -0.013732 | 122.4197 | 122.4289 | 0.14648 | -0.077819 | 122.3465 | 122.2778 | -0.073242 | 122.3602 | 122.4014 | 0.1236 | -0.091552 | 122.5021 | 122.438 | 122.4609 | -0.23346 | 122.4426 | 122.4243 | 122.4655 | -0.23804
3723.1094 | 122.5754 | -122.3694 | 0.11902 | -0.0078584 | -0.02051 | 0.017842 | 0.038373 | -0.031437 | -0.040005 | -0.016056 | -0.015182 | -0.0046506 | 0.0010959 | -0.093761 | -0.020474 | 4.2822e-05 | 0.059509 | 0.027466 | 0.068665 | 0.050354 | 0.11444 | 0.032043 | -0.10071 | 0.013733 | 0.10986 | 0.032043 | 0.064087 | 0.054932 | -0.054932 | -0.10529 | 122.4014 | 122.2687 | -0.004578 | 122.3969 | 122.4197 | 0.15106 | -0.05951 | 122.3145 | 122.2641 | -0.054932 | 122.3831 | 122.4014 | 0.13733 | -0.064087 | 122.4838 | 122.4289 | 122.438 | -0.21973 | 122.4335 | 122.4243 | 122.4792 | -0.22431
3727.5781 | 122.6624 | -122.3602 | 0.064087 | -0.00022891 | -0.014315 | 0.015278 | 0.040082 | -0.027591 | -0.033383 | -0.013065 | 7.627e-05 | -0.00016437 | 0.0047275 | -0.09013 | -0.013638 | -0.001239 | 0.068665 | -0.07782 | -0.018311 | 0.013733 | 0.14191 | -0.004578 | -0.13275 | -0.009155 | 0.009155 | -0.082397 | 0.091553 | 0.073242 | -0.054932 | -0.11902 | 122.3557 | 122.2275 | 0.07782 | 122.2824 | 122.374 | 0.14648 | 0.004578 | 122.3053 | 122.2412 | 0.027466 | 122.3511 | 122.2778 | 0.036622 | 0.009155 | 122.5021 | 122.4289 | 122.3419 | -0.19684 | 122.4518 | 122.4335 | 122.3694 | -0.18311
3729.625 | 122.612 | -122.3694 | 0.11902 | -0.00022891 | -0.015597 | 0.016774 | 0.039655 | -0.026951 | -0.036801 | -0.014133 | 7.627e-05 | -0.0014462 | 0.0053683 | -0.092693 | -0.014279 | -0.00038438 | 0.050354 | -0.068665 | -0.009155 | 0.009155 | 0.13733 | -0.009155 | -0.15564 | -0.059509 | 0.036621 | -0.068665 | 0.10071 | 0.082397 | -0.068665 | -0.11444 | 122.3602 | 122.2137 | 0.01831 | 122.3007 | 122.3785 | 0.16479 | -0.068665 | 122.3007 | 122.2549 | -0.018311 | 122.3099 | 122.3007 | 0.045776 | -0.036622 | 122.5067 | 122.4197 | 122.3602 | -0.27466 | 122.4701 | 122.4518 | 122.406 | -0.23346
3732.25 | 122.6761 | -122.3877 | 0.09613 | -0.0078584 | -0.01816 | 0.017201 | 0.033673 | -0.028019 | -0.03381 | -0.013065 | -0.0075532 | 0.0013308 | 0.0030185 | -0.089916 | -0.012997 | -0.00017078 | 0.050354 | -0.073242 | -0.032043 | 0.009155 | 0.15564 | 0.009155 | -0.15564 | -0.027466 | 0.009155 | -0.07782 | 0.07782 | 0.064087 | -0.054932 | -0.1236 | 122.3969 | 122.2321 | 0.05951 | 122.3145 | 122.3969 | 0.16479 | -0.045776 | 122.3328 | 122.2641 | -0.01831 | 122.3602 | 122.3099 | 0.045776 | -0.032043 | 122.5433 | 122.438 | 122.3557 | -0.25177 | 122.4655 | 122.4518 | 122.3969 | -0.21973
3734.1406 | 122.5113 | -122.4197 | 0.1236 | -0.015487 | -0.016878 | 0.017415 | 0.036237 | -0.028019 | -0.041073 | -0.012851 | -0.0075532 | -0.0025144 | 0.0019505 | -0.094829 | -0.01556 | -0.001239 | 0.10986 | 0.073242 | 0.10986 | 0.09613 | 0.10529 | 0.027466 | -0.10529 | 0.018311 | 0.12817 | 0 | 0.059509 | 0.073242 | -0.050354 | -0.11902 | 122.4472 | 122.3145 | -0.01831 | 122.493 | 122.5159 | 0.20142 | -0.013733 | 122.3694 | 122.3007 | -0.064087 | 122.4381 | 122.4197 | 0.11902 | -0.050354 | 122.525 | 122.5296 | 122.5296 | -0.22888 | 122.4792 | 122.493 | 122.5479 | -0.24261
3735.9375 | 122.5433 | -122.4289 | 0.1236 | -0.0078584 | -0.019869 | 0.020405 | 0.032392 | -0.029087 | -0.039792 | -0.015842 | -0.0075532 | -0.0035824 | 0.00024151 | -0.094402 | -0.013851 | 0.0019654 | 0.12817 | 0.073242 | 0.11902 | 0.068665 | 0.10071 | 0.036621 | -0.086975 | 0.050354 | 0.1236 | 0.027466 | 0.050354 | 0.050354 | -0.041199 | -0.09613 | 122.4655 | 122.3419 | -0.022888 | 122.5021 | 122.4976 | 0.15564 | 0.004578 | 122.3877 | 122.3328 | -0.073242 | 122.4792 | 122.4564 | 0.1236 | -0.073242 | 122.5296 | 122.5571 | 122.5479 | -0.21057 | 122.4792 | 122.4792 | 122.5525 | -0.21973
3737.7656 | 122.6257 | -122.3923 | 0.10071 | -0.0078584 | -0.016238 | 0.014637 | 0.034101 | -0.025455 | -0.032742 | -0.013065 | -0.0075532 | 0.0021854 | 0.0023777 | -0.093334 | -0.010433 | -0.00038438 | 0.045776 | -0.064087 | -0.022888 | 0.013733 | 0.15106 | 0.004578 | -0.1236 | -0.07782 | 0 | -0.10986 | 0.082397 | 0.073242 | -0.068665 | -0.13733 | 122.3969 | 122.2687 | 0.050354 | 122.3282 | 122.406 | 0.13733 | -0.054932 | 122.3236 | 122.2549 | -0.018311 | 122.3145 | 122.2824 | 0.027466 | -0.027466 | 122.5433 | 122.438 | 122.3694 | -0.2243 | 122.4747 | 122.4655 | 122.3923 | -0.23804
3739.6094 | 122.5479 | -122.4243 | 0.11902 | -0.0078584 | -0.016878 | 0.018483 | 0.037518 | -0.027164 | -0.039151 | -0.015201 | -0.0075532 | -0.0025144 | 0.0030185 | -0.09248 | -0.015347 | 0.0011108 | 0.082397 | 0.036621 | 0.068665 | 0.059509 | 0.11902 | 0.009155 | -0.12817 | -0.050354 | 0.09613 | -0.050354 | 0.082397 | 0.07782 | -0.068665 | -0.12817 | 122.4335 | 122.2961 | 0 | 122.4609 | 122.4838 | 0.18768 | -0.036622 | 122.3557 | 122.2961 | -0.036622 | 122.374 | 122.374 | 0.07782 | -0.041199 | 122.5433 | 122.5067 | 122.493 | -0.24719 | 122.5067 | 122.5021 | 122.5204 | -0.24719
3741.4062 | 122.6303 | -122.3877 | 0.091553 | -0.00022891 | -0.013674 | 0.015919 | 0.037305 | -0.027378 | -0.032528 | -0.0092199 | -0.0075532 | 0.00090363 | 0.0043003 | -0.09248 | -0.014706 | -0.0016662 | 0.064087 | -0.045776 | -0.004578 | 0.018311 | 0.14648 | 0.018311 | -0.12817 | -0.059509 | 0.009155 | -0.10986 | 0.091553 | 0.082397 | -0.054932 | -0.14648 | 122.406 | 122.2595 | 0.054931 | 122.3419 | 122.406 | 0.14649 | -0.027466 | 122.3328 | 122.2412 | 0 | 122.3282 | 122.2778 | 0.036621 | -0.009156 | 122.5342 | 122.4518 | 122.3831 | -0.21973 | 122.4792 | 122.4701 | 122.3969 | -0.23804
3743.2812 | 122.6761 | -122.3648 | 0.10986 | -0.023117 | -0.017946 | 0.015065 | 0.038587 | -0.02866 | -0.037014 | -0.01392 | -0.0075532 | -0.0023008 | 0.0034457 | -0.092266 | -0.016201 | -0.00017078 | 0.022888 | -0.045776 | 0.004578 | 0.027466 | 0.15564 | 0 | -0.15106 | -0.054932 | 0.054932 | -0.07782 | 0.091553 | 0.068665 | -0.068665 | -0.12817 | 122.3648 | 122.2137 | 0.045777 | 122.319 | 122.3923 | 0.17853 | -0.086975 | 122.2961 | 122.2366 | -0.01831 | 122.3099 | 122.287 | 0.050354 | -0.041198 | 122.5204 | 122.3877 | 122.3694 | -0.26093 | 122.4564 | 122.4335 | 122.4197 | -0.23804
3745.0625 | 122.6807 | -122.3831 | 0.064087 | -0.0078584 | -0.016451 | 0.015706 | 0.039441 | -0.031009 | -0.039578 | -0.012638 | -0.015182 | -0.001019 | 0.0040867 | -0.09312 | -0.015347 | 0.0015382 | 0.018311 | -0.041199 | 0 | 0.032043 | 0.15106 | -0.013733 | -0.15564 | -0.068665 | 0.050354 | -0.073242 | 0.091553 | 0.073242 | -0.082397 | -0.1236 | 122.3694 | 122.2275 | 0.086975 | 122.3419 | 122.4152 | 0.18768 | -0.045776 | 122.3007 | 122.2595 | 0.027466 | 122.3145 | 122.3099 | 0.050354 | 0.009155 | 122.5342 | 122.4014 | 122.3831 | -0.21973 | 122.4747 | 122.4564 | 122.4335 | -0.18768
3746.8438 | 122.6028 | -122.4197 | 0.13275 | 0.01503 | -0.023073 | 0.01656 | 0.037305 | -0.02866 | -0.042355 | -0.013492 | -0.015182 | -0.007214 | 0.0023777 | -0.095257 | -0.01556 | 0.0028198 | 0.032043 | 0.013733 | 0.073242 | 0.054932 | 0.10986 | 0.018311 | -0.11444 | -0.004578 | 0.10986 | 0.032043 | 0.059509 | 0.036621 | -0.045776 | -0.09613 | 122.4381 | 122.3053 | -0.022888 | 122.4335 | 122.4747 | 0.16937 | -0.10071 | 122.374 | 122.3236 | -0.073242 | 122.4152 | 122.4518 | 0.12817 | -0.09613 | 122.5296 | 122.4518 | 122.493 | -0.24719 | 122.4792 | 122.4564 | 122.5296 | -0.22888
3748.7188 | 122.6624 | -122.4197 | 0.073242 | -0.0078584 | -0.015383 | 0.016987 | 0.033032 | -0.026523 | -0.035092 | -0.013706 | 0.0077058 | 4.9234e-05 | 0.0023777 | -0.092266 | -0.011715 | 0.0017518 | 0.013733 | -0.068665 | -0.022888 | 0.004578 | 0.16022 | 0.004578 | -0.13275 | -0.054932 | -0.013733 | -0.10529 | 0.086975 | 0.068665 | -0.064087 | -0.14648 | 122.4243 | 122.287 | 0.086975 | 122.3511 | 122.4243 | 0.13733 | -0.059509 | 122.3557 | 122.2733 | 0.013733 | 122.3648 | 122.3145 | 0.041198 | -0.004577 | 122.58 | 122.4335 | 122.3969 | -0.20599 | 122.5067 | 122.4884 | 122.406 | -0.21973
3750.5469 | 122.7036 | -122.3969 | 0.064087 | 0.0074006 | -0.017946 | 0.015065 | 0.035596 | -0.02631 | -0.037014 | -0.012851 | -0.0075532 | -0.00080537 | 0.0030185 | -0.092907 | -0.014279 | -0.00038438 | 0.082397 | -0.004578 | 0.050354 | 0.036621 | 0.11902 | 0.027466 | -0.10986 | 0.050354 | 0.082397 | 0.022888 | 0.027466 | 0.050354 | -0.009155 | -0.09613 | 122.4243 | 122.287 | 0.054932 | 122.3923 | 122.4335 | 0.14648 | 0.01831 | 122.3877 | 122.3007 | -0.036621 | 122.4472 | 122.4197 | 0.11902 | -0.013733 | 122.5159 | 122.4792 | 122.4472 | -0.17395 | 122.4243 | 122.4472 | 122.4792 | -0.16022
3752.2969 | 122.6852 | -122.4014 | 0.082397 | -0.00022891 | -0.011111 | 0.017201 | 0.038587 | -0.027805 | -0.034451 | -0.013065 | 0.0077058 | -0.0016598 | 0.0030185 | -0.092266 | -0.013851 | -0.00081178 | 0.086975 | 0.022888 | 0.050354 | 0.050354 | 0.13275 | 0.009155 | -0.13733 | 0 | 0.09613 | -0.050354 | 0.068665 | 0.064087 | -0.054932 | -0.1236 | 122.4106 | 122.2641 | 0.050354 | 122.4243 | 122.4518 | 0.18768 | 0.004578 | 122.3465 | 122.2778 | -0.013732 | 122.4014 | 122.3511 | 0.073242 | -0.01831 | 122.5342 | 122.4884 | 122.4518 | -0.21973 | 122.4701 | 122.4655 | 122.4976 | -0.20599
3754.0938 | 122.5708 | -122.4564 | 0.11902 | -0.015487 | -0.015169 | 0.019764 | 0.036664 | -0.026096 | -0.04086 | -0.013279 | 7.627e-05 | -0.0012326 | 0.0028049 | -0.093975 | -0.018765 | -0.00081178 | 0.064087 | 0.036621 | 0.082397 | 0.073242 | 0.14191 | 0.013733 | -0.1236 | -0.045776 | 0.07782 | -0.041199 | 0.082397 | 0.073242 | -0.059509 | -0.13733 | 122.4701 | 122.3328 | 0.022888 | 122.493 | 122.5296 | 0.19684 | -0.054932 | 122.3969 | 122.319 | -0.036622 | 122.4106 | 122.4152 | 0.09613 | -0.045777 | 122.5983 | 122.5204 | 122.5388 | -0.24261 | 122.5388 | 122.5296 | 122.5342 | -0.25635
3755.9219 | 122.6624 | -122.4197 | 0.091553 | -0.00022891 | -0.014742 | 0.016987 | 0.037518 | -0.028232 | -0.036374 | -0.014133 | 7.627e-05 | -0.0016598 | 0.0023777 | -0.093548 | -0.01257 | 0.0013244 | 0.082397 | 0.022888 | 0.032043 | 0.050354 | 0.1236 | 0.009155 | -0.12817 | -0.022888 | 0.064087 | -0.068665 | 0.07782 | 0.068665 | -0.064087 | -0.1236 | 122.4289 | 122.2916 | 0.032043 | 122.4426 | 122.4701 | 0.17853 | -0.009156 | 122.3557 | 122.2961 | -0.013733 | 122.3969 | 122.3511 | 0.054931 | -0.022888 | 122.5433 | 122.5021 | 122.4518 | -0.21973 | 122.4976 | 122.4884 | 122.4838 | -0.21515
3758.6094 | 122.7402 | -122.406 | 0.091553 | -0.00022891 | -0.017733 | 0.018055 | 0.036664 | -0.030369 | -0.035519 | -0.012211 | -0.0075532 | -0.001019 | 0.0053683 | -0.09312 | -0.015774 | 0.0017518 | 0.041199 | -0.013733 | 0 | 0.013733 | 0.13275 | 0.013733 | -0.12817 | -0.004578 | 0.073242 | -0.009155 | 0.068665 | 0.032043 | -0.041199 | -0.10071 | 122.4197 | 122.2778 | 0.041198 | 122.3923 | 122.4197 | 0.14191 | -0.050354 | 122.3648 | 122.3053 | -0.022888 | 122.4014 | 122.3969 | 0.091553 | -0.05951 | 122.5388 | 122.4472 | 122.406 | -0.21973 | 122.4747 | 122.438 | 122.4792 | -0.19226
3761 | 122.6898 | -122.406 | 0.086975 | 0.0074006 | -0.017092 | 0.017415 | 0.036878 | -0.029728 | -0.034878 | -0.013279 | 7.627e-05 | -0.00037797 | 0.0019505 | -0.092693 | -0.01257 | 0.0015382 | 0.086975 | 0.027466 | 0.032043 | 0.041199 | 0.1236 | 0.013733 | -0.1236 | 0 | 0.09613 | -0.050354 | 0.086975 | 0.059509 | -0.059509 | -0.12817 | 122.4197 | 122.2824 | 0.036621 | 122.4335 | 122.4472 | 0.16479 | 0 | 122.3465 | 122.2778 | 0 | 122.406 | 122.3557 | 0.07782 | -0.027466 | 122.5296 | 122.493 | 122.438 | -0.21057 | 122.493 | 122.4655 | 122.5021 | -0.21515
3762.8125 | 122.612 | -122.4472 | 0.12817 | -0.0078584 | -0.017306 | 0.017201 | 0.041364 | -0.029087 | -0.04385 | -0.01926 | -0.0075532 | -0.005505 | 0.0017367 | -0.093975 | -0.019192 | -0.00059818 | 0.10529 | 0.11444 | 0.14191 | 0.10529 | 0.10986 | 0.036621 | -0.10071 | 0.050354 | 0.18768 | 0.07782 | 0.041199 | 0.036621 | -0.009155 | -0.09613 | 122.4838 | 122.3465 | -0.018311 | 122.5616 | 122.5525 | 0.20599 | -0.022888 | 122.438 | 122.3511 | -0.086975 | 122.4976 | 122.525 | 0.17395 | -0.091553 | 122.5571 | 122.5525 | 122.5891 | -0.22888 | 122.4884 | 122.4838 | 122.6349 | -0.2243
3764.75 | 122.6761 | -122.4335 | 0.09613 | -0.00022891 | -0.016451 | 0.014424 | 0.033887 | -0.0293 | -0.036587 | -0.014774 | -0.0075532 | 0.00026283 | 0.0025913 | -0.090771 | -0.011715 | -0.00081178 | 0.10071 | -0.009155 | 0.022888 | 0.050354 | 0.12817 | 0.018311 | -0.13733 | -0.036621 | 0.036621 | -0.082397 | 0.073242 | 0.073242 | -0.054932 | -0.1236 | 122.4518 | 122.2961 | 0.032044 | 122.4243 | 122.4838 | 0.18768 | 0.004578 | 122.3785 | 122.3099 | -0.022888 | 122.3969 | 122.3511 | 0.041199 | -0.022888 | 122.5616 | 122.5342 | 122.4564 | -0.23346 | 122.5067 | 122.5067 | 122.4701 | -0.21973
3766.5469 | 122.6395 | -122.4335 | 0.10071 | -0.015487 | -0.020296 | 0.015706 | 0.038587 | -0.0293 | -0.042355 | -0.014988 | 7.627e-05 | -0.0048642 | 0.00024151 | -0.096538 | -0.017483 | -0.00059818 | 0.11902 | 0.10529 | 0.13733 | 0.10986 | 0.10071 | 0.036621 | -0.10529 | 0.050354 | 0.17853 | 0.07782 | 0.059509 | 0.050354 | -0.027466 | -0.11444 | 122.4701 | 122.3282 | 0 | 122.5388 | 122.5433 | 0.21515 | 0.018311 | 122.406 | 122.319 | -0.041199 | 122.4838 | 122.5113 | 0.19226 | -0.050354 | 122.5342 | 122.5525 | 122.5708 | -0.20599 | 122.493 | 122.4838 | 122.612 | -0.21515
3768.5 | 122.6486 | -122.4426 | 0.10986 | -0.0078584 | -0.023501 | 0.02126 | 0.036237 | -0.029941 | -0.043637 | -0.015415 | -0.0075532 | -0.003796 | 0.0013095 | -0.096325 | -0.016628 | 0.00025642 | 0.13275 | 0.11902 | 0.13275 | 0.10986 | 0.11902 | 0.036621 | -0.11902 | 0.073242 | 0.16937 | 0.086975 | 0.045776 | 0.027466 | -0.022888 | -0.09613 | 122.4792 | 122.3236 | 0.009156 | 122.5616 | 122.5525 | 0.22888 | 0.022888 | 122.4197 | 122.3465 | -0.064087 | 122.5159 | 122.5296 | 0.1831 | -0.082397 | 122.5616 | 122.5754 | 122.5754 | -0.22888 | 122.4884 | 122.4701 | 122.612 | -0.20599
3771.0312 | 122.7356 | -122.4518 | 0.09613 | -0.0078584 | -0.018801 | 0.018483 | 0.033032 | -0.027805 | -0.034024 | -0.01456 | 7.627e-05 | 4.9234e-05 | 0.00088231 | -0.093334 | -0.01257 | -0.0020934 | 0.045776 | -0.059509 | -0.018311 | 0.009155 | 0.14648 | 0.004578 | -0.13275 | -0.032043 | 0 | -0.07782 | 0.082397 | 0.07782 | -0.059509 | -0.14191 | 122.4564 | 122.319 | 0.050354 | 122.3923 | 122.4609 | 0.14191 | -0.050354 | 122.3923 | 122.3099 | -0.013733 | 122.4197 | 122.374 | 0.064087 | -0.01831 | 122.5983 | 122.4976 | 122.4335 | -0.22888 | 122.5342 | 122.5296 | 122.4518 | -0.23804
3773.7031 | 122.6349 | -122.4701 | 0.11444 | -0.00022891 | -0.019655 | 0.020192 | 0.034741 | -0.028019 | -0.042782 | -0.014347 | -0.0075532 | -0.0040096 | 0.0019505 | -0.096111 | -0.015988 | 0.0023926 | 0.045776 | 0.022888 | 0.064087 | 0.064087 | 0.11444 | 0.041199 | -0.10529 | -0.013733 | 0.082397 | 0.004578 | 0.045776 | 0.041199 | -0.036621 | -0.10986 | 122.5113 | 122.3648 | 0 | 122.493 | 122.5342 | 0.16937 | -0.068665 | 122.4335 | 122.3602 | -0.068665 | 122.4564 | 122.4747 | 0.11444 | -0.073242 | 122.5845 | 122.5159 | 122.5342 | -0.21973 | 122.5159 | 122.5113 | 122.5525 | -0.2243
3776.3281 | 122.7493 | -122.4426 | 0.086975 | -0.0078584 | -0.018374 | 0.018696 | 0.034955 | -0.028446 | -0.035733 | -0.012638 | -0.0075532 | -0.0025144 | 0.0013095 | -0.093975 | -0.012997 | -0.00017078 | 0.091553 | 0.009155 | 0.036621 | 0.041199 | 0.12817 | 0.022888 | -0.11902 | 0.054932 | 0.086975 | 0.022888 | 0.050354 | 0.041199 | -0.027466 | -0.091553 | 122.4655 | 122.3236 | 0.041199 | 122.4518 | 122.4838 | 0.16022 | 0.004578 | 122.4152 | 122.3511 | -0.036621 | 122.4976 | 122.4655 | 0.11444 | -0.045776 | 122.5708 | 122.5342 | 122.4792 | -0.20599 | 122.493 | 122.4838 | 122.5296 | -0.17853
3778.7656 | 122.7036 | -122.4564 | 0.10071 | -0.00022891 | -0.0096152 | 0.017842 | 0.041364 | -0.028019 | -0.035092 | -0.013706 | 0.0077058 | 0.00047643 | 0.0060093 | -0.093334 | -0.012997 | -0.0020934 | 0.032043 | -0.07782 | -0.027466 | 0.018311 | 0.14191 | 0.004578 | -0.12817 | -0.082397 | -0.004578 | -0.11902 | 0.09613 | 0.068665 | -0.082397 | -0.14648 | 122.4609 | 122.3282 | 0.041199 | 122.3785 | 122.4747 | 0.14649 | -0.068665 | 122.374 | 122.3099 | -0.004578 | 122.374 | 122.3373 | 0.027465 | -0.032043 | 122.5983 | 122.4884 | 122.4289 | -0.22888 | 122.5525 | 122.525 | 122.4518 | -0.24719
3781.2188 | 122.7585 | -122.4518 | 0.073242 | -0.0078584 | -0.018801 | 0.018269 | 0.034528 | -0.026523 | -0.035946 | -0.013279 | -0.0075532 | -0.0029416 | 0.0028049 | -0.093761 | -0.016415 | 0.00068362 | 0.086975 | 0.027466 | 0.064087 | 0.054932 | 0.1236 | 0.045776 | -0.10529 | 0.032043 | 0.1236 | 0.022888 | 0.045776 | 0.041199 | -0.022888 | -0.09613 | 122.4976 | 122.3465 | 0.050354 | 122.4792 | 122.5067 | 0.16022 | 0.013733 | 122.4289 | 122.3557 | -0.027466 | 122.4838 | 122.4747 | 0.11902 | -0.032043 | 122.5754 | 122.5388 | 122.5159 | -0.17853 | 122.4976 | 122.493 | 122.5754 | -0.16937
3783.125 | 122.644 | -122.4838 | 0.1236 | -0.0078584 | -0.020724 | 0.019337 | 0.036237 | -0.030796 | -0.044064 | -0.014774 | -0.0075532 | -0.003796 | 0.0010959 | -0.096752 | -0.016842 | 0.002179 | 0.059509 | 0.013733 | 0.07782 | 0.064087 | 0.1236 | 0.036621 | -0.10529 | -0.004578 | 0.091553 | 0.013733 | 0.050354 | 0.054932 | -0.022888 | -0.10071 | 122.5204 | 122.3785 | 0 | 122.4976 | 122.5479 | 0.16937 | -0.064087 | 122.4609 | 122.3831 | -0.073242 | 122.4792 | 122.4976 | 0.11444 | -0.068664 | 122.6074 | 122.5433 | 122.5616 | -0.22888 | 122.5342 | 122.5388 | 122.5754 | -0.2243
3784.9062 | 122.7356 | -122.4655 | 0.10071 | -0.00022891 | -0.017306 | 0.017842 | 0.035382 | -0.031223 | -0.034665 | -0.013279 | -0.0075532 | -0.001019 | 0.0036593 | -0.092052 | -0.011501 | -0.00038438 | 0.054932 | -0.10071 | -0.004578 | 0.004578 | 0.13733 | -0.009155 | -0.14191 | -0.050354 | -0.013733 | -0.11902 | 0.09613 | 0.086975 | -0.068665 | -0.13733 | 122.4564 | 122.3236 | 0.036621 | 122.3648 | 122.4701 | 0.14649 | -0.045776 | 122.3969 | 122.3282 | -0.004578 | 122.4152 | 122.3465 | 0.01831 | -0.013733 | 122.6028 | 122.5204 | 122.4609 | -0.24262 | 122.5616 | 122.5525 | 122.4518 | -0.23804
3787 | 122.6349 | -122.493 | 0.1236 | -0.0078584 | -0.022005 | 0.019123 | 0.033673 | -0.024387 | -0.041073 | -0.013279 | -0.015182 | -0.0063596 | 0.0013095 | -0.096111 | -0.016415 | 0.0015382 | 0.073242 | 0.045776 | 0.09613 | 0.054932 | 0.10529 | 0.045776 | -0.09613 | 0.027466 | 0.091553 | 0.009155 | 0.041199 | 0.050354 | -0.027466 | -0.09613 | 122.5388 | 122.3969 | -0.01831 | 122.5388 | 122.5479 | 0.15106 | -0.050354 | 122.4655 | 122.3969 | -0.082397 | 122.5204 | 122.5021 | 0.10528 | -0.073242 | 122.5983 | 122.5662 | 122.5891 | -0.21973 | 122.5342 | 122.5433 | 122.5845 | -0.21973
3788.8594 | 122.6807 | -122.4747 | 0.13275 | -0.0078584 | -0.019655 | 0.020192 | 0.039227 | -0.032932 | -0.041928 | -0.014774 | -0.015182 | -0.007214 | 0.0025913 | -0.095043 | -0.017269 | -0.00017078 | 0.082397 | 0.032043 | 0.086975 | 0.064087 | 0.10071 | 0.032043 | -0.10986 | 0.022888 | 0.1236 | 0.045776 | 0.059509 | 0.041199 | -0.032043 | -0.11902 | 122.5067 | 122.3648 | -0.032043 | 122.5067 | 122.5388 | 0.17395 | -0.050354 | 122.4426 | 122.3557 | -0.073242 | 122.4976 | 122.5204 | 0.16479 | -0.091552 | 122.5754 | 122.5571 | 122.5616 | -0.24261 | 122.5342 | 122.5159 | 122.5983 | -0.25177
3790.6406 | 122.6852 | -122.4838 | 0.09613 | -0.0078584 | -0.021578 | 0.016987 | 0.037732 | -0.030796 | -0.037869 | -0.017338 | -0.015182 | -0.0048642 | 0.0021641 | -0.096111 | -0.017269 | -0.001239 | 0.13275 | 0.07782 | 0.11902 | 0.09613 | 0.11902 | 0.041199 | -0.10986 | 0.07782 | 0.17395 | 0.07782 | 0.050354 | 0.045776 | -0.022888 | -0.086975 | 122.525 | 122.374 | 0.022889 | 122.5616 | 122.58 | 0.20599 | 0.036621 | 122.4609 | 122.3969 | -0.045776 | 122.5616 | 122.5616 | 0.16479 | -0.050354 | 122.6028 | 122.6166 | 122.6028 | -0.20599 | 122.5342 | 122.5296 | 122.6578 | -0.1831
3792.5469 | 122.7585 | -122.4655 | 0.07782 | -0.00022891 | -0.017092 | 0.016133 | 0.039868 | -0.028873 | -0.034024 | -0.014988 | 0.0077058 | -0.0012326 | 0.0028049 | -0.093761 | -0.015774 | -0.0035888 | 0.068665 | -0.050354 | 0 | 0.036621 | 0.14191 | 0 | -0.13733 | -0.041199 | 0.036621 | -0.082397 | 0.10071 | 0.068665 | -0.082397 | -0.1236 | 122.4655 | 122.3282 | 0.064087 | 122.4152 | 122.5021 | 0.17395 | -0.009155 | 122.3831 | 122.3419 | 0.022888 | 122.4243 | 122.3831 | 0.041199 | -0.009155 | 122.6074 | 122.5342 | 122.4655 | -0.21515 | 122.5662 | 122.5342 | 122.5021 | -0.20142
3794.2656 | 122.6257 | -122.5159 | 0.11902 | 0.0074006 | -0.017519 | 0.017842 | 0.037946 | -0.026737 | -0.037869 | -0.012851 | -0.0075532 | -0.002728 | 0.0030185 | -0.094616 | -0.017056 | -0.00081178 | 0.1236 | 0.068665 | 0.10529 | 0.082397 | 0.10986 | 0.022888 | -0.11902 | 0 | 0.12817 | -0.013733 | 0.073242 | 0.064087 | -0.041199 | -0.11444 | 122.5388 | 122.3969 | -0.009156 | 122.5845 | 122.5983 | 0.20142 | 0.004577 | 122.4747 | 122.4014 | -0.045777 | 122.5159 | 122.5021 | 0.10071 | -0.054932 | 122.6257 | 122.6395 | 122.6212 | -0.23804 | 122.5891 | 122.58 | 122.644 | -0.23346
3796.0469 | 122.7493 | -122.4655 | 0.10071 | -0.00022891 | -0.01581 | 0.018055 | 0.031537 | -0.028873 | -0.032742 | -0.012638 | 7.627e-05 | -0.00080537 | 0.0015231 | -0.092907 | -0.0093652 | 0.00068362 | 0.045776 | -0.059509 | -0.022888 | 0.027466 | 0.13733 | 0.004578 | -0.1236 | -0.050354 | -0.004578 | -0.10071 | 0.082397 | 0.07782 | -0.07782 | -0.1236 | 122.4701 | 122.3419 | 0.036621 | 122.406 | 122.493 | 0.15106 | -0.054932 | 122.3877 | 122.3419 | -0.018311 | 122.4152 | 122.3648 | 0.022888 | -0.022888 | 122.6028 | 122.5113 | 122.4426 | -0.2243 | 122.5479 | 122.5433 | 122.4609 | -0.2243
3797.7656 | 122.7448 | -122.4609 | 0.091553 | -0.00022891 | -0.016024 | 0.013997 | 0.035596 | -0.0293 | -0.034665 | -0.011997 | 7.627e-05 | -0.002728 | 0.0043003 | -0.093975 | -0.01257 | -0.001239 | 0.10986 | 0.032043 | 0.032043 | 0.054932 | 0.12817 | -0.009155 | -0.11902 | 0.018311 | 0.086975 | -0.068665 | 0.073242 | 0.068665 | -0.059509 | -0.11902 | 122.4518 | 122.3419 | 0.036621 | 122.493 | 122.5159 | 0.17395 | 0.01831 | 122.4014 | 122.3419 | -0.018311 | 122.4792 | 122.3923 | 0.050354 | -0.022888 | 122.5891 | 122.5708 | 122.493 | -0.21057 | 122.5342 | 122.5296 | 122.5479 | -0.21057
3799.4844 | 122.7859 | -122.493 | 0.07782 | 0.0074006 | -0.015169 | 0.018269 | 0.035596 | -0.030796 | -0.037442 | -0.012424 | -0.015182 | 0.00047643 | 0.0036593 | -0.093548 | -0.01257 | 0.0023926 | 0.036621 | -0.027466 | -0.013733 | 0.013733 | 0.13733 | 0.004578 | -0.14191 | -0.013733 | 0.022888 | -0.050354 | 0.073242 | 0.054932 | -0.068665 | -0.1236 | 122.4976 | 122.3511 | 0.059509 | 122.4655 | 122.5067 | 0.15564 | -0.041199 | 122.4243 | 122.3694 | -0.004578 | 122.4792 | 122.4426 | 0.073242 | -0.022888 | 122.6303 | 122.5296 | 122.4792 | -0.21973 | 122.5662 | 122.5479 | 122.5159 | -0.20142
3801.2344 | 122.6395 | -122.5067 | 0.12817 | -0.0078584 | -0.020083 | 0.019337 | 0.040296 | -0.029087 | -0.044278 | -0.014133 | 7.627e-05 | -0.003796 | 0.0025913 | -0.096966 | -0.019192 | 0.00068362 | 0.11444 | 0.10529 | 0.13733 | 0.11902 | 0.11444 | 0.036621 | -0.10986 | 0.036621 | 0.17853 | 0.045776 | 0.036621 | 0.041199 | -0.022888 | -0.09613 | 122.5433 | 122.3969 | -0.013733 | 122.612 | 122.6257 | 0.22888 | -0.013733 | 122.4838 | 122.4106 | -0.091553 | 122.5433 | 122.5525 | 0.14191 | -0.086975 | 122.6212 | 122.6212 | 122.644 | -0.23804 | 122.5433 | 122.5479 | 122.6852 | -0.2243
3802.9375 | 122.7951 | -122.4792 | 0.10529 | -0.00022891 | -0.016451 | 0.019337 | 0.035596 | -0.028873 | -0.035946 | -0.012851 | -0.0075532 | -0.0014462 | 0.0019505 | -0.092907 | -0.014706 | -0.00081178 | 0.041199 | -0.059509 | -0.004578 | 0.013733 | 0.13733 | 0.004578 | -0.14648 | -0.041199 | 0.013733 | -0.086975 | 0.086975 | 0.064087 | -0.059509 | -0.12817 | 122.4838 | 122.3328 | 0.032043 | 122.4197 | 122.493 | 0.16022 | -0.064087 | 122.4197 | 122.3511 | -0.018311 | 122.438 | 122.3923 | 0.041199 | -0.041199 | 122.6166 | 122.5204 | 122.4747 | -0.25177 | 122.5662 | 122.5433 | 122.493 | -0.23346
3804.7031 | 122.6807 | -122.5296 | 0.12817 | -0.00022891 | -0.015383 | 0.01656 | 0.039655 | -0.027805 | -0.038937 | -0.016269 | -0.015182 | -0.0012326 | 0.0066501 | -0.093334 | -0.017269 | 0.0011108 | 0.018311 | -0.032043 | 0 | 0.013733 | 0.15564 | 0.004578 | -0.15106 | -0.064087 | 0.032043 | -0.07782 | 0.086975 | 0.068665 | -0.07782 | -0.14648 | 122.5342 | 122.3785 | 0.027466 | 122.4976 | 122.5433 | 0.16479 | -0.10986 | 122.4518 | 122.3831 | -0.041199 | 122.4655 | 122.4518 | 0.068664 | -0.059509 | 122.6852 | 122.5479 | 122.5296 | -0.27924 | 122.6166 | 122.5983 | 122.5616 | -0.27466
3806.4062 | 122.8043 | -122.4976 | 0.07782 | 0.0074006 | -0.016238 | 0.016774 | 0.033673 | -0.029087 | -0.035305 | -0.014774 | -0.0075532 | -0.0016598 | 0.0032321 | -0.09013 | -0.015133 | 0.00047002 | 0.032043 | -0.032043 | -0.027466 | 0.013733 | 0.15106 | 0 | -0.15106 | -0.045776 | 0.013733 | -0.091553 | 0.09613 | 0.07782 | -0.064087 | -0.13733 | 122.4976 | 122.3465 | 0.073242 | 122.4655 | 122.5113 | 0.16479 | -0.045777 | 122.4335 | 122.3602 | 0.01831 | 122.4518 | 122.406 | 0.045776 | 0 | 122.6486 | 122.5296 | 122.4701 | -0.22888 | 122.5937 | 122.5754 | 122.5113 | -0.21515
3808.2031 | 122.7997 | -122.4564 | 0.082397 | -0.00022891 | -0.01581 | 0.015706 | 0.036878 | -0.026737 | -0.03851 | -0.012424 | 7.627e-05 | -0.00059177 | 0.0045139 | -0.09248 | -0.014279 | -0.00059818 | 0.027466 | -0.027466 | -0.004578 | 0.018311 | 0.12817 | -0.004578 | -0.14191 | -0.018311 | 0.036621 | -0.050354 | 0.07782 | 0.064087 | -0.059509 | -0.13733 | 122.4518 | 122.3145 | 0.045777 | 122.4289 | 122.4747 | 0.16022 | -0.054931 | 122.3969 | 122.319 | -0.004577 | 122.438 | 122.406 | 0.086975 | -0.01831 | 122.5845 | 122.4838 | 122.4518 | -0.2243 | 122.5342 | 122.5204 | 122.493 | -0.21973
3810 | 122.7997 | -122.4564 | 0.073242 | -0.00022891 | -0.015597 | 0.015706 | 0.039014 | -0.02866 | -0.036801 | -0.012424 | -0.015182 | -0.00016437 | 0.0049411 | -0.09547 | -0.013424 | 0.0013244 | 0.059509 | -0.009155 | 0.018311 | 0.054932 | 0.13733 | 0.013733 | -0.13733 | -0.018311 | 0.086975 | -0.032043 | 0.073242 | 0.064087 | -0.068665 | -0.11902 | 122.4701 | 122.319 | 0.064087 | 122.4472 | 122.5113 | 0.19226 | -0.013733 | 122.3877 | 122.3373 | 0 | 122.438 | 122.4243 | 0.086976 | -0.009155 | 122.5937 | 122.5159 | 122.4747 | -0.21057 | 122.5296 | 122.5204 | 122.5433 | -0.19226
3811.9531 | 122.6578 | -122.525 | 0.1236 | -0.00022891 | -0.019442 | 0.017628 | 0.036878 | -0.029087 | -0.044064 | -0.013492 | 7.627e-05 | -0.007214 | 0.0032321 | -0.096325 | -0.016415 | 0.00025642 | 0.054932 | 0.054932 | 0.086975 | 0.050354 | 0.09613 | 0.036621 | -0.09613 | 0 | 0.09613 | 0.013733 | 0.054932 | 0.054932 | -0.009155 | -0.09613 | 122.5616 | 122.4289 | -0.027466 | 122.58 | 122.5754 | 0.14648 | -0.068664 | 122.5159 | 122.4289 | -0.068664 | 122.525 | 122.5388 | 0.10986 | -0.068664 | 122.6212 | 122.58 | 122.612 | -0.21973 | 122.58 | 122.58 | 122.6212 | -0.21973
3813.8594 | 122.6761 | -122.5571 | 0.12817 | -0.00022891 | -0.020937 | 0.016987 | 0.035809 | -0.029728 | -0.043423 | -0.015201 | 7.627e-05 | -0.0031552 | 0.00088231 | -0.094616 | -0.016201 | -0.00038438 | 0.07782 | 0.041199 | 0.07782 | 0.054932 | 0.11444 | 0.041199 | -0.10986 | 0.018311 | 0.10071 | 0.022888 | 0.054932 | 0.032043 | -0.013733 | -0.09613 | 122.5983 | 122.4472 | -0.013733 | 122.5983 | 122.612 | 0.16479 | -0.050354 | 122.5433 | 122.4609 | -0.073242 | 122.5754 | 122.58 | 0.11902 | -0.096131 | 122.6715 | 122.6349 | 122.6349 | -0.23804 | 122.612 | 122.5891 | 122.6578 | -0.2243
3815.7188 | 122.6715 | -122.5525 | 0.13275 | -0.0078584 | -0.022219 | 0.018055 | 0.035169 | -0.026523 | -0.038083 | -0.016056 | 7.627e-05 | -0.001019 | 0.0036593 | -0.094189 | -0.014492 | -0.00059818 | 0.07782 | 0.018311 | 0.022888 | 0.027466 | 0.1236 | 0.009155 | -0.13733 | -0.036621 | 0.054932 | -0.054932 | 0.07782 | 0.054932 | -0.059509 | -0.1236 | 122.5616 | 122.4152 | -0.009155 | 122.5708 | 122.58 | 0.16479 | -0.054931 | 122.493 | 122.4289 | -0.054931 | 122.5159 | 122.4976 | 0.068664 | -0.077819 | 122.6761 | 122.6303 | 122.5754 | -0.27008 | 122.6303 | 122.6074 | 122.6074 | -0.25635
3817.5469 | 122.6669 | -122.58 | 0.11902 | -0.015487 | -0.022219 | 0.019337 | 0.032392 | -0.029087 | -0.040432 | -0.014988 | 7.627e-05 | -0.0050778 | 0.0010959 | -0.094616 | -0.015988 | -0.00038438 | 0.1236 | 0.068665 | 0.10529 | 0.073242 | 0.10986 | 0.022888 | -0.091553 | 0.041199 | 0.10071 | 0.004578 | 0.045776 | 0.032043 | -0.054932 | -0.10529 | 122.6028 | 122.4884 | -0.009156 | 122.6486 | 122.6532 | 0.16479 | 0.004577 | 122.525 | 122.4747 | -0.073243 | 122.6212 | 122.5845 | 0.10986 | -0.086976 | 122.6898 | 122.7036 | 122.6852 | -0.21057 | 122.6257 | 122.612 | 122.6807 | -0.22431
3819.5156 | 122.6486 | -122.5479 | 0.13733 | 0.0074006 | -0.016878 | 0.017415 | 0.040296 | -0.026951 | -0.038723 | -0.015201 | 7.627e-05 | -0.0035824 | 0.0038731 | -0.094189 | -0.018765 | 0.00047002 | 0.11444 | 0.045776 | 0.086975 | 0.082397 | 0.11444 | 0.018311 | -0.1236 | -0.009155 | 0.10071 | -0.009155 | 0.086975 | 0.059509 | -0.032043 | -0.1236 | 122.5662 | 122.4243 | -0.022888 | 122.5937 | 122.6303 | 0.20599 | -0.022888 | 122.5159 | 122.4243 | -0.050354 | 122.5388 | 122.5388 | 0.11444 | -0.07782 | 122.6624 | 122.6624 | 122.6349 | -0.26093 | 122.6349 | 122.6074 | 122.6486 | -0.26093
3821.7812 | 122.7905 | -122.5067 | 0.086975 | -0.00022891 | -0.019442 | 0.016346 | 0.03645 | -0.027591 | -0.035519 | -0.013492 | 7.627e-05 | -0.003796 | 0.0015231 | -0.094189 | -0.01321 | -0.00038438 | 0.14648 | 0.064087 | 0.09613 | 0.091553 | 0.11444 | 0.032043 | -0.09613 | 0.068665 | 0.11902 | 0.018311 | 0.041199 | 0.032043 | -0.041199 | -0.09613 | 122.5388 | 122.4106 | 0.027466 | 122.5708 | 122.5983 | 0.18768 | 0.059509 | 122.4655 | 122.4106 | -0.045776 | 122.5754 | 122.525 | 0.11444 | -0.054932 | 122.6212 | 122.6532 | 122.6028 | -0.1831 | 122.5479 | 122.5388 | 122.6257 | -0.1831
3823.5625 | 122.8317 | -122.493 | 0.073242 | -0.00022891 | -0.018801 | 0.01891 | 0.03645 | -0.028232 | -0.03616 | -0.014133 | 7.627e-05 | 0.00090363 | 0.0030185 | -0.092907 | -0.014706 | 0.0015382 | 0.082397 | -0.050354 | 0 | 0.013733 | 0.14648 | -0.022888 | -0.12817 | 0 | 0.027466 | -0.059509 | 0.073242 | 0.068665 | -0.032043 | -0.11444 | 122.4701 | 122.3648 | 0.073242 | 122.4426 | 122.5067 | 0.14191 | 0.009155 | 122.4609 | 122.3785 | 0 | 122.493 | 122.4335 | 0.054932 | -0.004577 | 122.6395 | 122.5754 | 122.493 | -0.20142 | 122.5662 | 122.5616 | 122.5204 | -0.18768
3825.5 | 122.7631 | -122.525 | 0.07782 | -0.0078584 | -0.016878 | 0.017415 | 0.036664 | -0.0293 | -0.03381 | -0.014133 | -0.0075532 | 4.9234e-05 | 0.0047275 | -0.095257 | -0.010647 | -0.00017078 | 0.09613 | 0.009155 | 0.027466 | 0.045776 | 0.13733 | 0.004578 | -0.1236 | -0.009155 | 0.041199 | -0.091553 | 0.064087 | 0.064087 | -0.059509 | -0.12817 | 122.5296 | 122.4014 | 0.059509 | 122.5342 | 122.5708 | 0.16937 | 0.01831 | 122.4655 | 122.3969 | -0.013733 | 122.5159 | 122.4335 | 0.036621 | -0.013733 | 122.6624 | 122.6212 | 122.5525 | -0.20142 | 122.5891 | 122.5891 | 122.5662 | -0.20599
3827.2969 | 122.7676 | -122.5433 | 0.11902 | -0.015487 | -0.017733 | 0.018269 | 0.035596 | -0.028446 | -0.039792 | -0.013279 | 7.627e-05 | -0.004437 | 0.0019505 | -0.094616 | -0.014919 | 0.0017518 | 0.11902 | 0.091553 | 0.13275 | 0.10071 | 0.10071 | 0.045776 | -0.091553 | 0.059509 | 0.15106 | 0.041199 | 0.032043 | 0.018311 | -0.027466 | -0.10071 | 122.5891 | 122.4518 | -0.018311 | 122.6349 | 122.644 | 0.19226 | 0 | 122.5159 | 122.4426 | -0.086976 | 122.6028 | 122.5845 | 0.14191 | -0.10071 | 122.644 | 122.6624 | 122.6761 | -0.21057 | 122.5754 | 122.5616 | 122.6944 | -0.21973
3829.1094 | 122.8363 | -122.4884 | 0.082397 | -0.015487 | -0.019228 | 0.015919 | 0.039227 | -0.029514 | -0.038296 | -0.012211 | 7.627e-05 | -0.0012326 | 0.0028049 | -0.094402 | -0.015133 | -0.00017078 | 0.068665 | 0.004578 | 0.045776 | 0.045776 | 0.11902 | 0.022888 | -0.10071 | 0.041199 | 0.10529 | -0.004578 | 0.050354 | 0.041199 | -0.027466 | -0.09613 | 122.5113 | 122.3877 | 0.036622 | 122.493 | 122.5342 | 0.14648 | -0.013732 | 122.4609 | 122.3923 | -0.032043 | 122.5296 | 122.4838 | 0.091552 | -0.041198 | 122.6074 | 122.5571 | 122.5342 | -0.18311 | 122.5388 | 122.5296 | 122.5937 | -0.17853
3830.9062 | 122.6852 | -122.525 | 0.11902 | 0.0074006 | -0.015597 | 0.017842 | 0.037091 | -0.025028 | -0.03851 | -0.01392 | -0.0075532 | -0.0018734 | 0.0021641 | -0.09248 | -0.017056 | -0.0010254 | 0.045776 | -0.013733 | 0.018311 | 0.032043 | 0.13275 | 0.004578 | -0.13275 | -0.054932 | 0.064087 | -0.068665 | 0.091553 | 0.07782 | -0.054932 | -0.14191 | 122.5296 | 122.3923 | 0.013732 | 122.5113 | 122.5571 | 0.16479 | -0.073243 | 122.4701 | 122.3831 | -0.027466 | 122.4701 | 122.4564 | 0.073242 | -0.041199 | 122.6578 | 122.5708 | 122.5433 | -0.25177 | 122.6166 | 122.6028 | 122.5891 | -0.26093
3832.8438 | 122.7722 | -122.5204 | 0.082397 | -0.0078584 | -0.011965 | 0.017201 | 0.039655 | -0.029941 | -0.033169 | -0.013706 | 7.627e-05 | 0.0030398 | 0.0060093 | -0.093334 | -0.013424 | -0.001239 | 0.10529 | 0.027466 | 0.054932 | 0.059509 | 0.14191 | 0.022888 | -0.13275 | 0.004578 | 0.07782 | -0.050354 | 0.07782 | 0.073242 | -0.054932 | -0.12817 | 122.5433 | 122.3877 | 0.05951 | 122.5479 | 122.58 | 0.19226 | 0.022889 | 122.4655 | 122.3923 | -0.004577 | 122.525 | 122.4701 | 0.07782 | -0.009155 | 122.6624 | 122.6257 | 122.5754 | -0.21515 | 122.5983 | 122.5937 | 122.5983 | -0.21057
3834.5938 | 122.8363 | -122.5113 | 0.10071 | -0.00022891 | -0.01581 | 0.016133 | 0.036023 | -0.027805 | -0.037014 | -0.012424 | 7.627e-05 | -0.00059177 | 0.0023777 | -0.093334 | -0.01556 | 0.00025642 | 0.09613 | 0.022888 | 0.086975 | 0.064087 | 0.11902 | 0.032043 | -0.11902 | 0.045776 | 0.1236 | 0.032043 | 0.059509 | 0.054932 | -0.013733 | -0.10071 | 122.5433 | 122.3923 | 0.018311 | 122.5342 | 122.5754 | 0.18311 | -0.004578 | 122.4976 | 122.4106 | -0.041199 | 122.5571 | 122.5433 | 0.13275 | -0.045776 | 122.6303 | 122.6074 | 122.5983 | -0.21973 | 122.5708 | 122.5662 | 122.6349 | -0.20142
3836.4688 | 122.7676 | -122.5433 | 0.10529 | -0.00022891 | -0.020724 | 0.019337 | 0.035169 | -0.028019 | -0.044278 | -0.018192 | -0.015182 | -0.0031552 | 0.00088231 | -0.093975 | -0.018124 | 0.0023926 | 0.10986 | 0.09613 | 0.12817 | 0.10071 | 0.10529 | 0.045776 | -0.09613 | 0.073242 | 0.1831 | 0.091553 | 0.036621 | 0.032043 | -0.022888 | -0.10529 | 122.5891 | 122.4472 | 0 | 122.6395 | 122.644 | 0.19684 | 0.004577 | 122.5204 | 122.438 | -0.068665 | 122.6166 | 122.6349 | 0.19684 | -0.073243 | 122.6486 | 122.6532 | 122.6715 | -0.20142 | 122.58 | 122.5754 | 122.7264 | -0.21057
3838.3125 | 122.7859 | -122.5159 | 0.09613 | -0.0078584 | -0.010897 | 0.013783 | 0.0388 | -0.030796 | -0.034451 | -0.012211 | -0.0075532 | 0.0011172 | 0.0060093 | -0.092907 | -0.014492 | -0.0016662 | 0.12817 | 0.013733 | 0.032043 | 0.045776 | 0.13733 | 0.009155 | -0.13275 | -0.004578 | 0.068665 | -0.073242 | 0.09613 | 0.073242 | -0.054932 | -0.13275 | 122.525 | 122.3831 | 0.041199 | 122.5296 | 122.5616 | 0.17853 | 0.032044 | 122.4609 | 122.3831 | 0 | 122.5113 | 122.4426 | 0.059509 | -0.022888 | 122.6532 | 122.644 | 122.5479 | -0.22888 | 122.612 | 122.5891 | 122.5845 | -0.22888
3840.0781 | 122.8043 | -122.5479 | 0.09613 | -0.0078584 | -0.012606 | 0.013569 | 0.036023 | -0.026737 | -0.032956 | -0.012851 | -0.0075532 | 0.0032534 | 0.0055821 | -0.09248 | -0.013851 | -0.0010254 | 0.09613 | 0.027466 | 0.036621 | 0.054932 | 0.13275 | 0.018311 | -0.12817 | 0.009155 | 0.082397 | -0.054932 | 0.064087 | 0.059509 | -0.054932 | -0.12817 | 122.5662 | 122.4197 | 0.036621 | 122.5754 | 122.6028 | 0.18311 | 0 | 122.493 | 122.4197 | -0.032043 | 122.5571 | 122.493 | 0.073242 | -0.036621 | 122.6807 | 122.644 | 122.5845 | -0.2243 | 122.612 | 122.6074 | 122.6303 | -0.2243
3841.9219 | 122.7859 | -122.5159 | 0.10071 | -0.015487 | -0.015597 | 0.013783 | 0.035809 | -0.030155 | -0.035092 | -0.0094335 | 0.0077058 | 0.00090363 | 0.0025913 | -0.091411 | -0.011715 | 0.00068362 | 0.054932 | -0.045776 | -0.004578 | 0.018311 | 0.1236 | 0.004578 | -0.13275 | -0.082397 | 0.013733 | -0.10529 | 0.082397 | 0.086975 | -0.054932 | -0.13275 | 122.5204 | 122.3831 | 0.022888 | 122.4701 | 122.5342 | 0.15106 | -0.045776 | 122.4609 | 122.3831 | -0.018311 | 122.4335 | 122.4106 | 0.027465 | -0.013733 | 122.6395 | 122.5708 | 122.5113 | -0.23346 | 122.5983 | 122.6028 | 122.5296 | -0.23346
3843.875 | 122.8638 | -122.525 | 0.091553 | 0.0074006 | -0.017733 | 0.01656 | 0.036023 | -0.028019 | -0.038083 | -0.012424 | 7.627e-05 | 0.0013308 | 0.0034457 | -0.092907 | -0.01321 | 0.0023926 | 0.027466 | -0.041199 | 0.009155 | 0.013733 | 0.14648 | 0 | -0.14648 | -0.013733 | 0.045776 | -0.041199 | 0.073242 | 0.091553 | -0.041199 | -0.12817 | 122.525 | 122.3785 | 0.054931 | 122.4838 | 122.5388 | 0.16022 | -0.064087 | 122.4838 | 122.3969 | -0.018311 | 122.5113 | 122.4838 | 0.086975 | 0 | 122.6715 | 122.5525 | 122.5342 | -0.23804 | 122.5983 | 122.6166 | 122.5708 | -0.21973
3846 | 122.7585 | -122.5525 | 0.11444 | -0.0078584 | -0.019869 | 0.018696 | 0.036878 | -0.027805 | -0.044278 | -0.013706 | 0.0077058 | -0.0057186 | 0.0030185 | -0.095043 | -0.018124 | -0.00038438 | 0.045776 | 0.064087 | 0.09613 | 0.073242 | 0.13275 | 0.022888 | -0.09613 | 0.027466 | 0.16022 | 0.050354 | 0.045776 | 0.032043 | -0.018311 | -0.09613 | 122.5754 | 122.4564 | 0.01831 | 122.6166 | 122.6257 | 0.16937 | -0.068665 | 122.5342 | 122.4564 | -0.068665 | 122.58 | 122.6028 | 0.14648 | -0.082398 | 122.6852 | 122.5983 | 122.6486 | -0.21057 | 122.5983 | 122.5845 | 122.7127 | -0.21057
3848.0781 | 122.7036 | -122.5891 | 0.11902 | 0.0074006 | -0.023714 | 0.018483 | 0.035169 | -0.029941 | -0.041928 | -0.016483 | 0.0077058 | -0.004437 | 0.0015231 | -0.096325 | -0.014492 | 0.0011108 | 0.086975 | 0.059509 | 0.091553 | 0.059509 | 0.10071 | 0.068665 | -0.10529 | 0.022888 | 0.07782 | 0.018311 | 0.036621 | 0.045776 | -0.041199 | -0.09613 | 122.6578 | 122.4838 | -0.018311 | 122.6486 | 122.6486 | 0.16479 | -0.032044 | 122.5479 | 122.493 | -0.082398 | 122.612 | 122.6074 | 0.11444 | -0.073243 | 122.6898 | 122.6761 | 122.6807 | -0.22431 | 122.6257 | 122.6349 | 122.6669 | -0.21515
3849.875 | 122.8409 | -122.5433 | 0.086975 | -0.00022891 | -0.015597 | 0.017201 | 0.033246 | -0.029728 | -0.038723 | -0.013706 | 0.0077058 | 0.00090363 | 2.7914e-05 | -0.09312 | -0.011501 | -0.00017078 | 0.032043 | -0.064087 | -0.018311 | 0.009155 | 0.13733 | 0.009155 | -0.13733 | -0.036621 | 0.013733 | -0.064087 | 0.09613 | 0.064087 | -0.059509 | -0.11444 | 122.5525 | 122.406 | 0.050354 | 122.4792 | 122.5525 | 0.14648 | -0.054932 | 122.4838 | 122.4289 | 0.009155 | 122.5067 | 122.4792 | 0.050354 | -0.022888 | 122.6807 | 122.5754 | 122.525 | -0.2243 | 122.6395 | 122.6074 | 122.5571 | -0.20142
3851.6875 | 122.7219 | -122.58 | 0.13733 | -0.00022891 | -0.021792 | 0.016987 | 0.035596 | -0.027591 | -0.040219 | -0.016269 | 7.627e-05 | -0.0033688 | 0.0023777 | -0.094402 | -0.016842 | 0.0034608 | 0.10986 | 0.082397 | 0.1236 | 0.07782 | 0.10071 | 0.050354 | -0.086975 | 0.059509 | 0.11444 | 0.027466 | 0.054932 | 0.036621 | -0.045776 | -0.082397 | 122.6303 | 122.493 | -0.036621 | 122.6624 | 122.6578 | 0.16479 | -0.027466 | 122.5342 | 122.4976 | -0.082397 | 122.6395 | 122.6074 | 0.10986 | -0.10071 | 122.6807 | 122.6898 | 122.7036 | -0.2243 | 122.6349 | 122.6166 | 122.6944 | -0.21973
3853.5469 | 122.731 | -122.5708 | 0.13733 | 0.01503 | -0.017092 | 0.016346 | 0.039868 | -0.026951 | -0.039364 | -0.016697 | -0.0075532 | -0.00059177 | 0.0047275 | -0.095043 | -0.020474 | -0.0018798 | 0.059509 | 0 | 0.045776 | 0.041199 | 0.13275 | 0.013733 | -0.14648 | -0.054932 | 0.059509 | -0.059509 | 0.10986 | 0.068665 | -0.059509 | -0.15564 | 122.5845 | 122.4243 | -0.004578 | 122.5708 | 122.612 | 0.18768 | -0.07782 | 122.5113 | 122.4152 | -0.027466 | 122.5159 | 122.5113 | 0.096131 | -0.068664 | 122.7036 | 122.6303 | 122.6166 | -0.28381 | 122.6807 | 122.6395 | 122.6303 | -0.29297
3855.2656 | 122.8134 | -122.5708 | 0.10986 | 0.0074006 | -0.016451 | 0.013569 | 0.035382 | -0.028446 | -0.03146 | -0.012424 | 0.0077058 | 0.0013308 | 0.0030185 | -0.093334 | -0.01257 | -0.0023072 | 0.041199 | -0.073242 | -0.022888 | -0.004578 | 0.14648 | 0 | -0.12817 | -0.082397 | -0.027466 | -0.13733 | 0.09613 | 0.073242 | -0.073242 | -0.13275 | 122.5708 | 122.4426 | 0.036621 | 122.4976 | 122.5662 | 0.1236 | -0.068664 | 122.4976 | 122.4381 | -0.013733 | 122.4884 | 122.4335 | -0.004578 | -0.036621 | 122.7173 | 122.612 | 122.5479 | -0.23804 | 122.6669 | 122.644 | 122.5433 | -0.24261
3856.9844 | 122.7356 | -122.5754 | 0.12817 | 0.0074006 | -0.017946 | 0.015706 | 0.037305 | -0.028446 | -0.039792 | -0.016056 | -0.0075532 | -0.002728 | 0.0025913 | -0.093975 | -0.017056 | 0.00089722 | 0.10529 | 0.068665 | 0.11902 | 0.082397 | 0.11444 | 0.041199 | -0.073242 | 0.050354 | 0.1236 | 0.018311 | 0.050354 | 0.041199 | -0.022888 | -0.07782 | 122.6166 | 122.5021 | -0.013733 | 122.644 | 122.6578 | 0.15564 | -0.022888 | 122.5525 | 122.4976 | -0.07782 | 122.6257 | 122.5937 | 0.096131 | -0.086975 | 122.6898 | 122.6807 | 122.6944 | -0.20142 | 122.6257 | 122.6166 | 122.699 | -0.20599
3858.7188 | 122.7402 | -122.5983 | 0.11902 | -0.0078584 | -0.020724 | 0.018055 | 0.03645 | -0.0293 | -0.042996 | -0.013065 | 7.627e-05 | -0.002728 | 0.0010959 | -0.096111 | -0.015774 | 0.00089722 | 0.068665 | 0.032043 | 0.073242 | 0.059509 | 0.10529 | 0.036621 | -0.10071 | 0.004578 | 0.09613 | 0.022888 | 0.059509 | 0.036621 | -0.041199 | -0.091553 | 122.6349 | 122.4976 | -0.013733 | 122.6303 | 122.6578 | 0.16022 | -0.050354 | 122.5571 | 122.5067 | -0.05951 | 122.6028 | 122.6212 | 0.11444 | -0.082398 | 122.7036 | 122.6669 | 122.6715 | -0.21973 | 122.6578 | 122.6349 | 122.6944 | -0.21057
3860.4688 | 122.8455 | -122.5342 | 0.073242 | -0.0078584 | -0.014956 | 0.017842 | 0.037305 | -0.028446 | -0.035733 | -0.01392 | 7.627e-05 | -0.00059177 | 0.0025913 | -0.097393 | -0.014919 | -0.00038438 | 0.059509 | -0.027466 | 0.004578 | 0.041199 | 0.13275 | -0.009155 | -0.12817 | -0.036621 | 0.059509 | -0.068665 | 0.082397 | 0.07782 | -0.054932 | -0.13275 | 122.525 | 122.406 | 0.059509 | 122.5067 | 122.5754 | 0.16937 | -0.013733 | 122.4792 | 122.4014 | 0.009155 | 122.4976 | 122.4655 | 0.064086 | 0.004578 | 122.6669 | 122.5937 | 122.5388 | -0.20142 | 122.6166 | 122.612 | 122.5937 | -0.20599
3862.1719 | 122.85 | -122.5662 | 0.086975 | -0.0078584 | -0.017946 | 0.015065 | 0.035382 | -0.029941 | -0.034237 | -0.013706 | -0.015182 | 0.0011172 | 0.0034457 | -0.091411 | -0.013851 | 0.00068362 | 0.036621 | -0.059509 | -0.032043 | 0.004578 | 0.14191 | -0.009155 | -0.13275 | -0.050354 | -0.036621 | -0.10986 | 0.09613 | 0.059509 | -0.082397 | -0.13275 | 122.5571 | 122.4335 | 0.054932 | 122.5067 | 122.5708 | 0.13733 | -0.050354 | 122.4838 | 122.4335 | 0.009155 | 122.5159 | 122.4564 | 0.022888 | -0.027466 | 122.7081 | 122.6028 | 122.5342 | -0.21973 | 122.6624 | 122.6257 | 122.5296 | -0.21973
3863.8906 | 122.8592 | -122.5754 | 0.09613 | -0.0078584 | -0.018374 | 0.014637 | 0.032605 | -0.028232 | -0.035305 | -0.010715 | -0.0075532 | 0.00090363 | 0.0028049 | -0.093975 | -0.011929 | 0.0019654 | 0.027466 | -0.036621 | -0.013733 | 0.018311 | 0.15564 | 0.018311 | -0.13733 | -0.022888 | 0.022888 | -0.059509 | 0.086975 | 0.068665 | -0.064087 | -0.10071 | 122.5937 | 122.438 | 0.05951 | 122.5388 | 122.5937 | 0.15564 | -0.068664 | 122.5113 | 122.4747 | -0.009155 | 122.5525 | 122.5159 | 0.041199 | -0.027465 | 122.731 | 122.6028 | 122.5616 | -0.23346 | 122.6624 | 122.644 | 122.5983 | -0.19684
3865.6562 | 122.8729 | -122.5616 | 0.082397 | -0.00022891 | -0.014315 | 0.016346 | 0.035382 | -0.025669 | -0.03851 | -0.011783 | -0.0075532 | 0.00090363 | 0.0038731 | -0.093548 | -0.014919 | -0.0010254 | 0.059509 | -0.018311 | 0.018311 | 0.054932 | 0.13275 | 0.009155 | -0.12817 | -0.027466 | 0.091553 | -0.041199 | 0.054932 | 0.086975 | -0.068665 | -0.14648 | 122.5708 | 122.4335 | 0.050354 | 122.5433 | 122.6166 | 0.18311 | -0.022888 | 122.493 | 122.4152 | -0.027465 | 122.5342 | 122.5204 | 0.10529 | 0.004578 | 122.6944 | 122.6212 | 122.58 | -0.21057 | 122.6166 | 122.6486 | 122.6532 | -0.22888
3867.4219 | 122.7631 | -122.5937 | 0.12817 | -0.00022891 | -0.021151 | 0.017415 | 0.037732 | -0.028019 | -0.04385 | -0.012424 | 7.627e-05 | -0.0057186 | 0.0019505 | -0.095257 | -0.016628 | 0.003247 | 0.036621 | 0.027466 | 0.086975 | 0.045776 | 0.11902 | 0.032043 | -0.11444 | -0.004578 | 0.09613 | 0.013733 | 0.059509 | 0.041199 | -0.032043 | -0.086975 | 122.6257 | 122.4792 | -0.009155 | 122.6212 | 122.6395 | 0.16022 | -0.091553 | 122.5616 | 122.5067 | -0.068665 | 122.5891 | 122.6074 | 0.10071 | -0.086975 | 122.7127 | 122.6303 | 122.6807 | -0.24262 | 122.6532 | 122.6349 | 122.6898 | -0.21515
3869.1406 | 122.7905 | -122.5662 | 0.10529 | 0.0074006 | -0.021578 | 0.017842 | 0.034101 | -0.028873 | -0.038723 | -0.013492 | 7.627e-05 | -0.0023008 | -0.00061309 | -0.09547 | -0.013424 | 0.00068362 | 0.13733 | 0.091553 | 0.11902 | 0.091553 | 0.082397 | 0.050354 | -0.091553 | 0.054932 | 0.12817 | 0.054932 | 0.036621 | 0.032043 | -0.009155 | -0.086975 | 122.6166 | 122.4747 | -0.022889 | 122.6578 | 122.6578 | 0.18311 | 0.032043 | 122.5571 | 122.4792 | -0.068665 | 122.6212 | 122.6212 | 0.14191 | -0.073243 | 122.6486 | 122.7036 | 122.6852 | -0.19684 | 122.6028 | 122.5983 | 122.6944 | -0.19226
3870.8438 | 122.7768 | -122.58 | 0.1236 | 0.0074006 | -0.023073 | 0.01656 | 0.039655 | -0.030582 | -0.044278 | -0.016483 | 7.627e-05 | -0.005505 | 0.0015231 | -0.094402 | -0.018551 | 0.0015382 | 0.12817 | 0.10986 | 0.14648 | 0.09613 | 0.10986 | 0.045776 | -0.09613 | 0.07782 | 0.19684 | 0.073242 | 0.041199 | 0.041199 | -0.041199 | -0.10986 | 122.6257 | 122.4838 | -0.013733 | 122.6898 | 122.6761 | 0.19226 | 0.004578 | 122.5388 | 122.4701 | -0.082397 | 122.6578 | 122.6532 | 0.18311 | -0.082397 | 122.6898 | 122.7081 | 122.7264 | -0.21973 | 122.6212 | 122.6212 | 122.7768 | -0.23346
3872.5625 | 122.8363 | -122.5754 | 0.091553 | 0.0074006 | -0.016024 | 0.016346 | 0.03645 | -0.02631 | -0.031033 | -0.012424 | -0.0075532 | 0.0028262 | 0.0019505 | -0.093548 | -0.012997 | -0.00038438 | 0.041199 | -0.09613 | -0.036621 | -0.004578 | 0.13733 | 0.004578 | -0.13275 | -0.054932 | -0.013733 | -0.11444 | 0.086975 | 0.07782 | -0.064087 | -0.13733 | 122.58 | 122.4426 | 0.045776 | 122.4792 | 122.5708 | 0.12817 | -0.050354 | 122.5113 | 122.438 | -0.004578 | 122.5204 | 122.4609 | 0.022888 | -0.013733 | 122.7127 | 122.6166 | 122.5388 | -0.2243 | 122.6624 | 122.6532 | 122.5616 | -0.22888
3874.2812 | 122.7676 | -122.5891 | 0.10529 | -0.0078584 | -0.016024 | 0.01656 | 0.039441 | -0.029728 | -0.038083 | -0.015415 | -0.0075532 | -0.00059177 | 0.0021641 | -0.093761 | -0.018124 | -0.00017078 | 0.022888 | -0.036621 | 0 | 0.004578 | 0.14191 | -0.009155 | -0.13275 | -0.059509 | 0.045776 | -0.07782 | 0.091553 | 0.091553 | -0.068665 | -0.13275 | 122.58 | 122.4564 | 0.036621 | 122.5525 | 122.5937 | 0.13733 | -0.082398 | 122.5204 | 122.4564 | -0.013733 | 122.5296 | 122.5113 | 0.054931 | -0.013733 | 122.731 | 122.612 | 122.5891 | -0.23804 | 122.6807 | 122.6807 | 122.6349 | -0.23804
3876.0312 | 122.7905 | -122.5708 | 0.11902 | -0.0078584 | -0.020937 | 0.018055 | 0.037305 | -0.028232 | -0.041928 | -0.013492 | 7.627e-05 | -0.0031552 | 0.0036593 | -0.095684 | -0.018765 | 0.0030334 | 0.10986 | 0.11444 | 0.13733 | 0.10071 | 0.10986 | 0.032043 | -0.09613 | 0.082397 | 0.18768 | 0.091553 | 0.045776 | 0.036621 | -0.032043 | -0.086975 | 122.6028 | 122.4747 | -0.009156 | 122.6852 | 122.6715 | 0.19684 | -0.009156 | 122.5388 | 122.4838 | -0.073243 | 122.6532 | 122.6624 | 0.17853 | -0.082398 | 122.6807 | 122.6807 | 122.7081 | -0.21515 | 122.6166 | 122.6074 | 122.7585 | -0.20599
3877.75 | 122.7676 | -122.6028 | 0.1236 | -0.0078584 | -0.019869 | 0.014424 | 0.033887 | -0.025669 | -0.039364 | -0.014347 | 7.627e-05 | -0.0012326 | 0.00024151 | -0.095898 | -0.014279 | 0.00047002 | 0.13275 | 0.091553 | 0.13275 | 0.091553 | 0.10071 | 0.050354 | -0.086975 | 0.068665 | 0.1236 | 0.027466 | 0.045776 | 0.027466 | -0.022888 | -0.091553 | 122.6532 | 122.5159 | -0.022888 | 122.6944 | 122.6944 | 0.17853 | 0.009155 | 122.58 | 122.5113 | -0.07782 | 122.6715 | 122.6303 | 0.11902 | -0.09613 | 122.7036 | 122.7356 | 122.7356 | -0.21057 | 122.6486 | 122.6303 | 122.7264 | -0.21515
3879.4844 | 122.8409 | -122.5708 | 0.10986 | -0.0078584 | -0.016238 | 0.016346 | 0.038159 | -0.025883 | -0.034451 | -0.012851 | 7.627e-05 | 0.004108 | 0.0034457 | -0.093975 | -0.014065 | -0.0018798 | 0.11902 | 0.022888 | 0.045776 | 0.050354 | 0.14648 | 0.022888 | -0.10529 | 0.004578 | 0.073242 | -0.054932 | 0.073242 | 0.073242 | -0.050354 | -0.11902 | 122.5937 | 122.4655 | 0.036621 | 122.5937 | 122.6212 | 0.15564 | 0.009156 | 122.5204 | 122.4518 | -0.036621 | 122.5754 | 122.5159 | 0.064087 | -0.036621 | 122.7173 | 122.6898 | 122.6166 | -0.21515 | 122.644 | 122.644 | 122.644 | -0.22888
3881.2031 | 122.7493 | -122.6257 | 0.13275 | -0.0078584 | -0.021792 | 0.01656 | 0.036237 | -0.029728 | -0.04086 | -0.012851 | 7.627e-05 | -0.002087 | 0.0017367 | -0.094616 | -0.018124 | -0.001239 | 0.11902 | 0.064087 | 0.10529 | 0.064087 | 0.10529 | 0.036621 | -0.082397 | 0.045776 | 0.10986 | 0.018311 | 0.050354 | 0.041199 | -0.022888 | -0.086975 | 122.6624 | 122.5433 | -0.027465 | 122.6898 | 122.6898 | 0.14648 | -0.013732 | 122.6028 | 122.5388 | -0.082397 | 122.6715 | 122.644 | 0.10529 | -0.091552 | 122.731 | 122.7448 | 122.731 | -0.21515 | 122.6761 | 122.6669 | 122.7356 | -0.21973
3882.9688 | 122.8363 | -122.6028 | 0.10071 | -0.00022891 | -0.018801 | 0.016774 | 0.03645 | -0.025883 | -0.037869 | -0.014133 | 0.015335 | -0.0033688 | 0.0030185 | -0.093761 | -0.01321 | -0.00059818 | 0.14648 | 0.07782 | 0.1236 | 0.10986 | 0.09613 | 0.045776 | -0.09613 | 0.064087 | 0.15106 | 0.045776 | 0.050354 | 0.050354 | -0.032043 | -0.082397 | 122.6486 | 122.5067 | -0.004578 | 122.6807 | 122.7127 | 0.20599 | 0.045776 | 122.5708 | 122.5204 | -0.050354 | 122.6669 | 122.6486 | 0.12817 | -0.050354 | 122.699 | 122.7493 | 122.7264 | -0.19684 | 122.6532 | 122.6532 | 122.7539 | -0.18311
3884.7344 | 122.8592 | -122.5937 | 0.091553 | -0.00022891 | -0.014315 | 0.016346 | 0.034741 | -0.02866 | -0.032315 | -0.012851 | -0.015182 | 0.0021854 | 0.0036593 | -0.094829 | -0.011715 | 4.2822e-05 | 0.12817 | 0.018311 | 0.041199 | 0.050354 | 0.13275 | 0.013733 | -0.12817 | 0.004578 | 0.068665 | -0.073242 | 0.073242 | 0.064087 | -0.054932 | -0.11902 | 122.6074 | 122.4655 | 0.041198 | 122.612 | 122.644 | 0.17853 | 0.036621 | 122.5388 | 122.4747 | -0.018311 | 122.5983 | 122.5204 | 0.045777 | -0.027466 | 122.7264 | 122.7219 | 122.6349 | -0.21973 | 122.6669 | 122.6578 | 122.6624 | -0.21057
3886.4531 | 122.8867 | -122.58 | 0.082397 | 0.0074006 | -0.019015 | 0.015278 | 0.032605 | -0.028232 | -0.03616 | -0.011142 | 7.627e-05 | -0.00016437 | 0.0028049 | -0.091411 | -0.01257 | 0.00089722 | 0.036621 | -0.064087 | -0.022888 | 0.004578 | 0.13733 | 0.004578 | -0.14191 | -0.041199 | -0.004578 | -0.07782 | 0.091553 | 0.073242 | -0.07782 | -0.13275 | 122.5845 | 122.438 | 0.054932 | 122.5159 | 122.5845 | 0.14649 | -0.045776 | 122.5021 | 122.4472 | 0.009156 | 122.5388 | 122.5021 | 0.054931 | -0.009155 | 122.7173 | 122.6166 | 122.5571 | -0.2243 | 122.6715 | 122.6532 | 122.5754 | -0.21515
3888.2188 | 122.7448 | -122.612 | 0.13733 | 0.0074006 | -0.017946 | 0.019123 | 0.040082 | -0.026951 | -0.040432 | -0.01392 | 7.627e-05 | -0.002728 | 0.0034457 | -0.09547 | -0.015988 | 0.0013244 | 0.073242 | 0.082397 | 0.10529 | 0.082397 | 0.10986 | 0.041199 | -0.10986 | 0 | 0.13733 | 0 | 0.054932 | 0.036621 | -0.045776 | -0.11444 | 122.6532 | 122.5021 | -0.027466 | 122.6944 | 122.6944 | 0.19226 | -0.064087 | 122.5662 | 122.4976 | -0.082397 | 122.612 | 122.612 | 0.11444 | -0.10071 | 122.7219 | 122.6852 | 122.7173 | -0.24719 | 122.6669 | 122.6486 | 122.7493 | -0.25177
3889.9219 | 122.85 | -122.5845 | 0.091553 | -0.00022891 | -0.015383 | 0.01656 | 0.034314 | -0.030155 | -0.034451 | -0.014988 | 7.627e-05 | 0.0026126 | 0.0013095 | -0.091198 | -0.011501 | 0.0013244 | 0.027466 | -0.07782 | -0.032043 | 0 | 0.16022 | 0.004578 | -0.15106 | -0.059509 | -0.009155 | -0.086975 | 0.09613 | 0.068665 | -0.054932 | -0.12817 | 122.5891 | 122.4335 | 0.068664 | 122.5067 | 122.5845 | 0.15106 | -0.064087 | 122.5296 | 122.4564 | 0.004577 | 122.525 | 122.4976 | 0.041199 | -0.022888 | 122.7448 | 122.612 | 122.5525 | -0.24261 | 122.6807 | 122.6532 | 122.5754 | -0.21973
3891.6406 | 122.8226 | -122.612 | 0.10071 | -0.00022891 | -0.020937 | 0.019551 | 0.039441 | -0.0293 | -0.042782 | -0.01392 | 7.627e-05 | -0.0052914 | -0.00061309 | -0.09547 | -0.018765 | 0.002179 | 0.10071 | 0.086975 | 0.13275 | 0.10071 | 0.11902 | 0.027466 | -0.10529 | 0.068665 | 0.19684 | 0.09613 | 0.036621 | 0.032043 | -0.018311 | -0.09613 | 122.6395 | 122.5067 | 0.018311 | 122.699 | 122.7127 | 0.20599 | 0 | 122.5937 | 122.5159 | -0.064087 | 122.6807 | 122.7081 | 0.19226 | -0.068665 | 122.731 | 122.7127 | 122.7448 | -0.20599 | 122.6486 | 122.644 | 122.8088 | -0.19684
3893.375 | 122.7814 | -122.6257 | 0.13275 | -0.015487 | -0.016024 | 0.017628 | 0.039227 | -0.0293 | -0.04086 | -0.015629 | 7.627e-05 | -0.0031552 | 0.00066871 | -0.092907 | -0.016628 | 0.00089722 | 0.082397 | 0.041199 | 0.10529 | 0.054932 | 0.10071 | 0.036621 | -0.091553 | 0.036621 | 0.10529 | 0.009155 | 0.059509 | 0.041199 | -0.022888 | -0.09613 | 122.6624 | 122.5342 | -0.032043 | 122.6669 | 122.6807 | 0.14649 | -0.050354 | 122.6028 | 122.5296 | -0.073242 | 122.6624 | 122.6349 | 0.10528 | -0.091552 | 122.7264 | 122.7081 | 122.731 | -0.2243 | 122.6852 | 122.6669 | 122.731 | -0.22888
3895.125 | 122.7676 | -122.6395 | 0.12817 | -0.00022891 | -0.019228 | 0.018696 | 0.037946 | -0.027378 | -0.039792 | -0.014347 | 0.0077058 | -0.0016598 | -0.00061309 | -0.095898 | -0.015347 | 0.00089722 | 0.1236 | 0.082397 | 0.10986 | 0.082397 | 0.11444 | 0.045776 | -0.091553 | 0.045776 | 0.1236 | 0.018311 | 0.073242 | 0.018311 | -0.027466 | -0.10071 | 122.6852 | 122.5479 | -0.013733 | 122.7219 | 122.7219 | 0.17395 | -0.004578 | 122.612 | 122.5388 | -0.054932 | 122.6852 | 122.6578 | 0.11902 | -0.10986 | 122.7539 | 122.7631 | 122.7493 | -0.21973 | 122.7127 | 122.6578 | 122.7631 | -0.22888
3896.8438 | 122.9141 | -122.5754 | 0.091553 | -0.00022891 | -0.016878 | 0.017628 | 0.033887 | -0.028446 | -0.03381 | -0.014347 | 7.627e-05 | 0.0013308 | -0.00039949 | -0.095257 | -0.0093652 | -0.001239 | 0.054932 | -0.045776 | -0.009155 | 0.004578 | 0.15564 | 0.004578 | -0.14648 | -0.009155 | 0.013733 | -0.073242 | 0.07782 | 0.059509 | -0.036621 | -0.11902 | 122.58 | 122.4289 | 0.064087 | 122.5296 | 122.58 | 0.15106 | -0.036621 | 122.5388 | 122.4564 | -0.013733 | 122.5662 | 122.5021 | 0.045777 | -0.032044 | 122.731 | 122.6303 | 122.5662 | -0.23804 | 122.6532 | 122.6349 | 122.5891 | -0.21057
3898.6094 | 122.7722 | -122.6074 | 0.12817 | 0.0074006 | -0.018587 | 0.016774 | 0.038587 | -0.027378 | -0.041501 | -0.01456 | 7.627e-05 | -0.0023008 | -0.00018589 | -0.098247 | -0.017697 | 4.2822e-05 | 0.12817 | 0.11444 | 0.13275 | 0.10529 | 0.10071 | 0.045776 | -0.10529 | 0.059509 | 0.1831 | 0.045776 | 0.041199 | 0.041199 | -0.022888 | -0.091553 | 122.6532 | 122.5021 | -0.027466 | 122.7219 | 122.7127 | 0.21057 | 0 | 122.5845 | 122.5159 | -0.086975 | 122.6669 | 122.6532 | 0.13733 | -0.086975 | 122.7081 | 122.7356 | 122.7402 | -0.23346 | 122.6486 | 122.6486 | 122.7905 | -0.21973
3900.5 | 122.7768 | -122.6349 | 0.11444 | 0.0074006 | -0.016665 | 0.018483 | 0.038587 | -0.031223 | -0.039792 | -0.015201 | 0.0077058 | -0.0018734 | 0.0021641 | -0.093975 | -0.014492 | -0.00081178 | 0.11902 | 0.10529 | 0.13275 | 0.09613 | 0.10071 | 0.027466 | -0.09613 | 0.045776 | 0.16937 | 0.059509 | 0.050354 | 0.032043 | -0.022888 | -0.10529 | 122.6624 | 122.5388 | -0.013733 | 122.7402 | 122.731 | 0.19226 | 0.004578 | 122.612 | 122.5296 | -0.064087 | 122.6807 | 122.6944 | 0.16479 | -0.082398 | 122.7356 | 122.7539 | 122.7676 | -0.21057 | 122.6852 | 122.6669 | 122.8043 | -0.21973
3902.3125 | 122.8088 | -122.6578 | 0.13733 | -0.00022891 | -0.023073 | 0.020619 | 0.033887 | -0.029087 | -0.039578 | -0.014774 | -0.0075532 | -0.0016598 | 2.7914e-05 | -0.09547 | -0.014279 | 0.0023926 | 0.059509 | 0.032043 | 0.073242 | 0.050354 | 0.11902 | 0.022888 | -0.082397 | 0.018311 | 0.10071 | 0.013733 | 0.054932 | 0.064087 | -0.032043 | -0.10529 | 122.6807 | 122.5754 | -0.01831 | 122.6898 | 122.7081 | 0.13275 | -0.07782 | 122.6257 | 122.5525 | -0.082397 | 122.6761 | 122.6715 | 0.11902 | -0.073242 | 122.7768 | 122.7173 | 122.731 | -0.21973 | 122.7127 | 122.7219 | 122.7585 | -0.24262
3904.0469 | 122.8867 | -122.5891 | 0.07782 | -0.00022891 | -0.01816 | 0.016346 | 0.036664 | -0.029941 | -0.032528 | -0.012211 | -0.015182 | 0.0032534 | 0.00088231 | -0.092907 | -0.011715 | -0.0014526 | 0.11902 | 0.022888 | 0.032043 | 0.050354 | 0.13275 | 0.009155 | -0.11902 | 0.018311 | 0.091553 | -0.064087 | 0.07782 | 0.068665 | -0.036621 | -0.11444 | 122.5983 | 122.4701 | 0.054931 | 122.612 | 122.6395 | 0.16937 | 0.041199 | 122.5525 | 122.4747 | 0 | 122.6074 | 122.525 | 0.050354 | -0.009155 | 122.7219 | 122.7081 | 122.6212 | -0.19684 | 122.6669 | 122.6578 | 122.6807 | -0.19226
3905.8438 | 122.8317 | -122.644 | 0.11902 | -0.0078584 | -0.020083 | 0.020832 | 0.037732 | -0.029941 | -0.043637 | -0.014347 | -0.015182 | -0.0070004 | 0.0015231 | -0.095898 | -0.016201 | 0.0030334 | 0.045776 | 0.036621 | 0.10071 | 0.068665 | 0.11902 | 0.009155 | -0.11902 | 0.018311 | 0.11444 | 0.050354 | 0.059509 | 0.036621 | -0.032043 | -0.10071 | 122.6532 | 122.525 | 0 | 122.6807 | 122.7127 | 0.18768 | -0.073243 | 122.612 | 122.5433 | -0.05951 | 122.6624 | 122.6944 | 0.15106 | -0.082398 | 122.7631 | 122.6898 | 122.7448 | -0.23804 | 122.7036 | 122.6807 | 122.7585 | -0.21973
3907.6562 | 122.9279 | -122.5937 | 0.091553 | -0.0078584 | -0.016451 | 0.015278 | 0.033032 | -0.027805 | -0.03381 | -0.012424 | 7.627e-05 | 0.0011172 | -0.00018589 | -0.09312 | -0.011929 | -0.00081178 | 0.059509 | -0.027466 | -0.009155 | 0 | 0.14191 | 0 | -0.12817 | -0.018311 | 0.027466 | -0.045776 | 0.073242 | 0.054932 | -0.032043 | -0.11444 | 122.5937 | 122.4655 | 0.050354 | 122.5662 | 122.5937 | 0.12817 | -0.032044 | 122.5616 | 122.4792 | -0.018311 | 122.5754 | 122.5479 | 0.068665 | -0.036621 | 122.7356 | 122.6532 | 122.5845 | -0.21973 | 122.6669 | 122.6486 | 122.6212 | -0.20599
3909.3906 | 122.7722 | -122.6166 | 0.13733 | -0.0078584 | -0.017092 | 0.01891 | 0.037518 | -0.029728 | -0.039578 | -0.013492 | -0.015182 | -0.00059177 | 0.0021641 | -0.095257 | -0.017483 | 0.00047002 | 0.10071 | 0.059509 | 0.086975 | 0.068665 | 0.11444 | 0.018311 | -0.11444 | -0.018311 | 0.10071 | -0.032043 | 0.068665 | 0.091553 | -0.059509 | -0.1236 | 122.6349 | 122.5021 | -0.022888 | 122.6761 | 122.6852 | 0.18311 | -0.036621 | 122.5571 | 122.493 | -0.068664 | 122.5983 | 122.5845 | 0.091553 | -0.045776 | 122.731 | 122.7173 | 122.7036 | -0.25177 | 122.6852 | 122.7081 | 122.7173 | -0.26093
3911.1875 | 122.9141 | -122.6212 | 0.07782 | -0.015487 | -0.018374 | 0.013997 | 0.036237 | -0.0293 | -0.033596 | -0.012638 | 7.627e-05 | 0.0026126 | 0.0025913 | -0.092907 | -0.012997 | -0.002948 | 0.10071 | 0.009155 | 0.022888 | 0.054932 | 0.14191 | 0 | -0.13275 | 0.013733 | 0.086975 | -0.054932 | 0.07782 | 0.064087 | -0.059509 | -0.11444 | 122.6212 | 122.4884 | 0.064087 | 122.6303 | 122.6761 | 0.18768 | 0.022888 | 122.5616 | 122.5067 | 0 | 122.6349 | 122.5662 | 0.059509 | -0.013733 | 122.7631 | 122.7219 | 122.644 | -0.21057 | 122.699 | 122.6852 | 122.7081 | -0.19226
3912.9219 | 122.9187 | -122.58 | 0.073242 | -0.00022891 | -0.017946 | 0.016346 | 0.036023 | -0.027591 | -0.034237 | -0.013706 | 0.0077058 | 0.0026126 | 0.0015231 | -0.092052 | -0.012997 | 4.2822e-05 | 0.10071 | -0.004578 | 0.018311 | 0.050354 | 0.14191 | -0.004578 | -0.16479 | 0.009155 | 0.10071 | -0.050354 | 0.068665 | 0.064087 | -0.041199 | -0.11902 | 122.5754 | 122.4152 | 0.068665 | 122.5754 | 122.6303 | 0.21515 | 0.027466 | 122.5388 | 122.4609 | -0.004577 | 122.5891 | 122.5296 | 0.068665 | -0.009155 | 122.7219 | 122.6807 | 122.5983 | -0.23804 | 122.6486 | 122.644 | 122.6807 | -0.19226
3914.7188 | 122.8363 | -122.6395 | 0.12817 | -0.00022891 | -0.020296 | 0.014637 | 0.034528 | -0.028446 | -0.039578 | -0.014347 | 7.627e-05 | -0.0033688 | 0.0013095 | -0.094829 | -0.01556 | 0.0019654 | 0.11902 | 0.10071 | 0.13275 | 0.10071 | 0.091553 | 0.036621 | -0.11444 | 0.073242 | 0.15106 | 0.050354 | 0.041199 | 0.032043 | -0.036621 | -0.10071 | 122.6761 | 122.525 | -0.036621 | 122.7402 | 122.7402 | 0.21515 | -0.009155 | 122.6028 | 122.5388 | -0.086975 | 122.7127 | 122.6898 | 0.15106 | -0.096131 | 122.731 | 122.7585 | 122.7722 | -0.24262 | 122.6807 | 122.6715 | 122.7905 | -0.22888
3916.5156 | 122.9187 | -122.6303 | 0.09613 | -0.0078584 | -0.01816 | 0.017842 | 0.035382 | -0.029087 | -0.036374 | -0.011997 | 7.627e-05 | -0.001019 | 0.0030185 | -0.09312 | -0.01257 | 0.0019654 | 0.041199 | -0.068665 | -0.045776 | 0.009155 | 0.15106 | 0.004578 | -0.15106 | -0.032043 | 0.013733 | -0.07782 | 0.073242 | 0.073242 | -0.064087 | -0.12817 | 122.6349 | 122.4792 | 0.054932 | 122.5616 | 122.6395 | 0.16022 | -0.054931 | 122.5662 | 122.5021 | -0.022888 | 122.5983 | 122.5525 | 0.050354 | -0.022888 | 122.7814 | 122.6715 | 122.5845 | -0.24719 | 122.7036 | 122.7036 | 122.644 | -0.2243
3918.2344 | 122.7859 | -122.6486 | 0.13733 | -0.00022891 | -0.023287 | 0.018269 | 0.033246 | -0.030796 | -0.042569 | -0.013492 | -0.0075532 | -0.0023008 | 0.0010959 | -0.096752 | -0.017269 | 0.003247 | 0.086975 | 0.041199 | 0.086975 | 0.050354 | 0.082397 | 0.022888 | -0.091553 | 0.018311 | 0.10529 | 0.009155 | 0.041199 | 0.045776 | -0.032043 | -0.09613 | 122.6715 | 122.5571 | -0.054932 | 122.6898 | 122.699 | 0.14191 | -0.050354 | 122.6166 | 122.5525 | -0.09613 | 122.6669 | 122.6578 | 0.10528 | -0.091553 | 122.731 | 122.7356 | 122.7356 | -0.22888 | 122.6898 | 122.6944 | 122.7539 | -0.23346
3920.0156 | 122.8088 | -122.6486 | 0.12817 | -0.0078584 | -0.020937 | 0.018696 | 0.036664 | -0.029514 | -0.039578 | -0.01456 | -0.0075532 | 4.9234e-05 | 0.00066871 | -0.094189 | -0.012783 | 0.0019654 | 0.13275 | 0.07782 | 0.1236 | 0.09613 | 0.11444 | 0.036621 | -0.10529 | 0.059509 | 0.12817 | 0.041199 | 0.045776 | 0.036621 | -0.032043 | -0.10071 | 122.6852 | 122.5433 | -0.013733 | 122.7264 | 122.7448 | 0.20142 | 0.004577 | 122.6166 | 122.5479 | -0.082398 | 122.7081 | 122.6898 | 0.14191 | -0.091553 | 122.7631 | 122.7814 | 122.7722 | -0.23346 | 122.6944 | 122.6852 | 122.7768 | -0.22888
3921.7969 | 122.9187 | -122.6257 | 0.086975 | -0.00022891 | -0.017946 | 0.014851 | 0.038159 | -0.030155 | -0.03381 | -0.013279 | 7.627e-05 | 0.0043216 | 0.0038731 | -0.092266 | -0.014065 | -0.001239 | 0.054932 | -0.082397 | -0.027466 | 0.004578 | 0.13275 | 0.013733 | -0.13275 | -0.045776 | -0.013733 | -0.091553 | 0.091553 | 0.082397 | -0.059509 | -0.13275 | 122.6395 | 122.493 | 0.045776 | 122.5433 | 122.6303 | 0.13733 | -0.032043 | 122.5662 | 122.493 | 0.004578 | 122.58 | 122.5342 | 0.041198 | -0.004578 | 122.7585 | 122.6807 | 122.5983 | -0.21973 | 122.7173 | 122.7081 | 122.612 | -0.21973
3923.5781 | 122.8775 | -122.6349 | 0.091553 | -0.00022891 | -0.017946 | 0.015706 | 0.035169 | -0.027805 | -0.033383 | -0.01456 | 7.627e-05 | 0.00090363 | 0.0040867 | -0.093334 | -0.012142 | 0.0011108 | 0.086975 | -0.018311 | 0.009155 | 0.032043 | 0.10986 | -0.013733 | -0.14648 | -0.041199 | 0.013733 | -0.086975 | 0.073242 | 0.068665 | -0.064087 | -0.12817 | 122.6212 | 122.4884 | 0.01831 | 122.6166 | 122.6669 | 0.17853 | -0.004578 | 122.5708 | 122.5067 | -0.018311 | 122.5937 | 122.5479 | 0.041199 | -0.022888 | 122.7448 | 122.7219 | 122.644 | -0.23804 | 122.7081 | 122.7036 | 122.6486 | -0.21973
3925.3125 | 122.937 | -122.6212 | 0.086975 | -0.00022891 | -0.017306 | 0.01421 | 0.03645 | -0.028873 | -0.035519 | -0.014133 | 0.0077058 | 0.00047643 | 0.0021641 | -0.094829 | -0.013851 | 0.00089722 | 0.032043 | -0.050354 | -0.013733 | 0.009155 | 0.15564 | 0.009155 | -0.14648 | -0.022888 | 0.022888 | -0.050354 | 0.09613 | 0.054932 | -0.054932 | -0.11902 | 122.6303 | 122.4747 | 0.068665 | 122.5708 | 122.6303 | 0.15564 | -0.054932 | 122.5662 | 122.5021 | 0.009155 | 122.5983 | 122.5708 | 0.068665 | -0.032043 | 122.7768 | 122.6532 | 122.6074 | -0.23346 | 122.7173 | 122.6761 | 122.644 | -0.20599
3927.1094 | 122.818 | -122.6532 | 0.11902 | 0.0074006 | -0.020083 | 0.017628 | 0.035596 | -0.02631 | -0.041287 | -0.012851 | -0.015182 | -0.0040096 | 0.00088231 | -0.094616 | -0.017056 | 0.0026062 | 0.11902 | 0.086975 | 0.1236 | 0.091553 | 0.082397 | 0.027466 | -0.086975 | 0.050354 | 0.1236 | 0.032043 | 0.064087 | 0.027466 | -0.022888 | -0.10071 | 122.6807 | 122.5662 | -0.036622 | 122.7402 | 122.7448 | 0.17853 | 0 | 122.6303 | 122.5525 | -0.054932 | 122.7036 | 122.6852 | 0.13275 | -0.091553 | 122.7356 | 122.7722 | 122.7768 | -0.20599 | 122.7173 | 122.6807 | 122.7768 | -0.21973
3928.9062 | 122.8912 | -122.6578 | 0.10529 | -0.00022891 | -0.015383 | 0.015706 | 0.035809 | -0.025883 | -0.036374 | -0.01157 | -0.0075532 | 0.0026126 | 0.0032321 | -0.093761 | -0.01321 | -0.00038438 | 0.036621 | -0.082397 | -0.022888 | 0.018311 | 0.12817 | 0.004578 | -0.13275 | -0.082397 | -0.018311 | -0.13275 | 0.086975 | 0.073242 | -0.059509 | -0.13733 | 122.6624 | 122.525 | 0.022888 | 122.5754 | 122.6761 | 0.15106 | -0.068665 | 122.5983 | 122.5204 | -0.018311 | 122.5754 | 122.525 | 0.004578 | -0.032044 | 122.7859 | 122.6944 | 122.6349 | -0.23804 | 122.7448 | 122.731 | 122.6395 | -0.24262
3930.7031 | 122.8271 | -122.6944 | 0.10986 | -0.00022891 | -0.02286 | 0.017842 | 0.033887 | -0.027591 | -0.042996 | -0.014347 | -0.015182 | -0.002728 | 0.0021641 | -0.094829 | -0.016415 | 0.00089722 | 0.10986 | 0.10071 | 0.11902 | 0.07782 | 0.082397 | 0.050354 | -0.10071 | 0.050354 | 0.14648 | 0.041199 | 0.032043 | 0.027466 | -0.027466 | -0.082397 | 122.7448 | 122.5937 | -0.027466 | 122.7951 | 122.7722 | 0.17853 | 0 | 122.6669 | 122.612 | -0.07782 | 122.7448 | 122.7356 | 0.1236 | -0.082397 | 122.7768 | 122.8043 | 122.8134 | -0.21057 | 122.7264 | 122.7219 | 122.8409 | -0.19226
3932.5 | 122.937 | -122.6074 | 0.068665 | 0.0074006 | -0.01581 | 0.016346 | 0.035169 | -0.028873 | -0.037869 | -0.013492 | 7.627e-05 | 0.0017582 | 0.0019505 | -0.093975 | -0.014065 | -0.00017078 | 0.032043 | -0.045776 | 0.009155 | 0.009155 | 0.13733 | 0.022888 | -0.13275 | -0.027466 | 0.022888 | -0.054932 | 0.07782 | 0.059509 | -0.050354 | -0.1236 | 122.6303 | 122.4747 | 0.068664 | 122.5616 | 122.6166 | 0.14191 | -0.036622 | 122.5571 | 122.4838 | 0.009155 | 122.58 | 122.5525 | 0.068664 | -0.009156 | 122.7448 | 122.6395 | 122.6166 | -0.20142 | 122.6852 | 122.6669 | 122.6303 | -0.19226
3934.2812 | 122.9507 | -122.6395 | 0.086975 | -0.00022891 | -0.017092 | 0.015065 | 0.037518 | -0.031009 | -0.036374 | -0.013706 | 7.627e-05 | 0.00069003 | 0.0036593 | -0.091839 | -0.015133 | -0.00059818 | 0.050354 | -0.036621 | 0 | 0.013733 | 0.15564 | 0.009155 | -0.12817 | 0 | 0.045776 | -0.041199 | 0.068665 | 0.064087 | -0.050354 | -0.10529 | 122.6486 | 122.5113 | 0.068665 | 122.6028 | 122.6532 | 0.14191 | -0.036621 | 122.5891 | 122.5342 | -0.01831 | 122.6395 | 122.5983 | 0.064087 | -0.022888 | 122.7951 | 122.6898 | 122.6395 | -0.21515 | 122.7081 | 122.7036 | 122.6852 | -0.19226
3936.0156 | 122.9553 | -122.6028 | 0.10071 | -0.00022891 | -0.019442 | 0.015278 | 0.035382 | -0.029514 | -0.037014 | -0.013279 | -0.0075532 | -0.00059177 | 0.0021641 | -0.09248 | -0.015133 | 0.00025642 | 0.050354 | -0.041199 | 0.013733 | 0.018311 | 0.13733 | 0.013733 | -0.10529 | 0.018311 | 0.07782 | -0.022888 | 0.054932 | 0.054932 | -0.036621 | -0.10529 | 122.6166 | 122.4976 | 0.036621 | 122.5616 | 122.6212 | 0.1236 | -0.050354 | 122.5662 | 122.4976 | -0.045776 | 122.6212 | 122.58 | 0.082398 | -0.045776 | 122.7402 | 122.6532 | 122.6166 | -0.20599 | 122.6578 | 122.6578 | 122.6807 | -0.20599
3937.7969 | 122.9553 | -122.6166 | 0.091553 | -0.00022891 | -0.016665 | 0.016774 | 0.03645 | -0.027164 | -0.036374 | -0.012424 | 0.0077058 | 0.0019718 | 0.0053683 | -0.093975 | -0.012783 | -0.00059818 | 0.032043 | -0.064087 | -0.022888 | 0.013733 | 0.14191 | 0.004578 | -0.13275 | -0.036621 | 0.004578 | -0.07782 | 0.073242 | 0.064087 | -0.059509 | -0.13733 | 122.6212 | 122.4838 | 0.050354 | 122.5525 | 122.6303 | 0.14648 | -0.05951 | 122.5571 | 122.4792 | -0.018311 | 122.58 | 122.5388 | 0.059509 | -0.027466 | 122.7585 | 122.6486 | 122.5937 | -0.2243 | 122.6898 | 122.6807 | 122.6212 | -0.22888
3939.5938 | 122.9553 | -122.6578 | 0.082397 | -0.0078584 | -0.017519 | 0.016133 | 0.034741 | -0.02866 | -0.038083 | -0.01392 | 0.015335 | 0.0011172 | 0.0021641 | -0.093548 | -0.014065 | 4.2822e-05 | 0.036621 | -0.022888 | 0.027466 | 0.027466 | 0.14191 | 0.009155 | -0.11902 | -0.004578 | 0.064087 | -0.027466 | 0.054932 | 0.045776 | -0.036621 | -0.10071 | 122.6669 | 122.5388 | 0.05951 | 122.6349 | 122.6852 | 0.14649 | -0.045776 | 122.6212 | 122.5571 | -0.027465 | 122.6532 | 122.6303 | 0.073242 | -0.036621 | 122.7997 | 122.6944 | 122.6852 | -0.20142 | 122.7127 | 122.7036 | 122.7219 | -0.18311
3941.4062 | 122.7951 | -122.6944 | 0.10986 | -0.0078584 | -0.017306 | 0.018269 | 0.040082 | -0.027378 | -0.041501 | -0.016056 | 0.0077058 | -0.0012326 | 0.0030185 | -0.094402 | -0.017269 | 0.00068362 | 0.11444 | 0.086975 | 0.13733 | 0.091553 | 0.086975 | 0.050354 | -0.10986 | 0.027466 | 0.17395 | 0.050354 | 0.059509 | 0.041199 | -0.032043 | -0.086975 | 122.7448 | 122.5845 | -0.022888 | 122.7814 | 122.7859 | 0.20142 | 0.004578 | 122.6624 | 122.6074 | -0.050354 | 122.7219 | 122.7448 | 0.13733 | -0.068664 | 122.7814 | 122.8088 | 122.8317 | -0.21973 | 122.7539 | 122.7356 | 122.8683 | -0.19684
3943.125 | 122.8958 | -122.6578 | 0.086975 | 0.0074006 | -0.01581 | 0.015919 | 0.035382 | -0.026523 | -0.034237 | -0.01157 | -0.015182 | 0.0026126 | 0.0023777 | -0.092266 | -0.015347 | 0.00025642 | 0.073242 | -0.036621 | 0.009155 | 0.032043 | 0.11902 | 0.009155 | -0.13275 | -0.041199 | 0.004578 | -0.09613 | 0.082397 | 0.091553 | -0.068665 | -0.13275 | 122.6669 | 122.525 | 0.032044 | 122.6212 | 122.6898 | 0.16479 | -0.013733 | 122.5891 | 122.525 | -0.004578 | 122.6166 | 122.5616 | 0.036621 | 0.004578 | 122.7768 | 122.731 | 122.6669 | -0.21973 | 122.7402 | 122.7493 | 122.6624 | -0.21973
3944.9375 | 122.9507 | -122.644 | 0.086975 | -0.0078584 | -0.017092 | 0.016774 | 0.035809 | -0.027378 | -0.036801 | -0.011997 | 7.627e-05 | 0.0017582 | 0.0034457 | -0.094829 | -0.015133 | -0.00038438 | 0.032043 | -0.036621 | 0 | 0.022888 | 0.13733 | 0.004578 | -0.13733 | -0.041199 | 0.07782 | -0.059509 | 0.07782 | 0.064087 | -0.059509 | -0.12817 | 122.6486 | 122.5067 | 0.050354 | 122.6074 | 122.6669 | 0.16022 | -0.054932 | 122.5845 | 122.5159 | -0.009155 | 122.6028 | 122.5845 | 0.068665 | -0.022888 | 122.7814 | 122.6761 | 122.644 | -0.2243 | 122.7219 | 122.7081 | 122.7219 | -0.21515
3946.7344 | 122.818 | -122.6898 | 0.1236 | -0.0078584 | -0.019442 | 0.017842 | 0.039014 | -0.026737 | -0.039364 | -0.016483 | 7.627e-05 | 0.00026283 | 0.0036593 | -0.093761 | -0.019833 | 0.002179 | 0.054932 | 0 | 0.022888 | 0.036621 | 0.11902 | 0.009155 | -0.13275 | -0.059509 | 0.050354 | -0.059509 | 0.073242 | 0.086975 | -0.07782 | -0.11444 | 122.699 | 122.5571 | -0.004577 | 122.6898 | 122.7264 | 0.16937 | -0.068664 | 122.612 | 122.5754 | -0.050354 | 122.6303 | 122.6303 | 0.054932 | -0.036621 | 122.8088 | 122.7448 | 122.7127 | -0.25635 | 122.7631 | 122.7768 | 122.7402 | -0.23804
3948.5312 | 122.8455 | -122.6898 | 0.10986 | -0.0078584 | -0.02051 | 0.015919 | 0.038587 | -0.028446 | -0.03851 | -0.014988 | 0.0077058 | 0.0013308 | 0.0028049 | -0.093334 | -0.017483 | 4.2822e-05 | 0.018311 | -0.054932 | -0.004578 | 0.004578 | 0.15106 | -0.009155 | -0.15106 | -0.068665 | 0.032043 | -0.082397 | 0.09613 | 0.073242 | -0.068665 | -0.1236 | 122.6807 | 122.5388 | 0.041199 | 122.6349 | 122.6944 | 0.15564 | -0.091552 | 122.6212 | 122.5662 | -0.013733 | 122.6212 | 122.6074 | 0.041199 | -0.036621 | 122.8409 | 122.7081 | 122.6852 | -0.26093 | 122.7859 | 122.7631 | 122.7219 | -0.23346
3950.2656 | 122.8592 | -122.6852 | 0.10071 | -0.00022891 | -0.021578 | 0.018055 | 0.035596 | -0.029728 | -0.041928 | -0.015201 | 7.627e-05 | -0.0029416 | 0.00066871 | -0.094402 | -0.017056 | 0.0017518 | 0.036621 | 0.018311 | 0.073242 | 0.054932 | 0.11444 | 0.045776 | -0.11902 | -0.009155 | 0.10071 | 0.032043 | 0.054932 | 0.054932 | -0.041199 | -0.10071 | 122.731 | 122.5662 | 0.013733 | 122.7036 | 122.7402 | 0.17395 | -0.064087 | 122.644 | 122.5845 | -0.045776 | 122.6761 | 122.7173 | 0.13275 | -0.045776 | 122.7997 | 122.7219 | 122.7585 | -0.21973 | 122.7402 | 122.7402 | 122.7859 | -0.20142
3952.0625 | 122.9187 | -122.6624 | 0.07782 | 0.0074006 | -0.012179 | 0.01421 | 0.038587 | -0.026523 | -0.031674 | -0.012851 | 0.0077058 | 0.002399 | 0.0047275 | -0.091839 | -0.014279 | -0.0014526 | 0.027466 | -0.082397 | -0.032043 | 0 | 0.15106 | -0.004578 | -0.14191 | -0.059509 | -0.022888 | -0.11444 | 0.07782 | 0.068665 | -0.064087 | -0.13733 | 122.6578 | 122.5204 | 0.073242 | 122.58 | 122.6624 | 0.14191 | -0.050354 | 122.5983 | 122.525 | 0 | 122.6028 | 122.5479 | 0.022888 | -0.009155 | 122.8134 | 122.6898 | 122.6303 | -0.21973 | 122.7402 | 122.731 | 122.6395 | -0.21515
3953.7969 | 122.9187 | -122.6486 | 0.10071 | -0.0078584 | -0.015169 | 0.017842 | 0.035382 | -0.028446 | -0.035092 | -0.013279 | 7.627e-05 | 0.0019718 | 0.0013095 | -0.094402 | -0.011929 | -0.0018798 | 0.086975 | 0.004578 | 0.036621 | 0.045776 | 0.13733 | 0.009155 | -0.13275 | 0.018311 | 0.09613 | -0.036621 | 0.068665 | 0.064087 | -0.054932 | -0.13275 | 122.6578 | 122.5159 | 0.036621 | 122.6532 | 122.6944 | 0.17853 | -0.013733 | 122.5937 | 122.5159 | -0.032043 | 122.6669 | 122.612 | 0.09613 | -0.036621 | 122.7859 | 122.7356 | 122.6852 | -0.23346 | 122.7173 | 122.7127 | 122.7448 | -0.23346
3955.5781 | 122.9233 | -122.6532 | 0.07782 | 0.0074006 | -0.014956 | 0.014851 | 0.037732 | -0.027164 | -0.033596 | -0.010288 | -0.015182 | 0.0013308 | 0.0025913 | -0.09248 | -0.012356 | -0.00017078 | 0.10529 | -0.004578 | 0.036621 | 0.054932 | 0.13733 | 0.013733 | -0.14191 | -0.004578 | 0.068665 | -0.059509 | 0.073242 | 0.07782 | -0.036621 | -0.11902 | 122.6669 | 122.5113 | 0.059509 | 122.6486 | 122.7081 | 0.19684 | 0.027466 | 122.6166 | 122.5342 | -0.004578 | 122.6486 | 122.5937 | 0.05951 | 0 | 122.7905 | 122.7585 | 122.6898 | -0.21973 | 122.7264 | 122.731 | 122.7219 | -0.19684
3957.375 | 122.9187 | -122.6532 | 0.10986 | 0.0074006 | -0.018374 | 0.014851 | 0.036664 | -0.028232 | -0.037442 | -0.013492 | -0.0075532 | 0.0026126 | 0.0021641 | -0.09248 | -0.012997 | 0.0015382 | 0.018311 | -0.09613 | -0.032043 | -0.009155 | 0.12817 | 0 | -0.13275 | -0.054932 | -0.013733 | -0.091553 | 0.091553 | 0.068665 | -0.064087 | -0.12817 | 122.6532 | 122.5204 | 0.018311 | 122.5571 | 122.644 | 0.1236 | -0.091552 | 122.5891 | 122.525 | -0.01831 | 122.5983 | 122.5616 | 0.036621 | -0.041198 | 122.7814 | 122.6715 | 122.6212 | -0.24261 | 122.7448 | 122.7219 | 122.6395 | -0.23804
3959.1094 | 122.9553 | -122.6532 | 0.10071 | -0.015487 | -0.017306 | 0.01656 | 0.034101 | -0.026951 | -0.036374 | -0.011997 | 7.627e-05 | 0.002399 | 0.0019505 | -0.092693 | -0.013424 | 4.2822e-05 | 0.009155 | -0.086975 | -0.022888 | 0.009155 | 0.16022 | -0.004578 | -0.13275 | -0.064087 | -0.018311 | -0.086975 | 0.09613 | 0.068665 | -0.059509 | -0.1236 | 122.6486 | 122.5204 | 0.059509 | 122.5662 | 122.6624 | 0.14191 | -0.091553 | 122.5937 | 122.5296 | -0.004578 | 122.5891 | 122.5662 | 0.036621 | -0.032043 | 122.8134 | 122.6624 | 122.6303 | -0.23346 | 122.7493 | 122.7219 | 122.6349 | -0.2243
3960.9062 | 122.8271 | -122.6852 | 0.13275 | -0.0078584 | -0.017733 | 0.020192 | 0.039227 | -0.02631 | -0.042996 | -0.013492 | -0.0075532 | -0.0023008 | 0.0019505 | -0.09782 | -0.018124 | 0.0015382 | 0.10071 | 0.10071 | 0.12817 | 0.10529 | 0.10529 | 0.036621 | -0.10529 | 0.022888 | 0.1831 | 0.054932 | 0.036621 | 0.036621 | -0.013733 | -0.10071 | 122.7219 | 122.58 | -0.027465 | 122.7859 | 122.7905 | 0.21057 | -0.032043 | 122.6715 | 122.5845 | -0.09613 | 122.7081 | 122.7402 | 0.15564 | -0.09613 | 122.7905 | 122.7859 | 122.8134 | -0.23804 | 122.7219 | 122.7219 | 122.8683 | -0.23346
3962.7031 | 122.9782 | -122.6486 | 0.073242 | -0.00022891 | -0.019869 | 0.015278 | 0.035809 | -0.028446 | -0.035733 | -0.014133 | -0.015182 | 0.0028262 | 0.0017367 | -0.094402 | -0.01556 | 0.0023926 | 0.050354 | -0.022888 | 0.013733 | 0.041199 | 0.14191 | 0.022888 | -0.14191 | -0.036621 | 0.073242 | -0.041199 | 0.086975 | 0.073242 | -0.059509 | -0.12817 | 122.6715 | 122.5067 | 0.068665 | 122.6257 | 122.6898 | 0.18311 | -0.022888 | 122.5891 | 122.5204 | 0.013733 | 122.612 | 122.6074 | 0.086975 | 0 | 122.7905 | 122.699 | 122.6624 | -0.21515 | 122.7356 | 122.7219 | 122.7219 | -0.20142
3964.5 | 122.937 | -122.6761 | 0.09613 | -0.0078584 | -0.016878 | 0.016774 | 0.033887 | -0.027805 | -0.036374 | -0.012638 | 7.627e-05 | 0.002399 | 0.0021641 | -0.093761 | -0.015347 | -0.00081178 | 0.086975 | 0.009155 | 0.027466 | 0.068665 | 0.1236 | 0.013733 | -0.11902 | -0.013733 | 0.082397 | -0.041199 | 0.068665 | 0.07782 | -0.045776 | -0.1236 | 122.6898 | 122.5571 | 0.027466 | 122.6852 | 122.7448 | 0.18768 | -0.009155 | 122.6303 | 122.5525 | -0.027465 | 122.6624 | 122.6349 | 0.082397 | -0.01831 | 122.7997 | 122.7631 | 122.7036 | -0.21515 | 122.7448 | 122.7539 | 122.7585 | -0.21973
3966.3125 | 122.8409 | -122.6944 | 0.11444 | -0.015487 | -0.02051 | 0.019978 | 0.036664 | -0.0293 | -0.04321 | -0.01392 | -0.0075532 | -0.002728 | -0.0012539 | -0.098247 | -0.015133 | 0.0028198 | 0.091553 | 0.09613 | 0.10529 | 0.064087 | 0.10071 | 0.027466 | -0.10529 | 0.018311 | 0.10986 | 0.027466 | 0.059509 | 0.054932 | -0.032043 | -0.10071 | 122.7219 | 122.5891 | -0.013733 | 122.7905 | 122.7585 | 0.16937 | -0.022888 | 122.6624 | 122.5937 | -0.054932 | 122.7127 | 122.7219 | 0.12817 | -0.059509 | 122.7951 | 122.7859 | 122.7997 | -0.21973 | 122.7539 | 122.7493 | 122.8043 | -0.21515
3968.0469 | 122.8409 | -122.7127 | 0.14191 | -0.00022891 | -0.023928 | 0.021473 | 0.037732 | -0.030582 | -0.041073 | -0.013706 | 0.0077058 | -0.003796 | 2.7914e-05 | -0.095043 | -0.015347 | 0.0026062 | 0.073242 | 0.036621 | 0.073242 | 0.045776 | 0.086975 | 0.041199 | -0.091553 | 0.004578 | 0.07782 | 0.013733 | 0.054932 | 0.059509 | -0.022888 | -0.09613 | 122.7539 | 122.6212 | -0.054932 | 122.7493 | 122.7585 | 0.13733 | -0.068665 | 122.6898 | 122.6166 | -0.086975 | 122.7173 | 122.7264 | 0.10986 | -0.082398 | 122.7997 | 122.7859 | 122.7859 | -0.23346 | 122.7676 | 122.7722 | 122.7905 | -0.23804
3969.8438 | 122.8592 | -122.7264 | 0.13733 | -0.00022891 | -0.022433 | 0.019764 | 0.036023 | -0.031437 | -0.041073 | -0.01456 | 7.627e-05 | -0.001019 | -0.00018589 | -0.09547 | -0.015133 | 0.0023926 | 0.13275 | 0.064087 | 0.12817 | 0.068665 | 0.091553 | 0.027466 | -0.10986 | 0.032043 | 0.10529 | 0.018311 | 0.050354 | 0.050354 | -0.027466 | -0.09613 | 122.7539 | 122.6166 | -0.045776 | 122.7905 | 122.7951 | 0.17853 | -0.004578 | 122.699 | 122.6303 | -0.086975 | 122.7585 | 122.7448 | 0.11444 | -0.086975 | 122.818 | 122.8592 | 122.8546 | -0.24719 | 122.7768 | 122.7768 | 122.8317 | -0.23346
3971.6406 | 122.9691 | -122.6669 | 0.082397 | -0.00022891 | -0.013033 | 0.015492 | 0.035382 | -0.029728 | -0.034665 | -0.013279 | -0.0075532 | 0.0038944 | 0.0032321 | -0.095043 | -0.01321 | -0.0010254 | 0.1236 | -0.004578 | 0.027466 | 0.059509 | 0.12817 | 0.013733 | -0.14648 | 0 | 0.082397 | -0.045776 | 0.064087 | 0.073242 | -0.054932 | -0.12817 | 122.6807 | 122.5204 | 0.045777 | 122.6624 | 122.7264 | 0.20599 | 0.041199 | 122.612 | 122.5388 | -0.01831 | 122.6669 | 122.6212 | 0.082398 | -0.009155 | 122.7951 | 122.7905 | 122.6944 | -0.22888 | 122.731 | 122.7402 | 122.7493 | -0.21057
3973.4375 | 122.9553 | -122.6944 | 0.09613 | 0.0074006 | -0.01816 | 0.018483 | 0.036023 | -0.02866 | -0.039578 | -0.010715 | 7.627e-05 | -0.0035824 | 2.7914e-05 | -0.093975 | -0.015133 | 0.0013244 | 0.14191 | 0.07782 | 0.13275 | 0.10986 | 0.10529 | 0.041199 | -0.082397 | 0.068665 | 0.13733 | 0.036621 | 0.041199 | 0.036621 | -0.027466 | -0.086975 | 122.7356 | 122.612 | 0.009156 | 122.7722 | 122.8043 | 0.19226 | 0.045777 | 122.6669 | 122.6074 | -0.054931 | 122.7631 | 122.731 | 0.1236 | -0.059509 | 122.7997 | 122.8363 | 122.8271 | -0.17853 | 122.7356 | 122.731 | 122.8317 | -0.1831
3975.2344 | 122.8592 | -122.699 | 0.10529 | -0.00022891 | -0.017519 | 0.019123 | 0.036878 | -0.027591 | -0.040646 | -0.015201 | -0.0075532 | -0.0023008 | 0.0021641 | -0.096752 | -0.016628 | 4.2822e-05 | 0.13733 | 0.11444 | 0.14191 | 0.10071 | 0.10071 | 0.032043 | -0.10986 | 0.054932 | 0.18768 | 0.064087 | 0.050354 | 0.041199 | -0.018311 | -0.09613 | 122.731 | 122.5891 | -0.004578 | 122.8134 | 122.7997 | 0.21057 | 0.032043 | 122.6807 | 122.6028 | -0.054932 | 122.7539 | 122.7631 | 0.16022 | -0.064087 | 122.7997 | 122.8363 | 122.8409 | -0.21515 | 122.7493 | 122.7402 | 122.8867 | -0.20142
3976.9688 | 122.8958 | -122.6669 | 0.1236 | -0.0078584 | -0.022005 | 0.018055 | 0.037305 | -0.030582 | -0.042782 | -0.015629 | 0.0077058 | 0.014362 | 0.042539 | -0.098247 | -0.018124 | 0.003247 | 0.11444 | 0.073242 | 0.10529 | 0.082397 | 0.10529 | 0.022888 | -0.11902 | 0.064087 | 0.15564 | 0.07782 | 0.07782 | 0.059509 | -0.009155 | -0.09613 | 122.6898 | 122.5479 | -0.01831 | 122.7402 | 122.7493 | 0.20142 | -0.009155 | 122.6578 | 122.5708 | -0.045776 | 122.731 | 122.7448 | 0.17395 | -0.064087 | 122.7722 | 122.7814 | 122.7722 | -0.24261 | 122.7448 | 122.7264 | 122.8226 | -0.21973
3978.75 | 122.8592 | -122.7081 | 0.11444 | -0.00022891 | -0.016024 | 0.016774 | 0.038587 | -0.02866 | -0.037442 | -0.01392 | -0.0075532 | 0.00090363 | 0.0040867 | -0.093334 | -0.016842 | -0.00059818 | 0.054932 | -0.018311 | 0 | 0.027466 | 0.15106 | 0 | -0.14191 | -0.064087 | 0.032043 | -0.073242 | 0.10071 | 0.07782 | -0.064087 | -0.12817 | 122.7081 | 122.5662 | 0.036621 | 122.6898 | 122.7356 | 0.16937 | -0.059509 | 122.644 | 122.58 | -0.013733 | 122.644 | 122.6349 | 0.054932 | -0.036621 | 122.8592 | 122.7631 | 122.7081 | -0.25635 | 122.8088 | 122.7859 | 122.7402 | -0.24262
3980.5625 | 122.9965 | -122.6715 | 0.07782 | -0.00022891 | -0.017306 | 0.015706 | 0.032819 | -0.030582 | -0.034024 | -0.012638 | 7.627e-05 | 0.0030398 | 0.0036593 | -0.093975 | -0.012783 | -0.001239 | 0.073242 | -0.050354 | -0.018311 | 0 | 0.13275 | 0 | -0.12817 | -0.013733 | 0.027466 | -0.068665 | 0.09613 | 0.064087 | -0.041199 | -0.10986 | 122.6715 | 122.5433 | 0.054931 | 122.6212 | 122.6715 | 0.12817 | -0.004578 | 122.6303 | 122.5616 | 0.01831 | 122.6578 | 122.6028 | 0.041198 | -0.013733 | 122.8043 | 122.7448 | 122.6532 | -0.20599 | 122.7676 | 122.7356 | 122.699 | -0.18768
3982.2812 | 122.8912 | -122.7127 | 0.10986 | -0.0078584 | -0.023928 | 0.017842 | 0.034955 | -0.0293 | -0.040432 | -0.014347 | 0.0077058 | -0.0012326 | 0.00024151 | -0.094829 | -0.018978 | 0.0036744 | 0.073242 | 0.018311 | 0.07782 | 0.064087 | 0.10986 | 0.018311 | -0.10986 | 0.041199 | 0.13275 | 0.032043 | 0.073242 | 0.050354 | -0.027466 | -0.091553 | 122.731 | 122.6028 | 0 | 122.731 | 122.7768 | 0.17395 | -0.036621 | 122.6852 | 122.6212 | -0.036621 | 122.7539 | 122.7448 | 0.1236 | -0.059509 | 122.8226 | 122.7859 | 122.7905 | -0.21973 | 122.7859 | 122.7631 | 122.8455 | -0.20142
3984.0781 | 122.9782 | -122.6349 | 0.086975 | -0.0078584 | -0.015169 | 0.015492 | 0.039441 | -0.028232 | -0.03381 | -0.01456 | 7.627e-05 | 0.016498 | 0.046384 | -0.094189 | -0.013638 | -0.0010254 | 0.059509 | -0.041199 | 0 | 0.036621 | 0.15564 | -0.018311 | -0.13733 | -0.027466 | 0.059509 | -0.064087 | 0.10986 | 0.09613 | -0.064087 | -0.1236 | 122.6166 | 122.4976 | 0.068665 | 122.5937 | 122.6715 | 0.17395 | -0.027466 | 122.5708 | 122.5113 | 0.022888 | 122.6074 | 122.5708 | 0.059509 | 0.009155 | 122.7905 | 122.6944 | 122.6349 | -0.2243 | 122.7448 | 122.731 | 122.6944 | -0.21057
3985.875 | 122.9874 | -122.6669 | 0.086975 | -0.00022891 | -0.01346 | 0.017201 | 0.03346 | -0.029941 | -0.034878 | -0.011997 | 7.627e-05 | 0.0028262 | -0.00018589 | -0.093975 | -0.011501 | 0.0015382 | 0.032043 | -0.054932 | -0.022888 | 0.022888 | 0.12817 | 0 | -0.13733 | -0.041199 | -0.013733 | -0.09613 | 0.09613 | 0.064087 | -0.059509 | -0.13733 | 122.6669 | 122.5296 | 0.041199 | 122.612 | 122.6898 | 0.16022 | -0.054932 | 122.6074 | 122.5296 | 0.009155 | 122.6257 | 122.5708 | 0.041199 | -0.022888 | 122.7951 | 122.699 | 122.644 | -0.2243 | 122.7631 | 122.731 | 122.6532 | -0.2243
3987.6719 | 122.9782 | -122.6807 | 0.091553 | -0.0078584 | -0.018374 | 0.015065 | 0.034314 | -0.029087 | -0.038083 | -0.013706 | -0.0075532 | 0.00026283 | 0.0025913 | -0.094189 | -0.012783 | -0.00059818 | 0.10986 | 0.054932 | 0.09613 | 0.10071 | 0.10986 | 0.041199 | -0.10071 | 0.073242 | 0.1236 | 0.027466 | 0.045776 | 0.032043 | -0.013733 | -0.082397 | 122.7219 | 122.58 | 0.01831 | 122.7356 | 122.7814 | 0.20142 | 0.01831 | 122.6669 | 122.5983 | -0.045777 | 122.7539 | 122.7081 | 0.10986 | -0.05951 | 122.7905 | 122.7905 | 122.7768 | -0.19226 | 122.7264 | 122.7127 | 122.8043 | -0.17395
3989.4688 | 122.8638 | -122.7219 | 0.10529 | -0.0078584 | -0.017306 | 0.018269 | 0.0388 | -0.027164 | -0.039792 | -0.014988 | -0.015182 | -0.00059177 | 0.0025913 | -0.094829 | -0.015133 | 0.0036744 | 0.009155 | -0.027466 | 0.018311 | 0.004578 | 0.13733 | 0 | -0.14191 | -0.045776 | 0.045776 | -0.082397 | 0.10071 | 0.068665 | -0.059509 | -0.15106 | 122.7219 | 122.58 | 0.032043 | 122.6944 | 122.7264 | 0.14649 | -0.096131 | 122.6624 | 122.5708 | -0.004578 | 122.6761 | 122.6395 | 0.068665 | -0.036621 | 122.8592 | 122.731 | 122.7402 | -0.24719 | 122.8226 | 122.7905 | 122.7676 | -0.25635
3991.2656 | 122.9645 | -122.6852 | 0.091553 | -0.00022891 | -0.013033 | 0.013997 | 0.037518 | -0.028019 | -0.034451 | -0.012211 | 7.627e-05 | 0.0030398 | 0.0019505 | -0.092907 | -0.014279 | 0.002179 | 0.013733 | -0.07782 | -0.032043 | 0.009155 | 0.14191 | 0.009155 | -0.1236 | -0.050354 | -0.004578 | -0.10071 | 0.073242 | 0.068665 | -0.054932 | -0.14648 | 122.6944 | 122.5616 | 0.050354 | 122.6074 | 122.6944 | 0.13275 | -0.07782 | 122.6303 | 122.5388 | -0.018311 | 122.6349 | 122.5845 | 0.045776 | -0.022888 | 122.8271 | 122.699 | 122.6532 | -0.21515 | 122.7585 | 122.7539 | 122.6807 | -0.23804
3993.0156 | 122.9507 | -122.7173 | 0.10071 | -0.00022891 | -0.016238 | 0.014851 | 0.033887 | -0.029728 | -0.035733 | -0.012638 | 7.627e-05 | 0.0019718 | 0.0028049 | -0.093334 | -0.012783 | -0.00017078 | 0.022888 | -0.068665 | -0.009155 | 0.004578 | 0.14191 | 0.013733 | -0.14648 | -0.091553 | 0.004578 | -0.12817 | 0.091553 | 0.082397 | -0.054932 | -0.11902 | 122.731 | 122.5708 | 0.041199 | 122.6486 | 122.7219 | 0.15106 | -0.07782 | 122.6624 | 122.5983 | -0.009155 | 122.6257 | 122.5891 | -0.009155 | -0.018311 | 122.8592 | 122.7402 | 122.7081 | -0.24719 | 122.8088 | 122.7997 | 122.7219 | -0.21973
3994.8125 | 122.8821 | -122.7127 | 0.11444 | 0.0074006 | -0.016665 | 0.018269 | 0.037091 | -0.027378 | -0.04385 | -0.01456 | 7.627e-05 | -0.0035824 | 2.7914e-05 | -0.095043 | -0.018978 | -0.00059818 | 0.11444 | 0.11902 | 0.14191 | 0.10529 | 0.10986 | 0.041199 | -0.10529 | 0.064087 | 0.19684 | 0.054932 | 0.036621 | 0.032043 | -0.013733 | -0.082397 | 122.7539 | 122.6074 | -0.004578 | 122.8317 | 122.818 | 0.21057 | 0 | 122.699 | 122.6303 | -0.07782 | 122.7768 | 122.7676 | 0.13733 | -0.082398 | 122.8226 | 122.8271 | 122.8546 | -0.21973 | 122.7493 | 122.7448 | 122.9095 | -0.19684
3996.5625 | 122.8455 | -122.7493 | 0.10986 | -0.0078584 | -0.016665 | 0.018269 | 0.034955 | -0.031009 | -0.041073 | -0.013706 | 0.0077058 | -0.00080537 | 0.0015231 | -0.096966 | -0.01556 | -0.00038438 | 0.10529 | 0.07782 | 0.09613 | 0.09613 | 0.11902 | 0.027466 | -0.1236 | -0.013733 | 0.11902 | 0 | 0.064087 | 0.073242 | -0.041199 | -0.1236 | 122.7768 | 122.6257 | 0.009156 | 122.8271 | 122.8455 | 0.21973 | -0.004577 | 122.7081 | 122.6257 | -0.045776 | 122.7356 | 122.7493 | 0.1236 | -0.036621 | 122.8683 | 122.8546 | 122.8455 | -0.23346 | 122.8134 | 122.8226 | 122.8683 | -0.23346
3998.3438 | 122.8821 | -122.7448 | 0.11902 | 0.0074006 | -0.020083 | 0.016987 | 0.03346 | -0.028873 | -0.04086 | -0.015201 | 7.627e-05 | -0.0023008 | -0.00018589 | -0.092693 | -0.016415 | 0.0019654 | 0.13275 | 0.068665 | 0.1236 | 0.07782 | 0.086975 | 0.036621 | -0.091553 | 0.054932 | 0.1236 | 0.036621 | 0.045776 | 0.032043 | -0.022888 | -0.082397 | 122.7814 | 122.6532 | -0.032044 | 122.8134 | 122.8226 | 0.16937 | 0.013732 | 122.7219 | 122.6624 | -0.073243 | 122.7997 | 122.7814 | 0.11902 | -0.086976 | 122.8317 | 122.8775 | 122.8683 | -0.21057 | 122.7905 | 122.7768 | 122.8683 | -0.20142
4000.125 | 122.9691 | -122.7036 | 0.09613 | -0.015487 | -0.01816 | 0.014637 | 0.034955 | -0.0293 | -0.035946 | -0.012851 | -0.0075532 | 0.0028262 | 0.0038731 | -0.093334 | -0.014919 | -0.00081178 | 0.041199 | -0.10071 | -0.022888 | -0.009155 | 0.14648 | 0.004578 | -0.14648 | -0.050354 | -0.009155 | -0.10986 | 0.091553 | 0.073242 | -0.041199 | -0.12817 | 122.7081 | 122.5571 | 0.050354 | 122.6028 | 122.6944 | 0.13733 | -0.054931 | 122.6624 | 122.5754 | -0.004577 | 122.6532 | 122.5937 | 0.018311 | -0.022888 | 122.85 | 122.7448 | 122.6807 | -0.24261 | 122.7951 | 122.7768 | 122.6944 | -0.2243
4001.8594 | 122.905 | -122.7173 | 0.13275 | 0.0074006 | -0.026064 | 0.019337 | 0.034955 | -0.030582 | -0.04321 | -0.013492 | -0.0075532 | -0.0025144 | -0.00061309 | -0.096752 | -0.015988 | 0.0041016 | 0.050354 | 0.018311 | 0.068665 | 0.045776 | 0.11902 | 0.022888 | -0.10986 | 0.009155 | 0.10986 | 0.022888 | 0.050354 | 0.032043 | -0.050354 | -0.11444 | 122.7402 | 122.6074 | -0.013732 | 122.7356 | 122.7631 | 0.15564 | -0.082397 | 122.6669 | 122.6028 | -0.082397 | 122.7264 | 122.7402 | 0.13733 | -0.10071 | 122.8363 | 122.7676 | 122.7859 | -0.24261 | 122.7676 | 122.7493 | 122.8271 | -0.24719
4003.6406 | 122.9874 | -122.6852 | 0.086975 | -0.0078584 | -0.014315 | 0.015492 | 0.037946 | -0.026737 | -0.033383 | -0.012851 | -0.015182 | 0.048114 | 0.019254 | -0.084148 | -0.014065 | 0.048535 | 0.11902 | 0 | 0.036621 | 0.054932 | 0.14648 | 0 | -0.13275 | 0.009155 | 0.07782 | -0.045776 | 0.073242 | 0.09613 | -0.082397 | -0.1236 | 122.6852 | 122.5525 | 0.059509 | 122.6852 | 122.7402 | 0.18768 | 0.032044 | 122.6028 | 122.5616 | -0.013733 | 122.6944 | 122.6395 | 0.07782 | 0.009155 | 122.8317 | 122.8043 | 122.7219 | -0.21973 | 122.7585 | 122.7814 | 122.7631 | -0.21057
4005.4375 | 122.9462 | -122.7127 | 0.11444 | -0.0078584 | -0.016238 | 0.015706 | 0.035809 | -0.029941 | -0.034451 | -0.011142 | -0.0075532 | 0.0032534 | 0.0023777 | -0.094189 | -0.013638 | 4.2822e-05 | 0.036621 | -0.086975 | -0.032043 | 0.009155 | 0.14191 | -0.009155 | -0.15106 | -0.07782 | -0.013733 | -0.1236 | 0.07782 | 0.068665 | -0.059509 | -0.1236 | 122.7036 | 122.5616 | 0.027466 | 122.6257 | 122.7219 | 0.16022 | -0.07782 | 122.6532 | 122.5891 | -0.036621 | 122.6349 | 122.5891 | 0 | -0.045776 | 122.8546 | 122.7493 | 122.6807 | -0.2655 | 122.7905 | 122.7814 | 122.699 | -0.23804
4007.2344 | 122.9141 | -122.7219 | 0.13275 | -0.00022891 | -0.022646 | 0.018483 | 0.039014 | -0.027591 | -0.04385 | -0.014988 | -0.0075532 | -0.0014462 | 0.0017367 | -0.097179 | -0.016628 | 0.0013244 | 0.050354 | 0.022888 | 0.086975 | 0.054932 | 0.11444 | 0.045776 | -0.10529 | 0.018311 | 0.13733 | 0.036621 | 0.064087 | 0.054932 | -0.036621 | -0.086975 | 122.7676 | 122.6166 | -0.01831 | 122.7448 | 122.7768 | 0.16022 | -0.082397 | 122.6852 | 122.6349 | -0.068664 | 122.7402 | 122.7585 | 0.1236 | -0.077819 | 122.8363 | 122.7722 | 122.8088 | -0.23804 | 122.7859 | 122.7768 | 122.8592 | -0.21973
4008.9688 | 122.9416 | -122.7081 | 0.11902 | -0.00022891 | -0.020724 | 0.017415 | 0.03346 | -0.028232 | -0.036801 | -0.015415 | 0.0077058 | -0.00016437 | -0.00039949 | -0.093334 | -0.012997 | 0.00047002 | 0.15106 | 0.064087 | 0.1236 | 0.07782 | 0.09613 | 0.054932 | -0.091553 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.041199 | -0.013733 | -0.10529 | 122.7631 | 122.6166 | -0.022889 | 122.7722 | 122.7859 | 0.16937 | 0.032043 | 122.6944 | 122.6028 | -0.082398 | 122.7768 | 122.7539 | 0.15106 | -0.07782 | 122.8043 | 122.8592 | 122.8317 | -0.21057 | 122.7448 | 122.7493 | 122.8546 | -0.22431
4010.7656 | 122.8912 | -122.7219 | 0.11902 | 0.0074006 | -0.014742 | 0.019337 | 0.037946 | -0.031009 | -0.042141 | -0.013065 | 7.627e-05 | 0.00069003 | 0.0021641 | -0.096111 | -0.015774 | 0.0011108 | 0.12817 | 0.10071 | 0.13733 | 0.086975 | 0.082397 | 0.041199 | -0.09613 | 0.054932 | 0.18768 | 0.064087 | 0.041199 | 0.032043 | -0.004578 | -0.091553 | 122.7631 | 122.6257 | -0.036622 | 122.8226 | 122.8088 | 0.1831 | 0.009155 | 122.7173 | 122.6303 | -0.07782 | 122.7768 | 122.7859 | 0.15564 | -0.086976 | 122.8043 | 122.85 | 122.8592 | -0.21515 | 122.7631 | 122.7539 | 122.9095 | -0.21057
4012.5781 | 122.9782 | -122.7402 | 0.10529 | 0.0074006 | -0.010683 | 0.015065 | 0.03346 | -0.0293 | -0.035092 | -0.013706 | 0.0077058 | 0.0026126 | 2.7914e-05 | -0.093334 | -0.010861 | -0.00038438 | 0.045776 | -0.09613 | -0.041199 | 0.009155 | 0.15106 | 0 | -0.12817 | -0.050354 | -0.013733 | -0.10986 | 0.09613 | 0.082397 | -0.064087 | -0.11902 | 122.7402 | 122.612 | 0.045776 | 122.644 | 122.7493 | 0.13733 | -0.05951 | 122.6761 | 122.6212 | -0.009156 | 122.6898 | 122.6303 | 0.009156 | -0.022889 | 122.8912 | 122.7859 | 122.699 | -0.23346 | 122.8363 | 122.8226 | 122.7264 | -0.22431
4014.3125 | 122.8867 | -122.7539 | 0.13275 | -0.0078584 | -0.025851 | 0.017628 | 0.03645 | -0.028232 | -0.042355 | -0.014774 | -0.0075532 | 4.9234e-05 | -0.0012539 | -0.09547 | -0.017483 | 0.003888 | 0.091553 | 0.013733 | 0.082397 | 0.054932 | 0.10529 | 0.032043 | -0.10529 | -0.009155 | 0.09613 | 0.013733 | 0.054932 | 0.041199 | -0.022888 | -0.11902 | 122.7859 | 122.6486 | -0.027465 | 122.7676 | 122.8088 | 0.16022 | -0.041198 | 122.731 | 122.6349 | -0.077819 | 122.7448 | 122.7676 | 0.13275 | -0.091552 | 122.8592 | 122.8455 | 122.8363 | -0.23804 | 122.8088 | 122.7951 | 122.85 | -0.25177
4016.1094 | 122.9233 | -122.7402 | 0.11444 | -0.0078584 | -0.019228 | 0.017415 | 0.039227 | -0.029087 | -0.040432 | -0.014988 | -0.015182 | -0.00059177 | 0.00088231 | -0.094616 | -0.018124 | -0.00038438 | 0.16022 | 0.11444 | 0.15106 | 0.10986 | 0.11444 | 0.032043 | -0.10529 | 0.054932 | 0.19226 | 0.064087 | 0.064087 | 0.045776 | -0.013733 | -0.082397 | 122.7722 | 122.6349 | 0 | 122.8546 | 122.85 | 0.21515 | 0.045776 | 122.7264 | 122.6578 | -0.050354 | 122.7951 | 122.8043 | 0.14648 | -0.068665 | 122.8546 | 122.9004 | 122.8912 | -0.21973 | 122.8043 | 122.7859 | 122.9324 | -0.19684
4017.9062 | 122.8775 | -122.7493 | 0.12817 | -0.0078584 | -0.023287 | 0.015919 | 0.034741 | -0.031437 | -0.040219 | -0.015415 | 0.0077058 | 0.00090363 | 0.0030185 | -0.094616 | -0.014065 | 4.2822e-05 | 0.13733 | 0.064087 | 0.11444 | 0.064087 | 0.10071 | 0.050354 | -0.10071 | 0.045776 | 0.10529 | 0.013733 | 0.050354 | 0.041199 | -0.018311 | -0.09613 | 122.7997 | 122.6486 | -0.027466 | 122.8134 | 122.8134 | 0.1648 | 0.009155 | 122.731 | 122.6532 | -0.07782 | 122.7951 | 122.7631 | 0.10986 | -0.086975 | 122.85 | 122.8867 | 122.8638 | -0.22888 | 122.7997 | 122.7905 | 122.8546 | -0.2243
4019.6875 | 122.905 | -122.7539 | 0.13275 | -0.0078584 | -0.020083 | 0.019978 | 0.036664 | -0.027378 | -0.038937 | -0.016056 | -0.0075532 | 0.0017582 | 0.00045511 | -0.094616 | -0.012783 | 0.0011108 | 0.14191 | 0.10071 | 0.11902 | 0.073242 | 0.10529 | 0.036621 | -0.11444 | 0.073242 | 0.10529 | 0.022888 | 0.050354 | 0.045776 | -0.045776 | -0.091553 | 122.7905 | 122.6395 | -0.027465 | 122.8546 | 122.8271 | 0.18768 | 0.009156 | 122.7081 | 122.6624 | -0.082397 | 122.8271 | 122.7768 | 0.11444 | -0.086975 | 122.8592 | 122.8958 | 122.8729 | -0.24719 | 122.8043 | 122.7997 | 122.8592 | -0.2243
4021.4219 | 122.9828 | -122.7081 | 0.10986 | -0.015487 | -0.016024 | 0.017415 | 0.03346 | -0.032291 | -0.033169 | -0.013492 | 7.627e-05 | 0.0066714 | 0.0013095 | -0.092693 | -0.0082972 | 0.00047002 | 0.045776 | -0.064087 | -0.027466 | 0.009155 | 0.14648 | 0 | -0.14191 | -0.068665 | -0.013733 | -0.13275 | 0.086975 | 0.082397 | -0.054932 | -0.10986 | 122.7081 | 122.5662 | 0.036621 | 122.644 | 122.7173 | 0.15106 | -0.064087 | 122.6532 | 122.5983 | -0.022888 | 122.6395 | 122.5754 | -0.022888 | -0.027466 | 122.8546 | 122.7539 | 122.6807 | -0.25177 | 122.7951 | 122.7905 | 122.6944 | -0.21973
4023.2344 | 123.0331 | -122.7036 | 0.091553 | -0.00022891 | -0.016665 | 0.016774 | 0.037305 | -0.029514 | -0.035305 | -0.013279 | 0.0077058 | 0.0021854 | 0.00066871 | -0.094402 | -0.013638 | 0.0017518 | 0.073242 | -0.009155 | 0.036621 | 0.041199 | 0.11902 | 0.009155 | -0.11902 | 0.054932 | 0.10071 | 0.022888 | 0.064087 | 0.041199 | -0.036621 | -0.082397 | 122.7127 | 122.5845 | 0.027466 | 122.6944 | 122.7448 | 0.16022 | -0.018311 | 122.6669 | 122.6212 | -0.027466 | 122.7585 | 122.7264 | 0.10528 | -0.050354 | 122.8226 | 122.7768 | 122.7402 | -0.21057 | 122.7676 | 122.7448 | 122.8043 | -0.17395
4025.0156 | 123.0011 | -122.731 | 0.09613 | -0.00022891 | -0.01581 | 0.013783 | 0.035596 | -0.030582 | -0.039364 | -0.011356 | 7.627e-05 | 0.00090363 | 0.0017367 | -0.095684 | -0.01556 | 0.0017518 | 0.13275 | 0.086975 | 0.11902 | 0.09613 | 0.086975 | 0.022888 | -0.09613 | 0.086975 | 0.15106 | 0.041199 | 0.036621 | 0.045776 | -0.022888 | -0.091553 | 122.7539 | 122.6349 | -0.009155 | 122.818 | 122.8271 | 0.19226 | 0.036621 | 122.7081 | 122.6395 | -0.059509 | 122.818 | 122.7722 | 0.13275 | -0.050354 | 122.818 | 122.8638 | 122.85 | -0.19226 | 122.7676 | 122.7768 | 122.8821 | -0.18768
4026.75 | 122.9828 | -122.7036 | 0.07782 | -0.0078584 | -0.013888 | 0.015492 | 0.035382 | -0.0293 | -0.033169 | -0.013492 | -0.0075532 | 0.0043216 | 0.0034457 | -0.095257 | -0.012997 | -0.00038438 | 0.10071 | 0.027466 | 0.027466 | 0.050354 | 0.12817 | 0 | -0.12817 | 0.004578 | 0.073242 | -0.059509 | 0.091553 | 0.054932 | -0.041199 | -0.11902 | 122.7036 | 122.5754 | 0.050354 | 122.731 | 122.7539 | 0.17853 | 0.022888 | 122.6624 | 122.5845 | 0.013733 | 122.7081 | 122.644 | 0.05951 | -0.022888 | 122.8317 | 122.8043 | 122.731 | -0.20599 | 122.7951 | 122.7585 | 122.7768 | -0.19684
4028.5469 | 122.9965 | -122.7127 | 0.091553 | -0.00022891 | -0.014956 | 0.019337 | 0.0388 | -0.027378 | -0.036374 | -0.014133 | 7.627e-05 | 0.0028262 | 0.0038731 | -0.09547 | -0.015347 | 0.0011108 | 0.022888 | -0.036621 | -0.004578 | 0.013733 | 0.16022 | 0 | -0.15106 | -0.059509 | 0.054932 | -0.086975 | 0.10529 | 0.082397 | -0.064087 | -0.13275 | 122.7127 | 122.5616 | 0.068664 | 122.6761 | 122.7264 | 0.16479 | -0.068665 | 122.6486 | 122.58 | 0.013733 | 122.6532 | 122.6257 | 0.045776 | -0.009156 | 122.8729 | 122.7356 | 122.7081 | -0.24261 | 122.818 | 122.7951 | 122.7676 | -0.2243
4030.3438 | 123.0194 | -122.6715 | 0.086975 | -0.0078584 | -0.019655 | 0.016346 | 0.034314 | -0.028873 | -0.035305 | -0.013279 | -0.0075532 | 0.024829 | 0.038266 | -0.097393 | -0.013851 | 0.0036744 | 0.064087 | 0.027466 | 0.032043 | 0.045776 | 0.1236 | -0.013733 | -0.13733 | 0.004578 | 0.09613 | -0.036621 | 0.09613 | 0.086975 | -0.054932 | -0.11902 | 122.6578 | 122.5342 | 0.036621 | 122.699 | 122.7173 | 0.18311 | -0.022888 | 122.6166 | 122.5525 | 0.009155 | 122.6761 | 122.6349 | 0.082398 | 0 | 122.7951 | 122.7356 | 122.7036 | -0.2243 | 122.7676 | 122.7585 | 122.7676 | -0.20599
4032.1406 | 122.8958 | -122.7448 | 0.10986 | -0.00022891 | -0.017306 | 0.018696 | 0.038159 | -0.03165 | -0.043637 | -0.01456 | 0.0077058 | 0.0013308 | -0.0012539 | -0.096538 | -0.019619 | 0.003247 | 0.091553 | 0.10529 | 0.15106 | 0.10071 | 0.086975 | 0.027466 | -0.09613 | 0.041199 | 0.18768 | 0.036621 | 0.050354 | 0.045776 | -0.027466 | -0.09613 | 122.7722 | 122.6486 | -0.022888 | 122.85 | 122.8455 | 0.19684 | -0.01831 | 122.7173 | 122.6486 | -0.059509 | 122.7859 | 122.7814 | 0.13275 | -0.064087 | 122.8317 | 122.8363 | 122.8958 | -0.20599 | 122.7951 | 122.7905 | 122.9324 | -0.20599
4033.8594 | 122.9691 | -122.7264 | 0.07782 | -0.00022891 | -0.013247 | 0.016774 | 0.036878 | -0.026737 | -0.034451 | -0.011356 | 7.627e-05 | 0.0062442 | 0.0019505 | -0.093975 | -0.011501 | 0.00068362 | 0.073242 | 0 | 0.022888 | 0.032043 | 0.13275 | 0.018311 | -0.12817 | -0.032043 | 0.045776 | -0.07782 | 0.059509 | 0.064087 | -0.059509 | -0.11902 | 122.7448 | 122.5983 | 0.054931 | 122.7264 | 122.7585 | 0.16022 | -0.004578 | 122.6669 | 122.6074 | -0.018311 | 122.6944 | 122.6486 | 0.041199 | -0.013733 | 122.8592 | 122.7997 | 122.7493 | -0.20599 | 122.7859 | 122.7905 | 122.7722 | -0.19684
4035.6562 | 122.9416 | -122.7402 | 0.13733 | -0.0078584 | -0.018587 | 0.018483 | 0.039014 | -0.028446 | -0.045773 | -0.013279 | -0.0075532 | 0.023334 | 0.035489 | -0.099316 | -0.01791 | 0.0043152 | 0.086975 | 0.10986 | 0.13733 | 0.10071 | 0.10986 | 0.050354 | -0.11444 | 0.068665 | 0.19226 | 0.09613 | 0.091553 | 0.059509 | 0.004578 | -0.073242 | 122.7905 | 122.6257 | -0.027466 | 122.85 | 122.8409 | 0.21515 | -0.050354 | 122.7448 | 122.6669 | -0.045776 | 122.8088 | 122.8363 | 0.16937 | -0.07782 | 122.85 | 122.8271 | 122.8775 | -0.25177 | 122.8317 | 122.7997 | 122.9324 | -0.21057
4037.4531 | 122.9919 | -122.7081 | 0.091553 | -0.00022891 | -0.017946 | 0.018055 | 0.034314 | -0.027591 | -0.039578 | -0.01456 | 7.627e-05 | 0.0032534 | -0.0031765 | -0.097179 | -0.011929 | 0.0019654 | 0.11902 | 0.091553 | 0.10529 | 0.09613 | 0.10071 | 0.045776 | -0.10071 | 0.073242 | 0.14191 | 0.054932 | 0.041199 | 0.018311 | -0.036621 | -0.07782 | 122.7539 | 122.6074 | 0.009155 | 122.7997 | 122.8043 | 0.19684 | 0.027466 | 122.6715 | 122.6303 | -0.050354 | 122.7814 | 122.7631 | 0.13275 | -0.073242 | 122.8088 | 122.8271 | 122.8134 | -0.19226 | 122.7493 | 122.7264 | 122.85 | -0.16937
4039.25 | 123.0194 | -122.7173 | 0.09613 | -0.00022891 | -0.018587 | 0.016774 | 0.034314 | -0.026523 | -0.037014 | -0.012211 | 7.627e-05 | 0.0032534 | 0.00045511 | -0.096325 | -0.011929 | 0.0019654 | 0.12817 | 0.091553 | 0.1236 | 0.10529 | 0.10986 | 0.059509 | -0.091553 | 0.054932 | 0.13275 | 0.041199 | 0.036621 | 0.013733 | -0.009155 | -0.086975 | 122.7768 | 122.6257 | 0.013733 | 122.8088 | 122.8226 | 0.19684 | 0.032044 | 122.7081 | 122.6303 | -0.059509 | 122.7722 | 122.7585 | 0.12817 | -0.082397 | 122.8271 | 122.8455 | 122.8409 | -0.18768 | 122.7539 | 122.731 | 122.85 | -0.1831
4041.0312 | 122.9095 | -122.7402 | 0.14191 | -0.0078584 | -0.017733 | 0.016987 | 0.035169 | -0.0293 | -0.042569 | -0.013065 | -0.015182 | 0.0015446 | 0.0017367 | -0.096966 | -0.015133 | 0.0017518 | 0.068665 | 0.032043 | 0.09613 | 0.068665 | 0.09613 | 0.041199 | -0.11902 | 0 | 0.086975 | 0.009155 | 0.059509 | 0.041199 | -0.032043 | -0.10529 | 122.7814 | 122.6212 | -0.045777 | 122.7722 | 122.8088 | 0.18768 | -0.073242 | 122.7081 | 122.6349 | -0.082398 | 122.7402 | 122.7493 | 0.11444 | -0.10071 | 122.8363 | 122.8088 | 122.8363 | -0.26093 | 122.7997 | 122.7814 | 122.8271 | -0.24719
4042.7656 | 122.9919 | -122.7356 | 0.082397 | -0.00022891 | -0.017092 | 0.012501 | 0.034314 | -0.028446 | -0.032101 | -0.011356 | 7.627e-05 | 0.005176 | 2.7914e-05 | -0.092907 | -0.014706 | -0.0023072 | 0.09613 | -0.004578 | 0.018311 | 0.036621 | 0.13275 | 0.004578 | -0.14191 | -0.018311 | 0.036621 | -0.09613 | 0.086975 | 0.068665 | -0.059509 | -0.10529 | 122.7402 | 122.5937 | 0.050354 | 122.731 | 122.7722 | 0.17853 | 0.013733 | 122.6761 | 122.6303 | 0.004578 | 122.7173 | 122.6395 | 0.009156 | -0.013732 | 122.8683 | 122.8317 | 122.7539 | -0.2243 | 122.8226 | 122.8043 | 122.7722 | -0.18768
4044.5625 | 123.0469 | -122.7173 | 0.068665 | 0.0074006 | -0.017733 | 0.015919 | 0.0388 | -0.026951 | -0.037228 | -0.010929 | 7.627e-05 | 0.0062442 | 0.0010959 | -0.092693 | -0.013638 | 0.0019654 | 0.027466 | -0.036621 | -0.009155 | 0.013733 | 0.12817 | -0.004578 | -0.13275 | -0.013733 | 0.027466 | -0.064087 | 0.082397 | 0.054932 | -0.054932 | -0.11902 | 122.7127 | 122.5845 | 0.059509 | 122.6807 | 122.731 | 0.14648 | -0.041199 | 122.6624 | 122.5983 | 0.013732 | 122.7036 | 122.6532 | 0.054932 | -0.013733 | 122.8455 | 122.7448 | 122.7081 | -0.20142 | 122.7997 | 122.7722 | 122.7448 | -0.18768
4046.2969 | 122.9095 | -122.7905 | 0.13275 | -0.0078584 | -0.02286 | 0.01421 | 0.03645 | -0.028019 | -0.042141 | -0.014988 | -0.0075532 | 0.0030398 | -0.0031765 | -0.093975 | -0.017056 | 0.0043152 | 0.10071 | 0.086975 | 0.11444 | 0.073242 | 0.10071 | 0.032043 | -0.11444 | 0.032043 | 0.11902 | 0.018311 | 0.064087 | 0.041199 | -0.036621 | -0.10529 | 122.8226 | 122.6761 | -0.032043 | 122.8775 | 122.8638 | 0.18768 | -0.032043 | 122.7539 | 122.6852 | -0.068664 | 122.8226 | 122.8088 | 0.1236 | -0.091552 | 122.8912 | 122.8912 | 122.905 | -0.24719 | 122.8546 | 122.8317 | 122.9095 | -0.23804
4048.1094 | 122.905 | -122.7676 | 0.10986 | 0.01503 | -0.022005 | 0.016774 | 0.0388 | -0.029514 | -0.040432 | -0.015201 | 7.627e-05 | 0.0047488 | -0.0025357 | -0.092693 | -0.016415 | 0.00047002 | 0.11444 | 0.07782 | 0.10071 | 0.082397 | 0.091553 | 0.050354 | -0.10529 | 0.050354 | 0.10986 | 0.027466 | 0.054932 | 0.041199 | -0.036621 | -0.091553 | 122.818 | 122.6624 | -0.01831 | 122.8455 | 122.85 | 0.18768 | 0.004578 | 122.731 | 122.6761 | -0.054931 | 122.818 | 122.7951 | 0.11902 | -0.068664 | 122.8592 | 122.8821 | 122.8683 | -0.21515 | 122.8226 | 122.8088 | 122.8775 | -0.20142
4049.8906 | 122.9507 | -122.7539 | 0.11902 | -0.00022891 | -0.026491 | 0.015492 | 0.035382 | -0.034 | -0.042141 | -0.015415 | 7.627e-05 | 0.0017582 | -0.0038175 | -0.096752 | -0.016628 | 0.00025642 | 0.068665 | 0.036621 | 0.073242 | 0.068665 | 0.12817 | 0.022888 | -0.10071 | 0.032043 | 0.11902 | 0.041199 | 0.054932 | 0.041199 | -0.018311 | -0.09613 | 122.7768 | 122.6532 | 0.009155 | 122.7905 | 122.8226 | 0.16937 | -0.050354 | 122.7356 | 122.6578 | -0.064087 | 122.7859 | 122.7951 | 0.13733 | -0.07782 | 122.8821 | 122.8226 | 122.8271 | -0.21973 | 122.8088 | 122.7951 | 122.8729 | -0.21515
4051.6875 | 122.9462 | -122.7356 | 0.10986 | -0.00022891 | -0.019228 | 0.017201 | 0.036237 | -0.0293 | -0.04321 | -0.013065 | 7.627e-05 | 0.0028262 | -0.00082669 | -0.095257 | -0.015347 | -0.00038438 | 0.13275 | 0.11902 | 0.12817 | 0.10071 | 0.11444 | 0.032043 | -0.10986 | 0.064087 | 0.19684 | 0.054932 | 0.041199 | 0.032043 | -0.018311 | -0.10071 | 122.7676 | 122.6257 | 0.004578 | 122.8546 | 122.8363 | 0.21057 | 0.022888 | 122.7173 | 122.6349 | -0.068664 | 122.7997 | 122.7905 | 0.15564 | -0.07782 | 122.85 | 122.8683 | 122.8638 | -0.21973 | 122.7768 | 122.7676 | 122.9324 | -0.21057
4053.4219 | 123.0331 | -122.731 | 0.086975 | -0.00022891 | -0.017519 | 0.016987 | 0.03645 | -0.027591 | -0.033596 | -0.013492 | 0.0077058 | 0.0053898 | -0.00018589 | -0.095684 | -0.011074 | -0.0014526 | 0.068665 | -0.022888 | -0.004578 | 0.041199 | 0.12817 | 0 | -0.11444 | -0.022888 | 0.068665 | -0.054932 | 0.091553 | 0.054932 | -0.050354 | -0.10986 | 122.731 | 122.6166 | 0.041199 | 122.7081 | 122.7722 | 0.15564 | -0.01831 | 122.6807 | 122.6212 | 0.004578 | 122.7081 | 122.6761 | 0.054931 | -0.032043 | 122.8592 | 122.7997 | 122.7264 | -0.20142 | 122.8226 | 122.7859 | 122.7997 | -0.19684
4055.2188 | 123.0377 | -122.7631 | 0.09613 | -0.00022891 | -0.02051 | 0.018269 | 0.035382 | -0.02866 | -0.035946 | -0.010715 | 7.627e-05 | 0.002399 | -0.0014675 | -0.093761 | -0.013638 | -0.00059818 | 0.14191 | 0.059509 | 0.10986 | 0.07782 | 0.10529 | 0.059509 | -0.10071 | 0.068665 | 0.14191 | 0.036621 | 0.032043 | 0.050354 | -0.009155 | -0.10529 | 122.8226 | 122.6624 | 0.009156 | 122.8226 | 122.8409 | 0.17853 | 0.045777 | 122.7539 | 122.6578 | -0.064087 | 122.8317 | 122.7997 | 0.14191 | -0.045776 | 122.8683 | 122.905 | 122.8729 | -0.19684 | 122.7951 | 122.8134 | 122.905 | -0.20142
4056.9531 | 122.9965 | -122.7402 | 0.10071 | -0.00022891 | -0.014315 | 0.016987 | 0.034101 | -0.027805 | -0.034024 | -0.012424 | -0.0075532 | 0.0053898 | 0.0038731 | -0.092907 | -0.013851 | 4.2822e-05 | 0.041199 | -0.07782 | -0.045776 | 0.009155 | 0.14648 | 0.018311 | -0.14648 | -0.050354 | 0.004578 | -0.09613 | 0.091553 | 0.064087 | -0.059509 | -0.1236 | 122.7585 | 122.5937 | 0.045776 | 122.6624 | 122.7493 | 0.15564 | -0.059509 | 122.6807 | 122.6166 | -0.009155 | 122.6898 | 122.644 | 0.027466 | -0.036621 | 122.8867 | 122.7814 | 122.6944 | -0.24719 | 122.8317 | 122.8043 | 122.7448 | -0.2243
4058.7344 | 122.9324 | -122.7859 | 0.13275 | -0.00022891 | -0.022219 | 0.017415 | 0.035382 | -0.029514 | -0.041501 | -0.011356 | 0.0077058 | 0.00090363 | -0.0012539 | -0.097607 | -0.014919 | 0.00047002 | 0.10529 | 0.091553 | 0.1236 | 0.073242 | 0.10529 | 0.050354 | -0.10986 | 0.064087 | 0.11444 | 0.032043 | 0.041199 | 0.022888 | -0.032043 | -0.11444 | 122.8363 | 122.6761 | -0.027465 | 122.8775 | 122.8592 | 0.18311 | -0.027465 | 122.7539 | 122.6715 | -0.091552 | 122.85 | 122.818 | 0.14648 | -0.10986 | 122.8912 | 122.8912 | 122.9095 | -0.24261 | 122.8271 | 122.8088 | 122.9004 | -0.24719
4060.4688 | 123.0057 | -122.7585 | 0.10071 | -0.0078584 | -0.014101 | 0.013569 | 0.035382 | -0.028019 | -0.032956 | -0.010288 | 7.627e-05 | 0.0056034 | 0.0017367 | -0.09312 | -0.012142 | 0.0013244 | 0.054932 | -0.068665 | -0.013733 | 0.022888 | 0.14191 | -0.004578 | -0.14191 | -0.068665 | -0.004578 | -0.11444 | 0.091553 | 0.07782 | -0.068665 | -0.13733 | 122.7539 | 122.6166 | 0.041199 | 122.6898 | 122.7814 | 0.16479 | -0.045776 | 122.6898 | 122.6212 | -0.009155 | 122.6898 | 122.644 | 0.022888 | -0.022888 | 122.9004 | 122.8134 | 122.7448 | -0.24262 | 122.85 | 122.8363 | 122.7539 | -0.23804
4062.2656 | 123.0377 | -122.7356 | 0.082397 | -0.00022891 | -0.014742 | 0.017628 | 0.039227 | -0.028446 | -0.037869 | -0.010715 | -0.0075532 | 0.0045352 | 0.0045139 | -0.095043 | -0.014919 | 0.0013244 | 0.054932 | -0.041199 | -0.004578 | 0.022888 | 0.1236 | 0 | -0.13275 | -0.054932 | 0.045776 | -0.064087 | 0.073242 | 0.07782 | -0.073242 | -0.13733 | 122.7356 | 122.6028 | 0.041199 | 122.6944 | 122.7585 | 0.15564 | -0.027465 | 122.6624 | 122.5983 | -0.009155 | 122.6807 | 122.6715 | 0.073242 | -0.004577 | 122.8592 | 122.7905 | 122.731 | -0.21515 | 122.8088 | 122.8134 | 122.7814 | -0.21973
4064.0469 | 123.0515 | -122.7539 | 0.10071 | -0.0078584 | -0.016238 | 0.016133 | 0.036878 | -0.027378 | -0.037228 | -0.012851 | 0.0077058 | 0.0056034 | -0.00018589 | -0.092907 | -0.012783 | 0.00068362 | 0.027466 | -0.073242 | -0.022888 | 0.013733 | 0.13275 | 0.004578 | -0.13733 | -0.041199 | 0.013733 | -0.07782 | 0.10071 | 0.086975 | -0.045776 | -0.1236 | 122.7585 | 122.6166 | 0.032043 | 122.6807 | 122.7676 | 0.15106 | -0.073242 | 122.7081 | 122.6303 | 0 | 122.7127 | 122.6761 | 0.045776 | -0.013733 | 122.8867 | 122.7814 | 122.731 | -0.23804 | 122.8546 | 122.8409 | 122.7676 | -0.2243
4065.7812 | 123.0057 | -122.7448 | 0.068665 | -0.015487 | -0.017733 | 0.014424 | 0.035169 | -0.027378 | -0.035092 | -0.011142 | 7.627e-05 | 0.006885 | 0.0023777 | -0.095257 | -0.013851 | 0.0013244 | 0.11444 | 0.013733 | 0.032043 | 0.045776 | 0.12817 | 0.022888 | -0.13733 | -0.004578 | 0.07782 | -0.059509 | 0.073242 | 0.07782 | -0.054932 | -0.10529 | 122.7676 | 122.6074 | 0.059509 | 122.7585 | 122.7905 | 0.18311 | 0.045776 | 122.6898 | 122.6395 | 0.004577 | 122.7402 | 122.6852 | 0.045777 | 0.009155 | 122.8729 | 122.8592 | 122.7768 | -0.20599 | 122.818 | 122.8226 | 122.8226 | -0.17395
4067.5938 | 123.0011 | -122.7631 | 0.082397 | -0.00022891 | -0.019015 | 0.016133 | 0.034955 | -0.029514 | -0.039792 | -0.014347 | -0.0075532 | 0.004108 | -0.00039949 | -0.094189 | -0.016842 | 0.002179 | 0.027466 | -0.045776 | -0.027466 | 0.009155 | 0.12817 | -0.009155 | -0.14648 | -0.064087 | 0.050354 | -0.07782 | 0.09613 | 0.086975 | -0.064087 | -0.11902 | 122.7539 | 122.6166 | 0.045777 | 122.7173 | 122.7722 | 0.15564 | -0.054931 | 122.699 | 122.644 | 0.013733 | 122.699 | 122.6852 | 0.041199 | 0.004578 | 122.8912 | 122.7905 | 122.7356 | -0.22888 | 122.8592 | 122.85 | 122.8134 | -0.20142
4069.3906 | 122.9004 | -122.7951 | 0.13733 | -0.0078584 | -0.019655 | 0.016346 | 0.039014 | -0.027805 | -0.041928 | -0.013706 | -0.0075532 | 0.0028262 | 0.00088231 | -0.096111 | -0.01791 | 0.0013244 | 0.091553 | 0.045776 | 0.073242 | 0.068665 | 0.12817 | 0.013733 | -0.11902 | -0.027466 | 0.10071 | -0.027466 | 0.082397 | 0.064087 | -0.054932 | -0.1236 | 122.8088 | 122.6761 | -0.009155 | 122.8409 | 122.8638 | 0.18768 | -0.045776 | 122.7402 | 122.6715 | -0.054932 | 122.7676 | 122.7676 | 0.09613 | -0.073242 | 122.9233 | 122.8867 | 122.8683 | -0.25635 | 122.8775 | 122.8592 | 122.8958 | -0.26093
4071.125 | 122.9233 | -122.7585 | 0.11444 | -0.015487 | -0.019869 | 0.019337 | 0.038587 | -0.031437 | -0.042355 | -0.015842 | 7.627e-05 | 0.00069003 | 0.00066871 | -0.094829 | -0.018551 | -0.00038438 | 0.10986 | 0.09613 | 0.14191 | 0.091553 | 0.09613 | 0.027466 | -0.11902 | 0.036621 | 0.19226 | 0.045776 | 0.045776 | 0.036621 | -0.022888 | -0.091553 | 122.7859 | 122.6395 | -0.018311 | 122.8546 | 122.85 | 0.21057 | -0.004578 | 122.7356 | 122.6669 | -0.068665 | 122.7951 | 122.8043 | 0.13733 | -0.07782 | 122.8546 | 122.8683 | 122.9004 | -0.23346 | 122.8043 | 122.7951 | 122.9507 | -0.20599
4072.9375 | 122.937 | -122.7905 | 0.1236 | -0.015487 | -0.016238 | 0.017628 | 0.036237 | -0.027591 | -0.038937 | -0.01456 | -0.015182 | 0.0045352 | -0.0014675 | -0.094616 | -0.014919 | -0.001239 | 0.027466 | -0.041199 | -0.013733 | 0 | 0.15106 | 0.004578 | -0.12817 | -0.086975 | 0.045776 | -0.07782 | 0.10071 | 0.082397 | -0.064087 | -0.13275 | 122.7951 | 122.6624 | 0.027466 | 122.7493 | 122.7905 | 0.12817 | -0.09613 | 122.7264 | 122.6578 | -0.022888 | 122.7036 | 122.7127 | 0.054931 | -0.041199 | 122.9416 | 122.818 | 122.7768 | -0.25177 | 122.8912 | 122.8729 | 122.8363 | -0.25635
4074.7188 | 122.937 | -122.7722 | 0.13275 | -0.0078584 | -0.018374 | 0.017201 | 0.033887 | -0.0293 | -0.037655 | -0.015629 | 7.627e-05 | 0.0036808 | 0.0015231 | -0.092907 | -0.015347 | 0.002179 | 0.032043 | -0.036621 | 0.009155 | 0.013733 | 0.14191 | -0.018311 | -0.14648 | -0.054932 | 0.036621 | -0.07782 | 0.10986 | 0.086975 | -0.068665 | -0.14191 | 122.7539 | 122.6257 | 0.009156 | 122.7356 | 122.7859 | 0.16022 | -0.10071 | 122.7036 | 122.6303 | -0.022888 | 122.7173 | 122.6944 | 0.064087 | -0.045776 | 122.9141 | 122.8043 | 122.7814 | -0.27924 | 122.8821 | 122.8592 | 122.8088 | -0.27466
4076.4531 | 123.056 | -122.7539 | 0.091553 | 0.0074006 | -0.021364 | 0.015919 | 0.033246 | -0.028019 | -0.035733 | -0.014988 | -0.0075532 | 0.0026126 | 0.00024151 | -0.094829 | -0.01257 | 0.00047002 | 0.13275 | 0.041199 | 0.091553 | 0.09613 | 0.10071 | 0.045776 | -0.091553 | 0.068665 | 0.13733 | 0.032043 | 0.041199 | 0.027466 | -0.027466 | -0.10986 | 122.7997 | 122.6624 | 0.009155 | 122.7951 | 122.85 | 0.18768 | 0.041198 | 122.7264 | 122.644 | -0.050354 | 122.8226 | 122.7859 | 0.14191 | -0.064087 | 122.8546 | 122.8867 | 122.8455 | -0.18311 | 122.7951 | 122.7814 | 122.8912 | -0.20142
4078.25 | 122.9233 | -122.7997 | 0.1236 | -0.0078584 | -0.017946 | 0.017415 | 0.036878 | -0.027378 | -0.042355 | -0.012638 | 0.0077058 | 0.00026283 | 2.7914e-05 | -0.096752 | -0.014919 | 0.00068362 | 0.11902 | 0.086975 | 0.11444 | 0.10071 | 0.10986 | 0.022888 | -0.10071 | 0.027466 | 0.16022 | 0.050354 | 0.050354 | 0.054932 | -0.009155 | -0.10529 | 122.8226 | 122.699 | -0.013733 | 122.8867 | 122.9004 | 0.20142 | -0.004577 | 122.7905 | 122.6944 | -0.073242 | 122.8271 | 122.85 | 0.15564 | -0.068664 | 122.9095 | 122.9187 | 122.9141 | -0.2243 | 122.85 | 122.8546 | 122.9599 | -0.22888
4080.0312 | 122.9324 | -122.8134 | 0.13275 | -0.00022891 | -0.023714 | 0.01891 | 0.036237 | -0.026096 | -0.038723 | -0.013279 | 7.627e-05 | 0.00069003 | 0.00045511 | -0.09547 | -0.014706 | 0.0011108 | 0.1236 | 0.068665 | 0.10529 | 0.091553 | 0.09613 | 0.050354 | -0.082397 | 0.054932 | 0.10529 | 0.036621 | 0.073242 | 0.036621 | -0.036621 | -0.10529 | 122.8638 | 122.731 | -0.036621 | 122.8821 | 122.905 | 0.17395 | -0.009155 | 122.7768 | 122.7081 | -0.059509 | 122.8683 | 122.85 | 0.14191 | -0.09613 | 122.9095 | 122.937 | 122.9187 | -0.21515 | 122.8867 | 122.85 | 122.9187 | -0.23804
4081.8125 | 123.0469 | -122.7402 | 0.082397 | -0.0078584 | -0.016665 | 0.017628 | 0.039227 | -0.027164 | -0.035519 | -0.012851 | -0.0075532 | 0.0030398 | 0.0021641 | -0.094189 | -0.015133 | -0.00017078 | 0.041199 | -0.050354 | -0.018311 | 0.018311 | 0.15106 | 0.004578 | -0.14648 | -0.041199 | 0.059509 | -0.086975 | 0.086975 | 0.082397 | -0.059509 | -0.13733 | 122.7448 | 122.5937 | 0.068665 | 122.6898 | 122.7585 | 0.16479 | -0.041198 | 122.6807 | 122.6028 | 0.004578 | 122.699 | 122.6532 | 0.050354 | 0 | 122.8912 | 122.7814 | 122.7219 | -0.22888 | 122.8271 | 122.8226 | 122.7997 | -0.21973
4083.6094 | 122.9782 | -122.7814 | 0.13733 | -0.0078584 | -0.021578 | 0.016346 | 0.034741 | -0.028019 | -0.038083 | -0.013706 | -0.0075532 | 0.00069003 | 0.00045511 | -0.09547 | -0.015347 | 0.0011108 | 0.13275 | 0.07782 | 0.13275 | 0.086975 | 0.082397 | 0.041199 | -0.091553 | 0.073242 | 0.14648 | 0.041199 | 0.059509 | 0.036621 | -0.027466 | -0.07782 | 122.8226 | 122.6898 | -0.054932 | 122.8592 | 122.8683 | 0.17853 | -0.004578 | 122.7539 | 122.7036 | -0.07782 | 122.8546 | 122.8226 | 0.11902 | -0.10071 | 122.8638 | 122.9141 | 122.9141 | -0.22888 | 122.8409 | 122.818 | 122.9279 | -0.21515
4085.3438 | 123.0515 | -122.7631 | 0.09613 | 0.0074006 | -0.015597 | 0.017628 | 0.03645 | -0.030155 | -0.035092 | -0.013279 | 7.627e-05 | 0.004108 | 0.00088231 | -0.094189 | -0.013424 | 0.0011108 | 0.041199 | -0.07782 | -0.027466 | 0 | 0.13733 | -0.004578 | -0.14191 | -0.050354 | -0.018311 | -0.10071 | 0.086975 | 0.068665 | -0.054932 | -0.1236 | 122.7585 | 122.6212 | 0.041199 | 122.6852 | 122.7631 | 0.14191 | -0.054931 | 122.7081 | 122.6395 | -0.009155 | 122.7127 | 122.6624 | 0.022888 | -0.027465 | 122.9004 | 122.8043 | 122.7356 | -0.23804 | 122.85 | 122.8317 | 122.7448 | -0.21973
4087.125 | 123.0743 | -122.7448 | 0.091553 | -0.0078584 | -0.016451 | 0.015278 | 0.03645 | -0.028446 | -0.037869 | -0.012424 | -0.0075532 | 0.004108 | 0.0019505 | -0.093334 | -0.012356 | 0.0017518 | 0.045776 | -0.022888 | 0.009155 | 0.013733 | 0.13275 | 0 | -0.13733 | 0.004578 | 0.032043 | -0.050354 | 0.064087 | 0.059509 | -0.050354 | -0.1236 | 122.7448 | 122.6074 | 0.041198 | 122.7219 | 122.7585 | 0.15106 | -0.045777 | 122.6944 | 122.6212 | -0.027466 | 122.7493 | 122.6944 | 0.073242 | -0.032044 | 122.8775 | 122.7905 | 122.7539 | -0.22888 | 122.8088 | 122.8043 | 122.7768 | -0.21515
4088.875 | 123.0606 | -122.7585 | 0.10529 | -0.015487 | -0.017092 | 0.016987 | 0.036664 | -0.030796 | -0.038296 | -0.012424 | 0.0077058 | 0.0030398 | 0.00045511 | -0.093975 | -0.014919 | 0.0017518 | 0.1236 | 0.082397 | 0.10986 | 0.09613 | 0.10986 | 0.041199 | -0.10071 | 0.064087 | 0.12817 | 0.041199 | 0.027466 | 0.027466 | -0.027466 | -0.10071 | 122.7997 | 122.6578 | 0.004577 | 122.8409 | 122.8546 | 0.19684 | 0.01831 | 122.731 | 122.6578 | -0.07782 | 122.8226 | 122.7997 | 0.14191 | -0.07782 | 122.8683 | 122.8821 | 122.8683 | -0.20599 | 122.7859 | 122.7859 | 122.8867 | -0.20599
4090.6875 | 123.0606 | -122.7493 | 0.086975 | -0.015487 | -0.017946 | 0.015706 | 0.038159 | -0.029514 | -0.033383 | -0.011997 | -0.0075532 | 0.0032534 | 0.00045511 | -0.093548 | -0.013638 | -0.0010254 | 0.10071 | 0.009155 | 0.032043 | 0.045776 | 0.10986 | 0.013733 | -0.13733 | 0.004578 | 0.091553 | -0.050354 | 0.059509 | 0.07782 | -0.050354 | -0.11902 | 122.7631 | 122.612 | 0.022888 | 122.7585 | 122.7951 | 0.18311 | 0.013733 | 122.699 | 122.6303 | -0.027466 | 122.7539 | 122.699 | 0.068665 | -0.009155 | 122.8592 | 122.85 | 122.7814 | -0.2243 | 122.8088 | 122.8271 | 122.8409 | -0.20599
4092.5 | 122.9599 | -122.7997 | 0.11902 | -0.00022891 | -0.017306 | 0.021473 | 0.040296 | -0.03165 | -0.042141 | -0.01392 | 7.627e-05 | -0.0012326 | -0.0012539 | -0.097393 | -0.019406 | 0.00047002 | 0.10529 | 0.10986 | 0.14191 | 0.09613 | 0.09613 | 0.032043 | -0.082397 | 0.054932 | 0.19226 | 0.064087 | 0.054932 | 0.036621 | -0.013733 | -0.10071 | 122.8317 | 122.7173 | -0.022889 | 122.9095 | 122.8958 | 0.17853 | -0.013733 | 122.7859 | 122.699 | -0.064087 | 122.8546 | 122.8638 | 0.1648 | -0.082398 | 122.8958 | 122.905 | 122.9416 | -0.20142 | 122.8546 | 122.8363 | 122.9919 | -0.21973
4094.2812 | 122.9691 | -122.7951 | 0.11902 | -0.00022891 | -0.019015 | 0.015065 | 0.039014 | -0.027591 | -0.038296 | -0.012851 | 7.627e-05 | 0.0034672 | 0.00045511 | -0.094616 | -0.015133 | 0.0013244 | 0.036621 | -0.054932 | -0.009155 | 0 | 0.13733 | -0.004578 | -0.14648 | -0.064087 | 0.032043 | -0.073242 | 0.091553 | 0.086975 | -0.064087 | -0.13275 | 122.7905 | 122.6486 | 0.01831 | 122.7402 | 122.7951 | 0.14648 | -0.082398 | 122.731 | 122.6624 | -0.027466 | 122.731 | 122.7219 | 0.059509 | -0.032044 | 122.9324 | 122.8317 | 122.7859 | -0.2655 | 122.8867 | 122.8821 | 122.8271 | -0.25177
4096.0625 | 122.937 | -122.8226 | 0.13733 | -0.0078584 | -0.023287 | 0.015492 | 0.034741 | -0.029941 | -0.040646 | -0.012424 | 7.627e-05 | 0.00090363 | -0.0029629 | -0.093975 | -0.01556 | 0.0028198 | 0.10986 | 0.082397 | 0.11444 | 0.07782 | 0.10986 | 0.054932 | -0.091553 | 0.041199 | 0.10986 | 0.022888 | 0.050354 | 0.036621 | -0.032043 | -0.091553 | 122.8775 | 122.731 | -0.027466 | 122.905 | 122.9004 | 0.16937 | -0.027466 | 122.7905 | 122.731 | -0.086975 | 122.8638 | 122.8455 | 0.11444 | -0.10071 | 122.9324 | 122.9324 | 122.937 | -0.22888 | 122.8729 | 122.8592 | 122.9324 | -0.22888
4097.8594 | 123.056 | -122.7585 | 0.086975 | -0.0078584 | -0.016878 | 0.01656 | 0.034955 | -0.030155 | -0.037228 | -0.013492 | 7.627e-05 | 0.0056034 | 0.00045511 | -0.093761 | -0.015133 | 0.00068362 | 0.13733 | 0.059509 | 0.1236 | 0.091553 | 0.10529 | 0.059509 | -0.09613 | 0.064087 | 0.13733 | 0.041199 | 0.041199 | 0.013733 | -0.027466 | -0.091553 | 122.818 | 122.6624 | 0.018311 | 122.818 | 122.85 | 0.18768 | 0.050354 | 122.731 | 122.6669 | -0.045776 | 122.8226 | 122.7997 | 0.13275 | -0.073242 | 122.8638 | 122.8958 | 122.8821 | -0.1831 | 122.7997 | 122.7722 | 122.8958 | -0.17853
4099.5938 | 122.9874 | -122.7997 | 0.11444 | -0.00022891 | -0.018374 | 0.019551 | 0.037518 | -0.026737 | -0.044278 | -0.014988 | 7.627e-05 | -0.00080537 | -0.0010403 | -0.096752 | -0.018337 | 0.0013244 | 0.14648 | 0.11444 | 0.13275 | 0.11444 | 0.10529 | 0.027466 | -0.091553 | 0.091553 | 0.19684 | 0.086975 | 0.050354 | 0.050354 | -0.018311 | -0.086975 | 122.8271 | 122.7081 | -0.009155 | 122.9141 | 122.9141 | 0.20599 | 0.032043 | 122.7814 | 122.7127 | -0.064087 | 122.8912 | 122.8867 | 0.17395 | -0.064087 | 122.905 | 122.9462 | 122.9324 | -0.20599 | 122.85 | 122.85 | 122.9965 | -0.20142
4101.4062 | 123.024 | -122.7951 | 0.091553 | -0.0078584 | -0.017519 | 0.017415 | 0.035809 | -0.027805 | -0.033169 | -0.0085791 | 7.627e-05 | 0.0064578 | 2.7914e-05 | -0.094616 | -0.011715 | 0.00025642 | 0.086975 | 0.009155 | 0.018311 | 0.045776 | 0.13275 | -0.004578 | -0.13275 | -0.036621 | 0.022888 | -0.10071 | 0.086975 | 0.059509 | -0.050354 | -0.13275 | 122.7905 | 122.6624 | 0.041198 | 122.8043 | 122.8409 | 0.17853 | -0.004578 | 122.7448 | 122.6624 | -0.004578 | 122.7585 | 122.6944 | 0.032043 | -0.032044 | 122.9279 | 122.8821 | 122.8134 | -0.2243 | 122.8821 | 122.8546 | 122.818 | -0.2243
4103.2031 | 122.9965 | -122.7859 | 0.11444 | -0.0078584 | -0.02521 | 0.017842 | 0.036878 | -0.0293 | -0.042141 | -0.012424 | 7.627e-05 | -0.00080537 | 0.00088231 | -0.096538 | -0.018765 | 0.002179 | 0.054932 | 0.041199 | 0.082397 | 0.073242 | 0.11902 | 0.013733 | -0.10986 | 0.022888 | 0.10986 | 0.027466 | 0.073242 | 0.018311 | -0.036621 | -0.086975 | 122.7997 | 122.6761 | 0.004578 | 122.8271 | 122.8592 | 0.18311 | -0.059509 | 122.7493 | 122.699 | -0.041199 | 122.8088 | 122.8134 | 0.11444 | -0.09613 | 122.905 | 122.8409 | 122.8683 | -0.2243 | 122.8592 | 122.8043 | 122.8958 | -0.20142
4104.9219 | 123.0606 | -122.7768 | 0.086975 | -0.00022891 | -0.016878 | 0.015278 | 0.040082 | -0.02866 | -0.034878 | -0.013279 | 7.627e-05 | 0.005176 | 0.0043003 | -0.093548 | -0.015133 | 0.0015382 | 0.032043 | -0.045776 | -0.009155 | 0.022888 | 0.13733 | -0.004578 | -0.13733 | -0.054932 | 0.041199 | -0.082397 | 0.086975 | 0.073242 | -0.073242 | -0.13275 | 122.7722 | 122.6395 | 0.050354 | 122.731 | 122.7997 | 0.16022 | -0.054932 | 122.7036 | 122.644 | 0 | 122.7219 | 122.6944 | 0.050354 | -0.013733 | 122.9141 | 122.8088 | 122.7676 | -0.2243 | 122.8638 | 122.85 | 122.818 | -0.21973
4106.7188 | 122.9874 | -122.7768 | 0.10986 | -0.00022891 | -0.019228 | 0.018696 | 0.038373 | -0.029941 | -0.04321 | -0.015201 | -0.0075532 | 0.00090363 | 0.0015231 | -0.093975 | -0.017483 | 0.00089722 | 0.10986 | 0.13275 | 0.11902 | 0.09613 | 0.10071 | 0.041199 | -0.11444 | 0.054932 | 0.19226 | 0.059509 | 0.050354 | 0.050354 | -0.027466 | -0.09613 | 122.818 | 122.6624 | -0.009155 | 122.9095 | 122.8729 | 0.21057 | 0 | 122.7493 | 122.6807 | -0.059509 | 122.8317 | 122.8363 | 0.15564 | -0.059509 | 122.8775 | 122.8867 | 122.8958 | -0.2243 | 122.8271 | 122.8271 | 122.9691 | -0.20599
4108.5156 | 123.0881 | -122.7676 | 0.086975 | -0.0078584 | -0.01816 | 0.013356 | 0.037091 | -0.028019 | -0.037655 | -0.01456 | -0.0075532 | 0.0026126 | 2.7914e-05 | -0.094829 | -0.012997 | 4.2822e-05 | 0.086975 | 0 | 0.022888 | 0.041199 | 0.13733 | 0.018311 | -0.1236 | 0.045776 | 0.07782 | -0.009155 | 0.059509 | 0.059509 | -0.013733 | -0.09613 | 122.7859 | 122.644 | 0.050354 | 122.7676 | 122.8088 | 0.16479 | 0 | 122.7539 | 122.6715 | -0.027466 | 122.8134 | 122.7585 | 0.086975 | -0.027466 | 122.905 | 122.8546 | 122.7905 | -0.21057 | 122.8271 | 122.8271 | 122.8455 | -0.1831
4110.2344 | 123.0057 | -122.8226 | 0.14191 | 0.0074006 | -0.022005 | 0.01656 | 0.03645 | -0.030369 | -0.041073 | -0.014347 | 0.0077058 | 0.00069003 | 0.0030185 | -0.096111 | -0.016201 | 0.0019654 | 0.059509 | 0.018311 | 0.082397 | 0.050354 | 0.11444 | 0.022888 | -0.10986 | 0.027466 | 0.11902 | 0.027466 | 0.050354 | 0.050354 | -0.027466 | -0.10986 | 122.8455 | 122.7127 | -0.027466 | 122.8409 | 122.8729 | 0.16022 | -0.082398 | 122.7951 | 122.7127 | -0.091553 | 122.85 | 122.85 | 0.13733 | -0.091553 | 122.937 | 122.8821 | 122.905 | -0.25177 | 122.8729 | 122.8729 | 122.9416 | -0.25177
4112.0312 | 123.0972 | -122.7859 | 0.086975 | -0.00022891 | -0.018587 | 0.01421 | 0.033246 | -0.02631 | -0.034451 | -0.012851 | 7.627e-05 | 0.0026126 | 0.00024151 | -0.096111 | -0.011929 | -0.00017078 | 0.07782 | -0.009155 | 0.018311 | 0.032043 | 0.1236 | 0.013733 | -0.1236 | 0.050354 | 0.086975 | -0.027466 | 0.059509 | 0.045776 | -0.004578 | -0.086975 | 122.7997 | 122.6624 | 0.036621 | 122.7768 | 122.818 | 0.15564 | -0.009155 | 122.7814 | 122.699 | -0.027466 | 122.8363 | 122.7585 | 0.059509 | -0.041199 | 122.9095 | 122.8638 | 122.8043 | -0.21057 | 122.8455 | 122.8317 | 122.8729 | -0.17395
4113.8281 | 123.0331 | -122.7905 | 0.10529 | -0.00022891 | -0.01581 | 0.016987 | 0.035169 | -0.030369 | -0.033596 | -0.013065 | -0.0075532 | 0.0045352 | 0.0015231 | -0.095257 | -0.011715 | -0.0016662 | 0.073242 | -0.013733 | 0.009155 | 0.032043 | 0.13275 | -0.018311 | -0.12817 | -0.050354 | 0.027466 | -0.10071 | 0.082397 | 0.064087 | -0.054932 | -0.14191 | 122.7722 | 122.6624 | 0.027465 | 122.7768 | 122.8226 | 0.16022 | -0.032044 | 122.7356 | 122.6486 | -0.022889 | 122.7402 | 122.6898 | 0.041199 | -0.041199 | 122.9233 | 122.8638 | 122.7997 | -0.23346 | 122.8729 | 122.8546 | 122.818 | -0.24719
4115.5781 | 123.0835 | -122.7951 | 0.082397 | -0.0078584 | -0.017733 | 0.015706 | 0.034314 | -0.027164 | -0.03616 | -0.011356 | 0.0077058 | 0.0056034 | -0.00061309 | -0.095684 | -0.014279 | 0.0015382 | 0.10986 | 0.036621 | 0.073242 | 0.064087 | 0.11444 | 0.027466 | -0.10071 | 0.059509 | 0.11902 | 0.022888 | 0.036621 | 0.041199 | -0.027466 | -0.082397 | 122.8226 | 122.6944 | 0.032044 | 122.8317 | 122.8592 | 0.1648 | 0.027466 | 122.7676 | 122.7127 | -0.045776 | 122.8546 | 122.818 | 0.10528 | -0.041198 | 122.9095 | 122.905 | 122.8683 | -0.18311 | 122.8317 | 122.8363 | 122.9141 | -0.16479
4117.375 | 123.0835 | -122.7585 | 0.082397 | -0.015487 | -0.016665 | 0.015919 | 0.036664 | -0.031437 | -0.034237 | -0.011356 | -0.0075532 | 0.0056034 | 0.00088231 | -0.094616 | -0.01257 | 0.0015382 | 0.10071 | 0.018311 | 0.036621 | 0.045776 | 0.13275 | 0.004578 | -0.15106 | -0.004578 | 0.09613 | -0.050354 | 0.082397 | 0.07782 | -0.059509 | -0.12817 | 122.7631 | 122.6074 | 0.050354 | 122.7768 | 122.8043 | 0.19684 | 0.018311 | 122.699 | 122.6303 | 0 | 122.7539 | 122.7081 | 0.07782 | -0.004577 | 122.8912 | 122.8592 | 122.7951 | -0.23346 | 122.8409 | 122.8363 | 122.8546 | -0.21057
4119.1719 | 122.9553 | -122.7951 | 0.1236 | 0.0074006 | -0.017306 | 0.018696 | 0.040723 | -0.027378 | -0.040646 | -0.012851 | -0.0075532 | 0.002399 | -0.00061309 | -0.093975 | -0.016842 | 0.00047002 | 0.07782 | 0.068665 | 0.07782 | 0.059509 | 0.10071 | 0.032043 | -0.1236 | -0.018311 | 0.10529 | -0.032043 | 0.059509 | 0.041199 | -0.041199 | -0.1236 | 122.8271 | 122.6715 | -0.022888 | 122.8638 | 122.8546 | 0.1831 | -0.045776 | 122.7539 | 122.6715 | -0.064087 | 122.7768 | 122.7631 | 0.091553 | -0.082397 | 122.8958 | 122.8729 | 122.8729 | -0.24719 | 122.8546 | 122.8363 | 122.9004 | -0.24719
4120.9844 | 123.0835 | -122.7997 | 0.07782 | -0.0078584 | -0.020083 | 0.015278 | 0.034955 | -0.029728 | -0.037655 | -0.012638 | 7.627e-05 | 0.002399 | -0.0021085 | -0.093975 | -0.013851 | -0.00038438 | 0.13733 | 0.082397 | 0.11444 | 0.086975 | 0.10071 | 0.032043 | -0.09613 | 0.068665 | 0.1236 | 0.045776 | 0.064087 | 0.022888 | -0.027466 | -0.086975 | 122.8317 | 122.7036 | 0.022888 | 122.8821 | 122.8867 | 0.1831 | 0.059509 | 122.7722 | 122.7127 | -0.013733 | 122.8683 | 122.8455 | 0.13275 | -0.054932 | 122.9004 | 122.937 | 122.9141 | -0.17395 | 122.8638 | 122.8226 | 122.9233 | -0.16479
4122.7188 | 122.9828 | -122.8088 | 0.11444 | -0.0078584 | -0.024142 | 0.017201 | 0.036664 | -0.02631 | -0.041928 | -0.016056 | -0.015182 | 0.0019718 | -0.0021085 | -0.097179 | -0.017269 | 0.00089722 | 0.13275 | 0.1236 | 0.12817 | 0.086975 | 0.10071 | 0.041199 | -0.10071 | 0.064087 | 0.18768 | 0.082397 | 0.054932 | 0.036621 | -0.022888 | -0.086975 | 122.85 | 122.7081 | -0.013733 | 122.9324 | 122.8958 | 0.18768 | 0.01831 | 122.7859 | 122.7219 | -0.059509 | 122.8729 | 122.8912 | 0.16937 | -0.07782 | 122.9095 | 122.9416 | 122.937 | -0.21515 | 122.8638 | 122.8455 | 122.9965 | -0.20142
4124.5156 | 122.9874 | -122.8088 | 0.09613 | -0.00022891 | -0.014742 | 0.016987 | 0.040296 | -0.028446 | -0.036587 | -0.014347 | 7.627e-05 | 0.0047488 | 0.0017367 | -0.093761 | -0.017697 | -0.00038438 | 0.036621 | -0.050354 | -0.009155 | 0.009155 | 0.14648 | -0.009155 | -0.16022 | -0.059509 | 0.027466 | -0.068665 | 0.082397 | 0.07782 | -0.073242 | -0.14648 | 122.7997 | 122.6486 | 0.050354 | 122.7585 | 122.818 | 0.16937 | -0.059509 | 122.7356 | 122.6624 | -0.013733 | 122.7493 | 122.7402 | 0.077819 | -0.01831 | 122.9553 | 122.8455 | 122.7997 | -0.25635 | 122.8912 | 122.8867 | 122.8363 | -0.24261
4126.2344 | 123.1155 | -122.7631 | 0.10071 | -0.00022891 | -0.017519 | 0.017415 | 0.032605 | -0.029087 | -0.036374 | -0.011783 | -0.0075532 | 0.0049624 | -0.00018589 | -0.09312 | -0.014919 | -0.00038438 | 0.068665 | -0.041199 | 0.004578 | 0.022888 | 0.12817 | 0.027466 | -0.13733 | 0.009155 | 0.054932 | -0.032043 | 0.082397 | 0.064087 | -0.059509 | -0.10529 | 122.7905 | 122.6257 | 0.027466 | 122.7219 | 122.7859 | 0.16022 | -0.032043 | 122.7036 | 122.6578 | -0.018311 | 122.7722 | 122.731 | 0.073243 | -0.036621 | 122.8912 | 122.8317 | 122.7676 | -0.23804 | 122.8455 | 122.8271 | 122.818 | -0.20599
4128.0469 | 123.056 | -122.7951 | 0.09613 | -0.0078584 | -0.017519 | 0.01656 | 0.033673 | -0.028873 | -0.034024 | -0.012424 | 7.627e-05 | 0.006885 | 2.7914e-05 | -0.092693 | -0.010861 | 0.00025642 | 0.10071 | 0.009155 | 0.018311 | 0.054932 | 0.12817 | 0 | -0.1236 | -0.018311 | 0.059509 | -0.064087 | 0.082397 | 0.068665 | -0.059509 | -0.1236 | 122.7951 | 122.6715 | 0.032044 | 122.8043 | 122.85 | 0.17853 | 0.004578 | 122.7356 | 122.6715 | -0.013733 | 122.7768 | 122.731 | 0.059509 | -0.027465 | 122.9233 | 122.8958 | 122.8134 | -0.21973 | 122.8775 | 122.8638 | 122.8546 | -0.21973
4129.8281 | 123.0057 | -122.8363 | 0.10986 | -0.00022891 | -0.01816 | 0.019337 | 0.037091 | -0.028446 | -0.043637 | -0.013492 | 0.0077058 | -0.00016437 | -0.0012539 | -0.094402 | -0.018978 | 0.0017518 | 0.11902 | 0.09613 | 0.12817 | 0.10529 | 0.10986 | 0.050354 | -0.10071 | 0.073242 | 0.20142 | 0.09613 | 0.050354 | 0.027466 | -0.004578 | -0.091553 | 122.8867 | 122.7356 | 0 | 122.9324 | 122.9416 | 0.20599 | 0.009156 | 122.8317 | 122.7448 | -0.059509 | 122.9095 | 122.9324 | 0.18768 | -0.082397 | 122.9462 | 122.9553 | 122.9645 | -0.21057 | 122.8867 | 122.8638 | 123.0377 | -0.20142
4131.5625 | 123.0927 | -122.7768 | 0.086975 | -0.00022891 | -0.017946 | 0.018483 | 0.034741 | -0.027164 | -0.033383 | -0.012424 | -0.0075532 | 0.006885 | -0.0031765 | -0.09312 | -0.01257 | -0.00017078 | 0.11444 | 0.009155 | 0.036621 | 0.059509 | 0.13275 | -0.004578 | -0.1236 | 0.009155 | 0.10071 | -0.045776 | 0.082397 | 0.068665 | -0.050354 | -0.1236 | 122.7722 | 122.6532 | 0.045776 | 122.7859 | 122.8363 | 0.1831 | 0.027466 | 122.7264 | 122.6532 | -0.004578 | 122.7859 | 122.731 | 0.07782 | -0.01831 | 122.9095 | 122.8912 | 122.8134 | -0.21057 | 122.8592 | 122.8455 | 122.8775 | -0.21057
4133.3594 | 122.9828 | -122.8271 | 0.10986 | -0.015487 | -0.017092 | 0.017201 | 0.038159 | -0.028232 | -0.037655 | -0.01392 | -0.0075532 | 0.0032534 | 0.0021641 | -0.095898 | -0.015988 | 0.002179 | 0.013733 | -0.027466 | -0.018311 | 0.013733 | 0.15106 | -0.004578 | -0.14648 | -0.068665 | 0.045776 | -0.073242 | 0.082397 | 0.07782 | -0.073242 | -0.12817 | 122.8226 | 122.6807 | 0.041199 | 122.7997 | 122.8409 | 0.16022 | -0.09613 | 122.7539 | 122.699 | -0.027466 | 122.7585 | 122.7539 | 0.054932 | -0.032043 | 122.9782 | 122.8409 | 122.8088 | -0.25635 | 122.9095 | 122.905 | 122.8729 | -0.23804
4135.1562 | 122.9828 | -122.8271 | 0.11902 | -0.00022891 | -0.017519 | 0.015706 | 0.038587 | -0.027164 | -0.039364 | -0.015415 | 0.0077058 | 0.0030398 | -0.00082669 | -0.095898 | -0.016201 | 0.0019654 | 0.032043 | 0.004578 | 0.018311 | 0.018311 | 0.13275 | 0.004578 | -0.13733 | -0.068665 | 0.059509 | -0.054932 | 0.091553 | 0.082397 | -0.068665 | -0.13275 | 122.8317 | 122.6898 | 0.013732 | 122.8317 | 122.8455 | 0.15564 | -0.086976 | 122.7585 | 122.6944 | -0.027466 | 122.7585 | 122.7722 | 0.077819 | -0.036622 | 122.9599 | 122.8592 | 122.8455 | -0.25635 | 122.9187 | 122.9095 | 122.8867 | -0.25177
4136.9688 | 123.1018 | -122.7722 | 0.10529 | -0.00022891 | -0.014101 | 0.014637 | 0.0388 | -0.026523 | -0.035519 | -0.012638 | -0.0075532 | 0.0045352 | 0.0010959 | -0.095043 | -0.017697 | 0.00068362 | 0.068665 | -0.032043 | 0.004578 | 0.036621 | 0.14191 | 0.004578 | -0.13275 | -0.018311 | 0.086975 | -0.045776 | 0.082397 | 0.07782 | -0.059509 | -0.11902 | 122.7768 | 122.6395 | 0.036621 | 122.7402 | 122.8088 | 0.16937 | -0.036621 | 122.7127 | 122.6532 | -0.022889 | 122.7539 | 122.7264 | 0.073243 | -0.027466 | 122.9141 | 122.8409 | 122.7768 | -0.23804 | 122.8546 | 122.85 | 122.8592 | -0.22431
4138.7031 | 123.0927 | -122.7859 | 0.10529 | -0.0078584 | -0.020083 | 0.015706 | 0.036237 | -0.027805 | -0.03851 | -0.012851 | 0.0077058 | 0.0034672 | -0.0014675 | -0.094402 | -0.016201 | 0.0017518 | 0.09613 | 0.073242 | 0.091553 | 0.086975 | 0.07782 | 0.041199 | -0.10071 | 0.050354 | 0.13275 | 0.036621 | 0.050354 | 0.022888 | -0.013733 | -0.09613 | 122.8271 | 122.6852 | -0.027466 | 122.8592 | 122.8729 | 0.18768 | -0.009156 | 122.7722 | 122.6898 | -0.054932 | 122.8363 | 122.8226 | 0.13275 | -0.082398 | 122.8638 | 122.8821 | 122.8775 | -0.20599 | 122.8363 | 122.8088 | 122.9187 | -0.20142
4140.5 | 123.0927 | -122.7676 | 0.086975 | -0.00022891 | -0.014529 | 0.015278 | 0.034528 | -0.028446 | -0.035092 | -0.012851 | 0.0077058 | 0.006885 | -0.00082669 | -0.095684 | -0.011715 | -0.0014526 | 0.091553 | 0.004578 | 0.041199 | 0.068665 | 0.12817 | 0.013733 | -0.15106 | 0 | 0.10071 | -0.041199 | 0.086975 | 0.064087 | -0.054932 | -0.1236 | 122.7814 | 122.6166 | 0.041199 | 122.7722 | 122.8363 | 0.21973 | 0.004578 | 122.7127 | 122.644 | 0 | 122.7676 | 122.7264 | 0.082397 | -0.022888 | 122.8958 | 122.8592 | 122.8088 | -0.23804 | 122.8546 | 122.8317 | 122.8683 | -0.21057
4142.2969 | 122.9736 | -122.8455 | 0.12817 | -0.00022891 | -0.02521 | 0.01656 | 0.036664 | -0.027164 | -0.043423 | -0.014133 | 7.627e-05 | 0.0013308 | -0.0027493 | -0.093761 | -0.018337 | 0.0023926 | 0.068665 | 0.036621 | 0.086975 | 0.050354 | 0.09613 | 0.018311 | -0.10529 | -0.004578 | 0.09613 | 0.027466 | 0.059509 | 0.041199 | -0.032043 | -0.091553 | 122.8638 | 122.7402 | -0.032044 | 122.8821 | 122.8958 | 0.15564 | -0.059509 | 122.8134 | 122.7539 | -0.068665 | 122.8409 | 122.8729 | 0.11902 | -0.086975 | 122.9416 | 122.9141 | 122.9324 | -0.23346 | 122.905 | 122.8867 | 122.9416 | -0.21973
4144.0938 | 122.9736 | -122.8455 | 0.14191 | 0.0074006 | -0.023073 | 0.017201 | 0.034528 | -0.028232 | -0.04321 | -0.013706 | -0.0075532 | 0.0013308 | -0.0046719 | -0.095684 | -0.016201 | 0.0017518 | 0.091553 | 0.054932 | 0.082397 | 0.041199 | 0.10071 | 0.032043 | -0.10071 | 0.009155 | 0.10986 | 0.013733 | 0.045776 | 0.054932 | -0.036621 | -0.10986 | 122.8775 | 122.7448 | -0.041199 | 122.9004 | 122.8867 | 0.14191 | -0.050354 | 122.8088 | 122.7356 | -0.096131 | 122.8546 | 122.8592 | 0.1236 | -0.086975 | 122.9462 | 122.937 | 122.9279 | -0.24262 | 122.8912 | 122.9004 | 122.9553 | -0.25177
4145.8906 | 123.0057 | -122.818 | 0.10986 | 0.0074006 | -0.016451 | 0.017201 | 0.034314 | -0.0293 | -0.037442 | -0.015629 | -0.0075532 | 0.0038944 | 0.00045511 | -0.09547 | -0.015133 | 0.0028198 | 0.045776 | -0.018311 | 0 | 0.009155 | 0.14191 | 0.009155 | -0.14648 | -0.064087 | 0.036621 | -0.068665 | 0.10071 | 0.086975 | -0.07782 | -0.12817 | 122.8271 | 122.6715 | 0.032044 | 122.7997 | 122.8271 | 0.15564 | -0.064087 | 122.7402 | 122.6898 | -0.009155 | 122.7539 | 122.7493 | 0.059509 | -0.022888 | 122.9599 | 122.8638 | 122.818 | -0.25635 | 122.9187 | 122.905 | 122.8546 | -0.23804
4147.7031 | 123.0881 | -122.7768 | 0.086975 | 0.0074006 | -0.014315 | 0.014637 | 0.033887 | -0.026737 | -0.034665 | -0.010502 | 7.627e-05 | 0.006885 | 0.00088231 | -0.095043 | -0.011501 | -0.00081178 | 0.09613 | 0.004578 | 0.036621 | 0.045776 | 0.14191 | -0.004578 | -0.12817 | 0.009155 | 0.086975 | -0.032043 | 0.082397 | 0.068665 | -0.050354 | -0.10529 | 122.7722 | 122.6486 | 0.054932 | 122.7814 | 122.8226 | 0.17395 | 0.009155 | 122.7264 | 122.6715 | -0.004578 | 122.7859 | 122.7448 | 0.073243 | -0.01831 | 122.9187 | 122.8729 | 122.8134 | -0.21515 | 122.8592 | 122.8455 | 122.8638 | -0.19226
4149.4531 | 123.024 | -122.8317 | 0.11902 | -0.00022891 | -0.019015 | 0.018483 | 0.04115 | -0.029087 | -0.043423 | -0.01392 | -0.0075532 | 4.9234e-05 | 0.00066871 | -0.096325 | -0.020046 | 0.0015382 | 0.086975 | 0.045776 | 0.10529 | 0.073242 | 0.10986 | 0.032043 | -0.10529 | 0.050354 | 0.15106 | 0.073242 | 0.054932 | 0.036621 | -0.013733 | -0.10529 | 122.8638 | 122.7264 | -0.009156 | 122.8775 | 122.905 | 0.17853 | -0.032044 | 122.818 | 122.7264 | -0.064087 | 122.8821 | 122.905 | 0.17853 | -0.082398 | 122.9416 | 122.9187 | 122.937 | -0.22431 | 122.8867 | 122.8683 | 122.9828 | -0.22431
4151.25 | 123.1018 | -122.7905 | 0.082397 | -0.0078584 | -0.01581 | 0.015706 | 0.038587 | -0.0293 | -0.034878 | -0.011997 | -0.0075532 | 0.0083804 | 0.0030185 | -0.094402 | -0.013851 | -0.00059818 | 0.09613 | 0.004578 | 0.022888 | 0.032043 | 0.14191 | 0 | -0.14191 | -0.004578 | 0.086975 | -0.050354 | 0.086975 | 0.064087 | -0.059509 | -0.11902 | 122.7905 | 122.6486 | 0.05951 | 122.7951 | 122.8226 | 0.17395 | 0.013733 | 122.731 | 122.6715 | 0.004578 | 122.7859 | 122.7402 | 0.068665 | -0.01831 | 122.9324 | 122.8867 | 122.8134 | -0.2243 | 122.8775 | 122.8546 | 122.8775 | -0.20142
4152.9844 | 122.9919 | -122.8363 | 0.10529 | -0.023117 | -0.016451 | 0.016774 | 0.037091 | -0.025242 | -0.038937 | -0.010502 | 7.627e-05 | 0.0056034 | 0.0013095 | -0.094189 | -0.017056 | 0.00089722 | 0.041199 | -0.036621 | 0 | 0.009155 | 0.12817 | -0.004578 | -0.14648 | -0.054932 | 0.050354 | -0.073242 | 0.09613 | 0.091553 | -0.068665 | -0.14648 | 122.8317 | 122.6898 | 0.022888 | 122.7997 | 122.8455 | 0.15564 | -0.064087 | 122.7676 | 122.6898 | -0.009156 | 122.7814 | 122.7631 | 0.073242 | -0.013733 | 122.9645 | 122.8775 | 122.8363 | -0.25177 | 122.9324 | 122.9279 | 122.8867 | -0.25177
4154.7656 | 123.0881 | -122.7905 | 0.086975 | 0.0074006 | -0.016024 | 0.015278 | 0.039655 | -0.028232 | -0.037228 | -0.013065 | 7.627e-05 | 0.0064578 | 0.0034457 | -0.093761 | -0.015988 | 0.0019654 | 0.027466 | -0.064087 | 0 | 0.036621 | 0.14191 | 0.004578 | -0.12817 | -0.054932 | 0.054932 | -0.073242 | 0.086975 | 0.07782 | -0.068665 | -0.11444 | 122.7951 | 122.6624 | 0.054932 | 122.7264 | 122.8271 | 0.1648 | -0.059509 | 122.7219 | 122.6761 | 0 | 122.7356 | 122.7173 | 0.041199 | -0.009155 | 122.9324 | 122.818 | 122.7905 | -0.21515 | 122.8775 | 122.8683 | 122.8455 | -0.20142
4156.5 | 123.0606 | -122.818 | 0.10529 | -0.0078584 | -0.015597 | 0.013997 | 0.034101 | -0.026523 | -0.034665 | -0.013279 | 7.627e-05 | 0.0062442 | 2.7914e-05 | -0.091411 | -0.010433 | -0.00017078 | 0.10986 | 0.018311 | 0.027466 | 0.054932 | 0.1236 | 0.013733 | -0.11902 | -0.013733 | 0.064087 | -0.068665 | 0.07782 | 0.059509 | -0.064087 | -0.11444 | 122.8317 | 122.699 | 0.01831 | 122.8363 | 122.8729 | 0.17395 | 0.004577 | 122.7539 | 122.7036 | -0.027466 | 122.8043 | 122.7493 | 0.045776 | -0.045777 | 122.9416 | 122.9279 | 122.8455 | -0.22431 | 122.8958 | 122.8775 | 122.8821 | -0.21973
4158.3125 | 123.0652 | -122.8088 | 0.09613 | -0.00022891 | -0.017946 | 0.016133 | 0.039227 | -0.026523 | -0.03851 | -0.014347 | -0.0075532 | 0.0032534 | 0.0034457 | -0.093761 | -0.014279 | 0.003247 | 0.013733 | -0.036621 | -0.013733 | 0.013733 | 0.14648 | -0.004578 | -0.15106 | -0.059509 | 0.059509 | -0.082397 | 0.086975 | 0.073242 | -0.07782 | -0.13733 | 122.8043 | 122.6578 | 0.050354 | 122.7722 | 122.8226 | 0.16479 | -0.082397 | 122.731 | 122.6715 | -0.009155 | 122.7493 | 122.7264 | 0.054932 | -0.022888 | 122.9553 | 122.8226 | 122.7951 | -0.24719 | 122.8958 | 122.8821 | 122.8683 | -0.23346
4160.1094 | 123.1064 | -122.8043 | 0.09613 | 0.0074006 | -0.019655 | 0.015278 | 0.033673 | -0.031009 | -0.03851 | -0.01392 | 0.022965 | 0.0030398 | 2.7914e-05 | -0.095257 | -0.011501 | 0.0026062 | 0.10986 | 0.064087 | 0.10071 | 0.09613 | 0.10071 | 0.041199 | -0.10986 | 0.064087 | 0.13275 | 0.059509 | 0.027466 | 0.032043 | -0.013733 | -0.07782 | 122.8455 | 122.6944 | 0.004578 | 122.8683 | 122.9004 | 0.20599 | 0.013733 | 122.7905 | 122.7264 | -0.068664 | 122.8683 | 122.8638 | 0.13733 | -0.064087 | 122.905 | 122.9141 | 122.905 | -0.20599 | 122.8317 | 122.8363 | 122.937 | -0.17395
4161.8281 | 123.0743 | -122.8226 | 0.086975 | -0.00022891 | -0.015169 | 0.017201 | 0.036023 | -0.029514 | -0.035519 | -0.011142 | 7.627e-05 | 0.0056034 | -0.0021085 | -0.092693 | -0.013638 | 0.0013244 | 0.10071 | 0.022888 | 0.032043 | 0.054932 | 0.11902 | 0.018311 | -0.13275 | -0.004578 | 0.073242 | -0.064087 | 0.064087 | 0.082397 | -0.041199 | -0.12817 | 122.8409 | 122.6898 | 0.032044 | 122.8455 | 122.8775 | 0.18768 | 0.013733 | 122.7814 | 122.6944 | -0.022888 | 122.818 | 122.7585 | 0.064087 | -0.004578 | 122.9416 | 122.9233 | 122.8546 | -0.21973 | 122.8867 | 122.905 | 122.8958 | -0.21515
4163.6406 | 122.9782 | -122.8683 | 0.11444 | -0.0078584 | -0.017733 | 0.018696 | 0.037091 | -0.030155 | -0.044491 | -0.013706 | 7.627e-05 | 0.0026126 | -0.0010403 | -0.097607 | -0.017483 | 0.0015382 | 0.086975 | 0.068665 | 0.10071 | 0.082397 | 0.091553 | 0.022888 | -0.11444 | -0.004578 | 0.12817 | 0 | 0.068665 | 0.064087 | -0.036621 | -0.10986 | 122.8912 | 122.7539 | -0.022888 | 122.937 | 122.9507 | 0.19684 | -0.027466 | 122.8317 | 122.7585 | -0.045776 | 122.8638 | 122.8683 | 0.10986 | -0.050354 | 122.9599 | 122.9553 | 122.9691 | -0.22888 | 122.937 | 122.9324 | 122.9965 | -0.2243
4165.3906 | 123.024 | -122.8226 | 0.09613 | -0.0078584 | -0.016451 | 0.015278 | 0.039227 | -0.028232 | -0.040219 | -0.013706 | 7.627e-05 | 0.002399 | 2.7914e-05 | -0.093761 | -0.017056 | 0.0011108 | 0.13275 | 0.082397 | 0.13275 | 0.086975 | 0.086975 | 0.036621 | -0.086975 | 0.059509 | 0.14648 | 0.045776 | 0.041199 | 0.036621 | -0.036621 | -0.068665 | 122.8592 | 122.7356 | -0.009155 | 122.905 | 122.9095 | 0.17395 | 0.036621 | 122.7859 | 122.7539 | -0.054931 | 122.8821 | 122.8683 | 0.11444 | -0.059509 | 122.9095 | 122.9553 | 122.9553 | -0.1831 | 122.8638 | 122.8592 | 122.9691 | -0.16479
4167.1875 | 123.1018 | -122.8088 | 0.086975 | -0.00022891 | -0.019228 | 0.015919 | 0.033887 | -0.027805 | -0.034878 | -0.013706 | 0.0077058 | 0.0047488 | 0.00066871 | -0.094829 | -0.013851 | 0.0011108 | 0.12817 | 0.041199 | 0.10071 | 0.086975 | 0.09613 | 0.045776 | -0.11902 | 0.050354 | 0.13733 | 0.032043 | 0.050354 | 0.027466 | -0.004578 | -0.086975 | 122.8546 | 122.6898 | 0.009155 | 122.85 | 122.8958 | 0.20599 | 0.041199 | 122.8043 | 122.7219 | -0.036621 | 122.8592 | 122.8409 | 0.11902 | -0.059509 | 122.905 | 122.937 | 122.9095 | -0.20599 | 122.8592 | 122.8363 | 122.9462 | -0.17395
4168.9844 | 123.111 | -122.7997 | 0.09613 | -0.00022891 | -0.01282 | 0.016774 | 0.039441 | -0.028232 | -0.035733 | -0.013706 | 7.627e-05 | 0.0028262 | 0.0013095 | -0.094402 | -0.016201 | -0.0014526 | 0.045776 | -0.045776 | -0.009155 | 0.013733 | 0.15106 | 0.004578 | -0.13275 | -0.045776 | 0.054932 | -0.059509 | 0.091553 | 0.064087 | -0.064087 | -0.1236 | 122.8043 | 122.6669 | 0.054932 | 122.7539 | 122.8134 | 0.14648 | -0.050354 | 122.7356 | 122.6761 | -0.004577 | 122.7539 | 122.7402 | 0.064087 | -0.032043 | 122.9507 | 122.8455 | 122.7905 | -0.22888 | 122.8912 | 122.8638 | 122.8546 | -0.21973
4170.7188 | 123.056 | -122.8134 | 0.086975 | -0.00022891 | -0.016238 | 0.014424 | 0.034528 | -0.026951 | -0.033596 | -0.013065 | -0.0075532 | 0.006885 | 0.0019505 | -0.092266 | -0.012356 | -0.00059818 | 0.082397 | 0.004578 | 0.013733 | 0.041199 | 0.13733 | 0.022888 | -0.13733 | -0.018311 | 0.054932 | -0.064087 | 0.082397 | 0.073242 | -0.050354 | -0.1236 | 122.8363 | 122.6761 | 0.050354 | 122.818 | 122.8546 | 0.17853 | -0.004578 | 122.7631 | 122.6898 | -0.004578 | 122.7951 | 122.7493 | 0.059509 | -0.013733 | 122.9507 | 122.8958 | 122.8271 | -0.2243 | 122.8958 | 122.8867 | 122.8683 | -0.21057
4172.5156 | 123.1247 | -122.7997 | 0.091553 | -0.0078584 | -0.017092 | 0.018696 | 0.036023 | -0.030155 | -0.039792 | -0.011783 | -0.0075532 | 0.0045352 | -0.00018589 | -0.094616 | -0.01321 | 0.0019654 | 0.009155 | -0.059509 | -0.013733 | 0.009155 | 0.14191 | 0.004578 | -0.13275 | -0.032043 | 0.013733 | -0.068665 | 0.091553 | 0.082397 | -0.054932 | -0.11902 | 122.8043 | 122.6669 | 0.050354 | 122.7402 | 122.8088 | 0.14191 | -0.082398 | 122.7448 | 122.6807 | 0 | 122.7676 | 122.731 | 0.050354 | -0.009156 | 122.9416 | 122.8088 | 122.7859 | -0.2243 | 122.8912 | 122.8821 | 122.8134 | -0.21057
4174.25 | 122.9782 | -122.8592 | 0.13275 | -0.015487 | -0.019228 | 0.016346 | 0.040082 | -0.029514 | -0.042782 | -0.012424 | 7.627e-05 | 0.0011172 | 0.0028049 | -0.095257 | -0.017056 | 0.0017518 | 0.082397 | 0.091553 | 0.10986 | 0.091553 | 0.10529 | 0.027466 | -0.10986 | 0.004578 | 0.14648 | 0.018311 | 0.073242 | 0.073242 | -0.041199 | -0.10071 | 122.8867 | 122.7493 | -0.027465 | 122.9507 | 122.9507 | 0.20142 | -0.050354 | 122.818 | 122.7585 | -0.059509 | 122.8638 | 122.8775 | 0.11902 | -0.059509 | 122.9645 | 122.9416 | 122.9691 | -0.24261 | 122.9324 | 122.9324 | 123.0057 | -0.23346
4176.0469 | 123.1201 | -122.7859 | 0.082397 | -0.0078584 | -0.012179 | 0.012501 | 0.04115 | -0.028446 | -0.035733 | -0.013279 | 7.627e-05 | 0.005176 | 0.0055821 | -0.093761 | -0.015133 | -0.0023072 | 0.086975 | -0.018311 | 0.022888 | 0.050354 | 0.12817 | 0.009155 | -0.14191 | -0.013733 | 0.07782 | -0.050354 | 0.064087 | 0.086975 | -0.050354 | -0.14191 | 122.7951 | 122.644 | 0.045777 | 122.7676 | 122.8363 | 0.19226 | 0.004578 | 122.7356 | 122.644 | -0.01831 | 122.7722 | 122.7356 | 0.091553 | 0.004578 | 122.9141 | 122.8729 | 122.8088 | -0.2243 | 122.85 | 122.8729 | 122.8638 | -0.2243
4177.8438 | 122.9965 | -122.8729 | 0.1236 | -0.015487 | -0.020296 | 0.017842 | 0.036664 | -0.027805 | -0.041501 | -0.015201 | 7.627e-05 | 0.0011172 | 0.00066871 | -0.097179 | -0.015774 | 0.00068362 | 0.07782 | 0.10071 | 0.11902 | 0.10529 | 0.091553 | 0.032043 | -0.10071 | 0.013733 | 0.15106 | 0.032043 | 0.054932 | 0.054932 | -0.041199 | -0.10071 | 122.905 | 122.7722 | -0.032043 | 122.9736 | 122.9782 | 0.20599 | -0.045776 | 122.8317 | 122.7722 | -0.068664 | 122.8867 | 122.905 | 0.13275 | -0.068664 | 122.9645 | 122.9507 | 122.9919 | -0.2243 | 122.9279 | 122.9279 | 123.024 | -0.2243
4179.5938 | 123.0103 | -122.8683 | 0.11902 | 0.0074006 | -0.017092 | 0.018696 | 0.037518 | -0.028232 | -0.039364 | -0.01456 | -0.0075532 | 0.0015446 | 0.0025913 | -0.095898 | -0.018765 | 0.00068362 | 0.022888 | -0.036621 | 0.022888 | 0.018311 | 0.13275 | 0.004578 | -0.13733 | -0.054932 | 0.036621 | -0.068665 | 0.10071 | 0.086975 | -0.064087 | -0.13275 | 122.8729 | 122.731 | 0.013732 | 122.8317 | 122.8867 | 0.15564 | -0.096131 | 122.8043 | 122.7356 | -0.018311 | 122.8134 | 122.7997 | 0.064086 | -0.032044 | 123.0011 | 122.8912 | 122.8912 | -0.25635 | 122.9691 | 122.9553 | 122.905 | -0.25177
4181.4062 | 123.0469 | -122.85 | 0.12817 | -0.00022891 | -0.020296 | 0.01656 | 0.037946 | -0.02866 | -0.042355 | -0.016483 | 0.0077058 | 0.002399 | 0.0021641 | -0.095043 | -0.020474 | 0.0013244 | 0.054932 | 0.022888 | 0.073242 | 0.054932 | 0.11444 | 0.027466 | -0.11444 | 0.032043 | 0.11444 | 0.045776 | 0.059509 | 0.059509 | -0.036621 | -0.09613 | 122.8775 | 122.7356 | -0.013733 | 122.8729 | 122.905 | 0.16937 | -0.073242 | 122.8134 | 122.7539 | -0.068665 | 122.8821 | 122.8958 | 0.14191 | -0.068665 | 122.9645 | 122.905 | 122.9233 | -0.24262 | 122.9095 | 122.9095 | 122.9645 | -0.2243
4183.2031 | 123.1018 | -122.8271 | 0.09613 | -0.023117 | -0.017306 | 0.015492 | 0.032819 | -0.026523 | -0.037014 | -0.012424 | -0.0075532 | 0.004108 | 0.0025913 | -0.095043 | -0.012142 | 0.0011108 | 0.13733 | 0.068665 | 0.11444 | 0.091553 | 0.091553 | 0.041199 | -0.09613 | 0.050354 | 0.13733 | 0.036621 | 0.032043 | 0.027466 | -0.041199 | -0.082397 | 122.8683 | 122.731 | -0.004577 | 122.8958 | 122.9187 | 0.18768 | 0.041199 | 122.7859 | 122.7448 | -0.064087 | 122.8775 | 122.8638 | 0.11902 | -0.068664 | 122.9187 | 122.9645 | 122.9416 | -0.19226 | 122.8592 | 122.8546 | 122.9645 | -0.17853
4185.0156 | 122.9828 | -122.8775 | 0.12817 | 0.0074006 | -0.017092 | 0.018055 | 0.036878 | -0.027378 | -0.039364 | -0.013065 | 0.0077058 | 0.004108 | -0.00082669 | -0.09547 | -0.014279 | -0.00081178 | 0.091553 | 0.050354 | 0.073242 | 0.068665 | 0.1236 | 0.018311 | -0.11444 | -0.013733 | 0.091553 | -0.041199 | 0.086975 | 0.068665 | -0.045776 | -0.10529 | 122.8958 | 122.7631 | -0.004578 | 122.9279 | 122.9462 | 0.18311 | -0.036621 | 122.8317 | 122.7722 | -0.041199 | 122.8638 | 122.8363 | 0.064087 | -0.059509 | 123.0011 | 122.9691 | 122.9507 | -0.24262 | 122.9645 | 122.9462 | 122.9691 | -0.23346
4186.7656 | 123.0011 | -122.8546 | 0.13733 | -0.00022891 | -0.01816 | 0.018269 | 0.03645 | -0.029941 | -0.038296 | -0.016056 | -0.0075532 | 0.0015446 | -0.00082669 | -0.09547 | -0.015988 | 4.2822e-05 | 0.11902 | 0.086975 | 0.12817 | 0.09613 | 0.09613 | 0.027466 | -0.11902 | 0.041199 | 0.15564 | 0.041199 | 0.064087 | 0.036621 | -0.036621 | -0.09613 | 122.8821 | 122.7356 | -0.041199 | 122.9416 | 122.9507 | 0.21515 | -0.01831 | 122.818 | 122.7585 | -0.073242 | 122.8958 | 122.8958 | 0.13733 | -0.10071 | 122.9507 | 122.9736 | 122.9828 | -0.25635 | 122.9187 | 122.8912 | 123.0103 | -0.23346
4188.5625 | 123.0148 | -122.8409 | 0.11902 | -0.00022891 | -0.019869 | 0.018055 | 0.039014 | -0.028873 | -0.040005 | -0.014988 | 0.0077058 | 0.0021854 | -0.00018589 | -0.094616 | -0.016201 | 0.00047002 | 0.13275 | 0.11444 | 0.13733 | 0.091553 | 0.091553 | 0.050354 | -0.09613 | 0.073242 | 0.19226 | 0.059509 | 0.027466 | 0.050354 | -0.022888 | -0.091553 | 122.8912 | 122.7448 | -0.027466 | 122.9553 | 122.9324 | 0.18768 | 0.013732 | 122.818 | 122.7493 | -0.091553 | 122.9141 | 122.9004 | 0.15106 | -0.068665 | 122.9324 | 122.9736 | 122.9782 | -0.21515 | 122.8683 | 122.8912 | 123.0331 | -0.21057
4190.3125 | 123.0423 | -122.85 | 0.1236 | -0.00022891 | -0.024142 | 0.019551 | 0.034955 | -0.027805 | -0.040005 | -0.015415 | -0.0075532 | -0.00016437 | -0.0018949 | -0.092907 | -0.016842 | 0.0013244 | 0.07782 | 0.013733 | 0.07782 | 0.064087 | 0.09613 | 0.036621 | -0.091553 | 0.004578 | 0.086975 | 0.022888 | 0.050354 | 0.064087 | -0.004578 | -0.09613 | 122.8867 | 122.7585 | -0.027466 | 122.8638 | 122.9141 | 0.15564 | -0.045776 | 122.8455 | 122.7539 | -0.073242 | 122.8546 | 122.8729 | 0.11902 | -0.059509 | 122.9462 | 122.9279 | 122.9279 | -0.21515 | 122.9004 | 122.9141 | 122.937 | -0.21973
4192.1094 | 123.1293 | -122.8546 | 0.086975 | 0.0074006 | -0.019442 | 0.015065 | 0.034528 | -0.029941 | -0.031247 | -0.013065 | 7.627e-05 | 0.0066714 | 0.00066871 | -0.090343 | -0.014706 | -0.0016662 | 0.11444 | -0.004578 | 0.041199 | 0.036621 | 0.14191 | 0.027466 | -0.10529 | 0.054932 | 0.11902 | 0 | 0.041199 | 0.059509 | -0.013733 | -0.10071 | 122.8821 | 122.7493 | 0.054932 | 122.85 | 122.8912 | 0.14191 | 0.027466 | 122.8409 | 122.7539 | -0.045776 | 122.9095 | 122.8546 | 0.10071 | -0.027466 | 122.9965 | 122.9691 | 122.8958 | -0.19226 | 122.8958 | 122.9141 | 122.9736 | -0.18768
4193.9062 | 123.1338 | -122.8088 | 0.086975 | -0.00022891 | -0.013888 | 0.015492 | 0.03645 | -0.025669 | -0.031033 | -0.014133 | 7.627e-05 | 0.0088076 | 0.0032321 | -0.094616 | -0.014919 | -0.002948 | 0.11444 | 0.013733 | 0.050354 | 0.068665 | 0.14191 | 0.009155 | -0.15106 | 0.013733 | 0.091553 | -0.050354 | 0.073242 | 0.054932 | -0.050354 | -0.10986 | 122.818 | 122.6578 | 0.054932 | 122.8226 | 122.8775 | 0.21973 | 0.027466 | 122.7585 | 122.699 | -0.013733 | 122.8226 | 122.7585 | 0.059509 | -0.032043 | 122.9507 | 122.9233 | 122.8592 | -0.23804 | 122.8821 | 122.8638 | 122.9004 | -0.19684
4195.6562 | 122.9965 | -122.8592 | 0.13275 | -0.0078584 | -0.017733 | 0.018269 | 0.038373 | -0.025455 | -0.040646 | -0.011997 | -0.0075532 | 4.9234e-05 | 0.0013095 | -0.095043 | -0.014919 | 0.0034608 | 0.10071 | 0.086975 | 0.11444 | 0.086975 | 0.09613 | 0.022888 | -0.11902 | 0.022888 | 0.14191 | 0.009155 | 0.064087 | 0.045776 | -0.036621 | -0.10071 | 122.8821 | 122.7402 | -0.036621 | 122.9462 | 122.9462 | 0.20599 | -0.032043 | 122.8226 | 122.7585 | -0.068664 | 122.8821 | 122.8683 | 0.10986 | -0.086975 | 122.9553 | 122.9599 | 122.9736 | -0.25177 | 122.9233 | 122.905 | 123.0011 | -0.23346
4197.4375 | 123.0331 | -122.8134 | 0.11902 | -0.00022891 | -0.018801 | 0.018055 | 0.037946 | -0.029941 | -0.040646 | -0.015415 | -0.0075532 | 0.0013308 | 0.0021641 | -0.098675 | -0.018551 | 0.0019654 | 0.11902 | 0.10529 | 0.12817 | 0.091553 | 0.10071 | 0.027466 | -0.11902 | 0.068665 | 0.20142 | 0.064087 | 0.036621 | 0.022888 | -0.032043 | -0.086975 | 122.8409 | 122.6944 | -0.018311 | 122.9187 | 122.905 | 0.21057 | 0 | 122.7814 | 122.7264 | -0.082398 | 122.8821 | 122.8775 | 0.15106 | -0.096131 | 122.9141 | 122.9324 | 122.9416 | -0.23804 | 122.85 | 122.8363 | 123.0148 | -0.20599
4199.1719 | 123.0927 | -122.8317 | 0.10986 | 0.0074006 | -0.015597 | 0.016346 | 0.034741 | -0.029728 | -0.032742 | -0.01157 | 7.627e-05 | 0.0083804 | 0.0023777 | -0.095898 | -0.010433 | -0.00059818 | 0.082397 | -0.013733 | 0.004578 | 0.045776 | 0.11444 | 0.018311 | -0.13733 | -0.032043 | 0.032043 | -0.09613 | 0.064087 | 0.082397 | -0.045776 | -0.11902 | 122.85 | 122.6944 | 0.004578 | 122.818 | 122.8775 | 0.18311 | -0.027466 | 122.7859 | 122.7127 | -0.045776 | 122.7997 | 122.7356 | 0.022889 | -0.027466 | 122.9462 | 122.9141 | 122.8363 | -0.24719 | 122.8958 | 122.9141 | 122.8638 | -0.22888
4200.9062 | 123.0515 | -122.8592 | 0.10529 | 0.0074006 | -0.022433 | 0.017415 | 0.036023 | -0.031223 | -0.043637 | -0.01392 | 7.627e-05 | 0.0017582 | -0.00039949 | -0.095043 | -0.01791 | 0.0030334 | 0.09613 | 0.073242 | 0.10529 | 0.068665 | 0.10986 | 0.027466 | -0.11444 | 0.064087 | 0.16479 | 0.059509 | 0.064087 | 0.045776 | -0.045776 | -0.091553 | 122.8867 | 122.7448 | 0.004577 | 122.9324 | 122.9279 | 0.18311 | -0.009156 | 122.8134 | 122.7676 | -0.041199 | 122.9233 | 122.9187 | 0.15106 | -0.05951 | 122.9691 | 122.9553 | 122.9645 | -0.21973 | 122.9233 | 122.905 | 123.024 | -0.19684
4202.7031 | 123.0286 | -122.8775 | 0.10529 | -0.00022891 | -0.023287 | 0.01891 | 0.034741 | -0.025455 | -0.037014 | -0.014347 | -0.0075532 | 0.0034672 | -0.00061309 | -0.094402 | -0.015133 | 0.0011108 | 0.10529 | 0.073242 | 0.10529 | 0.091553 | 0.082397 | 0.032043 | -0.1236 | 0.059509 | 0.1236 | 0.018311 | 0.054932 | 0.032043 | -0.018311 | -0.10529 | 122.9095 | 122.7539 | -0.022889 | 122.9507 | 122.9691 | 0.21515 | 0 | 122.8592 | 122.7722 | -0.050354 | 122.937 | 122.8958 | 0.1236 | -0.073243 | 122.9599 | 122.9828 | 122.9828 | -0.22888 | 122.9324 | 122.9095 | 123.0011 | -0.21057
4204.5 | 123.0927 | -122.8638 | 0.10529 | -0.00022891 | -0.016451 | 0.014637 | 0.034528 | -0.029087 | -0.032315 | -0.013279 | -0.015182 | 0.0096622 | 0.0021641 | -0.095257 | -0.011288 | 4.2822e-05 | 0.050354 | -0.059509 | -0.018311 | 0.018311 | 0.15106 | 0.004578 | -0.12817 | -0.073242 | 0 | -0.11444 | 0.082397 | 0.054932 | -0.054932 | -0.12817 | 122.8683 | 122.7356 | 0.045776 | 122.8043 | 122.8821 | 0.14649 | -0.054932 | 122.8088 | 122.7356 | -0.022889 | 122.7905 | 122.7493 | 0.013733 | -0.050354 | 123.0148 | 122.9141 | 122.8455 | -0.23346 | 122.9462 | 122.9187 | 122.8638 | -0.23346
4206.2344 | 123.024 | -122.8867 | 0.1236 | -0.00022891 | -0.020083 | 0.01656 | 0.036023 | -0.030582 | -0.039578 | -0.01456 | 0.0077058 | 0.00090363 | 2.7914e-05 | -0.095257 | -0.016415 | 0.0036744 | 0.064087 | 0.027466 | 0.07782 | 0.050354 | 0.1236 | 0.032043 | -0.10529 | 0.009155 | 0.09613 | 0.022888 | 0.054932 | 0.064087 | -0.032043 | -0.09613 | 122.9187 | 122.7814 | 0 | 122.9141 | 122.937 | 0.15564 | -0.059509 | 122.8546 | 122.7905 | -0.068664 | 122.8958 | 122.9095 | 0.11902 | -0.059509 | 123.0103 | 122.9507 | 122.9645 | -0.22888 | 122.9416 | 122.9507 | 122.9828 | -0.21973
4208.0312 | 123.0286 | -122.8683 | 0.14191 | -0.00022891 | -0.020296 | 0.018696 | 0.037518 | -0.0293 | -0.039364 | -0.013065 | -0.0075532 | 0.0032534 | -0.00061309 | -0.096538 | -0.017269 | 0.0019654 | 0.082397 | 0.022888 | 0.073242 | 0.054932 | 0.082397 | 0.018311 | -0.10986 | 0.013733 | 0.091553 | 0.018311 | 0.054932 | 0.045776 | -0.027466 | -0.09613 | 122.8867 | 122.7585 | -0.05951 | 122.8912 | 122.9233 | 0.16479 | -0.05951 | 122.8409 | 122.7722 | -0.086975 | 122.8821 | 122.8867 | 0.11444 | -0.096131 | 122.9507 | 122.9507 | 122.9416 | -0.25177 | 122.9233 | 122.9141 | 122.9599 | -0.23804
4209.8438 | 123.056 | -122.8683 | 0.10529 | -0.00022891 | -0.011751 | 0.018483 | 0.039014 | -0.028446 | -0.03616 | -0.014988 | -0.015182 | 0.0066714 | 0.0034457 | -0.095898 | -0.01321 | -0.00059818 | 0.036621 | -0.045776 | -0.018311 | 0.009155 | 0.1236 | -0.018311 | -0.15106 | -0.059509 | 0.045776 | -0.09613 | 0.10529 | 0.059509 | -0.07782 | -0.14191 | 122.85 | 122.7173 | 0.01831 | 122.8226 | 122.8775 | 0.16022 | -0.068665 | 122.7905 | 122.7264 | 0 | 122.8088 | 122.7722 | 0.045777 | -0.045777 | 122.9919 | 122.905 | 122.85 | -0.25635 | 122.9736 | 122.9279 | 122.9141 | -0.24719
4211.5781 | 123.0698 | -122.8592 | 0.12817 | -0.00022891 | -0.020296 | 0.018055 | 0.035596 | -0.027378 | -0.040646 | -0.015415 | 7.627e-05 | 0.0015446 | -0.00018589 | -0.096325 | -0.018551 | 0.0015382 | 0.050354 | 0.027466 | 0.082397 | 0.054932 | 0.11444 | 0.050354 | -0.10529 | 0.022888 | 0.10529 | 0.032043 | 0.064087 | 0.045776 | -0.032043 | -0.10071 | 122.9095 | 122.7539 | -0.013733 | 122.8867 | 122.9141 | 0.16022 | -0.07782 | 122.8271 | 122.7585 | -0.064087 | 122.8821 | 122.8912 | 0.13275 | -0.082398 | 122.9736 | 122.9095 | 122.9416 | -0.23346 | 122.9233 | 122.905 | 122.9645 | -0.22888
4213.3594 | 123.0469 | -122.8683 | 0.13733 | -0.00022891 | -0.021151 | 0.014637 | 0.037732 | -0.0293 | -0.039151 | -0.014347 | 7.627e-05 | 0.0036808 | -0.0025357 | -0.096111 | -0.01556 | 0.0019654 | 0.064087 | 0.032043 | 0.082397 | 0.054932 | 0.10071 | 0.032043 | -0.10986 | 0.009155 | 0.10986 | 0.013733 | 0.045776 | 0.059509 | -0.036621 | -0.10529 | 122.9004 | 122.7585 | -0.036621 | 122.9004 | 122.9233 | 0.16479 | -0.073242 | 122.8317 | 122.7631 | -0.091553 | 122.8775 | 122.8821 | 0.11902 | -0.07782 | 122.9691 | 122.9324 | 122.9507 | -0.24719 | 122.9141 | 122.9279 | 122.9782 | -0.24262
4215.1562 | 123.0469 | -122.8958 | 0.11444 | -0.015487 | -0.02051 | 0.019551 | 0.036237 | -0.026523 | -0.040005 | -0.01392 | -0.0075532 | 0.004108 | 0.00066871 | -0.096966 | -0.015133 | 0.0026062 | 0.054932 | 0.018311 | 0.068665 | 0.045776 | 0.11902 | 0.036621 | -0.10071 | 0.022888 | 0.10071 | 0.032043 | 0.050354 | 0.036621 | -0.041199 | -0.10986 | 122.9324 | 122.7951 | 0.004578 | 122.9141 | 122.9416 | 0.14648 | -0.059509 | 122.8546 | 122.7859 | -0.064087 | 122.9187 | 122.9279 | 0.14191 | -0.07782 | 123.0148 | 122.9507 | 122.9645 | -0.21515 | 122.9462 | 122.9324 | 122.9965 | -0.2243
4216.9531 | 123.024 | -122.8912 | 0.13275 | -0.015487 | -0.017519 | 0.016346 | 0.034741 | -0.029087 | -0.037869 | -0.013492 | 0.0077058 | 0.0062442 | 0.00045511 | -0.096538 | -0.01556 | -0.00017078 | 0.12817 | 0.10071 | 0.11444 | 0.07782 | 0.091553 | 0.050354 | -0.10071 | 0.073242 | 0.11902 | 0.027466 | 0.059509 | 0.032043 | -0.022888 | -0.09613 | 122.9416 | 122.7905 | -0.041198 | 122.9919 | 122.9691 | 0.17853 | -0.004577 | 122.8683 | 122.7951 | -0.073242 | 122.9645 | 122.9187 | 0.1236 | -0.10071 | 122.9828 | 123.0194 | 123.0057 | -0.23346 | 122.9507 | 122.9233 | 123.0103 | -0.22888
4218.75 | 123.1338 | -122.8317 | 0.082397 | -0.0078584 | -0.01581 | 0.015706 | 0.037518 | -0.028873 | -0.032315 | -0.012638 | 7.627e-05 | 0.0096622 | 0.0025913 | -0.092266 | -0.012142 | -0.00038438 | 0.11444 | 0.032043 | 0.032043 | 0.054932 | 0.14648 | 0.013733 | -0.13275 | 0.022888 | 0.082397 | -0.050354 | 0.086975 | 0.054932 | -0.045776 | -0.10529 | 122.8455 | 122.699 | 0.064087 | 122.8638 | 122.8867 | 0.18768 | 0.032044 | 122.7859 | 122.7264 | 0.004578 | 122.8546 | 122.7814 | 0.054932 | -0.027465 | 122.9782 | 122.9462 | 122.8638 | -0.21515 | 122.9187 | 122.8867 | 122.9141 | -0.18768
4220.5625 | 123.143 | -122.8363 | 0.068665 | -0.0078584 | -0.016451 | 0.018696 | 0.032178 | -0.0293 | -0.03616 | -0.010502 | -0.0075532 | 0.005176 | 0.0021641 | -0.09547 | -0.012142 | 0.00025642 | 0.07782 | 0.022888 | 0.036621 | 0.059509 | 0.13733 | 0.013733 | -0.12817 | 0.009155 | 0.086975 | -0.054932 | 0.091553 | 0.054932 | -0.07782 | -0.1236 | 122.85 | 122.7081 | 0.068664 | 122.8592 | 122.8958 | 0.18768 | 0.009155 | 122.7585 | 122.7127 | 0.022888 | 122.8455 | 122.7814 | 0.068664 | -0.013733 | 122.9736 | 122.9141 | 122.8729 | -0.19684 | 122.9279 | 122.8912 | 122.9233 | -0.19226
4222.2969 | 123.0286 | -122.8912 | 0.1236 | 0.0074006 | -0.022433 | 0.01656 | 0.036237 | -0.02866 | -0.041714 | -0.012211 | 0.0077058 | 0.0030398 | -0.00061309 | -0.094189 | -0.015133 | 0.0034608 | 0.10071 | 0.086975 | 0.11444 | 0.068665 | 0.086975 | 0.045776 | -0.073242 | 0.059509 | 0.12817 | 0.027466 | 0.045776 | 0.050354 | -0.027466 | -0.086975 | 122.937 | 122.818 | -0.036621 | 122.9782 | 122.9599 | 0.14191 | -0.022888 | 122.8638 | 122.8043 | -0.07782 | 122.9507 | 122.9187 | 0.11444 | -0.073242 | 122.9782 | 122.9919 | 123.0057 | -0.19684 | 122.937 | 122.9416 | 123.0194 | -0.21057
4224.0625 | 123.1155 | -122.8546 | 0.10529 | -0.00022891 | -0.010897 | 0.015065 | 0.036878 | -0.029514 | -0.034237 | -0.010502 | 0.0077058 | 0.0070988 | 0.0019505 | -0.096111 | -0.01321 | 4.2822e-05 | 0.022888 | -0.068665 | -0.027466 | 0.009155 | 0.16022 | 0.018311 | -0.12817 | -0.041199 | -0.009155 | -0.10529 | 0.10986 | 0.068665 | -0.064087 | -0.13733 | 122.8729 | 122.7264 | 0.054931 | 122.7859 | 122.8638 | 0.13733 | -0.082398 | 122.7905 | 122.7173 | 0.004577 | 122.8134 | 122.7493 | 0.032043 | -0.036621 | 123.0148 | 122.8775 | 122.8271 | -0.23346 | 122.9645 | 122.9233 | 122.8455 | -0.24262
4225.8125 | 123.024 | -122.8821 | 0.11902 | -0.0078584 | -0.024782 | 0.016987 | 0.034955 | -0.0293 | -0.041501 | -0.013065 | 7.627e-05 | 0.0034672 | -0.0012539 | -0.09547 | -0.016201 | 0.0030334 | 0.082397 | 0.054932 | 0.07782 | 0.064087 | 0.10986 | 0.045776 | -0.11444 | 0.018311 | 0.10529 | 0.027466 | 0.045776 | 0.045776 | -0.018311 | -0.086975 | 122.9279 | 122.7676 | -0.009156 | 122.937 | 122.9462 | 0.17853 | -0.036622 | 122.8638 | 122.7951 | -0.073243 | 122.9004 | 122.9095 | 0.11444 | -0.073243 | 122.9919 | 122.9645 | 122.9599 | -0.23346 | 122.9279 | 122.9279 | 122.9874 | -0.20599
4227.6094 | 123.0057 | -122.9095 | 0.11444 | -0.00022891 | -0.018374 | 0.01656 | 0.038587 | -0.028232 | -0.038937 | -0.013065 | 7.627e-05 | 0.0047488 | 2.7914e-05 | -0.095043 | -0.017697 | 0.00025642 | 0.09613 | 0.07782 | 0.10529 | 0.091553 | 0.10529 | 0.018311 | -0.09613 | -0.004578 | 0.10986 | 0.004578 | 0.054932 | 0.068665 | -0.045776 | -0.11444 | 122.9279 | 122.8134 | -0.009155 | 122.9874 | 123.0011 | 0.18768 | -0.018311 | 122.8638 | 122.7951 | -0.059509 | 122.905 | 122.9141 | 0.11902 | -0.045776 | 123.0148 | 123.0057 | 123.0148 | -0.21057 | 122.9645 | 122.9782 | 123.0194 | -0.22888
4229.3438 | 123.0148 | -122.8912 | 0.12817 | -0.015487 | -0.020724 | 0.016774 | 0.034741 | -0.027805 | -0.041501 | -0.013279 | 7.627e-05 | 0.0053898 | 0.0013095 | -0.093548 | -0.016628 | 0.0011108 | 0.10529 | 0.036621 | 0.091553 | 0.059509 | 0.10529 | 0.050354 | -0.10071 | 0.032043 | 0.10071 | 0.022888 | 0.059509 | 0.045776 | -0.036621 | -0.09613 | 122.9416 | 122.7905 | -0.022888 | 122.9279 | 122.9507 | 0.16022 | -0.022888 | 122.8546 | 122.7951 | -0.068665 | 122.9233 | 122.9141 | 0.11902 | -0.082398 | 122.9965 | 122.9965 | 122.9828 | -0.22888 | 122.9507 | 122.937 | 122.9919 | -0.2243
4231.125 | 123.1476 | -122.8455 | 0.11444 | -0.00022891 | -0.02051 | 0.015492 | 0.032819 | -0.02631 | -0.037228 | -0.014347 | -0.015182 | 0.0073124 | 0.00045511 | -0.093761 | -0.011929 | -0.0010254 | 0.16022 | 0.059509 | 0.10071 | 0.10986 | 0.10529 | 0.050354 | -0.082397 | 0.073242 | 0.13733 | 0.041199 | 0.045776 | 0.022888 | -0.013733 | -0.064087 | 122.8958 | 122.7631 | -0.009155 | 122.905 | 122.9553 | 0.19226 | 0.045776 | 122.8317 | 122.7814 | -0.068665 | 122.9187 | 122.8867 | 0.10529 | -0.091553 | 122.9507 | 123.0057 | 122.9462 | -0.19684 | 122.8912 | 122.8683 | 122.9828 | -0.17853
4232.9219 | 123.143 | -122.8363 | 0.082397 | 0.0074006 | -0.01581 | 0.013997 | 0.038159 | -0.0293 | -0.034451 | -0.012424 | 7.627e-05 | 0.0079532 | -0.00061309 | -0.095684 | -0.014065 | -0.001239 | 0.07782 | -0.045776 | -0.004578 | 0.036621 | 0.13733 | 0.022888 | -0.13733 | -0.027466 | 0.073242 | -0.054932 | 0.091553 | 0.082397 | -0.050354 | -0.13275 | 122.8592 | 122.699 | 0.054932 | 122.7905 | 122.8729 | 0.17395 | -0.004577 | 122.7859 | 122.7036 | 0.009156 | 122.8088 | 122.7814 | 0.077819 | 0 | 122.9736 | 122.9141 | 122.8317 | -0.21973 | 122.9279 | 122.9187 | 122.9095 | -0.21515
4234.7031 | 123.0972 | -122.8455 | 0.09613 | 0.0074006 | -0.017092 | 0.01656 | 0.032819 | -0.027378 | -0.034878 | -0.011356 | 0.0077058 | 0.0098758 | 0.0019505 | -0.092693 | -0.010433 | -0.00059818 | 0.12817 | 0.013733 | 0.018311 | 0.032043 | 0.14191 | 0 | -0.14648 | -0.009155 | 0.07782 | -0.068665 | 0.068665 | 0.07782 | -0.050354 | -0.10986 | 122.8455 | 122.699 | 0.045777 | 122.8592 | 122.8775 | 0.17853 | 0.032044 | 122.7951 | 122.7356 | -0.027465 | 122.8363 | 122.7768 | 0.041198 | -0.01831 | 122.9874 | 122.9736 | 122.8638 | -0.24261 | 122.9141 | 122.9233 | 122.9233 | -0.20599
4236.5 | 123.0286 | -122.8958 | 0.13275 | -0.00022891 | -0.023073 | 0.015706 | 0.034528 | -0.029941 | -0.042569 | -0.014347 | 0.0077058 | 0.0015446 | 0.0013095 | -0.095684 | -0.016842 | 0.0026062 | 0.09613 | 0.064087 | 0.09613 | 0.050354 | 0.10071 | 0.022888 | -0.11444 | 0.018311 | 0.10986 | 0.018311 | 0.050354 | 0.050354 | -0.036621 | -0.091553 | 122.9187 | 122.7814 | -0.032043 | 122.9599 | 122.9462 | 0.16479 | -0.036621 | 122.8592 | 122.8043 | -0.082397 | 122.9141 | 122.9141 | 0.10986 | -0.082397 | 122.9965 | 122.9919 | 122.9919 | -0.24719 | 122.9462 | 122.9462 | 123.0057 | -0.2243
4238.2969 | 123.0377 | -122.8729 | 0.10986 | -0.00022891 | -0.01816 | 0.017201 | 0.039227 | -0.0293 | -0.039364 | -0.01157 | 7.627e-05 | 0.005176 | 0.0032321 | -0.094829 | -0.015133 | 0.00068362 | 0.036621 | -0.032043 | 0.013733 | 0.009155 | 0.15564 | -0.009155 | -0.12817 | -0.059509 | 0.050354 | -0.059509 | 0.086975 | 0.068665 | -0.07782 | -0.12817 | 122.8638 | 122.7448 | 0.045777 | 122.8409 | 122.8821 | 0.13733 | -0.073242 | 122.7951 | 122.7448 | -0.022888 | 122.8134 | 122.8134 | 0.068665 | -0.041198 | 123.0286 | 122.9095 | 122.8867 | -0.23804 | 122.9599 | 122.9416 | 122.9233 | -0.23804
4240.0312 | 123.0423 | -122.8775 | 0.12817 | -0.0078584 | -0.016878 | 0.019978 | 0.037946 | -0.028019 | -0.037442 | -0.015629 | 7.627e-05 | 0.005817 | 0.0023777 | -0.095684 | -0.016415 | 4.2822e-05 | 0.045776 | -0.022888 | 0.004578 | 0.004578 | 0.13733 | 0 | -0.14191 | -0.068665 | 0.045776 | -0.073242 | 0.09613 | 0.086975 | -0.07782 | -0.12817 | 122.8775 | 122.7356 | 0.009155 | 122.8546 | 122.8821 | 0.14649 | -0.082398 | 122.7997 | 122.7493 | -0.032044 | 122.8088 | 122.8043 | 0.054932 | -0.041199 | 123.0148 | 122.9233 | 122.8821 | -0.27008 | 122.9736 | 122.9645 | 122.9233 | -0.25635
4241.8281 | 123.0835 | -122.8958 | 0.1236 | -0.015487 | -0.022433 | 0.016987 | 0.037946 | -0.028446 | -0.041928 | -0.013706 | -0.0075532 | 0.0021854 | 0.00066871 | -0.098247 | -0.016842 | 0.0011108 | 0.036621 | 0.032043 | 0.082397 | 0.054932 | 0.11902 | 0.032043 | -0.10986 | 0.018311 | 0.11444 | 0.032043 | 0.050354 | 0.045776 | -0.018311 | -0.11444 | 122.9279 | 122.7859 | -0.004577 | 122.9279 | 122.9507 | 0.16479 | -0.086975 | 122.8775 | 122.7814 | -0.073242 | 122.9141 | 122.9279 | 0.14648 | -0.07782 | 123.0148 | 122.9324 | 122.9782 | -0.23346 | 122.9462 | 122.9416 | 123.0103 | -0.23804
4243.625 | 123.1201 | -122.85 | 0.09613 | 0.0074006 | -0.016451 | 0.014424 | 0.037518 | -0.029514 | -0.032742 | -0.013706 | 0.0077058 | 0.0070988 | 0.0019505 | -0.094402 | -0.012783 | -0.00081178 | 0.12817 | 0.018311 | 0.041199 | 0.050354 | 0.13275 | -0.009155 | -0.11444 | 0.018311 | 0.086975 | -0.054932 | 0.09613 | 0.054932 | -0.050354 | -0.12817 | 122.8409 | 122.7356 | 0.036621 | 122.8683 | 122.9004 | 0.16479 | 0.032044 | 122.7997 | 122.7219 | 0 | 122.8683 | 122.7951 | 0.073242 | -0.041198 | 122.9828 | 122.9782 | 122.8912 | -0.21057 | 122.9462 | 122.905 | 122.937 | -0.2243
4245.4375 | 123.1064 | -122.8271 | 0.091553 | -0.00022891 | -0.016665 | 0.015919 | 0.036878 | -0.031223 | -0.034024 | -0.012851 | 0.0077058 | 0.0066714 | 0.00066871 | -0.090984 | -0.014706 | 0.0017518 | 0.11444 | 0 | 0.022888 | 0.045776 | 0.1236 | 0.027466 | -0.11444 | -0.004578 | 0.068665 | -0.082397 | 0.073242 | 0.064087 | -0.050354 | -0.13275 | 122.8546 | 122.7127 | 0.032043 | 122.8271 | 122.8729 | 0.16022 | 0.022888 | 122.7768 | 122.6944 | -0.018311 | 122.8226 | 122.7448 | 0.050354 | -0.027466 | 122.9507 | 122.9416 | 122.85 | -0.20599 | 122.9004 | 122.8912 | 122.8958 | -0.2243
4247.2344 | 123.1567 | -122.8271 | 0.091553 | -0.0078584 | -0.016238 | 0.015278 | 0.035169 | -0.0293 | -0.035092 | -0.01157 | 0.0077058 | 0.005176 | 0.00024151 | -0.095257 | -0.012997 | -0.0010254 | 0.073242 | 0.004578 | 0.032043 | 0.064087 | 0.13733 | 0 | -0.14191 | -0.022888 | 0.086975 | -0.036621 | 0.086975 | 0.082397 | -0.045776 | -0.13733 | 122.8271 | 122.6852 | 0.045776 | 122.8317 | 122.8912 | 0.20599 | -0.018311 | 122.7814 | 122.6898 | -0.004578 | 122.8043 | 122.7905 | 0.10071 | -0.009156 | 122.9645 | 122.9004 | 122.8592 | -0.23346 | 122.9141 | 122.9095 | 122.9141 | -0.22888
4248.9688 | 123.0972 | -122.8683 | 0.10986 | 0.0074006 | -0.02051 | 0.016774 | 0.03346 | -0.028446 | -0.039792 | -0.012211 | -0.0075532 | 0.00090363 | -0.0010403 | -0.095043 | -0.014065 | 0.0019654 | 0.13275 | 0.082397 | 0.12817 | 0.09613 | 0.091553 | 0.059509 | -0.086975 | 0.068665 | 0.15106 | 0.054932 | 0.032043 | 0.032043 | -0.022888 | -0.082397 | 122.9279 | 122.7814 | -0.01831 | 122.9507 | 122.9645 | 0.1831 | 0.022888 | 122.8455 | 122.7859 | -0.07782 | 122.937 | 122.9233 | 0.13733 | -0.07782 | 122.9599 | 123.0011 | 122.9965 | -0.19684 | 122.9004 | 122.9004 | 123.0194 | -0.19226
4250.7656 | 123.0423 | -122.905 | 0.12817 | 0.0074006 | -0.022433 | 0.016346 | 0.037091 | -0.027591 | -0.043423 | -0.012211 | 7.627e-05 | 0.0017582 | 0.0030185 | -0.096966 | -0.016415 | 0.0013244 | 0.086975 | 0.036621 | 0.086975 | 0.045776 | 0.09613 | 0.032043 | -0.10529 | 0.018311 | 0.10071 | 0.022888 | 0.050354 | 0.036621 | -0.036621 | -0.091553 | 122.937 | 122.7997 | -0.032044 | 122.9416 | 122.9507 | 0.15106 | -0.041199 | 122.8683 | 122.8134 | -0.07782 | 122.9233 | 122.9279 | 0.11444 | -0.091553 | 123.0011 | 122.9919 | 122.9919 | -0.23346 | 122.9553 | 122.9416 | 123.0057 | -0.21973
4252.5 | 123.1705 | -122.8546 | 0.07782 | -0.00022891 | -0.015597 | 0.015492 | 0.035596 | -0.030369 | -0.034451 | -0.014774 | 7.627e-05 | 0.0060306 | 0.00045511 | -0.095043 | -0.012356 | 0.0013244 | 0.045776 | -0.045776 | -0.013733 | 0.013733 | 0.14191 | 0 | -0.12817 | -0.018311 | 0.022888 | -0.064087 | 0.082397 | 0.068665 | -0.036621 | -0.12817 | 122.8546 | 122.7264 | 0.064087 | 122.8088 | 122.8683 | 0.14191 | -0.032044 | 122.818 | 122.7264 | 0.004577 | 122.8363 | 122.7905 | 0.064087 | -0.009155 | 122.9965 | 122.9004 | 122.8409 | -0.20599 | 122.937 | 122.9233 | 122.8775 | -0.20599
4254.2812 | 123.0972 | -122.8683 | 0.10071 | -0.0078584 | -0.024355 | 0.017842 | 0.034101 | -0.030582 | -0.04321 | -0.01691 | -0.0075532 | 0.0028262 | -0.00061309 | -0.095898 | -0.017056 | 0.002179 | 0.10071 | 0.082397 | 0.11902 | 0.082397 | 0.10986 | 0.036621 | -0.10529 | 0.050354 | 0.17853 | 0.073242 | 0.050354 | 0.036621 | -0.027466 | -0.091553 | 122.905 | 122.7631 | 0.009155 | 122.9507 | 122.9507 | 0.18768 | 0 | 122.8409 | 122.7768 | -0.050354 | 122.9187 | 122.9416 | 0.16479 | -0.064087 | 122.9782 | 122.9691 | 122.9874 | -0.20599 | 122.9187 | 122.905 | 123.0469 | -0.19226
4256.0156 | 123.0972 | -122.8775 | 0.11902 | 0.0074006 | -0.02051 | 0.019123 | 0.038587 | -0.027805 | -0.042996 | -0.015201 | -0.0075532 | 0.0011172 | 0.0013095 | -0.094829 | -0.018551 | 0.00068362 | 0.12817 | 0.091553 | 0.12817 | 0.073242 | 0.10986 | 0.036621 | -0.10071 | 0.091553 | 0.19226 | 0.07782 | 0.059509 | 0.032043 | -0.022888 | -0.086975 | 122.9141 | 122.7768 | -0.009156 | 122.9691 | 122.9507 | 0.17395 | 0.009155 | 122.8546 | 122.7905 | -0.05951 | 122.9691 | 122.9553 | 0.16479 | -0.086976 | 122.9874 | 123.0057 | 123.0057 | -0.21973 | 122.937 | 122.9095 | 123.0698 | -0.20599
4257.8281 | 123.0789 | -122.905 | 0.10071 | -0.015487 | -0.01816 | 0.015492 | 0.035596 | -0.026737 | -0.035733 | -0.011783 | -0.015182 | 0.0036808 | 0.00024151 | -0.096111 | -0.014279 | -0.0016662 | 0.14648 | 0.086975 | 0.13275 | 0.073242 | 0.091553 | 0.050354 | -0.082397 | 0.07782 | 0.1236 | 0.059509 | 0.045776 | 0.036621 | -0.022888 | -0.091553 | 122.9553 | 122.8226 | -0.009155 | 122.9919 | 122.9782 | 0.15564 | 0.045776 | 122.8821 | 122.8134 | -0.054932 | 122.9828 | 122.9645 | 0.15106 | -0.064087 | 122.9965 | 123.0515 | 123.0377 | -0.18311 | 122.9507 | 122.9416 | 123.0286 | -0.19226
4259.5625 | 123.1155 | -122.8683 | 0.10071 | -0.015487 | -0.015597 | 0.014637 | 0.033673 | -0.029728 | -0.031033 | -0.011142 | -0.015182 | 0.0060306 | 0.0047275 | -0.094402 | -0.0095788 | 0.00025642 | 0.068665 | -0.018311 | 0 | 0.027466 | 0.13733 | 0.013733 | -0.12817 | -0.041199 | 0.022888 | -0.086975 | 0.086975 | 0.07782 | -0.054932 | -0.10986 | 122.8821 | 122.7402 | 0.036621 | 122.85 | 122.8958 | 0.15564 | -0.032043 | 122.8134 | 122.7585 | -0.013733 | 122.8271 | 122.7814 | 0.022888 | -0.022888 | 123.0057 | 122.937 | 122.8683 | -0.22888 | 122.9553 | 122.9462 | 122.8912 | -0.21057
4261.3438 | 123.1293 | -122.8683 | 0.091553 | -0.015487 | -0.017306 | 0.015065 | 0.034528 | -0.030369 | -0.034451 | -0.010288 | 7.627e-05 | 0.005817 | 0.0040867 | -0.091198 | -0.014706 | -0.0025208 | 0.027466 | -0.086975 | -0.041199 | 0.009155 | 0.14648 | 0.018311 | -0.12817 | -0.045776 | -0.004578 | -0.11444 | 0.064087 | 0.07782 | -0.050354 | -0.1236 | 122.8867 | 122.7402 | 0.054931 | 122.7814 | 122.8775 | 0.13733 | -0.064087 | 122.818 | 122.7448 | -0.027466 | 122.8226 | 122.7539 | 0.009155 | -0.013733 | 123.0148 | 122.8958 | 122.8271 | -0.21973 | 122.9324 | 122.9462 | 122.8638 | -0.21515
4263.125 | 123.1476 | -122.8546 | 0.086975 | -0.00022891 | -0.014315 | 0.015919 | 0.037732 | -0.029514 | -0.035305 | -0.012211 | 0.0077058 | 0.0064578 | 0.0025913 | -0.092907 | -0.010861 | 0.00047002 | 0.022888 | -0.082397 | -0.009155 | 0.013733 | 0.13275 | 0.004578 | -0.14648 | -0.050354 | -0.027466 | -0.086975 | 0.086975 | 0.082397 | -0.068665 | -0.13275 | 122.8592 | 122.7081 | 0.045776 | 122.7722 | 122.8683 | 0.16022 | -0.064087 | 122.7859 | 122.7219 | 0 | 122.8043 | 122.7676 | 0.045776 | -0.004578 | 122.9874 | 122.8775 | 122.8455 | -0.23346 | 122.9416 | 122.937 | 122.8271 | -0.21973
4264.8594 | 123.1888 | -122.8729 | 0.082397 | -0.00022891 | -0.017519 | 0.016774 | 0.036023 | -0.027591 | -0.036374 | -0.011997 | 7.627e-05 | 0.0056034 | 0.00045511 | -0.093334 | -0.014065 | 0.0013244 | 0.041199 | -0.041199 | 0.004578 | 0.018311 | 0.14191 | 0.009155 | -0.13733 | -0.004578 | 0.027466 | -0.041199 | 0.082397 | 0.073242 | -0.054932 | -0.09613 | 122.8821 | 122.7356 | 0.05951 | 122.8317 | 122.8912 | 0.15564 | -0.041198 | 122.818 | 122.7768 | 0 | 122.8683 | 122.8317 | 0.054931 | -0.009155 | 123.0148 | 122.9141 | 122.8775 | -0.21973 | 122.9553 | 122.9462 | 122.9004 | -0.17853
4266.6562 | 123.0881 | -122.8592 | 0.10529 | -0.00022891 | -0.022433 | 0.01656 | 0.041364 | -0.030155 | -0.043637 | -0.01456 | 0.0077058 | 0.0017582 | 0.0019505 | -0.094402 | -0.018337 | 0.0015382 | 0.10986 | 0.073242 | 0.1236 | 0.073242 | 0.10071 | 0.036621 | -0.10529 | 0.073242 | 0.16937 | 0.082397 | 0.036621 | 0.059509 | 0.004578 | -0.086975 | 122.8958 | 122.7539 | -0.004578 | 122.9324 | 122.9324 | 0.17853 | 0.004577 | 122.8638 | 122.7722 | -0.068665 | 122.9324 | 122.9416 | 0.16937 | -0.045777 | 122.9599 | 122.9691 | 122.9828 | -0.21057 | 122.8958 | 122.9187 | 123.0286 | -0.19226
4268.4531 | 123.0698 | -122.9004 | 0.1236 | -0.0078584 | -0.022005 | 0.016987 | 0.030683 | -0.027164 | -0.039151 | -0.011997 | 0.0077058 | 0.0030398 | -0.00039949 | -0.097393 | -0.012783 | 0.0011108 | 0.10529 | 0.10071 | 0.12817 | 0.064087 | 0.082397 | 0.032043 | -0.086975 | 0.064087 | 0.14191 | 0.054932 | 0.054932 | 0.027466 | -0.022888 | -0.082397 | 122.9324 | 122.8134 | -0.041199 | 123.0011 | 122.9645 | 0.15106 | -0.01831 | 122.8775 | 122.818 | -0.068664 | 122.9645 | 122.9553 | 0.13733 | -0.09613 | 122.9828 | 123.0057 | 123.0286 | -0.21057 | 122.9553 | 122.9279 | 123.0423 | -0.20599
4270.1719 | 123.0743 | -122.8958 | 0.11444 | -0.00022891 | -0.023928 | 0.019978 | 0.033673 | -0.027805 | -0.042782 | -0.013279 | 7.627e-05 | 0.0026126 | -0.00082669 | -0.097393 | -0.014919 | 0.00068362 | 0.14648 | 0.11902 | 0.1236 | 0.10529 | 0.09613 | 0.041199 | -0.091553 | 0.059509 | 0.17853 | 0.082397 | 0.045776 | 0.036621 | -0.032043 | -0.07782 | 122.937 | 122.8043 | -0.018311 | 123.0148 | 123.0011 | 0.19684 | 0.032043 | 122.8638 | 122.818 | -0.068665 | 122.9553 | 122.9782 | 0.16022 | -0.07782 | 122.9919 | 123.0423 | 123.0194 | -0.20599 | 122.9416 | 122.9324 | 123.0743 | -0.19226
4271.9688 | 123.0927 | -122.8775 | 0.10529 | -0.015487 | -0.017306 | 0.019764 | 0.037091 | -0.02866 | -0.035733 | -0.014774 | -0.0075532 | 0.005176 | 0.0023777 | -0.097179 | -0.015774 | -0.0020934 | 0.045776 | -0.045776 | -0.022888 | 0.013733 | 0.16022 | 0.004578 | -0.16022 | -0.054932 | 0.045776 | -0.082397 | 0.10071 | 0.091553 | -0.068665 | -0.13275 | 122.8821 | 122.7173 | 0.054931 | 122.8317 | 122.8912 | 0.17395 | -0.05951 | 122.8088 | 122.7448 | -0.004578 | 122.8226 | 122.7951 | 0.050354 | -0.013733 | 123.0377 | 122.9233 | 122.8546 | -0.2655 | 122.9782 | 122.9691 | 122.9233 | -0.23804
4273.7031 | 123.0423 | -122.905 | 0.11902 | -0.0078584 | -0.024569 | 0.017415 | 0.036023 | -0.032078 | -0.037442 | -0.013279 | 7.627e-05 | 0.0034672 | 2.7914e-05 | -0.094402 | -0.018337 | 4.2822e-05 | 0.11902 | 0.045776 | 0.091553 | 0.059509 | 0.082397 | 0.032043 | -0.086975 | 0.036621 | 0.10986 | 0.013733 | 0.054932 | 0.050354 | -0.027466 | -0.091553 | 122.937 | 122.818 | -0.036622 | 122.9507 | 122.9645 | 0.14648 | 0 | 122.8775 | 122.8134 | -0.064087 | 122.9416 | 122.9187 | 0.10529 | -0.068665 | 122.9874 | 123.024 | 122.9965 | -0.20599 | 122.9599 | 122.9553 | 123.0148 | -0.21057
4275.4844 | 123.1476 | -122.8821 | 0.082397 | -0.00022891 | -0.02051 | 0.01656 | 0.036023 | -0.027164 | -0.036801 | -0.013279 | -0.015182 | 0.005176 | 0.00066871 | -0.094402 | -0.014706 | 0.00025642 | 0.15564 | 0.054932 | 0.10529 | 0.09613 | 0.1236 | 0.036621 | -0.10529 | 0.068665 | 0.13733 | 0.045776 | 0.045776 | 0.045776 | -0.032043 | -0.07782 | 122.9187 | 122.7768 | 0.041199 | 122.937 | 122.9782 | 0.20142 | 0.073243 | 122.85 | 122.8043 | -0.036621 | 122.9507 | 122.9279 | 0.1236 | -0.036621 | 123.0057 | 123.0377 | 122.9874 | -0.18768 | 122.9279 | 122.9279 | 123.0194 | -0.16022
4277.2031 | 123.1293 | -122.8912 | 0.091553 | -0.0078584 | -0.016878 | 0.016774 | 0.031964 | -0.031223 | -0.035946 | -0.01157 | -0.0075532 | 0.0028262 | -0.0012539 | -0.094402 | -0.012356 | 0.0034608 | 0.13733 | 0.086975 | 0.13275 | 0.09613 | 0.086975 | 0.054932 | -0.09613 | 0.082397 | 0.15106 | 0.041199 | 0.027466 | 0.045776 | -0.027466 | -0.082397 | 122.9462 | 122.7951 | -0.004578 | 122.9782 | 122.9874 | 0.19226 | 0.045776 | 122.8638 | 122.8088 | -0.064087 | 122.9736 | 122.9324 | 0.1236 | -0.045777 | 122.9782 | 123.0286 | 123.024 | -0.18768 | 122.9187 | 122.937 | 123.0423 | -0.17395
4279 | 123.0423 | -122.9095 | 0.1236 | -0.00022891 | -0.019015 | 0.016346 | 0.040082 | -0.026096 | -0.039578 | -0.012851 | -0.0075532 | 0.0017582 | 0.0036593 | -0.096538 | -0.016201 | 0.00089722 | 0.068665 | 0.027466 | 0.086975 | 0.054932 | 0.10986 | 0.041199 | -0.10071 | 0.009155 | 0.082397 | -0.004578 | 0.068665 | 0.041199 | -0.022888 | -0.10986 | 122.9507 | 122.8088 | -0.013733 | 122.937 | 122.9645 | 0.15564 | -0.054931 | 122.8867 | 122.7997 | -0.054931 | 122.9187 | 122.905 | 0.10529 | -0.082397 | 123.0194 | 122.9782 | 122.9965 | -0.2243 | 122.9782 | 122.9507 | 122.9919 | -0.23346
4280.75 | 123.0789 | -122.905 | 0.13275 | 0.0074006 | -0.020724 | 0.019764 | 0.034101 | -0.029087 | -0.039578 | -0.012424 | 7.627e-05 | 0.0026126 | 0.0025913 | -0.096325 | -0.012356 | 0.0013244 | 0.14191 | 0.086975 | 0.12817 | 0.09613 | 0.10071 | 0.045776 | -0.091553 | 0.082397 | 0.14648 | 0.041199 | 0.059509 | 0.032043 | -0.009155 | -0.082397 | 122.9507 | 122.8134 | -0.032043 | 122.9919 | 123.0011 | 0.18768 | 0.009156 | 122.8958 | 122.8226 | -0.073242 | 122.9874 | 122.9462 | 0.1236 | -0.10071 | 123.0057 | 123.0469 | 123.0331 | -0.2243 | 122.9645 | 122.937 | 123.0515 | -0.21515
4282.5469 | 123.0469 | -122.905 | 0.12817 | -0.00022891 | -0.020937 | 0.019123 | 0.03645 | -0.029514 | -0.040219 | -0.01456 | 7.627e-05 | 0.0013308 | 0.0040867 | -0.095684 | -0.015774 | 0.0011108 | 0.11444 | 0.073242 | 0.10986 | 0.045776 | 0.09613 | 0.041199 | -0.10529 | 0.041199 | 0.10071 | 0.004578 | 0.054932 | 0.041199 | -0.032043 | -0.082397 | 122.9462 | 122.7997 | -0.032044 | 122.9782 | 122.9507 | 0.15106 | -0.013733 | 122.8729 | 122.8226 | -0.073242 | 122.9462 | 122.9095 | 0.086975 | -0.086975 | 123.0011 | 123.0194 | 123.0148 | -0.23346 | 122.9599 | 122.9462 | 123.0057 | -0.21057
4284.3594 | 123.0469 | -122.905 | 0.10529 | 0.0074006 | -0.017946 | 0.015706 | 0.032819 | -0.028232 | -0.037228 | -0.014347 | -0.0075532 | 0.004108 | 0.0030185 | -0.095257 | -0.014065 | -0.00059818 | 0.059509 | -0.009155 | 0.018311 | 0.013733 | 0.13733 | -0.004578 | -0.14191 | -0.041199 | 0.050354 | -0.059509 | 0.086975 | 0.07782 | -0.068665 | -0.14648 | 122.9004 | 122.7631 | 0.032043 | 122.8958 | 122.9187 | 0.15564 | -0.045777 | 122.8363 | 122.7585 | -0.018311 | 122.8638 | 122.8455 | 0.086975 | -0.027466 | 123.0423 | 122.9645 | 122.9233 | -0.24719 | 122.9919 | 122.9828 | 122.9553 | -0.25177
4286.0938 | 123.1659 | -122.8775 | 0.09613 | -0.0078584 | -0.019869 | 0.016774 | 0.035809 | -0.030155 | -0.035946 | -0.01392 | 0.0077058 | 0.0047488 | 0.0034457 | -0.091839 | -0.014706 | -0.001239 | 0.14191 | 0.068665 | 0.10986 | 0.09613 | 0.09613 | 0.041199 | -0.10529 | 0.082397 | 0.12817 | 0.027466 | 0.050354 | 0.022888 | 0.004578 | -0.068665 | 122.9187 | 122.7722 | 0 | 122.9462 | 122.9736 | 0.20142 | 0.045777 | 122.8821 | 122.8088 | -0.045776 | 122.9599 | 122.905 | 0.096131 | -0.073242 | 122.9736 | 123.0194 | 122.9874 | -0.20142 | 122.9279 | 122.9004 | 123.0057 | -0.16479
4287.875 | 123.0606 | -122.9187 | 0.12817 | 0.0074006 | -0.016878 | 0.017415 | 0.039655 | -0.027805 | -0.039578 | -0.01392 | -0.0075532 | 0.0011172 | 0.0013095 | -0.095043 | -0.015988 | 0.00089722 | 0.11902 | 0.07782 | 0.13733 | 0.10529 | 0.09613 | 0.041199 | -0.11902 | 0.027466 | 0.16022 | 0.027466 | 0.050354 | 0.032043 | -0.032043 | -0.11444 | 122.9599 | 122.7997 | -0.032044 | 122.9965 | 123.024 | 0.22431 | -0.009155 | 122.8867 | 122.8043 | -0.07782 | 122.9462 | 122.9462 | 0.14191 | -0.096131 | 123.0148 | 123.0377 | 123.056 | -0.24719 | 122.9691 | 122.9507 | 123.0789 | -0.24262
4289.6719 | 123.0789 | -122.9095 | 0.10986 | 0.0074006 | -0.02051 | 0.013783 | 0.03111 | -0.026523 | -0.035092 | -0.012424 | -0.0075532 | 0.0038944 | 0.0019505 | -0.096538 | -0.016201 | 4.2822e-05 | 0.14648 | 0.082397 | 0.11444 | 0.09613 | 0.091553 | 0.036621 | -0.09613 | 0.064087 | 0.14648 | 0.045776 | 0.027466 | 0.027466 | -0.032043 | -0.10071 | 122.9462 | 122.8134 | -0.01831 | 122.9919 | 123.0057 | 0.19226 | 0.036621 | 122.8775 | 122.8088 | -0.082397 | 122.9736 | 122.9553 | 0.14648 | -0.082397 | 123.0011 | 123.056 | 123.024 | -0.20599 | 122.937 | 122.937 | 123.056 | -0.21057
4291.4062 | 123.1705 | -122.8912 | 0.082397 | 0.01503 | -0.018587 | 0.014851 | 0.034741 | -0.026951 | -0.034451 | -0.012851 | 7.627e-05 | 0.0064578 | 0.0049411 | -0.09547 | -0.01257 | -0.00059818 | 0.054932 | -0.050354 | -0.018311 | 0.009155 | 0.14191 | 0.009155 | -0.15106 | -0.027466 | 0.004578 | -0.086975 | 0.091553 | 0.054932 | -0.054932 | -0.11902 | 122.9004 | 122.7402 | 0.05951 | 122.8409 | 122.9004 | 0.16022 | -0.027465 | 122.8363 | 122.7722 | 0.009156 | 122.8638 | 122.8043 | 0.032044 | -0.027465 | 123.0331 | 122.9462 | 122.8729 | -0.23346 | 122.9828 | 122.9462 | 122.8958 | -0.20142
4293.2031 | 123.1888 | -122.8867 | 0.07782 | -0.00022891 | -0.015169 | 0.016133 | 0.033887 | -0.027805 | -0.035733 | -0.011997 | -0.015182 | 0.0066714 | 0.0019505 | -0.093761 | -0.014065 | 0.0015382 | 0.045776 | -0.036621 | -0.004578 | 0.013733 | 0.12817 | 0.004578 | -0.1236 | -0.018311 | 0.027466 | -0.059509 | 0.068665 | 0.045776 | -0.050354 | -0.11902 | 122.8912 | 122.7631 | 0.050354 | 122.85 | 122.9004 | 0.13733 | -0.032044 | 122.8363 | 122.7676 | -0.009155 | 122.8683 | 122.8271 | 0.05951 | -0.032044 | 123.0148 | 122.9324 | 122.8821 | -0.20142 | 122.9553 | 122.9324 | 122.9141 | -0.19684
4294.9375 | 123.111 | -122.9324 | 0.12817 | 0.0074006 | -0.020083 | 0.017628 | 0.036664 | -0.029728 | -0.040646 | -0.014133 | 7.627e-05 | 0.002399 | 0.0023777 | -0.095043 | -0.016628 | 0.0013244 | 0.036621 | 0.027466 | 0.091553 | 0.064087 | 0.1236 | 0.041199 | -0.10071 | 0.018311 | 0.10529 | 0.027466 | 0.050354 | 0.036621 | -0.041199 | -0.10071 | 122.9736 | 122.8317 | -0.004578 | 122.9599 | 122.9965 | 0.1648 | -0.091553 | 122.8912 | 122.8317 | -0.07782 | 122.9507 | 122.9599 | 0.12817 | -0.091553 | 123.056 | 122.9691 | 123.024 | -0.22888 | 122.9828 | 122.9691 | 123.0377 | -0.22888
4296.7344 | 123.143 | -122.8775 | 0.07782 | 0.01503 | -0.014529 | 0.015065 | 0.036237 | -0.02866 | -0.033169 | -0.011142 | -0.0075532 | 0.006885 | 0.0021641 | -0.094189 | -0.010861 | -0.0010254 | 0.1236 | 0.032043 | 0.045776 | 0.054932 | 0.11902 | 0.018311 | -0.12817 | 0 | 0.07782 | -0.059509 | 0.059509 | 0.059509 | -0.036621 | -0.11444 | 122.8958 | 122.7493 | 0.041199 | 122.9095 | 122.9324 | 0.18311 | 0.045776 | 122.8409 | 122.7631 | -0.018311 | 122.8775 | 122.818 | 0.054932 | -0.018311 | 122.9965 | 123.0011 | 122.9233 | -0.20599 | 122.937 | 122.937 | 122.9553 | -0.19226
4298.5312 | 123.0972 | -122.9279 | 0.11444 | -0.0078584 | -0.021364 | 0.01891 | 0.034955 | -0.027591 | -0.044064 | -0.013279 | 0.0077058 | 0.0028262 | -0.00018589 | -0.096325 | -0.016628 | 0.0023926 | 0.041199 | 0.022888 | 0.082397 | 0.064087 | 0.09613 | 0.036621 | -0.10986 | 0.013733 | 0.11902 | 0.027466 | 0.050354 | 0.059509 | -0.041199 | -0.086975 | 122.9645 | 122.818 | -0.018311 | 122.9507 | 122.9919 | 0.17395 | -0.073242 | 122.8867 | 122.8409 | -0.064087 | 122.9416 | 122.9553 | 0.11444 | -0.054932 | 123.024 | 122.9691 | 123.0103 | -0.2243 | 122.9782 | 122.9874 | 123.0469 | -0.20142
4300.25 | 123.0789 | -122.9004 | 0.10986 | -0.0078584 | -0.016238 | 0.016774 | 0.037091 | -0.028232 | -0.039364 | -0.014774 | 7.627e-05 | 0.0062442 | 0.0040867 | -0.095043 | -0.015988 | 0.0013244 | 0.032043 | -0.036621 | 0 | 0.004578 | 0.14191 | -0.013733 | -0.14648 | -0.050354 | 0.045776 | -0.068665 | 0.09613 | 0.082397 | -0.054932 | -0.13733 | 122.8867 | 122.7539 | 0.032044 | 122.8638 | 122.905 | 0.15106 | -0.07782 | 122.8455 | 122.7631 | -0.013733 | 122.85 | 122.8317 | 0.068664 | -0.027466 | 123.0423 | 122.9324 | 122.9004 | -0.25635 | 122.9965 | 122.9828 | 122.9462 | -0.24719
4302.0312 | 123.0423 | -122.8958 | 0.1236 | -0.00022891 | -0.01816 | 0.016987 | 0.039441 | -0.027164 | -0.040219 | -0.014988 | 7.627e-05 | 0.0019718 | 0.0021641 | -0.095684 | -0.01791 | -0.00081178 | 0.11902 | 0.082397 | 0.10986 | 0.091553 | 0.11444 | 0.032043 | -0.09613 | 0.032043 | 0.15106 | 0.013733 | 0.054932 | 0.032043 | -0.050354 | -0.082397 | 122.9279 | 122.7997 | -0.009155 | 122.9782 | 122.9874 | 0.18768 | -0.004577 | 122.8455 | 122.8134 | -0.068664 | 122.9279 | 122.9095 | 0.09613 | -0.091553 | 123.0103 | 123.0148 | 123.0057 | -0.21973 | 122.9507 | 122.9279 | 123.0469 | -0.20599
4303.8281 | 123.1522 | -122.8912 | 0.09613 | -0.00022891 | -0.018801 | 0.013997 | 0.033887 | -0.028446 | -0.032742 | -0.014774 | 7.627e-05 | 0.007526 | 0.0055821 | -0.092266 | -0.01257 | -0.00059818 | 0.082397 | -0.018311 | 0.013733 | 0.027466 | 0.13275 | 0.009155 | -0.14191 | -0.036621 | 0.022888 | -0.091553 | 0.07782 | 0.064087 | -0.073242 | -0.1236 | 122.9004 | 122.7493 | 0.036621 | 122.8729 | 122.9187 | 0.16937 | -0.013733 | 122.818 | 122.7676 | -0.01831 | 122.8546 | 122.7997 | 0.032043 | -0.032043 | 123.024 | 122.9736 | 122.905 | -0.23804 | 122.9691 | 122.9553 | 122.9141 | -0.21973
4305.5781 | 123.0606 | -122.8958 | 0.10986 | -0.0078584 | -0.019442 | 0.015919 | 0.037305 | -0.028873 | -0.042141 | -0.017124 | -0.0075532 | 0.0019718 | 0.0013095 | -0.094829 | -0.017697 | 0.00025642 | 0.12817 | 0.10071 | 0.12817 | 0.10071 | 0.10071 | 0.054932 | -0.091553 | 0.041199 | 0.1831 | 0.059509 | 0.064087 | 0.041199 | -0.032043 | -0.086975 | 122.9507 | 122.8043 | -0.009155 | 122.9965 | 122.9965 | 0.19226 | 0.018311 | 122.8638 | 122.8088 | -0.045776 | 122.937 | 122.9553 | 0.14648 | -0.068664 | 122.9965 | 123.024 | 123.024 | -0.20142 | 122.9599 | 122.937 | 123.0789 | -0.19684
4307.375 | 123.0377 | -122.9416 | 0.10071 | -0.0078584 | -0.018801 | 0.016133 | 0.036664 | -0.028873 | -0.039151 | -0.014988 | -0.015182 | 0.0036808 | 0.0028049 | -0.096752 | -0.016628 | 0.00047002 | 0.091553 | 0.068665 | 0.086975 | 0.082397 | 0.10529 | 0.013733 | -0.1236 | 0 | 0.1236 | -0.009155 | 0.068665 | 0.050354 | -0.041199 | -0.11444 | 122.9553 | 122.818 | 0.004578 | 123.0103 | 123.024 | 0.20599 | -0.009155 | 122.9004 | 122.8271 | -0.032043 | 122.9416 | 122.9324 | 0.10529 | -0.050354 | 123.0469 | 123.0331 | 123.0286 | -0.2243 | 123.0103 | 122.9919 | 123.0652 | -0.21515
4309.1562 | 123.1842 | -122.9004 | 0.07782 | 0.0074006 | -0.018801 | 0.015706 | 0.03346 | -0.028873 | -0.036587 | -0.014347 | -0.015182 | 0.0036808 | 0.0028049 | -0.09312 | -0.01257 | 0.00047002 | 0.13733 | 0.054932 | 0.082397 | 0.09613 | 0.09613 | 0.045776 | -0.10071 | 0.064087 | 0.14648 | 0.036621 | 0.059509 | 0.041199 | -0.032043 | -0.091553 | 122.9462 | 122.7997 | 0.01831 | 122.9553 | 122.9965 | 0.19684 | 0.059509 | 122.8683 | 122.8088 | -0.018311 | 122.9645 | 122.937 | 0.12817 | -0.036621 | 122.9965 | 123.0377 | 122.9828 | -0.17853 | 122.9599 | 122.9416 | 123.0469 | -0.16937
4310.9062 | 123.1613 | -122.9095 | 0.10986 | -0.0078584 | -0.017733 | 0.015278 | 0.032605 | -0.027164 | -0.037014 | -0.011142 | -0.0075532 | 0.0034672 | 0.00066871 | -0.096325 | -0.011501 | 0.0019654 | 0.12817 | 0.082397 | 0.11902 | 0.091553 | 0.09613 | 0.045776 | -0.091553 | 0.086975 | 0.14191 | 0.050354 | 0.045776 | 0.018311 | -0.013733 | -0.07782 | 122.9553 | 122.818 | -0.013733 | 122.9919 | 123.0011 | 0.18311 | 0.018311 | 122.8958 | 122.8317 | -0.064087 | 122.9965 | 122.9599 | 0.12817 | -0.091552 | 123.0057 | 123.0377 | 123.0286 | -0.20142 | 122.9553 | 122.9279 | 123.0515 | -0.18768
4312.7031 | 123.0789 | -122.9279 | 0.11444 | -0.00022891 | -0.017092 | 0.019337 | 0.040082 | -0.030796 | -0.042569 | -0.015415 | -0.0075532 | 0.0034672 | 0.0030185 | -0.096111 | -0.017697 | -0.00017078 | 0.059509 | 0.036621 | 0.07782 | 0.045776 | 0.09613 | 0.036621 | -0.09613 | 0 | 0.10071 | 0.018311 | 0.064087 | 0.045776 | -0.013733 | -0.086975 | 122.9645 | 122.8317 | -0.018311 | 122.9645 | 122.9736 | 0.14191 | -0.054932 | 122.9141 | 122.8409 | -0.050354 | 122.9279 | 122.9462 | 0.10529 | -0.068665 | 123.024 | 122.9874 | 123.0057 | -0.21057 | 122.9919 | 122.9736 | 123.0286 | -0.20142
4314.5 | 123.1567 | -122.8683 | 0.09613 | -0.00022891 | -0.017519 | 0.01891 | 0.038587 | -0.02866 | -0.033596 | -0.01392 | 7.627e-05 | 0.0077396 | 0.0055821 | -0.09312 | -0.012997 | 0.00025642 | 0.045776 | -0.036621 | -0.018311 | 0.022888 | 0.16479 | -0.013733 | -0.15106 | -0.059509 | 0.059509 | -0.073242 | 0.09613 | 0.073242 | -0.064087 | -0.11444 | 122.8546 | 122.7173 | 0.068665 | 122.8317 | 122.8912 | 0.17395 | -0.050354 | 122.8043 | 122.7539 | 0 | 122.8088 | 122.7951 | 0.041199 | -0.022888 | 123.0331 | 122.9141 | 122.85 | -0.24719 | 122.9645 | 122.9416 | 122.9279 | -0.21057
4316.2344 | 123.1613 | -122.8958 | 0.09613 | -0.00022891 | -0.016238 | 0.015278 | 0.036237 | -0.0293 | -0.031674 | -0.010715 | 7.627e-05 | 0.0083804 | 0.0051547 | -0.09312 | -0.01321 | 0.0011108 | 0.091553 | -0.009155 | 0.009155 | 0.041199 | 0.1236 | 0.013733 | -0.14191 | -0.032043 | 0.022888 | -0.086975 | 0.07782 | 0.064087 | -0.064087 | -0.13275 | 122.9095 | 122.7539 | 0.027466 | 122.8867 | 122.937 | 0.18311 | -0.004577 | 122.8317 | 122.7631 | -0.01831 | 122.8638 | 122.8088 | 0.045776 | -0.032043 | 123.0194 | 122.9874 | 122.905 | -0.23804 | 122.9736 | 122.9599 | 122.9187 | -0.22888
4318.0312 | 123.1842 | -122.8867 | 0.073242 | -0.015487 | -0.019015 | 0.019764 | 0.036237 | -0.028019 | -0.037869 | -0.012424 | -0.015182 | 0.004108 | 0.0023777 | -0.093548 | -0.014919 | 0.002179 | 0.013733 | -0.027466 | -0.013733 | 0.027466 | 0.14648 | -0.009155 | -0.14191 | -0.068665 | 0.059509 | -0.073242 | 0.09613 | 0.059509 | -0.050354 | -0.12817 | 122.8775 | 122.7448 | 0.073242 | 122.8592 | 122.9141 | 0.16937 | -0.059509 | 122.8363 | 122.7585 | 0.022888 | 122.818 | 122.8134 | 0.054932 | -0.013733 | 123.0331 | 122.9004 | 122.8729 | -0.21515 | 122.9828 | 122.9462 | 122.9462 | -0.20142
4319.8281 | 123.1888 | -122.8683 | 0.07782 | -0.00022891 | -0.018587 | 0.015492 | 0.036878 | -0.026951 | -0.035519 | -0.013065 | -0.0075532 | 0.0053898 | 0.0047275 | -0.091839 | -0.013424 | 4.2822e-05 | 0.068665 | 0.018311 | 0.027466 | 0.050354 | 0.1236 | 0.013733 | -0.14191 | 0 | 0.10529 | -0.041199 | 0.068665 | 0.054932 | -0.036621 | -0.12817 | 122.8821 | 122.7264 | 0.045776 | 122.8867 | 122.9187 | 0.19226 | -0.009155 | 122.8317 | 122.7402 | -0.009155 | 122.8683 | 122.8271 | 0.086975 | -0.022888 | 122.9919 | 122.937 | 122.8958 | -0.21973 | 122.937 | 122.9233 | 122.9736 | -0.20599
4321.5781 | 123.2208 | -122.9004 | 0.07782 | -0.00022891 | -0.018801 | 0.017415 | 0.034528 | -0.030369 | -0.038083 | -0.013492 | 0.0077058 | 0.0049624 | 0.0043003 | -0.093975 | -0.01321 | 0.003247 | 0.036621 | -0.009155 | 0.009155 | 0.032043 | 0.13275 | 0.013733 | -0.11902 | -0.004578 | 0.07782 | -0.018311 | 0.059509 | 0.041199 | -0.032043 | -0.10071 | 122.9141 | 122.7814 | 0.054931 | 122.8912 | 122.9324 | 0.15106 | -0.041199 | 122.8683 | 122.7997 | -0.018311 | 122.8958 | 122.8821 | 0.082397 | -0.036621 | 123.0331 | 122.937 | 122.9095 | -0.19684 | 122.9599 | 122.9416 | 122.9782 | -0.17853
4323.3594 | 123.0652 | -122.9141 | 0.12817 | -0.0078584 | -0.021578 | 0.016774 | 0.035596 | -0.030369 | -0.04321 | -0.01392 | 0.0077058 | 0.0015446 | 0.0043003 | -0.094189 | -0.018551 | 0.0041016 | 0.059509 | 0.036621 | 0.086975 | 0.054932 | 0.10529 | 0.036621 | -0.091553 | 0.004578 | 0.09613 | 0.018311 | 0.045776 | 0.045776 | -0.027466 | -0.11444 | 122.9507 | 122.8226 | -0.022888 | 122.9507 | 122.9691 | 0.14649 | -0.068665 | 122.8867 | 122.7997 | -0.082398 | 122.9187 | 122.9324 | 0.13275 | -0.082398 | 123.0194 | 122.9736 | 123.0011 | -0.21973 | 122.9599 | 122.9599 | 123.0103 | -0.24262
4325.1406 | 123.0881 | -122.9233 | 0.10529 | 0.0074006 | -0.017092 | 0.01656 | 0.039227 | -0.028446 | -0.04086 | -0.014347 | 0.0077058 | 0.0060306 | 0.0032321 | -0.093334 | -0.01791 | -0.0018798 | 0.064087 | 0.013733 | 0.050354 | 0.050354 | 0.1236 | 0.009155 | -0.12817 | -0.045776 | 0.068665 | -0.050354 | 0.07782 | 0.068665 | -0.054932 | -0.1236 | 122.9324 | 122.7951 | 0.01831 | 122.937 | 122.9736 | 0.17853 | -0.041199 | 122.8683 | 122.7997 | -0.027466 | 122.8775 | 122.8729 | 0.073242 | -0.036621 | 123.0469 | 122.9874 | 122.9736 | -0.23346 | 123.0011 | 122.9919 | 122.9919 | -0.22888
4326.9531 | 123.1705 | -122.8958 | 0.09613 | -0.00022891 | -0.019228 | 0.016774 | 0.034314 | -0.029941 | -0.037655 | -0.01157 | -0.0075532 | 0.0036808 | 0.0030185 | -0.094616 | -0.014492 | 0.00089722 | 0.15106 | 0.036621 | 0.09613 | 0.086975 | 0.10529 | 0.050354 | -0.10529 | 0.059509 | 0.12817 | 0.050354 | 0.041199 | 0.022888 | -0.018311 | -0.086975 | 122.9462 | 122.7905 | 0.009156 | 122.9324 | 122.9828 | 0.19226 | 0.054932 | 122.8775 | 122.8088 | -0.054931 | 122.9553 | 122.9462 | 0.13733 | -0.073242 | 123.0011 | 123.0469 | 122.9919 | -0.20142 | 122.937 | 122.9187 | 123.024 | -0.1831
4328.7656 | 123.2025 | -122.8775 | 0.07782 | -0.00022891 | -0.019442 | 0.016774 | 0.035596 | -0.028232 | -0.035305 | -0.013492 | 7.627e-05 | 0.0056034 | 0.0049411 | -0.093548 | -0.013638 | -0.0014526 | 0.064087 | -0.013733 | 0.009155 | 0.041199 | 0.14648 | 0.009155 | -0.14648 | -0.036621 | 0.082397 | -0.041199 | 0.091553 | 0.064087 | -0.064087 | -0.11902 | 122.8867 | 122.731 | 0.068664 | 122.8638 | 122.9187 | 0.18768 | -0.013733 | 122.8134 | 122.7585 | 0.013733 | 122.8409 | 122.8363 | 0.07782 | -0.013733 | 123.024 | 122.9416 | 122.8867 | -0.2243 | 122.9691 | 122.9416 | 122.9599 | -0.19684
4330.5625 | 123.0881 | -122.9233 | 0.13733 | -0.00022891 | -0.023287 | 0.017842 | 0.03645 | -0.028232 | -0.04385 | -0.01392 | 7.627e-05 | 0.0017582 | 0.0032321 | -0.096325 | -0.01791 | 0.003888 | 0.054932 | 0.018311 | 0.07782 | 0.059509 | 0.11444 | 0.032043 | -0.11444 | 0 | 0.10071 | 0.004578 | 0.045776 | 0.036621 | -0.036621 | -0.09613 | 122.9553 | 122.8088 | -0.022888 | 122.9416 | 122.9828 | 0.17395 | -0.082397 | 122.8867 | 122.8271 | -0.091553 | 122.9233 | 122.9279 | 0.10071 | -0.10071 | 123.0377 | 122.9782 | 123.0011 | -0.25177 | 122.9691 | 122.9599 | 123.024 | -0.23346
4332.3594 | 123.1476 | -122.9141 | 0.07782 | -0.0078584 | -0.016451 | 0.015492 | 0.034101 | -0.028446 | -0.034237 | -0.011142 | -0.0075532 | 0.007526 | 0.0051547 | -0.095043 | -0.011715 | -0.0033752 | 0.050354 | -0.07782 | -0.009155 | 0.013733 | 0.15564 | -0.004578 | -0.14191 | -0.073242 | 0 | -0.11902 | 0.10071 | 0.082397 | -0.082397 | -0.14191 | 122.9095 | 122.7722 | 0.07782 | 122.8363 | 122.9279 | 0.15564 | -0.027466 | 122.8317 | 122.7722 | 0.022888 | 122.8409 | 122.7951 | 0.022888 | 0.004577 | 123.0698 | 122.9645 | 122.905 | -0.21973 | 123.0148 | 122.9965 | 122.9141 | -0.21973
4334.0625 | 123.2071 | -122.8775 | 0.068665 | -0.0078584 | -0.014529 | 0.013356 | 0.039227 | -0.027378 | -0.035519 | -0.013492 | 7.627e-05 | 0.0060306 | 0.0066501 | -0.093975 | -0.014492 | -0.0014526 | 0.073242 | -0.036621 | 0.004578 | 0.045776 | 0.1236 | 0.018311 | -0.15106 | -0.027466 | 0.073242 | -0.050354 | 0.068665 | 0.068665 | -0.054932 | -0.11902 | 122.8958 | 122.7264 | 0.054931 | 122.8409 | 122.9233 | 0.19684 | 0.004577 | 122.8226 | 122.7585 | 0 | 122.85 | 122.8271 | 0.068665 | 0 | 123.0011 | 122.9507 | 122.8821 | -0.21973 | 122.9462 | 122.9462 | 122.9507 | -0.18768
4335.8594 | 123.1934 | -122.9095 | 0.082397 | 0.0074006 | -0.017946 | 0.018055 | 0.032819 | -0.028446 | -0.039792 | -0.012638 | -0.0075532 | 0.0047488 | 0.0017367 | -0.093548 | -0.014065 | 0.0019654 | 0.1236 | 0.054932 | 0.10071 | 0.091553 | 0.10071 | 0.045776 | -0.086975 | 0.064087 | 0.13275 | 0.045776 | 0.036621 | 0.041199 | -0.027466 | -0.082397 | 122.9553 | 122.8226 | 0.018311 | 122.9645 | 123.0011 | 0.17853 | 0.041199 | 122.8821 | 122.8271 | -0.045776 | 122.9736 | 122.9553 | 0.12817 | -0.041198 | 123.0103 | 123.0331 | 123.0103 | -0.16937 | 122.9462 | 122.9507 | 123.0423 | -0.16479
4337.6719 | 123.1934 | -122.8912 | 0.091553 | -0.015487 | -0.017306 | 0.013142 | 0.037518 | -0.028446 | -0.035092 | -0.013279 | 7.627e-05 | 0.010303 | 0.0053683 | -0.092907 | -0.016415 | 0.00047002 | 0.09613 | -0.013733 | 0.027466 | 0.050354 | 0.10986 | -0.013733 | -0.12817 | -0.018311 | 0.086975 | -0.050354 | 0.07782 | 0.07782 | -0.045776 | -0.10986 | 122.8775 | 122.7631 | 0.01831 | 122.8775 | 122.9416 | 0.17853 | 0.004577 | 122.8455 | 122.7814 | -0.013733 | 122.8729 | 122.8409 | 0.059509 | -0.013733 | 123.0011 | 122.9874 | 122.9187 | -0.21973 | 122.9691 | 122.9691 | 122.9782 | -0.20142
4339.4688 | 123.175 | -122.905 | 0.064087 | -0.0078584 | -0.017306 | 0.016346 | 0.035382 | -0.029514 | -0.036587 | -0.013279 | 7.627e-05 | 0.0047488 | 0.0047275 | -0.094189 | -0.01257 | 0.0015382 | 0.036621 | -0.07782 | -0.018311 | 0.022888 | 0.12817 | 0.004578 | -0.13733 | -0.054932 | 0 | -0.09613 | 0.068665 | 0.068665 | -0.064087 | -0.11444 | 122.9095 | 122.7676 | 0.064087 | 122.8271 | 122.9279 | 0.16022 | -0.027466 | 122.8409 | 122.7905 | 0.004578 | 122.85 | 122.8088 | 0.018311 | 0.004578 | 123.0331 | 122.9416 | 122.8867 | -0.20142 | 122.9736 | 122.9736 | 122.905 | -0.17853
4341.1875 | 123.1384 | -122.905 | 0.09613 | -0.015487 | -0.015597 | 0.015919 | 0.039441 | -0.026951 | -0.040432 | -0.012424 | -0.015182 | 0.005176 | 0.0045139 | -0.093548 | -0.017697 | 0.0015382 | 0.013733 | -0.073242 | -0.009155 | 0.018311 | 0.15106 | -0.018311 | -0.14648 | -0.059509 | 0.036621 | -0.091553 | 0.10071 | 0.091553 | -0.068665 | -0.13275 | 122.8867 | 122.7585 | 0.054932 | 122.8317 | 122.9233 | 0.16479 | -0.082397 | 122.8363 | 122.7722 | 0.004578 | 122.8455 | 122.8134 | 0.041198 | -0.004577 | 123.056 | 122.9187 | 122.8958 | -0.24261 | 123.0057 | 122.9965 | 122.9416 | -0.22888
4343 | 123.1064 | -122.9324 | 0.10071 | -0.0078584 | -0.01816 | 0.018696 | 0.038587 | -0.028019 | -0.041928 | -0.013065 | 7.627e-05 | 0.0011172 | 0.0045139 | -0.095257 | -0.018978 | 0.0013244 | 0.10986 | 0.11444 | 0.14648 | 0.10986 | 0.10529 | 0.045776 | -0.10529 | 0.054932 | 0.19684 | 0.068665 | 0.050354 | 0.032043 | -0.018311 | -0.09613 | 122.9782 | 122.8271 | 0.004578 | 123.0469 | 123.0423 | 0.21515 | 0.009155 | 122.9141 | 122.8363 | -0.050354 | 122.9874 | 123.0011 | 0.16479 | -0.068665 | 123.0377 | 123.0423 | 123.0789 | -0.20599 | 122.9828 | 122.9645 | 123.1293 | -0.19684
4344.7969 | 123.0652 | -122.9279 | 0.11444 | -0.0078584 | -0.019228 | 0.016987 | 0.035382 | -0.02866 | -0.040219 | -0.016269 | 0.0077058 | 0.0034672 | 0.0040867 | -0.093975 | -0.015774 | 4.2822e-05 | 0.082397 | 0.050354 | 0.07782 | 0.068665 | 0.10071 | 0.018311 | -0.13275 | -0.032043 | 0.091553 | -0.032043 | 0.050354 | 0.068665 | -0.045776 | -0.11902 | 122.9462 | 122.7951 | -0.013733 | 122.9782 | 122.9965 | 0.20142 | -0.032044 | 122.8821 | 122.8088 | -0.064087 | 122.8958 | 122.8958 | 0.086976 | -0.045776 | 123.0286 | 123.0103 | 123.0057 | -0.24719 | 122.9782 | 122.9965 | 123.0194 | -0.23346
4346.5312 | 123.1567 | -122.9141 | 0.10529 | -0.00022891 | -0.016878 | 0.015065 | 0.033887 | -0.029941 | -0.033596 | -0.011356 | 7.627e-05 | 0.007526 | 0.0049411 | -0.095043 | -0.011929 | 4.2822e-05 | 0.013733 | -0.068665 | -0.045776 | 0.009155 | 0.15106 | 0 | -0.13275 | -0.059509 | -0.009155 | -0.091553 | 0.086975 | 0.068665 | -0.045776 | -0.11902 | 122.9141 | 122.7814 | 0.045776 | 122.8455 | 122.9233 | 0.14191 | -0.091553 | 122.8683 | 122.7951 | -0.018311 | 122.8546 | 122.8226 | 0.027466 | -0.036621 | 123.0652 | 122.9279 | 122.8683 | -0.23804 | 123.0011 | 122.9828 | 122.905 | -0.22431
4348.3281 | 123.1934 | -122.9004 | 0.10529 | -0.00022891 | -0.017519 | 0.015065 | 0.032819 | -0.026951 | -0.036801 | -0.012851 | 7.627e-05 | 0.0030398 | 0.0032321 | -0.096325 | -0.012142 | 0.0015382 | 0.11444 | 0.073242 | 0.11902 | 0.10071 | 0.09613 | 0.050354 | -0.09613 | 0.064087 | 0.13275 | 0.041199 | 0.041199 | 0.018311 | -0.009155 | -0.073242 | 122.9507 | 122.8043 | -0.009156 | 122.9736 | 123.0011 | 0.19684 | 0.009155 | 122.8912 | 122.8271 | -0.064087 | 122.9645 | 122.9416 | 0.11444 | -0.086975 | 122.9965 | 123.0148 | 123.0194 | -0.20142 | 122.9416 | 122.9187 | 123.0331 | -0.17853
4350.1094 | 123.0789 | -122.9416 | 0.10986 | -0.00022891 | -0.017306 | 0.019123 | 0.037732 | -0.028232 | -0.039792 | -0.013065 | 0.0077058 | 0.004108 | 0.0019505 | -0.096538 | -0.015774 | 0.0026062 | 0.009155 | -0.018311 | 0.013733 | 0.009155 | 0.13275 | 0.013733 | -0.13733 | -0.068665 | 0.054932 | -0.068665 | 0.091553 | 0.082397 | -0.064087 | -0.1236 | 122.9553 | 122.8043 | 0.022888 | 122.9233 | 122.9507 | 0.14648 | -0.10071 | 122.8775 | 122.818 | -0.01831 | 122.8729 | 122.8729 | 0.054931 | -0.027466 | 123.0743 | 122.9507 | 122.9553 | -0.24719 | 123.0331 | 123.024 | 122.9965 | -0.23346
4351.8438 | 123.1796 | -122.9141 | 0.07782 | -0.00022891 | -0.015383 | 0.016774 | 0.0388 | -0.029514 | -0.035092 | -0.013492 | -0.015182 | 0.0090214 | 0.0047275 | -0.09312 | -0.013424 | 0.00025642 | 0.10529 | 0.018311 | 0.045776 | 0.064087 | 0.13275 | 0.022888 | -0.13275 | 0.009155 | 0.068665 | -0.054932 | 0.07782 | 0.054932 | -0.050354 | -0.1236 | 122.937 | 122.7814 | 0.054931 | 122.9324 | 122.9782 | 0.19684 | 0.027466 | 122.8638 | 122.7905 | 0 | 122.9233 | 122.8592 | 0.068664 | -0.022888 | 123.0469 | 123.0194 | 122.9599 | -0.21057 | 122.9919 | 122.9691 | 122.9828 | -0.20142
4353.6406 | 123.0927 | -122.9324 | 0.09613 | -0.00022891 | -0.016024 | 0.018055 | 0.039655 | -0.02866 | -0.041287 | -0.01392 | 0.0077058 | 0.004108 | 0.0036593 | -0.094189 | -0.019833 | 0.0034608 | 0.027466 | -0.022888 | 0.013733 | 0.013733 | 0.13733 | 0.009155 | -0.14648 | -0.064087 | 0.054932 | -0.064087 | 0.09613 | 0.073242 | -0.064087 | -0.12817 | 122.9416 | 122.7859 | 0.041199 | 122.9095 | 122.9462 | 0.16022 | -0.068664 | 122.8683 | 122.8043 | 0 | 122.8683 | 122.8683 | 0.064087 | -0.022888 | 123.0698 | 122.9599 | 122.9462 | -0.24261 | 123.0286 | 123.0057 | 122.9874 | -0.2243
4355.4219 | 123.1522 | -122.905 | 0.091553 | -0.0078584 | -0.015597 | 0.016133 | 0.039441 | -0.029514 | -0.039792 | -0.014133 | 0.0077058 | 0.0056034 | 0.0047275 | -0.092052 | -0.016415 | 4.2822e-05 | 0.022888 | -0.064087 | -0.018311 | 0.004578 | 0.16022 | -0.013733 | -0.14648 | -0.073242 | 0.032043 | -0.07782 | 0.086975 | 0.091553 | -0.054932 | -0.11902 | 122.8912 | 122.7585 | 0.068664 | 122.8409 | 122.9095 | 0.15106 | -0.068665 | 122.85 | 122.7859 | -0.004578 | 122.8317 | 122.8271 | 0.041199 | 0 | 123.0652 | 122.9279 | 122.8867 | -0.23804 | 122.9919 | 122.9965 | 122.937 | -0.21057
4357.1562 | 123.2162 | -122.9004 | 0.091553 | -0.0078584 | -0.019228 | 0.015706 | 0.033246 | -0.029514 | -0.035305 | -0.013279 | 7.627e-05 | 0.006885 | 0.0053683 | -0.091625 | -0.013851 | -0.00059818 | 0.064087 | -0.059509 | 0.004578 | 0.009155 | 0.14191 | 0 | -0.1236 | -0.032043 | 0.018311 | -0.073242 | 0.082397 | 0.064087 | -0.050354 | -0.11902 | 122.9004 | 122.7768 | 0.050354 | 122.8409 | 122.9095 | 0.13275 | -0.027466 | 122.85 | 122.7814 | -0.009156 | 122.8683 | 122.8271 | 0.045777 | -0.027466 | 123.0423 | 122.9645 | 122.905 | -0.21515 | 122.9828 | 122.9645 | 122.9187 | -0.21057
4358.9531 | 123.1247 | -122.9645 | 0.09613 | -0.0078584 | -0.023928 | 0.019764 | 0.035169 | -0.028232 | -0.045132 | -0.014988 | 0.0077058 | 0.00069003 | 0.0055821 | -0.094829 | -0.018978 | 0.002179 | 0.041199 | 0.022888 | 0.086975 | 0.050354 | 0.091553 | 0.036621 | -0.10529 | 0.009155 | 0.10071 | 0.022888 | 0.059509 | 0.068665 | -0.045776 | -0.10071 | 123.0011 | 122.8592 | -0.004577 | 122.9874 | 123.0148 | 0.15564 | -0.054931 | 122.9187 | 122.8638 | -0.036621 | 122.9736 | 122.9874 | 0.1236 | -0.027465 | 123.056 | 123.0057 | 123.0515 | -0.20142 | 123.024 | 123.0331 | 123.0652 | -0.19684
4360.6875 | 123.1613 | -122.9233 | 0.082397 | -0.00022891 | -0.018801 | 0.014637 | 0.033887 | -0.027591 | -0.033169 | -0.013492 | 7.627e-05 | 0.0066714 | 0.0051547 | -0.094616 | -0.01257 | 0.0017518 | 0.022888 | -0.07782 | -0.032043 | 0.009155 | 0.13733 | 0 | -0.14191 | -0.073242 | -0.013733 | -0.1236 | 0.091553 | 0.07782 | -0.073242 | -0.13733 | 122.9233 | 122.7814 | 0.054932 | 122.8455 | 122.9324 | 0.15106 | -0.059509 | 122.85 | 122.7859 | 0.009156 | 122.85 | 122.7997 | 0.013733 | -0.004577 | 123.0606 | 122.9462 | 122.8912 | -0.2243 | 123.0148 | 123.0011 | 122.9095 | -0.21973
4362.4844 | 123.1201 | -122.9141 | 0.10529 | -0.00022891 | -0.020724 | 0.016774 | 0.037091 | -0.030369 | -0.042569 | -0.014347 | 0.015335 | 0.00069003 | 0.0060093 | -0.095043 | -0.01791 | 0.0026062 | 0.10529 | 0.10986 | 0.12817 | 0.10071 | 0.10986 | 0.027466 | -0.091553 | 0.059509 | 0.20142 | 0.068665 | 0.054932 | 0.027466 | -0.032043 | -0.082397 | 122.9416 | 122.8226 | 0.004577 | 123.024 | 123.0148 | 0.19226 | 0 | 122.8821 | 122.8317 | -0.050354 | 122.9736 | 122.9828 | 0.15106 | -0.07782 | 123.024 | 123.0194 | 123.0423 | -0.19684 | 122.9691 | 122.9416 | 123.1155 | -0.18768
4364.2812 | 123.1384 | -122.9462 | 0.11444 | -0.0078584 | -0.019655 | 0.018696 | 0.035596 | -0.030155 | -0.041287 | -0.017551 | 0.0077058 | 0.0019718 | 0.0047275 | -0.096325 | -0.015988 | -0.0010254 | 0.07782 | 0.032043 | 0.10529 | 0.073242 | 0.10071 | 0.041199 | -0.11902 | 0.036621 | 0.12817 | 0.050354 | 0.054932 | 0.036621 | -0.022888 | -0.09613 | 122.9874 | 122.8271 | -0.013733 | 122.9782 | 123.0194 | 0.19226 | -0.036621 | 122.9233 | 122.85 | -0.059509 | 122.9828 | 122.9965 | 0.14648 | -0.07782 | 123.0469 | 123.024 | 123.0515 | -0.23346 | 123.0011 | 122.9828 | 123.0743 | -0.21057
4366.0156 | 123.0469 | -122.9507 | 0.1236 | 0.0074006 | -0.019228 | 0.015065 | 0.040509 | -0.028019 | -0.04086 | -0.017338 | 7.627e-05 | 0.0030398 | 0.0068637 | -0.095043 | -0.01556 | 0.00025642 | 0.1236 | 0.073242 | 0.10529 | 0.082397 | 0.10529 | 0.022888 | -0.10529 | 0.013733 | 0.12817 | -0.004578 | 0.059509 | 0.050354 | -0.064087 | -0.11902 | 122.9736 | 122.8455 | -0.01831 | 123.024 | 123.0331 | 0.18768 | 0 | 122.8867 | 122.8317 | -0.064087 | 122.9645 | 122.9462 | 0.11444 | -0.073242 | 123.056 | 123.0743 | 123.056 | -0.22888 | 123.0103 | 123.0011 | 123.0789 | -0.24261
4367.8281 | 123.0927 | -122.9279 | 0.1236 | -0.0078584 | -0.020937 | 0.018055 | 0.036878 | -0.0293 | -0.040646 | -0.014774 | -0.0075532 | 0.0017582 | 0.0053683 | -0.095898 | -0.016201 | -0.00017078 | 0.068665 | 0.022888 | 0.068665 | 0.064087 | 0.09613 | 0.027466 | -0.09613 | 0 | 0.09613 | 0.004578 | 0.068665 | 0.041199 | -0.045776 | -0.10986 | 122.9553 | 122.8317 | -0.027466 | 122.9507 | 122.9919 | 0.16022 | -0.054931 | 122.8821 | 122.818 | -0.054931 | 122.9279 | 122.9324 | 0.11444 | -0.082397 | 123.024 | 122.9965 | 122.9965 | -0.21973 | 122.9965 | 122.9691 | 123.024 | -0.23346
4369.5781 | 123.1064 | -122.9462 | 0.1236 | -0.00022891 | -0.018587 | 0.017842 | 0.038159 | -0.028019 | -0.039151 | -0.015415 | -0.0075532 | 0.0036808 | 0.0036593 | -0.095898 | -0.016628 | -0.00017078 | 0.10071 | 0.073242 | 0.086975 | 0.059509 | 0.11902 | 0.036621 | -0.10071 | 0.027466 | 0.082397 | 0.009155 | 0.045776 | 0.041199 | -0.027466 | -0.10986 | 122.9828 | 122.8455 | -0.004577 | 123.0194 | 123.0057 | 0.16022 | -0.022888 | 122.9187 | 122.8363 | -0.07782 | 122.9736 | 122.9553 | 0.11902 | -0.082397 | 123.0652 | 123.0469 | 123.0331 | -0.2243 | 122.9919 | 122.9874 | 123.0286 | -0.23346
4371.3594 | 123.1934 | -122.9233 | 0.1236 | -0.0078584 | -0.014742 | 0.016346 | 0.033246 | -0.028446 | -0.033169 | -0.011997 | -0.0075532 | 0.0081668 | 0.0068637 | -0.092266 | -0.012783 | -0.004016 | 0.045776 | -0.082397 | -0.041199 | 0 | 0.13275 | 0.009155 | -0.15106 | -0.032043 | -0.013733 | -0.11444 | 0.086975 | 0.073242 | -0.041199 | -0.1236 | 122.9324 | 122.7722 | 0.009155 | 122.8409 | 122.9233 | 0.15106 | -0.07782 | 122.8821 | 122.7997 | -0.036621 | 122.8912 | 122.8088 | 0.009155 | -0.050354 | 123.056 | 122.9691 | 122.8821 | -0.27466 | 123.0103 | 122.9965 | 122.9095 | -0.24719
4373.1562 | 123.23 | -122.8958 | 0.086975 | -0.00022891 | -0.016024 | 0.016346 | 0.033673 | -0.025883 | -0.03381 | -0.012211 | -0.0075532 | 0.005176 | 0.0070773 | -0.093334 | -0.011501 | -0.0010254 | 0.068665 | 0.009155 | 0.013733 | 0.045776 | 0.13275 | 0.004578 | -0.13733 | 0 | 0.068665 | -0.054932 | 0.07782 | 0.064087 | -0.068665 | -0.13275 | 122.9004 | 122.7585 | 0.045776 | 122.905 | 122.9416 | 0.18311 | -0.01831 | 122.8271 | 122.7631 | -0.009155 | 122.8958 | 122.8409 | 0.077819 | -0.022888 | 123.0286 | 122.9645 | 122.9095 | -0.2243 | 122.9736 | 122.9599 | 122.9645 | -0.21973
4374.9531 | 123.0743 | -122.9691 | 0.12817 | 0.0074006 | -0.016024 | 0.018483 | 0.039441 | -0.028019 | -0.041287 | -0.012424 | -0.0075532 | 0.0030398 | 0.0070773 | -0.095257 | -0.018765 | 0.00025642 | 0.10071 | 0.086975 | 0.12817 | 0.10071 | 0.10529 | 0.045776 | -0.10529 | 0.022888 | 0.14648 | 0.018311 | 0.041199 | 0.054932 | -0.032043 | -0.10529 | 123.0148 | 122.8638 | -0.022888 | 123.056 | 123.0698 | 0.20599 | -0.027466 | 122.937 | 122.8638 | -0.086975 | 122.9919 | 122.9874 | 0.1236 | -0.073242 | 123.0743 | 123.0698 | 123.0972 | -0.23346 | 123.0103 | 123.024 | 123.1155 | -0.23346
4376.75 | 123.0881 | -122.9462 | 0.12817 | -0.00022891 | -0.018374 | 0.018269 | 0.036023 | -0.027805 | -0.039151 | -0.012851 | -0.0075532 | 0.002399 | 0.0049411 | -0.095257 | -0.014279 | 0.0028198 | 0.082397 | 0.073242 | 0.082397 | 0.073242 | 0.10986 | 0.018311 | -0.13275 | -0.018311 | 0.10529 | -0.050354 | 0.082397 | 0.054932 | -0.050354 | -0.11444 | 122.9645 | 122.8134 | -0.018311 | 123.0194 | 123.0194 | 0.20599 | -0.045777 | 122.8958 | 122.8317 | -0.045777 | 122.9279 | 122.8958 | 0.064087 | -0.073242 | 123.056 | 123.0286 | 123.0286 | -0.26093 | 123.0286 | 123.0011 | 123.0515 | -0.24262
4378.5 | 123.0698 | -122.9782 | 0.11444 | -0.015487 | -0.015597 | 0.015492 | 0.038373 | -0.026951 | -0.040005 | -0.014347 | 7.627e-05 | 0.0043216 | 0.0060093 | -0.09547 | -0.018337 | -0.00081178 | 0.09613 | 0.091553 | 0.09613 | 0.10071 | 0.11444 | 0.032043 | -0.10986 | 0.018311 | 0.14191 | 0.013733 | 0.059509 | 0.064087 | -0.027466 | -0.10986 | 123.0103 | 122.8683 | 0 | 123.0698 | 123.0789 | 0.21057 | -0.018311 | 122.9507 | 122.8683 | -0.054932 | 122.9965 | 122.9919 | 0.1236 | -0.050354 | 123.0927 | 123.0743 | 123.0743 | -0.2243 | 123.0377 | 123.0423 | 123.1201 | -0.2243
4380.2969 | 123.1338 | -122.9599 | 0.11444 | -0.0078584 | -0.024355 | 0.017201 | 0.035382 | -0.028446 | -0.039151 | -0.014774 | 7.627e-05 | 0.0019718 | 0.0057957 | -0.094189 | -0.016415 | 0.002179 | 0.16022 | 0.16479 | 0.11902 | 0.10071 | 0.10529 | 0.027466 | -0.10071 | 0.059509 | 0.19684 | 0.059509 | 0.050354 | 0.050354 | -0.022888 | -0.11902 | 122.9874 | 122.8592 | -0.009155 | 123.1247 | 123.0606 | 0.20142 | 0.045776 | 122.937 | 122.8409 | -0.064087 | 123.0194 | 123.0194 | 0.17853 | -0.064087 | 123.0652 | 123.1201 | 123.0789 | -0.21515 | 123.0103 | 123.0103 | 123.1567 | -0.23346
4382.0156 | 123.1705 | -122.9462 | 0.10071 | -0.015487 | -0.019015 | 0.017415 | 0.031537 | -0.029087 | -0.036374 | -0.012424 | -0.0075532 | 0.0036808 | 0.0047275 | -0.095898 | -0.013424 | -0.00038438 | 0.13275 | 0.086975 | 0.12817 | 0.091553 | 0.10529 | 0.036621 | -0.091553 | 0.068665 | 0.14648 | 0.045776 | 0.036621 | 0.018311 | -0.041199 | -0.082397 | 122.9828 | 122.8546 | 0.004578 | 123.0331 | 123.0377 | 0.18311 | 0.032043 | 122.905 | 122.8638 | -0.064087 | 123.0148 | 122.9919 | 0.12817 | -0.082397 | 123.0515 | 123.0789 | 123.0743 | -0.19226 | 122.9828 | 122.9645 | 123.0927 | -0.18311
4383.8125 | 123.175 | -122.937 | 0.10529 | -0.00022891 | -0.01581 | 0.015706 | 0.03346 | -0.0293 | -0.031887 | -0.011783 | 7.627e-05 | 0.0081668 | 0.0057957 | -0.094189 | -0.012356 | -0.001239 | 0.082397 | -0.018311 | 0 | 0.027466 | 0.13733 | 0.013733 | -0.14191 | -0.045776 | 0.009155 | -0.10529 | 0.086975 | 0.059509 | -0.064087 | -0.13733 | 122.9507 | 122.7951 | 0.032043 | 122.9187 | 122.9645 | 0.16937 | -0.022889 | 122.8729 | 122.7997 | -0.018311 | 122.8912 | 122.8317 | 0.032043 | -0.045777 | 123.0743 | 123.0194 | 122.937 | -0.24719 | 123.024 | 122.9965 | 122.9462 | -0.24262
4385.5469 | 123.0972 | -122.9507 | 0.13275 | -0.00022891 | -0.01581 | 0.019123 | 0.036878 | -0.027591 | -0.04086 | -0.013065 | -0.0075532 | 0.0015446 | 0.0070773 | -0.09547 | -0.017056 | 0.0013244 | 0.10529 | 0.11444 | 0.13733 | 0.10071 | 0.10529 | 0.059509 | -0.09613 | 0.054932 | 0.19226 | 0.050354 | 0.050354 | 0.041199 | -0.022888 | -0.09613 | 123.0103 | 122.8546 | -0.027465 | 123.0652 | 123.0515 | 0.19684 | -0.027465 | 122.9279 | 122.8546 | -0.082397 | 123.0057 | 123.0011 | 0.14648 | -0.091552 | 123.056 | 123.056 | 123.0881 | -0.22888 | 123.0011 | 122.9919 | 123.143 | -0.22888
4387.3438 | 123.23 | -122.9279 | 0.086975 | -0.00022891 | -0.017733 | 0.016774 | 0.03645 | -0.02866 | -0.036587 | -0.013706 | -0.0075532 | 0.0053898 | 0.0094273 | -0.093761 | -0.015347 | 0.00025642 | 0.027466 | -0.041199 | -0.004578 | 0.027466 | 0.14648 | 0.004578 | -0.15106 | -0.059509 | 0.054932 | -0.073242 | 0.086975 | 0.091553 | -0.064087 | -0.11444 | 122.9324 | 122.7768 | 0.059509 | 122.8867 | 122.9553 | 0.17853 | -0.059509 | 122.8638 | 122.8134 | 0 | 122.8683 | 122.8546 | 0.041199 | 0.004578 | 123.0743 | 122.9553 | 122.9233 | -0.23804 | 123.0148 | 123.0194 | 122.9828 | -0.20142
4389.0781 | 123.2071 | -122.9141 | 0.10071 | 0.0074006 | -0.018587 | 0.019123 | 0.036664 | -0.02866 | -0.037442 | -0.011356 | 0.0077058 | 0.0030398 | 0.0060093 | -0.095684 | -0.012997 | 0.0017518 | 0.13275 | 0.09613 | 0.11444 | 0.09613 | 0.10071 | 0.045776 | -0.091553 | 0.068665 | 0.14648 | 0.041199 | 0.022888 | 0.027466 | -0.027466 | -0.09613 | 122.9599 | 122.8226 | 0 | 123.0103 | 123.0103 | 0.18768 | 0.032043 | 122.8867 | 122.818 | -0.07782 | 122.9828 | 122.9553 | 0.13733 | -0.073242 | 123.0148 | 123.0469 | 123.0286 | -0.19226 | 122.937 | 122.9416 | 123.0606 | -0.19684
4390.875 | 123.0789 | -122.9233 | 0.12817 | -0.0078584 | -0.017092 | 0.017201 | 0.040936 | -0.027378 | -0.038937 | -0.013279 | 7.627e-05 | 0.0047488 | 0.0064365 | -0.095257 | -0.01791 | -0.0010254 | 0.11444 | 0.07782 | 0.10071 | 0.09613 | 0.10529 | 0.027466 | -0.09613 | 0.009155 | 0.1236 | -0.009155 | 0.041199 | 0.054932 | -0.041199 | -0.10071 | 122.9507 | 122.8271 | -0.022888 | 123.0011 | 123.0194 | 0.19226 | -0.013733 | 122.8821 | 122.8226 | -0.086975 | 122.9324 | 122.9141 | 0.091553 | -0.073242 | 123.0286 | 123.0377 | 123.024 | -0.2243 | 122.9645 | 122.9782 | 123.0469 | -0.22888
4392.6094 | 123.1842 | -122.9416 | 0.11444 | -0.00022891 | -0.019869 | 0.016346 | 0.034955 | -0.027591 | -0.038296 | -0.011997 | 0.0077058 | 0.0019718 | 0.0053683 | -0.095257 | -0.014492 | -0.0018798 | 0.14191 | 0.086975 | 0.1236 | 0.10071 | 0.086975 | 0.045776 | -0.091553 | 0.064087 | 0.14191 | 0.041199 | 0.045776 | 0.027466 | -0.041199 | -0.082397 | 122.9874 | 122.85 | -0.027466 | 123.0286 | 123.0423 | 0.19226 | 0.027466 | 122.9004 | 122.8592 | -0.068665 | 123.0057 | 122.9828 | 0.1236 | -0.086975 | 123.0286 | 123.0835 | 123.0652 | -0.20599 | 122.9874 | 122.9691 | 123.0835 | -0.19684
4394.4219 | 123.2391 | -122.9187 | 0.091553 | 0.0074006 | -0.017733 | 0.016133 | 0.034101 | -0.029087 | -0.035946 | -0.01392 | 7.627e-05 | 0.0062442 | 0.0055821 | -0.09248 | -0.01257 | -0.00059818 | 0.036621 | -0.027466 | 0 | 0.027466 | 0.1236 | 0 | -0.13733 | -0.045776 | 0.07782 | -0.064087 | 0.091553 | 0.054932 | -0.064087 | -0.11444 | 122.9187 | 122.7814 | 0.032043 | 122.8912 | 122.9462 | 0.16479 | -0.054932 | 122.8546 | 122.8043 | 0 | 122.8729 | 122.8546 | 0.050354 | -0.036621 | 123.0423 | 122.9553 | 122.9187 | -0.22888 | 123.0103 | 122.9736 | 122.9965 | -0.20599
4396.2031 | 123.111 | -122.9553 | 0.1236 | -0.00022891 | -0.024782 | 0.018696 | 0.034314 | -0.030796 | -0.041501 | -0.015842 | 7.627e-05 | 0.002399 | 0.0023777 | -0.097393 | -0.016415 | 0.0013244 | 0.041199 | 0.032043 | 0.07782 | 0.050354 | 0.11444 | 0.059509 | -0.10071 | 0.004578 | 0.082397 | 0.013733 | 0.068665 | 0.050354 | -0.036621 | -0.11902 | 123.0148 | 122.8546 | -0.009155 | 122.9874 | 123.0057 | 0.15106 | -0.082397 | 122.9187 | 122.8363 | -0.054931 | 122.9599 | 122.9691 | 0.13275 | -0.073242 | 123.0698 | 122.9965 | 123.0331 | -0.2243 | 123.024 | 123.0057 | 123.0377 | -0.24261
4398 | 123.2346 | -122.9187 | 0.086975 | 0.0074006 | -0.020724 | 0.017415 | 0.035809 | -0.027591 | -0.03616 | -0.013065 | 7.627e-05 | 0.004108 | 0.0043003 | -0.095257 | -0.013638 | 0.00025642 | 0.10986 | 0.004578 | 0.041199 | 0.041199 | 0.11902 | 0.036621 | -0.13275 | 0.050354 | 0.11902 | 0.013733 | 0.036621 | 0.036621 | -0.036621 | -0.09613 | 122.9553 | 122.7859 | 0.032044 | 122.9233 | 122.9599 | 0.17395 | 0.022888 | 122.8821 | 122.8226 | -0.050354 | 122.9691 | 122.9324 | 0.10986 | -0.050354 | 123.0377 | 123.0286 | 122.9599 | -0.21973 | 122.9553 | 122.9553 | 123.0377 | -0.1831
4399.7969 | 123.2025 | -122.9324 | 0.07782 | -0.0078584 | -0.015169 | 0.016346 | 0.039227 | -0.02631 | -0.035305 | -0.012851 | 7.627e-05 | 0.0047488 | 0.0079319 | -0.094402 | -0.016842 | -0.00038438 | 0.041199 | -0.059509 | 0.004578 | 0.027466 | 0.12817 | 0.009155 | -0.12817 | -0.054932 | 0.045776 | -0.082397 | 0.068665 | 0.10529 | -0.068665 | -0.13275 | 122.9416 | 122.8043 | 0.050354 | 122.8729 | 122.9599 | 0.15564 | -0.036621 | 122.8638 | 122.7997 | -0.009155 | 122.8775 | 122.85 | 0.050354 | 0.027466 | 123.0606 | 122.9736 | 122.937 | -0.20599 | 123.0011 | 123.0377 | 122.9782 | -0.21057
4401.5938 | 123.2208 | -122.9233 | 0.07782 | -0.00022891 | -0.017946 | 0.01656 | 0.034741 | -0.025455 | -0.036587 | -0.01157 | -0.0075532 | 0.0043216 | 0.0068637 | -0.093334 | -0.014492 | 0.00068362 | 0.14648 | 0.064087 | 0.10529 | 0.091553 | 0.09613 | 0.041199 | -0.10071 | 0.068665 | 0.14191 | 0.032043 | 0.045776 | 0.045776 | -0.018311 | -0.068665 | 122.9645 | 122.8226 | 0.01831 | 122.9874 | 123.0148 | 0.19226 | 0.068664 | 122.905 | 122.8546 | -0.032044 | 122.9919 | 122.9553 | 0.10071 | -0.032044 | 123.0194 | 123.0698 | 123.0286 | -0.17853 | 122.9691 | 122.9691 | 123.0652 | -0.14649
4403.3438 | 123.1888 | -122.9279 | 0.09613 | -0.00022891 | -0.014742 | 0.014424 | 0.035169 | -0.027164 | -0.034237 | -0.011142 | 7.627e-05 | 0.006885 | 0.0077183 | -0.094402 | -0.010861 | 0.00089722 | 0.054932 | -0.032043 | -0.009155 | 0.027466 | 0.12817 | 0.013733 | -0.14191 | -0.059509 | 0.009155 | -0.11444 | 0.086975 | 0.082397 | -0.068665 | -0.11444 | 122.9416 | 122.7859 | 0.032044 | 122.8958 | 122.9553 | 0.16937 | -0.041198 | 122.8592 | 122.8134 | -0.009155 | 122.8683 | 122.8134 | 0 | -0.013733 | 123.056 | 122.9828 | 122.9187 | -0.23804 | 123.0148 | 123.0103 | 122.937 | -0.21057
4405.1406 | 123.1155 | -122.9691 | 0.1236 | -0.0078584 | -0.021364 | 0.019978 | 0.034314 | -0.0293 | -0.042569 | -0.012851 | 0.0077058 | 0.0019718 | 0.0051547 | -0.097393 | -0.013424 | 0.0023926 | 0.10529 | 0.082397 | 0.1236 | 0.082397 | 0.082397 | 0.032043 | -0.09613 | 0.041199 | 0.1236 | 0.027466 | 0.054932 | 0.009155 | -0.036621 | -0.10529 | 123.0011 | 122.8729 | -0.041199 | 123.0515 | 123.0515 | 0.17853 | -0.01831 | 122.9324 | 122.8638 | -0.068664 | 123.0103 | 122.9965 | 0.13275 | -0.11444 | 123.0515 | 123.0743 | 123.0927 | -0.21973 | 123.024 | 122.9782 | 123.0927 | -0.22888
4406.875 | 123.2346 | -122.937 | 0.086975 | -0.00022891 | -0.015169 | 0.016774 | 0.036878 | -0.029087 | -0.035733 | -0.011356 | -0.0075532 | 0.0036808 | 0.0064365 | -0.095257 | -0.014706 | 0.00068362 | 0.068665 | 0.009155 | 0.041199 | 0.050354 | 0.12817 | -0.013733 | -0.15106 | -0.027466 | 0.086975 | -0.045776 | 0.07782 | 0.045776 | -0.050354 | -0.11902 | 122.9233 | 122.7859 | 0.041199 | 122.9462 | 122.9874 | 0.20142 | -0.01831 | 122.8867 | 122.818 | -0.009155 | 122.9095 | 122.8912 | 0.073243 | -0.041199 | 123.0652 | 123.0057 | 122.9782 | -0.23804 | 123.0148 | 122.9828 | 123.024 | -0.20599
4408.6719 | 123.1384 | -122.9736 | 0.11444 | -0.00022891 | -0.022433 | 0.016346 | 0.037946 | -0.027805 | -0.04385 | -0.015842 | -0.0075532 | -0.00016437 | 0.0051547 | -0.094189 | -0.015774 | 0.0026062 | 0.045776 | 0.036621 | 0.07782 | 0.050354 | 0.10529 | 0.027466 | -0.10986 | -0.013733 | 0.091553 | 0.018311 | 0.059509 | 0.036621 | -0.027466 | -0.10071 | 123.0011 | 122.8638 | -0.009155 | 123.0103 | 123.024 | 0.16022 | -0.068665 | 122.9462 | 122.8729 | -0.054932 | 122.9599 | 122.9919 | 0.11902 | -0.07782 | 123.0789 | 123.0194 | 123.0515 | -0.2243 | 123.0331 | 123.0103 | 123.0652 | -0.21515
4410.4688 | 123.2346 | -122.9233 | 0.082397 | -0.00022891 | -0.013674 | 0.018055 | 0.035382 | -0.029087 | -0.034878 | -0.012851 | -0.0075532 | 0.0045352 | 0.0068637 | -0.094829 | -0.010647 | 0.00025642 | 0.09613 | 0.018311 | 0.032043 | 0.059509 | 0.1236 | 0.022888 | -0.12817 | 0.009155 | 0.091553 | -0.050354 | 0.068665 | 0.054932 | -0.059509 | -0.11902 | 122.9462 | 122.7951 | 0.041199 | 122.9416 | 122.9828 | 0.18768 | 0.013733 | 122.8638 | 122.8043 | -0.013732 | 122.9324 | 122.8729 | 0.068665 | -0.027465 | 123.0469 | 123.0194 | 122.9553 | -0.21057 | 122.9919 | 122.9782 | 123.0148 | -0.20142
4412.25 | 123.1338 | -122.9645 | 0.11902 | -0.0078584 | -0.019655 | 0.017201 | 0.040296 | -0.026523 | -0.042569 | -0.015415 | -0.0075532 | 4.9234e-05 | 0.0066501 | -0.094829 | -0.022396 | 0.0030334 | 0.045776 | 0.032043 | 0.086975 | 0.059509 | 0.11444 | 0.022888 | -0.09613 | 0.032043 | 0.1236 | 0.041199 | 0.050354 | 0.041199 | -0.036621 | -0.091553 | 122.9874 | 122.8683 | -0.004578 | 122.9965 | 123.024 | 0.15564 | -0.073243 | 122.9279 | 122.8729 | -0.068665 | 122.9965 | 123.0057 | 0.13275 | -0.07782 | 123.0789 | 123.0103 | 123.0515 | -0.21515 | 123.0148 | 123.0057 | 123.0881 | -0.21057
4414 | 123.111 | -122.9874 | 0.13275 | 0.0074006 | -0.019869 | 0.018483 | 0.036023 | -0.026523 | -0.040646 | -0.013492 | -0.0075532 | 0.004108 | 0.0043003 | -0.095257 | -0.017483 | 0.00047002 | 0.12817 | 0.073242 | 0.11444 | 0.064087 | 0.091553 | 0.050354 | -0.07782 | 0.054932 | 0.10071 | 0.013733 | 0.054932 | 0.027466 | -0.027466 | -0.091553 | 123.0377 | 122.9095 | -0.041198 | 123.0606 | 123.0515 | 0.14191 | -0.004577 | 122.9599 | 122.8958 | -0.077819 | 123.0423 | 123.0011 | 0.10529 | -0.10529 | 123.0789 | 123.1155 | 123.1018 | -0.21057 | 123.0423 | 123.0148 | 123.0881 | -0.2243
4415.7969 | 123.1064 | -122.9553 | 0.11444 | -0.00022891 | -0.018587 | 0.016133 | 0.034741 | -0.026096 | -0.038296 | -0.014988 | 7.627e-05 | 0.0028262 | 0.0034457 | -0.094402 | -0.014919 | 0.002179 | 0.13275 | 0.073242 | 0.11444 | 0.07782 | 0.10071 | 0.050354 | -0.10986 | 0.068665 | 0.12817 | 0.041199 | 0.032043 | 0.045776 | -0.022888 | -0.086975 | 123.0057 | 122.8455 | -0.013733 | 123.0286 | 123.0331 | 0.18768 | 0.01831 | 122.9324 | 122.8683 | -0.082398 | 123.024 | 122.9965 | 0.12817 | -0.068665 | 123.056 | 123.0881 | 123.0698 | -0.2243 | 122.9874 | 123.0011 | 123.0835 | -0.20142
4417.6094 | 123.2346 | -122.9279 | 0.091553 | -0.00022891 | -0.019015 | 0.016133 | 0.036237 | -0.026096 | -0.035946 | -0.013065 | 7.627e-05 | 0.0077396 | 0.0066501 | -0.095257 | -0.012356 | -0.0014526 | 0.059509 | -0.036621 | -0.009155 | 0.022888 | 0.14191 | 0 | -0.13275 | -0.027466 | 0.064087 | -0.059509 | 0.10071 | 0.068665 | -0.050354 | -0.10529 | 122.9279 | 122.7951 | 0.050354 | 122.8912 | 122.9507 | 0.15564 | -0.032044 | 122.8775 | 122.8226 | 0.009155 | 122.9004 | 122.8683 | 0.045777 | -0.022888 | 123.0698 | 122.9874 | 122.9187 | -0.2243 | 123.0286 | 122.9965 | 122.9919 | -0.19684
4419.3438 | 123.1155 | -122.9599 | 0.10071 | -0.0078584 | -0.020083 | 0.017201 | 0.036023 | -0.025883 | -0.037228 | -0.014133 | 7.627e-05 | 0.0036808 | 0.0064365 | -0.096111 | -0.014065 | 0.00089722 | 0.013733 | -0.018311 | 0.013733 | 0.009155 | 0.13275 | 0.009155 | -0.14191 | -0.045776 | 0.036621 | -0.082397 | 0.10071 | 0.064087 | -0.082397 | -0.1236 | 122.9691 | 122.818 | 0.032043 | 122.9416 | 122.9691 | 0.15106 | -0.086975 | 122.8775 | 122.8363 | 0 | 122.9141 | 122.8775 | 0.041199 | -0.036621 | 123.0927 | 122.9736 | 122.9736 | -0.24262 | 123.0606 | 123.024 | 122.9965 | -0.2243
4421.125 | 123.1522 | -122.9691 | 0.11902 | 0.0074006 | -0.021578 | 0.018055 | 0.036664 | -0.029087 | -0.043423 | -0.013065 | -0.015182 | -0.00016437 | 0.0062229 | -0.094829 | -0.017056 | -0.00059818 | 0.045776 | 0.018311 | 0.059509 | 0.054932 | 0.10986 | 0.022888 | -0.09613 | 0.004578 | 0.10986 | 0.004578 | 0.059509 | 0.050354 | -0.027466 | -0.10071 | 122.9919 | 122.8729 | -0.009156 | 122.9874 | 123.024 | 0.15106 | -0.073243 | 122.9416 | 122.8683 | -0.05951 | 122.9736 | 122.9736 | 0.10529 | -0.068665 | 123.0789 | 123.0148 | 123.0286 | -0.21515 | 123.0286 | 123.0194 | 123.0789 | -0.21973
4422.9219 | 123.23 | -122.9141 | 0.086975 | -0.00022891 | -0.022433 | 0.016987 | 0.034741 | -0.027591 | -0.035519 | -0.013279 | 7.627e-05 | 0.005817 | 0.0051547 | -0.094616 | -0.014065 | -0.00038438 | 0.14191 | 0.068665 | 0.10071 | 0.091553 | 0.10071 | 0.050354 | -0.10071 | 0.073242 | 0.12817 | 0.027466 | 0.036621 | 0.027466 | -0.036621 | -0.07782 | 122.9645 | 122.8134 | 0.013733 | 122.9828 | 123.0057 | 0.19226 | 0.054932 | 122.8775 | 122.8363 | -0.050354 | 122.9874 | 122.9416 | 0.10529 | -0.059509 | 123.0148 | 123.056 | 123.0148 | -0.18768 | 122.9507 | 122.9416 | 123.0423 | -0.16479
4424.6562 | 123.2254 | -122.937 | 0.091553 | -0.0078584 | -0.018587 | 0.015706 | 0.033246 | -0.027591 | -0.03616 | -0.01392 | 7.627e-05 | 0.0049624 | 0.0036593 | -0.094616 | -0.012142 | -0.00059818 | 0.13275 | 0.082397 | 0.091553 | 0.09613 | 0.091553 | 0.045776 | -0.086975 | 0.073242 | 0.12817 | 0.041199 | 0.050354 | 0.013733 | -0.013733 | -0.082397 | 122.9828 | 122.85 | 0 | 123.0194 | 123.0331 | 0.1831 | 0.041198 | 122.9233 | 122.8546 | -0.041199 | 123.0103 | 122.9782 | 0.1236 | -0.07782 | 123.0286 | 123.0698 | 123.0286 | -0.17853 | 122.9874 | 122.9507 | 123.0652 | -0.17395
4426.4531 | 123.1155 | -122.9691 | 0.1236 | -0.00022891 | -0.021151 | 0.017415 | 0.0388 | -0.029941 | -0.040005 | -0.015629 | 0.0077058 | 0.0034672 | 0.0087863 | -0.093548 | -0.016842 | 0.00089722 | 0.091553 | 0.054932 | 0.09613 | 0.045776 | 0.10071 | 0.050354 | -0.10529 | 0.027466 | 0.091553 | 0.009155 | 0.036621 | 0.045776 | -0.032043 | -0.091553 | 123.0194 | 122.8638 | -0.022888 | 123.024 | 123.0148 | 0.15106 | -0.032043 | 122.937 | 122.8775 | -0.086975 | 122.9965 | 122.9782 | 0.10071 | -0.07782 | 123.0698 | 123.0606 | 123.0652 | -0.22888 | 123.0057 | 123.0148 | 123.0606 | -0.21515
4428.25 | 123.111 | -123.0011 | 0.13733 | -0.0078584 | -0.021792 | 0.019123 | 0.034528 | -0.030582 | -0.039364 | -0.013492 | 7.627e-05 | 0.0043216 | 0.0072909 | -0.096111 | -0.012783 | 0.00068362 | 0.12817 | 0.091553 | 0.10986 | 0.068665 | 0.09613 | 0.050354 | -0.10986 | 0.068665 | 0.11444 | 0.004578 | 0.041199 | 0.027466 | -0.032043 | -0.086975 | 123.0515 | 122.8912 | -0.041199 | 123.0927 | 123.0698 | 0.17853 | -0.009155 | 122.9691 | 122.9141 | -0.09613 | 123.0698 | 123.0057 | 0.091553 | -0.10986 | 123.0972 | 123.1293 | 123.111 | -0.24719 | 123.0423 | 123.0286 | 123.1155 | -0.2243
4430.0625 | 123.1064 | -122.9874 | 0.11902 | -0.015487 | -0.024355 | 0.019123 | 0.034741 | -0.030369 | -0.037014 | -0.01456 | 7.627e-05 | 0.0030398 | 0.0051547 | -0.09547 | -0.016415 | -0.00059818 | 0.12817 | 0.068665 | 0.091553 | 0.054932 | 0.09613 | 0.041199 | -0.11444 | 0.041199 | 0.086975 | -0.004578 | 0.045776 | 0.032043 | -0.027466 | -0.082397 | 123.0286 | 122.8729 | -0.022889 | 123.056 | 123.0423 | 0.16937 | 0.009155 | 122.9599 | 122.905 | -0.073243 | 123.0286 | 122.9828 | 0.077819 | -0.086976 | 123.0835 | 123.1155 | 123.0789 | -0.23346 | 123.0331 | 123.0194 | 123.0743 | -0.20142
4431.7969 | 123.1659 | -122.937 | 0.10071 | 0.0074006 | -0.02051 | 0.016987 | 0.034955 | -0.027805 | -0.034024 | -0.014347 | 7.627e-05 | 0.007526 | 0.0060093 | -0.094829 | -0.013424 | 4.2822e-05 | 0.054932 | -0.032043 | -0.022888 | 0.018311 | 0.13733 | 0.013733 | -0.15106 | -0.064087 | 0.018311 | -0.09613 | 0.086975 | 0.07782 | -0.068665 | -0.1236 | 122.9507 | 122.7859 | 0.036621 | 122.905 | 122.9553 | 0.16937 | -0.045776 | 122.8683 | 122.8134 | -0.013733 | 122.8729 | 122.8409 | 0.027466 | -0.022888 | 123.0743 | 122.9919 | 122.9141 | -0.25177 | 123.024 | 123.0148 | 122.9553 | -0.2243
4433.5938 | 123.1613 | -122.9462 | 0.10986 | -0.00022891 | -0.018374 | 0.019337 | 0.037091 | -0.028873 | -0.040005 | -0.015415 | -0.0075532 | 0.0017582 | 0.0070773 | -0.096966 | -0.018551 | 0.00025642 | 0.13733 | 0.14191 | 0.14648 | 0.10529 | 0.10529 | 0.036621 | -0.10986 | 0.068665 | 0.19226 | 0.064087 | 0.054932 | 0.032043 | -0.032043 | -0.091553 | 122.9828 | 122.8363 | -0.004577 | 123.0881 | 123.0515 | 0.21515 | 0.027466 | 122.9141 | 122.8546 | -0.054931 | 123.0148 | 123.0103 | 0.15564 | -0.07782 | 123.0515 | 123.0835 | 123.0927 | -0.21973 | 123.0011 | 122.9782 | 123.1384 | -0.20142
4435.3906 | 123.1247 | -122.9828 | 0.11902 | -0.0078584 | -0.021578 | 0.017842 | 0.037732 | -0.028232 | -0.04086 | -0.014347 | 0.0077058 | 0.0036808 | 0.0075047 | -0.095684 | -0.017697 | -0.00017078 | 0.086975 | 0.032043 | 0.091553 | 0.036621 | 0.10986 | 0.032043 | -0.10529 | 0.027466 | 0.086975 | 0 | 0.059509 | 0.045776 | -0.041199 | -0.10986 | 123.0148 | 122.8775 | -0.009156 | 123.0148 | 123.0194 | 0.14191 | -0.032044 | 122.9416 | 122.8729 | -0.05951 | 123.0103 | 122.9828 | 0.10986 | -0.073243 | 123.0927 | 123.0698 | 123.0743 | -0.22431 | 123.0423 | 123.0286 | 123.0698 | -0.22888
4437.1094 | 123.1659 | -122.9599 | 0.12817 | -0.015487 | -0.023287 | 0.01891 | 0.035169 | -0.0293 | -0.039792 | -0.015415 | 0.0077058 | 0.00026283 | 0.0087863 | -0.096325 | -0.017269 | -0.00059818 | 0.050354 | 0.032043 | 0.07782 | 0.059509 | 0.11902 | 0.027466 | -0.10529 | 0.022888 | 0.11444 | 0.022888 | 0.045776 | 0.036621 | -0.022888 | -0.09613 | 122.9874 | 122.8546 | -0.009155 | 122.9919 | 123.0194 | 0.16479 | -0.07782 | 122.937 | 122.8638 | -0.082398 | 122.9828 | 122.9828 | 0.11902 | -0.091553 | 123.0789 | 123.0103 | 123.0377 | -0.23346 | 123.0057 | 122.9965 | 123.0743 | -0.2243
4438.9062 | 123.1888 | -122.9507 | 0.073242 | -0.0078584 | -0.01346 | 0.01421 | 0.0388 | -0.026951 | -0.031033 | -0.010929 | 0.0077058 | 0.0079532 | 0.0066501 | -0.09248 | -0.011501 | -0.0033752 | 0.14191 | 0.018311 | 0.036621 | 0.064087 | 0.1236 | 0.004578 | -0.14648 | 0.022888 | 0.07782 | -0.07782 | 0.073242 | 0.050354 | -0.045776 | -0.13275 | 122.9553 | 122.8043 | 0.050354 | 122.9691 | 123.0148 | 0.21057 | 0.068665 | 122.905 | 122.818 | 0 | 122.9736 | 122.8729 | 0.054931 | -0.022888 | 123.0743 | 123.0927 | 122.9874 | -0.21973 | 123.024 | 123.0011 | 123.0286 | -0.20599
4440.6406 | 123.2208 | -122.9416 | 0.07782 | -0.0078584 | -0.017946 | 0.014424 | 0.036023 | -0.030155 | -0.033383 | -0.01157 | 7.627e-05 | 0.0088076 | 0.0085727 | -0.092266 | -0.013638 | -0.0010254 | 0.11444 | 0.013733 | 0.036621 | 0.059509 | 0.13733 | 0.004578 | -0.13275 | 0.013733 | 0.082397 | -0.050354 | 0.073242 | 0.082397 | -0.041199 | -0.10529 | 122.9462 | 122.8088 | 0.059509 | 122.9553 | 123.0011 | 0.19226 | 0.036621 | 122.9004 | 122.8363 | -0.004578 | 122.9553 | 122.8912 | 0.054932 | 0.004577 | 123.0789 | 123.056 | 122.9782 | -0.21057 | 123.0148 | 123.024 | 123.024 | -0.18311
4442.4219 | 123.1842 | -122.9645 | 0.091553 | -0.0078584 | -0.017306 | 0.015706 | 0.036237 | -0.030582 | -0.034878 | -0.011783 | 7.627e-05 | 0.0083804 | 0.0079319 | -0.093975 | -0.011715 | 0.0019654 | 0.068665 | -0.009155 | 0 | 0.009155 | 0.11444 | 0.013733 | -0.12817 | -0.045776 | 0.032043 | -0.10986 | 0.068665 | 0.07782 | -0.064087 | -0.11444 | 122.9782 | 122.8363 | 0.022888 | 122.9553 | 122.9736 | 0.13733 | -0.022888 | 122.9004 | 122.85 | -0.022888 | 122.9187 | 122.8546 | 0.004578 | -0.013733 | 123.0789 | 123.0331 | 122.9645 | -0.21973 | 123.0331 | 123.0423 | 122.9965 | -0.20599
4444.2188 | 123.1247 | -122.9874 | 0.12817 | -0.00022891 | -0.02051 | 0.016346 | 0.036878 | -0.030155 | -0.044064 | -0.013279 | 7.627e-05 | 0.0028262 | 0.0075047 | -0.095684 | -0.016628 | 0.0026062 | 0.059509 | 0.032043 | 0.082397 | 0.059509 | 0.086975 | 0.036621 | -0.082397 | 0 | 0.10529 | 0.013733 | 0.059509 | 0.041199 | -0.036621 | -0.082397 | 123.024 | 122.905 | -0.041199 | 123.0194 | 123.0469 | 0.14191 | -0.068665 | 122.9507 | 122.905 | -0.068665 | 122.9874 | 123.0011 | 0.09613 | -0.086975 | 123.0743 | 123.0469 | 123.0698 | -0.21057 | 123.0469 | 123.0286 | 123.0927 | -0.21057
4445.9531 | 123.1842 | -122.9645 | 0.082397 | -0.015487 | -0.017092 | 0.013356 | 0.035596 | -0.030155 | -0.032956 | -0.010929 | -0.015182 | 0.0079532 | 0.0064365 | -0.093548 | -0.012356 | 0.00089722 | 0.10986 | 0.009155 | 0.022888 | 0.054932 | 0.12817 | 0.018311 | -0.11902 | -0.004578 | 0.086975 | -0.073242 | 0.073242 | 0.068665 | -0.059509 | -0.11902 | 122.9828 | 122.8455 | 0.045777 | 122.9736 | 123.0194 | 0.17395 | 0.027466 | 122.905 | 122.8455 | -0.009155 | 122.9599 | 122.8912 | 0.045777 | -0.013732 | 123.0927 | 123.0743 | 122.9874 | -0.20142 | 123.0377 | 123.0331 | 123.0515 | -0.20142
4447.75 | 123.1659 | -122.9691 | 0.1236 | -0.00022891 | -0.023073 | 0.018483 | 0.036237 | -0.0293 | -0.043423 | -0.013492 | 0.015335 | 0.00026283 | 0.0077183 | -0.096111 | -0.01791 | 0.0017518 | 0.10071 | 0.10986 | 0.14191 | 0.091553 | 0.10071 | 0.041199 | -0.10529 | 0.073242 | 0.17853 | 0.082397 | 0.041199 | 0.027466 | -0.027466 | -0.07782 | 123.0103 | 122.8638 | -0.022888 | 123.0789 | 123.0606 | 0.19684 | -0.022888 | 122.9416 | 122.8912 | -0.082397 | 123.0423 | 123.0515 | 0.16022 | -0.09613 | 123.0698 | 123.0698 | 123.111 | -0.22888 | 123.0103 | 122.9965 | 123.1476 | -0.20142
4449.4844 | 123.2117 | -122.9324 | 0.10071 | -0.0078584 | -0.013247 | 0.016987 | 0.040296 | -0.025669 | -0.03616 | -0.013279 | 7.627e-05 | 0.0062442 | 0.0094273 | -0.09312 | -0.017056 | -0.00059818 | 0.050354 | -0.050354 | -0.027466 | 0.013733 | 0.14648 | 0 | -0.1236 | -0.064087 | 0.054932 | -0.068665 | 0.073242 | 0.064087 | -0.064087 | -0.13275 | 122.9324 | 122.8088 | 0.045776 | 122.8821 | 122.9462 | 0.13733 | -0.050354 | 122.8683 | 122.7997 | -0.027466 | 122.8683 | 122.8638 | 0.064086 | -0.036621 | 123.0789 | 122.9828 | 122.905 | -0.2243 | 123.0057 | 122.9965 | 122.9874 | -0.23346
4451.2656 | 123.1979 | -122.9645 | 0.082397 | -0.0078584 | -0.017733 | 0.014851 | 0.035809 | -0.029087 | -0.034237 | -0.010715 | 7.627e-05 | 0.0077396 | 0.0066501 | -0.093975 | -0.011715 | -0.00038438 | 0.068665 | -0.009155 | -0.004578 | 0.027466 | 0.15106 | 0 | -0.1236 | -0.032043 | 0.027466 | -0.10529 | 0.091553 | 0.068665 | -0.054932 | -0.11902 | 122.9645 | 122.8409 | 0.068665 | 122.9553 | 122.9919 | 0.15106 | -0.013732 | 122.9095 | 122.8455 | 0.009156 | 122.9324 | 122.8592 | 0.013733 | -0.013732 | 123.1155 | 123.0331 | 122.9599 | -0.20599 | 123.056 | 123.0331 | 122.9919 | -0.20142
4453.0625 | 123.111 | -122.9828 | 0.10986 | -0.0078584 | -0.017519 | 0.01656 | 0.036664 | -0.027164 | -0.042569 | -0.014774 | 7.627e-05 | 0.0019718 | 0.0060093 | -0.098034 | -0.015347 | 0.0013244 | 0.10986 | 0.11444 | 0.13275 | 0.091553 | 0.09613 | 0.036621 | -0.10071 | 0.041199 | 0.16479 | 0.045776 | 0.045776 | 0.027466 | -0.027466 | -0.10529 | 123.0194 | 122.8821 | -0.013733 | 123.0972 | 123.0743 | 0.19226 | 0 | 122.9553 | 122.8775 | -0.064087 | 123.024 | 123.0286 | 0.15106 | -0.082397 | 123.0789 | 123.0927 | 123.1155 | -0.21057 | 123.0286 | 123.0103 | 123.1476 | -0.21515
4454.8125 | 123.1018 | -122.9919 | 0.10986 | -0.0078584 | -0.018801 | 0.016774 | 0.037091 | -0.027591 | -0.041714 | -0.013706 | -0.0075532 | 0.0028262 | 0.0077183 | -0.095898 | -0.016201 | 0.0017518 | 0.10071 | 0.07782 | 0.091553 | 0.082397 | 0.11444 | 0.022888 | -0.11444 | 0.004578 | 0.11444 | -0.022888 | 0.068665 | 0.050354 | -0.054932 | -0.1236 | 123.0148 | 122.8775 | 0.004578 | 123.0698 | 123.0743 | 0.19684 | -0.009155 | 122.937 | 122.8683 | -0.041198 | 122.9965 | 122.9691 | 0.10071 | -0.059509 | 123.1064 | 123.0927 | 123.0835 | -0.2243 | 123.0606 | 123.0423 | 123.1064 | -0.23346
4456.6094 | 123.23 | -122.9553 | 0.09613 | -0.00022891 | -0.018374 | 0.016987 | 0.033673 | -0.027164 | -0.038083 | -0.014133 | 7.627e-05 | 0.0028262 | 0.0089999 | -0.093548 | -0.013638 | 0.00047002 | 0.12817 | 0.086975 | 0.10529 | 0.09613 | 0.082397 | 0.050354 | -0.10071 | 0.059509 | 0.15106 | 0.036621 | 0.032043 | 0.027466 | -0.022888 | -0.09613 | 123.0057 | 122.8546 | -0.013733 | 123.0423 | 123.0515 | 0.19684 | 0.032044 | 122.9324 | 122.8592 | -0.064087 | 123.0148 | 122.9919 | 0.13275 | -0.068664 | 123.0377 | 123.0835 | 123.0606 | -0.19684 | 122.9874 | 122.9828 | 123.1064 | -0.19226
4458.3906 | 123.262 | -122.9462 | 0.086975 | -0.00022891 | -0.017092 | 0.015278 | 0.035809 | -0.026951 | -0.035092 | -0.014133 | -0.0075532 | 0.0064578 | 0.0083591 | -0.095043 | -0.013424 | -0.00017078 | 0.050354 | -0.041199 | 0.004578 | 0.018311 | 0.14191 | 0.004578 | -0.13275 | -0.018311 | 0.027466 | -0.054932 | 0.059509 | 0.050354 | -0.050354 | -0.11902 | 122.9507 | 122.8134 | 0.054932 | 122.905 | 122.9645 | 0.15106 | -0.036621 | 122.8958 | 122.8271 | -0.027466 | 122.9279 | 122.8912 | 0.064087 | -0.036621 | 123.0881 | 122.9965 | 122.9507 | -0.21973 | 123.0057 | 122.9965 | 122.9736 | -0.20599
4460.1875 | 123.1522 | -122.9507 | 0.11902 | -0.00022891 | -0.020937 | 0.018269 | 0.037518 | -0.027164 | -0.042782 | -0.01456 | -0.0075532 | -0.00016437 | 0.0087863 | -0.095898 | -0.018765 | 0.0043152 | 0.036621 | 0.032043 | 0.082397 | 0.059509 | 0.10986 | 0.022888 | -0.1236 | -0.004578 | 0.09613 | 0.027466 | 0.050354 | 0.050354 | -0.032043 | -0.1236 | 122.9736 | 122.8271 | -0.009156 | 122.9828 | 123.0103 | 0.1831 | -0.082398 | 122.9187 | 122.8271 | -0.068665 | 122.9462 | 122.9782 | 0.15106 | -0.068665 | 123.0606 | 122.9874 | 123.0331 | -0.24261 | 123.0011 | 123.0011 | 123.0469 | -0.24261
4461.9375 | 123.1567 | -122.9782 | 0.10986 | 0.0074006 | -0.01816 | 0.017415 | 0.037732 | -0.026096 | -0.038083 | -0.014133 | 7.627e-05 | 0.0019718 | 0.0094273 | -0.095257 | -0.015774 | -0.001239 | 0.14191 | 0.082397 | 0.11902 | 0.09613 | 0.073242 | 0.050354 | -0.082397 | 0.059509 | 0.14648 | 0.027466 | 0.032043 | 0.022888 | -0.022888 | -0.07782 | 123.0286 | 122.8958 | -0.036621 | 123.0606 | 123.0743 | 0.17853 | 0.032044 | 122.9553 | 122.9004 | -0.07782 | 123.0377 | 123.0057 | 0.10529 | -0.086975 | 123.0515 | 123.1201 | 123.0972 | -0.19226 | 123.0103 | 123.0011 | 123.1247 | -0.18768